Merced | CA | 95340-0961 |  | 2012-05-15 | 2012-05-15 14:36 | 2012-05-15 15:10 | CARRIER - 48GS-030060301 | 58 | 1.8 | Yes | Yes | 28.2 | 22.3 | 5.9 | ACFF0F88825A4C2FBCB18832B91BEA46 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Newman | CA | 95360-2411 |  | 2012-05-29 | 2012-05-29 11:01 | 2012-05-29 11:18 | RUUD - NA | 78 | 2.3 | Yes | Yes | 17.7 | 19.7 | -2 | 252423B75864482B9ECCF0783F676E11 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Magalia | CA | 95954-9616 |  | 2012-05-31 | 2012-05-31 10:23 | 2012-05-31 11:15 | RHEEM - RPFB-036JAS | 94 | 4.9 | Yes | Yes | 28.8 | 23.4 | 5.4 | 411A6486D7C1430EA045813567B8432C |  | R22 | Non-TXV |  | 5.213% | 0.94787 | 10.02% | [5 empty] | Non-TXV | 5.213%
Fresno | CA | 93706-9119 |  | 2012-06-12 | 2012-06-12 13:38 | 2012-06-12 14:01 | RUUD - N/A | 75 | 5.4 | Yes | Yes | 19.7 | 20.3 | -0.6 | 444BA37EBEE148B9903CD3F7700283DD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.2% | 0.928 | 13.84% | [5 empty] | Non-TXV | 7.2%
Oroville | CA | 95965-4445 |  | 2012-06-06 | 2012-06-06 10:40 | 2012-06-06 11:30 | AMERICAN STANDARD - YCC036F1MOBH | 84 | 2.7 | Yes | Yes | 20 | 19.9 | 0.1 | D5B0A55DFDBD45CDBF0ECAC9F582FEB3 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Merced | CA | 95341-7000 |  | 2012-05-15 | 2012-05-15 12:38 | 2012-05-15 13:05 | BRYANT - 582ANW03606ONBAF | 72 | 3 | Yes | Yes | 23.8 | 19.7 | 4.2 | E7AC05A3F2DA46D68FE3040F6C146F69 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Selma | CA | 93662-3974 |  | 2012-08-14 | 2012-08-14 11:36 | 2012-08-14 11:54 | PAYNE - N/A | 90 | 2.6 | Yes | Yes | 19.1 | 17.4 | 1.7 | 6CEAD3EB17CA4853B8A3CB671A5002D7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Chico | CA | 95928-4017 |  | 2012-07-02 | 2012-07-02 10:58 | 2012-07-02 11:23 | COLEMAN - 565BJ024 | 70 | 3 | Yes | Yes | 24.7 | 21 | 3.7 | C539C831A3D24B23895CCF703ED45E95 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Manteca | CA | 95336-4141 |  | 2012-05-07 | 2012-05-07 15:00 | 2012-05-07 20:22 | LENNOX - HS19-461V-3P | 126 | 39.4 | Yes | Yes | 19.1 | 20.8 | -1.7 | 287DAA06AA454EB79058E6E0D3F4218D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 31.27% | 0.6873 | 60.09% | [5 empty] | Non-TXV | 31.27%
Merced | CA | 95341-7018 |  | 2012-05-10 | 2012-05-10 12:10 | 2012-05-10 12:25 | GOODMAN - CLJ36-1A | 109 | -7.7 | Yes | Yes | 21.1 | 20.9 | 0.2 | E18358F1CA4142DFA41C66EDD940E289 |  | R22 | Non-TXV |  | -7.064% | 1.0706 | 1.978% |  |  |  |  | Non-TXV |  |  | -7.064%
Stockton | CA | 95210-3443 |  | 2012-06-01 | 2012-06-01 09:00 | 2012-06-01 09:18 | BDP - 569BJ024 | 72 | -4.2 | Yes | Yes | 26 | 20.1 | 5.9 | 1DA123181FED48B5BD36C060470343EF |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Escalon | CA | 95320-2049 |  | 2012-07-12 | 2012-07-12 11:20 | 2012-07-12 11:45 | PAYNE - PA10JA042-B | 85 | 15.1 | Yes | Yes | 18.2 | 20.5 | -2.3 | B3F622650CDD431FA6BA7C09FC592ACD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.76% | 0.82235 | 34.14% | [5 empty] | Non-TXV | 17.76%
Chico | CA | 95973-8912 |  | 2012-05-11 | 2012-05-11 09:52 | 2012-05-11 10:08 | TRAIN - TIP048C1OOA4 | 147 | 8.7 | Yes | Yes | 22.8 | 23.1 | -0.3 | 04720449A80641FD8DC6093A7B2E4200 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.918% | 0.94082 | 11.37% | [5 empty] | Non-TXV | 5.918%
Merced | CA | 95341-7000 |  | 2012-05-09 | 2012-05-09 11:05 | 2012-05-09 11:25 | PAYNE - PY1PNB036060ABAA | 68 | 5.1 | Yes | Yes | 23.5 | 19.4 | 4.1 | 5C1983A3EA8240F7AF57E99BD71C08AC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Grass Valley | CA | 95945-6642 |  | 2012-05-30 | 2012-05-30 15:05 | 2012-05-30 15:28 | RHEEM - UNK | 58 | 16.7 | Yes | Yes | 21.7 | 19.9 | 1.8 | 7E96E1E5EC604B5D8EAA8C0061BEDF51 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 28.79% | 0.71207 | 55.33% | [5 empty] | Non-TXV | 28.79%
Fresno | CA | 93727-3516 |  | 2012-08-07 | 2012-08-07 09:58 | 2012-08-07 10:14 | BDP - 585CJ042075 | 104 | 3.7 | Yes | Yes | 22.7 | 20.7 | 2.1 | 7F9316803A014B2C9FC97C700665292A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.558% | 0.96442 | 6.837% | [5 empty] | Non-TXV | 3.558%
Stockton | CA | 95210-3608 |  | 2012-06-06 | 2012-06-06 13:10 | 2012-06-06 13:27 | PAYNE - PA13NA048-C | 114 | 4 | Yes | Yes | 24.1 | 20.8 | 3.3 | 0D42BF060E1843B189DC41325BBF3A27 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Stockton | CA | 95210-4631 |  | 2012-05-31 | 2012-05-31 13:04 | 2012-05-31 13:21 | BRYANT - 563CN018-B | 80 | 2.5 | Yes | Yes | 20.2 | 20.8 | -0.6 | 7454B4EF023C41C2A24F21A24D8B4679 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93711-0712 |  | 2012-07-30 | 2012-07-30 13:22 | 2012-07-31 18:46 | PAYNE - 58A03680YAC | 71 | 2.5 | Yes | Yes | 19.2 | 20.1 | -0.9 | 429B91A65D5A46758A853D6D3D094950 |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Oakdale | CA | 95361-3242 |  | 2012-06-12 | 2012-06-12 10:53 | 2012-06-12 11:15 | PAYNE - PY1PNB030060AAAA | 55 | 1.9 | Yes | Yes | 19.9 | 20.4 | -0.5 | 430C94112A7A43998603414D8363C61F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Merced | CA | 95341-7018 |  | 2012-05-10 | 2012-05-10 13:01 | 2012-05-10 13:19 | GOODMAN - CLJ36-1A | 109 | -6.4 | Yes | Yes | 25.6 | 21.6 | 4.1 | E6B3103BD47F4045B09B814CB4806472 |  | R22 | Non-TXV |  | -5.872% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.872%
Grass Valley | CA | 95945-6641 |  | 2012-06-14 | 2012-06-14 14:41 | 2012-06-14 14:41 | RUUD - UNK | 66 | 0 | Yes | Yes | 21.8 | 18.8 | 3 | 6BE23B661BC742FE8F2DB0D6E207EB4E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-8015 |  | 2012-06-13 | 2012-06-13 13:34 | 2012-06-13 14:14 | TRANE - 223ANA036-C | 127 | 10.8 | Yes | Yes | 21.6 | 22.5 | -0.9 | 846DB33059F34F1EA0120CA5921D5623 |  | R410A | Non-TXV |  | 8.504% | 0.91496 | 16.34% | [5 empty] | Non-TXV | 8.504%
Chico | CA | 95926-3467 |  | 2012-05-15 | 2012-05-15 14:17 | 2012-05-15 15:13 | CARRIER - UNK | 91 | 6 | Yes | Yes | 25.6 | 22.3 | 3.3 | 5CE3444D8BDA425E85C7A6770A0764A3 |  | R22 | Non-TXV |  | 6.593% | 0.93407 | 12.67% | [5 empty] | Non-TXV | 6.593%
Paradise | CA | 95969-6655 |  | 2012-05-15 | 2012-05-15 10:49 | 2012-05-15 11:07 | CARRIER - 50YQ036310 | 95 | 3.2 | Yes | Yes | 21 | 22 | -1 | FE236EB258A34FD5857CF3440719504C |  | R22 | Non-TXV |  | 3.368% | 0.96632 | 6.473% | [5 empty] | Non-TXV | 3.368%
Cameron Park | CA | 95682-8936 |  | 2012-07-26 | 2012-07-26 13:30 | 2012-07-26 13:30 | TAPPAN - CRMH-24-44-T | 90 | 0 | Yes | Yes | 20 | 21.8 | -1.8 | E0035C609C3C44D79E546FD88580FD16 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-5634 |  | 2012-05-09 | 2012-05-09 15:08 | 2012-05-09 15:45 | CARRIER - 4087C33149 | 69 | 5.1 | Yes | Yes | 20.7 | 21.9 | -1.2 | 17BF16634BA542E8B253D5CCD440E992 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.391% | 0.92609 | 14.2% | [5 empty] | Non-TXV | 7.391%
Los Banos | CA | 93635-3105 |  | 2012-05-16 | 2012-05-16 11:21 | 2012-05-16 11:40 | BRYANT - 583BNW036060AB | 104 | -6.1 | Yes | Yes | 20.9 | 19.1 | 1.8 | 07675F162FFC41AE8BA0BAAA21FC5F00 |  | R410A | Non-TXV |  | -5.865% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.865%
Los Banos | CA | 93635-6332 |  | 2012-06-13 | 2012-06-13 10:53 | 2012-06-13 11:19 | GOODMAN - CK30-1D | 70 | 4.9 | Yes | Yes | 19.5 | 19.8 | -0.3 | 85EDB7469C434D38A728B5D716AAA9E5 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Clovis | CA | 93612-4841 |  | 2012-05-30 | 2012-05-30 14:37 | 2012-05-30 14:55 | YORK - D2NP024N05606A | 100 | 3.2 | Yes | Yes | 20.5 | 20.7 | -0.2 | D78EF74815F54E119B23505FF2C4EE41 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Clovis | CA | 93611-3055 |  | 2012-08-06 | 2012-08-06 15:56 | 2012-08-06 16:17 | BDP - 558ANW036060ABAD | 69 | 4.5 | Yes | Yes | 19.3 | 21.3 | -2 | B23AEEF7EACC4729B8F1682BFD0016B9 |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Clovis | CA | 93612-0723 |  | 2012-06-13 | 2012-06-13 14:09 | 2012-06-13 14:09 | AMERICAN STANDARD - 2YCC3030A1040AA | 89 | 0 | Yes | Yes | 14 | 16.1 | -2.1 | CB2FA5BDF7AD4C9E9BAABA09C29FCFCB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3765 |  | 2012-05-17 | 2012-05-17 15:00 | 2012-05-17 15:32 | TRANE - BTD724A10080 | 68 | 4.8 | Yes | Yes | 27 | 21 | 6 | 639CA6449BC84F428028E16900DE29B0 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Stockton | CA | 95207-6015 |  | 2012-06-20 | 2012-06-20 11:23 | 2012-06-20 11:51 | PAYNE - PY1PNB024060AAAA | 53 | 6.7 | Yes | Yes | 18 | 19.9 | -1.9 | 59915B729AEF4CE1B55723F4EA9D43B8 |  | R22 | Non-TXV |  | 12.64% | 0.87358 | 24.29% | [5 empty] | Non-TXV | 12.64%
Grass Valley | CA | 95945-7878 |  | 2012-05-08 | 2012-05-08 16:38 | 2012-05-08 16:38 | CARRIER - 38YH018300 | 116 | 0 | Yes | Yes | 19.1 | 21.8 | -2.7 | 1B998BC95DAE467CB8EE024A26C1C45B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-3918 |  | 2012-06-06 | 2012-06-06 14:34 | 2012-06-06 15:13 | CARRIER - 38EB0423000 | 80 | 2.5 | Yes | Yes | 22.5 | 21.5 | 1 | 5E3251BA931D45D98EEB2D656218BD2F |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Los Banos | CA | 93635-3426 |  | 2012-05-14 | 2012-05-14 12:34 | 2012-05-14 12:59 | GOODMAN - CK24-1B | 74 | -4.4 | Yes | Yes | 20.7 | 19.8 | 0.9 | C01D869605404563AE25BDA21163AF07 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Merced | CA | 95341-7018 |  | 2012-05-10 | 2012-05-10 15:20 | 2012-05-10 15:38 | GOODMAN - CLJ30-1A | 105 | -6.2 | Yes | Yes | 23.4 | 21.8 | 1.7 | D540A07856DD407882264A879AC2DA93 |  | R22 | Non-TXV |  | -5.905% | 1.059 | 1.654% |  |  |  |  | Non-TXV |  |  | -5.905%
Los Banos | CA | 93635-5131 |  | 2012-05-16 | 2012-05-16 11:20 | 2012-05-16 11:50 | GOODMAN - CJ48-1GB | 149 | -14 | Yes | Yes | 24.2 | 20.4 | 3.8 | 94AAC2CF0D484AC385EBDDD9F89C63E7 |  | R22 | Non-TXV |  | -9.396% | 1.094 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.396%
Atwater | CA | 95301-3721 |  | 2012-05-10 | 2012-05-10 15:30 | 2012-05-10 15:30 | CARRIER - 48DL003M308379 | 54 | 0 | Yes | Yes | -1.5 | 9.2 | -10.7 | 79C98022FDB74100B575CC0E891A586A | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2160 |  | 2012-05-17 | 2012-05-17 12:27 | 2012-05-17 12:46 | RHEEM - D1NA024N03606C | 50 | 6.2 | Yes | Yes | 20.5 | 18.8 | 1.7 | 2D8335C48DBD457FBF128A7AF9B759DE | OK: Verified Refrigerant Charge | R22 | TXV |  | 12.4% | 0.876 | 23.83% | [5 empty] | TXV | 12.4%
Fresno | CA | 93727-1936 |  | 2012-08-07 | 2012-08-07 11:33 | 2012-08-07 11:53 | AMANA - PGA36B0702C | 112 | 10.8 | Yes | Yes | 17.6 | 19.5 | -1.9 | F49BEF89FE28496EB7C5DDBF121DB31C |  | R22 | Non-TXV |  | 9.643% | 0.90357 | 18.53% | [5 empty] | Non-TXV | 9.643%
Grass Valley | CA | 95945-4124 |  | 2012-05-16 | 2012-05-16 15:16 | 2012-05-16 15:35 | FRASER-JOHNSTON - HDEC-F018SB | 56 | 7.2 | Yes | Yes | 22.7 | 19.9 | 2.8 | B45050387C454EAA911ED5C1BD2A1C42 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Merced | CA | 95341-7008 |  | 2012-05-10 | 2012-05-10 14:01 | 2012-05-10 14:01 | GOODMAN - CLJ30 | 96 | 0 | Yes | Yes | 24.6 | 22.1 | 2.5 | EF0B8A97DC3D420481C83922DF895B16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2053 |  | 2012-05-11 | 2012-05-11 10:36 | 2012-05-11 10:53 | BDP - 585A030080YACR | 50 | 1.5 | Yes | Yes | 22.1 | 20.9 | 1.2 | 6E17B5D0FF984A56AC4241FC293B7956 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Yuba City | CA | 95991-6332 |  | 2012-07-20 | 2012-07-20 10:18 | 2012-07-20 10:37 | DAY & NIGHT - N4A3300AKC200 | 74 | 3.1 | Yes | Yes | 16 | 18.2 | -2.2 | 3B21121B0DF74FB2892578529221004D |  | R410A | TXV |  | 4.189% | 0.95811 | 8.051% | [5 empty] | TXV | 4.189%
Stockton | CA | 95210-5239 |  | 2012-05-29 | 2012-05-29 13:51 | 2012-05-29 14:09 | CARRIER - 585HJ036060 | 102 | -6 | Yes | Yes | 25.4 | 19.4 | 6 | 3056D857DAA6475F84C38381FEA7F530 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95206-6160 |  | 2012-05-08 | 2012-05-08 09:46 | 2012-05-08 09:46 | CARRIER - 38CKCO60370 | 134 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | A3CDFE57DEA749348BEDCFE6AE882C6F | OK: Verified Refrigerant Charge | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-2850 |  | 2012-05-15 | 2012-05-15 13:20 | 2012-05-15 14:14 | CARRIER - A5313993 | 82 | 3.4 | Yes | Yes | 26.9 | 21.2 | 5.7 | E406008079D64899B934F12A6D62354E |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Los Banos | CA | 93635-2712 |  | 2012-05-08 | 2012-05-08 11:01 | 2012-05-08 11:28 | TRANE - TTR036C100A1 | 92 | 4.5 | Yes | Yes | 21 | 21 | 0 | 12036ED7C8A9460E985B1F078787E697 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.891% | 0.95109 | 9.4% | [5 empty] | Non-TXV | 4.891%
Merced | CA | 95348-3660 |  | 2012-05-17 | 2012-05-17 13:18 | 2012-05-17 13:35 | TRANE - BTD724A100B0 | 68 | 4.6 | Yes | Yes | 21.9 | 24 | -2 | 9CFCB60C92794A10A45085398F3E58C7 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | Non-TXV | 6.765%
Fresno | CA | 93726-5003 |  | 2012-05-30 | 2012-05-30 11:14 | 2012-05-30 11:40 | WESTINGHOUSE - 1D02401A | 85 | 2.7 | Yes | Yes | 19.8 | 19.9 | -0.1 | DA9AC850DB9C49989BBE7CC413A30617 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Cutler | CA | 93615-2209 |  | 2012-07-02 | 2012-07-02 15:37 | 2012-07-02 16:02 | GOODMAN - GSC130481AF | 152 | 4.6 | Yes | Yes | 15.1 | 18.1 | -3 | C92FE946DDD24BABB2F3E87107C3B741 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95210-1779 |  | 2012-05-10 | 2012-05-10 13:09 | 2012-05-10 13:26 | CARRIER - 38FAU24310 | 58 | -3.4 | Yes | Yes | 18.6 | 21.5 | -2.9 | 2019FBBF8CAE4BF1B9D88D7453873E32 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Penn Valley | CA | 95946-8927 |  | 2012-08-14 | 2012-08-14 17:45 | 2012-08-14 17:45 | GOODMAN - CK24-1B | 71 | 0 | Yes | Yes | 18.9 | 20.1 | -1.2 | C0633D6896624DB689C1632D644EADA4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3660 |  | 2012-05-17 | 2012-05-17 11:37 | 2012-05-17 12:06 | TRANE - BTD724A100B0 | 68 | 5.8 | Yes | Yes | 18 | 21 | -3 | C1147D2E590F48D3AAE5475C07848E37 |  | R22 | Non-TXV |  | 8.529% | 0.91471 | 16.39% | [5 empty] | Non-TXV | 8.529%
Stockton | CA | 95207-6064 |  | 2012-06-15 | 2012-06-15 13:05 | 2012-06-15 13:25 | GE - PGB024050-1REV | 85 | 8.2 | Yes | Yes | 24.2 | 21.7 | 2.6 | 0389687AFD8D48A2AB7D2754C1539D52 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Stockton | CA | 95209-2231 |  | 2012-05-22 | 2012-05-22 14:10 | 2012-05-22 14:26 | RHEEM - UNK | 55 | 11.3 | Yes | Yes | 22.2 | 20.9 | 1.3 | 3F31881166DC41708B68E08FB6C62385 |  | R22 | Non-TXV |  | 20.55% | 0.79455 | 39.48% | [5 empty] | Non-TXV | 20.55%
Stockton | CA | 95206-3301 |  | 2012-05-22 | 2012-05-22 14:24 | 2012-05-22 14:49 | RHEEM - RRKA-A030JK06X | 54 | 4 | Yes | Yes | 17.4 | 19.9 | -2.5 | 61535EF8B74D47898C2F6EE60851B56C |  | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
Fresno | CA | 93722-4538 |  | 2012-06-06 | 2012-06-06 10:36 | 2012-06-06 10:56 | AMERICAN STANDARD - 2YCX3024A1040AA | 72 | 2.1 | Yes | Yes | 23.9 | 20.4 | 3.5 | 08E098F4814E4F6492A4D05C69F120AD |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Stockton | CA | 95207-6064 |  | 2012-06-28 | 2012-06-28 10:01 | 2012-06-28 10:01 | RHEEM - UNK | 96 | 0 | Yes | Yes | 21.1 | 19.3 | 1.8 | A15548DBD29145E8BC845B555AEB2641 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1856 |  | 2012-05-29 | 2012-05-29 09:38 | 2012-05-29 09:56 | BDP - 561AJX03000AAAA | 83 | 2.4 | Yes | Yes | 18 | 20.7 | -2.7 | 2DE4C0632C314E0F8D549744109AA109 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Stockton | CA | 95210-2617 |  | 2012-06-07 | 2012-06-07 09:53 | 2012-06-07 10:10 | RUUD - RRNL-B024JK06X | 77 | -4.5 | Yes | Yes | 21.7 | 19.5 | 2.2 | 02CEA97886084E23BAE407F7623BA8C3 |  | R410A | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Los Banos | CA | 93635-5389 |  | 2012-05-17 | 2012-05-17 10:22 | 2012-05-17 10:45 | BRYANT - 561CJ042 | 80 | -4.4 | Yes | Yes | 26.2 | 23.1 | 3.1 | AA62CDD26BCB4E5282B45BAE70750DA0 | OK: Verified Refrigerant Charge | R22 | TXV |  | -5.5% | 1.055 | 1.54% |  |  |  |  | TXV |  |  | -5.5%
Los Banos | CA | 93635-3253 |  | 2012-05-14 | 2012-05-14 15:09 | 2012-05-14 15:37 | ARCOAIR - AH036GA3 | 124 | -7.3 | Yes | Yes | 20.4 | 20.8 | -0.4 | 43E6F681F1AF4AF694370D0F521345B7 |  | R22 | Non-TXV |  | -5.887% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.887%
Stockton | CA | 95210-4440 |  | 2012-06-13 | 2012-06-13 14:13 | 2012-06-13 14:13 | PAYNE - 591ANX060000AAAA | 170 | 0 | Yes | Yes | 26.3 | 20.4 | 6 | 8E628D43F336412BBFE1C72CD9B1E71B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6721 |  | 2012-05-16 | 2012-05-16 12:33 | 2012-05-16 12:53 | BDP COMPNAY - 585HJ030040 | 68 | 2 | Yes | Yes | 22.7 | 20.4 | 2.3 | D97854D6B05F4C899853FC41F6AAB65B |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Manteca | CA | 95337-5461 |  | 2012-05-11 | 2012-05-11 10:05 | 2012-05-11 10:22 | YORK - H1RD036S06A | 145 | 4.4 | Yes | Yes | 19.7 | 20.6 | -0.9 | 258D0247A13846B6BA9813FB8A467365 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.832% | [5 empty] | Non-TXV | 3.034%
Merced | CA | 95340-6017 |  | 2012-05-08 | 2012-05-08 12:37 | 2012-05-08 12:57 | PAYNE - UNK | 85 | 6.6 | Yes | Yes | 22.2 | 22.3 | -0.1 | BBA0ACBF854342208FE19C04F83008AB | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | Non-TXV | 7.765%
Riverbank | CA | 95367-3306 |  | 2012-05-29 | 2012-05-29 15:16 | 2012-05-29 15:39 | KENMORE - TCA242AKA1 | 125 | 3.8 | Yes | Yes | 19.3 | 19.3 | 0 | 21A9575896054B888B9FE8E7AEA1DE90 |  | R22 | Non-TXV |  | 3.04% | 0.9696 | 5.842% | [5 empty] | Non-TXV | 3.04%
Stockton | CA | 95206-0000 |  | 2012-05-15 | 2012-05-15 11:57 | 2012-05-15 12:16 | GOODMAN - GSC130481AA | 158 | 18.2 | Yes | Yes | 17.2 | 19.1 | -1.9 | 42E76DE0FB9845ACA49D846CE20AC817 |  | R22 | Non-TXV |  | 11.52% | 0.88481 | 22.14% | [5 empty] | Non-TXV | 11.52%
Stockton | CA | 95206-2422 |  | 2012-05-08 | 2012-05-08 12:36 | 2012-05-08 12:54 | GOODMAN - GSC1304G1AA | 158 | 6.9 | Yes | Yes | 21.1 | 21.9 | -0.8 | AA88A0E6721B47949D3DB293D7CF3A62 | OK: Verified Refrigerant Charge | R22 | TXV |  | 4.367% | 0.95633 | 8.393% | [5 empty] | TXV | 4.367%
Chico | CA | 95928-4189 |  | 2012-05-21 | 2012-05-21 10:02 | 2012-05-21 10:02 | TEMPSTAR - PGC036K080E | 68 | 0 | Yes | Yes | 19.7 | 20.7 | -1 | 332D9BB2C9664C9CADEED9FA4948F8AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2314 |  | 2012-05-16 | 2012-05-16 12:23 | 2012-05-16 12:41 | UNK - CA30K-1S | 76 | -4.5 | Yes | Yes | 18.6 | 18.8 | -0.2 | A8F25EE357C34D778F1A73EF2FFCCC92 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Auburn | CA | 95602-2163 |  | 2012-05-09 | 2012-05-09 14:29 | 2012-05-09 14:46 | RHEEM - UNK | 48 | 1.6 | Yes | Yes | 21 | 21.4 | -0.4 | 6B66BA3BFDDD4A59816AEB1365EFE751 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Auburn | CA | 95603-3737 |  | 2012-05-10 | 2012-05-10 10:30 | 2012-05-10 10:50 | STANDARD - 7B0023B1OOA1 | 54 | 11.1 | Yes | Yes | 22 | 19.5 | 2.5 | FA906AE45EB442BEA8E97FCC89474C0C | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 20.56% | 0.79444 | 39.5% | [5 empty] | Non-TXV | 20.56%
Kerman | CA | 93630-9134 |  | 2012-05-17 | 2012-05-17 12:57 | 2012-05-17 13:24 | LENNOX - HS16-311U-1P | 89 | 2.6 | Yes | Yes | 23.2 | 20.4 | 2.8 | D12D424F7C47445DAB80A50426774385 |  | R22 | Non-TXV |  | 2.921% | 0.97079 | 5.614% | [5 empty] | Non-TXV | 2.921%
Kerman | CA | 93630-9134 |  | 2012-05-17 | 2012-05-17 14:18 | 2012-05-17 14:41 | LENNOX - HS16-261V-1P | 99 | 15.1 | Yes | Yes | 24.3 | 20.4 | 3.9 | 18F5FD6FFA394BF3876EA41F23756597 |  | R22 | Non-TXV |  | 15.25% | 0.84747 | 29.31% | [5 empty] | Non-TXV | 15.25%
Auburn | CA | 95603-3733 |  | 2012-05-10 | 2012-05-10 12:48 | 2012-05-10 13:06 | STANDARD - 7B0023B100A1 | 54 | 5.1 | Yes | Yes | 20 | 19.7 | 0.3 | 99F0B4E4B2914EA9A36B36C7D99F162E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Fresno | CA | 93722-5824 |  | 2012-07-02 | 2012-07-02 11:25 | 2012-07-02 11:48 | CARRIER - 585HJ036060 | 102 | 3 | Yes | Yes | 20.8 | 19.4 | 1.4 | D14102D24FCC4E6C9B7A820581E9CFE9 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Atwater | CA | 95301-6019 |  | 2012-05-17 | 2012-05-17 15:53 | 2012-05-17 16:15 | ARCOAIRE - H4H448GKB100 | 196 | 10.1 | Yes | Yes | 21.5 | 20.4 | 1.1 | 51764DA85D194024AF3BD6E401479464 |  | R410A | Non-TXV |  | 5.153% | 0.94847 | 9.903% | [5 empty] | Non-TXV | 5.153%
Auburn | CA | 95602-0000 |  | 2012-05-09 | 2012-05-09 11:10 | 2012-05-09 11:29 | STANDARD - 7B0023B100A | 54 | 1.9 | Yes | Yes | 19.5 | 21.5 | -2 | 3D7BE4CEF095499DA705630426912497 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Merced | CA | 95348-3763 |  | 2012-05-31 | 2012-05-31 10:44 | 2012-05-31 11:08 | TRANE - BTD724A10080 | 66 | 4 | Yes | Yes | 20 | 21 | -1 | 1FB25E0267F14FC3B04C46ECC3401FE4 |  | R22 | Non-TXV |  | 6.061% | 0.93939 | 11.65% | [5 empty] | Non-TXV | 6.061%
Fresno | CA | 93711-6521 |  | 2012-07-09 | 2012-07-09 13:54 | 2012-07-09 14:16 | YORK - D1NA030N03606C | 76 | 2.4 | Yes | Yes | 25.2 | 22.8 | 2.5 | 9CB23161CF884558B15C8FF911CCC8B0 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Auburn | CA | 95603-3741 |  | 2012-05-14 | 2012-05-14 12:57 | 2012-05-14 13:18 | STANDARD - 7B0023B100A1 | 54 | 8.3 | Yes | Yes | 17 | 19.5 | -2.5 | B5B616C940014905BDD69BDDED1FF9DA |  | R22 | Non-TXV |  | 15.37% | 0.8463 | 29.54% | [5 empty] | Non-TXV | 15.37%
Auburn | CA | 95603-3822 |  | 2012-05-09 | 2012-05-09 15:23 | 2012-05-09 15:40 | TRANE - YCC024F1LOBE | 64 | 2 | Yes | Yes | 23 | 19.9 | 3.1 | EEA6A816488149D0A1E1C562EBFC0696 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Auburn | CA | 95603-3744 |  | 2012-05-15 | 2012-05-15 12:36 | 2012-05-15 12:56 | STANDARD - 7B0023B100A1 | 54 | 9.4 | Yes | Yes | 17 | 19.8 | -2.8 | 946948D06437459A803FB72D15FC14F4 |  | R22 | Non-TXV |  | 17.41% | 0.82593 | 33.45% | [5 empty] | Non-TXV | 17.41%
Los Banos | CA | 93635-3815 |  | 2012-06-13 | 2012-06-13 13:44 | 2012-06-13 14:09 | AMANA - 2YCC3042A1064AA | 131 | 4.4 | Yes | Yes | 17.7 | 17.5 | 0.2 | 2E8223E6A17A40A3B3B1964B5C107CD9 |  | R22 | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
Caruthers | CA | 93609-9739 |  | 2012-06-14 | 2012-06-14 13:54 | 2012-06-14 14:11 | GOODMAN - GPG13420701A | 107 | 3.7 | Yes | Yes | 19.7 | 20.2 | -0.4 | 6E61A6341D7440AD9BF4845FE5BEE6D4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.458% | 0.96542 | 6.645% | [5 empty] | Non-TXV | 3.458%
Merced | CA | 95341-5334 |  | 2012-05-08 | 2012-05-08 13:09 | 2012-05-08 13:29 | BRYANT - 582ANW036060NBAF | 68 | 6.7 | Yes | Yes | 27.5 | 21.5 | 6 | 5E9D40A20F264AA98242AA3711A483EA | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | Non-TXV | 9.853%
Auburn | CA | 95603-3737 |  | 2012-05-11 | 2012-05-11 10:47 | 2012-05-11 11:04 | STANDARD - 7B0023B1OOA1 | 54 | 5.7 | Yes | Yes | 25.5 | 21 | 4.5 | A92DC5D754CC4B80BFC14D9A066D4930 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.56% | 0.89444 | 20.29% | [5 empty] | Non-TXV | 10.56%
Stockton | CA | 95210-3132 |  | 2012-06-19 | 2012-06-19 12:51 | 2012-06-19 13:08 | BDP - 567C024RCU | 60 | 2.1 | Yes | Yes | 22 | 21.4 | 0.6 | 7A162DE8395D472B9393D2AB19B075C6 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Los Banos | CA | 93635-9205 |  | 2012-05-18 | 2012-05-18 15:28 | 2012-05-18 15:28 | GIBSON - JS3BC-030KA | 68 | 0 | Yes | Yes | 25.6 | 23.5 | 2.1 | CFAB90FB53CB465C93D42D09EFE923A3 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3747 |  | 2012-05-16 | 2012-05-16 10:17 | 2012-05-16 10:38 | AMANA - AP13360901A | 122 | 5.7 | Yes | Yes | 19 | 19.9 | -0.9 | 1D7DCBB29F50415BBDCAC72500F2D12F |  | R22 | Non-TXV |  | 4.672% | 0.95328 | 8.979% | [5 empty] | Non-TXV | 4.672%
Auburn | CA | 95603-3739 |  | 2012-05-14 | 2012-05-14 13:52 | 2012-05-14 14:20 | STANDARD - 7B0023B100A1 | 54 | 5.4 | Yes | Yes | 24 | 19.9 | 4.1 | F651CDE90EAE49BFB48BD56D704F2CC9 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95206-6042 |  | 2012-05-14 | 2012-05-14 11:30 | 2012-05-14 11:48 | COMFORTMACKER - ACS024A2C1 | 62 | -5.8 | Yes | Yes | 16.8 | 19.4 | -2.6 | 4C9C06CC80ED49CE82BC3E62C249DA6B |  | R22 | Non-TXV |  | -9.355% | 1.0935 | 2.62% |  |  |  |  | Non-TXV |  |  | -9.355%
Auburn | CA | 95603-3744 |  | 2012-05-11 | 2012-05-11 13:39 | 2012-05-11 13:58 | STANDARD - 7B0023B100A1 | 54 | 11.5 | Yes | Yes | 21 | 19.8 | 1.2 | E93BBFC864C44F49BCC041712D64E470 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 21.3% | 0.78704 | 40.93% | [5 empty] | Non-TXV | 21.3%
Paradise | CA | 95969-6648 |  | 2012-05-10 | 2012-05-10 12:27 | 2012-05-10 12:55 | DAY N NIGHT - 30\80 008106T | 66 | 2 | Yes | Yes | 21.7 | 23.3 | -1.6 | A3A6A8528D2C485E978BA0D9A88A8486 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Fresno | CA | 93706-9436 |  | 2012-07-09 | 2012-07-09 15:26 | 2012-07-09 15:45 | RHEEM - N/A | 90 | 5.9 | Yes | Yes | 21.1 | 20.1 | 1 | 140BEE962CC846B4930D3356C0F32D38 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.556% | 0.93444 | 12.6% | [5 empty] | Non-TXV | 6.556%
Chico | CA | 95928-7601 |  | 2012-05-08 | 2012-05-08 16:18 | 2012-05-08 16:31 | ARI - E063413975 | 109 | 3.3 | Yes | Yes | 21 | 21.3 | -0.3 | BB5220FCD8C74C64890F1A8B081CDF8C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.028% | 0.96972 | 5.818% | [5 empty] | Non-TXV | 3.028%
Orosi | CA | 93647-2628 |  | 2012-07-16 | 2012-07-16 14:44 | 2012-07-16 15:02 | GOODMAN - GPG10300-1A | 50 | 1.6 | Yes | Yes | 19.1 | 21.4 | -2.3 | F294967A233B4936A2ED2397CEE493A4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Selma | CA | 93662-3918 |  | 2012-08-14 | 2012-08-14 13:27 | 2012-08-14 13:52 | BDP - 585JW030050ABAF | 58 | 10.9 | Yes | Yes | 16.3 | 18.8 | -2.5 | 87B4F949071640F4B823836CB86D4008 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.79% | 0.81207 | 36.12% | [5 empty] | Non-TXV | 18.79%
Stockton | CA | 95210-3103 |  | 2012-06-11 | 2012-06-11 12:59 | 2012-06-11 13:16 | RHEEM - RRKA-A030JK06E | 54 | 2.9 | Yes | Yes | 26.1 | 23.5 | 2.6 | 7C2430733E8048F6927E5F35A63F3179 |  | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Riverbank | CA | 95367-2452 |  | 2012-06-12 | 2012-06-12 14:26 | 2012-06-12 14:26 | GIBSON - GS3BA-024KA | 64 | 0 | Yes | Yes | 20 | 20.2 | -0.2 | E3B32C93AA714F7A8E8E2B7CA814143E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3744 |  | 2012-05-14 | 2012-05-14 11:09 | 2012-05-14 11:32 | STANDARD - 7B0023B100A1 | 54 | 6.7 | Yes | Yes | 20 | 19.9 | 0.1 | 035B3E15015A48089C0A0130341217A0 |  | R22 | Non-TXV |  | 12.41% | 0.87593 | 23.84% | [5 empty] | Non-TXV | 12.41%
Fresno | CA | 93711-6521 |  | 2012-07-05 | 2012-07-05 16:05 | 2012-07-05 16:29 | YORK - D1NA030NO3606C | 76 | 2.3 | Yes | Yes | 23.9 | 20.4 | 3.5 | 2C6EF18E7C0942BFAFCA27AD574C1AC3 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Fresno | CA | 93711-6521 |  | 2012-07-05 | 2012-07-05 16:32 | 2012-07-05 17:08 | YORK - D1NA030N03606C | 76 | 2.2 | Yes | Yes | 23.1 | 20.1 | 3 | 5EC502AE24EA40CC83074858AF4A6E77 |  | R22 | Non-TXV |  | 2.895% | 0.97105 | 5.563% | [5 empty] | Non-TXV | 2.895%
Stockton | CA | 95210-5200 |  | 2012-05-29 | 2012-05-29 15:50 | 2012-05-29 16:11 | DAY & NIGHT - 585HJ036060 | 103 | 15 | Yes | Yes | 25.6 | 21.3 | 4.3 | 04D77B7C1F0D45B1B35751432E1E84E6 |  | R22 | Non-TXV |  | 14.56% | 0.85437 | 27.99% | [5 empty] | Non-TXV | 14.56%
Chico | CA | 95928-6098 |  | 2012-05-08 | 2012-05-08 15:13 | 2012-05-08 15:13 | AMERICAN STANDARD - YCP030F1LOAB | 96 | 0 | Yes | Yes | 20.5 | 22 | -1.5 | 585F41C2A24E452A979F0B9FBB7B2A9F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-9663 |  | 2012-05-17 | 2012-05-17 14:04 | 2012-05-17 14:30 | BRYANT - 223ANA060-B | 200 | 7.5 | Yes | Yes | 23.3 | 22.7 | 0.6 | 407D6C8050BB49F0ABE8BCF8FCEBF337 | OK: Verified Refrigerant Charge | R410A | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Chico | CA | 95926-4823 |  | 2012-05-18 | 2012-05-18 15:26 | 2012-05-18 15:48 | DAYNNIGHT - N 4 H 32H H KE 100 | 90 | 4 | Yes | Yes | 22.4 | 22.6 | -0.2 | 99F0BCE1A00A44D98312E11B7113C99A |  | R410A | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Stockton | CA | 95205-4255 |  | 2012-05-15 | 2012-05-15 13:43 | 2012-05-15 14:04 | RHEEM - RRNA-B024JK06X | 70 | 3.8 | Yes | Yes | 19.8 | 20.2 | -0.4 | A32177068C3242A79C7B4289D3015E76 |  | R22 | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Sanger | CA | 93657-4206 |  | 2012-08-09 | 2012-08-09 13:25 | 2012-08-09 13:47 | TEMPSTAR - PGAA42C1K3 | 82 | 5 | Yes | Yes | 19.9 | 19.6 | 0.3 | 3C18C92C09F743FDB5D23D561819E08C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | Non-TXV | 6.098%
Fresno | CA | 93722-5559 |  | 2012-05-15 | 2012-05-15 13:45 | 2012-05-15 14:15 | CARRIER - 48KLA---300BE | 102 | 4.9 | Yes | Yes | 17.7 | 20.4 | -2.7 | 6FF55E20E7C34CC1AED398463212337D |  | R22 | Non-TXV |  | 4.804% | 0.95196 | 9.232% | [5 empty] | Non-TXV | 4.804%
Los Banos | CA | 93635-2640 |  | 2012-05-15 | 2012-05-15 10:57 | 2012-05-15 11:23 | GOODMAN - CK301A | 75 | 6.8 | Yes | Yes | 26.2 | 21.4 | 4.8 | D4EB53A8576547F6884ADCD50904104F |  | R22 | Non-TXV |  | 9.067% | 0.90933 | 17.42% | [5 empty] | Non-TXV | 9.067%
Stockton | CA | 95207-5433 |  | 2012-06-14 | 2012-06-14 10:20 | 2012-06-14 10:40 | DAY & NIGHT - 24-60YAC-108C | 53 | 6 | Yes | Yes | 20.3 | 19.9 | 0.4 | 7AA7B036F4F543EFAB463722DBDA07D6 |  | R22 | Non-TXV |  | 11.32% | 0.88679 | 21.76% | [5 empty] | Non-TXV | 11.32%
Fresno | CA | 93722-5559 |  | 2012-05-15 | 2012-05-15 12:32 | 2012-05-15 12:57 | CARRIER - 48KLA130---300BE | 68 | 2.2 | Yes | Yes | 25.6 | 21 | 4.6 | E93C956575A846119AD57D3C841FAD97 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Chico | CA | 95928-4193 |  | 2012-05-08 | 2012-05-08 11:53 | 2012-05-08 12:14 | UNK - TCA030AKA5 | 54 | 3.9 | Yes | Yes | 21.3 | 21 | 0.3 | 0247CF8D0A3040DCAA1AF413BC145E7C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Stockton | CA | 95210-1245 |  | 2012-06-21 | 2012-06-21 14:35 | 2012-06-21 14:51 | PAYNE - 24-60YAC108C | 58 | 5.8 | Yes | Yes | 20.1 | 20.6 | -0.5 | 413C7A2F97C14643A8C566E170E1C7C6 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Los Banos | CA | 93635-6337 |  | 2012-05-18 | 2012-05-18 10:00 | 2012-05-18 10:28 | GOODMAN - CK36-1A | 73 | -6 | Yes | Yes | 20.3 | 20.8 | -0.5 | 73A2228D8F6A4DA3AAC742A252D12F51 |  | R22 | Non-TXV |  | -8.219% | 1.0822 | 2.302% |  |  |  |  | Non-TXV |  |  | -8.219%
Stockton | CA | 95207-5404 |  | 2012-06-11 | 2012-06-11 15:03 | 2012-06-11 15:22 | GOODMAN - CK-241B | 71 | 8.1 | Yes | Yes | 23.9 | 23.1 | 0.8 | 0B17C4AF608E4FFB892FEE8BABB5E109 |  | R22 | Non-TXV |  | 11.41% | 0.88592 | 21.92% | [5 empty] | Non-TXV | 11.41%
Merced | CA | 95348-1655 |  | 2012-05-11 | 2012-05-11 12:01 | 2012-05-11 12:19 | GOODMAN - PG030120-1AB | 60 | 1.8 | Yes | Yes | 20.2 | 21 | -0.8 | 0FB6D4F089AB4FE2B92C1928AF37C3DD |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Oroville | CA | 95966-5414 |  | 2012-05-31 | 2012-05-31 12:19 | 2012-05-31 13:17 | BDP - GR4A-030K072X | 65 | 3.1 | Yes | Yes | 24.5 | 19.1 | 5.5 | 52E9AF545A934E31AD9DCBDF8B062453 |  | R22 | Non-TXV |  | 4.769% | 0.95231 | 9.165% | [5 empty] | Non-TXV | 4.769%
Los Banos | CA | 93635-2612 |  | 2012-05-15 | 2012-05-15 10:19 | 2012-05-15 10:43 | RHEEM - UNK | 76 | 6.4 | Yes | Yes | 17.7 | 19.4 | -1.7 | 06F0089B7E3F45ADAA62F3E5D27D14F1 |  | R22 | Non-TXV |  | 8.421% | 0.91579 | 16.18% | [5 empty] | Non-TXV | 8.421%
Stockton | CA | 95210-6708 |  | 2012-05-21 | 2012-05-21 10:44 | 2012-05-21 11:02 | YORK - H1DE030S06A | 80 | -4.7 | Yes | Yes | 16.9 | 19.7 | -2.7 | 1D3B6FC85BDE4B69A6B4920DA8EDB467 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Merced | CA | 95340-0663 |  | 2012-05-07 | 2012-05-07 16:01 | 2012-05-07 16:01 | RUUD - URGF-05E36JKR | 75 | 0 | Yes | Yes | 25.1 | 20.2 | 4.9 | 5FB2564D11DE4475A9127DAE5FE97DBB | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1544 |  | 2012-05-14 | 2012-05-14 11:39 | 2012-05-14 11:58 | PAYNE - N/A | 85 | 11.5 | Yes | Yes | 25 | 21.3 | 3.7 | 286A413F65144419AB50ADF0803ED910 |  | R22 | Non-TXV |  | 13.53% | 0.86471 | 26% | [5 empty] | Non-TXV | 13.53%
Tracy | CA | 95376-3186 |  | 2012-06-21 | 2012-06-21 12:10 | 2012-06-21 12:35 | RHEEM - RAFD-024JAS | 67 | 2 | Yes | Yes | 18.2 | 19.3 | -1.1 | 7FA0B4725B514CFEB9C4D121C7ED814C |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Manteca | CA | 95337-5641 |  | 2012-05-14 | 2012-05-14 11:15 | 2012-05-14 11:32 | CARRIER - 24ABB330W310 | 65 | 8.5 | Yes | Yes | 16.9 | 19.9 | -3 | 0ABED0D0C8124E529FCCE28223490862 |  | R410A | Non-TXV |  | 13.08% | 0.86923 | 25.13% | [5 empty] | Non-TXV | 13.08%
Winton | CA | 95388-8703 |  | 2012-05-07 | 2012-05-07 16:40 | 2012-05-07 16:40 | GOODMAN - GPG12420701A | 105 | 0 | Yes | Yes | 23 | 19.3 | 3.7 | D184589B97F3420CB7643FA565D5152C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6972 |  | 2012-07-05 | 2012-07-05 08:38 | 2012-07-05 09:34 | PAYNE - PY1PNB036060AAAA | 56 | 2.9 | Yes | Yes | 17.2 | 19.1 | -1.9 | 0C1F1AF8A4F448DFAA01D11E959C7603 |  | R22 | Non-TXV |  | 5.179% | 0.94821 | 9.952% | [5 empty] | Non-TXV | 5.179%
Fresno | CA | 93727-6482 |  | 2012-08-08 | 2012-08-08 08:23 | 2012-08-08 08:54 | LENNOX - 12ACB36-4P | 103 | 10.2 | Yes | Yes | 25.6 | 20.4 | 5.2 | 14ED27DC56F345DB9FF38EA80359F9E5 |  | R22 | Non-TXV |  | 9.903% | 0.90097 | 19.03% | [5 empty] | Non-TXV | 9.903%
Fresno | CA | 93711-1673 |  | 2012-05-16 | 2012-05-16 10:13 | 2012-05-16 10:31 | CARRIER - 48NMX036-301BE | 70 | 2.1 | Yes | Yes | 22.6 | 20.2 | 2.5 | 541F837857D242C39D82D194B7F63C16 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95210-1641 |  | 2012-05-30 | 2012-05-30 10:25 | 2012-05-30 10:42 | CARRIER - 48GX-030060301AD | 70 | -4.1 | Yes | Yes | 17.8 | 18.7 | -0.9 | DF217F32E8C14A7EBA796D088A64F07F |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Selma | CA | 93662-2649 |  | 2012-08-14 | 2012-08-14 10:05 | 2012-08-14 10:38 | PAYNE - N/A | 105 | 14.9 | Yes | Yes | 17.9 | 20.4 | -2.5 | 2F965896812044EE949D1641593D777B |  | R22 | Non-TXV |  | 14.19% | 0.8581 | 27.27% | [5 empty] | Non-TXV | 14.19%
Fresno | CA | 93722-4754 |  | 2012-05-31 | 2012-05-31 15:10 | 2012-05-31 15:26 | CARRIER - UNK | 100 | 22.1 | Yes | Yes | 18.5 | 21 | -2.5 | 23536D0FF6C14E5CA2BA2B0A7B08BCDF |  | R22 | Non-TXV |  | 22.1% | 0.779 | 42.47% | [5 empty] | Non-TXV | 22.1%
Selma | CA | 93662-2652 |  | 2012-08-14 | 2012-08-14 10:59 | 2012-08-14 11:17 | PAYNE - N/A | 120 | 3.8 | Yes | Yes | 18.6 | 20.5 | -1.9 | 1FB9558AB8F048DCB34D73CA24E3CB66 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Paradise | CA | 95969-3169 |  | 2012-05-11 | 2012-05-11 13:00 | 2012-05-11 13:36 | CARRIER - UNK | 90 | 3.3 | Yes | Yes | 24.1 | 23.5 | 0.7 | B077909156F54AC797992C394E40033B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Stockton | CA | 95210-2325 |  | 2012-05-10 | 2012-05-10 14:54 | 2012-05-10 15:13 | PAYNE - PY1PNB036060ABAA | 71 | 2.3 | Yes | Yes | 22.8 | 19.8 | 3 | 567FC7A4E4564B98BA298FB660E42F16 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.225% | [5 empty] | Non-TXV | 3.239%
Madera | CA | 93638-0403 |  | 2012-06-13 | 2012-06-13 13:15 | 2012-06-13 13:37 | CARRIER - UNK | 100 | 3.5 | Yes | Yes | 21.1 | 20.2 | 0.9 | FA12AAF7AC7949DB95AFD6510DF36277 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Penn Valley | CA | 95946-9454 |  | 2012-06-15 | 2012-06-15 11:23 | 2012-06-15 11:23 | RHEEM - UNK PAINTED | 87 | 0 | Yes | Yes | 21.4 | 18.7 | 2.7 | 30B60DFBEF7944D7965C73FA99AD4555 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-4803 |  | 2012-06-20 | 2012-06-20 13:56 | 2012-06-20 14:15 | GOODMAN - GSC130301EA | 82 | 2.4 | Yes | Yes | 20.5 | 23 | -2.5 | 6E765D07D6704CA0806CDE92DDF94F0E |  | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Stockton | CA | 95210-1822 |  | 2012-05-11 | 2012-05-11 08:42 | 2012-05-11 09:00 | GOODMAN - GPG13240701BB | 77 | 2.3 | Yes | Yes | 24.8 | 19.5 | 5.3 | DC76785305FA41138DA2390C632F4E5F |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Stockton | CA | 95210-5627 |  | 2012-05-21 | 2012-05-21 14:18 | 2012-05-21 14:35 | LENNOX - XC15-048-230-02 | 194 | 6 | Yes | Yes | 21.1 | 20.4 | 0.7 | 557E2E5D901940BFA929EC2A8C4C2538 |  | R410A | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Chico | CA | 95926-3608 |  | 2012-05-11 | 2012-05-11 12:22 | 2012-05-11 12:35 | BRYANT - 1AJX018000ACAA | 65 | 3.1 | Yes | Yes | 19.3 | 19 | 0.3 | 64C0953D0AE04D8B892A5816558F3C79 | OK: Verified Refrigerant Charge | R22 | TXV |  | 4.769% | 0.95231 | 9.165% | [5 empty] | TXV | 4.769%
Riverbank | CA | 95367-2320 |  | 2012-05-29 | 2012-05-29 14:28 | 2012-05-29 14:46 | GUARDIAN - GCGD36S21S2B | 85 | 5.6 | Yes | Yes | 17.6 | 19.4 | -1.8 | AF32E4F9F6874549899A575BF6A94DFD |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Merced | CA | 95341-6103 |  | 2012-05-09 | 2012-05-09 17:16 | 2012-05-09 17:34 | GOODMAN - CPLE30-1 | 100 | -5.9 | Yes | Yes | 21.6 | 21.7 | -0.1 | 064BBAD43B294B72A275D31226CD7109 |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Sanger | CA | 93657-9763 |  | 2012-05-22 | 2012-05-22 13:32 | 2012-05-22 14:01 | YORK - H1CF048S06A | 195 | 6.3 | Yes | Yes | 25.9 | 22 | 3.9 | 3363420D8D7243A5B9018A40C29645A8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.231% | 0.96769 | 6.209% | [5 empty] | Non-TXV | 3.231%
Merced | CA | 95341-7017 |  | 2012-05-16 | 2012-05-16 13:26 | 2012-05-16 13:53 | GOODMAN - CLJ361A | 109 | 17.3 | Yes | Yes | 25.8 | 19.9 | 5.9 | 383E50595042492CA898ED28A84C2F4D |  | R22 | Non-TXV |  | 15.87% | 0.84128 | 30.5% | [5 empty] | Non-TXV | 15.87%
Los Banos | CA | 93635-2640 |  | 2012-05-10 | 2012-05-10 14:15 | 2012-05-10 15:51 | GOODMAN - CK361-A | 73 | 5.3 | Yes | Yes | 26.9 | 22.1 | 4.8 | 472775CAE6564E229BF44F96E1CAA188 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.26% | 0.9274 | 13.95% | [5 empty] | Non-TXV | 7.26%
Tracy | CA | 95376-3186 |  | 2012-06-20 | 2012-06-20 10:54 | 2012-06-20 11:23 | RHEEM - RAFD-024JAS | 67 | 4.1 | Yes | Yes | 21.5 | 21 | 0.5 | 5B883ECC4BF642E499E6771A98CF8855 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.119% | 0.93881 | 11.76% | [5 empty] | Non-TXV | 6.119%
Grass Valley | CA | 95945-7127 |  | 2012-06-14 | 2012-06-14 13:29 | 2012-06-14 13:47 | RHEEM - AT-48B10 | 55 | 6.6 | Yes | Yes | 21.5 | 18.8 | 2.7 | 3CD956C746E94839A864D71182AC98D2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Los Banos | CA | 93635-9200 |  | 2012-05-24 | 2012-05-24 14:20 | 2012-05-24 14:44 | OTHER - JS3BC-048KA | 110 | 3.3 | Yes | Yes | 18.5 | 20.4 | -1.9 | E77647BCD56C4A388DB94917A5EA363A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Tracy | CA | 95376-3107 |  | 2012-07-03 | 2012-07-03 11:26 | 2012-07-03 11:51 | NORDYNE - JS3BA-024KA | 64 | 2.6 | Yes | Yes | 20.4 | 19.9 | 0.5 | 3DE7139BCAEC4E78912BEA0ACD23B0C4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Tracy | CA | 95376-2782 |  | 2012-06-20 | 2012-06-20 11:26 | 2012-06-20 11:51 | GIBSON - JS3BA-024KA | 64 | 11.9 | Yes | Yes | 18.5 | 21.5 | -3 | A4FD41779FF24F4DA78F713652ACE136 |  | R22 | Non-TXV |  | 18.59% | 0.81406 | 35.73% | [5 empty] | Non-TXV | 18.59%
Fresno | CA | 93706-4749 |  | 2012-06-12 | 2012-06-12 12:53 | 2012-06-12 12:53 | NORDYNE - R4GD-036K072X | 100 | 0 | Yes | Yes | 17 | 19.4 | -2.4 | B4C15E88ACF8408693A5BE75837C41FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-3178 |  | 2012-06-26 | 2012-06-26 10:07 | 2012-06-26 10:33 | RHEEM - RACC-024JAS | 49 | 1.9 | Yes | Yes | 19 | 19.3 | -0.3 | 766DBA03F8E544C7839E7C1526DECE9D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.878% | 0.96122 | 7.452% | [5 empty] | Non-TXV | 3.878%
Paradise | CA | 95969-3253 |  | 2012-05-15 | 2012-05-15 11:32 | 2012-05-15 11:32 | DAY N NIGHT - 30/80YAC-106C | 64 | 0 | Yes | Yes | 21.9 | 21.4 | 0.5 | D5D908A2428B475C965B6CCB31CA4546 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-6163 |  | 2012-06-15 | 2012-06-15 14:57 | 2012-06-15 15:48 | RHEEM - UNK | 55 | 1.8 | Yes | Yes | 23 | 20.3 | 2.8 | FB75EBF738154D4F9CF3A712157DADA6 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Chico | CA | 95973-8353 |  | 2012-05-10 | 2012-05-10 13:26 | 2012-05-10 13:44 | YORK - N2B024SO6B13 | 85 | 4.5 | Yes | Yes | 23.8 | 22 | 1.8 | D4BD28BD888D49BB909E5F6D770B990A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Yuba City | CA | 95991-3331 |  | 2012-07-02 | 2012-07-02 09:22 | 2012-07-02 09:40 | DAY & NIGHT - 593ANX036000AAAA | 115 | 8.7 | Yes | Yes | 20 | 18.1 | 1.9 | E7D4BF1584D043A99065441D9BF0B468 |  | R22 | Non-TXV |  | 7.565% | 0.92435 | 14.54% | [5 empty] | Non-TXV | 7.565%
Stockton | CA | 95206-2236 |  | 2012-05-08 | 2012-05-08 14:07 | 2012-05-08 14:33 | RHEEM - UNK | 70 | 12.9 | Yes | Yes | 20.7 | 23.7 | -3 | B76D9B8B93D9489C9E42921D487FF5AC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 18.43% | 0.81571 | 35.42% | [5 empty] | Non-TXV | 18.43%
Stockton | CA | 95210-3242 |  | 2012-06-08 | 2012-06-08 13:31 | 2012-06-08 13:49 | YORK - TCGD36S21S2HA | 63 | 2 | Yes | Yes | 20.5 | 20.4 | 0.1 | 12829FBF093D46A1824525E18DED7647 |  | R22 | Non-TXV |  | 3.175% | 0.96825 | 6.101% | [5 empty] | Non-TXV | 3.175%
Selma | CA | 93662-2325 |  | 2012-08-14 | 2012-08-14 08:54 | 2012-08-14 09:11 | RHEEM - RRMA-A036JK06X | 99 | 3.3 | Yes | Yes | 20.1 | 20.4 | -0.3 | 7B65566DE6EA4D0F900702258E60AE42 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Los Banos | CA | 93635-3107 |  | 2012-05-11 | 2012-05-11 12:25 | 2012-05-11 12:48 | CARRIER - 38TH036300 | 84 | 4.3 | Yes | Yes | 20.2 | 22.1 | -1.9 | BD1621A8F51944E2972F4CDA386D2696 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.119% | 0.94881 | 9.838% | [5 empty] | Non-TXV | 5.119%
Stockton | CA | 95210-2321 |  | 2012-05-16 | 2012-05-16 14:37 | 2012-05-16 14:56 | PAYNE - PY3PNA030060NB | 96 | -5.6 | Yes | Yes | 22.9 | 18.7 | 4.2 | A70EB75F80BA4165930246AEA01352CA |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Merced | CA | 95340-4157 |  | 2012-05-07 | 2012-05-07 13:16 | 2012-05-07 13:37 | CARRIER - 48GS030060301 | 55 | 4.3 | Yes | Yes | 21.4 | 20.9 | 0.5 | 4F2379272A684393979E3C707AB3D782 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.818% | 0.92182 | 15.02% | [5 empty] | Non-TXV | 7.818%
Chico | CA | 95926-1516 |  | 2012-05-11 | 2012-05-11 10:46 | 2012-05-11 11:03 | DAY N NIGHT - 588ANW036080ABBF | 67 | -5.5 | Yes | Yes | 21.6 | 20.4 | 1.2 | 09F7C795F58145FA81EAF9A4D3AE03FC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -8.209% | 1.0821 | 2.299% |  |  |  |  | Non-TXV |  |  | -8.209%
Chico | CA | 95973-0958 |  | 2012-05-09 | 2012-05-09 15:06 | 2012-05-09 15:06 | PAYNE - 24RAC-15BC | 48 | 0 | Yes | Yes | 18.3 | 21 | -2.7 | 6E283032B9544A4B9FA30E1D0705A911 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-9154 |  | 2012-05-31 | 2012-05-31 11:32 | 2012-05-31 11:53 | TRANE - TTR030C100A1 | 74 | 12.4 | Yes | Yes | 18.7 | 20.4 | -1.7 | 006FBE51007E40ECA2696A8E89C2C2A2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.76% | 0.83243 | 32.2% | [5 empty] | Non-TXV | 16.76%
Stockton | CA | 95210-2320 |  | 2012-06-19 | 2012-06-19 09:41 | 2012-06-19 10:00 | PAYNE - 24/60YAC108C | 51 | -3 | Yes | Yes | 24.2 | 19.1 | 5.1 | 50CF28FBFF524F52AD2C3655FDE13B78 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Los Banos | CA | 93635-3145 |  | 2012-05-16 | 2012-05-16 12:32 | 2012-05-16 12:52 | PAYNE - 591ANX036000AAAA | 88 | 3.2 | Yes | Yes | 21.5 | 20.4 | 1.1 | 5371575253B045858CAA737C8659910B |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Madera | CA | 93637-5404 |  | 2012-05-08 | 2012-05-08 16:10 | 2012-05-08 16:27 | FRASER N JOHNSTON - 80AW30106 | 55 | 3.1 | Yes | Yes | 18.8 | 20.4 | -1.6 | 4D46409CAC244D1293293CCEBDBFB1E5 |  | R22 | Non-TXV |  | 5.636% | 0.94364 | 10.83% | [5 empty] | Non-TXV | 5.636%
Yuba City | CA | 95993-9120 |  | 2012-05-09 | 2012-05-09 16:53 | 2012-05-09 17:11 | CARRIER - 38CKC036350 | 74 | -16.9 | Yes | Yes | 17.1 | 19.3 | -2.2 | 6AB14F8A28F84B33AB5CF1A8E36D765A | OK: Verified Refrigerant Charge | R22 | TXV |  | -22.84% | 1.2284 | 6.396% |  |  |  |  | TXV |  |  | -22.84%
Stockton | CA | 95204-4205 |  | 2012-05-08 | 2012-05-08 18:43 | 2012-05-08 19:01 | RUUD - UNK | 63 | 8 | Yes | Yes | 16 | 18.8 | -2.8 | 8D58E9470AD4433F8BBF75FF6B9F7E7F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 12.7% | 0.87302 | 24.4% | [5 empty] | Non-TXV | 12.7%
Fresno | CA | 93727-6587 |  | 2012-05-09 | 2012-05-09 15:23 | 2012-05-09 15:41 | LENNOX - 13ACD-042-230-01 | 111 | 10.4 | Yes | Yes | 23.3 | 21 | 2.3 | B72666CD569242CEA2752BC7DADFD8EA | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.369% | 0.90631 | 18.01% | [5 empty] | Non-TXV | 9.369%
Madera | CA | 93637-3005 |  | 2012-05-22 | 2012-05-22 16:45 | 2012-05-22 17:15 | CARRIER - N/A | 80 | 2.4 | Yes | Yes | 25.8 | 21.5 | 4.3 | 31C53AEBFD4C44598F7ACCA547C1A1A4 |  |  |  |  | 3% | 0.97 | 5.765% | [5 empty] | 0 | 3%
Tracy | CA | 95376-7014 |  | 2012-06-26 | 2012-06-26 11:12 | 2012-06-26 11:32 | BRYANT - 563CN030-C | 99 | 3 | Yes | Yes | 19.2 | 19.9 | -0.7 | CC7F88EAEA9E42959113B8EE74F40D5C |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Los Banos | CA | 93635-4420 |  | 2012-05-14 | 2012-05-14 14:35 | 2012-05-14 14:35 | DAY & NIGHT - PGD324060K001C | 72 | 0 | Yes | Yes | 21 | 21.2 | -0.1 | 1C72442CB32B4B64A285BA56673DEBEC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4507 |  | 2012-06-11 | 2012-06-11 12:30 | 2012-06-11 12:50 | PAYNE - PA13NR036-H | 54 | 12.7 | Yes | Yes | 25.5 | 22.4 | 3.2 | 610B05C373F84E6BA072E9C61B92CC95 |  | R22 | Non-TXV |  | 23.52% | 0.76481 | 45.2% | [5 empty] | Non-TXV | 23.52%
Fresno | CA | 93722-4572 |  | 2012-06-15 | 2012-06-15 12:00 | 2012-06-15 12:17 | ICP - PGC030K060E | 51 | 3.1 | Yes | Yes | 17.8 | 20.4 | -2.6 | 0D8F573C80184703B7534F4C05815883 |  | R22 | Non-TXV |  | 6.078% | 0.93922 | 11.68% | [5 empty] | Non-TXV | 6.078%
Sutter Creek | CA | 95685-4113 |  | 2012-07-17 | 2012-07-17 10:19 | 2012-07-17 10:42 | COLEMAN - BRSC0361BD | 63 | 10.6 | Yes | Yes | 19.5 | 22.3 | -2.8 | 22B83420A29D45089E19A64FD39D9679 |  | R22 | Non-TXV |  | 16.83% | 0.83175 | 32.33% | [5 empty] | Non-TXV | 16.83%
Stockton | CA | 95206-2801 |  | 2012-05-09 | 2012-05-09 15:02 | 2012-05-09 15:21 | RHEEM - RRNL-B024JKO6X | 77 | 8.6 | Yes | Yes | 26.2 | 20.4 | 5.8 | EFEE89BB366D437FB129DF70FA27E536 | OK: Verified Refrigerant Charge | R410A | TXV |  | 11.17% | 0.88831 | 21.46% | [5 empty] | TXV | 11.17%
Stockton | CA | 95206-1553 |  | 2012-05-18 | 2012-05-18 14:07 | 2012-05-18 14:33 | AIRE-FLO - 13ACD-036-230-15 | 92 | 5.7 | Yes | Yes | 18.7 | 21.2 | -2.5 | 17409D7BFEBF4FF9A7C4215F6A527574 |  | R22 | Non-TXV |  | 6.196% | 0.93804 | 11.91% | [5 empty] | Non-TXV | 6.196%
Merced | CA | 95340-2619 |  | 2012-05-14 | 2012-05-14 16:06 | 2012-05-14 16:27 | GENERAL ELECTRIC - BG3A830-1B | 76 | 5.1 | Yes | Yes | 22.5 | 19.9 | 2.6 | D54DFBD5D64F4DC595781EB1E67A7259 |  | R22 | Non-TXV |  | 6.711% | 0.93289 | 12.9% | [5 empty] | Non-TXV | 6.711%
Stockton | CA | 95210-1254 |  | 2012-05-07 | 2012-05-07 14:23 | 2012-05-07 14:40 | ICP - HAC236AKA1 | 113 | 3.6 | Yes | Yes | 24.8 | 21.3 | 3.5 | 802BBB27A1E846628374FDC816DD68BE | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.186% | 0.96814 | 6.122% | [5 empty] | Non-TXV | 3.186%
Auburn | CA | 95602-2308 |  | 2012-07-30 | 2012-07-30 11:53 | 2012-07-30 12:11 | HEIL - HAC0185AKA1 | 60 | 8 | Yes | Yes | 20.5 | 21.3 | -0.8 | 525E91BFEC6C4214BF2682633C508BF1 |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Lincoln | CA | 95648-1922 |  | 2012-07-24 | 2012-07-24 16:12 | 2012-07-24 17:17 | RUUD - UAHE-030JAS | 78 | 4.3 | Yes | Yes | 17.2 | 19.9 | -2.7 | CB9C1DA700CF4F07A886B4C1E2CB24EF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.513% | 0.94487 | 10.59% | [5 empty] | Non-TXV | 5.513%
Atwater | CA | 95301-2807 |  | 2012-05-10 | 2012-05-10 13:34 | 2012-05-10 13:51 | AMERICAN STANDARD - YCP042F1MOBAB | 72 | 6.6 | Yes | Yes | 24.2 | 19.9 | 4.3 | 844D3136745B4CB6BBE3197156D92BF0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Auburn | CA | 95603-3744 |  | 2012-05-14 | 2012-05-14 11:35 | 2012-05-14 11:57 | STANDARD - 7B0023B100A1 | 54 | 8.7 | Yes | Yes | 18 | 19.8 | -1.8 | C158D1EA63CB49218FD2D76891D9F5F0 |  | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Auburn | CA | 95603-3738 |  | 2012-05-10 | 2012-05-10 11:53 | 2012-05-10 12:14 | STANDARD - 7B0023B100A1 | 54 | 6 | Yes | Yes | 21 | 20.3 | 0.7 | 246CF732797A4E63BA88FA78793A4173 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Stockton | CA | 95207-6004 |  | 2012-06-14 | 2012-06-14 12:11 | 2012-06-14 12:28 | RHEEM - UNK | 64 | 4.5 | Yes | Yes | 21.7 | 20.9 | 0.8 | 63D96F3AB7584109A245D5F7762AE4E8 |  | R22 | Non-TXV |  | 7.031% | 0.92969 | 13.51% | [5 empty] | Non-TXV | 7.031%
Merced | CA | 95340-0955 |  | 2012-06-14 | 2012-06-14 11:16 | 2012-06-14 11:38 | AMERICAN STANDARD - YCY036G1M0AD | 129 | 3.8 | Yes | Yes | 25.4 | 21.4 | 4 | DD89C9CB4319454AA2DA7A392F93E3CD |  | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.661% | [5 empty] | Non-TXV | 2.946%
Fresno | CA | 93727-1850 |  | 2012-05-08 | 2012-05-08 18:03 | 2012-05-08 18:22 | PAYNE - PY2PNB042090ABAA | 85 | 5 | Yes | Yes | 21.1 | 21 | 0.1 | D744FA92138C470093BABBCE796E16FF | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Stockton | CA | 95207-5902 |  | 2012-06-14 | 2012-06-14 09:26 | 2012-06-14 09:26 | PAYNE - PY1PNB024040AAAA | 53 | 0 | Yes | Yes | 22.6 | 19.7 | 2.9 | 1AC309874F044CCC97EF7F1B0FD2695D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3718 |  | 2012-05-08 | 2012-05-08 17:21 | 2012-05-08 17:39 | BRYANT - 574ANW0240NB-- | 89 | 3.6 | Yes | Yes | 21.8 | 20.9 | 0.9 | 7928F9400DB74F3B895AD5360E7B526B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.045% | 0.95955 | 7.773% | [5 empty] | Non-TXV | 4.045%
Merced | CA | 95340-2739 |  | 2012-05-07 | 2012-05-07 17:36 | 2012-05-07 18:56 | RHEEM - HC105421B | 136 | 0 | Yes | Yes | 4 | 26.2 | -22.2 | F4E2683160D24D7C9044E3D871907C0B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-5334 |  | 2012-05-21 | 2012-05-21 12:04 | 2012-05-21 12:35 | BRYANT - 582ANW036060NBAF | 68 | 3.6 | Yes | Yes | 25.8 | 19.9 | 5.9 | 3B39F8C85E824A1D8D1808AD32307C68 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Orosi | CA | 93647-2156 |  | 2012-07-16 | 2012-07-16 13:59 | 2012-07-16 14:23 | BDP - 585CJ036075 | 84 | 8.3 | Yes | Yes | 25.1 | 21 | 4.1 | 57F0A71893924D8D81ADDDE96652F965 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.881% | 0.90119 | 18.99% | [5 empty] | Non-TXV | 9.881%
Los Banos | CA | 93635-3143 |  | 2012-05-10 | 2012-05-10 12:08 | 2012-05-10 12:31 | TRANE - 11D7488B100A | 116 | -8.2 | Yes | Yes | 20.8 | 19.6 | 1.2 | F7022655969C4AF5A5EE173DE379C69F | OK: Verified Refrigerant Charge. |  |  |  | -7.069% | 1.0707 | 1.98% |  |  |  |  | 0 |  |  | -7.069%
Magalia | CA | 95954-9545 |  | 2012-05-30 | 2012-05-30 12:06 | 2012-05-30 12:41 | TEMPSTAR - PHF036KOOOA | 95 | 5.8 | Yes | Yes | 24.7 | 20.9 | 3.8 | BF9174C298D046868CD9BD5504CBCAD6 |  | R22 | Non-TXV |  | 6.105% | 0.93895 | 11.73% | [5 empty] | Non-TXV | 6.105%
Stockton | CA | 95210-2358 |  | 2012-05-23 | 2012-05-23 14:05 | 2012-05-23 14:22 | GOODMAN - GPG13360701AA | 112 | 3.8 | Yes | Yes | 22.1 | 23.4 | -1.3 | 78CDB5C9F91D418282CA525BBECFD8E3 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Auburn | CA | 95602-2246 |  | 2012-05-16 | 2012-05-16 11:57 | 2012-05-16 12:17 | PAYNE - 561J018 | 53 | -5 | Yes | Yes | 17 | 18.3 | -1.3 | 850277F43F70424DB71AC3F9AA3AEF06 |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Cameron Park | CA | 95682-9069 |  | 2012-05-14 | 2012-05-14 14:50 | 2012-05-14 14:50 | CARRIER - 38BRG060300 | 200 | 0 | Yes | Yes | 25.6 | 20.6 | 5 | E4BABC24887D4D3AB82C2FE5ED07AA63 | OK: Verified Refrigerant Charge | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-4024 |  | 2012-05-16 | 2012-05-16 12:55 | 2012-05-16 13:22 | DAY & NIGHT - 30DNR-106A | 86 | 3.3 | Yes | Yes | 21.1 | 20.4 | 0.7 | 40EB413AFD4D4DAF8DA8391FCA1C776B | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.837% | 0.96163 | 7.374% | [5 empty] | Non-TXV | 3.837%
Auburn | CA | 95603-3737 |  | 2012-05-15 | 2012-05-15 11:27 | 2012-05-15 11:49 | STANDARD - 7B0023B100A1 | 54 | 8.1 | Yes | Yes | 19 | 18.8 | 0.2 | FF2322297F864DB1A956DD00C4A63ADC |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Merced | CA | 95340-0000 |  | 2012-05-07 | 2012-05-07 12:57 | 2012-05-07 13:22 | TRANE - 4YC3024B1064AA | 93 | 2.8 | Yes | Yes | 21.9 | 19.9 | 2 | A5247F6B6B3A46F9BABD5EA3ACDB8D78 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Atwater | CA | 95301-3722 |  | 2012-05-10 | 2012-05-10 12:57 | 2012-05-10 13:18 | GOODMAN - GPG10360701A | 75 | 2.2 | Yes | Yes | 21.6 | 19.9 | 1.7 | E670953441AB4D95A13C79FB92186C8D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.933% | 0.97067 | 5.637% | [5 empty] | Non-TXV | 2.933%
Fresno | CA | 93722-6008 |  | 2012-05-15 | 2012-05-15 14:33 | 2012-05-15 14:51 | OTHER - CA3030VKB1.822230 | 102 | 3.9 | Yes | Yes | 22.5 | 21 | 1.5 | 5D97CF4C956A4C59AA9058F3F0575C7B |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Auburn | CA | 95603-3742 |  | 2012-07-18 | 2012-07-18 10:18 | 2012-07-18 10:35 | OTHER - UNK | 54 | 11.7 | Yes | Yes | 23.2 | 19.9 | 3.3 | AACF9379EE784F159FCB5711F16B9782 |  | R22 | Non-TXV |  | 21.67% | 0.78333 | 41.64% | [5 empty] | Non-TXV | 21.67%
Stockton | CA | 95215-5913 |  | 2012-05-31 | 2012-05-31 15:30 | 2012-05-31 16:11 | YORK - BRCS0361BDG | 63 | 3.1 | Yes | Yes | 16.7 | 19.2 | -2.5 | DFDDB8B4B75E46F19B2E8DA0CBD15B37 |  | R22 | Non-TXV |  | 4.921% | 0.95079 | 9.456% | [5 empty] | Non-TXV | 4.921%
Merced | CA | 95341-5829 |  | 2012-06-07 | 2012-06-07 12:47 | 2012-06-07 13:10 | AMERICAN STANDARD - YCC036F1M0BA | 83 | 2.5 | Yes | Yes | 27 | 23.2 | 3.9 | 7E1ACFA2A7414D9E967EDF9B798BA21E |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Auburn | CA | 95603-3743 |  | 2012-05-11 | 2012-05-11 12:03 | 2012-05-11 12:27 | STANDARD - 7B0023B100A1 | 54 | 8.4 | Yes | Yes | 20 | 19.5 | 0.5 | 9029926E371246F082D0F60907B8A120 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Dinuba | CA | 93618-9608 |  | 2012-05-16 | 2012-05-16 15:42 | 2012-05-16 16:16 | N/A - N/A | 90 | 2.9 | Yes | Yes | 19.7 | 20.2 | -0.5 | 5B9063B3FC9640F0AF60F6FEAB53B0AB |  | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Livingston | CA | 95334-9728 |  | 2012-06-07 | 2012-06-07 13:05 | 2012-06-07 13:27 | LENNOX - 13ACX-030-230-15 | 68 | 2.1 | Yes | Yes | 17.7 | 20.2 | -2.5 | 288CB55769654E5F8D56AB8874B95352 |  | R410A | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Auburn | CA | 95603-3739 |  | 2012-05-18 | 2012-05-18 14:26 | 2012-05-18 14:49 | STANDARD - | 54 | 5.7 | Yes | Yes | 21 | 18.7 | 2.3 | 307460BC31F6492489E2A4AB2F7508B9 |  | R22 | Non-TXV |  | 10.56% | 0.89444 | 20.29% | [5 empty] | Non-TXV | 10.56%
Granite Bay | CA | 95746-9509 |  | 2012-07-13 | 2012-07-13 16:21 | 2012-07-13 16:37 | - RCE42A2D | 230 | 19.1 | Yes | Yes | 23.9 | 22 | 1.9 | 45BE096F01E440BBB575610DC186E65C |  | R22 | Non-TXV |  | 8.304% | 0.91696 | 15.96% | [5 empty] | Non-TXV | 8.304%
Marysville | CA | 95901-3241 |  | 2012-05-22 | 2012-05-22 10:32 | 2012-05-22 10:32 | OTHER - PGE12B30D75LA-3A | 85 | 3 | Yes | Yes | 39 | 23.1 | 15.9 | 4B4BB2790A5540FE88BE37949695660C | Add refrigerant: 3 oz | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Oroville | CA | 95966-5382 |  | 2012-06-07 | 2012-06-07 09:42 | 2012-06-07 10:19 | UNK - UNK | 75 | 5.2 | Yes | Yes | 22 | 22.2 | -0.2 | 0FC11AEBC94043E19516AB541C5ED993 |  | R22 | Non-TXV |  | 6.933% | 0.93067 | 13.32% | [5 empty] | Non-TXV | 6.933%
Fresno | CA | 93706-4209 |  | 2012-06-12 | 2012-06-12 09:10 | 2012-06-12 09:28 | YORK - D2NZ030N0506NXA | 117 | -4.7 | Yes | Yes | 21.7 | 21 | 0.7 | 1700292379444BFAB8FEDD1DB74D3EFB |  | R410A | TXV |  | -4.017% | 1.0402 | 1.125% |  |  |  |  | TXV |  |  | -4.017%
Stockton | CA | 95207-1622 |  | 2012-05-31 | 2012-05-31 11:19 | 2012-05-31 11:48 | RHEEM - RRGF-05E36JKR | 75 | 14.5 | Yes | Yes | 22.7 | 21.3 | 1.4 | 03432BC5A0884A42B626D7E1EDBBE8C2 |  | R22 | Non-TXV |  | 19.33% | 0.80667 | 37.15% | [5 empty] | Non-TXV | 19.33%
Stockton | CA | 95209-1536 |  | 2012-05-21 | 2012-05-21 16:25 | 2012-05-21 16:43 | DAYNIGHT - UNK | 57 | 8.8 | Yes | Yes | 23.8 | 21.2 | 2.6 | 09FC8772C2A940DC8AEFC85AAB1F7E59 |  | R22 | Non-TXV |  | 15.44% | 0.84561 | 29.67% | [5 empty] | Non-TXV | 15.44%
Stockton | CA | 95204-4718 |  | 2012-05-09 | 2012-05-09 10:30 | 2012-05-09 10:30 | THERMAL ZONE - TZGE-330JL080AX | 77 | 0 | Yes | Yes | 19.2 | 20.4 | -1.2 | 3508BD9D36964765865BA8EE334B453F | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-9717 |  | 2012-05-24 | 2012-05-24 11:48 | 2012-05-24 12:06 | CARRIER - DRC0361BE | 65 | 3.6 | Yes | Yes | 25.9 | 20.2 | 5.8 | 6C3ADCEAC3164FFF9CA2289546B09BAE |  | R22 | Non-TXV |  | 5.538% | 0.94462 | 10.64% | [5 empty] | Non-TXV | 5.538%
Valley Springs | CA | 95252-9024 |  | 2012-07-06 | 2012-07-06 09:13 | 2012-07-06 09:29 | GIBSON - JS3BA-036KA | 69 | 2.3 | Yes | Yes | 17.2 | 19.3 | -2.1 | 7793FFD93A9D4E85B7F578490F9653AF |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95207-7852 |  | 2012-05-30 | 2012-05-30 11:12 | 2012-05-30 11:29 | TRANE - YCX024F1L0BA | 71 | 7.8 | Yes | Yes | 18.6 | 18.6 | 0.1 | 86301632D16E456DB5FBFE148CE3B30A |  | R22 | Non-TXV |  | 10.99% | 0.89014 | 21.11% | [5 empty] | Non-TXV | 10.99%
Stockton | CA | 95207-4620 |  | 2012-06-08 | 2012-06-08 13:26 | 2012-06-08 13:46 | DAY & NIGHT - 585A024055YAC | 51 | 13.8 | Yes | Yes | 17.7 | 20.6 | -2.9 | 7F6130C0C1E748D6ACFDA71538C21979 |  | R22 | Non-TXV |  | 27.06% | 0.72941 | 52% | [5 empty] | Non-TXV | 27.06%
Stockton | CA | 95203-1331 |  | 2012-05-10 | 2012-05-10 12:36 | 2012-05-10 12:53 | AMANA - VCA36C2B | 80 | 3.9 | Yes | Yes | 15.4 | 17.7 | -2.3 | 2FC56C712AD1426DB2F2A831AA70247C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.875% | 0.95125 | 9.369% | [5 empty] | Non-TXV | 4.875%
Stockton | CA | 95207-7846 |  | 2012-05-30 | 2012-05-30 10:33 | 2012-05-30 10:50 | TRANE - YCC024F1LOBF | 64 | -6 | Yes | Yes | 19.6 | 19.4 | 0.2 | 2B02AACCA70442439C99FEDFB6DFD2A0 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Marysville | CA | 95901-3118 |  | 2012-05-15 | 2012-05-15 14:38 | 2012-05-15 14:58 | DAY&NIGHT - UNK | 73 | 12.1 | Yes | Yes | 24.5 | 19.7 | 4.8 | 3B9E3114487E4802A5A7BB40E18190E6 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16.58% | 0.83425 | 31.85% | [5 empty] | Non-TXV | 16.58%
Stockton | CA | 95207-7855 |  | 2012-05-30 | 2012-05-30 12:10 | 2012-05-30 12:33 | TRANE - YCC024F1LOBC | 64 | 5.6 | Yes | Yes | 18.3 | 19.8 | -1.5 | 94125012DB5F4D39A957465429DCC756 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Kerman | CA | 93630-1015 |  | 2012-05-17 | 2012-05-17 10:30 | 2012-05-17 11:04 | PAYNE - 588ANW036080ACAF | 67 | 2 | Yes | Yes | 23.3 | 21 | 2.3 | EB91C857FC7F4AD786E2400BB3EECB21 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Gustine | CA | 95322-1029 |  | 2012-05-30 | 2012-05-30 10:46 | 2012-05-30 11:04 | RHEEM - RAKA-48JAZ | 103 | 3.8 | Yes | Yes | 16.7 | 18.6 | -1.9 | 9C5C3B4BDF244D58A9608B567EB9821C |  | R22 | Non-TXV |  | 3.689% | 0.96311 | 7.09% | [5 empty] | Non-TXV | 3.689%
Stockton | CA | 95207-7846 |  | 2012-05-30 | 2012-05-30 10:25 | 2012-05-30 10:47 | TRANE - YCC024F1LOBF | 64 | 3.7 | Yes | Yes | 18.7 | 18.8 | -0.1 | 49F3DE0BB5884C529B13B464045EE3F6 |  | R22 | Non-TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | Non-TXV | 5.781%
Atwater | CA | 95301-4863 |  | 2012-06-13 | 2012-06-13 16:13 | 2012-06-13 16:34 | OTHER - GCGD30S41S3A | 60 | 4.2 | Yes | Yes | 21.1 | 21.3 | -0.2 | E9636F51820A4F0A90EAC505C70CC267 |  | R410A | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Stockton | CA | 95210-1937 |  | 2012-05-15 | 2012-05-15 10:18 | 2012-05-15 10:35 | BDP - 569BJ036 | 93 | 38.9 | Yes | Yes | 17.9 | 20.7 | -2.8 | 635EE6CA98C14028A2F1E61F7C1AE6EB |  | R22 | Non-TXV |  | 41.83% | 0.58172 | 80.38% | [5 empty] | Non-TXV | 41.83%
Stockton | CA | 95207-4628 |  | 2012-06-08 | 2012-06-08 12:17 | 2012-06-08 12:35 | RHEEM - HC-80-24-21C | 49 | 6.5 | Yes | Yes | 21.2 | 20.4 | 0.8 | 2FED442736DB44D98BF3C8F11019CAB2 |  | R22 | Non-TXV |  | 13.27% | 0.86735 | 25.49% | [5 empty] | Non-TXV | 13.27%
Dinuba | CA | 93618-9740 |  | 2012-05-23 | 2012-05-23 12:54 | 2012-05-23 12:54 | GOODMAN - GSH130421AC | 213 | 0 | Yes | Yes | 17 | 19.8 | -2.8 | 34FAF0E6673E4945AB31B8483E7B1517 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-9740 |  | 2012-05-23 | 2012-05-23 13:26 | 2012-05-23 13:50 | CARRIER - 38CQ048310 | 112 | 7.5 | Yes | Yes | 16.3 | 19.3 | -3 | BE8D1935323F45CCB5B81BFE017168F1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.696% | 0.93304 | 12.87% | [5 empty] | Non-TXV | 6.696%
Fresno | CA | 93722-3045 |  | 2012-05-31 | 2012-05-31 17:43 | 2012-05-31 18:05 | RUUD - UALA-042JAS | 85 | 23 | Yes | Yes | 20.5 | 20 | 0.6 | F5D88B34C430467A9A11720AAB5752A5 |  | R22 | Non-TXV |  | 27.06% | 0.72941 | 52% | [5 empty] | Non-TXV | 27.06%
Fresno | CA | 93650-1137 |  | 2012-06-13 | 2012-06-13 13:20 | 2012-06-13 13:38 | LENNOX - N/A | 96 | 2.9 | Yes | Yes | 20 | 19.6 | 0.4 | 402DC06DEF9D48808B01069D812E231E |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Winton | CA | 95388-9306 |  | 2012-05-07 | 2012-05-07 17:05 | 2012-05-07 17:05 | GOODMAN - G8C130361A | 77 | 0 | Yes | Yes | 20 | 22 | -2 | B1DCBBDC5C0A4A34B3D6D059B64DFCBD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4711 |  | 2012-05-16 | 2012-05-16 10:16 | 2012-05-16 10:34 | RHEEM - RRMA-A030JK08X | 80 | -5.6 | Yes | Yes | 24.1 | 20.1 | 4 | 8860B98C105545418375B5A09DC4F622 |  |  |  |  | -7% | 1.07 | 1.96% |  |  |  |  | 0 |  |  | -7%
Fresno | CA | 93722-6531 |  | 2012-05-29 | 2012-05-29 13:18 | 2012-05-29 13:38 | HEIL - NRGF24DDB04 | 53 | 1.6 | Yes | Yes | 22.8 | 21 | 1.8 | CF52D2A5B4EE4A1087E50757275AB1E3 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Stockton | CA | 95207-7844 |  | 2012-05-30 | 2012-05-30 09:40 | 2012-05-30 09:59 | TRANE - YCC024F1LOBF | 64 | -6 | Yes | Yes | 20.3 | 18.3 | 2 | 6F814E12B9E4400380217469A2FA0587 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Placerville | CA | 95667-8727 |  | 2012-06-13 | 2012-06-13 13:57 | 2012-06-13 14:16 | RUUD - UAMB-042JBZ | 96 | 9 | Yes | Yes | 18.1 | 19.5 | -1.4 | F5879EF9F3514670AA24C6D27A3379C7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Placerville | CA | 95667-8727 |  | 2012-06-13 | 2012-06-13 14:24 | 2012-06-13 14:50 | RUUD - UAMB-024JAZ | 66 | 7.9 | Yes | Yes | 21.2 | 20.7 | 0.5 | D9CAA75EADFE417D8EEF300C50E925F4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.97% | 0.8803 | 23% | [5 empty] | Non-TXV | 11.97%
Fresno | CA | 93727-6443 |  | 2012-08-08 | 2012-08-08 11:25 | 2012-08-08 11:52 | GOODMAN - GSC130361FA | 83 | 3.4 | Yes | Yes | 22.4 | 19.3 | 3.1 | DAD756A0FC5742F293BA20F566426AA3 |  | R22 | Non-TXV |  | 4.096% | 0.95904 | 7.872% | [5 empty] | Non-TXV | 4.096%
Placerville | CA | 95667-9425 |  | 2012-07-05 | 2012-07-05 16:03 | 2012-07-05 16:03 | COLEMAN - BRCQ0361BDG | 67 | 0 | Yes | Yes | 20 | 18.9 | 1.1 | 4A00E07B9FA04EDF8CC69701ABB31A49 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-7856 |  | 2012-05-30 | 2012-05-30 11:46 | 2012-05-30 11:46 | LENNOX - GCS29X-024-50-2PA | 52 | 0 | Yes | Yes | 17.2 | 19.4 | -2.2 | 5025CE9DD4B1410C8F60B52AA0842970 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4623 |  | 2012-07-06 | 2012-07-06 14:05 | 2012-07-06 14:22 | GOODMAN - CKL24-1F | 72 | 2.2 | Yes | Yes | 17.2 | 19.3 | -2.1 | 58233D93A2144E01BF8ADFB377CC6C58 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Fresno | CA | 93722-6540 |  | 2012-05-17 | 2012-05-17 12:54 | 2012-05-17 13:19 | OTHER - NRGF24DD0867.815015 | 53 | 1.7 | Yes | Yes | 17 | 19.9 | -2.9 | A0E76C4D9D2640E9961D09E1D696CA6C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Stockton | CA | 95207-7885 |  | 2012-05-30 | 2012-05-30 12:40 | 2012-05-30 13:00 | TRANE - YCC024F1LOBF | 64 | 9.6 | Yes | Yes | 16.7 | 18.5 | -1.8 | 1DEE743D7E0B4AA5AC43D1D37E5349E1 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Fresno | CA | 93727-7111 |  | 2012-05-11 | 2012-05-11 14:43 | 2012-05-11 15:13 | BDP COMPANY - N/A | 120 | 6.8 | Yes | Yes | 21.5 | 23.1 | -1.6 | 68239547064248E3A85DACFB87DCDF0E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Fresno | CA | 93722-6527 |  | 2012-05-17 | 2012-05-17 18:27 | 2012-05-17 18:51 | 0THER - NRGF24DDB04867.815015 | 53 | 2.6 | Yes | Yes | 19.1 | 21.8 | -2.7 | F5F8658E72494C348AC4F147B52D0678 |  | R22 | Non-TXV |  | 4.906% | 0.95094 | 9.428% | [5 empty] | Non-TXV | 4.906%
Tracy | CA | 95376-4500 |  | 2012-07-09 | 2012-07-09 12:05 | 2012-07-09 12:26 | YORK - D2NP024N05606A | 100 | 3 | Yes | Yes | 19.5 | 20.2 | -0.7 | 751596325C1E4EE8888AC771631D3EAF |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93611-3057 |  | 2012-08-06 | 2012-08-06 13:28 | 2012-08-06 13:46 | BRYANT - 583ANW060AAF | 82 | -5.8 | Yes | Yes | 13.7 | 15.8 | -2.1 | 86DA2DB2A4DB495CA916F211FD785749 |  | R22 | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Los Banos | CA | 93635-3154 |  | 2012-05-16 | 2012-05-16 13:56 | 2012-05-16 14:22 | RHEEM - RAKA-030JAZ | 66 | 2 | Yes | Yes | 21.3 | 20.6 | 0.7 | 182D06BFD35A4E4587FF8B26C724ED71 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Stockton | CA | 95207-7888 |  | 2012-05-30 | 2012-05-30 13:12 | 2012-05-30 13:36 | PAYNE - PY3GNAA24060NA- | 73 | 4.6 | Yes | Yes | 22.4 | 19.9 | 2.5 | CE481E6AED6F48B9AE44CF7793CD525F |  | R410A | TXV |  | 6.301% | 0.93699 | 12.11% | [5 empty] | TXV | 6.301%
Stockton | CA | 95210-6705 |  | 2012-05-29 | 2012-05-29 14:31 | 2012-05-29 14:48 | YORK - H1DE030S06B | 80 | -4.7 | Yes | Yes | 18.9 | 20.6 | -1.7 | 3B280701EDFC47219F0D38BB4753B7E8 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Stockton | CA | 95206-6432 |  | 2012-06-20 | 2012-06-20 14:20 | 2012-06-20 14:49 | CARRIER - 38CKC042350 | 81 | 4.7 | Yes | Yes | 18.5 | 20.4 | -1.9 | 5682EE27E504495AB12495ECBD1882A6 |  | R22 | TXV |  | 5.802% | 0.94198 | 11.15% | [5 empty] | TXV | 5.802%
Clovis | CA | 93611-3128 |  | 2012-05-15 | 2012-05-15 11:58 | 2012-05-15 12:16 | RHEEM - RRNA-B030JK06X | 72 | 2.1 | Yes | Yes | 22.1 | 20.4 | 1.7 | 8CFEF1A78AF54BE9BE2098D9F64CD914 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Ione | CA | 95640-9578 |  | 2012-07-17 | 2012-07-17 15:25 | 2012-07-17 15:53 | OTHER - S30A-030KA | 68 | -6.4 | Yes | Yes | 24 | 20.8 | 3.2 | DC6D059726EE49B9B9149B534055C50D |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95207-5837 |  | 2012-06-28 | 2012-06-28 09:15 | 2012-06-28 09:33 | RHEEM - RAKB-030JAZ | 66 | 6.5 | Yes | Yes | 17.6 | 19.8 | -2.2 | 1C4330718C11478D99CCF2D26AE3C49D |  | R22 | Non-TXV |  | 9.848% | 0.90152 | 18.93% | [5 empty] | Non-TXV | 9.848%
Gustine | CA | 95322-1418 |  | 2012-05-15 | 2012-05-15 14:45 | 2012-05-15 15:01 | LENNOX - UNK | 67 | 5.6 | Yes | Yes | 19.3 | 21 | -1.7 | 952F80DDACF44A7CAA284AFB855E6339 |  | R22 | Non-TXV |  | 8.358% | 0.91642 | 16.06% | [5 empty] | Non-TXV | 8.358%
Merced | CA | 95341-5837 |  | 2012-05-08 | 2012-05-08 13:48 | 2012-05-08 14:06 | AMERICAN STANDARD - TTR030C100AO | 74 | 7.8 | Yes | Yes | 19.6 | 21.5 | -1.9 | 26F1A395BB724945938CCA53D5264396 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.54% | 0.89459 | 20.26% | [5 empty] | Non-TXV | 10.54%
Gustine | CA | 95322-1611 |  | 2012-05-24 | 2012-05-24 13:46 | 2012-05-24 14:04 | CARRIER - H2RC048S06HA | 119 | 4.1 | Yes | Yes | 18.8 | 19.5 | -0.7 | 89CF89AC988845DA99E17467A41B6205 |  | R22 | Non-TXV |  | 3.445% | 0.96555 | 6.621% | [5 empty] | Non-TXV | 3.445%
Grass Valley | CA | 95945-6641 |  | 2012-05-30 | 2012-05-30 10:57 | 2012-05-30 10:57 | RHEEM - UNK | 58 | 0 | Yes | Yes | 16.7 | 19.5 | -2.8 | 81B909CE5AF14D51A08747D7DF58AD4A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3223 |  | 2012-06-12 | 2012-06-12 08:56 | 2012-06-12 09:12 | DAY & NIGHT - UNK | 80 | -4.7 | Yes | Yes | 21.6 | 19.7 | 1.9 | 37E463E6CD35448B82161D00E2101159 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Merced | CA | 95341-6103 |  | 2012-05-09 | 2012-05-09 12:38 | 2012-05-09 12:57 | WEATHER KING - 10AJB24A01 | 85 | 2.5 | Yes | Yes | 15.5 | 17.7 | -2.2 | EFD4E91B102B472EB174781217FEA222 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95207-2302 |  | 2012-05-31 | 2012-05-31 14:17 | 2012-05-31 14:34 | RHEEM - RRNL-BO30JK06X | 77 | 3.4 | Yes | Yes | 15.2 | 17.8 | -2.6 | 3447EC0E2948495BA43D8B2AD20F08A2 |  | R410A | TXV |  | 4.416% | 0.95584 | 8.486% | [5 empty] | TXV | 4.416%
Manteca | CA | 95336-2854 |  | 2012-05-09 | 2012-05-09 10:28 | 2012-05-09 10:47 | DAY & NIGHT - 585C030050 | 78 | 3.1 | Yes | Yes | 24.6 | 19.3 | 5.3 | 01D80AD91CE64BBDAA3FF3FCB83795D6 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
Merced | CA | 95341-6103 |  | 2012-05-09 | 2012-05-09 13:52 | 2012-05-09 14:10 | PAYNE - 591ANX024000AAAA | 51 | 1.8 | Yes | Yes | 22.9 | 20.4 | 2.5 | 202FFD4977584FBDB686C78C72E46814 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93722-8007 |  | 2012-07-02 | 2012-07-02 13:20 | 2012-07-02 13:43 | COLEMAN - DAYH-F024N045C | 70 | 2.1 | Yes | Yes | 20.1 | 19.5 | 0.6 | 1A78984A7B724E298EC46C02A9D332E4 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95210-1634 |  | 2012-05-09 | 2012-05-09 15:15 | 2012-05-09 15:36 | BDP - 585A024055YAC | 51 | 1.7 | Yes | Yes | 23.9 | 20.4 | 3.5 | E1234C11786248A889CA0987E9C6D858 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Sutter Creek | CA | 95685-9709 |  | 2012-07-20 | 2012-07-20 12:20 | 2012-07-20 12:20 | BDP - 561CJ036-C | 76 | 0 | Yes | Yes | 16.2 | 18.2 | -2 | 848E0C2DA38640559B0940D0306B9849 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6171 |  | 2012-05-15 | 2012-05-15 16:28 | 2012-05-15 16:28 | CARRIER - 48GX-024040301 | 52 | 0 | Yes | Yes | 18.8 | 20.8 | -2 | C6E5189BD99044988E2CCEBB4216C219 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5144 |  | 2012-05-10 | 2012-05-10 12:04 | 2012-05-10 12:23 | - 5856JW036060ABAF | 82 | -4.8 | Yes | Yes | 18.4 | 20.4 | -2 | DF4810C41A2940F6BF14C77C9B8BBC5F |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Manteca | CA | 95337-8559 |  | 2012-05-14 | 2012-05-14 12:57 | 2012-05-14 13:17 | GOODMAN - UNK | 64 | 4.1 | Yes | Yes | 17.6 | 19.5 | -1.9 | B2B06811DE3347A7B2FE5F5BAF5C8B9D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.406% | 0.93594 | 12.31% | [5 empty] | Non-TXV | 6.406%
Stockton | CA | 95210-2330 |  | 2012-05-18 | 2012-05-18 13:52 | 2012-05-18 14:09 | UNK - UNK | 50 | -2.9 | Yes | Yes | 26.4 | 22 | 4.4 | 422CAD51A4C349A2A4331D85D5ED7FEB |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Stockton | CA | 95204-1622 |  | 2012-05-07 | 2012-05-07 14:30 | 2012-05-07 15:14 | TRANE - TTX036C100A1 | 150 | 7.1 | Yes | Yes | 4.8 | 15.5 | -10.7 | 996E6C312FEF4C6F815C134A1BD941EE |  | R22 | Non-TXV |  | 4.733% | 0.95267 | 9.096% | [5 empty] | Non-TXV | 4.733%
Cameron Park | CA | 95682-7607 |  | 2012-05-14 | 2012-05-14 12:29 | 2012-05-14 12:50 | GOODMAN - GSC130361DE | 119 | 15.6 | Yes | Yes | 18.4 | 20.1 | -1.7 | 039982872DEE42CA98A9A8E1F156611C | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.11% | 0.86891 | 25.19% | [5 empty] | Non-TXV | 13.11%
Atascadero | CA | 93422-5576 |  | 2012-07-10 | 2012-07-10 13:13 | 2012-07-10 13:31 | BDP - 561CJ018-E | 53 | 2.7 | Yes | Yes | 18.3 | 20.4 | -2.1 | 1CAAD5D345D146FEB55C46B4D5BCD1C9 |  | R22 | Non-TXV |  | 5.094% | 0.94906 | 9.79% | [5 empty] | Non-TXV | 5.094%
Fresno | CA | 93722-4535 |  | 2012-06-06 | 2012-06-06 10:59 | 2012-06-06 11:18 | GOODMAN - PGB024050-1 | 54 | 1.6 | Yes | Yes | 23.9 | 20.4 | 3.5 | 93BEDE03CA544CE1BA92A99E577703CD |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Diamond Springs | CA | 95619-9359 |  | 2012-07-16 | 2012-07-16 16:52 | 2012-07-16 17:44 | CARRIER - 38EH024320 | 96 | 14.6 | Yes | Yes | 26.7 | 21 | 5.7 | 4BD745A2489F4C318CCDC9D59DA0071D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.21% | 0.84792 | 29.23% | [5 empty] | Non-TXV | 15.21%
Stockton | CA | 95206-2744 |  | 2012-05-14 | 2012-05-14 12:44 | 2012-05-14 13:03 | BRYANT - 582ANW030060NAAD | 55 | 5.8 | Yes | Yes | 26.2 | 20.9 | 5.3 | 0B2C1BD11645448190C31E49B77D86D8 | OK: Verified Refrigerant Charge | R22 | TXV |  | 10.55% | 0.89455 | 20.27% | [5 empty] | TXV | 10.55%
Atwater | CA | 95301-2321 |  | 2012-05-09 | 2012-05-09 15:17 | 2012-05-09 15:39 | RHEEM - RRKA-A024JK06E | 50 | 1.5 | Yes | Yes | 18.8 | 19.8 | -1 | D57337A7C77C4A45B1C7050B76993094 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-4538 |  | 2012-05-23 | 2012-05-23 11:05 | 2012-05-23 11:31 | GOODMAN - GPG13240451CB | 72 | 2.1 | Yes | Yes | 17.6 | 20.4 | -2.8 | 0A9A8A82089C40959FEBBD3592F46F84 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Merced | CA | 95340-5031 |  | 2012-05-15 | 2012-05-15 15:46 | 2012-05-15 16:05 | CARRIER - UNK | 88 | 5.4 | Yes | Yes | 23.3 | 20.4 | 2.9 | F41FDCA835B74030B5A75EB7EFAAD36C |  | R22 | Non-TXV |  | 6.136% | 0.93864 | 11.79% | [5 empty] | Non-TXV | 6.136%
Atwater | CA | 95301-2321 |  | 2012-05-09 | 2012-05-09 12:59 | 2012-05-09 13:23 | RHEEM - RRKA-A024JK06X | 50 | -2.9 | Yes | Yes | 19.3 | 19.8 | -0.5 | EC681FE9055A4664A51D30A3CB40064C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Sanger | CA | 93657-3046 |  | 2012-05-10 | 2012-05-10 11:54 | 2012-05-10 12:17 | N/A - N/A | 85 | 11.8 | Yes | Yes | 21.3 | 20.3 | 1 | DEFC5F8CFAFE469387230919D241112F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 13.88% | 0.86118 | 26.68% | [5 empty] | Non-TXV | 13.88%
Pinedale | CA | 93650-1317 |  | 2012-06-13 | 2012-06-13 15:03 | 2012-06-13 15:21 | CARRIER - 48SS-030060331 | 53 | 4.9 | Yes | Yes | 22.2 | 20.6 | 1.6 | 7FDB3736CC514F77A6DF93FD78ED502C |  | R22 | Non-TXV |  | 9.245% | 0.90755 | 17.77% | [5 empty] | Non-TXV | 9.245%
Fresno | CA | 93727-2222 |  | 2012-05-11 | 2012-05-11 11:44 | 2012-05-11 12:02 | YORK - D3GA024N02806A | 68 | 3 | Yes | Yes | 19.2 | 21.4 | -2.2 | B1FE3D8694A44C7DBDD94A1AA61D4474 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Oakdale | CA | 95361-7703 |  | 2012-05-29 | 2012-05-29 10:22 | 2012-05-29 10:51 | ARCOAIRE - G030GB2 | 74 | 2.3 | Yes | Yes | 17.7 | 19.8 | -2.1 | 31E2F079B98645E18997991C8A64BE98 |  | R22 | Non-TXV |  | 3.108% | 0.96892 | 5.973% | [5 empty] | Non-TXV | 3.108%
Stockton | CA | 95204-3649 |  | 2012-05-08 | 2012-05-08 15:05 | 2012-05-08 15:28 | LENNOX - GCS20H-261-50-1P | 49 | 2.4 | Yes | Yes | 17.8 | 19 | -1.2 | F78A1D3E2C3442F9B8562F5E63B67DC0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.898% | 0.95102 | 9.413% | [5 empty] | Non-TXV | 4.898%
Paso Robles | CA | 93446-5422 |  | 2012-07-11 | 2012-07-11 16:34 | 2012-07-11 16:54 | YORK - H4DH018S06A | 78 | 2.8 | Yes | Yes | 18.9 | 20.1 | -1.2 | 141502FABC2F4B7EBD0E9DE1F655B6EF |  | R22 | Non-TXV |  | 3.59% | 0.9641 | 6.899% | [5 empty] | Non-TXV | 3.59%
Manteca | CA | 95337-7921 |  | 2012-05-14 | 2012-05-14 12:11 | 2012-05-14 12:29 | YORK - H2RA036S06G | 63 | 2.6 | Yes | Yes | 20.2 | 19.5 | 0.7 | 221CE6FD00CE4292910F4DEA8D2CEC96 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.127% | 0.95873 | 7.931% | [5 empty] | Non-TXV | 4.127%
Yuba City | CA | 95991-1540 |  | 2012-06-13 | 2012-06-13 11:06 | 2012-06-13 11:32 | YORK - D1NA024N05606C | 54 | 2.2 | Yes | Yes | 17 | 19.3 | -2.3 | FA531E24ED964B549E8884FF6B0A6670 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Los Banos | CA | 93635-3088 |  | 2012-05-09 | 2012-05-09 12:42 | 2012-05-09 13:02 | GIBSON - JS3BC-036KA | 82 | 5.5 | Yes | Yes | 22.2 | 19.3 | 2.9 | 23903C81929C46B2B1F1314273368CD4 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6.707% | 0.93293 | 12.89% | [5 empty] | Non-TXV | 6.707%
Stockton | CA | 95210-2447 |  | 2012-05-23 | 2012-05-23 13:37 | 2012-05-23 13:53 | RHEEM - UNK | 54 | 1.7 | Yes | Yes | 21.5 | 19.8 | 1.7 | 4F12C3F4F9B240A89A5554D176899610 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Paso Robles | CA | 93446-5422 |  | 2012-07-11 | 2012-07-11 15:29 | 2012-07-11 15:54 | YORK - H4DH018S06A | 78 | 25.6 | Yes | Yes | 17.6 | 20.4 | -2.8 | E98EF8717F7B4850B026C948B1A1D918 |  | R22 | Non-TXV |  | 32.82% | 0.67179 | 63.07% | [5 empty] | Non-TXV | 32.82%
Fresno | CA | 93727-2222 |  | 2012-05-11 | 2012-05-11 12:11 | 2012-05-11 12:30 | YORK - D3GA024N02806A | 68 | 2 | Yes | Yes | 17.8 | 19 | -1.2 | D1A5F68ECBB14009AA97954AAA3CFA71 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Yuba City | CA | 95991-5802 |  | 2012-06-14 | 2012-06-14 10:19 | 2012-06-14 10:41 | OTHER - PGD342090K001C1 | 104 | -9.8 | Yes | Yes | 21 | 19.3 | 1.7 | 8FC594DFA03544F28D76D22B4454D97B |  | R410A | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Merced | CA | 95340-3539 |  | 2012-05-07 | 2012-05-07 16:20 | 2012-05-07 16:41 | BRYANT - 583ANW036060NAAF | 82 | 4.6 | Yes | Yes | 25 | 23.7 | 1.3 | AD55957C84DB464CAC50A547FB166EE0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.61% | 0.9439 | 10.78% | [5 empty] | Non-TXV | 5.61%
Merced | CA | 95341-5900 |  | 2012-05-16 | 2012-05-16 12:54 | 2012-05-16 13:12 | CARRIER - 591ANX018000AAAA | 48 | 5.4 | Yes | Yes | 24.3 | 20.2 | 4.1 | D489561B22B14BC6AB82F413C1CF010C |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Clovis | CA | 93611-5411 |  | 2012-05-10 | 2012-05-10 15:42 | 2012-05-10 15:42 | CARRIER - UNK | 75 | 0 | Yes | Yes | 18.2 | 21.2 | -3 | 0CAB8AFEDD1A4249B469F9DF63BA33ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3121 |  | 2012-05-16 | 2012-05-16 11:56 | 2012-05-16 12:26 | GOODMAN - GPG13480901AC | 145 | 5.4 | Yes | Yes | 23 | 20.1 | 2.9 | 30EE35B2472E407DA7A9ADC3FB5E5CE9 |  | R22 | Non-TXV |  | 3.724% | 0.96276 | 7.157% | [5 empty] | Non-TXV | 3.724%
French Camp | CA | 95231-9619 |  | 2012-07-24 | 2012-07-24 09:53 | 2012-07-24 10:15 | COLEMAN - 9536C901 | 58 | 2.5 | Yes | Yes | 22.9 | 17.2 | 5.7 | 7061E3293D424752862FE4F213FF33D4 |  | R22 | Non-TXV |  | 4.31% | 0.9569 | 8.284% | [5 empty] | Non-TXV | 4.31%
Lathrop | CA | 95330-9170 |  | 2012-05-15 | 2012-05-15 12:01 | 2012-05-15 12:20 | GOODMAN - CKJ24-1A | 86 | 3 | Yes | Yes | 18.4 | 20.4 | -2 | 94B28779575840D292B52C5338A599E2 |  | R22 | Non-TXV |  | 3.488% | 0.96512 | 6.704% | [5 empty] | Non-TXV | 3.488%
Merced | CA | 95341-7017 |  | 2012-05-30 | 2012-05-30 14:58 | 2012-05-30 15:26 | GOODMAN - CLJ421B | 84 | 15.8 | Yes | Yes | 20.5 | 22.1 | -1.6 | E6096BD5A1A9450AA04F30E790BE8EE1 |  | R22 | Non-TXV |  | 18.81% | 0.8119 | 36.15% | [5 empty] | Non-TXV | 18.81%
Stockton | CA | 95210-1741 |  | 2012-05-15 | 2012-05-15 11:12 | 2012-05-15 11:30 | WESTINGHOUSE - IE024AAAON | 55 | -3.2 | Yes | Yes | 19.1 | 19.4 | -0.3 | 5BB354AC512B466BBD40C07B32475C4F |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Auburn | CA | 95603-3743 |  | 2012-05-18 | 2012-05-18 12:59 | 2012-05-18 13:24 | STANDARD - 7B0023B100A1 | 53 | 4.9 | Yes | Yes | 23 | 19.7 | 3.3 | 017522174FAB4C83BDEED6718362BE6D |  | R22 | Non-TXV |  | 9.245% | 0.90755 | 17.77% | [5 empty] | Non-TXV | 9.245%
Clovis | CA | 93612-2343 |  | 2012-08-08 | 2012-08-08 17:45 | 2012-08-08 18:01 | RHEEM - RRPL-B036JK06X | 92 | 4.7 | Yes | Yes | 18.5 | 21.5 | -3 | E73B26E1738F4D54A58FDD69CEFEACA5 |  | R410A | Non-TXV |  | 5.109% | 0.94891 | 9.818% | [5 empty] | Non-TXV | 5.109%
Fresno | CA | 93722-6523 |  | 2012-05-17 | 2012-05-17 11:19 | 2012-05-17 11:54 | OTHER - NRGF24DDB04867.815015 | 53 | 2.7 | Yes | Yes | 15.7 | 19.5 | -3.8 | 45A3D4355F574488874D3C2D574A3B8B |  | R22 | Non-TXV |  | 5.094% | 0.94906 | 9.79% | [5 empty] | Non-TXV | 5.094%
Stockton | CA | 95210-3202 |  | 2012-06-13 | 2012-06-13 13:40 | 2012-06-13 13:58 | YORK - D2NP030N05606A | 73 | 2.5 | Yes | Yes | 22 | 19.3 | 2.7 | 276D45241AAA4D1CA681B3EEABA873B2 |  | R22 | Non-TXV |  | 3.425% | 0.96575 | 6.581% | [5 empty] | Non-TXV | 3.425%
Stockton | CA | 95207-2081 |  | 2012-06-06 | 2012-06-06 12:50 | 2012-06-06 13:06 | PAYNE - 565AJ018 | 50 | 5.9 | Yes | Yes | 17.7 | 19.5 | -1.8 | 6D1884CEE8B042A39C28FD94975BF0BF |  | R22 | Non-TXV |  | 11.8% | 0.882 | 22.68% | [5 empty] | Non-TXV | 11.8%
Paradise | CA | 95969-2509 |  | 2012-05-10 | 2012-05-10 10:58 | 2012-05-10 11:21 | GAMA - PCX036075-1AB REV B | 93 | 3.8 | Yes | Yes | 26 | 25.4 | 0.6 | AF80AA7D4BFA46459912F3B829DE0F93 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.086% | 0.95914 | 7.852% | [5 empty] | Non-TXV | 4.086%
Los Banos | CA | 93635-4813 |  | 2012-05-16 | 2012-05-16 12:57 | 2012-05-16 12:57 | BRYANT - 574BNW060090NB | 125 | 0 | Yes | Yes | 25 | 21.1 | 4 | FB67C6798500429DA6F20F7E20B92313 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3202 |  | 2012-06-12 | 2012-06-12 08:24 | 2012-06-12 08:41 | WESTINGHOUSE - IE030BAAON | 90 | -5.3 | Yes | Yes | 24.3 | 20.7 | 3.6 | 1F585D9B2126416C922C3DDC390E30DB |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Stockton | CA | 95206-2506 |  | 2012-05-08 | 2012-05-08 16:16 | 2012-05-08 16:42 | DAY NIGHT - 585A030080YAC | 50 | 13.7 | Yes | Yes | 21.3 | 23.7 | -2.4 | 0710BBF7033C408592EC9704A0C67846 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 27.4% | 0.726 | 52.66% | [5 empty] | Non-TXV | 27.4%
Paso Robles | CA | 93446-5422 |  | 2012-07-11 | 2012-07-11 16:08 | 2012-07-11 16:25 | YORK - H4DH018S06A | 78 | 2.3 | Yes | Yes | 18.9 | 19.9 | -1 | 58B2A4C193C946B98835E7FBE1783B01 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Stockton | CA | 95210-1741 |  | 2012-05-09 | 2012-05-09 14:06 | 2012-05-09 14:25 | WESTINGHOUSE - IE024AAAON | 55 | -3.2 | Yes | Yes | 18.4 | 21.4 | -3 | 6FC99198354E4CF1B7435CAAE5855057 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Auburn | CA | 95603-3738 |  | 2012-05-18 | 2012-05-18 11:25 | 2012-05-18 11:43 | STANDARD - 7B0023B100A1 | 54 | 1.8 | Yes | Yes | 17 | 19.5 | -2.5 | 4336FC1F01A44B3DB6B8EE78B2672612 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Atwater | CA | 95301-3517 |  | 2012-05-10 | 2012-05-10 15:58 | 2012-05-10 16:33 | CARRIER - 38TXA036330 | 105 | 7.5 | Yes | Yes | 29.1 | 23.4 | 5.7 | 79DF127E4FE442418D54151411C1108C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Pinedale | CA | 93650-1343 |  | 2012-06-13 | 2012-06-13 13:56 | 2012-06-13 14:15 | NORDYNE - GR4GC-036K072X | 78 | 2.3 | Yes | Yes | 19.3 | 18.1 | 1.2 | 02127A1671534B85AEE5AFA8AD8A16CE |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Auburn | CA | 95603-3742 |  | 2012-05-15 | 2012-05-15 14:19 | 2012-05-15 14:43 | STANDARD - 7B0023B100A1 | 54 | 5.3 | Yes | Yes | 20 | 19.3 | 0.7 | B6A2FCB411DA416BB35CB4C681952CA4 |  | R22 | Non-TXV |  | 9.815% | 0.90185 | 18.86% | [5 empty] | Non-TXV | 9.815%
Stockton | CA | 95206-5712 |  | 2012-06-08 | 2012-06-08 17:06 | 2012-06-08 17:28 | OTHER - AA1CJ036-C | 72 | 13.3 | Yes | Yes | 18.8 | 19.2 | -0.4 | 6430F9CC093E40EAAD9587E6F6A035E9 |  | R22 | TXV |  | 18.47% | 0.81528 | 35.5% | [5 empty] | TXV | 18.47%
Paso Robles | CA | 93446-5422 |  | 2012-07-12 | 2012-07-12 11:42 | 2012-07-12 12:03 | YORK - H4DH018S06A | 78 | 3.1 | Yes | Yes | 22.2 | 20.5 | 1.7 | F0BE7A5570114574B5FA41218C63615B |  | R22 | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
Stockton | CA | 95205-4638 |  | 2012-06-07 | 2012-06-07 15:10 | 2012-06-07 15:26 | LENNOX - GCS20RV-411-75-1P | 70 | 6.4 | Yes | Yes | 23.2 | 21.5 | 1.7 | 2C7D706F70F14E1FB6DEC099E0E1DAAC |  | R22 | Non-TXV |  | 9.143% | 0.90857 | 17.57% | [5 empty] | Non-TXV | 9.143%
Stockton | CA | 95207-6040 |  | 2012-06-28 | 2012-06-28 10:31 | 2012-06-28 10:49 | BRYANT - 582ANW024060AAAD | 53 | 6.5 | Yes | Yes | 20.5 | 18.7 | 1.8 | 8CB9A9DBF2D04FCA8D197477C2F223BE |  | R22 | Non-TXV |  | 12.26% | 0.87736 | 23.57% | [5 empty] | Non-TXV | 12.26%
Auburn | CA | 95602-8265 |  | 2012-05-29 | 2012-05-29 13:03 | 2012-05-29 13:19 | BRYANT - 604ANX036000AA | 169 | -9.9 | Yes | Yes | 16 | 18.7 | -2.7 | 9F8899FA6BA44843808B414FBE82F1BE |  | R22 | Non-TXV |  | -5.858% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.858%
Merced | CA | 95348-3025 |  | 2012-06-01 | 2012-06-01 14:44 | 2012-06-01 15:01 | BDP - 565BJ024 | 70 | 2.1 | Yes | Yes | 24.1 | 20.1 | 4 | 0AB27BC5EBD044099D1AC4B1D743AAA4 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Auburn | CA | 95602-2602 |  | 2012-07-24 | 2012-07-24 12:12 | 2012-07-24 12:33 | RHEEM - UNK | 70 | 3 | Yes | Yes | 19 | 19.3 | -0.3 | 9ECCC29C662541278E378F7CE807ECDF |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95206-2215 |  | 2012-05-08 | 2012-05-08 11:31 | 2012-05-08 11:50 | COMFERTMAKER - N2A336AKB200 | 70 | -4.9 | Yes | Yes | 17 | 19.4 | -2.4 | 7475BE3A49914F58898E3103B0F731AD | OK: Verified Refrigerant Charge | R22 | TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | TXV |  |  | -7%
Oakdale | CA | 95361-2903 |  | 2012-05-23 | 2012-05-23 11:14 | 2012-05-23 11:36 | BDP - 561AJ030-A | 66 | 7.9 | Yes | Yes | 18.9 | 19.1 | -0.2 | 1A6B8D28AAD74A28AB44A1574B4B9FF3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.97% | 0.8803 | 23% | [5 empty] | Non-TXV | 11.97%
Auburn | CA | 95603-3743 |  | 2012-05-11 | 2012-05-11 14:01 | 2012-05-11 14:31 | STANDARD - 7B0023B100A1 | 54 | 6.3 | Yes | Yes | 22 | 20.6 | 1.5 | ED0B3EC0F1774A2F99C6C17FEF76EEB7 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Fresno | CA | 93722-3003 |  | 2012-08-15 | 2012-08-15 09:20 | 2012-08-15 10:12 | OTHER - 42MC-000087CR | 135 | 4.5 | Yes | Yes | 19 | 20.2 | -1.2 | 62A3538D35CC4DE79ADB332FCF8A98E7 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Marysville | CA | 95901-8230 |  | 2012-05-23 | 2012-05-23 12:02 | 2012-05-23 12:32 | CARRIER - UNK | 60 | 9.8 | Yes | Yes | 19 | 21.3 | -2.3 | 7A99D4EC92014AB9B0F536E2E4884E94 |  | R22 | Non-TXV |  | 16.33% | 0.83667 | 31.39% | [5 empty] | Non-TXV | 16.33%
Fresno | CA | 93726-1235 |  | 2012-05-09 | 2012-05-09 13:23 | 2012-05-09 13:44 | - CE48-1EB | 85 | 2.5 | Yes | Yes | 16.9 | 19.8 | -2.9 | 0DFF9066ED99472584ECD89E4B8BABC7 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93727-5865 |  | 2012-08-08 | 2012-08-08 09:09 | 2012-08-08 09:29 | LENNOX - 13ACD-048-230-01 | 204 | 6.1 | Yes | Yes | 23.6 | 20.4 | 3.2 | 8967A08D00184C70B975DF5F7D3DC5DA |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Paso Robles | CA | 93446-5422 |  | 2012-07-12 | 2012-07-12 11:10 | 2012-07-12 11:30 | YORK - H4DH018S06A | 78 | 2.3 | Yes | Yes | 17.3 | 19.4 | -2.1 | E1330F4DFC8B42B6871728D8C1EA8062 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Stockton | CA | 95205-7793 |  | 2012-05-17 | 2012-05-17 11:16 | 2012-05-17 11:34 | BRYANT - 561CJ042-F | 93 | 6.6 | Yes | Yes | 18.6 | 19.8 | -1.2 | AB78D53110C14BC39C7C6BFDB94A91D1 | OK: Verified Refrigerant Charge | R22 | TXV |  | 7.097% | 0.92903 | 13.64% | [5 empty] | TXV | 7.097%
Dinuba | CA | 93618-4025 |  | 2012-05-08 | 2012-05-08 15:39 | 2012-05-08 16:02 | YORK - D1NA030N036AC | 76 | 2.6 | Yes | Yes | 17.4 | 19.8 | -2.4 | BE020D8B1C2F4CEDB6F9462E1398E69F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Paso Robles | CA | 93446-5422 |  | 2012-07-12 | 2012-07-12 10:38 | 2012-07-12 10:58 | YORK - H4DH018S06A | 78 | 2.4 | Yes | Yes | 15.9 | 18.2 | -2.3 | AE6B55CE32CF437B8A3633A2011B401F |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Marysville | CA | 95901-6836 |  | 2012-06-07 | 2012-06-07 09:42 | 2012-06-07 09:59 | OTHER - AC024M1021CA | 52 | 2.3 | Yes | Yes | 18 | 19.9 | -1.9 | AEBFB8D520214A89813152C6F3CE7279 |  | R22 | Non-TXV |  | 4.423% | 0.95577 | 8.5% | [5 empty] | Non-TXV | 4.423%
Fresno | CA | 93722-4128 |  | 2012-05-14 | 2012-05-14 14:48 | 2012-05-14 14:48 | RHEEM - RRNL-B036JK06X | 92 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | FAA349D10731473AA6572D5463FFCB14 | OK: Verified Refrigerant Charge | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1856 |  | 2012-05-10 | 2012-05-10 14:05 | 2012-05-10 14:24 | GOODMAN - GPG1330070M41AB | 80 | 2.4 | Yes | Yes | 23.5 | 20.6 | 3 | 6204F4DCED6143A1817F60904CC7F03F | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-3824 |  | 2012-05-08 | 2012-05-08 16:44 | 2012-05-08 17:01 | YORK - D1NA042N05606C | 76 | 4.7 | Yes | Yes | 5.4 | 20.4 | -15 | 29EC79BDA10740C996F9CA643FCFC5DE | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6.184% | 0.93816 | 11.88% | [5 empty] | Non-TXV | 6.184%
Paso Robles | CA | 93446-5423 |  | 2012-07-12 | 2012-07-12 13:27 | 2012-07-12 13:46 | YORK - H4DH018S06A | 78 | 5.1 | Yes | Yes | 20 | 18.8 | 1.2 | D4B7041AAE8748599021C917D95DAD81 |  | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Los Banos | CA | 93635-9408 |  | 2012-05-18 | 2012-05-18 11:34 | 2012-05-18 11:57 | BRYANT - 561CJ042B- | 93 | 6.4 | Yes | Yes | 16.8 | 19.7 | -2.9 | 979BF11F015844D1AE2F7A156CD6A1CC |  | R22 | Non-TXV |  | 6.882% | 0.93118 | 13.23% | [5 empty] | Non-TXV | 6.882%
Planada | CA | 95365-0000 |  | 2012-05-22 | 2012-05-22 13:00 | 2012-05-22 13:00 | RHEEM - RQNL--B036K000 | 85 | 0 | Yes | Yes | 19.2 | 18.5 | 0.8 | A4A47775272349AC973772519AC26045 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2231 |  | 2012-05-17 | 2012-05-17 10:30 | 2012-05-17 10:48 | COMFORTMAKER - N4A330AKC200 | 74 | 3.2 | Yes | Yes | 17.5 | 18 | -0.5 | DB373972541A4A069EF15AE50160D372 | OK: Verified Refrigerant Charge | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
Marysville | CA | 95901-6837 |  | 2012-05-31 | 2012-05-31 09:59 | 2012-05-31 10:15 | OTHER - AC024M1021A | 52 | 1.8 | Yes | Yes | 15 | 17.7 | -2.7 | 10A1E330B05C46EFA37BCA4791BA371C |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Manteca | CA | 95336-4057 |  | 2012-05-07 | 2012-05-07 16:21 | 2012-05-07 20:46 | INTERNATIONAL COMFORT PRODUCTS - NAC048AKA5 | 108 | 5.8 | Yes | Yes | 25.1 | 21.5 | 3.6 | AB4EE5721E5C4DB0BD53B57D41A031B9 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Stockton | CA | 95205-7808 |  | 2012-05-16 | 2012-05-16 15:20 | 2012-05-16 15:38 | PAYNE - PA10JA036-C | 73 | 3.3 | Yes | Yes | 19.2 | 21.3 | -2.1 | 47705365D97E4AF0BB81AC18189966FE | OK: Verified Refrigerant Charge | R22 | TXV |  | 4.521% | 0.95479 | 8.687% | [5 empty] | TXV | 4.521%
Tracy | CA | 95376-4911 |  | 2012-07-09 | 2012-07-09 11:05 | 2012-07-09 11:33 | CARRIER - 38CK042300 | 80 | 12.4 | Yes | Yes | 17.6 | 18.2 | -0.6 | 833913BBED4D49DBA37B72D2264E8CF3 |  | R22 | Non-TXV |  | 15.5% | 0.845 | 29.79% | [5 empty] | Non-TXV | 15.5%
Selma | CA | 93662-2868 |  | 2012-06-11 | 2012-06-11 12:20 | 2012-06-11 12:38 | GOODMAN - GPG10300701 | 50 | 4.6 | Yes | Yes | 23.8 | 20.8 | 3 | C4967C63ACE949FB8CAB6AB1C8E42A1D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.2% | 0.908 | 17.68% | [5 empty] | Non-TXV | 9.2%
Chico | CA | 95928-6847 |  | 2012-05-10 | 2012-05-10 12:20 | 2012-05-10 12:40 | - | 85 | 5.5 | Yes | Yes | 23.2 | 21.3 | 2 | 89F802AE3CFB49C994AB490DD8209859 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Chowchilla | CA | 93610-3266 |  | 2012-05-11 | 2012-05-11 11:21 | 2012-05-11 11:40 | GENERAL ELECTRIC - BTD718A100A0 | 46 | 1.4 | Yes | Yes | 21.6 | 20.4 | 1.2 | 9AA26C32F99A4964AFC48754864941F5 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Chowchilla | CA | 93610-3264 |  | 2012-05-11 | 2012-05-11 10:43 | 2012-05-11 11:01 | YORK - AC018M1021A | 49 | 1.5 | Yes | Yes | 22.6 | 20.4 | 2.2 | 1C8D1E081A3542329D5CBD6105DCAE0C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Chowchilla | CA | 93610-3267 |  | 2012-06-14 | 2012-06-14 12:46 | 2012-06-14 13:11 | WEATHER KING - 13AJA240700264 | 77 | 5.1 | Yes | Yes | 17.6 | 18.2 | -0.6 | CAF3CA9B16884C0191920EF30CA34643 |  | R22 | Non-TXV |  | 6.623% | 0.93377 | 12.73% | [5 empty] | Non-TXV | 6.623%
Stockton | CA | 95207-7435 |  | 2012-06-12 | 2012-06-12 12:18 | 2012-06-12 12:43 | RUUD - UAKA-030JAS | 66 | 13.4 | Yes | Yes | 25.1 | 20.8 | 4.3 | 8428CAC1D3874364B95775B60FD0B847 |  | R22 | Non-TXV |  | 20.3% | 0.79697 | 39.02% | [5 empty] | Non-TXV | 20.3%
Mendota | CA | 93640-1910 |  | 2012-07-09 | 2012-07-09 11:26 | 2012-07-09 11:44 | WESTINGHOUSE - N/A | 192 | 5.6 | Yes | Yes | 22.9 | 19.9 | 3 | 590447F32A6B4F47BF7184BFA6D5FDA0 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Oakdale | CA | 95361-3726 |  | 2012-06-07 | 2012-06-07 13:40 | 2012-06-07 14:04 | BRYANT - 574ANW036060NA-- | 167 | 5.2 | Yes | Yes | 20 | 21.5 | -1.5 | E207E3B3234848CA981764D4E92F078E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.114% | 0.96886 | 5.984% | [5 empty] | Non-TXV | 3.114%
Stockton | CA | 95210-1214 |  | 2012-06-28 | 2012-06-28 13:05 | 2012-06-28 13:28 | SEARS - 816231 | 67 | 9.7 | Yes | Yes | 18.7 | 21.1 | -2.4 | E4C6B17226404FF8BB803F105D77D2FB |  | R22 | Non-TXV |  | 14.48% | 0.85522 | 27.82% | [5 empty] | Non-TXV | 14.48%
Fresno | CA | 93722-4696 |  | 2012-05-29 | 2012-05-29 13:53 | 2012-05-29 14:13 | CARRIER - 38BRC042340 | 103 | 3.8 | Yes | Yes | 22.4 | 19.8 | 2.6 | E481022744DF42A7803386EE6D872E83 |  | R22 | TXV |  | 3.689% | 0.96311 | 7.09% | [5 empty] | TXV | 3.689%
Chowchilla | CA | 93610-3264 |  | 2012-06-14 | 2012-06-14 13:41 | 2012-06-14 15:34 | WEATHER KING - 13AJ24A01 | 77 | 3.2 | Yes | Yes | 18.6 | 18.1 | 0.5 | 8B7D2CB1A86E4D9683A16A72618F9A6D |  | R22 | Non-TXV |  | 4.156% | 0.95844 | 7.987% | [5 empty] | Non-TXV | 4.156%
Diamond Springs | CA | 95619-9300 |  | 2012-07-16 | 2012-07-16 14:32 | 2012-07-16 14:50 | CARRIER - 48SD-030060311 | 96 | 11.2 | Yes | Yes | 23.8 | 21.5 | 2.3 | 82AFC3E423B2415FAE801EBDD3CCC67A |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Tracy | CA | 95376-4906 |  | 2012-06-21 | 2012-06-21 14:49 | 2012-06-21 15:15 | BDP - 561AJ042-A | 89 | 3.7 | Yes | Yes | 21.8 | 20.4 | 1.4 | ED2B5B58013649E689AF3FC3C0515E2D |  | R22 | TXV |  | 4.157% | 0.95843 | 7.989% | [5 empty] | TXV | 4.157%
Stockton | CA | 95206-1949 |  | 2012-06-08 | 2012-06-08 13:02 | 2012-06-08 13:20 | AMANA - PGD36C0702E | 110 | 9.6 | Yes | Yes | 18.1 | 20.9 | -2.8 | 5BDABEA9643444CA8A2DA6BEE3CAB6B5 |  | R22 | Non-TXV |  | 8.727% | 0.91273 | 16.77% | [5 empty] | Non-TXV | 8.727%
Grass Valley | CA | 95945-7538 |  | 2012-05-30 | 2012-05-30 11:54 | 2012-05-30 12:15 | UNITARY PRODUCTS GROUP - BRCS0361BD | 63 | 15.7 | Yes | Yes | 23.2 | 19.9 | 3.3 | 1A306C7FC541472194469DAF63A98DBD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 24.92% | 0.75079 | 47.89% | [5 empty] | Non-TXV | 24.92%
Stockton | CA | 95210-1503 |  | 2012-05-09 | 2012-05-09 10:02 | 2012-05-09 10:21 | RUUD - RRKA-A024JK06X | 50 | 1.5 | Yes | Yes | 19.5 | 19.9 | -0.4 | 3C9697C0F86D4FB6BC0A1EEE95088ACF | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-7410 |  | 2012-05-22 | 2012-05-22 12:24 | 2012-05-22 12:47 | GIBSON - JS5BD030K | 134 | 14.7 | Yes | Yes | 26.4 | 22.5 | 3.9 | EF48E4859C4942E882C8E1F24BDB109C |  | R22 | Non-TXV |  | 10.97% | 0.8903 | 21.08% | [5 empty] | Non-TXV | 10.97%
Fresno | CA | 93727-3007 |  | 2012-05-07 | 2012-05-07 17:33 | 2012-05-07 18:02 | OTHER - NAC036AKC3 | 76 | 3.1 | Yes | Yes | 19.7 | 19.9 | -0.2 | 74B9377D93264F82ADF6F05AB34F30F0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.079% | 0.95921 | 7.839% | [5 empty] | Non-TXV | 4.079%
Stockton | CA | 95205-7891 |  | 2012-05-14 | 2012-05-14 14:35 | 2012-05-14 14:55 | BRYANT - 561CJ024-E | 55 | 2.8 | Yes | Yes | 18.4 | 18.3 | 0.1 | 166B3CF2839E4D5AACFE6C5F06527BA4 | OK: Verified Refrigerant Charge | R22 | Non-TXV |  | 5.091% | 0.94909 | 9.784% | [5 empty] | Non-TXV | 5.091%
Stockton | CA | 95205-8403 |  | 2012-07-12 | 2012-07-12 14:51 | 2012-07-12 15:12 | CARRIER - 38TH036300 | 84 | 7.5 | Yes | Yes | 19.8 | 19.9 | -0.1 | 913E8195D23B4301A1E38BFD735D7533 |  | R22 | Non-TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | Non-TXV | 8.929%
Grass Valley | CA | 95945-6646 |  | 2012-05-30 | 2012-05-30 14:04 | 2012-05-30 14:25 | COLEMAN - 2D24-611 | 61 | 2.1 | Yes | Yes | 20 | 19.5 | 0.5 | 94478472C85147C589A030BB9AB85BCD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.443% | 0.96557 | 6.616% | [5 empty] | Non-TXV | 3.443%
Stockton | CA | 95205-4941 |  | 2012-06-07 | 2012-06-07 15:28 | 2012-06-07 15:49 | RUUD - UAND-030JAZ | 88 | 5.6 | Yes | Yes | 16.2 | 18.8 | -2.6 | 42A1A828C8A1407CB1B0138F160AC494 |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Nevada City | CA | 95959-2428 |  | 2012-07-13 | 2012-07-13 12:01 | 2012-07-13 12:19 | PAYNE - PA10JA018-A | 62 | 12.7 | Yes | Yes | 19.9 | 22.6 | -2.7 | F046358BD46E4FE2BDE15350635222C3 |  | R22 | Non-TXV |  | 20.48% | 0.79516 | 39.37% | [5 empty] | Non-TXV | 20.48%
Los Banos | CA | 93635-4731 |  | 2012-05-17 | 2012-05-17 09:47 | 2012-05-17 10:12 | CARRIER - 585EJ030050 | 58 | 5.6 | Yes | Yes | 18.8 | 20.4 | -1.6 | 8AFB145B12A8438A8827D1E5AB21E65A |  | R22 | Non-TXV |  | 9.655% | 0.90345 | 18.56% | [5 empty] | Non-TXV | 9.655%
Paradise | CA | 95969-6034 |  | 2012-06-12 | 2012-06-12 13:57 | 2012-06-12 13:57 | DAY & NIGHT - 593CX036060AAA | 88 | 0 | Yes | Yes | 27.8 | 23.1 | 4.7 | 68035E1F33E244B3A0285359DA05774A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4871 |  | 2012-05-15 | 2012-05-15 11:24 | 2012-05-15 11:47 | LENNOX - HS9-311-6P | 78 | 2.3 | Yes | Yes | 17.8 | 20.2 | -2.4 | E9E859862D9F4504B42AED43159F0C81 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Marysville | CA | 95901-4928 |  | 2012-05-31 | 2012-05-31 10:38 | 2012-05-31 10:59 | BRYANT - 561CJ030-C | 71 | 9.7 | Yes | Yes | 20 | 20.8 | -0.8 | 6E80EE69A6914DEB8EF1D05D797322C2 |  | R22 | Non-TXV |  | 13.66% | 0.86338 | 26.26% | [5 empty] | Non-TXV | 13.66%
Stockton | CA | 95210-1503 |  | 2012-05-09 | 2012-05-09 10:36 | 2012-05-09 10:57 | RUUD - RRNL-B024JK06X | 79 | -4.6 | Yes | Yes | 18 | 18.1 | -0.1 | 593E2CD3E427476283CB9DC6FADB7D16 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Yuba City | CA | 95993-5235 |  | 2012-05-21 | 2012-05-21 11:14 | 2012-05-21 11:36 | PAYNE - PA134NR024-K | 65 | 12.5 | Yes | Yes | 17.4 | 19.7 | -2.3 | 5AB104C1167A4A6F92C9C18178C50256 |  | R22 | Non-TXV |  | 19.23% | 0.80769 | 36.96% | [5 empty] | Non-TXV | 19.23%
Tracy | CA | 95376-9011 |  | 2012-06-21 | 2012-06-21 10:11 | 2012-06-21 10:32 | BRYANT - 574DNWA36060NA-- | 100 | 4.7 | Yes | Yes | 19.2 | 19.6 | -0.4 | 69C419B300544F79811357B5EB89D7DA |  | R410A | TXV |  | 4.7% | 0.953 | 9.032% | [5 empty] | TXV | 4.7%
Chico | CA | 95926-2657 |  | 2012-05-08 | 2012-05-08 11:19 | 2012-05-08 11:48 | BPN - 588ANW024060ADBD | 38 | 4.4 | Yes | Yes | 26.3 | 24.7 | 1.6 | C0781BA17A6D4477A353ABD8385DC4CD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 11.58% | 0.88421 | 22.25% | [5 empty] | Non-TXV | 11.58%
Stockton | CA | 95204-5226 |  | 2012-06-06 | 2012-06-06 16:23 | 2012-06-06 16:40 | TRANE - BTD736A100A0 | 88 | 4 | Yes | Yes | 18.9 | 19.9 | -1 | B43880CD889F4CA6AD168147A2186BAA |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93706-4259 |  | 2012-06-13 | 2012-06-13 14:15 | 2012-06-13 14:38 | GOODMAN - GPEJ30-1B | 121 | 2.6 | Yes | Yes | 24.1 | 20.7 | 3.4 | 9CB4E4E4B0944375BADDC591E8215D13 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.149% | 0.97851 | 4.129% | [5 empty] | Non-TXV | 2.149%
Fresno | CA | 93706-4259 |  | 2012-07-09 | 2012-07-09 14:16 | 2012-07-09 14:35 | GOODMAN - CPL030-1B | 127 | 18 | Yes | Yes | 17.1 | 20.1 | -3 | B970C086CB0A470999C8CC4A403EF6B6 |  | R22 | Non-TXV |  | 14.17% | 0.85827 | 27.24% | [5 empty] | Non-TXV | 14.17%
Stockton | CA | 95207-3634 |  | 2012-06-07 | 2012-06-07 10:38 | 2012-06-07 10:59 | GOODMAN - GPG1348O9OM41AB | 125 | 6 | Yes | Yes | 22.3 | 20.2 | 2.1 | BC2F1D8116254420AF63C396764AAAE3 |  | R410A | TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | TXV | 4.8%
Merced | CA | 95340-0715 |  | 2012-06-15 | 2012-06-15 14:34 | 2012-06-16 01:19 | RUUD - UHAE-048JAS | 114 | 4.8 | Yes | Yes | 24.5 | 20.4 | 4.1 | 20CBA34B19694CAABCC8EC717773DDD6 |  | R22 | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Stockton | CA | 95205-5640 |  | 2012-05-16 | 2012-05-16 12:40 | 2012-05-16 12:40 | COMFORT AIRE - PGD324060K001C1 | 72 | 0 | Yes | Yes | 19.5 | 18.2 | 1.3 | 4BC932BFC9BE4BCDAB122B3161A1F712 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1128 |  | 2012-05-29 | 2012-05-29 10:10 | 2012-05-29 10:36 | YORK - NA | 91 | 2.7 | Yes | Yes | 18.7 | 19.9 | -1.2 | DB68733103284DCDAC16EE50DDE6DB42 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.967% | 0.97033 | 5.702% | [5 empty] | Non-TXV | 2.967%
Yuba City | CA | 95991-4319 |  | 2012-06-11 | 2012-06-11 14:40 | 2012-06-11 14:57 | OTHER - FS3BA-030KA- | 68 | -6.4 | Yes | Yes | 20 | 23 | -3 | 393996546B964D10A60078C4E11F64DE |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Oroville | CA | 95966-3658 |  | 2012-06-06 | 2012-06-06 12:43 | 2012-06-06 12:58 | CARRIER - 38TXA24-341 | 84 | 3.6 | Yes | Yes | 23.2 | 19.7 | 3.5 | 869BE6C706A340BDBF775FECDED836D6 |  | R410A | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95207-7522 |  | 2012-06-12 | 2012-06-12 11:01 | 2012-06-12 11:23 | HEIL - GPCM036K060F | 68 | 9.7 | Yes | Yes | 23 | 21.1 | 2 | FFB3C148B452494A86C6421AE63FFDC5 |  | R22 | Non-TXV |  | 14.26% | 0.85735 | 27.41% | [5 empty] | Non-TXV | 14.26%
Merced | CA | 95340-3890 |  | 2012-05-14 | 2012-05-14 13:06 | 2012-05-14 13:25 | RHEEM - RRGG05N18JKR | 39 | 6.9 | Yes | Yes | 21.5 | 21.4 | 0.1 | 0F27D3C8F9894EBAA117568520ADF2E4 |  | R22 | Non-TXV |  | 17.69% | 0.82308 | 34% | [5 empty] | Non-TXV | 17.69%
Yuba City | CA | 95991-2921 |  | 2012-06-11 | 2012-06-11 14:42 | 2012-06-11 14:42 | CARRIER - 48HJE005---331-- | 128 | 0 | Yes | Yes | 23.4 | 21.3 | 2.1 | 9A6E740937464E5DACF4B841B91AEB3D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-5534 |  | 2012-05-11 | 2012-05-11 11:11 | 2012-05-11 11:34 | RHEEM - RRNL-B024JK06X | 77 | 2.9 | Yes | Yes | 21.7 | 20.6 | 1.1 | B60BAF93A83F4580A35B1341016B6295 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 3.766% | 0.96234 | 7.238% | [5 empty] | Non-TXV | 3.766%
Merced | CA | 95340-3890 |  | 2012-05-07 | 2012-05-07 14:10 | 2012-05-07 14:10 | RHEEM - RRGG05N18JKR | 85 | 0 | Yes | Yes | 26.1 | 23.7 | 2.4 | 320AC44CB94C418894E90A1E4DE81C7D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-5423 |  | 2012-07-12 | 2012-07-12 15:00 | 2012-07-12 15:18 | YORK - H4DH018S06A | 78 | 3 | Yes | Yes | 22 | 20.7 | 1.3 | 0EFBDF186749480AB0C6F4CFEC772DC3 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Fresno | CA | 93711-1471 |  | 2012-08-09 | 2012-08-09 16:04 | 2012-08-09 16:28 | CARRIER - 48GX-036009301AD | 82 | 3.8 | Yes | Yes | 18.4 | 20.4 | -2 | 27545DCF55F246DCA4824D49A9EC5CFA |  | R22 | Non-TXV |  | 4.634% | 0.95366 | 8.906% | [5 empty] | Non-TXV | 4.634%
Yuba City | CA | 95993-6457 |  | 2012-06-06 | 2012-06-06 13:51 | 2012-06-06 13:51 | PAYNE - PY1PNB036060ABAA | 70 | 0 | Yes | Yes | 20 | 20.1 | -0.1 | 6643B08C8F114433941B6DA3D5F9B2BB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-8708 |  | 2012-07-12 | 2012-07-12 13:27 | 2012-07-12 13:44 | NORDYNE - JS3BA-024KA | 64 | 1.9 | Yes | Yes | 20.8 | 23.7 | -2.9 | 716C7014DF17431697156E5FE31BC988 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Merced | CA | 95348-8708 |  | 2012-07-12 | 2012-07-12 13:44 | 2012-07-12 14:02 | NORDYNE - JS3BA-024KA | 64 | 2 | Yes | Yes | 19.4 | 21.8 | -2.4 | E0214B0A12DA4814A7F795E791A18557 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Cameron Park | CA | 95682-8936 |  | 2012-06-13 | 2012-06-13 16:25 | 2012-06-13 16:25 | TAPPAN - CRMH-24-44-T | 90 | 0 | Yes | Yes | 16.9 | 19.7 | -2.8 | 3F66E524AE1D43E3867BCCFA7841040B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-5423 |  | 2012-07-12 | 2012-07-12 10:04 | 2012-07-12 10:22 | YORK - H4DH018S06A | 78 | -4.6 | Yes | Yes | 15.6 | 18.2 | -2.6 | 4E587D9405D44BC2BF3268FC50E020F3 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Paradise | CA | 95969-2539 |  | 2012-05-10 | 2012-05-10 10:29 | 2012-05-10 10:29 | UL - BRCSO241BD | 59 | 0 | Yes | Yes | 21 | 22.5 | -1.5 | 5828BF9DD6E2422A9234A9000B689E0C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Atascadero | CA | 93422-4125 |  | 2012-07-11 | 2012-07-11 08:32 | 2012-07-11 08:49 | HEIL - PGC024K060E | 58 | -3.4 | Yes | Yes | 18.7 | 20.3 | -1.6 | 348CE93DFB444A16BA668C099E14D153 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Dos Palos | CA | 93620-2417 |  | 2012-05-15 | 2012-05-15 13:04 | 2012-05-15 13:21 | GOODMAN - CK24-18 | 71 | -5 | Yes | Yes | 18.3 | 19.9 | -1.6 | 2E208B9874C548DB8A50114842FA4255 |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Merced | CA | 95348-3038 |  | 2012-05-31 | 2012-05-31 11:26 | 2012-05-31 11:45 | BDP - 565BJ018 | 85 | 2.5 | Yes | Yes | 16.8 | 19.5 | -2.7 | 5FEC2223E31B442F93D97928768B84B4 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Paso Robles | CA | 93446-5422 |  | 2012-07-12 | 2012-07-12 16:05 | 2012-07-12 16:24 | YORK - H4DH018S06A | 78 | 3.2 | Yes | Yes | 17.1 | 18.7 | -1.6 | 5DD5A6A61EE54325BC2AA209F5498958 |  | R22 | Non-TXV |  | 4.103% | 0.95897 | 7.884% | [5 empty] | Non-TXV | 4.103%
Manteca | CA | 95337-8577 |  | 2012-05-14 | 2012-05-14 15:47 | 2012-05-14 16:17 | TRANE - 2TTB0060A1000AA | 126 | 9 | Yes | Yes | 24.9 | 20.4 | 4.5 | E2A57427A7944BB0968153D46376F4A8 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Chico | CA | 95973-9179 |  | 2012-05-07 | 2012-05-07 20:09 | 2012-05-07 20:33 | LENNX - 12ACB36-5 | 103 | 3.5 | Yes | Yes | 20 | 17.9 | 2.1 | 5CCA5889D6704205AC1181D5D670E6C5 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.398% | 0.96602 | 6.53% | [5 empty] | Non-TXV | 3.398%
Stockton | CA | 95206-2848 |  | 2012-05-11 | 2012-05-11 10:14 | 2012-05-11 10:32 | RHEEM - RRNL-B030JK06X | 78 | -3 | Yes | Yes | 21.7 | 20.2 | 1.5 | D55CEAF731154D789D69423D045CD11A | OK: Verified Refrigerant Charge | R410A | TXV |  | -3.846% | 1.0385 | 1.077% |  |  |  |  | TXV |  |  | -3.846%
Escalon | CA | 95320-1649 |  | 2012-06-13 | 2012-06-13 09:50 | 2012-06-13 10:18 | HEIL - CA5518VKD3 | 59 | 1.7 | Yes | Yes | 18 | 20.9 | -2.9 | 608B5B0141F34878A0E1482C5E2062F8 |  | R22 | Non-TXV |  | 2.881% | 0.97119 | 5.537% | [5 empty] | Non-TXV | 2.881%
Stockton | CA | 95209-2750 |  | 2012-05-16 | 2012-05-16 13:27 | 2012-05-16 13:47 | DAY NIGHT - 585A024055YACR | 51 | 12 | Yes | Yes | 17.5 | 19.9 | -2.4 | 1E0F50754C7246AB8C7BF1257FCB798B |  | R22 | Non-TXV |  | 23.53% | 0.76471 | 45.22% | [5 empty] | Non-TXV | 23.53%
Stockton | CA | 95204-2215 |  | 2012-05-07 | 2012-05-07 13:08 | 2012-05-07 13:27 | CARRIER - 480L 003 | 49 | 2 | Yes | Yes | 4 | 12.2 | -8.2 | 5A99DADDA886404796E97AAB607EDB67 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.082% | 0.95918 | 7.844% | [5 empty] | Non-TXV | 4.082%
Fresno | CA | 93711-6521 |  | 2012-07-09 | 2012-07-09 13:11 | 2012-07-09 13:28 | YORK - D1NA030N03606C | 76 | 2.3 | Yes | Yes | 20 | 20.7 | -0.7 | FCDE639928CB41C4A0DF83DA9E8E1BEE |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Escalon | CA | 95320-9760 |  | 2012-06-13 | 2012-06-13 10:56 | 2012-06-13 11:17 | PAYNE - PA10JA036-C | 73 | 2.4 | Yes | Yes | 19.9 | 19.9 | 0 | 0633526AEC7348A9AEAA8B3F9C58C257 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Auburn | CA | 95603-3739 |  | 2012-05-29 | 2012-05-29 11:52 | 2012-05-29 12:09 | OTHER - 7B0023B100A1 | 54 | 10.4 | Yes | Yes | 23 | 19.7 | 3.3 | 2238A1920DA8427F9B0C3A902D3D3358 |  | R22 | Non-TXV |  | 19.26% | 0.80741 | 37.01% | [5 empty] | Non-TXV | 19.26%
Merced | CA | 95341-6916 |  | 2012-05-09 | 2012-05-09 12:53 | 2012-05-09 13:11 | CARRIER - 48GX036060301 | 82 | 4 | Yes | Yes | 22.1 | 20.4 | 1.7 | C5ED963FECA1482498382394C9AB6021 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | Non-TXV | 4.878%
Placerville | CA | 95667-5320 |  | 2012-07-23 | 2012-07-23 10:33 | 2012-07-23 10:33 | AMERICAN STANDARD - 2A6H3060A1000AA | 152 | 0 | Yes | Yes | 20.5 | 19.3 | 1.2 | EB0BF788DB9B470B9CB6C5A0BA560A7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-5049 |  | 2012-05-16 | 2012-05-16 10:52 | 2012-05-16 11:09 | BRYANT - 561CJX024-D | 55 | 3.1 | Yes | Yes | 19.1 | 14.1 | 5 | 6CDBB5E3B31A4F2E91F98A4A5E43A23F | OK: Verified Refrigerant Charge | R22 | TXV |  | 5.636% | 0.94364 | 10.83% | [5 empty] | TXV | 5.636%
Fresno | CA | 93711-1342 |  | 2012-08-09 | 2012-08-09 16:51 | 2012-08-09 17:10 | YORK - 38TKR043200 | 80 | 3.5 | Yes | Yes | 18.9 | 19.8 | -0.9 | 44272F99DAA64166B7BF5DD25C8F78FF |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Paradise | CA | 95969-6055 |  | 2012-05-14 | 2012-05-14 11:20 | 2012-05-14 11:20 | CARRIER - 48GP-060090311 | 139 | 0 | Yes | Yes | 18.2 | 20.4 | -2.2 | 212CAB79134346C2A30487FFA7E4B4DF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-5422 |  | 2012-07-13 | 2012-07-13 12:21 | 2012-07-13 12:41 | YORK - H4DH018S06A | 78 | 3.2 | Yes | Yes | 20.1 | 19.2 | 0.9 | D14DABECD9824860B37F80074CC5ECA4 |  | R22 | Non-TXV |  | 4.103% | 0.95897 | 7.884% | [5 empty] | Non-TXV | 4.103%
Auburn | CA | 95603-3738 |  | 2012-05-10 | 2012-05-10 14:10 | 2012-05-10 14:28 | STANDARD - 7B0023B100A1 | 54 | 8.8 | Yes | Yes | 17 | 18.8 | -1.8 | 91CEAF345C8A4909A76A557917E3A005 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 16.3% | 0.83704 | 31.32% | [5 empty] | Non-TXV | 16.3%
Stockton | CA | 95219-4975 |  | 2012-06-11 | 2012-06-11 14:53 | 2012-06-11 15:15 | AMERICAN STANDARD - TTR060C100A1 | 147 | 15 | Yes | Yes | 19.7 | 18.8 | 0.9 | 6DC1FE36C6EC4E228C52DD53BC79FFDB |  | R22 | Non-TXV |  | 10.2% | 0.89796 | 19.61% | [5 empty] | Non-TXV | 10.2%
Stockton | CA | 95207-5930 |  | 2012-05-31 | 2012-05-31 09:40 | 2012-05-31 09:58 | WEATHER KING - 10AJB36A01 | 80 | 9.8 | Yes | Yes | 21.3 | 20.4 | 0.9 | 71461476D5D344C8986D5E33413B9673 |  | R22 | Non-TXV |  | 12.25% | 0.8775 | 23.54% | [5 empty] | Non-TXV | 12.25%
Auburn | CA | 95603-3739 |  | 2012-05-29 | 2012-05-29 11:15 | 2012-05-29 11:35 | OTHER - 7B0023B100A1 | 54 | 10.4 | Yes | Yes | 21 | 19.9 | 1.1 | F398851D3E3047BCA2C1DA04083768E1 |  | R22 | Non-TXV |  | 19.26% | 0.80741 | 37.01% | [5 empty] | Non-TXV | 19.26%
Los Banos | CA | 93635-7400 |  | 2012-05-18 | 2012-05-18 12:56 | 2012-05-18 13:28 | GIBSON - JS3BC-036KA | 82 | 15 | Yes | Yes | 20.6 | 22.8 | -2.2 | A1D10A243AE3464EB06B6A23F10AA9C7 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.29% | 0.81707 | 35.15% | [5 empty] | Non-TXV | 18.29%
Auburn | CA | 95602-2601 |  | 2012-05-29 | 2012-05-29 16:47 | 2012-05-29 17:06 | RHEEM - UNK | 55 | -3.9 | Yes | Yes | 18 | 18.8 | -0.8 | 86B7BCE5D3AA426F9DC78D1CFD1CDAE5 |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Paso Robles | CA | 93446-5423 |  | 2012-07-12 | 2012-07-12 15:33 | 2012-07-12 15:54 | YORK - H4DH018S06A | 78 | 2.7 | Yes | Yes | 20.7 | 20.2 | 0.5 | 0F48946598EA4D89A55EA0043FCB2163 |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Fresno | CA | 93706-4260 |  | 2012-06-14 | 2012-06-14 10:22 | 2012-06-14 10:48 | GOODMAN - CPLJ30-1B | 123 | 3.6 | Yes | Yes | 22.7 | 17.6 | 5.1 | 4A761A448B2E46DCBA1669E08325E4FB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Fresno | CA | 93706-4260 |  | 2012-06-14 | 2012-06-14 10:57 | 2012-06-14 11:19 | GOODMAN - CPLJ30-1B | 123 | 10.1 | Yes | Yes | 22.7 | 19.7 | 3.1 | EACAD8BE2E424CF1A72FBBEF5FFE6850 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.211% | 0.91789 | 15.78% | [5 empty] | Non-TXV | 8.211%
Oakdale | CA | 95361-3445 |  | 2012-05-24 | 2012-05-24 15:11 | 2012-05-24 15:31 | BRYANT - 561CJ036-E | 70 | 9.1 | Yes | Yes | 20.7 | 21.9 | -1.2 | 051036F845624B239F9609AEF3C8A7FB |  | R22 | Non-TXV |  | 13% | 0.87 | 24.98% | [5 empty] | Non-TXV | 13%
Atwater | CA | 95301-0000 |  | 2012-05-08 | 2012-05-08 12:44 | 2012-05-08 13:02 | FRASER JOHNSTON - OJLA1A | 40 | 1.2 | Yes | Yes | 16.1 | 18.1 | -2 | 2C6BD657BAFD499192955E3005ACF2B5 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-8008 |  | 2012-05-17 | 2012-05-17 14:02 | 2012-05-17 14:20 | COLEMAN - D1NH030N05606C | 73 | 2.2 | Yes | Yes | 20.7 | 19.4 | 1.4 | D7277AAB087E44AA86FDCB9F32A35596 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Orosi | CA | 93647-1909 |  | 2012-05-09 | 2012-05-09 13:17 | 2012-05-09 13:47 | GOODMAN - GPG13360701A | 112 | 3.7 | Yes | Yes | 27 | 21.3 | 5.7 | AAEA80862D214115874010619CA2925E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Dos Palos | CA | 93620-2221 |  | 2012-05-15 | 2012-05-15 11:13 | 2012-05-15 11:13 | ARCOAIR - PGD336060K00C1 | 100 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | 6F55DF614A4D4D9483A3DCA2335E06E2 | OK: Verified Refrigerant Charge | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4515 |  | 2012-06-08 | 2012-06-08 14:15 | 2012-06-08 14:31 | GUARDIAN - GCGD18S21S1HA | 50 | 4.9 | Yes | Yes | 20.3 | 21.8 | -1.5 | ED7DDF6D84A64A7E9B250E680C90C192 |  | R22 | TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | TXV | 9.8%
Fresno | CA | 93706-4261 |  | 2012-07-05 | 2012-07-05 11:14 | 2012-07-05 11:32 | GOODMAN - CPLJ30-1B | 123 | 9 | Yes | Yes | 20.9 | 21 | -0.1 | 2823DDF3A36742E7BD5F520D12322CF0 |  | R22 | Non-TXV |  | 7.317% | 0.92683 | 14.06% | [5 empty] | Non-TXV | 7.317%
Manteca | CA | 95337-5251 |  | 2012-05-09 | 2012-05-09 13:28 | 2012-05-09 14:03 | YORK - D1NP024N05606A | 74 | 12.2 | Yes | Yes | 17.3 | 20.2 | -2.9 | BAFBA8601D724F058FC2A92BECE8FE57 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.49% | 0.83514 | 31.68% | [5 empty] | Non-TXV | 16.49%
Marysville | CA | 95901-7908 |  | 2012-06-15 | 2012-06-15 12:51 | 2012-06-15 13:20 | COLEMAN - BRCQ0361BD | 52 | 2 | Yes | Yes | 21 | 19.8 | 1.2 | 8C8B7D44FABF44C28ED018A2740B70C1 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Stockton | CA | 95206-2315 |  | 2012-05-08 | 2012-05-08 17:20 | 2012-05-08 17:50 | RHEEM - RRKA-A030JKO6X | 54 | -2.7 | Yes | Yes | 25 | 21.3 | 3.7 | 2D0ECCDFA9884E1A9742DFDA8EB459C9 | OK: Verified Refrigerant Charge | R22 | TXV |  | -5% | 1.05 | 1.4% |  |  |  |  | TXV |  |  | -5%
Stockton | CA | 95205-7715 |  | 2012-07-06 | 2012-07-06 12:57 | 2012-07-06 13:21 | GOODMAN - PGX048075 | 108 | 4.8 | Yes | Yes | 18.5 | 19.9 | -1.4 | 2EEE2EB630244CD4988CF2E405FA13AC |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Fresno | CA | 93706-4310 |  | 2012-06-13 | 2012-06-13 15:11 | 2012-06-13 15:40 | GOODMAN - PGB036100-1A | 87 | 3.2 | Yes | Yes | 20.5 | 20.7 | -0.2 | 5DE2586D0BCF462592E7C09D89C1A33C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.678% | 0.96322 | 7.069% | [5 empty] | Non-TXV | 3.678%
Fresno | CA | 93710-4850 |  | 2012-08-02 | 2012-08-02 14:04 | 2012-08-02 15:38 | DAY & NIGHT - 42DNR-108K | 88 | 4 | Yes | Yes | 18.5 | 20.1 | -1.6 | 776FE12C57B44AAFB8C3F166842CB62E |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Escalon | CA | 95320-1650 |  | 2012-06-28 | 2012-06-28 13:45 | 2012-06-28 14:14 | ICP - CA5518VKD3 | 59 | 5 | Yes | Yes | 20.2 | 21.2 | -1 | 6387B9B38C86453F87B83D9CA5980C7A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.475% | 0.91525 | 16.29% | [5 empty] | Non-TXV | 8.475%
Atwater | CA | 95301-4886 |  | 2012-05-15 | 2012-05-15 12:49 | 2012-05-15 13:19 | GOODMAN - BSC130421AC | 137 | 4.1 | Yes | Yes | 17.8 | 20.4 | -2.6 | B3A3DCE9E06D4DD2B6CB0CE7FAAE22DB | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.993% | 0.97007 | 5.751% | [5 empty] | Non-TXV | 2.993%
Marysville | CA | 95901-4607 |  | 2012-05-17 | 2012-05-17 14:38 | 2012-05-17 14:38 | CARRIER - 48SS-030060331-- | 56 | 0 | Yes | Yes | 25.2 | 20.4 | 4.8 | 807DFAF790C24A7CBAED47FD2702D814 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1433 |  | 2012-05-07 | 2012-05-07 15:11 | 2012-05-07 15:38 | ICP - PGN336060K01A1 | 130 | 4.9 | Yes | Yes | 27.9 | 21.9 | 6 | 55930FA96FF04F4D9B4BC2E1148DAF48 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.769% | 0.96231 | 7.244% | [5 empty] | Non-TXV | 3.769%
Fresno | CA | 93706-4260 |  | 2012-06-13 | 2012-06-13 14:40 | 2012-06-13 14:56 | GOODMAN - GPLJ30-1B | 123 | 14.6 | Yes | Yes | 25.6 | 20.7 | 4.9 | A60CA0E51AF743DBA721EE120D2101CE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.87% | 0.8813 | 22.81% | [5 empty] | Non-TXV | 11.87%
Oroville | CA | 95966-5419 |  | 2012-06-07 | 2012-06-07 10:54 | 2012-06-07 12:00 | RUUD - UAKB-036JAZ | 79 | 8.7 | Yes | Yes | 20.8 | 22.9 | -2.1 | CC1620D80D074777A1DB372FFC32A0F8 |  | R22 | Non-TXV |  | 11.01% | 0.88987 | 21.16% | [5 empty] | Non-TXV | 11.01%
Manteca | CA | 95337-5534 |  | 2012-05-21 | 2012-05-21 10:03 | 2012-05-21 10:03 | RHEEM - RRNL-B024JK06X | 78 | 0 | Yes | Yes | 20 | 19.7 | 0.3 | 87DCE83F0E864E639FABD66643A97ADB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Orosi | CA | 93647-1906 |  | 2012-05-09 | 2012-05-09 14:55 | 2012-05-09 15:16 | PAYNE - PY3PNA042060NA | 168 | 5.3 | Yes | Yes | 16.7 | 20.9 | -4.2 | 2ACDBD36A2A34F7DA8A89AA4E763511D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.155% | 0.96845 | 6.063% | [5 empty] | Non-TXV | 3.155%
Stockton | CA | 95209-2607 |  | 2012-05-17 | 2012-05-17 14:37 | 2012-05-17 14:55 | RHEEM - HC-100-36-21C | 49 | 8 | Yes | Yes | 18.9 | 19.9 | -1 | 33967A44DB9643958573D774CBA07C79 |  | R22 | Non-TXV |  | 16.33% | 0.83673 | 31.38% | [5 empty] | Non-TXV | 16.33%
Stockton | CA | 95206-4827 |  | 2012-05-24 | 2012-05-24 14:54 | 2012-05-24 15:15 | GOODMAN - CE30-1HB | 72 | 9.3 | Yes | Yes | 20.5 | 21 | -0.5 | 37CBC21836EF4A07A8DE0738E69030B7 |  | R22 | Non-TXV |  | 12.92% | 0.87083 | 24.82% | [5 empty] | Non-TXV | 12.92%
Fresno | CA | 93710-6411 |  | 2012-08-07 | 2012-08-07 15:42 | 2012-08-07 17:02 | GOODMAN - PGB042075 | 70 | 2.9 | Yes | Yes | 18.3 | 19.6 | -1.3 | 06F2E9A0AA3D49B08ED504AAFAAB2726 |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Fresno | CA | 93710-6411 |  | 2012-08-07 | 2012-08-07 17:04 | 2012-08-07 17:04 | GOODMAN - PGB042075 | 70 | 0 | Yes | Yes | 18.5 | 19.9 | -1.4 | 88C4D77CC19940838D8E2A10C633BB52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-1241 |  | 2012-05-21 | 2012-05-21 13:03 | 2012-05-21 13:22 | RHEEM - RRKA-AO24JK06X | 50 | 3.4 | Yes | Yes | 19.3 | 21.5 | -2.2 | C91A2683F0AC4192A6B66C72ADEF1E05 |  | R22 | TXV |  | 6.8% | 0.932 | 13.07% | [5 empty] | TXV | 6.8%
Fresno | CA | 93710-4323 |  | 2012-05-24 | 2012-05-24 13:41 | 2012-05-24 13:56 | RHEEM - RRKA-A03JK08X | 76 | 2.4 | Yes | Yes | 19.1 | 21.5 | -2.4 | 2F180BDCB27F4720A958EB26B1EA1599 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Los Banos | CA | 93635-3411 |  | 2012-05-14 | 2012-05-14 10:04 | 2012-05-14 10:40 | CARRIER - 38TH036300 | 90 | 4.3 | Yes | Yes | 26.3 | 20.3 | 6 | 4AB56D58452D4D50A62FA2A9361CDAEC |  | R22 | Non-TXV |  | 4.778% | 0.95222 | 9.182% | [5 empty] | Non-TXV | 4.778%
Fresno | CA | 93710-5228 |  | 2012-07-18 | 2012-07-18 09:12 | 2012-07-18 10:03 | OTHER - UNK | 56 | 2.3 | Yes | Yes | 18.8 | 21 | -2.2 | BA23D3B61DD0467B8EDB54B11829150C |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Corning | CA | 96021-2145 |  | 2012-05-18 | 2012-05-18 11:48 | 2012-05-18 12:13 | BRYANT - 574BNW036060NA | 149 | 4.8 | Yes | Yes | 17 | 19.3 | -2.3 | AABB0D3A50004C1C803541A9CF4C28E3 |  | R410A | Non-TXV |  | 3.221% | 0.96779 | 6.191% | [5 empty] | Non-TXV | 3.221%
Fresno | CA | 93710-5227 |  | 2012-05-24 | 2012-05-24 14:20 | 2012-05-24 14:39 | GOODMAN - UNK | 76 | 4.6 | Yes | Yes | 17.5 | 20.1 | -2.6 | C2D04FFC65A8404D915B00C5F113FE90 |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
Merced | CA | 95341-6714 |  | 2012-05-09 | 2012-05-09 10:00 | 2012-05-09 10:36 | NIGHT & DAY - UNK | 65 | 2.6 | Yes | Yes | 0.4 | 13.9 | -13.5 | 2AE98199EC47495E901A5C1C62364035 | Final Suction Temperature must be between 20°F and 80°F. Please check entries. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Tracy | CA | 95376-1346 |  | 2012-06-14 | 2012-06-14 12:39 | 2012-06-14 13:02 | RUUD - UAKA-048JAZ | 103 | 4.6 | Yes | Yes | 26.1 | 20.2 | 5.9 | 85BFF33AF6A3429EA052E246C283AE25 |  | R22 | TXV |  | 4.466% | 0.95534 | 8.583% | [5 empty] | TXV | 4.466%
Williams | CA | 95987-9012 |  | 2012-08-09 | 2012-08-09 15:31 | 2012-08-09 15:31 | NORDYNE - JS3BA-018KA | 63 | 0 | Yes | Yes | 7.8 | 21 | -13.2 | 01E3E97102D7470FBCEA01F70145613E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-5027 |  | 2012-05-16 | 2012-05-16 11:24 | 2012-05-16 11:41 | GOODMAN - PGB030075-1 | 54 | 4.3 | Yes | Yes | 19.9 | 20.9 | -1 | CDC93CDC99864687B239A2CEB53E26B9 |  | R22 | Non-TXV |  | 7.963% | 0.92037 | 15.3% | [5 empty] | Non-TXV | 7.963%
Stockton | CA | 95207-5931 |  | 2012-06-14 | 2012-06-14 11:19 | 2012-06-14 11:36 | LENNOX - 10ACC-036-230-04 | 74 | 4.5 | Yes | Yes | 21 | 18.5 | 2.5 | 9BB9E451EC22438B8CC4D0BB244ACA49 |  | R22 | TXV |  | 6.081% | 0.93919 | 11.69% | [5 empty] | TXV | 6.081%
Los Banos | CA | 93635-4506 |  | 2012-05-24 | 2012-05-24 13:31 | 2012-05-24 13:56 | DAY & NIGHT - UNK | 80 | 4.8 | Yes | Yes | 19.9 | 19.2 | 0.7 | 5268A54C730B4FD4B2D87D705D204F3B |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Chowchilla | CA | 93610-3343 |  | 2012-06-14 | 2012-06-14 11:49 | 2012-06-14 12:12 | AMERICAN STANDARD - 2A7A5036A1000AA | 137 | 4 | Yes | Yes | 19.5 | 17.5 | 2.1 | F3B40FC37BBA4D4DB21B6C5F492D7E78 |  | R22 | Non-TXV |  | 2.92% | 0.9708 | 5.611% | [5 empty] | Non-TXV | 2.92%
Riverbank | CA | 95367-2168 |  | 2012-06-28 | 2012-06-28 11:10 | 2012-06-28 11:33 | PAYNE - 591ANX048000ACAA | 128 | 5.8 | Yes | Yes | 19.2 | 21 | -1.8 | 3859BCFE6AE44D04BD62B3C098A7F0A3 |  | R22 | Non-TXV |  | 4.531% | 0.95469 | 8.708% | [5 empty] | Non-TXV | 4.531%
Stockton | CA | 95204-4526 |  | 2012-05-09 | 2012-05-09 11:07 | 2012-05-09 11:30 | YORK - D1NP030N05606A | 73 | 2.6 | Yes | Yes | 13.3 | 16.1 | -2.8 | A3434A2BAE364C83936EF88A31E42C25 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.562% | 0.96438 | 6.845% | [5 empty] | Non-TXV | 3.562%
Escalon | CA | 95320-0000 |  | 2012-06-13 | 2012-06-13 11:36 | 2012-06-13 11:57 | RUUD - UNK | 54 | 1.7 | Yes | Yes | 17.9 | 19 | -1.1 | 098581174B4444478CA886748279DF27 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Planada | CA | 95365-0000 |  | 2012-05-22 | 2012-05-22 13:42 | 2012-05-22 14:03 | RHEEM - RRNA-C060JK10X | 145 | 4.4 | Yes | Yes | 24.8 | 19.9 | 4.9 | CCF39B45295440AA837118D67EC8EE43 |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.832% | [5 empty] | Non-TXV | 3.034%
Stockton | CA | 95206-3881 |  | 2012-05-24 | 2012-05-24 11:26 | 2012-05-24 11:43 | CARRIER - 24ABA336A300 | 83 | 5.5 | Yes | Yes | 18.9 | 21 | -2.1 | 08743995819D492BB9FE8ED7EF5DB157 |  | R410A | TXV |  | 6.627% | 0.93373 | 12.73% | [5 empty] | TXV | 6.627%
Stockton | CA | 95219-4567 |  | 2012-06-15 | 2012-06-15 11:32 | 2012-06-15 11:57 | RUUD - UNK | 84 | 8.6 | Yes | Yes | 17.2 | 19.3 | -2.1 | BD483005A95A4AD89D94E0E01E445D58 |  | R22 | Non-TXV |  | 10.24% | 0.89762 | 19.68% | [5 empty] | Non-TXV | 10.24%
Newman | CA | 95360-9659 |  | 2012-05-29 | 2012-05-29 13:20 | 2012-05-29 13:49 | BRYANT - 563CN042-E | 137 | 4.1 | Yes | Yes | 20 | 21.5 | -1.5 | 308925D7856E42DF99393A04714C5308 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.993% | 0.97007 | 5.751% | [5 empty] | Non-TXV | 2.993%
Merced | CA | 95341-5765 |  | 2012-07-05 | 2012-07-05 10:40 | 2012-07-05 10:59 | ARCOAIRE - GPCM24K060D | 54 | -3.2 | Yes | Yes | 17.3 | 19.9 | -2.6 | 8677D6AD9A7F44A783F2172CBEC107F5 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Madera | CA | 93637-5677 |  | 2012-05-18 | 2012-05-18 13:04 | 2012-05-18 13:42 | DAY & NIGHT - 561AJ036-D | 75 | 2.8 | Yes | Yes | 21 | 19.1 | 2 | 22C9305609EA4153B65558390ABB9D78 | OK: Verified Refrigerant Charge | R22 | TXV |  | 3.733% | 0.96267 | 7.175% | [5 empty] | TXV | 3.733%
Merced | CA | 95341-7023 |  | 2012-05-10 | 2012-05-10 10:30 | 2012-05-10 10:56 | GOODMAN - CLJ361A | 109 | 3.5 | Yes | Yes | 19.5 | 20.3 | -0.8 | B7207678A38343218EF4D4CBAB667804 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.211% | 0.96789 | 6.171% | [5 empty] | Non-TXV | 3.211%
Orosi | CA | 93647-1920 |  | 2012-05-29 | 2012-05-29 13:02 | 2012-05-29 13:19 | UNITARY PRODUCTS GROUP - ERCS0361BBB | 96 | 2.8 | Yes | Yes | 23.9 | 20.6 | 3.4 | 0EA5713D4F4D48B9B6A31CF26B430E6E |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Red Bluff | CA | 96080-3030 |  | 2012-05-23 | 2012-05-23 13:15 | 2012-05-23 14:01 | LENNOX - GCS20RV-411-75-1P | 70 | 5 | Yes | Yes | 22.5 | 22.8 | -0.3 | 087CC11C8313427695A0F1D916B06240 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Madera | CA | 93637-4602 |  | 2012-05-18 | 2012-05-18 10:52 | 2012-05-18 11:09 | YORK - D1NP030N05606A | 73 | 2.1 | Yes | Yes | 23.8 | 19.9 | 3.9 | DA5DBE0725CA4018AACA5D7C68A4C23E |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Stockton | CA | 95206-4698 |  | 2012-05-24 | 2012-05-24 12:49 | 2012-05-24 13:07 | GOODMAN - CLJ60-1 | 141 | 10.3 | Yes | Yes | 17.6 | 18.6 | -1 | 60030A5259CD40D48FB0C46F7F0342DA |  | R22 | Non-TXV |  | 7.305% | 0.92695 | 14.04% | [5 empty] | Non-TXV | 7.305%
Clovis | CA | 93612-2545 |  | 2012-08-13 | 2012-08-13 16:45 | 2012-08-13 17:03 | OTHER - P69044-1C | 63 | 1.9 | Yes | Yes | 18.5 | 19.9 | -1.4 | 1CCD60EB3E134757BD4B4304871BDF09 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Fresno | CA | 93727-6931 |  | 2012-05-21 | 2012-05-21 13:58 | 2012-05-21 14:16 | THERMAL ZONE - TZAA-324-2A | 77 | 2.3 | Yes | Yes | 24.4 | 21 | 3.4 | F8657ED1327947969A8CFC93BAFC4172 |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Merced | CA | 95348-9440 |  | 2012-05-14 | 2012-05-14 13:57 | 2012-05-14 15:18 | BRYANT - 563CN048-H | 132 | 3.9 | Yes | Yes | 20.3 | 20 | 0.3 | 7F20DB703C9444CDA3381E5AE057114B |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Los Banos | CA | 93635-9475 |  | 2012-05-18 | 2012-05-18 14:45 | 2012-05-18 15:20 | BRYANT - 561CJ042-E | 80 | 5.6 | Yes | Yes | 22 | 22 | 0 | D91F80B0EA5D444E976F3A828B83A7F0 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Stockton | CA | 95205-5619 |  | 2012-05-29 | 2012-05-29 17:43 | 2012-05-29 18:01 | RHEEM - UNK | 74 | 3.8 | Yes | Yes | 21.5 | 20.4 | 1.1 | 491B48910A044BF0B5681A931B8AC7CA |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Penn Valley | CA | 95946-9530 |  | 2012-07-25 | 2012-07-25 13:33 | 2012-07-25 13:52 | GOODMAN - CKL30-1L | 74 | 2.4 | Yes | Yes | 22.9 | 18.7 | 4.2 | 110259973E784558A4598878AEC319B2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Stockton | CA | 95215-5912 |  | 2012-06-21 | 2012-06-21 11:19 | 2012-06-21 11:46 | HEIL - GPCM036K060D | 68 | 2.8 | Yes | Yes | 21 | 19.9 | 1.1 | 986730D843D94EB5A5C9C10E67783A7A |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Corning | CA | 96021-9647 |  | 2012-05-18 | 2012-05-18 10:58 | 2012-05-18 10:58 | AMANDA - RHF48C2C | 150 | 0 | Yes | Yes | 20.3 | 21.8 | -1.5 | 077F7B1E8D8842DB9283FFE83E423EB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-2737 |  | 2012-05-18 | 2012-05-18 15:03 | 2012-05-18 15:36 | RUUD - UAND-036JAZ | 117 | 0 | Yes | Yes | 18.3 | 19.8 | -1.5 | CDA92135614C41BF807E187BD8CCE240 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-0000 |  | 2012-06-08 | 2012-06-08 11:07 | 2012-06-08 11:49 | COLEMAN - 9636F801 | 90 | 5.1 | Yes | Yes | 23.2 | 22.8 | 0.4 | B2044631C90E4991A0201C2789288127 |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Paso Robles | CA | 93446-5423 |  | 2012-07-13 | 2012-07-13 10:01 | 2012-07-13 10:20 | YORK - H4DH018S06A | 78 | 2.6 | Yes | Yes | 19 | 18.7 | 0.3 | EC975145B564428681F849350EB0112F |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93722-4225 |  | 2012-05-29 | 2012-05-29 16:20 | 2012-05-29 16:38 | ICP - PGC036K060B | 71 | 2.1 | Yes | Yes | 22.7 | 19.3 | 3.4 | 995AEDA11A4746719FCD756CF90758BF |  | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Merced | CA | 95348-3037 |  | 2012-06-06 | 2012-06-06 09:28 | 2012-06-06 09:45 | BARD - 565JD1B18 | 58 | 2 | Yes | Yes | 19.6 | 20.9 | -1.3 | CFB60F5EC9934B37985F6453A9AF95A5 |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Stockton | CA | 95210-1824 |  | 2012-06-06 | 2012-06-06 11:08 | 2012-06-06 11:25 | RUUD - UAKA-042JAZ | 79 | -5.6 | Yes | Yes | 21.6 | 19.5 | 2.1 | 280E515CA9CE44549772671D74220FA9 |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Merced | CA | 95341-5466 |  | 2012-05-16 | 2012-05-16 10:35 | 2012-05-16 11:05 | RHEEM - 13AJN36A01 | 91 | 6.6 | Yes | Yes | 17.6 | 20.4 | -2.8 | 6B5E0267FD944D3D85E238BFB77A17B8 |  | R22 | Non-TXV |  | 7.253% | 0.92747 | 13.94% | [5 empty] | Non-TXV | 7.253%
Yuba City | CA | 95991-4311 |  | 2012-06-11 | 2012-06-11 12:19 | 2012-06-11 12:39 | OTHER - 561CJO36-E | 70 | 2.6 | Yes | Yes | 20 | 22 | -2 | F578AF439D654BD886E0B4CDE87A3920 |  | R22 | Non-TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | Non-TXV | 3.714%
Merced | CA | 95348-3031 |  | 2012-05-31 | 2012-05-31 12:15 | 2012-05-31 12:15 | BDP - 565BJ018 | 50 | 0 | Yes | Yes | 2.4 | 19.8 | -17.4 | C6EF9BD089B444409A64EE9259B1E9E0 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-9217 |  | 2012-05-18 | 2012-05-18 16:10 | 2012-05-18 16:33 | GIBSON - JS3BC-042KA | 102 | -6 | Yes | Yes | 24.5 | 20.7 | 3.8 | 46CDB36EBAD547228B7884FA4C54F035 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93727-4846 |  | 2012-06-08 | 2012-06-08 12:57 | 2012-06-08 13:22 | RHEEM - RRKA-A0360JK06E | 55 | 1.9 | Yes | Yes | 15.9 | 18.9 | -3 | 8344579B46654E798C5E2957AD349CD6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Riverbank | CA | 95367-3315 |  | 2012-06-12 | 2012-06-12 15:09 | 2012-06-12 15:31 | BRYANT - 598AN036-B | 195 | 8.7 | Yes | Yes | 23 | 19.5 | 3.5 | EA8F27C84AC04FEDBA3EFF7D6FA5E1D2 |  | R22 | TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | TXV | 4.462%
Sanger | CA | 93657-3121 |  | 2012-06-08 | 2012-06-08 16:01 | 2012-06-08 16:29 | YORK - D3NP024N03606NXB | 100 | 4 | Yes | Yes | 17.8 | 20.7 | -2.9 | 68D9F070789D48DB8B5C811EC7D8288B |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Sanger | CA | 93657-4215 |  | 2012-05-22 | 2012-05-22 11:25 | 2012-05-22 11:46 | ICP - PGAA4201K3 | 82 | 3 | Yes | Yes | 19.6 | 19.5 | 0.2 | 6A253DEB3E1440A4BD5D6E7A85428E9F |  | R22 | Non-TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | Non-TXV | 3.659%
Sanger | CA | 93657-4212 |  | 2012-08-09 | 2012-08-09 14:02 | 2012-08-09 14:21 | TEMPSTAR - PGAA30C1K4 | 79 | 2.7 | Yes | Yes | 15.4 | 15.8 | -0.3 | 1A6B4FD7A8A04471A8242730EF0A0E91 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Jackson | CA | 95642-2401 |  | 2012-07-20 | 2012-07-20 10:37 | 2012-07-20 10:37 | COLEMAN - BPGM0300701AA | 72 | 0 | Yes | Yes | 19.9 | 19.3 | 0.6 | 6314FF9C525945E0BB36E392A975CCE9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1204 |  | 2012-05-30 | 2012-05-30 12:06 | 2012-05-30 12:24 | YORK - DBYP-F030N070A | 73 | 3.2 | Yes | Yes | 18.6 | 20.7 | -2.1 | C63F9CCBB3EE4E3D82EC14E21C67AE00 |  | R22 | Non-TXV |  | 4.384% | 0.95616 | 8.424% | [5 empty] | Non-TXV | 4.384%
Merced | CA | 95341-5951 |  | 2012-06-14 | 2012-06-14 09:24 | 2012-06-14 09:44 | RHEEM - UNK | 75 | 2.3 | Yes | Yes | 23 | 20.2 | 2.8 | 107AB6C21D574044B54130BFBF62D0CD |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Stockton | CA | 95207-4618 |  | 2012-06-08 | 2012-06-08 12:54 | 2012-06-08 13:12 | DAY & NIGHT - 585A024055YAC | 51 | 5.2 | Yes | Yes | 19.5 | 22.1 | -2.6 | 3D7D399240454211883D8DEB78AC7B10 |  | R22 | Non-TXV |  | 10.2% | 0.89804 | 19.59% | [5 empty] | Non-TXV | 10.2%
Winton | CA | 95388-0000 |  | 2012-05-07 | 2012-05-07 10:48 | 2012-05-07 10:48 | AMERICAN STANDARD INC. - YCC036F1M0BC | 83 | 0 | Yes | Yes | 18.4 | 15.2 | 3.2 | E74CF173F174403EBF690129414C75CC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5763 |  | 2012-05-08 | 2012-05-08 10:45 | 2012-05-08 10:45 | JOHNSTON - N/A | 75 | 0 | Yes | Yes | 13.5 | 21.5 | -8 | D2DC6EB838444A4AAF0FBC6BD9235DBB | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-0000 |  | 2012-06-12 | 2012-06-12 14:56 | 2012-06-12 15:16 | NORDYNE - JS5BD-024KA | 94 | 12.8 | Yes | Yes | 17.9 | 20.3 | -2.4 | 99D82A363C814624AD8A5B43DC190E74 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.62% | 0.86383 | 26.17% | [5 empty] | Non-TXV | 13.62%
Atwater | CA | 95301-4209 |  | 2012-05-10 | 2012-05-10 12:01 | 2012-05-10 12:01 | UNITARY - DCYZ-F030N070 | 64 | 0 | Yes | Yes | 25.6 | 20.9 | 4.7 | 26A31E6A9EB5467084600E747144C397 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3813 |  | 2012-05-22 | 2012-05-22 14:00 | 2012-05-22 14:00 | BRYANT - 561CJ018-D | 53 | 0 | Yes | Yes | 15.4 | 18.3 | -2.9 | A90C5AFD8A9147A4A4B33C38BDD3C856 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-5423 |  | 2012-07-13 | 2012-07-13 09:22 | 2012-07-13 09:45 | YORK - H4DH018S06A | 78 | 5.4 | Yes | Yes | 17.5 | 20.3 | -2.8 | DA558FE71FD74A9198AA1A3C39DA0C89 |  | R22 | Non-TXV |  | 6.923% | 0.93077 | 13.3% | [5 empty] | Non-TXV | 6.923%
Auburn | CA | 95602-2231 |  | 2012-07-10 | 2012-07-10 14:21 | 2012-07-10 14:46 | HEIL - HAC018AKA1 | 60 | -5.6 | Yes | Yes | 24 | 20.4 | 3.6 | DE0D3DE5F8744DA4927BDE39CD960661 |  | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Stockton | CA | 95204-1734 |  | 2012-05-08 | 2012-05-08 13:57 | 2012-05-08 14:22 | AMANA - PGB30C0702D | 64 | 4.2 | Yes | Yes | 19.5 | 20.1 | -0.6 | 5C459C1865C94E8A8E0D6A47148301ED | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6.562% | 0.93437 | 12.61% | [5 empty] | Non-TXV | 6.562%
Merced | CA | 95348-9380 |  | 2012-05-14 | 2012-05-14 09:56 | 2012-05-14 10:11 | CARRIER - 38CKC036340 | 70 | 0.7 | Yes | Yes | 11.5 | 14.4 | -2.9 | 25889F3CACF846F983BE519A44E95ECA | OK: Verified Refrigerant Charge | R22 | TXV |  | 1% | 0.99 | 1.922% | [5 empty] | TXV | 1%
Rocklin | CA | 95677-3817 |  | 2012-07-12 | 2012-07-12 13:22 | 2012-07-12 13:40 | BRYANT - 561CJ018-D | 58 | -4.1 | Yes | Yes | 15 | 17 | -2 | 806C284E7DD14D8FBB44CCF7BF638FFF |  | R22 | Non-TXV |  | -7.069% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.069%
Paso Robles | CA | 93446-5423 |  | 2012-07-13 | 2012-07-13 11:46 | 2012-07-13 12:04 | YORK - H4DH018S06A | 78 | 2.9 | Yes | Yes | 18.5 | 19.3 | -0.8 | 5C16581AEBF0404397B63520D3BEE892 |  | R22 | Non-TXV |  | 3.718% | 0.96282 | 7.145% | [5 empty] | Non-TXV | 3.718%
Stockton | CA | 95209-2123 |  | 2012-06-15 | 2012-06-15 09:40 | 2012-06-15 10:01 | PAYNE - PY3GNAA24060NA | 76 | -4.5 | Yes | Yes | 22.1 | 19.4 | 2.7 | 3C02B2B32D6B48B7AF1F4F57C0DFE196 |  | R410A | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Rocklin | CA | 95677-3809 |  | 2012-06-12 | 2012-06-12 15:16 | 2012-06-12 15:33 | BRYANT - 561CJ03O-D | 69 | 2.1 | Yes | Yes | 16 | 18.8 | -2.8 | B2BB591A45F943FCB896B50BC5677320 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Oakdale | CA | 95361-3365 |  | 2012-05-24 | 2012-05-24 11:29 | 2012-05-24 11:49 | PAYNE - PH13NR024-H | 71 | 2.8 | Yes | Yes | 18.1 | 19.1 | -1 | CAD3A5163D3C4B0089214757A1243670 |  | R22 | Non-TXV |  | 3.944% | 0.96056 | 7.579% | [5 empty] | Non-TXV | 3.944%
Chico | CA | 95928-6322 |  | 2012-05-24 | 2012-05-24 10:41 | 2012-05-24 10:41 | NA - 661CJ024-A | 71 | 0 | Yes | Yes | 24.2 | 20.9 | 3.3 | FB8AF52F63CD43C093D8FE306672EA7A |  | R22 | TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3808 |  | 2012-07-30 | 2012-07-30 14:01 | 2012-07-30 14:23 | BRYANT - 561CJ024-D | 58 | 6.6 | Yes | Yes | 17.6 | 19.4 | -1.8 | FD0CF1EC1A4E42F3BB200DC78D542D50 |  | R22 | Non-TXV |  | 11.38% | 0.88621 | 21.87% | [5 empty] | Non-TXV | 11.38%
Merced | CA | 95348-1605 |  | 2012-05-30 | 2012-05-30 12:57 | 2012-05-30 13:16 | AMANA - APG13240451BA | 77 | 4.8 | Yes | Yes | 21.2 | 20.1 | 1.1 | D8877B20807A4623A66AE94A4B61FA39 |  | R22 | Non-TXV |  | 6.234% | 0.93766 | 11.98% | [5 empty] | Non-TXV | 6.234%
Fresno | CA | 93722-4508 |  | 2012-05-23 | 2012-05-23 12:04 | 2012-05-23 12:33 | GOODMAN - PGB024050-1 | 85 | 2.5 | Yes | Yes | 20.9 | 19.9 | 1 | 658F6D6CC15647B69F352EC8A6A0843C |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93727-4812 |  | 2012-06-25 | 2012-06-25 11:01 | 2012-06-25 11:28 | YORK - D2N0P024N05606A | 100 | 3.5 | Yes | Yes | 26.8 | 20.8 | 6 | D55D0820A4FB4B828B376FE97A9927F2 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Cameron Park | CA | 95682-8946 |  | 2012-05-31 | 2012-05-31 15:26 | 2012-05-31 15:26 | CARRIER - 25HBR324A310 | 85 | 0 | Yes | Yes | 23.1 | 19.9 | 3.2 | 46303480FFF2471DA9576AE3E04CA5C9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2231 |  | 2012-05-18 | 2012-05-18 14:52 | 2012-05-18 15:10 | RHEEM - RRNA-B030JK06X | 65 | 3.3 | Yes | Yes | 21.7 | 23.1 | -1.4 | D2D652887A1D40008016D694143DC579 | OK: Verified Refrigerant Charge | R22 | TXV |  | 5.077% | 0.94923 | 9.757% | [5 empty] | TXV | 5.077%
Manteca | CA | 95337-9607 |  | 2012-05-17 | 2012-05-17 13:33 | 2012-05-17 14:00 | ARCOAIRE - PGC024K060A | 58 | 5.1 | Yes | Yes | 21.6 | 22 | -0.4 | 4922F82A8DE44059AB077E5E3CB73DFB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.793% | 0.91207 | 16.9% | [5 empty] | Non-TXV | 8.793%
Fresno | CA | 93727-4810 |  | 2012-05-31 | 2012-05-31 12:59 | 2012-05-31 12:59 | BDP - 5858024050YACR | 53 | 0 | Yes | Yes | 23 | 19.3 | 3.7 | 6742E3F3855142208FDA223B772EEA8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-2226 |  | 2012-07-30 | 2012-07-30 10:34 | 2012-07-30 10:52 | OTHER - UNK PAINTED | 85 | -8 | Yes | Yes | 24.9 | 21.4 | 3.5 | B730C29966C6401CB9952E5315367303 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95205-4117 |  | 2012-05-29 | 2012-05-29 16:18 | 2012-05-29 16:35 | DAY & NIGHT - 585A030080YACR | 50 | 4.1 | Yes | Yes | 18.6 | 21.5 | -2.9 | 710FDB3750C14C1C96FEB4A38BBD3D38 |  | R22 | Non-TXV |  | 8.2% | 0.918 | 15.76% | [5 empty] | Non-TXV | 8.2%
Dinuba | CA | 93618-2500 |  | 2012-05-23 | 2012-05-23 11:56 | 2012-05-23 15:55 | GOODMAN - PGB030050-1 | 56 | 2.6 | Yes | Yes | 21.1 | 19.9 | 1.2 | 7DCEDC70E4BD49EC880846D434108C81 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Cameron Park | CA | 95682-8847 |  | 2012-05-31 | 2012-05-31 13:19 | 2012-05-31 13:19 | TRANE - BWD724A100A2 | 98 | 0 | Yes | Yes | 17.2 | 19.2 | -2 | 90ED40F4BF25461F9369C894E97400CB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2671 |  | 2012-08-13 | 2012-08-13 15:50 | 2012-08-13 16:06 | AMERICAN STANDARD - YCY036G1MOAD | 81 | 2.4 | Yes | Yes | 17.9 | 19.8 | -1.9 | 7837683CC5E84A1DB933F03469FC783E |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Paso Robles | CA | 93446-5422 |  | 2012-07-12 | 2012-07-12 16:36 | 2012-07-12 16:56 | YORK - H4DH018S06A | 78 | 2.9 | Yes | Yes | 19 | 19.6 | -0.6 | 627A7C9FD8FB4AA7B37CE954FA282F77 |  | R22 | Non-TXV |  | 3.718% | 0.96282 | 7.145% | [5 empty] | Non-TXV | 3.718%
Olivehurst | CA | 95961-7033 |  | 2012-05-23 | 2012-05-23 15:48 | 2012-05-23 16:10 | RHEEM - RQNL-B036 | 146 | 4.4 | Yes | Yes | 24 | 20.7 | 3.3 | 6F06C36198A64A4CA6182C96132D1246 |  | R410A | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Orland | CA | 95963-1108 |  | 2012-06-08 | 2012-06-08 15:51 | 2012-06-10 15:49 | PAYNE - PA13N024-B | 63 | 6.2 | Yes | Yes | 22.5 | 20.7 | 1.9 | B891D7A13B2B483FBC85DE3FC9605B27 |  | R410A | Non-TXV |  | 9.841% | 0.90159 | 18.91% | [5 empty] | Non-TXV | 9.841%
Stockton | CA | 95207-7845 |  | 2012-05-30 | 2012-05-30 09:26 | 2012-05-30 09:47 | TRANE - YCC024F1L0BF | 64 | 5 | Yes | Yes | 24.1 | 20.1 | 4 | 092E0E885C2848C5B540CCEEF2D2742C |  | R22 | Non-TXV |  | 7.812% | 0.92188 | 15.01% | [5 empty] | Non-TXV | 7.812%
Red Bluff | CA | 96080-2550 |  | 2012-05-18 | 2012-05-18 19:57 | 2012-05-18 19:57 | PAYNE - PY3PNA036090NA | 167 | 0 | Yes | Yes | 18.4 | 20.9 | -2.5 | 36FCA5EF4EEE484A8000C4BC1EFB19CE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-5423 |  | 2012-07-13 | 2012-07-13 08:49 | 2012-07-13 09:11 | YORK - H4DH018S06A | 78 | -4.6 | Yes | Yes | 17.7 | 18.9 | -1.2 | 54C407BC70A644AEBD0EAC8DF520997B |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Merced | CA | 95340-3544 |  | 2012-05-08 | 2012-05-08 15:01 | 2012-05-08 15:01 | YORK - D5YS036N08006A | 80 | 0 | Yes | Yes | 23.5 | 21 | 2.5 | 3393A31141EB4392A1FE1FA0AB9DFEB4 | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-5444 |  | 2012-05-18 | 2012-05-18 15:17 | 2012-05-18 15:42 | DAY & NIGHT - PGF330060K01 | 89 | 3.6 | Yes | Yes | 23.5 | 20.7 | 2.8 | 255590B3730E49F1A8F2DAFB9AA09BAC |  | R22 | Non-TXV |  | 4.045% | 0.95955 | 7.773% | [5 empty] | Non-TXV | 4.045%
Merced | CA | 95340-2746 |  | 2012-05-08 | 2012-05-08 10:48 | 2012-05-08 11:08 | GOODMAN - GPG13480701AB | 145 | 6.1 | Yes | Yes | 27.1 | 21.3 | 5.8 | 863BCDFE273A42CAAF23BD76621E1BF0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.207% | 0.95793 | 8.085% | [5 empty] | Non-TXV | 4.207%
Chowchilla | CA | 93610-9654 |  | 2012-05-21 | 2012-05-21 13:47 | 2012-05-21 14:12 | GOODMAN - GPG10240451A | 50 | -4.1 | Yes | Yes | 23.9 | 21 | 3 | 7C7C1F55433D422CAE0D24020C670939 |  | R22 | Non-TXV |  | -8.2% | 1.082 | 2.296% |  |  |  |  | Non-TXV |  |  | -8.2%
Paso Robles | CA | 93446-5422 |  | 2012-07-12 | 2012-07-12 12:51 | 2012-07-12 13:12 | YORK - H4DH018S06A | 78 | 2.7 | Yes | Yes | 17.1 | 19 | -1.9 | 6F091C9FB6BB47D1AD21B913B02E727D |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Fresno | CA | 93711-1510 |  | 2012-08-10 | 2012-08-10 16:22 | 2012-08-10 16:39 | GOODMAN - PG086075-1AB REV C | 90 | 2.9 | Yes | Yes | 18.3 | 19.8 | -1.5 | 1A881883EFE242BDB24379617CC0B065 |  | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Clovis | CA | 93612-2677 |  | 2012-08-13 | 2012-08-13 17:25 | 2012-08-13 17:58 | CARRIER - 43KL-136-311BE | 66 | 2.1 | Yes | Yes | 18.2 | 19.2 | -1 | 4A4074C0FF9645F2802C1B1AECE63E06 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Chowchilla | CA | 93610-3262 |  | 2012-06-14 | 2012-06-14 12:15 | 2012-06-14 12:37 | GE - BTD718A100A0 | 46 | 3.1 | Yes | Yes | 21.3 | 19.6 | 1.8 | EB3275A847B943BB9BA1798F41748D9E |  | R22 | Non-TXV |  | 6.739% | 0.93261 | 12.95% | [5 empty] | Non-TXV | 6.739%
Olivehurst | CA | 95961-0000 |  | 2012-05-23 | 2012-05-23 15:09 | 2012-05-23 15:26 | RUUD - UNK | 70 | 8.5 | Yes | Yes | 24 | 21.4 | 2.6 | 05941F8297A0438AB47C5B90F0656D6E |  | R22 | Non-TXV |  | 12.14% | 0.87857 | 23.34% | [5 empty] | Non-TXV | 12.14%
Chowchilla | CA | 93610-3262 |  | 2012-05-21 | 2012-05-21 14:40 | 2012-05-21 16:03 | GENERAL ELECTRIC - BTD718A100A0 | 46 | 3.5 | Yes | Yes | 19.3 | 21.8 | -2.5 | 35508492E0D049D199789843B04538FE |  | R22 | Non-TXV |  | 7.609% | 0.92391 | 14.62% | [5 empty] | Non-TXV | 7.609%
Fresno | CA | 93711-1584 |  | 2012-08-10 | 2012-08-10 17:31 | 2012-08-10 17:47 | YORK - D3YSO30N04506B | 66 | 4.2 | Yes | Yes | 18.1 | 20.4 | -2.3 | 23CCAD5130584ECC96A3AD3C628A0443 |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Stockton | CA | 95207-1557 |  | 2012-06-06 | 2012-06-06 11:32 | 2012-06-06 11:51 | DAY & NIGHT - 597CNX048-A | 170 | -9.6 | Yes | Yes | 19 | 19.3 | -0.3 | 39CD74DFC948434CB5CD28E7110348D9 |  | R22 | TXV |  | -5.647% | 1.0565 | 1.581% |  |  |  |  | TXV |  |  | -5.647%
Stockton | CA | 95207-6937 |  | 2012-05-31 | 2012-05-31 08:52 | 2012-05-31 09:12 | WESTINGHOUSE - 24WCU-10CB | 84 | 7.1 | Yes | Yes | 20.8 | 20.4 | 0.4 | 1A1D9A29F35B4713965C8298EABD7229 |  | R22 | Non-TXV |  | 8.452% | 0.91548 | 16.24% | [5 empty] | Non-TXV | 8.452%
Chowchilla | CA | 93610-3262 |  | 2012-07-06 | 2012-07-06 15:37 | 2012-07-06 16:07 | OTHER - 13AJM24A01 | 74 | 4.9 | Yes | Yes | 18.5 | 20.4 | -1.9 | D1A6B8F460A242568D5580E99751A925 |  | R410A | Non-TXV |  | 6.622% | 0.93378 | 12.73% | [5 empty] | Non-TXV | 6.622%
Oroville | CA | 95966-3753 |  | 2012-05-29 | 2012-05-29 16:07 | 2012-05-29 16:07 | GOOD MAN - SSX120361AE | 150 | 0 | Yes | Yes | 24.5 | 21.7 | 2.8 | A551768790D24E15807FEB2814A64DC6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-3753 |  | 2012-05-29 | 2012-05-29 16:31 | 2012-05-29 16:49 | DAY N NIGHT - 585CJ03605 | 84 | 4.6 | Yes | Yes | 21 | 22.9 | -1.9 | 8A0496F3B0454F3D9194C1DDFC2E85F1 |  | R22 | Non-TXV |  | 5.476% | 0.94524 | 10.52% | [5 empty] | Non-TXV | 5.476%
Corning | CA | 96021-2300 |  | 2012-05-18 | 2012-05-18 14:24 | 2012-05-18 14:52 | NA - H1RA024S06D | 57 | 2.9 | Yes | Yes | 21.5 | 20.4 | 1.1 | 4FA6AB7E5C9C41BFA27B422BF3DD9CDD |  | R22 | Non-TXV |  | 5.088% | 0.94912 | 9.777% | [5 empty] | Non-TXV | 5.088%
Tracy | CA | 95376-2230 |  | 2012-06-15 | 2012-06-15 13:50 | 2012-06-15 14:22 | RHEEM - RACA-030AA0 | 35 | 24.1 | Yes | Yes | 18.9 | 20.4 | -1.5 | 8016CF01DD0145B8B6B97FC612F9D1BC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 68.86% | 0.31143 | 132.3% | [5 empty] | Non-TXV | 68.86%
Chowchilla | CA | 93610-3263 |  | 2012-07-06 | 2012-07-06 13:05 | 2012-07-06 13:24 | GE - UNK | 56 | 3.6 | Yes | Yes | 19.2 | 20.8 | -1.6 | 911CC3FA579A4631B9B9FE1CF66393FE |  | R22 | Non-TXV |  | 6.429% | 0.93571 | 12.35% | [5 empty] | Non-TXV | 6.429%
Stockton | CA | 95210-1446 |  | 2012-05-10 | 2012-05-10 12:25 | 2012-05-10 12:44 | ICP - PGAD30D1K6 | 78 | 2.3 | Yes | Yes | 24.6 | 21.4 | 3.2 | 5ED5A5701D79436A9256BE80A07542DC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Stockton | CA | 95206-3430 |  | 2012-05-23 | 2012-05-23 12:00 | 2012-05-23 12:18 | PAYNE - 561AJC18-C | 52 | 4.6 | Yes | Yes | 17.8 | 20.4 | -2.6 | 9F4EA7F761004562B395E21B81F0901A |  | R22 | TXV |  | 8.846% | 0.91154 | 17% | [5 empty] | TXV | 8.846%
Orosi | CA | 93647-1906 |  | 2012-05-29 | 2012-05-29 14:37 | 2012-05-29 14:54 | GOODMAN - GPG13300701BB | 77 | 3.1 | Yes | Yes | 15.7 | 18.6 | -2.9 | 91034AF53BCB4BE6A53810B81768A0D5 |  | R22 | Non-TXV |  | 4.026% | 0.95974 | 7.737% | [5 empty] | Non-TXV | 4.026%
Stockton | CA | 95210-2614 |  | 2012-05-30 | 2012-05-30 13:19 | 2012-05-30 13:38 | GOODMAN - GPG13240451CB | 74 | -4.4 | Yes | Yes | 18.7 | 19.9 | -1.2 | 56A8954161124ABF896C713AF33ACB8D |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Magalia | CA | 95954-8913 |  | 2012-05-30 | 2012-05-30 10:58 | 2012-05-30 11:16 | DAY N NIGHT - 5658J030-P | 85 | 7.7 | Yes | Yes | 20.4 | 22.5 | -2.1 | 6052FBF179804E788E09C67D61F688E5 |  | R22 | Non-TXV |  | 9.059% | 0.90941 | 17.41% | [5 empty] | Non-TXV | 9.059%
Tracy | CA | 95376-6018 |  | 2012-06-25 | 2012-06-25 12:35 | 2012-06-25 12:57 | BDP - 565BJ036-A | 80 | 6.9 | Yes | Yes | 18.8 | 19.3 | -0.5 | 49E19B8B3BA847BD8F7E642DAEA3D247 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.625% | 0.91375 | 16.58% | [5 empty] | Non-TXV | 8.625%
Stockton | CA | 95210-1647 |  | 2012-05-18 | 2012-05-18 16:20 | 2012-05-18 16:38 | BDP - 585A02455YAC | 51 | 3.1 | Yes | Yes | 27.5 | 24.5 | 3 | 11E9C1D5191641A1BF13CC204173928C |  | R22 | Non-TXV |  | 6.078% | 0.93922 | 11.68% | [5 empty] | Non-TXV | 6.078%
Corning | CA | 96021-2071 |  | 2012-05-18 | 2012-05-18 10:00 | 2012-05-18 10:21 | RHEEM - NA | 45 | 2.5 | Yes | Yes | 21.9 | 19.9 | 2 | C2BB8653F1314BB0870D4E249CC35A54 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Fresno | CA | 93727-4442 |  | 2012-05-31 | 2012-05-31 16:27 | 2012-05-31 16:49 | GOODMAN - GSC13024 | 77 | 3.6 | Yes | Yes | 22.1 | 21.5 | 0.6 | 6D4FBBB219B34685BB254AA02587A047 |  | R22 | Non-TXV |  | 4.675% | 0.95325 | 8.985% | [5 empty] | Non-TXV | 4.675%
Penn Valley | CA | 95946-9620 |  | 2012-06-15 | 2012-06-15 13:39 | 2012-06-15 13:39 | TRANE - BTD736A100B0 | 88 | 0 | Yes | Yes | 22.1 | 19.9 | 2.2 | D1D6325E6E204CC5AB05BCB83EE7C35F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3414 |  | 2012-05-14 | 2012-05-14 12:14 | 2012-05-14 12:35 | GOODMAN - CKL18-11 | 83 | 3.6 | Yes | Yes | 26.1 | 21 | 5.1 | 5007C200A6FA4B1896DA1C443CFB7318 |  | R22 | Non-TXV |  | 4.337% | 0.95663 | 8.335% | [5 empty] | Non-TXV | 4.337%
Madera | CA | 93638-3273 |  | 2012-06-12 | 2012-06-12 15:20 | 2012-06-12 15:20 | OTHER - ACS030A2C1 | 71 | 0 | Yes | Yes | 17.2 | 19.9 | -2.7 | A9A590ED414E430B9FA9BA78CAD8773A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4838 |  | 2012-05-11 | 2012-05-11 13:25 | 2012-05-11 13:45 | BDP - 561CJ030-C | 71 | 2.1 | Yes | Yes | 18.1 | 20.8 | -2.7 | 848C288D87E44541A5414359EA94556C | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Manteca | CA | 95337-6660 |  | 2012-05-11 | 2012-05-11 13:04 | 2012-05-11 13:09 | BRYANT - 563CN036-C | 101 | 3.9 | Yes | Yes | 20.9 | 21.9 | -1 | 05404D09185543748ABF10DFB97BA972 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.861% | 0.96139 | 7.421% | [5 empty] | Non-TXV | 3.861%
Manteca | CA | 95337-6660 |  | 2012-05-11 | 2012-05-11 13:17 | 2012-05-11 13:38 | BRYANT - 563CN036-C | 101 | 14.8 | Yes | Yes | 20.1 | 21.5 | -1.4 | 93CA38774AD043BE9C6FE03047283A6F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 14.65% | 0.85347 | 28.16% | [5 empty] | Non-TXV | 14.65%
Los Banos | CA | 93635-6399 |  | 2012-05-29 | 2012-05-29 16:45 | 2012-05-29 17:07 | GIBSON - JS5BD-048K | 147 | 4.4 | Yes | Yes | 28.2 | 22.5 | 5.8 | FA66CFFC11FD47E088F125CD31CC6BD1 |  | R22 | Non-TXV |  | 2.993% | 0.97007 | 5.752% | [5 empty] | Non-TXV | 2.993%
Oroville | CA | 95965-4671 |  | 2012-06-13 | 2012-06-13 14:17 | 2012-06-13 14:45 | TRANE - 2TTB3030A1000AA | 88 | 6.9 | Yes | Yes | 21.5 | 20.8 | 0.7 | F7281F62457646BB961F160FA2F71221 |  | R22 | Non-TXV |  | 7.841% | 0.92159 | 15.07% | [5 empty] | Non-TXV | 7.841%
Stockton | CA | 95204-5415 |  | 2012-05-09 | 2012-05-09 12:09 | 2012-05-09 12:37 | RHEEM - RRKA-A030JK06X | 54 | 4.5 | Yes | Yes | 19.2 | 20.9 | -1.7 | 5122BAD639A24828A6C23B9A74924D55 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Red Bluff | CA | 96080-9522 |  | 2012-05-23 | 2012-05-23 16:49 | 2012-05-23 16:49 | BRYANT - PH10JA024E | 66 | 0 | Yes | Yes | 22 | 20.1 | 1.9 | B6242622A4824319BA0C75260AD77672 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-9522 |  | 2012-05-23 | 2012-05-23 16:54 | 2012-05-23 16:54 | AMANA - UNK | 76 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | 4B52DBC6F3BC44A58113B399A2E55854 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-3174 |  | 2012-05-14 | 2012-05-14 10:08 | 2012-05-14 10:25 | AMERICAN GENERAL - 6H0024A100A4 | 80 | 2.4 | Yes | Yes | 21.7 | 20.9 | 0.8 | 97707B7016E94DD2835A6E3A78A53914 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95340-3809 |  | 2012-05-14 | 2012-05-14 12:37 | 2012-05-14 12:55 | AMANA - GSC130301AD | 87 | 5.8 | Yes | Yes | 25.1 | 19.1 | 6 | FEA2A8E521E644FCA39B656EED4EE90B |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Yuba City | CA | 95991-8835 |  | 2012-07-12 | 2012-07-12 13:08 | 2012-07-12 13:08 | DAY & NIGHT - 565BJ024 | 70 | 0 | Yes | Yes | 21.8 | 20.5 | 1.3 | 4347B10B12C742C29F7141E14363812C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-3615 |  | 2012-06-22 | 2012-06-22 08:42 | 2012-06-22 09:04 | DAY & NIGHT - 588ANW036060ACAF | 67 | 7.5 | Yes | Yes | 19.5 | 19.1 | 0.4 | B2B7F30B6BEE4B62B260A432E49248D6 |  | R22 | Non-TXV |  | 11.19% | 0.88806 | 21.51% | [5 empty] | Non-TXV | 11.19%
Woodbridge | CA | 95258-9003 |  | 2012-06-25 | 2012-06-25 09:05 | 2012-06-25 09:23 | WEATHER KING - 10AJA3601 | 80 | -4.7 | Yes | Yes | 23 | 18.7 | 4.3 | D4A7CDC6F6DF4A77AFA33C9991E81E9C |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Oakdale | CA | 95361-3949 |  | 2012-05-24 | 2012-05-24 14:37 | 2012-05-24 14:53 | ICP - NAC024AKB1 | 67 | 8.8 | Yes | Yes | 20.3 | 21 | -0.7 | BE480D3692AA4515B6F7A911A28286BB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.13% | 0.86866 | 25.24% | [5 empty] | Non-TXV | 13.13%
Merced | CA | 95348-3412 |  | 2012-05-18 | 2012-05-18 11:17 | 2012-05-18 11:41 | GOODMAN - CKL1818 | 72 | 8.3 | Yes | Yes | 23.5 | 21 | 2.5 | 7F85739E7C0C4FBAA1FA87EBBD107092 |  | R22 | Non-TXV |  | 11.53% | 0.88472 | 22.15% | [5 empty] | Non-TXV | 11.53%
Tracy | CA | 95376-3208 |  | 2012-06-20 | 2012-06-20 16:03 | 2012-06-20 16:26 | YORK - D2YS024N03206A | 62 | 1.9 | Yes | Yes | 19.5 | 21.4 | -1.9 | 2BAD417A5F20444D835C03F13D8BBF0D |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Stockton | CA | 95204-4014 |  | 2012-05-08 | 2012-05-08 18:05 | 2012-05-08 18:05 | RHEEM - RRPL-B036JK08X | 99 | 0 | Yes | Yes | 17.4 | 16.8 | 0.6 | 02EC99DC7629472E9544638E687FF647 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5011 |  | 2012-05-30 | 2012-05-30 12:21 | 2012-05-30 12:40 | WESTINGHOUSE - 1D03401A | 69 | 3.6 | Yes | Yes | 21.3 | 21 | 0.3 | EF04FAF762E940AE95BF435E7D19156A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.217% | 0.94783 | 10.03% | [5 empty] | Non-TXV | 5.217%
Dinuba | CA | 93618-2936 |  | 2012-05-21 | 2012-05-21 11:08 | 2012-05-21 11:34 | GOODMAN - GPG1330701BB | 77 | 4.8 | Yes | Yes | 16.1 | 19.1 | -3 | D7589D3F3D734899B33A95A2B97F9F6F |  | R22 | Non-TXV |  | 6.234% | 0.93766 | 11.98% | [5 empty] | Non-TXV | 6.234%
Atwater | CA | 95301-3610 |  | 2012-05-16 | 2012-05-16 13:22 | 2012-05-16 13:46 | TRANE - 2YCC3024A1040AA | 88 | 2.6 | Yes | Yes | 20.9 | 19.7 | 1.2 | 2AD1CA8EE4D841F18DDDCA86CB9457AA |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Stockton | CA | 95206-5922 |  | 2012-05-30 | 2012-05-30 13:26 | 2012-05-30 13:47 | CARRIER - 38CKC048360 | 109 | 6 | Yes | Yes | 15.8 | 18.2 | -2.4 | 3790852B9EBD457EB0904E5F681876A4 |  | R22 | TXV |  | 5.505% | 0.94495 | 10.58% | [5 empty] | TXV | 5.505%
Manteca | CA | 95336-4923 |  | 2012-05-16 | 2012-05-16 13:39 | 2012-05-16 14:01 | PAYNE - PY1PNB024060AAAA | 53 | 1.8 | Yes | Yes | 19.9 | 19.9 | 0 | 2E48B9E77C0F4F8B8DC1E1B238F1870D |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Atascadero | CA | 93422-4566 |  | 2012-07-10 | 2012-07-10 10:31 | 2012-07-10 10:49 | BDP - 567C018RCU | 37 | 2.9 | Yes | Yes | 16.8 | 19.1 | -2.3 | 12DFC55695F144E1846C3B7BD8C486B1 |  | R22 | Non-TXV |  | 7.838% | 0.92162 | 15.06% | [5 empty] | Non-TXV | 7.838%
Kerman | CA | 93630-9352 |  | 2012-07-09 | 2012-07-09 13:00 | 2012-07-09 13:26 | LENNOX - 13ACC-048-230-01 | 158 | 4.6 | Yes | Yes | 23.8 | 20.7 | 3.1 | C4FC97852F004BE7AD6B25A52A97BAE6 |  | R22 | Non-TXV |  | 2.911% | 0.97089 | 5.595% | [5 empty] | Non-TXV | 2.911%
Stockton | CA | 95207-2332 |  | 2012-05-31 | 2012-05-31 15:08 | 2012-05-31 15:26 | KENMORE - UNK | 96 | 4.5 | Yes | Yes | 19.6 | 18 | 1.6 | 4A32267364BC47A1A32E015B9C7CA2E1 |  | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Stockton | CA | 95207-2217 |  | 2012-05-31 | 2012-05-31 13:19 | 2012-05-31 13:36 | GE - JA930H11 | 55 | 4.8 | Yes | Yes | 21.6 | 20.2 | 1.5 | 4B5C20F8C40645FA8732AC91FCAF8047 |  | R22 | Non-TXV |  | 8.727% | 0.91273 | 16.77% | [5 empty] | Non-TXV | 8.727%
Stockton | CA | 95206-2848 |  | 2012-05-22 | 2012-05-22 11:47 | 2012-05-22 12:15 | RHEEM - RRNL-B024JK06X | 78 | -4.6 | Yes | Yes | 24.8 | 20.8 | 4 | 00AEC0155D9C43E5B91E3E3B62239990 |  | R410A | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Stockton | CA | 95215-5850 |  | 2012-05-31 | 2012-05-31 13:29 | 2012-05-31 13:59 | AMANA - PGB30C0702E | 64 | 7.6 | Yes | Yes | 19.1 | 19.8 | -0.7 | E3A870FB6B334379A4972A685734CD44 |  | R22 | Non-TXV |  | 11.88% | 0.88125 | 22.82% | [5 empty] | Non-TXV | 11.88%
Merced | CA | 95341-6993 |  | 2012-05-09 | 2012-05-09 12:16 | 2012-05-09 12:42 | BRYANT - 582ANW042060NAAG | 100 | 5.8 | Yes | Yes | 25.7 | 20.4 | 5.3 | 4C4B948AE5D641AFA4563EDDCDC45881 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Manteca | CA | 95336-4923 |  | 2012-05-08 | 2012-05-08 14:39 | 2012-05-08 14:58 | PAYNE - P1PNB024060AAAA | 53 | 4.3 | Yes | Yes | 23.4 | 23.9 | -0.5 | BBAF06198C4C457BB52192D57167BA02 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.113% | 0.91887 | 15.59% | [5 empty] | Non-TXV | 8.113%
Chico | CA | 95928-4018 |  | 2012-07-02 | 2012-07-02 13:24 | 2012-07-02 17:50 | RHEEM - DAGL-024JA | 77 | 3.9 | Yes | Yes | 24.6 | 21.7 | 2.9 | D15C82010DAD4A6A851AA1ABA300A598 |  | R410A | Non-TXV |  | 5.065% | 0.94935 | 9.734% | [5 empty] | Non-TXV | 5.065%
Manteca | CA | 95337-4387 |  | 2012-05-30 | 2012-05-30 09:42 | 2012-05-30 10:03 | ICP - N2A318AKC200 | 53 | 10.8 | Yes | Yes | 20.4 | 19.1 | 1.3 | C618A34EED7247A6A04361E670323E46 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.38% | 0.79623 | 39.16% | [5 empty] | Non-TXV | 20.38%
Auburn | CA | 95602-2440 |  | 2012-05-29 | 2012-05-29 13:59 | 2012-05-29 14:17 | OTHER - UNK | 54 | 3.1 | Yes | Yes | 19 | 21 | -2 | 2248DC299EAC4E4DB870FF166AC0B437 |  | R22 | Non-TXV |  | 5.741% | 0.94259 | 11.03% | [5 empty] | Non-TXV | 5.741%
Atwater | CA | 95301-2811 |  | 2012-05-10 | 2012-05-10 14:56 | 2012-05-10 15:15 | GOODMAN - GPG13360701AC | 112 | 6.7 | Yes | Yes | 23.3 | 20.4 | 2.9 | 69E851D46639470A89925C740CD6F825 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.982% | 0.94018 | 11.5% | [5 empty] | Non-TXV | 5.982%
Stockton | CA | 95210-5673 |  | 2012-06-20 | 2012-06-20 10:49 | 2012-06-20 11:01 | OTHER - 2SCU13LB136P-2 | 92 | 3.1 | Yes | Yes | 19.7 | 21.5 | -1.8 | 997F42A3DEA4437A90EBB49530439DAE |  | R22 | Non-TXV |  | 3.37% | 0.9663 | 6.476% | [5 empty] | Non-TXV | 3.37%
Oakdale | CA | 95361-3368 |  | 2012-06-07 | 2012-06-07 12:24 | 2012-06-07 12:43 | DAY & NIGHT - 541DJ024 | 118 | 3.5 | Yes | Yes | 20.6 | 21.4 | -0.8 | D3778F754ED945FF93D6756A7ECD4280 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Auburn | CA | 95602-2356 |  | 2012-07-24 | 2012-07-24 09:08 | 2012-07-24 09:28 | GOODMAN - UNK | 80 | 10.2 | Yes | Yes | 18 | 20.9 | -2.9 | AFDDC599223B475CB926CA4819A97158 |  | R22 | Non-TXV |  | 12.75% | 0.8725 | 24.5% | [5 empty] | Non-TXV | 12.75%
Los Banos | CA | 93635-7402 |  | 2012-07-14 | 2012-07-14 09:51 | 2012-07-14 10:15 | GIBSON - JS5BD-036K | 138 | 20.1 | Yes | Yes | 19.5 | 18.7 | 0.8 | 8AC677ED839845309CB97DE9988DD30E |  | R22 | Non-TXV |  | 14.57% | 0.85435 | 27.99% | [5 empty] | Non-TXV | 14.57%
Stockton | CA | 95215-7330 |  | 2012-06-21 | 2012-06-21 13:34 | 2012-06-21 13:34 | GMC - VSX130361AA | 89 | 0 | Yes | Yes | 21 | 20.3 | 0.7 | A73BF14357EF4833B6DF26CCE2DDC9B0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-2358 |  | 2012-05-29 | 2012-05-29 14:29 | 2012-05-29 14:54 | RHEEM - UNK | 85 | 3.7 | Yes | Yes | 25 | 23.1 | 1.9 | E51789B90FB544439287508F7E5391AE |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Merced | CA | 95348-3413 |  | 2012-05-14 | 2012-05-14 12:41 | 2012-05-14 13:01 | GOODMAN - CK18-1B | 59 | 4.6 | Yes | Yes | 25.3 | 19.3 | 6 | 582F06C0AF1947B8B0A494F20EA12E2B |  | R22 | Non-TXV |  | 7.797% | 0.92203 | 14.98% | [5 empty] | Non-TXV | 7.797%
Los Banos | CA | 93635-6367 |  | 2012-05-31 | 2012-05-31 12:31 | 2012-05-31 13:06 | BRYANT - 563CN048-H | 136 | -7.7 | Yes | Yes | 17.7 | 19.3 | -1.6 | 7168E44DFAB14051BE289F93B0D1FB80 |  | R22 | TXV |  | -5.662% | 1.0566 | 1.586% |  |  |  |  | TXV |  |  | -5.662%
Fresno | CA | 93711-2931 |  | 2012-08-14 | 2012-08-14 16:40 | 2012-08-14 19:05 | PAYNE - 591AN042-D | 87 | 2.8 | Yes | Yes | 17.6 | 20.2 | -2.6 | D4788CCBA2F4440E874A40C6F418D9D1 |  | R22 | Non-TXV |  | 3.218% | 0.96782 | 6.185% | [5 empty] | Non-TXV | 3.218%
Auburn | CA | 95602-2355 |  | 2012-07-10 | 2012-07-10 13:00 | 2012-07-10 13:25 | RHEEM - RACA-018ABS | 30 | 3.1 | Yes | Yes | 18 | 21 | -3 | 89431832B2A84F5284411805D5BB9ADB |  | R22 | Non-TXV |  | 10.33% | 0.89667 | 19.86% | [5 empty] | Non-TXV | 10.33%
Stockton | CA | 95203-1432 |  | 2012-07-06 | 2012-07-06 11:50 | 2012-07-06 12:10 | TRANE - BTD730A100B0 | 74 | 6.4 | Yes | Yes | 17.7 | 19.8 | -2.1 | 582B473C9D554672B65C80EC84A3CFCD |  | R22 | Non-TXV |  | 8.649% | 0.91351 | 16.62% | [5 empty] | Non-TXV | 8.649%
Stockton | CA | 95212-2894 |  | 2012-05-29 | 2012-05-29 09:47 | 2012-05-29 10:06 | CARRIER - 38CKC036350 | 73 | -3.6 | Yes | Yes | 21.2 | 16.7 | 4.5 | 65672E6E2DF641A193BD5FD2659C281F |  | R22 | TXV |  | -4.932% | 1.0493 | 1.381% |  |  |  |  | TXV |  |  | -4.932%
Fresno | CA | 93711-2736 |  | 2012-08-10 | 2012-08-10 19:43 | 2012-08-10 20:12 | RHEEM - RAMCE-036JAZ | 93 | 3.7 | Yes | Yes | 19 | 20.4 | -1.4 | EBD9523A865B467F9A2898E63CD864BC |  | R22 | Non-TXV |  | 3.978% | 0.96022 | 7.646% | [5 empty] | Non-TXV | 3.978%
Stockton | CA | 95210-2125 |  | 2012-05-11 | 2012-05-11 11:23 | 2012-05-11 11:42 | BDP - 567C030RCU | 63 | 3.7 | Yes | Yes | 23.7 | 20.8 | 3 | 6ED8D1A1079A4F1D9336C7FEF5FFF4E9 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.873% | 0.94127 | 11.29% | [5 empty] | Non-TXV | 5.873%
Stockton | CA | 95212-2894 |  | 2012-05-17 | 2012-05-17 12:06 | 2012-05-17 12:25 | CARRIER - 38CKC048370 | 100 | 3 | Yes | Yes | 19.9 | 18.7 | 1.2 | 96A7A7659F6343C9B5F6048CDBA0BE21 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Jackson | CA | 95642-9554 |  | 2012-07-20 | 2012-07-20 11:18 | 2012-07-20 11:42 | CARRIER - 48GP-030060311VS | 88 | 12.9 | Yes | Yes | 23.1 | 20.7 | 2.4 | A3DEF72766D14E119A200144E9E5EF50 |  | R410A | Non-TXV |  | 14.66% | 0.85341 | 28.17% | [5 empty] | Non-TXV | 14.66%
Manteca | CA | 95337-4386 |  | 2012-05-17 | 2012-05-17 11:14 | 2012-05-17 11:38 | CARRIER - 38EN018310 | 55 | 10.4 | Yes | Yes | 15.9 | 18.7 | -2.8 | 6729E1C73C4B46A6BCB433FA9CDB49F7 |  | R22 | Non-TXV |  | 18.91% | 0.81091 | 36.34% | [5 empty] | Non-TXV | 18.91%
Grass Valley | CA | 95945-6106 |  | 2012-07-09 | 2012-07-09 10:12 | 2012-07-09 10:35 | OTHER - 561AJ018-A | 55 | -5.2 | Yes | Yes | 20 | 19.9 | 0.1 | 6D2F9F4B3CE24CDE9ED06FED6FF10EF6 |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Manteca | CA | 95336-3447 |  | 2012-05-07 | 2012-05-07 11:54 | 2012-05-07 11:54 | GENERAL ELECTRIC - BTR930A100A0 | 72 | 0 | Yes | Yes | 25.7 | 20.1 | 5.6 | 641DA119373E4464AD4F3B03EED410AC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-2221 |  | 2012-05-29 | 2012-05-29 13:22 | 2012-05-29 13:22 | LENNOX - 12GCS030X-75-6PB | 84 | 0 | Yes | Yes | 22.8 | 22.4 | 0.4 | F4E5E9C78B0E46A4A5409A8EEB686DD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2308 |  | 2012-06-06 | 2012-06-06 15:14 | 2012-06-06 15:31 | PAYNE - UNK | 72 | 11.8 | Yes | Yes | 27.3 | 22.6 | 4.7 | 54185C17E6C64EF499F0FD0412FAAD57 |  | R22 | Non-TXV |  | 16.39% | 0.83611 | 31.5% | [5 empty] | Non-TXV | 16.39%
Riverbank | CA | 95367-1908 |  | 2012-06-13 | 2012-06-13 13:34 | 2012-06-13 13:59 | CARRIER - 48ESNA3606030-- | 100 | 3.6 | Yes | Yes | 16.6 | 19.3 | -2.7 | 7BAA2F1F10D446F69BB9D4D2821FF014 |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Stockton | CA | 95210-4269 |  | 2012-05-22 | 2012-05-22 14:30 | 2012-05-22 14:47 | CARRIER - 38TH036300 | 85 | -6 | Yes | Yes | 26 | 21 | 5 | B6D77F81400E4FB1AD2A10BC604581C6 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Sutter Creek | CA | 95685-9709 |  | 2012-07-17 | 2012-07-17 14:25 | 2012-07-17 14:46 | CARRIER - 38GS030310 | 56 | -5.3 | Yes | Yes | 17 | 18.2 | -1.2 | 7C7C59DC0EF0426FBD3CB37A1D9E4E28 |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
Fresno | CA | 93722-5758 |  | 2012-06-06 | 2012-06-06 13:55 | 2012-06-06 14:14 | RHEEM - N/A | 48 | 1.4 | Yes | Yes | 26 | 20.4 | 5.6 | CE8F54B10A5245E8A716491A9E5AE39C |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Stockton | CA | 95212-3050 |  | 2012-05-22 | 2012-05-22 16:01 | 2012-05-22 16:18 | YORK - H2RD048S06B | 134 | 13.6 | Yes | Yes | 26 | 22 | 4 | 18D57690692544DD81F03BA9085C5682 |  | R22 | TXV |  | 10.15% | 0.89851 | 19.5% | [5 empty] | TXV | 10.15%
Stockton | CA | 95210-1813 |  | 2012-06-21 | 2012-06-21 10:08 | 2012-06-21 10:30 | HEIL - DAYA-F030N070C | 76 | 7.5 | Yes | Yes | 23.7 | 18.3 | 5.4 | 7FC91699754740189851BF64ADA7BFD7 |  | R22 | Non-TXV |  | 9.868% | 0.90132 | 18.96% | [5 empty] | Non-TXV | 9.868%
Fresno | CA | 93722-4565 |  | 2012-05-23 | 2012-05-23 13:48 | 2012-05-23 14:40 | YORK - D1NA024N03606CNFMM067943 | 85 | 3.4 | Yes | Yes | 23.2 | 25.6 | -2.4 | C3CA596074DC4153A0EBACC82EFC5FB6 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Escalon | CA | 95320-9616 |  | 2012-07-12 | 2012-07-12 10:39 | 2012-07-12 10:55 | TRANE - 2TTB3048A1000AA | 142 | 9.4 | Yes | Yes | 17.9 | 18.7 | -0.8 | 6BE1697DE00845F1A9CCB5ECCDA697F7 |  | R22 | Non-TXV |  | 6.62% | 0.9338 | 12.72% | [5 empty] | Non-TXV | 6.62%
Manteca | CA | 95336-4923 |  | 2012-05-08 | 2012-05-08 15:33 | 2012-05-08 15:54 | BDP - 585B024050YACR | 51 | 2.1 | Yes | Yes | 25.9 | 22.3 | 3.7 | 9EACAAEA839F4E7BACB7FFC82BAA759A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Clovis | CA | 93612-3666 |  | 2012-07-09 | 2012-07-09 15:18 | 2012-07-09 15:42 | JANITROL - CJ36-1FC | 59 | 3.5 | Yes | Yes | 19.1 | 20.1 | -1 | 89C48514F1EE44FE8051547C4B0AE2B0 |  | R22 | Non-TXV |  | 5.932% | 0.94068 | 11.4% | [5 empty] | Non-TXV | 5.932%
Fresno | CA | 93722-4568 |  | 2012-05-23 | 2012-05-23 16:35 | 2012-05-23 16:54 | PAYNE - 585A024055YAC | 85 | 2.6 | Yes | Yes | 19.3 | 21.8 | -2.5 | 1E8A7371957B47358934B75A6DA7F3AF |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Chowchilla | CA | 93610-3264 |  | 2012-06-14 | 2012-06-14 13:14 | 2012-06-14 13:33 | YORK - H4D8018S06A | 62 | 3.3 | Yes | Yes | 18.6 | 19.1 | -0.4 | 4A0DF87162364CD1805CC08E035B6455 |  | R22 | Non-TXV |  | 5.323% | 0.94677 | 10.23% | [5 empty] | Non-TXV | 5.323%
Stockton | CA | 95212-3136 |  | 2012-05-24 | 2012-05-24 12:00 | 2012-05-24 12:17 | YORK - H2RCO48SO6A | 119 | 16.9 | Yes | Yes | 18.5 | 21.4 | -2.9 | 1A760D1F7D304EB384614CF12B3AB6A7 |  | R22 | Non-TXV |  | 14.2% | 0.85798 | 27.29% | [5 empty] | Non-TXV | 14.2%
Chowchilla | CA | 93610-3262 |  | 2012-07-25 | 2012-07-25 16:22 | 2012-07-25 17:26 | RHEEM - 13AJN30A01 | 75 | 3.8 | Yes | Yes | 20.3 | 18.5 | 1.8 | E9ECDEC393B04B94BAD3E15B8132FEBE |  | R410A | Non-TXV |  | 5.067% | 0.94933 | 9.737% | [5 empty] | Non-TXV | 5.067%
Stockton | CA | 95209-1571 |  | 2012-05-21 | 2012-05-21 10:32 | 2012-05-21 10:51 | RHEEM - RRKA-AO3JK06X | 54 | 4.7 | Yes | Yes | 18.1 | 19.4 | -1.3 | 955C838653D545C4923B647ABE7C73C2 |  | R22 | TXV |  | 8.704% | 0.91296 | 16.73% | [5 empty] | TXV | 8.704%
Winton | CA | 95388-0000 |  | 2012-05-07 | 2012-05-07 16:20 | 2012-05-07 16:20 | NA - 13A0AA2A01 | 37 | 0 | Yes | Yes | 19.1 | 19.7 | -0.6 | 70336E7E3D5A4BCA83DC9DD40B2320FA | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4565 |  | 2012-05-23 | 2012-05-23 12:48 | 2012-05-23 13:06 | CARRIER - 585A024055AC | 51 | 2.1 | Yes | Yes | 17.8 | 20.7 | -2.9 | 5854815B9A964C07B90B7D6B2C3B738D |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Stockton | CA | 95210-2350 |  | 2012-05-23 | 2012-05-23 11:13 | 2012-05-23 11:29 | PAYNE - 24/60YAC108C | 53 | -3.7 | Yes | Yes | 24.5 | 21 | 3.5 | 8DED09D951094753BC7E8379D8DE30E2 |  | R22 | Non-TXV |  | -6.981% | 1.0698 | 1.955% |  |  |  |  | Non-TXV |  |  | -6.981%
Stockton | CA | 95209-2124 |  | 2012-05-18 | 2012-05-18 11:47 | 2012-05-18 12:07 | FRESER JOHNSTON - 80WR30E1NA | 55 | 13.8 | Yes | Yes | 23.7 | 23.6 | 0.1 | 0EE4F7C84E5C4588BEB33EDDFECE25C1 |  | R22 | Non-TXV |  | 25.09% | 0.74909 | 48.22% | [5 empty] | Non-TXV | 25.09%
Fresno | CA | 93722-4508 |  | 2012-05-23 | 2012-05-23 12:51 | 2012-05-23 13:17 | GOODMAN - PGB024050-1 | 54 | 1.6 | Yes | Yes | 22.5 | 21 | 1.5 | 15EEA103C71E4FA3BE1FBB220F4AAF88 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Atwater | CA | 95301-4021 |  | 2012-05-11 | 2012-05-11 10:46 | 2012-05-11 11:04 | AMERICAN STANDARD - YCC024F1LOBC | 64 | 1.9 | Yes | Yes | 17.9 | 19 | -1.1 | 8D5DDD60ACB843AD8A28072EA4F4BC5E | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93710-5227 |  | 2012-06-06 | 2012-06-06 11:42 | 2012-06-06 12:03 | DAY & NIGHT - 585CJ036075 | 84 | 2.5 | Yes | Yes | 24.8 | 20.4 | 4.4 | 53F57D38A4424A3F9DD20918894EFDC6 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Oroville | CA | 95966-5252 |  | 2012-05-31 | 2012-05-31 10:59 | 2012-05-31 11:18 | NORDYNE - GR4GA-030K072X | 67 | 2.5 | Yes | Yes | 23.5 | 21.5 | 2 | 89760A425E8F44969773EB7A8760D90E |  | R22 | Non-TXV |  | 3.731% | 0.96269 | 7.171% | [5 empty] | Non-TXV | 3.731%
Fresno | CA | 93722-4568 |  | 2012-05-23 | 2012-05-23 14:59 | 2012-05-23 15:17 | PAYNE - 55A024055YAC | 51 | 3.3 | Yes | Yes | 18.1 | 19.9 | -1.8 | E7954F98ECBC45ABB36871372AD157A4 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Fresno | CA | 93727-7214 |  | 2012-05-30 | 2012-05-30 16:13 | 2012-05-30 16:13 | UNITARY PRODUCTS GROUP - DCYP-F024N045B | 100 | 0 | Yes | Yes | 17.2 | 18.5 | -1.3 | 0827696440EE43DBAF17F7DE84626B71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7147 |  | 2012-05-29 | 2012-05-29 17:00 | 2012-05-29 17:18 | LENNOX - HS25-311-1P | 85 | 2.6 | Yes | Yes | 21.8 | 18.5 | 3.3 | 94BC8C81349F42B8A75DAACCA13B514D |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Stockton | CA | 95206-5626 |  | 2012-05-15 | 2012-05-15 13:04 | 2012-05-15 13:40 | PAYNE - 593ANX036000ABAA | 118 | -6.5 | Yes | Yes | 20.7 | 21.4 | -0.7 | 0033FA989EA846E694D75449D7A289AE |  | R22 | Non-TXV |  | -5.508% | 1.0551 | 1.543% |  |  |  |  | Non-TXV |  |  | -5.508%
Stockton | CA | 95206-5626 |  | 2012-05-15 | 2012-05-15 13:27 | 2012-05-15 13:46 | PAYNE - 593ANX036000ABAA | 136 | 14.4 | Yes | Yes | 18.4 | 18.3 | 0.1 | F3BAD0D09EAB459BB2AB021A9EAEE0B1 | OK: Verified Refrigerant Charge | R22 | TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | TXV | 10.59%
Fresno | CA | 93722-4566 |  | 2012-05-23 | 2012-05-23 12:14 | 2012-05-23 12:27 | CARRIER - 585A024055YAC | 53 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | 0326025820154E0E99F2934FA28D5D44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Orosi | CA | 93647-1909 |  | 2012-05-29 | 2012-05-29 12:14 | 2012-05-29 12:38 | DAY & NIGHT - 36/80 YAC-109T-C | 70 | 11 | Yes | Yes | 18.5 | 21 | -2.5 | A9230503F0314A1592C779F55E5DD36F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Stockton | CA | 95210-3132 |  | 2012-06-11 | 2012-06-11 14:26 | 2012-06-11 14:43 | BDP - 567C024RCU | 60 | -3.5 | Yes | Yes | 26.5 | 21.1 | 5.5 | 580336D8CB18443F9B1A2E4CD914F8C7 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Clovis | CA | 93611-6535 |  | 2012-05-22 | 2012-05-22 16:44 | 2012-05-22 16:44 | CARRIER - 38CKC060300 | 141 | 0 | Yes | Yes | 20.1 | 20.4 | -0.3 | BBD6764E1633453DB7E572FB21F1DDFF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3414 |  | 2012-05-29 | 2012-05-29 11:13 | 2012-05-29 11:33 | BRYANT - 574ANW036060NB-- | 114 | 4 | Yes | Yes | 19.1 | 19.9 | -0.8 | 0CF5CAFE4C5247A0B5E42274DF1DCC0A |  | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Tracy | CA | 95376-5303 |  | 2012-06-21 | 2012-06-21 13:49 | 2012-06-21 14:11 | GOODMAN - DE48-1EB | 100 | 3.4 | Yes | Yes | 18.6 | 19.8 | -1.2 | 311D9C669EF548B8838ED3605D333CD5 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Atwater | CA | 95301-4586 |  | 2012-05-14 | 2012-05-14 15:56 | 2012-05-14 16:14 | TRANE - 2TTB0036A100AA | 76 | 2.3 | Yes | Yes | 13.4 | 14.3 | -0.9 | 531F35A757F84FCC9179BAD8D222E7A8 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Firebaugh | CA | 93622-2746 |  | 2012-05-31 | 2012-05-31 17:45 | 2012-05-31 18:29 | LENNOX - 10GCS030-75-3PA | 51 | 1.5 | Yes | Yes | 23.1 | 21.5 | 1.6 | A5454CA5C78A48ADB837E3773B42F296 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Madera | CA | 93637-5451 |  | 2012-05-18 | 2012-05-18 12:21 | 2012-05-18 12:40 | RUUD - URGG-05E030JKR | 46 | 1.4 | Yes | Yes | 22.7 | 20.2 | 2.6 | CAC68C95B4234D5D954CDE90A9687B4F |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Stockton | CA | 95210-2317 |  | 2012-05-16 | 2012-05-16 13:08 | 2012-05-16 13:30 | BDP - 585A024055YAC | 51 | -3 | Yes | Yes | 17.3 | 18.8 | -1.5 | 56B40E423958425A945C073766BC73DF |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Clovis | CA | 93612-5702 |  | 2012-05-30 | 2012-05-30 10:24 | 2012-05-30 10:41 | YORK - DAYA-F040N110C | 92 | 2.7 | Yes | Yes | 17.3 | 20.2 | -2.9 | 7094100F4C6C4A8C9B90D0325D3235F2 |  | R22 | Non-TXV |  | 2.935% | 0.97065 | 5.64% | [5 empty] | Non-TXV | 2.935%
Manteca | CA | 95336-5954 |  | 2012-05-09 | 2012-05-09 16:34 | 2012-05-09 17:02 | YORK - H2RA030S06D | 62 | 14.8 | Yes | Yes | 19.3 | 20.9 | -1.6 | 871A71AC253A40C9B99BA06868095C01 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 23.87% | 0.76129 | 45.87% | [5 empty] | Non-TXV | 23.87%
Fresno | CA | 93722-4508 |  | 2012-05-23 | 2012-05-23 13:20 | 2012-05-23 13:36 | TAPPAN - N/A | 64 | 1.9 | Yes | Yes | 22.2 | 20.7 | 1.5 | 8C98694FC7114D4C855A49AA6AD3BF34 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93722-4506 |  | 2012-05-18 | 2012-05-18 15:55 | 2012-05-18 15:55 | GOODMAN - PGB024050-1 | 70 | 0 | Yes | Yes | 18.3 | 20.4 | -2.1 | CAA55F81048C43B989FDD8C017402812 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-6602 |  | 2012-05-21 | 2012-05-21 13:08 | 2012-05-21 13:25 | PAYNE - 591ANX042000ABAA | 112 | -7.9 | Yes | Yes | 26 | 22.2 | 3.9 | 0D163EA9BA964A49A1A2B2ECDCDCB99B |  | R22 | Non-TXV |  | -7.054% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.054%
San Andreas | CA | 95249-9631 |  | 2012-07-19 | 2012-07-19 09:49 | 2012-07-19 10:05 | NORDYNE - GR4GA-042K072X | 73 | -4.3 | Yes | Yes | 22.3 | 18.5 | 3.9 | 734CB5138F7C482DAA68C01E6298E1BA |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Fresno | CA | 93722-4506 |  | 2012-05-18 | 2012-05-18 14:48 | 2012-05-18 15:11 | GOODMAN - BGB024050-1 | 85 | 2.8 | Yes | Yes | 17.5 | 20.4 | -2.9 | AD2273C8543B440FBFF53066CA78CEC3 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Williams | CA | 95987-5103 |  | 2012-07-25 | 2012-07-25 09:51 | 2012-07-25 10:08 | PAYNE - PA10JA042-D | 85 | 6 | Yes | Yes | 17 | 18.8 | -1.8 | 57C2ABB1427640E79C4D97609B25B71F |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Stockton | CA | 95210-1247 |  | 2012-05-11 | 2012-05-11 09:49 | 2012-05-11 10:06 | PAYNE - UNK | 58 | 1.9 | Yes | Yes | 22.5 | 20.7 | 1.8 | 5138B814A0DD487DA88E89E66E651030 |  | R22 | Non-TXV |  | 3.276% | 0.96724 | 6.295% | [5 empty] | Non-TXV | 3.276%
Copperopolis | CA | 95228-0000 |  | 2012-07-17 | 2012-07-17 13:15 | 2012-07-17 13:32 | WESTINGHOUSE - FS5BD-030KA | 99 | -5.8 | Yes | Yes | 24.5 | 18.6 | 5.9 | 518F0311D7B14C398111CAEFD9765AA6 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Stockton | CA | 95212-3049 |  | 2012-05-17 | 2012-05-17 12:50 | 2012-05-17 13:10 | YORK - H2RC036S06HG | 83 | -5.9 | Yes | Yes | 18.5 | 20.4 | -1.9 | 49AD58F4AF6149D5B1F509F8B71365CA |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Stockton | CA | 95209-1242 |  | 2012-05-21 | 2012-05-21 11:41 | 2012-05-21 12:06 | WESTINGHOUSE - 1D030BEAON | 88 | 9.5 | Yes | Yes | 19.2 | 20.1 | -0.9 | 363C0E1BD97D405AB5F684933A55EA52 |  | R22 | Non-TXV |  | 10.8% | 0.89205 | 20.75% | [5 empty] | Non-TXV | 10.8%
Fresno | CA | 93722-4503 |  | 2012-06-01 | 2012-06-01 15:38 | 2012-06-01 15:59 | TAPPAN - N/A | 51 | 1.5 | Yes | Yes | 19.9 | 19 | 0.9 | 313B5171598B4A279CE6A68683F4DB03 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Yuba City | CA | 95991-1513 |  | 2012-07-12 | 2012-07-12 12:31 | 2012-07-12 12:50 | TEMPSTAR - PGAA24C1K4 | 66 | 11.1 | Yes | Yes | 17.3 | 20.2 | -2.9 | F64B746E80414F0C9A74523EF915BA0D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.82% | 0.83182 | 32.32% | [5 empty] | Non-TXV | 16.82%
Live Oak | CA | 95953-9501 |  | 2012-07-05 | 2012-07-05 08:32 | 2012-07-05 08:56 | RUUD - UAJCF3991-042JAS | 101 | -5.9 | Yes | Yes | 24 | 19.3 | 4.7 | 31BCCCDE18574168A1074A73FE1883E2 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Ripon | CA | 95366-9747 |  | 2012-06-22 | 2012-06-22 14:50 | 2012-06-22 15:12 | COPELAND - UNK | 56 | 5 | Yes | Yes | 19.5 | 20.2 | -0.6 | 6AA0A5EB03E0462CB678F3DF21D1729E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | Non-TXV | 8.929%
Los Banos | CA | 93635-3228 |  | 2012-05-11 | 2012-05-11 10:56 | 2012-05-11 11:14 | BRYANT - 582ANW024040AAAD | 53 | 4.1 | Yes | Yes | 27.2 | 21.3 | 5.9 | 1292C640A7174D5E98A276A91592DC2A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.736% | 0.92264 | 14.87% | [5 empty] | Non-TXV | 7.736%
Stockton | CA | 95210-3132 |  | 2012-06-11 | 2012-06-11 14:08 | 2012-06-11 14:08 | GOODMAN - UNK | 56 | 0 | Yes | Yes | 27.7 | 18.6 | 9.1 | 727504BCDDB348FE931FC8A804F787EA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atascadero | CA | 93422-4548 |  | 2012-07-11 | 2012-07-11 10:35 | 2012-07-11 10:58 | RHEEM - RACA-024ABQ | 24 | 17.5 | Yes | Yes | 21.9 | 22.9 | -1 | 2BAC0CA55D964CFD8207318044ED2F45 |  | R22 | Non-TXV |  | 72.92% | 0.27083 | 140.1% | [5 empty] | Non-TXV | 72.92%
Planada | CA | 95365-8046 |  | 2012-06-06 | 2012-06-06 15:53 | 2012-06-06 16:11 | GOODMAN - PGB030050-1 | 56 | 5.5 | Yes | Yes | 23.8 | 19.8 | 4 | 5FD0679CB87A498BBAD3AB0B596DEE56 |  | R22 | Non-TXV |  | 9.821% | 0.90179 | 18.87% | [5 empty] | Non-TXV | 9.821%
Stockton | CA | 95212-2202 |  | 2012-05-29 | 2012-05-29 13:21 | 2012-05-29 13:40 | OTHER - C1248CCD1VF | 137 | 9.5 | Yes | Yes | 23.5 | 20.4 | 3.1 | 787204AF7C2942578CF8D9339FB0CA0A |  | R22 | TXV |  | 6.934% | 0.93066 | 13.33% | [5 empty] | TXV | 6.934%
Stockton | CA | 95212-2202 |  | 2012-05-29 | 2012-05-29 13:32 | 2012-05-29 13:48 | FRESCHI - 22JO | 40 | 14.8 | Yes | Yes | 20.7 | 20.4 | 0.3 | 04AFB7DABE8E4CCEA139657518A92381 |  | R22 | Non-TXV |  | 37% | 0.63 | 71.11% | [5 empty] | Non-TXV | 37%
Los Banos | CA | 93635-3137 |  | 2012-05-09 | 2012-05-09 17:02 | 2012-05-09 17:21 | RUUD - UNK | 92 | 3.5 | Yes | Yes | 27.5 | 24.2 | 3.3 | 764884D04D354450A1EF9B8B9B89802F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.804% | 0.96196 | 7.311% | [5 empty] | Non-TXV | 3.804%
Yuba City | CA | 95991-5957 |  | 2012-06-14 | 2012-06-14 14:56 | 2012-06-14 15:14 | TRANE - RAUC302-A | 60 | 1.9 | Yes | Yes | 21 | 20.4 | 0.6 | F3A2D2F85A7F40519240846126601BB3 |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Live Oak | CA | 95953-2237 |  | 2012-05-24 | 2012-05-24 11:58 | 2012-05-24 11:58 | CARRIER - 48GS-0360690311-- | 71 | 0 | Yes | Yes | 21.7 | 20.6 | 1.2 | EF6F5467B1C94658BBC2EB0AE15196FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9583 |  | 2012-05-09 | 2012-05-09 10:28 | 2012-05-09 10:48 | GOODMAN - CKL36-1D | 72 | 2.2 | Yes | Yes | 20.2 | 18.7 | 1.5 | 826C3EFD01074288BE8B9B371329B989 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Gerber | CA | 96035-9669 |  | 2012-07-06 | 2012-07-06 10:21 | 2012-07-09 00:51 | COLEMAN - CCJF42S41S1 | 68 | 2.4 | Yes | Yes | 20.5 | 20.8 | -0.3 | 46DDAF0709C342D09263C2D943A53E23 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Merced | CA | 95341-6055 |  | 2012-05-09 | 2012-05-09 15:49 | 2012-05-09 16:07 | ARCO AIR - PGC024K060E | 54 | 1.7 | Yes | Yes | 20.8 | 22.5 | -1.7 | F1097B8B9D9241A6B08EFF225001459A |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Winton | CA | 95388-9537 |  | 2012-05-10 | 2012-05-10 11:30 | 2012-05-10 11:48 | LENNEX - NA | 82 | 2.5 | Yes | Yes | 18.5 | 20.4 | -1.9 | B0FB364D771B4577BE9C96EE3A453C91 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
El Nido | CA | 95317-9713 |  | 2012-07-14 | 2012-07-14 12:52 | 2012-07-14 12:52 | TEMPSTAR - N2A336AKB300 | 84 | 0 | Yes | Yes | 3.6 | 19 | -15.4 | 6B59024A3A64460D8A999DAB3596077E | Actual Subcooling cannot be negative. Please check entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1309 |  | 2012-05-08 | 2012-05-08 12:40 | 2012-05-08 13:02 | YORK - TCGD36S21S2HA | 63 | 1.9 | Yes | Yes | 20.1 | 19.3 | 0.8 | 20357BDDD89F4A7F8E44D6BDD88F28A0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Atwater | CA | 95301-3611 |  | 2012-05-14 | 2012-05-14 12:14 | 2012-05-14 12:38 | TRANE - YCC036F1M0BC | 83 | 2.5 | Yes | Yes | 23.1 | 19.1 | 4 | D9AA7B00B1B84795A39403E9CC18B09D |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Stockton | CA | 95205-5040 |  | 2012-05-21 | 2012-05-21 15:52 | 2012-05-21 16:12 | YORK - AC024M1021CG | 52 | 2.9 | Yes | Yes | 17.5 | 19.3 | -1.8 | F5645BAE583B41C6818CF0D73DE29927 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Stockton | CA | 95205-2800 |  | 2012-05-16 | 2012-05-16 17:50 | 2012-05-16 18:14 | OTHER - UNK | 58 | 2.9 | Yes | Yes | 19.5 | 21 | -1.5 | 7AA1F9FAB86D4080B19EA093CDC16E54 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95202-1418 |  | 2012-06-15 | 2012-06-15 16:13 | 2012-06-15 16:37 | GE - BTN936A100A0 | 144 | 16.2 | Yes | Yes | 17.5 | 19.2 | -1.7 | B61C7EAA60B54AE2A610431698B8C719 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Dos Palos | CA | 93620-2412 |  | 2012-05-15 | 2012-05-15 14:28 | 2012-05-15 14:28 | TRANE - TTB724A100A0 | 54 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | A1CC720CEE704959AE34FEF3EA330363 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4124 |  | 2012-05-10 | 2012-05-10 12:22 | 2012-05-10 12:41 | GOODMAN - PGB036050-1A | 60 | 1.8 | Yes | Yes | 25.7 | 19.9 | 5.8 | 2A4398E0D7FC46089D697DF492FCB64B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Madera | CA | 93638-0159 |  | 2012-06-12 | 2012-06-12 15:20 | 2012-06-12 15:47 | TRANE - YCY042G1M0AD | 85 | 2.5 | Yes | Yes | 22 | 21.9 | 0.1 | 21F5D888762445F9A53CDC7DDD7579A0 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Atascadero | CA | 93422-5838 |  | 2012-07-11 | 2012-07-11 09:14 | 2012-07-11 09:32 | BDP - 585GJ024040 | 54 | -3.2 | Yes | Yes | 24.4 | 18.9 | 5.5 | 616A72ABA7704045BEC21E143BB99619 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Merced | CA | 95348-3689 |  | 2012-05-17 | 2012-05-17 14:35 | 2012-05-17 15:01 | TRANE - BTD724A100B0 | 68 | 2.6 | Yes | Yes | 20.4 | 19.3 | 1.1 | 0051FE6092824915B1AF91FFC00BE879 |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Stockton | CA | 95205-4251 |  | 2012-05-29 | 2012-05-29 11:05 | 2012-05-29 11:21 | RHEEM - RAKA-060JAZ | 112 | 3.9 | Yes | Yes | 19.1 | 20.2 | -1.1 | 5A9A14090A424C488C73807A8807AFED |  | R22 | Non-TXV |  | 3.482% | 0.96518 | 6.692% | [5 empty] | Non-TXV | 3.482%
Chowchilla | CA | 93610-1906 |  | 2012-07-11 | 2012-07-11 13:30 | 2012-07-11 13:58 | HEIL - CA3018VKA3 | 68 | 3.2 | Yes | Yes | 16.7 | 17.1 | -0.4 | D5083DAA3AAC48B8988D841B1AE2B320 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Rocklin | CA | 95677-3165 |  | 2012-05-22 | 2012-05-22 12:25 | 2012-05-22 12:43 | CARRIER - UNK | 59 | 15.1 | Yes | Yes | 16.9 | 19.4 | -2.5 | BE2D0E813EA248D5982DECEE42466EA7 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 25.59% | 0.74407 | 49.18% | [5 empty] | Non-TXV | 25.59%
Grass Valley | CA | 95945-6347 |  | 2012-05-30 | 2012-05-30 13:10 | 2012-05-30 13:26 | BRYANT - 582ANW030060NAAD | 55 | 3.7 | Yes | Yes | 20 | 20.6 | -0.6 | DF86B31272B2484DB96BAF8A6AC43391 |  | R22 | Non-TXV |  | 6.727% | 0.93273 | 12.93% | [5 empty] | Non-TXV | 6.727%
Chowchilla | CA | 93610-1905 |  | 2012-07-11 | 2012-07-11 12:55 | 2012-07-11 13:16 | HEIL - CA3018VKA3 | 68 | -6.4 | Yes | Yes | 16.5 | 18 | -1.5 | 28310A3BF234488B9DFB6DF01804A2AD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Chowchilla | CA | 93610-1907 |  | 2012-07-12 | 2012-07-12 10:03 | 2012-07-12 10:29 | HEIL - CA3018VKA3 | 68 | 2.8 | Yes | Yes | 17.3 | 18.6 | -1.3 | 1F2CF856C9574B0FBB4B7D2CE521510B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fresno | CA | 93727-5531 |  | 2012-08-08 | 2012-08-08 10:29 | 2012-08-08 10:29 | WEATHER KING - 10AJA6001 | 132 | 0 | Yes | Yes | 23.7 | 20.2 | 3.5 | FEE5431CC66A4D1D810227869B32F594 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1537 |  | 2012-05-22 | 2012-05-22 11:05 | 2012-05-22 11:23 | PAYNE - N/A | 81 | 2.4 | Yes | Yes | 21.9 | 19.7 | 2.3 | E716A4C75553464795BCB49A9442DD85 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Merced | CA | 95348-3663 |  | 2012-05-31 | 2012-05-31 09:56 | 2012-05-31 10:13 | TRANE - 51D724A10093 | 62 | 3.6 | Yes | Yes | 19 | 19.9 | -0.9 | 9C586237A47B4C8EAC97F3D69F3B0B22 |  | R22 | Non-TXV |  | 5.806% | 0.94194 | 11.16% | [5 empty] | Non-TXV | 5.806%
Cameron Park | CA | 95682-9217 |  | 2012-05-31 | 2012-05-31 17:05 | 2012-05-31 17:22 | PAYNE - 541DJ030 | 102 | -9.6 | Yes | Yes | 19.7 | 20.4 | -0.7 | 3ED0F5A335D14A9DBA3652DCEE1BF8BD |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Clovis | CA | 93612-2367 |  | 2012-05-22 | 2012-05-22 12:27 | 2012-05-22 12:45 | YORK - DCYZ-F024N045 | 60 | 2 | Yes | Yes | 19.1 | 21.2 | -2.1 | 5F4C509C6AD0480BBC07FC83926A4C10 |  | R410A | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95207-7522 |  | 2012-06-01 | 2012-06-01 16:28 | 2012-06-01 16:44 | HEIL - PGCO30K060E---- | 52 | 8.8 | Yes | Yes | 22.3 | 22.6 | -0.3 | 2D29B2901D6542A1BA3687E7DD01521B |  | R22 | Non-TXV |  | 16.92% | 0.83077 | 32.52% | [5 empty] | Non-TXV | 16.92%
Chowchilla | CA | 93610-1907 |  | 2012-07-11 | 2012-07-11 14:43 | 2012-07-11 14:43 | HEIL - CA3018VKA3 | 68 | 10 | Yes | Yes | 15.3 | 10.8 | 4.5 | AEB687CEB86A425BAEAAAD0536DAAD82 | Add refrigerant: 10 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.71% | 0.85294 | 28.26% | [5 empty] | Non-TXV | 14.71%
Manteca | CA | 95336-5032 |  | 2012-05-08 | 2012-05-08 13:55 | 2012-05-08 14:15 | COMFORT MAKER - N2A336AKA200 | 88 | 3 | Yes | Yes | 25.4 | 22.9 | 2.5 | 401B2548D05B49898A06FC5723B6AC32 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Marysville | CA | 95901-4137 |  | 2012-06-07 | 2012-06-07 11:07 | 2012-06-07 11:24 | ICP - PGHE36G080E | 132 | 4.3 | Yes | Yes | 19 | 19.3 | -0.3 | C49820340A5F4ADD8A03501CD4CDF0C3 |  | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.26% | [5 empty] | Non-TXV | 3.258%
Olivehurst | CA | 95961-0000 |  | 2012-05-21 | 2012-05-21 15:49 | 2012-05-21 15:49 | TRANE - YCC024F1L0BJ | 66 | 0 | Yes | Yes | 24.1 | 20.4 | 3.7 | 2885BD42A5174B40971023D616E050AA | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-7321 |  | 2012-05-17 | 2012-05-17 11:50 | 2012-05-17 12:12 | CARRIER - 38EN024310 | 56 | 3.1 | Yes | Yes | 16.8 | 19.3 | -2.5 | 62426F46EE6F423CA4755794FDB6393E |  | R22 | Non-TXV |  | 5.536% | 0.94464 | 10.64% | [5 empty] | Non-TXV | 5.536%
Merced | CA | 95348-3666 |  | 2012-07-09 | 2012-07-09 12:35 | 2012-07-09 12:35 | TRANE - BTD724A100B0 | 69 | 0 | Yes | Yes | 2.6 | 19.7 | -17.1 | 69BAAACAA0584310B5DFE33D2380936A | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Ripon | CA | 95366-2845 |  | 2012-05-17 | 2012-05-17 15:23 | 2012-05-17 15:42 | GOODMAN - PGB030075-1 REV A | 56 | 2.8 | Yes | Yes | 20.1 | 20.8 | -0.7 | 3D7AC82A5B23488F8834B6155D297F20 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95205-2780 |  | 2012-05-14 | 2012-05-14 13:33 | 2012-05-14 13:55 | DAY & NIGHT - 585HJ018040 | 61 | 4.2 | Yes | Yes | 16.6 | 19.3 | -2.7 | 6EA071EA162440C9B2526F40A42A7EC9 |  | R22 | Non-TXV |  | 6.885% | 0.93115 | 13.23% | [5 empty] | Non-TXV | 6.885%
Manteca | CA | 95336-5015 |  | 2012-06-11 | 2012-06-11 11:37 | 2012-06-11 12:05 | RHEEM - RAKA-048JAZ | 103 | 3.1 | Yes | Yes | 19.7 | 20 | -0.2 | DAE8DE35A1974E7C922FFCE1379D2936 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Merced | CA | 95348-3764 |  | 2012-05-31 | 2012-05-31 10:24 | 2012-05-31 10:40 | TRANE - BTD724A10080 | 66 | 4.1 | Yes | Yes | 20.3 | 20.4 | -0.1 | 1DEC8BF93F184BC5A3F687BF27651495 |  | R22 | Non-TXV |  | 6.212% | 0.93788 | 11.94% | [5 empty] | Non-TXV | 6.212%
Stockton | CA | 95212-3207 |  | 2012-05-29 | 2012-05-29 11:30 | 2012-05-29 11:47 | GOODMAN - CLJ48-1 | 117 | 4.1 | Yes | Yes | 20 | 20.4 | -0.4 | 5E36A1F9BB7E44D9A8AE3F484C3AC334 |  | R22 | Non-TXV |  | 3.504% | 0.96496 | 6.734% | [5 empty] | Non-TXV | 3.504%
Fresno | CA | 93722-4429 |  | 2012-05-18 | 2012-05-18 12:30 | 2012-05-18 12:49 | BDP COMPANY - 585A024055YACR | 60 | 3.1 | Yes | Yes | 19.5 | 20.4 | -0.9 | 124007A315F44A68BB7145DC97D3B4E8 |  | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Merced | CA | 95348-3691 |  | 2012-05-17 | 2012-05-17 12:36 | 2012-05-17 13:02 | TRANE - BTD7244100B0 | 68 | 9.6 | Yes | Yes | 17.7 | 20.2 | -2.5 | FF2A876BC6A148B3907F012122586D19 |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Marysville | CA | 95901-4140 |  | 2012-07-02 | 2012-07-02 11:21 | 2012-07-02 11:21 | LENNOX - 12GCS036X-75-3PB | 110 | 0 | Yes | Yes | 22 | 16.1 | 5.9 | 52BED4669F3C4163A0CF9E4919644069 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-5422 |  | 2012-07-12 | 2012-07-12 14:25 | 2012-07-12 14:44 | YORK - H4DH018S06A | 78 | 2.4 | Yes | Yes | 19 | 19.2 | -0.2 | 41F01996A05D4470AD71FF555E7CCABE |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Atwater | CA | 95301-3932 |  | 2012-06-14 | 2012-06-14 11:32 | 2012-06-14 11:58 | PAYNE - PY1PNB024060AAAA | 55 | 2.3 | Yes | Yes | 19.9 | 18.8 | 1.1 | 51BD41D2D7CF4A338F87AB10CE6740FE |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
Merced | CA | 95341-6055 |  | 2012-05-09 | 2012-05-09 15:26 | 2012-05-09 15:45 | ARCO AIR - PGC024KO60E | 54 | 1.6 | Yes | Yes | 20.4 | 21.8 | -1.4 | 53480A36A81347318C5295A07F2F571B |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95219-3230 |  | 2012-06-11 | 2012-06-11 08:58 | 2012-06-11 09:33 | DAY & NIGHT - 30DNR-108C | 68 | 3.6 | Yes | Yes | 18.9 | 20.4 | -1.5 | 96220112B2244E129C9B6B192F2F0E91 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Olivehurst | CA | 95961-4522 |  | 2012-07-03 | 2012-07-03 13:54 | 2012-07-03 14:21 | ARMSTRONG - PGE10B24D050LA | 52 | 6.1 | Yes | Yes | 15.7 | 18.5 | -2.8 | 3ED69B4960E14C6BB88E658679C896F9 |  | R22 | Non-TXV |  | 11.73% | 0.88269 | 22.54% | [5 empty] | Non-TXV | 11.73%
Stockton | CA | 95207-6958 |  | 2012-06-20 | 2012-06-20 09:22 | 2012-06-20 09:42 | GOODMAN - CE25-1EB | 66 | 6.2 | Yes | Yes | 20.1 | 23.1 | -3 | 1320C08C096E4C9DB27098AE0747601D |  | R22 | Non-TXV |  | 9.394% | 0.90606 | 18.05% | [5 empty] | Non-TXV | 9.394%
Clovis | CA | 93612-3520 |  | 2012-05-30 | 2012-05-30 13:47 | 2012-05-30 14:08 | RHEEM - RRNA-B030JK06K | 73 | 2.4 | Yes | Yes | 17.3 | 18.7 | -1.4 | 9E3B40BD3A664EF88A5577D8A93386EF |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Merced | CA | 95340-3907 |  | 2012-05-16 | 2012-05-16 11:54 | 2012-05-16 12:22 | GOODMAN - GPG1348090M41AD | 125 | 5.1 | Yes | Yes | 23.4 | 19.3 | 4.1 | 2F6391570C784E399BB02472586AB2FC |  | R22 | Non-TXV |  | 4.08% | 0.9592 | 7.841% | [5 empty] | Non-TXV | 4.08%
Stockton | CA | 95209-1510 |  | 2012-06-25 | 2012-06-25 12:48 | 2012-06-25 13:05 | OTHER - CA9048VKD2 | 164 | 17.7 | Yes | Yes | 23.3 | 19.9 | 3.4 | 172437CB14004F90ACEC90B05D68AB21 |  | R22 | Non-TXV |  | 10.79% | 0.89207 | 20.74% | [5 empty] | Non-TXV | 10.79%
Fresno | CA | 93711-1447 |  | 2012-07-19 | 2012-07-19 16:33 | 2012-07-19 16:50 | OTHER - D2NP036N05606A | 106 | 3.1 | Yes | Yes | 19.7 | 20.4 | -0.7 | 546C8EF34DF04529A50C59DCD09FC2B7 |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
Dos Palos | CA | 93620-2250 |  | 2012-05-15 | 2012-05-15 15:17 | 2012-05-15 15:44 | GOODMAN - CKJ30-1B | 92 | -5.4 | Yes | Yes | 21.5 | 19.3 | 2.2 | 6BFAA9F1CC5342A7A62FC2DA3BBCF296 |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Fresno | CA | 93711-2608 |  | 2012-08-10 | 2012-08-10 19:18 | 2012-08-10 19:42 | GUARDIAN - RRNA-B036JK06X | 83 | 3.3 | Yes | Yes | 17.8 | 20.2 | -2.4 | D52D90C0A0C4469FB062D515BAEAC74D |  | R22 | Non-TXV |  | 3.976% | 0.96024 | 7.641% | [5 empty] | Non-TXV | 3.976%
Stockton | CA | 95207-4211 |  | 2012-06-08 | 2012-06-08 10:04 | 2012-06-08 10:21 | RHEEM - RRCC-030JAS | 58 | 6.8 | Yes | Yes | 18.9 | 21 | -2.1 | 402904E5521643F8955C21D87C138FBE |  | R22 | Non-TXV |  | 11.72% | 0.88276 | 22.53% | [5 empty] | Non-TXV | 11.72%
Stockton | CA | 95206-6089 |  | 2012-05-30 | 2012-05-30 15:22 | 2012-05-30 15:39 | CARRIER - 38BRC048350 | 165 | 7.6 | Yes | Yes | 18.4 | 20.3 | -1.9 | 22648FA4443641A8A3BF45C1EB822780 |  | R22 | TXV |  | 4.606% | 0.95394 | 8.852% | [5 empty] | TXV | 4.606%
Merced | CA | 95340-3561 |  | 2012-05-21 | 2012-05-21 13:54 | 2012-05-21 14:22 | AMANA - PGD30C0702X | 74 | 5.7 | Yes | Yes | 25.9 | 21.3 | 4.6 | FDE93B70DD304A57825FCBE446D8983B |  | R22 | Non-TXV |  | 7.703% | 0.92297 | 14.8% | [5 empty] | Non-TXV | 7.703%
Fresno | CA | 93711-1460 |  | 2012-08-10 | 2012-08-10 11:53 | 2012-08-10 12:48 | PAYNE - UNK | 67 | 4.1 | Yes | Yes | 18.9 | 20.7 | -1.8 | 3E8A0318DB7443248CB5E7A4DA8AD618 |  | R22 | Non-TXV |  | 6.119% | 0.93881 | 11.76% | [5 empty] | Non-TXV | 6.119%
Fresno | CA | 93711-0732 |  | 2012-08-09 | 2012-08-09 12:19 | 2012-08-09 12:42 | GOODMAN - PBG036075-1A | 60 | 2.4 | Yes | Yes | 15.8 | 18.6 | -2.8 | 3C0F1FDEC66544E1B16DDE59343ED7F4 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95205-6407 |  | 2012-05-21 | 2012-05-21 17:25 | 2012-05-21 17:43 | CARRIER - 48SDN024040311 | 89 | 6 | Yes | Yes | 21.8 | 22.4 | -0.6 | 0D2BA5BC696B422F879025796AE441ED |  | R22 | Non-TXV |  | 6.742% | 0.93258 | 12.96% | [5 empty] | Non-TXV | 6.742%
Winton | CA | 95388-9214 |  | 2012-05-18 | 2012-05-18 13:16 | 2012-05-18 13:38 | TRANE - TT07304100 | 95 | 4.3 | Yes | Yes | 21.1 | 19.9 | 1.2 | C3741CEA485A4868804E0D9161F8D71A |  | R22 | Non-TXV |  | 4.526% | 0.95474 | 8.699% | [5 empty] | Non-TXV | 4.526%
Stockton | CA | 95205-4633 |  | 2012-05-15 | 2012-05-15 15:14 | 2012-05-15 15:37 | RHEEM - RRNL-B036JK08X | 93 | 3 | Yes | Yes | 19.9 | 18.5 | 1.4 | 5AED5ACE6D60447DA9F0CEF008D41CB4 |  | R410A | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Stockton | CA | 95205-2767 |  | 2012-05-14 | 2012-05-14 12:28 | 2012-05-14 12:52 | YORK - D1NP036N05606 | 108 | 3.4 | Yes | Yes | 16.5 | 19 | -2.5 | B80D54E820264F63BF2A5D069B6F920B |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Fresno | CA | 93711-2110 |  | 2012-05-24 | 2012-05-24 14:14 | 2012-05-24 16:50 | PAYNE - PA12NA042-B | 101 | 3.7 | Yes | Yes | 22.5 | 20.4 | 2.1 | 853D6B99923D41A7BE3FAD3388346253 |  | R22 | TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | TXV | 3.663%
Fresno | CA | 93722-4405 |  | 2012-05-23 | 2012-05-23 11:09 | 2012-05-23 11:38 | GOODMAN - PGB024050-1 | 54 | 1.6 | Yes | Yes | 22.8 | 21.4 | 1.4 | D68C5115E5294B40947DA90971B3EDBE |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93710-7021 |  | 2012-05-24 | 2012-05-24 12:15 | 2012-05-24 12:32 | AMERICAN STANDARD - YCY030F1M0AB | 148 | 4.4 | Yes | Yes | 24.5 | 21 | 3.5 | C2B3AE9792164614A7992211A02AB542 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Clovis | CA | 93612-3666 |  | 2012-06-14 | 2012-06-14 09:25 | 2012-06-14 09:25 | GOODMAN - CKL181D | 83 | 0 | Yes | Yes | 23 | 21 | 2 | 848F08E4512E4BCC96B787701BEA03C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4421 |  | 2012-06-07 | 2012-06-07 15:25 | 2012-06-07 15:49 | PAYNE - 585A024055YAL | 54 | 2.2 | Yes | Yes | 20 | 20.4 | -0.4 | 3777CC0D553E4AE8B4C7D58D24B8A7E6 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Los Banos | CA | 93635-3050 |  | 2012-05-29 | 2012-05-29 18:00 | 2012-05-29 18:18 | CARRIER - 38CK030300 | 83 | 12.4 | Yes | Yes | 29.8 | 24.2 | 5.6 | C143F75BA33C419695C4BBC3F9AB1314 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.94% | 0.8506 | 28.71% | [5 empty] | Non-TXV | 14.94%
Stockton | CA | 95207-3869 |  | 2012-06-19 | 2012-06-19 12:05 | 2012-06-19 12:27 | HEIL - HAC060AKA | 131 | 8 | Yes | Yes | 26.9 | 23.4 | 3.5 | 4628BA377512447E8B27EBB51A0C590A |  | R22 | Non-TXV |  | 6.107% | 0.93893 | 11.74% | [5 empty] | Non-TXV | 6.107%
Manteca | CA | 95336-4021 |  | 2012-05-08 | 2012-05-08 12:03 | 2012-05-08 12:20 | GOODMAN - UNK | 92 | 2.8 | Yes | Yes | 21.3 | 19.1 | 2.2 | D1AFC5A9415D48AC9BD07CFF9C1526A8 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Dos Palos | CA | 93620-2047 |  | 2012-06-08 | 2012-06-08 10:42 | 2012-06-08 11:03 | OTHER - 3TAOH1 | 63 | 4 | Yes | Yes | 24.1 | 19.1 | 5 | 1C0BAB29E72E419E83DCC255D39E8958 |  | R22 | Non-TXV |  | 6.349% | 0.93651 | 12.2% | [5 empty] | Non-TXV | 6.349%
Oakdale | CA | 95361-8028 |  | 2012-05-24 | 2012-05-24 15:53 | 2012-05-24 16:13 | HEIL - CA3036VKA1 | 94 | 3.1 | Yes | Yes | 20.2 | 21.4 | -1.2 | ACCFF748365949BB86D74F0EBA9FB7A4 |  | R22 | Non-TXV |  | 3.298% | 0.96702 | 6.338% | [5 empty] | Non-TXV | 3.298%
Livingston | CA | 95334-1746 |  | 2012-05-22 | 2012-05-22 12:53 | 2012-05-22 13:10 | RHEEM - RRKA-0A030JK06X | 54 | 6.7 | Yes | Yes | 21.2 | 19.9 | 1.3 | 74FFE4F2A4C04837BB8D596142476404 |  | R22 | Non-TXV |  | 12.41% | 0.87593 | 23.84% | [5 empty] | Non-TXV | 12.41%
Fresno | CA | 93710-5330 |  | 2012-06-15 | 2012-06-15 13:29 | 2012-06-15 13:51 | AMERICAN STANDARD - YCY036G1M0AD | 129 | 3.8 | Yes | Yes | 22.4 | 20.2 | 2.2 | 021159711BBC4530909CB39DA2856348 |  | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.661% | [5 empty] | Non-TXV | 2.946%
Livingston | CA | 95334-1752 |  | 2012-05-22 | 2012-05-22 13:12 | 2012-05-22 13:30 | RHEEM - UNK | 57 | 7.2 | Yes | Yes | 24 | 21.5 | 2.5 | 65FC62F349E44236BDE964A830E52A5A |  | R22 | Non-TXV |  | 12.63% | 0.87368 | 24.28% | [5 empty] | Non-TXV | 12.63%
Livingston | CA | 95334-1752 |  | 2012-05-22 | 2012-05-22 13:41 | 2012-05-22 13:59 | RHEEM - UNK | 85 | 4 | Yes | Yes | 20.7 | 21.4 | -0.7 | A09425EB1D7B4B6EAC28DC4DE900385F |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Stockton | CA | 95206-3825 |  | 2012-05-23 | 2012-05-23 13:50 | 2012-05-23 14:08 | RHEEM - RRKA0A036JK06X | 62 | 3.9 | Yes | Yes | 19.8 | 21.3 | -1.5 | 2053CFC3063C4B63A41FB07504BAEB8F |  | R22 | Non-TXV |  | 6.29% | 0.9371 | 12.09% | [5 empty] | Non-TXV | 6.29%
Livingston | CA | 95334-1738 |  | 2012-05-08 | 2012-05-08 16:16 | 2012-05-08 16:34 | CARRIER - 38CKB042-301 | 85 | 7.1 | Yes | Yes | 21.3 | 21.7 | -0.4 | A988C2483C0946068F4CCFBB8F2B4A86 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.353% | 0.91647 | 16.05% | [5 empty] | Non-TXV | 8.353%
Stockton | CA | 95205-2614 |  | 2012-05-17 | 2012-05-17 14:39 | 2012-05-17 15:01 | AMANA - PGD24C0702E | 74 | 4.1 | Yes | Yes | 20.4 | 20.4 | 0 | 80BFC407A33D44B4B5DBBA944D8160E1 |  | R22 | Non-TXV |  | 5.541% | 0.94459 | 10.65% | [5 empty] | Non-TXV | 5.541%
Atwater | CA | 95301-2014 |  | 2012-05-11 | 2012-05-11 15:19 | 2012-05-11 15:37 | RHEEM - RAKA-048JAZ | 105 | 11.2 | Yes | Yes | 19.7 | 20.9 | -1.2 | 71E577E6DBEA4880AB224016D1A5107D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Merced | CA | 95341-8813 |  | 2012-05-29 | 2012-05-29 10:17 | 2012-05-29 10:50 | LENNOX - 13ACD03623002 | 111 | 14.7 | Yes | Yes | 25.4 | 19.4 | 6 | 624F1084FE634DC7BC8D61189DE8BF37 |  | R22 | Non-TXV |  | 13.24% | 0.86757 | 25.45% | [5 empty] | Non-TXV | 13.24%
Livingston | CA | 95334-1874 |  | 2012-05-29 | 2012-05-29 09:43 | 2012-05-29 10:01 | CARRIER - 591ANX036000AAAA | 84 | 3.5 | Yes | Yes | 21.9 | 18.2 | 3.7 | 0B89FDB29D93429B9A7B61555B8BF1D9 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Merced | CA | 95341-5771 |  | 2012-06-06 | 2012-06-06 17:45 | 2012-06-06 18:15 | YORK - D2NP024N05606A | 100 | 12.1 | Yes | Yes | 28.4 | 24.7 | 3.7 | 101E640952494288A15A5B9A31B6A25B |  | R22 | Non-TXV |  | 12.1% | 0.879 | 23.25% | [5 empty] | Non-TXV | 12.1%
Los Banos | CA | 93635-3056 |  | 2012-06-06 | 2012-06-06 09:42 | 2012-06-06 10:03 | CARRIER - 38CKC030340 | 67 | -2.8 | Yes | Yes | 18.2 | 20.1 | -1.9 | 6FD4DA6074864F388203E49471B094AC |  | R22 | TXV |  | -4.179% | 1.0418 | 1.17% |  |  |  |  | TXV |  |  | -4.179%
Merced | CA | 95340-0932 |  | 2012-05-18 | 2012-05-18 16:29 | 2012-05-18 16:48 | RHEEM - RRNAB030JK08X | 72 | 9.6 | Yes | Yes | 22 | 19 | 3 | BA5A3E75F2664BC7BEC235A1DF85570C |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Los Banos | CA | 93635-3067 |  | 2012-05-08 | 2012-05-08 14:22 | 2012-05-08 14:46 | BRYANT - 38CKXO24340 | 61 | 3.3 | Yes | Yes | 27 | 25.2 | 1.8 | ABD30C1E907C4AB087CC3A876D3871BF | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.41% | 0.9459 | 10.4% | [5 empty] | Non-TXV | 5.41%
Winton | CA | 95388-9435 |  | 2012-05-07 | 2012-05-07 12:41 | 2012-05-07 12:41 | NA - 13A0AA2A01 | 67 | 0 | Yes | Yes | 18.9 | 19.7 | -0.8 | 24AE417E140B4048A673FB9B7D8C9FE4 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-7124 |  | 2012-07-03 | 2012-07-03 11:34 | 2012-07-03 11:58 | OTHER - 38CK042340 | 80 | 5.6 | Yes | Yes | 18.7 | 19.9 | -1.2 | F674FB97B1CF4AF68E9F979F4642055E |  | R22 | TXV |  | 7% | 0.93 | 13.45% | [5 empty] | TXV | 7%
Atwater | CA | 95301-4838 |  | 2012-05-18 | 2012-05-18 09:44 | 2012-05-18 10:10 | BDP - 561CJ0300-C | 85 | 2.5 | Yes | Yes | 19.8 | 21.7 | -1.9 | 7A7839CAE8C94050B64F568A8BB875C3 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Los Banos | CA | 93635-8805 |  | 2012-05-18 | 2012-05-18 14:04 | 2012-05-18 14:54 | BRYANT - 561CJ036-F | 70 | 6.1 | Yes | Yes | 21 | 19.5 | 1.5 | 8B41885BC00543C495A59D45460BFF14 |  | R22 | Non-TXV |  | 8.714% | 0.91286 | 16.75% | [5 empty] | Non-TXV | 8.714%
Los Banos | CA | 93635-3263 |  | 2012-05-11 | 2012-05-11 13:07 | 2012-05-11 13:27 | DAY AND NIGHT - UNK | 78 | 5.7 | Yes | Yes | 26.5 | 23.2 | 3.3 | CE76B4D535A04657B6333D02EA70A253 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.308% | 0.92692 | 14.04% | [5 empty] | Non-TXV | 7.308%
Stockton | CA | 95207-5902 |  | 2012-06-20 | 2012-06-20 10:27 | 2012-06-20 10:45 | PAYNE - UNK | 96 | 12.4 | Yes | Yes | 24.3 | 21 | 3.3 | 69AC43779FAE42CA9AA7F77E107E979B |  | R22 | Non-TXV |  | 12.92% | 0.87083 | 24.82% | [5 empty] | Non-TXV | 12.92%
Stockton | CA | 95210-1237 |  | 2012-05-18 | 2012-05-18 10:23 | 2012-05-18 10:45 | RHEEM - RRKA-A024JK06X | 50 | -2.9 | Yes | Yes | 21.4 | 19.7 | 1.7 | ED55A56665E34034AAB16F4FA0C2F22A |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Fresno | CA | 93720-2210 |  | 2012-07-18 | 2012-07-18 11:15 | 2012-07-18 17:18 | RHEEM - RRPLB048JK08X | 89 | 2.7 | Yes | Yes | 19.5 | 19.9 | -0.4 | 44CC941DEF6D4CB19C9A7DE8DB6B08A8 |  | R410A | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Stockton | CA | 95210-1237 |  | 2012-05-18 | 2012-05-18 10:49 | 2012-05-18 11:18 | RHEEM - RRKA-A024JK06X | 50 | -3.5 | Yes | Yes | 21.8 | 20.4 | 1.4 | 0753502B0E62411D920E230580DAA1F9 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Planada | CA | 95365-8045 |  | 2012-07-02 | 2012-07-02 13:47 | 2012-07-02 14:12 | CARRIER - 50YQ024310 | 84 | -5.9 | Yes | Yes | 21.5 | 17.6 | 3.9 | AC8CCE868DC6423890F8D84A30825631 |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Yuba City | CA | 95993-8262 |  | 2012-05-21 | 2012-05-21 12:50 | 2012-05-21 12:50 | GOODMAN - UNK | 110 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | AFEFE885F7414821A0743E6C5A956FFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-3912 |  | 2012-05-24 | 2012-05-24 11:07 | 2012-05-24 11:07 | PAYNE - NAC030AKA1 | 82 | 0 | Yes | Yes | 18.8 | 21 | -2.2 | 5E49D9C33BBB400893A94A44952C4302 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5424 |  | 2012-07-19 | 2012-07-19 15:19 | 2012-07-19 15:40 | OTHER - N/A | 54 | 1.6 | Yes | Yes | 19.1 | 19.3 | -0.2 | 45E6A18341B0431FBAAB4464C469C562 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95212-3829 |  | 2012-05-22 | 2012-05-22 15:16 | 2012-05-22 15:33 | YORK - H1RA042S06G | 84 | 6.7 | Yes | Yes | 18.5 | 19.8 | -1.3 | 1BC2222A814D481494F9B92662BE6C35 |  | R22 | TXV |  | 7.976% | 0.92024 | 15.33% | [5 empty] | TXV | 7.976%
Stockton | CA | 95209-2732 |  | 2012-05-21 | 2012-05-21 09:56 | 2012-05-21 10:16 | KENMORE - TCA236AKA4 | 113 | 5.8 | Yes | Yes | 20.8 | 19.9 | 0.9 | 61C8439E1FDF4CC1B1DDC68CEC7AC442 |  | R22 | Non-TXV |  | 5.133% | 0.94867 | 9.864% | [5 empty] | Non-TXV | 5.133%
Dinuba | CA | 93618-2936 |  | 2012-05-23 | 2012-05-23 16:32 | 2012-05-23 17:04 | ICP - GPC036K060F | 68 | 3.5 | Yes | Yes | 20.2 | 20.9 | -0.7 | 00ED647BFB1E47A88B308898FC45E9A7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.147% | 0.94853 | 9.892% | [5 empty] | Non-TXV | 5.147%
Atwater | CA | 95301-4032 |  | 2012-07-02 | 2012-07-02 09:49 | 2012-07-02 10:05 | TRANE - BTX72AAT00B0 | 136 | 4.5 | Yes | Yes | 22.2 | 20.1 | 2.1 | C71687EE7AA4492F912781001E6C544F |  | R22 | Non-TXV |  | 3.309% | 0.96691 | 6.359% | [5 empty] | Non-TXV | 3.309%
Lodi | CA | 95240-7336 |  | 2012-06-25 | 2012-06-25 11:18 | 2012-06-25 11:18 | CARRIER - 50Y0036300 | 82 | 0 | Yes | Yes | 17.4 | 20 | -2.6 | D5CEEBA28CAE48FC9AFE80AB34FDDB63 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3704 |  | 2012-05-23 | 2012-05-23 17:02 | 2012-05-23 17:24 | NORDYNE - JS3BA-024KA | 64 | 2.1 | Yes | Yes | 20.1 | 19.3 | 0.8 | DBACBE0593894973B8DD4834AA202371 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Auburn | CA | 95603-3738 |  | 2012-05-18 | 2012-05-18 13:34 | 2012-05-18 13:58 | - 7B0023B100A1 | 54 | 5.2 | Yes | Yes | 20 | 19.3 | 0.7 | FB1E8F7412A447C28BCD6A300A1242B1 |  | R22 | Non-TXV |  | 9.63% | 0.9037 | 18.51% | [5 empty] | Non-TXV | 9.63%
Fresno | CA | 93727-1924 |  | 2012-05-21 | 2012-05-21 11:34 | 2012-05-21 11:34 | YORK - D1NH030N05606C | 73 | 0 | Yes | Yes | 25.9 | 20.2 | 5.7 | 2F6D71C1D9B148D0A488A72A3CC4E597 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1924 |  | 2012-05-21 | 2012-05-21 11:49 | 2012-05-21 12:45 | YORK - D1NP036N05606A | 108 | 3.2 | Yes | Yes | 25.5 | 20.1 | 5.5 | 4F7D489C9E58427B9EBAC6B55855C587 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93711-2109 |  | 2012-08-10 | 2012-08-10 19:14 | 2012-08-10 19:14 | ALLEGIANCE - 2A7A030481A1000AA | 142 | 0 | Yes | Yes | 18.3 | 20.4 | -2.1 | EB1991DA17254693BC4CED1AEDF79C30 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2618 |  | 2012-08-14 | 2012-08-14 20:29 | 2012-08-14 20:45 | DAY & NIGHT - UNK | 66 | 3.1 | Yes | Yes | 17.8 | 20.4 | -2.6 | 608C0FB196B442D6AC11E81F9A14F067 |  | R22 | Non-TXV |  | 4.697% | 0.95303 | 9.027% | [5 empty] | Non-TXV | 4.697%
Rocklin | CA | 95677-3650 |  | 2012-06-12 | 2012-06-12 12:11 | 2012-06-12 12:27 | CARRIER - 540JJ018 | 83 | 12 | Yes | Yes | 17.7 | 18 | -0.2 | 5F70CEE93D0C453582C6CF7E39C2AC0F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.46% | 0.85542 | 27.78% | [5 empty] | Non-TXV | 14.46%
Fresno | CA | 93710-3701 |  | 2012-08-07 | 2012-08-07 17:58 | 2012-08-07 18:22 | PAYNE - 591ANWYO42-B | 112 | 3.4 | Yes | Yes | 19.1 | 20.4 | -1.3 | 562BF6E6830E4E56BA45BC6BC4CDDBFA |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Winton | CA | 95388-9710 |  | 2012-05-18 | 2012-05-18 10:20 | 2012-05-18 10:38 | GOODMAN - PGB024050-1 | 54 | 3.5 | Yes | Yes | 20.2 | 21 | -0.8 | 0931BE076CA844C69510C98007BB5FC6 |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Paso Robles | CA | 93446-4205 |  | 2012-07-11 | 2012-07-11 13:48 | 2012-07-11 14:05 | WHIRLPOOL - NCABA30VB02 | 44 | 1.4 | Yes | Yes | 18.4 | 20.8 | -2.4 | 85D1FC9619DB45F7B26219C5389087CC |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Oroville | CA | 95966-5432 |  | 2012-07-18 | 2012-07-18 10:11 | 2012-07-18 10:44 | AMERICAN STANDARD - YCP036F1MOAA | 109 | 4.8 | Yes | Yes | 22.8 | 22.8 | 0 | F17EE4DC4C014A678DF1B0123FD9B0C1 |  | R22 | Non-TXV |  | 4.404% | 0.95596 | 8.463% | [5 empty] | Non-TXV | 4.404%
Fresno | CA | 93710-7115 |  | 2012-08-09 | 2012-08-09 17:34 | 2012-08-09 19:55 | YORK - UN K | 67 | 3 | Yes | Yes | 21 | 20.4 | 0.6 | 88FE210788A34286B3115FCABFED6839 |  | R22 | Non-TXV |  | 4.478% | 0.95522 | 8.605% | [5 empty] | Non-TXV | 4.478%
Stockton | CA | 95206-2143 |  | 2012-06-08 | 2012-06-08 14:56 | 2012-06-08 15:17 | OTHER - PGE10B42D075LA-3A | 73 | 5.3 | Yes | Yes | 17.2 | 19.9 | -2.7 | 4C2C6525CF774FC79C99CC20B3D3A456 |  | R22 | Non-TXV |  | 7.26% | 0.9274 | 13.95% | [5 empty] | Non-TXV | 7.26%
Atwater | CA | 95301-9666 |  | 2012-05-22 | 2012-05-22 12:06 | 2012-05-22 12:25 | GOODMAN - GPG13480901AC | 145 | 4.4 | Yes | Yes | 25.6 | 19.9 | 5.7 | 374A80342BF74CA4AF2650325C02C999 |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.832% | [5 empty] | Non-TXV | 3.034%
Tracy | CA | 95377-5624 |  | 2012-06-25 | 2012-06-25 11:18 | 2012-06-25 11:39 | GOODMAN - CKJ36-1AB | 97 | 2.9 | Yes | Yes | 19.3 | 19.3 | 0 | BDDD79B543564315ADBDACC26CCFB2B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Merced | CA | 95341-7016 |  | 2012-05-30 | 2012-05-30 11:37 | 2012-05-30 11:57 | BRYANT - 582ANW036060NBAF | 68 | 11.1 | Yes | Yes | 21.2 | 19.8 | 1.4 | ED2EBFB7E0F44E089591E8CC0ED56EB1 |  | R22 | Non-TXV |  | 16.32% | 0.83676 | 31.37% | [5 empty] | Non-TXV | 16.32%
Los Banos | CA | 93635-8522 |  | 2012-06-13 | 2012-06-13 11:54 | 2012-06-13 12:23 | AMERICAN STANDARD - WCHO36B100CA | 152 | 5.6 | Yes | Yes | 19 | 19.3 | -0.3 | D071AC1F8D0D42DFBDE76741AC79E76D |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Winton | CA | 95388-9243 |  | 2012-05-29 | 2012-05-29 14:05 | 2012-05-29 14:21 | GOODMAN - CK24-18 | 71 | 6.3 | Yes | Yes | 20.8 | 20.4 | 0.4 | 44858991960243F188569EB665C2B4A5 |  | R22 | Non-TXV |  | 8.873% | 0.91127 | 17.05% | [5 empty] | Non-TXV | 8.873%
Merced | CA | 95340-2945 |  | 2012-05-21 | 2012-05-21 11:29 | 2012-05-21 11:54 | KENMORE - TCA236AKAT | 113 | -6.6 | Yes | Yes | 15.8 | 17.9 | -2.1 | 93FFDA7AC2064D46BBAD7C53B9728A5F |  | R22 | Non-TXV |  | -5.841% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.841%
Marysville | CA | 95901-7344 |  | 2012-05-23 | 2012-05-23 11:32 | 2012-05-23 11:49 | CARRIER - 38CK030 | 85 | 8.2 | Yes | Yes | 17 | 19.9 | -2.9 | E2A7A57A130244C78C3C87869D103144 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Stockton | CA | 95209-1217 |  | 2012-05-22 | 2012-05-22 09:29 | 2012-05-22 09:48 | PAYNE - 567C042RCU | 74 | 3.3 | Yes | Yes | 17.6 | 18 | -0.4 | A14B4339D79744CE95F6B8E3E40B0C4B |  | R22 | Non-TXV |  | 4.459% | 0.95541 | 8.57% | [5 empty] | Non-TXV | 4.459%
Livingston | CA | 95334-1800 |  | 2012-05-22 | 2012-05-22 14:48 | 2012-05-22 15:11 | CARRIER - 48GSN048090301 | 82 | 2.8 | Yes | Yes | 25.2 | 21.3 | 3.9 | A0DCC0969F6446F18DA7C892228386DA |  | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Fresno | CA | 93726-7205 |  | 2012-05-22 | 2012-05-22 13:24 | 2012-05-22 13:34 | TAPPAN - N/A | 73 | 2.2 | Yes | Yes | 23.4 | 20.7 | 2.7 | 3F92C82CD570473C93E99D6AE94542B3 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Tracy | CA | 95304-8999 |  | 2012-06-25 | 2012-06-25 16:43 | 2012-06-25 17:02 | CARRIER - 38TH036300 | 84 | 7.5 | Yes | Yes | 19.8 | 21 | -1.2 | B6EFC37CF2FF4AD28234B1EC4AE9C18C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | Non-TXV | 8.929%
Fresno | CA | 93711-2615 |  | 2012-05-30 | 2012-05-30 13:44 | 2012-05-30 14:08 | GOODMAN - PGB036075-1A | 60 | 1.8 | Yes | Yes | 25.5 | 21.3 | 4.2 | 31A59622D6B34A76A329ACFA9446BD1A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95210-2251 |  | 2012-06-13 | 2012-06-13 10:52 | 2012-06-13 11:11 | BDP - 585HJW030040ABAF | 68 | 2.1 | Yes | Yes | 22.3 | 19.1 | 3.3 | 51AE2DB3A1004276AC516307FF870747 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Stockton | CA | 95210-5210 |  | 2012-06-19 | 2012-06-19 13:45 | 2012-06-19 14:04 | CARRIER - 38ENO15300 | 58 | 1.7 | Yes | Yes | 19 | 21.5 | -2.5 | 55B1AA53A30645D9AE68CBD636DFED30 |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Los Banos | CA | 93635-3779 |  | 2012-05-24 | 2012-05-24 12:08 | 2012-05-24 12:39 | DAY & NIGHT - 567CJO18 | 64 | 3.7 | Yes | Yes | 21 | 19.8 | 1.2 | C43CD02B2D6F4BF5882F590120CCD8EE |  | R22 | Non-TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | Non-TXV | 5.781%
Tracy | CA | 95376-1959 |  | 2012-06-15 | 2012-06-15 11:38 | 2012-06-15 12:04 | DAY & NIGHT - 567G030-B | 80 | 17.9 | Yes | Yes | 18.1 | 19.7 | -1.6 | 611B209F581342EFBF0EB865DFE28BFA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.38% | 0.77625 | 43% | [5 empty] | Non-TXV | 22.38%
Willows | CA | 95988-2930 |  | 2012-05-29 | 2012-05-29 18:09 | 2012-05-29 18:09 | DAY & NIGHT - UNK | 85 | 0 | Yes | Yes | 22.2 | 21 | 1.2 | 5C1D7C92BAAA4424BD59143D1BB5EBCC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1512 |  | 2012-05-18 | 2012-05-18 12:35 | 2012-05-18 13:00 | TRANE - TTN042C100A2 | 85 | 13.5 | Yes | Yes | 27.3 | 21.4 | 5.9 | 32B6B0A41EC047D98E2B3301935620B2 |  | R22 | Non-TXV |  | 15.88% | 0.84118 | 30.52% | [5 empty] | Non-TXV | 15.88%
Los Banos | CA | 93635-2907 |  | 2012-05-18 | 2012-05-18 12:20 | 2012-05-18 13:09 | TRANE - 2YCX3036A1064AA | 82 | 4.8 | Yes | Yes | 23.6 | 21.2 | 2.4 | 017D5CEACE624089B57C90A448DD217D |  | R22 | Non-TXV |  | 5.854% | 0.94146 | 11.25% | [5 empty] | Non-TXV | 5.854%
Fresno | CA | 93711-1542 |  | 2012-08-14 | 2012-08-14 11:22 | 2012-08-14 12:16 | - | 85 | 3.7 | Yes | Yes | 18 | 20.2 | -2.2 | B4A54FD28FA942C286B53FAB7C6ADE9C |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Los Banos | CA | 93635-3778 |  | 2012-05-24 | 2012-05-24 11:45 | 2012-05-24 12:05 | DAY & NIGHT - 567CJ0-18 | 64 | 4.5 | Yes | Yes | 17.1 | 18.8 | -1.7 | BA1AF0BCAAC94B80990FDDFB96BB0E25 |  | R22 | Non-TXV |  | 7.031% | 0.92969 | 13.51% | [5 empty] | Non-TXV | 7.031%
Los Banos | CA | 93635-9490 |  | 2012-05-31 | 2012-05-31 09:56 | 2012-05-31 10:25 | BRYANT - 561CJ048-G | 99 | -5.8 | Yes | Yes | 18.3 | 20.4 | -2.1 | DC7F075387E84142ACC41167B9542EB2 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Los Banos | CA | 93635-3781 |  | 2012-05-29 | 2012-05-29 11:43 | 2012-05-29 12:08 | DAY & NIGHT - 567GJ024 | 76 | 2.2 | Yes | Yes | 19.3 | 20.4 | -1.1 | 24F34C900B384BDAB867019FCA674E10 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.895% | 0.97105 | 5.563% | [5 empty] | Non-TXV | 2.895%
Stockton | CA | 95212-3802 |  | 2012-05-24 | 2012-05-24 10:25 | 2012-05-24 10:43 | CARRIER - 38CKC048370 | 101 | 14.9 | Yes | Yes | 22.4 | 21.9 | 0.5 | 7C887D7019CC45099E0DBB37337A3053 |  | R22 | TXV |  | 14.75% | 0.85248 | 28.35% | [5 empty] | TXV | 14.75%
Madera | CA | 93637-4751 |  | 2012-05-21 | 2012-05-21 10:15 | 2012-05-21 10:32 | TEMP STAR - 2NA324AKA200 | 70 | -4.1 | Yes | Yes | 19.8 | 20.4 | -0.6 | D1502363F07D4965AF16259EEBA0D405 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Fresno | CA | 93706-9330 |  | 2012-06-13 | 2012-06-13 13:17 | 2012-06-13 13:45 | ICP - T4A330GKA100 | 87 | -3.3 | Yes | Yes | 18.3 | 21 | -2.7 | B343FD9AABF84EFDA477CBEC84CC8D60 |  | R410A | TXV |  | -3.793% | 1.0379 | 1.062% |  |  |  |  | TXV |  |  | -3.793%
Los Banos | CA | 93635-3781 |  | 2012-05-23 | 2012-05-23 09:40 | 2012-05-23 10:02 | BDP - 567GJ018 | 58 | 9.4 | Yes | Yes | 28.3 | 22.5 | 5.8 | FD8AE658D38D4A359538240FE086D95D |  | R22 | Non-TXV |  | 16.21% | 0.83793 | 31.15% | [5 empty] | Non-TXV | 16.21%
Los Banos | CA | 93635-3781 |  | 2012-05-23 | 2012-05-23 10:14 | 2012-05-23 10:32 | BDP - 567GJ018 | 60 | 7.6 | Yes | Yes | 26.3 | 22.1 | 4.2 | E5CD6B92CE5145058945B734B4729B90 |  | R22 | Non-TXV |  | 12.67% | 0.87333 | 24.34% | [5 empty] | Non-TXV | 12.67%
Pollock Pines | CA | 95726-9406 |  | 2012-07-05 | 2012-07-05 09:48 | 2012-07-05 09:48 | OTHER - BRCS036180 | 70 | 0 | Yes | Yes | 25.1 | 19.9 | 5.2 | 7EFC8CDE171847B29DB1B8BA7DBFD7DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2948 |  | 2012-07-12 | 2012-07-12 10:00 | 2012-07-12 10:18 | DAY & NIGHT - PGF342080K01 | 184 | 8.8 | Yes | Yes | 16 | 17.9 | -1.9 | 31D62167E9214285AE2BA95945DC84B6 |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Los Banos | CA | 93635-3782 |  | 2012-05-23 | 2012-05-23 11:11 | 2012-05-23 11:44 | BRYANT - 561CJ024 | 54 | -3.2 | Yes | Yes | 30.6 | 24.8 | 5.8 | 85400E2CA8C5430793AB883B6099D566 |  | R22 | TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | TXV |  |  | -5.926%
Chico | CA | 95928-4024 |  | 2012-06-13 | 2012-06-13 12:51 | 2012-06-13 13:24 | - 597CN030-C | 97 | 2.9 | Yes | Yes | 18.1 | 20.7 | -2.6 | AB303411EB6B43D79B3A6CDACB3125D2 |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Atwater | CA | 95301-3953 |  | 2012-05-23 | 2012-05-23 14:04 | 2012-05-23 14:21 | GOODMAN - GPG1324045M41AC | 85 | 2.6 | Yes | Yes | 24.9 | 20.1 | 4.8 | 4098710044ED4CFB9C0146C374A0709B |  | R410A | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Los Banos | CA | 93635-5225 |  | 2012-05-29 | 2012-05-29 14:31 | 2012-05-29 14:54 | BRYANT - 561CJ042-B | 93 | 4.9 | Yes | Yes | 19.1 | 20.7 | -1.6 | 50EF93135FFD4D1DBCD8FA6D12ED051E |  | R22 | TXV |  | 5.269% | 0.94731 | 10.13% | [5 empty] | TXV | 5.269%
Livingston | CA | 95334-1874 |  | 2012-05-23 | 2012-05-23 12:39 | 2012-05-23 12:55 | CARRIER - 591ANX030000ABAA | 85 | 2.5 | Yes | Yes | 24.8 | 21 | 3.8 | D68C6D6CDBB24AF7B13CFDAF834CFD74 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Mendota | CA | 93640-0000 |  | 2012-08-15 | 2012-08-15 09:05 | 2012-08-15 09:25 | BRYANT - 113RNA042A | 127 | 9.4 | Yes | Yes | 19.2 | 17.7 | 1.5 | 55E7F54AE62644FE81281E3F84E005DD |  | R22 | Non-TXV |  | 7.402% | 0.92598 | 14.22% | [5 empty] | Non-TXV | 7.402%
Livingston | CA | 95334-1334 |  | 2012-05-29 | 2012-05-29 11:06 | 2012-05-29 11:23 | RUUD - UNK | 70 | 6.3 | Yes | Yes | 21.2 | 20.4 | 0.8 | D5B6279625AD4804AF6ACAA3E387E3F3 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Los Banos | CA | 93635-3781 |  | 2012-05-23 | 2012-05-23 10:38 | 2012-05-23 11:04 | BDP - 567OJ018 | 60 | 6.8 | Yes | Yes | 22.7 | 20.4 | 2.3 | 58D755909BB241B49D90AAAC4D6DC101 |  | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Winton | CA | 95388-9431 |  | 2012-06-13 | 2012-06-13 09:36 | 2012-06-13 10:03 | CARRIER - 48GS-030040301 | 55 | 1.6 | Yes | Yes | 21.4 | 19.3 | 2.1 | AE800B8F82274AC39440511780951C4E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Fresno | CA | 93727-4422 |  | 2012-05-31 | 2012-05-31 14:06 | 2012-05-31 14:36 | OTHER - AC024M1021CG | 52 | 20.9 | Yes | Yes | 15.5 | 18.5 | -3 | C9E47F85962A499CBBCB42770A64550D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 40.19% | 0.59808 | 77.24% | [5 empty] | Non-TXV | 40.19%
Fresno | CA | 93727-4423 |  | 2012-05-31 | 2012-05-31 14:38 | 2012-05-31 15:12 | COLEMAN - N/A | 60 | 4.2 | Yes | Yes | 18.9 | 20.2 | -1.3 | 6B25FA3A431B4A93BC05F2FC9E55356E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93711-2609 |  | 2012-06-08 | 2012-06-08 09:35 | 2012-06-08 09:35 | RUUD - URKA-A036JK06E | 62 | 0 | Yes | Yes | 20.5 | 19 | 1.5 | 0F20E79A2FB54603B41C4F6527C4138A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0734 |  | 2012-05-30 | 2012-05-30 12:18 | 2012-05-30 12:35 | YORK - D2NP036N05606A | 108 | 3.2 | Yes | Yes | 22.2 | 19.3 | 2.9 | 69D2EA7F2C2E4450863A82914F74CADA |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Oakdale | CA | 95361-7607 |  | 2012-05-22 | 2012-05-22 12:01 | 2012-05-22 12:29 | PAYNE - 588ANW024040ABAD | 40 | 1.6 | Yes | Yes | 18.7 | 19.9 | -1.2 | A089B30EFD184E21818310E996061CEB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Los Banos | CA | 93635-3782 |  | 2012-05-23 | 2012-05-23 12:39 | 2012-05-23 13:07 | BDP - 567GJ018 | 64 | 9.3 | Yes | Yes | 23.2 | 23.6 | -0.4 | F9B4F3B12AD04CD697CC9D4B9E068370 |  | R22 | Non-TXV |  | 14.53% | 0.85469 | 27.93% | [5 empty] | Non-TXV | 14.53%
Los Banos | CA | 93635-3783 |  | 2012-05-23 | 2012-05-23 14:30 | 2012-05-23 14:52 | BDP - 567GJ018 | 64 | 11.3 | Yes | Yes | 22.1 | 23.5 | -1.4 | 72E2FB30604145748836C621792E6783 |  | R22 | Non-TXV |  | 17.66% | 0.82344 | 33.93% | [5 empty] | Non-TXV | 17.66%
Los Banos | CA | 93635-3784 |  | 2012-06-08 | 2012-06-08 11:32 | 2012-06-08 11:57 | DAY & NIGHT - 567GJ018 | 64 | -4.5 | Yes | Yes | 17.3 | 19.3 | -2 | 87038AC629954D79A3C8779445AC1A04 |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Merced | CA | 95341-6973 |  | 2012-06-08 | 2012-06-08 11:25 | 2012-06-08 11:46 | PAYNE - PY1PNB024040AAAA | 53 | 2.3 | Yes | Yes | 20.2 | 19.7 | 0.6 | ACBB8875A90A4079964D309A8E1B08B7 |  | R22 | Non-TXV |  | 4.34% | 0.9566 | 8.34% | [5 empty] | Non-TXV | 4.34%
Merced | CA | 95340-2906 |  | 2012-05-18 | 2012-05-18 14:04 | 2012-05-18 14:33 | HEIL - CA3042VKA1 | 99 | 12.3 | Yes | Yes | 30.2 | 24.2 | 6 | 6CA02B7F5A1E46AB919D2AB965225960 |  | R22 | Non-TXV |  | 12.42% | 0.87576 | 23.88% | [5 empty] | Non-TXV | 12.42%
Planada | CA | 95365-0000 |  | 2012-05-22 | 2012-05-22 17:24 | 2012-05-22 17:42 | DAY & NIGHT - PGD324040K001C1 | 72 | 5.9 | Yes | Yes | 19.7 | 18.5 | 1.2 | DFFF3D1731734783B904B2ADC58C23A7 |  | R410A | Non-TXV |  | 8.194% | 0.91806 | 15.75% | [5 empty] | Non-TXV | 8.194%
Atwater | CA | 95301-4591 |  | 2012-05-18 | 2012-05-18 09:10 | 2012-05-18 09:28 | UNITARY - H2RA036S06E | 63 | 1.9 | Yes | Yes | 16 | 18.5 | -2.5 | D829F865911542C1AD1C92887BCED755 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Fresno | CA | 93722-7355 |  | 2012-05-29 | 2012-05-29 11:41 | 2012-05-29 12:09 | LENNOX - 12GCS042X-75-3PB | 133 | 4 | Yes | Yes | 26.1 | 21.5 | 4.6 | 978642AF9B2440F8A5C0109439E75181 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Atwater | CA | 95301-3950 |  | 2012-05-21 | 2012-05-21 12:06 | 2012-05-21 12:24 | UNITARY - GCGD48S41S3A | 73 | 2.1 | Yes | Yes | 22.3 | 18.4 | 4 | AB99A638ADEF49FDAE81413F74367D83 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Merced | CA | 95340-2948 |  | 2012-06-06 | 2012-06-06 09:44 | 2012-06-06 10:05 | GOODMAN - PGB024075-1 | 54 | -3.2 | Yes | Yes | 22 | 20.9 | 1.1 | 166CE71B75E3458E877B00F810368FB3 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Fresno | CA | 93710-6311 |  | 2012-05-30 | 2012-05-30 11:35 | 2012-05-30 11:56 | BDP - 585B042100YACR | 89 | 2.6 | Yes | Yes | 25.6 | 21 | 4.6 | CD19A467576E4432B88234B292CC10EE |  | R22 | Non-TXV |  | 2.921% | 0.97079 | 5.614% | [5 empty] | Non-TXV | 2.921%
Los Banos | CA | 93635-3783 |  | 2012-07-03 | 2012-07-03 13:37 | 2012-07-03 14:00 | DAY & NIGHT - 567GJ018 | 76 | 2.9 | Yes | Yes | 18.6 | 19.4 | -0.8 | 7E40F6F75A4546A1888C026ACC9CA18E |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Los Banos | CA | 93635-3770 |  | 2012-05-29 | 2012-05-29 10:37 | 2012-05-29 11:11 | TRANE - BTD724A100C0 | 68 | -4.8 | Yes | Yes | 18.1 | 20.2 | -2.1 | ABB4EA165AC340508C59289EBEC87662 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Merced | CA | 95348-1655 |  | 2012-05-30 | 2012-05-30 09:53 | 2012-05-30 10:11 | AMERICAN STANDARD - YCC024F1L0BH | 65 | 1.9 | Yes | Yes | 21.7 | 19.9 | 1.8 | 16F1644DE3EF40AF8E101C1D792DC930 |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Los Banos | CA | 93635-3775 |  | 2012-05-23 | 2012-05-23 14:20 | 2012-05-23 14:43 | AMERICAN STANDARD - 7A0024A100A2 | 67 | 3.2 | Yes | Yes | 19.8 | 21.9 | -2.1 | 2AEC569BDF054669B378364C0FA3E2EF | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.776% | 0.95224 | 9.179% | [5 empty] | Non-TXV | 4.776%
Stockton | CA | 95210-1237 |  | 2012-05-18 | 2012-05-18 14:31 | 2012-05-18 14:48 | DAY N NIGHT - 24/60YAC-108C | 50 | 1.7 | Yes | Yes | 26.4 | 21.4 | 5 | 391CC76F321B4716B1B42FA80DD539FA |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Merced | CA | 95340-1642 |  | 2012-06-12 | 2012-06-12 13:57 | 2012-06-12 14:28 | AMERICAN STANDARD - YCY048G1H0AD | 187 | 7.2 | Yes | Yes | 24.6 | 20.2 | 4.5 | D85D9A5D74AC4F6C8098B29797E31787 |  | R22 | Non-TXV |  | 3.85% | 0.9615 | 7.399% | [5 empty] | Non-TXV | 3.85%
Los Banos | CA | 93635-3782 |  | 2012-05-23 | 2012-05-23 13:10 | 2012-05-23 13:37 | BDP - 567GJ018 | 64 | 5.8 | Yes | Yes | 22 | 23.1 | -1.1 | 4EC0F8A47F6D40C28D6DD61966B81297 |  | R22 | Non-TXV |  | 9.062% | 0.90938 | 17.42% | [5 empty] | Non-TXV | 9.062%
Atwater | CA | 95301-3924 |  | 2012-05-21 | 2012-05-21 15:36 | 2012-05-21 15:58 | UNITARY - GCGD36S41S3A | 73 | 2.3 | Yes | Yes | 19.2 | 19.1 | 0.1 | 6332983A46D24AEBA16858378D76B1A9 |  | R410A | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Parlier | CA | 93648-2490 |  | 2012-08-15 | 2012-08-15 14:24 | 2012-08-15 14:42 | LENNOX - GCS29-30-75-2PA | 51 | 2.5 | Yes | Yes | 18.7 | 18 | 0.7 | C0EBCC2E94D64EA8BA5CDC70D634F2EE |  | R22 | Non-TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | Non-TXV | 4.902%
Planada | CA | 95365-0000 |  | 2012-05-22 | 2012-05-22 15:31 | 2012-05-22 15:53 | DAY & NIGHT - PGD324040K001C1 | 72 | 5.5 | Yes | Yes | 24.8 | 20.6 | 4.3 | E31FFE2668244ABC8B89C41C288E228E |  | R410A | Non-TXV |  | 7.639% | 0.92361 | 14.68% | [5 empty] | Non-TXV | 7.639%
Stockton | CA | 95207-6065 |  | 2012-06-25 | 2012-06-25 10:50 | 2012-06-25 11:13 | RHEEM - UNK | 96 | 12.5 | Yes | Yes | 22.7 | 19.6 | 3.1 | 9564904C11D14B05B08FB21B17BCD027 |  | R22 | Non-TXV |  | 13.02% | 0.86979 | 25.02% | [5 empty] | Non-TXV | 13.02%
Stockton | CA | 95207-6015 |  | 2012-06-15 | 2012-06-15 10:34 | 2012-06-15 10:57 | RHEEM - UNK | 67 | 10.7 | Yes | Yes | 17.1 | 19.8 | -2.7 | 757EA5E8B5164752A6BDDF5FF9BBC298 |  | R22 | Non-TXV |  | 15.97% | 0.8403 | 30.69% | [5 empty] | Non-TXV | 15.97%
Clovis | CA | 93612-4237 |  | 2012-06-07 | 2012-06-07 11:59 | 2012-06-07 12:17 | WESTINGHOUSE - N/A | 64 | 1.9 | Yes | Yes | 20.6 | 21.5 | -0.9 | C33ED4757AB64C2DB0A4F44549EF42E7 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Atwater | CA | 95301-3925 |  | 2012-07-16 | 2012-07-16 11:22 | 2012-07-16 13:22 | OTHER - NA | 81 | 2.4 | Yes | Yes | 17.9 | 20.7 | -2.8 | 2AC9B9CF161D40A48D7152E988E3A414 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Clovis | CA | 93612-4238 |  | 2012-06-07 | 2012-06-07 15:10 | 2012-06-07 15:59 | TRANE - YCC024F1L0BE | 64 | 1.9 | Yes | Yes | 27.3 | 22.3 | 5 | EE4F582AEBC34DDC9DA60FF2C340F1FE |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Yuba City | CA | 95991-2807 |  | 2012-06-11 | 2012-06-11 13:57 | 2012-06-11 14:15 | RUUD - UAMC-042JAZ | 96 | 21.4 | Yes | Yes | 21.2 | 21 | 0.2 | 9ECBA034E99242F989C15EC7C349B95F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.29% | 0.77708 | 42.84% | [5 empty] | Non-TXV | 22.29%
Clovis | CA | 93612-4238 |  | 2012-06-08 | 2012-06-08 11:17 | 2012-06-08 11:37 | OTHER - UNK | 85 | 2.6 | Yes | Yes | 18 | 20.4 | -2.4 | 5112ECE0CC594EA482D2AB1CB9764C4D |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Magalia | CA | 95954-9610 |  | 2012-06-07 | 2012-06-07 10:19 | 2012-06-07 10:56 | RUUD - UAMB-048JAZ | 162 | 6 | Yes | Yes | 18.7 | 18.6 | 0.1 | FED2F59E3B814D88A6FAD111C5AF09BE |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Stockton | CA | 95204-5710 |  | 2012-05-21 | 2012-05-21 12:50 | 2012-05-21 13:10 | CARRIER - 48GL042300BA | 104 | 5.8 | Yes | Yes | 18.3 | 21 | -2.7 | 07EF4EFE5D624AD08C088130A3C18522 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Merced | CA | 95341-5749 |  | 2012-06-01 | 2012-06-01 12:10 | 2012-06-01 12:37 | RUUD - URGG-05E25JKR | 39 | 2.5 | Yes | Yes | 21.5 | 19.1 | 2.4 | 3FC043E3F5334B6D9F014EAC3B870876 |  | R22 | Non-TXV |  | 6.41% | 0.9359 | 12.32% | [5 empty] | Non-TXV | 6.41%
Yuba City | CA | 95993-5208 |  | 2012-05-24 | 2012-05-24 16:08 | 2012-05-24 16:08 | BDP - 588ANW024060ADAD | 42 | 0 | Yes | Yes | 20.8 | 21.3 | -0.5 | 8A32DD5B03714BE59E64F80AAB06AD4E | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3368 |  | 2012-06-07 | 2012-06-07 17:17 | 2012-06-07 17:33 | DAY & NIGHT - 541DJ024 | 118 | 3.5 | Yes | Yes | 19.5 | 20.3 | -0.8 | B230330685494C16956E983F1DA4E7AE |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Parlier | CA | 93648-2473 |  | 2012-08-15 | 2012-08-15 13:36 | 2012-08-15 14:00 | CARRIER - 48SX0030040311 | 69 | 2.1 | Yes | Yes | 17.3 | 17.5 | -0.2 | FC6B27DB2B8743F3926F063CC2BA7197 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Merced | CA | 95341-6055 |  | 2012-06-08 | 2012-06-08 10:54 | 2012-06-08 11:21 | ARCOAIRE - PGC024K060E | 54 | -3.8 | Yes | Yes | 17.8 | 19.3 | -1.5 | FA66101181364467BB8603F58997145E |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Stockton | CA | 95203-2341 |  | 2012-07-02 | 2012-07-02 13:40 | 2012-07-02 13:40 | RHEEM - RRNA-B030JK06X | 72 | 0 | Yes | Yes | 22.8 | 19.9 | 2.9 | 10F8AAF94F7642D7BDF6AE52881A0BC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3727 |  | 2012-05-29 | 2012-05-29 13:15 | 2012-05-29 13:32 | OTHER - UNK | 54 | 2.2 | Yes | Yes | 17.7 | 19.3 | -1.6 | B5A5115BE6504F75B151F8C2E3FC76C7 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Clovis | CA | 93612-1580 |  | 2012-05-22 | 2012-05-22 14:34 | 2012-05-22 14:34 | PAYNE - 5856J018040 | 58 | 0 | Yes | Yes | 23.5 | 20.4 | 3.1 | 11128D5B66AA40C8A631E88F746B9117 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Live Oak | CA | 95953-9735 |  | 2012-07-05 | 2012-07-05 10:07 | 2012-07-05 10:24 | OTHER - UNK | 75 | 3 | Yes | Yes | 17 | 19.3 | -2.3 | 50E93B23A7454F5E9ACA75E03FD20AA7 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Kingsburg | CA | 93631-1020 |  | 2012-06-06 | 2012-06-06 15:27 | 2012-06-06 15:46 | ARCOAIRE - N/A | 90 | 5.6 | Yes | Yes | 18.8 | 20.6 | -1.7 | 95FD5BC7B15449E2A68B114D539EC4E1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.222% | 0.93778 | 11.96% | [5 empty] | Non-TXV | 6.222%
Corning | CA | 96021-2264 |  | 2012-05-23 | 2012-05-23 11:13 | 2012-05-23 11:13 | RHEEM - RAFD-025-JAS | 51 | 0 | Yes | Yes | 23 | 21 | 2.1 | 5E49942E099640E5AC077E3E4254D8CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-2805 |  | 2012-05-23 | 2012-05-23 12:10 | 2012-05-23 12:10 | UNK - UNK | 85 | 0 | Yes | Yes | 23.7 | 22.6 | 1.1 | 368B1CEC3EA748D9902D0BC36914DABF |  |  |  |  | 0% | 1 | 0%
Planada | CA | 95365-8018 |  | 2012-05-23 | 2012-05-23 13:33 | 2012-05-23 14:03 | WESTINGHOUSE - FS3BA-024KA | 64 | 3.7 | Yes | Yes | 20.9 | 19.6 | 1.3 | 9A4E8AD7DCF74F77A268B56FC7776AE5 |  | R22 | Non-TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | Non-TXV | 5.781%
Stockton | CA | 95206-3873 |  | 2012-05-24 | 2012-05-24 16:54 | 2012-05-24 16:54 | OTHER - TCGD42S41HASI | 69 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | 39FDF376557B49F89E6104A9474F28C7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4237 |  | 2012-06-14 | 2012-06-14 13:15 | 2012-06-14 13:32 | RUUD - N/A | 69 | 7.5 | Yes | Yes | 19.7 | 19.3 | 0.4 | 8A158E626F824ED8BAAC3DF89188D656 |  | R22 | Non-TXV |  | 10.87% | 0.8913 | 20.89% | [5 empty] | Non-TXV | 10.87%
Planada | CA | 95365-8018 |  | 2012-05-23 | 2012-05-23 15:26 | 2012-05-23 15:54 | WESTINGHOUSE - FS3BA-024KA | 64 | 3.9 | Yes | Yes | 19.4 | 19.6 | -0.2 | EAD4C8A502EA496394244B641D69EFD6 |  | R22 | Non-TXV |  | 6.094% | 0.93906 | 11.71% | [5 empty] | Non-TXV | 6.094%
Clovis | CA | 93619-9753 |  | 2012-05-30 | 2012-05-30 11:23 | 2012-05-30 11:43 | PAYNE - UNK | 56 | -3.3 | Yes | Yes | 18.5 | 21 | -2.5 | 3B649E08975B49BD83E16CA741B4C316 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Clovis | CA | 93612-4234 |  | 2012-07-13 | 2012-07-13 11:48 | 2012-07-13 12:29 | OTHER - N/A | 76 | 6.4 | Yes | Yes | 22.2 | 22.1 | 0.1 | 07595F4D0C1043C98091AC81EAAF8109 |  | R22 | Non-TXV |  | 8.421% | 0.91579 | 16.18% | [5 empty] | Non-TXV | 8.421%
Los Banos | CA | 93635-3236 |  | 2012-06-08 | 2012-06-08 17:04 | 2012-06-08 17:33 | TRANE - TTX736A100A2 | 130 | 35.7 | Yes | Yes | 26.9 | 24.2 | 2.7 | F0E0C731AFFB4859B1DF2602F7FD2B03 |  | R22 | Non-TXV |  | 27.46% | 0.72538 | 52.78% | [5 empty] | Non-TXV | 27.46%
Stockton | CA | 95207-7434 |  | 2012-06-25 | 2012-06-25 11:49 | 2012-06-25 12:06 | OTHER - 24TCA-04-01 | 80 | 8.8 | Yes | Yes | 17.7 | 20.2 | -2.5 | A371B052D8AA41C890BFF17B576E5A3A |  | R22 | Non-TXV |  | 11% | 0.89 | 21.14% | [5 empty] | Non-TXV | 11%
Stockton | CA | 95207-7762 |  | 2012-07-02 | 2012-07-02 10:08 | 2012-07-02 10:25 | AMERICAN STANDARD - CM18-1AA | 51 | -4.8 | Yes | Yes | 17.8 | 18.1 | -0.3 | D161408948E04ED69D0F751FF224C76D |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93725-1624 |  | 2012-08-10 | 2012-08-10 13:00 | 2012-08-10 13:30 | RHEEM - URMA-A030JK06E | 80 | 8.5 | Yes | Yes | 18.9 | 20.2 | -1.3 | 56E259F1CE2145AABB59164DA90F081C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.62% | 0.89375 | 20.42% | [5 empty] | Non-TXV | 10.62%
Planada | CA | 95365-0000 |  | 2012-05-22 | 2012-05-22 16:07 | 2012-05-22 16:45 | DAY & NIGHT - PGD324040K001C1 | 72 | 2.9 | Yes | Yes | 23.4 | 21.4 | 2 | 8B72BC5D55F8471B86F7273A7AA1EB8D |  | R22 | Non-TXV |  | 4.028% | 0.95972 | 7.741% | [5 empty] | Non-TXV | 4.028%
Rocklin | CA | 95677-3648 |  | 2012-05-29 | 2012-05-29 14:13 | 2012-05-29 14:13 | CARRIER - 540JJ018 | 83 | 0 | Yes | Yes | 19.5 | 19.4 | 0.1 | BE28E7AC30D84BDD95A2CF75FE84B2B3 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-9457 |  | 2012-05-23 | 2012-05-23 12:04 | 2012-05-23 12:21 | CARRIER - 591ANX024000AAAA | 85 | 2.5 | Yes | Yes | 23.3 | 19.9 | 3.4 | 2762C5E04865436EBF71DA2C015BF436 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Livingston | CA | 95334-1866 |  | 2012-05-29 | 2012-05-29 10:07 | 2012-05-29 10:23 | RHEEM - UNK | 67 | 3.4 | Yes | Yes | 19.8 | 21.5 | -1.7 | 4428114B4EED429C8703AB5A7380BF20 |  | R22 | Non-TXV |  | 5.075% | 0.94925 | 9.752% | [5 empty] | Non-TXV | 5.075%
Los Banos | CA | 93635-3769 |  | 2012-05-23 | 2012-05-23 11:07 | 2012-05-23 11:07 | TRANE - BTD724A100C0 | 68 | 0 | Yes | Yes | 22.4 | 23.7 | -1.3 | B57E0C9BA39B42BE9082DBDC49F1AC6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Planada | CA | 95365-0000 |  | 2012-05-23 | 2012-05-23 11:43 | 2012-05-23 12:09 | WESTINGHOUSE - FS3BA-024KA | 64 | 4.1 | Yes | Yes | 20.4 | 19.9 | 0.5 | 07B2677EBF2841229365625BA8461051 |  | R22 | Non-TXV |  | 6.406% | 0.93594 | 12.31% | [5 empty] | Non-TXV | 6.406%
Loomis | CA | 95650-9215 |  | 2012-06-12 | 2012-06-12 13:28 | 2012-06-12 13:28 | TRANE - 4YCY4036B1075AA | 118 | 0 | Yes | Yes | 21.5 | 20.1 | 1.5 | 8C5675560632428299EEE16C5AC7B800 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2126 |  | 2012-07-11 | 2012-07-11 09:22 | 2012-07-11 09:42 | RHEEM - RACB-030JAS | 46 | -3.2 | Yes | Yes | 27.2 | 22 | 5.2 | 65599C4C7C8947608832122379A351D9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -6.957% | 1.0696 | 1.948% |  |  |  |  | Non-TXV |  |  | -6.957%
Lincoln | CA | 95648-8138 |  | 2012-07-06 | 2012-07-06 14:08 | 2012-07-06 14:08 | UNITARY PRODUCTS GROUP - H2RC030S06G | 88 | 0 | Yes | Yes | 16.6 | 19 | -2.4 | F89ED61033B845E79B195676C21F7A1D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-5333 |  | 2012-05-29 | 2012-05-29 10:40 | 2012-05-29 11:06 | GOODMAN - CK30-18 | 76 | 13.9 | Yes | Yes | 23.8 | 19.9 | 3.9 | D37A1B4025B54A8AB93F806481BFEEB9 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.29% | 0.81711 | 35.15% | [5 empty] | Non-TXV | 18.29%
Valley Springs | CA | 95252-8874 |  | 2012-07-05 | 2012-07-05 09:11 | 2012-07-05 09:28 | PAYNE - PA10JA036-C | 78 | 7.6 | Yes | Yes | 17.8 | 19.9 | -2.1 | 60464ECAAAEB429F8D75CDC746DDD01E |  | R22 | Non-TXV |  | 9.744% | 0.90256 | 18.73% | [5 empty] | Non-TXV | 9.744%
Fresno | CA | 93710-4517 |  | 2012-08-07 | 2012-08-07 17:23 | 2012-08-07 17:49 | ALLEGIANCE - 7A2060B100A0 | 84 | 3.9 | Yes | Yes | 16.5 | 19.2 | -2.7 | E6F85151278F4986B3F37DC0E6F9973B |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Auburn | CA | 95603-3743 |  | 2012-05-18 | 2012-05-18 15:31 | 2012-05-18 15:47 | STANDARD - 7B0023B100A1 | 54 | 11 | Yes | Yes | 19 | 19.5 | -0.5 | 78F4FCC74E144A8A96072279F245A081 |  | R22 | Non-TXV |  | 20.37% | 0.7963 | 39.15% | [5 empty] | Non-TXV | 20.37%
Lincoln | CA | 95648-2127 |  | 2012-05-23 | 2012-05-23 11:35 | 2012-05-23 11:35 | BDP - 588ANW024060ADAD | 42 | 0 | Yes | Yes | 20.3 | 20.1 | 0.2 | 24FAFB155A514CD08477102207B88EF3 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3771 |  | 2012-05-23 | 2012-05-23 12:20 | 2012-05-23 12:49 | TRANE - BTD724A100C0 | 68 | -4 | Yes | Yes | 18.8 | 18.2 | 0.6 | B49BD1FC170C48969F5BDC3385DCBC91 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93710-5435 |  | 2012-05-24 | 2012-05-24 15:01 | 2012-05-24 15:58 | CARRIER - 24ABB336W310 | 85 | 2.7 | Yes | Yes | 18.9 | 20.4 | -1.5 | FC43748832894674947C1C923A3F08CD |  | R410A | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Rocklin | CA | 95677-3654 |  | 2012-07-06 | 2012-07-06 11:29 | 2012-07-06 11:49 | GOODMAN - GSH130181BB | 85 | 5.6 | Yes | Yes | 16 | 18.2 | -2.2 | 8944D8E1E65440479C96CA3C1EEA1323 |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Chico | CA | 95928-7666 |  | 2012-05-23 | 2012-05-23 12:55 | 2012-05-23 14:03 | BRYANT - 563CN036-B | 108 | 4.2 | Yes | Yes | 24.1 | 23.7 | 0.4 | E4CE5E79BD6449DBAE3D93B97D8EAC3C |  | R22 | TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | TXV | 3.889%
Fresno | CA | 93706-4215 |  | 2012-07-09 | 2012-07-09 13:41 | 2012-07-09 14:02 | RHEEM - RRPL-BO36JK06X | 92 | 2.7 | Yes | Yes | 20.5 | 21 | -0.5 | 4545C8F548F54CEFA34698CD43A54D1F |  | R410A | Non-TXV |  | 2.935% | 0.97065 | 5.64% | [5 empty] | Non-TXV | 2.935%
Paradise | CA | 95969-6026 |  | 2012-06-13 | 2012-06-13 10:03 | 2012-06-13 10:33 | BRYANT - 582ANW024060AAAD | 54 | 6 | Yes | Yes | 22 | 20.9 | 1.1 | 60E47751300341A9AF3C6F189ADACFBD |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Parlier | CA | 93648-2492 |  | 2012-08-15 | 2012-08-15 14:57 | 2012-08-15 15:34 | LENNOX - GCS29X-030-75-2PA | 51 | 2.4 | Yes | Yes | 14.8 | 16.4 | -1.6 | C0A20B20F5BD470C900AEBE8769F7A67 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Tracy | CA | 95377-8902 |  | 2012-06-26 | 2012-06-26 15:33 | 2012-06-26 15:59 | BRYANT - 556AN036-F | 153 | 5.6 | Yes | Yes | 22.1 | 19.9 | 2.2 | 9B194AA1145742F79C3CD4A4EF3C37B2 |  | R410A | TXV |  | 3.66% | 0.9634 | 7.034% | [5 empty] | TXV | 3.66%
Tracy | CA | 95377-8902 |  | 2012-06-26 | 2012-06-26 15:42 | 2012-06-26 16:05 | YORK - AC060X1021A | 118 | 3.5 | Yes | Yes | 19.9 | 20.4 | -0.5 | F512FED3A00943C3A198AF035113AAA0 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Lincoln | CA | 95648-2107 |  | 2012-05-23 | 2012-05-23 11:07 | 2012-05-23 11:07 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 25.8 | 20.4 | 5.4 | 1DA2894DD7B24A3AAED6CDA19465EB95 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3646 |  | 2012-06-12 | 2012-06-12 12:43 | 2012-06-12 12:43 | CARRIER - 540JJ018 | 83 | 0 | Yes | Yes | 20.3 | 20.7 | -0.4 | 6C23F5CF2C064459BCDB19719B253D1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1412 |  | 2012-05-24 | 2012-05-24 11:25 | 2012-05-24 11:46 | ICP - PGC024K040E | 85 | 3.3 | Yes | Yes | 16.3 | 19.3 | -3 | 6E83BE6C24AD4437AEF86AF80BFBFA9A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Dos Palos | CA | 93620-2049 |  | 2012-05-31 | 2012-05-31 12:33 | 2012-05-31 12:59 | GOODMAN - CK361A | 73 | 7.3 | Yes | Yes | 18.3 | 21.2 | -2.9 | 18948CAAF9974F649B73D86C90FA0211 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95215-5231 |  | 2012-06-21 | 2012-06-21 11:48 | 2012-06-21 12:04 | COMFORT AIRE - PGC024K040E | 54 | 3.2 | Yes | Yes | 23.6 | 21.3 | 2.3 | 348E932DA2FB4ACAB723580604A25457 |  | R22 | Non-TXV |  | 5.926% | 0.94074 | 11.39% | [5 empty] | Non-TXV | 5.926%
Livingston | CA | 95334-1123 |  | 2012-05-29 | 2012-05-29 11:29 | 2012-05-29 11:46 | GOODMAN - GPG13360701AC | 110 | 7 | Yes | Yes | 23 | 20.7 | 2.3 | FC4194B80B39463C9C3ECCF598D72F57 |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Los Banos | CA | 93635-3768 |  | 2012-05-23 | 2012-05-23 13:54 | 2012-05-23 14:17 | TRANE - BTD724A100CO | 68 | 13.7 | Yes | Yes | 22.4 | 24 | -1.6 | 7357A9ADE2B64DF8AE12522E802D6DD4 |  | R22 | Non-TXV |  | 20.15% | 0.79853 | 38.72% | [5 empty] | Non-TXV | 20.15%
Merced | CA | 95341-5854 |  | 2012-06-12 | 2012-06-12 15:10 | 2012-06-12 15:35 | PAYNE - PY1PNB042060AAAA | 100 | -5.9 | Yes | Yes | 27.1 | 21.2 | 5.9 | 9610BF700F7E42EEB60D9D20AB3034D8 |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Atwater | CA | 95301-3932 |  | 2012-06-06 | 2012-06-06 09:33 | 2012-06-06 09:55 | COLEMAN - GPG13240451CB | 74 | 2.2 | Yes | Yes | 28.4 | 22.8 | 5.6 | 010AA3A7EEC84FEE9B70558A86BD2313 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Paradise | CA | 95969-5966 |  | 2012-07-17 | 2012-07-17 10:13 | 2012-07-17 10:56 | DAY & NIGHT - 56BJ024 | 65 | 5.5 | Yes | Yes | 26.2 | 21.4 | 4.8 | 664DA3EEF6924072AB98E7BC6BE427BB |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Fresno | CA | 93711-1312 |  | 2012-08-14 | 2012-08-14 17:07 | 2012-08-14 19:03 | - HAC042AKA4 | 99 | 4.1 | Yes | Yes | 17.8 | 20.7 | -2.9 | 5C5E06D19D33441885BE309A97454C46 |  | R22 | Non-TXV |  | 4.141% | 0.95859 | 7.959% | [5 empty] | Non-TXV | 4.141%
Stockton | CA | 95207-4209 |  | 2012-06-08 | 2012-06-08 10:44 | 2012-06-08 10:44 | YORK - D1NP030N05606A | 85 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | 95A9A2E534824CA29FABBE926DE89064 |  | R22 | TXV |  | 0% | 1 | 0%
Olivehurst | CA | 95961-0000 |  | 2012-07-17 | 2012-07-17 13:54 | 2012-07-17 14:44 | OTHER - 2PGE13E30068LP-1A | 98 | 9.3 | Yes | Yes | 20 | 18.2 | 1.8 | 86326904655B469D899980FAB7F97327 |  | R22 | Non-TXV |  | 9.49% | 0.9051 | 18.24% | [5 empty] | Non-TXV | 9.49%
Atascadero | CA | 93422-4245 |  | 2012-07-10 | 2012-07-10 08:54 | 2012-07-10 09:18 | GOODMAN - GSC130481AF | 152 | -8.9 | Yes | Yes | 24.5 | 19.1 | 5.4 | 70A6B0BD2C944E779ECE87429450C5C9 |  | R22 | Non-TXV |  | -5.855% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.855%
Fresno | CA | 93710-6411 |  | 2012-05-31 | 2012-05-31 10:01 | 2012-05-31 10:24 | GOODMAN - PGB04205-1 REV A | 71 | -4.2 | Yes | Yes | 18.6 | 21.3 | -2.7 | 8AF3420A72E64091962B45E5AAFF88A5 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Fresno | CA | 93710-6411 |  | 2012-05-31 | 2012-05-31 10:26 | 2012-05-31 10:26 | GOODMAN - PGB04205-1 REV A | 71 | 0 | Yes | Yes | 17.9 | 19.9 | -2 | 447B913D629146229321C616F2A40423 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-3689 |  | 2012-05-18 | 2012-05-18 13:23 | 2012-05-18 13:57 | UNK - 661CJ024-B | 72 | 2.2 | Yes | Yes | 24.5 | 22 | 2.5 | CC0A2CE5203641C8BA5C1A8146C843C8 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Clovis | CA | 93611-5104 |  | 2012-05-22 | 2012-05-22 11:29 | 2012-05-22 11:55 | FRASER N JOHNSTON CO - 80WR36G1NA | 118 | 5.5 | Yes | Yes | 19.2 | 20.4 | -1.2 | 6ED7DC6A0E9A474C8727A62BEECE951E |  | R22 | Non-TXV |  | 4.661% | 0.95339 | 8.957% | [5 empty] | Non-TXV | 4.661%
Clovis | CA | 93611-3042 |  | 2012-08-06 | 2012-08-06 16:21 | 2012-08-06 16:37 | RUUD - URKA-A036JK | 84 | 2.6 | Yes | Yes | 18.3 | 19.9 | -1.6 | D904C94B3D8943598E0156478928176A |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Merced | CA | 95348-1612 |  | 2012-07-20 | 2012-07-20 10:06 | 2012-07-20 10:28 | OTHER - NA | 52 | 1.6 | Yes | Yes | 17.8 | 19 | -1.2 | 377212639D6C455188A772E85D930838 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Selma | CA | 93662-2913 |  | 2012-05-18 | 2012-05-18 11:21 | 2012-05-18 11:21 | RHEEM - URKA-A036JK06E | 62 | 0 | Yes | Yes | 20.9 | 20.6 | 0.3 | 60477E0050584A2F9C67392FBB01640C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5426 |  | 2012-05-22 | 2012-05-22 10:51 | 2012-05-22 11:14 | BDP - 561AJX030000AAAA | 85 | 12.2 | Yes | Yes | 27.4 | 21.4 | 6 | 5970B4C9C2BB4FCAA66002F2AC999FDB |  | R22 | Non-TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | Non-TXV | 14.35%
Merced | CA | 95348-1606 |  | 2012-05-30 | 2012-05-30 08:55 | 2012-05-30 09:15 | GOODMAN - GPG13240451BA | 77 | 2.3 | Yes | Yes | 24.2 | 18.3 | 6 | 6DB563A63AC34E0F87BDB512D73045EE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Stockton | CA | 95210-2329 |  | 2012-07-18 | 2012-07-18 13:56 | 2012-07-18 14:17 | GOODMAN - PGB030050-1REVA | 56 | 27.8 | Yes | Yes | 21.3 | 20.4 | 0.9 | 4FD73B910FFA4125A8DACC695BB16E06 |  | R22 | Non-TXV |  | 49.64% | 0.50357 | 95.4% | [5 empty] | Non-TXV | 49.64%
Selma | CA | 93662-2415 |  | 2012-05-18 | 2012-05-18 12:13 | 2012-05-18 12:42 | UPG - BRCS0421 | 84 | 12.6 | Yes | Yes | 18 | 20.2 | -2.2 | A9C8D81DC02E40ABBD16E784756D8A91 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Stockton | CA | 95203-2252 |  | 2012-06-14 | 2012-06-14 11:22 | 2012-06-14 11:41 | DAY & NIGHT - 565AJ018 | 50 | 5 | Yes | Yes | 16.2 | 18.8 | -2.6 | F5A425DBB4E74A1AB77CBB671F838D6F |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Oakdale | CA | 95361-0000 |  | 2012-06-07 | 2012-06-07 11:17 | 2012-06-07 11:34 | GOODMAN - CSC130421AC | 137 | 8.5 | Yes | Yes | 23 | 18.7 | 4.3 | D6BBEEBAFB374BFC806F0144B170BB75 |  | R22 | Non-TXV |  | 6.204% | 0.93796 | 11.92% | [5 empty] | Non-TXV | 6.204%
Parlier | CA | 93648-0000 |  | 2012-07-13 | 2012-07-13 12:59 | 2012-07-13 13:45 | LENNOX - 10GCS030-75-2PA | 51 | 1.7 | Yes | Yes | 19 | 20.4 | -1.4 | FAA4FE855FA4482EB14C74AE2683D4C1 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Madera | CA | 93637-4640 |  | 2012-05-21 | 2012-05-21 15:59 | 2012-05-21 16:25 | YORK - D1NA024N03606C | 55 | -3.9 | Yes | Yes | 17.5 | 20.4 | -2.9 | B5D27A6300DE4EB2B131A5EBDF613756 |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Fresno | CA | 93727-5678 |  | 2012-08-08 | 2012-08-08 09:45 | 2012-08-08 10:08 | LENNOX - HS29-036-5P | 70 | 2.8 | Yes | Yes | 17.2 | 19.8 | -2.6 | CC099AFECCFC4C258C975F2E210A9CF0 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Planada | CA | 95365-8022 |  | 2012-05-23 | 2012-05-23 14:06 | 2012-05-23 14:43 | WESTINGHOUSE - FS3BA-024KA | 64 | 5.7 | Yes | Yes | 20.2 | 19.3 | 0.9 | 4D9F50D592434BC89A3AEA7747E15FD1 |  | R22 | Non-TXV |  | 8.906% | 0.91094 | 17.12% | [5 empty] | Non-TXV | 8.906%
Fresno | CA | 93722-4535 |  | 2012-05-23 | 2012-05-23 10:19 | 2012-05-23 10:37 | AMICAN STANDARD - YCCO24F1LJ | 75 | -4.4 | Yes | Yes | 20.5 | 19.9 | 0.6 | 4766F11F904B4C8790121F0AF7861DCC |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Fresno | CA | 93722-4510 |  | 2012-06-01 | 2012-06-01 15:01 | 2012-06-01 15:01 | AMANA - APG13240451AA | 77 | 0 | Yes | Yes | 20.1 | 19.3 | 0.8 | 2E99BDF751F14ADD95896636D1E0C4ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dos Palos | CA | 93620-2747 |  | 2012-05-31 | 2012-05-31 10:44 | 2012-05-31 11:10 | RUUD - URKAA030JK06E | 85 | 10.7 | Yes | Yes | 24.5 | 20.6 | 3.9 | 9C07E0FA116A4CB3ACD03E35D8AC58ED |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Fresno | CA | 93725-1504 |  | 2012-08-10 | 2012-08-10 11:46 | 2012-08-10 12:06 | RHEEM - RRNA-B036JK06X | 86 | 6.4 | Yes | Yes | 23.3 | 19.7 | 3.6 | D7E505D631C54A2D961AA2BD952FAFCA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.442% | 0.92558 | 14.3% | [5 empty] | Non-TXV | 7.442%
Oakdale | CA | 95361-4192 |  | 2012-06-12 | 2012-06-12 10:15 | 2012-06-12 10:33 | PAYNE - PA10JA030-C | 65 | 2.9 | Yes | Yes | 18.7 | 19.9 | -1.2 | 8DB5A95A6B5742359A47D6F9AFF771D5 |  | R22 | Non-TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | Non-TXV | 4.462%
Planada | CA | 95365-0000 |  | 2012-06-06 | 2012-06-06 13:22 | 2012-06-06 13:40 | WESTINGHOUSE - FS3BA-030KA | 68 | 3.8 | Yes | Yes | 20.8 | 19.1 | 1.8 | 77EABC1CFAF148C5B944F964A6DCCF61 |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Red Bluff | CA | 96080-2912 |  | 2012-07-06 | 2012-07-06 09:06 | 2012-07-06 09:32 | GOODMAN - GPG153609041B | 102 | 5.7 | Yes | Yes | 24.7 | 21 | 3.7 | 37EC996B207E479E8B7199A27EFCDAAB |  | R410A | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Marysville | CA | 95901-4016 |  | 2012-05-23 | 2012-05-23 12:52 | 2012-05-23 13:15 | RHEEM - RRKA-A024JK06X | 50 | 3.6 | Yes | Yes | 24 | 24.4 | -0.4 | E5C1035E44A54A4597A3C540B923877F |  | R22 | Non-TXV |  | 7.2% | 0.928 | 13.84% | [5 empty] | Non-TXV | 7.2%
Planada | CA | 95365-8019 |  | 2012-08-14 | 2012-08-14 12:41 | 2012-08-14 13:06 | WESTINGHOUSE - FS3BA-024KA | 64 | 4.4 | Yes | Yes | 17.9 | 18.6 | -0.7 | 87C9F3EE377B4ABE8A97D631541729F0 |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Stockton | CA | 95209-2743 |  | 2012-06-01 | 2012-06-01 11:40 | 2012-06-01 12:04 | DAY & NIGHT - 585A024055YACR | 51 | 4.9 | Yes | Yes | 26 | 20.6 | 5.4 | D6AC36EEE30249DB9726EFA61133CEE3 |  | R22 | Non-TXV |  | 9.608% | 0.90392 | 18.46% | [5 empty] | Non-TXV | 9.608%
Atwater | CA | 95301-4449 |  | 2012-07-02 | 2012-07-02 10:55 | 2012-07-02 12:26 | OTHER - NA | 68 | 2 | Yes | Yes | 23.1 | 17.1 | 6 | 87B0A6E7B9874952834E08C4516595A2 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Huron | CA | 93234-0000 |  | 2012-07-20 | 2012-07-20 10:52 | 2012-07-20 11:10 | RHEEM - RRNA-B042JK08X | 104 | 3.1 | Yes | Yes | 22.8 | 19.7 | 3.1 | AFB0E3CF3F8049ABBA3D7DC4B144206F |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Merced | CA | 95341-6879 |  | 2012-05-24 | 2012-05-24 12:27 | 2012-05-24 12:50 | YORK - H1DB030S06A | 67 | 2.2 | Yes | Yes | 26.3 | 20.4 | 5.9 | F6F4A4446FEA477993DB268E70296A23 |  | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Planada | CA | 95365-0000 |  | 2012-06-06 | 2012-06-06 12:53 | 2012-06-06 13:16 | WESTINGHOUSE - FS3BA-024KA | 64 | 4.6 | Yes | Yes | 20 | 20.1 | -0.1 | 18B337238ED44898A4FD71E811816DEC |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Huron | CA | 93234-0000 |  | 2012-07-20 | 2012-07-20 08:58 | 2012-07-20 09:20 | LENNOX - 12GCS042-75-6PB | 133 | 4 | Yes | Yes | 25.1 | 20.7 | 4.4 | BA2667B0D4DA41A58CAF90F90873DCE1 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Mendota | CA | 93640-0000 |  | 2012-08-15 | 2012-08-15 09:32 | 2012-08-15 09:56 | BRYANT - 113RNA036C | 88 | 7.4 | Yes | Yes | 15.4 | 15 | 0.4 | 8C1E4C80C2B54E36B36BBEB0B9C7EC8D |  | R22 | TXV |  | 8.409% | 0.91591 | 16.16% | [5 empty] | TXV | 8.409%
Fresno | CA | 93722-4508 |  | 2012-05-23 | 2012-05-23 11:48 | 2012-05-23 12:05 | TAPPAN - RTA-22-75-41-S | 41 | 1.2 | Yes | Yes | 22.9 | 19.9 | 3 | D887E1773B874C5AB8962DC9A7979A0C |  | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Manteca | CA | 95336-3601 |  | 2012-05-18 | 2012-05-18 12:38 | 2012-05-18 12:58 | CARRIER - 38CK036340 | 70 | 2.1 | Yes | Yes | 21.8 | 20.4 | 1.4 | D775BC2A1BAF4547A24561C8756F7BC0 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Firebaugh | CA | 93622-2325 |  | 2012-05-31 | 2012-05-31 13:37 | 2012-05-31 13:55 | DAY & NIGHT - 588ANW060100AEAG | 112 | 3.4 | Yes | Yes | 25.6 | 21.7 | 3.9 | 31D433D0531C4ABCAE41ECA9B70D8194 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Planada | CA | 95365-0000 |  | 2012-05-23 | 2012-05-23 12:53 | 2012-05-23 13:10 | WESTINGHOUSE - FS3BA-024KA | 64 | 5.2 | Yes | Yes | 18.8 | 19.5 | -0.7 | F21C9049014147A69DD5A7E40594D31B |  | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Stockton | CA | 95204-5833 |  | 2012-07-06 | 2012-07-06 15:18 | 2012-07-06 15:37 | RHEEM - 13AJM18A01 | 75 | 5 | Yes | Yes | 19.9 | 19.9 | 0 | DA3D56BF3B3845B79AC9E31A80E5D522 |  | R410A | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Newman | CA | 95360-2411 |  | 2012-05-30 | 2012-05-30 10:12 | 2012-05-30 10:31 | OTHER - TZAA-3362A757 | 76 | 5.3 | Yes | Yes | 19.4 | 19.9 | -0.5 | 6C06AB2451AC40E1BF21C8674185E9F3 |  | R22 | Non-TXV |  | 6.974% | 0.93026 | 13.4% | [5 empty] | Non-TXV | 6.974%
Los Banos | CA | 93635-3778 |  | 2012-05-23 | 2012-05-23 15:13 | 2012-05-23 15:13 | DAY & NIGHT - 567CJ018 | 64 | 2.5 | Yes | Yes | 21.9 | 24 | -2.1 | 4EB9AB70CBB04C9990A7DAB9BDE2E136 | Add refrigerant: 2.5 oz Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.906% | 0.96094 | 7.507% | [5 empty] | Non-TXV | 3.906%
Merced | CA | 95341-6879 |  | 2012-05-24 | 2012-05-24 14:08 | 2012-05-24 14:33 | GOODMAN - CKL241H | 72 | 5.1 | Yes | Yes | 25.5 | 21 | 4.5 | F3FDC38DF37F46B6A1BEF4E0CD342FEA |  | R22 | Non-TXV |  | 7.083% | 0.92917 | 13.61% | [5 empty] | Non-TXV | 7.083%
Stockton | CA | 95204-5833 |  | 2012-07-02 | 2012-07-02 16:02 | 2012-07-02 16:18 | GOODMAN - CK18-1B | 53 | 4.2 | Yes | Yes | 25.1 | 20.9 | 4.2 | CD3BD8DFB4E04D8494A35C80B9C76143 |  | R22 | Non-TXV |  | 7.925% | 0.92075 | 15.23% | [5 empty] | Non-TXV | 7.925%
Livingston | CA | 95334-1324 |  | 2012-05-22 | 2012-05-22 14:14 | 2012-05-22 14:31 | WEATHER KING - 10AJB36A01 | 78 | 5.1 | Yes | Yes | 19.5 | 18.5 | 1 | 598A1EA72AF843729A195BC5E4CC9AA5 |  | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Oakdale | CA | 95361-9457 |  | 2012-05-23 | 2012-05-23 10:34 | 2012-05-23 10:53 | - AG030GB2 | 74 | 13.7 | Yes | Yes | 18.8 | 19.1 | -0.3 | C8C094594C0A4E96A8AEC60929D8C1D7 |  | R22 | Non-TXV |  | 18.51% | 0.81486 | 35.58% | [5 empty] | Non-TXV | 18.51%
Dos Palos | CA | 93620-9405 |  | 2012-06-08 | 2012-06-08 11:18 | 2012-06-08 11:36 | OTHER - UNK | 136 | 13 | Yes | Yes | 18.4 | 19.4 | -1 | 4C3CF0230BB0415F8870F98440FC4256 |  | R22 | Non-TXV |  | 9.559% | 0.90441 | 18.37% | [5 empty] | Non-TXV | 9.559%
Fresno | CA | 93710-3628 |  | 2012-08-02 | 2012-08-02 11:41 | 2012-08-02 11:41 | BRYANT - 574BNW030060NB | 128 | 0 | Yes | Yes | 17.6 | 19.9 | -2.3 | BE2E0C8D6F8046B2A314477F32571B4D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-1315 |  | 2012-05-22 | 2012-05-22 12:21 | 2012-05-22 12:38 | RHEEM - RNL-B024JK06X | 78 | 8.4 | Yes | Yes | 23.8 | 20.8 | 3 | BC2DD9F57C6844B3B1148E3916B49F31 |  | R410A | Non-TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | Non-TXV | 10.77%
Stockton | CA | 95207-4271 |  | 2012-06-12 | 2012-06-12 09:21 | 2012-06-12 09:40 | GOODMAN - CSC130241AE | 93 | 6.8 | Yes | Yes | 17 | 19.1 | -2.1 | 3027F8814E324EADB882111CE61AA31C |  | R22 | Non-TXV |  | 7.312% | 0.92688 | 14.05% | [5 empty] | Non-TXV | 7.312%
Oakdale | CA | 95361-3418 |  | 2012-06-07 | 2012-06-07 14:28 | 2012-06-07 14:45 | RUUD - UNK | 54 | 2.2 | Yes | Yes | 19.9 | 21.3 | -1.3 | 8747B6EE112B4870B436EE0AA2DAA6B9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
San Andreas | CA | 95249-9684 |  | 2012-07-19 | 2012-07-19 09:07 | 2012-07-19 09:23 | BDP - 597CN048-B | 168 | -11.9 | Yes | Yes | 19.6 | 18.8 | 0.8 | 526D2F16C5264879BBF8A524EE2D59D8 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Oakdale | CA | 95361-2909 |  | 2012-05-23 | 2012-05-23 11:49 | 2012-05-23 12:11 | CARRIER - 48SS-036060331-- | 67 | 2.1 | Yes | Yes | 19.1 | 20.6 | -1.5 | 7AE525A509894428AED5825DD0BEF269 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Planada | CA | 95365-0000 |  | 2012-05-23 | 2012-05-23 13:13 | 2012-05-23 13:30 | WESTINGHOUSE - FS3BA-024KA | 64 | 5.3 | Yes | Yes | 19.7 | 19.7 | 0 | 34FDF5BB69C44CAF966A0404EF0725BA |  | R22 | Non-TXV |  | 8.281% | 0.91719 | 15.91% | [5 empty] | Non-TXV | 8.281%
Sanger | CA | 93657-2934 |  | 2012-08-09 | 2012-08-09 08:59 | 2012-08-09 09:27 | CARRIER - 48VLNA4809030 | 149 | 27.7 | Yes | Yes | 21.8 | 19.3 | 2.5 | E0D61E8E9ADE448C9DBE6048A9D994D7 |  | R410A | Non-TXV |  | 18.59% | 0.81409 | 35.73% | [5 empty] | Non-TXV | 18.59%
Stockton | CA | 95215-5437 |  | 2012-06-13 | 2012-06-13 11:26 | 2012-06-13 11:45 | RUUD - URKA-A042JK08X | 69 | 3.3 | Yes | Yes | 18.9 | 19.5 | -0.6 | 4E20865B97E24BC6980C7CFDC1E2DF08 |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Fresno | CA | 93710-5745 |  | 2012-08-10 | 2012-08-10 20:14 | 2012-08-10 20:14 | BDP - UNK | 77 | 0 | Yes | Yes | 18.8 | 19.6 | -0.8 | 74BC1921B3A84A4490E242BEBA0340F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5742 |  | 2012-05-30 | 2012-05-30 13:01 | 2012-05-30 13:21 | BDP - 58ANW060080ADAG | 112 | 3.4 | Yes | Yes | 22.9 | 21 | 1.9 | 7BE657CD7F514B4A9E3CB0E13FEAD924 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Los Banos | CA | 93635-3771 |  | 2012-05-23 | 2012-05-23 15:45 | 2012-05-23 16:05 | TRANE - BTD724A100C0 | 68 | -4 | Yes | Yes | 21.9 | 20.4 | 1.5 | 6C4597762A9445B6A9BB7184892CD761 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Dos Palos | CA | 93620-2617 |  | 2012-05-31 | 2012-05-31 10:11 | 2012-05-31 10:34 | BRYANT - 113RNA048000BCAA | 117 | -4.4 | Yes | Yes | 18.2 | 19.5 | -1.3 | E600036A60E646FA945771206F927948 |  | R22 | TXV |  | -3.761% | 1.0376 | 1.053% |  |  |  |  | TXV |  |  | -3.761%
Fresno | CA | 93725-1201 |  | 2012-08-10 | 2012-08-10 11:25 | 2012-08-10 11:43 | RHEEM - N/A | 90 | 8.2 | Yes | Yes | 21.1 | 16.4 | 4.7 | FEBF426E56BE428CBBF2D4911527DB74 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.111% | 0.90889 | 17.51% | [5 empty] | Non-TXV | 9.111%
Los Banos | CA | 93635-3778 |  | 2012-07-05 | 2012-07-05 10:24 | 2012-07-05 10:46 | BDP - 567GJ018 | 64 | 7.4 | Yes | Yes | 16.3 | 17.6 | -1.3 | C4FA6635826F4E0C9B2A7218037C03B6 |  | R22 | Non-TXV |  | 11.56% | 0.88438 | 22.22% | [5 empty] | Non-TXV | 11.56%
Oakdale | CA | 95361-3346 |  | 2012-06-12 | 2012-06-12 11:38 | 2012-06-12 11:59 | PAYNE - PYP1NB042060AAAA | 100 | 2.9 | Yes | Yes | 25.1 | 21.4 | 3.7 | 4232E59BC3BE4CE4A6FAD482324F2950 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Clovis | CA | 93611-6691 |  | 2012-08-08 | 2012-08-08 17:41 | 2012-08-08 17:41 | LENNOX - 13AC-060-230-01 | 168 | 0 | Yes | Yes | 18.5 | 19.8 | -1.3 | F78DED5C71DA4BDAA9FFCB6F629DF7D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4044 |  | 2012-06-11 | 2012-06-11 12:08 | 2012-06-11 12:33 | CARRIER - 591ANX042000AAAA | 106 | 3.7 | Yes | Yes | 20.6 | 20.8 | -0.2 | 9557823A6DE0423B91F984E8E91A986A |  | R22 | Non-TXV |  | 3.491% | 0.96509 | 6.708% | [5 empty] | Non-TXV | 3.491%
Fresno | CA | 93720-1492 |  | 2012-06-13 | 2012-06-13 12:43 | 2012-06-13 12:43 | RHEEM - RRNL-B042JK08X | 112 | 0 | Yes | Yes | 25.2 | 21.5 | 3.7 | 4572365B61F74927A95518293B6A213C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Live Oak | CA | 95953-2240 |  | 2012-05-24 | 2012-05-24 11:14 | 2012-05-24 11:36 | ICP - PGC048K080E----- | 100 | 5 | Yes | Yes | 24.2 | 20.1 | 4.1 | 860F1781AC5442AD80DFE7A37E4499D1 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Atwater | CA | 95301-3953 |  | 2012-05-23 | 2012-05-23 14:30 | 2012-05-23 14:55 | RUUD - NA | 45 | 1.4 | Yes | Yes | 24.5 | 21.7 | 2.9 | 6A56F7E019444D0F8445728DF03C08E3 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Olivehurst | CA | 95961-0000 |  | 2012-07-23 | 2012-07-23 13:13 | 2012-07-23 13:29 | RUUD - URGG-10E43JKR | 109 | 3.3 | Yes | Yes | 20 | 20.4 | -0.4 | DACAEF12459248728BB1737A6598DB05 |  | R22 | Non-TXV |  | 3.028% | 0.96972 | 5.818% | [5 empty] | Non-TXV | 3.028%
Clovis | CA | 93612-2367 |  | 2012-05-22 | 2012-05-22 12:57 | 2012-05-22 13:18 | RHEEM - UNK | 56 | -3.3 | Yes | Yes | 17.8 | 20.4 | -2.6 | F2B345C1287F440E98E575153DDF85E4 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Merced | CA | 95341-7023 |  | 2012-06-08 | 2012-06-08 14:35 | 2012-06-08 14:56 | GOODMAN - CLJ301A | 105 | 7.6 | Yes | Yes | 28.3 | 23.6 | 4.7 | 448CD9E34AD245A0883D969AC85313D5 |  | R22 | Non-TXV |  | 7.238% | 0.92762 | 13.91% | [5 empty] | Non-TXV | 7.238%
Merced | CA | 95341-6884 |  | 2012-05-24 | 2012-05-24 13:01 | 2012-05-24 13:30 | YORK - H1DB024S06A | 67 | 6.3 | Yes | Yes | 20.1 | 20.3 | -0.2 | 7283C53008AA430CAC3EF8A65FE28701 |  | R22 | Non-TXV |  | 9.403% | 0.90597 | 18.07% | [5 empty] | Non-TXV | 9.403%
Los Banos | CA | 93635-3774 |  | 2012-05-23 | 2012-05-23 10:32 | 2012-05-23 10:55 | TRANE - BTD724A100C0 | 68 | -4 | Yes | Yes | 17.5 | 18.5 | -1 | E10DF37EB8B44F279FF825DDE6B460A3 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Merced | CA | 95341-6874 |  | 2012-05-24 | 2012-05-24 11:36 | 2012-05-24 12:10 | YORK - H1DB024S06A | 67 | 9 | Yes | Yes | 24.4 | 20.1 | 4.3 | AD43B31218A24035BB7E3BD374FF99C0 |  | R22 | Non-TXV |  | 13.43% | 0.86567 | 25.81% | [5 empty] | Non-TXV | 13.43%
Paso Robles | CA | 93446-5435 |  | 2012-07-13 | 2012-07-13 15:05 | 2012-07-13 15:24 | CARRIER - 38EZG030300 | 88 | 3 | Yes | Yes | 18.4 | 20.9 | -2.5 | 00ECD9C6B4454C259EFB8E049C3BA480 |  | R410A | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Orland | CA | 95963-1977 |  | 2012-06-08 | 2012-06-08 15:23 | 2012-06-08 15:23 | YORK - D3YS02N03206B | 62 | 0 | Yes | Yes | 21.2 | 22.4 | -1.2 | B2F099F8EF514283A1C89D407DAFFE41 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3773 |  | 2012-06-08 | 2012-06-08 16:03 | 2012-06-08 16:31 | TRANE - BTD724A100C0 | 68 | -4 | Yes | Yes | 15.9 | 17.9 | -2 | 2DF94B4FFB42454DABD619B93E9A0EDC |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Merced | CA | 95341-6870 |  | 2012-05-24 | 2012-05-24 10:26 | 2012-05-24 10:26 | YORK - H1DB024S068A | 67 | 0 | Yes | Yes | 43.4 | 10.8 | 32.6 | D96BAAC56A3640CFB53ED6031A87158B | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0000 |  | 2012-05-24 | 2012-05-24 12:42 | 2012-05-24 13:02 | LENNOX - 13ACD-048-230-02 | 204 | 7.4 | Yes | Yes | 23 | 19.9 | 3.1 | DE68F8D0D02140A7A232C1C808A47422 |  | R22 | Non-TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | Non-TXV | 3.627%
Fresno | CA | 93727-3346 |  | 2012-06-25 | 2012-06-25 16:11 | 2012-06-25 16:39 | YORK - D3NP024N03606A | 100 | 3.4 | Yes | Yes | 21.1 | 20.2 | 1 | 4CA370B5BF6346AE880C14CE89CE6E94 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Madera | CA | 93637-4866 |  | 2012-05-18 | 2012-05-18 11:38 | 2012-05-18 11:55 | LENNOX - 13ACC-042-230-02 | 123 | 3.7 | Yes | Yes | 24.6 | 20.7 | 3.9 | B1BD04146D374D17843ABA5115CB2189 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.781% | [5 empty] | Non-TXV | 3.008%
Paso Robles | CA | 93446-5434 |  | 2012-07-13 | 2012-07-13 14:36 | 2012-07-13 14:53 | CARRIER - 38EZG030300 | 88 | 2.6 | Yes | Yes | 15.3 | 16.1 | -0.8 | AF84F11A270949C884237A4AEE15CF39 |  | R410A | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Los Banos | CA | 93635-3779 |  | 2012-06-08 | 2012-06-08 10:06 | 2012-06-08 10:45 | DAY & NIGHT - 567GJ018 | 64 | -7.5 | Yes | Yes | 18.5 | 17.3 | 1.2 | C3A6EC24F7A044CA9AAA4C99281BA928 |  | R22 | Non-TXV |  | -11.72% | 1.1172 | 3.282% |  |  |  |  | Non-TXV |  |  | -11.72%
Clovis | CA | 93611-3108 |  | 2012-07-05 | 2012-07-05 13:59 | 2012-07-05 14:06 | CARRIER - 48ESNA4206030 | 63 | 2.4 | Yes | Yes | 19 | 20.2 | -1.2 | 82067F70CDEA4125AD005F0C122AC0DC |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Oakdale | CA | 95361-9506 |  | 2012-06-07 | 2012-06-07 15:06 | 2012-06-07 15:26 | GOODMAN - VSC130361BA | 83 | 2.7 | Yes | Yes | 18.5 | 20.7 | -2.2 | 6628F7A88B2B459C904E4CF331B0627B |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Fresno | CA | 93727-3347 |  | 2012-05-31 | 2012-05-31 11:47 | 2012-05-31 12:08 | RHEEM - N/A | 60 | 26.8 | Yes | Yes | 25.6 | 20.4 | 5.2 | 3448C01E636D4F5C9B17F43B85B6F3E3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 44.67% | 0.55333 | 85.84% | [5 empty] | Non-TXV | 44.67%
Riverdale | CA | 93656-9713 |  | 2012-07-19 | 2012-07-19 09:29 | 2012-07-19 09:51 | TEMPSTAR - PGAA29C1K1 | 74 | 2.2 | Yes | Yes | 23.2 | 18.5 | 4.7 | D0E787F334F04AEF90E03930D7103C63 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Stockton | CA | 95206-5322 |  | 2012-05-24 | 2012-05-24 16:03 | 2012-05-24 16:03 | RHEEM - RAHE-036JAS | 91 | 0 | Yes | Yes | 21.3 | 19.7 | 1.6 | D364D6FC70B2409DBE113A69049339D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3779 |  | 2012-05-23 | 2012-05-23 11:55 | 2012-05-23 12:20 | BDP - 567GJ018 | 64 | 2.6 | Yes | Yes | 19.8 | 16.6 | 3.2 | E184ED0397D74BBF948709DF66CCA367 |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Merced | CA | 95340-3373 |  | 2012-06-12 | 2012-06-12 08:59 | 2012-06-12 08:59 | RHEEM - UNK | 80 | -7.5 | Yes | Yes | 13.9 | 20.4 | -6.5 | 323DB21C70894D3A9F96797D9DE69BDF | Remove refrigerant: 7.5 oz Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Riverdale | CA | 93656-9713 |  | 2012-07-19 | 2012-07-19 10:10 | 2012-07-19 10:28 | HEIL - PGC030K060A | 52 | 1.6 | Yes | Yes | 23.8 | 18.6 | 5.2 | DC0A187F8E104785B7FC0AF6A0F15FCD |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Chico | CA | 95928-5780 |  | 2012-05-21 | 2012-05-21 15:24 | 2012-05-21 15:24 | TRANE - YCC018F1LOBH | 85 | 0 | Yes | Yes | 21.3 | 22.6 | -1.3 | DFF47EFBA1004EAF900A53DCEC8FEC67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0892 |  | 2012-08-09 | 2012-08-09 17:23 | 2012-08-09 19:58 | LENNOX - HS22-511-1P | 80 | 2.7 | Yes | Yes | 20.3 | 21.3 | -1 | D5BEFCF3F31044598E371A4DD3F87369 |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Los Banos | CA | 93635-3781 |  | 2012-05-23 | 2012-05-23 16:48 | 2012-05-23 17:14 | DAY & NIGHT - 567GJ024 | 76 | 2.2 | Yes | Yes | 24.1 | 22.4 | 1.7 | B43D96B88B0A4688AAE30D6067D4F174 |  | R22 | Non-TXV |  | 2.895% | 0.97105 | 5.563% | [5 empty] | Non-TXV | 2.895%
Winton | CA | 95388-9730 |  | 2012-05-18 | 2012-05-18 10:56 | 2012-05-18 11:21 | BRYANT - 574ANW030060NB | 96 | 9.9 | Yes | Yes | 20.3 | 20.4 | -0.1 | 234F9636A5294328B1EC066C5D41C3E4 |  | R22 | Non-TXV |  | 10.31% | 0.89687 | 19.82% | [5 empty] | Non-TXV | 10.31%
Lathrop | CA | 95330-9759 |  | 2012-05-31 | 2012-05-31 13:18 | 2012-05-31 13:37 | OTHER - GCGD36S41S3A | 73 | 4.7 | Yes | Yes | 22 | 19.1 | 3 | EBD8F01C2E1E4963B66878CE15D5B62E |  | R410A | Non-TXV |  | 6.438% | 0.93562 | 12.37% | [5 empty] | Non-TXV | 6.438%
Planada | CA | 95365-0000 |  | 2012-05-23 | 2012-05-23 14:47 | 2012-05-23 15:12 | WESTINGHOUSE - FS3BA-024KA | 64 | 3.1 | Yes | Yes | 18.8 | 19.3 | -0.5 | DEEEA1D9776841FCB6F07664872FF052 |  | R22 | Non-TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | Non-TXV | 4.844%
Stockton | CA | 95204-5831 |  | 2012-06-19 | 2012-06-19 15:51 | 2012-06-19 16:12 | COLEMAN - BRCS0181BB | 56 | 5.5 | Yes | Yes | 19.7 | 20.4 | -0.7 | 40922FB1FA784383AC263B4EE23E42C1 |  | R22 | Non-TXV |  | 9.821% | 0.90179 | 18.87% | [5 empty] | Non-TXV | 9.821%
Riverdale | CA | 93656-9713 |  | 2012-07-19 | 2012-07-19 11:10 | 2012-07-19 11:32 | TEMPSTAR - PGAA29C1K1 | 74 | 2.5 | Yes | Yes | 21.7 | 17.2 | 4.5 | 6DD75B9CF8BD467A997280D5C2724F4B |  | R22 | Non-TXV |  | 3.378% | 0.96622 | 6.492% | [5 empty] | Non-TXV | 3.378%
Paso Robles | CA | 93446-5436 |  | 2012-07-13 | 2012-07-13 13:25 | 2012-07-13 13:43 | CARRIER - 38EZG024300 | 80 | 2.4 | Yes | Yes | 17.7 | 18.6 | -0.9 | 648DC5F7DD264AF9B8BB8891A3245C11 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-5831 |  | 2012-06-19 | 2012-06-19 15:22 | 2012-06-19 15:43 | RHEEM - 13AJM18A01 | 75 | 5.7 | Yes | Yes | 20.1 | 18.8 | 1.3 | 55B3DE894B6246948884357440CBD832 |  | R410A | Non-TXV |  | 7.6% | 0.924 | 14.61% | [5 empty] | Non-TXV | 7.6%
Los Banos | CA | 93635-3800 |  | 2012-06-13 | 2012-06-13 13:21 | 2012-06-13 13:39 | GIBSON - JS5BD-024K | 104 | 3.7 | Yes | Yes | 19.6 | 18.9 | 0.7 | 00B7F84761BA4524967E964CBE3B0296 |  | R22 | Non-TXV |  | 3.558% | 0.96442 | 6.837% | [5 empty] | Non-TXV | 3.558%
Merced | CA | 95340-2615 |  | 2012-06-11 | 2012-06-11 09:08 | 2012-06-11 09:30 | GOODMAN - GSC130241DA | 83 | 10.4 | Yes | Yes | 24.1 | 24.1 | 0 | CECDA0FFB5AB40CC808C883AE318B4C4 |  | R22 | Non-TXV |  | 12.53% | 0.8747 | 24.08% | [5 empty] | Non-TXV | 12.53%
Los Banos | CA | 93635-3781 |  | 2012-05-23 | 2012-05-23 17:37 | 2012-05-23 17:37 | DAY & NIGHT - 567GJ018 | 64 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | 1D2B89BE61874DF6BBEB27F9CC677816 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-5833 |  | 2012-07-02 | 2012-07-02 16:20 | 2012-07-02 16:36 | OTHER - BRCS0181BB | 56 | 2.1 | Yes | Yes | 21.3 | 20.1 | 1.2 | 42DC591ED8D54686B262D5F34F3C8842 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95205-2839 |  | 2012-06-07 | 2012-06-07 12:53 | 2012-06-07 13:11 | BRYANT - 561CJ030-E | 67 | 6.1 | Yes | Yes | 17.6 | 19.2 | -1.6 | F05207392B864FE6A3FBB4286352CE36 |  | R22 | TXV |  | 9.104% | 0.90896 | 17.5% | [5 empty] | TXV | 9.104%
Chico | CA | 95928-6044 |  | 2012-05-24 | 2012-05-24 17:38 | 2012-05-24 17:53 | TRANE - YCCO18F1LOBJ | 62 | 2.3 | Yes | Yes | 20.5 | 21.3 | -0.8 | 9313D230D1524462A5223565F2421924 |  | R22 | Non-TXV |  | 3.71% | 0.9629 | 7.129% | [5 empty] | Non-TXV | 3.71%
Planada | CA | 95365-0000 |  | 2012-06-14 | 2012-06-14 11:28 | 2012-06-14 11:52 | OTHER - FS3BA024KA | 64 | 8.9 | Yes | Yes | 21.3 | 24.1 | -2.8 | 2B7DF9BB7CAB4045B40E5D34C0024E68 |  | R22 | Non-TXV |  | 13.91% | 0.86094 | 26.72% | [5 empty] | Non-TXV | 13.91%
Dos Palos | CA | 93620-2236 |  | 2012-06-08 | 2012-06-08 10:12 | 2012-06-08 10:33 | PAYNE - 30RAC1S4T | 133 | 8.8 | Yes | Yes | 21.7 | 19.1 | 2.6 | 65E2BD323B9E47869286A3796E8768EA |  | R22 | Non-TXV |  | 6.617% | 0.93383 | 12.72% | [5 empty] | Non-TXV | 6.617%
Merced | CA | 95341-6868 |  | 2012-05-24 | 2012-05-24 09:46 | 2012-05-24 10:09 | YORK - HLDB024S068 | 67 | 9.2 | Yes | Yes | 23.1 | 19.3 | 3.8 | DEEBBC16139247FCBB392E8E26C67F4D |  | R22 | Non-TXV |  | 13.73% | 0.86269 | 26.39% | [5 empty] | Non-TXV | 13.73%
Los Banos | CA | 93635-9409 |  | 2012-06-07 | 2012-06-07 15:26 | 2012-06-07 15:48 | BRYANT - 561CJ042-B | 86 | 2.6 | Yes | Yes | 17.4 | 19.9 | -2.5 | 3C432A02C1AD4B4B97DE8CEC53939405 |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Durham | CA | 95938-9600 |  | 2012-07-13 | 2012-07-13 17:13 | 2012-07-13 17:32 | JANITROL - CL1-341A8 | 85 | 2.6 | Yes | Yes | 25.1 | 21.4 | 3.7 | 03D38493AB18477C868D3370D36D25CA |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Stockton | CA | 95205-2639 |  | 2012-05-21 | 2012-05-21 18:37 | 2012-05-21 19:00 | PAYNE - PA10JA024-A | 68 | 3.2 | Yes | Yes | 17.6 | 19.3 | -1.7 | 43E3C35E4FE34428952344A626B40165 |  | R22 | TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | TXV | 4.706%
Ripon | CA | 95366-2179 |  | 2012-06-11 | 2012-06-11 14:50 | 2012-06-11 15:16 | DAY & NIGHT - 565AJ024 | 70 | 2.2 | Yes | Yes | 20.8 | 22.3 | -1.5 | 08CBD6F258D041228489DAFDE616947C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Stockton | CA | 95210-1452 |  | 2012-05-18 | 2012-05-18 15:39 | 2012-05-18 15:56 | YORK - D3NZ030N05606NXA | 64 | 2.1 | Yes | Yes | 24.7 | 20.2 | 4.5 | FD496B4CB6E54DCF93AB1E6ECB612E3F | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Fresno | CA | 93727-3346 |  | 2012-05-31 | 2012-05-31 18:38 | 2012-05-31 19:03 | RHEEM - N/A | 60 | 15.2 | Yes | Yes | 0.4 | 19.5 | -19.1 | DAEFB571532C404AA293F5340A0C8015 |  | R22 | Non-TXV |  | 25.33% | 0.74667 | 48.69% | [5 empty] | Non-TXV | 25.33%
Stockton | CA | 95206-6390 |  | 2012-05-30 | 2012-05-30 17:11 | 2012-05-30 17:33 | GOODMAN - CLJ42-1A | 99 | 3 | Yes | Yes | 23 | 20.4 | 2.6 | 9DD93DB8126442A69ADF852A7290C6AB |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Clovis | CA | 93611-7152 |  | 2012-08-08 | 2012-08-08 18:04 | 2012-08-08 18:21 | RUUD - UNK | 89 | 8.3 | Yes | Yes | 18.5 | 20.4 | -1.9 | 49878D3BFC994361B2CED0AD76348830 |  | R22 | Non-TXV |  | 9.326% | 0.90674 | 17.92% | [5 empty] | Non-TXV | 9.326%
Chico | CA | 95926-3684 |  | 2012-05-24 | 2012-05-24 10:16 | 2012-05-24 10:16 | DAY & NIGHT - 661BJ024-C | 89 | 0 | Yes | Yes | 19.8 | 21.3 | -1.5 | 5273BFB1EBCF4BAFA229737108469A5C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2122 |  | 2012-06-13 | 2012-06-13 12:34 | 2012-06-13 12:50 | BRYANT - 561CJ030-D | 68 | -4 | Yes | Yes | 22.4 | 20.1 | 2.3 | FA890DEE562B4EE7A9F2CDAC64FD3B03 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Merced | CA | 95341-5138 |  | 2012-05-21 | 2012-05-21 10:50 | 2012-05-21 11:17 | CARRIER - 48GS024040301 | 85 | 7.5 | Yes | Yes | 22.7 | 20.3 | 2.4 | 89969742FAD646C485A42645A8ABDC3E |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Cutler | CA | 93615-9717 |  | 2012-07-23 | 2012-07-23 14:43 | 2012-07-23 15:21 | CARRIER - 591ANX0360000AAAA | 81 | 2.6 | Yes | Yes | 17.9 | 20.8 | -2.9 | 121FFD33EFE74FC283B088EDCF8B2A41 |  | R22 | Non-TXV |  | 3.21% | 0.9679 | 6.169% | [5 empty] | Non-TXV | 3.21%
Chico | CA | 95926-4286 |  | 2012-05-28 | 2012-05-28 11:09 | 2012-05-28 12:05 | DAY N NIGHT - 585CJ030050 | 78 | 3.6 | Yes | Yes | 23.5 | 20.4 | 3.1 | 2EC6EA24E7CD4098BF0529EC92C65C3B |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Atascadero | CA | 93422-5576 |  | 2012-07-10 | 2012-07-10 14:49 | 2012-07-10 15:07 | RHEEM - RACA-018AAQ | 30 | 2.7 | Yes | Yes | 20 | 20.4 | -0.4 | CD56847A54A1485AB634656251652BE4 |  | R22 | Non-TXV |  | 9% | 0.84118 | 30.52% | [5 empty] | Non-TXV | 9%
Fresno | CA | 93711-6048 |  | 2012-05-30 | 2012-05-30 14:33 | 2012-05-30 15:11 | ICP - GPCM048K080D | 100 | 2.9 | Yes | Yes | 21 | 18.3 | 2.7 | B365A3AD94DE41468615DD9A434BADB6 |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Stockton | CA | 95207-7620 |  | 2012-06-01 | 2012-06-01 14:26 | 2012-06-01 14:42 | PAYNE - 567C018RCU | 37 | 4.5 | Yes | Yes | 21.5 | 21.8 | -0.3 | B4F3DA8E0ECE4AAAB6AF52CE47F71AB7 |  | R22 | Non-TXV |  | 12.16% | 0.87838 | 23.37% | [5 empty] | Non-TXV | 12.16%
Willows | CA | 95988-2711 |  | 2012-06-08 | 2012-06-08 10:11 | 2012-06-08 10:27 | YORK - DCYP-F024N045A | 70 | 4.4 | Yes | Yes | 25.4 | 22.9 | 2.5 | A99809A78E054C80A48AA9969B8B0614 |  | R22 | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Tracy | CA | 95376-1326 |  | 2012-06-14 | 2012-06-14 10:38 | 2012-06-14 10:56 | DAY & NIGHT - 591ANX030000ABAA | 67 | 4.7 | Yes | Yes | 26 | 22.1 | 3.9 | 73B552F5FB1D4C849A002026704E2E53 |  | R22 | Non-TXV |  | 7.015% | 0.92985 | 13.48% | [5 empty] | Non-TXV | 7.015%
Paso Robles | CA | 93446-5429 |  | 2012-07-09 | 2012-07-09 15:17 | 2012-07-09 15:35 | CARRIER - 38EZG030300 | 88 | 2.8 | Yes | Yes | 20.8 | 23.1 | -2.3 | EFAAE9F96D99480AA5B39EB4C21EC7A7 |  | R410A | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Mendota | CA | 93640-0000 |  | 2012-08-15 | 2012-08-15 10:03 | 2012-08-15 10:28 | BRYANT - 113RNA036C | 88 | 7.7 | Yes | Yes | 18.7 | 12.8 | 5.9 | A57FA0ACCD474B06A1EE8E97880F89EB |  | R22 | TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | TXV | 8.75%
Merced | CA | 95341-6988 |  | 2012-05-24 | 2012-05-24 16:37 | 2012-05-24 16:57 | PAYNE - PY1PNB036060ABAA | 68 | -4 | Yes | Yes | 26.3 | 22.4 | 3.9 | 243C26134452404B8B8AFE64FF013196 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95209-1880 |  | 2012-07-11 | 2012-07-11 11:31 | 2012-07-11 11:49 | BRYANT - 561CX024000AEAA | 58 | 2.4 | Yes | Yes | 19.3 | 19.9 | -0.6 | CDBD36A67C93478D9815CFF67EF67160 |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Fresno | CA | 93725-1223 |  | 2012-05-24 | 2012-05-24 16:18 | 2012-05-24 16:37 | AMERICAN STANDARD - YCX042F1M0BC | 85 | 5.7 | Yes | Yes | 26.2 | 21.8 | 4.5 | 98B5CBF751554211A5769F9D195A06CE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Paso Robles | CA | 93446-5435 |  | 2012-07-13 | 2012-07-13 14:05 | 2012-07-13 14:23 | CARRIER - 38EZG030300 | 88 | 2.6 | Yes | Yes | 15.5 | 18 | -2.5 | AFB82A6020B240F28D081EF3DB4906E8 |  | R410A | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Los Banos | CA | 93635-4802 |  | 2012-05-24 | 2012-05-24 15:07 | 2012-05-24 15:30 | BRYANT - 563N036-C | 104 | 4.1 | Yes | Yes | 26.1 | 20.2 | 6 | CB88FCEEBDCB49E5BC2736985BB84657 |  | R22 | Non-TXV |  | 3.942% | 0.96058 | 7.576% | [5 empty] | Non-TXV | 3.942%
Cameron Park | CA | 95682-8113 |  | 2012-06-13 | 2012-06-13 17:08 | 2012-06-13 17:08 | GOODMAN - GSZ130301AC | 124 | 0 | Yes | Yes | 19.9 | 18.9 | 1 | 67C9F2048BA142B1A8BB35D6E5F04EC0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-5707 |  | 2012-06-11 | 2012-06-11 12:22 | 2012-06-11 12:38 | YORK - B1HH048A06B | 192 | 11 | Yes | Yes | 22.5 | 22.4 | 0.1 | 2E1D3242AD64492BBE6C869588C63F55 |  | R22 | Non-TXV |  | 5.729% | 0.94271 | 11.01% | [5 empty] | Non-TXV | 5.729%
Merced | CA | 95348-1655 |  | 2012-06-12 | 2012-06-12 08:43 | 2012-06-12 09:08 | GOODMAN - PGB030050-1 REV A | 56 | 1.7 | Yes | Yes | 20.5 | 18.7 | 1.8 | 1273766461B046DD93B9504995676F44 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Planada | CA | 95365-0000 |  | 2012-07-02 | 2012-07-02 10:44 | 2012-07-02 11:09 | WESTINGHOUSE - FS3BA-030KA | 68 | 4.2 | Yes | Yes | 20.5 | 18 | 2.5 | 8E6447FFD3B644B89E069EA4D56880BB |  | R22 | Non-TXV |  | 6.176% | 0.93824 | 11.87% | [5 empty] | Non-TXV | 6.176%
Fresno | CA | 93722-6728 |  | 2012-06-15 | 2012-06-15 11:03 | 2012-06-15 11:34 | BDP - 585HJW024040ABAF | 64 | 2.3 | Yes | Yes | 16.9 | 19.9 | -3 | D19D880E5D414CFF95A19C248CA4811A |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Tracy | CA | 95376-2136 |  | 2012-06-20 | 2012-06-20 10:34 | 2012-06-20 11:00 | PAYNE - 563CN024 | 87 | 3.5 | Yes | Yes | 17.9 | 19.9 | -2 | 94F4BA2D93384152A07419A2B0EF29C4 |  | R22 | TXV |  | 4.023% | 0.95977 | 7.731% | [5 empty] | TXV | 4.023%
Auburn | CA | 95602-2163 |  | 2012-07-19 | 2012-07-19 13:07 | 2012-07-19 13:26 | RHEEM - UNK PAINTED | 54 | 7.5 | Yes | Yes | 17 | 19.1 | -2.1 | E4AE0587C93E483E95A727F97AF48858 |  | R22 | Non-TXV |  | 13.89% | 0.86111 | 26.69% | [5 empty] | Non-TXV | 13.89%
Selma | CA | 93662-4324 |  | 2012-06-07 | 2012-06-07 09:14 | 2012-06-07 09:41 | UNITARY PRODUCTS GROUP - H2RC030S06G | 60 | 8.4 | Yes | Yes | 17.1 | 20 | -2.9 | 04D9F36C0F764DAA850343B58B28C87E |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Manteca | CA | 95336-5033 |  | 2012-05-18 | 2012-05-18 16:10 | 2012-05-18 16:30 | COLEMAN - 9536A901 | 56 | 4.2 | Yes | Yes | 21.9 | 21.4 | 0.5 | 06FDED4F833F41499EEFF4A131683DF0 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Fresno | CA | 93710-3618 |  | 2012-05-24 | 2012-05-24 10:29 | 2012-05-24 10:49 | INTERNATIONAL COMFORT PRODUCTS - PGF030K60E | 70 | 3 | Yes | Yes | 19.3 | 21 | -1.7 | 22714EF1ACA44A71887A61D0FE8CE972 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Biola | CA | 93606-0000 |  | 2012-07-20 | 2012-07-20 13:22 | 2012-07-20 13:55 | AMANA - PGB36C0702E | 64 | 1.9 | Yes | Yes | 24.4 | 19.9 | 4.5 | 0075F02A287D42DDB4C719DD5EC8DDB3 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Chico | CA | 95973-0461 |  | 2012-05-23 | 2012-05-23 15:35 | 2012-05-23 15:35 | YORK - H2RC036S06A | 83 | 0 | Yes | Yes | 19.8 | 22.1 | -2.2 | 247A06174D9C4BDBAC92E6352BED8C53 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3929 |  | 2012-05-29 | 2012-05-29 10:31 | 2012-05-29 10:52 | GOODMAN - CKL24-1 | 76 | -7.2 | Yes | Yes | 21 | 19.1 | 1.9 | A8593C0D0F1F4DEFB30EBD53FB6AAF03 |  | R22 | Non-TXV |  | -9.474% | 1.0947 | 2.653% |  |  |  |  | Non-TXV |  |  | -9.474%
Fresno | CA | 93722-4696 |  | 2012-06-01 | 2012-06-01 11:45 | 2012-06-01 12:35 | CARRIER - N/A | 90 | 2.7 | Yes | Yes | 19.7 | 20.7 | -1 | B5626438333248878EB1A6725494CB0E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Manteca | CA | 95337-6000 |  | 2012-05-21 | 2012-05-21 10:50 | 2012-05-21 11:09 | BRYANT - 567G042 | 84 | 2.9 | Yes | Yes | 27.5 | 21.5 | 6 | 4654E398F4C94C2D9BA257AD95908F7A |  | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Selma | CA | 93662-2413 |  | 2012-08-14 | 2012-08-14 09:25 | 2012-08-14 09:45 | UNITARY PRODUCTS GROUP - DAYQ-F048N080A | 70 | 2.2 | Yes | Yes | 16.6 | 19.4 | -2.8 | FE2ECA09A5AA43D2AB85C271DDB5D634 |  | R410A | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Stockton | CA | 95204-4953 |  | 2012-05-21 | 2012-05-21 10:33 | 2012-05-21 10:54 | YORK - H1RA024S06G | 59 | 2.2 | Yes | Yes | 15.9 | 18.6 | -2.7 | A7A828DC456D47B481881F18044D14BD |  | R22 | Non-TXV |  | 3.729% | 0.96271 | 7.166% | [5 empty] | Non-TXV | 3.729%
Fresno | CA | 93710-6431 |  | 2012-08-07 | 2012-08-07 15:55 | 2012-08-07 16:24 | RUUD - URMA-A036JK0E | 79 | 2.7 | Yes | Yes | 19.6 | 20.4 | -0.8 | 6DEBEB4E132F4393948CDD2839E48A05 |  | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Fresno | CA | 93710-6431 |  | 2012-08-07 | 2012-08-07 16:25 | 2012-08-07 16:25 | RUUD - URMA-A036JK0E | 79 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 168802AF768B4EB38FBA9248794C4286 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-9484 |  | 2012-05-22 | 2012-05-22 10:17 | 2012-05-22 10:35 | RHEEM - RRKA-A048JK10X | 75 | 2.9 | Yes | Yes | 18.7 | 18.7 | 0 | ECEEBBC10EC24C459A3F35438417324B |  | R22 | Non-TXV |  | 3.867% | 0.96133 | 7.431% | [5 empty] | Non-TXV | 3.867%
Fresno | CA | 93710-4307 |  | 2012-05-24 | 2012-05-24 12:48 | 2012-05-24 13:05 | PAYNE - UNK | 66 | -3.9 | Yes | Yes | 18.6 | 20.4 | -1.8 | 2FE395201DE04228BB1D9677C05E4722 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Clovis | CA | 93612-1581 |  | 2012-05-22 | 2012-05-22 17:28 | 2012-05-22 17:56 | PAYNE - 5856J018040 | 55 | 5.3 | Yes | Yes | 21.2 | 21.3 | 0 | FDB163E85983496399E7E4985D6B51BC |  | R22 | Non-TXV |  | 9.636% | 0.90364 | 18.52% | [5 empty] | Non-TXV | 9.636%
Parlier | CA | 93648-2444 |  | 2012-08-15 | 2012-08-15 12:51 | 2012-08-15 13:13 | OTHER - NRGF30DDB04 | 53 | 4.2 | Yes | Yes | 18.2 | 17.3 | 1 | AAD87FF0B38848A78EDA1D11BEE04921 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.925% | 0.92075 | 15.23% | [5 empty] | Non-TXV | 7.925%
Fresno | CA | 93711-1556 |  | 2012-08-10 | 2012-08-10 16:43 | 2012-08-10 17:04 | YORK - DINAAO036N03606C | 63 | 3.3 | Yes | Yes | 17.2 | 19.9 | -2.7 | 9FC2940A00B147739C18A25DFD8A8985 |  | R22 | Non-TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | Non-TXV | 5.238%
Stockton | CA | 95219-7129 |  | 2012-06-11 | 2012-06-11 16:02 | 2012-06-11 16:23 | CARRIER - 38CKC060370 | 131 | 4.8 | Yes | Yes | 17.6 | 20.2 | -2.6 | F9960BE94DAB466DBA612965C3AD977D |  | R22 | TXV |  | 3.664% | 0.96336 | 7.042% | [5 empty] | TXV | 3.664%
Fresno | CA | 93711-6508 |  | 2012-08-14 | 2012-08-14 19:09 | 2012-08-14 20:07 | YORK - DAYA-F042N090C | 76 | 3.5 | Yes | Yes | 18.7 | 20.2 | -1.5 | F4584D614C2D43D693E3C87C05CABD02 |  | R22 | Non-TXV |  | 4.605% | 0.95395 | 8.85% | [5 empty] | Non-TXV | 4.605%
Atwater | CA | 95301-3728 |  | 2012-06-06 | 2012-06-06 08:41 | 2012-06-06 08:59 | COLEMAN - DAYP-F036N070A | 108 | 3.2 | Yes | Yes | 10.6 | 12.6 | -2 | 9423E0D8924A482CB9760B20D365223E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Rocklin | CA | 95677-3650 |  | 2012-06-07 | 2012-06-07 17:04 | 2012-06-07 17:04 | CARRIER - 540JJ018 | 83 | 0 | Yes | Yes | 18.7 | 19.3 | -0.6 | E2FE428A78644595899128339A6E8A2E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fowler | CA | 93625-2660 |  | 2012-05-24 | 2012-05-24 17:21 | 2012-05-24 17:38 | CARRIER - N/A | 85 | 8.6 | Yes | Yes | 20.2 | 21.4 | -1.2 | 064C9D9941FD45659D52D6E6E2F33B92 |  | R22 | Non-TXV |  | 10.12% | 0.89882 | 19.44% | [5 empty] | Non-TXV | 10.12%
Paso Robles | CA | 93446-5436 |  | 2012-07-13 | 2012-07-13 12:51 | 2012-07-13 13:11 | CARRIER - 38EZG030300 | 88 | 10.7 | Yes | Yes | 16.9 | 19.3 | -2.4 | DD0ECB65D63F4CFAAF59B4FCD7CC2DF2 |  | R410A | Non-TXV |  | 12.16% | 0.87841 | 23.37% | [5 empty] | Non-TXV | 12.16%
Merced | CA | 95340-3326 |  | 2012-05-30 | 2012-05-30 10:47 | 2012-05-30 10:47 | PAYNE - 585EJ036075 | 82 | 0 | Yes | Yes | 21.4 | 19.1 | 2.3 | 13FCECF6EA324813AE04E4E19719FAC8 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4236 |  | 2012-06-07 | 2012-06-07 14:22 | 2012-06-07 14:39 | GOODMAN - GPC12240451A | 64 | 10.3 | Yes | Yes | 25.9 | 21 | 4.9 | A7E2CB148AFB439F968DCD60D7FC2EA0 |  | R22 | Non-TXV |  | 16.09% | 0.83906 | 30.93% | [5 empty] | Non-TXV | 16.09%
Caruthers | CA | 93609-9473 |  | 2012-06-15 | 2012-06-15 10:56 | 2012-06-15 11:14 | GUARDIAN - PG8030050-1 | 56 | 2 | Yes | Yes | 21.2 | 20.4 | 0.8 | 834B86BF689149D0A8B24237216D4E21 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Caruthers | CA | 93609-9473 |  | 2012-06-15 | 2012-06-15 11:17 | 2012-06-15 11:47 | GUARDIAN - PGB024050-1 | 54 | 2.2 | Yes | Yes | 19.2 | 21.3 | -2.1 | AF0E910FD8CF43D8AE256B8BE3CADE38 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Red Bluff | CA | 96080-4131 |  | 2012-05-23 | 2012-05-23 14:12 | 2012-05-23 15:13 | YORK - D1NA030N05606C | 75 | 2.4 | Yes | Yes | 21 | 23.5 | -2.5 | 33FAA7C99B794BCC900D4BAE718EBE98 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95207-4175 |  | 2012-06-08 | 2012-06-08 11:17 | 2012-06-08 11:41 | DAY & NIGHT - 585GJW024040ABAF | 54 | 7.3 | Yes | Yes | 23.2 | 18.8 | 4.4 | 9EF49632EE1F4F308C096B293138FFC6 |  | R22 | Non-TXV |  | 13.52% | 0.86481 | 25.98% | [5 empty] | Non-TXV | 13.52%
Shingle Springs | CA | 95682-8040 |  | 2012-08-02 | 2012-08-02 11:05 | 2012-08-02 11:28 | CARRIER - 38CKC036340 | 74 | -35.2 | Yes | Yes | 24.3 | 20.3 | 4 | E4E5BA80BDF9435D982DC5CBFDB84FA4 |  | R22 | TXV |  | -47.57% | 1.4757 | 13.32% |  |  |  |  | TXV |  |  | -47.57%
Paradise | CA | 95969-3841 |  | 2012-06-11 | 2012-06-11 11:36 | 2012-06-11 11:36 | RUUD - NA | 115 | 0 | Yes | Yes | 22.3 | 22 | 0.3 | BCBEFFA4FC2F4E1290D06AAFB27FAECA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4168 |  | 2012-08-14 | 2012-08-14 14:21 | 2012-08-14 14:52 | ICP - PGAA30C1K6 | 79 | 2.3 | Yes | Yes | 15.7 | 15.9 | -0.2 | 0F2B672E7D814BF4B0A4974178FC55FF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.911% | 0.97089 | 5.595% | [5 empty] | Non-TXV | 2.911%
Los Banos | CA | 93635-5442 |  | 2012-08-02 | 2012-08-02 11:14 | 2012-08-02 11:14 | DAY & NIGHT - 561AJ036-B | 76 | 0 | Yes | Yes | 22.9 | 21.5 | 1.4 | 7924B7AF456A44E5A01A995FE7F54904 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3326 |  | 2012-05-30 | 2012-05-30 13:41 | 2012-05-30 14:00 | BRYANT - 582ANW0300060NAAD | 55 | -4.5 | Yes | Yes | 24.8 | 21.2 | 3.6 | C0EA2B24AD724BF383B3A6083E31905B |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Tracy | CA | 95304-9327 |  | 2012-06-26 | 2012-06-26 18:24 | 2012-06-26 18:53 | DAY & NIGHT - 591ANX048000ABAA | 115 | 3.6 | Yes | Yes | 19.8 | 19.8 | 0 | FCA2356BC67745829B8D3E665AC320F1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.13% | 0.9687 | 6.016% | [5 empty] | Non-TXV | 3.13%
Clovis | CA | 93612-4230 |  | 2012-06-06 | 2012-06-06 14:22 | 2012-06-06 14:22 | OTHER - UNK | 70 | 0 | Yes | Yes | 20.2 | 21 | -0.8 | 727F7270A50145AB992DBD421721D3D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3770 |  | 2012-05-29 | 2012-05-29 15:21 | 2012-05-29 16:07 | TRANE - BTD724A100C0 | 68 | 2 | Yes | Yes | 17.7 | 19.9 | -2.2 | 739E1FFE908941B6BDD39640833C0120 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Merced | CA | 95341-5221 |  | 2012-07-02 | 2012-07-02 14:00 | 2012-07-02 14:16 | BDP - 585HJ030040 | 68 | 9.8 | Yes | Yes | 22.2 | 20.6 | 1.6 | 0BD99529F02549E0B467B43B28E13FAC |  | R22 | Non-TXV |  | 14.41% | 0.85588 | 27.7% | [5 empty] | Non-TXV | 14.41%
Stockton | CA | 95207-6040 |  | 2012-06-15 | 2012-06-15 09:33 | 2012-06-15 10:01 | RHEEM - UNK | 74 | -4.1 | Yes | Yes | 20.1 | 22.1 | -2 | 85478554333C4A9D9C1FDFF488F13476 |  | R22 | Non-TXV |  | -5.541% | 1.0554 | 1.552% |  |  |  |  | Non-TXV |  |  | -5.541%
Clovis | CA | 93612-4230 |  | 2012-06-06 | 2012-06-06 11:45 | 2012-06-06 11:59 | OTHER - UNK | 70 | 5.1 | Yes | Yes | 17.1 | 19.9 | -2.8 | C92F3D03E4BD4B968F783851D33A7E04 |  | R22 | Non-TXV |  | 7.286% | 0.92714 | 14% | [5 empty] | Non-TXV | 7.286%
Sanger | CA | 93657-2909 |  | 2012-07-23 | 2012-07-23 12:13 | 2012-07-23 13:07 | GOODMAN - CK36-1T | 76 | 2.8 | Yes | Yes | 20.1 | 21 | -0.9 | 60537B410395487181464DE6BA3F48E1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Clovis | CA | 93612-4233 |  | 2012-06-08 | 2012-06-08 15:16 | 2012-06-08 15:42 | GOODMAN - GPG12240451A | 64 | 2.7 | Yes | Yes | 18.5 | 21 | -2.5 | 552E2DD236AD42829B4348076AC88127 |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Planada | CA | 95365-8020 |  | 2012-06-06 | 2012-06-06 13:43 | 2012-06-06 14:42 | WESTINGHOUSE - FS3BA-030KA | 68 | 5.6 | Yes | Yes | 19.1 | 19.4 | -0.3 | CEC133897FDA492DA642060BAC9C6897 |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Los Banos | CA | 93635-3768 |  | 2012-07-14 | 2012-07-14 11:00 | 2012-07-14 11:19 | TRANE - BTD724A1000X0 | 68 | 2.1 | Yes | Yes | 20.5 | 19.8 | 0.7 | DEE4CE66D3CC403DB26FE862777DE351 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Paradise | CA | 95969-5719 |  | 2012-06-11 | 2012-06-11 12:58 | 2012-06-11 13:52 | GOODMAN - CRT36-1A | 140 | 22.7 | Yes | Yes | 20.7 | 22.9 | -2.2 | D6F1A4E2020A423CADC791D3510A4A24 |  | R22 | Non-TXV |  | 16.21% | 0.83786 | 31.16% | [5 empty] | Non-TXV | 16.21%
Atwater | CA | 95301-2844 |  | 2012-05-18 | 2012-05-18 14:00 | 2012-06-18 11:50 | DAY & NIGHT - NA | 50 | 0 | Yes | Yes | 19.9 | 20.9 | -1 | 485A5FBC7DFB43F18BC8096D90BE7EAE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1201 |  | 2012-06-08 | 2012-06-08 15:09 | 2012-06-08 15:09 | BDP - 585B030075YACR | 50 | 0 | Yes | Yes | 19.2 | 20.9 | -1.7 | 5F1528B28A8749DC9D1633E43FD51B21 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-1902 |  | 2012-07-11 | 2012-07-11 13:35 | 2012-07-11 15:40 | HEIL - CA3018VKA3 | 68 | 2.6 | Yes | Yes | 16.6 | 19 | -2.4 | 8C9658D38A594639872D3725B9C1E978 |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Merced | CA | 95341-6873 |  | 2012-05-24 | 2012-05-24 10:58 | 2012-05-24 11:27 | OTHER - H1DB030S06A | 67 | 2.8 | Yes | Yes | 20.3 | 20.1 | 0.2 | 50A614B0555C469A8E207D00EDF4C752 |  | R22 | Non-TXV |  | 4.179% | 0.95821 | 8.031% | [5 empty] | Non-TXV | 4.179%
Merced | CA | 95348-1656 |  | 2012-05-30 | 2012-05-30 14:06 | 2012-05-30 16:04 | GOODMAN - PGB024050-1 | 54 | 1.6 | Yes | Yes | 21.1 | 20.4 | 0.7 | 589EFAC5DF5B44BC8EF605FFB6067E18 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95207-5919 |  | 2012-05-30 | 2012-05-30 14:57 | 2012-05-30 15:14 | RHEEM - RRNA-B024JKO6X | 70 | 5.7 | Yes | Yes | 21.5 | 20.5 | 1 | F730E6A32D7E415EA7BA9FB4EB60D620 |  | R22 | TXV |  | 8.143% | 0.91857 | 15.65% | [5 empty] | TXV | 8.143%
Chowchilla | CA | 93610-1902 |  | 2012-07-11 | 2012-07-11 13:15 | 2012-07-11 13:33 | HEIL - CA3018VKA3 | 68 | 2.1 | Yes | Yes | 16 | 18.5 | -2.5 | 4A7780FB1D614A798692BBCA09649561 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Manteca | CA | 95337-5522 |  | 2012-05-30 | 2012-05-30 15:22 | 2012-05-30 15:39 | AMANA - APG13300701A | 77 | 4.4 | Yes | Yes | 17.9 | 20.1 | -2.2 | 161DA61852774B6B992B522D6D8928B0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Selma | CA | 93662-4239 |  | 2012-05-18 | 2012-05-18 14:31 | 2012-05-18 17:55 | RUDD - N/A | 120 | 3.7 | Yes | Yes | 19.2 | 20.4 | -1.2 | 402F67E7FEDC4F709537947512F40722 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Chowchilla | CA | 93610-1903 |  | 2012-07-11 | 2012-07-11 12:52 | 2012-07-11 13:12 | HEIL - CAB301BUKA3 | 60 | 3.2 | Yes | Yes | 16.3 | 18.7 | -2.4 | EF95B9225C2E479F9E334F2391F0E2F3 |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Chowchilla | CA | 93610-1903 |  | 2012-07-12 | 2012-07-12 11:11 | 2012-07-12 11:28 | HEIL - CA3018VKA3 | 68 | 5 | Yes | Yes | 15.6 | 17.5 | -1.9 | 4CF34BDB819E4524A83D93811330BF7B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.353% | 0.92647 | 14.13% | [5 empty] | Non-TXV | 7.353%
Selma | CA | 93662-3972 |  | 2012-06-07 | 2012-06-07 14:55 | 2012-06-07 15:02 | CARRIER - 48NL1030300 | 85 | 2.7 | Yes | Yes | 20.5 | 18.7 | 1.9 | D785FA54A9464930BFBB53A33A22EFB0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Chowchilla | CA | 93610-1903 |  | 2012-07-11 | 2012-07-11 11:28 | 2012-07-11 11:56 | HEIL - CA3018VKA3 | 68 | 2.9 | Yes | Yes | 22.1 | 18.5 | 3.6 | 750D15E10BD7405A97DF3F3DCCEF2350 |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Stockton | CA | 95207-6065 |  | 2012-06-15 | 2012-06-15 11:59 | 2012-06-15 12:19 | DAY & NIGHT - 585CJ02450 | 72 | 10.8 | Yes | Yes | 19.4 | 19.3 | 0.1 | 49BC1830819C4DAA84DDD251DF7E8209 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Oakdale | CA | 95361-3447 |  | 2012-06-07 | 2012-06-07 16:33 | 2012-06-07 16:54 | YORK - D1N2030N03606C | 76 | 2.5 | Yes | Yes | 18.7 | 20.4 | -1.7 | 83C3D9EC7B52423D941B9E2628FF30B8 |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Chowchilla | CA | 93610-1905 |  | 2012-07-12 | 2012-07-12 09:01 | 2012-07-12 09:27 | HEIL - CA3018VKA3 | 68 | 2.1 | Yes | Yes | 18.6 | 16.9 | 1.7 | 47E0F8DE31844BC7AEE94CA9AFDD1BDB |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Merced | CA | 95341-6731 |  | 2012-05-21 | 2012-05-21 11:32 | 2012-05-21 11:53 | RHEEM - UNK | 85 | 7.5 | Yes | Yes | 26.3 | 21 | 5.3 | F8E54765D01B48ED8709023F6A9128DF |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Stockton | CA | 95207-6053 |  | 2012-06-15 | 2012-06-15 12:22 | 2012-06-15 12:42 | PAYNE - PY3PNA024040NB--- | 89 | -4.3 | Yes | Yes | 22.9 | 19.8 | 3.2 | 5E1ED871F92943C1A9E5497277D95491 |  | R22 | Non-TXV |  | -4.831% | 1.0483 | 1.353% |  |  |  |  | Non-TXV |  |  | -4.831%
Le Grand | CA | 95333-9745 |  | 2012-06-14 | 2012-06-14 09:30 | 2012-06-14 09:59 | OTHER - CCU10A42A | 89 | 9.1 | Yes | Yes | 23.5 | 24.7 | -1.2 | B3CC00B54823410CBD05961EA9802EEF |  | R22 | Non-TXV |  | 10.22% | 0.89775 | 19.65% | [5 empty] | Non-TXV | 10.22%
Clovis | CA | 93612-4230 |  | 2012-06-06 | 2012-06-06 11:24 | 2012-06-06 11:24 | GOODMAN - APG12240451A | 65 | 0 | Yes | Yes | 17.7 | 19.9 | -2.2 | 6396EFFDA7D64AE199DF840404A44405 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-1907 |  | 2012-08-13 | 2012-08-13 14:56 | 2012-08-13 15:21 | OTHER - CA3018VKA3 | 68 | 6.7 | Yes | Yes | 25.1 | 19.5 | 5.6 | 7DDE983EF47B4BF6B21F28814B02FA31 |  | R22 | Non-TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | Non-TXV | 9.853%
Stockton | CA | 95207-6004 |  | 2012-06-14 | 2012-06-14 12:59 | 2012-06-14 13:23 | RHEEM - UNK | 64 | 16.6 | Yes | Yes | 15.4 | 17.2 | -1.8 | 7DEE0CEB1C89415693D8C7BC4343AC75 |  | R22 | Non-TXV |  | 25.94% | 0.74062 | 49.85% | [5 empty] | Non-TXV | 25.94%
Fresno | CA | 93725-1210 |  | 2012-08-10 | 2012-08-10 09:06 | 2012-08-10 09:24 | BDP - 585B048125YACR | 109 | 17.9 | Yes | Yes | 23 | 19.7 | 3.3 | C8D7A8A0C4F94C1FBB34B393EA3E2B9E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.42% | 0.83578 | 31.56% | [5 empty] | Non-TXV | 16.42%
Clovis | CA | 93612-4233 |  | 2012-06-07 | 2012-06-07 10:35 | 2012-06-07 10:53 | GOODMAN - GPG12240451A | 64 | 1.9 | Yes | Yes | 23.1 | 20.8 | 2.3 | 7F836AFE7B5F4B08832C061F707A22CD |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Oakdale | CA | 95361-3447 |  | 2012-05-29 | 2012-05-29 11:47 | 2012-05-29 12:09 | YORK - D1NA030N03606C | 76 | 2.4 | Yes | Yes | 22.7 | 20.1 | 2.6 | AD4FA5CEA9584CA2A37E74C1391CEEB2 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Merced | CA | 95340-5118 |  | 2012-06-06 | 2012-06-06 11:25 | 2012-06-06 11:56 | TRANE - YCP030F1M0AB | 106 | 3.2 | Yes | Yes | 22.9 | 22.5 | 0.4 | 5DED323B53F042D4B301F302D6CBBAE9 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Los Banos | CA | 93635-3770 |  | 2012-05-23 | 2012-05-23 13:16 | 2012-05-23 13:37 | TRANE - BTD724A100C0 | 68 | 3.6 | Yes | Yes | 23.5 | 23.1 | 0.4 | 2BEC2CADC5FB44F5BC7F9066288B7ACB | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Chowchilla | CA | 93610-1907 |  | 2012-07-11 | 2012-07-11 14:18 | 2012-07-11 14:34 | HEIL - CA3018VKA3 | 68 | 2.8 | Yes | Yes | 18.1 | 19.5 | -1.4 | AA98B2C937144F0FA511CEB58BDF8C8B |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Yuba City | CA | 95993-7134 |  | 2012-07-05 | 2012-07-05 13:28 | 2012-07-05 13:46 | OTHER - UNK | 90 | 4.3 | Yes | Yes | 17 | 19.9 | -2.9 | 64CDEFD0390F4701B5617E5CC2D83283 |  | R22 | Non-TXV |  | 4.778% | 0.95222 | 9.182% | [5 empty] | Non-TXV | 4.778%
Merced | CA | 95340-2361 |  | 2012-06-06 | 2012-06-06 13:26 | 2012-06-06 14:09 | TRANE - TTD742A100A0 | 106 | -7.5 | Yes | Yes | 21.2 | 20.8 | 0.4 | FD451F94C11E4F21BF633BA39A3FAA11 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.075% | 1.0708 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.075%
Chowchilla | CA | 93610-1904 |  | 2012-07-25 | 2012-07-25 15:47 | 2012-07-25 16:12 | YORK - CA3018UKA3 | 68 | 2.2 | Yes | Yes | 15.8 | 17.7 | -1.9 | A136FC74B305422A8013EA71D15A8E57 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Chowchilla | CA | 93610-1904 |  | 2012-07-11 | 2012-07-11 12:02 | 2012-07-11 12:20 | HEIL - CA3018VKA3 | 68 | -4 | Yes | Yes | 19 | 18.5 | 0.5 | 1CB7E61FAB974B9A85C5C2C6CC0DDA6E |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Chowchilla | CA | 93610-1903 |  | 2012-07-12 | 2012-07-12 08:09 | 2012-07-12 08:30 | HEIL - CA3014VKA3 | 68 | 2.5 | Yes | Yes | 22.2 | 19.3 | 2.9 | C019D95C8EB146B49B720EEA8F259BB5 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Chowchilla | CA | 93610-1905 |  | 2012-07-12 | 2012-07-12 10:35 | 2012-07-12 10:59 | HEIL - CA3018VKA3 | 68 | 2.6 | Yes | Yes | 22 | 19.5 | 2.5 | 1C041991CF28400098004E99ADC3927A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Chowchilla | CA | 93610-1902 |  | 2012-07-11 | 2012-07-11 15:45 | 2012-07-11 16:29 | YORK - H4BD018506A | 62 | 2.6 | Yes | Yes | 15.8 | 17.9 | -2.1 | 4A083290A1B54E53A4FB205C5FB23FA3 |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Clovis | CA | 93612-4231 |  | 2012-06-06 | 2012-06-06 10:34 | 2012-06-06 10:55 | AMERICAN STANDARD - YCC024F1LOBI | 65 | 2 | Yes | Yes | 17.7 | 20.1 | -2.4 | 23C123C4ECA0462AA670A5F7457263A6 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Los Banos | CA | 93635-3578 |  | 2012-07-09 | 2012-07-09 11:58 | 2012-07-09 12:21 | AIRE-FLO - 24ECW060GA | 84 | 14.1 | Yes | Yes | 22.7 | 21 | 1.7 | E6EF27D890BB4F56A8CBCCB9010B3FF4 |  | R22 | Non-TXV |  | 16.79% | 0.83214 | 32.26% | [5 empty] | Non-TXV | 16.79%
Clovis | CA | 93612-4232 |  | 2012-07-30 | 2012-07-30 10:05 | 2012-07-30 10:37 | BDP - UNK | 85 | 2.8 | Yes | Yes | 17.8 | 20.4 | -2.6 | 4CB6871364B34AB49FACA45AE26FA2FF |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Clovis | CA | 93612-4231 |  | 2012-06-06 | 2012-06-06 10:59 | 2012-06-06 11:21 | GOODMAN - GPG12240451A | 65 | 2.6 | Yes | Yes | 17.5 | 20.4 | -2.9 | 25CAEAC601CE48B993324B192D1B7C76 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Chowchilla | CA | 93610-1904 |  | 2012-07-12 | 2012-07-12 09:35 | 2012-07-12 09:56 | HEIL - CA3018VKA3 | 68 | 2.2 | Yes | Yes | 21.3 | 18.5 | 2.8 | 20D18E67B2FE4919928D21BFDF4155E2 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Fresno | CA | 93710-6519 |  | 2012-05-31 | 2012-05-31 11:01 | 2012-05-31 11:21 | CARRIER - 36GSG18310 | 85 | 4.8 | Yes | Yes | 17.4 | 20.4 | -3 | 9BF31317E9BC47C3A85DE0E1E9DC84AB |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Selma | CA | 93662-4805 |  | 2012-06-15 | 2012-06-15 13:00 | 2012-06-15 13:19 | ICP - PGAD24B1K3 | 65 | 10.4 | Yes | Yes | 17.8 | 20.4 | -2.6 | 0F0536BF997F4EB0A04E7D3855738F7C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Clovis | CA | 93612-4232 |  | 2012-06-11 | 2012-06-11 13:43 | 2012-06-11 13:59 | GOODMAN - GPG12240451A | 85 | 2.5 | Yes | Yes | 25.8 | 21.5 | 4.3 | C5E5E737970E4C9FAF2F8F84E5664688 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Oroville | CA | 95966-6937 |  | 2012-05-31 | 2012-05-31 14:47 | 2012-05-31 15:57 | TRANE - TTB024C100AO | 51 | 2 | Yes | Yes | 22.7 | 21.4 | 1.3 | F4AB6218455E4C868C6AEDEFC7758DF8 |  | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Los Banos | CA | 93635-5427 |  | 2012-05-22 | 2012-05-22 13:07 | 2012-05-22 13:29 | BDP - 561AJ024 | 55 | 13.5 | Yes | Yes | 22.7 | 23.1 | -0.4 | 608532E708344563A3F7003D4708D546 |  | R22 | Non-TXV |  | 24.55% | 0.75455 | 47.17% | [5 empty] | Non-TXV | 24.55%
Livingston | CA | 95334-1752 |  | 2012-06-07 | 2012-06-07 09:09 | 2012-06-07 09:26 | RHEEM - RRKA-A030JK06X | 85 | 2.5 | Yes | Yes | 23.3 | 20 | 3.3 | 397CF1F25FB24EEB9A9D14B6936D79D5 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95203-1318 |  | 2012-07-02 | 2012-07-02 10:08 | 2012-07-02 10:32 | BRYANT - 582ANW036090AAAF | 56 | 3.3 | Yes | Yes | 19.7 | 20.4 | -0.7 | 04069FDBC6AB4C6788A773B19F2E1330 |  | R22 | Non-TXV |  | 5.893% | 0.94107 | 11.32% | [5 empty] | Non-TXV | 5.893%
Merced | CA | 95340-2949 |  | 2012-06-11 | 2012-06-11 11:16 | 2012-06-11 11:35 | GOODMAN - PGB0240751 | 54 | 9.1 | Yes | Yes | 23.6 | 21 | 2.6 | B4896CA8A571477D9045D4D9FECBEFD7 |  | R22 | Non-TXV |  | 16.85% | 0.83148 | 32.39% | [5 empty] | Non-TXV | 16.85%
Stockton | CA | 95212-3540 |  | 2012-05-24 | 2012-05-24 11:14 | 2012-05-24 11:33 | GOODMAN - CLJ42-1A | 99 | 4.2 | Yes | Yes | 18.5 | 20.4 | -1.9 | 9F601946B3AB4351BD31E997BE68A77B |  | R22 | TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | TXV | 4.242%
Fresno | CA | 93725-1890 |  | 2012-08-10 | 2012-08-10 14:33 | 2012-08-10 14:52 | GOODMAN - GPG13360701AB | 113 | 3.4 | Yes | Yes | 16.8 | 18.8 | -2 | 286EB613EBFE4B94AA1C7B805CC9E0F5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.009% | 0.96991 | 5.782% | [5 empty] | Non-TXV | 3.009%
Fresno | CA | 93710-3912 |  | 2012-05-24 | 2012-05-24 11:57 | 2012-05-24 12:24 | GOODMAN - CK36-1B | 85 | 3.2 | Yes | Yes | 18.6 | 19.9 | -1.3 | 4CFBDB67CB0341E1B4300D100F9C22BB |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Livingston | CA | 95334-9671 |  | 2012-07-10 | 2012-07-10 08:45 | 2012-07-10 09:10 | BDP - 588ANW036060ADAF | 67 | 2 | Yes | Yes | 22.2 | 21 | 1.2 | 201003FCA6774FB1B23D66B98362B7AC |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Stockton | CA | 95204-1504 |  | 2012-07-06 | 2012-07-06 15:51 | 2012-07-06 16:17 | DAY & NIGHT - UNK | 71 | 5.1 | Yes | Yes | 19.4 | 19.3 | 0.1 | 85394664A4784F22B742C22F429354A0 |  | R22 | Non-TXV |  | 7.183% | 0.92817 | 13.8% | [5 empty] | Non-TXV | 7.183%
Clovis | CA | 93612-4239 |  | 2012-06-07 | 2012-06-07 14:54 | 2012-06-07 14:54 | TRANE - YCC024F1L0BJ | 65 | 0 | Yes | Yes | 22.9 | 21 | 1.9 | 1F9C5ED3502A4D99822A77527385F7F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-9694 |  | 2012-06-08 | 2012-06-08 14:08 | 2012-06-08 14:26 | ICP - PGC030K060D | 52 | 6.8 | Yes | Yes | 24.6 | 24.1 | 0.5 | 0F3AB4943F2D4B1C846A07F32EB84CDF |  | R22 | Non-TXV |  | 13.08% | 0.86923 | 25.13% | [5 empty] | Non-TXV | 13.08%
Stockton | CA | 95206-5131 |  | 2012-06-12 | 2012-06-12 10:03 | 2012-06-12 10:24 | CARRIER - 38CKC036350 | 70 | 4 | Yes | Yes | 19 | 20.4 | -1.4 | 0A2EB71151834C72BC8286271BBB372F |  | R22 | TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | TXV | 5.714%
Chico | CA | 95973-0888 |  | 2012-05-23 | 2012-05-23 15:03 | 2012-05-23 15:29 | GIBSON - GT3BA-024KA | 85 | 5.1 | Yes | Yes | 16.7 | 17 | -0.3 | 5CC7F39B9EDD4BDD87FFE61E083066CD |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Stockton | CA | 95205-5653 |  | 2012-05-21 | 2012-05-21 16:52 | 2012-05-21 17:23 | GOODMAN - CLJ18-1 | 85 | 2.8 | Yes | Yes | 20.3 | 19.8 | 0.5 | 0785A5F2489B42FB9F40B467297C94F9 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Huron | CA | 93234-0000 |  | 2012-07-13 | 2012-07-13 09:49 | 2012-07-13 10:58 | GOODMAN - GPG13300451AB | 69 | 5.9 | Yes | Yes | 19.2 | 20.2 | -0.9 | 5781A1F1C3594B23BA957D66008BFF00 |  | R22 | Non-TXV |  | 8.551% | 0.91449 | 16.43% | [5 empty] | Non-TXV | 8.551%
Stockton | CA | 95205-6565 |  | 2012-07-06 | 2012-07-06 11:23 | 2012-07-06 11:43 | GOODMAN - CLJ18-1 | 58 | 7.3 | Yes | Yes | 15.3 | 17.2 | -1.9 | 2FADBBA447694A9CADF06002AB07F756 |  | R22 | TXV |  | 12.59% | 0.87414 | 24.19% | [5 empty] | TXV | 12.59%
Parlier | CA | 93648-2490 |  | 2012-07-13 | 2012-07-13 11:52 | 2012-07-13 12:42 | LENNOX - GCS29-030-75-2PA | 51 | 3.4 | Yes | Yes | 19.5 | 20.5 | -1 | 15191ED06D554DB29C38C5774EEF709C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93722-4766 |  | 2012-06-01 | 2012-06-01 14:25 | 2012-06-01 14:51 | BDP - NRGF36DDB04 | 90 | 8.6 | Yes | Yes | 19.8 | 22.4 | -2.6 | DFED5C8A1DBA4DBDAFC3C02C5AA72B22 |  | R22 | Non-TXV |  | 9.556% | 0.90444 | 18.36% | [5 empty] | Non-TXV | 9.556%
Fresno | CA | 93722-9720 |  | 2012-08-14 | 2012-08-14 20:20 | 2012-08-14 20:20 | YORK - UNK | 111 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | 7AD51C36D8924EBE976A2EAC846F1FFE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3793 |  | 2012-07-03 | 2012-07-03 12:37 | 2012-07-03 13:07 | CARRIER - 38YCC018340 | 72 | 0 | Yes | Yes | 13.1 | 20.4 | -7.3 | E062DD02D0014B7F9AECA091D4E719F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2352 |  | 2012-06-12 | 2012-06-12 12:43 | 2012-06-12 13:02 | OTHER - 24ECW060GA | 84 | 1.5 | Yes | Yes | 17.7 | 19.6 | -1.9 | DB269560EAF143D0843C5C299B042837 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 1.786% | 0.98214 | 3.432% | [5 empty] | Non-TXV | 1.786%
Fresno | CA | 93710-5377 |  | 2012-05-30 | 2012-05-30 10:51 | 2012-05-30 11:08 | YORK - D1NA024N03606C | 54 | 1.6 | Yes | Yes | 22 | 20.4 | 1.6 | B0BB79C074424CC8AF11E02920FFE300 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Clovis | CA | 93612-4232 |  | 2012-06-06 | 2012-06-06 13:20 | 2012-06-06 13:40 | NORDYNE - GR4GA-024K045X | 71 | 2.8 | Yes | Yes | 17.5 | 20.4 | -2.9 | D589B68D58BA4EE88DFAA9008DD87838 |  | R22 | Non-TXV |  | 3.944% | 0.96056 | 7.579% | [5 empty] | Non-TXV | 3.944%
Clovis | CA | 93612-4232 |  | 2012-06-08 | 2012-06-08 12:03 | 2012-06-08 12:23 | - YCC024F1LOBF | 52 | -3.7 | Yes | Yes | 17.7 | 19.8 | -2.1 | B0904C2FE29649B2B5E7403769405B8F |  | R22 | Non-TXV |  | -7.115% | 1.0712 | 1.993% |  |  |  |  | Non-TXV |  |  | -7.115%
Riverbank | CA | 95367-2955 |  | 2012-06-08 | 2012-06-08 11:39 | 2012-06-08 12:04 | YORK - DAYP-F030N070A | 73 | 4.9 | Yes | Yes | 18.2 | 18.8 | -0.6 | 3966718668014336B8C25787336E946C |  | R22 | Non-TXV |  | 6.712% | 0.93288 | 12.9% | [5 empty] | Non-TXV | 6.712%
Clovis | CA | 93612-4235 |  | 2012-06-14 | 2012-06-14 10:25 | 2012-06-14 10:42 | TRANE - YCC030F1M0BH | 69 | 2 | Yes | Yes | 23.3 | 19.9 | 3.5 | 847C7D2D67254949A8CA6B610FEEFFB3 |  | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
Clovis | CA | 93612-4239 |  | 2012-06-14 | 2012-06-14 11:28 | 2012-06-14 11:46 | HEIL - NRGF24DDB03 | 53 | 1.6 | Yes | Yes | 19 | 19.7 | -0.7 | 7123A26D98034E0DA12A01B7AC1C1B32 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Fresno | CA | 93722-2231 |  | 2012-08-14 | 2012-08-14 13:54 | 2012-08-14 14:30 | CARRIER - UNK | 67 | 4 | Yes | Yes | 18 | 20.4 | -2.4 | 3D3DBB1CBA54445797E8C40C4A8DB83E |  | R22 | Non-TXV |  | 5.97% | 0.9403 | 11.47% | [5 empty] | Non-TXV | 5.97%
Selma | CA | 93662-2944 |  | 2012-06-15 | 2012-06-15 13:46 | 2012-06-15 14:05 | YORK - DBYP-F042N080A | 150 | 17.2 | Yes | Yes | 22.4 | 20.7 | 1.7 | FFF15FE4B47B418594E458838B4B7AE6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.47% | 0.88533 | 22.04% | [5 empty] | Non-TXV | 11.47%
Willows | CA | 95988-2221 |  | 2012-06-08 | 2012-06-08 12:08 | 2012-06-08 12:47 | YORK - D1NA036N05606C | 67 | 9.9 | Yes | Yes | 19.4 | 20.9 | -1.5 | A23AE2536A9F4996B455A34B801ADA7A |  | R22 | Non-TXV |  | 14.78% | 0.85224 | 28.4% | [5 empty] | Non-TXV | 14.78%
Rocklin | CA | 95677-3648 |  | 2012-07-06 | 2012-07-06 09:34 | 2012-07-06 09:58 | DAY & NIGHT - UNK | 83 | 6.3 | Yes | Yes | 18 | 17.4 | 0.6 | 0DAF4EAFF0374FDAB84C005520C5E513 |  | R22 | Non-TXV |  | 7.59% | 0.9241 | 14.59% | [5 empty] | Non-TXV | 7.59%
Stockton | CA | 95205-5650 |  | 2012-06-01 | 2012-06-01 14:09 | 2012-06-01 14:31 | GOODMAN - CLJ18-1 | 85 | 4.7 | Yes | Yes | 17.8 | 17.9 | -0.1 | F7FCFFAE1F5C4AC486ADEEFC69BC4434 |  | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Clovis | CA | 93612-4235 |  | 2012-06-13 | 2012-06-13 13:20 | 2012-06-13 13:44 | GOODMAN - GPG10240451A | 85 | 4.1 | Yes | Yes | 19.5 | 20.4 | -0.9 | 3E9A87D438FE4BD28B18667A083D2731 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Stockton | CA | 95210-2617 |  | 2012-06-07 | 2012-06-07 11:58 | 2012-06-07 12:16 | PAYNE - PY1PNB030060AAAA | 58 | 1.7 | Yes | Yes | 24.8 | 21 | 3.8 | E40D81E4034142779BA376555E09440E |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Clovis | CA | 93612-4239 |  | 2012-06-08 | 2012-06-08 13:39 | 2012-06-08 13:55 | OTHER - UNK | 85 | 2.6 | Yes | Yes | 18.5 | 21 | -2.5 | 00435A7C147B4E2A848E6AE9E0CFFB13 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Clovis | CA | 93612-4235 |  | 2012-06-14 | 2012-06-14 12:16 | 2012-06-14 12:48 | HEIL - N/A | 69 | 2.1 | Yes | Yes | 18 | 20.2 | -2.2 | C063BFF5718C4B20B58D17569E808006 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Los Banos | CA | 93635-3757 |  | 2012-06-15 | 2012-06-15 12:10 | 2012-06-15 12:39 | AMERICAN STANDARD - 2A6H1024A1000AB | 72 | 3.9 | Yes | Yes | 22.7 | 21.7 | 1 | 1BA9E2E8C57040D08A117AAC176DC676 |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Auburn | CA | 95602-2600 |  | 2012-07-30 | 2012-07-30 12:44 | 2012-07-30 13:04 | CARRIER - UNK CUT OFF ON DATA PLATE | 56 | 11 | Yes | Yes | 19.1 | 20.4 | -1.3 | 04C1D7E14349441E8B5B4A961F2BFD43 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 19.64% | 0.80357 | 37.75% | [5 empty] | Non-TXV | 19.64%
Clovis | CA | 93612-0411 |  | 2012-08-13 | 2012-08-13 18:07 | 2012-08-13 18:41 | BDP - 588ANW03606ADAF | 67 | 2.1 | Yes | Yes | 17.5 | 20.4 | -2.9 | 7D970723DB874B9A821615A47E96EAF1 |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Selma | CA | 93662-2518 |  | 2012-06-07 | 2012-06-07 12:20 | 2012-06-07 12:40 | ICP - PGAA42E1K6 | 70 | 5.9 | Yes | Yes | 23.3 | 21 | 2.3 | BA0575AE374C48B69112D9D580921ACB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.429% | 0.91571 | 16.2% | [5 empty] | Non-TXV | 8.429%
Stockton | CA | 95205-6150 |  | 2012-06-01 | 2012-06-01 14:32 | 2012-06-01 14:52 | PAYNE - 584BNW024040AABE | 76 | 4.2 | Yes | Yes | 20.2 | 22 | -1.8 | 4F8D20D27DC248089951D2B39E712925 |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Rocklin | CA | 95677-3647 |  | 2012-06-07 | 2012-06-07 12:38 | 2012-06-07 12:56 | CARRIER - 540JJ018 | 83 | 15.5 | Yes | Yes | 16.7 | 18.7 | -2 | 318E8D48634F404A9AD8429FF5E94520 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.67% | 0.81325 | 35.89% | [5 empty] | Non-TXV | 18.67%
Stockton | CA | 95210-2617 |  | 2012-06-07 | 2012-06-07 12:25 | 2012-06-07 12:43 | PAYNE - PY1PNB030060AAAA | 58 | -3.4 | Yes | Yes | 25.7 | 20 | 5.8 | 88F2F12C4E8E48EEB3D36415AB86794D |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Tracy | CA | 95376-1810 |  | 2012-06-14 | 2012-06-14 13:53 | 2012-06-14 14:13 | BRYANT - 561CJ036-E | 70 | 7.9 | Yes | Yes | 18.5 | 21 | -2.5 | 39BFB5A772D342D2A23B65E8FDA14AF2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.29% | 0.88714 | 21.69% | [5 empty] | Non-TXV | 11.29%
Auburn | CA | 95602-8237 |  | 2012-06-12 | 2012-06-12 09:42 | 2012-06-12 10:03 | OTHER - EADC-024JAS | 61 | 1.9 | Yes | Yes | 18 | 20.3 | -2.3 | 5E179DFC1FD24725B475450E4DF2E77A |  | R22 | Non-TXV |  | 3.115% | 0.96885 | 5.986% | [5 empty] | Non-TXV | 3.115%
Stockton | CA | 95210-2609 |  | 2012-06-19 | 2012-06-19 11:58 | 2012-06-19 12:16 | BDP - 561CJ060-A | 158 | 4.7 | Yes | Yes | 23.3 | 19.4 | 3.9 | F392A33C7A064FB2A6E89A341FBCBD4F |  | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.717% | [5 empty] | Non-TXV | 2.975%
Auburn | CA | 95602-2605 |  | 2012-07-10 | 2012-07-10 11:05 | 2012-07-10 11:28 | CARRIER - UNK | 80 | -5.6 | Yes | Yes | 19 | 18.8 | 0.2 | 9D0B84C9882B45CF951344F2F7728535 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Merced | CA | 95348-1656 |  | 2012-06-08 | 2012-06-08 11:03 | 2012-06-08 11:29 | GOODMAN - PGB024050-1 | 56 | 3.3 | Yes | Yes | 20.4 | 21 | -0.6 | 7E92D7268E4545668132CA50920FE6BB |  | R22 | Non-TXV |  | 5.893% | 0.94107 | 11.32% | [5 empty] | Non-TXV | 5.893%
Rocklin | CA | 95677-3648 |  | 2012-07-12 | 2012-07-12 11:06 | 2012-07-12 11:31 | OTHER - 540J018 | 83 | 3 | Yes | Yes | 17 | 19.9 | -2.9 | 4268B937610440BD9D08D656D1F5E420 |  | R22 | TXV |  | 3.614% | 0.96386 | 6.946% | [5 empty] | TXV | 3.614%
Selma | CA | 93662-3020 |  | 2012-06-07 | 2012-06-07 13:03 | 2012-06-07 13:26 | RHEEM - RRKA-A036JK06X | 62 | 2.3 | Yes | Yes | 18.5 | 18.1 | 0.4 | EB6D22A9A01741E0A4F2D61549D938BE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.71% | 0.9629 | 7.129% | [5 empty] | Non-TXV | 3.71%
Selma | CA | 93662-2449 |  | 2012-06-07 | 2012-06-07 10:53 | 2012-06-07 11:09 | YORK - D3NZ042N06506NZA | 78 | -3.1 | Yes | Yes | 21.7 | 19.3 | 2.4 | 5AF8D2EC18664FACB75D82F53C4A2C86 |  | R410A | TXV |  | -3.974% | 1.0397 | 1.113% |  |  |  |  | TXV |  |  | -3.974%
Fresno | CA | 93727-7507 |  | 2012-08-07 | 2012-08-07 12:57 | 2012-08-07 13:19 | NORDYNE - N/A | 120 | 5.4 | Yes | Yes | 19 | 20.1 | -1.1 | E73D0920261048FEAEDB5E8F9A5B7857 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Atwater | CA | 95301-2845 |  | 2012-06-15 | 2012-06-15 09:56 | 2012-06-15 10:18 | OTHER - PGC024K060A | 58 | 1.7 | Yes | Yes | 18.4 | 19.2 | -0.8 | 7F8CFEF3E67D49F7BD9898CDA9EA803F |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Fresno | CA | 93706-9283 |  | 2012-06-13 | 2012-06-13 10:28 | 2012-06-13 10:45 | OTHER - N/A | 105 | 20.8 | Yes | Yes | 22.5 | 19.9 | 2.6 | 4EF5C60F99794F4AB03BE26B7A963362 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.81% | 0.8019 | 38.07% | [5 empty] | Non-TXV | 19.81%
Auburn | CA | 95602-2217 |  | 2012-07-09 | 2012-07-09 16:00 | 2012-07-09 16:00 | OTHER - CM-18-41-T PAINTED | 51 | 0 | Yes | Yes | 22 | 21.7 | 0.3 | 1D20B3BC51E14DC1BE31E6CC389EF0E0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4326 |  | 2012-08-02 | 2012-08-02 11:59 | 2012-08-02 12:26 | PAYNE - UNK | 63 | 2.7 | Yes | Yes | 18.4 | 20.4 | -2 | D1037A56E79846DC8CE4C4D7A44BF166 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Selma | CA | 93662-2101 |  | 2012-06-07 | 2012-06-07 11:26 | 2012-06-07 11:43 | ICP - GPCM042K080I | 107 | 4.2 | Yes | Yes | 21.6 | 20.4 | 1.2 | A8A35DDB93C348169502D21EC390E674 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.925% | 0.96075 | 7.543% | [5 empty] | Non-TXV | 3.925%
Dinuba | CA | 93618-9791 |  | 2012-05-21 | 2012-05-21 12:16 | 2012-05-21 12:36 | UPG - HBBD-F024SC | 88 | 4.1 | Yes | Yes | 25.2 | 23.7 | 1.5 | E238B0256E2B472D8DB337CF6FE916E4 |  | R22 | Non-TXV |  | 4.659% | 0.95341 | 8.954% | [5 empty] | Non-TXV | 4.659%
Chico | CA | 95926-3818 |  | 2012-05-18 | 2012-05-18 14:56 | 2012-05-18 15:24 | YORK - D1NA030N05606B | 80 | 3.9 | Yes | Yes | 25.5 | 22.5 | 3 | D7B4629F11B04DF1807CFEA30326C88A |  | R22 | Non-TXV |  | 4.875% | 0.95125 | 9.369% | [5 empty] | Non-TXV | 4.875%
Stockton | CA | 95207-5271 |  | 2012-06-20 | 2012-06-20 14:21 | 2012-06-20 14:39 | DAY & NIGHT - 567024RCU | 60 | 11 | Yes | Yes | 22.5 | 22.4 | 0.1 | F634FDBC241F409E96AA1F9DB990EAF4 |  | R22 | Non-TXV |  | 18.33% | 0.81667 | 35.23% | [5 empty] | Non-TXV | 18.33%
Madera | CA | 93638-1784 |  | 2012-06-13 | 2012-06-13 11:07 | 2012-06-13 11:24 | BRYANT - 574BNW036060NB | 149 | -6.1 | Yes | Yes | 24.3 | 19.3 | 5 | A31BFE1B069C41C1A2C20E92603987A5 |  | R410A | TXV |  | -4.094% | 1.0409 | 1.147% |  |  |  |  | TXV |  |  | -4.094%
Dinuba | CA | 93618-2657 |  | 2012-05-23 | 2012-05-23 14:32 | 2012-05-23 14:52 | GOODMAN - GPG13360701AA | 112 | 3.6 | Yes | Yes | 26.5 | 20.8 | 5.7 | D22CBCB46DE64C3687E37CEFB6498413 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Dinuba | CA | 93618-9217 |  | 2012-05-21 | 2012-05-21 13:20 | 2012-05-21 13:39 | ICP - PGAD36D1K3 | 68 | 4.1 | Yes | Yes | 23.2 | 19.8 | 3.4 | 711B42F16EBE4E6DA89608E4F5BF0F04 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.029% | 0.93971 | 11.59% | [5 empty] | Non-TXV | 6.029%
Chowchilla | CA | 93610-3407 |  | 2012-05-24 | 2012-05-24 11:46 | 2012-05-24 12:08 | FRASER & JONHSTONE - 80WE30G1NA | 87 | -5.1 | Yes | Yes | 22.5 | 22.1 | 0.4 | FD7BFEB469894B459924AF92CD2D9F2D |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Madera | CA | 93638-3231 |  | 2012-07-02 | 2012-07-02 12:57 | 2012-07-02 13:18 | TRANE - 2TTZ9036A1000AA | 224 | 6.7 | Yes | Yes | 18.2 | 16.4 | 1.8 | B2DA25FE7B2E49098792A75BE5DE54D0 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.748% | [5 empty] | Non-TXV | 2.991%
Yuba City | CA | 95991-5004 |  | 2012-06-13 | 2012-06-13 14:54 | 2012-06-13 15:21 | OTHER - AC030A2A1 | 85 | 10.4 | Yes | Yes | 17 | 19.2 | -2.2 | ECDADD279747445D8FB449883FBA1A41 |  | R22 | Non-TXV |  | 12.24% | 0.87765 | 23.51% | [5 empty] | Non-TXV | 12.24%
Marysville | CA | 95901-4288 |  | 2012-05-21 | 2012-05-21 15:44 | 2012-05-21 16:01 | UNK - 540JJ018 | 83 | 2.5 | Yes | Yes | 22 | 22.1 | -0.1 | 0C620B42C1E547A29F0803A76593ACD9 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Chico | CA | 95926-1667 |  | 2012-05-18 | 2012-05-18 10:17 | 2012-05-18 10:45 | DAYNNIGHT - N2A324AKC200 | 57 | 1.8 | Yes | Yes | 21.5 | 21.8 | -0.3 | B7B80974FDA44880B98A879AD8DD444A |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Marysville | CA | 95901-6717 |  | 2012-06-08 | 2012-06-08 10:04 | 2012-06-08 10:32 | YORK - H4DH036S06A | 95 | 9.6 | Yes | Yes | 26.1 | 20.4 | 5.7 | E0410FA6FC8A43D09F089A86669BF219 |  | R22 | Non-TXV |  | 10.11% | 0.89895 | 19.42% | [5 empty] | Non-TXV | 10.11%
Marysville | CA | 95901-4275 |  | 2012-05-21 | 2012-05-21 14:59 | 2012-05-21 15:22 | UNK - 540JJ018 | 83 | -7.8 | Yes | Yes | 20 | 20.9 | -0.9 | 01E13EB77DD047C4AB1203CE7552B84A |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Dinuba | CA | 93618-2933 |  | 2012-05-29 | 2012-05-29 11:33 | 2012-05-29 11:37 | CARRIER - 48GS003090301 | 56 | 1.8 | Yes | Yes | 21.4 | 21.5 | -0.1 | 3B05FD1E25534E81AFF4A2D10F5536D3 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Dinuba | CA | 93618-1743 |  | 2012-06-06 | 2012-06-06 10:41 | 2012-06-06 11:08 | ARMSTRONG - PGE12B48D100A-3A | 167 | 5.1 | Yes | Yes | 22.6 | 20.6 | 2 | A6292BEC2C1749A6BCD50504C4B4C590 |  | R22 | Non-TXV |  | 3.054% | 0.96946 | 5.869% | [5 empty] | Non-TXV | 3.054%
Yuba City | CA | 95991-5818 |  | 2012-06-14 | 2012-06-14 11:01 | 2012-06-14 11:20 | OTHER - 24ACR330A300 | 95 | -7.8 | Yes | Yes | 19 | 19.2 | -0.2 | 27AEBEAB007F410B9B99753D4D1F2819 |  | R22 | Non-TXV |  | -8.211% | 1.0821 | 2.299% |  |  |  |  | Non-TXV |  |  | -8.211%
Yuba City | CA | 95993-8817 |  | 2012-05-21 | 2012-05-21 13:32 | 2012-05-21 13:32 | INTERNATIONAL COMFORT PRODUCTS - N2A360AKB200 | 147 | 0 | Yes | Yes | 18.6 | 21.4 | -2.8 | BF1252B85A814C6BB53DFE6477E5B56C |  | R22 | TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1773 |  | 2012-06-11 | 2012-06-11 11:31 | 2012-06-11 11:54 | BRYANT - 582ANW036060NBAF | 68 | 4.9 | Yes | Yes | 26.8 | 21.4 | 5.4 | A79C3CBF0E5845F789C00A628F7ECEFC |  | R22 | Non-TXV |  | 7.206% | 0.92794 | 13.85% | [5 empty] | Non-TXV | 7.206%
Diamond Springs | CA | 95619-9317 |  | 2012-07-05 | 2012-07-05 11:44 | 2012-07-05 12:05 | TRANE - 2TTR2036A1000AA | 96 | 14.9 | Yes | Yes | 24.1 | 19.1 | 5 | CC9284F77DB4471DA53B3DEC714067F3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.52% | 0.84479 | 29.83% | [5 empty] | Non-TXV | 15.52%
Madera | CA | 93638-1776 |  | 2012-07-03 | 2012-07-03 11:05 | 2012-07-03 11:22 | OTHER - 582ANW030040NAAD | 55 | 9 | Yes | Yes | 23.2 | 24.1 | -0.9 | AD79532521AF40518CEE693D8141A949 |  | R22 | Non-TXV |  | 16.36% | 0.83636 | 31.45% | [5 empty] | Non-TXV | 16.36%
Paso Robles | CA | 93446-4813 |  | 2012-07-09 | 2012-07-09 12:45 | 2012-07-09 13:01 | BDP - 567GJ036 | 93 | 6 | Yes | Yes | 22.3 | 20.2 | 2.2 | 2A1D75E6F2684CB7AA02EEF1BEA70A14 |  | R22 | Non-TXV |  | 6.452% | 0.93548 | 12.4% | [5 empty] | Non-TXV | 6.452%
Madera | CA | 93637-3061 |  | 2012-05-18 | 2012-05-18 10:20 | 2012-05-18 10:37 | PAYNE - N/A | 74 | 2.2 | Yes | Yes | 25.5 | 21.3 | 4.3 | 1CC0595488DC428DB4655CAA1CDB2B0C |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Chico | CA | 95928-4712 |  | 2012-07-03 | 2012-07-03 14:09 | 2012-07-03 14:25 | YORK - H1C8030S0GA | 71 | 8 | Yes | Yes | 23.5 | 22.1 | 1.4 | 09C915B019054B5F85B2EABA9954B541 |  | R22 | Non-TXV |  | 11.27% | 0.88732 | 21.65% | [5 empty] | Non-TXV | 11.27%
Chico | CA | 95928-4712 |  | 2012-07-26 | 2012-07-26 12:22 | 2012-07-26 12:59 | YORK - H1CB030SO6A | 79 | 7.9 | Yes | Yes | 24 | 22.3 | 1.8 | B6112AF3C8F94181AA31D2A143824A2E |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Madera | CA | 93638-1782 |  | 2012-06-11 | 2012-06-11 11:58 | 2012-06-11 12:23 | BRYANT - 574BNW030040NB | 128 | 4.1 | Yes | Yes | 22.3 | 20.4 | 1.9 | 43FF2D1662C94D22B1556D342158FB65 |  | R410A | Non-TXV |  | 3.203% | 0.96797 | 6.156% | [5 empty] | Non-TXV | 3.203%
Madera | CA | 93637-6214 |  | 2012-06-08 | 2012-06-08 11:41 | 2012-06-08 11:58 | LENNOX - 10GCS042-75-6PB | 73 | 2.2 | Yes | Yes | 23.1 | 20.4 | 2.7 | 4EF29C27C8CA4A5C9ADA3C6442CC4909 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Madera | CA | 93637-5515 |  | 2012-07-03 | 2012-07-03 09:29 | 2012-07-03 09:48 | OTHER - UNK | 69 | 9.6 | Yes | Yes | 21 | 19.3 | 1.7 | 3E70C05D63E2485E898C58C40C632F34 |  | R22 | Non-TXV |  | 13.91% | 0.86087 | 26.74% | [5 empty] | Non-TXV | 13.91%
Chico | CA | 95926-4330 |  | 2012-05-22 | 2012-05-22 12:20 | 2012-05-22 12:20 | RHEEM - RAKA-024JAZ | 50 | 0 | Yes | Yes | 25.3 | 19.7 | 5.6 | 448F4D8FB2D944A4B215E636B3E35F90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-2026 |  | 2012-05-21 | 2012-05-21 14:18 | 2012-05-21 14:18 | RHEEMRRNA-B036JK08X - | 83 | 0 | Yes | Yes | 21.4 | 23.1 | -1.7 | F089DEFD07A1425A9BB1D41798408873 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-6266 |  | 2012-05-22 | 2012-05-22 15:41 | 2012-05-22 16:05 | BDP - 585EJ030075 | 58 | 7.4 | Yes | Yes | 25.8 | 21.2 | 4.7 | E69DA6B71D89445898DB579B527AD6A0 |  | R22 | Non-TXV |  | 12.76% | 0.87241 | 24.52% | [5 empty] | Non-TXV | 12.76%
Paradise | CA | 95969-6155 |  | 2012-06-11 | 2012-06-11 14:56 | 2012-06-11 17:47 | GOODMAN - CKL24-1L | 76 | 12.8 | Yes | Yes | 19.2 | 21.9 | -2.7 | 9DC771FE392A45D6A1889F935CFA30FF |  | R22 | Non-TXV |  | 16.84% | 0.83158 | 32.37% | [5 empty] | Non-TXV | 16.84%
Madera | CA | 93638-2105 |  | 2012-06-12 | 2012-06-12 12:43 | 2012-06-12 13:12 | CARRIER - 480L029-BB | 48 | 1.4 | Yes | Yes | 24.2 | 20.9 | 3.3 | A76007A1F62940A3BD3EB59A17E646A4 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Merced | CA | 95340-3803 |  | 2012-05-30 | 2012-05-30 12:28 | 2012-05-30 12:47 | GOODMAN - GPG13300451AA | 77 | 2.3 | Yes | Yes | 17.9 | 20.2 | -2.3 | E84DE19DD63B4CAE8003781AD396A70B |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Marysville | CA | 95901-4286 |  | 2012-05-21 | 2012-05-21 14:24 | 2012-05-21 14:47 | UNK - 540JJ018 | 83 | -4.9 | Yes | Yes | 18 | 19.4 | -1.4 | 9230E395981C4A2ABCD8924F40E0624D |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Yuba City | CA | 95991-6224 |  | 2012-06-14 | 2012-06-14 12:18 | 2012-06-14 12:43 | OTHER - DRCS0361BE | 83 | 2.6 | Yes | Yes | 18 | 20.4 | -2.4 | CEF4DECC4E97428F9EA5832867D956D9 |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Chico | CA | 95928-5753 |  | 2012-05-21 | 2012-05-21 12:03 | 2012-05-21 12:37 | AMANDA - PGB24C0452D | 65 | 2.8 | Yes | Yes | 25.3 | 22.5 | 2.8 | 204EC0A78B87412FABBBE1EB46DCA579 |  | R22 | Non-TXV |  | 4.308% | 0.95692 | 8.278% | [5 empty] | Non-TXV | 4.308%
Placerville | CA | 95667-5836 |  | 2012-06-13 | 2012-06-13 09:49 | 2012-06-13 10:07 | GOODMAN - CKT40-1B | 147 | 13.1 | Yes | Yes | 25.5 | 19.5 | 6 | DAF73C4B40F74A0EA18200A13F26006B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.912% | 0.91088 | 17.13% | [5 empty] | Non-TXV | 8.912%
Madera | CA | 93637-6215 |  | 2012-06-12 | 2012-06-12 08:49 | 2012-06-12 08:49 | LENNOX - 10GCS036X-75-6PB | 58 | 0 | Yes | Yes | 19.1 | 19.7 | -0.6 | 684F9147774741F58DAB3F0A836F9126 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Granite Bay | CA | 95746-7333 |  | 2012-07-13 | 2012-07-13 15:24 | 2012-07-13 15:41 | LENNOX - GCS26X-048-125-2PA | 172 | 27.7 | Yes | Yes | 26.1 | 20.7 | 5.4 | E52B231A3CA144789FF0DA6FC1036901 |  | R22 | Non-TXV |  | 16.1% | 0.83895 | 30.95% | [5 empty] | Non-TXV | 16.1%
Chico | CA | 95926-3169 |  | 2012-05-18 | 2012-05-18 12:33 | 2012-05-18 12:54 | FRASHER-JOHNSON - UNK | 88 | 6.8 | Yes | Yes | 23 | 21.7 | 1.4 | 3ECD752FF8E147CEA3C9DD3B4BBA529E |  | R22 | Non-TXV |  | 7.727% | 0.92273 | 14.85% | [5 empty] | Non-TXV | 7.727%
Placerville | CA | 95667-3427 |  | 2012-06-13 | 2012-06-13 10:45 | 2012-06-13 11:09 | GOODMAN - CKJ42-1AB | 106 | 12.8 | Yes | Yes | 22.9 | 19.5 | 3.4 | 9E60173215EC443D99618A2C213EC917 |  | R22 | Non-TXV |  | 12.08% | 0.87925 | 23.21% | [5 empty] | Non-TXV | 12.08%
Marysville | CA | 95901-4287 |  | 2012-05-21 | 2012-05-21 12:41 | 2012-05-21 13:09 | UNK - 540JJ018 | 83 | 4.5 | Yes | Yes | 20 | 21 | -1 | 877EF99B48244182BF7EC6B2E22F40B0 |  | R22 | Non-TXV |  | 5.422% | 0.94578 | 10.42% | [5 empty] | Non-TXV | 5.422%
Yuba City | CA | 95991-7538 |  | 2012-07-10 | 2012-07-10 11:27 | 2012-07-10 11:27 | GOODMAN - CM036-1EB | 57 | 0 | Yes | Yes | 26.4 | 21.2 | 5.3 | 3D70420CAA9D407A97265C90DCD2C577 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-4195 |  | 2012-05-22 | 2012-05-22 11:22 | 2012-05-22 11:57 | TEMPSTAR - CA9624VKB2 | 102 | 3.2 | Yes | Yes | 19.7 | 21 | -1.3 | 381DC6F3D9584B0E9CF364FB36675123 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Madera | CA | 93638-1520 |  | 2012-07-12 | 2012-07-12 09:05 | 2012-07-12 09:27 | OTHER - 80WE30G1NA | 69 | 2.8 | Yes | Yes | 18.3 | 20.7 | -2.4 | 46D50DE1300049C09C9ABA7841E77456 |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Paradise | CA | 95969-5964 |  | 2012-06-12 | 2012-06-12 14:21 | 2012-06-12 16:46 | LENNOX - M/NH527-042-3P | 144 | 4.4 | Yes | Yes | 25.8 | 22.6 | 3.2 | C940D47B746B444196F1AD1045587F99 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Oroville | CA | 95965-3524 |  | 2012-05-29 | 2012-05-29 10:22 | 2012-05-29 10:22 | CARRIER - 585HJ024040 | 68 | 0 | Yes | Yes | 23.7 | 21 | 2.7 | DAE5AC771B4B4C6F92AC08E33DC3A5E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-2906 |  | 2012-06-12 | 2012-06-12 12:20 | 2012-06-12 12:46 | OTHER - UNK | 96 | 14.3 | Yes | Yes | 21.6 | 20.8 | 0.8 | 5C95D2F4FA2F4B33A5375D7C2DC72428 |  | R22 | Non-TXV |  | 14.9% | 0.85104 | 28.63% | [5 empty] | Non-TXV | 14.9%
Yuba City | CA | 95993-8006 |  | 2012-06-11 | 2012-06-11 12:32 | 2012-06-11 12:50 | DAY & NIGHT - 591ANX036000AAAA | 82 | 10 | Yes | Yes | 23.4 | 19.9 | 3.5 | 3330512F82E44AD7849B86D65087B01C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.2% | 0.87805 | 23.44% | [5 empty] | Non-TXV | 12.2%
Oroville | CA | 95966-8300 |  | 2012-06-07 | 2012-06-07 12:02 | 2012-06-07 13:26 | TRANE - 2YCX3048A1096AA | 144 | 8 | Yes | Yes | 25.4 | 22.5 | 2.9 | B92BEF2C056A40D48E2BB87538FD7D0C |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Manteca | CA | 95336-3524 |  | 2012-05-18 | 2012-05-18 14:29 | 2012-05-18 14:53 | GENERAL ELECTRIC - BGTA730B1B01 | 53 | 5.8 | Yes | Yes | 19.8 | 19.9 | -0.1 | 882DBF06C16A4F659523B067167D57BB |  | R22 | Non-TXV |  | 10.94% | 0.89057 | 21.03% | [5 empty] | Non-TXV | 10.94%
Merced | CA | 95341-7010 |  | 2012-05-30 | 2012-05-30 10:57 | 2012-05-30 11:24 | GOODMAN - GSC130301EA | 82 | 14.2 | Yes | Yes | 17.5 | 19.8 | -2.3 | BCAE466008E340ADA44CD56E90629E14 |  | R22 | Non-TXV |  | 17.32% | 0.82683 | 33.28% | [5 empty] | Non-TXV | 17.32%
Chico | CA | 95928-4196 |  | 2012-05-22 | 2012-05-22 14:12 | 2012-05-22 14:16 | TEMPSTAR - TCA024AKA5 | 70 | 2.2 | Yes | Yes | 24 | 22 | 2 | 446399D9BF17435D8B5FE206509E43AC |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Los Banos | CA | 93635-3296 |  | 2012-05-29 | 2012-05-29 13:01 | 2012-05-29 13:28 | DAY & NIGHT - 561AJ048-D | 112 | 20 | Yes | Yes | 19 | 21.3 | -2.3 | 687E3ED53DB54386834B3C1A352BC9E1 |  | R22 | TXV |  | 17.86% | 0.82143 | 34.32% | [5 empty] | TXV | 17.86%
Madera | CA | 93638-9765 |  | 2012-07-03 | 2012-07-03 11:32 | 2012-07-03 12:01 | OTHER - D1NP036N05606A | 108 | 12 | Yes | Yes | 31.8 | 27.3 | 4.5 | 81B515934A5849E08E617E1FD67FE736 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Magalia | CA | 95954-9105 |  | 2012-05-31 | 2012-05-31 10:58 | 2012-05-31 11:16 | DAY N NIGHT - 597CN0360-B | 92 | -5.2 | Yes | Yes | 20.2 | 22.5 | -2.3 | 815DC7CBDF6C4B3B9B02B16FF3952AEE |  | R22 | TXV |  | -5.652% | 1.0565 | 1.583% |  |  |  |  | TXV |  |  | -5.652%
Marysville | CA | 95901-7521 |  | 2012-05-23 | 2012-05-23 14:03 | 2012-05-23 14:03 | OTHER - UNK | 75 | 0 | Yes | Yes | 20 | 22.6 | -2.6 | 9ED3421FF97F4909ADD8DFB3CA7FA277 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-4411 |  | 2012-05-22 | 2012-05-22 14:55 | 2012-05-22 15:14 | GOODMAN - GPG1324041BB | 77 | 7.2 | Yes | Yes | 29 | 23.7 | 5.3 | 22293323965040249159FBA7DEFFE539 |  | R22 | Non-TXV |  | 9.351% | 0.90649 | 17.97% | [5 empty] | Non-TXV | 9.351%
Paradise | CA | 95969-5319 |  | 2012-06-11 | 2012-06-11 10:50 | 2012-06-11 11:21 | LENNOX - HS31-030-230-01 | 89 | 6.2 | Yes | Yes | 20.4 | 19.9 | 0.5 | BF663A2BD9B842DBBD5E1842FD28A4CC |  | R22 | Non-TXV |  | 6.966% | 0.93034 | 13.39% | [5 empty] | Non-TXV | 6.966%
Marysville | CA | 95901-4404 |  | 2012-05-22 | 2012-05-22 13:13 | 2012-05-22 13:33 | GOODMAN - GPG13240451BB | 77 | 11.1 | Yes | Yes | 18 | 20.9 | -2.9 | 460426ECCB644D448D2956B322E78962 |  | R22 | Non-TXV |  | 14.42% | 0.85584 | 27.7% | [5 empty] | Non-TXV | 14.42%
Dinuba | CA | 93618-2204 |  | 2012-05-21 | 2012-05-21 16:22 | 2012-05-21 16:40 | GOODMAN - CKL36-1D | 72 | 2.2 | Yes | Yes | 24.2 | 19.4 | 4.9 | 67C811F5010743C0BB9601FC24BC5557 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Marysville | CA | 95901-3522 |  | 2012-05-22 | 2012-05-22 14:10 | 2012-05-22 14:28 | CARRIER - 24ABB336A310 | 84 | 3.7 | Yes | Yes | 13 | 15 | -2 | C2C756F454164D20ABD621BBCC593CA6 |  | R410A | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Dobbins | CA | 95935-0000 |  | 2012-07-25 | 2012-07-25 10:51 | 2012-07-25 11:09 | GOODMAN - GSC130481AG | 147 | 8.2 | Yes | Yes | 26.2 | 21.8 | 4.4 | 06B073F06C9541CCA803E808334AD3B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.578% | 0.94422 | 10.72% | [5 empty] | Non-TXV | 5.578%
Oroville | CA | 95966-8200 |  | 2012-06-01 | 2012-06-01 16:10 | 2012-06-01 16:48 | YORK - H1RD042S06G | 152 | 4.6 | Yes | Yes | 21 | 20 | 1.1 | 7597D3D53A4847B3AAE9D57DA5B9084D |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Placerville | CA | 95667-8773 |  | 2012-07-05 | 2012-07-05 13:34 | 2012-07-05 13:54 | BDP - 541DJ018 | 83 | 30.5 | Yes | Yes | 21.7 | 19.7 | 2 | FD9996EE008A4CF48C1264BBB596D111 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 36.75% | 0.63253 | 70.62% | [5 empty] | Non-TXV | 36.75%
Oroville | CA | 95966-9453 |  | 2012-07-05 | 2012-07-05 13:55 | 2012-07-05 14:56 | YORK - B1HA060A06B | 161 | 6 | Yes | Yes | 20 | 21.5 | -1.5 | B7994A9DB9304D158ABD86267238AE01 |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.162% | [5 empty] | Non-TXV | 3.727%
Diamond Springs | CA | 95619-9316 |  | 2012-07-16 | 2012-07-16 15:24 | 2012-07-16 15:43 | GOODMAN - CK42-1C | 92 | 10.2 | Yes | Yes | 19.6 | 21.5 | -1.9 | 3A0565F9A5E340ADB99B1505ABA38868 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.09% | 0.88913 | 21.31% | [5 empty] | Non-TXV | 11.09%
Placerville | CA | 95667-8771 |  | 2012-07-16 | 2012-07-16 12:36 | 2012-07-16 13:02 | BDP - 541DJ018 | 85 | 16.6 | Yes | Yes | 22.8 | 19.1 | 3.8 | 8CA757487B174FA28C9AF19ABD3D1373 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 19.53% | 0.80471 | 37.53% | [5 empty] | Non-TXV | 19.53%
Placerville | CA | 95667-3315 |  | 2012-07-05 | 2012-07-05 14:55 | 2012-07-05 15:15 | TRANE - 2TTR4036A1000AA | 118 | 7.2 | Yes | Yes | 23.9 | 20.4 | 3.5 | 1AD1B656E4B646FCB28D2236655671B8 |  | R22 | TXV |  | 6.102% | 0.93898 | 11.73% | [5 empty] | TXV | 6.102%
Merced | CA | 95340-4507 |  | 2012-05-21 | 2012-05-21 15:04 | 2012-05-21 15:30 | RHEEM - RRNL-B042JK08X | 112 | -6.6 | Yes | Yes | 25 | 21.5 | 3.5 | 0E18EAFB19354B168707295F207067D0 |  | R410A | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Corning | CA | 96021-2729 |  | 2012-05-23 | 2012-05-23 11:47 | 2012-05-23 12:06 | CARRIER - 38CK018340 | 52 | 1.7 | Yes | Yes | 25.5 | 20.8 | 4.7 | CFE1E454D8DC4FCD8B821523F6932FF3 |  | R22 | Non-TXV |  | 3.269% | 0.96731 | 6.283% | [5 empty] | Non-TXV | 3.269%
Merced | CA | 95341-6985 |  | 2012-06-08 | 2012-06-08 13:26 | 2012-06-08 13:53 | PAYNE - PY1PNB036060AAAA | 56 | 5.2 | Yes | Yes | 26.4 | 21.8 | 4.6 | E2B427F16BE24C4C9A46B85EF0C64FD1 |  | R22 | Non-TXV |  | 9.286% | 0.90714 | 17.85% | [5 empty] | Non-TXV | 9.286%
Marysville | CA | 95901-4126 |  | 2012-05-22 | 2012-05-22 11:19 | 2012-05-22 11:19 | BRYANT - 574DNWA24040NA | 72 | 0 | Yes | Yes | 22 | 18.2 | 3.8 | 605F6D21739A4EE7A46E6CBFFE8D2DD2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Olivehurst | CA | 95961-4529 |  | 2012-07-03 | 2012-07-03 15:24 | 2012-07-03 15:24 | GOODMAN - GSC130361DF | 120 | 0 | Yes | Yes | 4.9 | 15.8 | -10.9 | 9B1DE7FC46584651902F1E224A02B6A9 | Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Liquid Temperature cannot be less than outdoor air temperature. Check entries and calibration. Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-9713 |  | 2012-06-15 | 2012-06-15 13:31 | 2012-06-15 13:54 | CARRIER - 38TXA036-331 | 110 | 5.7 | Yes | Yes | 24.1 | 21.4 | 2.7 | 460CE9E18E3749859B2BC551BCCB8EED |  | R410A | Non-TXV |  | 5.182% | 0.94818 | 9.958% | [5 empty] | Non-TXV | 5.182%
Merced | CA | 95341-9006 |  | 2012-05-29 | 2012-05-29 11:06 | 2012-05-29 11:26 | AIRE-FLO - TZAA3362A | 85 | 10.8 | Yes | Yes | 25.5 | 20.1 | 5.4 | CE6739E6352641E78F56A5D0EBB4AB07 |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
Stockton | CA | 95210-2617 |  | 2012-06-12 | 2012-06-12 11:14 | 2012-06-12 11:31 | TRANE - 2YCC3024A1040AB | 72 | 2.6 | Yes | Yes | 21.4 | 21 | 0.4 | CADB2F0734C548E99436833DCC16CFD8 |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Merced | CA | 95348-1570 |  | 2012-05-31 | 2012-05-31 09:44 | 2012-05-31 10:02 | OTHER - 80AW30-106 | 99 | 3 | Yes | Yes | 18.6 | 19.9 | -1.3 | 58BECC51398246469EFCB6A4F60CA6B5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Oroville | CA | 95965-4076 |  | 2012-06-13 | 2012-06-13 12:52 | 2012-06-13 13:22 | TRANE - 4TTB4030E1000AA | 112 | 9.1 | Yes | Yes | 19 | 21.7 | -2.7 | 39F2FD96ECA24C0EB19F475B88B9809A |  | R410A | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Orland | CA | 95963-9702 |  | 2012-05-21 | 2012-05-21 12:47 | 2012-05-21 13:46 | NA - BPHH0361BA | 96 | 3.8 | Yes | Yes | 18.9 | 20.8 | -1.9 | 22DF22CD1C774D57BAF8B385E723E891 |  | R22 | Non-TXV |  | 3.958% | 0.96042 | 7.607% | [5 empty] | Non-TXV | 3.958%
Oroville | CA | 95965-3336 |  | 2012-07-05 | 2012-07-05 09:02 | 2012-07-05 09:02 | AMERICAN STANDARD - 4A7B4030E1000AA | 115 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | 2B988EFA43914D39AA791B9509D708BB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2714 |  | 2012-06-01 | 2012-06-01 14:25 | 2012-06-01 14:42 | OTHER - TZAA-348-2A757 | 135 | 4 | Yes | Yes | 16.6 | 14.8 | 1.8 | 93D3DE53F30049EB8BDB8F18321EA0D0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Grass Valley | CA | 95945-5635 |  | 2012-05-30 | 2012-05-30 10:08 | 2012-05-30 10:27 | LENNOX - UNK | 60 | -5.6 | Yes | Yes | 18 | 20.1 | -2.1 | AEB44D6C2AF3474BBC5080BFAB313B5B |  | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Chico | CA | 95928-4713 |  | 2012-07-12 | 2012-07-12 13:27 | 2012-07-12 13:52 | YORK - H1CB030S06A | 79 | 3.7 | Yes | Yes | 25.9 | 20.7 | 5.3 | 2158357F53BB4A19A05E12882C174DA6 |  | R22 | Non-TXV |  | 4.684% | 0.95316 | 9.001% | [5 empty] | Non-TXV | 4.684%
Madera | CA | 93638-4795 |  | 2012-07-03 | 2012-07-03 12:18 | 2012-07-03 12:50 | OTHER - 12AJB42A01 | 115 | 13.5 | Yes | Yes | 24.8 | 26.3 | -1.5 | 67C0FC465AB8440E888F4D45CA9AF983 |  | R22 | Non-TXV |  | 11.74% | 0.88261 | 22.56% | [5 empty] | Non-TXV | 11.74%
Chico | CA | 95928-5751 |  | 2012-05-21 | 2012-05-21 11:17 | 2012-05-21 11:17 | AMERICAN STANDARD - 4YCC3030A1075AA | 85 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | B44E36FAB0C14BAC961A4C7C937C8A44 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-6242 |  | 2012-06-12 | 2012-06-12 14:25 | 2012-06-12 14:56 | AIRE-FLO - 38ETG030300 | 133 | 6.1 | Yes | Yes | 24.1 | 21 | 3.1 | FA0806CC1DC44CB5BEBBF5002FE41DA4 |  | R410A | Non-TXV |  | 4.586% | 0.95414 | 8.814% | [5 empty] | Non-TXV | 4.586%
Merced | CA | 95340-2417 |  | 2012-05-18 | 2012-05-18 13:28 | 2012-05-18 13:45 | RHEEM - UNK | 78 | 11.5 | Yes | Yes | 24.2 | 22 | 2.2 | F77AC93A6F2C4A3B894F27331AB13F01 |  | R22 | Non-TXV |  | 14.74% | 0.85256 | 28.33% | [5 empty] | Non-TXV | 14.74%
Merced | CA | 95340-0907 |  | 2012-05-18 | 2012-05-18 11:52 | 2012-05-18 12:16 | YORK - D1NH036N07206A | 104 | 11.3 | Yes | Yes | 25.6 | 20.1 | 5.5 | 3D914AE1F54F44A4B107C435BE1181C6 |  | R22 | Non-TXV |  | 10.87% | 0.89135 | 20.88% | [5 empty] | Non-TXV | 10.87%
Chico | CA | 95928-5751 |  | 2012-06-13 | 2012-06-13 13:27 | 2012-06-13 18:26 | TRANE - YCC018F1LOBH | 56 | 3.4 | Yes | Yes | 21.4 | 16.9 | 4.5 | B6486C8B269540CB9C066C9A1826D3ED |  | R22 | Non-TXV |  | 6.071% | 0.93929 | 11.67% | [5 empty] | Non-TXV | 6.071%
Oroville | CA | 95965-4581 |  | 2012-05-29 | 2012-05-29 13:58 | 2012-05-29 14:23 | AMERICAN STANDARD - 4A7B4030E1000AA | 112 | 3.9 | Yes | Yes | 27.9 | 22.4 | 5.5 | FEF0C7A4B1BF44EBB752FF00A7DD1CC8 |  | R410A | Non-TXV |  | 3.482% | 0.96518 | 6.692% | [5 empty] | Non-TXV | 3.482%
Chico | CA | 95928-6779 |  | 2012-05-30 | 2012-05-30 15:07 | 2012-05-30 15:07 | AMERICAN STANDARD - 4AB4030E1000AA | 85 | 0 | Yes | Yes | 25.4 | 22.3 | 3.2 | 613CC52D9C2646E28F4B6A57332AC6F6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7024 |  | 2012-05-30 | 2012-05-30 14:27 | 2012-05-30 14:52 | GOODMAN - CLJ421B | 84 | 13.6 | Yes | Yes | 22.9 | 21.3 | 1.6 | 40A87A5192FA4136AED3D043CBC271BC |  | R22 | Non-TXV |  | 16.19% | 0.8381 | 31.11% | [5 empty] | Non-TXV | 16.19%
Oroville | CA | 95965-4077 |  | 2012-06-13 | 2012-06-13 12:00 | 2012-06-13 12:16 | TRANE - 4TTB4030E1000AA | 112 | 6.7 | Yes | Yes | 25.7 | 21.9 | 3.8 | 124CB03DB6B44487AC5750D9141A6707 |  | R22 | Non-TXV |  | 5.982% | 0.94018 | 11.5% | [5 empty] | Non-TXV | 5.982%
Merced | CA | 95341-7023 |  | 2012-05-30 | 2012-05-30 13:45 | 2012-05-30 14:18 | GOODMAN - CLJ301A | 105 | 10.1 | Yes | Yes | 19.7 | 22.3 | -2.6 | 8BE65C868A4D4A02920F59E4B1C1DDA8 |  | R22 | Non-TXV |  | 9.619% | 0.90381 | 18.49% | [5 empty] | Non-TXV | 9.619%
Chico | CA | 95928-4322 |  | 2012-05-21 | 2012-05-21 13:36 | 2012-05-21 14:42 | TRANE XR 13 - 2TTR3042A10000AA | 108 | 13.2 | Yes | Yes | 24.5 | 22.1 | 2.4 | 831C2355A0974A169CDEB0459E2F0539 |  | R22 | Non-TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | Non-TXV | 12.22%
Oroville | CA | 95965-4540 |  | 2012-06-06 | 2012-06-06 15:18 | 2012-06-06 15:18 | TRANE - 4TTB4030E1000AA | 113 | 0 | Yes | Yes | 20.1 | 19.8 | 0.3 | 7C0DEFAAD2D14636A4982EC66454122F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6711 |  | 2012-05-24 | 2012-05-24 15:42 | 2012-05-24 16:02 | DAY & NIGHT - N/A | 50 | 1.6 | Yes | Yes | 21.2 | 23.8 | -2.6 | 008C7E36916844B49DC9BF02354418E4 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Atwater | CA | 95301-4874 |  | 2012-05-23 | 2012-05-23 13:35 | 2012-05-23 13:52 | LENNOX - HS9-811-5P | 47 | 1.4 | Yes | Yes | 17.8 | 20.2 | -2.4 | 4A51132DFD0B41F7B584F5317555E4B2 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.979% | 0.97021 | 5.724% | [5 empty] | Non-TXV | 2.979%
Atwater | CA | 95301-2737 |  | 2012-05-18 | 2012-05-18 12:27 | 2012-05-18 12:44 | AMERICAN STANDARD - YCP036F1M0AC | 109 | 3.3 | Yes | Yes | 23.7 | 20.3 | 3.4 | 66FAD38919304E5BA745170F35F44C01 |  | R22 | Non-TXV |  | 3.028% | 0.96972 | 5.818% | [5 empty] | Non-TXV | 3.028%
Merced | CA | 95341-6711 |  | 2012-06-07 | 2012-06-07 14:33 | 2012-06-07 15:03 | DAY & NIGHT - UNK | 80 | 15.8 | Yes | Yes | 23.2 | 23.5 | -0.3 | AF64B4D0D51D40A3B539B322B645D107 |  | R22 | Non-TXV |  | 19.75% | 0.8025 | 37.96% | [5 empty] | Non-TXV | 19.75%
Chico | CA | 95928-6043 |  | 2012-05-22 | 2012-05-22 12:57 | 2012-05-22 13:21 | AMERICAN STANDARD - 2YCX3030A1064AA | 115 | 4 | Yes | Yes | 19.1 | 19.8 | -0.7 | B927247A3E0046D885CBD0D4F97CBFEE |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Tracy | CA | 95376-2213 |  | 2012-06-15 | 2012-06-15 12:32 | 2012-06-15 12:57 | YORK - TCGD36S41S3HA | 73 | 9.1 | Yes | Yes | 19.3 | 19.6 | -0.3 | 94829D2E36F848A3B327780021AB1E7A |  | R410A | Non-TXV |  | 12.47% | 0.87534 | 23.96% | [5 empty] | Non-TXV | 12.47%
Dos Palos | CA | 93620-2203 |  | 2012-05-31 | 2012-05-31 13:05 | 2012-05-31 13:30 | DAY & NIGHT - 36DNR108T | 86 | 5.4 | Yes | Yes | 18.1 | 21 | -2.9 | 1DB9660E87E141388F8ACEB50888079C |  | R22 | Non-TXV |  | 6.279% | 0.93721 | 12.07% | [5 empty] | Non-TXV | 6.279%
Merced | CA | 95348-1570 |  | 2012-05-30 | 2012-05-30 12:23 | 2012-05-30 12:43 | YORK - D1NP030N05606A | 73 | 4.7 | Yes | Yes | 19.6 | 21 | -1.4 | C569A30C426E4017B2274AC95460B217 |  | R22 | Non-TXV |  | 6.438% | 0.93562 | 12.37% | [5 empty] | Non-TXV | 6.438%
Ripon | CA | 95366-2746 |  | 2012-05-21 | 2012-05-21 13:53 | 2012-05-21 14:21 | BRYANT - 588ANW024040ACAD | 38 | 3.1 | Yes | Yes | 20.7 | 22.6 | -1.9 | 4DE9F5CC2AFA4991871A81724D97E000 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.158% | 0.91842 | 15.68% | [5 empty] | Non-TXV | 8.158%
Rocklin | CA | 95765-4172 |  | 2012-05-22 | 2012-05-22 17:13 | 2012-05-22 17:37 | CARRIER - 38EH030340 | 126 | 8.8 | Yes | Yes | 18.4 | 21.3 | -2.9 | CE3BE8CC80DC4BB0A6F1A6D8D6EAB39D | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.984% | 0.93016 | 13.42% | [5 empty] | Non-TXV | 6.984%
Riverbank | CA | 95367-3831 |  | 2012-05-29 | 2012-05-29 15:54 | 2012-05-29 16:18 | RHEEM - RAHE-030JAS | 78 | 2.3 | Yes | Yes | 16.6 | 17.4 | -0.8 | 2040F4A6D08A47C59CCA4BE56EAECE7F |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Atwater | CA | 95301-9522 |  | 2012-05-22 | 2012-05-22 10:54 | 2012-05-22 11:12 | RHEEM - HC-80-30-21C | 48 | 1.4 | Yes | Yes | 24.4 | 19.9 | 4.5 | D54940CCDC5042669A27258DED8325E3 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Chico | CA | 95928-6044 |  | 2012-05-24 | 2012-05-24 11:43 | 2012-05-24 12:10 | PREMIER - ATV019C100CLT | 43 | 2.9 | Yes | Yes | 18.7 | 21.3 | -2.6 | 9DB4AE3496F14E55B39EAB5349F09DF4 |  | R22 | Non-TXV |  | 6.744% | 0.93256 | 12.96% | [5 empty] | Non-TXV | 6.744%
Clovis | CA | 93612-4915 |  | 2012-05-22 | 2012-05-22 16:02 | 2012-05-22 16:23 | YORK - D1NH036N05606C | 108 | 3.2 | Yes | Yes | 17.7 | 20.2 | -2.5 | A55D7E0369BC45838764ABC900915BCB |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93711-1357 |  | 2012-06-15 | 2012-06-15 11:39 | 2012-06-15 11:58 | SEARS - 8674811161 | 74 | 7.1 | Yes | Yes | 22.6 | 20.6 | 2 | E41C29B00C884A1080929A00466F05E8 |  | R22 | Non-TXV |  | 9.595% | 0.90405 | 18.44% | [5 empty] | Non-TXV | 9.595%
Rocklin | CA | 95765-4156 |  | 2012-07-12 | 2012-07-12 11:48 | 2012-07-12 12:13 | OTHER - UNK | 95 | -6.7 | Yes | Yes | 19 | 20.4 | -1.4 | 49AC418077FF4FF7836CF01341990A1D |  | R22 | Non-TXV |  | -7.053% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.053%
Stockton | CA | 95206-6384 |  | 2012-05-30 | 2012-05-30 16:53 | 2012-05-30 17:09 | GOODMAN - CLJ36-1A | 109 | 3.8 | Yes | Yes | 19.1 | 21 | -1.9 | 8E79A3C5E270461ABBB98CF9CDC2A6DB |  | R22 | Non-TXV |  | 3.486% | 0.96514 | 6.7% | [5 empty] | Non-TXV | 3.486%
Chico | CA | 95928-5751 |  | 2012-07-26 | 2012-07-26 12:58 | 2012-07-26 13:46 | WATERFURNACE - ATH019C100CRB | 47 | 6.3 | Yes | Yes | 18 | 20.9 | -2.9 | 080FFE45751B4EF781FC48830E555D4E |  | R22 | Non-TXV |  | 13.4% | 0.86596 | 25.76% | [5 empty] | Non-TXV | 13.4%
Magalia | CA | 95954-9548 |  | 2012-06-12 | 2012-06-12 11:39 | 2012-06-12 11:58 | WESTINGHOUSE - HR036SAWCF47824 | 67 | 11 | Yes | Yes | 21.5 | 21.1 | 0.4 | 0C002F91293547FFAF8A635BBB3A7E6B |  | R22 | Non-TXV |  | 16.42% | 0.83582 | 31.55% | [5 empty] | Non-TXV | 16.42%
Clovis | CA | 93611-4550 |  | 2012-05-22 | 2012-05-22 15:19 | 2012-05-22 15:39 | PAYNE - 585J03075YACR | 65 | 2.9 | Yes | Yes | 17.2 | 20.2 | -3 | 8FEF215053A74A6C968F9E1BE9758E45 |  | R22 | Non-TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | Non-TXV | 4.462%
Oroville | CA | 95965-3336 |  | 2012-07-05 | 2012-07-05 09:17 | 2012-07-05 09:17 | AMERICAN STANDARD - 4A7B4030E1000AA | 112 | 0 | Yes | Yes | 19.4 | 20.7 | -1.3 | AFB52E2477754519B4B6672152A3B636 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2534 |  | 2012-05-22 | 2012-05-22 16:57 | 2012-05-22 17:15 | YORK - D1NP030N05606A | 73 | 6.3 | Yes | Yes | 18.3 | 20 | -1.7 | 03C139BB2B974DEDAB9583A268590972 |  | R22 | Non-TXV |  | 8.63% | 0.9137 | 16.59% | [5 empty] | Non-TXV | 8.63%
Marysville | CA | 95901-4619 |  | 2012-06-15 | 2012-06-15 08:26 | 2012-06-15 08:49 | GOODMAN - GPG13240451BB | 77 | 15.8 | Yes | Yes | 23 | 21.3 | 1.8 | 1795B2D2DDD7413593DAC6150EFD33CC |  | R22 | Non-TXV |  | 20.52% | 0.79481 | 39.43% | [5 empty] | Non-TXV | 20.52%
Merced | CA | 95340-5007 |  | 2012-05-21 | 2012-05-21 10:12 | 2012-05-21 10:40 | RHEEM - RAMC030JAZ | 85 | 8.2 | Yes | Yes | 23.4 | 21.2 | 2.2 | A2E33725CF4F42DBA9097E3A943953A6 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Chico | CA | 95928-6082 |  | 2012-05-24 | 2012-05-24 14:24 | 2012-05-24 14:24 | TRANE - YCP030F1LOAA | 103 | 0 | Yes | Yes | 22.2 | 21 | 1.2 | 930BF87763F2463B97AC853A3B5234B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3415 |  | 2012-05-18 | 2012-05-18 13:29 | 2012-05-18 13:51 | TEMPSTAR - TCA430AKA5 | 190 | 5.6 | Yes | Yes | 20.3 | 22.3 | -2 | B4C33FD4FC0A46CCB80F14F1BA6A639F |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Magalia | CA | 95954-9643 |  | 2012-05-31 | 2012-05-31 12:39 | 2012-05-31 13:12 | AMERICAN STANDARD - 2WCX3030A1000AA | 99 | 2.9 | Yes | Yes | 20.8 | 21.9 | -1.1 | 335297A48BEC49BE868A977853AF4109 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Fowler | CA | 93625-2339 |  | 2012-05-24 | 2012-05-24 17:58 | 2012-05-24 22:29 | CARRIER - 48SS-036060331 | 67 | 2.2 | Yes | Yes | 15 | 18 | -3 | 97FD4137305A4FC09B1A056714D756CD |  | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Yuba City | CA | 95993-8006 |  | 2012-06-08 | 2012-06-08 09:48 | 2012-06-08 10:12 | DAY & NIGHT - 591ANX036000AAAA | 90 | 8.2 | Yes | Yes | 18 | 20.4 | -2.4 | A40C6CF0D4D94BBCA317F46163F97019 |  | R22 | Non-TXV |  | 9.111% | 0.90889 | 17.51% | [5 empty] | Non-TXV | 9.111%
Stockton | CA | 95206-6046 |  | 2012-06-12 | 2012-06-12 15:48 | 2012-06-12 16:07 | YORK - AC030X1221A | 76 | 6.9 | Yes | Yes | 17.2 | 19 | -1.8 | 2987841289E94484B7F41DF8DA2175E1 |  | R22 | Non-TXV |  | 9.079% | 0.90921 | 17.45% | [5 empty] | Non-TXV | 9.079%
Reedley | CA | 93654-5308 |  | 2012-07-13 | 2012-07-13 11:12 | 2012-07-13 11:29 | CARRIER - 38CKB024320 | 69 | 2.1 | Yes | Yes | 18.6 | 21 | -2.4 | A8086D6F193E4A848B813B2AB24CF29D |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Madera | CA | 93637-5307 |  | 2012-05-18 | 2012-05-18 16:17 | 2012-05-18 16:35 | YORK - DCYZ-F030N070A | 64 | 1.9 | Yes | Yes | 25.9 | 20.4 | 5.5 | EFA4216FEC674644BAFE20E81A2AF689 |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Reedley | CA | 93654-2048 |  | 2012-07-13 | 2012-07-13 10:50 | 2012-07-13 11:10 | CARRIER - 48GS-024060901 | 53 | 1.8 | Yes | Yes | 18.5 | 21.2 | -2.7 | 472693B7C17D40DCA30F68642316DABC |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Stockton | CA | 95210-3531 |  | 2012-05-24 | 2012-05-24 14:04 | 2012-05-24 14:22 | FRESCHI - UNK | 100 | 14.6 | Yes | Yes | 22.9 | 18.5 | 4.4 | 6896CEAD28A141F48370B537D3AC2AF2 |  | R22 | Non-TXV |  | 14.6% | 0.854 | 28.06% | [5 empty] | Non-TXV | 14.6%
Chico | CA | 95928-5751 |  | 2012-05-21 | 2012-05-21 12:53 | 2012-05-21 12:53 | TRANE XE 1200 - YCP030F1L0AA | 105 | 0 | Yes | Yes | 23.5 | 21.4 | 2.1 | 45EBB9A9E5A24B498C90E88F90366DA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-1910 |  | 2012-05-29 | 2012-05-29 14:43 | 2012-05-29 15:02 | YORK - D1NQ024N03606NXA | 56 | 1.6 | Yes | Yes | 22.9 | 20.2 | 2.7 | 53C4C0F492AB4EE49F2033D8553854C1 |  | R410A | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Fresno | CA | 93727-3979 |  | 2012-05-21 | 2012-05-21 12:26 | 2012-05-21 12:44 | AMERICAN STANDARD - YCC024F1L0BJ | 66 | 2 | Yes | Yes | 23.6 | 19.8 | 3.8 | 56E7153616744C458C9383984E97CA08 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Chico | CA | 95928-7520 |  | 2012-05-23 | 2012-05-23 11:55 | 2012-05-23 11:55 | PREMIER 2 - ATV019C100RT | 43 | 0 | Yes | Yes | 20.7 | 23.1 | -2.4 | 17D3F83846BD47F0A939E3F75225A76F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-5780 |  | 2012-07-03 | 2012-07-03 10:26 | 2012-07-03 11:08 | TRANE - YCCO18F1LOBH | 71 | 4.4 | Yes | Yes | 22.5 | 21 | 1.5 | C32BE07755284BF4923B6FF563C35C20 |  | R22 | Non-TXV |  | 6.197% | 0.93803 | 11.91% | [5 empty] | Non-TXV | 6.197%
Manteca | CA | 95336-2727 |  | 2012-05-18 | 2012-05-18 10:39 | 2012-05-18 11:10 | BDP COMPANY - 567CJ024 | 60 | 3.1 | Yes | Yes | 19.7 | 19.5 | 0.2 | 35FB76557EA1426AB632EA56FB9239F7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Stockton | CA | 95205-3141 |  | 2012-05-29 | 2012-05-29 13:41 | 2012-05-29 13:58 | GOODMAN - CKL36-1H | 71 | 2.3 | Yes | Yes | 18.2 | 18.8 | -0.6 | EE5EB4779FDF456A9C8D457C86B7EC10 |  | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.225% | [5 empty] | Non-TXV | 3.239%
Chico | CA | 95928-7521 |  | 2012-07-30 | 2012-07-30 16:34 | 2012-07-30 16:56 | AMERICAN STANDARD - YC024F1L0BJ | 47 | 4.1 | Yes | Yes | 18.9 | 21 | -2.1 | 8E36279C12E64906A39F64DBB565185A |  | R22 | Non-TXV |  | 8.723% | 0.91277 | 16.76% | [5 empty] | Non-TXV | 8.723%
Fresno | CA | 93727-7374 |  | 2012-06-13 | 2012-06-13 10:20 | 2012-06-13 10:20 | HEIL - PGAA36C1K4 | 69 | 0 | Yes | Yes | 19.4 | 19.7 | -0.3 | 0072ACDCA0764C90942561F9466C52FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-6028 |  | 2012-06-06 | 2012-06-06 14:49 | 2012-06-06 15:09 | GOODMAN - PGB024050-1 | 54 | -3.2 | Yes | Yes | 19.2 | 19.1 | 0.2 | B08B6CAAD0F84865AE90ACD2DDBD33CF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Fresno | CA | 93710-6437 |  | 2012-07-09 | 2012-07-09 12:06 | 2012-07-09 12:35 | GOODMAN - CK42-1C | 86 | 2.6 | Yes | Yes | 20 | 20.4 | -0.4 | C5DB0AFCDD1A4C0CA2A199832CE4049A |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Stockton | CA | 95210-3268 |  | 2012-06-13 | 2012-06-13 10:11 | 2012-06-13 10:28 | GE - BTB936A100C2 | 83 | -4.9 | Yes | Yes | 24.7 | 20.1 | 4.7 | F6CD9353C682420CA2EBFDE79FDC4B29 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Chico | CA | 95928-6097 |  | 2012-05-22 | 2012-05-22 13:36 | 2012-05-22 14:04 | AMERICAN STANDARD - 2YCX3030A1064AA | 88 | 4.9 | Yes | Yes | 20.6 | 23.3 | -2.7 | 7242C55444044CD9AECA215B8B128679 |  | R22 | Non-TXV |  | 5.568% | 0.94432 | 10.7% | [5 empty] | Non-TXV | 5.568%
Marysville | CA | 95901-7703 |  | 2012-05-31 | 2012-05-31 11:54 | 2012-05-31 12:10 | TRANE - TTB030C100A2 | 66 | 5.8 | Yes | Yes | 17 | 19.4 | -2.4 | 0BC9F756C1F84C7397819F95F2C5BA61 |  | R22 | Non-TXV |  | 8.788% | 0.91212 | 16.89% | [5 empty] | Non-TXV | 8.788%
Stockton | CA | 95215-7449 |  | 2012-05-31 | 2012-05-31 12:42 | 2012-05-31 12:42 | TRANE - SFHA-301-LE | 65 | 0 | Yes | Yes | 23.1 | 19.3 | 3.8 | 31E0DB574E534700919DA132B6CBD0A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4359 |  | 2012-06-15 | 2012-06-15 10:10 | 2012-06-15 10:46 | BRYANT - 582ANW03606NBAF | 69 | 2.1 | Yes | Yes | 17 | 19.9 | -2.9 | 9CF4A0AA288B4646B10A483858092680 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Stockton | CA | 95205-4338 |  | 2012-05-21 | 2012-05-21 15:20 | 2012-05-21 15:41 | DAY & NIGHT - 567C036RCU | 67 | 6.4 | Yes | Yes | 19.9 | 21.3 | -1.3 | 827A4D5E3766408D8AC63CFC0B0C7808 |  | R22 | Non-TXV |  | 9.552% | 0.90448 | 18.36% | [5 empty] | Non-TXV | 9.552%
Live Oak | CA | 95953-2279 |  | 2012-08-13 | 2012-08-13 11:47 | 2012-08-13 11:47 | PAYNE - PA13NR024-H | 65 | 0 | Yes | Yes | 14.6 | 17.5 | -2.9 | 9DD8C0370A7249FEB7820FF64483247D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-7205 |  | 2012-05-31 | 2012-05-31 09:25 | 2012-05-31 09:40 | RHEEM - RRKA-A030JK06X | 54 | 1.8 | Yes | Yes | 17.6 | 19.5 | -1.9 | 83CFECA5D13644EB85A8D516BFDD6A12 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Chico | CA | 95928-7521 |  | 2012-07-03 | 2012-07-03 09:57 | 2012-07-03 10:13 | TRANE - YCC024F1LOBJ | 65 | 5.8 | Yes | Yes | 21.7 | 21.3 | 0.4 | F34B72BDF0BD4540AE4E899EC71E3127 |  | R22 | Non-TXV |  | 8.923% | 0.91077 | 17.15% | [5 empty] | Non-TXV | 8.923%
Chico | CA | 95928-4351 |  | 2012-06-01 | 2012-06-01 12:30 | 2012-06-01 12:30 | PAYNE - 597AN030-A | 88 | 0 | Yes | Yes | 20.1 | 19.7 | 0.4 | EA2A1927A2CE45D5BA249D7B4AC994C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-1114 |  | 2012-05-24 | 2012-05-24 14:43 | 2012-05-24 15:00 | HEIL - UNK | 108 | 6.9 | Yes | Yes | 20.9 | 20.9 | 0 | AE6562D245D04C9D8D68A2B3F0745519 |  | R22 | Non-TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | Non-TXV | 6.389%
Stockton | CA | 95206-3036 |  | 2012-07-24 | 2012-07-24 10:50 | 2012-07-24 11:11 | RUUD - UNK | 96 | 22.5 | Yes | Yes | 20.7 | 20.6 | 0.1 | 1FC4B86F39E549E29783159DCA9D734A |  | R22 | Non-TXV |  | 23.44% | 0.76562 | 45.04% | [5 empty] | Non-TXV | 23.44%
Marysville | CA | 95901-4423 |  | 2012-05-22 | 2012-05-22 15:44 | 2012-05-22 16:05 | HEIL - CA5030UKB1 | 79 | 7.8 | Yes | Yes | 25 | 20.4 | 4.6 | D9BB2764BB574438B945F5AA97C20DA4 |  | R22 | Non-TXV |  | 9.873% | 0.90127 | 18.97% | [5 empty] | Non-TXV | 9.873%
Merced | CA | 95348-1627 |  | 2012-05-30 | 2012-05-30 10:33 | 2012-05-30 10:52 | GOODMAN - GPG1336070M41AC | 85 | 2.6 | Yes | Yes | 25.7 | 19.7 | 6 | B3A76FF942074DF4B7FE71385D0D32BC |  | R410A | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Madera | CA | 93637-6252 |  | 2012-05-21 | 2012-05-21 11:00 | 2012-05-21 11:22 | CARRIER - 24ABA342A300 | 105 | 3.3 | Yes | Yes | 16.8 | 19.3 | -2.5 | 4A64675F88D54B569204A38DBD93075F |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Merced | CA | 95340-4030 |  | 2012-05-21 | 2012-05-21 16:15 | 2012-05-21 16:15 | TRANE - YCC030F1M0BC | 76 | 0 | Yes | Yes | 25.9 | 23.5 | 2.4 | C0790936C6974C5684A2C349C8C4E3D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-3129 |  | 2012-05-29 | 2012-05-29 15:28 | 2012-05-29 16:03 | GOODMAN - GS130241AE | 91 | 2.9 | Yes | Yes | 23.5 | 21 | 2.5 | 6093ED4DDA664AE3920C896378336A91 |  | R22 | Non-TXV |  | 3.187% | 0.96813 | 6.124% | [5 empty] | Non-TXV | 3.187%
Merced | CA | 95340-2417 |  | 2012-06-11 | 2012-06-11 09:43 | 2012-06-11 10:03 | GE - BTD730A100A0 | 74 | 11.2 | Yes | Yes | 22.3 | 23.6 | -1.3 | 0AE6057845EB4EF5AC8E0EE1DF625335 |  | R22 | Non-TXV |  | 15.14% | 0.84865 | 29.09% | [5 empty] | Non-TXV | 15.14%
Oroville | CA | 95965-3407 |  | 2012-06-06 | 2012-06-06 09:39 | 2012-06-06 09:39 | YORK - BRCS042113DG | 70 | 0 | Yes | Yes | 22.8 | 20.7 | 2.1 | CC187479B5F0454C81713861ADA7FC89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7016 |  | 2012-06-13 | 2012-06-13 13:17 | 2012-06-13 13:35 | AIRE-FLO - 582ANW036060NBAF | 68 | 7 | Yes | Yes | 27.5 | 21.5 | 6 | F53CE346994D462BB88F66CF4A2F35EE |  | R22 | Non-TXV |  | 10.29% | 0.89706 | 19.78% | [5 empty] | Non-TXV | 10.29%
Merced | CA | 95340-5052 |  | 2012-05-31 | 2012-05-31 14:21 | 2012-05-31 14:39 | AIRE-FLO - PG0030K060A | 52 | 8.8 | Yes | Yes | 16.9 | 19.1 | -2.2 | CF953A187C234ED4B5123393CD704B23 |  | R22 | Non-TXV |  | 16.92% | 0.83077 | 32.52% | [5 empty] | Non-TXV | 16.92%
Merced | CA | 95341-5315 |  | 2012-06-14 | 2012-06-14 13:52 | 2012-06-14 14:19 | YORK - 12DB048S06A | 111 | 3.7 | Yes | Yes | 25.2 | 20.6 | 4.6 | 85390CDFB80F422A9C472A5A1262A7D2 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Madera | CA | 93637-2935 |  | 2012-05-18 | 2012-05-18 15:42 | 2012-05-18 15:42 | FRASER JOHNSTON - 80AW36-106 | 80 | 0 | Yes | Yes | 23.1 | 21.9 | 1.2 | 2FD42A38DED24B2D8F87A5BB29CEEE3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-8714 |  | 2012-05-29 | 2012-05-29 12:44 | 2012-05-29 13:11 | GOODMAN - CKL30-10 | 69 | 10.6 | Yes | Yes | 20.4 | 20.7 | -0.3 | 8D16657B585B434CAA90152A2C191BBD |  | R22 | Non-TXV |  | 15.36% | 0.84638 | 29.52% | [5 empty] | Non-TXV | 15.36%
Winton | CA | 95388-9246 |  | 2012-05-18 | 2012-05-18 12:39 | 2012-05-18 12:56 | GOODMAN - UNK | 85 | 8.3 | Yes | Yes | 20.5 | 22 | -1.5 | EAD2B1C19CED4061A523DCA1D304B3BD |  | R22 | Non-TXV |  | 9.765% | 0.90235 | 18.77% | [5 empty] | Non-TXV | 9.765%
Merced | CA | 95341-7016 |  | 2012-05-30 | 2012-05-30 12:03 | 2012-05-30 12:21 | BRYANT - 582ANW036060NBAF | 68 | 7.9 | Yes | Yes | 23.9 | 19.9 | 4 | 9CA9FDBE57CF4B09B659E1EF7141B626 |  | R22 | Non-TXV |  | 11.62% | 0.88382 | 22.33% | [5 empty] | Non-TXV | 11.62%
Merced | CA | 95340-4959 |  | 2012-05-30 | 2012-05-30 15:02 | 2012-05-30 15:02 | GOODMAN - CK24-B1 | 71 | 0 | Yes | Yes | 18.7 | 20.9 | -2.2 | 4D355F6EAD8D4597A3B2B05C6FE9B4F0 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-9644 |  | 2012-07-31 | 2012-07-31 10:08 | 2012-07-31 10:27 | BARD - PH36-1 | 85 | 25.6 | Yes | Yes | 20.1 | 20.1 | 0 | 959B7768749F447BA43ADE59BCC14525 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 30.12% | 0.69882 | 57.88% | [5 empty] | Non-TXV | 30.12%
Stockton | CA | 95219-4909 |  | 2012-06-21 | 2012-06-21 15:51 | 2012-06-21 16:15 | DAY & NIGHT - 591ANX042000ABAA | 112 | 3.8 | Yes | Yes | 21.7 | 19.9 | 1.8 | CB47505499324E6F9508204F61BC1539 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Stockton | CA | 95206-5813 |  | 2012-05-30 | 2012-05-30 12:08 | 2012-05-30 12:25 | RHEEM - RRNL-B030JK06X | 77 | 5.8 | Yes | Yes | 21.8 | 21 | 0.8 | 71FF203B3E884BCC89FC8F07402FA6AF |  | R410A | Non-TXV |  | 7.532% | 0.92468 | 14.48% | [5 empty] | Non-TXV | 7.532%
Chico | CA | 95928-7520 |  | 2012-05-30 | 2012-05-30 15:12 | 2012-05-30 16:04 | TRANE - YCC024FK0BJ | 65 | 5.5 | Yes | Yes | 24.8 | 22.1 | 2.7 | B15727BD5EE64BB78F2A461A0718A9A1 |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Tracy | CA | 95376-4131 |  | 2012-07-09 | 2012-07-09 10:19 | 2012-07-09 10:46 | DAY & NIGHT - UNK | 71 | 2.1 | Yes | Yes | 19.1 | 20.2 | -1.1 | F69117D089E443829E289CE2458D8E28 |  | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Merced | CA | 95348-1655 |  | 2012-05-30 | 2012-05-30 10:15 | 2012-05-30 10:32 | PAYNE - PY3PNA036060NB | 114 | 3.4 | Yes | Yes | 25.7 | 20.4 | 5.3 | 6D03005D323C444D8C95665AC54515AE | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Gustine | CA | 95322-1910 |  | 2012-05-24 | 2012-05-24 13:08 | 2012-05-24 13:30 | RHEEM - RAKA-037JAZ | 85 | 3.6 | Yes | Yes | 22.9 | 21.4 | 1.5 | 7E8F3BC844164BEBB39390C32E7DA857 |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Los Banos | CA | 93635-3579 |  | 2012-05-22 | 2012-05-22 10:06 | 2012-05-22 10:06 | FRASER JONHSTONE - 24ECW060GA | 84 | 0 | Yes | Yes | 4.7 | 21.3 | -16.6 | 5024E9DB6E774B36A7D559D9EE167421 | Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4903 |  | 2012-05-18 | 2012-05-18 14:14 | 2012-05-18 14:35 | GIBSON - UNK | 82 | 10.7 | Yes | Yes | 22 | 20.1 | 2 | 3C42A616673E4B0091785120E0ED5023 |  | R22 | Non-TXV |  | 13.05% | 0.86951 | 25.08% | [5 empty] | Non-TXV | 13.05%
Merced | CA | 95348-1655 |  | 2012-05-31 | 2012-05-31 12:44 | 2012-05-31 13:05 | AMERICAN STANDARD - YCC030F1M0AA | 73 | 2.2 | Yes | Yes | 17.6 | 18.9 | -1.3 | E82E60F4E90D445E9A0F410043751DB6 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Stockton | CA | 95206-5819 |  | 2012-05-30 | 2012-05-30 12:51 | 2012-05-30 13:11 | RUUD - UAFD-036JAS | 80 | 4.4 | Yes | Yes | 17.8 | 20.4 | -2.6 | 625EB05F794C4A6DB75EE4ADB9796413 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Chico | CA | 95928-5942 |  | 2012-05-22 | 2012-05-22 10:03 | 2012-05-22 10:24 | DAY N NIGHT - PGD33060K001C1 | 105 | 3.2 | Yes | Yes | 21 | 22.8 | -1.8 | 8C061E78903F4B17AE2C65D7F50C7FF2 |  | R410A | Non-TXV |  | 3.048% | 0.96952 | 5.857% | [5 empty] | Non-TXV | 3.048%
Marysville | CA | 95901-6810 |  | 2012-05-22 | 2012-05-22 16:44 | 2012-05-22 17:04 | GOODMAN - UNK | 74 | 12.8 | Yes | Yes | 18 | 19.4 | -1.4 | C2A8DE7B88C44C929BB06F1E7541B45A |  | R22 | Non-TXV |  | 17.3% | 0.82703 | 33.24% | [5 empty] | Non-TXV | 17.3%
Oroville | CA | 95965-4797 |  | 2012-06-06 | 2012-06-06 12:15 | 2012-06-06 12:15 | TRANE - TTB024C100A2 | 55 | 0 | Yes | Yes | 21.7 | 20.4 | 1.3 | 217218A0FFB84123B938F90BD43E125B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Plumas Lake | CA | 95961-9061 |  | 2012-07-18 | 2012-07-18 14:39 | 2012-07-18 15:05 | CARRIER - UNK | 98 | 7 | Yes | Yes | 16 | 18.5 | -2.5 | 3D575925E19E4BB69E9DB37106AF328C |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Plumas Lake | CA | 95961-9134 |  | 2012-07-30 | 2012-07-30 13:08 | 2012-07-30 13:30 | CARRIER - 30BRC3630 | 100 | 6.6 | Yes | Yes | 16 | 18.7 | -2.7 | 87261294EFE94A16B32A9AE38F261EA7 |  | R22 | Non-TXV |  | 6.6% | 0.934 | 12.68% | [5 empty] | Non-TXV | 6.6%
Merced | CA | 95348-1127 |  | 2012-05-29 | 2012-05-29 15:21 | 2012-05-29 15:49 | AIRE-FLO - 588ANW030040ACAD | 85 | 5.2 | Yes | Yes | 23.4 | 19.5 | 3.9 | CEBCB66AAF274436A3E40270E8F917B6 |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Stockton | CA | 95219-3625 |  | 2012-06-15 | 2012-06-15 09:58 | 2012-06-15 10:19 | YORK - H2CC036A06A | 76 | 2.3 | Yes | Yes | 18.4 | 20.4 | -2 | 52F3547205754DB5BA10B4302F420F10 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Atwater | CA | 95301-3728 |  | 2012-05-21 | 2012-05-21 10:50 | 2012-05-21 11:09 | GOODMAN - GPG13360701AC | 112 | 3.4 | Yes | Yes | 23.2 | 19.3 | 3.9 | 6B2A7EB044A0404E9475E6BDFDA4D994 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Olivehurst | CA | 95961-4637 |  | 2012-08-01 | 2012-08-01 11:27 | 2012-08-01 11:46 | TRANE - YCY036G1M0AC | 129 | 3.9 | Yes | Yes | 24 | 20.9 | 3.1 | ED82D8CDFF6E42919B661E7C90F7B74D |  | R22 | TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | TXV | 3.023%
Oroville | CA | 95965-9210 |  | 2012-07-18 | 2012-07-18 11:19 | 2012-07-18 11:39 | TRANE - 4TTB4030E1000AA | 112 | 4.2 | Yes | Yes | 21.2 | 19.7 | 1.5 | E63A6A06C8F74416B94D6780B4D24B7E |  | R410A | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Chico | CA | 95928-6098 |  | 2012-05-24 | 2012-05-24 11:05 | 2012-05-24 11:28 | TRANE - YCC018F1LOBJ | 62 | 8.5 | Yes | Yes | 24 | 21.1 | 3 | 11BF2E8C0C384F03BD6190C490564AEC |  | R22 | Non-TXV |  | 13.71% | 0.8629 | 26.35% | [5 empty] | Non-TXV | 13.71%
Paso Robles | CA | 93446-3243 |  | 2012-07-11 | 2012-07-11 12:23 | 2012-07-11 12:41 | BDP - 567GJ048 | 125 | 4 | Yes | Yes | 27.1 | 24.8 | 2.3 | C78637D4C2CE4024AA67554BB44F6395 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95206-2883 |  | 2012-05-22 | 2012-05-22 16:07 | 2012-05-22 16:31 | PAYNE - 561CJ030-C | 72 | 3.6 | Yes | Yes | 18.8 | 20.9 | -2.1 | 7391E87E183244ED8C3D884567FA3FDB |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Merced | CA | 95340-3436 |  | 2012-05-21 | 2012-05-21 12:15 | 2012-05-21 12:15 | PAYNE - 588ANW036060ACAF | 67 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | A655D646E48C473583838ACCBE654F03 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-3345 |  | 2012-06-06 | 2012-06-06 15:46 | 2012-06-06 17:28 | YORK - YCJD36S41S1HA | 72 | 5.5 | Yes | Yes | 24.6 | 22.1 | 2.6 | 4B85031B8EA44B72808DA527C797B183 |  | R410A | Non-TXV |  | 7.639% | 0.92361 | 14.68% | [5 empty] | Non-TXV | 7.639%
Penn Valley | CA | 95946-9605 |  | 2012-06-15 | 2012-06-15 14:16 | 2012-06-15 14:16 | TRANE - YCC030F1M0BC | 72 | 0 | Yes | Yes | 20.9 | 20.9 | 0 | AB1959E5DA0D49CCA9425C794743C2DD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2224 |  | 2012-05-30 | 2012-05-30 12:30 | 2012-05-30 12:49 | CARRIER - 48GS-036060301 | 56 | 1.6 | Yes | Yes | 24 | 21 | 3 | A70614CBA5934D24A7A7240ABF1150C9 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Merced | CA | 95341-7016 |  | 2012-05-30 | 2012-05-30 13:18 | 2012-05-30 13:36 | BRYANT - 582ANW042060NAAG | 100 | 7 | Yes | Yes | 27.2 | 21.2 | 6 | 1A0B904B51824FAD830B5E4B04ABF04F |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Merced | CA | 95348-1541 |  | 2012-07-05 | 2012-07-05 13:22 | 2012-07-05 13:42 | BDP - NA | 53 | 1.6 | Yes | Yes | 18.2 | 20.3 | -2.1 | 57E97ED57DBB424E8248AF6387D65B29 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Merced | CA | 95341-5941 |  | 2012-06-12 | 2012-06-12 15:56 | 2012-06-12 15:56 | RHEEM - RRNL-B036JK06X | 92 | 0 | Yes | Yes | 15.8 | 18.6 | -2.8 | 3B82B671BE3D43D889D5BBB9A4D3CCF7 |  | R410A | TXV |  | 0% | 1 | 0%
Madera | CA | 93638-3294 |  | 2012-06-15 | 2012-06-15 12:08 | 2012-06-15 12:25 | YORK - D1NH030N03606C | 73 | 6 | Yes | Yes | 23.2 | 23 | 0.2 | C2B7DD02C68C4C62887BA9EE5D8E5967 |  | R22 | Non-TXV |  | 8.219% | 0.91781 | 15.8% | [5 empty] | Non-TXV | 8.219%
Orland | CA | 95963-9687 |  | 2012-07-05 | 2012-07-05 10:20 | 2012-07-05 10:37 | HEIL - N4H336AKB300 | 100 | 7.9 | Yes | Yes | 19.2 | 20.9 | -1.7 | C4801893BC04407BB2DED8950EDE49BF |  | R410A | Non-TXV |  | 7.9% | 0.921 | 15.18% | [5 empty] | Non-TXV | 7.9%
Chico | CA | 95928-7520 |  | 2012-06-01 | 2012-06-01 11:43 | 2012-06-01 12:11 | AMERICAN STANDARD - YCPAC | 106 | 4.9 | Yes | Yes | 18.7 | 20.6 | -1.9 | 607B408FF417428184FD71182F036AC8 |  | R22 | Non-TXV |  | 4.623% | 0.95377 | 8.884% | [5 empty] | Non-TXV | 4.623%
Placerville | CA | 95667-8670 |  | 2012-07-05 | 2012-07-05 16:50 | 2012-07-05 16:50 | TRANE - YCY024G1M0AD | 104 | 0 | Yes | Yes | 23.8 | 20.4 | 3.4 | E8391A8A9FED41F0A245F6AACE04CB10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2043 |  | 2012-06-06 | 2012-06-06 14:20 | 2012-06-06 14:39 | DAY & NIGHT - 569BJ036 | 93 | 13.9 | Yes | Yes | 19.4 | 20.4 | -1 | E07FB33314A54DBCA4A20FF31DEF00F5 |  | R22 | Non-TXV |  | 14.95% | 0.85054 | 28.72% | [5 empty] | Non-TXV | 14.95%
Dinuba | CA | 93618-9502 |  | 2012-05-21 | 2012-05-21 15:36 | 2012-05-21 15:54 | TEMPSTAR - CA3048VKA1 | 138 | 4.2 | Yes | Yes | 21.8 | 19.1 | 2.7 | 4FB188BBF4124364832C15EDE757F609 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Stockton | CA | 95210-4233 |  | 2012-05-22 | 2012-05-22 10:44 | 2012-05-22 11:03 | CARRIER - 591ANX024000AAAA | 56 | -4 | Yes | Yes | 23.8 | 19.3 | 4.5 | AA1A8899769C4727926CB46F6CF545E3 |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Manteca | CA | 95337-8994 |  | 2012-05-21 | 2012-05-21 12:54 | 2012-05-21 13:18 | RHEEM - RAKA-060JAZ | 112 | 3.4 | Yes | Yes | 21.6 | 21.5 | 0.1 | 5D835836E17145418841368918A0C0DA | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Atwater | CA | 95301-2606 |  | 2012-05-18 | 2012-05-18 15:11 | 2012-05-18 15:29 | GOODMAN - GPG1330045M41AC | 80 | 2.4 | Yes | Yes | 22 | 20.4 | 1.6 | 37B78A482356411398DEFB6BFB749677 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Atwater | CA | 95301-4863 |  | 2012-05-22 | 2012-05-22 10:22 | 2012-05-22 10:39 | RHEEM - NA | 60 | 1.8 | Yes | Yes | 19.2 | 19.7 | -0.4 | 20C2A8810926402A88E312507530F9F1 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Planada | CA | 95365-8033 |  | 2012-05-22 | 2012-05-22 14:12 | 2012-05-22 14:44 | GOODMAN - GPG1336070M1AB | 85 | 2.8 | Yes | Yes | 25.7 | 19.9 | 5.8 | 9EA752E757914A33BA272D61E76B9793 |  | R410A | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Chico | CA | 95928-6779 |  | 2012-05-30 | 2012-05-30 13:38 | 2012-05-30 14:57 | AMERICAN STANDARD - 4A7B4030E1000AA | 114 | 6 | Yes | Yes | 20.5 | 21 | -0.5 | 8F29C6BAB31E44E6B583497953AFD693 |  | R410A | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Atwater | CA | 95301-4885 |  | 2012-07-05 | 2012-07-05 11:58 | 2012-07-05 12:24 | RHEEM - RAFA030RJQ | 59 | 1.8 | Yes | Yes | 17.4 | 19.5 | -2.1 | 4F7A87928D12480DB1DD2D19003BE21D |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Valley Springs | CA | 95252-9483 |  | 2012-07-06 | 2012-07-06 10:39 | 2012-07-06 10:56 | RUUD - UAKA-030JAZ | 62 | -3.6 | Yes | Yes | 19.6 | 19.8 | -0.2 | E0C0B8F573A04D44A1C2A75FD78A8D87 |  | R22 | Non-TXV |  | -5.806% | 1.0581 | 1.626% |  |  |  |  | Non-TXV |  |  | -5.806%
Valley Springs | CA | 95252-9015 |  | 2012-07-06 | 2012-07-06 11:52 | 2012-07-06 12:11 | BRYANT - 113RNA048-C | 124 | 3.9 | Yes | Yes | 21.5 | 21 | 0.5 | BED3D0DF1E804FF79D771077D062098B |  | R22 | Non-TXV |  | 3.145% | 0.96855 | 6.044% | [5 empty] | Non-TXV | 3.145%
Chico | CA | 95928-4713 |  | 2012-07-10 | 2012-07-10 12:59 | 2012-07-10 13:19 | YORK - H1CB030506A | 81 | 6.1 | Yes | Yes | 21.1 | 22 | -0.9 | 223339FBC8E043A99FB59315D8A4ECCE |  | R22 | Non-TXV |  | 7.531% | 0.92469 | 14.47% | [5 empty] | Non-TXV | 7.531%
Merced | CA | 95340-1617 |  | 2012-05-31 | 2012-05-31 14:57 | 2012-05-31 15:22 | AIRE-FLO - TTN048C100A0 | 151 | 10.8 | Yes | Yes | 16.6 | 18.8 | -2.2 | 2B111170E3D4456ABB20F1C997C55DA5 |  | R22 | Non-TXV |  | 7.152% | 0.92848 | 13.75% | [5 empty] | Non-TXV | 7.152%
Chico | CA | 95926-2863 |  | 2012-05-18 | 2012-05-18 11:34 | 2012-05-18 11:34 | YORK - H2DA036S06A | 92 | 0 | Yes | Yes | 26 | 21.7 | 4.4 | 37DE1782CAF8412E97FF28040ACC9EC3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-3831 |  | 2012-08-16 | 2012-08-16 14:30 | 2012-08-16 15:08 | RHEEM - RAHE-036JAS | 91 | 19.3 | Yes | Yes | 19.8 | 20.6 | -0.8 | E07CB9C71D59432FAF4295419E7718F6 |  | R22 | Non-TXV |  | 21.21% | 0.78791 | 40.76% | [5 empty] | Non-TXV | 21.21%
Rocklin | CA | 95765-4263 |  | 2012-05-23 | 2012-05-23 13:47 | 2012-05-23 13:47 | UNITARY PRODUCTS GROUP - AC024M1021A | 52 | 0 | Yes | Yes | 17.3 | 18.7 | -1.4 | 0CC801E87A3F47469A6494440BC2A237 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2546 |  | 2012-07-05 | 2012-07-05 09:25 | 2012-07-05 09:54 | TRANE - UNK | 69 | 3.9 | Yes | Yes | 20.7 | 21 | -0.3 | B4B9A659230741FD8A5537391C468BBB |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Yuba City | CA | 95993-5230 |  | 2012-05-21 | 2012-05-21 12:14 | 2012-05-21 12:14 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 22.5 | 19.7 | 2.9 | 71465AF946BC4C4396E598E77D3C2FCB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-5100 |  | 2012-07-26 | 2012-07-26 13:48 | 2012-07-26 14:08 | AMERICAN STANDARD - 4A7B4030E1000AA | 112 | 8.4 | Yes | Yes | 20.2 | 22.5 | -2.3 | 5C942904819D419C8D35AB1166ED0D45 |  | R410A | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95205-3714 |  | 2012-05-29 | 2012-05-29 14:35 | 2012-05-29 15:00 | RUUD - UAMB-030JAZ | 77 | 4.5 | Yes | Yes | 17 | 19.9 | -2.9 | 5A734A00EABB4AC7B21CD573D18585BD |  | R22 | Non-TXV |  | 5.844% | 0.94156 | 11.23% | [5 empty] | Non-TXV | 5.844%
Selma | CA | 93662-9725 |  | 2012-06-11 | 2012-06-11 14:09 | 2012-06-11 14:23 | CARRIER - 50HS-048-311 | 136 | 4.6 | Yes | Yes | 22.6 | 20.9 | 1.7 | 6BC751A0A0CC4BDFBD2E9844A22A7533 |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Marysville | CA | 95901-6813 |  | 2012-05-23 | 2012-05-23 10:49 | 2012-05-23 11:07 | CARRIER - 38CK024340 | 54 | -7.3 | Yes | Yes | 13 | 15.2 | -2.2 | D91A7387C5D641D1868A514A8BAD419B |  | R22 | Non-TXV |  | -13.52% | 1.1352 | 3.786% |  |  |  |  | Non-TXV |  |  | -13.52%
Madera | CA | 93637-5729 |  | 2012-06-08 | 2012-06-08 12:25 | 2012-06-08 12:44 | CARRIER - 38TH030310 | 68 | 2 | Yes | Yes | 24 | 19.8 | 4.2 | 2CE52A688DCA4C2386606668C9533815 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Merced | CA | 95340-1670 |  | 2012-06-11 | 2012-06-11 12:29 | 2012-06-11 12:54 | RUUD - UACC030JAS | 58 | 9.3 | Yes | Yes | 25.9 | 20.9 | 5 | DDE6FCE3A6A54FAFB99792F3C33AB52F |  | R22 | Non-TXV |  | 16.03% | 0.83966 | 30.81% | [5 empty] | Non-TXV | 16.03%
Stockton | CA | 95206-2046 |  | 2012-05-22 | 2012-05-22 11:27 | 2012-05-22 11:44 | RUUD - UNK | 96 | 8.5 | Yes | Yes | 17.4 | 19.9 | -2.5 | 11B87BBB70134A108EB4836869F96784 |  | R22 | Non-TXV |  | 8.854% | 0.91146 | 17.02% | [5 empty] | Non-TXV | 8.854%
Madera | CA | 93637-2663 |  | 2012-05-21 | 2012-05-21 14:18 | 2012-05-21 19:35 | YORK - UNK | 85 | 3.1 | Yes | Yes | 17.5 | 20.4 | -2.9 | C28E0EC91AC14F60B74630B8F0AE0D90 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Merced | CA | 95341-6762 |  | 2012-06-07 | 2012-06-07 12:45 | 2012-06-07 13:05 | DAY & NIGHT - 580AN024040 | 80 | 7.5 | Yes | Yes | 26 | 23.9 | 2.1 | EF614A55628747ADAB0D0624CCDB08BD |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Atwater | CA | 95301-4879 |  | 2012-07-05 | 2012-07-05 14:12 | 2012-07-05 14:32 | OTHER - NA | 62 | 1.8 | Yes | Yes | 18.1 | 18.3 | -0.2 | D2F8FC0A650D4E27B514EF050D3A101B |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Reedley | CA | 93654-7015 |  | 2012-07-16 | 2012-07-16 10:20 | 2012-07-16 10:47 | WEATHER KING - 14AJA36A01 | 144 | 4.3 | Yes | Yes | 17.4 | 20.4 | -3 | 07E144F655A24E5C86B8FB6EF39DCCB9 |  | R22 | Non-TXV |  | 2.986% | 0.97014 | 5.739% | [5 empty] | Non-TXV | 2.986%
Reedley | CA | 93654-7015 |  | 2012-07-16 | 2012-07-16 11:29 | 2012-07-16 11:53 | WEATHER KING - 14AJA30A01 | 113 | 3.5 | Yes | Yes | 19 | 20.1 | -1.1 | A54FB1FCAD8C4683A5EF7EFB69C30100 |  | R22 | Non-TXV |  | 3.097% | 0.96903 | 5.952% | [5 empty] | Non-TXV | 3.097%
Merced | CA | 95341-7006 |  | 2012-05-30 | 2012-05-30 10:19 | 2012-05-30 10:44 | GOODMAN - CLJ301 | 96 | 13.9 | Yes | Yes | 18.8 | 21.5 | -2.7 | 7779D9B8DB064801B200F6F1907A51FD |  | R22 | Non-TXV |  | 14.48% | 0.85521 | 27.83% | [5 empty] | Non-TXV | 14.48%
Merced | CA | 95341-7001 |  | 2012-05-29 | 2012-05-29 14:13 | 2012-05-29 14:39 | AIRE-FLO - PY1PNB036060ABAA | 85 | 9.8 | Yes | Yes | 23.8 | 19.7 | 4.1 | 1E0D02FE1DAF45E1973B7C2342F9A496 |  | R22 | Non-TXV |  | 11.53% | 0.88471 | 22.16% | [5 empty] | Non-TXV | 11.53%
Merced | CA | 95348-1500 |  | 2012-05-30 | 2012-05-30 13:34 | 2012-05-30 13:59 | HEIL - CA3016UAK3 | 67 | 7.2 | Yes | Yes | 19.2 | 20.4 | -1.2 | C8A23B8E9E204087B50FB6E52558F15C |  | R22 | Non-TXV |  | 10.75% | 0.89254 | 20.65% | [5 empty] | Non-TXV | 10.75%
Merced | CA | 95348-1500 |  | 2012-05-31 | 2012-05-31 12:58 | 2012-05-31 13:15 | BDP - 151CJ018-B | 85 | 4.1 | Yes | Yes | 18.1 | 19.8 | -1.7 | 5575DD2D34414CF99204BEA3714A1BB4 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Yuba City | CA | 95993-8851 |  | 2012-05-24 | 2012-05-24 14:30 | 2012-05-24 14:30 | DAY & NIGHT - 585GJ036060 | 82 | 0 | Yes | Yes | 19.1 | 19.3 | -0.2 | 73DD88FFB85049E38ABAD69EDE7DE584 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-8315 |  | 2012-05-30 | 2012-05-30 16:03 | 2012-05-30 16:03 | LENNOX - HS25-461-1P | 133 | 0 | Yes | Yes | 22.1 | 22.6 | -0.5 | EDF095EB8DA14993BC211E2C09E2FF4A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2682 |  | 2012-05-21 | 2012-05-21 13:54 | 2012-05-21 14:15 | CARRIER - 38EZG048300 | 125 | 7.2 | Yes | Yes | 21.1 | 20.9 | 0.2 | F466C931D6FF4966B14C676838DCD9D3 |  | R410A | TXV |  | 5.76% | 0.9424 | 11.07% | [5 empty] | TXV | 5.76%
Merced | CA | 95348-1544 |  | 2012-07-10 | 2012-07-10 12:26 | 2012-07-10 13:06 | GOODMAN - GSC030241EA | 85 | 2.6 | Yes | Yes | 16 | 17.5 | -1.5 | ED87CD6A82AD4FDC9CDA88C1183873FE |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93722-3736 |  | 2012-05-24 | 2012-05-24 14:50 | 2012-05-24 15:29 | CARRIER - 38TDA36300 | 183 | 20.1 | Yes | Yes | 18.9 | 20.1 | -1.2 | C11CB1E80FAF4208A4D0D2389A79EB2B |  | R22 | Non-TXV |  | 10.98% | 0.89016 | 21.11% | [5 empty] | Non-TXV | 10.98%
Fresno | CA | 93720-5456 |  | 2012-07-09 | 2012-07-09 08:14 | 2012-07-09 08:55 | LENNOX - 13ACC-048-230-01 | 158 | 4.7 | Yes | Yes | 21.4 | 21.5 | -0.1 | 1960A93E79B34A348286FA1E018D203F |  | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.717% | [5 empty] | Non-TXV | 2.975%
Chico | CA | 95928-5942 |  | 2012-05-22 | 2012-05-22 11:54 | 2012-05-22 12:35 | AMERICAN STANDARD - 4YCC3030A1075AA | 97 | 4.1 | Yes | Yes | 19.9 | 20.8 | -0.9 | F2BE7719D9CE406AA1FDE7FF2FB7C647 |  | R410A | Non-TXV |  | 4.227% | 0.95773 | 8.123% | [5 empty] | Non-TXV | 4.227%
Merced | CA | 95341-6711 |  | 2012-06-07 | 2012-06-07 11:32 | 2012-06-07 11:50 | DAY & NIGHT - UNK | 56 | 7.3 | Yes | Yes | 23.3 | 22.1 | 1.2 | 23AFFDCC35F04B6D8B71F3F8A5AED013 |  | R22 | Non-TXV |  | 13.04% | 0.86964 | 25.05% | [5 empty] | Non-TXV | 13.04%
Reedley | CA | 93654-3814 |  | 2012-07-16 | 2012-07-16 11:54 | 2012-07-16 12:22 | NORDYNE - N/A | 90 | 4.2 | Yes | Yes | 18.2 | 20.4 | -2.2 | 781291F5FC9348A5A619E07E66B7850C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Winton | CA | 95388-9643 |  | 2012-05-24 | 2012-05-24 10:52 | 2012-05-24 11:11 | AMERICAN STANDARD - YCY030G1M0AD | 124 | 3.7 | Yes | Yes | 26.2 | 20.7 | 5.5 | 1695D775835544E49327405D1D3C21F1 |  | R22 | Non-TXV |  | 2.984% | 0.97016 | 5.734% | [5 empty] | Non-TXV | 2.984%
Atwater | CA | 95301-4879 |  | 2012-05-24 | 2012-05-24 15:40 | 2012-05-24 15:57 | LENNOX - NA | 70 | 2.1 | Yes | Yes | 17.7 | 20.4 | -2.7 | 025398974EE94E058BF1FDEDF7DF1768 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Atwater | CA | 95301-4880 |  | 2012-06-15 | 2012-06-15 11:19 | 2012-06-15 12:02 | GOODMAN - CK30-1B | 79 | 2.3 | Yes | Yes | 24.5 | 19.9 | 4.6 | CC3418A721604920B600393516E5019D |  | R22 | Non-TXV |  | 2.911% | 0.97089 | 5.595% | [5 empty] | Non-TXV | 2.911%
Merced | CA | 95348-2303 |  | 2012-05-30 | 2012-05-30 13:42 | 2012-05-30 14:03 | OTHER - NA | 54 | 1.6 | Yes | Yes | 16.5 | 18.5 | -2 | E368DA5783D745CF81CB59B6B50F7675 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Orange Cove | CA | 93646-2180 |  | 2012-07-13 | 2012-07-13 08:54 | 2012-07-13 09:11 | CARRIER - 48SX-030060321AA | 69 | 2 | Yes | Yes | 19.3 | 18.4 | 0.9 | 341C6594F8514191B44B973FD8DF1789 |  | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
Chowchilla | CA | 93610-3407 |  | 2012-06-14 | 2012-06-14 10:57 | 2012-06-14 11:17 | OTHER - 80WE3061 | 90 | 4.6 | Yes | Yes | 21.3 | 19.3 | 2 | 8ECCBF4D5C3749DEB9B82B188A03F420 |  | R22 | Non-TXV |  | 5.111% | 0.94889 | 9.822% | [5 empty] | Non-TXV | 5.111%
Grass Valley | CA | 95945-7335 |  | 2012-07-09 | 2012-07-09 10:10 | 2012-07-09 10:10 | GOODMAN - CK24-1B | 71 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | 7CD472CE8B014DB49D54D1EC6AC81BFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-3507 |  | 2012-05-30 | 2012-05-30 17:46 | 2012-05-30 18:08 | AMANA - PGB30C0702E | 64 | 2.1 | Yes | Yes | 21.9 | 19.7 | 2.2 | 0CA7B65E24354663B75D95C5D1EFA07D |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
French Camp | CA | 95231-9713 |  | 2012-07-09 | 2012-07-09 10:30 | 2012-07-09 10:50 | CARRIER - 38EN036320 | 92 | -8.7 | Yes | Yes | 14.4 | 17.2 | -2.8 | DB85E320B78C4279B6F82F2B2FEFA7C2 |  | R22 | Non-TXV |  | -9.457% | 1.0946 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.457%
Stockton | CA | 95210-4226 |  | 2012-05-22 | 2012-05-22 12:59 | 2012-05-22 13:17 | CARRIER - 591ANX024000AAAA | 56 | -3.3 | Yes | Yes | 21.6 | 21 | 0.6 | 3661C946ABE140959119C8F931A710C9 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Madera | CA | 93638-1558 |  | 2012-06-11 | 2012-06-11 15:26 | 2012-06-11 15:47 | OTHER - GR6GD-X30K045X | 96 | 3.4 | Yes | Yes | 25.8 | 20.2 | 5.6 | B046B2AB1FD54391B92EDE02A2515634 |  | R410A | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Madera | CA | 93637-4873 |  | 2012-05-18 | 2012-05-18 13:57 | 2012-05-18 14:17 | LENNOX - 13ACC-042-230-01 | 123 | 3.7 | Yes | Yes | 27.2 | 21.5 | 5.7 | D295C2E22B9048E0BCE2C2A8C25C8108 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.781% | [5 empty] | Non-TXV | 3.008%
Merced | CA | 95341-7712 |  | 2012-05-29 | 2012-05-29 11:59 | 2012-05-29 12:22 | AIRE-FLO - UAKA030JAZ | 85 | 8.4 | Yes | Yes | 21.5 | 18.8 | 2.7 | E25D3BFA1E5046C1B1E2D2AD50EE7D82 |  | R22 | Non-TXV |  | 9.882% | 0.90118 | 18.99% | [5 empty] | Non-TXV | 9.882%
Chico | CA | 95926-4466 |  | 2012-05-18 | 2012-05-18 14:16 | 2012-05-18 14:16 | BRYANT - 213RNA024000BCAA | 96 | 0 | Yes | Yes | 25.2 | 22.1 | 3.1 | 8422FB73A587474F86C9FD83317A4A2A | OK: Verified Refrigerant Charge | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6059 |  | 2012-07-03 | 2012-07-03 14:25 | 2012-07-03 14:47 | GOODMAN - GSC130601BC | 169 | 6.8 | Yes | Yes | 21.7 | 20.2 | 1.6 | 771856028FC54B9ABC7D9F5DBED8EBB1 |  | R22 | Non-TXV |  | 4.024% | 0.95976 | 7.733% | [5 empty] | Non-TXV | 4.024%
Tracy | CA | 95376-9612 |  | 2012-06-26 | 2012-06-26 12:11 | 2012-06-26 12:35 | RHEEM - FAFD-048JBS | 101 | 13 | Yes | Yes | 18.3 | 19.9 | -1.6 | 88ED334B6F58405780B4A1C2E3FEAC5B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.87% | 0.87129 | 24.74% | [5 empty] | Non-TXV | 12.87%
Atwater | CA | 95301-4805 |  | 2012-05-22 | 2012-05-22 11:24 | 2012-05-22 11:32 | BDP - 598ANX036000ABAA | 205 | 6.2 | Yes | Yes | 22.9 | 18.9 | 4.1 | 28D40CB1BDE6458D8766873E6A35F308 |  | R22 | Non-TXV |  | 3.024% | 0.96976 | 5.812% | [5 empty] | Non-TXV | 3.024%
Fresno | CA | 93722-4421 |  | 2012-05-18 | 2012-05-18 14:15 | 2012-05-18 14:38 | PAYNE - 585A024055YAC | 55 | 1.8 | Yes | Yes | 18.4 | 21 | -2.6 | E78F62F351B64C7F92A2FC5C0D34AEA0 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Stockton | CA | 95210-2311 |  | 2012-05-23 | 2012-05-23 10:15 | 2012-05-23 10:32 | GE - 21TA930H1D | 102 | 3.3 | Yes | Yes | 20.5 | 19.7 | 0.8 | 864A6917D1D142CBBF216E1F6CD0FDE9 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Madera | CA | 93638-3540 |  | 2012-07-13 | 2012-07-13 09:20 | 2012-07-13 09:46 | CARRIER - N/A | 69 | 2 | Yes | Yes | 24.4 | 21.9 | 2.5 | 3398909F0A2E45C2A559019433936522 |  | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
Marysville | CA | 95901-7707 |  | 2012-05-31 | 2012-05-31 12:26 | 2012-05-31 12:51 | LENNOX - HS22-261V-2P | 104 | 3.5 | Yes | Yes | 18 | 19.3 | -1.3 | DAE65D4528F143369FA1CB81889BBCFA |  | R22 | Non-TXV |  | 3.365% | 0.96635 | 6.468% | [5 empty] | Non-TXV | 3.365%
Marysville | CA | 95901-7708 |  | 2012-05-31 | 2012-05-31 14:27 | 2012-05-31 14:50 | GOODMAN - CKJ42-1AB | 106 | 9.8 | Yes | Yes | 17 | 19.3 | -2.3 | 04ECF7F3541B4B9C877F86691CEFC66B |  | R22 | Non-TXV |  | 9.245% | 0.90755 | 17.77% | [5 empty] | Non-TXV | 9.245%
Fresno | CA | 93722-4411 |  | 2012-05-23 | 2012-05-23 17:31 | 2012-05-23 17:55 | PAYNE - 585A024055 | 52 | 1.8 | Yes | Yes | 19 | 21.3 | -2.3 | 315111E69EA94996A0B350FCE9FA3C2F |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Merced | CA | 95348-1655 |  | 2012-07-03 | 2012-07-03 09:47 | 2012-07-03 10:08 | PAYNE - PY1PNB024060AAAA | 55 | 1.8 | Yes | Yes | 21 | 19.7 | 1.3 | 7B7625CDC99D44E8BE82B6288A1A4BF3 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Rocklin | CA | 95677-2550 |  | 2012-05-29 | 2012-05-29 09:31 | 2012-05-29 09:53 | TRANE - BWD718A100B0 | 88 | 6 | Yes | Yes | 23.9 | 18.7 | 5.2 | 6491993786234FBC9E2258DE82937941 |  | R22 | Non-TXV |  | 6.818% | 0.93182 | 13.1% | [5 empty] | Non-TXV | 6.818%
Los Banos | CA | 93635-3407 |  | 2012-05-22 | 2012-05-22 12:53 | 2012-05-22 13:21 | BRYANT - 583BNW030040AB-- | 85 | 0.5 | Yes | Yes | 23.3 | 22.6 | 0.7 | 90B68E34F799490D92E3AC91AC24473D |  | R410A | TXV |  | 0.5882% | 0.99412 | 1.13% | [5 empty] | TXV | 0.5882%
Oroville | CA | 95965-4076 |  | 2012-07-05 | 2012-07-05 09:53 | 2012-07-05 10:09 | TRANE - 4TTB4030E1000AA | 113 | 3.5 | Yes | Yes | 21 | 21 | 0 | CDA0B506FD294779B073AD5FE7CC5BAD |  | R410A | Non-TXV |  | 3.097% | 0.96903 | 5.952% | [5 empty] | Non-TXV | 3.097%
Merced | CA | 95348-8717 |  | 2012-05-31 | 2012-05-31 13:36 | 2012-05-31 13:52 | GOODMAN - CRT48-1 | 144 | 8.3 | Yes | Yes | 16.8 | 19.8 | -3 | 8FACECEDF3A4457BA6DDD664085464CC |  | R22 | Non-TXV |  | 5.764% | 0.94236 | 11.08% | [5 empty] | Non-TXV | 5.764%
Marysville | CA | 95901-7706 |  | 2012-05-31 | 2012-05-31 13:15 | 2012-05-31 13:15 | LENNOX - HS22-261V12D | 104 | 0 | Yes | Yes | 18 | 17.2 | 0.8 | E38D3670C436496AB5959346B604DF26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-7107 |  | 2012-05-30 | 2012-05-30 12:34 | 2012-05-30 12:56 | LENNOX - HS29-311-3P | 69 | 2.1 | Yes | Yes | 23 | 21.2 | 1.8 | B6418077154540BF8056C3E4DFF3AB03 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Chico | CA | 95928-7521 |  | 2012-06-08 | 2012-06-08 11:40 | 2012-06-08 11:54 | TRANE - YCP036F1LOAC | 107 | 3.3 | Yes | Yes | 22 | 21.5 | 0.5 | 1C6DFD683D0A4CB7A3504BB53EE895E3 |  | R22 | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Chico | CA | 95928-7523 |  | 2012-07-03 | 2012-07-03 09:30 | 2012-07-03 09:55 | TRANE - YCC018F1LOBJ | 75 | 6.4 | Yes | Yes | 26.4 | 21.3 | 5.1 | 1DBB25D4C9464FBCA897B0D10C0A4E10 |  | R22 | Non-TXV |  | 8.533% | 0.91467 | 16.4% | [5 empty] | Non-TXV | 8.533%
Chico | CA | 95973-7833 |  | 2012-05-30 | 2012-05-30 11:16 | 2012-05-30 11:46 | PAYNE - PH10JA024-C | 85 | 2.9 | Yes | Yes | 23.5 | 22.4 | 1.2 | 07CE82123B1142F6916337420D22977B |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Merced | CA | 95341-6847 |  | 2012-05-21 | 2012-05-21 12:46 | 2012-05-21 13:13 | RHEEM - RRKAA030JK06X | 85 | 7.7 | Yes | Yes | 27.7 | 22.6 | 5.1 | 0B00C254484B444FB5E2ED7D8932C313 |  | R22 | Non-TXV |  | 9.059% | 0.90941 | 17.41% | [5 empty] | Non-TXV | 9.059%
Fresno | CA | 93722-4436 |  | 2012-05-18 | 2012-05-18 13:52 | 2012-05-18 14:11 | GOODMAN - PGB024050-1 | 50 | 1.6 | Yes | Yes | 17.1 | 19.9 | -2.8 | B025FBABC3A14748BE09ABAC034668C3 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Winton | CA | 95388-9701 |  | 2012-05-18 | 2012-05-18 12:09 | 2012-05-18 12:26 | TRANE - YCC024F1LBH | 69 | 6.1 | Yes | Yes | 20.3 | 20.9 | -0.6 | E6DCB50468214241B4C93BD447529720 |  | R22 | Non-TXV |  | 8.841% | 0.91159 | 16.99% | [5 empty] | Non-TXV | 8.841%
Chico | CA | 95928-5948 |  | 2012-05-22 | 2012-05-22 11:12 | 2012-05-22 11:12 | TRANE - YCP030F1LOAA | 106 | 0 | Yes | Yes | 18.6 | 19.8 | -1.2 | 79346500611944CB860E553B132BC09F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-5948 |  | 2012-06-13 | 2012-06-13 18:31 | 2012-06-13 18:31 | AMERICAN STANDARD - 2YCX3030A1064AA | 88 | 0 | Yes | Yes | 27.5 | 24.2 | 3.3 | EC6B6E2FAD3C4022AFFFFDD95A0CC7B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6863 |  | 2012-06-08 | 2012-06-08 11:51 | 2012-06-08 12:09 | RHEEM - RRGF-05E24JKR | 42 | 3.5 | Yes | Yes | 21.2 | 19.9 | 1.3 | BFD408DD4EBB46DA88F9B8F4101C6EBA |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Madera | CA | 93637-6704 |  | 2012-06-13 | 2012-06-13 09:43 | 2012-06-13 10:25 | CARRIER - 48GX-042060301 | 118 | -11.1 | Yes | Yes | 21.8 | 20.9 | 0.9 | 23FA9BF2FF4E45E8B5B3D38437ED66D7 |  | R22 | Non-TXV |  | -9.407% | 1.0941 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.407%
Fresno | CA | 93722-4411 |  | 2012-05-18 | 2012-05-18 11:45 | 2012-05-18 12:01 | YORK - D2NP024NO5006A | 100 | 4.2 | Yes | Yes | 18.5 | 20.7 | -2.2 | F451186AAB654FE2A90A48DBAB4E12B2 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Winton | CA | 95388-9701 |  | 2012-05-18 | 2012-05-18 11:43 | 2012-05-18 12:00 | GOODMAN - GPG13240701BB | 79 | 3.5 | Yes | Yes | 25.9 | 20.2 | 5.8 | F6B4FC88301E41A4935D48B46492EF28 |  | R22 | Non-TXV |  | 4.43% | 0.9557 | 8.514% | [5 empty] | Non-TXV | 4.43%
Fresno | CA | 93727-5658 |  | 2012-05-21 | 2012-05-21 13:07 | 2012-05-21 13:25 | YORK - N1DN0365060 | 127 | 3.8 | Yes | Yes | 24.9 | 20.4 | 4.5 | 80C6789AF20145D5BE9722CCD89C1E69 |  | R22 | Non-TXV |  | 2.992% | 0.97008 | 5.75% | [5 empty] | Non-TXV | 2.992%
Merced | CA | 95340-3406 |  | 2012-07-20 | 2012-07-20 12:52 | 2012-07-20 13:11 | AIRE-FLO - UNK | 66 | 5.5 | Yes | Yes | 19.5 | 19.3 | 0.2 | CF9D60E6B8024F0795CDFBAD956079AB |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Stockton | CA | 95209-1104 |  | 2012-05-22 | 2012-05-22 13:22 | 2012-05-22 13:44 | GOODMAN - PGB048075-1 REV A | 86 | 8.5 | Yes | Yes | 24.4 | 21.6 | 2.8 | 07574B5DEF9E45059AC89641D2C716B7 |  | R22 | TXV |  | 9.884% | 0.90116 | 18.99% | [5 empty] | TXV | 9.884%
Chico | CA | 95928-5780 |  | 2012-05-21 | 2012-05-21 15:44 | 2012-05-21 18:26 | MERICAN STANDARD - 2YCX3030A1064AA | 89 | 14.2 | Yes | Yes | 24.2 | 23.2 | 1 | DF6EA2DCA350472898AB5E47FE260FBE |  | R22 | Non-TXV |  | 15.96% | 0.84045 | 30.66% | [5 empty] | Non-TXV | 15.96%
Merced | CA | 95341-6855 |  | 2012-05-21 | 2012-05-21 13:23 | 2012-05-21 13:42 | HEIL - PGF330080K011A1 | 152 | 8.8 | Yes | Yes | 22.8 | 22.1 | 0.7 | 6AA89906BA404C17B02079608A28DE41 |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Lincoln | CA | 95648-8298 |  | 2012-05-23 | 2012-05-23 12:50 | 2012-05-23 13:09 | CARRIER - 38CKC060370 | 134 | 7.9 | Yes | Yes | 21.6 | 20.3 | 1.3 | 1665BFAF88514F82A6FB51AE971AC173 |  | R22 | TXV |  | 5.896% | 0.94104 | 11.33% | [5 empty] | TXV | 5.896%
Stockton | CA | 95219-3937 |  | 2012-06-21 | 2012-06-21 15:14 | 2012-06-21 15:37 | DAY & NIGHT - YAC-108T | 54 | 2.9 | Yes | Yes | 22.5 | 19.7 | 2.9 | 7B763BA1A60444E7B20A79C7B56BEA81 |  | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Atwater | CA | 95301-4734 |  | 2012-06-11 | 2012-06-11 14:39 | 2012-06-11 14:58 | GOODMAN - CK36-1T | 76 | 2.4 | Yes | Yes | 19.6 | 21.2 | -1.6 | 7E6A15F2677447D090C55A86D48D3137 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Paso Robles | CA | 93446-5431 |  | 2012-07-09 | 2012-07-09 15:59 | 2012-07-09 16:16 | CARRIER - 38EZG030300 | 88 | 2.8 | Yes | Yes | 17.6 | 19.1 | -1.5 | 4EB527FDB6264B24B1669915EB880117 |  | R410A | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Manteca | CA | 95336-7061 |  | 2012-05-21 | 2012-05-21 11:47 | 2012-05-21 12:08 | BRYANT - 563CN060-F | 200 | 10.8 | Yes | Yes | 19.7 | 20.9 | -1.2 | 15F6F83BBB554632B7E6D69B33F3D2AA |  | R22 | TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | TXV | 5.4%
Merced | CA | 95341-7037 |  | 2012-06-08 | 2012-06-08 16:06 | 2012-06-08 16:33 | LENNOX - 13ACD03623001 | 111 | 12.2 | Yes | Yes | 31.9 | 27.6 | 4.3 | B9BBB20275C9460196D90ADBBEF9C38B |  | R22 | Non-TXV |  | 10.99% | 0.89009 | 21.12% | [5 empty] | Non-TXV | 10.99%
Clovis | CA | 93612-4236 |  | 2012-06-07 | 2012-06-07 13:43 | 2012-06-07 14:19 | WESTINGHOUSE - N/A | 64 | 3.9 | Yes | Yes | 22.7 | 19.9 | 2.9 | 2AD874F94C4C49008D0A7381984C03C0 |  | R22 | Non-TXV |  | 6.094% | 0.93906 | 11.71% | [5 empty] | Non-TXV | 6.094%
Chico | CA | 95926-4559 |  | 2012-06-07 | 2012-06-07 19:13 | 2012-06-07 19:13 | PAYNE - 585HJW042060ABAF | 80 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | 18D9F48EB2414150A2424DF3C7DF2F13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1848 |  | 2012-06-08 | 2012-06-08 11:23 | 2012-06-08 13:23 | ICP - PGF036K060B | 71 | 2.4 | Yes | Yes | 19.2 | 18.7 | 0.5 | 348671978BD544E78B0CA99AF57D686C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.38% | 0.9662 | 6.496% | [5 empty] | Non-TXV | 3.38%
Chico | CA | 95926-2366 |  | 2012-06-07 | 2012-06-07 14:56 | 2012-06-07 15:17 | BRYANT - 561CJ024-D | 56 | 4.2 | Yes | Yes | 23.2 | 20.4 | 2.8 | 92897AF9C09E471480340FCF0AE6250D |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Dos Palos | CA | 93620-2217 |  | 2012-06-08 | 2012-06-08 09:29 | 2012-06-08 09:55 | GOODMAN - GSC130481AG | 147 | 5 | Yes | Yes | 19.2 | 19.9 | -0.7 | 85C20E93B519436DBBAC033AF25BAB88 |  | R22 | Non-TXV |  | 3.401% | 0.96599 | 6.537% | [5 empty] | Non-TXV | 3.401%
Clovis | CA | 93612-2608 |  | 2012-08-13 | 2012-08-13 16:10 | 2012-08-13 16:42 | CARRIER - 38TR030300 | 88 | 3.1 | Yes | Yes | 16.8 | 19.6 | -2.8 | 9D8EF8B72451499BBEDA80DED2BB6023 |  | R22 | Non-TXV |  | 3.523% | 0.96477 | 6.77% | [5 empty] | Non-TXV | 3.523%
Merced | CA | 95348-1336 |  | 2012-05-31 | 2012-05-31 11:33 | 2012-05-31 12:00 | LENNOX - 10ACB30-7P | 69 | 16.8 | Yes | Yes | 21.7 | 19.2 | 2.5 | 14499121B46249B4BEC4A9A583B1AA02 |  | R22 | Non-TXV |  | 24.35% | 0.75652 | 46.79% | [5 empty] | Non-TXV | 24.35%
Merced | CA | 95340-3311 |  | 2012-06-01 | 2012-06-01 15:35 | 2012-06-01 15:35 | DAY & NIGHT - 585A030080YAC | 50 | 0 | Yes | Yes | 21.5 | 19.6 | 1.9 | 69B24FD564C84CE49B0D0AEF43566B7F | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4236 |  | 2012-07-03 | 2012-07-03 12:43 | 2012-07-03 13:06 | HEIL - NRGF24DDB03 | 53 | 6.7 | Yes | Yes | 24.4 | 21 | 3.5 | 825BAFD3BB8547499A903CD8EF18A5CE |  | R22 | Non-TXV |  | 12.64% | 0.87358 | 24.29% | [5 empty] | Non-TXV | 12.64%
Oakdale | CA | 95361-9502 |  | 2012-06-07 | 2012-06-07 15:47 | 2012-06-07 16:11 | TAPPAN - CM 36 41 | 54 | 2 | Yes | Yes | 20.5 | 21.5 | -1 | 8AA795CD4009488699E2897EA5388FD6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Merced | CA | 95340-1728 |  | 2012-06-11 | 2012-06-11 10:16 | 2012-06-11 10:42 | ICP - HAC030AKA5 | 74 | 16.9 | Yes | Yes | 25.9 | 22.6 | 3.3 | C18125877A524FBF8014435988F0117F |  | R22 | Non-TXV |  | 22.84% | 0.77162 | 43.89% | [5 empty] | Non-TXV | 22.84%
Stockton | CA | 95205-6527 |  | 2012-07-09 | 2012-07-09 12:53 | 2012-07-09 13:10 | GOODMAN - CLJ18-1 | 85 | 4.1 | Yes | Yes | 15 | 17.7 | -2.7 | 719C3655AB0B48E0AFAE93F9C3974453 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Oroville | CA | 95965-4047 |  | 2012-06-01 | 2012-06-01 09:52 | 2012-06-01 10:05 | AMERICAN STANDARD - 7A2048A100A2 | 132 | 5.9 | Yes | Yes | 22 | 21.3 | 0.8 | 92F7A58FD2054C48B751A9D45B8123F0 |  | R22 | Non-TXV |  | 4.47% | 0.9553 | 8.59% | [5 empty] | Non-TXV | 4.47%
Stockton | CA | 95210-2617 |  | 2012-06-07 | 2012-06-07 12:55 | 2012-06-07 12:55 | GOODMAN - GPG13240451BB | 77 | 0 | Yes | Yes | 25.7 | 21.3 | 4.5 | 1B953AD36C8043098B19F3C0BC905A31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1623 |  | 2012-06-01 | 2012-06-01 09:27 | 2012-06-01 09:27 | TRANE - BWB942A100A3 | 153 | 0 | Yes | Yes | 17.3 | 18.8 | -1.5 | 0F2E2DC554C64FEDA805198D128BE187 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-2973 |  | 2012-06-08 | 2012-06-08 14:27 | 2012-06-08 14:46 | GOODMAN - PG030075-1B | 54 | 2.1 | Yes | Yes | 20.4 | 20.9 | -0.5 | 4AECD2B599B342FD936F0C3089D24B23 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Newman | CA | 95360-1060 |  | 2012-07-06 | 2012-07-06 09:30 | 2012-07-06 09:48 | WEATHER KING - 12AJA2401 | 99 | 2.6 | Yes | Yes | 18 | 20.2 | -2.2 | 8A568CFD037140DC8716129BCD0AD643 |  | R22 | Non-TXV |  | 2.626% | 0.97374 | 5.047% | [5 empty] | Non-TXV | 2.626%
Merced | CA | 95340-1743 |  | 2012-06-01 | 2012-06-01 10:14 | 2012-06-01 10:34 | RHEEM - RRKA-A036JK08X | 62 | -3.6 | Yes | Yes | 24.8 | 19.4 | 5.5 | F97B3B4238E44CF1B3B47E459FE5C3F6 |  | R22 | Non-TXV |  | -5.806% | 1.0581 | 1.626% |  |  |  |  | Non-TXV |  |  | -5.806%
Newman | CA | 95360-1058 |  | 2012-07-06 | 2012-07-06 09:52 | 2012-07-06 10:09 | WEATHER KING - 12AJA2401 | 99 | 2.5 | Yes | Yes | 18 | 19.9 | -1.9 | 876D3B84965E469DB3E284A2DE9DF1A6 |  | R22 | Non-TXV |  | 2.525% | 0.97475 | 4.853% | [5 empty] | Non-TXV | 2.525%
Stockton | CA | 95210-2617 |  | 2012-06-12 | 2012-06-12 10:37 | 2012-06-12 10:54 | GOODMAN - GPG13240451BB | 77 | 3 | Yes | Yes | 26.4 | 21.3 | 5.2 | AB639FE6B3CE496A857CDF3F0BE4C2E6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.896% | 0.96104 | 7.487% | [5 empty] | Non-TXV | 3.896%
Fresno | CA | 93725-1663 |  | 2012-06-08 | 2012-06-08 09:58 | 2012-06-08 10:23 | OTHER - 24ABA342A300 | 98 | 3 | Yes | Yes | 21.7 | 20.3 | 1.4 | E477F1D47ADA4C8A8865308C276D3259 |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Merced | CA | 95341-6953 |  | 2012-06-08 | 2012-06-08 12:29 | 2012-06-08 12:54 | RHEEM - UNK | 80 | 5.7 | Yes | Yes | 24.3 | 19.8 | 4.5 | C8CE390C307C4CF0AA169CB2D1FC06E2 |  | R22 | Non-TXV |  | 7.125% | 0.92875 | 13.69% | [5 empty] | Non-TXV | 7.125%
Fresno | CA | 93710-4819 |  | 2012-08-02 | 2012-08-02 13:22 | 2012-08-02 14:01 | BRYANT - 113RNA036B | 80 | 4.2 | Yes | Yes | 18 | 20.7 | -2.7 | 8FC367A6E487487FBC66D4FC3BCB63EE |  | R22 | Non-TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | Non-TXV | 5.25%
Chico | CA | 95926-2221 |  | 2012-06-07 | 2012-06-07 14:12 | 2012-06-07 14:45 | LENNOX - 10ACB36-12P | 85 | 2.5 | Yes | Yes | 18.2 | 21 | -2.8 | BCEB6A4DA009405F90FBB43E9C40283C |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93710-6520 |  | 2012-06-15 | 2012-06-15 10:22 | 2012-06-15 10:39 | CARRIER - 38GS018310 | 48 | 1.5 | Yes | Yes | 23.5 | 21 | 2.5 | 230E65B230BA4E9CA03C1DB72B427573 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Merced | CA | 95348-4040 |  | 2012-06-13 | 2012-06-13 11:11 | 2012-06-13 11:32 | GOODMAN - GPG13360701AB | 112 | 3.4 | Yes | Yes | 27.2 | 21.2 | 6 | A39F2D9C3133490FABEB9308CAA8115B |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Fresno | CA | 93720-1996 |  | 2012-06-13 | 2012-06-13 11:10 | 2012-06-13 11:29 | CARRIER - N/A | 80 | 2.4 | Yes | Yes | 23.1 | 20.4 | 2.7 | 33F793A59745421AA19D51CA10E91063 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95341-7025 |  | 2012-06-11 | 2012-06-11 15:13 | 2012-06-11 15:27 | YORK - H2RD030S06D | 93 | 12 | Yes | Yes | 19.4 | 21.2 | -1.8 | 43072E70CEFB41EC9BC8E6DC98C19155 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.9% | 0.87097 | 24.8% | [5 empty] | Non-TXV | 12.9%
Planada | CA | 95365-0000 |  | 2012-07-02 | 2012-07-02 12:07 | 2012-07-02 12:39 | WESTINGHOUSE - FS3BA-024KA | 64 | 4.2 | Yes | Yes | 21.4 | 16.8 | 4.6 | 2AE6756F11CC43BBBEBF73C9A43844B9 |  | R22 | Non-TXV |  | 6.562% | 0.93437 | 12.61% | [5 empty] | Non-TXV | 6.562%
Fresno | CA | 93722-3290 |  | 2012-08-15 | 2012-08-15 20:19 | 2012-08-15 20:46 | RUUD - UNK | 86 | 3.2 | Yes | Yes | 19 | 20.7 | -1.7 | 77BC9630C8704048A7AF261530CF10A8 |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Merced | CA | 95340-5002 |  | 2012-06-01 | 2012-06-01 10:34 | 2012-06-01 10:54 | RHEEM - RRNAB036JK08X | 83 | 15.1 | Yes | Yes | 19.4 | 19.9 | -0.5 | FCCA70535D9E4F82896A22B10EC09470 |  | R22 | Non-TXV |  | 18.19% | 0.81807 | 34.96% | [5 empty] | Non-TXV | 18.19%
Clovis | CA | 93611-3007 |  | 2012-06-11 | 2012-06-11 11:41 | 2012-06-11 11:41 | DAY & NIGHT - N/A | 80 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | BDE000FC85E54049BF91D3E4B6E818D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3132 |  | 2012-08-09 | 2012-08-09 12:14 | 2012-08-09 12:55 | RHEEM - N/A | 90 | 19.1 | Yes | Yes | 18.8 | 17.4 | 1.4 | 95BBAC27E77A4A3D888160F53FEFC55B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.22% | 0.78778 | 40.78% | [5 empty] | Non-TXV | 21.22%
Magalia | CA | 95954-9311 |  | 2012-05-31 | 2012-05-31 13:31 | 2012-05-31 13:55 | COLEMAN - 2048-901 | 73 | 2.4 | Yes | Yes | 17.9 | 20.9 | -3 | 88233A839F044E739DB5BBCCE9DD7E59 |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Oakdale | CA | 95361-3145 |  | 2012-06-28 | 2012-06-28 10:13 | 2012-06-28 10:34 | TRANE - TTP036D100A0 | 133 | 4 | Yes | Yes | 19.4 | 19.9 | -0.5 | 5C84CB45761245508232FB312D433307 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Chico | CA | 95926-2216 |  | 2012-06-07 | 2012-06-07 12:42 | 2012-06-07 13:40 | BRYANT - 113ANA024-C | 55 | 7.9 | Yes | Yes | 23.5 | 22.1 | 1.4 | E96B59B70BC448C1A03D8B0DBC2EF898 |  | R410A | TXV |  | 14.36% | 0.85636 | 27.6% | [5 empty] | TXV | 14.36%
Fresno | CA | 93706-1301 |  | 2012-07-09 | 2012-07-09 12:17 | 2012-07-09 12:38 | RHEEM - HC-80-30-21C | 48 | 2.3 | Yes | Yes | 17.2 | 19.4 | -2.2 | 628D97373BDD48C084D019B767FB223E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Stockton | CA | 95210-2620 |  | 2012-06-11 | 2012-06-11 10:36 | 2012-06-11 10:53 | DAY & NIGHT - 24/60YAC108C | 53 | 1.7 | Yes | Yes | 20.6 | 21.5 | -0.9 | C117773C1E574716A4B845BF14A957E1 |  | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Merced | CA | 95340-2311 |  | 2012-06-01 | 2012-06-01 11:02 | 2012-06-01 11:38 | YORK - H2RA030S06D | 62 | 7.4 | Yes | Yes | 24.2 | 19.9 | 4.3 | DC475A5B4A084DCBB453E54A09A5BE46 |  | R22 | Non-TXV |  | 11.94% | 0.88065 | 22.94% | [5 empty] | Non-TXV | 11.94%
Stockton | CA | 95215-4845 |  | 2012-06-21 | 2012-06-21 12:23 | 2012-06-21 12:55 | RHEEM - RRKA-A036JK06X | 62 | 4 | Yes | Yes | 19.8 | 20.4 | -0.6 | 80EFC7F2A7CC44EE93D65CB41AE9B9B2 |  | R22 | Non-TXV |  | 6.452% | 0.93548 | 12.4% | [5 empty] | Non-TXV | 6.452%
Riverbank | CA | 95367-0000 |  | 2012-06-28 | 2012-06-28 12:21 | 2012-06-28 12:50 | DAY & NIGHT - UNK | 54 | 2.9 | Yes | Yes | 17.3 | 19.5 | -2.2 | 4ADED21B6D9344A5B4905F1CB5BA1EFD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Chico | CA | 95926-2737 |  | 2012-07-20 | 2012-07-20 10:29 | 2012-07-20 10:46 | BRYANT - AA1CJ018-C | 69 | 2.5 | Yes | Yes | 17.1 | 19.9 | -2.8 | 62F5B6FB86C24FFA8E1D139B50260614 |  | R22 | TXV |  | 3.623% | 0.96377 | 6.963% | [5 empty] | TXV | 3.623%
Sanger | CA | 93657-2341 |  | 2012-08-09 | 2012-08-09 14:47 | 2012-08-09 15:09 | BRYANT - 563CN036-D | 101 | 18.7 | Yes | Yes | 22.2 | 19.1 | 3.2 | C08795E0A7B645A28AE6230793661644 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.51% | 0.81485 | 35.58% | [5 empty] | Non-TXV | 18.51%
Newman | CA | 95360-1426 |  | 2012-07-06 | 2012-07-06 12:15 | 2012-07-06 12:34 | RUUD - UAHE-030JAS | 78 | 2.3 | Yes | Yes | 21.9 | 20.7 | 1.2 | A9C85C9C56C040C7B4FC4FBA584B8889 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Chico | CA | 95926-2768 |  | 2012-07-23 | 2012-07-23 12:25 | 2012-07-23 12:56 | OTHER - FS3BC-024KA | 65 | 4.1 | Yes | Yes | 22 | 21 | 1 | 49954FCEBB4345D4AC82A622313FA0E4 |  | R22 | Non-TXV |  | 6.308% | 0.93692 | 12.12% | [5 empty] | Non-TXV | 6.308%
Stockton | CA | 95210-2620 |  | 2012-06-11 | 2012-06-11 11:02 | 2012-06-11 11:18 | DAY & NIGHT - 24/60YAC108C | 53 | 2.4 | Yes | Yes | 21.1 | 22.1 | -1 | F8DD5F4F3F6E4D768361B303D9C5CE02 |  | R22 | Non-TXV |  | 4.528% | 0.95472 | 8.702% | [5 empty] | Non-TXV | 4.528%
Merced | CA | 95348-9238 |  | 2012-06-13 | 2012-06-13 12:28 | 2012-06-13 12:49 | YORK - D1NH060N09006 | 140 | 4.1 | Yes | Yes | 24.6 | 19.6 | 5 | C76336C37C12453EB851134A0D38E763 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.628% | [5 empty] | Non-TXV | 2.929%
Fresno | CA | 93710-6535 |  | 2012-06-01 | 2012-06-01 13:21 | 2012-06-01 13:46 | OTHER - UNK | 85 | 2.8 | Yes | Yes | 19.6 | 21.5 | -1.9 | 0D8CC264D30F4DF199F17A5B0F1619F7 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Riverbank | CA | 95367-2668 |  | 2012-06-08 | 2012-06-08 15:18 | 2012-06-08 15:36 | ICP - CA5030VKB1 | 79 | 3.1 | Yes | Yes | 19.8 | 21 | -1.2 | E47FD4D8648940B98E70434321AE48D0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.924% | 0.96076 | 7.541% | [5 empty] | Non-TXV | 3.924%
Fresno | CA | 93710-6534 |  | 2012-06-01 | 2012-06-01 13:56 | 2012-06-01 14:23 | AMERICAN STANDARD - YCC030FL0BJ | 71 | 2.7 | Yes | Yes | 17.3 | 19.9 | -2.6 | B51C704EFD4844A7B3446290864C3D99 |  | R22 | Non-TXV |  | 3.803% | 0.96197 | 7.308% | [5 empty] | Non-TXV | 3.803%
Stockton | CA | 95210-2349 |  | 2012-06-19 | 2012-06-19 10:11 | 2012-06-19 10:30 | GOODMAN - PGB024050-1 | 54 | 2 | Yes | Yes | 22.4 | 19.9 | 2.5 | 5316EAD0E9C8408AA2262BBE80F1CFA3 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Newman | CA | 95360-1060 |  | 2012-07-06 | 2012-07-06 09:42 | 2012-07-06 09:59 | GOODMAN - NA | 51 | 2.5 | Yes | Yes | 21.2 | 23.4 | -2.2 | 58E54887DAD841FA9E4E66AABD6CA522 |  | R22 | Non-TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | Non-TXV | 4.902%
Livingston | CA | 95334-9791 |  | 2012-07-03 | 2012-07-03 09:20 | 2012-07-03 09:41 | RHEEM - RRGF-05E24-JKR | 42 | 1.3 | Yes | Yes | 27.9 | 21.9 | 6 | 6EAEC68EBED24210B5EDB4F856A7085E |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Stockton | CA | 95210-2349 |  | 2012-06-08 | 2012-06-08 10:16 | 2012-06-08 10:33 | GOODMAN - PGB024050-1 | 54 | -3.2 | Yes | Yes | 22 | 19.3 | 2.7 | DE8F0D00557F452A9532A103FEEE8993 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Fresno | CA | 93710-4607 |  | 2012-06-15 | 2012-06-15 09:55 | 2012-06-15 10:20 | RUUD - N/A | 80 | 2.4 | Yes | Yes | 22 | 21 | 1 | 05389AAC0548433DA28EFB6CEE6C60DB |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Sanger | CA | 93657-8783 |  | 2012-08-15 | 2012-08-15 11:37 | 2012-08-15 12:11 | UNITARY PRODUCTS GROUP - H2RD048S06B | 134 | 4 | Yes | Yes | 20.8 | 19.4 | 1.5 | 7AB40CF7C12A458DA719BD342AB4FAEC |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Sanger | CA | 93657-2954 |  | 2012-08-15 | 2012-08-15 10:13 | 2012-08-15 10:46 | BDP - 585HJW036060 | 102 | 3.1 | Yes | Yes | 24.2 | 18.5 | 5.7 | ADA96DED175E4152B67153A53952CE46 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Selma | CA | 93662-3701 |  | 2012-08-14 | 2012-08-14 12:24 | 2012-08-14 13:03 | GOODMAN - PGJ030050-1A | 72 | 3.2 | Yes | Yes | 13.1 | 15.5 | -2.4 | 332691B8682747B99EE1E5D19CE32A14 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Sanger | CA | 93657-8748 |  | 2012-08-15 | 2012-08-15 10:49 | 2012-08-15 11:12 | LENNOX - 10ACC-048-230-04 | 96 | 9.7 | Yes | Yes | 20 | 20.7 | -0.7 | C99BF99931094662BB8294D7BE8EEA19 |  | R22 | Non-TXV |  | 10.1% | 0.89896 | 19.42% | [5 empty] | Non-TXV | 10.1%
Sanger | CA | 93657-8634 |  | 2012-08-15 | 2012-08-15 09:40 | 2012-08-15 09:55 | GOODMAN - CKL36-1L | 84 | 2.7 | Yes | Yes | 24.5 | 20.2 | 4.3 | D6E96D7A01554EC6ABBDB85708F58F25 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Stockton | CA | 95215-9725 |  | 2012-06-13 | 2012-06-13 12:08 | 2012-06-13 12:28 | PAYNE - UNK | 54 | 6 | Yes | Yes | 18.5 | 19.5 | -1 | 4F21E321F44A4EC188848F94DDF1A042 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Fresno | CA | 93725-1204 |  | 2012-07-05 | 2012-07-05 15:22 | 2012-07-05 19:21 | GOODMAN - GPG1330045M41AC | 80 | 2.5 | Yes | Yes | 23.2 | 20.7 | 2.5 | 6297716E220F4533A4A596BD260FA5F7 |  | R410A | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Atwater | CA | 95301-3536 |  | 2012-06-01 | 2012-06-01 13:25 | 2012-06-01 13:43 | AMERICAN STANDARD - YCC036F1MOBE | 83 | 2.4 | Yes | Yes | 21 | 21.3 | -0.3 | F6B66D625CF349E48F58DB519494E529 |  | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Stockton | CA | 95204-3451 |  | 2012-06-06 | 2012-06-06 14:54 | 2012-06-06 14:54 | ARCOAIRE - AG036GA1 | 74 | 0 | Yes | Yes | 20.2 | 19.8 | 0.4 | 3DBBAA908F6C4335B60E6AA4EAE18F50 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7037 |  | 2012-06-13 | 2012-06-13 10:59 | 2012-06-13 11:26 | LENNOX - 13ACD03623001 | 111 | 14.6 | Yes | Yes | 31.1 | 28.3 | 2.8 | 2CCD665AE08A4D24B100AB46BEFD498E |  | R22 | Non-TXV |  | 13.15% | 0.86847 | 25.28% | [5 empty] | Non-TXV | 13.15%
Parlier | CA | 93648-2472 |  | 2012-07-13 | 2012-07-13 12:20 | 2012-07-13 12:40 | CARRIER - 485X-036060321 | 84 | 2.6 | Yes | Yes | 18.7 | 19.6 | -0.9 | 70C4E2D88B384E9BA5F9A3554F970EA4 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Riverbank | CA | 95367-9631 |  | 2012-06-08 | 2012-06-08 12:56 | 2012-06-08 13:44 | RHEEM - 13PJ24A01 | 91 | 5.5 | Yes | Yes | 20.8 | 19.9 | 0.9 | 628E6E2FE147462D8AD21556577DC41C |  | R410A | TXV |  | 6.044% | 0.93956 | 11.62% | [5 empty] | TXV | 6.044%
Atwater | CA | 95301-3512 |  | 2012-06-11 | 2012-06-11 11:06 | 2012-06-11 11:28 | AMERICAN STANDARD - YCC036F1MOBK | 85 | 5.7 | Yes | Yes | 25.8 | 22.6 | 3.2 | 5A5495DD5EE9453A9CD533FB18BC48E9 |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Merced | CA | 95341-7030 |  | 2012-06-08 | 2012-06-08 15:10 | 2012-06-08 15:27 | BRYANT - 582ANW030040NAAD | 55 | 5.7 | Yes | Yes | 27.5 | 22.1 | 5.4 | 83AD6DC5FE3342C1AE8E56B484BD533A |  | R22 | Non-TXV |  | 10.36% | 0.89636 | 19.92% | [5 empty] | Non-TXV | 10.36%
Fresno | CA | 93725-4009 |  | 2012-07-05 | 2012-07-05 13:19 | 2012-07-05 13:36 | CARRIER - N/A | 180 | 17 | Yes | Yes | 24.6 | 20.2 | 4.4 | 46B79EF63CE140AEBF6AD0AA209A618C |  | R410A | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Live Oak | CA | 95953-9650 |  | 2012-07-05 | 2012-07-05 09:22 | 2012-07-05 09:40 | CARRIER - 38CKC036350 | 70 | 2.9 | Yes | Yes | 19 | 19.3 | -0.3 | 39ACFA9671074BFB9775F7AE534C4661 |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Clovis | CA | 93612-4238 |  | 2012-06-08 | 2012-06-08 12:44 | 2012-06-08 13:01 | HEIL - UNK | 74 | 6.9 | Yes | Yes | 18.9 | 20.4 | -1.5 | 04AB74B1C5E745EB816C64EF330AECB0 |  | R22 | Non-TXV |  | 9.324% | 0.90676 | 17.92% | [5 empty] | Non-TXV | 9.324%
Merced | CA | 95348-1601 |  | 2012-06-06 | 2012-06-06 12:23 | 2012-06-06 12:44 | WHIRLPOOL - UNK | 65 | 7.3 | Yes | Yes | 20.6 | 20.9 | -0.3 | 97CFF0060265422EA3B3B6BDF086068A |  | R22 | Non-TXV |  | 11.23% | 0.88769 | 21.58% | [5 empty] | Non-TXV | 11.23%
Colusa | CA | 95932-2572 |  | 2012-07-16 | 2012-07-16 08:35 | 2012-07-16 09:05 | OTHER - UNK | 55 | 3 | Yes | Yes | 21 | 19.3 | 1.7 | B8A9495FCF5642C2AC69FB1AA6B09921 |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Yuba City | CA | 95993-9206 |  | 2012-06-06 | 2012-06-06 10:41 | 2012-06-06 10:58 | BDP - 585HJ030040 | 68 | 13 | Yes | Yes | 25.9 | 20.1 | 5.8 | 22962E1E4C464CA38006C135EA9DBD88 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 19.12% | 0.80882 | 36.74% | [5 empty] | Non-TXV | 19.12%
Stockton | CA | 95210-4624 |  | 2012-06-01 | 2012-06-01 14:12 | 2012-06-01 14:24 | RUUD - UNK | 50 | 2 | Yes | Yes | 20.7 | 20.7 | 0 | 2E8DE138323D4D9C970D26D969047416 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95207-2047 |  | 2012-06-07 | 2012-06-07 09:36 | 2012-06-07 09:58 | WESTINGHOUSE - IE024PCAON | 84 | 13.2 | Yes | Yes | 18.5 | 19.9 | -1.4 | B3DAB95A8405485E81B8FB1F34CCD1F4 |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Newman | CA | 95360-1415 |  | 2012-06-14 | 2012-06-14 08:47 | 2012-06-14 09:05 | YORK - D3NZ036N05606NXB | 64 | 1.9 | Yes | Yes | 19.7 | 18.5 | 1.2 | 4E533089815F4A4CACA029CDF54C9AE6 |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Colusa | CA | 95932-2438 |  | 2012-07-18 | 2012-07-18 08:59 | 2012-07-18 09:37 | CARRIER - 24ACA442A300 | 164 | 5.8 | Yes | Yes | 25 | 19.5 | 5.5 | 37E016380DB34EBCA82F52BBD9DD957E |  | R410A | TXV |  | 3.537% | 0.96463 | 6.797% | [5 empty] | TXV | 3.537%
Stockton | CA | 95207-5433 |  | 2012-06-22 | 2012-06-22 11:53 | 2012-06-22 12:13 | DAY & NIGHT - 24-60YAC-108C | 52 | 6.3 | Yes | Yes | 23.7 | 19.9 | 3.8 | 5B75082F8F1F4003ADF8D56C21D97056 |  | R22 | Non-TXV |  | 12.12% | 0.87885 | 23.28% | [5 empty] | Non-TXV | 12.12%
Selma | CA | 93662-4226 |  | 2012-06-11 | 2012-06-11 13:02 | 2012-06-11 13:19 | RUUD - N/A | 90 | 4.4 | Yes | Yes | 20 | 20.4 | -0.4 | 0F1DE63C2B6C4139987FF2426BE80E6F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.889% | 0.95111 | 9.395% | [5 empty] | Non-TXV | 4.889%
Yuba City | CA | 95991-1708 |  | 2012-06-13 | 2012-06-13 10:19 | 2012-06-13 10:48 | RHEEM - UNK | 80 | 11.2 | Yes | Yes | 18 | 20.7 | -2.7 | DCDA89584133455188FA0B0CBCD73715 |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Chico | CA | 95928-5704 |  | 2012-06-11 | 2012-06-11 18:58 | 2012-06-11 19:47 | OTHER - JS3BC-024KA | 100 | 3 | Yes | Yes | 22.7 | 22.3 | 0.4 | 32E3E548A81A4BB5918378E1FD0FB0D8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95207-7728 |  | 2012-06-21 | 2012-06-21 13:51 | 2012-06-21 14:13 | RUUD - UAKA-018JAZ | 85 | 12.2 | Yes | Yes | 20.6 | 23.2 | -2.6 | 5F00194B9C834783BA7AC41131440449 |  | R22 | Non-TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | Non-TXV | 14.35%
Colusa | CA | 95932-3206 |  | 2012-07-18 | 2012-07-18 09:53 | 2012-07-18 10:27 | LENNOX - HS26-30-2P | 78 | -7.3 | Yes | Yes | 16 | 19.3 | -3.3 | D99E50C1E3A34CC788388463CFE9E30B | Remove refrigerant: 7.3 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.359% | 1.0936 | 2.621% |  |  |  |  | Non-TXV |  |  | -9.359%
Atwater | CA | 95301-2433 |  | 2012-06-01 | 2012-06-01 10:50 | 2012-06-01 11:06 | GOODMAN - CPKE24-1B | 96 | 2.9 | Yes | Yes | 20.1 | 19.5 | 0.6 | CFC69757884A4CDB84602B75027CB7B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Gustine | CA | 95322-1633 |  | 2012-06-14 | 2012-06-14 12:09 | 2012-06-14 12:25 | UNITARY PRODUCTS GROUP - H2RA036S06D | 85 | 2.5 | Yes | Yes | 18.7 | 19.7 | -1 | 0AD4C2B548E04E3DAAEF1D70FF4793D0 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Olivehurst | CA | 95961-7449 |  | 2012-07-11 | 2012-07-11 14:40 | 2012-07-11 14:59 | PAYNE - 567C030RCU | 75 | -7.1 | Yes | Yes | 21 | 19.5 | 1.5 | 49FF24785A8B4285850083D175A96DF1 |  | R22 | Non-TXV |  | -9.467% | 1.0947 | 2.651% |  |  |  |  | Non-TXV |  |  | -9.467%
Manteca | CA | 95336-4630 |  | 2012-06-01 | 2012-06-01 09:54 | 2012-06-01 09:54 | RHEEM - RRNL-B036JK06X | 93 | 0 | Yes | Yes | 19.1 | 20.7 | -1.6 | E76C8A926C1E4BCFA4F887B595F080EE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-2504 |  | 2012-06-11 | 2012-06-11 09:37 | 2012-06-11 09:58 | RHEEM - RACC-030JAS | 58 | 14.5 | Yes | Yes | 21.6 | 20.2 | 1.4 | FC56CC53A4244BD5944CE2BB7F5E8186 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 25% | 0.75 | 48.04% | [5 empty] | Non-TXV | 25%
Stockton | CA | 95207-6574 |  | 2012-06-25 | 2012-06-25 14:53 | 2012-06-25 15:36 | DAY & NIGHT - 567CJ024 | 60 | 8 | Yes | Yes | 18.6 | 20.6 | -2 | 525EE550B6074FDBB5694A90CBF70747 |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Ripon | CA | 95366-9660 |  | 2012-06-11 | 2012-06-11 13:36 | 2012-06-11 14:28 | DAY & NIGHT - UNK | 54 | 4.5 | Yes | Yes | 17.6 | 20.4 | -2.8 | 3D993B6A6DD342E2A23A1C17AA4AFD28 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Fresno | CA | 93727-2034 |  | 2012-08-07 | 2012-08-07 10:32 | 2012-08-07 10:59 | AMERICAN STANDARD - 2YCC3042A1075AA | 131 | 13.8 | Yes | Yes | 18.8 | 20.1 | -1.3 | F85207D0AB1543FCA83EF3C7F3FA150E |  | R22 | Non-TXV |  | 10.53% | 0.89466 | 20.24% | [5 empty] | Non-TXV | 10.53%
Yuba City | CA | 95991-5938 |  | 2012-06-15 | 2012-06-15 13:20 | 2012-06-15 13:50 | DAY & NIGHT - 5670C030RCC1 | 69 | 12.2 | Yes | Yes | 20.2 | 21 | -0.8 | 2D008875F5DC45A6B197F7922695541C |  | R22 | Non-TXV |  | 17.68% | 0.82319 | 33.98% | [5 empty] | Non-TXV | 17.68%
Fresno | CA | 93727-1942 |  | 2012-08-07 | 2012-08-07 15:23 | 2012-08-07 15:54 | UNITARY PRODUCTS GROUP - CZB03011A | 116 | 7.5 | Yes | Yes | 14.8 | 17.7 | -2.9 | B33F31BB5E8240DBBC464FA86C913312 |  | R410A | Non-TXV |  | 6.466% | 0.93534 | 12.43% | [5 empty] | Non-TXV | 6.466%
Paradise | CA | 95969-4183 |  | 2012-06-14 | 2012-06-14 12:46 | 2012-06-14 17:17 | PAYNE - PA10JA018-C | 60 | 6.4 | Yes | Yes | 25.6 | 21.9 | 3.7 | 21ADEB0DD67C48279BDE1D7DEB10F6CF |  | R22 | TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | TXV | 10.67%
Fresno | CA | 93710-6520 |  | 2012-06-06 | 2012-06-06 12:24 | 2012-06-06 12:41 | ICP - NACS24AKB7 | 60 | 1.8 | Yes | Yes | 25.3 | 21 | 4.3 | EBC0EA2D60074C45A546DC58010222EE |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93727-1836 |  | 2012-07-06 | 2012-07-06 10:59 | 2012-07-06 11:20 | BRYANT - 561CJ036-E | 70 | 17 | Yes | Yes | 19.1 | 22 | -2.9 | 331AD9A915CE445DB93B1D3F37E12346 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 24.29% | 0.75714 | 46.67% | [5 empty] | Non-TXV | 24.29%
Clovis | CA | 93612-2302 |  | 2012-08-13 | 2012-08-13 18:02 | 2012-08-13 18:02 | CARRIER - 36790YAC108C | 91 | 0 | Yes | Yes | 17.9 | 20.1 | -2.2 | 68D5600289734BB2BBF99503ECC4FD69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6520 |  | 2012-06-01 | 2012-06-01 15:16 | 2012-06-01 15:50 | CARRIER - UNK | 59 | 1.8 | Yes | Yes | 19 | 20.7 | -1.7 | D7F914C55EDA45B88CC9DB0011298EF0 |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Clovis | CA | 93612-2353 |  | 2012-06-11 | 2012-06-11 10:38 | 2012-06-11 11:03 | CARRIER - N/A | 78 | 16.4 | Yes | Yes | 22.2 | 21 | 1.2 | 87FDDC74BFC04DD183EBC22CCA9D7C63 |  | R22 | Non-TXV |  | 21.03% | 0.78974 | 40.41% | [5 empty] | Non-TXV | 21.03%
Clovis | CA | 93612-2353 |  | 2012-06-11 | 2012-06-11 12:19 | 2012-06-11 12:19 | AMERICAN STANDARD - 2YCX3036A1064AA | 82 | 0 | Yes | Yes | 21.8 | 21.3 | 0.5 | 4222604CDEE64E1E95E08CA39B9DDC6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6534 |  | 2012-06-01 | 2012-06-01 11:30 | 2012-06-01 11:30 | OTHER - UNK | 85 | 0 | Yes | Yes | 19.3 | 20.8 | -1.5 | 0015516586E94BFA9F731AA11B6FF173 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3800 |  | 2012-06-07 | 2012-06-07 12:53 | 2012-06-07 13:11 | OTHER - 7B0023B100A1 | 54 | 4.1 | Yes | Yes | 22.1 | 21.5 | 0.6 | B81D809F000044979DD61BC4D9EB016E |  | R22 | Non-TXV |  | 7.593% | 0.92407 | 14.59% | [5 empty] | Non-TXV | 7.593%
Fresno | CA | 93710-6554 |  | 2012-06-01 | 2012-06-01 10:46 | 2012-06-01 10:46 | OTHER - UNK | 55 | 0 | Yes | Yes | 19 | 19.8 | -0.8 | 172118CFD2344AB890F0269ABDEFA52B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Orland | CA | 95963-9575 |  | 2012-07-30 | 2012-07-30 19:10 | 2012-07-30 19:30 | LENNOX - 12GCS042X-100-6P3 | 130 | 5.2 | Yes | Yes | 20.9 | 20.2 | 0.7 | A926B25547D145689633390263CCFD8F |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Merced | CA | 95341-7038 |  | 2012-06-14 | 2012-06-14 12:21 | 2012-06-14 12:48 | LENNOX - 13ACD-042-230-02 | 111 | -6.1 | Yes | Yes | 23.7 | 21.2 | 2.5 | 816117DE34C74C1B9C13C6E3EB0631F0 |  | R22 | TXV |  | -5.495% | 1.055 | 1.539% |  |  |  |  | TXV |  |  | -5.495%
Fresno | CA | 93727-5007 |  | 2012-08-07 | 2012-08-07 09:28 | 2012-08-07 09:55 | ARCOAIRE - PGME42G0752 | 105 | 3.2 | Yes | Yes | 22 | 19.8 | 2.2 | B63324A07811443EB3B3CDC6C25A70A2 |  | R22 | Non-TXV |  | 3.048% | 0.96952 | 5.857% | [5 empty] | Non-TXV | 3.048%
Chico | CA | 95926-3064 |  | 2012-07-12 | 2012-07-12 11:41 | 2012-07-12 12:13 | DAY & NIGHT - 591ANX030000AAAA | 76 | 4 | Yes | Yes | 23.9 | 21.7 | 2.2 | 4049D760D91F4778B85B9F4E7A7804B0 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Ripon | CA | 95366-2863 |  | 2012-06-22 | 2012-06-22 15:38 | 2012-06-22 16:00 | BRYANT - 574DNWA24040NA-- | 72 | 2.8 | Yes | Yes | 21.7 | 18.7 | 3 | EBF34AA45E084117820AC1A31E6066EB |  | R410A | TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | TXV | 3.889%
Chico | CA | 95926-2747 |  | 2012-07-16 | 2012-07-16 09:01 | 2012-07-16 09:17 | TEMPSTAR - TCA024KA1 | 69 | 5.5 | Yes | Yes | 22.4 | 20.4 | 2 | 565A3312B91742D58E343C26F5FFDAB5 |  | R22 | Non-TXV |  | 7.971% | 0.92029 | 15.32% | [5 empty] | Non-TXV | 7.971%
Fresno | CA | 93710-4008 |  | 2012-08-02 | 2012-08-02 10:52 | 2012-08-02 11:38 | GOODMAN - PGB048075-REVA | 80 | 2.4 | Yes | Yes | 17.3 | 20.1 | -2.8 | 9E8B1C82B370405F8E6F7BF84480BC50 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95926-2363 |  | 2012-07-02 | 2012-07-02 09:08 | 2012-07-02 09:41 | GOODMAN - G8C130241AE | 93 | 6.8 | Yes | Yes | 25.4 | 21.9 | 3.6 | 552E47960B664751B84B79DA8AF3F12F |  | R22 | Non-TXV |  | 7.312% | 0.92688 | 14.05% | [5 empty] | Non-TXV | 7.312%
Fresno | CA | 93710-4010 |  | 2012-08-02 | 2012-08-02 16:00 | 2012-08-02 16:18 | DAY & NIGHT - UNK | 82 | 3.1 | Yes | Yes | 18.5 | 20.2 | -1.7 | 2A9A9D622E0E4260BBC9E92283B5FE3E |  | R22 | Non-TXV |  | 3.78% | 0.9622 | 7.265% | [5 empty] | Non-TXV | 3.78%
Atwater | CA | 95301-2547 |  | 2012-07-02 | 2012-07-02 08:52 | 2012-07-02 09:09 | GOODMAN - CPKE24-1A0 | 106 | 3.2 | Yes | Yes | 12.6 | 14.4 | -1.8 | 34AC97E179E24FFCAC71427D20002003 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Fresno | CA | 93722-5127 |  | 2012-06-01 | 2012-06-01 16:00 | 2012-06-01 16:22 | RHEEM - N/A | 90 | 2.8 | Yes | Yes | 18.6 | 21.6 | -3 | FE651395799D4FF7B58BE4F547EE602D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Tracy | CA | 95376-4818 |  | 2012-06-20 | 2012-06-20 13:10 | 2012-06-20 13:35 | YORK - DAYH-F036N070C | 108 | 3.2 | Yes | Yes | 18.5 | 19.7 | -1.2 | 75FB7FFA03384860824B6AAC4F36DAFD |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Merced | CA | 95340-1418 |  | 2012-06-07 | 2012-06-07 09:18 | 2012-06-07 09:45 | AMERICAN STANDARD - 2A7B0048A1000AA | 109 | -7.7 | Yes | Yes | 16.5 | 18.7 | -2.2 | 1D24139E94FF4655A747A416378FDD54 |  | R22 | Non-TXV |  | -7.064% | 1.0706 | 1.978% |  |  |  |  | Non-TXV |  |  | -7.064%
Chico | CA | 95928-7102 |  | 2012-07-03 | 2012-07-03 14:27 | 2012-07-03 14:50 | AMERICAN STANDARD - UNK | 69 | 4.3 | Yes | Yes | 22 | 20.7 | 1.4 | 0EFE3930762D45579E5002B416D19AA3 |  | R22 | Non-TXV |  | 6.232% | 0.93768 | 11.98% | [5 empty] | Non-TXV | 6.232%
Planada | CA | 95365-8016 |  | 2012-07-02 | 2012-07-02 11:18 | 2012-07-02 11:18 | WESTINGHOUSE - FS3BA-030KA | 68 | 0 | Yes | Yes | 19.9 | 17.4 | 2.5 | 2D6EFCFCDABE45028FE7614A6EE68FB8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3246 |  | 2012-06-08 | 2012-06-08 14:33 | 2012-06-08 14:49 | BDP - 561AJ048-B | 106 | 3.4 | Yes | Yes | 21.4 | 20.7 | 0.7 | 9DBC3D6AB40746FD89199E7E79572109 |  | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
San Andreas | CA | 95249-9522 |  | 2012-07-19 | 2012-07-19 08:10 | 2012-07-19 08:28 | LENNOX - HS29-018-3P | 60 | -3.5 | Yes | Yes | 19.9 | 18.2 | 1.7 | 05E2700B67C1406D8479F354F6398627 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Clovis | CA | 93612-4237 |  | 2012-06-07 | 2012-06-07 11:25 | 2012-06-07 11:46 | WESTINGHOUSE - N/A | 64 | 1.9 | Yes | Yes | 22.5 | 21 | 1.5 | F0B3901F64624DCF8A4BBF4A04FB83F7 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Clovis | CA | 93612-4232 |  | 2012-06-14 | 2012-06-14 13:46 | 2012-06-14 14:03 | TRANE - YCC024F1L0BH | 65 | 2 | Yes | Yes | 21.7 | 20.4 | 1.3 | 50E3FD98602848A5A62CC83096635B24 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Merced | CA | 95340-3384 |  | 2012-06-13 | 2012-06-13 08:57 | 2012-06-13 09:15 | OTHER - UNK | 78 | 10 | Yes | Yes | 22.1 | 19.9 | 2.2 | 7FA9227A1FAD479B9011F79732AFADB2 |  | R22 | Non-TXV |  | 12.82% | 0.87179 | 24.64% | [5 empty] | Non-TXV | 12.82%
Manteca | CA | 95337-6047 |  | 2012-06-01 | 2012-06-01 13:37 | 2012-06-01 14:01 | YORK - H2RA036S06E | 63 | 11.7 | Yes | Yes | 19.7 | 20.4 | -0.7 | 4900BB26CBEB4F17AB3BECADD3184FEE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Paso Robles | CA | 93446-7173 |  | 2012-07-09 | 2012-07-09 14:03 | 2012-07-09 14:27 | GOODMAN - CK30-1T | 76 | 2.6 | Yes | Yes | 19.1 | 21.3 | -2.2 | 9D93D132157F41059E9902B64C955F39 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Merced | CA | 95340-4918 |  | 2012-06-01 | 2012-06-01 11:19 | 2012-06-01 11:37 | RHEEM - RRKAA018JK04E | 44 | 8.7 | Yes | Yes | 18.8 | 19.8 | -1 | 417431414E5C448B9238B948523F2ACB |  | R22 | Non-TXV |  | 19.77% | 0.80227 | 38% | [5 empty] | Non-TXV | 19.77%
Colfax | CA | 95713-0000 |  | 2012-07-19 | 2012-07-19 11:14 | 2012-07-19 11:14 | OTHER - AFAIR10B48A | 100 | 0 | Yes | Yes | 21.3 | 19.1 | 2.2 | E745797DFC7442E4812206763178C12B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-9717 |  | 2012-06-08 | 2012-06-08 13:27 | 2012-06-08 13:46 | OTHER - B2SP036A06A | 112 | 3.4 | Yes | Yes | 22.2 | 21.5 | 0.7 | 68F07655C72E42BDA37DA99F7A6AA962 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Madera | CA | 93637-4919 |  | 2012-06-08 | 2012-06-08 13:11 | 2012-06-08 13:30 | HEIL - NRGF30DDB04 | 53 | 1.6 | Yes | Yes | 17 | 19.9 | -2.9 | 2819A34A376147758369A7896AED4D40 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Chico | CA | 95926-3052 |  | 2012-06-07 | 2012-06-07 16:18 | 2012-06-07 19:16 | DAY & NIGHT - 591ANX03000ABAA | 71 | 13 | Yes | Yes | 19.4 | 19.9 | -0.4 | E7765802807C47FDBB40435F19D9CEDD |  | R22 | Non-TXV |  | 18.31% | 0.8169 | 35.19% | [5 empty] | Non-TXV | 18.31%
Fresno | CA | 93725-1654 |  | 2012-08-10 | 2012-08-10 13:51 | 2012-08-10 14:13 | OTHER - 24ABA342A300 | 98 | 4.6 | Yes | Yes | 22.2 | 19.1 | 3.1 | 02EFCA9D44914E80A7F34118A5428D76 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 4.694% | 0.95306 | 9.021% | [5 empty] | Non-TXV | 4.694%
Auburn | CA | 95602-2352 |  | 2012-07-30 | 2012-07-30 11:16 | 2012-07-30 11:34 | RHEEM - RACA-018ABS | 30 | 20.3 | Yes | Yes | 22.5 | 20.9 | 1.6 | D93142F5390E4FF484E7A41A9B23783A |  | R22 | Non-TXV |  | 67.67% | 0.32333 | 130% | [5 empty] | Non-TXV | 67.67%
Oroville | CA | 95965-3477 |  | 2012-06-13 | 2012-06-13 09:52 | 2012-06-13 10:11 | AMERICAN STANDARD - YCC024F1LOBJ | 65 | 7.4 | Yes | Yes | 18.9 | 21.5 | -2.6 | 006292E6A8014982A11ABF544CDFF72B |  | R22 | Non-TXV |  | 11.38% | 0.88615 | 21.88% | [5 empty] | Non-TXV | 11.38%
Stockton | CA | 95205-4615 |  | 2012-07-12 | 2012-07-12 13:53 | 2012-07-12 14:11 | TRANE - SFHA-301-L6 | 68 | 4.6 | Yes | Yes | 17.2 | 19.9 | -2.7 | 910F3DF47B9D407AB6A53AC30C28EF21 |  | R22 | Non-TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | Non-TXV | 6.765%
Colfax | CA | 95713-9259 |  | 2012-07-19 | 2012-07-19 11:53 | 2012-07-19 12:11 | AMERICAN STANDARD - YCC048F1H0BG | 128 | 9.6 | Yes | Yes | 20.6 | 19.7 | 0.9 | 33FD21C05A1248B1A2A5968D91973D63 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Fresno | CA | 93722-2721 |  | 2012-08-14 | 2012-08-14 20:10 | 2012-08-14 20:10 | CARRIER - 38BRB060300 | 192 | 0 | Yes | Yes | 16.3 | 18.5 | -2.2 | DCAF8C1E05A2466681E5816F0E66E8E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1776 |  | 2012-07-02 | 2012-07-02 09:50 | 2012-07-02 10:11 | BRYANT - 582ANW036060NBAF | 68 | 2.5 | Yes | Yes | 24.4 | 18.5 | 5.9 | 82F06101787241B3B0D5DDD411A73389 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Selma | CA | 93662-2601 |  | 2012-06-07 | 2012-06-07 10:09 | 2012-06-07 10:29 | ICP - PGF036K060B | 71 | 6.2 | Yes | Yes | 26 | 20.4 | 5.6 | 9DB1D8781E814D33956572A0DF4B6548 |  | R22 | Non-TXV |  | 8.732% | 0.91268 | 16.78% | [5 empty] | Non-TXV | 8.732%
Red Bluff | CA | 96080-3142 |  | 2012-06-01 | 2012-06-01 17:10 | 2012-06-02 11:59 | COLEMAN - DAYP-F036N070A | 108 | 3.4 | Yes | Yes | 18.9 | 21.7 | -2.8 | 5C4504E898B6428290A136E5D35A6ACE |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Sanger | CA | 93657-2159 |  | 2012-08-09 | 2012-08-09 11:29 | 2012-08-09 11:45 | YORK - 02GA030N03206C | 80 | 2.5 | Yes | Yes | 17.6 | 20.4 | -2.8 | E66065809F1A44D1AC602E153516ECDA |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Merced | CA | 95340-3612 |  | 2012-06-01 | 2012-06-01 13:03 | 2012-06-01 13:03 | RHEEM - RRNL-B024JK06X | 77.8 | 0 | Yes | Yes | 19.7 | 18.5 | 1.2 | 780F220EF06F4CCA96D2653CA39DF760 |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2822 |  | 2012-06-07 | 2012-06-07 11:21 | 2012-06-07 11:48 | HEIL - PGC036K060B | 73 | 2.6 | Yes | Yes | 22.5 | 21.3 | 1.2 | 8CB61997B15D474B9332D6AD5942B21D |  | R22 | Non-TXV |  | 3.562% | 0.96438 | 6.845% | [5 empty] | Non-TXV | 3.562%
Clovis | CA | 93612-4237 |  | 2012-06-13 | 2012-06-13 11:36 | 2012-06-13 12:14 | OTHER - UNK | 56 | 1.8 | Yes | Yes | 18 | 20.7 | -2.7 | 2DC1008F0D0D4ECE8D5DB39B82C05971 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Sanger | CA | 93657-2257 |  | 2012-08-09 | 2012-08-09 09:49 | 2012-08-09 10:08 | BDP - 585AO36080YACR | 60 | 11.3 | Yes | Yes | 20.9 | 19.6 | 1.3 | C473FC56CA83412D83670052328A2245 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.83% | 0.81167 | 36.19% | [5 empty] | Non-TXV | 18.83%
Oakdale | CA | 95361-3116 |  | 2012-06-12 | 2012-06-12 09:12 | 2012-06-12 09:42 | DAY & NIGHT - 585HJ024040 | 68 | 3 | Yes | Yes | 19.9 | 19.3 | 0.6 | C156929DD139497298EC343632137DD4 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Mendota | CA | 93640-0000 |  | 2012-08-15 | 2012-08-15 10:32 | 2012-08-15 10:55 | BRYANT - 113RNA036B | 88 | 11.3 | Yes | Yes | 20.3 | 18.7 | 1.6 | E6A8719F75A44552A39591945716F2E3 |  | R22 | Non-TXV |  | 12.84% | 0.87159 | 24.68% | [5 empty] | Non-TXV | 12.84%
Auburn | CA | 95602-2238 |  | 2012-07-19 | 2012-07-19 13:46 | 2012-07-19 13:46 | YORK - YCJD18S41S1HA | 51 | 0 | Yes | Yes | 20.9 | 19 | 1.9 | 38D0BB191B5749258F5E430889B0211A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4235 |  | 2012-06-07 | 2012-06-07 12:57 | 2012-06-07 13:14 | TRANE - YCCA0240BH8 | 65 | 2.5 | Yes | Yes | 25.3 | 20.9 | 4.4 | 93874ED206E84F7BAD8AAAEEDD310235 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Rocklin | CA | 95677-3421 |  | 2012-06-07 | 2012-06-07 10:41 | 2012-06-07 10:41 | BDP - 588ANW024060AAAD | 44 | 0 | Yes | Yes | 16.5 | 19.1 | -2.6 | 4E327694339849D49AAE0CC406E14B5C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2042 |  | 2012-08-15 | 2012-08-15 09:08 | 2012-08-15 09:08 | PAYNE - 48NLT042-301BE | 120 | 0 | Yes | Yes | 22.7 | 19.9 | 2.8 | A24931A39B9240298B700BAF2C6FFEC4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3144 |  | 2012-06-28 | 2012-06-28 09:48 | 2012-06-28 10:12 | BDP - 567C024RCU | 92 | 3 | Yes | Yes | 18.6 | 19.9 | -1.3 | 4896579569414D08AFD76387D39EF9E2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Merced | CA | 95341-6021 |  | 2012-06-07 | 2012-06-07 14:49 | 2012-06-07 15:16 | TRANE - TTD736B100D0 | 80 | -7.5 | Yes | Yes | 26.2 | 21 | 5.2 | D95ED224A044474D83450F6F80B55FD6 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Sanger | CA | 93657-2033 |  | 2012-06-08 | 2012-06-08 16:43 | 2012-06-08 17:11 | BDP - 585EJW042075AAAF | 84 | 6.3 | Yes | Yes | 26.8 | 21.5 | 5.3 | 73AD6CF1D491450AA5452791BBEDE330 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Clovis | CA | 93612-4235 |  | 2012-06-11 | 2012-06-11 13:00 | 2012-06-11 13:00 | TRANE - YCC024F1L0BC | 64 | 0 | Yes | Yes | 22.6 | 20.5 | 2.1 | FAD3C6F089EB445E90515E0EE1CDC196 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2339 |  | 2012-08-09 | 2012-08-09 10:41 | 2012-08-09 11:08 | CARRIER - 38SE0003300 | 93 | 14.9 | Yes | Yes | 21.6 | 17.6 | 4 | 31D7364F825148C9BABFDB012007A7EF |  | R22 | Non-TXV |  | 16.02% | 0.83978 | 30.79% | [5 empty] | Non-TXV | 16.02%
Atascadero | CA | 93422-2153 |  | 2012-07-12 | 2012-07-12 08:15 | 2012-07-12 08:32 | NORDYNE - FS3BA-042KA | 87 | -5.1 | Yes | Yes | 21.8 | 19.1 | 2.7 | 483565A218B34340867792F77248D684 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Stockton | CA | 95212-3064 |  | 2012-06-15 | 2012-06-15 08:34 | 2012-06-15 09:03 | CARRIER - 38CKC036350 | 74 | 2.6 | Yes | Yes | 19.8 | 21 | -1.2 | 253B1A6E5E4D49CFA011A6BDE6C42787 |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Los Banos | CA | 93635-2902 |  | 2012-07-12 | 2012-07-12 11:10 | 2012-07-12 11:27 | TRANE - 2YCC3036A1064AA | 82 | 11.9 | Yes | Yes | 23.8 | 22.8 | 1 | 2B6711C722164B2ABB8C57AEEC26BCC9 |  | R22 | Non-TXV |  | 14.51% | 0.85488 | 27.89% | [5 empty] | Non-TXV | 14.51%
Fresno | CA | 93726-5402 |  | 2012-06-01 | 2012-06-01 10:12 | 2012-06-01 10:32 | WESTINGHOUSE - N/A | 60 | 1.8 | Yes | Yes | 22 | 20.7 | 1.3 | 99ACF548ED3A4123B8C67A9042556D60 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95341-7027 |  | 2012-07-05 | 2012-07-05 09:49 | 2012-07-05 10:18 | BRYANT - 582ANW042060NAAG | 100 | -3.9 | Yes | Yes | 24.5 | 20.9 | 3.6 | 8F1037F95A0245948BCF9E2DA3D301F5 |  | R22 | TXV |  | -3.9% | 1.039 | 1.092% |  |  |  |  | TXV |  |  | -3.9%
Clovis | CA | 93612-4618 |  | 2012-06-13 | 2012-06-13 16:09 | 2012-06-13 16:37 | PAYNE - UNK | 67 | 4.7 | Yes | Yes | 17.9 | 20.4 | -2.5 | B0B9E2C4CCEA42DAAED55BC158825FA7 |  | R22 | Non-TXV |  | 7.015% | 0.92985 | 13.48% | [5 empty] | Non-TXV | 7.015%
Los Banos | CA | 93635-2951 |  | 2012-07-06 | 2012-07-06 09:25 | 2012-07-06 10:01 | DAY & NIGHT - 591ANX030000ABAA | 67 | -3.9 | Yes | Yes | 22.4 | 19.4 | 3 | 432B43284E194C8B995E82572829CB27 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Merced | CA | 95341-5720 |  | 2012-06-07 | 2012-06-07 11:09 | 2012-06-07 11:31 | RHEEM - UNK | 65 | -3.8 | Yes | Yes | 21.5 | 20.7 | 0.8 | 4425F092AD1440D1B94523FF2490E1F1 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Fresno | CA | 93710-5921 |  | 2012-08-09 | 2012-08-09 09:55 | 2012-08-09 10:21 | PAYNE - UNK | 71 | 3.3 | Yes | Yes | 18.4 | 20.4 | -2 | 3BA28FED39524C5D9057C8F21B13CFE4 |  | R22 | Non-TXV |  | 4.648% | 0.95352 | 8.932% | [5 empty] | Non-TXV | 4.648%
Fresno | CA | 93710-6534 |  | 2012-06-01 | 2012-06-01 14:35 | 2012-06-01 15:07 | YORK - D2NPO24NO560 | 100 | 3 | Yes | Yes | 20.1 | 20.4 | -0.3 | C46FEF668FCE4981B46BE7CD7ECB5DEA |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93612-5051 |  | 2012-06-14 | 2012-06-14 14:20 | 2012-06-14 15:05 | CARRIER - 48KLA130300BE | 68 | 2 | Yes | Yes | 22.6 | 19.3 | 3.3 | AA4C2289BEE745B1A412453EC9994639 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95206-3260 |  | 2012-07-06 | 2012-07-06 12:25 | 2012-07-06 12:44 | CARRIER - 38CKC048---371-- | 100 | 12.2 | Yes | Yes | 21.3 | 21.3 | 0 | 3732BE7636404C5BAE0C556D944AE381 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.2% | 0.878 | 23.45% | [5 empty] | Non-TXV | 12.2%
Fresno | CA | 93722-5331 |  | 2012-06-01 | 2012-06-01 13:56 | 2012-06-01 14:04 | BDP - 585C102450 | 73 | 6.1 | Yes | Yes | 19.4 | 19.3 | 0.1 | 6C7F9DF3EBB04B469C6752F233D78112 |  | R22 | Non-TXV |  | 8.356% | 0.91644 | 16.06% | [5 empty] | Non-TXV | 8.356%
Mendota | CA | 93640-1931 |  | 2012-08-16 | 2012-08-16 11:24 | 2012-08-16 11:43 | WESTINGHOUSE - UNK | 96 | 4.9 | Yes | Yes | 19.6 | 18.8 | 0.8 | 4E8B5A02CB7A4612A0B88F6DE2826638 |  | R22 | Non-TXV |  | 5.104% | 0.94896 | 9.809% | [5 empty] | Non-TXV | 5.104%
Clovis | CA | 93612-4234 |  | 2012-06-07 | 2012-06-07 09:55 | 2012-06-07 10:17 | WESTINGHOUSE - N/A | 51 | 7.7 | Yes | Yes | 18.6 | 20.3 | -1.7 | 13F598B703104BFEAE85A2F9F97A8F73 |  | R22 | Non-TXV |  | 15.1% | 0.84902 | 29.02% | [5 empty] | Non-TXV | 15.1%
Merced | CA | 95348-4023 |  | 2012-06-15 | 2012-06-15 14:37 | 2012-06-15 15:30 | GOODMAN - CKL36LL | 88 | 6.7 | Yes | Yes | 18.4 | 19.2 | -0.8 | 5963EAE23BE54AE5ACF09E5C4CB30CE9 |  | R22 | Non-TXV |  | 7.614% | 0.92386 | 14.63% | [5 empty] | Non-TXV | 7.614%
Clovis | CA | 93612-4238 |  | 2012-06-08 | 2012-06-08 14:14 | 2012-06-08 14:33 | TRANE - YCC024F1LOBJ | 88 | 2.9 | Yes | Yes | 18.5 | 20.2 | -1.7 | 8AC7AD399A394F288B828DEA68028726 |  | R22 | Non-TXV |  | 3.295% | 0.96705 | 6.333% | [5 empty] | Non-TXV | 3.295%
Manteca | CA | 95336-4555 |  | 2012-07-02 | 2012-07-02 13:17 | 2012-07-02 13:48 | BRYANT - 588ANW024040ACAD | 38 | 17.7 | Yes | Yes | 19.5 | 21.2 | -1.7 | 0CABD472601248BEA2DC13F1A01E8E6E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 46.58% | 0.53421 | 89.51% | [5 empty] | Non-TXV | 46.58%
Winton | CA | 95388-9317 |  | 2012-06-07 | 2012-06-07 12:03 | 2012-06-07 12:29 | RHEEM - RRNA-B030JK06X | 72 | 2.6 | Yes | Yes | 21.1 | 18.9 | 2.2 | 7D1D3108D93B4B01A6026F504FBAF9EF |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Chico | CA | 95926-2758 |  | 2012-07-24 | 2012-07-24 14:42 | 2012-07-24 16:15 | HEIL - N4A324KB200 | 56 | 2.2 | Yes | Yes | 21.6 | 22.5 | -0.9 | E6137D4B20B0478992B8FD5DF16BC7B7 |  | R410A | TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | TXV | 3.929%
Ripon | CA | 95366-2024 |  | 2012-06-06 | 2012-06-06 14:19 | 2012-06-06 14:40 | BRYANT - 574DNW024040NA-- | 105 | 3.8 | Yes | Yes | 18.6 | 18.6 | 0 | BEFB1926E7704B0C8C32227B361804F9 |  | R410A | TXV |  | 3.619% | 0.96381 | 6.955% | [5 empty] | TXV | 3.619%
Fresno | CA | 93722-5041 |  | 2012-06-06 | 2012-06-06 09:45 | 2012-06-06 09:45 | YORK - DAYA-F048N110C | 92 | 0 | Yes | Yes | 25.8 | 21 | 4.8 | F2064A0EA7BC44E2BEE582E2A8E43298 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6554 |  | 2012-06-01 | 2012-06-01 12:30 | 2012-06-01 12:46 | RUUD - RRNA-B024JK00X | 78 | 2.4 | Yes | Yes | 19.9 | 21.5 | -1.6 | 8E29DA96478B497C931126EAF751ED29 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Chowchilla | CA | 93610-2120 |  | 2012-07-06 | 2012-07-06 11:11 | 2012-07-06 11:29 | BDP - 585EJ030050 | 58 | 3.4 | Yes | Yes | 19.3 | 18.8 | 0.5 | 1B72CBD550DF453D9E8E1BFBFA164027 |  | R22 | Non-TXV |  | 5.862% | 0.94138 | 11.27% | [5 empty] | Non-TXV | 5.862%
Ripon | CA | 95366-9725 |  | 2012-06-11 | 2012-06-11 15:38 | 2012-06-11 16:14 | ARCOAIRE - PGAA60E1K4 | 99 | 4.8 | Yes | Yes | 21.5 | 22.8 | -1.3 | E0D6F30D684E45B09695D90F06833A9A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.848% | 0.95152 | 9.318% | [5 empty] | Non-TXV | 4.848%
Merced | CA | 95348-2234 |  | 2012-07-05 | 2012-07-05 10:23 | 2012-07-05 10:47 | RHEEM - HC-100-36-21C | 48 | 4.5 | Yes | Yes | 21.8 | 20.3 | 1.6 | 146290FCDA014EB093311BA60992DE25 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Fresno | CA | 93710-7123 |  | 2012-08-09 | 2012-08-09 11:01 | 2012-08-09 11:31 | ARCOAIRE - NA048AKA1 | 129 | 4.2 | Yes | Yes | 17.2 | 19.8 | -2.6 | C677504845344BB3B0B4AFA0DCDFF7E9 |  | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
Stockton | CA | 95209-4822 |  | 2012-06-21 | 2012-06-21 12:34 | 2012-06-21 12:50 | PAYNE - 591AN048-C | 128 | 8.4 | Yes | Yes | 22.1 | 20.8 | 1.3 | 7FD0A062F7384894B89937D97CC462A3 |  | R22 | Non-TXV |  | 6.562% | 0.93437 | 12.61% | [5 empty] | Non-TXV | 6.562%
Fresno | CA | 93726-1838 |  | 2012-06-01 | 2012-06-01 11:44 | 2012-06-01 12:17 | CARRIER - 48GL036300BA | 84 | 7.4 | Yes | Yes | 26.7 | 20.7 | 6 | F95F74DB26CC4EDC9D5A48E5FC81E2CC |  | R22 | Non-TXV |  | 8.81% | 0.9119 | 16.93% | [5 empty] | Non-TXV | 8.81%
Chico | CA | 95926-2837 |  | 2012-07-02 | 2012-07-02 12:33 | 2012-07-02 12:59 | OTHER - NA | 80 | 9.3 | Yes | Yes | 21.2 | 22 | -0.8 | 8B15EDAA0A7F4F9B879CED0B9F17D803 |  | R22 | Non-TXV |  | 11.62% | 0.88375 | 22.34% | [5 empty] | Non-TXV | 11.62%
Merced | CA | 95340-0950 |  | 2012-06-12 | 2012-06-12 11:43 | 2012-06-12 12:13 | RHEEM - RRMA-A042JK08X | 114 | 4.7 | Yes | Yes | 22.2 | 21.2 | 1 | 5E74AEC0A85445AE98A385B4ACD9AF75 |  | R22 | Non-TXV |  | 4.123% | 0.95877 | 7.923% | [5 empty] | Non-TXV | 4.123%
Ripon | CA | 95366-2032 |  | 2012-06-06 | 2012-06-06 15:03 | 2012-06-06 15:31 | GOODMAN - PG8030????? REV A | 56 | 2.5 | Yes | Yes | 18.2 | 20.9 | -2.7 | 7AD5459DDEFF41848C2704A934F9E2D5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.464% | 0.95536 | 8.579% | [5 empty] | Non-TXV | 4.464%
Dinuba | CA | 93618-2909 |  | 2012-07-09 | 2012-07-09 09:52 | 2012-07-09 10:09 | DAY & NIGHT - 36/80YAC 107C | 67 | 7.8 | Yes | Yes | 18 | 19 | -1 | 1914E9C40C46425692D86E7145431090 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.64% | 0.88358 | 22.37% | [5 empty] | Non-TXV | 11.64%
Ripon | CA | 95366-2415 |  | 2012-06-06 | 2012-06-06 16:02 | 2012-06-06 16:29 | BDP - 585A018050YAC | 52 | 1.7 | Yes | Yes | 21.4 | 22.9 | -1.5 | ACC761D78FAB48AA93E28736F9717BB1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.269% | 0.96731 | 6.283% | [5 empty] | Non-TXV | 3.269%
Clovis | CA | 93612-4239 |  | 2012-06-08 | 2012-06-08 15:45 | 2012-06-08 15:45 | HEIL - 867.815014 | 62 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | A0A991D995E440DDAF94D1A35F161267 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4517 |  | 2012-06-07 | 2012-06-07 15:43 | 2012-06-07 16:05 | ICP - ACS048A2B2 | 101 | 13.8 | Yes | Yes | 18 | 20.7 | -2.7 | 9082802E98764A82A26EEE9E4EE7EA45 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.66% | 0.86337 | 26.26% | [5 empty] | Non-TXV | 13.66%
Stockton | CA | 95212-3214 |  | 2012-06-14 | 2012-06-14 13:36 | 2012-06-14 13:59 | GOODMAN - CKL49-1 | 109 | 3.8 | Yes | Yes | 23 | 21.3 | 1.7 | 8C92A949CDC9419E845EE100079DCCCD |  | R22 | Non-TXV |  | 3.486% | 0.96514 | 6.7% | [5 empty] | Non-TXV | 3.486%
Clovis | CA | 93612-4235 |  | 2012-06-07 | 2012-06-07 12:45 | 2012-06-07 13:09 | HEIL - N/A | 64 | 1.9 | Yes | Yes | 21.1 | 21.5 | -0.4 | 9F1665BD62D247B79F7DE164EFC9D500 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Clovis | CA | 93612-4237 |  | 2012-06-13 | 2012-06-13 12:27 | 2012-06-13 12:33 | GOODMAN - GPG13240451BA | 55 | -3.9 | Yes | Yes | 18.1 | 20.4 | -2.3 | 86079198062547138F5ED851B900D3A0 |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Mendota | CA | 93640-1934 |  | 2012-08-16 | 2012-08-16 15:32 | 2012-08-16 15:55 | OTHER - UNK | 96 | 3.2 | Yes | Yes | 17.2 | 18.5 | -1.3 | 0BC81F624A1B4B4DAC501F71B61378EF |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Clovis | CA | 93612-4231 |  | 2012-06-06 | 2012-06-06 12:11 | 2012-06-06 13:03 | GOODMAN - GPG12240451A | 64 | 3.5 | Yes | Yes | 17.6 | 20.2 | -2.6 | DBFA13586D5F454ABD343BE1C1C0AB89 |  | R22 | Non-TXV |  | 5.469% | 0.94531 | 10.51% | [5 empty] | Non-TXV | 5.469%
Clovis | CA | 93612-4238 |  | 2012-07-09 | 2012-07-09 12:21 | 2012-07-09 12:43 | OTHER - UNK | 62 | 2 | Yes | Yes | 18.7 | 19.9 | -1.2 | E2375C4A7E114DD2B98FE6C7D29F0572 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Clovis | CA | 93612-4232 |  | 2012-06-08 | 2012-06-08 14:48 | 2012-06-08 15:15 | WESTINGHOUSE - ID017JAACA | 63 | -3.7 | Yes | Yes | 18.2 | 20.4 | -2.2 | 739E15B9583A43BD90B7F59C66F3B621 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Clovis | CA | 93612-4231 |  | 2012-06-06 | 2012-06-06 12:32 | 2012-06-06 13:02 | GOODMAN - GPG12240451A | 65 | 3.3 | Yes | Yes | 19.2 | 22 | -2.8 | C339F4D3488B47FC9DED8867393CFA68 |  | R22 | Non-TXV |  | 5.077% | 0.94923 | 9.757% | [5 empty] | Non-TXV | 5.077%
Fresno | CA | 93727-7106 |  | 2012-07-06 | 2012-07-06 13:08 | 2012-07-06 13:30 | RHEEM - HC 120 48 1B | 85 | 6.9 | Yes | Yes | 19.5 | 20.9 | -1.4 | BDAAAF3F517B41D1998914A12E206E77 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.118% | 0.91882 | 15.6% | [5 empty] | Non-TXV | 8.118%
Fresno | CA | 93727-7106 |  | 2012-07-06 | 2012-07-06 13:36 | 2012-07-06 14:04 | AMERICAN STANDARD - YCP024F1M0BB | 118 | 14.3 | Yes | Yes | 21.8 | 22.1 | -0.3 | F979C35FC5DF43B89AC90FD492ECAF1C |  | R22 | Non-TXV |  | 12.12% | 0.87881 | 23.29% | [5 empty] | Non-TXV | 12.12%
Planada | CA | 95365-0000 |  | 2012-07-11 | 2012-07-11 10:11 | 2012-07-11 10:35 | WESTINGHOUSE - FS3BA-030KA | 68 | 4 | Yes | Yes | 25.2 | 20.8 | 4.4 | 37D5457DD2374D7093E2E29EB878EBB6 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Fresno | CA | 93726-2127 |  | 2012-06-01 | 2012-06-01 10:55 | 2012-06-01 10:55 | PAYNE - 36/80-YAC108C-C | 101 | 0 | Yes | Yes | 24.9 | 19.3 | 5.6 | EF0A20E9A1B7449B8FD40B6CCEB18CB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3021 |  | 2012-07-12 | 2012-07-12 11:44 | 2012-07-12 12:03 | HEIL - CA3048VKA1 | 145 | 16.5 | Yes | Yes | 28.2 | 28.7 | -0.5 | 6D292288BF6248E8A16700C1A41D2679 |  | R22 | Non-TXV |  | 11.38% | 0.88621 | 21.87% | [5 empty] | Non-TXV | 11.38%
Fresno | CA | 93710-4332 |  | 2012-08-07 | 2012-08-07 17:07 | 2012-08-07 17:14 | BDP - UNK | 76 | 3.6 | Yes | Yes | 17.2 | 20.1 | -2.9 | 9BED6C2491CC40E8B67459D4F139BED9 |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Fresno | CA | 93726-1021 |  | 2012-06-07 | 2012-06-07 13:34 | 2012-06-07 13:50 | GOODMAN - CKC36-1T | 77 | 3.8 | Yes | Yes | 18.8 | 21.5 | -2.7 | 665D9F1D20094FFAB1908B756F9207BB |  | R22 | Non-TXV |  | 4.935% | 0.95065 | 9.484% | [5 empty] | Non-TXV | 4.935%
Chico | CA | 95926-2750 |  | 2012-07-26 | 2012-07-26 09:30 | 2012-07-26 09:46 | PAYNE - NA | 48 | 5.4 | Yes | Yes | 21.8 | 20.8 | 1 | 2A0B7F58214148DD930C4DA869EB8746 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Atwater | CA | 95301-4107 |  | 2012-06-11 | 2012-06-11 08:36 | 2012-06-11 08:54 | TRANE - 4YCY4048A1096AA | 131 | 3.9 | Yes | Yes | 18.9 | 18.8 | 0.1 | 7DA5094F362440468A3D26ED868CF62B |  | R410A | Non-TXV |  | 2.977% | 0.97023 | 5.721% | [5 empty] | Non-TXV | 2.977%
Fresno | CA | 93710-4004 |  | 2012-08-16 | 2012-08-16 12:16 | 2012-08-16 12:47 | RHEEM - RRMA-036JK06X | 96 | 5.4 | Yes | Yes | 19.4 | 18.8 | 0.6 | 2618E860E2D04AC794D622DA3D6C9E17 |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Merced | CA | 95340-3002 |  | 2012-07-02 | 2012-07-02 09:37 | 2012-07-02 10:00 | RHEEM - HC105421B | 82 | 13.8 | Yes | Yes | 31.2 | 27.1 | 4.1 | DA0AFAC4BCAB49B6983B1668C03E0D19 |  | R22 | Non-TXV |  | 16.83% | 0.83171 | 32.34% | [5 empty] | Non-TXV | 16.83%
Chico | CA | 95926-2754 |  | 2012-07-25 | 2012-07-25 16:02 | 2012-07-25 16:02 | DAY & NIGHT - NA324AKB200 | 56 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | ED2FBD1431DF401EA0AC6AC756D13E03 |  | R410A | TXV |  | 0% | 1 | 0%
Corning | CA | 96021-2038 |  | 2012-07-05 | 2012-07-05 12:06 | 2012-07-05 12:27 | CARRIER - 38EN024310 | 56 | 4.4 | Yes | Yes | 26.1 | 21.7 | 4.4 | 4739E887A7DA49A88E57A03F41A872CC |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Los Banos | CA | 93635-9204 |  | 2012-07-05 | 2012-07-05 12:40 | 2012-07-05 13:01 | NORDYNE - JS3BC030KA | 68 | 10.3 | Yes | Yes | 20.1 | 22.4 | -2.3 | 25E87E328FDC4688898C42175111B8B7 |  | R22 | Non-TXV |  | 15.15% | 0.84853 | 29.11% | [5 empty] | Non-TXV | 15.15%
Auburn | CA | 95603-3005 |  | 2012-07-06 | 2012-07-06 14:32 | 2012-07-06 14:49 | OTHER - PGE10B30D075LA-3A | 51 | 1.5 | Yes | Yes | 24 | 21.3 | 2.7 | D6B30F769461492384BEAF1B098E79F7 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Grass Valley | CA | 95945-7952 |  | 2012-07-09 | 2012-07-09 11:38 | 2012-07-09 11:56 | DAY & NIGHT - UNK FADED | 83 | 8.2 | Yes | Yes | 26.2 | 20.4 | 5.8 | 600DEF471E5C46F4B790DD885DB086D5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.88% | 0.9012 | 18.99% | [5 empty] | Non-TXV | 9.88%
Auburn | CA | 95603-5500 |  | 2012-06-06 | 2012-06-06 12:00 | 2012-06-06 12:16 | DAY & NIGHT - 585HJW018040ABAC | 60 | 1.8 | Yes | Yes | 21 | 19.9 | 1.1 | D908646AB6F7417BBDE8A7E8DA20D73C |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Atwater | CA | 95301-4879 |  | 2012-07-02 | 2012-07-02 12:09 | 2012-07-02 12:25 | LENNOX - HS9-3113P | 77 | 4.9 | Yes | Yes | 18.3 | 18.9 | -0.6 | CA92AE1B6F9F4EF69F084F2E56555293 |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Stockton | CA | 95203-1061 |  | 2012-06-14 | 2012-06-14 13:02 | 2012-06-14 13:21 | GOODMAN - PGB024075-1 | 54 | 9 | Yes | Yes | 17.8 | 20.2 | -2.4 | F2B153AF0810490C8863A1F0BDCB4044 |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Oroville | CA | 95965-4581 |  | 2012-06-01 | 2012-06-01 12:13 | 2012-06-01 13:56 | AMERICAN STANDARD - 4A784030E100AA | 104 | 3.8 | Yes | Yes | 21 | 19.8 | 1.2 | E1F77A07DE0C48A197AF9446A0EEA5E9 |  | R410A | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Merced | CA | 95348-2214 |  | 2012-07-05 | 2012-07-05 12:20 | 2012-07-05 12:36 | AMERICAN STANDARD - YCC036F1M0BF | 86 | 3.8 | Yes | Yes | 17.9 | 20.4 | -2.5 | CEE0F9AC219D485491F3784097F5787B |  | R22 | Non-TXV |  | 4.419% | 0.95581 | 8.492% | [5 empty] | Non-TXV | 4.419%
Merced | CA | 95348-1321 |  | 2012-06-12 | 2012-06-12 09:43 | 2012-06-12 10:04 | RUUD - UAKA-030JAZ | 62 | 1.9 | Yes | Yes | 24 | 21 | 3 | 430C7DF421094188B14FC74AA10005D3 |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Stockton | CA | 95210-2044 |  | 2012-06-08 | 2012-06-08 10:54 | 2012-06-08 11:11 | BDP - 585A030080YAC | 50 | -4.1 | Yes | Yes | 26.9 | 21 | 5.9 | 4EEE7B7605364F6C9275AFB15A8EC22C |  | R22 | Non-TXV |  | -8.2% | 1.082 | 2.296% |  |  |  |  | Non-TXV |  |  | -8.2%
Stockton | CA | 95210-2040 |  | 2012-06-07 | 2012-06-07 09:11 | 2012-06-07 09:31 | DAY & NIGHT - 585A030080YACR | 50 | 1.5 | Yes | Yes | 21.4 | 19.1 | 2.3 | C912CCB8E1C744FD81DB0C55DDD2077A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95341-6980 |  | 2012-06-08 | 2012-06-08 13:07 | 2012-06-08 13:24 | PAYNE - PYPNB036060ABAA | 68 | 4.4 | Yes | Yes | 25.6 | 20.4 | 5.2 | BE7AA9AE73E140F6A79A0704908288A3 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Merced | CA | 95348-2613 |  | 2012-07-09 | 2012-07-09 11:51 | 2012-07-09 12:12 | GOODMAN - GSC13024EA | 77 | 3.8 | Yes | Yes | 16.4 | 18.8 | -2.4 | B139731E599E432E895A09E4B9AFF099 |  | R22 | Non-TXV |  | 4.935% | 0.95065 | 9.484% | [5 empty] | Non-TXV | 4.935%
Winton | CA | 95388-0000 |  | 2012-07-25 | 2012-07-25 09:57 | 2012-07-25 10:18 | RUUD - NA | 58 | 1.8 | Yes | Yes | 16.8 | 16.4 | 0.4 | 6704637A85634323A18CDBF5D93B1058 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Stockton | CA | 95215-7506 |  | 2012-07-05 | 2012-07-05 12:54 | 2012-07-05 13:15 | GOODMAN - UNK | 98 | 3.1 | Yes | Yes | 18.2 | 17.2 | 1 | 083A07F4F0194EFB91D51E3A8751CE12 |  | R22 | Non-TXV |  | 3.163% | 0.96837 | 6.079% | [5 empty] | Non-TXV | 3.163%
Stockton | CA | 95205-2578 |  | 2012-06-01 | 2012-06-01 10:12 | 2012-06-01 10:35 | CARRIER - 38EZG048300 | 125 | 5 | Yes | Yes | 19.3 | 20.4 | -1.1 | A6FDB87333474BCC83E84C27C336A815 |  | R410A | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Merced | CA | 95341-6854 |  | 2012-06-07 | 2012-06-07 13:19 | 2012-06-07 13:40 | RHEEM - UNK | 76 | 8.3 | Yes | Yes | 22.4 | 21 | 1.4 | B5BBB2A0F67641298468AA1EC1EF2912 |  | R22 | Non-TXV |  | 10.92% | 0.89079 | 20.99% | [5 empty] | Non-TXV | 10.92%
Atwater | CA | 95301-0000 |  | 2012-07-05 | 2012-07-05 11:35 | 2012-07-05 11:55 | OTHER - GCGD30S41S3A | 62 | 1.9 | Yes | Yes | 20.6 | 20.4 | 0.2 | 505E7E4EF44E4AC78432A278BB0FF60D |  | R410A | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Merced | CA | 95341-6230 |  | 2012-06-12 | 2012-06-12 15:20 | 2012-06-12 15:49 | COPELAND - C1T24-1B | 99 | 5.4 | Yes | Yes | 21 | 19 | 2 | DF3CBF0EA75941EB81C756AF4C92C04F |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Penn Valley | CA | 95946-9490 |  | 2012-06-15 | 2012-06-15 12:42 | 2012-06-15 13:00 | TRANE - YCC024F1L0BJ | 66 | 6.3 | Yes | Yes | 22.1 | 21.2 | 0.9 | 08101E665CC249C7A4A6E2F12ADFBC1F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Merced | CA | 95341-6209 |  | 2012-06-15 | 2012-06-15 14:03 | 2012-06-15 14:27 | GOODMAN - CLT24-1B | 99 | 3.3 | Yes | Yes | 19.3 | 20.2 | -0.9 | AC0CC0A7B6A24105980DFF8702FA199D |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Riverbank | CA | 95367-2764 |  | 2012-06-08 | 2012-06-08 11:06 | 2012-06-08 11:24 | GOODMAN - CK42-1C | 86 | 6.1 | Yes | Yes | 19.8 | 20.4 | -0.6 | FF09DEF189F84F63859CD013C87FC63B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.093% | 0.92907 | 13.63% | [5 empty] | Non-TXV | 7.093%
Paradise | CA | 95969-5657 |  | 2012-07-06 | 2012-07-06 11:43 | 2012-07-06 12:08 | HEIL - NRCE30DCB02 | 45 | 3.9 | Yes | Yes | 22.5 | 20.1 | 2.4 | 8D6F866D4A214B6F8CDC8734621E9F6F |  | R22 | Non-TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | Non-TXV | 8.667%
Winton | CA | 95388-0000 |  | 2012-06-07 | 2012-06-07 11:45 | 2012-06-07 12:03 | OTHER - 18ECW045GA | 85 | 2.5 | Yes | Yes | 18 | 19.7 | -1.7 | 47BE7EAFFA97440980DB3DEFF17CBB2B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Grass Valley | CA | 95945-6831 |  | 2012-07-09 | 2012-07-09 11:02 | 2012-07-09 11:30 | CARRIER - 50HS-024-311 | 70 | 11.9 | Yes | Yes | 18 | 20.4 | -2.4 | 795379C5ACBF435BBD0B22EBEEFA1527 |  | R22 | Non-TXV |  | 17% | 0.83 | 32.67% | [5 empty] | Non-TXV | 17%
Penn Valley | CA | 95946-8819 |  | 2012-06-15 | 2012-06-15 10:49 | 2012-06-15 10:49 | RHEEM - RRMA-A48JK10X | 115 | 0 | Yes | Yes | 17.2 | 18.7 | -1.5 | 6710642E3C1E46679E5BE68246C80C19 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-5659 |  | 2012-07-02 | 2012-07-02 12:47 | 2012-07-02 13:13 | HEIL - UNK | 85 | 11.2 | Yes | Yes | 22.4 | 21 | 1.5 | 0651772665E348079AF3AF2778BE7152 |  | R22 | Non-TXV |  | 13.18% | 0.86824 | 25.32% | [5 empty] | Non-TXV | 13.18%
Los Banos | CA | 93635-4526 |  | 2012-07-05 | 2012-07-05 11:27 | 2012-07-05 11:45 | WESTINGHOUSE - UNK | 88 | 15 | Yes | Yes | 18.8 | 21.3 | -2.5 | 7ABE25B5BBD14E5D8B357268B00B216B |  | R22 | Non-TXV |  | 17.05% | 0.82955 | 32.76% | [5 empty] | Non-TXV | 17.05%
Oakdale | CA | 95361-2509 |  | 2012-06-12 | 2012-06-12 13:33 | 2012-06-12 13:55 | ICP - AG024GB3 | 73 | 3.5 | Yes | Yes | 19.7 | 21 | -1.3 | 2142B16F6A0E414A86BA52BB534B6C85 |  | R22 | Non-TXV |  | 4.795% | 0.95205 | 9.214% | [5 empty] | Non-TXV | 4.795%
Madera | CA | 93637-6266 |  | 2012-06-11 | 2012-06-11 11:42 | 2012-06-11 11:59 | CARRIER - 585EW030075ABAF | 76 | 5.9 | Yes | Yes | 17.6 | 19.9 | -2.3 | 9861A93D4D0847DB8F35CFD0D67AC6E9 |  | R22 | Non-TXV |  | 7.763% | 0.92237 | 14.92% | [5 empty] | Non-TXV | 7.763%
Madera | CA | 93638-3453 |  | 2012-06-12 | 2012-06-12 14:18 | 2012-06-12 14:35 | RHEEM - RKA-A024JKO8E | 65 | 2.7 | Yes | Yes | 17.3 | 20.2 | -2.9 | 4C06828D9D12483481CE6A1FFB82AD99 |  | R22 | Non-TXV |  | 4.154% | 0.95846 | 7.983% | [5 empty] | Non-TXV | 4.154%
Georgetown | CA | 95634-0000 |  | 2012-07-30 | 2012-07-30 09:12 | 2012-07-30 09:36 | BRYANT - 582ANW024060NAAD | 56 | -4 | Yes | Yes | 18.1 | 19.1 | -1 | 6A24295B787149F7A23F993C1D0647A6 |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Los Banos | CA | 93635-3513 |  | 2012-06-07 | 2012-06-07 10:55 | 2012-06-07 11:20 | TRANE - YCY036G1MOAC | 129 | 6.1 | Yes | Yes | 24.9 | 20.3 | 4.6 | 010A8F956D2D414981669EFC9924B938 |  | R22 | Non-TXV |  | 4.729% | 0.95271 | 9.087% | [5 empty] | Non-TXV | 4.729%
Stockton | CA | 95206-2040 |  | 2012-07-11 | 2012-07-11 10:10 | 2012-07-11 10:32 | GOODMAN - CKL36-1L | 84 | 5.2 | Yes | Yes | 19 | 20.3 | -1.3 | CC70F3CDFC0A495E93AE711276AD2517 |  | R22 | Non-TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | Non-TXV | 6.19%
Lathrop | CA | 95330-9184 |  | 2012-05-31 | 2012-05-31 14:06 | 2012-05-31 14:27 | GOODMAN - CKJ42-1AB | 106 | 3.7 | Yes | Yes | 18.9 | 19.8 | -0.9 | 743CCD67F11C45D298EFA38FC2928276 |  | R22 | Non-TXV |  | 3.491% | 0.96509 | 6.708% | [5 empty] | Non-TXV | 3.491%
Atwater | CA | 95301-4032 |  | 2012-06-11 | 2012-06-11 11:39 | 2012-06-11 11:59 | OTHER - 60WR24E1NA | 56 | 3 | Yes | Yes | 20.8 | 21.7 | -0.9 | 0F9BFB42484B426E85738B21B0446DD5 |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Atwater | CA | 95301-4810 |  | 2012-06-12 | 2012-06-12 09:36 | 2012-06-12 09:57 | BRYANT - 598AN036-B | 192 | 7.3 | Yes | Yes | 18 | 20.7 | -2.7 | 05D7C9730DE7494386EE2C2ADE90D080 |  | R22 | Non-TXV |  | 3.802% | 0.96198 | 7.307% | [5 empty] | Non-TXV | 3.802%
Merced | CA | 95348-3738 |  | 2012-06-07 | 2012-06-07 08:50 | 2012-06-07 09:09 | HEIL - PGC036K060N | 71 | 3.8 | Yes | Yes | 21.9 | 19.8 | 2.1 | 666CD324F7D045DD925C0EC917CE6014 |  | R22 | Non-TXV |  | 5.352% | 0.94648 | 10.29% | [5 empty] | Non-TXV | 5.352%
Yuba City | CA | 95991-7541 |  | 2012-06-15 | 2012-06-15 10:14 | 2012-06-15 10:34 | PAYNE - PA10JA042-D | 90 | 7.6 | Yes | Yes | 21.3 | 20.2 | 1.2 | 696C4797ADE041BD84BEB563ADAE3D9A |  | R22 | TXV |  | 8.444% | 0.91556 | 16.23% | [5 empty] | TXV | 8.444%
Merced | CA | 95341-6700 |  | 2012-06-14 | 2012-06-14 13:17 | 2012-06-14 13:57 | OTHER - TTR036C100AO | 92 | 11.5 | Yes | Yes | 23.9 | 21 | 2.9 | E78DF782FA33494AAEE825C4E7A20CD4 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Marysville | CA | 95901-9698 |  | 2012-06-08 | 2012-06-08 14:16 | 2012-06-08 14:16 | LENNOX - CHP29-048-1PA | 120 | 0 | Yes | Yes | 19.8 | 18.8 | 1 | 14824C205A1E497FAC2855478F752EF2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-8815 |  | 2012-06-11 | 2012-06-11 11:04 | 2012-06-11 11:28 | CARRIER - 48GX-048090311--- | 85 | 4.9 | Yes | Yes | 15.6 | 18.1 | -2.5 | 351FEBFD53F448FD8FA0F4A6E9A8E9AE |  | R22 | Non-TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | Non-TXV | 5.765%
Los Banos | CA | 93635-9488 |  | 2012-06-13 | 2012-06-13 12:54 | 2012-06-13 13:19 | BRYANT - 561CJ048-G | 101 | 5.2 | Yes | Yes | 18 | 20.4 | -2.4 | FF5B292E126749FC9AA5EF5691C87FFB |  | R22 | Non-TXV |  | 5.149% | 0.94851 | 9.894% | [5 empty] | Non-TXV | 5.149%
Los Banos | CA | 93635-4523 |  | 2012-06-07 | 2012-06-07 13:55 | 2012-06-07 14:16 | OTHER - BRSC0361CB | 74 | 2.9 | Yes | Yes | 27.5 | 21.5 | 6 | 5D91C249B67E4E6DBEF51D0E4C63BC49 |  | R22 | Non-TXV |  | 3.919% | 0.96081 | 7.531% | [5 empty] | Non-TXV | 3.919%
Yuba City | CA | 95993-9618 |  | 2012-07-12 | 2012-07-12 15:01 | 2012-07-12 15:19 | ARCOAIRE - PGC030K860A | 52 | 5 | Yes | Yes | 18.5 | 15.6 | 2.9 | 8B60F03F4180402288F75A82B18CFE56 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.615% | 0.90385 | 18.48% | [5 empty] | Non-TXV | 9.615%
Madera | CA | 93637-4883 |  | 2012-06-08 | 2012-06-08 14:34 | 2012-06-08 14:52 | LENNOX - 13ACD-042-230-01 | 111 | 3.3 | Yes | Yes | 24.8 | 20.4 | 4.4 | FA355EE7F2584F9BB26BDA39CB72ECDE |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Merced | CA | 95348-2648 |  | 2012-07-06 | 2012-07-06 12:13 | 2012-07-06 12:30 | CARRIER - 38CKCD18330 | 55 | 3.2 | Yes | Yes | 18.8 | 20.4 | -1.6 | 1990D9D73426437086FA9FD5CCB1AB71 |  | R22 | Non-TXV |  | 5.818% | 0.94182 | 11.18% | [5 empty] | Non-TXV | 5.818%
Stockton | CA | 95210-3208 |  | 2012-06-12 | 2012-06-12 12:03 | 2012-06-12 12:20 | GE - BTB930A100A1 | 53 | 1.9 | Yes | Yes | 25 | 20.9 | 4.1 | 1C369BAFFAE24C5FBDC185F6313EE625 |  | R22 | Non-TXV |  | 3.585% | 0.96415 | 6.889% | [5 empty] | Non-TXV | 3.585%
Los Banos | CA | 93635-3147 |  | 2012-06-06 | 2012-06-06 10:54 | 2012-06-06 11:16 | PAYNE - 591ANX036000AAAA | 83 | 3.7 | Yes | Yes | 20.8 | 16.5 | 4.3 | D62D35B3FE12470EBF9444170DC7B145 |  | R22 | Non-TXV |  | 4.458% | 0.95542 | 8.567% | [5 empty] | Non-TXV | 4.458%
Merced | CA | 95340-1452 |  | 2012-06-13 | 2012-06-13 10:09 | 2012-06-13 10:29 | GOODMAN - PGB0240751 | 54 | 9.1 | Yes | Yes | 22.2 | 23.6 | -1.4 | 692F1483299847FFA09BB68288799CAC |  | R22 | Non-TXV |  | 16.85% | 0.83148 | 32.39% | [5 empty] | Non-TXV | 16.85%
Atwater | CA | 95301-4888 |  | 2012-06-06 | 2012-06-06 14:30 | 2012-06-06 14:48 | RHEEM - RAFA-030JAQ | 59 | 1.8 | Yes | Yes | 18.6 | 20.3 | -1.7 | 66CAC09C148D4385B7C25356B1BC0F3F |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Merced | CA | 95341-6209 |  | 2012-06-07 | 2012-06-07 09:08 | 2012-06-07 09:29 | GOODMAN - CLT241B | 99 | 3.8 | Yes | Yes | 19.2 | 15.2 | 4 | 5BDB49CFADCB4D2CB566344A99DD0C87 |  | R22 | Non-TXV |  | 3.838% | 0.96162 | 7.377% | [5 empty] | Non-TXV | 3.838%
Placerville | CA | 95667-4009 |  | 2012-06-13 | 2012-06-13 11:38 | 2012-06-13 11:58 | AMANA - PGA30B0702C | 84.1 | 17.7 | Yes | Yes | 23.6 | 19.9 | 3.7 | 2DDAB1F8809C4726A58B760366209AA1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 21.05% | 0.78954 | 40.45% | [5 empty] | Non-TXV | 21.05%
Chico | CA | 95973-7861 |  | 2012-07-23 | 2012-07-23 08:58 | 2012-07-23 09:17 | OTHER - R2H324GKR2 | 71 | 3.3 | Yes | Yes | 24.5 | 22.4 | 2.2 | 6975BE76545748FC8445E07FF70E0CFE |  | R22 | TXV |  | 4.648% | 0.95352 | 8.932% | [5 empty] | TXV | 4.648%
Atwater | CA | 95301-2308 |  | 2012-06-01 | 2012-06-01 09:42 | 2012-06-01 10:01 | OTHER - GPFM24K060E | 54 | 1.6 | Yes | Yes | 19.8 | 18.7 | 1.1 | A18B95525DA2486B926E48C6F3BDE6CA |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Merced | CA | 95341-6230 |  | 2012-06-12 | 2012-06-12 14:35 | 2012-06-12 14:54 | COPELAND - CLT24-1B | 99 | 4.7 | Yes | Yes | 23.1 | 20.4 | 2.7 | C084F1FAF73946979E6758FD123B77E6 |  | R22 | Non-TXV |  | 4.747% | 0.95253 | 9.124% | [5 empty] | Non-TXV | 4.747%
Chico | CA | 95928-4711 |  | 2012-07-13 | 2012-07-13 09:54 | 2012-07-13 10:12 | YORK - H1CB030S06A | 74 | 6.8 | Yes | Yes | 23.6 | 20.7 | 2.9 | 8FA77F17B5DC471DAFF5EC8BEEC7DD4E |  | R22 | Non-TXV |  | 9.189% | 0.90811 | 17.66% | [5 empty] | Non-TXV | 9.189%
Merced | CA | 95341-6865 |  | 2012-06-12 | 2012-06-12 11:34 | 2012-06-12 11:57 | GOODMAN - GPG13240451BA | 77 | 4.8 | Yes | Yes | 26.1 | 20.4 | 5.7 | BED2C9CEF3384E85B36EEEDDDFA49A50 |  | R22 | Non-TXV |  | 6.234% | 0.93766 | 11.98% | [5 empty] | Non-TXV | 6.234%
El Dorado | CA | 95623-4241 |  | 2012-07-23 | 2012-07-23 11:10 | 2012-07-23 11:31 | GOODMAN - GSH130181CA | 127 | 8.4 | Yes | Yes | 16.5 | 19.3 | -2.8 | 70AF268771B04406A38DB85FA4C8C5E5 |  | R22 | Non-TXV |  | 6.614% | 0.93386 | 12.71% | [5 empty] | Non-TXV | 6.614%
Granite Bay | CA | 95746-6240 |  | 2012-07-13 | 2012-07-13 14:02 | 2012-07-13 14:29 | TRANE - TWPO42C100A2 | 176 | 37.6 | Yes | Yes | 18.7 | 19.7 | -0.9 | 0B29A4203E1048E0BED9950674C5F36B |  | R22 | Non-TXV |  | 21.36% | 0.78636 | 41.06% | [5 empty] | Non-TXV | 21.36%
Merced | CA | 95341-6955 |  | 2012-06-13 | 2012-06-13 14:22 | 2012-06-13 14:42 | AIRE-FLO - D3NZ024N03606NXA | 58 | 11.2 | Yes | Yes | 24.9 | 20.8 | 4.1 | C0EF7B15A9E84AD5835CE4EA410ED3E7 |  | R410A | Non-TXV |  | 19.31% | 0.8069 | 37.11% | [5 empty] | Non-TXV | 19.31%
Merced | CA | 95341-6230 |  | 2012-07-03 | 2012-07-03 13:24 | 2012-07-03 13:50 | GOODMAN - CLT24-1B | 99 | -5.8 | Yes | Yes | 23.6 | 20.8 | 2.8 | 1A8B4EC0BE5341FF99BB0A853B46CAE7 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Merced | CA | 95348-3300 |  | 2012-06-07 | 2012-06-07 09:37 | 2012-06-07 09:54 | BDP - 585BJ01018 | 71 | 3 | Yes | Yes | 18.5 | 20.4 | -1.9 | 483737DAF02247FF8DC82B26F5FD59A4 |  | R22 | Non-TXV |  | 4.225% | 0.95775 | 8.12% | [5 empty] | Non-TXV | 4.225%
Merced | CA | 95348-3387 |  | 2012-07-06 | 2012-07-06 14:36 | 2012-07-06 14:52 | BDP - 565BJ018 | 82 | -4.8 | Yes | Yes | 23 | 18.8 | 4.2 | 69A0A7F3C6BD438D950EC409B46E009F |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Merced | CA | 95340-4508 |  | 2012-07-02 | 2012-07-02 11:23 | 2012-07-02 11:41 | AMERICAN STANDARD - YCX030F1MOBC | 102 | 12.4 | Yes | Yes | 21.8 | 23.6 | -1.8 | 9DB926D112A44AE4A9F0D44C76CD3827 |  | R22 | Non-TXV |  | 12.16% | 0.87843 | 23.36% | [5 empty] | Non-TXV | 12.16%
Atwater | CA | 95301-4887 |  | 2012-06-06 | 2012-06-06 13:10 | 2012-06-06 13:37 | OTHER - NA | 45 | 1.4 | Yes | Yes | 15.7 | 17.5 | -1.8 | 3299C06EDD8147BF97CA5ACF4DA46C02 |  | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Chico | CA | 95973-0891 |  | 2012-07-25 | 2012-07-25 16:05 | 2012-07-25 16:25 | GIBSON - JT3BA-018KA | 70 | 4 | Yes | Yes | 20.5 | 20.7 | -0.2 | ADECED5EEA36485DB0FA60F14BA97961 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Yuba City | CA | 95991-2404 |  | 2012-06-15 | 2012-06-15 10:01 | 2012-06-15 10:44 | PAYNE - 588ANW036080ACAF | 85 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | 3A21C58A05E04705BB24A4E203D4718D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-3509 |  | 2012-06-06 | 2012-06-06 14:27 | 2012-06-06 15:05 | COLEMAN - 9536C901 | 54 | 4 | Yes | Yes | 25.5 | 21.7 | 3.8 | 925034CB02FE4429B4F670FD4B824C4B |  | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
Merced | CA | 95341-6249 |  | 2012-06-11 | 2012-06-11 09:13 | 2012-06-11 09:42 | YORK - H2RA030S06G | 62 | 10.7 | Yes | Yes | 19.4 | 21.7 | -2.3 | F89F97BD1D1E4F0EA29B66DE08600128 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 17.26% | 0.82742 | 33.17% | [5 empty] | Non-TXV | 17.26%
Yuba City | CA | 95993-5600 |  | 2012-06-01 | 2012-06-01 12:29 | 2012-06-01 12:45 | LENNOX - 10GSC024X-75-3PA | 52 | 3.8 | Yes | Yes | 18 | 20.9 | -2.9 | 987B94DE6C52466FB2245A50947A2273 |  | R22 | Non-TXV |  | 7.308% | 0.92692 | 14.04% | [5 empty] | Non-TXV | 7.308%
Rocklin | CA | 95677-3169 |  | 2012-06-01 | 2012-06-01 14:56 | 2012-06-01 15:15 | GOODMAN - CRT18-1 | 94 | -6.6 | Yes | Yes | 15 | 18 | -3 | B3A38D4D54EC457FB912415008A1F1DD |  | R22 | Non-TXV |  | -7.021% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.021%
Stockton | CA | 95207-2824 |  | 2012-06-19 | 2012-06-19 10:28 | 2012-06-19 10:46 | GOODMAN - CLT30-1B | 107 | 4.8 | Yes | Yes | 17.6 | 20.4 | -2.8 | 1A560E5D7C014F85AD58F9A274DC6223 |  | R22 | TXV |  | 4.486% | 0.95514 | 8.621% | [5 empty] | TXV | 4.486%
Chico | CA | 95928-4197 |  | 2012-06-08 | 2012-06-08 19:42 | 2012-06-08 20:24 | WESTINGHOUSE - FS3BA-030KA | 69 | 2.4 | Yes | Yes | 22.8 | 20.1 | 2.7 | 0FAB2F60A0B5491186B019354B8E7C7E |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Merced | CA | 95348-4359 |  | 2012-06-13 | 2012-06-13 10:31 | 2012-06-13 10:51 | RHEEM - RAKA-024JAS | 51 | 2.5 | Yes | Yes | 15 | 16.7 | -1.7 | 9262178CAA614FEC9BBB1976D45AD129 |  | R22 | Non-TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | Non-TXV | 4.902%
Yuba City | CA | 95993-3588 |  | 2012-06-01 | 2012-06-01 09:01 | 2012-06-01 09:27 | HEIL - N2A330AKA200 | 82 | 2.7 | Yes | Yes | 18 | 19 | -1 | 6A0120199DBC4493AE0E6466E5CA8740 |  | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Merced | CA | 95348-3309 |  | 2012-07-03 | 2012-07-03 12:49 | 2012-07-03 13:12 | BDP - UNK | 66 | 4.6 | Yes | Yes | 18 | 18.8 | -0.8 | 138F227921684C6E810637411E953DB1 |  | R22 | Non-TXV |  | 6.97% | 0.9303 | 13.39% | [5 empty] | Non-TXV | 6.97%
Red Bluff | CA | 96080-3981 |  | 2012-06-01 | 2012-06-01 15:57 | 2012-06-01 15:57 | TRAIN - 2TTB2036A1000AA | 96 | 0 | Yes | Yes | 20.6 | 19.7 | 0.9 | 1C6BABEF267A4272ABACA236FF583304 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9675 |  | 2012-06-08 | 2012-06-08 11:17 | 2012-06-08 11:39 | OTHER - UNK | 85 | -8 | Yes | Yes | 21 | 21.9 | -0.9 | 3A8E1E6A29AA4339A65112E8049F508B |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Penn Valley | CA | 95946-8928 |  | 2012-08-14 | 2012-08-14 17:21 | 2012-08-14 17:21 | YORK - H2DB024S06B | 58 | 0 | Yes | Yes | 0 | 14.4 | -14.4 | E6CA27E8631E4CD8941CAF3D1616F7F7 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-1007 |  | 2012-06-06 | 2012-06-06 15:28 | 2012-06-06 15:46 | TRANE - TTX742B100A0 | 170 | 22.2 | Yes | Yes | 26.7 | 20.8 | 5.9 | 6861AC526541466B8EBEAF1EFFBFEED7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.06% | 0.86941 | 25.1% | [5 empty] | Non-TXV | 13.06%
Los Banos | CA | 93635-2800 |  | 2012-06-07 | 2012-06-07 13:20 | 2012-06-07 13:43 | BRYANT - 561AJ030-A | 72 | 0 | Yes | Yes | 30.6 | 21.3 | 9.4 | 86E36F4096DF46389B0D70A41A5232EB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8007 |  | 2012-06-08 | 2012-06-08 10:21 | 2012-06-08 10:47 | DAY & NIGHT - 591ANX036000AAAA | 90 | 9.5 | Yes | Yes | 20 | 20.4 | -0.4 | D0C0797BD2324C42B755D8E3F5FE2DD5 |  | R22 | Non-TXV |  | 10.56% | 0.89444 | 20.29% | [5 empty] | Non-TXV | 10.56%
Olivehurst | CA | 95961-0000 |  | 2012-07-03 | 2012-07-03 12:03 | 2012-07-03 12:20 | TRANE - TTN030D100A0 | 86 | 7.2 | Yes | Yes | 21.3 | 18.7 | 2.6 | 3FBA8297C8084D849335AB6D59022998 |  | R22 | TXV |  | 8.372% | 0.91628 | 16.09% | [5 empty] | TXV | 8.372%
Olivehurst | CA | 95961-0000 |  | 2012-07-03 | 2012-07-03 12:23 | 2012-07-03 12:23 | UNITARY PRODUCTS GROUP - TCGD36541S1HA | 86 | 0 | Yes | Yes | -0.8 | 21 | -21.8 | FFD9F3E32C1A4BE392A2EE8EC0D31D9C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4887 |  | 2012-07-03 | 2012-07-03 11:54 | 2012-07-03 12:15 | OTHER - NA | 43 | 2.6 | Yes | Yes | 16.6 | 19.1 | -2.5 | DEEC81159E8F4E8FBCFA223978736FBB |  | R22 | Non-TXV |  | 6.047% | 0.93953 | 11.62% | [5 empty] | Non-TXV | 6.047%
Valley Springs | CA | 95252-8202 |  | 2012-07-16 | 2012-07-16 09:24 | 2012-07-16 09:41 | YORK - THGD3621S1A | 145 | -8.5 | Yes | Yes | 18.7 | 18.7 | 0 | 67EE529CA8E6440787B17BF8367DDE80 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Penn Valley | CA | 95946-9692 |  | 2012-07-25 | 2012-07-25 12:50 | 2012-07-25 12:50 | BRYANT - 542D042HP | 181 | 0 | Yes | Yes | 17.1 | 19.8 | -2.7 | 40AF4D0ED1CE4F40AE3C9276ADFBDCE4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-7004 |  | 2012-06-19 | 2012-06-19 15:30 | 2012-06-19 15:47 | LENNOX - HS23-411-3P | 92 | 2.8 | Yes | Yes | 23 | 20.9 | 2.1 | DFD34477D5144BA8B69CCA5FF32BC0AC |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Corning | CA | 96021-2028 |  | 2012-06-06 | 2012-06-06 13:21 | 2012-06-06 13:21 | GOODMAN - GSC140241AC | 127 | 0 | Yes | Yes | 24.8 | 22 | 2.8 | 4A37AB987C134EB4B10B2BD4EF6E0E7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Andreas | CA | 95249-9666 |  | 2012-07-19 | 2012-07-19 11:06 | 2012-07-19 11:23 | BDP - 561CJ042-A | 80 | -4.7 | Yes | Yes | 22.3 | 19.9 | 2.4 | D779B97184D04281839E03689D61A85E |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Chico | CA | 95973-0889 |  | 2012-07-19 | 2012-07-19 16:08 | 2012-07-19 16:08 | GIBSON - GT3B-024KA | 63 | 0 | Yes | Yes | 19 | 20.6 | -1.6 | 5CFAC830B6684DF9B731EFEB30FA19ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4142 |  | 2012-06-13 | 2012-06-13 14:13 | 2012-06-13 15:49 | GOODMAN - CKL36-1D | 72 | 4.5 | Yes | Yes | 22 | 20.7 | 1.4 | F9FDE0CEF32847C9B4D1F5854F084C4C |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Gridley | CA | 95948-9536 |  | 2012-07-19 | 2012-07-19 10:08 | 2012-07-19 10:27 | YORK - H2RC048S06G | 119 | 26.4 | Yes | Yes | 16 | 18.8 | -2.8 | 7D92F59B20C24D6792BF741DCFF2E8C9 |  | R22 | Non-TXV |  | 22.18% | 0.77815 | 42.63% | [5 empty] | Non-TXV | 22.18%
Merced | CA | 95348-3014 |  | 2012-06-07 | 2012-06-07 14:08 | 2012-06-07 14:28 | LUXAIRE - 42ECW080GA | 125 | 4.5 | Yes | Yes | 21.9 | 23.2 | -1.3 | ADB47148824E45BE8C8045088066FA1A |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Los Banos | CA | 93635-3440 |  | 2012-06-08 | 2012-06-08 13:08 | 2012-06-08 13:08 | CARRIER - 38TH042330 | 96 | 0 | Yes | Yes | 29.5 | 24.7 | 4.8 | BDCF70EC0B7647EDAC9C2808D2AFAF65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3378 |  | 2012-06-15 | 2012-06-15 11:42 | 2012-06-15 12:10 | GOODMAN - CK30-TT | 78 | 6.4 | Yes | Yes | 20.9 | 18.8 | 2.1 | 9FC6E5518F064B97A6C508A392C85DAE |  | R22 | Non-TXV |  | 8.205% | 0.91795 | 15.77% | [5 empty] | Non-TXV | 8.205%
Yuba City | CA | 95993-1607 |  | 2012-06-01 | 2012-06-01 10:16 | 2012-06-01 10:41 | CARRIER - 38T5A036330 | 151 | -5.5 | Yes | Yes | 18 | 20.4 | -2.4 | 6A495E9048164253AE1603F4A7EA7B84 |  | R410A | Non-TXV |  | -3.642% | 1.0364 | 1.02% |  |  |  |  | Non-TXV |  |  | -3.642%
Yuba City | CA | 95993-6020 |  | 2012-06-06 | 2012-06-06 16:29 | 2012-06-06 16:58 | OTHER - HARB-F024SA | 118 | 23.1 | Yes | Yes | 19 | 21.3 | -2.3 | F29840233E3541509CD08EC20482669D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 19.58% | 0.80424 | 37.62% | [5 empty] | Non-TXV | 19.58%
Rocklin | CA | 95677-3480 |  | 2012-06-07 | 2012-06-07 16:12 | 2012-06-07 16:12 | TRANE - YCX036G1M0AA | 109 | 0 | Yes | Yes | 26.6 | 21.2 | 5.4 | 4681E8E1C146448C91B27B9897EA2435 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4885 |  | 2012-07-11 | 2012-07-11 10:25 | 2012-07-11 10:48 | CARRIER - 38CE003300 | 77 | 4.9 | Yes | Yes | 20.4 | 20.4 | 0 | A4C1E75E19A84EF68CCD6C99BD09C8EB |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Rocklin | CA | 95677-3168 |  | 2012-06-01 | 2012-06-01 14:24 | 2012-06-01 14:24 | CARRIER - 38EN018310 | 59 | 0 | Yes | Yes | 17.2 | 18.8 | -1.6 | B8DF3C5CF2724D33811A071B8B5FBD2D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-2613 |  | 2012-06-01 | 2012-06-01 10:40 | 2012-06-01 11:00 | ICP - CA9036VKD1 | 124 | 5.2 | Yes | Yes | 26.1 | 21.3 | 4.8 | 4078539581C642BCA54FEFEA1360E1CE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Rocklin | CA | 95677-3534 |  | 2012-06-07 | 2012-06-07 13:45 | 2012-06-07 14:04 | CARRIER - 38EN018310 | 59 | 2.3 | Yes | Yes | 20 | 19.9 | 0.1 | A7B9F951AC8541D6A6C95387A79E72FE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.898% | 0.96102 | 7.492% | [5 empty] | Non-TXV | 3.898%
Madera | CA | 93638-0423 |  | 2012-06-15 | 2012-06-15 09:15 | 2012-06-15 09:35 | YORK - DCRAF030N054A | 80 | 8.6 | Yes | Yes | 22.6 | 22.5 | 0.1 | E45CD8F3BA1E43889BE72FE82998C293 |  | R22 | Non-TXV |  | 10.75% | 0.8925 | 20.66% | [5 empty] | Non-TXV | 10.75%
Rocklin | CA | 95677-2655 |  | 2012-06-01 | 2012-06-01 10:03 | 2012-06-01 10:03 | TRANE - TTD724B100B0 | 60 | 0 | Yes | Yes | 17.8 | 18.8 | -1 | 73CC09288DF445688C46DA1038159360 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-9309 |  | 2012-06-06 | 2012-06-06 11:48 | 2012-06-06 12:08 | GOODMAN - GPG13240701BB | 77 | 2.3 | Yes | Yes | 24 | 19.5 | 4.5 | FDE7CDAB6636440BA9975A3AD027A987 |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Atwater | CA | 95301-9309 |  | 2012-06-13 | 2012-06-13 10:30 | 2012-06-13 10:56 | LENNOX - CHP15-461-3P | 119 | 4.8 | Yes | Yes | 17.9 | 19.6 | -1.7 | 6411B7716B7941F7918C4418D08ED66D |  | R22 | Non-TXV |  | 4.034% | 0.95966 | 7.752% | [5 empty] | Non-TXV | 4.034%
Yuba City | CA | 95991-2429 |  | 2012-07-26 | 2012-07-26 12:19 | 2012-07-26 12:45 | BRYANT - 582ANW024060AAAD | 60 | -5.6 | Yes | Yes | 25.5 | 22.4 | 3.2 | 1FB5A659DD564736B191CCCD442DFC64 |  | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Yuba City | CA | 95991-8404 |  | 2012-07-10 | 2012-07-10 13:46 | 2012-07-10 13:46 | GOODMAN - CJ30-1FB | 110 | 0 | Yes | Yes | 20.5 | 19.7 | 0.8 | BDAF9AAE014A47DDB1C5245CF9DB307D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-6142 |  | 2012-06-15 | 2012-06-15 14:54 | 2012-06-15 14:54 | DAY & NIGHT - N4A336AKB200 | 82 | 0 | Yes | Yes | 25.9 | 21.3 | 4.6 | E4D91A09493D4DDE9AFF8C0C43BD2564 |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95348-4359 |  | 2012-06-13 | 2012-06-13 10:45 | 2012-06-13 11:08 | RHEEM - RAKA-024JAS | 51 | 1.5 | Yes | Yes | 16.7 | 15.5 | 1.2 | 38E6C72427444E06B6050B420782DA37 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Yuba City | CA | 95991-4377 |  | 2012-07-24 | 2012-07-24 12:33 | 2012-07-24 13:19 | BRYANT - 661CJ024-C | 74 | -4.4 | Yes | Yes | 19 | 18.3 | 0.7 | 607CA11052C04E7383F7C0F44B381729 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Dinuba | CA | 93618-1950 |  | 2012-07-02 | 2012-07-02 12:35 | 2012-07-02 12:52 | RHEEM - N/A | 60 | 11.6 | Yes | Yes | 18.3 | 21.3 | -3 | EAC2D2FC5B424C44B4B9E474361CE7E0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.33% | 0.80667 | 37.15% | [5 empty] | Non-TXV | 19.33%
Rocklin | CA | 95677-2400 |  | 2012-06-01 | 2012-06-01 11:28 | 2012-06-01 11:55 | BDP - 561AJ042-D | 80 | 8.1 | Yes | Yes | 15.4 | 18.2 | -2.8 | 2D1E88AC623947FD9189E84D83BB7448 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.12% | 0.89875 | 19.46% | [5 empty] | Non-TXV | 10.12%
Rocklin | CA | 95677-3526 |  | 2012-07-12 | 2012-07-12 12:37 | 2012-07-12 12:57 | CARRIER - 38EN018310 | 55 | 2.3 | Yes | Yes | 18 | 20.4 | -2.4 | EB2305DA790C4160A4331FFD9B051037 |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
Murphys | CA | 95247-9305 |  | 2012-07-17 | 2012-07-17 10:09 | 2012-07-17 10:26 | BDP - 588ANW036080ACAF | 69 | -4.1 | Yes | Yes | 24.6 | 18.7 | 5.9 | D06C1C21839F4EF2BD76A196A0DE0DF3 |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Penn Valley | CA | 95946-9315 |  | 2012-06-15 | 2012-06-15 10:03 | 2012-06-15 10:03 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 22.1 | 19.1 | 3 | B0FC02B2544B48E78DBED598F3FC995C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sonora | CA | 95370-5756 |  | 2012-07-23 | 2012-07-23 09:52 | 2012-07-23 10:15 | TRANE - YCX048F1H0BB | 162 | -11.4 | Yes | Yes | 19 | 18.7 | 0.3 | ACD6C5C4513447A3A35B220824909C4B |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Sonora | CA | 95370-5741 |  | 2012-07-23 | 2012-07-23 12:24 | 2012-07-23 12:40 | RUUD - UAPC-048JAZ | 228 | 7.2 | Yes | Yes | 20.9 | 19.7 | 1.2 | DF2C517F3AF5485CA04E1E2675C58D11 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Penn Valley | CA | 95946-8806 |  | 2012-06-15 | 2012-06-15 12:00 | 2012-06-15 12:17 | BDP - 541B034SHR | 85 | 6.1 | Yes | Yes | 18 | 20 | -2 | 7A5C2D4D92784A5A9A768FE4DE7811CB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Sonora | CA | 95370-6936 |  | 2012-07-23 | 2012-07-23 09:13 | 2012-07-23 09:32 | PAYNE - PH13NR018-K | 85 | 3.3 | Yes | Yes | 17.4 | 18.7 | -1.3 | 7142C19F69B84D7F94B7D5C88BB2CF33 |  | R22 | TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | TXV | 3.882%
Merced | CA | 95340-3962 |  | 2012-06-01 | 2012-06-01 09:30 | 2012-06-01 09:52 | GOODMAN - CK241B | 71 | 2.4 | Yes | Yes | 21.1 | 21.4 | -0.3 | 7E8283F516BE433F8DCA3855F27571EF |  | R22 | Non-TXV |  | 3.38% | 0.9662 | 6.496% | [5 empty] | Non-TXV | 3.38%
Los Banos | CA | 93635-0000 |  | 2012-06-08 | 2012-06-08 14:47 | 2012-06-08 15:15 | BRYANT - 589ANW036060ADAF | 84 | -3.4 | Yes | Yes | 26 | 21.5 | 4.5 | FBDAE64409E146BEBEE83266A186ABD0 | OK: Verified Refrigerant Charge Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -4.048% | 1.0405 | 1.134% |  |  |  |  | TXV |  |  | -4.048%
Merced | CA | 95348-3036 |  | 2012-07-05 | 2012-07-05 09:00 | 2012-07-05 09:17 | BDP - 56505B18 | 60 | 2.8 | Yes | Yes | 18.6 | 20.4 | -1.8 | 7677395F367149A4BBA591740B1C8812 |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Merced | CA | 95348-3036 |  | 2012-06-15 | 2012-06-15 13:50 | 2012-06-15 14:16 | DAY & NIGHT - UNK | 70 | 3.8 | Yes | Yes | 21.1 | 19.5 | 1.6 | EB5C8F12A8E847D7864B08775889EEC8 |  | R22 | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Yuba City | CA | 95993-3585 |  | 2012-06-01 | 2012-06-01 09:38 | 2012-06-01 09:56 | KENMORE - UNK | 71 | 6.1 | Yes | Yes | 19 | 19.5 | -0.5 | E2FB153CECCD4ECF97A3A1FB80F3C99A |  | R22 | Non-TXV |  | 8.592% | 0.91408 | 16.51% | [5 empty] | Non-TXV | 8.592%
Yuba City | CA | 95993-7681 |  | 2012-06-11 | 2012-06-11 11:51 | 2012-06-11 11:51 | BRYANT - 561CJ048-A | 106 | 0 | Yes | Yes | 20.2 | 21.5 | -1.3 | 0E047D286FB54B5B8418E4BBC8143CAE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3385 |  | 2012-07-06 | 2012-07-06 13:50 | 2012-07-06 14:06 | BDP - 5658J018 | 85 | 3 | Yes | Yes | 18.8 | 19.5 | -0.7 | 7ABE564751B545E88FC0CC9088757182 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Merced | CA | 95340-0646 |  | 2012-06-12 | 2012-06-12 10:16 | 2012-06-12 10:16 | OTHER - 80WR30E1NA | 53 | 9 | Yes | Yes | 25 | 21.9 | 3.1 | 479E686549CE41CBB0200F3542C38090 | Add refrigerant: 9 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.98% | 0.83019 | 32.63% | [5 empty] | Non-TXV | 16.98%
Yuba City | CA | 95993-6048 |  | 2012-06-01 | 2012-06-01 15:06 | 2012-06-01 15:31 | DAY & NIGHT - 591ANX036000AAAA | 87 | 5.3 | Yes | Yes | 25 | 20.4 | 4.6 | 07B8C4259B1E4BF493212CA8D677BF2B |  | R22 | Non-TXV |  | 6.092% | 0.93908 | 11.71% | [5 empty] | Non-TXV | 6.092%
Merced | CA | 95348-3035 |  | 2012-07-03 | 2012-07-03 13:30 | 2012-07-03 13:52 | UNITARY PRODUCTS GROUP - C1018BBD1V | 58 | 4.5 | Yes | Yes | 16.8 | 19.8 | -3 | B93C5CB5C02240F0BF4A5064CAE59281 |  | R22 | Non-TXV |  | 7.759% | 0.92241 | 14.91% | [5 empty] | Non-TXV | 7.759%
Atwater | CA | 95301-4461 |  | 2012-06-11 | 2012-06-11 14:06 | 2012-06-11 14:32 | AMERICAN STANDARD - YCC024F1L0BB | 64 | 1.9 | Yes | Yes | 17.5 | 19.3 | -1.8 | 76E2B8E2BF9D487781404C5CF4A81768 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Chico | CA | 95926-2415 |  | 2012-06-01 | 2012-06-01 10:13 | 2012-06-01 10:13 | GOODMAN - PGJ030050-1 | 72 | 0 | Yes | Yes | 23.4 | 21.7 | 1.7 | B5DDCE83E6C2400986B627C108E4255E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4879 |  | 2012-06-14 | 2012-06-14 12:09 | 2012-06-14 12:31 | RHEEM - UNK | 80 | 4.3 | Yes | Yes | 20.1 | 20.1 | 0 | 5688B92D1BD54209BA4D7573B3727BF9 |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Atwater | CA | 95301-4879 |  | 2012-06-14 | 2012-06-14 09:31 | 2012-06-14 09:47 | GOODMAN - CK30-1B | 71 | 3.3 | Yes | Yes | 18.6 | 19.8 | -1.2 | B38526F259434361A9CDA9821CE9F8AD |  | R22 | Non-TXV |  | 4.648% | 0.95352 | 8.932% | [5 empty] | Non-TXV | 4.648%
Paradise | CA | 95969-6254 |  | 2012-06-11 | 2012-06-11 09:33 | 2012-06-11 10:04 | DAY N NIGHT - 657ANX036000ABAF | 89 | 4.3 | Yes | Yes | 20.7 | 22.2 | -1.5 | F76C23FE27AF4A3DB649396463229318 |  | R22 | Non-TXV |  | 4.831% | 0.95169 | 9.285% | [5 empty] | Non-TXV | 4.831%
Orland | CA | 95963-1841 |  | 2012-07-05 | 2012-07-05 09:15 | 2012-07-05 09:39 | LENNOX - HS18-411-8P | 68 | 6.6 | Yes | Yes | 24.2 | 21.7 | 2.6 | 540F4FE3D426438BA222A7BB9DF660DF |  | R22 | Non-TXV |  | 9.706% | 0.90294 | 18.65% | [5 empty] | Non-TXV | 9.706%
Stockton | CA | 95206-2935 |  | 2012-06-20 | 2012-06-20 11:49 | 2012-06-20 12:06 | RHEEM - RRNL-B024JK06X | 78 | 5 | Yes | Yes | 22.1 | 20.4 | 1.7 | E2B5F90EEB2F471FA623865E7A6DE68C |  | R410A | Non-TXV |  | 6.41% | 0.9359 | 12.32% | [5 empty] | Non-TXV | 6.41%
Merced | CA | 95348-3038 |  | 2012-06-08 | 2012-06-08 11:45 | 2012-06-08 12:02 | OTHER - UNK | 55 | 3.4 | Yes | Yes | 21.9 | 19.1 | 2.8 | 578D422BF0924102B4BB723043FAE0AC |  | R22 | Non-TXV |  | 6.182% | 0.93818 | 11.88% | [5 empty] | Non-TXV | 6.182%
Winton | CA | 95388-9262 |  | 2012-06-07 | 2012-06-07 12:31 | 2012-06-07 12:50 | OTHER - GCGD36S41S3A | 73 | 2.2 | Yes | Yes | 16.3 | 18 | -1.7 | BB2EDD1812ED4F24870A53FD36D70542 |  | R410A | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Yuba City | CA | 95991-1218 |  | 2012-06-11 | 2012-06-11 10:34 | 2012-06-11 10:34 | BRYANT - 582ANW024040NAAD | 56 | 0 | Yes | Yes | 22.2 | 21.2 | 1 | 13138CB00BEC4B3398FD47099BF5D78D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5112 |  | 2012-06-01 | 2012-06-01 10:00 | 2012-06-01 10:21 | PAYNE - PY1PNB036060AAAA | 56 | 5.9 | Yes | Yes | 20.5 | 19 | 1.5 | 2B7DF58145E34BBE855C584D5581647F |  | R22 | Non-TXV |  | 10.54% | 0.89464 | 20.25% | [5 empty] | Non-TXV | 10.54%
Plumas Lake | CA | 95961-9130 |  | 2012-07-30 | 2012-07-30 11:26 | 2012-07-30 11:47 | CARRIER - 38BRC036350 | 100 | -9.4 | Yes | Yes | 15 | 17.9 | -2.9 | 459AFA8B69F44C709884388CD2A34027 |  | R22 | Non-TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.4%
Magalia | CA | 95954-9325 |  | 2012-05-31 | 2012-05-31 14:11 | 2012-05-31 14:51 | BRYANT - 163ANA042-B | 125 | 5.4 | Yes | Yes | 21.2 | 21.5 | -0.3 | 993529BA03A2468299B0A2A9F957FFAF |  | R410A | Non-TXV |  | 4.32% | 0.9568 | 8.302% | [5 empty] | Non-TXV | 4.32%
Atwater | CA | 95301-4871 |  | 2012-07-03 | 2012-07-03 11:05 | 2012-07-03 11:05 | - | 85 | 0 | Yes | Yes | 9.8 | 20.4 | -10.6 | E40327B6084A4FD990555FED401AA459 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3447 |  | 2012-06-12 | 2012-06-12 13:17 | 2012-06-12 13:34 | GE - BTR724A100A1 | 70 | 2.2 | Yes | Yes | 22.5 | 21 | 1.5 | E7A606056B5A4B64BEEE15530651A10B |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Yuba City | CA | 95993-7111 |  | 2012-06-08 | 2012-06-08 15:14 | 2012-06-08 15:40 | BRYANT - 582ANW030060AAAD | 55 | 6 | Yes | Yes | 20 | 22.6 | -2.6 | DE01103CE59847F88E6D167E7C0E0F34 |  | R22 | Non-TXV |  | 10.91% | 0.89091 | 20.96% | [5 empty] | Non-TXV | 10.91%
Winton | CA | 95388-9326 |  | 2012-06-13 | 2012-06-13 08:31 | 2012-06-13 08:49 | RHEEM - 13AJA24A01 | 85 | 2.5 | Yes | Yes | 17.3 | 18.7 | -1.4 | 207A7F2F419C40BBBFC9AA2295A117D1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Sonora | CA | 95370-8138 |  | 2012-07-23 | 2012-07-23 11:36 | 2012-07-23 11:53 | BDP - 588ANW060100AEAG | 112 | 3.6 | Yes | Yes | 22.7 | 19.7 | 3 | FD9011025AE048DD8391E25BAFA0C281 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Stockton | CA | 95205-5672 |  | 2012-07-18 | 2012-07-18 09:37 | 2012-07-18 10:00 | RHEEM - RRKA-A030JKO8X | 54 | 6.9 | Yes | Yes | 15.6 | 18 | -2.4 | 3A7C24D18D7D46F4A583B6FEC5F590DB |  | R22 | TXV |  | 12.78% | 0.87222 | 24.56% | [5 empty] | TXV | 12.78%
Manteca | CA | 95337-6048 |  | 2012-06-01 | 2012-06-01 14:30 | 2012-06-01 15:18 | YORK - UNK | 54 | 15.7 | Yes | Yes | 20.6 | 19.8 | 0.8 | 0707A603699D46DF9BD23EC1F4B670C1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 29.07% | 0.70926 | 55.87% | [5 empty] | Non-TXV | 29.07%
Marysville | CA | 95901-3508 |  | 2012-06-07 | 2012-06-07 14:40 | 2012-06-07 15:08 | OTHER - UNK | 44 | 13.4 | Yes | Yes | 26 | 23.1 | 2.9 | 2EA74E6F6C5545DB87E7F33E7DBDD97F |  | R22 | Non-TXV |  | 30.45% | 0.69545 | 58.53% | [5 empty] | Non-TXV | 30.45%
Yuba City | CA | 95993-5214 |  | 2012-06-06 | 2012-06-06 14:31 | 2012-06-06 14:31 | RHEEM - AT-38B1 Q | 45 | 0 | Yes | Yes | 16.7 | 19.6 | -2.9 | AE1283660CF54AFC8E81A676C1542CA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-3517 |  | 2012-06-06 | 2012-06-06 12:21 | 2012-06-06 12:21 | CARRIER - 48GS-048115301-- | 82 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | 0F61E56807DD49E3B5B4193D652B6C07 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-8815 |  | 2012-06-11 | 2012-06-11 11:15 | 2012-06-11 11:35 | CARRIER - 38QH042310 | 194 | 7.5 | Yes | Yes | 21.8 | 19 | 2.8 | 86A43ED6FB6942978E0DD0717ACD8CE0 |  | R22 | Non-TXV |  | 3.866% | 0.96134 | 7.43% | [5 empty] | Non-TXV | 3.866%
Manteca | CA | 95337-4376 |  | 2012-06-01 | 2012-06-01 10:35 | 2012-06-01 10:52 | TRANE - BTD730A100A0 | 74 | 2.4 | Yes | Yes | 19.3 | 20.1 | -0.8 | 1C1C0AA5C1504BBD87648B6CABB77FC1 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Lincoln | CA | 95648-9748 |  | 2012-07-11 | 2012-07-11 12:00 | 2012-07-11 12:00 | RUUD - 13PJL48A01 | 141 | 0 | Yes | Yes | 24.9 | 22 | 2.9 | 5E8D0632F4034B9F9A7A964223366250 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-5651 |  | 2012-06-01 | 2012-06-01 15:41 | 2012-06-01 15:58 | RUUD - UNK | 80 | 4.3 | Yes | Yes | 28 | 22.1 | 5.9 | D7B58B73DC9445F38DFF8C58C1A56321 |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Merced | CA | 95340-5048 |  | 2012-06-01 | 2012-06-01 08:26 | 2012-06-01 08:46 | GOODMAN - PGB0300501 | 56 | 4.6 | Yes | Yes | 18.4 | 18.7 | -0.3 | 1A9D684A00B347A79CC55F958E7CFA00 |  | R22 | Non-TXV |  | 8.214% | 0.91786 | 15.79% | [5 empty] | Non-TXV | 8.214%
Stockton | CA | 95210-2352 |  | 2012-06-13 | 2012-06-13 11:38 | 2012-06-13 11:54 | HEIL - PGAA24C1K1 | 64 | 2.2 | Yes | Yes | 19.5 | 18.8 | 0.7 | E359BF52C8F3430ABD02607C82F1660B |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Merced | CA | 95340-2310 |  | 2012-06-06 | 2012-06-06 12:30 | 2012-06-06 13:03 | AMANA - RCE24C2D | 130 | -4.7 | Yes | Yes | 18 | 18.8 | -0.8 | D5668988C9A74ECF8CACF050CF783EE9 |  | R22 | TXV |  | -3.615% | 1.0362 | 1.012% |  |  |  |  | TXV |  |  | -3.615%
Merced | CA | 95340-5047 |  | 2012-06-13 | 2012-06-13 11:44 | 2012-06-13 12:02 | AIRE-FLO - 585HJ024040 | 68 | 11.2 | Yes | Yes | 22.6 | 23 | -0.4 | 6378837EA3AB493BB0365A9388E75F49 |  | R22 | Non-TXV |  | 16.47% | 0.83529 | 31.65% | [5 empty] | Non-TXV | 16.47%
Auburn | CA | 95603-3313 |  | 2012-06-06 | 2012-06-06 14:52 | 2012-06-06 14:52 | OTHER - 561CJX03000ACAA | 71 | 0 | Yes | Yes | 1 | 18.2 | -17.2 | 62CDF09BA2A3452AB31928E3A7F0448D | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3037 |  | 2012-06-07 | 2012-06-07 13:37 | 2012-06-07 13:53 | BDP - UNK | 60 | 2.2 | Yes | Yes | 26.2 | 22 | 4.2 | BF5652499D3E44C085BEDD71152DFF89 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Red Bluff | CA | 96080-3331 |  | 2012-06-06 | 2012-06-06 12:00 | 2012-06-06 12:45 | COLEMAN - CLJ36-1A | 109 | 3.3 | Yes | Yes | 26.8 | 21.4 | 5.4 | 59ECBCAD2D274DCB92D61F8B1C406100 |  | R22 | Non-TXV |  | 3.028% | 0.96972 | 5.818% | [5 empty] | Non-TXV | 3.028%
Merced | CA | 95348-3037 |  | 2012-06-15 | 2012-06-15 13:32 | 2012-06-15 13:48 | WEATHER KING - 13AJ18A01 | 67 | 4.9 | Yes | Yes | 21.4 | 19.3 | 2.1 | E363AA68403D45508E521B25F57ABE01 |  | R22 | Non-TXV |  | 7.313% | 0.92687 | 14.05% | [5 empty] | Non-TXV | 7.313%
Stockton | CA | 95219-3111 |  | 2012-06-19 | 2012-06-19 10:56 | 2012-06-19 11:19 | RHEEM - AT-30B1 0 | 56 | 5 | Yes | Yes | 15.4 | 17.7 | -2.3 | 2E4265B8F3CE4A608BBC6771044B7E20 |  | R22 | Non-TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | Non-TXV | 8.929%
Paradise | CA | 95969-2408 |  | 2012-07-06 | 2012-07-06 10:17 | 2012-07-06 10:52 | RHEEM - RAFD-030JAS | 69 | 13.9 | Yes | Yes | 23 | 21.8 | 1.2 | 128F9729EAEF445C8E019E360D4EACB2 |  | R22 | Non-TXV |  | 20.14% | 0.79855 | 38.71% | [5 empty] | Non-TXV | 20.14%
Burson | CA | 95225-0000 |  | 2012-07-16 | 2012-07-16 12:25 | 2012-07-16 12:44 | YORK - BRCS0481BD | 117 | 3.4 | Yes | Yes | 21.2 | 19.3 | 1.9 | 4B80351BF36A4E3BAEFEB48243FF5808 |  | R22 | Non-TXV |  | 2.906% | 0.97094 | 5.585% | [5 empty] | Non-TXV | 2.906%
Atwater | CA | 95301-2678 |  | 2012-06-01 | 2012-06-01 12:27 | 2012-06-01 12:47 | RHEEM - RRNL-B036JK06X | 93 | 2.8 | Yes | Yes | 21.6 | 18.8 | 2.8 | D597B071476C4C4FB741A222854D36FB |  | R410A | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Yuba City | CA | 95991-1839 |  | 2012-07-20 | 2012-07-20 11:11 | 2012-07-20 11:27 | PAYNE - PA10JA024-C | 64 | 9.4 | Yes | Yes | 20 | 19 | 1 | B61AF4983C37463AA28264DD791D405F |  | R22 | Non-TXV |  | 14.69% | 0.85313 | 28.23% | [5 empty] | Non-TXV | 14.69%
Cameron Park | CA | 95682-7615 |  | 2012-07-26 | 2012-07-26 12:39 | 2012-07-26 13:00 | GOODMAN - CPLE30-1A | 104 | -7.3 | Yes | Yes | 19.4 | 19.3 | 0.1 | 6482FEA030C3422EA89AEFE0741161F1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.019% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.019%
Chico | CA | 95973-0887 |  | 2012-08-01 | 2012-08-01 10:18 | 2012-08-01 10:47 | PAYNE - PH10JAO18-C | 71 | 7.8 | Yes | Yes | 24 | 20.3 | 3.7 | 86F136499FAE4E0391E009165BC88FF5 |  | R22 | Non-TXV |  | 10.99% | 0.89014 | 21.11% | [5 empty] | Non-TXV | 10.99%
Marysville | CA | 95901-3946 |  | 2012-06-07 | 2012-06-07 12:50 | 2012-06-07 12:50 | LENNOX - HSNXA19-048-230-01 | 141 | 0 | Yes | Yes | 21 | 18.8 | 2.2 | C1D41BC148734D41B032DCDB896B76A3 |  | R410A | TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-1003 |  | 2012-06-11 | 2012-06-11 09:41 | 2012-06-11 10:01 | AMERICAN STANDARD - YCC048F1MOBF | 100 | 5.1 | Yes | Yes | 19.5 | 21.3 | -1.8 | 73FA9ED487DC46CB9BEBB4E830170713 |  | R22 | Non-TXV |  | 5.1% | 0.949 | 9.801% | [5 empty] | Non-TXV | 5.1%
Stockton | CA | 95219-3513 |  | 2012-06-11 | 2012-06-11 13:41 | 2012-06-11 13:59 | GMC - VSC130361AA | 119 | 6.4 | Yes | Yes | 17.4 | 20.4 | -3 | EEE97D6846A8431FACB26746EA56275F |  | R22 | Non-TXV |  | 5.378% | 0.94622 | 10.34% | [5 empty] | Non-TXV | 5.378%
Atwater | CA | 95301-2526 |  | 2012-07-05 | 2012-07-05 10:58 | 2012-07-05 11:20 | GE - NA | 47 | 1.4 | Yes | Yes | 18.6 | 19.4 | -0.8 | 942699E31B5A4C6A9F31404079A2B669 |  | R22 | Non-TXV |  | 2.979% | 0.97021 | 5.724% | [5 empty] | Non-TXV | 2.979%
Merced | CA | 95348-3025 |  | 2012-06-07 | 2012-06-07 10:06 | 2012-06-07 10:34 | OTHER - UNK | 56 | 1.7 | Yes | Yes | 18 | 20.7 | -2.7 | 7D8C435E518A47DA9DBA544E3F1085C4 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Merced | CA | 95348-2706 |  | 2012-06-08 | 2012-06-08 13:38 | 2012-06-08 13:58 | YORK - DZN048N09006NXA | 137 | 5.3 | Yes | Yes | 17.4 | 19.8 | -2.4 | 68E9CA3A23124ECB86B21AF40B5FE154 |  | R410A | Non-TXV |  | 3.869% | 0.96131 | 7.435% | [5 empty] | Non-TXV | 3.869%
Stockton | CA | 95203-1323 |  | 2012-07-02 | 2012-07-02 09:16 | 2012-07-02 09:35 | RHEEM - RRNL-B042JK08X | 112 | 5.9 | Yes | Yes | 18.8 | 20.2 | -1.4 | 0AFF8D0CA82A40A4A9BFEA3C77E631AB |  | R410A | Non-TXV |  | 5.268% | 0.94732 | 10.12% | [5 empty] | Non-TXV | 5.268%
Los Banos | CA | 93635-3069 |  | 2012-06-06 | 2012-06-06 14:17 | 2012-06-06 14:38 | AIRE-FLO - JS3BC024KA | 63 | 6.5 | Yes | Yes | 24 | 23.1 | 0.9 | 5D440A8CF0BC479CB9F4D97B8D9DE84B |  | R22 | Non-TXV |  | 10.32% | 0.89683 | 19.83% | [5 empty] | Non-TXV | 10.32%
Rocklin | CA | 95677-2316 |  | 2012-06-12 | 2012-06-12 11:23 | 2012-06-12 11:23 | TRANE - TTR042D100B0 | 81 | 0 | Yes | Yes | 0.3 | 20.7 | -20.4 | 41A4B0815E9140E0B06CD41FCD036783 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3529 |  | 2012-06-01 | 2012-06-01 16:03 | 2012-06-01 16:03 | GOODMAN - CK8-1B | 59 | 0 | Yes | Yes | 16.1 | 18.7 | -2.6 | EA44BC6809F84C3683C83433091E9109 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-5270 |  | 2012-06-11 | 2012-06-11 13:20 | 2012-06-11 13:38 | DAY & NIGHT - 567024RCU | 60 | 5.1 | Yes | Yes | 20.5 | 20.5 | 0 | 0039DC44309D452FA68B578B1C7F280C |  | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Yuba City | CA | 95991-6601 |  | 2012-06-14 | 2012-06-14 13:30 | 2012-06-14 13:51 | - 591ANX024A | 60 | 2.5 | Yes | Yes | 23 | 22.5 | 0.5 | CDB63349CACC4AB782494F833B68ECEF |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Newman | CA | 95360-1812 |  | 2012-06-14 | 2012-06-14 09:07 | 2012-06-14 09:38 | PAYNE - NA | 60 | 1.9 | Yes | Yes | 19.6 | 19.6 | 0 | 614EAB08D2194A098DAD07C4A2528C4D |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Yuba City | CA | 95993-9006 |  | 2012-06-06 | 2012-06-06 11:22 | 2012-06-06 11:22 | CARRIER - 38BRC042330 | 108 | 0 | Yes | Yes | 17.6 | 19.5 | -1.9 | FCA2E70BB2C540F096401A1E07669B7D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-2430 |  | 2012-06-11 | 2012-06-11 11:52 | 2012-06-11 12:12 | RHEEM - RAKA-042JAZ | 79 | -6.5 | Yes | Yes | 23.1 | 19.9 | 3.2 | 9C6B49F834624DC9833C5118301F1CE1 |  | R22 | Non-TXV |  | -8.228% | 1.0823 | 2.304% |  |  |  |  | Non-TXV |  |  | -8.228%
Newman | CA | 95360-1819 |  | 2012-06-14 | 2012-06-14 10:00 | 2012-06-14 10:18 | PAYNE - 584ANW030040 | 56 | 1.6 | Yes | Yes | 20.8 | 19.9 | 0.9 | FB5B4B777340491FAA314F3BB36B0291 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Yuba City | CA | 95991-4959 |  | 2012-06-13 | 2012-06-13 13:09 | 2012-06-13 13:30 | DAY & NIGHT - 565BJO36 | 80 | 9.5 | Yes | Yes | 16 | 18.8 | -2.8 | F178064B46E9404BA7E600A286331EE2 |  | R22 | Non-TXV |  | 11.88% | 0.88125 | 22.82% | [5 empty] | Non-TXV | 11.88%
Manteca | CA | 95336-2971 |  | 2012-05-31 | 2012-05-31 15:15 | 2012-05-31 15:15 | COLEMAN - DRC80361BB | 55 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 950F5DC0BE2A4BB2B356952D17B9EC62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-5221 |  | 2012-06-11 | 2012-06-11 14:13 | 2012-06-11 14:33 | DAY & NIGHT - UNK | 96 | 19 | Yes | Yes | 20.4 | 21.5 | -1.1 | A276E42D2E8C4C45AA593DD07E63C7B9 |  | R22 | Non-TXV |  | 19.79% | 0.80208 | 38.04% | [5 empty] | Non-TXV | 19.79%
Stockton | CA | 95210-0000 |  | 2012-06-01 | 2012-06-01 09:41 | 2012-06-01 10:00 | RUUD - UAPC-036JAZ | 160 | -9.4 | Yes | Yes | 25.9 | 20 | 6 | A2F9696C951841E78D41772775499C8F |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Yuba City | CA | 95991-4318 |  | 2012-06-11 | 2012-06-11 11:09 | 2012-06-11 11:26 | DAY & NIGHT - UNK | 85 | 4.6 | Yes | Yes | 21 | 20.8 | 0.2 | 053B1F4C59444FC29F1935C807ABEEB4 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Merced | CA | 95348-3302 |  | 2012-06-15 | 2012-06-15 07:58 | 2012-06-15 08:20 | GOODMAN - GPG1324045M41AB | 80 | 2.4 | Yes | Yes | 22.5 | 18.2 | 4.3 | 06D3E7A4FFAC454D8A374BD773E46436 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Valley Springs | CA | 95252-0000 |  | 2012-07-05 | 2012-07-05 14:33 | 2012-07-05 14:52 | TRANE - TTR060C100A2 | 146 | 4.4 | Yes | Yes | 27.4 | 22.1 | 5.3 | E3FC9A324BB04AEDA3801986C33F9E07 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Merced | CA | 95348-3371 |  | 2012-06-08 | 2012-06-08 10:33 | 2012-06-08 10:51 | RHEEM - RRKAA030JK06X | 56 | 1.8 | Yes | Yes | 19.2 | 19.9 | -0.7 | 9D560EB3CE3C4FC8B35FA8275D6C145A |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Newman | CA | 95360-1735 |  | 2012-06-14 | 2012-06-14 08:24 | 2012-06-14 08:44 | OTHER - RCE36ECA | 225 | 6.8 | Yes | Yes | 22.6 | 20.2 | 2.5 | 365CD39ABBFE475D9BBB4897B20E4B89 |  | R22 | Non-TXV |  | 3.022% | 0.96978 | 5.808% | [5 empty] | Non-TXV | 3.022%
Manteca | CA | 95336-5909 |  | 2012-06-01 | 2012-06-01 11:16 | 2012-06-01 11:41 | GOODMAN - CKL24-1L | 76 | 2.8 | Yes | Yes | 19.1 | 21 | -1.9 | C81110CB6E764D92BE998932CB329542 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Yuba City | CA | 95991-5807 |  | 2012-06-14 | 2012-06-14 09:59 | 2012-06-14 09:59 | CARRIER - 48GX-036090301AD | 82 | 0 | Yes | Yes | 20 | 19.3 | 0.7 | FB6572F555ED4AE09DE4B6BB508BB990 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-5452 |  | 2012-07-02 | 2012-07-02 13:08 | 2012-07-02 13:30 | DAY & NIGHT - 585HJW024040ABAE | 68 | -6.4 | Yes | Yes | 21 | 21.2 | -0.2 | 41295BAB2AB6439C804DB6AB07CF02BD |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Marysville | CA | 95901-5226 |  | 2012-07-02 | 2012-07-02 12:27 | 2012-07-02 12:47 | HEIL - PGAA29C1K1 | 74 | -7 | Yes | Yes | 20.9 | 18 | 2.9 | 3C582D4D9A354F3FB3B97272F0EA1968 |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Stockton | CA | 95219-3229 |  | 2012-06-11 | 2012-06-11 09:59 | 2012-06-11 10:16 | OTHER - N2A324AKA200 | 71 | 2.7 | Yes | Yes | 17.9 | 20.8 | -2.9 | 11644EB853DF46B79A5FFCBDA8148B6A |  | R22 | TXV |  | 3.803% | 0.96197 | 7.308% | [5 empty] | TXV | 3.803%
Placerville | CA | 95667-8208 |  | 2012-06-13 | 2012-06-13 12:48 | 2012-06-13 12:48 | CARRIER - 541DB048 | 174 | 0 | Yes | Yes | 23.8 | 20.2 | 3.6 | DC8CBA748D4F412DBE4783D9011FB17D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-8874 |  | 2012-07-05 | 2012-07-05 10:00 | 2012-07-05 10:17 | BRYANT - 561CJ036-D | 84 | -4.9 | Yes | Yes | 18.3 | 18.7 | -0.4 | B00E16CFEF854EE6B0D8C0901CB2F09B |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Valley Springs | CA | 95252-9216 |  | 2012-07-06 | 2012-07-06 09:49 | 2012-07-06 10:07 | BRYANT - 574DNWA24060NA | 78 | 2.5 | Yes | Yes | 25.3 | 19.8 | 5.5 | CB3681C0FC344FD3A5887D651EB5DAA3 |  | R410A | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Lincoln | CA | 95648-8493 |  | 2012-07-11 | 2012-07-11 10:10 | 2012-07-11 10:10 | YORK - H2RC024S06A | 71 | 0 | Yes | Yes | 18.9 | 20.1 | -1.2 | 55DCB8565D1C475C86A017ED60664546 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1347 |  | 2012-06-06 | 2012-06-06 11:14 | 2012-06-06 11:32 | RUUD - URMA-A042JK08X | 114 | 6.8 | Yes | Yes | 19.6 | 20.9 | -1.3 | A2C6839D6F8F4C9DB073613AF98F5C0B |  | R22 | Non-TXV |  | 5.965% | 0.94035 | 11.46% | [5 empty] | Non-TXV | 5.965%
Chico | CA | 95928-6043 |  | 2012-07-03 | 2012-07-03 12:13 | 2012-07-03 12:13 | OTHER - ATH0220100CLG | 59 | 0 | Yes | Yes | 18.8 | 20.7 | -1.9 | BF33007661994DFC94A2915FE254BA0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3300 |  | 2012-06-12 | 2012-06-12 10:44 | 2012-06-12 11:08 | CARRIER - 48SS-024060331 | 40 | 1.3 | Yes | Yes | 24 | 20.8 | 3.2 | E255DFE3453D4C7EAEAC0F79F57EA0EA |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Paradise | CA | 95969-6323 |  | 2012-06-11 | 2012-06-11 14:25 | 2012-06-11 17:46 | BRYANT - 574DNWA36060NA | 100 | 6.5 | Yes | Yes | 23.2 | 23.1 | 0.1 | C0617629C62144D0A817F1D46ECCCEB1 |  | R410A | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Manteca | CA | 95337-8572 |  | 2012-06-06 | 2012-06-06 12:15 | 2012-06-06 12:34 | TRANE - TTB060D100A0 | 131 | 5.3 | Yes | Yes | 22.1 | 20.4 | 1.7 | BA9207E43D9741BCBA553B792867826B |  | R22 | Non-TXV |  | 4.046% | 0.95954 | 7.775% | [5 empty] | Non-TXV | 4.046%
Chico | CA | 95928-7520 |  | 2012-06-11 | 2012-06-11 13:15 | 2012-06-11 13:33 | TRANE - YCC024F1LOBJ | 67 | 6.3 | Yes | Yes | 19.4 | 21.8 | -2.4 | 51A0AE3EE3354153BAFD916409FDB426 |  | R22 | Non-TXV |  | 9.403% | 0.90597 | 18.07% | [5 empty] | Non-TXV | 9.403%
Lincoln | CA | 95648-8510 |  | 2012-07-11 | 2012-07-11 12:49 | 2012-07-11 13:06 | GOODMAN - VSH130481AA | 223 | 19.8 | Yes | Yes | 19.4 | 21 | -1.6 | C4336A616F734581A6F16C71F37579FE |  | R22 | Non-TXV |  | 8.879% | 0.91121 | 17.06% | [5 empty] | Non-TXV | 8.879%
Lincoln | CA | 95648-8526 |  | 2012-07-11 | 2012-07-11 11:19 | 2012-07-11 11:19 | PAYNE - PA13NA036-C | 75 | 0 | Yes | Yes | 21.5 | 19.3 | 2.2 | 0A49E69FED0A4629847CF92E5031A2D6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-2620 |  | 2012-06-12 | 2012-06-12 10:33 | 2012-06-12 10:33 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 17.8 | 19.7 | -1.9 | 273500CD43C0481F8CC6C1CDFF668697 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3320 |  | 2012-07-10 | 2012-07-10 10:23 | 2012-07-10 10:46 | CARRIER - 38CKC024320 | 72 | 2.8 | Yes | Yes | 19 | 21.4 | -2.4 | 2E048DD1554E428D8A477063042E54BD |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Chico | CA | 95928-7520 |  | 2012-06-13 | 2012-06-13 18:39 | 2012-06-13 19:01 | OTHER - ATH022C100CRE | 58 | 6.3 | Yes | Yes | 22.6 | 19.8 | 2.8 | 829945FA4F9644859AA799F6F72E2EB2 |  | R22 | Non-TXV |  | 10.86% | 0.89138 | 20.87% | [5 empty] | Non-TXV | 10.86%
Willows | CA | 95988-2021 |  | 2012-06-12 | 2012-06-12 11:58 | 2012-06-12 12:34 | ALLEGIANCE - 7A2042A100A0 | 152 | 8.8 | Yes | Yes | 19.7 | 22.3 | -2.6 | C1A301254CFD4EF2A09C1A625BF18FD9 |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Lincoln | CA | 95648-9617 |  | 2012-07-06 | 2012-07-06 13:01 | 2012-07-06 13:22 | RHEEM - RRKA-A036JK06X | 62 | 5.6 | Yes | Yes | 19.4 | 19.8 | -0.4 | 38851C62FA904E00A173E6ABE3A471F9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.032% | 0.90968 | 17.36% | [5 empty] | Non-TXV | 9.032%
Lincoln | CA | 95648-9617 |  | 2012-07-06 | 2012-07-06 13:26 | 2012-07-06 13:26 | RHEEM - RRKA-A036JK08E | 62 | 0 | Yes | Yes | 20.5 | 20.1 | 0.4 | 7B770A91463D4D64916B4D95BD7CFD3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5923 |  | 2012-06-20 | 2012-06-20 15:12 | 2012-06-20 15:29 | OTHER - 38CKC048300 | 102 | 4.9 | Yes | Yes | 20.9 | 21 | -0.1 | EAA4EFD2DC584136B10D1C35E403E528 |  | R22 | TXV |  | 4.804% | 0.95196 | 9.232% | [5 empty] | TXV | 4.804%
Stockton | CA | 95206-5912 |  | 2012-06-08 | 2012-06-08 16:27 | 2012-06-08 16:47 | CARRIER - 38CKC060300 | 153 | 8.5 | Yes | Yes | 19.2 | 21.3 | -2.1 | CE6176FDDFBD4049AB6B81AD319649FA |  | R22 | TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | TXV | 5.556%
Loomis | CA | 95650-9550 |  | 2012-06-12 | 2012-06-12 12:39 | 2012-06-12 12:55 | RHEEM - UNK | 65 | 2.9 | Yes | Yes | 23 | 18 | 5 | 90B2863E6FE34E4096031138A0D9DBEA |  | R22 | Non-TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | Non-TXV | 4.462%
Planada | CA | 95365-8068 |  | 2012-06-14 | 2012-06-14 10:46 | 2012-06-14 11:10 | RUUD - EAFF031JAZ | 96 | 12.7 | Yes | Yes | 19.1 | 21.9 | -2.8 | 8FA45181BB6E4129BA6758AAE70BA1BF |  | R22 | Non-TXV |  | 13.23% | 0.86771 | 25.42% | [5 empty] | Non-TXV | 13.23%
Planada | CA | 95365-8068 |  | 2012-06-06 | 2012-06-06 16:53 | 2012-06-06 18:17 | OTHER - EAFF-037JAZ | 94 | 3 | Yes | Yes | 21.2 | 19.6 | 1.7 | 48CD0C70120C4C489DF7C41BDBD68C39 |  | R22 | Non-TXV |  | 3.191% | 0.96809 | 6.133% | [5 empty] | Non-TXV | 3.191%
Stockton | CA | 95207-2109 |  | 2012-06-06 | 2012-06-06 13:33 | 2012-06-06 13:53 | RHEEM - AD38B10A | 70 | 9 | Yes | Yes | 15.7 | 18.5 | -2.8 | F7C718C32933468DB24A81509F2D9F77 |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Stockton | CA | 95209-4335 |  | 2012-06-01 | 2012-06-01 13:20 | 2012-06-01 13:42 | CARRIER - 38CKC060--371-- | 85 | 6.8 | Yes | Yes | 18.7 | 18.5 | 0.2 | 27E3B8CC2DE94EFF849D087439309685 |  | R22 | TXV |  | 8% | 0.92 | 15.37% | [5 empty] | TXV | 8%
Stockton | CA | 95210-3136 |  | 2012-06-19 | 2012-06-19 09:06 | 2012-06-19 09:25 | HEIL - PGAA30C1K1 | 75 | -4.4 | Yes | Yes | 24.9 | 19.3 | 5.6 | 46990B5CBECE494893080771130B8732 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Planada | CA | 95365-0000 |  | 2012-06-14 | 2012-06-14 10:11 | 2012-06-14 10:27 | AMANA - PGB24C04520 | 64 | 7.8 | Yes | Yes | 29.2 | 25.9 | 3.3 | 9E265B0F8BC44AC48B0CCFAE849ECC3C |  | R22 | Non-TXV |  | 12.19% | 0.87813 | 23.42% | [5 empty] | Non-TXV | 12.19%
Stockton | CA | 95206-3633 |  | 2012-06-08 | 2012-06-08 15:41 | 2012-06-08 15:59 | OTHER - 561AJ030-B | 67 | 3.7 | Yes | Yes | 17.5 | 19.3 | -1.8 | C37831F3F1014987A30E0C1C5384BB72 |  | R22 | Non-TXV |  | 5.522% | 0.94478 | 10.61% | [5 empty] | Non-TXV | 5.522%
Stockton | CA | 95205-6452 |  | 2012-06-20 | 2012-06-20 09:27 | 2012-06-20 09:44 | GOODMAN - GPG1330070M41AA | 80 | 5.7 | Yes | Yes | 20 | 20.7 | -0.6 | C28085BA0C9F475BBC96B5EFA4A9E13E |  | R410A | Non-TXV |  | 7.125% | 0.92875 | 13.69% | [5 empty] | Non-TXV | 7.125%
Stockton | CA | 95204-1562 |  | 2012-06-06 | 2012-06-06 10:32 | 2012-06-06 11:11 | OTHER - UNK | 36 | 3.9 | Yes | Yes | 16.4 | 19.3 | -2.9 | 39B528DD6C0E45AF8BFC0B5CB136B749 |  | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Marysville | CA | 95901-4442 |  | 2012-06-07 | 2012-06-07 13:14 | 2012-06-07 13:36 | PAYNE - PY1PNB024060AAAA | 53 | 3.4 | Yes | Yes | 19 | 19.9 | -0.9 | 9BD4673C95244E8B94517650C2160C6B |  | R22 | Non-TXV |  | 6.415% | 0.93585 | 12.33% | [5 empty] | Non-TXV | 6.415%
Marysville | CA | 95901-4617 |  | 2012-06-08 | 2012-06-08 11:51 | 2012-06-08 12:26 | AMERICAN STANDARD - YCC042F1M0BH | 104 | 7.4 | Yes | Yes | 23.6 | 19.8 | 3.8 | 33D885D4C5234967B49B16B800E99F60 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.115% | 0.92885 | 13.67% | [5 empty] | Non-TXV | 7.115%
Olivehurst | CA | 95961-0000 |  | 2012-08-01 | 2012-08-01 08:56 | 2012-08-01 09:25 | OTHER - UNK | 80 | -7.5 | Yes | Yes | 19 | 20.1 | -1.1 | 13149B7D846E43F5ACB325C40B598E73 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Yuba City | CA | 95993-8200 |  | 2012-06-06 | 2012-06-06 09:40 | 2012-06-06 09:40 | TRANE - TTD730B100A1 | 69 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | 09FCA4454C204F95AACD452FE04CDAE6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Sutter | CA | 95982-2544 |  | 2012-07-16 | 2012-07-16 10:47 | 2012-07-16 11:04 | YORK - H1OA030S06A | 83 | 2.8 | Yes | Yes | 16 | 18.8 | -2.8 | CCB372D79C37412AA8FB0A51CFD04AAB |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Paso Robles | CA | 93446-3413 |  | 2012-07-13 | 2012-07-13 08:13 | 2012-07-13 08:31 | GOODMAN - GSC130301DA | 87 | 4.1 | Yes | Yes | 19.3 | 18.7 | 0.6 | 3F9FDF0198BE4EF386AE3C42439F1FB1 |  | R22 | Non-TXV |  | 4.713% | 0.95287 | 9.057% | [5 empty] | Non-TXV | 4.713%
Orland | CA | 95963-1542 |  | 2012-06-08 | 2012-06-08 14:30 | 2012-06-08 15:02 | DAY N NIGHT - NA | 73 | 3.9 | Yes | Yes | 22.8 | 20.4 | 2.4 | 9208C8A4CE084169B615F2FD61BB637E |  | R22 | Non-TXV |  | 5.342% | 0.94658 | 10.27% | [5 empty] | Non-TXV | 5.342%
Stockton | CA | 95207-4522 |  | 2012-06-08 | 2012-06-08 14:56 | 2012-06-08 15:13 | RHEEM - RACB-036JAS | 50 | 11.6 | Yes | Yes | 21.4 | 23.2 | -1.8 | C70CE8D543D941DF85B3E2E4C7CEC1B6 |  | R22 | Non-TXV |  | 23.2% | 0.768 | 44.59% | [5 empty] | Non-TXV | 23.2%
Oroville | CA | 95965-4540 |  | 2012-06-01 | 2012-06-01 12:04 | 2012-06-01 12:04 | AMERICAN STANDARD - 4A7B4030E1000AA | 113 | 0 | Yes | Yes | 21.6 | 19.9 | 1.7 | 82D0359CB4734E49B9AF4ECD85BA7E6C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-6221 |  | 2012-06-13 | 2012-06-13 14:26 | 2012-06-13 14:48 | LENNOX - 10GCS036-75-6PB | 58 | -3.4 | Yes | Yes | 27 | 21.5 | 5.5 | 9951638D823941F9BFE3040A28653ED2 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Valley Springs | CA | 95252-9239 |  | 2012-07-05 | 2012-07-05 13:08 | 2012-07-05 13:26 | OTHER - UNK | 51 | -3 | Yes | Yes | 19.2 | 20.4 | -1.2 | F178EF41CEF24A488EDEF9B22FCC315F |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Marysville | CA | 95901-3836 |  | 2012-06-07 | 2012-06-07 10:32 | 2012-06-07 10:50 | YORK - D1HN048N09006C | 128 | -7.5 | Yes | Yes | 19 | 17.7 | 1.3 | AFC8E8F50AFC4082BF9ECCCB4F18C7DF |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Stockton | CA | 95204-1727 |  | 2012-06-06 | 2012-06-06 13:02 | 2012-06-06 13:36 | RUUD - UAKA-037JAZ | 79 | -6.5 | Yes | Yes | 25.2 | 21.3 | 3.9 | 004A92612EDE41C99C980387AA015111 |  | R22 | Non-TXV |  | -8.228% | 1.0823 | 2.304% |  |  |  |  | Non-TXV |  |  | -8.228%
Stockton | CA | 95207-6009 |  | 2012-06-20 | 2012-06-20 12:08 | 2012-06-20 12:33 | PAYNE - 30RCUH108C | 117 | 9.6 | Yes | Yes | 24.2 | 22.1 | 2.2 | D9B335D4467A406D82E7E2E84CBC3DAE |  | R22 | Non-TXV |  | 8.205% | 0.91795 | 15.77% | [5 empty] | Non-TXV | 8.205%
Merced | CA | 95340-1337 |  | 2012-06-13 | 2012-06-13 09:26 | 2012-06-13 09:45 | ICP - PHD324000K000C1 | 150 | 6.4 | Yes | Yes | 21.1 | 20.9 | 0.2 | BF075AEF1D544CE38B8D4D1B76E19038 |  | R410A | Non-TXV |  | 4.267% | 0.95733 | 8.2% | [5 empty] | Non-TXV | 4.267%
Madera | CA | 93637-9354 |  | 2012-06-14 | 2012-06-14 13:44 | 2012-06-14 14:09 | CARRIER - 48ESN048090301 | 144 | 4.4 | Yes | Yes | 15.1 | 18 | -2.9 | 2ED798BB7B884A8380AFDEC2833C691B |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Chico | CA | 95928-4018 |  | 2013-11-20 | 2013-11-20 10:25 | 2013-11-20 10:25 | YORK - UNK | 70 | 0 | Yes | Yes | 27.1 | 20.4 | 6.7 | B50A30CE11844B52BFC2D17447587322 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2718 |  | 2012-06-12 | 2012-06-12 12:46 | 2012-06-12 13:02 | GOODMAN - PGB024050-1A | 54 | 1.7 | Yes | Yes | 25.9 | 21.7 | 4.2 | BE0F372E0BB34A778A670D67605F3E5D |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Oroville | CA | 95966-5263 |  | 2012-06-13 | 2012-06-13 15:38 | 2012-06-13 17:50 | RHEEM - NA | 105 | 4.9 | Yes | Yes | 24.4 | 21.1 | 3.4 | AACD5738615A43ABAAF682F17F65D49D |  | R410A | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Merced | CA | 95340-1331 |  | 2012-07-06 | 2012-07-06 09:46 | 2012-07-06 10:39 | BRYANT - 561CJ018-D | 54 | 3.5 | Yes | Yes | 21 | 19.4 | 1.6 | BBDB6133A5164E1BB0D341ACE1B2D76A |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Rocklin | CA | 95677-3809 |  | 2012-06-12 | 2012-06-12 15:36 | 2012-06-12 15:52 | BRYANT - 561CJ024-D | 55 | 2.1 | Yes | Yes | 17 | 19.3 | -2.3 | CB309BB2AFBC4E12852C1B5485BD9C77 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Merced | CA | 95341-6678 |  | 2012-06-07 | 2012-06-07 12:09 | 2012-06-07 12:26 | BDP - UNK | 58 | 8.2 | Yes | Yes | 24.4 | 22 | 2.4 | 8620E383256B4043B77D591DE19384CD |  | R22 | Non-TXV |  | 14.14% | 0.85862 | 27.17% | [5 empty] | Non-TXV | 14.14%
Stockton | CA | 95207-2843 |  | 2012-06-11 | 2012-06-11 09:06 | 2012-06-11 09:24 | BRYANT - 582ANW0360S0AAAF | 56 | -4.6 | Yes | Yes | 22.6 | 20.1 | 2.5 | 17A269E009A54CC5A79F565339E06AD9 |  | R22 | TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | TXV |  |  | -8.214%
Merced | CA | 95348-2224 |  | 2012-06-12 | 2012-06-12 13:12 | 2012-06-12 13:30 | LENNOX - 10GCS042-100-6PB | 73 | 2.1 | Yes | Yes | 26.9 | 21.3 | 5.6 | E074F7369D2F44BF962F6FC8E0A56767 |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Orland | CA | 95963-9154 |  | 2012-06-08 | 2012-06-08 13:33 | 2012-06-08 14:01 | YORK - B1HH036A06B | 140 | 4.8 | Yes | Yes | 19.2 | 22 | -2.8 | AD3DBDF1FABC4300BFFAFD63C3915FA7 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Stockton | CA | 95209-2317 |  | 2012-06-01 | 2012-06-01 11:08 | 2012-06-01 11:25 | RHEEM - UNK | 86 | 5.1 | Yes | Yes | 16.5 | 18.6 | -2.1 | CA2FAA7159C648B4A1F396B577F9149D |  | R22 | Non-TXV |  | 5.93% | 0.9407 | 11.4% | [5 empty] | Non-TXV | 5.93%
Merced | CA | 95341-6635 |  | 2012-06-14 | 2012-06-14 10:11 | 2012-06-14 10:36 | RHEEM - RRNL-B036JK06X | 92 | -5.4 | Yes | Yes | 25.6 | 19.6 | 6 | CCA9D9BBF41D4FA79706EA425AE3DD6C |  | R410A | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Merced | CA | 95340-1302 |  | 2012-06-14 | 2012-06-14 15:07 | 2012-06-14 15:26 | BRYANT - 561CJ018-C | 66 | 2.2 | Yes | Yes | 25 | 22.1 | 2.9 | 0F4376F369F04A7E9C9C5F7473116B15 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95207-5415 |  | 2012-06-11 | 2012-06-11 11:05 | 2012-06-11 11:24 | DAY & NIGHT - 24[60.YAC-108C | 53 | 5.9 | Yes | Yes | 26.5 | 22.4 | 4.2 | 263178C120504663A3947FCCA5D2177B |  | R22 | Non-TXV |  | 11.13% | 0.88868 | 21.39% | [5 empty] | Non-TXV | 11.13%
Merced | CA | 95340-3461 |  | 2012-06-12 | 2012-06-12 11:06 | 2012-06-12 11:06 | ICP - GPCK018K040D | 57 | 0 | Yes | Yes | 16.8 | 19.5 | -2.7 | 59356139AB254617A6B60AF9E8FF72A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-3508 |  | 2012-06-11 | 2012-06-11 10:18 | 2012-06-11 10:35 | OTHER - C630K-1S | 76 | 3 | Yes | Yes | 18.9 | 21 | -2.1 | 787680B9F44D49ACBC765C0EB9CBCE9D |  | R22 | Non-TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | Non-TXV | 3.947%
Winton | CA | 95388-9325 |  | 2012-06-15 | 2012-06-15 10:05 | 2012-06-15 10:26 | GOODMAN - BSC130-21AC | 76 | 3 | Yes | Yes | 19.6 | 21 | -1.4 | 9EFEAD2EBCEA47E4A7104938F1FB0FA3 |  | R22 | Non-TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | Non-TXV | 3.947%
Yuba City | CA | 95993-9236 |  | 2012-07-10 | 2012-07-10 12:16 | 2012-07-10 12:16 | - PA13NR042-H | 112 | 0 | Yes | Yes | 27 | 21 | 6 | 7E31B25084F441A2AE85CFD64361A07C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-8300 |  | 2012-06-08 | 2012-06-08 16:27 | 2012-06-08 16:27 | CARRIER - 38CKC036350 | 74 | 0 | Yes | Yes | 17.8 | 19.8 | -2 | 4D2795E49A774904BAAC2BE22858305A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2843 |  | 2012-06-07 | 2012-06-07 13:06 | 2012-06-07 13:24 | PAYNE - PY1PNB030040AAAA | 54 | 1.6 | Yes | Yes | 24.7 | 22.5 | 2.2 | E9D12EA7A7644D8D84ECC1E755A3AD11 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Chico | CA | 95926-1916 |  | 2012-06-07 | 2012-06-07 12:02 | 2012-06-07 12:02 | OTHER - 561CJ024-3 | 56 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | 3D15AA6768954C6FB27FBFCD23F9B6B8 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-3444 |  | 2012-06-21 | 2012-06-21 11:01 | 2012-06-21 11:30 | ARCOAIRE - HAC030AKA4 | 74 | 2.7 | Yes | Yes | 18.8 | 19.3 | -0.5 | 7032CCD32EE34A0F88DA39DAA1406148 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | Non-TXV | 3.649%
Red Bluff | CA | 96080-4409 |  | 2012-06-06 | 2012-06-06 09:39 | 2012-06-06 10:32 | BRYANT - 574DNW036090NA | 146 | 20.2 | Yes | Yes | 22.9 | 21.8 | 1.1 | 32545739706F417B83C552ECA83A8ACA |  | R410A | Non-TXV |  | 13.84% | 0.86164 | 26.59% | [5 empty] | Non-TXV | 13.84%
Manteca | CA | 95336-3341 |  | 2012-06-22 | 2012-06-22 11:50 | 2012-06-22 12:20 | BRYANT - 165ANA036- | 165 | -9.7 | Yes | Yes | 19.5 | 20.3 | -0.8 | 65791F51BED3445796B58ACF6712E889 |  | R410A | TXV |  | -5.879% | 1.0588 | 1.646% |  |  |  |  | TXV |  |  | -5.879%
Orland | CA | 95963-1947 |  | 2012-07-05 | 2012-07-05 09:41 | 2012-07-05 10:02 | AMERICAN STANDARD - YCY036G1M0AD | 130 | 5.2 | Yes | Yes | 24.8 | 21.5 | 3.3 | 8204E0C74C314F529B3089F2C28E383C |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Yuba City | CA | 95993-5209 |  | 2012-06-08 | 2012-06-08 13:06 | 2012-06-08 13:30 | LENNOX - 10ACB24-9P | 64 | 6 | Yes | Yes | 18 | 21 | -3 | C9EB259DBF3B402187C2146DB39F24F7 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Rocklin | CA | 95677-3808 |  | 2012-07-03 | 2012-07-03 14:23 | 2012-07-03 14:40 | BRYANT - 561CJ030-D | 70 | 2.4 | Yes | Yes | 18 | 20.2 | -2.2 | E3426855C9294AE0B3F45F8E73458B0A |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Stockton | CA | 95207-7120 |  | 2012-06-12 | 2012-06-12 14:09 | 2012-06-12 14:30 | TRANE - TTN036C100B3 | 117 | 10.5 | Yes | Yes | 26.2 | 22.1 | 4.1 | 4750943F022E45D8BFE24EF6A0D18C5A |  | R22 | Non-TXV |  | 8.974% | 0.91026 | 17.25% | [5 empty] | Non-TXV | 8.974%
Auburn | CA | 95603-3401 |  | 2012-07-12 | 2012-07-12 10:01 | 2012-07-12 10:22 | - 561CJ042-A | 80 | -4.7 | Yes | Yes | 24 | 20.6 | 3.4 | AD41130A3EFE465AB3CDF551CE8C852D |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Auburn | CA | 95603-3320 |  | 2012-07-24 | 2012-07-24 09:41 | 2012-07-24 10:01 | RHEEM - RRK-A024JK06K | 50 | 7.4 | Yes | Yes | 25 | 21.4 | 3.6 | A062B8A9748A4D8595C70C8A2887D9C8 |  | R22 | Non-TXV |  | 14.8% | 0.852 | 28.44% | [5 empty] | Non-TXV | 14.8%
Stockton | CA | 95206-1891 |  | 2012-06-08 | 2012-06-08 13:21 | 2012-06-08 13:37 | GOODMAN - GSC130361DE0705 | 119 | -7 | Yes | Yes | 23.3 | 19.3 | 4 | 159ADB78D73B4B159D2F65AEEEEC467D |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Loomis | CA | 95650-8803 |  | 2012-07-18 | 2012-07-18 12:54 | 2012-07-18 13:16 | TRANE - 2TTX4036B1000AA | 118 | 18.4 | Yes | Yes | 27.5 | 21.5 | 6 | FF32E5E1DD2943DE818318F2A44083CE |  | R22 | Non-TXV |  | 15.59% | 0.84407 | 29.97% | [5 empty] | Non-TXV | 15.59%
Rocklin | CA | 95765-5401 |  | 2012-07-03 | 2012-07-03 12:28 | 2012-07-03 12:55 | CARRIER - 38CKC030300 | 75 | 7.3 | Yes | Yes | 16 | 18.2 | -2.2 | 42D7B39934804534907792FDCC67A802 |  | R22 | Non-TXV |  | 9.733% | 0.90267 | 18.71% | [5 empty] | Non-TXV | 9.733%
Tracy | CA | 95376-4311 |  | 2012-07-11 | 2012-07-11 10:15 | 2012-07-11 10:42 | YORK - H1CH024S06A | 176 | 5.4 | Yes | Yes | 18.5 | 19.8 | -1.3 | BD4F520F65E340BD9276918A44952EF6 |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Chico | CA | 95928-7520 |  | 2012-07-30 | 2012-07-30 16:59 | 2012-07-30 17:44 | OTHER - ATHO22C100CLE | 58 | 5.9 | Yes | Yes | 19.9 | 20.4 | -0.5 | C88C775D0DD2430390A5F6AFC3DCB0B4 |  | R22 | Non-TXV |  | 10.17% | 0.89828 | 19.55% | [5 empty] | Non-TXV | 10.17%
Chico | CA | 95928-6780 |  | 2012-07-03 | 2012-07-03 14:01 | 2012-07-03 14:01 | AMERICAN STANDARD - 4A7B030E100AA | 113 | 0 | Yes | Yes | 22.5 | 21.3 | 1.3 | 5C1604AC5DEA4F7588C58D44CA07181E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-0298 |  | 2012-07-02 | 2012-07-02 11:47 | 2012-07-02 12:11 | CARRIER - 48GS-036060311 | 68 | 3 | Yes | Yes | 18.9 | 18.3 | 0.6 | 20F38A550480468AAD248CE0D0691388 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Los Banos | CA | 93635-3422 |  | 2012-06-06 | 2012-06-06 11:38 | 2012-06-06 11:59 | AIRE-FLO - N2A336AKB200 | 84 | 0.7 | Yes | Yes | 18.2 | 19.9 | -1.7 | 255BA53DAFD045F9BDAE32B3279DD233 |  | R22 | TXV |  | 0.8333% | 0.99167 | 1.601% | [5 empty] | TXV | 0.8333%
Atwater | CA | 95301-0000 |  | 2012-06-11 | 2012-06-11 13:10 | 2012-06-11 13:10 | LENNOX - UNK | 58 | 0 | Yes | Yes | 19.7 | 21.4 | -1.7 | A3FF0239A76C45DB87BB5181D9E4ACA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2005 |  | 2012-06-25 | 2012-06-25 09:39 | 2012-06-25 10:00 | RUUD - UAMC-036JAS | 93 | -6.6 | Yes | Yes | 19 | 18 | 1 | 2163C6077C364F22B6B35BF9E3C71644 |  | R22 | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Stockton | CA | 95210-1520 |  | 2012-06-14 | 2012-06-14 09:07 | 2012-06-14 09:23 | PAYNE - 30/80YAC106T-C | 68 | -4 | Yes | Yes | 24.5 | 20.4 | 4.1 | 2673453652244002B5FB6CB84163B101 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Magalia | CA | 95954-8820 |  | 2012-06-12 | 2012-06-12 10:58 | 2012-06-12 11:22 | AMANA - PGB30C07020 | 66 | 2 | Yes | Yes | 24.5 | 22.5 | 2 | 021FA94C249B4251AC5C3B6D2DB7A25C |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Gustine | CA | 95322-9632 |  | 2012-06-08 | 2012-06-08 11:47 | 2012-06-08 12:08 | BRYANT - 561CJ042-A | 80 | 2.4 | Yes | Yes | 22.4 | 20.7 | 1.7 | EFB88F9AD94A41BCAFD29CFB3B80FDA7 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Gustine | CA | 95322-9630 |  | 2012-08-13 | 2012-08-13 11:43 | 2012-08-13 12:03 | OTHER - UNK | 76 | 2.5 | Yes | Yes | 21.1 | 20.3 | 0.9 | 2B44490B1B2D453F95BCF00DFF60C378 |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Chico | CA | 95926-5205 |  | 2012-06-08 | 2012-06-08 20:27 | 2012-06-08 21:11 | PAYNE - 593ANX042000AAAD | 162 | 5.1 | Yes | Yes | 19.4 | 19.8 | -0.4 | 603278C6E1164F35906B3B875FA5527B |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Stockton | CA | 95207-4849 |  | 2012-06-25 | 2012-06-25 10:14 | 2012-06-25 10:14 | RHEEM - RRNA-B036JK06X | 85 | 0 | Yes | Yes | 16.1 | 18.6 | -2.4 | 0ACF19F60AC74865A17C1CA70B0E5893 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-4647 |  | 2012-06-08 | 2012-06-08 13:52 | 2012-06-08 14:30 | YORK - D1NP048N09006A | 132 | 3.9 | Yes | Yes | 25 | 20.4 | 4.6 | 8E0653282CC44DB3A8B514A72C2CCBE8 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Stockton | CA | 95207-4456 |  | 2012-06-08 | 2012-06-08 15:41 | 2012-06-08 16:02 | GOODMAN - SSX140421BA | 170 | -10 | Yes | Yes | 30.2 | 24.4 | 5.8 | 9E1E11D1326C49B683CFEFC19C591CFE |  | R410A | TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | TXV |  |  | -5.882%
Stockton | CA | 95205-6507 |  | 2012-06-01 | 2012-06-01 16:12 | 2012-06-01 16:32 | OTHER - PGF336060K01A1 | 176 | 5.4 | Yes | Yes | 18 | 19.3 | -1.3 | AA6E5155C23E41CBA80004312786A4CA |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Nevada City | CA | 95959-8750 |  | 2012-07-13 | 2012-07-13 10:21 | 2012-07-13 10:38 | CARRIER - 38EN048320 | 122 | -11.5 | Yes | Yes | 20.7 | 18.5 | 2.3 | 1A5DDB2A354F4A1A81F782F7CF0F2FDA |  | R22 | Non-TXV |  | -9.426% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.426%
Stockton | CA | 95207-3143 |  | 2012-06-07 | 2012-06-07 13:58 | 2012-06-07 14:23 | COMFORT AIRE - 24P1B-1E0 | 65 | 11.4 | Yes | Yes | 22.6 | 23.7 | -1.1 | 3416684D0DAD42B6A6476C1F6C4C8FD2 |  | R22 | Non-TXV |  | 17.54% | 0.82462 | 33.71% | [5 empty] | Non-TXV | 17.54%
Marysville | CA | 95901-3611 |  | 2012-07-26 | 2012-07-26 17:00 | 2012-07-26 17:17 | GOODMAN - CKL18-1 | 53 | -9.4 | Yes | Yes | 27 | 21.5 | 5.5 | 934427AFACD74554A635E60A9C8029DE |  | R22 | Non-TXV |  | -17.74% | 1.1774 | 4.967% |  |  |  |  | Non-TXV |  |  | -17.74%
Madera | CA | 93637-2807 |  | 2012-06-14 | 2012-06-14 14:43 | 2012-06-14 15:05 | CARRIER - 48GX-042060301 | 118 | 5.1 | Yes | Yes | 17.6 | 20.4 | -2.8 | 2C015EF836ED4459B78C2D36B7D28F8B |  | R22 | Non-TXV |  | 4.322% | 0.95678 | 8.306% | [5 empty] | Non-TXV | 4.322%
Marysville | CA | 95901-8256 |  | 2012-06-08 | 2012-06-08 12:55 | 2012-06-08 12:55 | CARRIER - 38CKC048370 | 104 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 9B82CCBB8880412485045292B6EB274E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0641 |  | 2012-07-19 | 2012-07-19 16:51 | 2012-07-19 17:23 | GIBSON - G53BA-024KA | 67 | 2.7 | Yes | Yes | 18.8 | 21 | -2.2 | 66D3885144CA4184AAA9764772341502 |  | R22 | Non-TXV |  | 4.03% | 0.9597 | 7.744% | [5 empty] | Non-TXV | 4.03%
Marysville | CA | 95901-3604 |  | 2012-07-02 | 2012-07-02 10:30 | 2012-07-02 10:30 | NORDYNE - JS3BA-030KA | 88 | 0 | Yes | Yes | 24.1 | 18.6 | 5.5 | BBBB9EC0C24443EDB90DE0CF17027CF6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-2208 |  | 2012-06-06 | 2012-06-06 16:48 | 2012-06-06 17:07 | GOODMAN - GPG1330045M41AC | 85 | -3.7 | Yes | Yes | 22.9 | 19.7 | 3.3 | F1EE896B55854813B5AA52FFF9467BEF |  | R410A | TXV |  | -4.353% | 1.0435 | 1.219% |  |  |  |  | TXV |  |  | -4.353%
Stockton | CA | 95207-3440 |  | 2012-06-07 | 2012-06-07 12:07 | 2012-06-07 12:25 | GOODMAN - CK30-1B | 76 | 3 | Yes | Yes | 19.8 | 21 | -1.2 | 33D15C1D40E6417CB52212DC3E8F609D |  | R22 | Non-TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | Non-TXV | 3.947%
Stockton | CA | 95207-7011 |  | 2012-06-13 | 2012-06-13 13:31 | 2012-06-13 14:00 | GOODMAN - VSC130301BA | 87 | 3.2 | Yes | Yes | 19.1 | 18.3 | 0.8 | 6AFB67B2C0AE4EC79558E8AFAFA3D6AA |  | R22 | Non-TXV |  | 3.678% | 0.96322 | 7.069% | [5 empty] | Non-TXV | 3.678%
Stockton | CA | 95206-5604 |  | 2012-06-20 | 2012-06-20 12:53 | 2012-06-20 13:10 | BRYANT - 561CJ048-A | 102 | 5.6 | Yes | Yes | 19.9 | 20.7 | -0.8 | B8E566D663124C678B7EE0FBA6B30BB1 |  | R22 | TXV |  | 5.49% | 0.9451 | 10.55% | [5 empty] | TXV | 5.49%
Stockton | CA | 95212-2873 |  | 2012-06-14 | 2012-06-14 12:50 | 2012-06-14 13:09 | CARRIER - 38CKC060370 | 133 | 4.2 | Yes | Yes | 21.1 | 20.4 | 0.7 | 8AA1516AA8144640ADFA8E8AF93B3679 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Merced | CA | 95341-7705 |  | 2012-06-15 | 2012-06-15 08:19 | 2012-06-15 08:38 | BDP - 585GJ030040 | 58 | 5.9 | Yes | Yes | 21.1 | 20.9 | 0.2 | D9F87365F41B41BCAADAA501101F1C41 |  | R22 | Non-TXV |  | 10.17% | 0.89828 | 19.55% | [5 empty] | Non-TXV | 10.17%
Marysville | CA | 95901-7247 |  | 2012-07-13 | 2012-07-13 13:10 | 2012-07-13 13:33 | DAY & NIGHT - UNK | 90 | 3.2 | Yes | Yes | 20 | 20.4 | -0.4 | D1FDACF5A26D497AAC6769E0CDA6C7E3 |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Marysville | CA | 95901-3927 |  | 2012-06-15 | 2012-06-15 09:04 | 2012-06-15 09:28 | RUUD - RRNL-B030JK06X | 76 | 2.3 | Yes | Yes | 20 | 19.9 | 0.1 | 481D30F2888B411995232B4F78CE99CB |  | R410A | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Riverbank | CA | 95367-2803 |  | 2012-06-08 | 2012-06-08 10:36 | 2012-06-08 11:00 | DAY & NIGHT - 542EJ024 | 100 | 3 | Yes | Yes | 20.1 | 18.2 | 1.9 | DB2D3075278C43ADAEADBD0251036B38 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Plumas Lake | CA | 95961-9126 |  | 2012-07-30 | 2012-07-30 14:23 | 2012-07-30 14:42 | CARRIER - 38BRC030320 | 100 | 2.9 | Yes | Yes | 15.6 | 18.2 | -2.6 | 6DB70D0B3B6543EE98C04DD694E4F93F |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Stockton | CA | 95207-3144 |  | 2012-06-07 | 2012-06-07 15:52 | 2012-06-07 16:10 | YORK - D3NP024N05606A | 100 | 12.7 | Yes | Yes | 23.7 | 20.4 | 3.3 | DFCADA7447C64546B44F85D5BBE2F40A |  | R22 | TXV |  | 12.7% | 0.873 | 24.41% | [5 empty] | TXV | 12.7%
Tracy | CA | 95376-2108 |  | 2012-06-15 | 2012-06-15 10:54 | 2012-06-15 11:22 | WESTINGHOUSE - UNK | 54 | 6.1 | Yes | Yes | 19.5 | 22.1 | -2.6 | AC50640B0E8043D3B8304013F1421772 |  | R22 | Non-TXV |  | 11.3% | 0.88704 | 21.71% | [5 empty] | Non-TXV | 11.3%
Merced | CA | 95348-3691 |  | 2012-07-10 | 2012-07-10 11:43 | 2012-07-10 12:15 | TRANE - TTB024C100A0 | 58 | 1.8 | Yes | Yes | 17.4 | 19.7 | -2.3 | EE3265C7F6B941808B1F561F783C8971 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Red Bluff | CA | 96080-2537 |  | 2012-07-17 | 2012-07-17 18:18 | 2012-07-17 19:37 | BRYANT - 563CN048-H | 65 | 2.6 | Yes | Yes | 21.5 | 21.2 | 0.3 | 3D255A9789DA4ED39C03CC40A6870282 |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Manteca | CA | 95336-2862 |  | 2012-06-06 | 2012-06-06 10:00 | 2012-06-06 10:31 | YORK - D1NA024N5606C | 50 | 7.2 | Yes | Yes | 17.8 | 20.1 | -2.3 | 1C7BB512E62E4BB1A89E2235A9029B0E |  | R22 | Non-TXV |  | 14.4% | 0.856 | 27.67% | [5 empty] | Non-TXV | 14.4%
Stockton | CA | 95203-2101 |  | 2012-07-02 | 2012-07-02 13:05 | 2012-07-02 13:24 | RHEEM - RRKA-A030JK06X | 54 | 5.1 | Yes | Yes | 21.1 | 20.4 | 0.7 | 0795DAC8CCA74BB4A2AFA637BEC4C06C |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Stockton | CA | 95210-1639 |  | 2012-06-06 | 2012-06-06 11:43 | 2012-06-06 11:59 | BDP - 589ANW036080ACAF | 86 | -5.1 | Yes | Yes | 22.2 | 20.9 | 1.3 | 92A5E1549E2B482D9155A79C60EB7D5E |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Chico | CA | 95928-7523 |  | 2012-07-30 | 2012-07-30 18:36 | 2012-07-30 18:36 | TRANE - 2YCC3030A1040AA | 88 | 0 | Yes | Yes | 24.5 | 20.4 | 4.1 | E715E8D762A84DCB990362CC2EAAEE4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3165 |  | 2012-06-01 | 2012-06-01 13:28 | 2012-06-01 14:00 | CARRIER - 38EN018310SM | 59 | 24.4 | Yes | Yes | 16.4 | 18.2 | -1.8 | 6C8F73DF639C429A8CFA0A0E57BFF336 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 41.36% | 0.58644 | 79.48% | [5 empty] | Non-TXV | 41.36%
Stockton | CA | 95215-8143 |  | 2012-07-11 | 2012-07-11 15:45 | 2012-07-11 16:14 | RUUD - URKA-A036JK08X | 62 | 4.3 | Yes | Yes | 21.7 | 17.7 | 4 | 74830B4759DC479389C1B545897FD891 |  | R22 | Non-TXV |  | 6.935% | 0.93065 | 13.33% | [5 empty] | Non-TXV | 6.935%
Rocklin | CA | 95677-3813 |  | 2012-07-03 | 2012-07-03 13:32 | 2012-07-03 13:51 | BRYANT - 561CJ030-E | 66 | 2.3 | Yes | Yes | 17 | 19.3 | -2.3 | 0B7A5D4DA6264651BD2872628587F53B |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Stockton | CA | 95204-2122 |  | 2012-06-06 | 2012-06-06 14:18 | 2012-06-06 14:38 | DAY & NIGHT - 587ANZ030050AAA | 66 | 5.1 | Yes | Yes | 21.1 | 22.2 | -1.1 | 4CE21FFDCDBF41A69C0C3FCE453AFA8F |  | R22 | Non-TXV |  | 7.727% | 0.92273 | 14.85% | [5 empty] | Non-TXV | 7.727%
Stockton | CA | 95207-2306 |  | 2012-06-11 | 2012-06-11 15:58 | 2012-06-11 16:15 | DAY & NIGHT - UNK | 105 | 15.4 | Yes | Yes | 20.6 | 22.4 | -1.8 | 9C303429320A4D9097DABF1740E9B60D |  | R22 | Non-TXV |  | 14.67% | 0.85333 | 28.19% | [5 empty] | Non-TXV | 14.67%
Merced | CA | 95341-6984 |  | 2012-06-13 | 2012-06-13 13:45 | 2012-06-13 14:11 | AIRE-FLO - PY1PNB030040AAAA | 55 | 7.4 | Yes | Yes | 26.9 | 28.6 | -1.7 | 4BEDF8D475A04FECB76AC47C76D760BE |  | R22 | Non-TXV |  | 13.45% | 0.86545 | 25.86% | [5 empty] | Non-TXV | 13.45%
Atwater | CA | 95301-4870 |  | 2012-06-15 | 2012-06-15 10:21 | 2012-06-15 10:52 | CARRIER - 38CE003300 | 71 | 2.3 | Yes | Yes | 19 | 18.9 | 0.1 | 58160E8E05584296A120F894CBCF020A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.225% | [5 empty] | Non-TXV | 3.239%
Stockton | CA | 95207-2832 |  | 2012-08-10 | 2012-08-10 11:25 | 2012-08-10 11:41 | AMANA - RCE36A2D | 96 | 6.6 | Yes | Yes | 17.2 | 18.7 | -1.5 | 3FD1E06ACCBF4E64967825848401FB6C |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Auburn | CA | 95603-5017 |  | 2012-08-08 | 2012-08-08 09:58 | 2012-08-08 09:58 | TRANE - TTD730B100A1 | 69 | 0 | Yes | Yes | 20.4 | 19.7 | 0.7 | 16F0670352D449779D6CCE75C524957E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-2916 |  | 2012-07-23 | 2012-07-23 14:19 | 2012-07-23 14:37 | DAY & NIGHT - 580AN016040 | 67 | 2.4 | Yes | Yes | 20.8 | 21.3 | -0.5 | 18D861BD020E4B16A4E560E13714B138 |  | R22 | Non-TXV |  | 3.582% | 0.96418 | 6.884% | [5 empty] | Non-TXV | 3.582%
Paradise | CA | 95969-6621 |  | 2012-06-12 | 2012-06-12 12:23 | 2012-06-12 12:23 | AMERICAN STANDARD - 2YCX3030A1075AA | 88 | 0 | Yes | Yes | 24.6 | 22.1 | 2.5 | 8C6344668C314C3592F2FE03D0590A05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2941 |  | 2012-06-28 | 2012-06-28 08:27 | 2012-06-28 08:48 | AIRE-FLO - UNK | 96 | 7.2 | Yes | Yes | 19 | 19.4 | -0.4 | C9CDA34507574737AC31D5A543317BFE |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Los Banos | CA | 93635-2711 |  | 2012-06-07 | 2012-06-07 14:34 | 2012-06-07 14:51 | TRANE - TTR036C100A1 | 92 | 7 | Yes | Yes | 18.4 | 19.7 | -1.3 | 1F710ABA88A642B0ACF27DB2295B186A |  | R22 | Non-TXV |  | 7.609% | 0.92391 | 14.62% | [5 empty] | Non-TXV | 7.609%
Chico | CA | 95928-6097 |  | 2012-06-11 | 2012-06-11 18:37 | 2012-06-11 18:53 | OTHER - ATH022C106CRE | 58 | 4.1 | Yes | Yes | 24.3 | 21.8 | 2.6 | ACEA32AF6DEA43749037A1AC532E2625 |  | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Marysville | CA | 95901-3728 |  | 2012-06-15 | 2012-06-15 09:52 | 2012-06-15 10:17 | OTHER - 589ANW036080ABAF | 85 | -8 | Yes | Yes | 19 | 20.4 | -1.4 | A324517C4401443ABA0F77B33800F284 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Dos Palos | CA | 93620-9425 |  | 2012-06-08 | 2012-06-08 12:29 | 2012-06-08 12:50 | ICP - HAC048AKA5 | 123 | 10.1 | Yes | Yes | 30.2 | 24.2 | 6 | 3EE71E7A6CEB41C29A670CD59BFB3493 |  | R22 | Non-TXV |  | 8.211% | 0.91789 | 15.78% | [5 empty] | Non-TXV | 8.211%
Stockton | CA | 95206-0000 |  | 2012-06-08 | 2012-06-08 10:39 | 2012-06-08 11:00 | BRYANT - 563CN030-B | 99 | -6.2 | Yes | Yes | 23.2 | 19.9 | 3.3 | A3B34921AD5547A68B3C04476B782E20 |  | R22 | TXV |  | -6.263% | 1.0626 | 1.754% |  |  |  |  | TXV |  |  | -6.263%
Stockton | CA | 95206-0000 |  | 2012-06-08 | 2012-06-08 10:50 | 2012-06-08 11:07 | BRYANT - 563CN042-C | 104 | 3.8 | Yes | Yes | 20.3 | 19.9 | 0.4 | 0A4B35AC72AD4751978465CDC6D74DFE |  | R22 | TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | TXV | 3.654%
Chico | CA | 95928-6044 |  | 2012-06-11 | 2012-06-11 19:50 | 2012-06-11 20:12 | AMERICAN STANDARD - 2YCX3030A10641AA | 89 | 7.3 | Yes | Yes | 23.4 | 22 | 1.4 | 9AE3CCB11F56413084B38D07DC0B78AD |  | R22 | Non-TXV |  | 8.202% | 0.91798 | 15.76% | [5 empty] | Non-TXV | 8.202%
Stockton | CA | 95203-1340 |  | 2012-06-14 | 2012-06-14 14:29 | 2012-06-14 14:46 | TRANE - 2YCX3036A1096AA | 82 | 4.7 | Yes | Yes | 19.8 | 20.8 | -1 | 00CB380014054820891AA4A16D9E5966 |  | R22 | Non-TXV |  | 5.732% | 0.94268 | 11.02% | [5 empty] | Non-TXV | 5.732%
Dinuba | CA | 93618-9340 |  | 2012-06-06 | 2012-06-06 12:11 | 2012-06-06 12:36 | CARRIER - N/A | 120 | 10.4 | Yes | Yes | 23 | 20.2 | 2.8 | 40F3F055BCEA4DBEBCAED90B0A847160 |  | R22 | Non-TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | Non-TXV | 8.667%
Auburn | CA | 95603-2842 |  | 2012-07-10 | 2012-07-10 09:43 | 2012-07-10 10:02 | PAYNE - 561CJ048-A | 85 | 2.6 | Yes | Yes | 19 | 19.8 | -0.8 | 425ECAAAAFDA4129B455785A5BACF2DC |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Atwater | CA | 95301-2832 |  | 2012-06-01 | 2012-06-01 12:52 | 2012-06-01 13:11 | AMERICAN STANDARD - YCX036F1M0AD | 114 | 3.4 | Yes | Yes | 22.3 | 20.4 | 1.9 | CB2A6A7185F44886A91FA38970C3F657 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Merced | CA | 95348-2341 |  | 2012-07-09 | 2012-07-09 10:55 | 2012-07-09 11:13 | GOODMAN - GPG13240451CB | 78 | 2.6 | Yes | Yes | 19.3 | 19.7 | -0.4 | 6D023391A2964A139DE0400B93858BBB |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Auburn | CA | 95603-4350 |  | 2012-07-10 | 2012-07-10 12:15 | 2012-07-10 12:36 | CARRIER - 38CKC030340 | 75 | 2.8 | Yes | Yes | 18 | 20.4 | -2.4 | 1A396CA251884EA0B94FB9EAD80EB7CF |  | R22 | Non-TXV |  | 3.733% | 0.96267 | 7.175% | [5 empty] | Non-TXV | 3.733%
Durham | CA | 95938-9635 |  | 2012-07-13 | 2012-07-13 17:34 | 2012-07-13 17:50 | COLEMAN - UNK | 65 | 5.3 | Yes | Yes | 23 | 20.9 | 2.1 | 0F2C0C4A058149EE85D926335AAB4B50 |  | R22 | Non-TXV |  | 8.154% | 0.91846 | 15.67% | [5 empty] | Non-TXV | 8.154%
Stockton | CA | 95210-2011 |  | 2012-06-11 | 2012-06-11 11:56 | 2012-06-11 12:17 | YORK - H2RD030S06B | 93 | 2.8 | Yes | Yes | 18.2 | 19.3 | -1.1 | 428D2BE69FAC401FAAAFD3E971915ED7 |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Los Banos | CA | 93635-3064 |  | 2012-06-06 | 2012-06-06 10:18 | 2012-06-06 10:41 | BRYANT - 563CN030 | 98 | 0.8 | Yes | Yes | 25.2 | 21.9 | 3.3 | A3333D3DB0634585A277E08E89E5C450 |  | R22 | Non-TXV |  | 0.8163% | 0.99184 | 1.569% | [5 empty] | Non-TXV | 0.8163%
Atwater | CA | 95301-4869 |  | 2012-06-12 | 2012-06-12 14:50 | 2012-06-12 15:06 | LENNOX - HS9-11 | 76 | 3.8 | Yes | Yes | 20.8 | 20.1 | 0.8 | 212D33C57F4D44F1BD21A96A655F3B32 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Atwater | CA | 95301-4869 |  | 2012-06-12 | 2012-06-12 12:43 | 2012-06-12 13:21 | LENNOX - HS9-311 | 77 | 4.9 | Yes | Yes | 20.1 | 19.8 | 0.3 | C1FC5DC6FDEC444A90F900C3C1586F90 |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Dos Palos | CA | 93620-0000 |  | 2012-06-15 | 2012-06-15 11:30 | 2012-06-15 11:53 | OTHER - R4GD-030K045X | 93 | 2.9 | Yes | Yes | 18.1 | 19.1 | -0.9 | 303FED2F2B0F4718817A727CFE2A7063 |  | R22 | Non-TXV |  | 3.118% | 0.96882 | 5.993% | [5 empty] | Non-TXV | 3.118%
Merced | CA | 95340-2376 |  | 2012-06-01 | 2012-06-01 13:49 | 2012-06-01 13:49 | GOODMAN - CK36-1B | 76 | 0 | Yes | Yes | 22.1 | 17.9 | 4.3 | 081B5290D95149BDB6D57C57ADE39350 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3246 |  | 2012-06-06 | 2012-06-06 09:06 | 2012-06-06 09:25 | PAYNE - PA10JA030 | 66 | 2.4 | Yes | Yes | 26.3 | 20.9 | 5.4 | 295F8070DC3344C688CF74EF41580631 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Yuba City | CA | 95993-7603 |  | 2012-06-01 | 2012-06-01 13:10 | 2012-06-01 13:26 | RHEEM - RAFD-042JBS | 79 | 3.9 | Yes | Yes | 17 | 19.3 | -2.3 | CC74A7B872814EF0981DA67EE75A5417 |  | R22 | Non-TXV |  | 4.937% | 0.95063 | 9.487% | [5 empty] | Non-TXV | 4.937%
Los Banos | CA | 93635-5455 |  | 2012-05-31 | 2012-05-31 14:43 | 2012-05-31 15:12 | BRYANT - 561CJ042-A | 80 | 6.7 | Yes | Yes | 27.1 | 22.3 | 4.8 | 8C9883B8BF0E42DB817D22BFF19FFA48 |  | R22 | Non-TXV |  | 8.375% | 0.91625 | 16.09% | [5 empty] | Non-TXV | 8.375%
Marysville | CA | 95901-8269 |  | 2012-06-15 | 2012-06-15 11:52 | 2012-06-15 12:19 | CARRIER - UNK | 93 | 5.4 | Yes | Yes | 18 | 20.6 | -2.6 | D32FFF5E682B4BB5A837EE46D8365AAD |  | R22 | Non-TXV |  | 5.806% | 0.94194 | 11.16% | [5 empty] | Non-TXV | 5.806%
Los Banos | CA | 93635-5470 |  | 2012-05-31 | 2012-05-31 13:37 | 2012-05-31 14:04 | YORK - H1RA048S06D | 117 | 5 | Yes | Yes | 28.3 | 23.4 | 4.9 | C62EC1941AEA43F0A06DE996D338148F |  | R22 | Non-TXV |  | 4.274% | 0.95726 | 8.213% | [5 empty] | Non-TXV | 4.274%
Stockton | CA | 95210-3271 |  | 2012-06-01 | 2012-06-01 10:23 | 2012-06-01 10:41 | GE - BTB930A100A3 | 53 | -3.7 | Yes | Yes | 20.2 | 18.5 | 1.7 | 0D91554A2F744FA4B633B53ACA14756E |  | R22 | Non-TXV |  | -6.981% | 1.0698 | 1.955% |  |  |  |  | Non-TXV |  |  | -6.981%
Oroville | CA | 95966-5431 |  | 2012-06-01 | 2012-06-01 19:51 | 2012-06-01 20:08 | DAY & NIGHT - 588ANW048080AEBG | 102 | 9.1 | Yes | Yes | 20.3 | 22 | -1.7 | 6BE8AA63E1184E41A01A83ADD48B6403 |  | R22 | Non-TXV |  | 8.922% | 0.91078 | 17.15% | [5 empty] | Non-TXV | 8.922%
Stockton | CA | 95203-1257 |  | 2012-06-14 | 2012-06-14 13:43 | 2012-06-14 14:04 | AMANA - PGD24C0702E | 74 | 2.7 | Yes | Yes | 20.7 | 19.5 | 1.2 | F00E0569E8854196BDCD2AF738E62B2E |  | R22 | Non-TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | Non-TXV | 3.649%
Atwater | CA | 95301-4870 |  | 2012-06-15 | 2012-06-15 10:54 | 2012-06-15 11:13 | UNITARY PRODUCTS GROUP - GCGD30S21S2A | 55 | 1.7 | Yes | Yes | 17.5 | 18.9 | -1.4 | 4B5B4564CD044A998CECB47E49C03577 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Merced | CA | 95348-2338 |  | 2012-06-12 | 2012-06-12 12:18 | 2012-06-12 12:42 | TRANE - 2TTB3030A1000AA | 88 | 2.6 | Yes | Yes | 25 | 19.1 | 5.9 | 91370B7DA8B64BC2BC0D804E54FE1ED3 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Stockton | CA | 95203-1905 |  | 2012-06-14 | 2012-06-14 15:17 | 2012-06-14 16:33 | GOODMAN - PGB024075-1 | 54 | 3.4 | Yes | Yes | 22.5 | 18.5 | 4 | 4521DA9AC5114766B215CC034BFA6C89 |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Stockton | CA | 95207-6220 |  | 2012-06-13 | 2012-06-13 11:27 | 2012-06-13 11:44 | RHEEM - RAMB-048JAS | 162 | 13.5 | Yes | Yes | 23.7 | 20.2 | 3.6 | 96D9FD2C44504C69B935413A59034238 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Newman | CA | 95360-1703 |  | 2012-06-14 | 2012-06-14 09:40 | 2012-06-14 09:58 | OTHER - ACS030A2C1 | 71 | 2.1 | Yes | Yes | 25.6 | 20.4 | 5.2 | FF629291231E4992AFE6B4A897701D23 |  | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Merced | CA | 95348-3387 |  | 2012-06-15 | 2012-06-15 11:09 | 2012-06-15 11:37 | GOODMAN - UNK | 74 | 3.4 | Yes | Yes | 20 | 21 | -1 | D3DD452F918E44CD95E1214FE21B18DE |  | R22 | Non-TXV |  | 4.595% | 0.95405 | 8.83% | [5 empty] | Non-TXV | 4.595%
Rocklin | CA | 95677-4769 |  | 2012-06-12 | 2012-06-12 13:51 | 2012-06-12 13:51 | GOODMAN - CJ48-1GB | 149 | 0 | Yes | Yes | 27.5 | 22.3 | 5.2 | 0E31D33512B44987A6F6047203B97A28 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Granite Bay | CA | 95746-9110 |  | 2012-07-13 | 2012-07-13 17:17 | 2012-07-13 17:17 | LENNOX - HS19-311-7P | 65 | 0 | Yes | Yes | 25.2 | 21.9 | 3.3 | 2780CE9A1AED4AE28E5115764D2E7440 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-6036 |  | 2012-06-01 | 2012-06-01 11:05 | 2012-06-01 11:23 | PAYNE - PA13NA024-B | 63 | 2 | Yes | Yes | 16 | 18.6 | -2.6 | 6D47EE00AA09470AB650EA3B45011B25 |  | R410A | Non-TXV |  | 3.175% | 0.96825 | 6.101% | [5 empty] | Non-TXV | 3.175%
Gridley | CA | 95948-9432 |  | 2012-07-24 | 2012-07-24 10:27 | 2012-07-24 10:27 | GOODMAN - GPG13360701AC | 112 | 0 | Yes | Yes | 19.4 | 19.9 | -0.5 | 2466F26C1184479CABCF253D3238F334 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Plumas Lake | CA | 95961-9022 |  | 2012-07-30 | 2012-07-30 10:49 | 2012-07-30 11:12 | CARRIER - 38CKC030340 | 75 | -4.4 | Yes | Yes | 18 | 21 | -3 | 55389B421614404A88CAF39E3B75C4DA |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Los Banos | CA | 93635-2603 |  | 2012-06-15 | 2012-06-15 12:43 | 2012-06-15 13:37 | DAY & NIGHT - 593CJ048-A | 104 | 3.1 | Yes | Yes | 19.7 | 19.9 | -0.2 | D8DC36FD864E40E4A3B86A5EE770738C |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Oroville | CA | 95966-5530 |  | 2012-06-07 | 2012-06-07 13:10 | 2012-06-07 13:27 | CARRIER - 38BR048300 | 163 | 6.5 | Yes | Yes | 18.2 | 20.4 | -2.2 | 5541B291B63E45B182C55BE8CA4DFB76 |  | R22 | TXV |  | 3.988% | 0.96012 | 7.664% | [5 empty] | TXV | 3.988%
Atwater | CA | 95301-4871 |  | 2012-06-13 | 2012-06-13 11:28 | 2012-06-13 11:50 | LENNOX - HS9-3116P | 74 | 2.4 | Yes | Yes | 19.7 | 19.3 | 0.4 | 3C8F35F3477445B9B984255B4185CB57 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Yuba City | CA | 95991-2958 |  | 2012-06-14 | 2012-06-14 14:01 | 2012-06-14 14:32 | TRANE - TTN036C100B2 | 117 | 14.1 | Yes | Yes | 18 | 20.2 | -2.2 | 1E09C01B6CCC43EDBF73B7977A23B64D |  | R22 | Non-TXV |  | 12.05% | 0.87949 | 23.16% | [5 empty] | Non-TXV | 12.05%
Merced | CA | 95340-5111 |  | 2012-06-01 | 2012-06-01 11:51 | 2012-06-01 12:12 | AMERICAN STANDARD - YCY030G1MOAC | 120 | 14.5 | Yes | Yes | 20 | 19.9 | 0.1 | 8497995FD54B4A4FB9B78E565663985C |  | R22 | Non-TXV |  | 12.08% | 0.87917 | 23.22% | [5 empty] | Non-TXV | 12.08%
Gustine | CA | 95322-1918 |  | 2012-07-12 | 2012-07-12 09:56 | 2012-07-12 09:56 | GOODMAN - NA | 73 | 0 | Yes | Yes | 9.8 | 20.4 | -10.6 | C67B24F50A464612ACAE50A26C9C3BEC | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6991 |  | 2012-06-08 | 2012-06-08 18:43 | 2012-06-08 19:10 | BRYANT - 582ANW04206 | 100 | 3.3 | Yes | Yes | 24.5 | 20.3 | 4.2 | 86F30BB742E64563BE9C14EF8CAD61FD |  | R22 | Non-TXV |  | 3.3% | 0.967 | 6.342% | [5 empty] | Non-TXV | 3.3%
Merced | CA | 95341-5859 |  | 2012-06-07 | 2012-06-07 15:38 | 2012-06-07 15:38 | OTHER - 80WB30E1NA | 54 | 0 | Yes | Yes | 0 | 10.8 | -10.8 | 973AF8BC394A4CC0B6204414089B7A6C | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3104 |  | 2012-06-06 | 2012-06-06 13:53 | 2012-06-06 14:13 | BRYANT - 582ANW024060AAAD | 57 | 1.9 | Yes | Yes | 19 | 20.6 | -1.6 | DFC595570965495485361E0DA1F5EF32 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Los Banos | CA | 93635-3285 |  | 2012-06-06 | 2012-06-06 13:19 | 2012-06-06 13:44 | AIRE-FLO - 561AJ048 | 102 | 15.2 | Yes | Yes | 25.9 | 22.2 | 3.7 | A62B8409AD8D4E16BD7D729E7D5D4090 |  | R22 | Non-TXV |  | 14.9% | 0.85098 | 28.64% | [5 empty] | Non-TXV | 14.9%
Stockton | CA | 95209-2318 |  | 2012-06-25 | 2012-06-25 13:58 | 2012-06-25 14:15 | HEIL - CA906 | 192 | 5.4 | Yes | Yes | 21.7 | 19.6 | 2.2 | 518BDE7E57994B7A8D82B9722F326162 |  | R22 | Non-TXV |  | 2.812% | 0.97188 | 5.405% | [5 empty] | Non-TXV | 2.812%
Auburn | CA | 95603-4008 |  | 2012-06-06 | 2012-06-06 11:01 | 2012-06-06 11:18 | TRANE - | 70 | 5.4 | Yes | Yes | 26 | 20.6 | 5.4 | A6CC637EA08E4209BAAA61A2A003E5DD |  | R22 | Non-TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | Non-TXV | 7.714%
Stockton | CA | 95205-2607 |  | 2012-07-06 | 2012-07-06 10:28 | 2012-07-06 10:54 | YORK - D1NH030N05606 | 73 | 3.7 | Yes | Yes | 20.1 | 19.9 | 0.2 | 2E9C422C59DF44E4A4C7835233971BFB |  | R22 | Non-TXV |  | 5.068% | 0.94932 | 9.741% | [5 empty] | Non-TXV | 5.068%
Stockton | CA | 95206-6273 |  | 2012-07-03 | 2012-07-03 13:55 | 2012-07-03 14:20 | CARRIER - 38CKC060300 | 153 | 6.3 | Yes | Yes | 20.8 | 20.3 | 0.5 | A0F0FA178247462BBBB18EF5E3B35209 |  | R22 | TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | TXV | 4.118%
Grass Valley | CA | 95945-4310 |  | 2012-07-10 | 2012-07-10 08:21 | 2012-07-10 09:07 | TRANE - YCZ050F1HOEA | 189 | 6.4 | Yes | Yes | 23 | 18.7 | 4.3 | C59443F49B864858A40BEFEDF93D67A9 |  | R22 | Non-TXV |  | 3.386% | 0.96614 | 6.508% | [5 empty] | Non-TXV | 3.386%
Planada | CA | 95365-8034 |  | 2012-06-06 | 2012-06-06 16:24 | 2012-06-06 16:46 | GOODMAN - GSC130421A A | 143 | 4.7 | Yes | Yes | 24.6 | 21 | 3.6 | 48CE9F1294E848E693A8876083F4283E |  | R22 | Non-TXV |  | 3.287% | 0.96713 | 6.316% | [5 empty] | Non-TXV | 3.287%
Stockton | CA | 95207-7434 |  | 2012-06-12 | 2012-06-12 13:09 | 2012-06-12 13:25 | BRYANT - 582ANW036060AAAF | 56 | 11.6 | Yes | Yes | 21.4 | 19.8 | 1.6 | 4433A4612D5A411C93D64E388671C6F5 |  | R22 | Non-TXV |  | 20.71% | 0.79286 | 39.81% | [5 empty] | Non-TXV | 20.71%
Stockton | CA | 95210-1454 |  | 2012-06-15 | 2012-06-15 12:30 | 2012-06-15 12:30 | BDP - 585CJ02450 | 72 | 0 | Yes | Yes | 25.7 | 20.1 | 5.6 | B2CE49B351734046AAED9934824554B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5426 |  | 2012-06-13 | 2012-06-13 12:26 | 2012-06-13 12:49 | COLEMAN - TGD24S21S2ZHA | 57 | 3.2 | Yes | Yes | 20.2 | 20.6 | -0.4 | 5A0DAA0FC8F642C4B8B07DA53FC1F0C4 |  | R22 | Non-TXV |  | 5.614% | 0.94386 | 10.79% | [5 empty] | Non-TXV | 5.614%
Newman | CA | 95360-9510 |  | 2012-06-14 | 2012-06-14 10:49 | 2012-06-14 11:06 | GOODMAN - CKL49-1A | 112 | 3.4 | Yes | Yes | 18.3 | 18.7 | -0.4 | B9C9F99A75E7445FB66BA650DC057D3C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Stockton | CA | 95212-2917 |  | 2012-06-20 | 2012-06-20 12:56 | 2012-06-20 13:13 | RHEEM - RAKA-024JAS | 51 | 1.6 | Yes | Yes | 18 | 20.5 | -2.5 | 821B35A132EC4A4E83FD824E4DF9F8B5 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Ione | CA | 95640-9629 |  | 2012-07-20 | 2012-07-20 13:36 | 2012-07-20 13:54 | UNITARY PRODUCTS GROUP - BRCQ0361BD | 52 | 4.4 | Yes | Yes | 20.4 | 19.9 | 0.5 | 8255C9323B03423EB0EB028EB29DDF98 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Marysville | CA | 95901-4449 |  | 2012-06-07 | 2012-06-07 13:59 | 2012-06-07 14:21 | OTHER - CA5536VKD2 | 82 | 7.6 | Yes | Yes | 21 | 21.5 | -0.5 | EFDA17F38F5745AC841081A860F4C7C6 |  | R22 | Non-TXV |  | 9.268% | 0.90732 | 17.81% | [5 empty] | Non-TXV | 9.268%
Olivehurst | CA | 95961-4236 |  | 2012-07-11 | 2012-07-11 09:35 | 2012-07-11 09:59 | OTHER - UNK | 85 | 7.2 | Yes | Yes | 20.5 | 21 | -0.5 | 10299508B4D14A06A1FDF83F1418E139 |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Stockton | CA | 95210-2311 |  | 2012-06-06 | 2012-06-06 13:47 | 2012-06-06 14:08 | UNK - UNK | 85 | -5 | Yes | Yes | 24.5 | 20.8 | 3.7 | EE9793A43E224D829A77A827BB178B18 |  |  |  |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | 0 |  |  | -5.882%
Marysville | CA | 95901-4250 |  | 2012-07-17 | 2012-07-17 11:51 | 2012-07-17 12:11 | CARRIER - 38TXA030330 | 96 | 8.5 | Yes | Yes | 19.5 | 18.7 | 0.8 | C1DB8258727C433CB34F5134AF4FB26E |  | R410A | Non-TXV |  | 8.854% | 0.91146 | 17.02% | [5 empty] | Non-TXV | 8.854%
Fresno | CA | 93726-6049 |  | 2012-06-07 | 2012-06-07 10:42 | 2012-06-07 11:04 | COMFORT AIRE - PGAD361K6 | 102 | -7.2 | Yes | Yes | 18.3 | 21 | -2.7 | FB44A2CA708742D6A0BF3DB722FA3F6D |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Marysville | CA | 95901-7054 |  | 2012-06-08 | 2012-06-08 11:03 | 2012-06-08 11:03 | RHEEM - RRNA-B036JK06X | 83.2 | 0 | Yes | Yes | 20.2 | 19.1 | 1.1 | B4649074840845A3990C340B6E2E1457 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Orosi | CA | 93647-0000 |  | 2012-07-16 | 2012-07-16 13:08 | 2012-07-16 13:27 | CARRIER - 24ABR330A310 | 84 | 7.1 | Yes | Yes | 17.1 | 19.1 | -2 | 59D89155B6884021822C87AF3DEFB06F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.452% | 0.91548 | 16.24% | [5 empty] | Non-TXV | 8.452%
Marysville | CA | 95901-4250 |  | 2012-07-17 | 2012-07-17 13:08 | 2012-07-17 13:08 | GOODMAN - CK30-1A | 76 | 0 | Yes | Yes | 21.5 | 18.8 | 2.7 | 9140A19A3EA3402BA4545B78F6F27211 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-9353 |  | 2012-06-13 | 2012-06-13 11:38 | 2012-06-13 11:56 | RHEEM - RRKA-A036JK06X | 62 | 1.9 | Yes | Yes | 17.4 | 19.1 | -1.7 | 4E6F5D4058E24E83B7D2AEC6917E4049 |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Chico | CA | 95926-7778 |  | 2012-06-01 | 2012-06-01 13:56 | 2012-06-01 15:13 | TEMPSTAR - TCA430AKAA | 190 | 6.9 | Yes | Yes | 22.2 | 21.5 | 0.7 | B8101390A1ED41B58107603D57820558 |  | R22 | Non-TXV |  | 3.632% | 0.96368 | 6.979% | [5 empty] | Non-TXV | 3.632%
Marysville | CA | 95901-3906 |  | 2012-06-08 | 2012-06-08 15:06 | 2012-06-08 15:06 | PAYNE - PY3PNA036060NB-- | 115 | 0 | Yes | Yes | 27.5 | 21.7 | 5.8 | 2C4350BC635749DEB15E48926BEAFABB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4436 |  | 2012-06-01 | 2012-06-01 13:39 | 2012-06-01 13:57 | PAYNE - 585A024055YAC | 51 | 1.5 | Yes | Yes | 24 | 19.6 | 4.4 | 95BF60E950E643E0AB0A39EE20D6B741 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Yuba City | CA | 95993-5900 |  | 2012-06-01 | 2012-06-01 14:26 | 2012-06-01 14:40 | LENNOX - 10AC-036-230 | 74 | 9.8 | Yes | Yes | 15 | 17.7 | -2.7 | D86743C5C33A4E2EBD26FBF4F3295897 |  | R22 | Non-TXV |  | 13.24% | 0.86757 | 25.45% | [5 empty] | Non-TXV | 13.24%
Stockton | CA | 95215-6724 |  | 2012-06-13 | 2012-06-13 14:19 | 2012-06-13 14:51 | BRYANT - 574DNWA36060NA | 100 | 3.6 | Yes | Yes | 18.8 | 19.8 | -1 | 374864E6A72140578F0677D9553958B6 |  | R410A | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Paradise | CA | 95969-4201 |  | 2012-07-06 | 2012-07-06 11:10 | 2012-07-06 11:10 | AMERICAN STANDARD - 2YCX336A1075AA | 82 | 0 | Yes | Yes | 24.4 | 21 | 3.4 | F1427E128D364FF48000C1515AFA3A92 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2813 |  | 2012-06-12 | 2012-06-12 13:08 | 2012-06-12 13:26 | OTHER - NAC030AKC3 | 75 | 5.2 | Yes | Yes | 18.2 | 20.2 | -2 | D5872522D817416C96844DB3FC022E65 |  | R22 | Non-TXV |  | 6.933% | 0.93067 | 13.32% | [5 empty] | Non-TXV | 6.933%
Durham | CA | 95938-9661 |  | 2012-07-13 | 2012-07-13 16:20 | 2012-07-13 17:10 | DAY & NIGHT - C4A348GKD200 | 113 | 3.4 | Yes | Yes | 24.1 | 22.1 | 2 | 63856690994544CBA1D889660301BCBE |  | R410A | Non-TXV |  | 3.009% | 0.96991 | 5.782% | [5 empty] | Non-TXV | 3.009%
Stockton | CA | 95205-8002 |  | 2012-06-07 | 2012-06-07 15:58 | 2012-06-07 15:58 | GOODMAN - GSC130361FA | 83 | 0 | Yes | Yes | 22.9 | 19.9 | 3 | EF6627BAF12D4C0895EE51B276CF34ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-3912 |  | 2012-06-01 | 2012-06-01 16:30 | 2012-06-01 16:50 | REEM - NA | 68 | 9.7 | Yes | Yes | 19.2 | 22 | -2.8 | 900DC99341E543D397BA8555E578481B |  | R22 | Non-TXV |  | 14.26% | 0.85735 | 27.41% | [5 empty] | Non-TXV | 14.26%
Atwater | CA | 95301-4866 |  | 2012-06-12 | 2012-06-12 10:22 | 2012-06-12 10:41 | RHEEM - UNK | 69 | 4.3 | Yes | Yes | 21.3 | 20.8 | 0.5 | B46591E385DC4F1C98CAA31906D950C5 |  | R22 | Non-TXV |  | 6.232% | 0.93768 | 11.98% | [5 empty] | Non-TXV | 6.232%
Magalia | CA | 95954-9336 |  | 2012-06-12 | 2012-06-12 09:39 | 2012-06-12 10:18 | OTHER - 2436A961 | 82 | -4.8 | Yes | Yes | 25.1 | 20.1 | 5 | A9155834B3F04CEE90CC5F0AF767280E |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Paradise | CA | 95969-5661 |  | 2012-06-13 | 2012-06-13 12:04 | 2012-06-13 12:24 | RHEEM - RRGF-05E30JKR | 67 | 0 | Yes | Yes | 20.5 | 22 | -1.5 | E1B845AD76604E9F82928D11A8B77611 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-9360 |  | 2012-06-22 | 2012-06-22 10:59 | 2012-06-22 11:21 | CARRIER - 38BRC048370 | 136 | 4.1 | Yes | Yes | 18 | 18.8 | -0.8 | 56DDFBE4D32E469796C9323760DB4A95 |  | R22 | Non-TXV |  | 3.015% | 0.96985 | 5.794% | [5 empty] | Non-TXV | 3.015%
Rocklin | CA | 95677-2560 |  | 2012-06-07 | 2012-06-07 15:02 | 2012-06-07 15:22 | TRANE - TTD742A100A0 | 106 | 33 | Yes | Yes | 23.7 | 22 | 1.7 | 30C73E743F5D4F2DBBAF4B7EA2740546 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 31.13% | 0.68868 | 59.83% | [5 empty] | Non-TXV | 31.13%
Auburn | CA | 95603-5827 |  | 2012-07-06 | 2012-07-06 12:39 | 2012-07-06 13:02 | GOODMAN - CKL49-1L | 111 | 11.4 | Yes | Yes | 19 | 20.4 | -1.4 | 1E2B2C8D0AEE493A8BE663D698C11B60 |  | R22 | Non-TXV |  | 10.27% | 0.8973 | 19.74% | [5 empty] | Non-TXV | 10.27%
Red Bluff | CA | 96080-2918 |  | 2012-06-06 | 2012-06-06 10:34 | 2012-06-06 10:52 | BRYANT - BRCQ048B | 93 | 4.1 | Yes | Yes | 23.3 | 21.5 | 1.9 | D1EB7A29DBDF465E944F370DE48D1814 |  | R22 | Non-TXV |  | 4.409% | 0.95591 | 8.472% | [5 empty] | Non-TXV | 4.409%
Merced | CA | 95341-6634 |  | 2012-06-07 | 2012-06-07 09:40 | 2012-06-07 09:58 | OTHER - URGG05E24JKR | 42 | 5.6 | Yes | Yes | 19.4 | 19.9 | -0.5 | 796BE8335FF8438B849E496C6F9CCFD3 |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Stockton | CA | 95215-8121 |  | 2012-06-21 | 2012-06-21 14:18 | 2012-06-21 14:40 | DAY & NIGHT - 593CJ030-B | 70 | 4.2 | Yes | Yes | 22.6 | 20.9 | 1.7 | C86E936B09F940E6A4134B8925B3A13C |  | R22 | TXV |  | 6% | 0.94 | 11.53% | [5 empty] | TXV | 6%
Firebaugh | CA | 93622-9637 |  | 2012-06-15 | 2012-06-15 10:27 | 2012-06-15 10:52 | OTHER - 60WR24A1PA | 54 | 3 | Yes | Yes | 19.3 | 19 | 0.3 | BCF076CD4DC04C52BEF9E92D00CC4B40 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Cutler | CA | 93615-0000 |  | 2012-07-11 | 2012-07-11 12:10 | 2012-07-11 14:45 | GOODMAN - GPG13420701AA | 107 | 5.7 | Yes | Yes | 20.4 | 20.4 | 0 | 8213321C0BB0446BB4F2A873BF6314A9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.327% | 0.94673 | 10.24% | [5 empty] | Non-TXV | 5.327%
Manteca | CA | 95337-5140 |  | 2012-06-06 | 2012-06-06 11:05 | 2012-06-06 11:27 | GOODMAN - UNK | 54 | 1.7 | Yes | Yes | 19 | 19.8 | -0.8 | 1F25B32077BE4A93AEF88272EE7CA049 |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Firebaugh | CA | 93622-9636 |  | 2012-06-15 | 2012-06-15 09:29 | 2012-06-15 09:57 | PAYNE - UNK | 50 | 1.6 | Yes | Yes | 26.1 | 20.1 | 6 | A53C20B3E5624273A5C44FF7F17F1F96 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Atwater | CA | 95301-4859 |  | 2012-07-02 | 2012-07-02 11:30 | 2012-07-02 11:52 | GOODMAN - CK30-1B | 80 | 3.3 | Yes | Yes | 17.8 | 19.7 | -1.9 | 617219EB9743441CAB079B202BFF0F10 |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Firebaugh | CA | 93622-9640 |  | 2012-06-15 | 2012-06-15 11:28 | 2012-06-15 11:49 | PAYNE - UNK | 50 | -2.9 | Yes | Yes | 25.2 | 19.8 | 5.4 | D648B1BB2B7D414DB1FD8E967A928071 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Firebaugh | CA | 93622-9636 |  | 2012-06-15 | 2012-06-15 08:47 | 2012-06-15 09:25 | PAYNE - UNK | 50 | 1.6 | Yes | Yes | 26.4 | 21.5 | 4.9 | 32525BE48AB546FBB3916A02BC41EABD |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Oroville | CA | 95966-9374 |  | 2012-06-07 | 2012-06-07 14:17 | 2012-06-07 22:18 | TRANE - ATTR03036A1000A | 101 | 12 | Yes | Yes | 19.9 | 21.9 | -2 | 1CC90CD1214646F0AB77154A6490610B |  | R22 | Non-TXV |  | 11.88% | 0.88119 | 22.83% | [5 empty] | Non-TXV | 11.88%
Stockton | CA | 95215-7344 |  | 2012-06-13 | 2012-06-13 13:18 | 2012-06-13 13:42 | TRANE - YCY036G1M0AC | 129 | 5.8 | Yes | Yes | 25.5 | 21.9 | 3.6 | 96A77ABC2E98412E9B620AA5FCBF31E0 |  | R22 | Non-TXV |  | 4.496% | 0.95504 | 8.641% | [5 empty] | Non-TXV | 4.496%
Fresno | CA | 93722-2619 |  | 2012-06-01 | 2012-06-01 12:38 | 2012-06-01 12:59 | CARRIER - 38BR048300 | 164 | 12.7 | Yes | Yes | 18.8 | 19 | -0.2 | 91FA07E7751E4DB497C6711286F25295 |  | R22 | Non-TXV |  | 7.744% | 0.92256 | 14.88% | [5 empty] | Non-TXV | 7.744%
Caruthers | CA | 93609-9404 |  | 2012-06-15 | 2012-06-15 10:13 | 2012-06-15 10:32 | YORK - DBYP-F024N045A | 100 | 3.6 | Yes | Yes | 22.1 | 20.6 | 1.5 | 300EA58DB3C24D53B4DC95DFA2633A79 |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Marysville | CA | 95901-3042 |  | 2012-06-07 | 2012-06-07 11:50 | 2012-06-07 12:14 | OTHER - PGAA42C1K3 | 82 | 2.9 | Yes | Yes | 24 | 20.4 | 3.6 | 54ECB4FF68D2493D8C7D3BB145DC611F |  | R22 | Non-TXV |  | 3.537% | 0.96463 | 6.797% | [5 empty] | Non-TXV | 3.537%
Merced | CA | 95348-2106 |  | 2012-06-08 | 2012-06-08 09:05 | 2012-06-08 09:22 | CARRIER - 585WG36060ABAF | 82 | 2.5 | Yes | Yes | 19.2 | 19.9 | -0.7 | EA4417C7D8C8421C9D96899D62B5D77C |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Yuba City | CA | 95991-8469 |  | 2012-06-15 | 2012-06-15 10:49 | 2012-06-15 12:13 | CARRIER - 38CKC030340 | 77 | 7.9 | Yes | Yes | 26.4 | 21.9 | 4.5 | B33AAEAA5EEF4062BF9E8309DF687326 |  | R22 | TXV |  | 10.26% | 0.8974 | 19.72% | [5 empty] | TXV | 10.26%
Marysville | CA | 95901-4434 |  | 2012-07-25 | 2012-07-25 11:36 | 2012-07-25 12:05 | TRANE - 4YCZ6036A1075AA | 111 | 3.3 | Yes | Yes | 23.3 | 19.3 | 4 | E42FA1873684434E851FC5252F961702 |  | R410A | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Riverdale | CA | 93656-0000 |  | 2012-07-19 | 2012-07-19 08:52 | 2012-07-19 09:10 | HEIL - CA5560VK02 | 150 | 4.5 | Yes | Yes | 24.8 | 21 | 3.8 | F61F7F5301EA4385B527ABF43FB31AED |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93612-4319 |  | 2012-06-11 | 2012-06-11 14:13 | 2012-06-11 14:32 | YORK - D1NH024N03606C | 70 | 2.1 | Yes | Yes | 22 | 19.8 | 2.2 | 3E2D1BDB61EA44DBB6F926AB793B2C22 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Riverbank | CA | 95367-3080 |  | 2012-06-28 | 2012-06-28 11:49 | 2012-06-28 12:19 | RHEEM - RRNA-B030JK06X | 72 | 2.2 | Yes | Yes | 26.1 | 21.4 | 4.7 | EA72CFA7445645DFB5DE44F1215FB39C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Dinuba | CA | 93618-9389 |  | 2012-07-09 | 2012-07-09 10:26 | 2012-07-09 10:47 | BRYANT - 588ANW036060ADAF | 67 | 2.2 | Yes | Yes | 20.5 | 19.9 | 0.6 | EF4F8074F5FB4C75A89B4F6A9485B1FF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Stockton | CA | 95210-2600 |  | 2012-06-14 | 2012-06-14 11:32 | 2012-06-14 11:49 | ICP - PGN330060K01A1 | 96 | 3.1 | Yes | Yes | 25.9 | 20.2 | 5.8 | 27E660CDC448484F8AB500123E1DEDA1 |  | R22 | Non-TXV |  | 3.229% | 0.96771 | 6.206% | [5 empty] | Non-TXV | 3.229%
Yuba City | CA | 95991-0000 |  | 2012-06-15 | 2012-06-15 10:49 | 2012-06-15 11:14 | YORK - H2RC04250 | 108 | 3.2 | Yes | Yes | 24.5 | 21.2 | 3.4 | 2A027D4EB5384ED2A0A423D2B6ED0807 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93722-4429 |  | 2012-06-01 | 2012-06-01 14:14 | 2012-06-01 14:33 | PAYNE - 585A024055YACR | 51 | 1.5 | Yes | Yes | 20.3 | 20.4 | -0.1 | 96C6707CD6004E2497AD19DFDD7D77CF |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93727-1942 |  | 2012-06-08 | 2012-06-08 14:14 | 2012-06-08 14:33 | COLEMAN - N/A | 90 | 2.7 | Yes | Yes | 24.3 | 21.4 | 3 | BA861F599AEB40BB99FC0B69D4BC6C97 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95340-2550 |  | 2012-06-01 | 2012-06-01 14:35 | 2012-06-01 14:58 | OTHER - 120WR48A1NA | 93 | 6.2 | Yes | Yes | 16.9 | 19.6 | -2.7 | 33D869635F9C488F954404B95FF58D64 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Merced | CA | 95340-5127 |  | 2012-06-01 | 2012-06-01 14:29 | 2012-06-01 14:53 | TRANE - 2YCX3030A1064AA | 85 | 12.2 | Yes | Yes | 16.4 | 19.4 | -3 | 033637200BAA44A4B3838B563DAB1967 |  | R22 | Non-TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | Non-TXV | 14.35%
Auburn | CA | 95603-4008 |  | 2012-07-12 | 2012-07-12 09:20 | 2012-07-12 09:37 | OTHER - UNK | 85 | -7 | Yes | Yes | 20 | 22.5 | -2.5 | 8FDA0E69CA9C4F5494A8B287911C23FC |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Merced | CA | 95340-3891 |  | 2012-06-01 | 2012-06-01 13:45 | 2012-06-01 14:12 | ICP - GPCM24K040F | 54 | 8.8 | Yes | Yes | 22 | 21.3 | 0.7 | 740F72EE03EB495798A10AE585F117B1 |  | R22 | Non-TXV |  | 16.3% | 0.83704 | 31.32% | [5 empty] | Non-TXV | 16.3%
Chico | CA | 95973-1215 |  | 2012-06-08 | 2012-06-08 18:56 | 2012-06-08 18:56 | CARRIER - 48ESNAZ404030 | 88 | 0 | Yes | Yes | 22.1 | 20.7 | 1.4 | 55A9BDBF9688453D96A179D0C9000DE9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-3110 |  | 2012-06-15 | 2012-06-15 14:32 | 2012-06-15 14:50 | OTHER - UNK | 36 | 4.9 | Yes | Yes | 18.1 | 20.3 | -2.2 | 5016E2D904CF4AD0A3C6960DE68891C2 |  | R22 | Non-TXV |  | 13.61% | 0.86389 | 26.16% | [5 empty] | Non-TXV | 13.61%
Fresno | CA | 93727-3411 |  | 2012-06-25 | 2012-06-25 09:51 | 2012-06-25 10:11 | GOODMAN - PGB042075-1 | 68 | 2.8 | Yes | Yes | 23.1 | 20.5 | 2.6 | 731DD70C8D744EE1A30AFA42F2213BFD |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Atwater | CA | 95301-4888 |  | 2012-06-06 | 2012-06-06 14:49 | 2012-06-06 15:09 | LENNOX - HS9-311-6P | 78 | 2.3 | Yes | Yes | 21.4 | 21.7 | -0.2 | 391443D3BAFE48B6A0B54842F705C370 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Magalia | CA | 95954-9765 |  | 2012-06-12 | 2012-06-12 12:26 | 2012-06-12 12:44 | CARRIER - 38CK036330 | 81 | 2.5 | Yes | Yes | 20.5 | 22.3 | -1.8 | 2244C1C8248C46FBBAABAA34E4EE14DB |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Red Bluff | CA | 96080-2218 |  | 2012-06-01 | 2012-06-01 15:10 | 2012-06-01 15:59 | RHEEM - RRPL-B036JK08E | 92 | 2.8 | Yes | Yes | 25.5 | 23.2 | 2.3 | 5798A9D584BA458C8613F10864A3E58D |  | R410A | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Fresno | CA | 93710-5435 |  | 2012-06-01 | 2012-06-01 16:47 | 2012-06-01 17:02 | RUUD - UAJC-042JAS | 99 | 3.1 | Yes | Yes | 18 | 21 | -3 | 4654D385BD864DBF8B9D2E1E7D09D52B |  | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Stockton | CA | 95205-6448 |  | 2012-06-07 | 2012-06-07 16:54 | 2012-06-07 17:19 | YORK - D1NP048N09006A | 132 | 4.2 | Yes | Yes | 21.3 | 21.5 | -0.2 | 62F76AC2B0A34F8C9B69A21CA15FA6B2 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Stockton | CA | 95205-6448 |  | 2012-06-07 | 2012-06-07 16:34 | 2012-06-07 16:51 | YORK - D2NP024N05606A | 100 | 4.7 | Yes | Yes | 28 | 23.7 | 4.3 | 855DEDA978C2454BBBFE701504C82EFB |  | R22 | Non-TXV |  | 4.7% | 0.953 | 9.032% | [5 empty] | Non-TXV | 4.7%
Stockton | CA | 95210-2600 |  | 2012-06-07 | 2012-06-07 11:05 | 2012-06-07 11:22 | ICP - PGN324040K01A1 | 94 | 2.9 | Yes | Yes | 23.3 | 19.3 | 4 | 53A516F114A841BE9BF7D15E89B7CF6B |  | R22 | Non-TXV |  | 3.085% | 0.96915 | 5.929% | [5 empty] | Non-TXV | 3.085%
Auburn | CA | 95603-9042 |  | 2012-06-06 | 2012-06-06 13:06 | 2012-06-06 13:27 | GOODMAN - GSC130601BC | 169 | -11.9 | Yes | Yes | 21 | 20.1 | 0.9 | 3CC92B18C204499A9F3DAAE8D471FF2C |  | R22 | Non-TXV |  | -7.041% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.041%
Atwater | CA | 95301-3525 |  | 2012-07-02 | 2012-07-02 09:57 | 2012-07-02 10:18 | BDP - 585GJ018040 | 55 | 1.7 | Yes | Yes | 17.1 | 19 | -1.9 | 656D881AC37848F3A719EA15674EF115 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Sanger | CA | 93657-3003 |  | 2012-06-11 | 2012-06-11 09:54 | 2012-06-11 09:54 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 23.5 | 20.7 | 2.8 | 1EC76982B04D478088079859856D5658 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-1234 |  | 2012-06-07 | 2012-06-07 08:41 | 2012-06-07 09:03 | CARRIER - 48GX-036090301AD | 82 | 2.4 | Yes | Yes | 22.7 | 19.9 | 2.8 | 072CD10EB0F74155872A6CC37E975A79 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Tracy | CA | 95377-8252 |  | 2012-06-25 | 2012-06-25 15:53 | 2012-06-25 16:11 | GOODMAN - CKJ48-1AB | 118 | 3.7 | Yes | Yes | 19.2 | 20.7 | -1.5 | 77A9610E13B04E18B3C2E006B2137D75 |  | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Merced | CA | 95340-3819 |  | 2012-06-01 | 2012-06-01 08:53 | 2012-06-01 09:21 | YORK - D1NH036N05606C | 108 | 9 | Yes | Yes | 20.5 | 19.2 | 1.3 | 5F4DB77C9F6C4A66A6ED9D33E8FBFE73 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Stockton | CA | 95215-4867 |  | 2012-06-13 | 2012-06-13 14:53 | 2012-06-13 15:13 | RHEEM - RAKA-030JAZ | 66 | 3.9 | Yes | Yes | 18.2 | 20.4 | -2.2 | 4684E8E404BD464AB2052E967FDE1156 |  | R22 | Non-TXV |  | 5.909% | 0.94091 | 11.36% | [5 empty] | Non-TXV | 5.909%
Atwater | CA | 95301-4888 |  | 2012-06-06 | 2012-06-06 12:38 | 2012-06-06 12:55 | RHEEM - RAFA-030JAQ | 59 | 1.8 | Yes | Yes | 16.5 | 18.3 | -1.8 | 6E3A919DF62141E2A2D6FED8FE8CE8B2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Los Banos | CA | 93635-0000 |  | 2012-06-13 | 2012-06-13 11:26 | 2012-06-13 11:48 | ARCOAIRE - H2A336GKA100 | 141 | 4.5 | Yes | Yes | 20.2 | 19.3 | 0.9 | BB546DA4B61643318F6B2952A1B1BFF7 |  | R22 | Non-TXV |  | 3.191% | 0.96809 | 6.133% | [5 empty] | Non-TXV | 3.191%
Los Banos | CA | 93635-3286 |  | 2012-06-06 | 2012-06-06 12:26 | 2012-06-06 13:06 | AIRE-FLO - 561AJ048 | 102 | 1.1 | Yes | Yes | 20.9 | 19.5 | 1.4 | F3B6BEA64DED446A83501039BCF5B284 |  | R22 | Non-TXV |  | 1.078% | 0.98922 | 2.073% | [5 empty] | Non-TXV | 1.078%
Cantua Creek | CA | 93608-9707 |  | 2012-07-13 | 2012-07-13 11:06 | 2012-07-13 14:20 | GOODMAN - GSC1303001CA | 105 | 3.5 | Yes | Yes | 18.4 | 20.4 | -2 | 0D9518991F9D473EA2E60E81F3939664 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Atwater | CA | 95301-4886 |  | 2012-06-06 | 2012-06-06 13:56 | 2012-06-06 14:18 | OTHER - NA | 48 | 1.4 | Yes | Yes | 17 | 19.7 | -2.7 | 935553A8AE394F5192C3DD949701645D |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Merced | CA | 95348-2843 |  | 2012-07-06 | 2012-07-06 10:52 | 2012-07-06 11:15 | BRYANT - 582ANW030040AAAD | 56 | 2.2 | Yes | Yes | 19.4 | 20.9 | -1.5 | 92F0162B2DCC4956BC9B487F69F57ECA |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Oroville | CA | 95966-7716 |  | 2012-06-01 | 2012-06-01 14:48 | 2012-06-01 14:48 | TEMPSTAR - PGCO60K140B | 106 | 0 | Yes | Yes | 27.1 | 21.7 | 5.4 | F3EBD55375FD48C885DCF44B10BAAD81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1031 |  | 2012-06-14 | 2012-06-14 10:31 | 2012-06-14 10:41 | LENNOX - 13GCSXA-24-068X-230-1A | 62 | 3.8 | Yes | Yes | 17.8 | 19.9 | -2.1 | 1BBA9C04CE3C485D87413BEDE6A4424E |  | R22 | Non-TXV |  | 6.129% | 0.93871 | 11.78% | [5 empty] | Non-TXV | 6.129%
Tracy | CA | 95377-9265 |  | 2012-07-03 | 2012-07-03 13:53 | 2012-07-03 14:16 | TRANE - 2TTB3048A1000AA | 142 | 7.5 | Yes | Yes | 19.3 | 21 | -1.7 | 698F823D193E4B038AB3A8A57F712142 |  | R22 | Non-TXV |  | 5.282% | 0.94718 | 10.15% | [5 empty] | Non-TXV | 5.282%
Paso Robles | CA | 93446-1107 |  | 2012-07-09 | 2012-07-09 13:17 | 2012-07-09 13:34 | YORK - H2RA030S06D | 62 | 1.9 | Yes | Yes | 20.2 | 19.9 | 0.3 | A634962163954C06A4C5FC934015185F |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Chico | CA | 95926-3480 |  | 2012-06-07 | 2012-06-07 19:19 | 2012-06-07 19:38 | GOODMAN - PGB030075-1 | 59 | 3 | Yes | Yes | 20.7 | 21.2 | -0.5 | E3E3DA1387D44F499DC022652D2CAFCB |  | R22 | Non-TXV |  | 5.085% | 0.94915 | 9.772% | [5 empty] | Non-TXV | 5.085%
Fresno | CA | 93726-4210 |  | 2012-06-07 | 2012-06-07 11:49 | 2012-06-07 12:06 | COLEMAN - DAYP-F036NO7OA | 108 | 3.4 | Yes | Yes | 17.9 | 20.4 | -2.5 | 5B28414C93384FB6B091D9027A107273 |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Fresno | CA | 93722-4587 |  | 2012-06-06 | 2012-06-06 14:43 | 2012-06-06 15:02 | ARCOAIRE - PGME30G0907 | 73 | 2.2 | Yes | Yes | 22.5 | 20.1 | 2.4 | E95F89172C374B26A207C787B4E73558 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Merced | CA | 95341-6241 |  | 2012-06-07 | 2012-06-07 10:57 | 2012-06-07 11:18 | AMERICAN STANDARD - YCC024F1LOBD | 64 | 9.9 | Yes | Yes | 24.7 | 21.5 | 3.2 | 91BD8DFC46DB457492E1003E062AAA9A |  | R22 | Non-TXV |  | 15.47% | 0.84531 | 29.73% | [5 empty] | Non-TXV | 15.47%
Colusa | CA | 95932-2716 |  | 2012-07-16 | 2012-07-16 09:12 | 2012-07-16 09:29 | LENNOX - GCS29-036-75-2PA | 58 | 1.7 | Yes | Yes | 24 | 19.1 | 4.9 | DE992460A7FF424EAE279C56AAC15567 |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Atwater | CA | 95301-4886 |  | 2012-06-15 | 2012-06-15 11:55 | 2012-06-15 12:15 | CARRIER - 38CE003300 | 71 | 2.1 | Yes | Yes | 17.9 | 18.9 | -0.9 | FF169BF9D06D4714B2150F5D80DD1C54 |  | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Stockton | CA | 95206-6056 |  | 2012-06-21 | 2012-06-21 12:05 | 2012-06-21 12:21 | GOODMAN - CKJ48-1A | 118 | 4.9 | Yes | Yes | 18.7 | 20.2 | -1.5 | EE61E5FE68BA4C4293B0CD84A0B45902 |  | R22 | Non-TXV |  | 4.153% | 0.95847 | 7.98% | [5 empty] | Non-TXV | 4.153%
Grass Valley | CA | 95945-5067 |  | 2012-06-14 | 2012-06-14 11:20 | 2012-06-14 11:20 | TRANE - TTR036C100A2 | 92 | 0 | Yes | Yes | 24.3 | 20.4 | 3.9 | 9E41501C2FD8476298209F7A0B4A98B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4886 |  | 2012-06-13 | 2012-06-13 12:33 | 2012-06-13 13:03 | GOODMAN - GSC130361DF | 121 | 5.2 | Yes | Yes | 18.4 | 19.5 | -1.1 | EAB619EC57C0492B93595F19870327EB |  | R22 | Non-TXV |  | 4.298% | 0.95702 | 8.259% | [5 empty] | Non-TXV | 4.298%
Grass Valley | CA | 95945-7535 |  | 2012-06-19 | 2012-06-19 15:03 | 2012-06-19 15:29 | DAY & NIGHT - 597BN024-A | 99 | -9.3 | Yes | Yes | 22 | 20.4 | 1.6 | 18F4234F76FA4C0E93145983F2BBF27F |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
Lincoln | CA | 95648-1682 |  | 2012-07-06 | 2012-07-06 11:00 | 2012-07-06 11:26 | RHEEM - RAKA-042JAZ | 85 | 6.9 | Yes | Yes | 17.8 | 19.4 | -1.6 | 87B5178BE7DB4FB1B2BF445BC2D27AA3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.118% | 0.91882 | 15.6% | [5 empty] | Non-TXV | 8.118%
Merced | CA | 95348-1243 |  | 2012-06-12 | 2012-06-12 09:07 | 2012-06-12 09:37 | OTHER - BTD724A100A10 | 68 | 2 | Yes | Yes | 27.2 | 22.4 | 4.8 | 5C78A898D5034DA98BCCCFF3872D43AD |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Merced | CA | 95348-3016 |  | 2012-06-07 | 2012-06-07 10:47 | 2012-06-07 11:09 | TRANE - TTR030C100A2 | 76 | 10.2 | Yes | Yes | 17.8 | 19.9 | -2.1 | 98A3BC53F8934F43A37E141B49858504 |  | R22 | Non-TXV |  | 13.42% | 0.86579 | 25.79% | [5 empty] | Non-TXV | 13.42%
Stockton | CA | 95207-5819 |  | 2012-06-19 | 2012-06-19 11:15 | 2012-06-19 11:33 | AMANA - RCB30C2A | 77 | 9.2 | Yes | Yes | 18.5 | 20.4 | -1.9 | 28F2BE72DD5B4DCE8B43F20288CE2122 |  | R22 | Non-TXV |  | 11.95% | 0.88052 | 22.96% | [5 empty] | Non-TXV | 11.95%
Atwater | CA | 95301-4886 |  | 2012-07-02 | 2012-07-02 12:38 | 2012-07-02 12:38 | OTHER - UNK | 85 | 0 | Yes | Yes | 18.4 | 20.1 | -1.7 | CCD40DC56F0D4D35963CD7777D22FB32 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-7871 |  | 2012-06-08 | 2012-06-08 19:38 | 2012-06-08 19:38 | DAY & NIGHT - N2K336AKB200 | 119 | 0 | Yes | Yes | 21.5 | 20.1 | 1.4 | B23FBB077D7A432688585733B82B86F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-1655 |  | 2012-06-12 | 2012-06-12 08:20 | 2012-06-12 08:41 | BRYANT - 582ANW024060NAAD | 53 | 1.6 | Yes | Yes | 25.5 | 19.5 | 6 | D5C583A2935C473692296677CE5DC927 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Stockton | CA | 95206-6009 |  | 2012-06-12 | 2012-06-12 15:19 | 2012-06-12 15:39 | OTHER - AC036X1021A | 63 | 3.6 | Yes | Yes | 21.5 | 21 | 0.5 | D611C79801344A5C901894A978FB42B8 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Stockton | CA | 95219-7204 |  | 2012-06-19 | 2012-06-19 13:33 | 2012-06-19 13:51 | CARRIER - 38CK0C60370 | 131 | 10.2 | Yes | Yes | 21.1 | 19.5 | 1.6 | CC9FDC598CAE452E98192B40ED5505FD |  | R22 | TXV |  | 7.786% | 0.92214 | 14.96% | [5 empty] | TXV | 7.786%
Merced | CA | 95340-6163 |  | 2012-06-01 | 2012-06-01 12:30 | 2012-06-01 12:52 | CARRIER - 38BRB024300 | 86 | -3.3 | Yes | Yes | 19.5 | 18.7 | 0.8 | BCF257ABEBAF4D1483931381DE81B632 |  | R22 | TXV |  | -3.837% | 1.0384 | 1.075% |  |  |  |  | TXV |  |  | -3.837%
Manteca | CA | 95336-4853 |  | 2012-06-11 | 2012-06-11 09:47 | 2012-06-11 10:11 | GOODMAN - PGB30050-1 REV A | 56 | 2 | Yes | Yes | 20.8 | 19.7 | 1.1 | E369AFE35E8D44709A935D1DF1943AC8 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Kerman | CA | 93630-1440 |  | 2012-06-14 | 2012-06-14 11:03 | 2012-06-14 11:30 | GUARDIAN - GPG13300701B | 77 | 2.6 | Yes | Yes | 17.6 | 20.4 | -2.8 | DFE6295A689541A996D493211EA570CC |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Dinuba | CA | 93618-3311 |  | 2012-06-06 | 2012-06-06 11:10 | 2012-06-06 11:30 | BDP - 585EJ036075 | 82 | 2.6 | Yes | Yes | 19.9 | 20 | -0.1 | 3ACDB79AF4284B0A9FE9CBF2A37DC74D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Red Bluff | CA | 96080-2139 |  | 2012-06-06 | 2012-06-06 11:30 | 2012-06-06 14:26 | RHEEM - RRNA-A036JK08E | 114 | 4.4 | Yes | Yes | 19.8 | 22 | -2.2 | 272D62D1A6784B76B8AA4EE85F41E5FC |  | R22 | Non-TXV |  | 3.86% | 0.9614 | 7.417% | [5 empty] | Non-TXV | 3.86%
Stockton | CA | 95215-1708 |  | 2012-06-13 | 2012-06-13 10:41 | 2012-06-13 11:02 | RHEEM - RRKA-A030JK06X | 54 | 3.4 | Yes | Yes | 17.5 | 19.3 | -1.8 | C9E04B5550054E3BA75BDEAD3BB2B31D |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Merced | CA | 95348-1128 |  | 2012-06-06 | 2012-06-06 10:26 | 2012-06-06 10:45 | AMERICAN STANDARD - YCC030F1MOBH | 70 | 3.7 | Yes | Yes | 18.1 | 20.3 | -2.2 | 6B203FA01ED14FCA93C1C2784DE1A762 |  | R22 | Non-TXV |  | 5.286% | 0.94714 | 10.16% | [5 empty] | Non-TXV | 5.286%
Olivehurst | CA | 95961-4515 |  | 2012-07-03 | 2012-07-03 13:11 | 2012-07-03 13:11 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 17.1 | 18.1 | -1 | 3292427097BA4DF68C6202423329A6DC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Orosi | CA | 93647-9722 |  | 2012-07-23 | 2012-07-23 15:25 | 2012-07-23 15:46 | DAY & NIGHT - 36/80YAC-108C | 90 | 15.2 | Yes | Yes | 25.8 | 21 | 4.8 | 4D70993422F044DBB82A7D9DE8198CA2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.89% | 0.83111 | 32.46% | [5 empty] | Non-TXV | 16.89%
Merced | CA | 95340-4260 |  | 2012-07-14 | 2012-07-14 13:54 | 2012-07-14 13:54 | RHEEM - RPFB-024JAS | 59 | 0 | Yes | Yes | 18.3 | 21 | -2.7 | 786310DA938B4F0CBD35246903E74AF7 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-1656 |  | 2012-06-08 | 2012-06-08 12:37 | 2012-06-08 12:54 | OTHER - UNK | 78 | 5 | Yes | Yes | 21.7 | 21.3 | 0.4 | 48196234B4114DE29DE153AC52BAE8F7 |  | R22 | Non-TXV |  | 6.41% | 0.9359 | 12.32% | [5 empty] | Non-TXV | 6.41%
Atwater | CA | 95301-2550 |  | 2012-06-14 | 2012-06-14 10:47 | 2012-06-14 11:06 | AMERICAN STANDARD - 2A7A1036A1000AA | 74 | 3.8 | Yes | Yes | 19.9 | 19.5 | 0.4 | 733D13BCA7E84F07939E37837F8C6EFF |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Paradise | CA | 95969-5517 |  | 2012-07-02 | 2012-07-02 10:25 | 2012-07-02 10:44 | RUUD - RRNA-A036JK08E | 113 | 3.5 | Yes | Yes | 20.7 | 20.1 | 0.6 | 8D0772D367C240FC9AEE9D2E496D81F7 |  | R22 | Non-TXV |  | 3.097% | 0.96903 | 5.952% | [5 empty] | Non-TXV | 3.097%
Cantua Creek | CA | 93608-9707 |  | 2012-07-13 | 2012-07-13 13:59 | 2012-07-13 14:17 | GOODMAN - GSC13030QCA | 85 | 2.8 | Yes | Yes | 18.4 | 20.4 | -2 | 60DDDDC8EAF44746BA614A85E4BF0711 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Marysville | CA | 95901-9785 |  | 2012-07-25 | 2012-07-25 12:35 | 2012-07-25 12:55 | CARRIER - 38CKC036350 | 74 | -2.7 | Yes | Yes | 20.4 | 18.8 | 1.6 | 87F7B67C8F9944ADA283D4ACA57CBCA4 |  | R22 | TXV |  | -3.649% | 1.0365 | 1.022% |  |  |  |  | TXV |  |  | -3.649%
Gustine | CA | 95322-9608 |  | 2012-06-08 | 2012-06-08 10:46 | 2012-06-08 11:05 | UNITARY PRODUCTS GROUP - TGD48S21S2HA | 69 | 2 | Yes | Yes | 15.6 | 15.5 | 0.1 | 6833349E0AE44F01AA1F71D9F1167706 |  | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
Los Banos | CA | 93635-5370 |  | 2012-06-07 | 2012-06-07 11:25 | 2012-06-07 12:01 | BRYANT - 561CJ036-D | 84 | 5.4 | Yes | Yes | 20.3 | 21.8 | -1.5 | 390583E1DF7B46D79BD9F9285051F9CE |  | R22 | Non-TXV |  | 6.429% | 0.93571 | 12.35% | [5 empty] | Non-TXV | 6.429%
Los Banos | CA | 93635-5370 |  | 2012-06-07 | 2012-06-07 11:38 | 2012-06-07 12:03 | BRYANT - 561CJ036-D | 84 | 24.5 | Yes | Yes | 18.6 | 21.5 | -2.9 | 14D8843524404B7EBF55C09A015DA20C |  | R22 | Non-TXV |  | 29.17% | 0.70833 | 56.05% | [5 empty] | Non-TXV | 29.17%
Yuba City | CA | 95991-8421 |  | 2012-06-15 | 2012-06-15 09:41 | 2012-06-15 09:53 | GOODMAN - CJ30-1FB | 128 | 7.9 | Yes | Yes | 26.6 | 20.9 | 5.7 | 6050DC8455544FB6830107C7F7D753C2 |  | R22 | Non-TXV |  | 6.172% | 0.93828 | 11.86% | [5 empty] | Non-TXV | 6.172%
Merced | CA | 95348-1655 |  | 2012-06-13 | 2012-06-13 09:33 | 2012-06-13 09:54 | GOODMAN - PGB024050-1 | 56 | 2.3 | Yes | Yes | 18.4 | 19.9 | -1.5 | EA66B835C3F248658C7440E77D6BF30C |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Clovis | CA | 93611-7154 |  | 2012-06-11 | 2012-06-11 15:18 | 2012-06-11 15:41 | RUUD - UAMA-036JAS | 85 | 2.5 | Yes | Yes | 26.1 | 20.2 | 5.9 | 91FB4161C40F4630B122212335014B07 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93711-6562 |  | 2012-06-15 | 2012-06-15 16:03 | 2012-06-15 16:39 | BDP - 585GJ030040 | 54 | 2.5 | Yes | Yes | 24.6 | 19.9 | 4.7 | FC5EB35635CC42C384310D395F7D85BA |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Olivehurst | CA | 95961-4443 |  | 2012-07-17 | 2012-07-17 14:48 | 2012-07-17 15:14 | RHEEM - RAFD-031JAS | 64 | 5.3 | Yes | Yes | 22.5 | 18.7 | 3.8 | 5D2AC9D5093544B88BE05180011F5479 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.281% | 0.91719 | 15.91% | [5 empty] | Non-TXV | 8.281%
Kingsburg | CA | 93631-2040 |  | 2012-06-06 | 2012-06-06 13:34 | 2012-06-06 13:54 | GOODMAN - PGB036075-1A | 60 | 2.3 | Yes | Yes | 18.6 | 19.4 | -0.8 | 9861DC81183F478C8E900A14A1EA05F5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.833% | 0.96167 | 7.367% | [5 empty] | Non-TXV | 3.833%
Atwater | CA | 95301-4779 |  | 2012-06-15 | 2012-06-15 09:36 | 2012-06-15 09:54 | GOODMAN - CK36-1B | 76 | 2.3 | Yes | Yes | 26.7 | 21.4 | 5.3 | CAB27E55FF7442D7B0D52FB46B79F807 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Merced | CA | 95340-1609 |  | 2012-06-11 | 2012-06-11 11:21 | 2012-06-11 12:04 | PAYNE - UNK | 75 | 9.6 | Yes | Yes | 23.7 | 21.3 | 2.4 | 7CB0CC107990485894DB0A2037045F43 |  | R22 | Non-TXV |  | 12.8% | 0.872 | 24.6% | [5 empty] | Non-TXV | 12.8%
Stockton | CA | 95205-3844 |  | 2012-06-01 | 2012-06-01 10:56 | 2012-06-01 11:18 | PAYNE - PY2PNB030040ABAA | 68 | 5.3 | Yes | Yes | 17.8 | 20.2 | -2.4 | DC9C0706C0AC4BFBB013C520543FC7AA |  | R22 | Non-TXV |  | 7.794% | 0.92206 | 14.98% | [5 empty] | Non-TXV | 7.794%
Stockton | CA | 95210-2287 |  | 2012-06-21 | 2012-06-21 10:53 | 2012-06-21 11:11 | DAY & NIGHT - 585HJ036060ABAF | 101 | 15.1 | Yes | Yes | 27.5 | 22.1 | 5.4 | 923D919F0103448F82312964DF0EB6AC |  | R22 | Non-TXV |  | 14.95% | 0.8505 | 28.73% | [5 empty] | Non-TXV | 14.95%
Manteca | CA | 95336-3108 |  | 2012-05-31 | 2012-05-31 16:41 | 2012-05-31 17:06 | RHEEM - RAKA-037JAZ | 79 | 3.4 | Yes | Yes | 19.5 | 21.3 | -1.8 | 6538F58B4C614D2F9B69E9E30842F4C5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.304% | 0.95696 | 8.271% | [5 empty] | Non-TXV | 4.304%
Stockton | CA | 95205-8418 |  | 2012-06-01 | 2012-06-01 17:44 | 2012-06-01 18:08 | RUUD - UAPB-024JAZ | 51 | 3.6 | Yes | Yes | 20.3 | 20.8 | -0.5 | 922C9672A6804237B3E8FEEFE892872A |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Chico | CA | 95973-7836 |  | 2012-07-23 | 2012-07-23 09:21 | 2012-07-23 09:21 | PAYNE - PH13NR024-H | 75 | 0 | Yes | Yes | 22.5 | 21.4 | 1.1 | 9BEED1AA40CC4DA18EDCE8731C7ED100 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-2414 |  | 2012-06-11 | 2012-06-11 13:20 | 2012-06-11 13:38 | LENNOX - 10AC36-4P | 99 | 5.8 | Yes | Yes | 18.8 | 19.5 | -0.7 | DE453F386F8C464B8277D60B73832F75 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.859% | 0.94141 | 11.26% | [5 empty] | Non-TXV | 5.859%
Auburn | CA | 95603-3864 |  | 2012-06-12 | 2012-06-12 11:15 | 2012-06-12 11:43 | OTHER - 561CJ024-A | 55 | 9 | Yes | Yes | 21 | 23.1 | -2.1 | 97D03EF054BE4D368A028779DE404B61 |  | R22 | Non-TXV |  | 16.36% | 0.83636 | 31.45% | [5 empty] | Non-TXV | 16.36%
Fresno | CA | 93722-3278 |  | 2012-06-01 | 2012-06-01 10:24 | 2012-06-01 10:58 | YORK - H1RAQ42SQ6A | 85 | 17.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | 4FAA9D32EA2746719AB7422B449BFAF5 |  | R22 | Non-TXV |  | 21.06% | 0.78941 | 40.47% | [5 empty] | Non-TXV | 21.06%
Magalia | CA | 95954-9624 |  | 2012-05-31 | 2012-05-31 15:13 | 2012-05-31 17:28 | RHEEM - RRGG-05E30JKR | 48 | 2.9 | Yes | Yes | 26.1 | 24 | 2.1 | CEA7797789674C01B4F35F774E4D7470 |  | R22 | Non-TXV |  | 6.042% | 0.93958 | 11.61% | [5 empty] | Non-TXV | 6.042%
Sanger | CA | 93657-3633 |  | 2012-07-03 | 2012-07-03 10:38 | 2012-07-03 10:56 | DAY & NIGHT - N/A | 120 | 3.8 | Yes | Yes | 23.1 | 19.5 | 3.6 | 4E8D3D7D31FC43CBAE932D5CB2768FE3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Atwater | CA | 95301-4863 |  | 2012-06-12 | 2012-06-12 11:03 | 2012-06-12 11:34 | OTHER - GCGD30S43S14 | 62 | 2.6 | Yes | Yes | 19.9 | 21.2 | -1.3 | CC75C5DBFB614084BDDC2DD450EF86AD |  | R410A | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Atwater | CA | 95301-4863 |  | 2012-06-12 | 2012-06-12 11:36 | 2012-06-12 12:05 | LENNOX - HS9-311-6P | 73 | 2.5 | Yes | Yes | 18.2 | 21.2 | -3 | 7FDEB62F46664768A6F4990494938EDC |  | R22 | Non-TXV |  | 3.425% | 0.96575 | 6.581% | [5 empty] | Non-TXV | 3.425%
Atwater | CA | 95301-4765 |  | 2012-06-13 | 2012-06-13 15:21 | 2012-06-13 15:48 | AMERICAN STANDARD - YCC030F1MOBB | 70 | 3.2 | Yes | Yes | 22.7 | 19.3 | 3.4 | 59869C48D71F4CBB9DAE0A5023298ADE |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Merced | CA | 95341-5783 |  | 2012-06-07 | 2012-06-07 11:44 | 2012-06-07 11:44 | GOODMAN - GPG13240451BA | 77 | 0 | Yes | Yes | 29.6 | 24.6 | 5 | 211AC1CC9CF54105BA9C2AE414B1E99D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-9610 |  | 2012-07-09 | 2012-07-09 12:22 | 2012-07-09 12:22 | AMANA - UNK WEATHERED | 94 | 0 | Yes | Yes | 16.5 | 18.7 | -2.2 | D053D3A8D8024C73B7F753E546996477 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-9015 |  | 2012-07-13 | 2012-07-13 09:47 | 2012-07-13 09:47 | CARRIER - 38CKC036350 | 74 | 0 | Yes | Yes | 19.1 | 21.3 | -2.2 | 0E90F07D4CE14B4B86A2E5AF1CB23084 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-2575 |  | 2012-06-07 | 2012-06-07 10:16 | 2012-06-07 10:35 | RHEEM - RRPL-B036JK08X | 93 | 2.8 | Yes | Yes | 22.7 | 20.6 | 2.1 | 08779784B07B4B74992E82802ED7E9B4 |  | R410A | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Merced | CA | 95348-1627 |  | 2012-06-06 | 2012-06-06 11:49 | 2012-06-06 12:11 | YORK - DAYA-F018N045C | 85 | 4 | Yes | Yes | 20.5 | 21 | -0.5 | BFBD67553E33474CA8358539CCC39579 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Newman | CA | 95360-1484 |  | 2012-08-07 | 2012-08-07 10:04 | 2012-08-07 10:29 | OTHER - UNK | 71 | 4.2 | Yes | Yes | 18.3 | 19.6 | -1.3 | B96C03415A544C01BB3BCFBDB481AEBB |  | R22 | Non-TXV |  | 5.915% | 0.94085 | 11.37% | [5 empty] | Non-TXV | 5.915%
Yuba City | CA | 95993-6461 |  | 2012-07-12 | 2012-07-12 09:55 | 2012-07-12 10:19 | RHEEM - AT-38B10 | 42 | -4 | Yes | Yes | 22.5 | 19 | 3.5 | 02EA2D2C0A3C49A59C7D850FB0730364 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.524% | 1.0952 | 2.667% |  |  |  |  | Non-TXV |  |  | -9.524%
Fresno | CA | 93711-0583 |  | 2012-07-19 | 2012-07-19 13:58 | 2012-07-19 14:37 | YORK - H1DA030S06A | 81 | 3.7 | Yes | Yes | 18.1 | 19.8 | -1.7 | 71C2C47F17324506A5C64A6E0A9F55ED |  | R22 | Non-TXV |  | 4.568% | 0.95432 | 8.779% | [5 empty] | Non-TXV | 4.568%
Merced | CA | 95340-1509 |  | 2012-06-11 | 2012-06-11 12:02 | 2012-06-11 12:21 | AMANA - PGD42C0902E | 120 | 7.3 | Yes | Yes | 29.1 | 23.6 | 5.5 | 650EFB681BAA408EAAAC4228872DF0D5 |  | R22 | Non-TXV |  | 6.083% | 0.93917 | 11.69% | [5 empty] | Non-TXV | 6.083%
Atwater | CA | 95301-4885 |  | 2012-06-13 | 2012-06-13 11:51 | 2012-06-13 12:14 | CARRIER - 38CE003300 | 70 | 2.8 | Yes | Yes | 23.8 | 21 | 2.8 | 9F2071870CC44B37B517107A6DA09187 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Gustine | CA | 95322-9615 |  | 2012-06-08 | 2012-06-08 10:24 | 2012-06-08 10:42 | OTHER - NA | 85 | 2.5 | Yes | Yes | 28.6 | 22.7 | 6 | B1E451A4DA2C42FA88C708B5E855B846 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Chico | CA | 95926-2415 |  | 2012-06-01 | 2012-06-01 10:43 | 2012-06-01 11:17 | FRASER JOHNSTON - 60WR30 | 63 | 4.4 | Yes | Yes | 24 | 22 | 2 | 8C55D8762D9B4307A383057BDD9F6E18 |  | R22 | Non-TXV |  | 6.984% | 0.93016 | 13.42% | [5 empty] | Non-TXV | 6.984%
Manteca | CA | 95337-6819 |  | 2012-06-11 | 2012-06-11 09:05 | 2012-06-11 09:26 | TRANE - TT3736B100B0 | 86 | 2.6 | Yes | Yes | 20.4 | 20.9 | -0.5 | 75405FD156FB4DF0879F61F18849A418 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Atwater | CA | 95301-4863 |  | 2012-06-14 | 2012-06-14 10:12 | 2012-06-14 10:41 | OTHER - GCGD30S41S3A | 62 | 2.5 | Yes | Yes | 14 | 15.7 | -1.7 | 5F3129F2C1B54929BE2B84EF99E963CF |  | R22 | Non-TXV |  | 4.032% | 0.95968 | 7.749% | [5 empty] | Non-TXV | 4.032%
Los Banos | CA | 93635-9543 |  | 2012-05-31 | 2012-05-31 15:55 | 2012-05-31 16:22 | BRYANT - 588ANW036060ADAF | 67 | 8.4 | Yes | Yes | 21.5 | 20.2 | 1.4 | AFE81F56193247CDA5C93513F44A5440 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.54% | 0.87463 | 24.09% | [5 empty] | Non-TXV | 12.54%
Los Banos | CA | 93635-2817 |  | 2012-06-06 | 2012-06-06 14:51 | 2012-06-06 15:24 | AIRE-FLO - H2RC036S06A | 83 | 10.1 | Yes | Yes | 25.6 | 22.6 | 3 | FF3A83ED9FD24946A0CEF40A59BDC3DF |  | R22 | Non-TXV |  | 12.17% | 0.87831 | 23.39% | [5 empty] | Non-TXV | 12.17%
Grass Valley | CA | 95945-5622 |  | 2012-07-09 | 2012-07-09 09:02 | 2012-07-09 09:19 | PAYNE - PA12NA042-B | 101 | 4 | Yes | Yes | 25 | 19.5 | 5.5 | 10B978DC8DDC43488AB8282ECB27BF9D |  | R22 | Non-TXV |  | 3.96% | 0.9604 | 7.611% | [5 empty] | Non-TXV | 3.96%
Stockton | CA | 95209-1538 |  | 2012-06-01 | 2012-06-01 09:50 | 2012-06-01 10:08 | PAYNE - PY1PNB024040AAAA | 53 | -5 | Yes | Yes | 23.8 | 19.8 | 4 | 464E24CFAB9C471783A6D64B41594BE5 |  | R22 | TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | TXV |  |  | -9.434%
Grass Valley | CA | 95945-7517 |  | 2012-06-14 | 2012-06-14 10:28 | 2012-06-14 10:49 | PAYNE - 588ANW018040ABAD | 42 | 7.4 | Yes | Yes | 23 | 20.8 | 2.2 | 124A4145235149DEBF12C2A77A9E6CC1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.62% | 0.82381 | 33.86% | [5 empty] | Non-TXV | 17.62%
Auburn | CA | 95603-4511 |  | 2012-06-06 | 2012-06-06 10:04 | 2012-06-06 10:21 | DAY & NIGHT - UNK | 75 | 3.3 | Yes | Yes | 28 | 22.9 | 5.1 | 07139879A9DC49E98A13896DC5454F0A |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Nevada City | CA | 95959-2917 |  | 2012-07-13 | 2012-07-13 11:07 | 2012-07-13 11:36 | LENNOX - HS16-411-4P | 99 | 4.5 | Yes | Yes | 26.3 | 20.4 | 5.9 | 650C0ABF5A7041C199EC7980CEA8FAC5 |  | R22 | TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | TXV | 4.545%
Stockton | CA | 95210-2354 |  | 2012-07-02 | 2012-07-02 08:35 | 2012-07-02 08:53 | PAYNE - PY1PNB030060AAAA | 58 | -3.4 | Yes | Yes | 22 | 18.7 | 3.3 | 333FBE4E75764B0898A6FD19EE8B32FB |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Lincoln | CA | 95648-2340 |  | 2012-07-11 | 2012-07-11 15:08 | 2012-07-11 15:08 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 17.7 | 19.9 | -2.2 | 3F2EAE330D764EF69A59B042A02DDC17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-1655 |  | 2012-07-03 | 2012-07-03 10:26 | 2012-07-03 10:49 | AMERICAN STANDARD - YCC030F1M0BA | 69 | 5.3 | Yes | Yes | 19.8 | 20.2 | -0.4 | 80D2EA6983F04EFE9A9C62E1ACAD19C8 |  | R22 | Non-TXV |  | 7.681% | 0.92319 | 14.76% | [5 empty] | Non-TXV | 7.681%
Stockton | CA | 95203-1203 |  | 2012-07-04 | 2012-07-04 12:02 | 2012-07-04 12:24 | RHEEM - UNK | 56 | 7 | Yes | Yes | 16.8 | 19.2 | -2.4 | E04EBF02753A40679A32BBB5CD77560A |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Auburn | CA | 95603-4677 |  | 2012-07-06 | 2012-07-06 13:27 | 2012-07-06 13:47 | TRANE - YCC042F1MOBH | 104 | 3.1 | Yes | Yes | 26 | 21.4 | 4.6 | 6DD064011429476DA8A2C7419307D57F |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Fresno | CA | 93725-1849 |  | 2012-08-16 | 2012-08-16 13:40 | 2012-08-16 14:09 | RHEEM - RAHE-048JAS | 114 | 11.1 | Yes | Yes | 12.5 | 15.5 | -3 | CBF3F008B060479AAA69FECC83E3E949 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.737% | 0.90263 | 18.71% | [5 empty] | Non-TXV | 9.737%
Lincoln | CA | 95648-2337 |  | 2012-07-25 | 2012-07-25 14:41 | 2012-07-25 15:02 | YORK - H1RA024S060 | 59 | 2.2 | Yes | Yes | 17 | 19.5 | -2.5 | 125C9127278A4E4E9EEE28C685369A11 |  | R22 | Non-TXV |  | 3.729% | 0.96271 | 7.166% | [5 empty] | Non-TXV | 3.729%
Lincoln | CA | 95648-2336 |  | 2012-07-06 | 2012-07-06 15:09 | 2012-07-06 15:27 | YORK - H1RA024S06D | 59 | 9.9 | Yes | Yes | 19.4 | 18.9 | 0.5 | 12D02C6FB10740428DE94C7AAD7FE353 |  | R22 | Non-TXV |  | 16.78% | 0.8322 | 32.25% | [5 empty] | Non-TXV | 16.78%
Red Bluff | CA | 96080-3800 |  | 2012-07-05 | 2012-07-05 13:07 | 2012-07-05 19:47 | CARRIER - 38CKC036350 | 70 | 9.5 | Yes | Yes | 21.9 | 20.4 | 1.5 | 7C68ED1E0F3C4EAC9F66C9A740CA0744 |  | R22 | Non-TXV |  | 13.57% | 0.86429 | 26.08% | [5 empty] | Non-TXV | 13.57%
Paradise | CA | 95969-5962 |  | 2012-07-06 | 2012-07-06 09:13 | 2012-07-06 09:40 | DAY & NIGHT - 585HJW024040ABAE | 70 | 2.2 | Yes | Yes | 22.5 | 21 | 1.5 | CA551E7EF32449689528FE49C01CE021 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Planada | CA | 95365-8014 |  | 2012-07-02 | 2012-07-02 09:32 | 2012-07-02 10:00 | BRYANT - 574BNW030040NB | 128 | -4.7 | Yes | Yes | 16 | 15.3 | 0.7 | 2D33537CB7D64607AEF9AC03B1E91A45 |  | R410A | TXV |  | -3.672% | 1.0367 | 1.028% |  |  |  |  | TXV |  |  | -3.672%
Lincoln | CA | 95648-2338 |  | 2012-07-06 | 2012-07-06 15:33 | 2012-07-06 15:57 | YORK - H2RA030S06D | 62 | 8.9 | Yes | Yes | 16.7 | 18.1 | -1.4 | A7DD76490A5D4B8BA091F4D43EA761F0 |  | R22 | Non-TXV |  | 14.35% | 0.85645 | 27.59% | [5 empty] | Non-TXV | 14.35%
Oroville | CA | 95966-5314 |  | 2012-07-05 | 2012-07-05 17:06 | 2012-07-05 17:39 | TRANE - YC030F1LOAC | 108 | 5.8 | Yes | Yes | 22.5 | 21.4 | 1.1 | 7C657B26E59C4FE98C2D9A6CA8F425FE |  | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Chico | CA | 95926-1035 |  | 2012-07-19 | 2012-07-19 10:55 | 2012-07-19 10:55 | OTHER - R2A324GKR1 | 71 | 0 | Yes | Yes | 22.5 | 20.7 | 1.9 | CCB56730C74D4EE9AEA1B7739EFA3B0F |  | R22 | TXV |  | 0% | 1 | 0%
Planada | CA | 95365-8046 |  | 2012-07-02 | 2012-07-02 08:21 | 2012-07-02 09:02 | CARRIER - 48GX-048115301AD | 114 | 3.5 | Yes | Yes | 20.1 | 18.6 | 1.6 | 0D28F92D955C45F78564B4279B5365AB |  | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
Los Banos | CA | 93635-2920 |  | 2012-07-03 | 2012-07-03 11:12 | 2012-07-03 11:35 | DAY & NIGHT - 567G036 | 93 | 2.8 | Yes | Yes | 26.4 | 21 | 5.4 | 626D230FCBFB4BD1BAF575E52B3DF829 |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Fresno | CA | 93725-1887 |  | 2012-08-16 | 2012-08-16 15:39 | 2012-08-16 15:57 | LENNOX - 12GCS036X-75-3PA | 110 | 4.1 | Yes | Yes | 21.5 | 20.2 | 1.3 | 0B1FA94D9032462B9B358D61EC131930 |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.163% | [5 empty] | Non-TXV | 3.727%
Stockton | CA | 95206-5813 |  | 2012-07-03 | 2012-07-03 15:30 | 2012-07-03 15:54 | PAYNE - PY1PNB036060ABAA | 68 | 4.2 | Yes | Yes | 22.5 | 19.8 | 2.7 | 622F6738F4CD47A8B05F0F4CC1D95923 |  | R22 | Non-TXV |  | 6.176% | 0.93824 | 11.87% | [5 empty] | Non-TXV | 6.176%
Chico | CA | 95973-8360 |  | 2012-07-17 | 2012-07-17 13:34 | 2012-07-17 15:33 | RUUD - UAFD-025JAS | 52 | 1.8 | Yes | Yes | 20 | 20.7 | -0.7 | 69F23041A42E420CB22FD787AE205362 |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Merced | CA | 95348-2341 |  | 2012-07-03 | 2012-07-03 11:32 | 2012-07-03 12:05 | PAYNE - PY3GN24040NA | 73 | 2.5 | Yes | Yes | 18.5 | 19.5 | -1 | 3F1BF97565814855978D8D6D5AADA49C |  | R410A | Non-TXV |  | 3.425% | 0.96575 | 6.581% | [5 empty] | Non-TXV | 3.425%
Chico | CA | 95926-2737 |  | 2012-07-24 | 2012-07-24 14:00 | 2012-07-24 14:18 | TEMPSTAR - TCA024AKA1 | 69 | 3.1 | Yes | Yes | 20.1 | 21.9 | -1.8 | 8BA76CF3514B4CB4A7D0397C0150652C |  | R22 | Non-TXV |  | 4.493% | 0.95507 | 8.634% | [5 empty] | Non-TXV | 4.493%
Chico | CA | 95926-1033 |  | 2012-07-12 | 2012-07-12 10:19 | 2012-07-12 11:01 | PAYNE - 593BJ024-A | 67 | 5.5 | Yes | Yes | 24.1 | 21.5 | 2.6 | 70578A927F344FC29B57F5656CF576EF |  | R22 | Non-TXV |  | 8.209% | 0.91791 | 15.78% | [5 empty] | Non-TXV | 8.209%
Chico | CA | 95973-8313 |  | 2012-07-23 | 2012-07-23 17:09 | 2012-07-23 17:09 | RUUD - UAFD-025JAS | 52 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 917542C3FBF140E4BE6CDB1ABC4B6982 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3208 |  | 2012-07-10 | 2012-07-10 12:02 | 2012-07-10 12:23 | COLEMAN - UNK | 74 | 3.6 | Yes | Yes | 24.6 | 19.6 | 5 | EAC7180A1B78432097E6BC5DFA2094F4 |  | R22 | Non-TXV |  | 4.865% | 0.95135 | 9.349% | [5 empty] | Non-TXV | 4.865%
Fresno | CA | 93725-1885 |  | 2012-08-16 | 2012-08-16 11:31 | 2012-08-16 11:53 | LENNOX - 12GCS048-100-5PB | 167 | 5.6 | Yes | Yes | 19.5 | 17.3 | 2.2 | 8552D376D7864BEF80A9CD5432A2CB00 |  | R22 | Non-TXV |  | 3.353% | 0.96647 | 6.444% | [5 empty] | Non-TXV | 3.353%
Mendota | CA | 93640-0000 |  | 2012-08-15 | 2012-08-15 11:11 | 2012-08-15 11:29 | OTHER - UNK | 88 | 8.9 | Yes | Yes | 13.1 | 13.7 | -0.6 | 8E2B7DBBF86F48779CA1451AFE4CFE29 |  | R22 | Non-TXV |  | 10.11% | 0.89886 | 19.44% | [5 empty] | Non-TXV | 10.11%
Merced | CA | 95341-5610 |  | 2012-07-02 | 2012-07-02 15:08 | 2012-07-02 15:29 | AMERICAN STANDARD - YCP024F1M0BB | 118 | -6.9 | Yes | Yes | 24.6 | 19.5 | 5.1 | DDCD9583A110400CABCB143A8ED07557 |  | R22 | Non-TXV |  | -5.847% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.847%
Atwater | CA | 95301-2606 |  | 2012-07-02 | 2012-07-02 11:52 | 2012-07-02 12:25 | GOODMAN - PGB030050-REVA | 56 | 1.6 | Yes | Yes | 17.1 | 17.2 | -0.1 | 1ED46037EC164EB6B48728F1A806706C |  | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Merced | CA | 95341-5611 |  | 2012-07-03 | 2012-07-03 08:38 | 2012-07-03 08:58 | GOODMAN - PGB030075-1 | 56 | -4 | Yes | Yes | 20 | 19.9 | 0.1 | 25950DD7D03A40E9AD13E25ADFDF85C3 |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Merced | CA | 95340-4905 |  | 2012-07-02 | 2012-07-02 13:17 | 2012-07-02 13:35 | OTHER - RRKAA036JK06X | 62 | 8.3 | Yes | Yes | 23.1 | 19.5 | 3.6 | DC77CDA5F54B430CB1BAA69EF06F8908 |  | R22 | Non-TXV |  | 13.39% | 0.86613 | 25.73% | [5 empty] | Non-TXV | 13.39%
Mendota | CA | 93640-1935 |  | 2012-08-16 | 2012-08-16 13:26 | 2012-08-16 15:29 | OTHER - R4GD-042K072X | 192 | 5.6 | Yes | Yes | 21.2 | 19.5 | 1.7 | D69C73C507F7444BB45617768BA579C3 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Planada | CA | 95365-8010 |  | 2012-07-11 | 2012-07-11 10:38 | 2012-07-11 11:09 | BRYANT - 582ANW030040NAAD | 54 | 5.2 | Yes | Yes | 26 | 20.6 | 5.5 | 06565DEB5112470E86FE59A2D644D2C8 |  | R22 | Non-TXV |  | 9.63% | 0.9037 | 18.51% | [5 empty] | Non-TXV | 9.63%
Fresno | CA | 93710-4905 |  | 2012-08-16 | 2012-08-16 15:54 | 2012-08-16 15:54 | BDP - 567042R00 | 78 | 0 | Yes | Yes | 6.7 | 14.9 | -8.2 | B218B71DDFFA43C3871CBC75AE4E1739 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Mendota | CA | 93640-1935 |  | 2012-08-16 | 2012-08-16 16:50 | 2012-08-16 17:33 | WESTINGHOUSE - R4GD-036K072X | 100 | 3.2 | Yes | Yes | 15.8 | 18.2 | -2.4 | CB3652866897417E94A34FDD6391AD20 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95219-3224 |  | 2012-07-05 | 2012-07-05 14:03 | 2012-07-05 14:24 | RUUD - UANC-024JAZ | 72 | 6 | Yes | Yes | 17.6 | 19.9 | -2.3 | 47C814FFD8C34AEB9292BC238060860A |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Chico | CA | 95926-1539 |  | 2012-07-06 | 2012-07-06 17:14 | 2012-07-06 17:14 | LENNOX - M/NXC13-036-230-03 | 89 | 0 | Yes | Yes | 25.3 | 21.8 | 3.6 | 034CA72511434049865EC270FD796FD0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-9391 |  | 2012-07-02 | 2012-07-02 09:44 | 2012-07-02 10:18 | NORDYNE - R4GD-X42K100X | 192 | -11.3 | Yes | Yes | 17.2 | 18.6 | -1.4 | 879D3DB7068341A8A91D4D58796BBEED |  | R22 | Non-TXV |  | -5.885% | 1.0589 | 1.648% |  |  |  |  | Non-TXV |  |  | -5.885%
Chico | CA | 95926-3058 |  | 2012-07-13 | 2012-07-13 09:33 | 2012-07-13 09:49 | DAY & NIGHT - 591ANX03000000AAAA | 76 | 3.5 | Yes | Yes | 21 | 20.4 | 0.6 | 3FD038D60F1B47F8B897991099095B8D |  | R22 | Non-TXV |  | 4.605% | 0.95395 | 8.85% | [5 empty] | Non-TXV | 4.605%
Paradise | CA | 95969-5517 |  | 2012-07-02 | 2012-07-02 11:26 | 2012-07-02 12:26 | WESTINGHOUSE - 1D024MOA | 70 | 5.7 | Yes | Yes | 19.5 | 20.4 | -0.9 | ED62B319437A4FC59AE8D18CD01CCD0B |  | R22 | Non-TXV |  | 8.143% | 0.91857 | 15.65% | [5 empty] | Non-TXV | 8.143%
Fresno | CA | 93710-4714 |  | 2012-07-10 | 2012-07-10 11:16 | 2012-07-10 12:04 | KENMORE - E10103041 | 177 | 6.6 | Yes | Yes | 18.5 | 20.2 | -1.7 | 88FFB62EE9D9436A882FCA02683EEC56 |  | R22 | Non-TXV |  | 3.729% | 0.96271 | 7.166% | [5 empty] | Non-TXV | 3.729%
Valley Springs | CA | 95252-9508 |  | 2012-07-16 | 2012-07-16 10:06 | 2012-07-16 10:24 | HEIL - NPHCA40AK01 | 112 | 3.6 | Yes | Yes | 18.1 | 18.8 | -0.7 | 1EA3433A579A49799D8B585D4216F548 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Madera | CA | 93637-4897 |  | 2012-07-02 | 2012-07-02 10:59 | 2012-07-02 11:21 | LENNOX - 13ACD-042-230-02 | 111 | 4.1 | Yes | Yes | 24.5 | 18.5 | 6 | CDDDFD86C15742CB962C0209546DA12D |  | R22 | Non-TXV |  | 3.694% | 0.96306 | 7.098% | [5 empty] | Non-TXV | 3.694%
Fresno | CA | 93722-6345 |  | 2012-07-02 | 2012-07-02 12:44 | 2012-07-02 13:04 | CARRIER - N/A | 80 | 2.4 | Yes | Yes | 23 | 19.9 | 3.1 | 76D454E8977B4787BEE169C64CDD219B |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-3104 |  | 2012-07-06 | 2012-07-06 10:59 | 2012-07-06 10:59 | CARRIER - 48SS-024040311 | 40 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | ACAC2D486868456B9FDA080E778C4C2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6535 |  | 2012-07-06 | 2012-07-06 11:12 | 2012-07-06 11:22 | RHEEM - RRNL-B024JK06X | 77 | 2.6 | Yes | Yes | 19.2 | 20.2 | -0.9 | 139FA363A6D24EA18E240ED3AB56FB7D |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Fresno | CA | 93726-1103 |  | 2012-07-06 | 2012-07-06 08:42 | 2012-07-06 09:02 | BRYANT - 588ANW036080ACAF | 85 | 12.8 | Yes | Yes | 26.9 | 21 | 5.9 | F85D9D0BA6A047D7BCE5B298C7E94F7E |  | R22 | Non-TXV |  | 15.06% | 0.84941 | 28.94% | [5 empty] | Non-TXV | 15.06%
Fresno | CA | 93706-2417 |  | 2012-07-05 | 2012-07-05 10:29 | 2012-07-05 10:45 | RHEEM - HC 75 29 1B | 56 | 1.7 | Yes | Yes | 20.9 | 20.4 | 0.5 | BAE669ABF1B748E190C6125373D0B942 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Mendota | CA | 93640-1944 |  | 2012-07-09 | 2012-07-09 12:00 | 2012-07-09 12:17 | WESTINGHOUSE - N/A | 192 | 5.9 | Yes | Yes | 26.3 | 20.4 | 5.9 | 04B8FB165D4C47F995BC77AEF4356D59 |  | R22 | Non-TXV |  | 3.073% | 0.96927 | 5.905% | [5 empty] | Non-TXV | 3.073%
Selma | CA | 93662-9773 |  | 2012-07-03 | 2012-07-03 13:50 | 2012-07-03 14:12 | DUCANE - AC10B42-A | 98 | 3.3 | Yes | Yes | 22.4 | 19.9 | 2.6 | F14CC26D876B450DB1627B88297A0A69 |  | R22 | Non-TXV |  | 3.367% | 0.96633 | 6.471% | [5 empty] | Non-TXV | 3.367%
Merced | CA | 95348-2137 |  | 2012-07-11 | 2012-07-11 14:51 | 2012-07-11 15:23 | BDP - H585HW042 | 85 | 3.3 | Yes | Yes | 21.7 | 19.5 | 2.2 | 4FE0DA209ED34F918EE781E81FB7A4E9 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Stockton | CA | 95207-7728 |  | 2012-06-28 | 2012-06-28 13:40 | 2012-06-28 13:58 | RHEEM - RAKA-024JAZ | 50 | 5.1 | Yes | Yes | 19 | 19.8 | -0.8 | 9176D359FD6243F0BD81AAEB0ADA2F66 |  | R22 | Non-TXV |  | 10.2% | 0.898 | 19.6% | [5 empty] | Non-TXV | 10.2%
Red Bluff | CA | 96080-4521 |  | 2012-07-17 | 2012-07-17 17:53 | 2012-07-17 18:11 | COMFORT AIRE - NAC230AKA4 | 80 | 3.3 | Yes | Yes | 22.1 | 20.7 | 1.4 | F0186E873DD940DEB4BF9AC84EE22F16 |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Mendota | CA | 93640-0000 |  | 2012-08-15 | 2012-08-15 11:37 | 2012-08-15 11:55 | AIRE-FLO - UNK | 84 | 6.8 | Yes | Yes | 16.4 | 16.3 | 0.1 | DA33F635437B4935AEE67C669FE37248 |  | R22 | Non-TXV |  | 8.095% | 0.91905 | 15.56% | [5 empty] | Non-TXV | 8.095%
Marysville | CA | 95901-3524 |  | 2012-07-02 | 2012-07-02 08:41 | 2012-07-02 09:05 | TEMPSTAR - CA536VKD2 | 82 | -7.7 | Yes | Yes | 20.4 | 18.2 | 2.2 | 7780AA8BFB884B0B8C3266331C361EC6 |  | R22 | Non-TXV |  | -9.39% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.39%
Chico | CA | 95926-1032 |  | 2012-07-10 | 2012-07-10 09:41 | 2012-07-10 10:13 | RHEEM - RACC-024JAS | 70 | 5.6 | Yes | Yes | 22.6 | 20.1 | 2.5 | B844DA6D530C49AE8B016DBA68F8FC46 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Yuba City | CA | 95991-6727 |  | 2012-07-02 | 2012-07-02 11:37 | 2012-07-02 11:58 | LENNOX - 10ACC-060-230-40 | 130 | 4.7 | Yes | Yes | 20 | 20.1 | -0.1 | 0A8ED4E2CB89484E81D68DCE1C7F0C60 |  | R22 | Non-TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | Non-TXV | 3.615%
Merced | CA | 95340-3464 |  | 2012-07-10 | 2012-07-10 15:34 | 2012-07-10 19:28 | RHEEM - RAMB-036JAZ | 93 | 4.4 | Yes | Yes | 18.3 | 19.1 | -0.8 | C869134D6D154997A92CA6D9770FB9D6 |  | R22 | Non-TXV |  | 4.731% | 0.95269 | 9.092% | [5 empty] | Non-TXV | 4.731%
Clovis | CA | 93612-4231 |  | 2012-07-03 | 2012-07-03 13:56 | 2012-07-03 14:21 | OTHER - 600317A18A | 54 | 1.7 | Yes | Yes | 20.3 | 16.8 | 3.5 | BD8B427378EA451ABCECDA7AAA86C4E7 |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Clovis | CA | 93612-5867 |  | 2012-07-03 | 2012-07-03 11:28 | 2012-07-03 11:48 | DAY & NIGHT - 585HJ036060 | 102 | 3 | Yes | Yes | 23.9 | 19.3 | 4.6 | 2A90D361C818486EAB68B1242EDC2721 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93726-2040 |  | 2012-07-05 | 2012-07-05 09:21 | 2012-07-05 09:42 | DAY & NIGHT - N/A | 80 | 2.4 | Yes | Yes | 23.8 | 20.4 | 3.4 | 3A2BDDE45F3C46728B3AC00F8081D8A1 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95341-7725 |  | 2012-07-05 | 2012-07-05 11:26 | 2012-07-05 11:47 | GIBSON - JS3BA-036KA | 69 | -4.1 | Yes | Yes | 23.7 | 20.2 | 3.5 | 4F7CFC2C5E9E44F383A72358387BE738 |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Clovis | CA | 93611-2067 |  | 2012-07-09 | 2012-07-09 11:39 | 2012-07-09 12:13 | CARRIER - 48SX-06008051AA | 100 | 3.3 | Yes | Yes | 18.5 | 20.7 | -2.2 | 43E4D72485CE4C09B716C0F88C7B2510 |  | R22 | Non-TXV |  | 3.3% | 0.967 | 6.342% | [5 empty] | Non-TXV | 3.3%
Paso Robles | CA | 93446-2321 |  | 2012-07-11 | 2012-07-11 17:25 | 2012-07-11 17:42 | PAYNE - PY3GNAA24040NA | 78 | 3 | Yes | Yes | 23.8 | 20.8 | 3 | A3642361268D462AA57BA4B05CA07E9E |  | R410A | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Fresno | CA | 93725-1145 |  | 2012-08-16 | 2012-08-16 09:57 | 2012-08-16 10:16 | UNITARY PRODUCTS GROUP - DAYH-F036N070C | 108 | 3.2 | Yes | Yes | 19.8 | 17.7 | 2.1 | B027441B286D448DBD5C3EF432DE16B4 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Tracy | CA | 95376-1894 |  | 2012-07-03 | 2012-07-03 09:58 | 2012-07-03 10:34 | OTHER - CA36K-1S | 50 | 1.6 | Yes | Yes | 19.9 | 19.3 | 0.6 | B46C1EBC05A84BDEA0441FDE6E4A7CC1 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Chico | CA | 95926-2749 |  | 2012-07-20 | 2012-07-20 10:58 | 2012-07-20 12:02 | BRYANT - AA1CJ018-C | 69 | 6 | Yes | Yes | 26.2 | 21.9 | 4.3 | F97C106F81EC4977B420F209A6B268B8 |  | R22 | TXV |  | 8.696% | 0.91304 | 16.71% | [5 empty] | TXV | 8.696%
Merced | CA | 95341-6983 |  | 2012-08-08 | 2012-08-08 12:52 | 2012-08-08 13:09 | AIRE-FLO - PY1PNB030040AAAA | 55 | 7.4 | Yes | Yes | 28.5 | 22.5 | 6 | 480310CA9E1A44A5874A6F4D9F1989B2 |  | R22 | Non-TXV |  | 13.45% | 0.86545 | 25.86% | [5 empty] | Non-TXV | 13.45%
Stockton | CA | 95210-4631 |  | 2012-08-09 | 2012-08-09 12:11 | 2012-08-09 12:11 | BRYANT - 563CN018-B | 80 | 0 | Yes | Yes | 18.1 | 18.6 | -0.5 | A3551AA8BC464ED8B1ADCED085392EC1 |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4138 |  | 2012-07-05 | 2012-07-05 10:58 | 2012-07-05 11:17 | OTHER - DBYPF036N070A | 108 | 6.6 | Yes | Yes | 25.6 | 24 | 1.6 | 5917D811712B43DD8844701E1A1B025F |  | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Chico | CA | 95926-3052 |  | 2012-07-02 | 2012-07-02 11:47 | 2012-07-02 12:17 | DAY & NIGHT - 591ANX030000AAAA | 76 | 5.9 | Yes | Yes | 24 | 20.4 | 3.6 | 21A50293D449489182A4C9BB12383290 |  | R22 | Non-TXV |  | 7.763% | 0.92237 | 14.92% | [5 empty] | Non-TXV | 7.763%
Planada | CA | 95365-8021 |  | 2012-07-02 | 2012-07-02 12:48 | 2012-07-02 12:48 | WESTINGHOUSE - FS3BA-024KA | 64 | 0 | Yes | Yes | 16.6 | 16.4 | 0.3 | 6B0976E785154A7A9869838D49F7A1D1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3789 |  | 2012-07-05 | 2012-07-05 12:53 | 2012-07-05 13:20 | BDP - 561AJ024-E | 55 | 1.6 | Yes | Yes | 22.7 | 20.6 | 2.1 | 7AF56A63A613496DB47573BE7A3297C7 |  | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Mendota | CA | 93640-1941 |  | 2012-07-09 | 2012-07-09 10:55 | 2012-07-09 11:12 | WESTINGHOUSE - R4GD-042K096X | 192 | 5.6 | Yes | Yes | 19.6 | 19.9 | -0.3 | A856797FDF304D43BF92C2B870C4408B |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Rocklin | CA | 95677-3123 |  | 2012-07-19 | 2012-07-19 15:49 | 2012-07-19 16:06 | DAY & NIGHT - 585B018050YACR | 52 | 11.3 | Yes | Yes | 19.4 | 19.3 | 0.1 | B6C6D82E20164660BC180850FCD5D037 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.73% | 0.78269 | 41.76% | [5 empty] | Non-TXV | 21.73%
Paradise | CA | 95969-3354 |  | 2012-07-02 | 2012-07-02 09:45 | 2012-07-02 10:09 | CARRIER - 38CK036340 | 71 | 3.3 | Yes | Yes | 21 | 20.7 | 0.3 | 796DB8C99EDF40A88C987C32D5B03E29 |  | R22 | Non-TXV |  | 4.648% | 0.95352 | 8.932% | [5 empty] | Non-TXV | 4.648%
Auburn | CA | 95603-4515 |  | 2012-07-03 | 2012-07-03 08:58 | 2012-07-03 09:19 | DAY & NIGHT - 588ANW024060 | 40 | 1.2 | Yes | Yes | 17 | 19.5 | -2.5 | A80E2D90E7D2459E825B9A829BCBC375 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Lincoln | CA | 95648-2340 |  | 2012-07-25 | 2012-07-25 14:13 | 2012-07-25 14:34 | YORK - H2RA030S060 | 61 | 2.3 | Yes | Yes | 18 | 20.3 | -2.3 | F5BD60C5C0E84FBEBA125C23FE61F687 |  | R22 | Non-TXV |  | 3.77% | 0.9623 | 7.246% | [5 empty] | Non-TXV | 3.77%
Rocklin | CA | 95677-3648 |  | 2012-07-03 | 2012-07-03 10:38 | 2012-07-03 10:59 | OTHER - UNK | 92 | 14 | Yes | Yes | 18 | 20.4 | -2.4 | B4B25B14E3A343F098B45CF1DA37BCB1 |  | R22 | Non-TXV |  | 15.22% | 0.84783 | 29.24% | [5 empty] | Non-TXV | 15.22%
Mendota | CA | 93640-1941 |  | 2012-08-16 | 2012-08-16 17:37 | 2012-08-16 17:57 | WESTINGHOUSE - R4GD-036K072X | 100 | 5 | Yes | Yes | 21.2 | 19.3 | 2 | 4C6417277ADF423CA6F029599FACF58D |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Auburn | CA | 95603-3738 |  | 2012-07-24 | 2012-07-24 11:23 | 2012-07-24 11:40 | OTHER - 7B0023B100A1 | 54 | 9.8 | Yes | Yes | 25 | 20.2 | 4.8 | 96FF4E4D368A49F38FFCB8E4C9581028 |  | R22 | Non-TXV |  | 18.15% | 0.81852 | 34.88% | [5 empty] | Non-TXV | 18.15%
Mendota | CA | 93640-1942 |  | 2012-08-16 | 2012-08-16 12:51 | 2012-08-16 13:07 | WESTINGHOUSE - UNK | 100 | 3.3 | Yes | Yes | 19.4 | 18.6 | 0.8 | 19DC9DEEBE5C41769738E2F3841CA302 |  | R22 | Non-TXV |  | 3.3% | 0.967 | 6.342% | [5 empty] | Non-TXV | 3.3%
Oroville | CA | 95966-5378 |  | 2012-07-18 | 2012-07-18 09:13 | 2012-07-18 09:29 | OTHER - NA | 90 | 3.7 | Yes | Yes | 24.5 | 21.2 | 3.3 | 4A9ADA26931B4F6EA74936D46A72C39D |  | R22 | Non-TXV |  | 4.111% | 0.95889 | 7.901% | [5 empty] | Non-TXV | 4.111%
Red Bluff | CA | 96080-5101 |  | 2012-07-06 | 2012-07-06 08:33 | 2012-07-06 08:49 | RHEEM - NA | 100 | 4.8 | Yes | Yes | 19.2 | 21.4 | -2.2 | AB4BDD912E784A33B5B24860F137CE60 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Los Banos | CA | 93635-3951 |  | 2012-07-06 | 2012-07-06 08:41 | 2012-07-06 09:11 | RUUD - UNMA036JAZ | 75 | -5.3 | Yes | Yes | 18.6 | 19.4 | -0.8 | 47FAF4B7C91446B4A3A8B8C5B14CC7D1 |  | R22 | Non-TXV |  | -7.067% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.067%
Fresno | CA | 93727-6830 |  | 2012-07-06 | 2012-07-06 14:17 | 2012-07-06 15:00 | LENNOX - GCS29X-036-75-2PA | 58 | 3 | Yes | Yes | 24.5 | 20.9 | 3.6 | 60926AE10A274A45BACF6277E36765E9 |  | R22 | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Merced | CA | 95348-2206 |  | 2012-07-12 | 2012-07-12 11:02 | 2012-07-12 13:11 | GOODMAN - CKL36-1L | 95 | 2.8 | Yes | Yes | 18.9 | 20.4 | -1.5 | 635D182D358048F8943CA9E2618A878B |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Los Banos | CA | 93635-9421 |  | 2012-07-09 | 2012-07-09 09:47 | 2012-07-09 10:13 | BRYANT - 561CJ042B | 83 | 8.3 | Yes | Yes | 30.4 | 25.3 | 5.1 | 37753A160EF74CF48CAB1AF2226F3FE6 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Murphys | CA | 95247-9337 |  | 2012-07-17 | 2012-07-17 09:02 | 2012-07-17 09:19 | CARRIER - UNK | 83 | -4.9 | Yes | Yes | 21.1 | 19.3 | 1.8 | 4EC7281929DB4039AD22EDA65784E7BD |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Fresno | CA | 93722-4728 |  | 2012-07-02 | 2012-07-02 10:32 | 2012-07-02 10:32 | CARRIER - N/A | 80 | 0 | Yes | Yes | 20.8 | 18.9 | 2 | BA4727B01594453698CE83CD1F7F6CA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7046 |  | 2012-07-06 | 2012-07-06 15:16 | 2012-07-06 15:33 | GIBSON - UNK | 59 | 3.2 | Yes | Yes | 18.1 | 20.4 | -2.3 | 1E854CF2C20D4D9FB08CC6A92D1B8D5B |  | R22 | Non-TXV |  | 5.424% | 0.94576 | 10.42% | [5 empty] | Non-TXV | 5.424%
Fresno | CA | 93727-2035 |  | 2012-07-06 | 2012-07-06 11:25 | 2012-07-06 11:41 | ICP - PGC042K080E | 84 | 3.2 | Yes | Yes | 21.4 | 20.1 | 1.3 | EAB6F5103A644735BDB9F69EB23AB84C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Los Banos | CA | 93635-5329 |  | 2012-07-05 | 2012-07-05 13:10 | 2012-07-05 13:25 | - 562CJ036B | 96 | 6.8 | Yes | Yes | 27.2 | 26.7 | 0.5 | AD9A030B7F304595AD8CF0EA226B272B |  | R22 | TXV |  | 7.083% | 0.92917 | 13.61% | [5 empty] | TXV | 7.083%
Los Banos | CA | 93635-9448 |  | 2012-07-09 | 2012-07-09 10:24 | 2012-07-09 10:53 | BRYANT - 561CJ036E | 68 | 11.6 | Yes | Yes | 32 | 27.7 | 4.3 | 616834E7BB61442780FD2993C7EEE9D7 |  | R22 | Non-TXV |  | 17.06% | 0.82941 | 32.78% | [5 empty] | Non-TXV | 17.06%
Sanger | CA | 93657-2158 |  | 2012-07-23 | 2012-07-23 09:51 | 2012-07-23 10:10 | PAYNE - N/A | 90 | 2.8 | Yes | Yes | 19.9 | 22.6 | -2.7 | E41EB69C896949A5B9838D4F0220026A |  | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Dinuba | CA | 93618-3739 |  | 2012-07-02 | 2012-07-02 11:03 | 2012-07-02 11:25 | ICP - NAC060AKA9 | 130 | 4.1 | Yes | Yes | 22.5 | 18.5 | 4 | FACEC1A0706245A1987371B0FC9EE6D4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.154% | 0.96846 | 6.061% | [5 empty] | Non-TXV | 3.154%
Clovis | CA | 93612-2690 |  | 2012-07-18 | 2012-07-18 17:27 | 2012-07-18 17:43 | YORK - D1NPO30N05605A | 73 | -4.3 | Yes | Yes | 18.7 | 20.4 | -1.7 | 6EE647985C2E4BD7A70C725EA38AD7A0 |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Gridley | CA | 95948-9405 |  | 2012-07-24 | 2012-07-24 11:05 | 2012-07-24 11:31 | AMANA - RCC48A2B | 138 | 5.9 | Yes | Yes | 20.7 | 19.9 | 0.8 | 85FAC125F6FF44458D01B0D6C4B19A50 |  | R22 | Non-TXV |  | 4.275% | 0.95725 | 8.216% | [5 empty] | Non-TXV | 4.275%
Stockton | CA | 95206-5162 |  | 2012-07-09 | 2012-07-09 11:27 | 2012-07-09 11:45 | DAY & NIGHT - 591AN048-C | 128 | 5.9 | Yes | Yes | 22.3 | 18 | 4.3 | DD4D90757C7147EA8DFAB68810286560 |  | R22 | Non-TXV |  | 4.609% | 0.95391 | 8.858% | [5 empty] | Non-TXV | 4.609%
Clovis | CA | 93612-2337 |  | 2012-07-13 | 2012-07-13 13:01 | 2012-07-13 13:25 | YORK - 36ECW080GB | 129 | 4 | Yes | Yes | 21.5 | 21.3 | 0.3 | 1CD16BB6633E494F8CC940563BB1F056 |  | R22 | Non-TXV |  | 3.101% | 0.96899 | 5.959% | [5 empty] | Non-TXV | 3.101%
Chico | CA | 95926-2763 |  | 2012-07-25 | 2012-07-25 11:14 | 2012-07-25 11:31 | DAY & NIGHT - N4A324AKB200 | 59 | 6 | Yes | Yes | 23.5 | 21.3 | 2.3 | B29F44C3FFB24B23A664F8ECF350D2C0 |  | R410A | TXV |  | 10.17% | 0.89831 | 19.54% | [5 empty] | TXV | 10.17%
Dos Palos | CA | 93620-2637 |  | 2012-07-06 | 2012-07-06 14:40 | 2012-07-06 15:16 | GOODMAN - PG8030050-1 | 56 | 4.4 | Yes | Yes | 22.9 | 22.4 | 0.5 | C380D6057F8746A095DB8E38DED33DE3 |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Dinuba | CA | 93618-3525 |  | 2012-07-11 | 2012-07-11 10:35 | 2012-07-11 10:59 | CARRIER - 38CKC042310 | 83 | 13.9 | Yes | Yes | 22.9 | 19.2 | 3.7 | 18D6AC551162490E9D5E33AE5E55C891 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16.75% | 0.83253 | 32.18% | [5 empty] | Non-TXV | 16.75%
Fresno | CA | 93710-3914 |  | 2012-08-16 | 2012-08-16 10:23 | 2012-08-16 10:48 | CARRIER - 2ABS342AAAA | 107 | 8.6 | Yes | Yes | 17.7 | 19.2 | -1.5 | 26B4CF4017E143DF9E43BE96BDFB049A |  | R22 | Non-TXV |  | 8.037% | 0.91963 | 15.45% | [5 empty] | Non-TXV | 8.037%
Stockton | CA | 95210-1469 |  | 2012-07-02 | 2012-07-02 14:03 | 2012-07-02 14:26 | PAYNE - PY1PNB030060AAAA | 55 | 3.2 | Yes | Yes | 19.9 | 20.6 | -0.7 | 3EB6E80377734EC098ADDD8C4AFF7958 |  | R22 | Non-TXV |  | 5.818% | 0.94182 | 11.18% | [5 empty] | Non-TXV | 5.818%
Ripon | CA | 95366-2193 |  | 2012-07-02 | 2012-07-02 15:45 | 2012-07-02 16:04 | BDP - 5658J030 B | 113 | 3.4 | Yes | Yes | 19.6 | 20.4 | -0.8 | 1BBBBE4F6F7143D981E14457AC4616F4 |  | R22 | Non-TXV |  | 3.009% | 0.96991 | 5.782% | [5 empty] | Non-TXV | 3.009%
Madera | CA | 93637-3310 |  | 2012-07-02 | 2012-07-02 13:48 | 2012-07-02 15:17 | YORK - D1NA036N03606C | 67 | 3.7 | Yes | Yes | 22.5 | 19.5 | 3 | D134F17F7B6A4F679940425C91FDC356 |  | R22 | Non-TXV |  | 5.522% | 0.94478 | 10.61% | [5 empty] | Non-TXV | 5.522%
Riverbank | CA | 95367-3900 |  | 2012-07-12 | 2012-07-12 13:38 | 2012-07-12 13:56 | OTHER - UNK | 64 | 3 | Yes | Yes | 18.9 | 19.2 | -0.3 | 13D5D329280C4E80954F418E9CDBEB86 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Sanger | CA | 93657-3217 |  | 2012-07-03 | 2012-07-03 11:47 | 2012-07-03 12:14 | GOODMAN - GPG13300701BB | 77 | 2.8 | Yes | Yes | 26.9 | 21 | 5.9 | A1545D34A6BE442EBE8CE3072D86A859 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Winton | CA | 95388-0000 |  | 2012-07-05 | 2012-07-05 10:21 | 2012-07-05 10:38 | RHEEM - RRKA-A036JK06X | 62 | 1.9 | Yes | Yes | 25.7 | 20.1 | 5.7 | 0A42F319164C4E53A218D66D7A3AD547 |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Dinuba | CA | 93618-9392 |  | 2012-07-02 | 2012-07-02 10:23 | 2012-07-02 10:43 | DAY & NIGHT - 588ANW030040ABAD | 88 | 2.7 | Yes | Yes | 21.3 | 19.7 | 1.6 | 4E0866305AFD4AC3810078B01967BC2A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Los Banos | CA | 93635-9488 |  | 2012-07-09 | 2012-07-09 11:07 | 2012-07-09 11:35 | AIRE-FLO - 561CJ060H | 131 | 15.5 | Yes | Yes | 25.1 | 24.8 | 0.3 | C9E46D0BBAE74E74B8CC83042C742B33 |  | R22 | Non-TXV |  | 11.83% | 0.88168 | 22.74% | [5 empty] | Non-TXV | 11.83%
Merced | CA | 95340-2729 |  | 2012-07-14 | 2012-07-14 08:15 | 2012-07-14 08:42 | YORK - H4DB036S06A | 73 | 2.2 | Yes | Yes | 16.6 | 19.1 | -2.5 | E3714912B52242CAA5A50FD4AB9FAB14 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Stockton | CA | 95206-4679 |  | 2012-08-09 | 2012-08-09 10:28 | 2012-08-09 10:28 | PAYNE - PA13NR030-J | 75 | 0 | Yes | Yes | 15 | 17.4 | -2.4 | DB18D2007DE74A53BA6322133C845130 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-1032 |  | 2012-07-12 | 2012-07-12 09:57 | 2012-07-12 10:13 | OTHER - TGA024AKA1 | 69 | 2.7 | Yes | Yes | 23.5 | 21.3 | 2.2 | C9296BB493BC4E289402D9E1AF1BBFDD |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Clovis | CA | 93612-2460 |  | 2012-07-05 | 2012-07-05 10:52 | 2012-07-05 11:18 | OTHER - UNK | 62 | 4.5 | Yes | Yes | 17.6 | 20.2 | -2.6 | 7368E3AD828F4D9E8A4311919336E2B5 |  | R22 | Non-TXV |  | 7.258% | 0.92742 | 13.95% | [5 empty] | Non-TXV | 7.258%
Lathrop | CA | 95330-8939 |  | 2012-07-02 | 2012-07-02 09:49 | 2012-07-02 10:10 | GOODMAN - CKL36-1H | 71 | 2.2 | Yes | Yes | 17.4 | 18.2 | -0.8 | CED2265722E54F6D880592D8B72AF0B8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.099% | 0.96901 | 5.955% | [5 empty] | Non-TXV | 3.099%
Chico | CA | 95926-3148 |  | 2012-07-10 | 2012-07-10 12:27 | 2012-07-10 13:05 | AMERICAN STANDARD - YCX024F1LOAB | 69 | 5.8 | Yes | Yes | 21.1 | 21 | 0.1 | 14CFEB049B4B401FB3497681456D9F79 |  | R22 | Non-TXV |  | 8.406% | 0.91594 | 16.15% | [5 empty] | Non-TXV | 8.406%
Stockton | CA | 95203-2252 |  | 2012-07-11 | 2012-07-11 09:34 | 2012-07-11 09:54 | DAY & NIGHT - 565AJ018 | 50 | 4.9 | Yes | Yes | 18.1 | 19.9 | -1.8 | 2B8307FCBCD64E7BA04A3AB4AEDB4F91 |  | R22 | Non-TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | Non-TXV | 9.8%
Clovis | CA | 93612-1581 |  | 2012-07-10 | 2012-07-10 10:48 | 2012-07-10 11:07 | PAYNE - 585GJ018040 | 55 | 1.6 | Yes | Yes | 20.4 | 19.9 | 0.5 | 35C0310E5EC64CFDBE9FA9A0628012A7 |  | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Stockton | CA | 95203-2250 |  | 2012-07-04 | 2012-07-04 10:45 | 2012-07-04 11:02 | DAY & NIGHT - 565AJ018 | 50 | 2.5 | Yes | Yes | 22.7 | 18.7 | 4 | 26A2D805C29F4FBAAD2C6F8A6248143A |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Merced | CA | 95341-6620 |  | 2012-07-23 | 2012-07-23 14:50 | 2012-07-23 15:12 | YORK - D3NZ030N05606NXA | 64 | 1.9 | Yes | Yes | 19.5 | 20.9 | -1.4 | 4B9EDEBB677D46F3959932DB02C84240 |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Merced | CA | 95341-6539 |  | 2012-07-03 | 2012-07-03 10:48 | 2012-07-03 11:16 | TRANE - BTD736A100B0 | 88 | -5.2 | Yes | Yes | 22.9 | 21.4 | 1.5 | 016A7FBD2A1C462BB779F3475D720385 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Clovis | CA | 93612-5062 |  | 2012-07-09 | 2012-07-09 10:15 | 2012-07-09 10:33 | GOODMAN - PGB030050-1REVA | 66 | 2.5 | Yes | Yes | 18.3 | 19.6 | -1.3 | 9209E24B72DE49FAA4074E753C6A71D3 |  | R22 | Non-TXV |  | 3.788% | 0.96212 | 7.279% | [5 empty] | Non-TXV | 3.788%
Sanger | CA | 93657-3508 |  | 2012-07-10 | 2012-07-10 17:01 | 2012-07-10 17:01 | UNITARY PRODUCTS GROUP - DCYZ-F042N080A | 78 | 0 | Yes | Yes | 18.1 | 20.8 | -2.7 | 67DF3EBBA2CB4901B988CDBDB17D9153 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4433 |  | 2012-07-05 | 2012-07-05 10:51 | 2012-07-05 11:14 | LENNOX - 10GCS036X-75-3PA | 58 | 1.7 | Yes | Yes | 25.3 | 20.4 | 4.9 | 213915C2D1104B0EB7A7C2BC1B86ABFB |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Mendota | CA | 93640-1935 |  | 2012-07-11 | 2012-07-11 15:25 | 2012-07-11 15:43 | WESTINGHOUSE - UNK | 71 | 3.2 | Yes | Yes | 17.8 | 20.4 | -2.6 | 01802AE523E24229B3E9490F5F07BCDE |  | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
Fresno | CA | 93727-6905 |  | 2012-07-06 | 2012-07-06 15:06 | 2012-07-06 15:25 | COLEMAN - ERC0241BBB | 88 | 3.5 | Yes | Yes | 22.5 | 20.1 | 2.4 | F71607ACECDF4C93B94D97D6A51462FF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.977% | 0.96023 | 7.643% | [5 empty] | Non-TXV | 3.977%
Chico | CA | 95926-2760 |  | 2012-07-23 | 2012-07-23 12:58 | 2012-07-23 14:16 | PAYNE - CDCB-4260 | 56 | 7.5 | Yes | Yes | 25 | 22.3 | 2.7 | 73214F0EDDF84251BBD1581E9F9A00AA |  | R22 | Non-TXV |  | 13.39% | 0.86607 | 25.74% | [5 empty] | Non-TXV | 13.39%
Los Banos | CA | 93635-3775 |  | 2012-07-05 | 2012-07-05 09:54 | 2012-07-05 10:16 | TRANE - BTD72AA100CO | 68 | 7.9 | Yes | Yes | 16.6 | 17.7 | -1.1 | 1F76F8CD672742C28AC841DEC747DB66 |  | R22 | Non-TXV |  | 11.62% | 0.88382 | 22.33% | [5 empty] | Non-TXV | 11.62%
Atwater | CA | 95301-4891 |  | 2012-07-03 | 2012-07-03 11:38 | 2012-07-03 11:57 | RHEEM - RAFA-030JAQ | 59 | 1.8 | Yes | Yes | 17.5 | 19.2 | -1.7 | 0299916B734644DD87D550F1AAE87C26 |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Fresno | CA | 93710-4722 |  | 2012-07-09 | 2012-07-09 09:24 | 2012-07-09 10:01 | GOODMAN - CK36-1A | 73 | -4.3 | Yes | Yes | 21.8 | 20.9 | 0.9 | A1A4E19F70E34ED187DF3AC46329360B |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Fresno | CA | 93706-2846 |  | 2012-07-30 | 2012-07-30 14:30 | 2012-07-30 15:38 | GOODMAN - GPG1330045 | 80 | 2.6 | Yes | Yes | 18.5 | 19.3 | -0.8 | FA9088B1C6AB41C3879D9F00CF61709A |  | R410A | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Paradise | CA | 95969-2347 |  | 2012-07-02 | 2012-07-02 09:13 | 2012-07-02 09:13 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 19.2 | 20.4 | -1.2 | 42CC35BF74534A86B1C8D291E7A05E35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-2021 |  | 2012-07-02 | 2012-07-02 18:55 | 2012-07-02 19:12 | RHEEM - UNK | 69 | 10 | Yes | Yes | 23.3 | 18.1 | 5.2 | 5FF9186B7AF14FE4880FFF606D56D7CA |  | R22 | Non-TXV |  | 14.49% | 0.85507 | 27.85% | [5 empty] | Non-TXV | 14.49%
Los Banos | CA | 93635-3097 |  | 2012-07-06 | 2012-07-06 10:08 | 2012-07-06 10:32 | GIBSON - UNK | 75 | -4.4 | Yes | Yes | 21.8 | 21 | 0.8 | 772BD4485DC44937B1DC30D7E4F0B646 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Paradise | CA | 95969-3918 |  | 2012-07-02 | 2012-07-02 13:43 | 2012-07-02 13:43 | DAY & NIGHT - 5EJW30075ABHE | 58 | 0 | Yes | Yes | 21.9 | 20.7 | 1.3 | 7844499A33D34C1FB0B84AA7F9774F43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3772 |  | 2012-07-03 | 2012-07-03 13:11 | 2012-07-03 13:32 | TRANE - BTD724A100C0 | 68 | 4.9 | Yes | Yes | 20.3 | 19.9 | 0.4 | 91DEBB3D322A45A09EDA4D40696A5C00 |  | R22 | Non-TXV |  | 7.206% | 0.92794 | 13.85% | [5 empty] | Non-TXV | 7.206%
Fresno | CA | 93706-3220 |  | 2012-07-05 | 2012-07-05 10:48 | 2012-07-05 11:07 | GOODMAN - PGF330060K01AL | 98 | 3 | Yes | Yes | 20.6 | 19.6 | 1 | AF886F150E69496DBCD6B4B979316D1C |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Marysville | CA | 95901-9469 |  | 2012-07-02 | 2012-07-02 15:52 | 2012-07-02 16:11 | YORK - H1RD042S06G | 152 | 9.9 | Yes | Yes | 22.3 | 21 | 1.3 | 872DFD39765F49E3B2CDC6EF06ACB254 |  | R22 | Non-TXV |  | 6.513% | 0.93487 | 12.52% | [5 empty] | Non-TXV | 6.513%
Yuba City | CA | 95991-6644 |  | 2012-07-16 | 2012-07-16 11:46 | 2012-07-16 12:10 | DAY & NIGHT - UNK | 60 | 7.6 | Yes | Yes | 18 | 21 | -3 | D90AB250BE2C4FAE9DC9E76269DB328A |  | R22 | Non-TXV |  | 12.67% | 0.87333 | 24.34% | [5 empty] | Non-TXV | 12.67%
Fresno | CA | 93725-1857 |  | 2012-07-05 | 2012-07-05 14:26 | 2012-07-05 14:43 | LENNOX - HS25-311-1P | 128 | 4.6 | Yes | Yes | 21.3 | 21.5 | -0.2 | 5D6E8EA6DE764208810AB1F775DF52BC |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Los Banos | CA | 93635-6336 |  | 2012-07-05 | 2012-07-05 11:56 | 2012-07-05 12:16 | GOODMAN - CKJ301A | 85 | 11.3 | Yes | Yes | 23.3 | 20.4 | 2.9 | FB25B647A7604FB2A9F2E494785CD29A |  | R22 | Non-TXV |  | 13.29% | 0.86706 | 25.55% | [5 empty] | Non-TXV | 13.29%
Stockton | CA | 95204-1908 |  | 2012-07-06 | 2012-07-06 15:06 | 2012-07-06 15:06 | BRYANT - 582ANW036090AAAF | 56 | 0 | Yes | Yes | 16.2 | 19.1 | -2.9 | 01CBC9192E1F40F48F1B9A440F416616 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Orange Cove | CA | 93646-9315 |  | 2012-08-08 | 2012-08-08 13:10 | 2012-08-08 13:40 | UNITARY PRODUCTS GROUP - AC018M1021A | 49 | 3 | Yes | Yes | 25.8 | 20.1 | 5.7 | 7707ED3002D4415FA4C9D6A412010B1B |  | R22 | Non-TXV |  | 6.122% | 0.93878 | 11.77% | [5 empty] | Non-TXV | 6.122%
Los Banos | CA | 93635-3739 |  | 2012-07-03 | 2012-07-03 10:39 | 2012-07-03 11:07 | HEIL - NAC036AKA1 | 87 | 4 | Yes | Yes | 21 | 19 | 2 | 1975EC64E5CA4BD1AA7FCDC3E694C69F |  | R22 | Non-TXV |  | 4.598% | 0.95402 | 8.836% | [5 empty] | Non-TXV | 4.598%
Marysville | CA | 95901-8252 |  | 2012-07-13 | 2012-07-13 11:28 | 2012-07-13 11:46 | CARRIER - 38CKC030340 | 75 | 6.8 | Yes | Yes | 16 | 19 | -3 | DE5B29DE202E4AB08BCA0F71D319DE3D |  | R22 | Non-TXV |  | 9.067% | 0.90933 | 17.42% | [5 empty] | Non-TXV | 9.067%
Fresno | CA | 93710-5263 |  | 2012-07-02 | 2012-07-02 15:18 | 2012-07-02 15:41 | DAY & NIGHT - N/A | 64 | 1.9 | Yes | Yes | 20.1 | 21 | -0.9 | DBB8FEFC05A64E7D8229FD320F476569 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Oroville | CA | 95966-5206 |  | 2012-07-10 | 2012-07-10 09:16 | 2012-07-10 09:16 | TRANE - YCX042F1M0BD | 117 | 0 | Yes | Yes | 24 | 21.8 | 2.2 | 1655C07C2309422EA2A8784C379BFE5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-3557 |  | 2012-07-06 | 2012-07-06 09:35 | 2012-07-06 10:06 | CARRIER - 38EH048320 | 137 | 5.1 | Yes | Yes | 22.9 | 20.4 | 2.5 | D280D425318741A5ACDDB5CEA8AA5596 |  | R22 | Non-TXV |  | 3.723% | 0.96277 | 7.154% | [5 empty] | Non-TXV | 3.723%
Atwater | CA | 95301-2547 |  | 2012-07-02 | 2012-07-02 09:06 | 2012-07-02 09:28 | GOODMAN - GSH13003001AA | 85 | 2.6 | Yes | Yes | 17.2 | 18.5 | -1.3 | 7EE7F8FA398E41FBA93068F4986F51DC |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Madera | CA | 93637-5420 |  | 2012-07-03 | 2012-07-03 10:31 | 2012-07-03 10:56 | OTHER - 585A036080YAC | 60 | 8.3 | Yes | Yes | 26.4 | 26.5 | -0.1 | D53D351D7D2F432588118E54C11B79AC |  | R22 | Non-TXV |  | 13.83% | 0.86167 | 26.58% | [5 empty] | Non-TXV | 13.83%
Merced | CA | 95341-6627 |  | 2012-07-03 | 2012-07-03 11:45 | 2012-07-03 12:21 | RHEEM - N/A | 50 | 1.5 | Yes | Yes | 23.6 | 23 | 0.6 | 5E344A9D13C542288F01021B5CA076F8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93710-6554 |  | 2012-07-06 | 2012-07-06 14:05 | 2012-07-06 15:14 | YORK - D1NA024N03606C | 54 | 2.1 | Yes | Yes | 19.1 | 20.4 | -1.3 | D9D2F6EC077346F8B392D19F5496B9B3 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Stockton | CA | 95210-2601 |  | 2012-07-02 | 2012-07-02 10:41 | 2012-07-02 10:58 | ICP - GPCM036K060D | 70 | 2.5 | Yes | Yes | 19.4 | 18.8 | 0.6 | C73FF5ACDE4842E095A20F20DC342CB5 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Fresno | CA | 93710-6535 |  | 2012-07-06 | 2012-07-06 12:58 | 2012-07-06 12:58 | OTHER - 60WR24A12 | 85 | 0 | Yes | Yes | 19.4 | 21.5 | -2.1 | 05E077F051C547BEAEB311243CE860C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6535 |  | 2012-07-06 | 2012-07-06 12:31 | 2012-07-06 12:51 | OTHER - 60WR24A1P | 53 | 1.8 | Yes | Yes | 18.6 | 20.4 | -1.8 | 21936A03314A4B9EA351AE3E35B35ABF |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Lathrop | CA | 95330-8848 |  | 2012-07-02 | 2012-07-02 12:09 | 2012-07-02 12:37 | BRYANT - 38EZG042300 | 100 | 20.6 | Yes | Yes | 20.2 | 21.5 | -1.3 | 5AB1560068DB4B66B275711CD3F21106 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 20.6% | 0.794 | 39.59% | [5 empty] | Non-TXV | 20.6%
Paradise | CA | 95969-4523 |  | 2012-07-17 | 2012-07-17 10:59 | 2012-07-17 11:20 | BRYANT - 30-579A | 44 | 2.3 | Yes | Yes | 21.5 | 20.7 | 0.8 | B0A2FD5EA1064783A2CD497CD9D1C481 |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Fresno | CA | 93725-1295 |  | 2012-08-16 | 2012-08-16 10:37 | 2012-08-16 11:06 | CARRIER - 48SS-024040321 | 38 | 15.6 | Yes | Yes | 17.2 | 19.5 | -2.3 | A05647967B4E46C5BC5B536DC3991AD6 |  | R22 | Non-TXV |  | 41.05% | 0.58947 | 78.89% | [5 empty] | Non-TXV | 41.05%
Oroville | CA | 95966-5743 |  | 2012-07-05 | 2012-07-05 12:22 | 2012-07-05 12:55 | NORDYNE - JS3B4030E1000AA | 101 | 10.2 | Yes | Yes | 25.5 | 21 | 4.5 | 619C6DE242F842E08AE15ADFA729E7D4 |  | R22 | Non-TXV |  | 10.1% | 0.89901 | 19.41% | [5 empty] | Non-TXV | 10.1%
Stockton | CA | 95210-1206 |  | 2012-07-02 | 2012-07-02 13:31 | 2012-07-02 13:44 | RHEEM - UNK | 96 | 4.7 | Yes | Yes | 26 | 21.2 | 4.8 | 85EEA903790845109F4088938901FF52 |  | R22 | Non-TXV |  | 4.896% | 0.95104 | 9.409% | [5 empty] | Non-TXV | 4.896%
Clovis | CA | 93612-3005 |  | 2012-07-13 | 2012-07-13 13:53 | 2012-07-13 14:20 | DAY & NIGHT - N/A | 69 | 2.1 | Yes | Yes | 20.5 | 20.4 | 0.1 | CB0A110FE22A4C408B235ED337E3FE49 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Chowchilla | CA | 93610-2118 |  | 2012-07-06 | 2012-07-06 11:44 | 2012-07-06 12:10 | PAYNE - PY1PJB048115ABAA | 81 | 5 | Yes | Yes | 20.2 | 19.3 | 0.9 | A0FD6BC317854B3E885FF087FA71FF7A |  | R22 | Non-TXV |  | 6.173% | 0.93827 | 11.86% | [5 empty] | Non-TXV | 6.173%
Fresno | CA | 93725-1885 |  | 2012-07-05 | 2012-07-05 14:02 | 2012-07-05 14:22 | LENNOX - 12GCS048X | 167 | 5.7 | Yes | Yes | 22.4 | 20.4 | 2 | 5AB8B906849742708B2E8433245DAA6D |  | R22 | Non-TXV |  | 3.413% | 0.96587 | 6.559% | [5 empty] | Non-TXV | 3.413%
Merced | CA | 95340-4604 |  | 2012-07-02 | 2012-07-02 12:28 | 2012-07-02 12:51 | OTHER - CKL301L | 74 | 3.9 | Yes | Yes | 25.2 | 19.3 | 5.9 | 37FAE8430FDC4FB4AE0357DCB24EADF8 |  | R22 | Non-TXV |  | 5.27% | 0.9473 | 10.13% | [5 empty] | Non-TXV | 5.27%
Tracy | CA | 95376-4445 |  | 2012-07-03 | 2012-07-03 14:32 | 2012-07-03 14:52 | CARRIER - 568EBX060000AGAA | 232 | 29.1 | Yes | Yes | 25.6 | 21.3 | 4.3 | 02552C86CC594230841ACCEDE3573BCF |  | R22 | Non-TXV |  | 12.54% | 0.87457 | 24.11% | [5 empty] | Non-TXV | 12.54%
Stockton | CA | 95219-3502 |  | 2012-07-18 | 2012-07-18 12:21 | 2012-07-18 12:42 | GOODMAN - GPG10240651A | 50 | 5.1 | Yes | Yes | 15.5 | 18.5 | -3 | 1C3D7EA78AE94654875DF75D6C7B29B1 |  | R22 | TXV |  | 10.2% | 0.898 | 19.6% | [5 empty] | TXV | 10.2%
Clovis | CA | 93612-5061 |  | 2012-07-09 | 2012-07-09 11:06 | 2012-07-09 11:21 | RHEEM - RRA-A036JK06E | 63 | 2.4 | Yes | Yes | 19.6 | 21 | -1.4 | 97D6601DDDA0461F94D952E2DBE4FF2D |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Merced | CA | 95348-1602 |  | 2012-07-03 | 2012-07-03 10:12 | 2012-07-03 10:12 | YORK - D1NA030N03606C | 74 | 0 | Yes | Yes | 2.9 | 20.4 | -17.5 | F71E532B3BC742EB9283E88AF92302E6 | Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Liquid Temperature cannot be less than outdoor air temperature. Check entries and calibration. Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-9768 |  | 2012-07-03 | 2012-07-03 09:41 | 2012-07-03 10:01 | DAY & NIGHT - 568EJO36 | 138 | 14.8 | Yes | Yes | 23 | 20.4 | 2.6 | 13E8D26080D94A4DB991355B9F4C60BC |  | R22 | Non-TXV |  | 10.72% | 0.89275 | 20.61% | [5 empty] | Non-TXV | 10.72%
Fresno | CA | 93706-5921 |  | 2012-07-05 | 2012-07-05 12:00 | 2012-07-05 12:47 | YORK - D3NZ036N05606NXA | 64 | 1.9 | Yes | Yes | 18.2 | 19.9 | -1.7 | 0CCAF5871B6544A1B108C98A29F0914B |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Oroville | CA | 95966-6622 |  | 2012-07-10 | 2012-07-10 09:41 | 2012-07-10 10:01 | OTHER - 2TTB3030A1000AA | 89 | 7.3 | Yes | Yes | 23 | 21.3 | 1.8 | CD70B7754E0E4419A4BBF9696440D82D |  | R22 | Non-TXV |  | 8.202% | 0.91798 | 15.76% | [5 empty] | Non-TXV | 8.202%
Fresno | CA | 93726-2724 |  | 2012-07-05 | 2012-07-05 10:11 | 2012-07-05 10:11 | DAY & NIGHT - 585CJ036075 | 85 | 0 | Yes | Yes | 23.4 | 21.4 | 2 | 8792CD2BCFF34F4BBF4C680A37EAA7F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-9553 |  | 2012-07-06 | 2012-07-06 09:42 | 2012-07-06 09:42 | LENNOX - UNK FADED | 85 | 0 | Yes | Yes | 19.8 | 19.3 | 0.5 | 7B2F54EDDFD2468DBB66DEA10497F8FF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3651 |  | 2012-07-03 | 2012-07-03 11:13 | 2012-07-03 11:35 | GOODMAN - GSH130181CA | 127 | -12 | Yes | Yes | 17 | 19.4 | -2.4 | 0928CDEEC88148BFA18EAC554B255EE2 |  | R22 | Non-TXV |  | -9.449% | 1.0945 | 2.646% |  |  |  |  | Non-TXV |  |  | -9.449%
Auburn | CA | 95603-9036 |  | 2012-07-03 | 2012-07-03 08:16 | 2012-07-03 08:35 | TRANE - TTR042C100A2 | 110 | 9.8 | Yes | Yes | 25 | 19.7 | 5.3 | 9CE9AA40E9B64296B497B1246D9DE714 |  | R22 | TXV |  | 8.909% | 0.91091 | 17.12% | [5 empty] | TXV | 8.909%
Stockton | CA | 95209-5113 |  | 2012-06-28 | 2012-06-28 12:09 | 2012-06-28 12:34 | DAY & NIGHT - 565BJ036 | 84 | 9.1 | Yes | Yes | 18.8 | 21.2 | -2.4 | 4296FDB0913A4113898E8E853638C2B8 |  | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Fresno | CA | 93726-0718 |  | 2012-07-11 | 2012-07-11 10:33 | 2012-07-11 10:53 | TEMPSTAR - PGAA36D1K4 | 69 | 2 | Yes | Yes | 22.2 | 20.3 | 2 | 605FE92A27EB47EBBCEBD68AC3371053 |  | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
Clovis | CA | 93612-3412 |  | 2012-07-30 | 2012-07-30 10:49 | 2012-07-30 11:17 | DUCANE - SG121B36075 | 97 | 3.3 | Yes | Yes | 19 | 19.3 | -0.3 | CF1F9B250469475791C0D11E0377E73E |  | R22 | Non-TXV |  | 3.402% | 0.96598 | 6.538% | [5 empty] | Non-TXV | 3.402%
Chico | CA | 95926-2751 |  | 2012-07-26 | 2012-07-26 09:51 | 2012-07-26 10:07 | PAYNE - 24RAC-1S8C | 48 | 4.8 | Yes | Yes | 26.8 | 22.2 | 4.6 | 01939ECB265C4F3093EC6EE97E24F9B9 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93722-5298 |  | 2012-07-06 | 2012-07-06 11:57 | 2012-07-06 12:16 | PAYNE - 585HJW03606A | 102 | 3.1 | Yes | Yes | 24.1 | 21 | 3.1 | 2A00C59989A040CCB5961EDC64003D4F |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Tracy | CA | 95376-3502 |  | 2012-07-03 | 2012-07-03 12:50 | 2012-07-03 13:27 | HEIL - PGAD02FB1K1 | 73 | 2.2 | Yes | Yes | 17.3 | 18.1 | -0.8 | 8816A81556574E0E928E0BB35EB6325D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Fresno | CA | 93727-2402 |  | 2012-07-06 | 2012-07-06 09:34 | 2012-07-06 10:31 | GOODMAN - CKJ48-1B | 110 | 5.7 | Yes | Yes | 24.9 | 22 | 2.9 | 984C2EBA4EE14D2D9F1568A4CE5E6BF5 |  | R22 | Non-TXV |  | 5.182% | 0.94818 | 9.958% | [5 empty] | Non-TXV | 5.182%
Magalia | CA | 95954-9012 |  | 2012-07-11 | 2012-07-11 10:47 | 2012-07-11 10:47 | CARRIER - 48GS-042090301 | 100 | 0 | Yes | Yes | 23.2 | 21.5 | 1.7 | 30193ECDC539404A8A0A0F4D6A7FE06F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-4226 |  | 2012-07-02 | 2012-07-02 11:50 | 2012-07-02 12:12 | OTHER - UAKA030JAZ | 66 | 4.7 | Yes | Yes | 23.5 | 19 | 4.5 | 0786F5D308A14594A28A91BDFD3C35B5 |  | R22 | Non-TXV |  | 7.121% | 0.92879 | 13.69% | [5 empty] | Non-TXV | 7.121%
Clovis | CA | 93611-3129 |  | 2012-07-05 | 2012-07-05 14:36 | 2012-07-05 15:33 | BDP - 589ANW048120ACBD | 89 | 4.1 | Yes | Yes | 16.7 | 19.2 | -2.5 | 4367CF23C503492790B9DE06C21E558B |  | R22 | Non-TXV |  | 4.607% | 0.95393 | 8.853% | [5 empty] | Non-TXV | 4.607%
Manteca | CA | 95336-3724 |  | 2012-07-12 | 2012-07-12 09:31 | 2012-07-12 09:53 | GOODMAN - CE25-1EB | 66 | 2.3 | Yes | Yes | 18.4 | 19.9 | -1.5 | A4029768C51E4D20AF7978A828AC5880 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Madera | CA | 93638-1785 |  | 2012-07-02 | 2012-07-02 12:15 | 2012-07-02 12:48 | BRYANT - 574BNW036060NB-- | 148 | 4.6 | Yes | Yes | 26.3 | 21 | 5.3 | 01596ECD7B6F42B6B1E772A14F7D7DFF |  | R410A | Non-TXV |  | 3.108% | 0.96892 | 5.973% | [5 empty] | Non-TXV | 3.108%
Chico | CA | 95973-1227 |  | 2012-07-03 | 2012-07-03 12:11 | 2012-07-03 12:28 | AMERICAN STANDARD - YCY060G1MOAC | 151 | 6.8 | Yes | Yes | 21.1 | 21.4 | -0.3 | 27B2ACB1B3E84765BEFC8AB666028ABD |  | R22 | Non-TXV |  | 4.503% | 0.95497 | 8.654% | [5 empty] | Non-TXV | 4.503%
Clovis | CA | 93612-2439 |  | 2012-07-09 | 2012-07-09 16:04 | 2012-07-09 16:21 | RUUD - 4AK-018JA2 | 60 | 1.8 | Yes | Yes | 18.1 | 20.4 | -2.3 | 8B92E53E688F433C9ACACAB80E354FD6 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95926-5324 |  | 2012-07-06 | 2012-07-06 16:48 | 2012-07-06 16:48 | TRANE - UNK | 80 | 0 | Yes | Yes | 23.1 | 21.2 | 1.9 | 5CAE9AA7C4CB464280EFE17953620A0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2547 |  | 2012-07-02 | 2012-07-02 09:26 | 2012-07-02 09:54 | OTHER - 10AJB36A05 | 80 | 2.6 | Yes | Yes | 19 | 19.7 | -0.6 | 3A9B7B50E89C44A9A09AB5BACEE1635A |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Stockton | CA | 95207-7762 |  | 2012-07-02 | 2012-07-02 10:42 | 2012-07-02 11:03 | AMERICAN STANDARD - CM18-4TT | 50 | 9 | Yes | Yes | 17.7 | 19.6 | -1.9 | B822740E3AF44965BDE2D4604C2F07CE |  | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Mendota | CA | 93640-1906 |  | 2012-08-15 | 2012-08-15 12:01 | 2012-08-15 12:19 | AIRE-FLO - UNK | 88 | 12.2 | Yes | Yes | 15.4 | 16.3 | -0.9 | BFC094334A53437F950182088DD43603 |  | R22 | Non-TXV |  | 13.86% | 0.86136 | 26.64% | [5 empty] | Non-TXV | 13.86%
Clovis | CA | 93612-4233 |  | 2012-07-03 | 2012-07-03 14:30 | 2012-07-03 14:54 | GOODMAN - GPG12240451A | 64 | 4.3 | Yes | Yes | 23.2 | 18.7 | 4.5 | 2A258B7250794BF6906489AB62CD8A28 |  | R22 | Non-TXV |  | 6.719% | 0.93281 | 12.91% | [5 empty] | Non-TXV | 6.719%
Mendota | CA | 93640-1925 |  | 2012-08-15 | 2012-08-15 13:26 | 2012-08-15 13:52 | OTHER - UNK | 88 | 8.4 | Yes | Yes | 17.7 | 16.6 | 1.1 | C66BB69C4C384230A3EC50811E93466E |  | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Fresno | CA | 93710-4215 |  | 2012-07-09 | 2012-07-09 11:20 | 2012-07-09 11:46 | RHEEM - RRNA-B030JK06X | 65 | -3.8 | Yes | Yes | 21.2 | 18.3 | 2.9 | 0DA26B0F2BF84A619D02C9CC38BBE314 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Atwater | CA | 95301-4215 |  | 2012-07-02 | 2012-07-02 10:11 | 2012-07-02 10:29 | RUUD - URKA-A042JK0B | 70 | 2.5 | Yes | Yes | 17 | 19.5 | -2.5 | 4DAEEDAB62344704A89FB6D68AB405E3 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Fresno | CA | 93725-0919 |  | 2012-08-16 | 2012-08-16 16:21 | 2012-08-16 16:49 | BRYANT - 563CN030-B | 98 | 3.2 | Yes | Yes | 18.2 | 20.9 | -2.7 | 8659BC0FC1ED47198D662F7936FDB356 |  | R22 | Non-TXV |  | 3.265% | 0.96735 | 6.275% | [5 empty] | Non-TXV | 3.265%
Merced | CA | 95341-6449 |  | 2012-07-05 | 2012-07-05 12:19 | 2012-07-05 12:49 | GOODMAN - PGB030050-1 | 56 | -3.3 | Yes | Yes | 27.2 | 21.5 | 5.7 | E496445C906B4D27BCA1EC19A5DB209A |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Fresno | CA | 93710-5263 |  | 2012-07-06 | 2012-07-06 11:38 | 2012-07-06 12:29 | BDP - 36 80 YAC 108T | 66 | 2.2 | Yes | Yes | 19.4 | 21 | -1.6 | 4F9C902A1AD94BF59EA579A174F2B676 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Chico | CA | 95926-9618 |  | 2012-07-12 | 2012-07-12 11:06 | 2012-07-12 11:24 | MONTGOMERY WARD - NA | 75 | 2.3 | Yes | Yes | 21.7 | 20.3 | 1.4 | 981C999BD5844C2BB20724A24810A7F3 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Stockton | CA | 95206-5809 |  | 2012-07-10 | 2012-07-10 16:54 | 2012-07-10 17:17 | RUUD - URGG-05E245RR | 66 | 11.5 | Yes | Yes | 18.1 | 21.1 | -3 | 34009D10AB8742D9AC91CF2755D68726 |  | R22 | Non-TXV |  | 17.42% | 0.82576 | 33.49% | [5 empty] | Non-TXV | 17.42%
Mendota | CA | 93640-1935 |  | 2012-08-16 | 2012-08-16 11:55 | 2012-08-16 12:27 | WESTINGHOUSE - R4GD-042K072X | 192 | 5.8 | Yes | Yes | 21.3 | 19 | 2.3 | 15B54AACD25D4693A2C20B52D9BFBAAC |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Atwater | CA | 95301-9543 |  | 2012-07-03 | 2012-07-03 13:25 | 2012-07-03 14:02 | GOODMAN - GPG12300701A | 73 | 2.1 | Yes | Yes | 26.6 | 21.4 | 5.2 | 51455DF6114347BAA769714A0E537B21 |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Merced | CA | 95341-7510 |  | 2012-07-03 | 2012-07-03 15:13 | 2012-07-03 15:47 | TRANE - TTR030C100A2 | 74 | 4.4 | Yes | Yes | 23.5 | 20.6 | 2.9 | BA70E3D781D0461F9E10B006D46623A6 |  | R22 | Non-TXV |  | 5.946% | 0.94054 | 11.43% | [5 empty] | Non-TXV | 5.946%
Los Banos | CA | 93635-4019 |  | 2012-07-06 | 2012-07-06 12:21 | 2012-07-06 12:58 | BRYANT - 561CJ048-A | 102 | -4.8 | Yes | Yes | 26.2 | 21.4 | 4.8 | 8B113B1EEA744C86AF33B5E9852295B7 |  | R22 | TXV |  | -4.706% | 1.0471 | 1.318% |  |  |  |  | TXV |  |  | -4.706%
Madera | CA | 93638-2641 |  | 2012-07-25 | 2012-07-25 15:05 | 2012-07-25 15:31 | GOODMAN - GPG1342070M41AC | 105 | 3.3 | Yes | Yes | 24.3 | 19 | 5.3 | 810124D22D834E6289EEF7E449C65CF3 |  | R410A | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Chico | CA | 95926-4209 |  | 2012-07-17 | 2012-07-17 12:14 | 2012-07-17 12:35 | PAYNE - 3304E33387 | 88 | 4.7 | Yes | Yes | 21 | 20.7 | 0.3 | 44D1BF0E7AD649C1B81D631CFD794675 |  | R22 | Non-TXV |  | 5.341% | 0.94659 | 10.26% | [5 empty] | Non-TXV | 5.341%
Merced | CA | 95340-2367 |  | 2012-07-10 | 2012-07-10 13:44 | 2012-07-10 14:20 | COLEMAN - UNK | 72 | 5.7 | Yes | Yes | 23.4 | 20.8 | 2.6 | 3A2C7091577F43709D04F19E3A7D7F83 |  | R22 | Non-TXV |  | 7.917% | 0.92083 | 15.21% | [5 empty] | Non-TXV | 7.917%
Tracy | CA | 95376-1811 |  | 2012-07-03 | 2012-07-03 15:17 | 2012-07-03 15:39 | GOODMAN - GSC130421BA | 95 | 7.8 | Yes | Yes | 18.1 | 18.6 | -0.5 | 4DC27EA4DD8F4BDC9A6743D0A2F0ACF7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.211% | 0.91789 | 15.78% | [5 empty] | Non-TXV | 8.211%
Madera | CA | 93638-1822 |  | 2012-07-02 | 2012-07-02 10:19 | 2012-07-02 10:19 | OTHER - 80WE36G1 | 125 | 0 | Yes | Yes | 8.9 | 16.6 | -7.7 | EA418F5F21F245D38D702D75B6C5752B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-9473 |  | 2012-07-06 | 2012-07-06 10:56 | 2012-07-06 11:39 | BRYANT - 561CJ048-F | 109 | -25.1 | Yes | Yes | 20.5 | 23.1 | -2.6 | 6EC3DAEB7CF8478CA4F102D57FD57F9A |  | R22 | TXV |  | -23.03% | 1.2303 | 6.449% |  |  |  |  | TXV |  |  | -23.03%
Sanger | CA | 93657-3411 |  | 2012-07-10 | 2012-07-10 12:25 | 2012-07-10 12:43 | ICP - PGF336060K01 | 146 | 4.5 | Yes | Yes | 17.3 | 17.1 | 0.2 | 5BC27DE9A30844E19972C4424B9B876D |  | R22 | Non-TXV |  | 3.082% | 0.96918 | 5.923% | [5 empty] | Non-TXV | 3.082%
Red Bluff | CA | 96080-3944 |  | 2012-07-11 | 2012-07-11 17:57 | 2012-07-11 18:20 | PAYNE - 56C024RC4 | 55 | 1.9 | Yes | Yes | 22.1 | 21.3 | 0.9 | 70B64C0F6E824F5A87DFC5F0C2320333 |  | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Yuba City | CA | 95991-6811 |  | 2012-07-02 | 2012-07-02 12:16 | 2012-07-02 12:36 | OTHER - 113RNA042000BBAA | 120 | 9 | Yes | Yes | 17 | 19.1 | -2.1 | 9B411750C22B45B6B8552567F4E242A7 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Chico | CA | 95928-9190 |  | 2012-07-20 | 2012-07-20 13:25 | 2012-07-22 22:24 | YORK - H2CB024S06B | 65 | 6.1 | Yes | Yes | 26.3 | 22.4 | 3.9 | A6F8F7086F7343D5A7F30F710E69CFCF |  | R22 | Non-TXV |  | 9.385% | 0.90615 | 18.04% | [5 empty] | Non-TXV | 9.385%
Yuba City | CA | 95991-3318 |  | 2012-07-02 | 2012-07-02 11:10 | 2012-07-02 11:27 | HEIL - MPGAA2401KA | 70 | 2.5 | Yes | Yes | 20 | 19.3 | 0.7 | 5511C60F5AEA4C24BC9349F7686025E7 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Marysville | CA | 95901-3605 |  | 2012-07-17 | 2012-07-17 10:47 | 2012-07-17 10:47 | SINGER - ACR50019-2B | 40 | 0 | Yes | Yes | 24.5 | 18.7 | 5.8 | 5DAA58EF0208439192D0D684BF36DC21 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-2639 |  | 2012-07-09 | 2012-07-09 12:33 | 2012-07-09 12:57 | AIRE-FLO - CK301B | 76 | 12.8 | Yes | Yes | 25.9 | 28.3 | -2.4 | 5341867301D14186BA1C94D6A94BD210 |  | R22 | Non-TXV |  | 16.84% | 0.83158 | 32.37% | [5 empty] | Non-TXV | 16.84%
Stockton | CA | 95210-3400 |  | 2012-07-02 | 2012-07-02 09:55 | 2012-07-02 10:12 | PAYNE - 585HJ024040 | 68 | 2.2 | Yes | Yes | 19.7 | 17.9 | 1.8 | 5F14AB4E490749108FAFA4B84F23D782 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Chico | CA | 95926-4260 |  | 2012-07-16 | 2012-07-16 12:01 | 2012-07-16 12:26 | PAYNE - PH10JA030-A | 85 | 8.9 | Yes | Yes | 15.7 | 18.2 | -2.5 | E8B7EF50684440B696BCBE14AF7094DD |  | R22 | Non-TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | Non-TXV | 10.47%
Yuba City | CA | 95991-1225 |  | 2012-07-13 | 2012-07-13 14:18 | 2012-07-13 14:34 | RHEEM - UNK | 90 | 13.6 | Yes | Yes | 21 | 20.9 | 0.1 | 4D7F622425A54282B77078E4CAB5F968 |  | R22 | Non-TXV |  | 15.11% | 0.84889 | 29.04% | [5 empty] | Non-TXV | 15.11%
Los Banos | CA | 93635-3302 |  | 2012-07-03 | 2012-07-03 12:05 | 2012-07-03 12:33 | YORK - D1NP036N05606A | 108 | 3.6 | Yes | Yes | 20.5 | 20.4 | 0.1 | 7ACFBBA0311345189E84EDDE9A47E6E3 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Clovis | CA | 93612-2444 |  | 2012-07-09 | 2012-07-09 16:28 | 2012-07-09 16:28 | OTHER - NAC036AKA4 | 69 | 0 | Yes | Yes | 18.9 | 19.9 | -1 | 8BB75AE158334EFF8E4BC2F4B7610446 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-6209 |  | 2012-07-23 | 2012-07-23 11:01 | 2012-07-23 11:25 | LENNOX - 10ACC-230-02 | 77 | -8 | Yes | Yes | 22 | 20.3 | 1.7 | FE8CEA6065CD42FA938C19C54F832CCF |  | R22 | TXV |  | -10.39% | 1.1039 | 2.91% |  |  |  |  | TXV |  |  | -10.39%
Angels Camp | CA | 95222-9368 |  | 2012-07-17 | 2012-07-17 12:12 | 2012-07-17 12:29 | BRYANT - 582ANW036060AAAF | 61 | 1.9 | Yes | Yes | 22.5 | 20.4 | 2.1 | 28D5D19EB57B4BD48297652CAB917DBD |  | R22 | Non-TXV |  | 3.115% | 0.96885 | 5.986% | [5 empty] | Non-TXV | 3.115%
Stockton | CA | 95206-5645 |  | 2012-07-06 | 2012-07-06 13:59 | 2012-07-06 14:16 | CARRIER - 38TD036300 | 183 | 9.3 | Yes | Yes | 15 | 17.2 | -2.2 | E684061E501D4823B34ACC6A536CDEB1 |  | R22 | Non-TXV |  | 5.082% | 0.94918 | 9.766% | [5 empty] | Non-TXV | 5.082%
Marysville | CA | 95901-3529 |  | 2012-07-02 | 2012-07-02 09:27 | 2012-07-02 09:51 | BRYANT - 550AN048-E | 162 | 11.1 | Yes | Yes | 24.2 | 19.1 | 5.1 | BFE2C27F411F451CAF1F59543F5CB64F |  | R410A | TXV |  | 6.852% | 0.93148 | 13.17% | [5 empty] | TXV | 6.852%
Merced | CA | 95340-3544 |  | 2012-07-10 | 2012-07-10 14:40 | 2012-07-10 15:29 | OTHER - 100AW36-106 | 72 | 5 | Yes | Yes | 22.9 | 20.7 | 2.2 | 7D373B5DCFB94FCCBF9FA0D24BD860DC |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Marysville | CA | 95901-3610 |  | 2012-07-23 | 2012-07-23 12:14 | 2012-07-23 12:41 | OTHER - DAGA-018JA | 67 | 4.2 | Yes | Yes | 17 | 19.9 | -2.9 | D913C1F16E8F43C69827BCB975A97556 |  | R22 | Non-TXV |  | 6.269% | 0.93731 | 12.05% | [5 empty] | Non-TXV | 6.269%
Chico | CA | 95926-4206 |  | 2012-07-13 | 2012-07-13 09:15 | 2012-07-13 09:31 | HEIL - N2H324AKA200 | 96 | 4.4 | Yes | Yes | 21 | 20.7 | 0.3 | EEB6C79274C84725982B9FEED53555FE |  | R22 | TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | TXV | 4.583%
Yuba City | CA | 95991-4327 |  | 2012-07-18 | 2012-07-18 12:58 | 2012-07-18 13:18 | LENNOX - GCS20R-461-125-2P | 83 | 7.2 | Yes | Yes | 17 | 19.4 | -2.4 | E6C94DCB902A41FFBF4CC8DF97CA0130 |  | R22 | Non-TXV |  | 8.675% | 0.91325 | 16.67% | [5 empty] | Non-TXV | 8.675%
Marysville | CA | 95901-5440 |  | 2012-07-03 | 2012-07-03 09:25 | 2012-07-03 09:46 | NORDYNE - FS3BA-042KA | 87 | 5 | Yes | Yes | 24.6 | 19.1 | 5.5 | 12AC2EEB6A754522BC54269CA76BC7D9 |  | R22 | Non-TXV |  | 5.747% | 0.94253 | 11.04% | [5 empty] | Non-TXV | 5.747%
Clovis | CA | 93612-2446 |  | 2012-07-05 | 2012-07-05 10:05 | 2012-07-05 10:25 | CARRIER - 563CNX036000AAAA | 115 | 3.9 | Yes | Yes | 17.9 | 20.7 | -2.8 | 223FF146F2934D079E8DFCF6FF392B93 |  | R22 | Non-TXV |  | 3.391% | 0.96609 | 6.517% | [5 empty] | Non-TXV | 3.391%
Marysville | CA | 95901-4417 |  | 2012-07-02 | 2012-07-02 14:44 | 2012-07-02 15:04 | DAY & NIGHT - N2A330AKC200 | 68 | -5.6 | Yes | Yes | 20.6 | 19.4 | 1.3 | 2FEFD9CCB3A04FFF888F22FFFEE1C4EC |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Yuba City | CA | 95991-4727 |  | 2012-07-10 | 2012-07-10 10:54 | 2012-07-10 10:54 | HEIL - HAC030AKA1 | 74 | 0 | Yes | Yes | 19.7 | 19.5 | 0.2 | 9DABB50066414A9D99CBD36947304DE5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-3983 |  | 2012-07-23 | 2012-07-23 17:12 | 2012-07-23 17:30 | TRANE - 2TTB2048A1000AA | 120 | 3.6 | Yes | Yes | 21.8 | 21.8 | 0 | 7055E650C31447E59CC43791B6B88A6E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Mendota | CA | 93640-1909 |  | 2012-08-15 | 2012-08-15 12:29 | 2012-08-15 12:47 | AIRE-FLO - UNK | 88 | 7.5 | Yes | Yes | 15.2 | 15.3 | -0.1 | 10EF50DAEA874AEF8F79A86BE0AF0766 |  | R22 | Non-TXV |  | 8.523% | 0.91477 | 16.38% | [5 empty] | Non-TXV | 8.523%
Fresno | CA | 93725-1635 |  | 2012-07-10 | 2012-07-10 10:28 | 2012-07-10 10:53 | CARRIER - 48SS-042080321 | 82 | 2.7 | Yes | Yes | 16.6 | 18.3 | -1.7 | 36C138C2AE124CED9A4A59A33C158CEB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Chico | CA | 95926-1034 |  | 2012-07-16 | 2012-07-16 09:27 | 2012-07-16 10:13 | RHEEM - RAFD-024JAS | 67 | 3.1 | Yes | Yes | 22.4 | 21.9 | 0.5 | 04C2A1E9B2124C14BEFDE3C008431328 |  | R22 | Non-TXV |  | 4.627% | 0.95373 | 8.892% | [5 empty] | Non-TXV | 4.627%
Angels Camp | CA | 95222-9368 |  | 2012-07-17 | 2012-07-17 11:45 | 2012-07-17 12:02 | CARRIER - 48GS-042090301 | 102 | 3.1 | Yes | Yes | 24.5 | 19.1 | 5.4 | EAE723DC78F34B60985F7A035D1FF355 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Chico | CA | 95926-1909 |  | 2012-07-06 | 2012-07-06 16:51 | 2012-07-06 17:12 | RHEEM - RRMA-A042JK08E | 115 | 3.4 | Yes | Yes | 25.5 | 22.4 | 3.2 | F3482D19172F435A9EB0BB6ADCB5C7A4 |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Clovis | CA | 93611-6047 |  | 2012-07-09 | 2012-07-09 14:40 | 2012-07-09 14:58 | LENNOX - HS22-41V-2P | 136 | 4.1 | Yes | Yes | 17.7 | 20.4 | -2.7 | D26A69100D9540FAA386C00D1B9B5CD6 |  | R22 | Non-TXV |  | 3.015% | 0.96985 | 5.794% | [5 empty] | Non-TXV | 3.015%
Merced | CA | 95340-3919 |  | 2012-07-02 | 2012-07-02 10:16 | 2012-07-02 10:46 | TRANE - TTD76OB100A1 | 129 | 10.8 | Yes | Yes | 15.6 | 13 | 2.6 | 2E9B5620191547959743FF4B7010DF30 |  | R22 | Non-TXV |  | 8.372% | 0.91628 | 16.09% | [5 empty] | Non-TXV | 8.372%
Merced | CA | 95340-3919 |  | 2012-07-02 | 2012-07-02 10:48 | 2012-07-02 11:05 | TRANE - TTD76OB100A1 | 129 | 8.8 | Yes | Yes | 17.6 | 17 | 0.6 | CD1AE00A614B40F2981FD064D4DD8365 |  | R22 | Non-TXV |  | 6.822% | 0.93178 | 13.11% | [5 empty] | Non-TXV | 6.822%
Chico | CA | 95928-6437 |  | 2013-11-20 | 2013-11-20 10:22 | 2013-11-20 10:22 | AMERICAN STANDARD - UNK | 115 | 0 | Yes | Yes | 24 | 20.4 | 3.6 | FA7A31DBFA564CDDBE56B35621D63811 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Firebaugh | CA | 93622-9601 |  | 2012-07-09 | 2012-07-09 09:50 | 2012-07-09 10:07 | OTHER - N/A | 64 | 4.6 | Yes | Yes | 23.2 | 20.2 | 3 | 74A64B27252E48F8A178342C32D7821B |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Chico | CA | 95926-3348 |  | 2012-07-10 | 2012-07-10 11:39 | 2012-07-10 12:07 | PAYNE - 565RJ024 | 75 | 5.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | 8AF4E04BBD9D49FFB314EBAED71A8DE9 |  | R22 | Non-TXV |  | 7.2% | 0.928 | 13.84% | [5 empty] | Non-TXV | 7.2%
Madera | CA | 93636-8224 |  | 2012-07-13 | 2012-07-13 10:33 | 2012-07-13 10:57 | LENNOX - 12ACB60-3P | 176 | -6.4 | Yes | Yes | 23.4 | 21 | 2.4 | 1F50434022514C8290713BADC8425D82 |  | R22 | TXV |  | -3.636% | 1.0364 | 1.018% |  |  |  |  | TXV |  |  | -3.636%
Tracy | CA | 95304-8009 |  | 2012-07-03 | 2012-07-03 09:18 | 2012-07-03 09:41 | UNITARY PRODUCTS GROUP - BRC0361BD | 63 | 8.9 | Yes | Yes | 18.8 | 19.7 | -0.9 | 5C772F50184D47D3B2D7CE36C50E7DC2 |  | R22 | Non-TXV |  | 14.13% | 0.85873 | 27.15% | [5 empty] | Non-TXV | 14.13%
Chico | CA | 95926-4262 |  | 2012-07-16 | 2012-07-16 11:06 | 2012-07-16 11:21 | PAYNE - PH10JA030-A | 88 | 4.1 | Yes | Yes | 24.8 | 22.5 | 2.3 | 2268D79FB9924443AF9D63AEC3008394 |  | R22 | TXV |  | 4.659% | 0.95341 | 8.954% | [5 empty] | TXV | 4.659%
Clovis | CA | 93612-5036 |  | 2012-07-03 | 2012-07-03 10:43 | 2012-07-03 11:01 | CARRIER - 48SS-030040321 | 53 | 1.6 | Yes | Yes | 22.3 | 21 | 1.3 | 39A2FE3B06BE4CE7ADB3EDDA9DD7EE3F |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Sanger | CA | 93657-2124 |  | 2012-07-10 | 2012-07-10 11:55 | 2012-07-10 12:19 | BRYANT - 582ANW030060NAAD | 55 | 3 | Yes | Yes | 17.2 | 20.2 | -3 | 5A4E367E13384D838807B3A92C63A5CF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Clovis | CA | 93611-3050 |  | 2012-07-18 | 2012-07-18 18:10 | 2012-07-18 19:05 | AMERICAN STANDARD - YCC036F1MOBH | 83 | 2.8 | Yes | Yes | 18.2 | 20.7 | -2.5 | 4FED0B818BBD4B6D8F6FBA6C4C09A92E |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Chico | CA | 95926-1211 |  | 2012-07-02 | 2012-07-02 09:43 | 2012-07-02 10:01 | LENNOX - HS23-261-1P | 85 | 6.5 | Yes | Yes | 22.9 | 20.9 | 2 | EC7FB4C81F55421580501E49F8407D93 |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Auburn | CA | 95603-3680 |  | 2012-07-18 | 2012-07-18 12:08 | 2012-07-18 12:08 | OTHER - 561AJ048-B | 106 | 0 | Yes | Yes | 25.1 | 19.1 | 6 | 9B8E877DCC7A4F1884AA64F7CF0389EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-3954 |  | 2012-08-16 | 2012-08-16 11:19 | 2012-08-16 11:41 | PAYNE - UNK | 82 | 5.5 | Yes | Yes | 18.8 | 19 | -0.2 | 460A74C0825C4E63993D108AB15D4C95 |  | R22 | Non-TXV |  | 6.707% | 0.93293 | 12.89% | [5 empty] | Non-TXV | 6.707%
Merced | CA | 95341-9065 |  | 2012-07-03 | 2012-07-03 14:12 | 2012-07-03 14:36 | AMANA - PGD36C0702E | 110 | -6.5 | Yes | Yes | 25.1 | 21.6 | 3.6 | E2F0E8041BDF42C5829B296E9D071ADA |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Fresno | CA | 93710-3953 |  | 2012-08-16 | 2012-08-16 10:49 | 2012-08-16 11:18 | LENNOX - 13ACC-036-230-01 | 117 | 3.7 | Yes | Yes | 19.1 | 20.4 | -1.3 | B7A77B8E5F6A48B2B824474CF6A1C39B |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Livingston | CA | 95334-1524 |  | 2012-07-09 | 2012-07-09 09:25 | 2012-07-09 09:52 | ARCOAIRE - GPFM30K060E | 54 | 2.2 | Yes | Yes | 19.6 | 20.2 | -0.6 | B6FF883BA8BB4F82AAF96D55F5DCD21D |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Fresno | CA | 93710-4546 |  | 2012-08-16 | 2012-08-16 09:30 | 2012-08-16 09:49 | CARRIER - 38CKB042300 | 89 | 4.3 | Yes | Yes | 18.2 | 20.7 | -2.5 | 1F8976A35EE54EA494BF5C331C8471E1 |  | R22 | Non-TXV |  | 4.831% | 0.95169 | 9.285% | [5 empty] | Non-TXV | 4.831%
Rocklin | CA | 95677-3439 |  | 2012-07-06 | 2012-07-06 10:44 | 2012-07-06 11:00 | - RPCA-030JBS | 93 | -5.5 | Yes | Yes | 20 | 21.4 | -1.4 | BF0037C41D7B4B1DA4E50C67B07D2CCA |  | R22 | Non-TXV |  | -5.914% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.914%
Fresno | CA | 93726-2222 |  | 2012-07-06 | 2012-07-06 10:07 | 2012-07-06 10:36 | YORK - DAYP-F036N070A | 108 | 3.2 | Yes | Yes | 21.2 | 19.3 | 1.9 | B060906331B041168C3A6498562CF715 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93710-3834 |  | 2012-08-16 | 2012-08-16 11:42 | 2012-08-16 12:14 | PAYNE - UNK | 55 | 4.1 | Yes | Yes | 20.2 | 18.3 | 1.9 | C310FDFC46C14AC19FE0359173565DE9 |  | R22 | Non-TXV |  | 7.455% | 0.92545 | 14.33% | [5 empty] | Non-TXV | 7.455%
Sanger | CA | 93657-2957 |  | 2012-07-03 | 2012-07-03 11:00 | 2012-07-03 11:43 | BDP - 585HJ036060ABAF | 102 | 12.2 | Yes | Yes | 16.2 | 16.3 | -0.1 | 67C77DA5E5BA49C08DEBA360CB408F88 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.96% | 0.88039 | 22.99% | [5 empty] | Non-TXV | 11.96%
Fresno | CA | 93710-4620 |  | 2012-08-16 | 2012-08-16 09:54 | 2012-08-16 10:21 | RHEEM - RLPL-B042JK08 | 114 | 5.1 | Yes | Yes | 18.6 | 19.8 | -1.2 | 9B665D92D065480D9259BCC7CF9C6054 |  | R410A | Non-TXV |  | 4.474% | 0.95526 | 8.597% | [5 empty] | Non-TXV | 4.474%
Clovis | CA | 93612-2628 |  | 2012-07-05 | 2012-07-05 12:02 | 2012-07-05 21:01 | RUUD - UNK | 70 | 2.8 | Yes | Yes | 19.4 | 19.9 | -0.5 | DAAF915BD9D2497DA6F8F9E12175BD55 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Chico | CA | 95926-3204 |  | 2012-07-03 | 2012-07-03 08:54 | 2012-07-03 09:11 | COLEMAN - NA | 80 | 5 | Yes | Yes | 23.5 | 20.4 | 3.1 | 2F846DE6A50249749509CB41C4F79DC1 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Mendota | CA | 93640-1925 |  | 2012-08-15 | 2012-08-15 12:50 | 2012-08-15 13:19 | AIRE-FLO - UNK | 88 | 14.8 | Yes | Yes | 14.6 | 15.5 | -0.9 | BD58EEB51CF24838A42296185CE0529F |  | R22 | Non-TXV |  | 16.82% | 0.83182 | 32.32% | [5 empty] | Non-TXV | 16.82%
Livingston | CA | 95334-1044 |  | 2012-07-03 | 2012-07-03 09:44 | 2012-07-03 10:05 | YORK - D3NZ030N05606NXA | 64 | 1.9 | Yes | Yes | 24.3 | 19.7 | 4.7 | 830340839BE448F097C2C757A9ADBB45 |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Dos Palos | CA | 93620-2220 |  | 2012-07-06 | 2012-07-06 13:56 | 2012-07-06 14:21 | ARCOAIRE - PHF324000K00A1 | 128 | 3.9 | Yes | Yes | 19.3 | 18.1 | 1.2 | 39C3D54251704A1CA3C56633D2BD38BD |  | R22 | Non-TXV |  | 3.047% | 0.96953 | 5.855% | [5 empty] | Non-TXV | 3.047%
Fresno | CA | 93725-1631 |  | 2012-08-16 | 2012-08-16 09:23 | 2012-08-16 09:46 | YORK - D2NP042N06506A | 150 | 4.6 | Yes | Yes | 22.6 | 19.7 | 2.9 | 161091BDD60942E594BA27E52C4AD174 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Merced | CA | 95341-5660 |  | 2012-07-03 | 2012-07-03 09:13 | 2012-07-03 09:50 | GOODMAN - CPLE24-1A | 106 | 3.6 | Yes | Yes | 22.3 | 19.3 | 3 | EE6F466D796F4C4EB885C45110941E27 |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Fresno | CA | 93722-4688 |  | 2012-07-02 | 2012-07-02 09:49 | 2012-07-02 09:49 | YORK - H2RC036S06HA | 85 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 8EA953186A4B4E3A9FE3860F71015901 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4688 |  | 2012-07-02 | 2012-07-02 09:57 | 2012-07-02 10:14 | YORK - H2RC030S06HA | 88 | 2.6 | Yes | Yes | 20.9 | 20.4 | 0.5 | 87D5C7A2125242E9AFE4D9AD09C24438 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Mendota | CA | 93640-1925 |  | 2012-08-16 | 2012-08-16 10:47 | 2012-08-16 11:11 | WESTINGHOUSE - UNK | 100 | 3.7 | Yes | Yes | 19.1 | 18.8 | 0.3 | 417EBBF94DC445D19A109EB4C12BFE23 |  | R22 | Non-TXV |  | 3.7% | 0.963 | 7.111% | [5 empty] | Non-TXV | 3.7%
Lincoln | CA | 95648-1981 |  | 2012-07-06 | 2012-07-06 12:11 | 2012-07-06 12:11 | GOODMAN - GPG1330070M41AC | 80 | 0 | Yes | Yes | 19.7 | 18.1 | 1.6 | F99B4F660C744723A014E023989234AC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6102 |  | 2012-07-02 | 2012-07-02 14:22 | 2012-07-02 14:40 | ICP - GPCM36K080F | 86 | 2.5 | Yes | Yes | 18.5 | 18.5 | 0 | D38869B47F6A466899F9F37CAB1E3B02 |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Oroville | CA | 95966-5429 |  | 2012-07-18 | 2012-07-18 09:56 | 2012-07-18 10:12 | ALLEGIANCE - 7A0036A10A1 | 88 | 4.7 | Yes | Yes | 23.9 | 22.6 | 1.3 | 9FA7DF0023E24858B05E3B275DB5D47E |  | R22 | Non-TXV |  | 5.341% | 0.94659 | 10.26% | [5 empty] | Non-TXV | 5.341%
Stockton | CA | 95207-2317 |  | 2012-06-28 | 2012-06-28 11:22 | 2012-06-28 11:42 | HEIL - PGC024KO40E | 54 | 6.4 | Yes | Yes | 16.8 | 19.6 | -2.8 | 25BBB6AFBEBD4670990AD56B47FB5516 |  | R22 | Non-TXV |  | 11.85% | 0.88148 | 22.78% | [5 empty] | Non-TXV | 11.85%
Fresno | CA | 93725-1278 |  | 2012-08-16 | 2012-08-16 17:15 | 2012-08-16 17:33 | GOODMAN - GPG153709041AA | 112 | 3.4 | Yes | Yes | 19.6 | 19.1 | 0.5 | AE72DEA816A74765B4AE266459C59E72 |  | R410A | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Clovis | CA | 93612-2460 |  | 2012-07-10 | 2012-07-10 12:45 | 2012-07-10 13:54 | OTHER - N/A | 80 | 2.4 | Yes | Yes | 21.7 | 20.4 | 1.3 | 4B9C4BCCB41543B5AE5412AA44F322A4 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93723-9408 |  | 2012-07-10 | 2012-07-10 10:14 | 2012-07-10 11:02 | BDP - 588ANW048100AFAG | 100 | 3.5 | Yes | Yes | 18.3 | 20.2 | -1.9 | 5C1EFD4F5C714EE3834A399B7A19A19F |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Marysville | CA | 95901-3605 |  | 2012-07-20 | 2012-07-20 12:54 | 2012-07-20 13:15 | GOODMAN - GSC130241AE | 73 | 2.9 | Yes | Yes | 18 | 20.4 | -2.4 | 9CF9D3EBE7574C52AE72E1425A79C2AB |  | R22 | Non-TXV |  | 3.973% | 0.96027 | 7.634% | [5 empty] | Non-TXV | 3.973%
Magalia | CA | 95954-9611 |  | 2012-07-11 | 2012-07-11 09:02 | 2012-07-11 09:53 | YORK - EZCP048A06A | 128 | 4.7 | Yes | Yes | 24.4 | 21.2 | 3.2 | B946787A3E8348A682DBDA2704AFA26D |  | R22 | Non-TXV |  | 3.672% | 0.96328 | 7.057% | [5 empty] | Non-TXV | 3.672%
Marysville | CA | 95901-9575 |  | 2012-07-02 | 2012-07-02 13:46 | 2012-07-02 13:46 | TRANE - TTB036C100A2 | 90 | 0 | Yes | Yes | 18 | 18.1 | -0.1 | 0F25FB515D5043B085DFEE41C916FF65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2374 |  | 2012-08-16 | 2012-08-16 18:39 | 2012-08-16 18:57 | DAY & NIGHT - 36/80 VAC 108C G | 90 | 8.4 | Yes | Yes | 20.4 | 20.6 | -0.1 | E01AB73C9D364DA9B7E4475C581C896D |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Magalia | CA | 95954-9702 |  | 2012-07-11 | 2012-07-11 16:31 | 2012-07-11 16:39 | CARRIER - 38EH042320 | 60 | 2.6 | Yes | Yes | 21 | 20.4 | 0.6 | 32926B0FDFE94B8F9378CF1DDD214920 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Stockton | CA | 95210-1734 |  | 2012-07-02 | 2012-07-02 13:07 | 2012-07-02 13:26 | YORK - BRCS0241BD | 59 | -3.5 | Yes | Yes | 15.5 | 18.1 | -2.6 | 6FE3DD60C5FB4C0F9B5B9FBE861094B5 |  | R22 | Non-TXV |  | -5.932% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.932%
Atwater | CA | 95301-4552 |  | 2012-07-02 | 2012-07-02 10:44 | 2012-07-02 11:01 | CARRIER - 48XPN036060311 | 148 | 5.4 | Yes | Yes | 19.6 | 20.9 | -1.3 | 7A070C3B7A814F6A8E886719F6D08C9A |  | R410A | Non-TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | Non-TXV | 3.649%
Newman | CA | 95360-1223 |  | 2012-07-12 | 2012-07-12 09:01 | 2012-07-12 09:20 | BRYANT - 583ANW030060AAHD | 68 | 2 | Yes | Yes | 19.9 | 19.2 | 0.7 | 2573EA4041D74D45AF5B696529114647 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Cutler | CA | 93615-2009 |  | 2012-07-02 | 2012-07-02 13:40 | 2012-07-02 14:01 | GOODMAN - GPG13420701AA | 128 | 3.8 | Yes | Yes | 20.8 | 20.7 | 0.1 | 4C541F0CD7E443078B09445D8FA610E9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Marysville | CA | 95901-4287 |  | 2012-07-17 | 2012-07-17 12:32 | 2012-07-17 12:49 | BDP - 540JJ018 | 83 | 4.9 | Yes | Yes | 20.9 | 19.7 | 1.2 | E25C922731B1494BAC686C186E760B9B |  | R22 | Non-TXV |  | 5.904% | 0.94096 | 11.35% | [5 empty] | Non-TXV | 5.904%
Livingston | CA | 95334-1524 |  | 2012-07-10 | 2012-07-10 09:13 | 2012-07-10 09:37 | RUUD - URMAA030JK | 80 | 2.4 | Yes | Yes | 17.5 | 18.8 | -1.3 | 21956C625A5F47579D27E28B1A14FE14 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Marysville | CA | 95901-4288 |  | 2012-07-13 | 2012-07-13 12:30 | 2012-07-13 12:54 | GOODMAN - 540JJ018 | 88 | -8.3 | Yes | Yes | 19 | 19.9 | -0.9 | 39FDACA8219242A891889B5C2658754B |  | R22 | Non-TXV |  | -9.432% | 1.0943 | 2.641% |  |  |  |  | Non-TXV |  |  | -9.432%
Marysville | CA | 95901-3137 |  | 2012-07-25 | 2012-07-25 14:11 | 2012-07-25 14:29 | DAY & NIGHT - 584AN060100 | 112 | 3.4 | Yes | Yes | 21.5 | 19.6 | 1.9 | 2477886FCED2451DA45AAB687B236CDA |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Sanger | CA | 93657-2738 |  | 2012-07-10 | 2012-07-10 13:52 | 2012-07-10 14:13 | LENNOX - GCS29X-042-100-1PA | 75 | 2.6 | Yes | Yes | 21.6 | 19.9 | 1.8 | 98F376CFD1704D1CAB87CCB4E540333A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.467% | 0.96533 | 6.662% | [5 empty] | Non-TXV | 3.467%
Stockton | CA | 95210-1249 |  | 2012-07-02 | 2012-07-02 12:33 | 2012-07-02 12:49 | YORK - D3NP024N05606NXB | 100 | 3.1 | Yes | Yes | 18.4 | 18.7 | -0.3 | 0B7E8486EEDF429D9969DB09C0AAF8F0 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Marysville | CA | 95901-4277 |  | 2012-07-03 | 2012-07-03 10:18 | 2012-07-03 10:40 | BDP - 540JJ018 | 83 | 6.8 | Yes | Yes | 21.7 | 19.5 | 2.2 | 6C4E9703F19E4003A71305D6CD69D539 |  | R22 | Non-TXV |  | 8.193% | 0.91807 | 15.74% | [5 empty] | Non-TXV | 8.193%
Escalon | CA | 95320-0000 |  | 2012-07-12 | 2012-07-12 12:20 | 2012-07-12 12:39 | UNK - UNK | 85 | 13.1 | Yes | Yes | 18.4 | 19.3 | -0.9 | F6049D0469224C69901252761211C6C9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. |  |  |  | 15.41% | 0.84588 | 29.62% | [5 empty] | 0 | 15.41%
Chowchilla | CA | 93610-8606 |  | 2012-07-11 | 2012-07-11 11:31 | 2012-07-11 11:59 | TRANE - 2TTB0036A1000AA | 76 | 2.5 | Yes | Yes | 19.5 | 15.8 | 3.7 | 1D41B4ADF0D744C088D4C195BFE1711F |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Olivehurst | CA | 95961-9393 |  | 2012-07-03 | 2012-07-03 15:28 | 2012-07-03 15:28 | OTHER - UNK PAINTED | 94 | 0 | Yes | Yes | 22.7 | 19.6 | 3.1 | 6DC18E7527BB44FB89907C7640893C56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-6036 |  | 2012-07-05 | 2012-07-05 12:46 | 2012-07-05 13:12 | OTHER - HARB-F024SA | 118 | -6.9 | Yes | Yes | 20 | 20.9 | -0.9 | C8D3C70A4C274D5EB69A4E94A3400C84 |  | R22 | Non-TXV |  | -5.847% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.847%
Yuba City | CA | 95991-6539 |  | 2012-07-24 | 2012-07-24 10:02 | 2012-07-24 10:34 | BDP - 567C030RCU | 63 | 4.2 | Yes | Yes | 20.4 | 18.2 | 2.2 | 53B2C6EE731C40CAB914C3885943A677 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Dos Palos | CA | 93620-2532 |  | 2012-07-09 | 2012-07-09 14:26 | 2012-07-09 14:46 | ICP - PGC018K040D | 62 | 10.3 | Yes | Yes | 22.8 | 23.7 | -0.9 | 4C999DC81CD34490B5D14F63C1CC459A |  | R22 | Non-TXV |  | 16.61% | 0.83387 | 31.93% | [5 empty] | Non-TXV | 16.61%
Clovis | CA | 93612-4917 |  | 2012-07-10 | 2012-07-10 09:26 | 2012-07-10 09:43 | ICP - NAC242AKA1 | 126 | 3.8 | Yes | Yes | 24.6 | 20.4 | 4.2 | 9710E60116DB4903BC7132DD70DB5EB6 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Dos Palos | CA | 93620-9625 |  | 2012-07-12 | 2012-07-12 12:35 | 2012-07-12 12:57 | RUUD - UNK | 78 | 17 | Yes | Yes | 25.5 | 28.3 | -2.8 | 5F6896D00C064B95A64A427FDAEA05CC |  | R22 | Non-TXV |  | 21.79% | 0.78205 | 41.88% | [5 empty] | Non-TXV | 21.79%
Yuba City | CA | 95991-4365 |  | 2012-07-23 | 2012-07-23 10:20 | 2012-07-23 10:20 | OTHER - PH13NR024 | 75 | 0 | Yes | Yes | 13 | 19.3 | -6.3 | 7D8ABF74165C4F1EA64D8FE7C3EF00A0 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-7117 |  | 2012-07-05 | 2012-07-05 14:01 | 2012-07-05 14:23 | LENNOX - 13GCSA-24-068X-230-1A | 104 | 3.2 | Yes | Yes | 17 | 19.8 | -2.8 | 6803E696495C4ABA97C5D13628458276 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Clovis | CA | 93612-4022 |  | 2012-07-25 | 2012-07-25 10:11 | 2012-07-25 10:42 | YORK - D1NH036N05606C | 108 | 3.6 | Yes | Yes | 20.8 | 19.9 | 0.9 | 419E8FCCA0BE4D50B9CF0FB6A0D68E06 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Clovis | CA | 93612-4022 |  | 2012-07-03 | 2012-07-03 10:09 | 2012-07-03 10:09 | BDP - 585A0360B0YACR | 85 | 0 | Yes | Yes | 25.1 | 20.4 | 4.7 | 92EB18A9E16E4A19A0DE9860B691BCE5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95965-9610 |  | 2012-07-05 | 2012-07-05 10:50 | 2012-07-05 11:30 | OTHER - JS3BA036KA | 75 | 2.3 | Yes | Yes | 20 | 21 | -1 | 362BF663647D41DA95591C0C66085A23 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Chico | CA | 95928-6437 |  | 2012-07-06 | 2012-07-06 13:10 | 2012-07-06 16:46 | RUUD - UAFD-024JAS | 69 | 2.4 | Yes | Yes | 22.4 | 20.7 | 1.7 | 6EED1CAD0FE646338FFD715C37A25B84 |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Yuba City | CA | 95991-6536 |  | 2012-07-16 | 2012-07-16 14:29 | 2012-07-16 14:45 | GOODMAN - CK30-1A | 75 | -6.2 | Yes | Yes | 20 | 19.9 | 0.1 | 96AF71B8FD434B0993451A75A57ACA90 |  | R22 | Non-TXV |  | -8.267% | 1.0827 | 2.315% |  |  |  |  | Non-TXV |  |  | -8.267%
Yuba City | CA | 95991-4545 |  | 2012-07-02 | 2012-07-02 09:52 | 2012-07-02 10:18 | OTHER - GS3B-036KA | 69 | 2.1 | Yes | Yes | 20 | 19 | 1 | 72C7E2959A654F85A7FB612776B27A87 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Fresno | CA | 93710-6129 |  | 2012-07-10 | 2012-07-10 16:40 | 2012-07-10 17:01 | BDP - 588ANW048100AEAG | 101 | 4.7 | Yes | Yes | 17.3 | 19.2 | -1.9 | 84BF50C1737D426AA090525D844FF5D1 |  | R22 | Non-TXV |  | 4.653% | 0.95347 | 8.943% | [5 empty] | Non-TXV | 4.653%
Marysville | CA | 95901-6555 |  | 2012-08-03 | 2012-08-03 13:46 | 2012-08-03 14:05 | GOODMAN - CKL36-1L | 84 | 2.8 | Yes | Yes | 17 | 19.9 | -2.9 | 41A840107DCE4BF3BEC1EC1BC5EF59BE |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Riverdale | CA | 93656-9713 |  | 2012-07-19 | 2012-07-19 10:34 | 2012-07-19 10:55 | TEMPSTAR - PGAA29C1K1 | 74 | 2.2 | Yes | Yes | 23.3 | 21 | 2.3 | 19EEF69FDC464BDAB2DF768838B8C418 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Fresno | CA | 93725-1137 |  | 2012-08-16 | 2012-08-16 12:59 | 2012-08-16 13:16 | AMERICAN STANDARD - YCC030F1M0BJ | 72 | 3.6 | Yes | Yes | 17.3 | 19.9 | -2.6 | DBD888F71B964362ABBC1B88D5EB915C |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95209-4155 |  | 2012-07-02 | 2012-07-02 12:34 | 2012-07-02 12:54 | PAYNE - 563ANO60-A | 202 | 8.1 | Yes | Yes | 14.2 | 16.4 | -2.2 | A145E28DEDF141B7A6691E20D0606A44 |  | R22 | Non-TXV |  | 4.01% | 0.9599 | 7.706% | [5 empty] | Non-TXV | 4.01%
Fresno | CA | 93710-4813 |  | 2012-07-10 | 2012-07-10 12:41 | 2012-07-10 12:58 | YORK - AC042X12210 | 109 | 3.5 | Yes | Yes | 18.3 | 19.8 | -1.5 | 8C7607321FBE4FB18456DAD4193A0E49 |  | R22 | Non-TXV |  | 3.211% | 0.96789 | 6.171% | [5 empty] | Non-TXV | 3.211%
Merced | CA | 95340-3811 |  | 2012-07-10 | 2012-07-10 08:36 | 2012-07-10 08:54 | GOODMAN - PGB0300501A | 56 | 8.6 | Yes | Yes | 25.7 | 19.8 | 5.9 | 335F41EE3DB1433A90A102E07DD1C466 |  | R22 | Non-TXV |  | 15.36% | 0.84643 | 29.51% | [5 empty] | Non-TXV | 15.36%
Manteca | CA | 95337-5178 |  | 2012-07-10 | 2012-07-10 10:47 | 2012-07-10 11:59 | BDP - 565BJ036 | 84 | 2.5 | Yes | Yes | 18.3 | 19.5 | -1.2 | A56EFB6FAA7A4692B295E799F9569815 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Clovis | CA | 93612-5003 |  | 2012-07-03 | 2012-07-03 09:21 | 2012-07-03 09:47 | YORK - D1NP048N09006A | 132 | 7.4 | Yes | Yes | 19.3 | 20.2 | -0.9 | C3744FA594D745A7A2CFCF5F35E1FD36 |  | R22 | Non-TXV |  | 5.606% | 0.94394 | 10.77% | [5 empty] | Non-TXV | 5.606%
Los Banos | CA | 93635-2640 |  | 2012-07-10 | 2012-07-10 11:29 | 2012-07-10 11:58 | GOODMAN - CK24-1B | 71 | 2.9 | Yes | Yes | 22.7 | 22.5 | 0.2 | DD407995B3614841B6CA7983D457A5E9 |  | R22 | Non-TXV |  | 4.085% | 0.95915 | 7.85% | [5 empty] | Non-TXV | 4.085%
Chico | CA | 95973-5828 |  | 2012-07-24 | 2012-07-24 23:36 | 2012-07-24 23:36 | BRYANT - 563CN036-A | 122 | 0 | Yes | Yes | 22.1 | 22 | 0.1 | E2815CD1B4FA41CD95AB96FC4E54A5C4 |  | R22 | TXV |  | 0% | 1 | 0%
Chico | CA | 95926-3064 |  | 2012-07-16 | 2012-07-16 12:31 | 2012-07-17 18:24 | OTHER - JS3BC-030KA | 68 | 6.3 | Yes | Yes | 24.8 | 20.6 | 4.2 | 699DE41C9DB54D8581ED652D5EB34E54 |  | R22 | Non-TXV |  | 9.265% | 0.90735 | 17.8% | [5 empty] | Non-TXV | 9.265%
Chico | CA | 95926-1959 |  | 2012-07-26 | 2012-07-26 10:38 | 2012-07-26 10:58 | OTHER - NA | 88 | 4.7 | Yes | Yes | 20.9 | 21.7 | -0.8 | 82545AAF5F924BE6A873A7012B083848 |  | R22 | Non-TXV |  | 5.341% | 0.94659 | 10.26% | [5 empty] | Non-TXV | 5.341%
Escalon | CA | 95320-8514 |  | 2012-07-10 | 2012-07-10 13:40 | 2012-07-10 14:00 | BDP - 661BJ030-C | 118 | 9.4 | Yes | Yes | 19.5 | 20.9 | -1.4 | 2004FEDD5D0E4F699F98C9BB25DE4712 |  | R22 | Non-TXV |  | 7.966% | 0.92034 | 15.31% | [5 empty] | Non-TXV | 7.966%
Fresno | CA | 93723-7642 |  | 2012-07-12 | 2012-07-12 10:48 | 2012-07-12 11:26 | LENNOX - 13ACC-048-230-01 | 158 | 4.7 | Yes | Yes | 18.6 | 20.1 | -1.5 | 160A9DA3C9E045DEB7F8012E5E0DE0B3 |  | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.717% | [5 empty] | Non-TXV | 2.975%
Escalon | CA | 95320-9703 |  | 2012-07-10 | 2012-07-10 14:19 | 2012-07-10 14:41 | YORK - D3NZ030N05606NXA | 64 | 1.9 | Yes | Yes | 17.2 | 17.5 | -0.3 | 1E50D04E9F674E78831DF8444FB29BB7 |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Stockton | CA | 95210-1419 |  | 2012-07-13 | 2012-07-13 12:48 | 2012-07-13 13:08 | BRYANT - 582ANW036060NBAF | 68 | 7.3 | Yes | Yes | 17.3 | 19.4 | -2.1 | 98B1ACA0115E40D49A9EBBDA938874DA |  | R22 | Non-TXV |  | 10.74% | 0.89265 | 20.63% | [5 empty] | Non-TXV | 10.74%
Fresno | CA | 93710-4007 |  | 2012-08-16 | 2012-08-16 12:49 | 2012-08-16 13:34 | YORK - D5YS036N0506A | 84 | 5.2 | Yes | Yes | 22.2 | 18 | 4.2 | AF7D8E6618CF4D29AA6B5C150FCAA56D |  | R22 | Non-TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | Non-TXV | 6.19%
Fresno | CA | 93710-4007 |  | 2012-08-16 | 2012-08-16 12:52 | 2012-08-16 13:34 | YORK - D5YS036N0506A | 84 | 6.5 | Yes | Yes | 23.4 | 18.8 | 4.6 | 42A5D1B2A0594A0E9DF84C5EEF874ED1 |  | R22 | Non-TXV |  | 7.738% | 0.92262 | 14.87% | [5 empty] | Non-TXV | 7.738%
Fresno | CA | 93710-4007 |  | 2012-08-16 | 2012-08-16 12:56 | 2012-08-16 13:33 | YORK - D5YS036N0506A | 84 | 7.7 | Yes | Yes | 20.9 | 18.8 | 2.1 | 0E6D90CCD33145AD862622AC33A6BF18 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Chico | CA | 95926-7764 |  | 2012-07-13 | 2012-07-13 10:27 | 2012-07-13 10:27 | WESTINGHOUSE - R4GD-042K072X | 191 | 0 | Yes | Yes | 22.3 | 20.1 | 2.3 | E6399B11F5C6418AAF7D4CF7FE5ABB18 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1734 |  | 2012-07-10 | 2012-07-10 10:43 | 2012-07-10 11:00 | DAY & NIGHT - 584AN024060 | 52 | 2.9 | Yes | Yes | 18.8 | 19 | -0.2 | 57AFA8C17B6F4A5D82784D70F0808CE7 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Lodi | CA | 95242-0000 |  | 2012-07-16 | 2012-07-16 14:03 | 2012-07-16 14:20 | GOODMAN - UNK | 76 | -4.5 | Yes | Yes | 23.5 | 19.2 | 4.4 | C351AD5380D9448FA7A745B5359424F8 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Fresno | CA | 93726-2125 |  | 2012-07-11 | 2012-07-11 09:05 | 2012-07-11 09:24 | HEIL - PGAD42D1K4 | 180 | 5.3 | Yes | Yes | 20 | 19.3 | 0.7 | 0D5E88477FDF4E50936B7D80492F6BA3 |  | R22 | Non-TXV |  | 2.944% | 0.97056 | 5.659% | [5 empty] | Non-TXV | 2.944%
Stockton | CA | 95207-7204 |  | 2012-08-06 | 2012-08-06 15:34 | 2012-08-06 16:00 | PAYNE - 568DJ036 | 154 | 20.1 | Yes | Yes | 20.3 | 21.4 | -1.1 | 6F76F725980D4535A28E4C8CCC222C47 |  | R22 | Non-TXV |  | 13.05% | 0.86948 | 25.08% | [5 empty] | Non-TXV | 13.05%
Stockton | CA | 95204-4505 |  | 2012-07-10 | 2012-07-10 12:19 | 2012-07-10 12:47 | GE - 24B21 | 65 | 10.8 | Yes | Yes | 23.9 | 21.4 | 2.5 | 1A42D29A67304571AA02235A9757D148 |  | R22 | Non-TXV |  | 16.62% | 0.83385 | 31.93% | [5 empty] | Non-TXV | 16.62%
Stockton | CA | 95205-6332 |  | 2012-07-11 | 2012-07-11 16:53 | 2012-07-11 16:53 | GUARDIAN - GCGD36S21S2B | 64 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | AFB9F6B123BA4848A505510396CAFF7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-2343 |  | 2012-07-11 | 2012-07-11 11:22 | 2012-07-11 11:47 | ICP - NAC024AKC3 | 71 | 2.8 | Yes | Yes | 20.6 | 21.3 | -0.7 | A948EC58E0C842F19750C93F47228823 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.944% | 0.96056 | 7.579% | [5 empty] | Non-TXV | 3.944%
Manteca | CA | 95336-2965 |  | 2012-07-10 | 2012-07-10 10:05 | 2012-07-10 10:29 | TRANE - BTD724A100B0 | 85 | 3.2 | Yes | Yes | 20.3 | 19.2 | 1.1 | 743A005FAC0A40BE8D5CF9920A42B414 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Valley Springs | CA | 95252-9501 |  | 2012-07-16 | 2012-07-16 08:17 | 2012-07-16 08:36 | PAYNE - PH13NR030-K | 85 | 10.6 | Yes | Yes | 17.6 | 18.7 | -1.1 | 20A2EC45DC3F43B6AE043A91F1597CA4 |  | R22 | Non-TXV |  | 12.47% | 0.87529 | 23.97% | [5 empty] | Non-TXV | 12.47%
Livingston | CA | 95334-1138 |  | 2012-07-10 | 2012-07-10 09:39 | 2012-07-10 09:55 | GOODMAN - CKL36-1L | 85 | 2.6 | Yes | Yes | 20.7 | 20.4 | 0.3 | 0A875CD416084FC3B48F532F41FBD8DC |  |  |  |  | 3.059% | 0.96941 | 5.878% | [5 empty] | 0 | 3.059%
Stockton | CA | 95210-1630 |  | 2012-07-19 | 2012-07-19 09:54 | 2012-07-19 10:12 | CARRIER - 38GS024300 | 48 | -4.5 | Yes | Yes | 17 | 17.1 | -0.1 | BF92CEEC60CA45659A5F6181A6589B0E |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Clovis | CA | 93612-4801 |  | 2012-07-30 | 2012-07-30 09:18 | 2012-07-30 10:04 | OTHER - UNK | 70 | 2.8 | Yes | Yes | 17.3 | 19.9 | -2.6 | 1EDC5F9E0E0E4E1793C6510DFA73C18C |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Escalon | CA | 95320-9642 |  | 2012-07-10 | 2012-07-10 15:04 | 2012-07-10 15:41 | RHEEM - RANL-037JAZ | 106 | 14.7 | Yes | Yes | 17.4 | 16.7 | 0.7 | 08AA7EC9136B4321938239F1C0EC913E |  | R410A | Non-TXV |  | 13.87% | 0.86132 | 26.65% | [5 empty] | Non-TXV | 13.87%
Merced | CA | 95348-3402 |  | 2012-07-20 | 2012-07-20 15:26 | 2012-07-20 15:51 | OTHER - NA | 49 | 1.5 | Yes | Yes | 15.8 | 17.5 | -1.7 | 4B3DA8F2C09E4032A4092503D51C3152 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Stockton | CA | 95204-1437 |  | 2012-07-10 | 2012-07-10 11:26 | 2012-07-10 11:45 | GE - TA33FK1 | 96 | 20.1 | Yes | Yes | 18.6 | 21.2 | -2.6 | ED6ED778814648EFADE908F6B719D4F0 |  | R22 | Non-TXV |  | 20.94% | 0.79063 | 40.24% | [5 empty] | Non-TXV | 20.94%
Stockton | CA | 95205-2576 |  | 2012-07-11 | 2012-07-11 13:17 | 2012-07-11 13:37 | CARRIER - 38EZG048300 | 125 | 7.6 | Yes | Yes | 20.7 | 19.3 | 1.4 | EB857D66F2434EDA814513958B59F638 |  | R410A | TXV |  | 6.08% | 0.9392 | 11.68% | [5 empty] | TXV | 6.08%
Chico | CA | 95926-3056 |  | 2012-07-10 | 2012-07-10 10:49 | 2012-07-10 11:00 | DAY & NIGHT - 591ANX030000AAAA | 76 | 3 | Yes | Yes | 18.6 | 20.6 | -2 | 93B68FD264A94EF2A3CB056E3D0AD128 |  | R22 | Non-TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | Non-TXV | 3.947%
Lincoln | CA | 95648-1535 |  | 2012-07-11 | 2012-07-11 15:39 | 2012-07-11 15:39 | PAYNE - PA10JA036-C | 85 | 0 | Yes | Yes | 18 | 19.8 | -1.8 | 127E956831594F2A8D08C5B28A5640F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1249 |  | 2012-07-10 | 2012-07-10 09:55 | 2012-07-10 10:25 | BDP - 585B036075YACR | 60 | 2.1 | Yes | Yes | 18.1 | 20.1 | -2 | 2135A4E79EA94773B8249511EFF4864C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Fresno | CA | 93723-7613 |  | 2012-07-12 | 2012-07-12 13:33 | 2012-07-12 14:02 | LENNOX - UNK | 74 | 3.3 | Yes | Yes | 18.6 | 20.4 | -1.8 | 39BB44130A4746A7ADB4315A8DB621D3 |  | R22 | Non-TXV |  | 4.459% | 0.95541 | 8.57% | [5 empty] | Non-TXV | 4.459%
Ripon | CA | 95366-3245 |  | 2012-07-11 | 2012-07-11 14:38 | 2012-07-11 15:06 | DAY & NIGHT - 585HJW030040 | 68 | 16.5 | Yes | Yes | 13.3 | 14.4 | -1.1 | F7033D241C7545DFB5483D384A19BBFF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 24.26% | 0.75735 | 46.63% | [5 empty] | Non-TXV | 24.26%
Red Bluff | CA | 96080-4230 |  | 2012-07-11 | 2012-07-11 16:44 | 2012-07-11 17:55 | BRYANT - 574DNWA24040NA | 71 | 2.5 | Yes | Yes | 23.7 | 22.1 | 1.6 | 602D29C9AE4B4957A73F08A72C5DF02B |  | R410A | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Manteca | CA | 95336-4940 |  | 2012-07-10 | 2012-07-10 09:25 | 2012-07-10 09:46 | BRYANT - 574ANW024040NB-- | 89 | 3.1 | Yes | Yes | 18.4 | 19.5 | -1.1 | D3E9EE5A200E418ABE3601191FF25991 |  | R22 | Non-TXV |  | 3.483% | 0.96517 | 6.694% | [5 empty] | Non-TXV | 3.483%
Stockton | CA | 95207-7441 |  | 2012-07-11 | 2012-07-11 09:08 | 2012-07-11 09:26 | DAY & NIGHT - UNK | 96 | 12.1 | Yes | Yes | 17.1 | 19.9 | -2.8 | 02E5F79C736E4639A9CDA8BBF8054F8E |  | R22 | Non-TXV |  | 12.6% | 0.87396 | 24.22% | [5 empty] | Non-TXV | 12.6%
Chico | CA | 95926-4206 |  | 2012-07-16 | 2012-07-16 10:32 | 2012-07-16 10:50 | HEIL - PH13NR024000CAA | 100 | 3 | Yes | Yes | 22 | 20.9 | 1.1 | 732F42A423FA4F7B8F4BDDD2975B9442 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95973-7691 |  | 2012-07-10 | 2012-07-10 14:19 | 2012-07-10 20:41 | YORK - 563CNX048000AF | 164 | 6.6 | Yes | Yes | 19.4 | 20.4 | -1 | E7FE12F4B6074AA6809282BA0B695554 |  | R22 | TXV |  | 4.024% | 0.95976 | 7.734% | [5 empty] | TXV | 4.024%
Fresno | CA | 93727-8730 |  | 2012-07-25 | 2012-07-25 13:35 | 2012-07-25 14:20 | YORK - D1NA036N03606C | 67 | 2.1 | Yes | Yes | 21.6 | 20.3 | 1.4 | 8DB2F3C50B8A46A4A717BC42F9B585F6 |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Los Banos | CA | 93635-2820 |  | 2012-07-10 | 2012-07-10 12:26 | 2012-07-10 13:32 | GOODMAN - CK24-1B | 71 | 2.2 | Yes | Yes | 18.4 | 20.4 | -2 | FE115038B78F42B2A9228400C14A9F55 |  | R22 | Non-TXV |  | 3.099% | 0.96901 | 5.955% | [5 empty] | Non-TXV | 3.099%
Merced | CA | 95341-7007 |  | 2012-07-10 | 2012-07-10 10:00 | 2012-07-10 10:36 | GOODMAN - CLJ301 | 96 | 14.1 | Yes | Yes | 21.5 | 23.4 | -1.9 | FAB89B345A444C268650DCB9B38E0583 |  | R22 | Non-TXV |  | 14.69% | 0.85313 | 28.23% | [5 empty] | Non-TXV | 14.69%
Stockton | CA | 95210-1249 |  | 2012-07-11 | 2012-07-11 12:26 | 2012-07-11 12:46 | PAYNE - 24-60-YAC108-C | 53 | 3.1 | Yes | Yes | 19.8 | 20.2 | -0.4 | 6A8F0062DC3C42EDBE79C33CC4D2FE27 |  | R22 | Non-TXV |  | 5.849% | 0.94151 | 11.24% | [5 empty] | Non-TXV | 5.849%
Fresno | CA | 93727-8120 |  | 2012-07-10 | 2012-07-10 09:14 | 2012-07-10 09:35 | DAY & NIGHT - N/A | 90 | 5.1 | Yes | Yes | 23.1 | 21.4 | 1.7 | 12CB420C4E724AC9B4A3D6DC244D5724 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Clovis | CA | 93612-5119 |  | 2012-07-10 | 2012-07-10 11:57 | 2012-07-10 12:16 | GOODMAN - PGB024050-1 | 54 | 1.6 | Yes | Yes | 20.3 | 20.4 | -0.1 | 2AC3870EC92049A4881E6046D0A5D370 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Mendota | CA | 93640-1904 |  | 2012-07-11 | 2012-07-11 11:20 | 2012-07-11 11:49 | YORK - D1NA03CN03606A | 72 | 3.1 | Yes | Yes | 17.6 | 20.1 | -2.5 | BF2AC3400EF14963828802E4A243640B |  | R22 | Non-TXV |  | 4.306% | 0.95694 | 8.274% | [5 empty] | Non-TXV | 4.306%
Stockton | CA | 95210-1853 |  | 2012-07-12 | 2012-07-12 14:05 | 2012-07-12 14:25 | OTHER - 24-60YAC108TC | 54 | 2.6 | Yes | Yes | 15.5 | 18.1 | -2.6 | DC7126F02A794C4680BBA081D71964A6 |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Parlier | CA | 93648-2505 |  | 2012-08-15 | 2012-08-15 16:08 | 2012-08-15 16:35 | AMERICAN STANDARD - YCY030G1M0AA | 120 | 4.2 | Yes | Yes | 17.5 | 17.5 | 0.1 | 3E570CDE096E47709B2F02BE270FA747 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Plumas Lake | CA | 95961-9031 |  | 2012-07-30 | 2012-07-30 12:09 | 2012-07-30 12:36 | YORK - H2RA030S060 | 62 | 2.5 | Yes | Yes | 17 | 19.3 | -2.3 | 5BCF4D6418BE4E69B071E43ED1EE7657 |  | R22 | Non-TXV |  | 4.032% | 0.95968 | 7.749% | [5 empty] | Non-TXV | 4.032%
Tracy | CA | 95376-2324 |  | 2012-07-11 | 2012-07-11 11:04 | 2012-07-11 11:26 | GE - BGT4924H1K | 52 | 1.8 | Yes | Yes | 18.8 | 19.7 | -0.9 | 606E21632D774FED8EED005CAE4E978D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Tracy | CA | 95376-2324 |  | 2012-07-11 | 2012-07-11 11:20 | 2012-07-11 11:42 | GE - 21TA936H1F | 101 | 3.1 | Yes | Yes | 19.2 | 20.1 | -0.8 | 1BEE4756C02343178065F3D60A128195 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Stockton | CA | 95210-2307 |  | 2012-07-12 | 2012-07-12 14:56 | 2012-07-12 15:13 | BRYANT - 561CJX036000AFAA | 71 | 10.7 | Yes | Yes | 19.4 | 21.5 | -2.1 | 66D289DED8714107A58C23EA5A1EF088 |  | R22 | Non-TXV |  | 15.07% | 0.8493 | 28.96% | [5 empty] | Non-TXV | 15.07%
Parlier | CA | 93648-2020 |  | 2012-07-16 | 2012-07-16 09:29 | 2012-07-16 09:52 | GOODMAN - GPG13360701AB | 112 | 3.3 | Yes | Yes | 24.8 | 19.8 | 5 | 39B065EE74E54AAD94EA53BAF9EED57D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.662% | [5 empty] | Non-TXV | 2.946%
Marysville | CA | 95901-3605 |  | 2012-07-13 | 2012-07-13 10:15 | 2012-07-13 10:32 | GOODMAN - CKL18-1 | 53 | 5.1 | Yes | Yes | 20 | 19.5 | 0.5 | CF03B5CC739A4151BAE4ECF8965EE2D5 |  | R22 | Non-TXV |  | 9.623% | 0.90377 | 18.49% | [5 empty] | Non-TXV | 9.623%
Stockton | CA | 95210-1162 |  | 2012-07-11 | 2012-07-11 13:42 | 2012-07-11 14:08 | DAY & NIGHT - 585802405YACR | 48 | 3.3 | Yes | Yes | 15 | 13 | 2 | A8C81149FE1C496FB96BFBF6B1165FFB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Stockton | CA | 95207-3506 |  | 2012-07-11 | 2012-07-11 10:31 | 2012-07-11 10:48 | PAYNE - ACSO30A2C1 | 71 | 16.9 | Yes | Yes | 21.9 | 20 | 1.9 | CDD9A1FA02FF42B1AFB88F1DC0138FB5 |  | R22 | Non-TXV |  | 23.8% | 0.76197 | 45.74% | [5 empty] | Non-TXV | 23.8%
Stockton | CA | 95219-4591 |  | 2012-07-18 | 2012-07-18 14:47 | 2012-07-18 14:47 | RHEEM - RACB-018JAS | 28 | 0 | Yes | Yes | 20.6 | 19.3 | 1.3 | 3E2C36C9803E403FB4CDD021CD0D461D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9511 |  | 2012-07-11 | 2012-07-11 09:29 | 2012-07-11 10:03 | AMANA - PGB24C0452E | 62 | 2.6 | Yes | Yes | 22.7 | 18.9 | 3.8 | B07A49BF7E614B2088FFCDE3B69BFB1F |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Sanger | CA | 93657-3416 |  | 2012-07-10 | 2012-07-10 14:44 | 2012-07-10 15:25 | RHEEM - RRMA-036JK06X | 99 | 6.8 | Yes | Yes | 16.6 | 19.3 | -2.7 | 3BB4394BA8CE4BE3BFA1A52E1F814629 |  | R22 | Non-TXV |  | 6.869% | 0.93131 | 13.2% | [5 empty] | Non-TXV | 6.869%
Olivehurst | CA | 95961-0000 |  | 2012-07-11 | 2012-07-11 10:25 | 2012-07-11 10:54 | OTHER - DAYA-F036N070C | 67 | 2 | Yes | Yes | 25 | 19.9 | 5.1 | A8741B8ADF154B53B37B4FA781E7177D |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Stockton | CA | 95212-3033 |  | 2012-07-12 | 2012-07-12 15:36 | 2012-07-12 16:18 | YORK - H2RC036S06HG | 83 | 5.7 | Yes | Yes | 17.4 | 19.3 | -1.9 | CC9139B430964F5FA84D92F9EC72C552 |  | R22 | Non-TXV |  | 6.867% | 0.93133 | 13.2% | [5 empty] | Non-TXV | 6.867%
Marysville | CA | 95901-9560 |  | 2012-07-17 | 2012-07-17 09:42 | 2012-07-17 09:42 | LENNOX - HS19-411-3P | 85 | 0 | Yes | Yes | 24.6 | 18.7 | 5.9 | 54635268009044D39603BBF6DDEAEF4C |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1712 |  | 2012-07-10 | 2012-07-10 10:02 | 2012-07-10 10:12 | DAY & NIGHT - 585HJW024040ABAE | 85 | 12.7 | Yes | Yes | 18.2 | 18.3 | 0 | 2DE180E2F6B4405EBB3534FBE80275C9 |  | R22 | Non-TXV |  | 14.94% | 0.85059 | 28.71% | [5 empty] | Non-TXV | 14.94%
Chowchilla | CA | 93610-0000 |  | 2012-07-11 | 2012-07-11 12:01 | 2012-07-11 12:34 | GOODMAN - CRT42-1 | 125 | 3.7 | Yes | Yes | 19.3 | 18 | 1.3 | F224E41FC380406A978432D0A7E18435 |  | R22 | Non-TXV |  | 2.96% | 0.9704 | 5.688% | [5 empty] | Non-TXV | 2.96%
Stockton | CA | 95210-3256 |  | 2012-07-19 | 2012-07-19 09:20 | 2012-07-19 09:37 | DAY & NIGHT - 565BJ024 | 70 | -6.6 | Yes | Yes | 15 | 18 | -3 | 50C2ADE451764409922EBAA34F7DB896 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Fresno | CA | 93726-0334 |  | 2012-07-11 | 2012-07-11 09:49 | 2012-07-11 10:07 | RHEEM - RRKA-A030JK06X | 54 | 1.6 | Yes | Yes | 18 | 19.8 | -1.8 | 4D4E1543026840CF89A2F564802C64CD |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93722-4506 |  | 2012-07-30 | 2012-07-30 15:41 | 2012-07-30 15:57 | GOODMAN - UNK | 69 | 3.4 | Yes | Yes | 18.3 | 19.6 | -1.3 | 8294F2496A5541FDA380FB608648EB2D |  | R22 | Non-TXV |  | 4.928% | 0.95072 | 9.47% | [5 empty] | Non-TXV | 4.928%
Olivehurst | CA | 95961-4709 |  | 2012-07-11 | 2012-07-11 08:55 | 2012-07-11 09:15 | GOODMAN - CLT36-1B | 140 | -13.2 | Yes | Yes | 18 | 18.8 | -0.8 | 576168C6BDCE451B93EFB97252876D87 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Paradise | CA | 95969-3204 |  | 2012-07-20 | 2012-07-20 09:13 | 2012-07-20 09:37 | LENNOX - GCS20R-411-75-1P | 70 | 6.9 | Yes | Yes | 26 | 22.6 | 3.4 | A41F5CC818B2488C87DEE17DC0D27752 |  | R22 | Non-TXV |  | 9.857% | 0.90143 | 18.94% | [5 empty] | Non-TXV | 9.857%
Stockton | CA | 95212-9439 |  | 2012-07-19 | 2012-07-19 14:09 | 2012-07-19 14:31 | GUARDIAN - TCGD42S21S2HA | 67 | 7.5 | Yes | Yes | 18.8 | 20.8 | -2 | 7A91ADA847DA42C392A811735714D7EA |  | R22 | Non-TXV |  | 11.19% | 0.88806 | 21.51% | [5 empty] | Non-TXV | 11.19%
Stockton | CA | 95212-9439 |  | 2012-07-19 | 2012-07-19 14:26 | 2012-07-19 14:39 | DAY & NIGHT - 585803687YAC | 60 | 6.2 | Yes | Yes | 22.8 | 23.6 | -0.8 | AB2F31A1E3CF4CF8BD3199ED8F0C6DCA |  | R22 | Non-TXV |  | 10.33% | 0.89667 | 19.86% | [5 empty] | Non-TXV | 10.33%
Stockton | CA | 95215-6055 |  | 2012-07-12 | 2012-07-12 12:38 | 2012-07-12 13:02 | OTHER - 60WE24G1NA | 52 | 5 | Yes | Yes | 16.2 | 18.5 | -2.3 | FCA59B50888942339000BE5CB9C99485 |  | R22 | Non-TXV |  | 9.615% | 0.90385 | 18.48% | [5 empty] | Non-TXV | 9.615%
Olivehurst | CA | 95961-0000 |  | 2012-07-11 | 2012-07-11 11:36 | 2012-07-11 11:52 | RHEEM - RAFD-031JAS | 64 | 1.9 | Yes | Yes | 16 | 17.5 | -1.5 | 21BAFC219C864F5CAF3BE983F403F1E7 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Mendota | CA | 93640-1925 |  | 2012-07-11 | 2012-07-11 10:57 | 2012-07-11 11:18 | WESTINGHOUSE - UNK | 65 | 2.3 | Yes | Yes | 18.6 | 21 | -2.4 | 2FD8E2294D1048088577E51563EFED3F |  | R22 | Non-TXV |  | 3.538% | 0.96462 | 6.8% | [5 empty] | Non-TXV | 3.538%
Stockton | CA | 95210-2108 |  | 2012-08-03 | 2012-08-03 09:20 | 2012-08-03 09:38 | GOODMAN - GSC130361DF | 120 | -7.1 | Yes | Yes | 18.3 | 18.2 | 0.1 | 4DD4C72C39024B49A585EB8F971EE25B |  | R22 | Non-TXV |  | -5.917% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.917%
Yuba City | CA | 95993-9326 |  | 2012-07-10 | 2012-07-10 14:33 | 2012-07-10 14:55 | LENNOX - GCS16-411-100-1P | 76 | 9.9 | Yes | Yes | 18.9 | 19.9 | -1 | 0FE3EBA8814C4EEEA65234AE0448BF29 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.03% | 0.86974 | 25.03% | [5 empty] | Non-TXV | 13.03%
Chico | CA | 95926-4204 |  | 2012-07-12 | 2012-07-12 12:12 | 2012-07-12 12:45 | RUUD - UPKA-024JAZ | 72 | 3 | Yes | Yes | 20.6 | 21.6 | -1 | 5CDF52C0D4CE4C12BD8A618C680AF0AA |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Valley Springs | CA | 95252-9526 |  | 2012-07-19 | 2012-07-19 12:23 | 2012-07-19 12:46 | BARD - PH1230 | 99 | 3.1 | Yes | Yes | 17.2 | 19.4 | -2.2 | EC05E9B084854139B3D40CDFDD6E4188 |  | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Yuba City | CA | 95991-4364 |  | 2012-07-12 | 2012-07-12 16:07 | 2012-07-12 16:07 | ARMSTRONG - SHP10G30A-1 | 111 | 0 | Yes | Yes | -0.5 | 19 | -19.5 | AC15120A5CC04B29B5A26D5C4F2D3A18 | Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-4811 |  | 2012-07-20 | 2012-07-20 09:23 | 2012-07-20 09:59 | DAY & NIGHT - 589ANW030080ACAD | 70 | -7.8 | Yes | Yes | 27 | 21.9 | 5.1 | 10CD3775497A4887BF3A545A25D6638F |  | R22 | Non-TXV |  | -11.14% | 1.1114 | 3.121% |  |  |  |  | Non-TXV |  |  | -11.14%
Stockton | CA | 95210-1659 |  | 2012-07-23 | 2012-07-23 13:50 | 2012-07-23 14:09 | PAYNE - 591AN030-B | 68 | 3.7 | Yes | Yes | 19.1 | 21.7 | -2.6 | CF1ECC8543FA49D782477DFD56C56D84 |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Tracy | CA | 95376-3415 |  | 2012-07-11 | 2012-07-11 13:34 | 2012-07-11 14:06 | AMERICAN STANDARD - YCC030F1M0BC | 69 | 7.1 | Yes | Yes | 22 | 20.2 | 1.8 | 87B6A5AD17C746ECB51EF8EE5DB88837 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.29% | 0.8971 | 19.77% | [5 empty] | Non-TXV | 10.29%
Merced | CA | 95340-7004 |  | 2012-07-10 | 2012-07-10 09:02 | 2012-07-10 09:20 | GOODMAN - PGB0360501B | 50 | 8.2 | Yes | Yes | 24.7 | 22 | 2.7 | 7C6C8877AF5E4051A3C73259AEFE7D36 |  | R22 | Non-TXV |  | 16.4% | 0.836 | 31.52% | [5 empty] | Non-TXV | 16.4%
Olivehurst | CA | 95961-0000 |  | 2012-07-23 | 2012-07-23 15:07 | 2012-07-23 15:23 | BRYANT - UNK | 75 | 4.6 | Yes | Yes | 21 | 20.3 | 0.7 | 76AB45C6E3F24382A79EA01C0ED06C72 |  | R22 | Non-TXV |  | 6.133% | 0.93867 | 11.79% | [5 empty] | Non-TXV | 6.133%
Los Banos | CA | 93635-5328 |  | 2012-07-12 | 2012-07-12 10:11 | 2012-07-12 10:30 | GOODMAN - CKJ421B | 106 | 10.9 | Yes | Yes | 28 | 22 | 6 | BD9C71136C73490D95339BFA380D1C89 |  | R22 | Non-TXV |  | 10.28% | 0.89717 | 19.76% | [5 empty] | Non-TXV | 10.28%
Stockton | CA | 95206-5659 |  | 2012-08-15 | 2012-08-15 12:47 | 2012-08-15 13:10 | CARRIER - 38TDA036300 | 185 | 5.5 | Yes | Yes | 17 | 18.3 | -1.3 | 125E03C0969340A99D8F00479A7D1F98 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Merced | CA | 95348-2114 |  | 2012-07-19 | 2012-07-19 14:30 | 2012-07-19 14:30 | YORK - UNK | 132 | 0 | Yes | Yes | 18.4 | 19.2 | -0.8 | B5C36FBF368D42AEA8CAA9A5913F4ACE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-8124 |  | 2012-07-24 | 2012-07-24 12:11 | 2012-07-24 12:42 | TRANE - TTB024C1000A2 | 54 | 8.7 | Yes | Yes | 19.6 | 20.6 | -1 | 37F9A766310B43E2A759C6478D564265 |  | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Los Banos | CA | 93635-2822 |  | 2012-07-23 | 2012-07-23 09:55 | 2012-07-23 10:15 | GOODMAN - CK36-1B | 76 | -6.3 | Yes | Yes | 22.6 | 21.4 | 1.2 | 639975B9D64744409B4E86F8EA3EC9B6 |  | R22 | Non-TXV |  | -8.289% | 1.0829 | 2.321% |  |  |  |  | Non-TXV |  |  | -8.289%
Stockton | CA | 95206-3232 |  | 2012-08-10 | 2012-08-10 14:17 | 2012-08-10 14:17 | PAYNE - PY3GNAA30060NA | 98 | 0 | Yes | Yes | 25.4 | 20.1 | 5.3 | 7BC2EA4CDBF54D1BB51F643483874C6B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-8124 |  | 2012-07-12 | 2012-07-12 11:45 | 2012-07-12 12:05 | YORK - H2RA036S06E | 63 | 3.1 | Yes | Yes | 22.3 | 19.5 | 2.8 | 62BB181E91284541B926B6562E6EE1AD |  | R22 | Non-TXV |  | 4.921% | 0.95079 | 9.456% | [5 empty] | Non-TXV | 4.921%
Magalia | CA | 95954-9370 |  | 2012-08-13 | 2012-08-13 10:26 | 2012-08-13 10:54 | DAY & NIGHT - NA | 64 | 5 | Yes | Yes | 22.3 | 20.9 | 1.4 | 93B6F365E1A14C23BDC2736FA97C55C5 |  | R22 | Non-TXV |  | 7.812% | 0.92188 | 15.01% | [5 empty] | Non-TXV | 7.812%
Stockton | CA | 95212-3414 |  | 2012-07-19 | 2012-07-19 10:39 | 2012-07-19 10:59 | YORK - H2RC042S06A | 107 | 4.8 | Yes | Yes | 16 | 18.8 | -2.8 | B0BE9053981240BD8203B40EC4E81164 |  | R22 | Non-TXV |  | 4.486% | 0.95514 | 8.621% | [5 empty] | Non-TXV | 4.486%
Chico | CA | 95926-1524 |  | 2012-07-10 | 2012-07-10 09:03 | 2012-07-10 09:19 | AMANA - PGD42C0902E | 120 | 4 | Yes | Yes | 24.2 | 21.2 | 3.1 | 16F88C0DA57A4A6D93D150C75BA2E941 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95341-5708 |  | 2012-07-10 | 2012-07-10 10:53 | 2012-07-10 11:15 | LUXAIRE - 80W30G1 | 90 | 10.3 | Yes | Yes | 19.5 | 20.7 | -1.2 | 7EB792C1C7D0407881C067304C8510DC |  | R22 | Non-TXV |  | 11.44% | 0.88556 | 21.99% | [5 empty] | Non-TXV | 11.44%
Los Banos | CA | 93635-9412 |  | 2012-07-20 | 2012-07-20 09:29 | 2012-07-20 10:02 | ICP - AH036GA3 | 124 | 12.9 | Yes | Yes | 22.7 | 17.9 | 4.8 | 038FA8DBB47141E88656DC680BCBB300 |  | R22 | Non-TXV |  | 10.4% | 0.89597 | 19.99% | [5 empty] | Non-TXV | 10.4%
Stockton | CA | 95207-4292 |  | 2012-07-23 | 2012-07-23 09:04 | 2012-07-23 09:04 | RUUD - UAND-042JAS | 136 | 0 | Yes | Yes | 15 | 17.9 | -2.9 | 57B9D82F3A06487894D5227B1A672BF1 |  | R22 | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2312 |  | 2012-07-23 | 2012-07-23 08:56 | 2012-07-23 09:16 | ICP - GPFM36K060F | 85 | 2.7 | Yes | Yes | 20.5 | 21 | -0.5 | E33117CBC9C84EB6963ED8ECDB81E39C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Stockton | CA | 95203-1216 |  | 2012-07-31 | 2012-07-31 11:08 | 2012-07-31 11:26 | YORK - H2RA036S06D | 63 | 4.7 | Yes | Yes | 19.1 | 19.8 | -0.7 | 3709CF9421C347AA884090E801917E46 |  | R22 | Non-TXV |  | 7.46% | 0.9254 | 14.34% | [5 empty] | Non-TXV | 7.46%
Stockton | CA | 95209-5005 |  | 2012-07-18 | 2012-07-18 13:01 | 2012-07-18 13:18 | GOODMAN - GPG13240451BA | 77 | 2.6 | Yes | Yes | 26.3 | 20.4 | 6 | 7127AD6A7B3645E699E85B6BDF1E6DE4 |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Merced | CA | 95348-2221 |  | 2012-07-19 | 2012-07-19 13:29 | 2012-07-19 13:55 | BDP - 585GJ048AF | 67 | 3.1 | Yes | Yes | 20.4 | 20.6 | -0.2 | 3A73D94218314F71A04389841341A1A2 |  | R22 | Non-TXV |  | 4.627% | 0.95373 | 8.892% | [5 empty] | Non-TXV | 4.627%
Manteca | CA | 95337-6864 |  | 2012-07-10 | 2012-07-10 12:26 | 2012-07-10 12:49 | DAY & NIGHT - 597AN042-A | 169 | 11.6 | Yes | Yes | 20.8 | 22 | -1.2 | 13F49D21E42F4E8BB634CDBEC022773B |  | R22 | Non-TXV |  | 6.864% | 0.93136 | 13.19% | [5 empty] | Non-TXV | 6.864%
Fresno | CA | 93722-6104 |  | 2012-07-19 | 2012-07-19 14:30 | 2012-07-19 14:56 | YORK - D1NA036N05606C | 67 | 2 | Yes | Yes | 25.5 | 20.4 | 5.1 | A9B14A3C71444F1987A35A4D8C1EBB6A |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Stockton | CA | 95215-1012 |  | 2012-07-19 | 2012-07-19 13:19 | 2012-07-19 13:42 | LENNOX - 10GCSO36-75-1PA | 58 | 4.5 | Yes | Yes | 18.2 | 18.7 | -0.5 | 2952DD8E00FB4AD9BA0F0E953193407E |  | R22 | Non-TXV |  | 7.759% | 0.92241 | 14.91% | [5 empty] | Non-TXV | 7.759%
Merced | CA | 95341-5627 |  | 2012-07-20 | 2012-07-20 13:19 | 2012-07-20 13:58 | AIRE-FLO - PY1PNB030040AAAA | 55 | 10 | Yes | Yes | 24.2 | 26.5 | -2.3 | F8E73D041A554619A7E16F9808346304 |  | R22 | Non-TXV |  | 18.18% | 0.81818 | 34.94% | [5 empty] | Non-TXV | 18.18%
Marysville | CA | 95901-3626 |  | 2012-07-20 | 2012-07-20 13:35 | 2012-07-20 13:51 | AMERICAN STANDARD - YCC036F1MOBK | 85 | 2.6 | Yes | Yes | 20 | 22.5 | -2.5 | 47C4F6178D6E4FE0BAAAB137AAFFA465 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Yuba City | CA | 95991-7514 |  | 2012-07-25 | 2012-07-25 08:52 | 2012-07-25 09:16 | BDP - 561GJ024 | 76 | 4 | Yes | Yes | 20.3 | 19.3 | 1 | A53BACF1F564479A948926C0E4CF6634 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Merced | CA | 95348-1339 |  | 2012-07-19 | 2012-07-19 13:08 | 2012-07-19 13:27 | LENNOX - 10ACB30-7P | 70 | 2.8 | Yes | Yes | 18.9 | 19.8 | -0.9 | D947B9BE317E44F18533D78AE730983E |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Olivehurst | CA | 95961-0000 |  | 2012-07-23 | 2012-07-23 14:31 | 2012-07-23 14:50 | RHEEM - RAHE-030JAS | 78 | 3.1 | Yes | Yes | 18 | 19.9 | -1.9 | B06BFF20DE6B4ABFA1FC88D7EB4E37C8 |  | R22 | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
Stockton | CA | 95210-4171 |  | 2012-07-23 | 2012-07-23 14:39 | 2012-07-23 14:57 | RUUD - UAHE-048JAS | 114 | 6.2 | Yes | Yes | 24.8 | 21.5 | 3.3 | DE4042BCE25E4EE1BA154060D16F5766 |  | R22 | Non-TXV |  | 5.439% | 0.94561 | 10.45% | [5 empty] | Non-TXV | 5.439%
Marysville | CA | 95901-5414 |  | 2012-07-31 | 2012-07-31 11:55 | 2012-07-31 12:16 | - PA13NF024-J | 72 | -4.3 | Yes | Yes | 17.5 | 20.4 | -2.9 | AE827C65B452436FBD26180BBE8B858F |  | R22 | Non-TXV |  | -5.972% | 1.0597 | 1.673% |  |  |  |  | Non-TXV |  |  | -5.972%
Brownsville | CA | 95919-0000 |  | 2012-07-25 | 2012-07-25 09:52 | 2012-07-25 09:52 | TRANE - 4TTX4048B1000AA | 127 | 0 | Yes | Yes | 23.6 | 19.5 | 4.1 | 1A9C2FAF085E4D4F9801E0DDDC551BDD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-0000 |  | 2012-07-19 | 2012-07-19 14:58 | 2012-07-19 15:17 | DAY & NIGHT - PGD336060K001C1 | 100 | 3.8 | Yes | Yes | 21 | 19.4 | 1.6 | 134CD2541E8E452E8FCA256EF3DE4EAE |  | R410A | TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | TXV | 3.8%
Stockton | CA | 95209-2169 |  | 2012-07-18 | 2012-07-18 08:24 | 2012-07-18 08:41 | YORK - D3NZ024N05606NXA | 58 | -3.4 | Yes | Yes | 23.8 | 18.7 | 5.1 | 7011B213E7C9464A81F79B4D39A69900 |  | R410A | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Merced | CA | 95348-2241 |  | 2012-07-20 | 2012-07-20 08:18 | 2012-07-20 08:40 | GOODMAN - GSC130361FA | 83 | 2.5 | Yes | Yes | 18.7 | 18.5 | 0.2 | 5F2C5887F0334A61A1BD431ECB06910F |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Fresno | CA | 93706-1439 |  | 2012-07-19 | 2012-07-19 18:14 | 2012-07-19 18:31 | OTHER - UNK | 70 | 2.4 | Yes | Yes | 17.1 | 19.6 | -2.5 | EA81CE6E8E854E3DA0CBF8877E7B090D |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Merced | CA | 95341-5657 |  | 2012-07-23 | 2012-07-23 15:33 | 2012-07-23 15:49 | PAYNE - PH13NR030-E | 105 | 4.1 | Yes | Yes | 17.9 | 19.8 | -1.9 | 69E38250A19A4103878E2E00FA6B7946 |  | R22 | TXV |  | 3.905% | 0.96095 | 7.504% | [5 empty] | TXV | 3.905%
Olivehurst | CA | 95961-7554 |  | 2012-07-23 | 2012-07-23 13:53 | 2012-07-23 14:07 | GOODMAN - GSH130361AD | 188 | 5.8 | Yes | Yes | 16 | 18.7 | -2.7 | 4E9395994A2046FAB922CB41D87ACFF3 |  | R22 | TXV |  | 3.085% | 0.96915 | 5.929% | [5 empty] | TXV | 3.085%
Merced | CA | 95341-7728 |  | 2012-07-25 | 2012-07-25 11:06 | 2012-07-25 11:30 | RUUD - 4AKA037JAZ | 85 | 2.5 | Yes | Yes | 19.5 | 18.3 | 1.2 | 7574721EC8E24BBA9C4A6289D85805AB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Tracy | CA | 95376-3123 |  | 2012-08-15 | 2012-08-15 15:09 | 2012-08-15 15:30 | YORK - D1NQ036N05606NXA | 58 | 1.8 | Yes | Yes | 22.2 | 18.1 | 4.1 | BECD3B5F609940E4AE907AFEDD647EA2 |  | R410A | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Merced | CA | 95341-5802 |  | 2012-07-23 | 2012-07-23 12:56 | 2012-07-23 13:16 | GOODMAN - PGB030050-1 | 56 | 1.9 | Yes | Yes | 22.7 | 21.3 | 1.4 | B570228CAAAC4DA7B5CA3CDB0794B396 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Clovis | CA | 93611-0382 |  | 2012-07-30 | 2012-07-30 11:42 | 2012-07-30 12:28 | YORK - 2094E836 | 86 | -6.1 | Yes | Yes | 17.4 | 19.6 | -2.2 | EA2F27E79F7A474FB2484D4C718026AB |  | R22 | Non-TXV |  | -7.093% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.093%
Stockton | CA | 95209-2147 |  | 2012-07-18 | 2012-07-18 13:16 | 2012-07-18 13:34 | DAY & NIGHT - UNK | 101 | 4.7 | Yes | Yes | 21.9 | 20.2 | 1.7 | 4DCC99CF15B744CC987A3742B95F606F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.653% | 0.95347 | 8.943% | [5 empty] | Non-TXV | 4.653%
Marysville | CA | 95901-3865 |  | 2012-07-25 | 2012-07-25 10:41 | 2012-07-25 10:58 | PAYNE - PA10JA018-A | 61 | -3.6 | Yes | Yes | 26.9 | 21 | 5.9 | 9372DD50D0C143549BA1067C1F832946 |  | R22 | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Atwater | CA | 95301-2066 |  | 2012-07-10 | 2012-07-10 10:12 | 2012-07-10 10:29 | WESTINGHOUSE - NA | 77 | 2.3 | Yes | Yes | 23.9 | 20.4 | 3.5 | 323D42345B1B4471BA979455CF564F8B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Stockton | CA | 95207-4688 |  | 2012-07-11 | 2012-07-11 09:47 | 2012-07-11 10:05 | RUUD - URKA-A030JK06X | 54 | 2.7 | Yes | Yes | 18.7 | 19.9 | -1.2 | 65BF850387264BEB9B33907DAA5B5574 |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Yuba City | CA | 95991-5956 |  | 2012-07-12 | 2012-07-12 13:54 | 2012-07-12 14:13 | NORDYNE - FS3BA-036KA | 69 | 5.3 | Yes | Yes | 18.9 | 19.1 | -0.2 | AFE8195A40D34925BB45540E2D0C2588 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.681% | 0.92319 | 14.76% | [5 empty] | Non-TXV | 7.681%
Atwater | CA | 95301-9601 |  | 2012-07-10 | 2012-07-10 10:38 | 2012-07-10 10:38 | COLEMAN - NA | 82 | 0 | Yes | Yes | 13.3 | 20.6 | -7.3 | C1E9866BB21F4E5687CB552A14EE1E61 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-4727 |  | 2012-07-26 | 2012-07-26 13:31 | 2012-07-26 13:48 | RHEEM - RAK-060JAZ | 112 | -10.5 | Yes | Yes | 22 | 20.4 | 1.6 | B9D334FBA3634614A270B304DC3ED7C1 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Yuba City | CA | 95991-3745 |  | 2012-07-12 | 2012-07-12 11:47 | 2012-07-12 12:07 | RHEEM - UNK | 58 | 26.7 | Yes | Yes | 26.4 | 22.1 | 4.3 | ADF3600910FD46C2A5EB46037DEBDC74 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 46.03% | 0.53966 | 88.47% | [5 empty] | Non-TXV | 46.03%
Stockton | CA | 95207-3364 |  | 2012-07-10 | 2012-07-10 15:16 | 2012-07-10 15:34 | GE - 36RCU108C | 85 | 7.8 | Yes | Yes | 15.2 | 17.2 | -2 | E612BD2379D54F10B9E353C747A24021 |  | R22 | Non-TXV |  | 9.176% | 0.90824 | 17.64% | [5 empty] | Non-TXV | 9.176%
Tracy | CA | 95376-2738 |  | 2012-07-11 | 2012-07-11 09:36 | 2012-07-11 10:00 | BRYANT - 583ANW036090AAHF | 82 | 2.5 | Yes | Yes | 18.3 | 19.9 | -1.6 | C9C71F70B02D4FA39A2C77175BAABF83 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Stockton | CA | 95215-6831 |  | 2012-07-12 | 2012-07-12 12:09 | 2012-07-12 12:36 | DAY & NIGHT - PGC042K080E | 84 | 3.4 | Yes | Yes | 18.6 | 19.9 | -1.3 | 75A49573D3694E7489ED42964B80B48C |  | R22 | Non-TXV |  | 4.048% | 0.95952 | 7.779% | [5 empty] | Non-TXV | 4.048%
Stockton | CA | 95206-6034 |  | 2012-07-23 | 2012-07-23 10:40 | 2012-07-23 10:57 | YORK - H2RA030S06A | 46 | 3 | Yes | Yes | 22.8 | 19.2 | 3.6 | A630F00B243040B79E100A53276F697D |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Merced | CA | 95340-2357 |  | 2012-07-11 | 2012-07-11 09:57 | 2012-07-11 10:23 | TRANE - BTD730A100B0 | 74 | -4.4 | Yes | Yes | 25.6 | 20.4 | 5.2 | 9893D76A3B4A4B58B37487417EF5CEB3 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Los Banos | CA | 93635-2901 |  | 2012-07-12 | 2012-07-12 10:41 | 2012-07-12 10:58 | BDP - 585HJW030040ABAF | 68 | 11.8 | Yes | Yes | 25.7 | 26.8 | -1.1 | 330D098B97854DD787F05963DE671EA5 |  | R22 | Non-TXV |  | 17.35% | 0.82647 | 33.35% | [5 empty] | Non-TXV | 17.35%
Merced | CA | 95340-1664 |  | 2012-07-20 | 2012-07-20 12:01 | 2012-07-20 12:17 | AIRE-FLO - 48SX036060331AA | 84 | 6.4 | Yes | Yes | 17.9 | 19.4 | -1.5 | F209FFC612D94183AB949860E5B2864E |  | R22 | Non-TXV |  | 7.619% | 0.92381 | 14.64% | [5 empty] | Non-TXV | 7.619%
Chico | CA | 95973-8948 |  | 2012-07-12 | 2012-07-12 09:13 | 2012-07-12 09:16 | GOODMAN - GSH130301A | 153 | 9.4 | Yes | Yes | 23 | 21.7 | 1.4 | A4445E7429B742599349C2997B8BCBD8 |  | R22 | Non-TXV |  | 6.144% | 0.93856 | 11.81% | [5 empty] | Non-TXV | 6.144%
Chico | CA | 95973-8948 |  | 2012-07-12 | 2012-07-12 09:18 | 2012-07-12 09:52 | GOODMAN - GHP1348H21AB | 228 | 7.1 | Yes | Yes | 19.9 | 20.9 | -1 | 7F199F80217D48139CB4158F5F491BF4 |  | R22 | Non-TXV |  | 3.114% | 0.96886 | 5.984% | [5 empty] | Non-TXV | 3.114%
Merced | CA | 95341-5782 |  | 2012-07-14 | 2012-07-14 15:25 | 2012-07-14 15:25 | OTHER - 60WB18F1NA | 36 | 0 | Yes | Yes | 15.8 | 20.6 | -4.8 | DA25EE76A0B94C22BFEE590C9AC7487C | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-3268 |  | 2012-07-31 | 2012-07-31 13:26 | 2012-07-31 13:51 | TRANE - 2YCC3024A1040AB | 72 | 5.6 | Yes | Yes | 22.8 | 20.6 | 2.2 | 3170F527DA3F450F9468F5BC5453C64E |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Chico | CA | 95926-3060 |  | 2012-07-19 | 2012-07-19 12:37 | 2012-07-19 16:03 | OTHER - 591ANX030000AAAA | 75 | 3.9 | Yes | Yes | 23.7 | 22.1 | 1.6 | 895633252CB940C68A5023FE6EA3F26A |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Los Banos | CA | 93635-3817 |  | 2012-07-20 | 2012-07-20 10:39 | 2012-07-20 10:57 | AIRE-FLO - 589ANW036060ADAF | 84 | 8 | Yes | Yes | 18.4 | 19.8 | -1.4 | E05EA9E858B646908C1958F405D845D7 |  | R22 | Non-TXV |  | 9.524% | 0.90476 | 18.3% | [5 empty] | Non-TXV | 9.524%
Lincoln | CA | 95648-1667 |  | 2012-07-24 | 2012-07-24 14:31 | 2012-07-24 14:53 | RUUD - UAKA-037JAZ | 79 | 9.6 | Yes | Yes | 20.8 | 20.4 | 0.4 | B8C932FFFB2F48A4988AB513478B2CF0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.15% | 0.87848 | 23.35% | [5 empty] | Non-TXV | 12.15%
Lincoln | CA | 95648-2075 |  | 2012-07-24 | 2012-07-24 13:40 | 2012-07-24 14:06 | AMERICAN STANDARD - YCY030F1M0AA | 150 | 16.4 | Yes | Yes | 24.3 | 21.4 | 2.9 | 17A0B87771234E70A02D513CAEFA99E9 |  | R22 | Non-TXV |  | 10.93% | 0.89067 | 21.01% | [5 empty] | Non-TXV | 10.93%
Chico | CA | 95926-5303 |  | 2012-07-19 | 2012-07-19 16:12 | 2012-07-19 16:48 | RUUD - UAF-024JAS | 69 | 8.8 | Yes | Yes | 19.5 | 19.5 | 0.1 | E6633EDAEB2B48C68BA26C69254DDA29 |  | R22 | Non-TXV |  | 12.75% | 0.87246 | 24.51% | [5 empty] | Non-TXV | 12.75%
Auburn | CA | 95603-4652 |  | 2012-07-18 | 2012-07-18 11:26 | 2012-07-18 11:26 | DAY & NIGHT - PGN4300040K1 | 125 | 0 | Yes | Yes | 20.9 | 19 | 1.9 | 5CD4096BD8994015A58213B343B21E7E |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3948 |  | 2012-07-25 | 2012-07-25 11:48 | 2012-07-25 12:04 | GE - BTN936BL00A0 | 179 | 5.4 | Yes | Yes | 20.3 | 22.1 | -1.8 | F631F196393042C99DE7C37262AE1EFD |  | R22 | Non-TXV |  | 3.017% | 0.96983 | 5.798% | [5 empty] | Non-TXV | 3.017%
Rocklin | CA | 95677-3180 |  | 2012-07-19 | 2012-07-19 14:38 | 2012-07-19 14:58 | GOODMAN - GSC130181 | 89 | 8.3 | Yes | Yes | 15.7 | 18.6 | -2.9 | 03448F6D3F6A4CFB9A8CC92BDB83DA8C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.326% | 0.90674 | 17.92% | [5 empty] | Non-TXV | 9.326%
Chico | CA | 95973-8971 |  | 2012-07-25 | 2012-07-25 11:33 | 2012-07-25 11:49 | PAYNE - 569CB048 | 129 | 10.7 | Yes | Yes | 22.5 | 20.6 | 2 | BCC1445F3641438C84B1A8D53BBE7DD5 |  | R22 | Non-TXV |  | 8.295% | 0.91705 | 15.94% | [5 empty] | Non-TXV | 8.295%
Stockton | CA | 95205-4638 |  | 2012-08-06 | 2012-08-06 12:02 | 2012-08-06 12:20 | AMERICAN STANDARD - YCC030F1MOBJ | 72 | 4.4 | Yes | Yes | 21.5 | 20.8 | 0.7 | FE64582F81CC46288702A1F76A215A1F |  | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Rocklin | CA | 95677-3517 |  | 2012-07-18 | 2012-07-18 14:18 | 2012-07-18 14:40 | - 38EN018310 | 59 | 19.9 | Yes | Yes | 18.1 | 20.4 | -2.3 | 17995AFEB0A4470A95E239F1337A64C3 |  | R22 | Non-TXV |  | 33.73% | 0.66271 | 64.82% | [5 empty] | Non-TXV | 33.73%
Auburn | CA | 95603-4104 |  | 2012-07-24 | 2012-07-24 10:38 | 2012-07-24 11:01 | RHEEM - 13PJL24A01 | 91 | 3.3 | Yes | Yes | 19 | 21.4 | -2.4 | 681F99BAA6734819A2283FD8AD21659A |  | R410A | TXV |  | 3.626% | 0.96374 | 6.969% | [5 empty] | TXV | 3.626%
Lincoln | CA | 95648-1517 |  | 2012-07-24 | 2012-07-24 15:11 | 2012-07-24 15:31 | AMANA - RCC36C2A | 110 | 10.2 | Yes | Yes | 22.5 | 20.1 | 2.5 | B66B79BB726C45918A67935C1219051E |  | R22 | Non-TXV |  | 9.273% | 0.90727 | 17.82% | [5 empty] | Non-TXV | 9.273%
Auburn | CA | 95603-9447 |  | 2012-08-08 | 2012-08-08 10:35 | 2012-08-08 10:35 | TRANE - WCH036B100AB | 152 | 0 | Yes | Yes | 25.4 | 19.5 | 5.9 | 2E0B1E7CBF534A3D94F2CAF9A221CEF3 |  | R22 | TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-2543 |  | 2012-07-24 | 2012-07-24 14:05 | 2012-07-24 14:22 | PAYNE - 567C018RC0 | 70 | 2.8 | Yes | Yes | 22 | 20.1 | 1.9 | 50C17FA463EB4D0381FE48F80510B35D |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Atwater | CA | 95301-2552 |  | 2012-07-19 | 2012-07-19 11:40 | 2012-07-19 11:59 | GUARDIAN - AC036X1322A | 96 | 3.3 | Yes | Yes | 19.3 | 20.4 | -1.1 | F798A295E073403C8644FFF53281C887 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Merced | CA | 95341-5732 |  | 2012-07-23 | 2012-07-23 13:42 | 2012-07-23 13:42 | OTHER - UNK | 50 | 0 | Yes | Yes | 20.5 | 17.1 | 3.4 | 279C8782507043029A2513327FBAD2DE | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-2552 |  | 2012-08-08 | 2012-08-08 16:25 | 2012-08-08 16:25 | BDP - 567C018RCU | 37 | 0 | Yes | Yes | 15.3 | 17.6 | -2.3 | B4F48D2AF9A1462F8F241E1CF3871725 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-3010 |  | 2012-08-09 | 2012-08-09 10:06 | 2012-08-09 10:22 | GOODMAN - CKL36-1K | 85 | 6.9 | Yes | Yes | 18 | 19.9 | -1.9 | 7648B5C0F6B548829249F0E76F72DB59 |  | R22 | Non-TXV |  | 8.118% | 0.91882 | 15.6% | [5 empty] | Non-TXV | 8.118%
Livingston | CA | 95334-1855 |  | 2012-07-19 | 2012-07-19 09:21 | 2012-07-19 09:43 | GOODMAN - CK30-1A | 76 | 3.2 | Yes | Yes | 18.1 | 20.3 | -2.2 | BA8914E90C17487392FF05068CCFDFFA |  | R22 | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Stockton | CA | 95210-4630 |  | 2012-07-18 | 2012-07-18 13:42 | 2012-07-18 13:59 | YORK - TCGD24S41S3HA | 61 | -3.6 | Yes | Yes | 18.9 | 18.9 | 0 | C890F6B8BF4D4725B56534E30696A374 |  | R410A | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Fresno | CA | 93711-1543 |  | 2012-07-19 | 2012-07-19 14:00 | 2012-07-19 14:00 | GOODMAN - GPG1336045M41AD | 85 | 0 | Yes | Yes | 24.1 | 18.5 | 5.6 | 334F245DE0E74175AB67246FF44EE194 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-8707 |  | 2012-07-19 | 2012-07-19 13:03 | 2012-07-19 13:21 | ICP - PHF336000K00A1 | 178 | 6.2 | Yes | Yes | 18.8 | 18.3 | 0.5 | F527B761AE194C93AFE2C54D9EC141DF |  | R22 | Non-TXV |  | 3.483% | 0.96517 | 6.694% | [5 empty] | Non-TXV | 3.483%
Chico | CA | 95928-7602 |  | 2012-07-20 | 2012-07-20 09:51 | 2012-07-20 10:14 | BRYANT - PH10JA024-C | 72 | 7.9 | Yes | Yes | 21 | 22 | -1 | CBD9C5197A9C4B25932F545BC081D353 |  | R22 | TXV |  | 10.97% | 0.89028 | 21.09% | [5 empty] | TXV | 10.97%
Fresno | CA | 93710-6307 |  | 2012-07-25 | 2012-07-25 12:04 | 2012-07-25 12:32 | TAPPAN - UNK | 82 | 2.6 | Yes | Yes | 24.8 | 20.2 | 4.6 | 2F9A076410E24C9887C172A2E1F0176A |  | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Clovis | CA | 93612-2559 |  | 2012-07-25 | 2012-07-25 10:47 | 2012-07-25 11:08 | GOODMAN - GSC130421AC | 137 | 4.3 | Yes | Yes | 26.3 | 20.4 | 5.9 | 527654CD44CD4C3CBE9583F91C321D43 |  | R22 | Non-TXV |  | 3.139% | 0.96861 | 6.032% | [5 empty] | Non-TXV | 3.139%
Stockton | CA | 95209-4023 |  | 2012-07-18 | 2012-07-18 09:45 | 2012-07-18 10:03 | BDP - 585B024050YACR | 51 | 2 | Yes | Yes | 20.9 | 19.3 | 1.6 | 6A1C7DEC65DF42BEA247BD0B5172005E |  | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Stockton | CA | 95205-2932 |  | 2012-08-06 | 2012-08-06 11:26 | 2012-08-06 11:44 | RHEEM - RRKA-A024JK06X | 50 | 5.4 | Yes | Yes | 20.3 | 22.1 | -1.8 | 6C9D4976A7D044C6812EA2AE41D49271 |  | R22 | Non-TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | Non-TXV | 10.8%
Oroville | CA | 95966-6605 |  | 2012-07-18 | 2012-07-18 11:46 | 2012-07-18 12:09 | AMERICAN STANDARD - TTD730B10A0 | 69 | 3.7 | Yes | Yes | 24.1 | 21.2 | 2.9 | 2E9EA152778F44D2A13F017208CD37D4 |  | R22 | Non-TXV |  | 5.362% | 0.94638 | 10.31% | [5 empty] | Non-TXV | 5.362%
Livingston | CA | 95334-1872 |  | 2012-07-19 | 2012-07-19 09:44 | 2012-07-19 10:01 | CARRIER - 591ANX042000ABAA | 85 | 4.3 | Yes | Yes | 18.4 | 21 | -2.6 | E4A01A6E29F544CFAF22C2CD6C5D7851 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Stockton | CA | 95210-1442 |  | 2012-07-18 | 2012-07-18 14:10 | 2012-07-18 14:10 | YORK - D1NA024N05606C | 54 | 0 | Yes | Yes | 19.4 | 19.3 | 0.1 | F7B9F0579CBC45C8A7D2AB96EC92612A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-5016 |  | 2012-08-16 | 2012-08-16 14:36 | 2012-08-16 14:57 | LENNOX - 12GCS036-75-3PA | 110 | 3.6 | Yes | Yes | 18 | 20.4 | -2.4 | 287FF49C707F43C2AFC8ACCAF2052CA0 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Kerman | CA | 93630-1728 |  | 2012-07-20 | 2012-07-20 12:23 | 2012-07-20 12:42 | ALLEGIANCE - 7A0036A100A1 | 86 | 2.5 | Yes | Yes | 25.3 | 20.2 | 5.1 | FC5C1F3C3C93474796403BC54A3943A4 |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Sanger | CA | 93657-9492 |  | 2012-07-23 | 2012-07-23 10:58 | 2012-07-23 11:16 | OTHER - N/A | 90 | 3.9 | Yes | Yes | 18.4 | 20.3 | -1.9 | 3A5FF526228441C0A6EA39E3979161F8 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Sanger | CA | 93657-9492 |  | 2012-07-23 | 2012-07-23 11:17 | 2012-07-23 11:37 | BDP - 588ANW048080ABAG | 101 | 3.4 | Yes | Yes | 21.7 | 20.9 | 0.8 | 89DB6D7C199E4559ABE92E0D4CB71969 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.366% | 0.96634 | 6.469% | [5 empty] | Non-TXV | 3.366%
Stockton | CA | 95209-4023 |  | 2012-07-18 | 2012-07-18 09:10 | 2012-07-18 09:28 | BDP - 585B024050YACR | 51 | 1.6 | Yes | Yes | 16.2 | 18.7 | -2.5 | 46C0E6C45A484CAF8E2C180CC1A02F13 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Merced | CA | 95348-1943 |  | 2012-07-25 | 2012-07-25 12:12 | 2012-07-25 12:48 | RHEEM - RAKA-042JAZ | 79 | 2.6 | Yes | Yes | 18.9 | 20.7 | -1.8 | 6FEA223CC0D14F57AF23D62FA6B6FF85 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Magalia | CA | 95954-8815 |  | 2012-07-19 | 2012-07-19 09:50 | 2012-07-19 10:34 | RUUD - URGG-05E30JKR | 62 | 2.2 | Yes | Yes | 24.5 | 21.2 | 3.3 | E9B0BEF10BC94C12B626E908DDDE0A37 |  | R22 | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Marysville | CA | 95901-3533 |  | 2012-07-19 | 2012-07-19 14:03 | 2012-07-19 14:20 | YORK - H2RC048S06A | 119 | 11.9 | Yes | Yes | 16 | 18.6 | -2.6 | 293C29C7CED541E0813E8CB5EADF4082 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Huron | CA | 93234-0000 |  | 2012-07-20 | 2012-07-20 10:20 | 2012-07-20 10:38 | CARRIER - N/A | 80 | 2.4 | Yes | Yes | 24.4 | 19.7 | 4.7 | BA07C0D450314D9A966CF08FAF78D05C |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Olivehurst | CA | 95961-4144 |  | 2012-07-25 | 2012-07-25 12:14 | 2012-07-25 12:38 | RUUD - 13AJA60A01 | 191 | 5.7 | Yes | Yes | 21 | 19.9 | 1.1 | 4252FFE7A7B24BE3BD1C2845F468A058 |  | R22 | Non-TXV |  | 2.984% | 0.97016 | 5.735% | [5 empty] | Non-TXV | 2.984%
Live Oak | CA | 95953-2241 |  | 2012-07-23 | 2012-07-23 09:37 | 2012-07-23 09:58 | OTHER - DAYA-F036N070C | 67 | 2 | Yes | Yes | 20 | 18.7 | 1.3 | C284E5A1A7FE4DC7A5D3EBFA45AF5C6C |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Yuba City | CA | 95993-1601 |  | 2012-07-18 | 2012-07-18 12:08 | 2012-07-18 12:28 | OTHER - 567C030RCO | 63 | 5.8 | Yes | Yes | 20 | 19.9 | 0.1 | D6421A9FEF1B4B6B8A938DE32DE0010A |  | R22 | Non-TXV |  | 9.206% | 0.90794 | 17.69% | [5 empty] | Non-TXV | 9.206%
Marysville | CA | 95901-4819 |  | 2012-07-25 | 2012-07-25 13:29 | 2012-07-25 13:46 | LENNOX - GCS20R-511-125-2P | 115 | 3.7 | Yes | Yes | 25.6 | 20.4 | 5.2 | F20ACC6B85E640688E74AC7A798EC95E |  | R22 | Non-TXV |  | 3.217% | 0.96783 | 6.183% | [5 empty] | Non-TXV | 3.217%
Fresno | CA | 93710-6352 |  | 2012-07-19 | 2012-07-19 15:41 | 2012-07-19 16:53 | GOODMAN - CK24-18 | 73 | -4.3 | Yes | Yes | 19.1 | 19.9 | -0.8 | C0A52A2E90994F3C93C842B1857E44DB |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Marysville | CA | 95901-7201 |  | 2012-07-31 | 2012-07-31 11:11 | 2012-07-31 11:29 | OTHER - 561CJ024-A | 60 | -3.5 | Yes | Yes | 19.9 | 20.4 | -0.5 | C729F1EE5D25480093564A8C110602FF |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Marysville | CA | 95901-8254 |  | 2012-07-19 | 2012-07-19 13:17 | 2012-07-19 13:34 | CARRIER - 38CKC36350 | 75 | 9.5 | Yes | Yes | 17 | 19.3 | -2.3 | DC64008240374B7990C9DFAC2580DBDF |  | R22 | Non-TXV |  | 12.67% | 0.87333 | 24.34% | [5 empty] | Non-TXV | 12.67%
Olivehurst | CA | 95961-4405 |  | 2012-08-01 | 2012-08-01 10:44 | 2012-08-01 11:09 | OTHER - UNK | 85 | 2.8 | Yes | Yes | 20 | 19.3 | 0.7 | A348FED7529141549724196237067471 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Oroville | CA | 95966-9660 |  | 2012-07-24 | 2012-07-24 09:59 | 2012-07-24 10:38 | AMERICAN STANDARD - 4WCY4036A1000AA | 118 | 4.8 | Yes | Yes | 24.9 | 22 | 2.9 | 3E26C1C70C66404E9E4A99B02F061D94 |  | R22 | Non-TXV |  | 4.068% | 0.95932 | 7.817% | [5 empty] | Non-TXV | 4.068%
Chico | CA | 95926-3258 |  | 2012-07-19 | 2012-07-19 11:39 | 2012-07-19 11:56 | LENNOX - 13ACC-030-230-01 | 107 | 5.7 | Yes | Yes | 19 | 20.7 | -1.7 | 16FF2F64561A4B3FAE21FE46EC92A959 |  | R22 | Non-TXV |  | 5.327% | 0.94673 | 10.24% | [5 empty] | Non-TXV | 5.327%
Riverdale | CA | 93656-9243 |  | 2012-07-19 | 2012-07-19 12:27 | 2012-07-19 12:48 | LENNOX - 12GCS036X-75-3PA | 110 | 9.3 | Yes | Yes | 22.7 | 20.4 | 2.3 | 22234D5AA2FB41A0A3DCA8418772194D |  | R22 | Non-TXV |  | 8.455% | 0.91545 | 16.25% | [5 empty] | Non-TXV | 8.455%
Winton | CA | 95388-9535 |  | 2012-07-19 | 2012-07-19 10:30 | 2012-07-19 11:05 | OTHER - CTG042E7C | 119 | 4 | Yes | Yes | 17.8 | 19.9 | -2.1 | 00CDE58246434A44A7E56162CC33B0B7 |  | R22 | Non-TXV |  | 3.361% | 0.96639 | 6.46% | [5 empty] | Non-TXV | 3.361%
Huron | CA | 93234-0000 |  | 2012-07-20 | 2012-07-20 09:47 | 2012-07-20 10:17 | TEMPSTAR - PGF330060K01A2 | 89 | 2.6 | Yes | Yes | 20.9 | 19.9 | 1 | 07D50242F6274A34A834ACA7B01D68E9 |  | R22 | Non-TXV |  | 2.921% | 0.97079 | 5.614% | [5 empty] | Non-TXV | 2.921%
Oroville | CA | 95965-4751 |  | 2012-07-18 | 2012-07-18 12:25 | 2012-07-18 12:46 | DAY & NIGHT - 561AJ030-A | 73 | -3.4 | Yes | Yes | 19.4 | 19.9 | -0.5 | CDA31133B71447BB8FF9FC17D49E9D8D |  | R22 | TXV |  | -4.658% | 1.0466 | 1.304% |  |  |  |  | TXV |  |  | -4.658%
Fresno | CA | 93727-7210 |  | 2012-07-19 | 2012-07-19 12:19 | 2012-07-19 13:06 | DAY & NIGHT - 535A0360807ACR | 62 | 2.1 | Yes | Yes | 17.4 | 19.3 | -1.9 | C625AFC977F84515B7952306E9F664EF |  | R22 | Non-TXV |  | 3.387% | 0.96613 | 6.509% | [5 empty] | Non-TXV | 3.387%
Winton | CA | 95388-8719 |  | 2012-07-19 | 2012-07-19 11:06 | 2012-07-19 11:32 | RUUD - UNK | 78 | 4.6 | Yes | Yes | 20.4 | 20.6 | -0.2 | 7163C4C9E1484F7783468CE44AA9F955 |  | R22 | Non-TXV |  | 5.897% | 0.94103 | 11.33% | [5 empty] | Non-TXV | 5.897%
Grass Valley | CA | 95949-6591 |  | 2012-07-19 | 2012-07-19 09:53 | 2012-07-19 09:53 | GE - BWC024B100A | 100 | 0 | Yes | Yes | 20.2 | 19.9 | 0.3 | 87030C10BD0D439F9AC927D58DFCAF9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-5296 |  | 2012-08-14 | 2012-08-14 09:48 | 2012-08-14 10:20 | BDP - 563CN030-A | 102 | -12 | Yes | Yes | 25.8 | 20.2 | 5.6 | 199DBCD5AA5343FA9CF1AE6D4C72F44A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -11.76% | 1.1176 | 3.295% |  |  |  |  | Non-TXV |  |  | -11.76%
Lincoln | CA | 95648-8666 |  | 2012-08-15 | 2012-08-15 11:12 | 2012-08-15 11:30 | YORK - H2RC036S06A | 83 | 18.1 | Yes | Yes | 20.1 | 20.4 | -0.3 | AA37D797B0B54DA692FF080B7A5F73D0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 21.81% | 0.78193 | 41.91% | [5 empty] | Non-TXV | 21.81%
Lincoln | CA | 95648-8666 |  | 2012-08-15 | 2012-08-15 11:45 | 2012-08-15 11:45 | YORK - E1RA018S06D | 78 | 0 | Yes | Yes | 21.8 | 21.4 | 0.4 | 8D6EAD684C284CC5ADCB0E62A89A95F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0743 |  | 2012-08-16 | 2012-08-16 14:58 | 2012-08-16 14:58 | YORK - H1RA024506D | 59 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D8426B72E6F24AC09C46520EB301D607 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2384 |  | 2013-08-06 | 2013-08-06 18:15 | 2013-08-06 18:31 | BDP - 585HJW024040ABAC | 68 | 8.2 | Yes | Yes | 20 | 20.9 | -0.9 | 463CC169D79046D78FA15BB739F86E1E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.06% | 0.87941 | 23.17% | [5 empty] | Non-TXV | 12.06%
Stockton | CA | 95205-4611 |  | 2013-06-06 | 2013-06-06 10:07 | 2013-06-06 10:28 | DAY & NIGHT - 591ANX024000AAAA | 51 | 4.4 | Yes | Yes | 19 | 19.3 | -0.3 | 968AD5CEE1874E5887A1E88A09EACA7D |  | R22 | Non-TXV |  | 8.627% | 0.91373 | 16.58% | [5 empty] | Non-TXV | 8.627%
Stockton | CA | 95205-4611 |  | 2013-06-04 | 2013-06-04 10:55 | 2013-06-04 11:18 | PAYNE - PA10JA024-A | 68 | 6.2 | Yes | Yes | 21 | 19.3 | 1.7 | 5EB24BE560A1450890F79FA5A02E5AB4 |  | R22 | TXV |  | 9.118% | 0.90882 | 17.52% | [5 empty] | TXV | 9.118%
Chico | CA | 95928-7663 |  | 2013-08-02 | 2013-08-02 14:20 | 2013-08-02 14:37 | ICP - 563CN036-C | 101 | 3.9 | Yes | Yes | 21.6 | 20.7 | 1 | 7C0F91DE05E140E2AF53F91B5E4CCE4E |  | R22 | Non-TXV |  | 3.861% | 0.96139 | 7.421% | [5 empty] | Non-TXV | 3.861%
Tracy | CA | 95376-2055 |  | 2013-08-15 | 2013-08-15 11:02 | 2013-08-15 11:20 | BDP - 561CJ048-A | 85 | 5.7 | Yes | Yes | 20.5 | 20.4 | 0.1 | 473C933A9CFD463D83BD8AFAB06C8E12 |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Yuba City | CA | 95991-3925 |  | 2013-05-24 | 2013-05-24 12:37 | 2013-05-24 12:56 | ALLEGIANCE - 2A7A5036A1000AA | 137 | -12.9 | Yes | Yes | 19 | 20.9 | -1.9 | A3FB3F15879A40ED808346B04FEA1CFA |  | R22 | Non-TXV |  | -9.416% | 1.0942 | 2.637% |  |  |  |  | Non-TXV |  |  | -9.416%
Red Bluff | CA | 96080-8960 |  | 2013-05-23 | 2013-05-23 17:31 | 2013-05-23 17:31 | DAY & NIGHT - 693ANX048000ABAA | 194 | 0 | Yes | Yes | 24.5 | 20.7 | 3.8 | 0E19ACB099C34BE0BD8EF59F3FB292B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5562 |  | 2013-08-29 | 2013-08-29 10:33 | 2013-08-29 10:33 | RHEEM - RRPL-B036JK06X | 93 | 0 | Yes | Yes | 20.4 | 19.9 | 0.6 | 568F93C11C8F448BA38411E184C5CB1F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1900 |  | 2013-06-11 | 2013-06-11 14:18 | 2013-06-11 14:35 | HEIL - CA9636VKA3 | 156 | -9.2 | Yes | Yes | 23 | 19.6 | 3.4 | 2385D1AD666D4D20BF7B5721B22ED859 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Auburn | CA | 95603-5812 |  | 2013-06-12 | 2013-06-12 09:59 | 2013-06-12 10:23 | TRANE - 2TWX4042B1000AA | 154 | 5.6 | Yes | Yes | 20 | 19.9 | 0.1 | A6547ACC02FD4D86941F4ED473687053 |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Auburn | CA | 95603-3125 |  | 2013-05-28 | 2013-05-28 11:47 | 2013-05-28 12:16 | - 561CJ030-B | 70 | 5.6 | Yes | Yes | 25 | 19.5 | 5.5 | EBCABAFC68C64CC5A9247C290B493B17 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Fresno | CA | 93722-2725 |  | 2013-06-20 | 2013-06-20 11:29 | 2013-06-20 11:29 | - H2DH042506A | 110 | 0 | Yes | Yes | 17.9 | 20.8 | -2.9 | 49BFDA9E790A48A1A67542A4795FCC7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0532 |  | 2013-06-22 | 2013-06-22 04:26 | 2013-06-22 04:26 | KENMORE - UNK | 108 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | CA656A340FF6410390B4B84684B3FD3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-3542 |  | 2013-05-24 | 2013-05-24 13:00 | 2013-05-24 13:00 | DAY & NIGHT - PGD324060K001C1 | 77 | 0 | Yes | Yes | 23.8 | 19.9 | 3.9 | 1F624EF670D7424EA0EE0C89AF310859 |  | R410A | TXV |  | 0% | 1 | 0%
Sutter | CA | 95982-2309 |  | 2013-09-30 | 2013-09-30 14:11 | 2013-09-30 14:44 | CARRIER - 38TXA036330 | 101 | 3.7 | Yes | Yes | 17 | 17.6 | -0.6 | 7F5FD166712240C5BFEB19BDA2856CD2 |  | R410A | TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | TXV | 3.663%
Willows | CA | 95988-2056 |  | 2013-06-27 | 2013-06-27 19:33 | 2013-06-27 19:55 | GOODMAN - CK-3011A | 70 | 6.6 | Yes | Yes | 25.5 | 22 | 3.5 | E9A29402E836412081DF9A9E51919F8D |  | R22 | Non-TXV |  | 9.429% | 0.90571 | 18.12% | [5 empty] | Non-TXV | 9.429%
Willows | CA | 95988-2521 |  | 2013-09-09 | 2013-09-09 12:47 | 2013-09-09 13:14 | BRYANT - 583BNW036090NB | 105 | 3.2 | Yes | Yes | 20 | 22.8 | -2.8 | AA7FC7A3ABBC4F989B064C2E92D535AB |  | R410A | Non-TXV |  | 3.048% | 0.96952 | 5.857% | [5 empty] | Non-TXV | 3.048%
Colusa | CA | 95932-2932 |  | 2013-09-17 | 2013-09-17 13:07 | 2013-09-17 13:07 | DAY & NIGHT - UNK | 95 | 0 | Yes | Yes | 19 | 17.3 | 1.7 | AC95DFE4136A42FC9899B6916111C37D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Williams | CA | 95987-0000 |  | 2013-09-12 | 2013-09-12 10:08 | 2013-09-12 10:26 | LENNOX - HSXB15-048-230-01 | 125 | 4.6 | Yes | Yes | 17 | 17.1 | -0.1 | B18C11577DC24BFB9A0E558E0D7B296E |  | R410A | TXV |  | 3.68% | 0.9632 | 7.072% | [5 empty] | TXV | 3.68%
Clovis | CA | 93611-6656 |  | 2013-07-02 | 2013-07-02 09:49 | 2013-07-02 10:13 | LENNOX - 12ACB48-5P | 171 | 16.2 | Yes | Yes | 20.3 | 19.5 | 0.8 | 4A9D6FDEB30B42FE922E32D490C48094 |  | R22 | Non-TXV |  | 9.474% | 0.90526 | 18.21% | [5 empty] | Non-TXV | 9.474%
Yuba City | CA | 95993-1664 |  | 2013-06-21 | 2013-06-21 09:00 | 2013-06-21 09:18 | RHEEM - RAJC-042JAD | 99 | 11.4 | Yes | Yes | 18 | 20.4 | -2.4 | 5CAA94B01B3346359BB73B1C2577524A |  | R22 | Non-TXV |  | 11.52% | 0.88485 | 22.13% | [5 empty] | Non-TXV | 11.52%
Selma | CA | 93662-4299 |  | 2013-07-31 | 2013-07-31 16:16 | 2013-07-31 16:52 | GOODMAN - CKL42-1A | 95 | 3.4 | Yes | Yes | 19.5 | 19.6 | -0.1 | 09C6847076BA477591BCCA4D148F498B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.579% | 0.96421 | 6.878% | [5 empty] | Non-TXV | 3.579%
Hamilton City | CA | 95951-0000 |  | 2013-09-23 | 2013-09-23 11:35 | 2013-09-23 12:08 | AMANA - PGB36C0702E | 64 | 8.8 | Yes | Yes | 20.9 | 20.8 | 0.1 | 4C785B21F3A64EE98A1BEA9C946476E2 |  | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Willows | CA | 95988-2269 |  | 2013-06-26 | 2013-06-26 18:23 | 2013-06-26 18:23 | PAYNE - PA13NR030-J | 75 | 0 | Yes | Yes | 21.2 | 16.9 | 4.3 | 27CB677124464899B5F9A0DE9B5DB2CA |  | R22 | TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-4036 |  | 2013-05-28 | 2013-05-28 13:51 | 2013-05-28 13:51 | GOODMAN - GSH130181AC | 127 | 0 | Yes | Yes | 19.9 | 19.5 | 0.4 | ED53F4A8EC0146F88955BC6432A568D2 |  | R22 | TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-6619 |  | 2013-05-28 | 2013-05-28 15:05 | 2013-05-28 15:05 | TRANE - 4TTX4030A1000AA | 79 | 0 | Yes | Yes | 21.3 | 18.9 | 2.4 | 05624E283AD6489DA2B33DC0F32A2AC7 |  | R410A | TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-5820 |  | 2013-06-20 | 2013-06-20 09:48 | 2013-06-20 09:48 | PAYNE - 597AN042-A | 175 | 0 | Yes | Yes | 20.1 | 20.6 | -0.5 | 18885C16D4A24705A892B01F8E40E160 |  | R22 | Non-TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-5820 |  | 2013-06-20 | 2013-06-20 10:27 | 2013-06-20 10:27 | PAYNE - 597AN042-A | 175 | 0 | Yes | Yes | 23.4 | 20.4 | 3 | 6C2E728BB8F64344A78B2C2B6D32CE2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-8137 |  | 2013-06-18 | 2013-06-18 14:05 | 2013-06-18 14:28 | NORDYNE - GT3BA-036KA | 96 | 4 | Yes | Yes | 16 | 18.7 | -2.7 | 9FA7A8A94E5446DE9B271F0BA4F833F9 |  | R22 | TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | TXV | 4.167%
El Dorado Hills | CA | 95762-5533 |  | 2013-07-08 | 2013-07-08 10:16 | 2013-07-08 10:36 | YORK - H2RC048S06A | 120 | 7.3 | Yes | Yes | 17 | 19.9 | -2.9 | 38BF5C11FF4643E8ACBE351C6300B460 |  | R22 | Non-TXV |  | 6.083% | 0.93917 | 11.69% | [5 empty] | Non-TXV | 6.083%
El Dorado Hills | CA | 95762-7311 |  | 2013-06-01 | 2013-06-01 12:10 | 2013-06-01 12:29 | CARRIER - 38TD060310 | 85 | 6 | Yes | Yes | 22 | 20.8 | 1.2 | 874583DB6B004CC4815F6017EC284407 |  | R410A | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
El Dorado Hills | CA | 95762-5036 |  | 2013-06-19 | 2013-06-19 14:38 | 2013-06-19 14:38 | OTHER - UNK | 106 | 0 | Yes | Yes | 19.9 | 20.1 | -0.2 | F04FA4F8F3C24D6687E4815B112248FF |  | R22 | TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-3702 |  | 2013-06-20 | 2013-06-20 14:34 | 2013-06-20 14:34 | LENNOX - HS26-060-2P | 168 | 0 | Yes | Yes | 25.3 | 21.1 | 4.2 | 6E457BC12C5D45B3AE81BB2AF77842B8 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9111 |  | 2013-05-24 | 2013-05-24 13:39 | 2013-05-24 13:39 | CARRIER - 38BRC048370 | 141 | 0 | Yes | Yes | 17.3 | 20 | -2.7 | FA31DD5B832040B3BDAEB195503728D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-9545 |  | 2013-05-23 | 2013-05-23 11:44 | 2013-05-23 12:11 | PAYNE - PA13NR024000AHAA | 72 | -6.8 | Yes | Yes | 25 | 20.7 | 4.3 | 220838283A734E35B560CAAC6B30A7F0 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Lincoln | CA | 95648-9787 |  | 2013-09-25 | 2013-09-25 17:32 | 2013-09-25 17:32 | AMERICAN STANDARD - 2A7A8048B1000AA | 85 | 0 | Yes | Yes | 25.7 | 20.7 | 5 | 13238770C2844A9781E780FA27C6C8DC |  | R22 | TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-9787 |  | 2013-09-25 | 2013-09-25 18:06 | 2013-09-25 18:06 | AMERICAN STANDARD - 2A7A5024A1000AA | 123 | 0 | Yes | Yes | 25.8 | 20.6 | 5.2 | 3AA8CCC5E4064AF09E78289EB9669D3E |  | R22 | TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2458 |  | 2013-05-23 | 2013-05-23 14:38 | 2013-05-23 14:38 | UNITARY PRODUCTS GROUP - H1RA042S06D | 84 | 0 | Yes | Yes | 16.8 | 19.5 | -2.7 | 980B63BA5BD54E38B68E259581543DD6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2929 |  | 2013-05-23 | 2013-05-23 13:12 | 2013-05-23 13:12 | CARRIER - 38CKC036350 | 74 | 0 | Yes | Yes | 20.4 | 19.7 | 0.7 | 10934BAAA9304859B9412A9EE498F8DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-8212 |  | 2013-06-03 | 2013-06-03 09:59 | 2013-06-03 10:16 | YORK - H2RA036S06E | 63 | 5 | Yes | Yes | 22.3 | 19.5 | 2.8 | 91547C981293446188FF8F65F04829CC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.937% | 0.92063 | 15.25% | [5 empty] | Non-TXV | 7.937%
Lincoln | CA | 95648-2076 |  | 2013-05-23 | 2013-05-23 17:01 | 2013-05-23 17:22 | RHEEM - RRKA-A036JK06X | 62 | 5.2 | Yes | Yes | 20 | 20 | 0 | ACFCC6B9FCDC4812A89C5090900CF825 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.387% | 0.91613 | 16.12% | [5 empty] | Non-TXV | 8.387%
Rocklin | CA | 95677-3340 |  | 2013-07-20 | 2013-07-20 10:00 | 2013-07-20 10:23 | CARRIER - 38BRB03031 | 98 | 4.3 | Yes | Yes | 16 | 18.1 | -2.1 | A441D5151BED4558927FF9BA309FCA51 |  | R22 | Non-TXV |  | 4.388% | 0.95612 | 8.432% | [5 empty] | Non-TXV | 4.388%
Rocklin | CA | 95765-5104 |  | 2013-08-29 | 2013-08-29 13:07 | 2013-08-29 15:45 | RHEEM - 14AJM60A01 | 240 | 9.1 | Yes | Yes | 25 | 20.9 | 4.1 | AECEFCDEE737429B978A86B188C61D25 |  | R410A | Non-TXV |  | 3.792% | 0.96208 | 7.287% | [5 empty] | Non-TXV | 3.792%
Lincoln | CA | 95648-2935 |  | 2013-06-03 | 2013-06-03 14:00 | 2013-06-03 14:19 | CARRIER - 38CKC060370 | 133 | 7.2 | Yes | Yes | 20.1 | 19.3 | 0.8 | EEA758DC728140E993427FFE6DB6293B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.414% | 0.94586 | 10.4% | [5 empty] | Non-TXV | 5.414%
Lincoln | CA | 95648-8154 |  | 2013-07-06 | 2013-07-06 13:19 | 2013-07-06 13:42 | YORK - H2RC036S06HG | 83 | 6.5 | Yes | Yes | 17 | 19.8 | -2.8 | A652D962E427475891C23A101D22893E |  | R22 | Non-TXV |  | 7.831% | 0.92169 | 15.05% | [5 empty] | Non-TXV | 7.831%
Lincoln | CA | 95648-2926 |  | 2013-06-18 | 2013-06-18 17:42 | 2013-06-18 18:01 | YORK - H2RC024S06A | 71 | 4.9 | Yes | Yes | 18 | 20.9 | -2.9 | CEE5F74EDA95443E82A648A3928ED6B6 |  | R22 | Non-TXV |  | 6.901% | 0.93099 | 13.26% | [5 empty] | Non-TXV | 6.901%
Rocklin | CA | 95765-5434 |  | 2013-08-10 | 2013-08-10 12:17 | 2013-08-10 12:39 | BRYANT - 563CN060-D | 195 | 9.5 | Yes | Yes | 23 | 19.4 | 3.6 | 5D34872F54A7496A8070158D75651245 |  | R22 | TXV |  | 4.872% | 0.95128 | 9.363% | [5 empty] | TXV | 4.872%
Stockton | CA | 95203-1531 |  | 2013-05-24 | 2013-05-24 12:49 | 2013-05-24 12:49 | RHEEM - RRKA-A024JK06X | 50 | 0 | Yes | Yes | 21.2 | 23.2 | -2 | CA2F0E1D1F9E4558B9AE7494588D6FC4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-1531 |  | 2013-05-24 | 2013-05-24 16:05 | 2013-05-24 16:05 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 15.2 | 18.2 | -3 | 9F6AAC21A9B641DDACB05D56E2EBE4EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-5000 |  | 2013-05-24 | 2013-05-24 16:38 | 2013-05-24 16:58 | LENNOX - 10ACC-060-230-04 | 130 | 9.9 | Yes | Yes | 21.1 | 21.8 | -0.7 | 5AAEA7C59AF74E20B033C2304A291900 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 7.615% | 0.92385 | 14.64% | [5 empty] | TXV | 7.615%
Livingston | CA | 95334-9659 |  | 2013-08-21 | 2013-08-21 16:30 | 2013-08-21 17:03 | OTHER - BRCS048B | 105 | 3.2 | Yes | Yes | 18.9 | 19.9 | -1 | DA04ACEC575846879D5FE2532C595D91 |  | R22 | Non-TXV |  | 3.048% | 0.96952 | 5.857% | [5 empty] | Non-TXV | 3.048%
Fresno | CA | 93705-0344 |  | 2013-06-18 | 2013-06-18 10:24 | 2013-06-18 10:31 | RHEEM - RRNAB030JK06X | 72 | 9.6 | Yes | Yes | 24.5 | 19.3 | 5.2 | AB8E19CF879B4A22B8E584EEB643F7CB |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Auburn | CA | 95602-2600 |  | 2013-05-23 | 2013-05-23 13:48 | 2013-05-23 14:05 | RHEEM - UNK | 40 | 4.7 | Yes | Yes | 23 | 20.1 | 2.9 | C074001818FE4C139316915B20025896 |  | R22 | Non-TXV |  | 11.75% | 0.8825 | 22.58% | [5 empty] | Non-TXV | 11.75%
Stockton | CA | 95212-3477 |  | 2013-07-23 | 2013-07-23 14:20 | 2013-07-23 14:38 | CARRIER - 38CK030340 | 66 | 2.2 | Yes | Yes | 16.4 | 19.1 | -2.7 | 37FBD9CA79614F17A86C7406F090BB91 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Madera | CA | 93637-2964 |  | 2013-09-05 | 2013-09-05 10:04 | 2013-09-05 10:05 | RHEEM - UNK | 68 | 7.4 | Yes | Yes | 19.5 | 17.4 | 2.1 | 1CD048D3C7F94E5FB57717B0396ABAE1 |  | R22 | Non-TXV |  | 10.88% | 0.89118 | 20.91% | [5 empty] | Non-TXV | 10.88%
Stockton | CA | 95206-5211 |  | 2013-06-20 | 2013-06-20 09:53 | 2013-06-20 10:31 | BRYANT - 561CJ048-A | 159 | 11.5 | Yes | Yes | 23.1 | 22 | 1.1 | DF0B3240ED7C4E60B7126CD3895CFD53 |  | R22 | Non-TXV |  | 7.233% | 0.92767 | 13.9% | [5 empty] | Non-TXV | 7.233%
Stockton | CA | 95209-1313 |  | 2013-05-24 | 2013-05-24 12:55 | 2013-05-24 13:26 | PAYNE - 585A042100YAC | 85 | 14.9 | Yes | Yes | 22 | 19.8 | 2.2 | 22D14F432F83475DA8A767DFD645E53C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.53% | 0.82471 | 33.69% | [5 empty] | Non-TXV | 17.53%
Madera | CA | 93637-4225 |  | 2013-06-17 | 2013-06-17 11:21 | 2013-06-17 11:21 | GOODMAN - APG13600901BB | 163 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | F619AA8911214BEA85C67851486B8453 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4815 |  | 2013-06-25 | 2013-06-25 15:57 | 2013-06-25 16:12 | DAY & NIGHT - UNK | 76 | 7.2 | Yes | Yes | 21.7 | 19.3 | 2.4 | 06948CA68A1943F09CAF029EF38AB621 |  | R22 | Non-TXV |  | 9.474% | 0.90526 | 18.21% | [5 empty] | Non-TXV | 9.474%
Fresno | CA | 93722-6010 |  | 2013-06-21 | 2013-06-21 10:15 | 2013-06-21 10:33 | HEIL - CA3036VKB1 | 79 | 8 | Yes | Yes | 18.8 | 17.9 | 0.9 | 05778294A2C345E5838A5E35B523B43B |  | R22 | Non-TXV |  | 10.13% | 0.89873 | 19.46% | [5 empty] | Non-TXV | 10.13%
Fresno | CA | 93720-3218 |  | 2013-06-21 | 2013-06-21 10:31 | 2013-06-21 10:33 | RHEEM - HO-140-48-21C | 105 | 3.5 | Yes | Yes | 23.9 | 19.9 | 4 | 257BE81D12254B9C8E86A8407BFBF1A1 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93710-5816 |  | 2013-06-21 | 2013-06-21 17:14 | 2013-06-22 04:26 | BRYANT - 583ANW048090AAAF | 114 | -8 | Yes | Yes | 17.5 | 18.5 | -1 | E1CDCD1A0F374AEEA030A5750CB79CD2 |  | R22 | Non-TXV |  | -7.018% | 1.0702 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.018%
Fresno | CA | 93703-4030 |  | 2013-05-31 | 2013-05-31 17:00 | 2013-05-31 17:00 | OTHER - UNK | 100 | 0 | Yes | Yes | 20.4 | 19 | 1.4 | 222CC7557E874E74A7AD83FB91674021 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-4119 |  | 2013-08-16 | 2013-08-16 11:01 | 2013-08-16 11:17 | ICP - GPFM48K080E | 100 | 3.5 | Yes | Yes | 21.8 | 19.6 | 2.2 | DAA0105A9D0A4661A7D51A884082D8B6 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Stockton | CA | 95206-4504 |  | 2013-06-14 | 2013-06-14 10:51 | 2013-06-14 11:09 | GOODMAN - CKL36-1H | 85 | 2.8 | Yes | Yes | 25.8 | 21.8 | 4.1 | 617647DE08084B43A700D746BEAEC9E9 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Stockton | CA | 95210-1522 |  | 2013-06-17 | 2013-06-17 11:39 | 2013-06-17 11:57 | YORK - D3NZ024N03606NXA | 58 | 1.8 | Yes | Yes | 21.7 | 21 | 0.8 | DF23AA4BEF3A4760ADB0939AF00E7133 |  | R410A | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Stockton | CA | 95209-2104 |  | 2013-05-24 | 2013-05-24 14:07 | 2013-05-24 14:35 | GOODMAN - GSC130361DE | 119 | 6.9 | Yes | Yes | 24.2 | 21.3 | 2.9 | EB985CE1644D40EF9A9D8771987917AE |  | R22 | TXV |  | 5.798% | 0.94202 | 11.14% | [5 empty] | TXV | 5.798%
Fowler | CA | 93625-9662 |  | 2013-09-19 | 2013-09-19 15:22 | 2013-09-19 16:08 | RHEEM - RAKA-037JAZ | 79 | 5.4 | Yes | Yes | 18 | 17.3 | 0.7 | D301FD4C25F44B58A8F5E3A8C616B04B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.835% | 0.93165 | 13.14% | [5 empty] | Non-TXV | 6.835%
Manteca | CA | 95337-8223 |  | 2013-05-24 | 2013-05-24 12:46 | 2013-05-24 13:16 | BRYANT - 561CJ036-E | 70 | 2.2 | Yes | Yes | 25.5 | 22.4 | 3.1 | 1DE1C3564C6348E8AE231FA7DC0C3AB6 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Stockton | CA | 95206-4726 |  | 2013-06-17 | 2013-06-17 08:35 | 2013-06-17 08:59 | RHEEM - NK | 85 | 4.4 | Yes | Yes | 22.4 | 19.3 | 3.1 | 88C167B94D5E439A8DA1E89C673F88AF |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Stockton | CA | 95210-1412 |  | 2013-06-06 | 2013-06-06 13:43 | 2013-06-06 13:59 | GOODMAN - PGB030050-1A | 56 | 1.8 | Yes | Yes | 17.6 | 19.3 | -1.7 | 8E14166415C04150BE28B3FC1BE8B012 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Corning | CA | 96021-8662 |  | 2013-06-14 | 2013-06-14 11:59 | 2013-06-14 11:59 | GOODMAN - CPLE42-1 | 139 | 0 | Yes | Yes | 23.3 | 19.5 | 3.8 | 2BC2DD9BA722464DB4347A6C18BAE60F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-9681 |  | 2013-05-23 | 2013-05-23 18:32 | 2013-05-23 18:32 | DUCANE - 2AC13B42-1A | 150 | 0 | Yes | Yes | 23 | 18 | 5 | 40CA22C6D28F4F51BC202DE84239CAA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-9681 |  | 2013-05-23 | 2013-05-23 19:10 | 2013-05-23 19:26 | DUCANE - 2AC13B42-1A | 150 | 7.2 | Yes | Yes | 25 | 19.3 | 5.7 | C9D985BFD5164AF382CE9ED61E14A5AE |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Red Bluff | CA | 96080-5213 |  | 2013-05-31 | 2013-05-31 20:59 | 2013-05-31 20:59 | OTHER - SCU10G42A-A | 87 | 0 | Yes | Yes | 25.5 | 22.1 | 3.4 | CF4CD32919234632BC88EE295919CEA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-9009 |  | 2013-05-23 | 2013-05-23 18:06 | 2013-05-23 18:26 | TEMPSTAR - TCA248AKAS | 157 | 4.7 | Yes | Yes | 24.5 | 18.9 | 5.7 | C4CE61D3DE3146998D682E3AD5895E5D |  | R22 | Non-TXV |  | 2.994% | 0.97006 | 5.753% | [5 empty] | Non-TXV | 2.994%
Chico | CA | 95926-4377 |  | 2013-06-05 | 2013-06-05 11:05 | 2013-06-05 11:30 | BDP - 5856JW018040ABAC | 55 | 5.6 | Yes | Yes | 15.2 | 18.1 | -2.9 | 93485750742E4E95BC9A34F1D04884E5 |  | R22 | Non-TXV |  | 10.18% | 0.89818 | 19.57% | [5 empty] | Non-TXV | 10.18%
Dinuba | CA | 93618-3015 |  | 2013-06-24 | 2013-06-24 16:46 | 2013-06-24 17:14 | ICP - PGF024K060E | 54 | 1.7 | Yes | Yes | 22.8 | 20.4 | 2.4 | 0985E748BE154850BF2FFE5C6513E484 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Stockton | CA | 95207-3421 |  | 2013-05-31 | 2013-05-31 12:42 | 2013-05-31 12:42 | LENNOX - GCS20R411-50-2P | 70 | 0 | Yes | Yes | 21 | 21.2 | -0.1 | C28C3E3A4A9F4287B95B2450EA4E2E76 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-6824 |  | 2013-07-15 | 2013-07-15 13:46 | 2013-07-15 14:13 | LENNOX - UNK | 95 | 3.5 | Yes | Yes | 26 | 22 | 4 | C19DA89BC8794E8CBF9E487249BE3A22 |  | R22 | TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | TXV | 3.684%
Yuba City | CA | 95991-1565 |  | 2013-05-24 | 2013-05-24 13:28 | 2013-05-24 13:28 | PAYNE - 5410J024 | 118 | 0 | Yes | Yes | 21 | 19.5 | 1.5 | F802097967DE4C6481B51EB8E8FB95E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-4754 |  | 2013-10-10 | 2013-10-10 13:32 | 2013-10-10 13:57 | PAYNE - 3Y3PNA024060NA | 120 | 12.2 | Yes | Yes | 26.9 | 21.2 | 5.7 | 80378A17302C4F6698738C3DC628B9A6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.17% | 0.89833 | 19.54% | [5 empty] | Non-TXV | 10.17%
Fresno | CA | 93727-7907 |  | 2013-06-17 | 2013-06-17 10:30 | 2013-06-17 10:32 | YORK - D1NP036N05606A | 108 | 3.2 | Yes | Yes | 20.4 | 20.2 | 0.2 | 3598977E82754A5BBF37D5F9D8B382AC |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Manteca | CA | 95336-2987 |  | 2013-07-18 | 2013-07-18 15:02 | 2013-07-18 15:33 | BRYANT - 563CN036-E | 101 | 3.2 | Yes | Yes | 26.7 | 22.3 | 4.4 | 313BBD32B2C14D429536C023F1E8ED4E |  | R22 | Non-TXV |  | 3.168% | 0.96832 | 6.089% | [5 empty] | Non-TXV | 3.168%
Stockton | CA | 95210-3624 |  | 2013-06-06 | 2013-06-06 09:12 | 2013-06-06 09:30 | HEIL - ACS030A2C1 | 71 | -4.2 | Yes | Yes | 18.1 | 17.7 | 0.4 | CA10F64D6A9545BEA8E0F2FC4B9A99F6 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Manteca | CA | 95337-8005 |  | 2013-05-30 | 2013-05-30 13:15 | 2013-05-30 13:38 | PAYNE - 591AN042-D | 96 | 5.6 | Yes | Yes | 22.5 | 20.9 | 1.6 | E7F3222F383F49FBAEB12B697DFCDBCD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Clovis | CA | 93611-6552 |  | 2013-06-17 | 2013-06-17 09:47 | 2013-06-17 10:08 | CARRIER - 38CK060370 | 131 | 19.3 | Yes | Yes | 20.3 | 20.4 | -0.1 | 723E2E7B8E5E4290A5C092F38510A7EF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.73% | 0.85267 | 28.31% | [5 empty] | Non-TXV | 14.73%
Gerber | CA | 96035-0000 |  | 2013-08-19 | 2013-08-19 11:23 | 2013-08-19 13:54 | CARRIER - NA | 75 | 5.7 | Yes | Yes | 15.6 | 18.3 | -2.7 | 62300B8CA2824A30B19A6F5415E36AEE |  | R22 | Non-TXV |  | 7.6% | 0.924 | 14.61% | [5 empty] | Non-TXV | 7.6%
Manteca | CA | 95336-7044 |  | 2013-05-24 | 2013-05-24 16:22 | 2013-05-24 16:50 | BRYANT - 563CN048-D | 165 | 19.2 | Yes | Yes | 19.5 | 20.8 | -1.3 | 6336E2C6F8DA42FAAC9AC8D000FE0BF2 |  | R22 | Non-TXV |  | 11.64% | 0.88364 | 22.36% | [5 empty] | Non-TXV | 11.64%
Auburn | CA | 95603-3733 |  | 2013-05-23 | 2013-05-23 15:30 | 2013-05-23 15:57 | OTHER - 7B0023B100A1 | 54 | 1.6 | Yes | Yes | 21 | 20.1 | 0.9 | B443A859F63B452188D2B5D4D4AFF3C8 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95210-1246 |  | 2013-06-28 | 2013-06-28 11:14 | 2013-06-28 11:35 | RUUD - URMA-A024JK06X | 70 | -4.9 | Yes | Yes | 18.6 | 16.5 | 2.1 | 07652C73176E4D0A9C90B252E768691B |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Yuba City | CA | 95993-5005 |  | 2013-09-06 | 2013-09-06 16:12 | 2013-09-06 16:36 | LENNOX - 10ACC-060-230-02 | 130 | -4.7 | Yes | Yes | 20.5 | 22 | -1.5 | DC9787D4C1D04276A6A747A22A75CD3D |  | R22 | TXV |  | -3.615% | 1.0362 | 1.012% |  |  |  |  | TXV |  |  | -3.615%
Stockton | CA | 95204-1340 |  | 2013-06-01 | 2013-06-01 11:48 | 2013-06-01 12:04 | GOODMAN - PG030075-1AB | 66 | 3.5 | Yes | Yes | 19.3 | 17.9 | 1.4 | 62A59929B46E47A79DD93DF5221F10B0 |  | R22 | Non-TXV |  | 5.303% | 0.94697 | 10.19% | [5 empty] | Non-TXV | 5.303%
Fresno | CA | 93722-4900 |  | 2013-07-18 | 2013-07-18 10:08 | 2013-07-18 10:09 | OTHER - DRCS0481RD | 122 | 16.5 | Yes | Yes | 22.2 | 21.5 | 0.7 | 85032C1B30C841018C5C39B99600508F |  | R22 | Non-TXV |  | 13.52% | 0.86475 | 25.99% | [5 empty] | Non-TXV | 13.52%
Clovis | CA | 93611-2040 |  | 2013-06-12 | 2013-06-12 16:38 | 2013-06-12 16:38 | RHEEM - RRMA-A036JK06X | 99 | 0 | Yes | Yes | 26.2 | 20.6 | 5.6 | DC9F034A3ECA44EAA4E2B3E40F4547C6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-2219 |  | 2013-05-24 | 2013-05-24 14:51 | 2013-05-24 14:51 | BDP - 585A018030YAC | 52 | 0 | Yes | Yes | 17.1 | 19.3 | -2.2 | 4533683AD41D473CA06B2CF6DC59515A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-7435 |  | 2013-06-25 | 2013-06-25 13:10 | 2013-06-25 13:12 | OTHER - 59BN030-A | 108 | 5.7 | Yes | Yes | 14.4 | 17.4 | -3 | 9516CC46F6FC4911AB3E940569A2A85D |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Dinuba | CA | 93618-9107 |  | 2013-07-26 | 2013-07-26 23:00 | 2013-07-26 23:02 | PAYNE - N/A | 152 | 5.6 | Yes | Yes | 23 | 20.7 | 2.3 | C2DFF6443EBF4070B0DBB1F167BBD337 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Chico | CA | 95926-1554 |  | 2013-08-01 | 2013-08-01 16:05 | 2013-08-01 16:27 | AIRE-FLO - AFAIR10B48-A | 100 | 23.3 | Yes | Yes | 26.7 | 20.7 | 6 | 333F0A365BA143CE94DFD26059D0DBAA |  | R22 | Non-TXV |  | 23.3% | 0.767 | 44.78% | [5 empty] | Non-TXV | 23.3%
Paradise | CA | 95969-4810 |  | 2013-06-12 | 2013-06-12 10:08 | 2013-06-12 10:37 | YORK - D1NA024N05606C | 54 | 7.7 | Yes | Yes | 16.4 | 18.8 | -2.4 | 8F2E6C69F6594FB3AB2703659B08F6BE |  | R22 | Non-TXV |  | 14.26% | 0.85741 | 27.4% | [5 empty] | Non-TXV | 14.26%
Stockton | CA | 95209-3913 |  | 2013-05-23 | 2013-05-23 14:47 | 2013-05-23 14:47 | GOODMAN - CK42-1C | 92 | 0 | Yes | Yes | 19.6 | 22 | -2.4 | 8B2BD38FD37244A7A6ECE72A68EB1811 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-2601 |  | 2013-05-28 | 2013-05-28 10:56 | 2013-05-28 11:19 | PAYNE - PY3PNA024040NB | 89 | 4.3 | Yes | Yes | 18.2 | 18.2 | 0 | 0CEA372E591A4F97B312BA79711223B4 |  | R22 | Non-TXV |  | 4.831% | 0.95169 | 9.285% | [5 empty] | Non-TXV | 4.831%
Stockton | CA | 95209-2419 |  | 2013-05-30 | 2013-05-30 10:21 | 2013-05-30 10:21 | AMERICAN STANDARD - 2A7A4042B1000A | 137 | 0 | Yes | Yes | 23.2 | 18.3 | 4.9 | D22D7401F0CC4EADB8AFEEEA60F69DC0 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4900 |  | 2013-07-16 | 2013-07-16 16:34 | 2013-07-16 16:34 | INTERTHERM - CN48I77JY11 | 74 | 0 | Yes | Yes | 21.5 | 24.2 | -2.7 | 867235DB22EF49E2B2010B1A645C85C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3574 |  | 2013-09-03 | 2013-09-03 10:25 | 2013-09-03 10:27 | DUCANE - AC10B24 | 60 | 3.6 | Yes | Yes | 24.1 | 18.1 | 6 | 61AC6F7B60ED4B4DA102EC35207C72D0 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Stockton | CA | 95207-3623 |  | 2013-06-04 | 2013-06-04 10:29 | 2013-06-04 10:46 | RHEEM - UNK | 80 | 9 | Yes | Yes | 18.4 | 18.3 | 0.1 | F8F5C696F45A4C2EAB2C2A437EAC42CC |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Merced | CA | 95341-7017 |  | 2013-06-11 | 2013-06-11 13:55 | 2013-06-11 14:16 | GOODMAN - CKL301A | 78 | 6.8 | Yes | Yes | 16.6 | 19.2 | -2.5 | 2D1428CA17E74564ADDE36EC802E2A13 |  | R22 | Non-TXV |  | 8.718% | 0.91282 | 16.75% | [5 empty] | Non-TXV | 8.718%
Auburn | CA | 95603-9370 |  | 2013-08-14 | 2013-08-14 14:43 | 2013-08-14 15:12 | PAYNE - 565BJ030 | 72 | 3.4 | Yes | Yes | 19 | 21.5 | -2.5 | FC6D6B1495F4434BA204B3FC0A97B5AB |  | R22 | TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | TXV | 4.722%
Fresno | CA | 93721-2409 |  | 2013-06-20 | 2013-06-20 09:19 | 2013-06-20 09:35 | GOODMAN - UNK | 78 | 4.4 | Yes | Yes | 16.4 | 18.3 | -1.9 | 7C12A15707BC48A980FC7C772197A288 |  | R22 | Non-TXV |  | 5.641% | 0.94359 | 10.84% | [5 empty] | Non-TXV | 5.641%
Stockton | CA | 95206-4726 |  | 2013-09-19 | 2013-09-19 14:25 | 2013-09-19 14:44 | RHEEM - RAHE-042JAS | 101 | -9.5 | Yes | Yes | 18.6 | 21.5 | -2.9 | 7DAFD888DC5E444E9133B88F8031ECD2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.406% | 1.0941 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.406%
Clovis | CA | 93611-4508 |  | 2013-06-27 | 2013-06-27 10:15 | 2013-06-27 10:33 | RHEEM - RRPL-B030JK06X | 76 | 3 | Yes | Yes | 17.8 | 19 | -1.2 | 26D822B5846341288184C2ACE8FFD93F |  | R410A | TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | TXV | 3.947%
Chico | CA | 95973-0933 |  | 2013-06-11 | 2013-06-11 09:40 | 2013-06-11 09:56 | TRANE - TTB1B042C100A1 | 103 | 3.2 | Yes | Yes | 23 | 20 | 3.1 | B36995A1FB9D4A6C9D3F2C711CB2F179 |  | R22 | Non-TXV |  | 3.107% | 0.96893 | 5.971% | [5 empty] | Non-TXV | 3.107%
Fresno | CA | 93727-3546 |  | 2013-08-12 | 2013-08-12 13:52 | 2013-08-12 14:29 | BDP - 585HJW036-60 | 102 | 3.5 | Yes | Yes | 22.5 | 21.2 | 1.4 | C293A871CFD5421A8C790D73F1ECECE6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.431% | 0.96569 | 6.594% | [5 empty] | Non-TXV | 3.431%
Auburn | CA | 95602-2603 |  | 2013-05-23 | 2013-05-23 12:47 | 2013-05-23 13:06 | TRANE - TTB018C100AD | 47 | 6.5 | Yes | Yes | 22 | 20.7 | 1.3 | DFDD5ABF00B34E9CAD07D28AE883B78F |  | R22 | Non-TXV |  | 13.83% | 0.8617 | 26.58% | [5 empty] | Non-TXV | 13.83%
Clovis | CA | 93612-2647 |  | 2013-06-18 | 2013-06-18 09:07 | 2013-06-18 09:26 | BDP - 585EJW036075ABAF | 82 | 2.5 | Yes | Yes | 23.3 | 20.7 | 2.6 | D8A49737A30542808F92EF26613AEB6D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Marysville | CA | 95901-8202 |  | 2013-06-03 | 2013-06-03 10:40 | 2013-06-03 11:01 | OTHER - CJ36-LGB | 85 | -8 | Yes | Yes | 23 | 21.7 | 1.3 | 06E176D100C544A29CAF271586883180 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93727-5618 |  | 2013-08-30 | 2013-08-30 11:59 | 2013-08-30 12:01 | CARRIER - 48GS-060090301AD | 129 | 5.8 | Yes | Yes | 27 | 21 | 6 | 7A85D9AC7F7B413494D91314A5575ECE |  | R22 | Non-TXV |  | 4.496% | 0.95504 | 8.641% | [5 empty] | Non-TXV | 4.496%
Los Banos | CA | 93635-2931 |  | 2013-05-28 | 2013-05-28 11:52 | 2013-05-28 11:56 | CARRIER - 580ANC30040 | 85 | 3.9 | Yes | Yes | 18.2 | 19.2 | -1 | ED0061A82E61466CAD07DB6AE0EC676C |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Fresno | CA | 93705-0214 |  | 2013-06-18 | 2013-06-18 09:53 | 2013-06-18 09:56 | OTHER - 585A030080YACR | 50 | 5.8 | Yes | Yes | 22.3 | 19.1 | 3.2 | 7DD65D87C17F41838798BA2C25EC04B4 |  | R22 | Non-TXV |  | 11.6% | 0.884 | 22.29% | [5 empty] | Non-TXV | 11.6%
Fresno | CA | 93727-3038 |  | 2013-06-11 | 2013-06-11 09:52 | 2013-06-11 09:52 | OTHER - N/A | 90 | 0 | Yes | Yes | 21.4 | 18.8 | 2.6 | 0DF35F55E2EA44FAA75E3D910A41D83B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6121 |  | 2013-06-21 | 2013-06-21 13:08 | 2013-06-21 13:33 | GOODMAN - CKJ48-1AB | 118 | 13 | Yes | Yes | 20.5 | 19.8 | 0.7 | 4B153F472B3345FFBD79C475525BEA98 |  | R22 | Non-TXV |  | 11.02% | 0.88983 | 21.17% | [5 empty] | Non-TXV | 11.02%
Palermo | CA | 95968-9635 |  | 2013-09-10 | 2013-09-10 11:47 | 2013-09-10 12:04 | PAYNE - PA10JA036-A | 85 | -6 | Yes | Yes | 18 | 20.9 | -2.9 | 29F2E05730A340B38E493FAEEC21EAAB |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93723-7638 |  | 2013-06-24 | 2013-06-24 10:14 | 2013-06-24 10:24 | LENNOX - 13ACC060230 | 168 | 10.7 | Yes | Yes | 22.4 | 19.8 | 2.6 | A9541C6F40D746A79ABDE62294D9B298 |  | R22 | Non-TXV |  | 6.369% | 0.93631 | 12.24% | [5 empty] | Non-TXV | 6.369%
Fresno | CA | 93711-2030 |  | 2013-08-27 | 2013-08-27 12:39 | 2013-08-27 12:41 | ARCOAIRE - PGME60G1157 | 212 | 6.7 | Yes | Yes | 22.3 | 19.5 | 2.8 | 9674C8CFD22E4526943D26C34C106350 |  | R22 | Non-TXV |  | 3.16% | 0.9684 | 6.074% | [5 empty] | Non-TXV | 3.16%
Clovis | CA | 93611-9202 |  | 2013-07-02 | 2013-07-02 11:58 | 2013-07-02 12:00 | LENNOX - HS14-S11U-7P | 177 | 22.1 | Yes | Yes | 18.3 | 20.6 | -2.3 | 0206F8704AAA4CE898917F3B861CC227 |  | R22 | Non-TXV |  | 12.49% | 0.87514 | 24% | [5 empty] | Non-TXV | 12.49%
Fresno | CA | 93722-5628 |  | 2013-07-17 | 2013-07-17 09:36 | 2013-07-17 09:38 | CARRIER - UNK | 76 | 7.8 | Yes | Yes | 21.4 | 17.6 | 3.8 | 5FD884B10051469A86E5E7E487E1F2A1 |  | R22 | Non-TXV |  | 10.26% | 0.89737 | 19.72% | [5 empty] | Non-TXV | 10.26%
Grass Valley | CA | 95949-9564 |  | 2013-06-13 | 2013-06-13 14:47 | 2013-06-13 15:06 | CARRIER - 38CKC024230 | 69 | 8.5 | Yes | Yes | 17 | 19.1 | -2.1 | 32C854E791674876AA02EC96276C7053 |  | R22 | Non-TXV |  | 12.32% | 0.87681 | 23.67% | [5 empty] | Non-TXV | 12.32%
Tracy | CA | 95376-3325 |  | 2013-05-28 | 2013-05-28 15:30 | 2013-05-28 15:51 | CARRIER - 589ANW030060ACAD | 69 | -4.1 | Yes | Yes | 20.1 | 19.3 | 0.8 | 5CA3577C87D3447CAD91B3F5DF9089A6 |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Granite Bay | CA | 95746-9629 |  | 2013-06-22 | 2013-06-22 11:06 | 2013-06-22 11:06 | PAYNE - 565BB060 | 120 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | D3591640DE574AAEA2C1630664F96F9E | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Chico | CA | 95928-5857 |  | 2013-07-08 | 2013-07-08 19:35 | 2013-07-08 20:00 | LENNOX - H34-311-6P | 78 | 13.3 | Yes | Yes | 14.9 | 17.7 | -2.8 | 2A91C4F482004798BB592DE9E790D775 |  | R22 | Non-TXV |  | 17.05% | 0.82949 | 32.77% | [5 empty] | Non-TXV | 17.05%
Orland | CA | 95963-2031 |  | 2013-06-17 | 2013-06-17 10:42 | 2013-06-17 11:40 | OTHER - NACM005225 | 112 | 3.6 | Yes | Yes | 20.3 | 20.4 | -0.1 | 1B172484967E4A97B6813C9D03B113C0 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Clovis | CA | 93612-4902 |  | 2013-06-28 | 2013-06-28 16:31 | 2013-06-28 16:31 | TAPPAN - RTA 36-75-42-T | 62 | 0 | Yes | Yes | 21.3 | 17.4 | 3.9 | 887C85CB546A47D0A4BA9E3B8E6361F2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2259 |  | 2013-08-06 | 2013-08-06 16:04 | 2013-08-06 16:21 | YORK - DAYH-F036N070C | 108 | 7.7 | Yes | Yes | 20.9 | 20.6 | 0.4 | 097213DFE8A94C0FB2354C096DB42BC7 |  | R22 | Non-TXV |  | 7.13% | 0.9287 | 13.7% | [5 empty] | Non-TXV | 7.13%
Fresno | CA | 93710-5631 |  | 2013-06-04 | 2013-06-04 10:46 | 2013-06-04 11:02 | DAY & NIGHT - 589ANW036080ACBF | 86 | 2.9 | Yes | Yes | 20.9 | 20.4 | 0.5 | 2927CE2DE2074279BB40CF2A5F82F82C |  | R22 | Non-TXV |  | 3.372% | 0.96628 | 6.48% | [5 empty] | Non-TXV | 3.372%
Manteca | CA | 95336-3336 |  | 2013-08-26 | 2013-08-26 14:56 | 2013-08-26 15:16 | ICP - NAC024GKC3 | 71 | 2.1 | Yes | Yes | 19.4 | 20.6 | -1.2 | 63409C300D664B4BA92C1D57DE36083C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Manteca | CA | 95336-5954 |  | 2013-05-29 | 2013-05-29 10:48 | 2013-05-29 11:07 | YORK - H2RA030S06D | 62 | 10.6 | Yes | Yes | 21.3 | 20.4 | 0.9 | F3505D23460E4197A6F51E25762EB10E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.1% | 0.82903 | 32.86% | [5 empty] | Non-TXV | 17.1%
Riverdale | CA | 93656-9212 |  | 2013-09-05 | 2013-09-05 09:42 | 2013-09-05 10:12 | CARRIER - N/A | 90 | 17.8 | Yes | Yes | 17.6 | 20.4 | -2.8 | A47E9B9D3F544230BBE702317FE51533 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.78% | 0.80222 | 38.01% | [5 empty] | Non-TXV | 19.78%
Fresno | CA | 93706-4102 |  | 2013-07-16 | 2013-07-16 14:23 | 2013-07-16 14:25 | PAYNE - 585HJW030040 | 68 | 2.1 | Yes | Yes | 24.6 | 19.5 | 5.1 | F7F6564FAF1A4A2B9BCD1B3F5767D758 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Clovis | CA | 93611-2082 |  | 2013-08-16 | 2013-08-16 09:06 | 2013-08-16 09:47 | LENNOX - GCS29X-030-75-2PA | 51 | 3.6 | Yes | Yes | 19 | 20.7 | -1.7 | 128D105EA96646CFB6941EF850D7D30E |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Fresno | CA | 93722-6193 |  | 2013-06-21 | 2013-06-21 14:22 | 2013-06-21 14:27 | OTHER - 585HJW024040 | 78 | 8 | Yes | Yes | 24.2 | 20.9 | 3.3 | 6A69BB0113884F37A8858D0F44EADAD7 |  | R22 | Non-TXV |  | 10.26% | 0.89744 | 19.71% | [5 empty] | Non-TXV | 10.26%
Fresno | CA | 93722-6193 |  | 2013-06-21 | 2013-06-21 14:29 | 2013-06-21 14:37 | OTHER - 585HJW024040 | 78 | 9.7 | Yes | Yes | 22.2 | 19.8 | 2.4 | 2A8ECAE19F6C49A8A3E1A1E60725EC23 |  | R22 | Non-TXV |  | 12.44% | 0.87564 | 23.9% | [5 empty] | Non-TXV | 12.44%
Fresno | CA | 93705-3538 |  | 2013-06-19 | 2013-06-19 16:19 | 2013-06-19 16:26 | ARCOAIRE - AG024GB3 | 73 | 5.9 | Yes | Yes | 24.3 | 23.6 | 0.7 | F7D4AB77BB614A52996AD19CA22019F9 |  | R22 | Non-TXV |  | 8.082% | 0.91918 | 15.53% | [5 empty] | Non-TXV | 8.082%
Fresno | CA | 93710-3804 |  | 2013-06-21 | 2013-06-21 14:57 | 2013-06-22 04:29 | YORK - AC042X1322A | 142 | 5 | Yes | Yes | 15.9 | 18.3 | -2.4 | A24820CD0321438A8721734A567F2DAF |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Fresno | CA | 93727-6477 |  | 2013-07-19 | 2013-07-19 10:16 | 2013-07-19 10:16 | LENNOX - 12ACB36-5P | 103 | 0 | Yes | Yes | 17.3 | 19.8 | -2.5 | D13E4C3605D3454C83E72678E1F5E457 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6040 |  | 2013-06-20 | 2013-06-20 15:52 | 2013-06-20 16:09 | CARRIER - AC042X1021A | 84 | 7.1 | Yes | Yes | 21.9 | 17.4 | 4.5 | B8CFE90F0A3A4D7297D2F83F20BE20C2 |  | R22 | Non-TXV |  | 8.452% | 0.91548 | 16.24% | [5 empty] | Non-TXV | 8.452%
Fowler | CA | 93625-9637 |  | 2013-09-19 | 2013-09-19 17:17 | 2013-09-19 17:23 | GOODMAN - PGB030100-1 | 61 | 3.8 | Yes | Yes | 19.2 | 19.8 | -0.6 | D080C14627AC4D44BA054207F0409C01 |  | R22 | Non-TXV |  | 6.23% | 0.9377 | 11.97% | [5 empty] | Non-TXV | 6.23%
Fresno | CA | 93705-2668 |  | 2013-07-19 | 2013-07-19 08:33 | 2013-07-19 09:24 | RHEEM - RRM-A024JK6X | 70 | 2.4 | Yes | Yes | 24.7 | 20.4 | 4.3 | DCD1D9A708EF4331AAE8B41577F2DB93 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Fresno | CA | 93702-1353 |  | 2013-06-24 | 2013-06-24 15:16 | 2013-06-24 15:18 | LENNOX - 12GCS042756PD | 133 | 13.8 | Yes | Yes | 23.2 | 20.4 | 2.8 | ED9C2AC009644B1DA5751A579E4D8647 |  | R22 | Non-TXV |  | 10.38% | 0.89624 | 19.94% | [5 empty] | Non-TXV | 10.38%
Newman | CA | 95360-1866 |  | 2013-06-04 | 2013-06-04 08:40 | 2013-06-04 09:04 | BDP - 561AJ030-A | 66 | 2.9 | Yes | Yes | 18 | 19.4 | -1.4 | A86C2ADFEF064EFAA69E17BAE8F8E3EF |  | R22 | Non-TXV |  | 4.394% | 0.95606 | 8.444% | [5 empty] | Non-TXV | 4.394%
Newman | CA | 95360-1506 |  | 2013-06-04 | 2013-06-04 09:40 | 2013-06-04 10:04 | UNITARY PRODUCTS GROUP - H2RD060S06B | 162 | 14.3 | Yes | Yes | 26.3 | 20.7 | 5.6 | 6FBA039AA8944F78A9E356E690C49BC6 |  | R22 | Non-TXV |  | 8.827% | 0.91173 | 16.96% | [5 empty] | Non-TXV | 8.827%
Stockton | CA | 95210-1762 |  | 2013-06-10 | 2013-06-10 11:25 | 2013-06-10 11:44 | DAY & NIGHT - 585B024050YACR | 51 | -3 | Yes | Yes | 17.5 | 17.6 | -0.1 | 5C16DE0D9401480D8BEB1C67DB6C85AA |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95205-4652 |  | 2013-08-15 | 2013-08-15 12:11 | 2013-08-15 12:30 | YORK - D1NA036N05606C | 67 | 6.3 | Yes | Yes | 26.3 | 21.2 | 5.1 | 80025AEEC5C24BD7BA43B03F8BF615EE |  | R22 | Non-TXV |  | 9.403% | 0.90597 | 18.07% | [5 empty] | Non-TXV | 9.403%
Ripon | CA | 95366-3204 |  | 2013-10-09 | 2013-10-09 10:52 | 2013-10-09 11:22 | DAY & NIGHT - 585HJW024040ABAF | 68 | 2.1 | Yes | Yes | 21.7 | 18.7 | 3 | 44F700033E034CA693E9A7EE5B916367 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Stockton | CA | 95212-3481 |  | 2013-06-18 | 2013-06-18 08:47 | 2013-06-18 09:19 | UNITARY PRODUCTS GROUP - AC036X1222A | 84 | 15.5 | Yes | Yes | 17.3 | 19.8 | -2.5 | 84932665A8564388BE87A3A1C1610830 |  | R22 | Non-TXV |  | 18.45% | 0.81548 | 35.46% | [5 empty] | Non-TXV | 18.45%
Stockton | CA | 95209-2219 |  | 2013-05-24 | 2013-05-24 14:46 | 2013-05-24 15:38 | ARMSTRONG - 2SCU13LB136P | 111 | 24.2 | Yes | Yes | 21.5 | 20.4 | 1.1 | D61D2E1974BF4482847432DC58F91BF4 | Add refrigerant: 19.7 oz | R22 | Non-TXV |  | 21.8% | 0.78198 | 41.9% | [5 empty] | Non-TXV | 21.8%
Tracy | CA | 95376-1936 |  | 2013-05-24 | 2013-05-24 13:54 | 2013-05-24 14:34 | CARRIER - CA9642UKA1 | 156 | 4.8 | Yes | Yes | 28.7 | 22.8 | 5.9 | 049E267D556C4D7281305F0449A0BEFA |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95207-3602 |  | 2013-05-31 | 2013-05-31 13:20 | 2013-05-31 13:20 | YORK - D3NP024N05606A | 100 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | C4B0AD6E55114B8A98CFB426B1CA67EF |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-5108 |  | 2013-06-19 | 2013-06-19 15:24 | 2013-06-19 15:46 | RUUD - UAFD-030JAS | 69 | 2.3 | Yes | Yes | 21.9 | 21.5 | 0.4 | C12FD9C5B5784DD39304BF393DFBB9C7 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95210-1448 |  | 2013-06-07 | 2013-06-07 12:34 | 2013-06-07 12:51 | LENNOX - GCS26X-036-75-2PA | 110 | 3.6 | Yes | Yes | 17.3 | 17.4 | -0.1 | 6382C14B9DF64EA3BD0C08D65BC92425 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Stockton | CA | 95210-1311 |  | 2013-06-26 | 2013-06-26 08:23 | 2013-06-26 08:43 | RUUD - UAMA-036JAZ | 96 | -5.6 | Yes | Yes | 18.3 | 18.2 | 0.1 | 37B77FC1EEE74256816491B2AA836213 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95207-4212 |  | 2013-06-13 | 2013-06-13 13:26 | 2013-06-13 13:26 | PAYNE - PY1NB024060AAAA | 53 | 0 | Yes | Yes | 21 | 21 | 0 | 7178C04727C74B23A5320E9A405FE0BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7038 |  | 2013-06-11 | 2013-06-11 10:42 | 2013-06-11 10:59 | LENNOX - 13ACD042230 | 111 | 7.3 | Yes | Yes | 21.1 | 18.7 | 2.4 | 247AF59D2C2A4EB5A9EF62DFED828364 |  | R22 | Non-TXV |  | 6.577% | 0.93423 | 12.64% | [5 empty] | Non-TXV | 6.577%
Stockton | CA | 95210-1502 |  | 2013-06-18 | 2013-06-18 09:35 | 2013-06-18 09:53 | PAYNE - PY1PNB030060AAAA | 58 | -4.1 | Yes | Yes | 24.6 | 19.3 | 5.3 | 44CB0A328DF24F11B45CC63BF7987C8D |  | R22 | Non-TXV |  | -7.069% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.069%
Stockton | CA | 95210-1502 |  | 2013-06-17 | 2013-06-17 12:08 | 2013-06-17 12:25 | PAYNE - 24/60YAC-108C | 53 | -3.1 | Yes | Yes | 27 | 21 | 6 | EC22E5ED9DDE4D45B032026650DF21FC |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Lathrop | CA | 95330-9574 |  | 2013-06-07 | 2013-06-07 09:54 | 2013-06-07 10:19 | GOODMAN - VSX130361AA | 89 | 2.7 | Yes | Yes | 23.5 | 19.3 | 4.2 | E5099A6888CE452A9978EDAADF48B11B |  | R410A | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Lathrop | CA | 95330-8654 |  | 2013-07-30 | 2013-07-30 10:49 | 2013-07-30 11:08 | CARRIER - 24ABA369A300 | 136 | 4.2 | Yes | Yes | 21.4 | 19.1 | 2.3 | C742040CB12B47E282C79B8116326616 |  | R410A | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Stockton | CA | 95204-2812 |  | 2013-05-31 | 2013-05-31 13:43 | 2013-05-31 13:43 | LENNOX - GCS10-411-50-1P | 82 | 0 | Yes | Yes | 22.5 | 20.2 | 2.3 | C98E2DF10112424C9336A94CB2870436 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1502 |  | 2013-06-18 | 2013-06-18 11:52 | 2013-06-18 12:08 | PAYNE - PY3PNA024060NB | 95 | 3.3 | Yes | Yes | 21.3 | 19.3 | 2 | 4434AAA5F3654EBEAE0ECFBEC5EE78E5 |  | R22 | Non-TXV |  | 3.474% | 0.96526 | 6.676% | [5 empty] | Non-TXV | 3.474%
Selma | CA | 93662-4147 |  | 2013-07-31 | 2013-07-31 14:16 | 2013-07-31 14:50 | GOODMAN - CK60-1C | 121 | 5.8 | Yes | Yes | 18 | 19.6 | -1.6 | AE2EA241670D437B8067E89D7E008CC6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.793% | 0.95207 | 9.212% | [5 empty] | Non-TXV | 4.793%
Tracy | CA | 95377-0214 |  | 2013-05-30 | 2013-05-30 09:35 | 2013-05-30 09:54 | PAYNE - 561CJ036-D | 102 | 4.1 | Yes | Yes | 22.4 | 19.9 | 2.5 | 9179F5FB7FAA4D94A2C4D42AEA726A18 |  | R22 | Non-TXV |  | 4.02% | 0.9598 | 7.725% | [5 empty] | Non-TXV | 4.02%
Stockton | CA | 95206-6073 |  | 2013-06-19 | 2013-06-19 13:04 | 2013-06-19 13:22 | GOODMAN - CKJ48-1AB | 118 | 6.9 | Yes | Yes | 25.1 | 21 | 4.1 | D56F0882ECBC4C89B289ABB7018793F1 |  | R22 | TXV |  | 5.847% | 0.94153 | 11.24% | [5 empty] | TXV | 5.847%
Stockton | CA | 95206-2240 |  | 2013-06-21 | 2013-06-21 09:21 | 2013-06-21 09:46 | CARRIER - 38CE003300 | 85 | 9.8 | Yes | Yes | 18.9 | 19.6 | -0.7 | B93698B9E3BD4FEBB4626F22E5AF3F0E |  | R22 | Non-TXV |  | 11.53% | 0.88471 | 22.16% | [5 empty] | Non-TXV | 11.53%
Stockton | CA | 95205-3450 |  | 2013-06-12 | 2013-06-12 10:57 | 2013-06-12 10:57 | HEIL - UNK | 96 | 0 | Yes | Yes | 19.5 | 19.3 | 0.2 | 057CDD093D45400A87CC010C30CB5B77 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-7838 |  | 2013-06-05 | 2013-06-05 13:51 | 2013-06-05 14:10 | GOODMAN - CKJ30-1B | 92 | 5.5 | Yes | Yes | 19.9 | 18.7 | 1.2 | EE3FC6D5B8A641D09EEC8E81A2C1DAF6 |  | R22 | Non-TXV |  | 5.978% | 0.94022 | 11.49% | [5 empty] | Non-TXV | 5.978%
Tracy | CA | 95377-1167 |  | 2013-06-04 | 2013-06-04 11:11 | 2013-06-04 11:50 | YORK - H2RC036S06A | 93 | 10.8 | Yes | Yes | 22.6 | 22.6 | 0 | 45EA22C528D545199AF6272709CA1E26 |  | R22 | Non-TXV |  | 11.61% | 0.88387 | 22.32% | [5 empty] | Non-TXV | 11.61%
Stockton | CA | 95206-1223 |  | 2013-07-13 | 2013-07-13 12:04 | 2013-07-13 12:34 | GOODMAN - GPG13240451BB | 77 | 9.4 | Yes | Yes | 24.8 | 19.2 | 5.6 | C3245DFB62A74AE69CC175D78CFBF955 |  | R22 | Non-TXV |  | 12.21% | 0.87792 | 23.46% | [5 empty] | Non-TXV | 12.21%
Stockton | CA | 95206-3069 |  | 2013-06-12 | 2013-06-12 14:19 | 2013-06-12 14:39 | AMANA - UNK | 85 | 7.4 | Yes | Yes | 21.4 | 20.6 | 0.8 | 45CCAFB8907C4DFF91262E713381D488 |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Stockton | CA | 95205-4120 |  | 2013-06-04 | 2013-06-04 09:27 | 2013-06-04 09:27 | DAY & NIGHT - N2A330AKA200 | 83 | 0 | Yes | Yes | 21.6 | 20.3 | 1.3 | 1D13EBF655C84CDC968449215CEA6842 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-3318 |  | 2013-06-03 | 2013-06-03 12:15 | 2013-06-03 12:44 | BDP - 598AN036-B | 195 | 8 | Yes | Yes | 23.8 | 20.4 | 3.4 | D5316ED99E1A4BD3A54BC3229B454B3D |  | R22 | TXV |  | 4.103% | 0.95897 | 7.884% | [5 empty] | TXV | 4.103%
Stockton | CA | 95219-8073 |  | 2013-06-21 | 2013-06-21 09:25 | 2013-06-21 09:43 | RUUD - RRNA-B024JK06X | 70 | -4.9 | Yes | Yes | 18.1 | 17.2 | 0.9 | 3153D7D979B24521B4D200150AB41CCD |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Yuba City | CA | 95991-3469 |  | 2013-05-24 | 2013-05-24 17:54 | 2013-05-24 17:54 | CARRIER - 38CKC060320 | 133 | 0 | Yes | Yes | 20.2 | 19.9 | 0.3 | 6B12C8E585FF485682F069F410496296 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6471 |  | 2013-06-14 | 2013-06-14 12:22 | 2013-06-14 12:27 | LENNOX - 12ACB48-4P | 171 | 5 | Yes | Yes | 24.2 | 20.4 | 3.8 | F1622FB443BA4B9D8FD0477677C05277 |  | R22 | Non-TXV |  | 2.924% | 0.97076 | 5.619% | [5 empty] | Non-TXV | 2.924%
Stockton | CA | 95209-2650 |  | 2013-05-23 | 2013-05-23 11:40 | 2013-05-23 11:40 | DAY & NIGHT - 561AJ030-A | 83 | 0 | Yes | Yes | 20.7 | 19.7 | 1 | A3FF852583A848D9AC0CCA3047B3CDCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3010 |  | 2013-06-12 | 2013-06-12 14:09 | 2013-06-12 14:34 | GOODMAN - CKJ48-1AB | 118 | 23.2 | Yes | Yes | 21 | 22.6 | -1.6 | F14482B595B7450FB63F0C7D8DD10A03 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.66% | 0.80339 | 37.78% | [5 empty] | Non-TXV | 19.66%
Stockton | CA | 95207-6944 |  | 2013-06-04 | 2013-06-04 15:52 | 2013-06-04 15:57 | AMANA - RCB30C2A | 77 | 5 | Yes | Yes | 20.7 | 19.3 | 1.4 | 55F33523756544AC909419AF1006B624 |  | R22 | Non-TXV |  | 6.494% | 0.93506 | 12.48% | [5 empty] | Non-TXV | 6.494%
Stockton | CA | 95215-2319 |  | 2013-06-05 | 2013-06-05 11:05 | 2013-06-05 11:24 | OTHER - PGF330060K01A1 | 152 | 10.4 | Yes | Yes | 20 | 17.6 | 2.4 | ECF3690459CB4E2487CC9DAC54B80D7B |  | R22 | Non-TXV |  | 6.842% | 0.93158 | 13.15% | [5 empty] | Non-TXV | 6.842%
Stockton | CA | 95210-1949 |  | 2013-06-12 | 2013-06-12 09:25 | 2013-06-12 09:46 | OTHER - UNK | 64 | -3.8 | Yes | Yes | 18.5 | 18.2 | 0.3 | 3C84A52D9EED496D8027E77481697212 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Stockton | CA | 95210-4449 |  | 2013-06-19 | 2013-06-19 14:10 | 2013-06-19 14:30 | HEIL - CA5048VKA1 | 178 | 9.3 | Yes | Yes | 23.1 | 20.7 | 2.4 | D2B0861C257148EEBE62C37CCF2FBA02 |  | R22 | Non-TXV |  | 5.225% | 0.94775 | 10.04% | [5 empty] | Non-TXV | 5.225%
Stockton | CA | 95219-3518 |  | 2013-06-21 | 2013-06-21 10:28 | 2013-06-21 10:49 | ARMSTRONG - 2SCU13LB130P-1 | 85 | -6 | Yes | Yes | 22.7 | 19.3 | 3.4 | 0C84CB4271D74EA8B9223AB88E09CD3A |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Stockton | CA | 95206-4767 |  | 2013-09-04 | 2013-09-04 10:52 | 2013-09-04 11:15 | ICP - CA9030VKA2 | 130 | 9.1 | Yes | Yes | 22.8 | 20.1 | 2.7 | 3CD95CE376FC4622938327E5018FB644 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Stockton | CA | 95205-7847 |  | 2013-06-05 | 2013-06-05 10:55 | 2013-06-05 11:14 | HEIL - UNK | 54 | 2.8 | Yes | Yes | 20.6 | 18.8 | 1.8 | DFAFF7DF26A0498AB623DA8A233BB861 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Stockton | CA | 95206-4720 |  | 2013-06-14 | 2013-06-14 08:37 | 2013-06-14 08:58 | TRANE - TTR030C100A3 | 66 | 6 | Yes | Yes | 21 | 20.2 | 0.8 | 1C0100A6B45D4EF48CF88AA6AA72ADBD |  | R22 | Non-TXV |  | 9.091% | 0.90909 | 17.47% | [5 empty] | Non-TXV | 9.091%
Stockton | CA | 95206-5625 |  | 2013-06-21 | 2013-06-21 11:56 | 2013-06-21 12:26 | GOODMAN - GSC130601BC | 85 | 5.3 | Yes | Yes | 26.2 | 20.4 | 5.8 | 10BC00CA9B904647AFD6B2DF1897C2C6 |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Stockton | CA | 95219-5482 |  | 2013-07-29 | 2013-07-29 11:23 | 2013-07-29 11:41 | CARRIER - 38EN018310SM | 55 | 7.9 | Yes | Yes | 14.9 | 17.7 | -2.8 | 71D83AFCF4B0480397575645EF4EE150 |  | R22 | Non-TXV |  | 14.36% | 0.85636 | 27.6% | [5 empty] | Non-TXV | 14.36%
Fresno | CA | 93702-3847 |  | 2013-06-19 | 2013-06-19 11:02 | 2013-06-19 11:05 | GOODMAN - GPG1324045M41AD | 80 | 9.8 | Yes | Yes | 21.6 | 19.7 | 1.9 | DD9F46B8C029481ABF0139BD28A598B3 |  | R22 | Non-TXV |  | 12.25% | 0.8775 | 23.54% | [5 empty] | Non-TXV | 12.25%
Stockton | CA | 95206-4720 |  | 2013-06-14 | 2013-06-14 09:55 | 2013-06-14 10:18 | RHEEM - RAHE-042JAS | 85 | 8.2 | Yes | Yes | 21.4 | 20.4 | 1 | 7CF9BA0F96A647E9A6D8DCA05EFADAD1 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Foresthill | CA | 95631-0000 |  | 2013-08-14 | 2013-08-14 15:31 | 2013-08-14 15:31 | RHEEM - RPNA-043J 000 | 70 | 0 | Yes | Yes | 21.3 | 19.5 | 1.8 | FBF7D97514AC4590B1CD1B1576A3A009 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-0000 |  | 2013-08-14 | 2013-08-14 15:48 | 2013-08-14 15:48 | RUUD - UPND- 024J 005 | 80 | 0 | Yes | Yes | 23.9 | 21 | 2.9 | FC92ED8FC9E24EC983A780267330A976 |  | R22 | TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3529 |  | 2013-06-27 | 2013-06-27 14:25 | 2013-06-27 14:31 | GOODMAN - CK491B | 90 | 6.2 | Yes | Yes | 22.9 | 20.2 | 2.7 | 8307BB69D2F44075AB1C3788DDC247AA |  | R22 | Non-TXV |  | 6.889% | 0.93111 | 13.24% | [5 empty] | Non-TXV | 6.889%
Manteca | CA | 95336-3452 |  | 2013-05-28 | 2013-05-28 14:28 | 2013-05-28 15:04 | AMANA - RCE36A2D | 230 | 17.1 | Yes | Yes | 19.4 | 18.6 | 0.8 | 085887BDD5AC4E759C371E5A08756829 |  | R22 | Non-TXV |  | 7.435% | 0.92565 | 14.29% | [5 empty] | Non-TXV | 7.435%
Marysville | CA | 95901-4053 |  | 2013-06-04 | 2013-06-04 14:50 | 2013-06-04 15:06 | GE - UNK | 80 | 3.4 | Yes | Yes | 19 | 20.4 | -1.4 | 418C345F79D74BB1BEB759AC1EE21E0B |  | R22 | TXV |  | 4.25% | 0.9575 | 8.168% | [5 empty] | TXV | 4.25%
Fresno | CA | 93722-5151 |  | 2013-07-16 | 2013-07-16 14:38 | 2013-07-16 14:39 | CARRIER - 48KLAA130 | 60 | 9.8 | Yes | Yes | 22.1 | 20.7 | 1.4 | 5A30AB766D7446D6B129B19061C2B63E |  | R22 | Non-TXV |  | 16.33% | 0.83667 | 31.39% | [5 empty] | Non-TXV | 16.33%
Stockton | CA | 95210-1778 |  | 2013-06-10 | 2013-06-10 12:40 | 2013-06-10 13:07 | CARRIER - 38EA024310 | 55 | -3.2 | Yes | Yes | 24.8 | 19 | 5.8 | 20478FCD64CC447C9BACF47359581224 |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Fresno | CA | 93704-4079 |  | 2013-09-19 | 2013-09-19 15:38 | 2013-09-19 15:39 | OTHER - UNK | 56 | 7.4 | Yes | Yes | 26.3 | 21.2 | 5.1 | F6E76EE3C2A74A07905DF9166BF101EB |  | R22 | Non-TXV |  | 13.21% | 0.86786 | 25.39% | [5 empty] | Non-TXV | 13.21%
Clovis | CA | 93611-4590 |  | 2013-06-15 | 2013-06-15 12:38 | 2013-06-15 12:59 | BDP - 585GJW036060ABAF | 82 | 2.7 | Yes | Yes | 19.7 | 19.9 | -0.2 | D192DDD709004AE083B4A53C3606F997 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Clovis | CA | 93612-4809 |  | 2013-06-18 | 2013-06-18 15:46 | 2013-06-18 16:05 | YORK - D1NA036N03606C | 67 | 3.3 | Yes | Yes | 22.9 | 20.8 | 2.1 | B9E43EA10080496B86EDE7DDF10CF664 |  | R22 | Non-TXV |  | 4.925% | 0.95075 | 9.465% | [5 empty] | Non-TXV | 4.925%
Fresno | CA | 93703-2726 |  | 2013-05-31 | 2013-05-31 14:44 | 2013-05-31 15:04 | ICP - GFM30K60E | 53 | 6.9 | Yes | Yes | 18.2 | 20.4 | -2.2 | C4DDCC8B99804D6DAD92B01FC02AA43F |  | R22 | Non-TXV |  | 13.02% | 0.86981 | 25.02% | [5 empty] | Non-TXV | 13.02%
Stockton | CA | 95210-1915 |  | 2013-06-11 | 2013-06-11 14:50 | 2013-06-11 14:50 | GOODMAN - CKL36-1H | 69 | 0 | Yes | Yes | 18 | 19.7 | -1.7 | A1C2675FF5C04221B4CF4DFF4A3D7B55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mendota | CA | 93640-4002 |  | 2013-08-21 | 2013-08-21 13:19 | 2013-08-21 13:20 | BRYANT - 113RNA042-A | 114 | 6.3 | Yes | Yes | 25 | 19.5 | 5.5 | 1BF27F7E9AFD4B199E2E7B3002595974 |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Riverbank | CA | 95367-2865 |  | 2013-06-03 | 2013-06-03 14:11 | 2013-06-03 14:33 | CARRIER - GSC130301EB | 66 | 11 | Yes | Yes | 28.3 | 22.6 | 5.7 | C50DE5B331A04D96B82EE7A5E2940DB6 |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Dos Palos | CA | 93620-9521 |  | 2013-07-08 | 2013-07-08 11:23 | 2013-07-08 11:28 | OTHER - 7777UNK | 100 | 3.2 | Yes | Yes | 16 | 18.8 | -2.8 | 077BFCEAF3444C8AAF590BA9F4078BFC |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93705-2677 |  | 2013-08-02 | 2013-08-02 11:13 | 2013-08-02 11:50 | GOODMAN - PGL024050-1 | 60 | 2.3 | Yes | Yes | 18.5 | 20.4 | -1.9 | 3CDF1449D53D439796BA65CC2A59441D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.833% | 0.96167 | 7.367% | [5 empty] | Non-TXV | 3.833%
Stockton | CA | 95210-5131 |  | 2013-07-11 | 2013-07-11 11:34 | 2013-07-11 11:52 | RHEEM - UNK | 80 | 2.9 | Yes | Yes | 24.5 | 20.4 | 4.1 | 7711DB5CB2274BCCA03C6DF1AF9EAF49 |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Fresno | CA | 93705-2676 |  | 2013-08-12 | 2013-08-12 10:56 | 2013-08-12 10:58 | GOODMAN - GPG122407016 | 64 | 2.3 | Yes | Yes | 26.3 | 21.3 | 5 | 6605D3929F42431ABA737BBCAD6993E0 |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Stockton | CA | 95206-6018 |  | 2013-07-05 | 2013-07-05 08:24 | 2013-07-05 08:53 | GOODMAN - UNK | 85 | 7.4 | Yes | Yes | 18.8 | 19.9 | -1.1 | 87608F32424749EA980F4EC6F60D0DF0 |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Stockton | CA | 95206-5920 |  | 2013-06-19 | 2013-06-19 14:37 | 2013-06-19 14:55 | CARRIER - 38CKC048300 | 103 | 6.1 | Yes | Yes | 22.1 | 20.4 | 1.7 | 90FF39306F50429A8ACE5254490794F4 |  | R22 | TXV |  | 5.922% | 0.94078 | 11.38% | [5 empty] | TXV | 5.922%
Stockton | CA | 95206-5513 |  | 2013-06-20 | 2013-06-20 10:10 | 2013-06-20 10:27 | BRYANT - 561CJX048000AAAA | 104 | 6 | Yes | Yes | 20.8 | 17.4 | 3.4 | FDB04C23D71242988DAB01F395C86E29 |  | R22 | TXV |  | 5.769% | 0.94231 | 11.09% | [5 empty] | TXV | 5.769%
Tracy | CA | 95377-7047 |  | 2013-07-19 | 2013-07-19 11:01 | 2013-07-19 11:25 | BRYANT - 561CJ036-E | 70 | -4.9 | Yes | Yes | 20 | 15.8 | 4.2 | 62871567797C4D9EAD7D60522F320051 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Tracy | CA | 95377-7047 |  | 2013-07-19 | 2013-07-19 10:52 | 2013-07-19 11:26 | BRYANT - 561CJ036-E | 70 | 2.6 | Yes | Yes | 18.1 | 20.7 | -2.6 | DAA86A6369B5489380146C939A6A0080 |  | R22 | Non-TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | Non-TXV | 3.714%
Stockton | CA | 95205-8004 |  | 2013-06-05 | 2013-06-05 12:05 | 2013-06-05 12:05 | PAYNE - 561AJ024-E | 56 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | F80CCE5290CE43E38A117623BC460612 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-5457 |  | 2013-05-24 | 2013-05-24 14:20 | 2013-05-24 14:40 | DAY & NIGHT - UNK | 95 | 9.4 | Yes | Yes | 20 | 19.1 | 0.9 | 61F2162271684F12AF2B52A0B296696F |  | R22 | Non-TXV |  | 9.895% | 0.90105 | 19.02% | [5 empty] | Non-TXV | 9.895%
Fresno | CA | 93702-2158 |  | 2013-06-24 | 2013-06-24 14:41 | 2013-06-24 14:50 | RHEEM - RRNAB030JK06X | 65 | 5.7 | Yes | Yes | 23.7 | 19.8 | 3.9 | 4CD0B8F9504C4C5BABDAA41C53097F49 |  | R22 | Non-TXV |  | 8.769% | 0.91231 | 16.85% | [5 empty] | Non-TXV | 8.769%
Tracy | CA | 95376-5414 |  | 2013-06-05 | 2013-06-05 15:06 | 2013-06-05 15:06 | TRANE - TTR742AA100A0 | 138 | 0 | Yes | Yes | 25.3 | 19.9 | 5.4 | 60623C16A98A4B84B13CAA1A6C7914C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0675 |  | 2013-06-03 | 2013-06-03 10:57 | 2013-06-03 11:35 | COLEMAN - 2430A901 | 35 | 12.9 | Yes | Yes | 24 | 21.5 | 2.5 | BC7259B395A64BC78594086E92DBB7F0 |  | R22 | Non-TXV |  | 36.86% | 0.63143 | 70.83% | [5 empty] | Non-TXV | 36.86%
Red Bluff | CA | 96080-3220 |  | 2013-05-23 | 2013-05-23 17:39 | 2013-05-23 17:58 | YORK - B1HH036A06B | 140 | 5.6 | Yes | Yes | 25.5 | 21.8 | 3.8 | E663CDC404E34F7582B5DED4677B8AD1 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Oroville | CA | 95966-3704 |  | 2013-06-19 | 2013-06-19 08:52 | 2013-06-19 09:10 | LENNOX - HP21-511-2P | 248 | 14 | Yes | Yes | 19.9 | 14.7 | 5.2 | 97786E0CC8E64CCFA581BD87809456EC |  | R22 | Non-TXV |  | 5.645% | 0.94355 | 10.85% | [5 empty] | Non-TXV | 5.645%
Los Banos | CA | 93635-2903 |  | 2013-10-10 | 2013-10-10 12:16 | 2013-10-10 12:18 | BDP - 777UNK | 68 | 2.3 | Yes | Yes | 25.2 | 20.1 | 5.1 | 01B383072FB24D839259F7534FBEB78D |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Fresno | CA | 93706-4516 |  | 2013-07-16 | 2013-07-16 11:56 | 2013-07-16 11:58 | YORK - D1NP036N05606A | 108 | 3.8 | Yes | Yes | 25.5 | 19.8 | 5.7 | 9AFA430E6C7448AA82D1E16888F0A893 |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Clovis | CA | 93612-3325 |  | 2013-06-18 | 2013-06-18 10:45 | 2013-06-18 11:09 | CARRIER - N/A | 90 | 2.9 | Yes | Yes | 22.7 | 20.4 | 2.3 | BBDFDB86A1944F869EA11C6F369BDC52 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Fowler | CA | 93625-2409 |  | 2013-08-20 | 2013-08-20 13:54 | 2013-08-20 14:22 | OTHER - N/A | 81 | 8.1 | Yes | Yes | 16 | 18.6 | -2.6 | B6EBF12702084459AE78CCF7FFABD126 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Los Banos | CA | 93635-6369 |  | 2013-06-04 | 2013-06-04 10:23 | 2013-06-04 10:28 | BRYANT - 563CN042 | 103 | 4.1 | Yes | Yes | 18.9 | 19.3 | -0.4 | 5B02B28B85A448FEB02BCD6A33CF6D69 |  | R22 | TXV |  | 3.981% | 0.96019 | 7.65% | [5 empty] | TXV | 3.981%
Oroville | CA | 95966-9532 |  | 2013-08-29 | 2013-08-29 13:10 | 2013-08-29 13:30 | OTHER - UNK | 80 | 2.8 | Yes | Yes | 17.1 | 19.5 | -2.4 | 4B2875E858184D57965AD6CBA4272501 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Fresno | CA | 93704-6322 |  | 2013-06-19 | 2013-06-19 11:38 | 2013-06-19 11:43 | ICP - PGAD36D1K6 | 102 | 6.5 | Yes | Yes | 19.9 | 18.2 | 1.7 | 6239A4F3C8934B25A4A9C124E914EFB5 |  | R22 | Non-TXV |  | 6.373% | 0.93627 | 12.25% | [5 empty] | Non-TXV | 6.373%
San Joaquin | CA | 93660-0000 |  | 2013-08-28 | 2013-08-28 10:15 | 2013-08-28 10:19 | OTHER - CA5536VKA1 | 100 | 3 | Yes | Yes | 24.5 | 18.5 | 6 | 57747AB0F7CE429AA25D3A8930F4D950 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93725-9311 |  | 2013-06-20 | 2013-06-20 12:31 | 2013-06-20 12:33 | CARRIER - 7777UNK | 116 | 4.4 | Yes | Yes | 22.8 | 20.4 | 2.4 | 5A398B18BC33458E9FE9DF9F2CA456DA |  | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Mariposa | CA | 95338-9749 |  | 2013-08-02 | 2013-08-02 12:30 | 2013-08-02 12:33 | AMERICAN STANDARD - 2A7B3036A1000A | 101 | 3.4 | Yes | Yes | 18.2 | 20.4 | -2.2 | A1C6BF5D1AD14C6AB50307F9D0CF5347 |  | R22 | Non-TXV |  | 3.366% | 0.96634 | 6.469% | [5 empty] | Non-TXV | 3.366%
Atwater | CA | 95301-4233 |  | 2013-06-14 | 2013-06-14 09:04 | 2013-06-14 09:07 | YORK - D3NZ030N05606NXA | 64 | 2 | Yes | Yes | 22.2 | 19.5 | 2.7 | B850A0C2B26F42E0859562FC07BF537E |  | R410A | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93722-7207 |  | 2013-08-08 | 2013-08-08 13:06 | 2013-08-08 13:08 | TRANE - YCC018F1L0VH | 60 | 1.8 | Yes | Yes | 23.7 | 20.1 | 3.6 | 588F9539B255427497277C019F2BCBBB |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Newman | CA | 95360-1058 |  | 2013-06-05 | 2013-06-05 10:42 | 2013-06-05 11:13 | WEATHER KING - 12AJ2401 | 85 | 2.6 | Yes | Yes | 18 | 19.7 | -1.7 | 4E3BC4E565654046AD19A412035BD596 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Livingston | CA | 95334-1882 |  | 2013-06-11 | 2013-06-11 11:54 | 2013-06-11 12:12 | AMERICAN STANDARD - TTR030C100A0 | 74 | 9.8 | Yes | Yes | 22.3 | 19.8 | 2.5 | D3FF7545D6274DBEA3BC04320210C82F |  | R22 | Non-TXV |  | 13.24% | 0.86757 | 25.45% | [5 empty] | Non-TXV | 13.24%
Winton | CA | 95388-9381 |  | 2013-06-14 | 2013-06-14 13:53 | 2013-06-14 13:56 | RHEEM - RRNLB036JK06X | 92 | 4.7 | Yes | Yes | 19.2 | 20.1 | -0.9 | F037F369B9074F418CE1572F25806AF0 |  | R410A | Non-TXV |  | 5.109% | 0.94891 | 9.818% | [5 empty] | Non-TXV | 5.109%
Merced | CA | 95341-7713 |  | 2013-06-13 | 2013-06-13 16:00 | 2013-06-13 16:05 | BRYANT - 561CJ036 | 70 | 5.9 | Yes | Yes | 21.4 | 20.4 | 1 | 8401FDE030C54D4CAA7AFCD10E7C6FE8 |  | R22 | Non-TXV |  | 8.429% | 0.91571 | 16.2% | [5 empty] | Non-TXV | 8.429%
Fresno | CA | 93705-2653 |  | 2013-08-02 | 2013-08-02 14:16 | 2013-08-02 14:37 | GOODMAN - PGJ024050-1B | 57 | 6.6 | Yes | Yes | 18.3 | 20.8 | -2.5 | 5A3D142D331D4561B8B0E202A9E548B0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.58% | 0.88421 | 22.25% | [5 empty] | Non-TXV | 11.58%
Merced | CA | 95341-7021 |  | 2013-06-11 | 2013-06-11 12:50 | 2013-06-11 12:58 | GOODMAN - CLJ421B | 84 | 12.3 | Yes | Yes | 17.7 | 19.6 | -1.9 | 23CDB4BE3B064449B6AF8312C6122032 |  | R22 | Non-TXV |  | 14.64% | 0.85357 | 28.14% | [5 empty] | Non-TXV | 14.64%
Los Banos | CA | 93635-3225 |  | 2013-05-29 | 2013-05-29 12:38 | 2013-05-29 12:40 | AIRE-FLO - UNK | 92 | 5.2 | Yes | Yes | 18.4 | 20.4 | -2 | 9B6CC43E3C1247059D2DDAD74B288616 |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Stevinson | CA | 95374-9799 |  | 2013-07-30 | 2013-07-30 15:17 | 2013-07-30 15:24 | LENNOX - 13ACD-030-230-01 | 85 | 4.9 | Yes | Yes | 23.5 | 17.5 | 6 | F8ED504557364CBB8682EDB2A53DFA6A |  | R22 | Non-TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | Non-TXV | 5.765%
Dos Palos | CA | 93620-9486 |  | 2013-07-08 | 2013-07-08 11:59 | 2013-07-08 12:04 | BRYANT - 7777UNK | 100 | 3.6 | Yes | Yes | 16.8 | 19.6 | -2.8 | D3131D1D87BA4C0E8CA004C8C1CC7EAC |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Atwater | CA | 95301-4455 |  | 2013-06-06 | 2013-06-06 11:50 | 2013-06-06 11:59 | RHEEM - RRKAA030JK08E | 54 | 5.3 | Yes | Yes | 18.8 | 20.4 | -1.6 | 1F5A8FE41EB24951B2F735AC0EE77190 |  | R22 | Non-TXV |  | 9.815% | 0.90185 | 18.86% | [5 empty] | Non-TXV | 9.815%
Merced | CA | 95348-3722 |  | 2013-07-03 | 2013-07-03 15:28 | 2013-07-03 15:31 | ARMSTRONG - RPGE13A36075LP | 117 | 7.9 | Yes | Yes | 21.9 | 22.1 | -0.2 | 3BF43995344D49CB9F158724F57A919C |  | R410A | Non-TXV |  | 6.752% | 0.93248 | 12.98% | [5 empty] | Non-TXV | 6.752%
Fresno | CA | 93725-1146 |  | 2013-10-25 | 2013-10-25 13:18 | 2013-10-25 13:19 | PAYNE - 777UNK | 80 | 2.7 | Yes | Yes | 21.8 | 19.3 | 2.5 | FAD02FC4B63640E89881007C041D93CE |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Atwater | CA | 95301-4727 |  | 2013-06-07 | 2013-06-07 13:17 | 2013-06-07 13:18 | CARRIER - 591ANX042000ABAA | 112 | 8.7 | Yes | Yes | 25.7 | 21.4 | 4.3 | 193CAB55BCD344EBBB4B9EB6714F5666 |  | R22 | Non-TXV |  | 7.768% | 0.92232 | 14.93% | [5 empty] | Non-TXV | 7.768%
Atwater | CA | 95301-4887 |  | 2013-08-14 | 2013-08-14 10:31 | 2013-08-14 11:01 | LENNOX - H89-311-6P | 78 | 14 | Yes | Yes | 20.4 | 20.4 | 0 | 5D9F5A23E9E24CA2949B57E9CD277041 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.95% | 0.82051 | 34.49% | [5 empty] | Non-TXV | 17.95%
Atwater | CA | 95301-4859 |  | 2013-06-11 | 2013-06-11 14:45 | 2013-06-11 14:47 | RHEEM - RAFA-030JAQ | 59 | 3.1 | Yes | Yes | 16 | 18.8 | -2.8 | 27C25E262498406A8E2E7E81F010C995 |  | R22 | Non-TXV |  | 5.254% | 0.94746 | 10.1% | [5 empty] | Non-TXV | 5.254%
Atwater | CA | 95301-4875 |  | 2013-06-14 | 2013-06-14 11:27 | 2013-06-14 11:37 | OTHER - GCGD30S41S1A | 62 | 4.4 | Yes | Yes | 24.6 | 18.7 | 5.9 | CE295704FBA040C78215A818D8C64567 |  | R410A | Non-TXV |  | 7.097% | 0.92903 | 13.64% | [5 empty] | Non-TXV | 7.097%
Atwater | CA | 95301-4269 |  | 2013-06-14 | 2013-06-14 09:29 | 2013-06-14 10:01 | TRANE - TTN036C100B2 | 117 | 22.6 | Yes | Yes | 22.3 | 19.9 | 2.4 | CDFB4BE070554EE4AED498575005B009 |  | R22 | Non-TXV |  | 19.32% | 0.80684 | 37.12% | [5 empty] | Non-TXV | 19.32%
Livingston | CA | 95334-9660 |  | 2013-06-11 | 2013-06-11 09:16 | 2013-06-11 09:43 | OTHER - BRCS030B | 72 | 4 | Yes | Yes | 25.3 | 19.4 | 5.9 | 697867FFFCEF4304BBDC144C45E4AC4E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Atwater | CA | 95301-4861 |  | 2013-06-07 | 2013-06-07 10:17 | 2013-06-07 10:21 | LENNOX - HS93116P | 78 | 0 | Yes | Yes | 18.3 | 19.3 | -1 | DCE9D9F9D6EB4582967F546674B39357 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4880 |  | 2013-08-13 | 2013-08-13 16:55 | 2013-08-13 17:16 | GOODMAN - CK30-1B | 76 | 3.2 | Yes | Yes | 19.8 | 18.5 | 1.3 | 500402E6C54D479497AD299EDA7E01D5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Merced | CA | 95341-5442 |  | 2013-06-12 | 2013-06-12 09:42 | 2013-06-12 09:48 | AMANA - RCE36C2A | 150 | 9.4 | Yes | Yes | 24.9 | 20.4 | 4.5 | F78A6AEF02B14FEA8ED98823D7218D49 |  | R22 | Non-TXV |  | 6.267% | 0.93733 | 12.04% | [5 empty] | Non-TXV | 6.267%
Fresno | CA | 93722-4900 |  | 2013-06-21 | 2013-06-21 10:59 | 2013-06-21 11:14 | COLEMAN - ERCS0481BBB | 134 | 6.3 | Yes | Yes | 25.1 | 21.4 | 3.7 | A397D8BAB7A8469BB1B88970197E7A50 |  | R22 | Non-TXV |  | 4.701% | 0.95299 | 9.035% | [5 empty] | Non-TXV | 4.701%
Placerville | CA | 95667-4034 |  | 2013-05-28 | 2013-05-28 12:47 | 2013-05-28 12:47 | TRANE - 2TWB0024A1000AB | 72 | 14.1 | Yes | Yes | 17.3 | 20 | -2.7 | 10CBD07F4D6B49CD978B762E1D528D7A | Add refrigerant: 14.1 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 19.58% | 0.80417 | 37.63% | [5 empty] | Non-TXV | 19.58%
Fresno | CA | 93710-5375 |  | 2013-08-10 | 2013-08-10 13:57 | 2013-08-11 00:40 | UNK - UNK | 85 | 2.7 | Yes | Yes | 19.4 | 19 | 0.4 | 094BF546CEC54C67B4563210810D8209 |  |  |  |  | 3.176% | 0.96824 | 6.104% | [5 empty] | 0 | 3.176%
Tracy | CA | 95377-7931 |  | 2013-06-04 | 2013-06-04 10:27 | 2013-06-04 10:58 | GOODMAN - CKT36-1AB | 85 | -8 | Yes | Yes | 21.9 | 21.4 | 0.5 | F4FB7A9E451E427DAFE8143A61ECF808 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Paradise | CA | 95969-4818 |  | 2013-08-05 | 2013-08-05 13:36 | 2013-08-05 17:56 | BRYANT - 582ANW030060AAAD | 55 | 7.7 | Yes | Yes | 18.9 | 20 | -1.1 | A580DA4881624A20A8F5533AA0D278DB |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Fresno | CA | 93722-5287 |  | 2013-07-11 | 2013-07-11 18:18 | 2013-07-11 18:53 | BRYANT - 563CN036-F | 103 | 7.3 | Yes | Yes | 22.9 | 21.7 | 1.2 | 649F74200F73436AA7214B409394F7C6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.087% | 0.92913 | 13.62% | [5 empty] | Non-TXV | 7.087%
Magalia | CA | 95954-9393 |  | 2013-08-03 | 2013-08-03 11:05 | 2013-08-03 11:36 | YORK - H1RA042SO6D | 84 | 8 | Yes | Yes | 19.9 | 22.3 | -2.4 | CF13F4A457CC48F2A2A7055A30FE8F0B |  | R22 | Non-TXV |  | 9.524% | 0.90476 | 18.3% | [5 empty] | Non-TXV | 9.524%
Stockton | CA | 95210-5111 |  | 2013-07-30 | 2013-07-30 09:47 | 2013-07-30 10:13 | RUUD - UAHE-048JAS | 114 | 12.1 | Yes | Yes | 20.5 | 19.7 | 0.8 | 77E17245267B4B918DDF71AF6601CE20 |  | R22 | Non-TXV |  | 10.61% | 0.89386 | 20.4% | [5 empty] | Non-TXV | 10.61%
Auburn | CA | 95603-4906 |  | 2013-06-17 | 2013-06-17 13:04 | 2013-06-17 13:25 | BDP - 589ANW04210ADAF | 91 | -6.4 | Yes | Yes | 27.9 | 22.6 | 5.3 | E012D6B7304C4362991AE78AB4BEDEEB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.033% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.033%
Gerber | CA | 96035-9718 |  | 2013-09-13 | 2013-09-13 14:53 | 2013-09-13 15:10 | BRYANT - 114ANA060-D | 103 | 7.3 | Yes | Yes | 15.7 | 18.5 | -2.8 | D0BE13811E914747A7E5D05808F47228 |  | R410A | TXV |  | 7.087% | 0.92913 | 13.62% | [5 empty] | TXV | 7.087%
Stockton | CA | 95202-1115 |  | 2013-07-09 | 2013-07-09 10:24 | 2013-07-09 10:43 | CARRIER - 38CKC048300 | 102 | 4.1 | Yes | Yes | 26.5 | 21.5 | 5 | 932B908B6D0846959AB4D30A31C44B99 |  | R22 | Non-TXV |  | 4.02% | 0.9598 | 7.725% | [5 empty] | Non-TXV | 4.02%
Chico | CA | 95973-0743 |  | 2013-06-03 | 2013-06-03 11:37 | 2013-06-03 12:07 | YORK - HIRA042506D | 84 | 4.2 | Yes | Yes | 24.3 | 22.4 | 2 | 61DF6180765E402EB90F526B259E4C65 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Yuba City | CA | 95991-6732 |  | 2013-07-16 | 2013-07-16 12:49 | 2013-07-16 13:14 | LENNOX - 10ACC-060-230-0 | 130 | 21.4 | Yes | Yes | 23 | 18.7 | 4.3 | 02769C81E65A4CABBFAD18D0DCEE38F5 |  | R22 | Non-TXV |  | 16.46% | 0.83538 | 31.64% | [5 empty] | Non-TXV | 16.46%
Rescue | CA | 95672-9690 |  | 2013-10-03 | 2013-10-03 16:20 | 2013-10-03 16:20 | UNITARY PRODUCTS GROUP - GHRD18S41S1A | 86 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 0C277872835E45BDBAEBBE87FA8AEBE9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2652 |  | 2013-08-12 | 2013-08-12 11:18 | 2013-08-12 11:20 | OTHER - 7777UNK | 64 | 1.9 | Yes | Yes | 22.8 | 19.9 | 3 | D106ACBA2A6D403CBD8349A4EBE93FCB |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Manteca | CA | 95336-7049 |  | 2013-05-29 | 2013-05-29 12:46 | 2013-05-29 13:03 | BRYANT - 563CN048-D | 165 | 6.6 | Yes | Yes | 20.9 | 19.4 | 1.5 | AE11B0E44C394C65863CE35F64C73BDE |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Fresno | CA | 93726-1515 |  | 2013-05-30 | 2013-05-30 15:11 | 2013-05-30 15:31 | GE - TC036F1B | 112 | 10.1 | Yes | Yes | 20.4 | 17.2 | 3.2 | 8A7F7BABAF634C7F8BF90671329A2D5F |  | R22 | Non-TXV |  | 9.018% | 0.90982 | 17.33% | [5 empty] | Non-TXV | 9.018%
Stockton | CA | 95205-2554 |  | 2013-06-04 | 2013-06-04 15:48 | 2013-06-04 16:31 | GOODMAN - CKL36-JL | 84 | 4.1 | Yes | Yes | 19.7 | 20.4 | -0.7 | 76D87878EAC14093BF736436CB4F0F75 |  | R22 | Non-TXV |  | 4.881% | 0.95119 | 9.38% | [5 empty] | Non-TXV | 4.881%
Livingston | CA | 95334-1805 |  | 2013-06-10 | 2013-06-10 09:15 | 2013-06-10 09:37 | RHEEM - RRNA-B36JK06X | 83 | 2.5 | Yes | Yes | 22.6 | 18.7 | 3.9 | 3159DD4A615343A2833347067F2F8AFB |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Jackson | CA | 95642-9471 |  | 2013-08-20 | 2013-08-20 08:17 | 2013-08-20 08:36 | PAYNE - PY1PNB036090ABAA | 68 | -6.4 | Yes | Yes | 19.2 | 21 | -1.8 | 20375E99974A41C8B465F3A46F8787B6 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Red Bluff | CA | 96080-3926 |  | 2013-05-29 | 2013-05-29 13:26 | 2013-05-29 13:26 | GOODMAN - GSH130241B | 83 | 0 | Yes | Yes | 20.5 | 20.7 | -0.2 | 526EB317F4F64D6498D21FE7895A0E37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2270 |  | 2013-06-05 | 2013-06-05 10:56 | 2013-06-05 11:01 | OTHER - PGD336060K001C1 | 100 | 4.1 | Yes | Yes | 21.6 | 18.8 | 2.8 | 24649AA09D96469DA206CFF21AA05AF8 |  | R410A | Non-TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | Non-TXV | 4.1%
Stockton | CA | 95207-6591 |  | 2013-06-04 | 2013-06-04 14:12 | 2013-06-04 14:33 | PAYNE - 569A042RCUE | 114 | 19.2 | Yes | Yes | 18 | 17.8 | 0.3 | D8C645D864304D1E826E94D1BEC4958E |  | R22 | Non-TXV |  | 16.84% | 0.83158 | 32.37% | [5 empty] | Non-TXV | 16.84%
Stockton | CA | 95206-5247 |  | 2013-06-20 | 2013-06-20 15:17 | 2013-06-20 15:50 | RHEEM - UNK | 85 | 8.4 | Yes | Yes | 23.3 | 22.6 | 0.7 | CEEF455B2BAB46FEBCA93D51E8C9658F |  | R22 | Non-TXV |  | 9.882% | 0.90118 | 18.99% | [5 empty] | Non-TXV | 9.882%
Rocklin | CA | 95677-4790 |  | 2013-06-17 | 2013-06-17 09:24 | 2013-06-17 09:52 | CARRIER - 38CKC024320 | 69 | -4.1 | Yes | Yes | 23 | 19.9 | 3.1 | 9F21EF2B16E448B2A60389E56B010C75 |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Fresno | CA | 93726-5421 |  | 2013-06-19 | 2013-06-19 10:27 | 2013-06-19 10:30 | CARRIER - 48SX-036060331AA | 84 | 3.8 | Yes | Yes | 24.2 | 19.8 | 4.4 | 4E2C17E004DA4DD3AABC72139C9BECDB |  | R22 | Non-TXV |  | 4.524% | 0.95476 | 8.694% | [5 empty] | Non-TXV | 4.524%
Oroville | CA | 95966-3663 |  | 2013-06-20 | 2013-06-20 20:16 | 2013-06-20 20:33 | BRYANT - 574DNW03606NA | 146 | 0 | Yes | Yes | 18.2 | 19.4 | -1.2 | F189F68FF9814439B5F336D4AC1755C0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2918 |  | 2013-06-05 | 2013-06-05 10:46 | 2013-06-05 11:03 | BRYANT - 582ANW036090NBAF | 70 | 2.8 | Yes | Yes | 21.5 | 20.4 | 1.1 | 79E42C9FB0DE44288CA4A6130558CB5F |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Merced | CA | 95341-7025 |  | 2013-08-06 | 2013-08-06 10:22 | 2013-08-06 10:49 | UNITARY PRODUCTS GROUP - H2RD036S06B | 96 | 3.4 | Yes | Yes | 18 | 18.2 | -0.2 | BB9E9FC9D48347F69D14793C7F145DB6 |  | R22 | TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | TXV | 3.542%
Red Bluff | CA | 96080-2581 |  | 2013-06-04 | 2013-06-04 16:42 | 2013-06-04 18:41 | YORK - H1RA024S06D | 59 | 1.9 | Yes | Yes | 28.1 | 22.6 | 5.5 | 3CC886889ECE449CAD0E31078E53913C |  | R22 | Non-TXV |  | 3.22% | 0.9678 | 6.189% | [5 empty] | Non-TXV | 3.22%
Auburn | CA | 95602-2138 |  | 2013-06-08 | 2013-06-08 08:51 | 2013-06-08 09:14 | GE - UNK | 70 | 9.6 | Yes | Yes | 20 | 18.7 | 1.3 | 598DC2FDED2A47228626FE2495FEC8C6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.71% | 0.86286 | 26.36% | [5 empty] | Non-TXV | 13.71%
Clovis | CA | 93611-4037 |  | 2013-06-13 | 2013-06-13 15:53 | 2013-06-13 16:18 | GOODMAN - PGB036075-1A | 60 | 4.7 | Yes | Yes | 22.5 | 21.3 | 1.3 | 78847F63434D4BBEAA3EBF4A9A0EECE2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.833% | 0.92167 | 15.05% | [5 empty] | Non-TXV | 7.833%
Manteca | CA | 95336-9697 |  | 2013-05-28 | 2013-05-28 09:43 | 2013-05-28 10:18 | BRYANT - 54ANW048090NB-- | 196 | 15.3 | Yes | Yes | 21.2 | 19 | 2.2 | F8E9C5E86451487BAFE9272966E29203 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.806% | 0.92194 | 15% | [5 empty] | Non-TXV | 7.806%
Auburn | CA | 95603-6302 |  | 2013-06-17 | 2013-06-17 11:03 | 2013-06-17 11:35 | BRYANT - 563CN036-1 | 114 | 15.9 | Yes | Yes | 26.9 | 21.2 | 5.8 | CB6192A859ED47AEA3AE57F765B238DB |  | R22 | Non-TXV |  | 13.95% | 0.86053 | 26.8% | [5 empty] | Non-TXV | 13.95%
Newman | CA | 95360-9535 |  | 2013-06-04 | 2013-06-04 14:47 | 2013-06-04 15:04 | CARRIER - 38CKC060370 | 131 | 5.9 | Yes | Yes | 20 | 21.9 | -1.9 | 1B54BBEA0958461DB8575633CDAC67A3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.504% | 0.95496 | 8.655% | [5 empty] | Non-TXV | 4.504%
Red Bluff | CA | 96080-8941 |  | 2013-05-30 | 2013-05-30 12:34 | 2013-05-30 12:34 | BRYANT - 550AN060-B | 192 | 0 | Yes | Yes | 26.3 | 22 | 4.3 | 644320E3C3CA4AE0B300028F7BF94146 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-3216 |  | 2013-07-06 | 2013-07-06 11:11 | 2013-07-06 11:34 | LENNOX - 13ACD-060-230-01 | 214 | 15.4 | Yes | Yes | 18 | 20.4 | -2.4 | A5772FCBC8B04AC19672FF181568A8CF |  | R22 | TXV |  | 7.196% | 0.92804 | 13.83% | [5 empty] | TXV | 7.196%
Fresno | CA | 93720-4041 |  | 2013-06-24 | 2013-06-24 10:46 | 2013-06-24 10:51 | TEMPSTAR - CA7036VKA2 | 140 | 4.2 | Yes | Yes | 20.4 | 17.5 | 2.9 | 0ECEC7C5C45E40C58B3E0252D8B1AEE8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93726-4908 |  | 2013-06-05 | 2013-06-05 17:51 | 2013-06-05 18:01 | GOODMAN - PGY048075 | 80 | 3.5 | Yes | Yes | 23.4 | 17.6 | 5.8 | EF281659D45B4BA3AA5B642D73A5511A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Yuba City | CA | 95991-2447 |  | 2013-05-31 | 2013-05-31 16:09 | 2013-05-31 16:37 | LENNOX - 13ACC-036-230-01 | 118 | -33.6 | Yes | Yes | 22.4 | 23.6 | -1.2 | C6991A418E6F4283AE9AF99619B12679 |  | R22 | TXV |  | -28.47% | 1.2847 | 7.974% |  |  |  |  | TXV |  |  | -28.47%
Yuba City | CA | 95991-2447 |  | 2013-06-02 | 2013-06-02 22:35 | 2013-06-02 22:54 | LENNOX - 13ACC-036-230-01 | 115 | 5 | Yes | Yes | 23.5 | 24.2 | -0.7 | 50A26126FA354BC1BFC1C5F8CFA11D36 |  | R22 | TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | TXV | 4.348%
Stockton | CA | 95206-6271 |  | 2013-06-18 | 2013-06-18 13:39 | 2013-06-18 13:56 | PAYNE - PA1ANR04800GAJA | 138 | 5.4 | Yes | Yes | 23.6 | 19.8 | 3.8 | 9CE468250C5849818DAA3B89849197B6 |  | R22 | TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | TXV | 3.913%
Manteca | CA | 95337-6652 |  | 2013-05-24 | 2013-05-24 14:41 | 2013-05-24 15:01 | BRYANT - 563CN036-C | 101 | 3.3 | Yes | Yes | 20.1 | 21.4 | -1.3 | 5D05B30FD530444EB8ACD09FCFF44A89 |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Manteca | CA | 95337-6652 |  | 2013-05-24 | 2013-05-24 14:49 | 2013-05-24 15:12 | BRYANT - 563CN036-C | 101 | 6.7 | Yes | Yes | 19.4 | 20 | -0.6 | 5CCD4301D6884B4BA95B6AD83CA4A202 |  | R22 | Non-TXV |  | 6.634% | 0.93366 | 12.75% | [5 empty] | Non-TXV | 6.634%
Red Bluff | CA | 96080-2580 |  | 2013-05-28 | 2013-05-28 12:17 | 2013-05-28 12:17 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 23 | 21.8 | 1.2 | 90EE40EECC914873A7C69872D15440BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-8577 |  | 2013-05-24 | 2013-05-24 11:34 | 2013-05-24 11:53 | TRANE - 2TTB0060A10000AA | 126 | 9.8 | Yes | Yes | 28.4 | 23.1 | 5.3 | ACA5CAD52A7B444AACB7EA3D21C69A95 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Rocklin | CA | 95765-5835 |  | 2013-07-20 | 2013-07-20 11:15 | 2013-07-20 11:37 | GOODMAN - CKJ36-10 | 90 | 2.7 | Yes | Yes | 16 | 18.1 | -2.1 | 679F8309228D47769396BF14B3994828 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 3% | 0.97 | 5.765% | [5 empty] | TXV | 3%
Rocklin | CA | 95765-5835 |  | 2013-07-20 | 2013-07-20 11:24 | 2013-07-20 11:24 | GOODMAN - CK36-1D | 90 | 0 | Yes | Yes | 18 | 19.3 | -1.3 | 3F0162A445C048F797AA0530A89D7DC6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-4700 |  | 2013-06-27 | 2013-06-27 12:51 | 2013-06-27 13:13 | RHEEM - RAFD-031JAS | 85 | -8 | Yes | Yes | 20.6 | 17.9 | 2.7 | 70BF929759984B09A7571104ACFB73EF |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95210-1610 |  | 2013-06-17 | 2013-06-17 13:28 | 2013-06-17 13:47 | YORK - D1NA036N05606C | 67 | -3.9 | Yes | Yes | 28.2 | 22.5 | 5.7 | F46F0EF8EAFF4EB9B668943084373FA4 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Rescue | CA | 95672-9695 |  | 2013-08-10 | 2013-08-10 11:33 | 2013-08-10 11:33 | PAYNE - 5410J018 | 83 | 0 | Yes | Yes | 20 | 19.1 | 0.9 | 27CB9D3F2D6641DEB9F08621FB8C5BC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4250 |  | 2013-08-15 | 2013-08-15 11:36 | 2013-08-15 11:57 | BDP - 585HJWO36060ABAF | 102 | 15.6 | Yes | Yes | 18 | 18.6 | -0.6 | 2EAF4D9815844B2D89F7DD8800AD063A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
Sutter | CA | 95982-2404 |  | 2013-09-30 | 2013-09-30 13:43 | 2013-09-30 14:09 | RUUD - 14AJM60A01 | 240 | 8.8 | Yes | Yes | 21.5 | 17.9 | 3.6 | 8D1FEE85383740A5AD1F04B479ED14CD |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Red Bluff | CA | 96080-2679 |  | 2013-05-28 | 2013-05-28 17:15 | 2013-05-28 17:38 | DAY & NIGHT - 588ANW030080AAAD | 51 | 5.6 | Yes | Yes | 23.6 | 22.6 | 1 | E342EA83490A40A2BEDF6234344A4152 |  | R22 | Non-TXV |  | 10.98% | 0.8902 | 21.1% | [5 empty] | Non-TXV | 10.98%
Atwater | CA | 95301-2270 |  | 2013-06-05 | 2013-06-05 11:13 | 2013-06-05 11:17 | AMANA - PGD36C0702E | 84 | 3.6 | Yes | Yes | 27.4 | 21.5 | 5.9 | ECAC652B38B84B7BBB535D38D2CEC026 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95206-6006 |  | 2013-07-08 | 2013-07-08 11:30 | 2013-07-08 11:52 | GOODMAN - CKL42-1A | 116 | -10.9 | Yes | Yes | 26.5 | 21.3 | 5.2 | 72243DDD49C442D78685ABAD83985BEA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.397% | 1.094 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.397%
Chico | CA | 95928-7053 |  | 2013-07-03 | 2013-07-03 18:56 | 2013-07-03 19:14 | GOODMAN - GSC130241AE | 93 | 2.9 | Yes | Yes | 21.6 | 20.1 | 1.6 | D5D7AFD92F0F4EABAE97203ABB0771F0 |  | R22 | Non-TXV |  | 3.118% | 0.96882 | 5.993% | [5 empty] | Non-TXV | 3.118%
Marysville | CA | 95901-8245 |  | 2013-06-03 | 2013-06-03 10:03 | 2013-06-03 10:20 | BRYANT - 38CKC030340 | 70 | 4.9 | Yes | Yes | 19 | 20.4 | -1.4 | 518715FC557944B7964A0E7574F1C4F1 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Lincoln | CA | 95648-8707 |  | 2013-05-30 | 2013-05-30 11:52 | 2013-05-30 12:12 | OTHER - H2RC036S06A | 83 | 5.4 | Yes | Yes | 19 | 19.1 | -0.1 | 1BF59A76E35244AF9F9D3AF397756047 |  | R22 | Non-TXV |  | 6.506% | 0.93494 | 12.5% | [5 empty] | Non-TXV | 6.506%
Atwater | CA | 95301-2293 |  | 2013-06-05 | 2013-06-05 12:36 | 2013-06-05 12:39 | RHEEM - RRNAC060JK10X | 145 | 8.1 | Yes | Yes | 25.6 | 20.1 | 5.5 | B4CD69A2F8584D59A74FE572ED52013A |  | R22 | Non-TXV |  | 5.586% | 0.94414 | 10.74% | [5 empty] | Non-TXV | 5.586%
Atwater | CA | 95301-4876 |  | 2013-06-11 | 2013-06-11 11:45 | 2013-06-11 11:46 | GUARDIAN - GCGD30S41S3A | 62 | 4.2 | Yes | Yes | 19 | 18.1 | 0.9 | E605121C4E3841868416742025A12206 |  | R410A | Non-TXV |  | 6.774% | 0.93226 | 13.02% | [5 empty] | Non-TXV | 6.774%
Fresno | CA | 93727-7101 |  | 2013-06-18 | 2013-06-18 11:07 | 2013-06-18 11:08 | PAYNE - 585A036090YAC | 60 | 5.1 | Yes | Yes | 24.6 | 21 | 3.6 | D6F80C916FBC4215A22216DAE839429D |  | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Fresno | CA | 93703-3717 |  | 2013-06-11 | 2013-06-11 10:48 | 2013-06-11 10:48 | GOODMAN - GPG13240451BA | 74 | 0 | Yes | Yes | 20.6 | 17.9 | 2.7 | F927975A15344A2EA7A78B8D9FD77384 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6017 |  | 2013-06-14 | 2013-06-14 14:45 | 2013-06-14 15:13 | LENNOX - HS26-060-6P | 162 | 5 | Yes | Yes | 23.5 | 20.5 | 3 | A9088F9CCFED44B7A64F636663F91C6E |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Fresno | CA | 93720-2661 |  | 2013-06-21 | 2013-06-21 10:06 | 2013-06-21 10:08 | CARRIER - 48XLNO36060301 | 149 | 4.7 | Yes | Yes | 17.8 | 20.2 | -2.4 | A6A290655594444F9FBF6554C1D340C1 |  | R410A | Non-TXV |  | 3.154% | 0.96846 | 6.062% | [5 empty] | Non-TXV | 3.154%
Clovis | CA | 93611-2051 |  | 2013-06-26 | 2013-06-26 10:00 | 2013-06-26 10:58 | GOODMAN - PGB036075-1A | 60 | -3.5 | Yes | Yes | 19.6 | 16.3 | 3.3 | 04A7223BA41A4B36900DC9AE60EC94E9 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93703-3226 |  | 2013-10-27 | 2013-10-27 22:18 | 2013-10-27 22:20 | TRANE - YCC030F`MOBH | 69 | 3.5 | Yes | Yes | 22.2 | 18.7 | 3.5 | 1CD332B4DFBE4F028953C12133A45125 |  | R22 | Non-TXV |  | 5.072% | 0.94928 | 9.748% | [5 empty] | Non-TXV | 5.072%
Tracy | CA | 95377-8713 |  | 2013-06-04 | 2013-06-04 09:42 | 2013-06-04 10:13 | BRYANT - 38CKC048360 | 109 | -10.3 | Yes | Yes | 18.3 | 18.2 | 0.1 | FDA04AFE873244FFA631BACF2B501555 |  | R22 | Non-TXV |  | -9.45% | 1.0945 | 2.646% |  |  |  |  | Non-TXV |  |  | -9.45%
Manteca | CA | 95337-4439 |  | 2013-05-28 | 2013-05-28 15:50 | 2013-05-28 16:18 | BDP - 561CJ0024-C | 69 | 8.4 | Yes | Yes | 19.1 | 19 | 0.1 | 53F3B02DF5C346CEB71803B72874A9CA |  | R22 | Non-TXV |  | 12.17% | 0.87826 | 23.4% | [5 empty] | Non-TXV | 12.17%
Fresno | CA | 93727-6826 |  | 2013-06-19 | 2013-06-19 09:50 | 2013-06-19 09:52 | RUUD - URMA-A036JK08E | 99 | 5.4 | Yes | Yes | 21.7 | 19.6 | 2.2 | 323998ABFA2C45DB89B6D6C0AB4D345F |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Chico | CA | 95973-0493 |  | 2013-06-04 | 2013-06-04 13:33 | 2013-06-04 13:33 | TEMPSTAR - TCA036AKC4 | 96 | 0 | Yes | Yes | 26.5 | 20.8 | 5.7 | F0685701214A471B91A7BE91B3CEAB4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2340 |  | 2013-06-05 | 2013-06-05 13:08 | 2013-06-05 13:11 | RUUD - URGG05E30JKR | 46 | 4.7 | Yes | Yes | 25 | 20.6 | 4.4 | 9E22EA86FC5F4CCBA7F3976BFF00B5F2 |  | R22 | Non-TXV |  | 10.22% | 0.89783 | 19.64% | [5 empty] | Non-TXV | 10.22%
Auburn | CA | 95602-8103 |  | 2013-08-13 | 2013-08-13 12:23 | 2013-08-13 12:23 | PAYNE - 588ANW036080ACBF | 69 | 0 | Yes | Yes | 19.5 | 19.4 | 0.1 | 15F64132A022480487CADA941FAE3353 | OK: Verified Refrigerant Charge Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3056 |  | 2013-06-28 | 2013-06-28 10:48 | 2013-06-28 11:18 | AMERICAN STANDARD - YCC042F1M0BG | 101 | 3.3 | Yes | Yes | 15.8 | 16.1 | -0.3 | 16CB53AB0FA4439592CDF0231F7471AF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Stockton | CA | 95206-3800 |  | 2013-06-13 | 2013-06-13 13:35 | 2013-06-13 14:00 | GOODMAN - GSC130361GA | 85 | 14 | Yes | Yes | 23.2 | 20.4 | 2.8 | C3042A69F27B4BBEB0D93E8B4AC8B066 |  | R22 | Non-TXV |  | 16.47% | 0.83529 | 31.65% | [5 empty] | Non-TXV | 16.47%
Auburn | CA | 95603-2705 |  | 2013-06-17 | 2013-06-17 14:44 | 2013-06-17 14:44 | RUUD - UAKA-030JAZ | 66 | 0 | Yes | Yes | 21.8 | 22.6 | -0.8 | 573D8937DA2B493B9021F2353AF11B95 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1513 |  | 2013-06-11 | 2013-06-11 13:40 | 2013-06-11 14:05 | ICP - GPCM030K060F | 68 | -4 | Yes | Yes | 19.9 | 18.8 | 1.1 | 54BFD42DF8004EFAB3E35142D7ACC2EC |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93703-1920 |  | 2013-06-25 | 2013-06-25 17:02 | 2013-06-25 17:18 | YORK - D3NZ024N05606NXA | 57 | 8.7 | Yes | Yes | 17.8 | 20.4 | -2.6 | 76A5C921A74D4A02AA6C23342B96D094 |  | R410A | Non-TXV |  | 15.26% | 0.84737 | 29.33% | [5 empty] | Non-TXV | 15.26%
Rocklin | CA | 95677-3116 |  | 2013-08-12 | 2013-08-12 08:46 | 2013-08-12 09:03 | TRANE - 2TTB0042A1000AA | 95 | -3.5 | Yes | Yes | 23 | 18.3 | 4.7 | F93AE3969B52414E95AF7CFC3BA7751A |  | R22 | TXV |  | -3.684% | 1.0368 | 1.032% |  |  |  |  | TXV |  |  | -3.684%
Gerber | CA | 96035-9700 |  | 2013-08-19 | 2013-08-19 14:13 | 2013-08-19 14:35 | COLEMAN - BRCOQ0361BD | 52 | 3.5 | Yes | Yes | 28 | 22 | 6 | 0D7DD554B8A341E89A54549A7D3A8D26 |  | R22 | Non-TXV |  | 6.731% | 0.93269 | 12.94% | [5 empty] | Non-TXV | 6.731%
Clovis | CA | 93611-3065 |  | 2013-06-13 | 2013-06-13 13:11 | 2013-06-13 13:47 | GOODMAN - N/A | 60 | 2.3 | Yes | Yes | 28.7 | 23.9 | 4.9 | 7EF8BCA869164F8684F37842DFA7FC3A |  | R22 | Non-TXV |  | 3.833% | 0.96167 | 7.367% | [5 empty] | Non-TXV | 3.833%
Livingston | CA | 95334-9545 |  | 2013-07-03 | 2013-07-03 08:16 | 2013-07-03 08:42 | DAY & NIGHT - 545AJ036 | 70 | 9.2 | Yes | Yes | 18.4 | 19.2 | -0.8 | 6F9F92B4362F439AAD648D9372F446D3 |  | R22 | Non-TXV |  | 13.14% | 0.86857 | 25.26% | [5 empty] | Non-TXV | 13.14%
Yuba City | CA | 95991-1540 |  | 2013-11-20 | 2013-11-20 10:02 | 2013-11-20 10:02 | CARRIER - UNK | 85 | 0 | Yes | Yes | 31 | 20.4 | 10.6 | 205A838074B142AE98CDA866E63A189F | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-6067 |  | 2013-07-01 | 2013-07-01 11:11 | 2013-07-01 11:35 | BRYANT - 550AN036-F | 85 | -10 | Yes | Yes | 18.5 | 20.2 | -1.7 | 6D6DEAC32D8443CC8D1F3F0C90A788ED |  | R410A | TXV |  | -11.76% | 1.1176 | 3.295% |  |  |  |  | TXV |  |  | -11.76%
Stockton | CA | 95205-3629 |  | 2013-07-10 | 2013-07-10 11:05 | 2013-07-10 11:39 | ICP - NAC036AKC3 | 94 | 24.2 | Yes | Yes | 22.5 | 23.7 | -1.2 | 2ADC782C757147EC96D505C6F0FAE03C |  | R22 | Non-TXV |  | 25.74% | 0.74255 | 49.48% | [5 empty] | Non-TXV | 25.74%
Newman | CA | 95360-1239 |  | 2013-06-05 | 2013-06-05 09:08 | 2013-06-05 09:30 | RUUD - UAND-042JAZ | 136 | 4.1 | Yes | Yes | 20.1 | 19.1 | 1 | 571A804E4C9D4315AE089F834CE7F6B8 |  | R22 | Non-TXV |  | 3.015% | 0.96985 | 5.794% | [5 empty] | Non-TXV | 3.015%
Newman | CA | 95360-1239 |  | 2013-06-05 | 2013-06-05 09:20 | 2013-06-05 09:58 | RUUD - UAND-024JAZ | 76 | 13.3 | Yes | Yes | 22.3 | 20.1 | 2.2 | E238AD73C1A0417197ED28C37AAD74B7 |  | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Merced | CA | 95340-3049 |  | 2013-07-01 | 2013-07-01 17:22 | 2013-07-01 17:24 | RHEEM - RRGC05N31JKR | 48 | 7.1 | Yes | Yes | 21.9 | 19.9 | 2 | 26A0376E108642529AA382CE1CAC368F |  | R22 | Non-TXV |  | 14.79% | 0.85208 | 28.43% | [5 empty] | Non-TXV | 14.79%
Stockton | CA | 95209-1351 |  | 2013-05-30 | 2013-05-30 10:54 | 2013-05-30 11:14 | COMFORT AIRE - N4A348AKB200 | 85 | 6.5 | Yes | Yes | 23.2 | 17.7 | 5.5 | BB6BF6C6E63B45C39FD74E872E2FF226 |  | R410A | TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | TXV | 7.647%
Stockton | CA | 95210-5331 |  | 2013-07-29 | 2013-07-29 12:51 | 2013-07-29 13:07 | BDP - 561CJ036--D | 100 | -9.4 | Yes | Yes | 17.8 | 17.4 | 0.4 | 482E7B7C83C84CCF9F166FD25258481E |  | R22 | TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | TXV |  |  | -9.4%
Yuba City | CA | 95993-5220 |  | 2013-06-07 | 2013-06-07 09:19 | 2013-06-07 09:40 | GOODMAN - CLJ48-1C | 130 | 12.1 | Yes | Yes | 3 | 18.8 | -15.8 | 880BEF75FEDA4EB0A518820EC5E15E0F |  | R22 | Non-TXV |  | 9.308% | 0.90692 | 17.89% | [5 empty] | Non-TXV | 9.308%
Atwater | CA | 95301-2666 |  | 2013-06-05 | 2013-06-05 14:11 | 2013-06-05 14:13 | CARRIER - 48GS042060301 | 100 | 5.2 | Yes | Yes | 24.9 | 20.1 | 4.8 | A6A453FBBADC4E1DA791D68FD5AA23EA |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Livingston | CA | 95334-9409 |  | 2013-06-10 | 2013-06-10 11:22 | 2013-06-10 11:43 | RHEEM - RRGF-05E36JKR | 75 | 6.3 | Yes | Yes | 20.4 | 19 | 1.4 | CD3EC6DEBADF42399DC1E1A8D4E5D3B0 |  | R22 | Non-TXV |  | 8.4% | 0.916 | 16.14% | [5 empty] | Non-TXV | 8.4%
Clovis | CA | 93611-2054 |  | 2013-06-13 | 2013-06-13 11:00 | 2013-06-13 21:25 | BRYANT - 582ANW036090AAAF | 56 | 3.5 | Yes | Yes | 23.1 | 23.4 | -0.3 | DD6E166A28C24332808B907D8E550827 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fresno | CA | 93703-4009 |  | 2013-06-25 | 2013-06-25 13:14 | 2013-06-25 13:30 | AMERICAN STANDARD - 4YCY400A1075AB | 96 | 2.9 | Yes | Yes | 17.7 | 19.5 | -1.8 | F2A85405BF8A4007A2351C42B217B635 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Atwater | CA | 95301-3740 |  | 2013-06-14 | 2013-06-14 15:43 | 2013-06-14 15:46 | GOODMAN - GPG13420701AB | 107 | 7 | Yes | Yes | 26.1 | 21.5 | 4.6 | 3AEB210C3EDD48278C197E8C4CAF4253 |  | R22 | Non-TXV |  | 6.542% | 0.93458 | 12.57% | [5 empty] | Non-TXV | 6.542%
Stockton | CA | 95210-5694 |  | 2013-05-29 | 2013-05-29 13:05 | 2013-05-29 13:27 | COLEMAN - BRCQ042C | 63 | 1.9 | Yes | Yes | 25.9 | 20.9 | 5 | FC9478B9E3154EB7A8D919D93421D4B8 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Fresno | CA | 93710-7114 |  | 2013-06-11 | 2013-06-11 11:49 | 2013-06-11 12:21 | GOODMAN - 9604074608 | 70 | 2.6 | Yes | Yes | 16.8 | 19.1 | -2.3 | 5BFF785632B64357966EF8D65EFF1E10 |  | R22 | Non-TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | Non-TXV | 3.714%
Stockton | CA | 95206-3138 |  | 2013-06-13 | 2013-06-13 09:05 | 2013-06-13 09:22 | RHEEM - UNK | 85 | 3.7 | Yes | Yes | 22.7 | 20.1 | 2.7 | B2C06106EC8843178BB47F1B8BE8CC06 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Stockton | CA | 95209-1313 |  | 2013-05-24 | 2013-05-24 12:08 | 2013-05-24 12:08 | PAYNE - PA13NA030-B | 57 | 0 | Yes | Yes | 17.9 | 20.6 | -2.7 | 120B298F521644C9876DA18334A402CB |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3736 |  | 2013-05-29 | 2013-05-29 15:49 | 2013-05-29 16:09 | HEIL - CA3030VKB1 | 66 | -3.9 | Yes | Yes | 18 | 20.4 | -2.4 | 9EAB1C83FAD54CF299A099AE06355894 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Fresno | CA | 93727-1953 |  | 2013-06-08 | 2013-06-08 13:07 | 2013-06-08 13:30 | CARRIER - 38TKB036300 | 83 | 18.3 | Yes | Yes | 22.2 | 21.7 | 0.5 | E157D6B1D6D1477E8878F26B161A2F78 |  | R22 | Non-TXV |  | 22.05% | 0.77952 | 42.37% | [5 empty] | Non-TXV | 22.05%
Stockton | CA | 95215-7420 |  | 2013-06-06 | 2013-06-06 13:48 | 2013-06-06 14:09 | GOODMAN - PGB030050-1A | 56 | 2.8 | Yes | Yes | 21.6 | 19.2 | 2.4 | 392A9D07584E4452BEAAC2066CF31459 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95219-4903 |  | 2013-06-25 | 2013-06-25 09:05 | 2013-06-25 09:22 | CARRIER - 591ANX036000AAAA | 85 | -7 | Yes | Yes | 21.5 | 17.1 | 4.4 | B019E9712F71484CA15EE37722022561 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Granite Bay | CA | 95746-9487 |  | 2013-06-21 | 2013-06-21 11:47 | 2013-06-21 12:12 | OTHER - UNK | 123 | 25.2 | Yes | Yes | 22.1 | 20.6 | 1.5 | 132FF46B4B074A38935AA3575577BC12 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 20.49% | 0.79512 | 39.37% | [5 empty] | Non-TXV | 20.49%
Stockton | CA | 95219-3518 |  | 2013-06-20 | 2013-06-20 09:41 | 2013-06-20 10:02 | AMANA - GSC130301AD | 117 | 12.6 | Yes | Yes | 19.8 | 18.8 | 1 | 2E881CFB6DC04963B1FD7099DF53465E |  | R22 | Non-TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | Non-TXV | 10.77%
Stockton | CA | 95206-6420 |  | 2013-06-19 | 2013-06-19 11:01 | 2013-06-19 11:20 | - 38BRC060360 | 202 | 23.1 | Yes | Yes | 18 | 18.8 | -0.8 | 05392FFABF60412FA56961D62A499180 |  | R22 | Non-TXV |  | 11.44% | 0.88564 | 21.98% | [5 empty] | Non-TXV | 11.44%
Cameron Park | CA | 95682-8601 |  | 2013-05-30 | 2013-05-30 13:44 | 2013-05-30 14:41 | GOODMAN - ASZ140481AE | 270 | 30.2 | Yes | Yes | 18.6 | 19.3 | -0.7 | 6F8A31AF321E4BDEA4EAAE33A5F59998 |  | R410A | TXV |  | 11.19% | 0.88815 | 21.5% | [5 empty] | TXV | 11.19%
Rocklin | CA | 95677-3123 |  | 2013-08-06 | 2013-08-06 10:58 | 2013-08-06 10:58 | DAY & NIGHT - UNK | 52 | 0 | Yes | Yes | 20.9 | 19.1 | 1.8 | 0E1D68E0600946418AD1241D4A738F5C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Gerber | CA | 96035-9785 |  | 2013-05-31 | 2013-05-31 20:52 | 2013-05-31 21:08 | OTHER - NA | 115 | 3.5 | Yes | Yes | 23.2 | 21 | 2.2 | A675DF25216C44898DAB6493B13D559D |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Auburn | CA | 95602-8930 |  | 2013-06-08 | 2013-06-08 09:57 | 2013-06-08 10:27 | CARRIER - 38CK0340 | 75 | 19.2 | Yes | Yes | 17 | 19.5 | -2.5 | DF9CBD661CFC4365AC80D9C0C8119CEE |  | R22 | Non-TXV |  | 25.6% | 0.744 | 49.2% | [5 empty] | Non-TXV | 25.6%
Stockton | CA | 95219-3937 |  | 2013-06-21 | 2013-06-21 09:51 | 2013-06-21 10:09 | PAYNE - PY3PNA030060NB | 98 | -8.1 | Yes | Yes | 24.2 | 19.3 | 4.9 | 20AAE5F49F6E41E1810E2913A5539459 |  | R22 | Non-TXV |  | -8.265% | 1.0827 | 2.315% |  |  |  |  | Non-TXV |  |  | -8.265%
Atwater | CA | 95301-4879 |  | 2013-08-14 | 2013-08-14 09:56 | 2013-08-14 10:18 | GOODMAN - CM30-1EB | 70 | 2.8 | Yes | Yes | 18.1 | 19.8 | -1.7 | 1C4104F4F54C45EAA28A40D9D52EDDB6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Dinuba | CA | 93618-1628 |  | 2013-07-29 | 2013-07-29 09:23 | 2013-07-29 10:11 | GOODMAN - GPG1336070M41DA | 70 | 2.6 | Yes | Yes | 18 | 20.7 | -2.7 | ECCDBC890C0E40F589ED449B90E90C5A | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | TXV | 3.714%
Dinuba | CA | 93618-2721 |  | 2013-06-20 | 2013-06-20 15:09 | 2013-06-20 15:25 | ICP - PGC036K060B | 71 | 3.5 | Yes | Yes | 22.4 | 22 | 0.4 | 540AEECD0B3E424CAF51C7A5A7933676 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.93% | 0.9507 | 9.474% | [5 empty] | Non-TXV | 4.93%
Stockton | CA | 95209-4032 |  | 2013-05-22 | 2013-05-22 11:15 | 2013-05-22 11:15 | DAY & NIGHT - 585J024075YACR | 67 | 0 | Yes | Yes | 27 | 20.6 | 6.4 | 141F2658B8374D36B8FC0558B32858E4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-3015 |  | 2013-08-08 | 2013-08-08 16:16 | 2013-08-08 17:27 | ICP - PGF324040K01A2 | 64 | 2.3 | Yes | Yes | 21.5 | 19.7 | 1.8 | 9DE5CD984A1042D68AF28F56011F6AAC |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Madera | CA | 93637-2959 |  | 2013-07-08 | 2013-07-08 12:22 | 2013-07-08 12:22 | GOODMAN - GPG1336070M41DA | 62 | 0 | Yes | Yes | 18 | 21 | -3 | C8FC30329FAC4A6689CA8E41F69BB3C5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-8988 |  | 2013-06-20 | 2013-06-20 11:19 | 2013-06-20 11:19 | CARRIER - 38QH030310 | 128 | 0 | Yes | Yes | 20.4 | 20.9 | -0.5 | 6282D4D3E7FF488894241E74EA23F115 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4812 |  | 2013-06-07 | 2013-06-07 10:44 | 2013-06-07 10:44 | PAYNE - PY3GNAA30060NA | 103 | 0 | Yes | Yes | 20.1 | 17.7 | 2.4 | 3885DE08AED14BB29D414468312A90BF |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3230 |  | 2013-06-11 | 2013-06-11 11:12 | 2013-06-11 11:35 | GOODMAN - PGB024050 | 54 | 1.7 | Yes | Yes | 22.5 | 20.5 | 2 | ADF8C096C1F74A1F97A0FEC0C10CF48E |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Stockton | CA | 95210-2130 |  | 2013-06-28 | 2013-06-28 11:52 | 2013-06-28 12:16 | NORDYNE - JS5BD-036KA | 110 | -6.5 | Yes | Yes | 23.9 | 17.9 | 6 | 6CD7C9BB34D542F8A3473560865F54BA |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
E Palo Alto | CA | 94303-1008 |  | 2013-10-14 | 2013-10-14 17:36 | 2013-10-14 17:54 | WEATHER KING - 13AJA36A01 | 108 | 3.2 | Yes | Yes | 19 | 20.7 | -1.7 | F1B6613D28DD45B6BA957B24EDAE15BF |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Clovis | CA | 93611-5951 |  | 2013-08-22 | 2013-08-22 09:16 | 2013-08-22 10:14 | BDP - 585HJW036060ABAF | 102 | 14.2 | Yes | Yes | 17.5 | 20.4 | -2.9 | 6D058358CEE64FAC9CABE334F539E24F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.92% | 0.86078 | 26.75% | [5 empty] | Non-TXV | 13.92%
Red Bluff | CA | 96080-9272 |  | 2013-05-30 | 2013-05-30 14:29 | 2013-05-30 21:50 | BRYANT - 1007E19454 | 130 | 0 | Yes | Yes | 25.6 | 22 | 3.6 | A3B3B03BEAF5489F9704BAF50CE2B842 | Add refrigerant: 3.8 oz | R410A | TXV |  | 0% | 1 | 0%
Pollock Pines | CA | 95726-9215 |  | 2013-07-29 | 2013-07-29 12:09 | 2013-07-29 12:09 | GIBSON - JS5BD-024K | 104 | 0 | Yes | Yes | 19 | 21.2 | -2.2 | 472D99418D36435AAE4767B2C94B5505 |  | R22 | TXV |  | 0% | 1 | 0%
Ione | CA | 95640-5415 |  | 2013-06-26 | 2013-06-26 14:49 | 2013-06-26 15:36 | PAYNE - PA12NA060-A | 184 | 13.4 | Yes | Yes | 14.2 | 17 | -2.8 | 6A23C3FB912241D1B28D30C171C6FA34 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.283% | 0.92717 | 14% | [5 empty] | Non-TXV | 7.283%
Marysville | CA | 95901-3331 |  | 2013-06-26 | 2013-06-26 08:32 | 2013-06-26 08:55 | LENNOX - HS26-042-2P | 104 | -12.2 | Yes | Yes | 19.5 | 19.3 | 0.3 | 55ACE885B99148A785D8F21B9D34EC0F |  | R22 | Non-TXV |  | -11.73% | 1.1173 | 3.285% |  |  |  |  | Non-TXV |  |  | -11.73%
Stockton | CA | 95215-1132 |  | 2013-06-20 | 2013-06-20 09:16 | 2013-06-20 09:54 | CARRIER - 38EN048320SM | 117 | 3.7 | Yes | Yes | 21.1 | 19.3 | 1.8 | 82393E5D63584855A21070FCB61D7711 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Gerber | CA | 96035-9742 |  | 2013-08-19 | 2013-08-19 14:06 | 2013-08-19 18:07 | COLEMAN - 6352-729 | 85 | 2.7 | Yes | Yes | 24.4 | 18.8 | 5.6 | D2E36760E29546A5949F1A7D603621AA |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Fresno | CA | 93727-7535 |  | 2013-06-19 | 2013-06-19 13:26 | 2013-06-19 13:28 | AMERICAN STANDARD - YCY048G1H0AC | 183 | 5.8 | Yes | Yes | 26.1 | 20.7 | 5.4 | CEA48044539C48C7B4E016839AD4CF01 |  | R22 | Non-TXV |  | 3.169% | 0.96831 | 6.091% | [5 empty] | Non-TXV | 3.169%
Stockton | CA | 95206-4720 |  | 2013-06-18 | 2013-06-18 08:46 | 2013-06-18 09:08 | RHEEM - RAHE-042JAS | 85 | 4.8 | Yes | Yes | 25.3 | 19.4 | 5.9 | 7363703DE1284F67AB6647CE75CC2E59 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Oroville | CA | 95966-3951 |  | 2013-06-19 | 2013-06-19 10:43 | 2013-06-19 12:25 | CARRIER - 38YXAO42320 | 138 | 4.2 | Yes | Yes | 35 | 20.4 | 14.6 | 64705AB365954C0A8A051E7E5CA04E84 |  | R410A | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Olivehurst | CA | 95961-7505 |  | 2013-08-30 | 2013-08-30 14:27 | 2013-08-30 14:52 | OTHER - UNK | 64 | 2.7 | Yes | Yes | 23.6 | 20.5 | 3.1 | C5E79A9504FE49069B7124BA22ABAE90 |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Stockton | CA | 95206-6251 |  | 2013-07-26 | 2013-07-26 16:12 | 2013-07-26 16:50 | GOODMAN - CKJ42-1D | 99 | -11.1 | Yes | Yes | 18.8 | 14.4 | 4.4 | 094B66BF12CB4DA3A9982B8CAF86830A |  | R22 | Non-TXV |  | -11.21% | 1.1121 | 3.14% |  |  |  |  | Non-TXV |  |  | -11.21%
Los Banos | CA | 93635-3312 |  | 2013-05-30 | 2013-05-30 12:04 | 2013-05-30 12:07 | BDP - 585CJ036075 | 84 | 8.3 | Yes | Yes | 21 | 19.9 | 1.1 | 0C19FC74EA6C45B58A1F464357930FAF |  | R22 | Non-TXV |  | 9.881% | 0.90119 | 18.99% | [5 empty] | Non-TXV | 9.881%
Red Bluff | CA | 96080-9348 |  | 2013-06-01 | 2013-06-01 09:55 | 2013-06-01 10:24 | BRYANT - PA12NA060-A | 181 | 7.5 | Yes | Yes | 25.4 | 21 | 4.4 | B2392B4E204F4E2CB52FD943958F1AEE |  | R22 | TXV |  | 4.144% | 0.95856 | 7.963% | [5 empty] | TXV | 4.144%
Stockton | CA | 95205-6344 |  | 2013-07-18 | 2013-07-18 13:01 | 2013-07-18 13:25 | GOODMAN - PGB036075-1A | 60 | 5.3 | Yes | Yes | 21.1 | 21 | 0.1 | 1A2FECEF2E8B4E8FA0553795388CE804 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.833% | 0.91167 | 16.98% | [5 empty] | Non-TXV | 8.833%
Fresno | CA | 93727-5067 |  | 2013-06-14 | 2013-06-14 11:10 | 2013-06-14 11:12 | GOODMAN - PGB042075-1 | 68 | 0 | Yes | Yes | 17.3 | 21.5 | -4.2 | 5F6B9EDEA8F449ECBEA4C643CBBEF6E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-9513 |  | 2013-05-29 | 2013-05-29 11:59 | 2013-05-29 12:25 | TRANE - TTR036C100A1 | 92 | 13.9 | Yes | Yes | 19 | 20.4 | -1.4 | BEB328459C2949B0AE63D725F8C85626 |  | R22 | Non-TXV |  | 15.11% | 0.84891 | 29.04% | [5 empty] | Non-TXV | 15.11%
Los Banos | CA | 93635-5305 |  | 2013-07-29 | 2013-07-29 12:47 | 2013-07-29 12:54 | GOODMAN - CK42-1B | 92 | 2.9 | Yes | Yes | 15.5 | 18.2 | -2.7 | CDC4B028678644789B072D130BD16F2D |  | R22 | Non-TXV |  | 3.152% | 0.96848 | 6.058% | [5 empty] | Non-TXV | 3.152%
Rocklin | CA | 95677-2541 |  | 2013-06-11 | 2013-06-11 15:57 | 2013-06-11 15:57 | PAYNE - 567J018RCU | 37 | 0 | Yes | Yes | 26 | 20.2 | 5.8 | 64FF4B431E5645D7AC28EC7DA3F11E2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-3450 |  | 2013-06-04 | 2013-06-04 08:47 | 2013-06-04 09:04 | TRANE - YCC018F1L0BJ | 56 | 2.9 | Yes | Yes | 16.9 | 18.3 | -1.4 | 33BA5CEE40D5429C8FE9D2D93557CB59 |  | R22 | Non-TXV |  | 5.179% | 0.94821 | 9.952% | [5 empty] | Non-TXV | 5.179%
Los Banos | CA | 93635-3162 |  | 2013-06-13 | 2013-06-13 12:17 | 2013-06-13 12:27 | BDP - 587ANZ030060AAAE | 67 | 7.6 | Yes | Yes | 21.1 | 18.3 | 2.8 | 72A839D380B34AAB846D1386F2D25A39 |  | R22 | Non-TXV |  | 11.34% | 0.88657 | 21.8% | [5 empty] | Non-TXV | 11.34%
Marysville | CA | 95901-4047 |  | 2013-06-04 | 2013-06-04 13:57 | 2013-06-04 14:22 | GOODMAN - GSH13018AC | 127 | 4.6 | Yes | Yes | 15 | 17.7 | -2.7 | 042B45CCC77F40259714B92F63F6078E |  | R22 | Non-TXV |  | 3.622% | 0.96378 | 6.961% | [5 empty] | Non-TXV | 3.622%
Paso Robles | CA | 93446-2053 |  | 2013-08-05 | 2013-08-05 13:51 | 2013-08-05 14:17 | DAY & NIGHT - 562GJXO4803938A | 115 | 3.9 | Yes | Yes | 21.7 | 20.2 | 1.5 | 4E262DA5BBEF4EE8867047DCB29A4E76 |  | R22 | Non-TXV |  | 3.391% | 0.96609 | 6.517% | [5 empty] | Non-TXV | 3.391%
Clovis | CA | 93611-2080 |  | 2013-08-06 | 2013-08-06 09:05 | 2013-08-06 09:10 | LENNOX - GCS29030752PA | 51 | 4.7 | Yes | Yes | 25 | 19.9 | 5.1 | F51E5E55EAB847659E52DB8494422749 |  | R22 | Non-TXV |  | 9.216% | 0.90784 | 17.71% | [5 empty] | Non-TXV | 9.216%
Vina | CA | 96092-0000 |  | 2013-10-25 | 2013-10-25 15:45 | 2013-10-25 16:05 | TEMPSTAR - PGCO42K080B | 87 | 6.6 | Yes | Yes | 19.3 | 22.2 | -2.9 | 0CEDA0A935734D5BA3EB0888ADB1B9C8 |  | R22 | Non-TXV |  | 7.586% | 0.92414 | 14.58% | [5 empty] | Non-TXV | 7.586%
Stockton | CA | 95203-1738 |  | 2013-07-29 | 2013-07-29 09:59 | 2013-07-29 10:18 | YORK - H2RA036S06E | 63 | 11.2 | Yes | Yes | 24 | 18.7 | 5.3 | C28145A221DB43019383B33788C3D992 |  | R22 | Non-TXV |  | 17.78% | 0.82222 | 34.16% | [5 empty] | Non-TXV | 17.78%
Manteca | CA | 95336-6909 |  | 2013-05-28 | 2013-05-28 13:43 | 2013-05-28 14:01 | BRYANT - 577CNWA30060NA-- | 86 | 3.2 | Yes | Yes | 17.7 | 19.3 | -1.6 | F55FF676C96B4DABBCC7C7E84B3648AC |  | R410A | TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | TXV | 3.721%
Lincoln | CA | 95648-8141 |  | 2013-06-03 | 2013-06-03 18:04 | 2013-06-03 18:39 | YORK - H2RC024S06G | 71 | 3.3 | Yes | Yes | 15.9 | 18.7 | -2.8 | C661DEF970F64F2D92890A2D9DC4DB6A |  | R22 | TXV |  | 4.648% | 0.95352 | 8.932% | [5 empty] | TXV | 4.648%
Stockton | CA | 95210-6707 |  | 2013-05-28 | 2013-05-28 10:16 | 2013-05-28 10:16 | GOODMAN - CJ30-1FB | 110 | 0 | Yes | Yes | 21.4 | 18.2 | 3.2 | 95F6C653E8F641898807BCF4A00AD8A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-5221 |  | 2013-05-31 | 2013-05-31 09:37 | 2013-05-31 10:07 | LENNOX - HS26-048-5P | 111 | 5.2 | Yes | Yes | 19.4 | 19.9 | -0.5 | 69BA423F3C454B51ABD2581F08E802DA |  | R22 | TXV |  | 4.685% | 0.95315 | 9.003% | [5 empty] | TXV | 4.685%
Dinuba | CA | 93618-3082 |  | 2013-07-25 | 2013-07-25 17:26 | 2013-07-25 18:10 | RHEEM - RRL-B024JK06X | 77 | 5 | Yes | Yes | 16.8 | 19.3 | -2.5 | E6DDF6D4875F4C048328C684F8D51178 |  | R410A | TXV |  | 6.494% | 0.93506 | 12.48% | [5 empty] | TXV | 6.494%
Stockton | CA | 95210-4437 |  | 2013-05-29 | 2013-05-29 10:16 | 2013-05-29 10:16 | PAYNE - 591ANX030000ABAA | 68 | 0 | Yes | Yes | 20.9 | 17.6 | 3.3 | 6498FD48040A43E18DA589625B46EFCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-1803 |  | 2013-06-20 | 2013-06-20 12:23 | 2013-06-20 12:50 | GOODMAN - CK36-1A | 66 | 4.8 | Yes | Yes | 18 | 20.4 | -2.4 | 57CA4CAAFC564A8F8F4CE5E57E771963 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Dinuba | CA | 93618-3015 |  | 2013-06-21 | 2013-06-21 13:21 | 2013-06-21 14:08 | ICP - PGF024K060A | 58 | 5.8 | Yes | Yes | 17.2 | 20.1 | -2.9 | 64B784F3525E437FAE2AD947B579D478 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95212-2897 |  | 2013-06-12 | 2013-06-12 13:29 | 2013-06-12 14:05 | CARRIER - 38CKC048360 | 97 | 3.1 | Yes | Yes | 20.7 | 21.4 | -0.7 | 9D28771D00F9449EAF543F66BA9277DE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.196% | 0.96804 | 6.142% | [5 empty] | Non-TXV | 3.196%
Fresno | CA | 93727-5427 |  | 2013-06-18 | 2013-06-18 10:31 | 2013-06-18 10:34 | BRYANT - 561CJ048-A | 104 | 6.5 | Yes | Yes | 21.4 | 19.9 | 1.5 | 900286154CE6456391AA6D598499E846 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Stockton | CA | 95210-2052 |  | 2013-06-13 | 2013-06-13 10:26 | 2013-06-13 10:51 | DAY & NIGHT - 585A030080YAC | 50 | -2.9 | Yes | Yes | 26.7 | 20.9 | 5.8 | 3953053ECB084EC695BC82D26FDD67F3 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Dinuba | CA | 93618-1803 |  | 2013-07-25 | 2013-07-25 16:46 | 2013-07-25 22:03 | ICP - HAC236AKA1 | 113 | 4 | Yes | Yes | 22.7 | 18.4 | 4.3 | 83AD84F6811347ABBC9106DF68523A77 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.54% | 0.9646 | 6.803% | [5 empty] | Non-TXV | 3.54%
Fresno | CA | 93703-2808 |  | 2013-07-01 | 2013-07-01 09:45 | 2013-07-01 09:47 | WEATHER KING - WKMAA048JK08E | 176 | 16.8 | Yes | Yes | 24.6 | 20.1 | 4.5 | 065776F901AB4CED951DA736CBAF6086 |  | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Stockton | CA | 95207-6004 |  | 2013-06-04 | 2013-06-04 11:52 | 2013-06-04 11:58 | GOODMAN - PGB030075-1-REVA | 56 | 6.6 | Yes | Yes | 22.3 | 17.7 | 4.6 | 6AA6E03ADFFA4785BF638DD3B725114C |  | R22 | Non-TXV |  | 11.79% | 0.88214 | 22.65% | [5 empty] | Non-TXV | 11.79%
Forest Ranch | CA | 95942-0000 |  | 2013-09-10 | 2013-09-10 09:49 | 2013-09-10 10:14 | AMERICAN STANDARD - YCPO48F1H0AC | 166 | 5.5 | Yes | Yes | 18.3 | 21 | -2.7 | 1CCB82173DB242C89F3897C95D1D4872 |  | R22 | Non-TXV |  | 3.313% | 0.96687 | 6.367% | [5 empty] | Non-TXV | 3.313%
Lincoln | CA | 95648-3240 |  | 2013-05-31 | 2013-05-31 13:29 | 2013-05-31 13:48 | CARRIER - 24ABA348310 | 121 | 4.4 | Yes | Yes | 16.6 | 19.6 | -3 | AF144C9E98BF4BC195A03136D9E9D24D |  | R410A | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Los Banos | CA | 93635-8545 |  | 2013-06-03 | 2013-06-03 15:23 | 2013-06-03 15:31 | GOODMAN - CRT481 | 145 | 6.2 | Yes | Yes | 21.6 | 20.6 | 1 | E3445126092C4329A38028B06E0576CD |  | R22 | Non-TXV |  | 4.276% | 0.95724 | 8.217% | [5 empty] | Non-TXV | 4.276%
Atwater | CA | 95301-2619 |  | 2013-06-26 | 2013-06-26 17:13 | 2013-06-26 17:20 | - D1NA042N05606C | 76 | 6.8 | Yes | Yes | 26.4 | 21.3 | 5.1 | 0B98521491E84718B9B7C8E0839E69D4 |  | R22 | Non-TXV |  | 8.947% | 0.91053 | 17.19% | [5 empty] | Non-TXV | 8.947%
Stockton | CA | 95206-1551 |  | 2013-06-10 | 2013-06-10 13:19 | 2013-06-10 13:41 | WESTINGHOUSE - ES4BD-030KB | 85 | 7.4 | Yes | Yes | 20.8 | 17 | 3.8 | E134BAC03E594DAEAFE95145E1F4A08D |  | R410A | TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | TXV | 8.706%
Ione | CA | 95640-9661 |  | 2013-08-01 | 2013-08-01 17:36 | 2013-08-01 17:36 | TEMPSTAR - 867 815034 | 53 | 0 | Yes | Yes | 28 | 23.1 | 4.9 | 5F71E8BD7DE14D8B93E70DFBC1710614 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-1492 |  | 2013-07-01 | 2013-07-01 10:38 | 2013-07-01 11:07 | AMERICAN STANDARD - YCP042F1M0AA | 128 | 4.4 | Yes | Yes | 20.5 | 21 | -0.5 | C11D168946504BD6B5EAEAC46E669F8A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Newman | CA | 95360-9605 |  | 2013-06-05 | 2013-06-05 12:46 | 2013-06-05 13:16 | RUUD - UNK | 64 | 2.6 | Yes | Yes | 19.3 | 19.9 | -0.5 | 65C71B93B3EF4C239561FDCBFEA5176E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Tehama | CA | 96090-0000 |  | 2013-09-11 | 2013-09-11 12:13 | 2013-09-11 12:35 | BRYANT - 601ANX036000AAAF | 113 | 3.4 | Yes | Yes | 18.7 | 21.3 | -2.6 | E0C8A963E0154F57A442EF58A78D097A |  | R22 | Non-TXV |  | 3.009% | 0.96991 | 5.782% | [5 empty] | Non-TXV | 3.009%
Los Banos | CA | 93635-2943 |  | 2013-06-13 | 2013-06-13 12:49 | 2013-06-13 12:54 | RUUD - UAFD048JBS | 101 | 14.8 | Yes | Yes | 19.3 | 17.6 | 1.7 | D68525D801344B16A55332A8B07B0904 |  | R22 | Non-TXV |  | 14.65% | 0.85347 | 28.16% | [5 empty] | Non-TXV | 14.65%
Rocklin | CA | 95677-3507 |  | 2013-06-17 | 2013-06-17 11:55 | 2013-06-17 12:18 | CARRIER - 38EN018310 | 55 | 1.6 | Yes | Yes | 16 | 17.7 | -1.7 | 585FF493DF4F4E3F8171F2BB95280C97 |  | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Stockton | CA | 95212-3831 |  | 2013-06-18 | 2013-06-18 13:55 | 2013-06-18 14:20 | YORK - H2RC036S06G | 83 | 5.3 | Yes | Yes | 18.5 | 20.4 | -1.9 | BFCAE3644C2D490A8FD93A1178555ADC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.386% | 0.93614 | 12.27% | [5 empty] | Non-TXV | 6.386%
Gustine | CA | 95322-9599 |  | 2013-10-09 | 2013-10-09 14:35 | 2013-10-09 14:36 | YORK - H1RA042S06D | 84 | 10.7 | Yes | Yes | 20.5 | 17.1 | 3.4 | BC8DE1BFB98B436EB7B241EF205D000A |  | R22 | Non-TXV |  | 12.74% | 0.87262 | 24.48% | [5 empty] | Non-TXV | 12.74%
Gustine | CA | 95322-9599 |  | 2013-10-09 | 2013-10-09 15:07 | 2013-10-09 15:08 | YORK - H1RA042S06D | 84 | 7.1 | Yes | Yes | 16.7 | 18.2 | -1.5 | 0628FD81CED74FE4A2C30497174BCBD5 |  | R22 | Non-TXV |  | 8.452% | 0.91548 | 16.24% | [5 empty] | Non-TXV | 8.452%
Magalia | CA | 95954-9207 |  | 2013-07-17 | 2013-07-17 15:18 | 2013-07-17 15:55 | RUUD - RKMA-A060JL10E | 184 | 6 | Yes | Yes | 20 | 20.2 | -0.1 | F7AC71C9A0BE41318A2A562EDCBBAFE8 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Clovis | CA | 93611-5221 |  | 2013-06-19 | 2013-06-19 17:04 | 2013-06-19 17:14 | BDP - 585GJW042060ABAF | 84 | 3.3 | Yes | Yes | 26.1 | 22.5 | 3.6 | 2C0A2C1F927542588E142CC91F76A1C7 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Auburn | CA | 95603-6059 |  | 2013-06-28 | 2013-06-28 10:13 | 2013-06-28 10:33 | RUUD - UAPC-060JAZ | 296 | -25.1 | Yes | Yes | 18.8 | 19.8 | -1 | DEAD5919B55841F6A739283877FD5705 |  | R22 | TXV |  | -8.48% | 1.0848 | 2.375% |  |  |  |  | TXV |  |  | -8.48%
Auburn | CA | 95603-6059 |  | 2013-06-28 | 2013-06-28 10:37 | 2013-06-28 10:37 | RUUD - UAPC-060JAZ | 296 | 0 | Yes | Yes | 19.1 | 19.2 | -0.1 | 039A8BDA17E747C59EAB10E85157CCA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6098 |  | 2013-06-19 | 2013-06-19 12:18 | 2013-06-19 12:34 | GOODMAN - CLJ48-1A | 130 | 9.2 | Yes | Yes | 23.7 | 19.4 | 4.3 | C327CC0F9ED641E4A32E82650F30355D |  | R22 | TXV |  | 7.077% | 0.92923 | 13.6% | [5 empty] | TXV | 7.077%
Stockton | CA | 95209-5187 |  | 2013-06-10 | 2013-06-10 12:30 | 2013-06-10 12:30 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 24.7 | 19.9 | 4.9 | F002796759E847EF92E7787F1A4BD93C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3675 |  | 2013-06-05 | 2013-06-05 10:05 | 2013-06-05 10:23 | PAYNE - 591ANX036000AAAA | 86 | 3 | Yes | Yes | 20.6 | 18.8 | 1.8 | DA97234AD31C4C5986682E1600394BDB |  | R22 | Non-TXV |  | 3.488% | 0.96512 | 6.704% | [5 empty] | Non-TXV | 3.488%
Red Bluff | CA | 96080-9757 |  | 2013-05-31 | 2013-05-31 21:03 | 2013-05-31 21:03 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 22.4 | 21.5 | 0.9 | 89941ACD794D4A8E91A8E43EF9540FB4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-9629 |  | 2013-07-09 | 2013-07-09 14:27 | 2013-07-09 14:31 | OTHER - FS5BD-036K | 114 | 3.8 | Yes | Yes | 21.4 | 20.4 | 1 | C00F403FE04E4333B6556869166B14A2 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95210-2050 |  | 2013-06-12 | 2013-06-12 11:27 | 2013-06-12 11:27 | BDP - 585A030080YAC | 66 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | 16C3231697DD4176A20CADD4D4DFA0EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3107 |  | 2013-05-31 | 2013-05-31 11:44 | 2013-05-31 12:09 | RHEEM - UNK | 64 | 7.1 | Yes | Yes | 22.9 | 18.3 | 4.6 | F3B7CA5CC1BE43A6A5E03C1A0FF7B724 |  | R22 | Non-TXV |  | 11.09% | 0.88906 | 21.32% | [5 empty] | Non-TXV | 11.09%
Stockton | CA | 95212-2112 |  | 2013-08-17 | 2013-08-17 12:32 | 2013-08-17 12:50 | YORK - TCGD36S21S2HA | 63 | 3.5 | Yes | Yes | 24.7 | 18.8 | 5.9 | 78108AC26BF74FC68B941E7734AEBD7A |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Yuba City | CA | 95993-3554 |  | 2013-09-06 | 2013-09-06 13:38 | 2013-09-06 14:02 | DAY & NIGHT - 545AJ036 | 147 | 5.5 | Yes | Yes | 21 | 20.6 | 0.4 | 0453CD5C5DB74EE089270B6403AA6894 |  | R22 | Non-TXV |  | 3.741% | 0.96259 | 7.19% | [5 empty] | Non-TXV | 3.741%
Sanger | CA | 93657-3908 |  | 2013-08-07 | 2013-08-07 13:20 | 2013-08-07 14:07 | ICP - NAC024AKC3 | 71 | 2.4 | Yes | Yes | 20 | 18.8 | 1.2 | CC72DCF3A73A4766A2373C4EFC230ABA |  | R22 | Non-TXV |  | 3.38% | 0.9662 | 6.496% | [5 empty] | Non-TXV | 3.38%
Lincoln | CA | 95648-1598 |  | 2013-05-23 | 2013-05-23 15:46 | 2013-05-23 16:05 | RHEEM - RAFD-031JAS | 64 | 12.6 | Yes | Yes | 17.1 | 19.9 | -2.8 | 55F528FDD9574E139B15BECD4770C74D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.69% | 0.80312 | 37.84% | [5 empty] | Non-TXV | 19.69%
Stockton | CA | 95212-3838 |  | 2013-06-18 | 2013-06-18 14:34 | 2013-06-18 14:58 | CARRIER - 38CKC060370 | 131 | 4 | Yes | Yes | 18.7 | 20.2 | -1.5 | AA121EFA6DBD4A6984EABD6F5FF03B41 |  | R22 | Non-TXV |  | 3.053% | 0.96947 | 5.868% | [5 empty] | Non-TXV | 3.053%
Yuba City | CA | 95991-6541 |  | 2013-05-24 | 2013-05-24 15:20 | 2013-05-24 15:49 | PAYNE - 567C030C0 | 85 | 17.2 | Yes | Yes | 17 | 19.1 | -2.1 | 6398748647154CBCBABB42C9EE7AC466 |  | R22 | Non-TXV |  | 20.24% | 0.79765 | 38.89% | [5 empty] | Non-TXV | 20.24%
Fresno | CA | 93711-6021 |  | 2013-06-24 | 2013-06-24 10:46 | 2013-06-24 11:05 | YORK - D1NA036N05606C | 68 | 2.2 | Yes | Yes | 17.5 | 19.3 | -1.8 | 03DB3F645A7245B7B5ADF0DEEC70CCAF |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Clovis | CA | 93611-1433 |  | 2013-06-12 | 2013-06-12 14:09 | 2013-06-12 14:28 | YORK - D1NH048N0906C | 128 | 4 | Yes | Yes | 18.6 | 17 | 1.6 | D0A5D31DD19248F986C5AB2035CEE0B6 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Manteca | CA | 95336-6919 |  | 2013-05-28 | 2013-05-28 12:38 | 2013-05-28 13:11 | BDP - 585GJW030040 | 58 | 2.5 | Yes | Yes | 17.4 | 18.8 | -1.4 | ED6AA4522BC04E178D326C2CA0B442A9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.31% | 0.9569 | 8.284% | [5 empty] | Non-TXV | 4.31%
Fresno | CA | 93703-1561 |  | 2013-05-29 | 2013-05-29 13:05 | 2013-05-29 13:05 | OTHER - D1NH048N09006C | 130 | 4.1 | Yes | Yes | 18.5 | 19 | -0.5 | 3CEF6FFD500448A3871AFBA6814151D2 | Add refrigerant: 4.1 oz | R22 | Non-TXV |  | 3.154% | 0.96846 | 6.061% | [5 empty] | Non-TXV | 3.154%
Fresno | CA | 93727-1958 |  | 2013-06-08 | 2013-06-08 13:46 | 2013-06-08 13:59 | RUUD - N/A | 90 | 4.8 | Yes | Yes | 20.4 | 21 | -0.6 | 1B512ADC28B04D88AAB63AF3677852D7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Fresno | CA | 93710-5372 |  | 2013-07-23 | 2013-07-23 08:20 | 2013-07-23 08:22 | BDP - 585HJW024040ABAE | 68 | 9.5 | Yes | Yes | 24 | 21.4 | 2.6 | 0041548F50AE4662AE9F0A7C0BDF8813 |  | R22 | Non-TXV |  | 13.97% | 0.86029 | 26.85% | [5 empty] | Non-TXV | 13.97%
Colfax | CA | 95713-9003 |  | 2013-07-25 | 2013-07-25 10:54 | 2013-07-25 10:54 | TRANE - TTR042C100A0 | 110 | 0 | Yes | Yes | 21 | 20.6 | 0.4 | BE065F5CD144499B988389A32DCB8252 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-8813 |  | 2013-05-31 | 2013-05-31 09:57 | 2013-05-31 10:29 | YORK - H2RA036S06E | 63 | 12.4 | Yes | Yes | 22.3 | 19.8 | 2.5 | B9F70CBA923245A78CE46B5EA16DC8C2 |  | R22 | Non-TXV |  | 19.68% | 0.80317 | 37.83% | [5 empty] | Non-TXV | 19.68%
Fresno | CA | 93703-1103 |  | 2013-05-28 | 2013-05-28 23:00 | 2013-05-28 23:51 | OTHER - DCYZ-F036N07OA | 85 | 2.7 | Yes | Yes | 20.4 | 20.4 | 0 | 5CFFF7A0C2E94D4D96E1FAE146356010 |  | R410A | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Cameron Park | CA | 95682-7818 |  | 2013-05-30 | 2013-05-30 15:05 | 2013-05-30 15:05 | OTHER - DAGA-048JA | 132 | 0 | Yes | Yes | 18.1 | 19.1 | -1 | D47F06A71E074E91B57090CF424B0F1C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6341 |  | 2013-07-19 | 2013-07-19 12:25 | 2013-07-19 12:44 | GOODMAN - CLJ42-1A | 99 | 4.3 | Yes | Yes | 21 | 18.5 | 2.5 | B9E3DE6D047946759A923703D87BC5FF |  | R22 | Non-TXV |  | 4.343% | 0.95657 | 8.347% | [5 empty] | Non-TXV | 4.343%
Clovis | CA | 93611-3135 |  | 2013-08-06 | 2013-08-06 10:08 | 2013-08-06 10:09 | BRYANT - 582ANW042060AAAG | 100 | 8.5 | Yes | Yes | 24.4 | 21.5 | 2.9 | 60B19CF553FD4BBBB9A4D6EBD9064C97 |  | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Lincoln | CA | 95648-7605 |  | 2013-07-13 | 2013-07-13 15:47 | 2013-07-13 16:08 | CARRIER - UNK | 195 | 5.8 | Yes | Yes | 17 | 18.1 | -1.1 | 8AB844EE01614B0C9704F98D1BEDCB2A |  | R22 | Non-TXV |  | 2.974% | 0.97026 | 5.716% | [5 empty] | Non-TXV | 2.974%
Fresno | CA | 93727-7219 |  | 2013-06-14 | 2013-06-14 14:07 | 2013-06-14 14:09 | GOODMAN - GPG13300451AB | 77 | 3.1 | Yes | Yes | 21.2 | 20.1 | 1.1 | 8654E52C919B454C9170898C08993F18 |  | R22 | Non-TXV |  | 4.026% | 0.95974 | 7.737% | [5 empty] | Non-TXV | 4.026%
Clovis | CA | 93611-3158 |  | 2013-06-13 | 2013-06-13 14:33 | 2013-06-13 15:04 | BRYANT - 583ANE030060AAAD | 68 | 3 | Yes | Yes | 18.5 | 20.6 | -2.1 | 767BB2E5497D48DB8285F3A642590CCA |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Riverbank | CA | 95367-3853 |  | 2013-06-03 | 2013-06-03 11:29 | 2013-06-03 11:52 | CARRIER - 38BRB036310 | 114 | 3.5 | Yes | Yes | 25.9 | 21 | 4.9 | 0FF8F9977DA7405C9803FA133CEB328B |  | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
Tracy | CA | 95376-3194 |  | 2013-06-05 | 2013-06-05 12:53 | 2013-06-05 13:15 | YORK - H1DA024S06A | 65 | 3.3 | Yes | Yes | 27.3 | 21.3 | 6 | 80CC2DFBC48342C1BB14C683311B99E2 |  | R22 | Non-TXV |  | 5.077% | 0.94923 | 9.757% | [5 empty] | Non-TXV | 5.077%
Magalia | CA | 95954-9393 |  | 2013-07-19 | 2013-07-19 12:35 | 2013-07-19 13:17 | CARRIER - 50N0030300 | 103 | 3.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | 4FF72687C553439B881A8118C1C2C639 |  | R22 | Non-TXV |  | 3.301% | 0.96699 | 6.344% | [5 empty] | Non-TXV | 3.301%
Clovis | CA | 93611-3124 |  | 2013-06-13 | 2013-06-13 15:07 | 2013-06-13 15:30 | AMERICAN STANDARD - YCY060G1M0AD | 151 | 4.6 | Yes | Yes | 27.8 | 22.6 | 5.2 | EA739126884946AFAC96BFB5C7A270F6 |  | R22 | Non-TXV |  | 3.046% | 0.96954 | 5.854% | [5 empty] | Non-TXV | 3.046%
Stockton | CA | 95210-2046 |  | 2013-06-12 | 2013-06-12 10:30 | 2013-06-12 10:49 | DAY & NIGHT - 585A030080YAC | 50 | 1.7 | Yes | Yes | 18 | 19.9 | -1.9 | C8108575FD514528AD02EF6731233159 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Fresno | CA | 93703-3713 |  | 2013-06-06 | 2013-06-06 12:42 | 2013-06-06 12:42 | WHIRLPOOL - D1NP06006A | 142 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | 3A6AE32E8A6D41CA9F27397D0696E83C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3228 |  | 2013-06-03 | 2013-06-03 09:59 | 2013-06-03 10:26 | CARRIER - 38TK036300 | 117 | 15.5 | Yes | Yes | 18 | 19.7 | -1.7 | EE531E41FF2F4A038C41D74D449408A2 |  | R22 | Non-TXV |  | 13.25% | 0.86752 | 25.46% | [5 empty] | Non-TXV | 13.25%
Oakdale | CA | 95361-3228 |  | 2013-06-03 | 2013-06-03 10:30 | 2013-06-03 10:49 | PAYNE - PA10JA024-A | 67 | 2.1 | Yes | Yes | 20.8 | 20.4 | 0.4 | 7B2D2A0A99214DA988C44AEEB0326165 |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Fresno | CA | 93703-2427 |  | 2013-05-31 | 2013-05-31 11:57 | 2013-05-31 12:15 | YORK - D2NP036N05606A | 85 | 6 | Yes | Yes | 22 | 20.7 | 1.3 | 5406F7A9D0CD4DAE8C68678404695E01 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Atwater | CA | 95301-4892 |  | 2013-06-11 | 2013-06-11 14:19 | 2013-06-11 14:21 | RHEEM - RAFA-30JA0 | 59 | 5 | Yes | Yes | 15.3 | 18.2 | -2.9 | 75EAA6DDBBDD4CE98A75E8660EB18D29 |  | R22 | Non-TXV |  | 8.475% | 0.91525 | 16.29% | [5 empty] | Non-TXV | 8.475%
Tracy | CA | 95377-7211 |  | 2013-05-30 | 2013-05-30 12:04 | 2013-05-30 12:40 | CARRIER - 38CK042350 | 93 | 4.5 | Yes | Yes | 24.5 | 21 | 3.5 | B78A0B7F0C6B43D4A7E6935F1EDE46B3 |  | R22 | Non-TXV |  | 4.839% | 0.95161 | 9.299% | [5 empty] | Non-TXV | 4.839%
Clovis | CA | 93611-3136 |  | 2013-06-26 | 2013-06-26 11:41 | 2013-06-26 12:06 | PAYNE - PY3GNAA48090NA | 100 | 3.6 | Yes | Yes | 19.7 | 19.5 | 0.2 | 3C5DCE34A8F748B9B2BB6D26116DFDB6 |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Tracy | CA | 95376-0754 |  | 2013-05-28 | 2013-05-28 10:25 | 2013-05-28 11:02 | DAY & NIGHT - 561AJ024-E | 124 | 10.9 | Yes | Yes | 20.7 | 18.8 | 1.9 | 091372FB753B4C86911ED0430AF8D2BA |  | R22 | Non-TXV |  | 8.79% | 0.9121 | 16.89% | [5 empty] | Non-TXV | 8.79%
Oroville | CA | 95965-9679 |  | 2013-06-19 | 2013-06-19 18:23 | 2013-06-19 18:39 | GOODMAN - 6SC130301DA | 87 | 12.2 | Yes | Yes | 24 | 20.4 | 3.6 | 23CF9BF89CD9428F8F60627DFAC79151 |  | R22 | Non-TXV |  | 14.02% | 0.85977 | 26.95% | [5 empty] | Non-TXV | 14.02%
Clovis | CA | 93611-5153 |  | 2013-06-14 | 2013-06-14 12:54 | 2013-06-14 13:10 | BDP - 585EJW036075ABAF | 82 | 2.7 | Yes | Yes | 20.5 | 19.7 | 0.8 | 78792625A4EE4627B4C51D1D06F29C87 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Stockton | CA | 95205-4912 |  | 2013-06-04 | 2013-06-04 12:04 | 2013-06-04 12:04 | PAYNE - PA10JA036-C | 73 | 0 | Yes | Yes | 20.9 | 21.4 | -0.5 | 42D8186052BF41F39A02D9644911ED18 |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-1444 |  | 2013-07-01 | 2013-07-01 11:42 | 2013-07-01 12:02 | BDP - 585EJW036075AA | 82 | 4.4 | Yes | Yes | 18.8 | 21.2 | -2.4 | 9923BF971F7641A79895F708E759E72B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.366% | 0.94634 | 10.31% | [5 empty] | Non-TXV | 5.366%
Stockton | CA | 95210-2287 |  | 2013-06-12 | 2013-06-12 12:00 | 2013-06-12 12:21 | DAY & NIGHT - 585HJ030040 | 68 | -4 | Yes | Yes | 24.6 | 20.2 | 4.4 | 113D7D1EA530446DAB8928CABF3FE7A0 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95206-1363 |  | 2013-06-10 | 2013-06-10 11:22 | 2013-06-10 11:43 | GOODMAN - CKL36-1D | 85 | -8 | Yes | Yes | 20.9 | 18.8 | 2.1 | F89361E8FF9643FF8D60D828689A8F46 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Yuba City | CA | 95991-8443 |  | 2013-07-16 | 2013-07-16 11:59 | 2013-07-16 12:21 | OTHER - NDA460GKA100 | 215 | 25 | Yes | Yes | 17 | 19.3 | -2.3 | F3CF3E99B0F34726B0CCC936D4C7E0B8 |  | R22 | TXV |  | 11.63% | 0.88372 | 22.35% | [5 empty] | TXV | 11.63%
Stockton | CA | 95207-7547 |  | 2013-06-01 | 2013-06-01 10:55 | 2013-06-01 11:17 | GOODMAN - CKL-42 | 98 | 8.2 | Yes | Yes | 22 | 18.6 | 3.4 | 70DA6C1FEC9946CC9B74823BEFAE920A |  | R22 | TXV |  | 8.367% | 0.91633 | 16.08% | [5 empty] | TXV | 8.367%
Stockton | CA | 95203-1214 |  | 2013-05-28 | 2013-05-28 10:23 | 2013-05-28 10:23 | PAYNE - PY3GNAA30060NA | 98 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | D8FAF6F077F847779390A74579EDEC7B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2733 |  | 2013-06-14 | 2013-06-14 10:26 | 2013-06-14 10:45 | YORK - AC042X1221B | 109 | 21.3 | Yes | Yes | 17.3 | 19.7 | -2.4 | E87879E4FED7445BB5A7EF0B4D11FA6E |  | R22 | Non-TXV |  | 19.54% | 0.80459 | 37.55% | [5 empty] | Non-TXV | 19.54%
Lathrop | CA | 95330-8536 |  | 2013-06-07 | 2013-06-07 12:28 | 2013-06-07 12:46 | YORK - H2RD036D06B | 96 | 2.9 | Yes | Yes | 18.7 | 19.5 | -0.8 | FEAD29343AA44519A5F944A2C0299DE1 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Stockton | CA | 95204-2804 |  | 2013-05-31 | 2013-05-31 10:30 | 2013-05-31 10:56 | GOODMAN - CKJ42-1A | 99 | 3.3 | Yes | Yes | 16 | 17.5 | -1.5 | 04E6E773A328441FACC6B1C70392E4F3 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95206-5722 |  | 2013-06-20 | 2013-06-20 14:14 | 2013-06-20 14:32 | BRYANT - 561CJXO60000AAAA | 153 | 5.8 | Yes | Yes | 22 | 19.1 | 2.9 | 03E48891746F4CB5911D76667CB97E13 |  | R22 | Non-TXV |  | 3.791% | 0.96209 | 7.285% | [5 empty] | Non-TXV | 3.791%
Tracy | CA | 95376-3194 |  | 2013-06-05 | 2013-06-05 12:20 | 2013-06-05 12:41 | YORK - HD1A024S06A | 65 | -6.1 | Yes | Yes | 21.7 | 17.6 | 4.1 | 6EE7BCD9251644D1ADC5B6E84D5A2604 |  | R22 | Non-TXV |  | -9.385% | 1.0938 | 2.628% |  |  |  |  | Non-TXV |  |  | -9.385%
Los Banos | CA | 93635-6355 |  | 2013-10-10 | 2013-10-10 20:30 | 2013-10-10 20:32 | BRYANT - 561CJ036-E | 73 | 3 | Yes | Yes | 22 | 21 | 1 | 65560D4B7CBB4AA8A60C46DFA2D5E394 |  | R22 | Non-TXV |  | 4.11% | 0.9589 | 7.898% | [5 empty] | Non-TXV | 4.11%
Stockton | CA | 95209-2607 |  | 2013-05-23 | 2013-05-23 12:29 | 2013-05-23 13:33 | RHEEM - HC-80-24-21C | 49 | 8.5 | Yes | Yes | 17.2 | 20.1 | -2.9 | C33A038696734A7FA04DA87655503EC5 |  | R22 | Non-TXV |  | 17.35% | 0.82653 | 33.34% | [5 empty] | Non-TXV | 17.35%
Fresno | CA | 93727-6420 |  | 2013-06-13 | 2013-06-13 14:39 | 2013-06-13 14:43 | BRYANT - 38BRB042300 | 132 | 6.9 | Yes | Yes | 20.6 | 22.6 | -2 | 93CA738685EE435FBAFF314F34A1042C |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Fresno | CA | 93727-6843 |  | 2013-06-14 | 2013-06-14 13:16 | 2013-06-14 13:18 | LENNOX - 10GCS036X-75-3PA | 58 | 4.1 | Yes | Yes | 25.6 | 22.1 | 3.5 | E9DF3E849B7A4A31B1950416DF399CCD |  | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Madera | CA | 93637-6250 |  | 2013-08-05 | 2013-08-05 11:38 | 2013-08-05 11:39 | OTHER - 38ETG030300 | 133 | 14.5 | Yes | Yes | 22.2 | 19.2 | 3 | 575D64FBBA7044129BC8C874C6D6711E |  | R22 | Non-TXV |  | 10.9% | 0.89098 | 20.95% | [5 empty] | Non-TXV | 10.9%
Tracy | CA | 95376-3184 |  | 2013-05-29 | 2013-05-29 14:58 | 2013-05-29 15:17 | RHEEM - UNK | 85 | 4.8 | Yes | Yes | 25.3 | 22.1 | 3.2 | 0AE9F2A896034DC9A1DD57969789C4EB |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Pollock Pines | CA | 95726-9004 |  | 2013-09-19 | 2013-09-19 11:43 | 2013-09-19 11:43 | AIRE-FLO - 4AC13L30P-5A | 68 | 0 | Yes | Yes | 26.2 | 20.9 | 5.3 | 72FF4480BDC24719933B0AC7E2E5BFCB |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6913 |  | 2013-08-22 | 2013-08-22 10:17 | 2013-08-22 10:35 | YORK - H1DH036S06A | 117 | 3.6 | Yes | Yes | 16.5 | 18.5 | -2 | 6D22E69F3BBF4F8581ACEA4DB4B1AA95 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Lincoln | CA | 95648-1938 |  | 2013-07-06 | 2013-07-06 14:02 | 2013-07-06 14:35 | LENNOX - GC10-41-75-1P | 71 | -3.6 | Yes | Yes | 17 | 19.9 | -2.9 | B31992636F564E129DEEF2331385A7C9 |  | R22 | Non-TXV |  | -5.07% | 1.0507 | 1.42% |  |  |  |  | Non-TXV |  |  | -5.07%
Placerville | CA | 95667-9595 |  | 2013-05-29 | 2013-05-29 13:45 | 2013-05-29 14:14 | COLEMAN - FRCS0301BD | 158 | 17.3 | Yes | Yes | 17 | 19.5 | -2.5 | 0F246BEE1A094BBE9203A25C49AF5725 |  | R22 | Non-TXV |  | 10.95% | 0.89051 | 21.04% | [5 empty] | Non-TXV | 10.95%
Placerville | CA | 95667-9595 |  | 2013-05-29 | 2013-05-29 14:09 | 2013-05-29 14:29 | COLEMAN - FRCS0301BD | 158 | 17.1 | Yes | Yes | 17 | 19.9 | -2.9 | 9F63E5BBD44645A68AA4A87520D272BB |  | R22 | Non-TXV |  | 10.82% | 0.89177 | 20.8% | [5 empty] | Non-TXV | 10.82%
Livingston | CA | 95334-1872 |  | 2013-08-27 | 2013-08-27 15:02 | 2013-08-27 15:26 | CARRIER - 591ANX036000AAA | 81 | 2.5 | Yes | Yes | 23.3 | 22.2 | 1.1 | AAAA945854544A528E53F706C0A85828 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Merced | CA | 95341-7001 |  | 2013-08-06 | 2013-08-06 09:31 | 2013-08-06 09:57 | PAYNE - PY1PNB030040AAA | 55 | 1.6 | Yes | Yes | 25.4 | 19.9 | 5.5 | E8BE1ED36E2A452789D54718AD2651CB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Yuba City | CA | 95991-6540 |  | 2013-06-21 | 2013-06-21 10:42 | 2013-06-21 11:02 | OTHER - 567C030RCU | 63 | 13.7 | Yes | Yes | 19 | 21.4 | -2.4 | 36756129591A4DC4B81351F6F8E8FE10 |  | R22 | Non-TXV |  | 21.75% | 0.78254 | 41.79% | [5 empty] | Non-TXV | 21.75%
Lincoln | CA | 95648-8009 |  | 2013-05-31 | 2013-05-31 08:59 | 2013-05-31 09:20 | YORK - H1RD042S06G | 152 | -5.9 | Yes | Yes | 17 | 19.5 | -2.5 | 78AA63990CBA4861834F5CCC7B57CC97 |  | R22 | Non-TXV |  | -3.882% | 1.0388 | 1.087% |  |  |  |  | Non-TXV |  |  | -3.882%
Clovis | CA | 93611-1413 |  | 2013-06-13 | 2013-06-13 09:48 | 2013-06-13 10:07 | YORK - DBYP-F030N070A | 73 | 3 | Yes | Yes | 18.1 | 20.4 | -2.3 | A889E87A1E224C6EBBC6458AF301C0FD |  | R22 | Non-TXV |  | 4.11% | 0.9589 | 7.898% | [5 empty] | Non-TXV | 4.11%
Tracy | CA | 95376-3184 |  | 2013-05-29 | 2013-05-29 13:31 | 2013-05-29 13:53 | RHEEM - UNK | 85 | 18.2 | Yes | Yes | 21.5 | 19.8 | 1.7 | 875582A219F14378AAB5E9EBFB8F073D |  | R22 | Non-TXV |  | 21.41% | 0.78588 | 41.15% | [5 empty] | Non-TXV | 21.41%
Live Oak | CA | 95953-2241 |  | 2013-09-10 | 2013-09-10 14:36 | 2013-09-10 14:59 | OTHER - DAYA-F036N070C | 67 | 2.1 | Yes | Yes | 23 | 19.5 | 3.5 | 55EAB8F2870E4AF5A1CE162B72FD5561 |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
El Dorado Hills | CA | 95762-9747 |  | 2013-06-19 | 2013-06-19 12:25 | 2013-06-19 12:44 | CARRIER - 38BRG042300 | 108 | 9.1 | Yes | Yes | 19.5 | 20.4 | -0.9 | A4472887049847EAA5FAECA058E6BAB9 |  | R22 | TXV |  | 8.426% | 0.91574 | 16.19% | [5 empty] | TXV | 8.426%
Atwater | CA | 95301-4136 |  | 2013-06-06 | 2013-06-06 09:48 | 2013-06-06 09:55 | AMANA - RCE24A2D | 160 | 4.9 | Yes | Yes | 18 | 19.3 | -1.3 | 3659E8D119AC4BA1A9B46993CDAC7D9A |  | R22 | Non-TXV |  | 3.062% | 0.96937 | 5.885% | [5 empty] | Non-TXV | 3.062%
Stockton | CA | 95207-2025 |  | 2013-05-29 | 2013-05-29 10:41 | 2013-05-29 11:00 | TRANE - YCX036F1MOBC | 116 | 8.9 | Yes | Yes | 23.9 | 18.2 | 5.7 | 5421251E359F4ECAA774CA4ED1016112 |  | R22 | Non-TXV |  | 7.672% | 0.92328 | 14.74% | [5 empty] | Non-TXV | 7.672%
Dinuba | CA | 93618-1718 |  | 2013-06-20 | 2013-06-20 11:33 | 2013-06-20 11:51 | RHEEM - RRMA-A036JK06X | 99 | 3.8 | Yes | Yes | 26 | 21 | 5 | EA8C345EFFFC451EBD016EC5F55B10CA |  | R22 | Non-TXV |  | 3.838% | 0.96162 | 7.377% | [5 empty] | Non-TXV | 3.838%
Stockton | CA | 95207-3802 |  | 2013-06-04 | 2013-06-04 09:01 | 2013-06-04 09:01 | PAYNE - 38BR036300 | 122 | 0 | Yes | Yes | 22.7 | 18.8 | 3.9 | 91E3A93FD88B4516B596C8780FC56CB9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-9488 |  | 2013-06-22 | 2013-06-22 09:56 | 2013-06-22 09:56 | OTHER - 3235-7-8B | 76 | 0 | Yes | Yes | 22 | 16.5 | 5.5 | 3E7A99834FAD4E779157F3FFDFDFB6EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-9751 |  | 2013-06-11 | 2013-06-11 13:37 | 2013-06-11 13:39 | OTHER - CP330-1AB | 80 | 4.4 | Yes | Yes | 18.8 | 18.3 | 0.6 | 326592DA19D5476D9A2F24EE66AE0C45 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Chico | CA | 95973-0429 |  | 2013-06-04 | 2013-06-04 12:56 | 2013-06-04 13:31 | YORK - H2CB036506A | 91 | 6.6 | Yes | Yes | 25 | 21.8 | 3.3 | B81C0DA329CE48828F7DD436A494F371 |  | R22 | Non-TXV |  | 7.253% | 0.92747 | 13.94% | [5 empty] | Non-TXV | 7.253%
Oroville | CA | 95966-5601 |  | 2013-08-06 | 2013-08-06 12:18 | 2013-08-06 12:47 | TRANE - YCZ060F1M0AD | 200 | 7.4 | Yes | Yes | 22.4 | 21.5 | 0.9 | 1419C6CFCBDC4D888D402F5A00F43A5C |  | R22 | Non-TXV |  | 3.7% | 0.963 | 7.111% | [5 empty] | Non-TXV | 3.7%
Stockton | CA | 95212-3401 |  | 2013-06-21 | 2013-06-21 11:35 | 2013-06-21 12:04 | YORK - H1RA048S06D | 117 | 3.5 | Yes | Yes | 21.8 | 19.9 | 1.9 | 0E5E3013E17F412FA679004CC786AF68 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Chico | CA | 95973-9484 |  | 2013-07-11 | 2013-07-11 11:15 | 2013-07-11 11:59 | NORDYNE - GQRC036K | 104 | 12.5 | Yes | Yes | 17.7 | 20.4 | -2.7 | 1D66F1C8A90149D8B94B782281B56811 |  | R22 | Non-TXV |  | 12.02% | 0.87981 | 23.1% | [5 empty] | Non-TXV | 12.02%
Stockton | CA | 95206-4660 |  | 2013-06-13 | 2013-06-13 12:42 | 2013-06-13 13:08 | RHEEM - RAKA-042JAZ | 85 | 4.6 | Yes | Yes | 22.3 | 20.9 | 1.4 | 5F8D364B7DE749A393E86F9ED78FDCF0 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Tracy | CA | 95377-1123 |  | 2013-06-03 | 2013-06-03 08:57 | 2013-06-03 09:13 | WEATHER KING - 10AJA4801 | 85 | 8.1 | Yes | Yes | 22.9 | 20.9 | 2 | D32BA972E84F4287984A393B6FBE7A59 |  | R22 | Non-TXV |  | 9.529% | 0.90471 | 18.31% | [5 empty] | Non-TXV | 9.529%
Magalia | CA | 95954-9611 |  | 2013-07-18 | 2013-07-18 09:45 | 2013-07-18 10:10 | CARRIER - 38TH030310 | 69 | 6.5 | Yes | Yes | 17.4 | 19.9 | -2.5 | 8CD9991FE18449C5BFD71B56A751BC61 |  | R22 | Non-TXV |  | 9.42% | 0.9058 | 18.1% | [5 empty] | Non-TXV | 9.42%
Stockton | CA | 95219-5488 |  | 2013-06-20 | 2013-06-20 14:51 | 2013-06-20 14:51 | CARRIER - 38EN018310 | 55 | 0 | Yes | Yes | 21.4 | 19.4 | 2 | 841B9888FB5B4CD3AC7DE052C67471D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1937 |  | 2013-07-26 | 2013-07-26 14:20 | 2013-07-26 14:50 | PAYNE - PY1PNB030060AAAA | 55 | 5.1 | Yes | Yes | 18.8 | 21.5 | -2.7 | C49D79E19624413A8D06D71A19F85D86 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.273% | 0.90727 | 17.82% | [5 empty] | Non-TXV | 9.273%
Stockton | CA | 95206-5726 |  | 2013-07-16 | 2013-07-16 16:39 | 2013-07-16 16:39 | BRYANT - 561CJ048-A | 102 | 0 | Yes | Yes | 20.1 | 19.6 | 0.5 | 5DE7BDA70E454DE58173D90E33D0E571 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2031 |  | 2013-06-04 | 2013-06-04 16:31 | 2013-06-04 16:52 | YORK - H2RA030S06G | 52 | 6.8 | Yes | Yes | 16.7 | 17.8 | -1.1 | 8B7B340DEF81412CB4CA5E8D249B0A0B |  | R22 | Non-TXV |  | 13.08% | 0.86923 | 25.13% | [5 empty] | Non-TXV | 13.08%
Stockton | CA | 95210-1454 |  | 2013-06-11 | 2013-06-11 10:04 | 2013-06-11 10:24 | BDP - 585A030080YACR | 50 | 5.5 | Yes | Yes | 22.3 | 19.6 | 2.7 | C4CFFE18664B4F6E9726CD30708B027D |  | R22 | Non-TXV |  | 11% | 0.89 | 21.14% | [5 empty] | Non-TXV | 11%
Stockton | CA | 95205-6439 |  | 2013-06-04 | 2013-06-04 12:33 | 2013-06-04 13:05 | GOODMAN - GSC130301AE | 117 | 7.8 | Yes | Yes | 21.2 | 17.9 | 3.3 | 38DDC5D9AF724F9CA503BB778E5ADF6F |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Merced | CA | 95348-2548 |  | 2013-07-03 | 2013-07-03 14:58 | 2013-07-03 15:04 | GOODMAN - CKL361D | 75 | 7.9 | Yes | Yes | 23.9 | 22.3 | 1.6 | C3FF95563D874458B8BA2916B5924ED8 |  | R22 | Non-TXV |  | 10.53% | 0.89467 | 20.24% | [5 empty] | Non-TXV | 10.53%
Clovis | CA | 93611-5914 |  | 2013-07-08 | 2013-07-08 09:42 | 2013-07-08 10:02 | CARRIER - 48KLA136--300BE | 102 | 3.9 | Yes | Yes | 28.7 | 22.9 | 5.8 | 7A3C0634088C41128ECA6E94BDBB1F2E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Stockton | CA | 95206-1869 |  | 2013-06-10 | 2013-06-10 12:08 | 2013-06-10 12:26 | PAYNE - UNK | 85 | -8 | Yes | Yes | 21.6 | 21.9 | -0.3 | D2BFA316E2A3481F90604170D1DCB696 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Tracy | CA | 95376-2740 |  | 2013-06-25 | 2013-06-25 11:31 | 2013-06-25 11:59 | DAY & NIGHT - UNK | 85 | -6 | Yes | Yes | 22.9 | 18.3 | 4.6 | 2B934EC515C846E9ACBAF188EF1D9D26 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Lathrop | CA | 95330-8918 |  | 2013-06-20 | 2013-06-20 15:49 | 2013-06-20 16:21 | GOODMAN - CKJ48-1AB | 118 | 28.5 | Yes | Yes | 20.7 | 20.8 | -0.1 | 1A2B98AF5F7748EAA67C88F949505209 |  | R22 | Non-TXV |  | 24.15% | 0.75847 | 46.42% | [5 empty] | Non-TXV | 24.15%
Fresno | CA | 93727-2716 |  | 2013-06-11 | 2013-06-11 09:06 | 2013-06-11 09:29 | BDP - 567GJ048 | 125 | 12.8 | Yes | Yes | 25.5 | 20.4 | 5.1 | 3B9949240AB64E67BC24F6B2A0C771F7 |  | R22 | Non-TXV |  | 10.24% | 0.8976 | 19.68% | [5 empty] | Non-TXV | 10.24%
Stockton | CA | 95212-2856 |  | 2013-06-12 | 2013-06-12 11:50 | 2013-06-12 12:07 | CARRIER - 38CKC060371 | 131 | 4 | Yes | Yes | 18.9 | 19.3 | -0.4 | 7D48195D04A244E4BD92D4BBC5D6023B |  | R22 | Non-TXV |  | 3.053% | 0.96947 | 5.868% | [5 empty] | Non-TXV | 3.053%
Stockton | CA | 95210-1330 |  | 2013-06-06 | 2013-06-06 14:19 | 2013-06-06 14:49 | RHEEM - RAKA-037JAZ | 79 | 2.5 | Yes | Yes | 16.8 | 18.7 | -1.9 | 36B208DF667243AF8BF49B8CF2D4AC3B |  | R22 | Non-TXV |  | 3.165% | 0.96835 | 6.082% | [5 empty] | Non-TXV | 3.165%
Fresno | CA | 93703-3474 |  | 2013-06-27 | 2013-06-27 01:16 | 2013-06-27 01:38 | AMERICAN STANDARD - YCZ050F1H0AE | 169 | 5.1 | Yes | Yes | 19.8 | 20.4 | -0.6 | DCE965B58B974871B789095EF1EC1D9F |  | R22 | Non-TXV |  | 3.018% | 0.96982 | 5.799% | [5 empty] | Non-TXV | 3.018%
Fresno | CA | 93727-0000 |  | 2013-06-08 | 2013-06-08 09:57 | 2013-06-08 10:24 | BDP - 588ANW060080ABAG | 112 | 18.7 | Yes | Yes | 21.3 | 21.2 | 0.1 | 5BCA11EB8A024DC2A7F697C5216ADFB0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.7% | 0.83304 | 32.09% | [5 empty] | Non-TXV | 16.7%
Paradise | CA | 95969-4243 |  | 2013-06-28 | 2013-06-28 20:25 | 2013-06-28 20:25 | PAYNE - 5930CJ030-B | 70 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | E70C2456707E4D59A25FF46CF0BD2A68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Durham | CA | 95938-9783 |  | 2013-09-06 | 2013-09-06 11:30 | 2013-09-06 18:50 | COLEMAN - 9541-901 | 53 | 11.2 | Yes | Yes | 21.2 | 19.8 | 1.4 | A50B5A3058C54D498C54F633284570D0 |  | R22 | Non-TXV |  | 21.13% | 0.78868 | 40.61% | [5 empty] | Non-TXV | 21.13%
Chico | CA | 95926-3059 |  | 2013-06-05 | 2013-06-05 12:06 | 2013-06-05 12:28 | DAY & NIGHT - 591ANX030000AAAA | 76 | 8 | Yes | Yes | 25 | 19.7 | 5.3 | F991087CC2384514B3119E2ED57581C9 |  | R22 | Non-TXV |  | 10.53% | 0.89474 | 20.23% | [5 empty] | Non-TXV | 10.53%
Paradise | CA | 95969-4317 |  | 2013-06-13 | 2013-06-13 16:03 | 2013-06-13 16:03 | OTHER - AC030X12224 | 80 | 0 | Yes | Yes | 22.9 | 19.2 | 3.7 | 16E7E216A56C4A78945A5EE6DD1453A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6519 |  | 2013-06-13 | 2013-06-13 10:16 | 2013-06-13 10:16 | COLEMAN - 7836-901 | 65 | 0 | Yes | Yes | 20.1 | 21.5 | -1.4 | 755D575C4D764E27B95E7F54E6A9587C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-4803 |  | 2013-06-05 | 2013-06-05 11:32 | 2013-06-05 11:51 | YORK - D1NA02405606C | 54 | 1.6 | Yes | Yes | 23 | 19.9 | 3.1 | E66F7C36EE2F49AFBA312CB05DE3769E |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Chico | CA | 95973-0675 |  | 2013-07-08 | 2013-07-08 21:33 | 2013-07-08 21:56 | OTHER - CA5536VKD2 | 81 | 2.9 | Yes | Yes | 22.2 | 22.3 | -0.1 | 9E1E426EB779412EB10833107B8AFD78 |  | R22 | Non-TXV |  | 3.58% | 0.9642 | 6.88% | [5 empty] | Non-TXV | 3.58%
Chico | CA | 95973-1077 |  | 2013-07-10 | 2013-07-10 19:03 | 2013-07-10 19:56 | PAYNE - 5858V030 | 73 | 6.7 | Yes | Yes | 20.6 | 21.4 | -0.8 | 5736BF3DE3F94DC5AF3DEAB870D93E1C |  | R22 | Non-TXV |  | 9.178% | 0.90822 | 17.64% | [5 empty] | Non-TXV | 9.178%
Dinuba | CA | 93618-9752 |  | 2013-06-24 | 2013-06-24 13:05 | 2013-06-24 13:05 | CARRIER - 50XZ-60-301 | 215 | 0 | Yes | Yes | 15.7 | 18.6 | -2.9 | 0611E4BA99C94590935BB9BCCAECB2A0 |  | R410A | TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9675 |  | 2013-11-20 | 2013-11-20 10:29 | 2013-11-20 10:29 | YORK - H1RA048506D | 117 | 0 | Yes | Yes | 30.2 | 20.4 | 9.8 | 71EF542C3444416B8C07E2D125B39B70 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0911 |  | 2013-08-21 | 2013-08-21 16:30 | 2013-08-21 16:30 | BRYANT - 58ZANW024060NAAD | 53 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | F9928C27510A4FA4BFC03D595EBA968E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3228 |  | 2013-08-08 | 2013-08-08 10:23 | 2013-08-08 10:25 | RHEEM - RRKAA030JK06X | 54 | 2.3 | Yes | Yes | 18.1 | 15.7 | 2.4 | A5115728E825482C9F0719FE25ED77AE |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Chico | CA | 95928-4341 |  | 2013-08-30 | 2013-08-30 08:29 | 2013-08-30 08:47 | DAY & NIGHT - 584ANW048100 | 128 | -7.5 | Yes | Yes | 25 | 21 | 4 | 238CD3C71D034D11B27883732123F4FF |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Chico | CA | 95928-6749 |  | 2013-07-03 | 2013-07-03 17:50 | 2013-07-03 18:10 | LENNOX - GCS16R-J11-2G-1P | 70 | 10.5 | Yes | Yes | 22.2 | 22 | 0.2 | 60B4E4B850AA4EEDB09CDB38A882F13A |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Paradise | CA | 95969-4740 |  | 2013-06-13 | 2013-06-13 11:32 | 2013-06-13 12:10 | BRYANT - D1NP036N05606A | 108 | 6.2 | Yes | Yes | 19.8 | 22 | -2.2 | 44C2B2A15DCA45BB942B1BA88633D118 |  | R22 | Non-TXV |  | 5.741% | 0.94259 | 11.03% | [5 empty] | Non-TXV | 5.741%
Stockton | CA | 95210-1414 |  | 2013-06-07 | 2013-06-07 10:39 | 2013-06-07 10:58 | YORK - D1NX036N06506A | 156 | -9.2 | Yes | Yes | 25.2 | 19.9 | 5.3 | A1117C7F54264C1DAA37027FBAF68641 |  | R410A | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Stockton | CA | 95206-2482 |  | 2013-06-12 | 2013-06-12 10:58 | 2013-06-12 11:19 | RHEEM - RAMB-036JAZ | 85 | 8.7 | Yes | Yes | 22.5 | 21 | 1.5 | EDC6AFB7160841BD82C0B95ED04F3296 |  | R22 | Non-TXV |  | 10.24% | 0.89765 | 19.67% | [5 empty] | Non-TXV | 10.24%
Oroville | CA | 95965-4182 |  | 2013-07-26 | 2013-07-26 11:02 | 2013-07-26 20:52 | LENNOX - E1RAO48S06D | 121 | 9.3 | Yes | Yes | 18 | 20.1 | -2.1 | DBE04ACC6F754F04A8EBF2D1EC8BBB70 |  | R22 | Non-TXV |  | 7.686% | 0.92314 | 14.77% | [5 empty] | Non-TXV | 7.686%
Stockton | CA | 95205-7806 |  | 2013-06-11 | 2013-06-11 14:53 | 2013-06-11 14:53 | GUARDIAN - GCGD30S41S3A | 62 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 94A7BD610543465FBADEFF56CFE2BBFC |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6408 |  | 2013-06-21 | 2013-06-21 08:38 | 2013-06-21 09:00 | PAYNE - PA13NR03600GAJAA | 89 | 5 | Yes | Yes | 20.8 | 19.1 | 1.8 | A033F2B4769A4F3AA713C42E509106C9 |  | R22 | TXV |  | 5.618% | 0.94382 | 10.8% | [5 empty] | TXV | 5.618%
Stockton | CA | 95210-2601 |  | 2013-06-05 | 2013-06-05 14:39 | 2013-06-05 14:56 | YORK - D1NA024N05606C | 54 | 1.8 | Yes | Yes | 21.9 | 21 | 0.9 | C1BCADB5D6AA47C48DC5CEC876B109C6 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Tracy | CA | 95376-2045 |  | 2013-06-25 | 2013-06-25 10:40 | 2013-06-25 11:06 | YORK - H2RA036S06E | 63 | 5.6 | Yes | Yes | 22 | 16.6 | 5.4 | D557BFC3148C41EBAA905EB0F0A4CF82 |  | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Riverbank | CA | 95367-3134 |  | 2013-06-14 | 2013-06-14 12:03 | 2013-06-14 12:32 | RUUD - UAKA-030JAZ | 62 | 2.6 | Yes | Yes | 20.9 | 22.6 | -1.7 | E6A238C5B533478EA061B7273DCDF334 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Stockton | CA | 95210-1305 |  | 2013-06-06 | 2013-06-06 12:38 | 2013-06-06 13:23 | KENMORE - TCA048AKA4 | 123 | -7.2 | Yes | Yes | 24.2 | 18.4 | 5.9 | 63AE0D8726864C779FB9DDFBFDFA3AF3 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Clovis | CA | 93612-5879 |  | 2013-06-21 | 2013-06-21 10:14 | 2013-06-21 10:35 | CARRIER - 48NLX030-30`BE | 67 | 10.1 | Yes | Yes | 19 | 19.9 | -0.9 | 1A5B727F27354F8DBAF33603F2E973E1 |  | R22 | Non-TXV |  | 15.07% | 0.84925 | 28.97% | [5 empty] | Non-TXV | 15.07%
Manteca | CA | 95337-5304 |  | 2013-06-19 | 2013-06-19 12:54 | 2013-06-19 13:16 | YORK - 02GA036N08006C | 84 | 2.6 | Yes | Yes | 19.3 | 20.2 | -0.9 | E82B818617CE488CB5E365747F915402 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Stockton | CA | 95206-4719 |  | 2013-06-14 | 2013-06-14 09:18 | 2013-06-14 09:42 | TRANE - CA9030UKA2 | 85 | 7.6 | Yes | Yes | 20.8 | 20.3 | 0.5 | 4A27E21377F24E43B7A8DFA7D6583F68 |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Stockton | CA | 95205-4743 |  | 2013-06-04 | 2013-06-04 11:30 | 2013-06-04 11:46 | RHEEM - UNK | 54 | 4.6 | Yes | Yes | 20.5 | 18.8 | 1.7 | E6CE9456BAF749089328D9D764F8C4D7 |  | R22 | Non-TXV |  | 8.519% | 0.91481 | 16.37% | [5 empty] | Non-TXV | 8.519%
Stockton | CA | 95212-3142 |  | 2013-06-13 | 2013-06-13 15:10 | 2013-06-13 15:27 | YORK - H1RA042S06G | 85 | 4.8 | Yes | Yes | 19.1 | 19.8 | -0.7 | 907A3065435040148D7C08CE77CB84E8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Manteca | CA | 95337-8990 |  | 2013-05-31 | 2013-05-31 11:46 | 2013-05-31 12:04 | YORK - H3RA060S06N | 106 | 3.3 | Yes | Yes | 20.1 | 20.2 | 0 | 4D4E0698C5874203A6AAC4618BB62D17 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.113% | 0.96887 | 5.983% | [5 empty] | Non-TXV | 3.113%
Oakdale | CA | 95361-3401 |  | 2013-06-14 | 2013-06-14 11:38 | 2013-06-14 12:02 | GOODMAN - CE30-1HB | 72 | 3.4 | Yes | Yes | 18.7 | 19.8 | -1.1 | 241BA71723B24D359ADA726BB257D16A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Stockton | CA | 95207-3304 |  | 2013-06-04 | 2013-06-04 09:35 | 2013-06-04 09:54 | TRANE - 2TTX4036B1000AA | 118 | 9.2 | Yes | Yes | 17.9 | 18.8 | -0.9 | 2286D020EF034D81858486615DA70BE7 |  | R22 | TXV |  | 7.797% | 0.92203 | 14.98% | [5 empty] | TXV | 7.797%
Riverbank | CA | 95367-9619 |  | 2013-08-29 | 2013-08-29 12:25 | 2013-08-29 13:03 | YORK - HARR-F036SA | 108 | 3.3 | Yes | Yes | 23.8 | 19.3 | 4.5 | FE338A51FF6C4D2AA0B6416C42B2DA8E |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Lathrop | CA | 95330-9174 |  | 2013-06-07 | 2013-06-07 10:46 | 2013-06-07 11:07 | GOODMAN - CKJ42-1AB | 106 | 5.3 | Yes | Yes | 19.2 | 20.3 | -1.1 | D87162ADDF17484E98626ADBF6AF8CA1 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95215-6740 |  | 2013-06-20 | 2013-06-20 11:36 | 2013-06-20 11:55 | TRANE - `UNK | 185 | 5.6 | Yes | Yes | 25 | 20.4 | 4.6 | 2B9B1D500C9E4A73AA4A6E734955A1D2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.027% | 0.96973 | 5.817% | [5 empty] | Non-TXV | 3.027%
Stockton | CA | 95204-4833 |  | 2013-06-01 | 2013-06-01 10:43 | 2013-06-01 11:01 | GOODMAN - PGB030050-1A | 56 | 3.3 | Yes | Yes | 19.9 | 20.4 | -0.5 | 66FCF9ECC17B4F188C5E350CC39E5865 |  | R22 | Non-TXV |  | 5.893% | 0.94107 | 11.32% | [5 empty] | Non-TXV | 5.893%
Stockton | CA | 95204-4833 |  | 2013-06-01 | 2013-06-01 10:22 | 2013-06-01 10:41 | GOODMAN - PGB030050-1A | 56 | 3 | Yes | Yes | 20 | 21 | -1 | 879459816DB145B09650BC61718B9FF6 |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Newman | CA | 95360-1750 |  | 2013-06-04 | 2013-06-04 13:28 | 2013-06-04 13:48 | UNITARY PRODUCTS GROUP - H2RA030S06D | 62 | 5.4 | Yes | Yes | 20.9 | 21.7 | -0.8 | 051EAB458DF344FFA4E99A81A7CA6CE2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.71% | 0.9129 | 16.74% | [5 empty] | Non-TXV | 8.71%
Clovis | CA | 93611-3119 |  | 2013-06-13 | 2013-06-13 13:49 | 2013-06-13 14:31 | PAYNE - N/A | 120 | 3.8 | Yes | Yes | 21.8 | 19.7 | 2.1 | B282A898F3BC4A4F9BD7FAFD24A95145 |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Stockton | CA | 95210-2009 |  | 2013-07-03 | 2013-07-03 08:37 | 2013-07-03 08:56 | RHEEM - 14AJM36A01 | 130 | -9.2 | Yes | Yes | 19.4 | 16.3 | 3.1 | C440F3FE23BD476CB7872B5884F3C612 |  | R410A | Non-TXV |  | -7.077% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.077%
Stockton | CA | 95206-6378 |  | 2013-06-21 | 2013-06-21 10:40 | 2013-06-21 10:57 | GOODMAN - GSC130361GB | 77 | 8.3 | Yes | Yes | 22.5 | 19.9 | 2.6 | 852203F615EF4F28AACBA3B49CDC76D9 |  | R22 | TXV |  | 10.78% | 0.89221 | 20.72% | [5 empty] | TXV | 10.78%
Chico | CA | 95973-7867 |  | 2013-10-18 | 2013-10-18 16:45 | 2013-10-18 17:04 | LENNOX - HS26-036-4P | 87 | 5 | Yes | Yes | 17 | 19.9 | -2.9 | 5DA1A5EF0BB147F0A781FCE540C33999 |  | R22 | Non-TXV |  | 5.747% | 0.94253 | 11.04% | [5 empty] | Non-TXV | 5.747%
Stockton | CA | 95212-3465 |  | 2013-06-17 | 2013-06-17 14:33 | 2013-06-17 14:50 | CARRIER - 38CKC042340 | 80 | 3.3 | Yes | Yes | 20.2 | 21.5 | -1.3 | E4D4B20CB1EA4B11AFFDC21BE2EC23C4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Tehama | CA | 96090-0000 |  | 2013-09-27 | 2013-09-27 14:05 | 2013-09-27 15:31 | AMANA - PHB24CO2E | 68 | 5.4 | Yes | Yes | 21.6 | 18.6 | 3 | A6A1A4FD26854335B3DA9BB5AB583AA4 |  | R22 | Non-TXV |  | 7.941% | 0.92059 | 15.26% | [5 empty] | Non-TXV | 7.941%
Yuba City | CA | 95991-5805 |  | 2013-05-31 | 2013-05-31 18:21 | 2013-05-31 18:21 | CARRIER - 584BNW036060AABF | 64 | 0 | Yes | Yes | 22.9 | 21.3 | 1.7 | BD3CD30B36844EBA8799136A3E446B39 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5921 |  | 2013-06-19 | 2013-06-19 13:59 | 2013-06-19 14:19 | CARRIER - 38CKC048--301 | 104 | -6.1 | Yes | Yes | 19.6 | 18.8 | 0.8 | 8763DE3B3E914222840B43F777E9F8B8 |  | R22 | TXV |  | -5.865% | 1.0587 | 1.643% |  |  |  |  | TXV |  |  | -5.865%
Stockton | CA | 95206-1314 |  | 2013-06-10 | 2013-06-10 09:57 | 2013-06-10 10:25 | HEIL - NCABA24AB03 | 85 | 4.4 | Yes | Yes | 19.3 | 19.3 | 0 | 4EB7CDDF498A4B1189D46A5E475EDB82 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Stockton | CA | 95212-3128 |  | 2013-06-13 | 2013-06-13 14:01 | 2013-06-13 14:20 | YORK - H1RA042S06D | 84 | 13.4 | Yes | Yes | 19.9 | 20.4 | -0.5 | 238A7C65870C40D6ACA907AECB03A37A |  | R22 | Non-TXV |  | 15.95% | 0.84048 | 30.66% | [5 empty] | Non-TXV | 15.95%
Tracy | CA | 95377-8221 |  | 2013-06-04 | 2013-06-04 13:48 | 2013-06-04 14:22 | DAY & NIGHT - 561CJ030-A | 83 | 5.9 | Yes | Yes | 24.5 | 18.5 | 6 | D9C0539D686643B6A46915F2A490F25C |  | R22 | Non-TXV |  | 7.108% | 0.92892 | 13.66% | [5 empty] | Non-TXV | 7.108%
Stockton | CA | 95212-3035 |  | 2013-06-13 | 2013-06-13 13:08 | 2013-06-13 13:28 | YORK - H2RC036S06G | 83 | 2.5 | Yes | Yes | 20.7 | 21 | -0.3 | 52EBF2ABC6524527B838731CE6A40160 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Lodi | CA | 95240-9341 |  | 2013-08-21 | 2013-08-21 14:27 | 2013-08-21 14:40 | CARRIER - 24ABR348A320 | 119 | 7.7 | Yes | Yes | 22 | 19.8 | 2.2 | 9311730D3DBC44A498C3D00C560A685B |  | R22 | TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | TXV | 6.471%
Stockton | CA | 95205-3831 |  | 2013-06-04 | 2013-06-04 14:25 | 2013-06-04 14:41 | YORK - AC036X1021A | 63 | 3.4 | Yes | Yes | 21.3 | 19.9 | 1.4 | FBC174C63D2047D39A9BE00D373B18B5 |  | R22 | Non-TXV |  | 5.397% | 0.94603 | 10.37% | [5 empty] | Non-TXV | 5.397%
Chico | CA | 95926-3135 |  | 2013-07-02 | 2013-07-02 17:19 | 2013-07-02 17:19 | TRANE - 4XC26048A1096AA | 136 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | CD478DC2A47348E89F586F4F225B14BC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-5387 |  | 2013-06-04 | 2013-06-04 08:30 | 2013-06-04 09:18 | AMERICAN STANDARD - 287A8048A1000AA | 252 | 9.6 | Yes | Yes | 21.6 | 19.4 | 2.2 | 9E313F503AC7495C8D33444328DFE4BF |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Stockton | CA | 95210-3442 |  | 2013-06-13 | 2013-06-13 12:07 | 2013-06-13 12:27 | GE - BTB930A100A3 | 53 | -3.1 | Yes | Yes | 25.3 | 21 | 4.3 | B3620778A78340949C32A509ED74E4E3 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Merced | CA | 95348-8721 |  | 2013-06-08 | 2013-06-08 10:10 | 2013-06-08 10:16 | CARRIER - 7777UNK | 110 | 5.3 | Yes | Yes | 19 | 19.1 | -0.1 | 8E41E18AE5A44D9F9DCF5B68B9B77970 |  | R410A | Non-TXV |  | 4.818% | 0.95182 | 9.259% | [5 empty] | Non-TXV | 4.818%
Chico | CA | 95926-2947 |  | 2013-07-31 | 2013-07-31 10:02 | 2013-07-31 10:23 | GE - UNK | 80 | 4.2 | Yes | Yes | 24.6 | 18.7 | 5.9 | 0B18DF0537724F4993C5DE7305E2D292 |  | R22 | Non-TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | Non-TXV | 5.25%
Chico | CA | 95926-1507 |  | 2013-08-01 | 2013-08-01 15:09 | 2013-08-01 15:27 | LENNOX - 12GCS048-100-4PA | 167 | 5.5 | Yes | Yes | 25.8 | 19.9 | 5.9 | A491131EEEC345DFB1692257E977FDEB |  | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.329% | [5 empty] | Non-TXV | 3.293%
Yuba City | CA | 95993-8984 |  | 2013-08-28 | 2013-08-28 09:19 | 2013-08-28 09:46 | GIBSON - JS3BC-042KA | 102 | 3.7 | Yes | Yes | 16 | 18.6 | -2.6 | 45BD4471BA8942EEB7050A08F09A4764 |  | R22 | Non-TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | Non-TXV | 3.627%
Red Bluff | CA | 96080-3548 |  | 2013-05-29 | 2013-05-29 12:32 | 2013-05-29 12:32 | COLEMAN - 9636-601 | 100 | 0 | Yes | Yes | 27.9 | 22.1 | 5.8 | B00065565753481CAAC502D142DAE4FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-8035 |  | 2013-07-01 | 2013-07-01 12:48 | 2013-07-01 13:07 | RHEEM - RRNL-B030JK06X | 76 | 2.3 | Yes | Yes | 18.4 | 19.7 | -1.3 | 6F9EF9A5ECCA47C5901FC259E300B464 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95207-4439 |  | 2013-06-03 | 2013-06-03 12:40 | 2013-06-03 12:58 | GOODMAN - CKL-36 | 96 | 12.5 | Yes | Yes | 24 | 21.2 | 2.8 | F89E73B6ABEA4EC9A0A9114D81D1A7D0 |  | R22 | Non-TXV |  | 13.02% | 0.86979 | 25.02% | [5 empty] | Non-TXV | 13.02%
Stockton | CA | 95210-1484 |  | 2013-06-19 | 2013-06-19 08:47 | 2013-06-19 09:06 | PAYNE - 585A024055AC | 51 | -4.2 | Yes | Yes | 23.1 | 18.8 | 4.3 | 046F410BB5714AFBA33B7B0A8C6A25B6 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Clovis | CA | 93611-3900 |  | 2013-06-14 | 2013-06-14 10:09 | 2013-06-14 10:45 | BRYANT - 563CNX04200AEAA | 103 | 4.7 | Yes | Yes | 21.9 | 17.6 | 4.3 | A99AE979DC1C49AABEAF5F1ACD911144 |  | R22 | Non-TXV |  | 4.563% | 0.95437 | 8.769% | [5 empty] | Non-TXV | 4.563%
Clovis | CA | 93611-6024 |  | 2013-06-14 | 2013-06-14 15:35 | 2013-06-14 15:43 | PAYNE - N/A | 90 | 5.7 | Yes | Yes | 21.2 | 22.5 | -1.3 | 3606ED1978564FF5942E72C85EAA095C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Clovis | CA | 93611-6024 |  | 2013-06-14 | 2013-06-14 15:59 | 2013-06-14 16:11 | PAYNE - N/A | 90 | 2.8 | Yes | Yes | 18.8 | 20.6 | -1.8 | 07649A9DF5AC44D9903233550FC0ED92 |  | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Cameron Park | CA | 95682-8626 |  | 2013-06-20 | 2013-06-20 12:58 | 2013-06-20 13:28 | PAYNE - PH13NR036-F | 115 | 46.1 | Yes | Yes | 17 | 19.9 | -2.9 | 4FB527331DFF4016B6E79AFC36F577B0 |  | R22 | Non-TXV |  | 40.09% | 0.59913 | 77.04% | [5 empty] | Non-TXV | 40.09%
Stockton | CA | 95207-6508 |  | 2013-07-29 | 2013-07-29 09:59 | 2013-07-29 10:17 | RUUD - UAFD036JAS | 80 | -4.7 | Yes | Yes | 18.6 | 18.2 | 0.4 | D867B475ABBF45F787657E0F5E95DE6E |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Stockton | CA | 95215-9703 |  | 2013-06-06 | 2013-06-06 11:35 | 2013-06-06 11:35 | GUARDIAN - TCGD60S21S2A | 84 | 0 | Yes | Yes | 20.2 | 18.6 | 1.7 | 4F695D87867A4161A45F3D8125949B18 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7540 |  | 2013-06-17 | 2013-06-17 10:01 | 2013-06-17 10:03 | CARRIER - 7777UNK | 80 | 3.8 | Yes | Yes | 25.7 | 21.5 | 4.2 | 79A6D9ED6AF64BE6A429334ADA3BBAA0 |  | R22 | Non-TXV |  | 4.75% | 0.9525 | 9.128% | [5 empty] | Non-TXV | 4.75%
Stockton | CA | 95207-5132 |  | 2013-06-01 | 2013-06-01 09:41 | 2013-06-01 10:02 | AMANA - RCC36A2B | 114 | 5.2 | Yes | Yes | 19.5 | 19 | 0.5 | 1F7D784589A34CDFB2CBE8DCAC729E6E |  | R22 | Non-TXV |  | 4.561% | 0.95439 | 8.766% | [5 empty] | Non-TXV | 4.561%
Stockton | CA | 95219-3629 |  | 2013-06-20 | 2013-06-20 12:53 | 2013-06-20 13:11 | - 113RNA042-A | 115 | -8.1 | Yes | Yes | 26 | 22.3 | 3.7 | C1AD84DF796C403CB7C67C54A1BF7061 |  | R22 | Non-TXV |  | -7.043% | 1.0704 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.043%
Stockton | CA | 95206-4507 |  | 2013-06-13 | 2013-06-13 11:29 | 2013-06-13 11:45 | GOODMAN - CLJ48-I | 85 | 14.1 | Yes | Yes | 19.4 | 20.4 | -1 | 02851F816C99460CBDBAF77A2AAB2F24 |  | R22 | Non-TXV |  | 16.59% | 0.83412 | 31.88% | [5 empty] | Non-TXV | 16.59%
Tracy | CA | 95376-2135 |  | 2013-05-24 | 2013-05-24 12:59 | 2013-05-24 13:42 | WESTINGHOUSE - SP036CAW | 55 | 3.9 | Yes | Yes | 24.2 | 21 | 3.3 | E51E41A9ED3240DEA524A1F2EC1BD006 |  | R22 | TXV |  | 7.091% | 0.92909 | 13.63% | [5 empty] | TXV | 7.091%
Stockton | CA | 95206-6035 |  | 2013-06-19 | 2013-06-19 15:31 | 2013-06-19 15:48 | CARRIER - ACS048A2B2 | 101 | 8.8 | Yes | Yes | 22.7 | 20.4 | 2.3 | 1FF45B5880474492A09BD4E6EF1B3ABE |  | R22 | Non-TXV |  | 8.713% | 0.91287 | 16.74% | [5 empty] | Non-TXV | 8.713%
Fresno | CA | 93703-3226 |  | 2013-06-03 | 2013-06-03 13:13 | 2013-06-03 13:38 | CARRIER - UNK | 102 | 3.7 | Yes | Yes | 17.9 | 19.8 | -1.9 | 12A174CC1EBB4915B4AA1F64F0B8192B |  | R22 | Non-TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | Non-TXV | 3.627%
Chico | CA | 95926-2032 |  | 2013-06-06 | 2013-06-06 09:28 | 2013-06-06 16:31 | LENNOX - GCS20R-411-100-1P | 70 | 2.2 | Yes | Yes | 16.7 | 18.6 | -1.9 | 52426108B32A4EDF93E1DABE927BDBB7 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Clovis | CA | 93612-5868 |  | 2013-06-25 | 2013-06-25 11:18 | 2013-06-25 11:40 | CARRIER - N/A | 90 | 2.9 | Yes | Yes | 20.2 | 18 | 2.2 | DD80581979324353BC341285291E4D7F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Stockton | CA | 95212-3463 |  | 2013-06-18 | 2013-06-18 09:45 | 2013-06-18 10:08 | CARRIER - 38CKC042340 | 80 | 3.1 | Yes | Yes | 20.4 | 19.8 | 0.6 | 14A66BBD85EE4F6C92EA9EEAAF754736 |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Chico | CA | 95926-1670 |  | 2013-06-06 | 2013-06-06 17:11 | 2013-06-06 17:11 | DAY & NIGHT - PGD324060K00K1 | 110 | 0 | Yes | Yes | 19.1 | 18 | 1.1 | E951D7EBE82D4C2DB2951C61AAB432E8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2602 |  | 2013-07-31 | 2013-07-31 13:56 | 2013-07-31 14:15 | DAY & NIGHT - 24/60YAC-108C | 51 | -3 | Yes | Yes | 21.7 | 20.4 | 1.3 | E3B80F0BE8CA4199B2BA9E537B278041 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95206-6291 |  | 2013-06-19 | 2013-06-19 09:34 | 2013-06-19 09:54 | CARRIER - 38CKC030340 | 70 | 5.4 | Yes | Yes | 20.1 | 18.6 | 1.6 | 0530E19CC18E4C3BB3DFD8C8DACE291E |  | R22 | TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | TXV | 7.714%
Chico | CA | 95926-7156 |  | 2013-07-02 | 2013-07-02 17:25 | 2013-07-02 17:52 | YORK - H2CB036S06A | 117 | 7.5 | Yes | Yes | 23.4 | 20.1 | 3.4 | A7124DE71BA24C78A57F3EB66881929B |  | R22 | Non-TXV |  | 6.41% | 0.9359 | 12.32% | [5 empty] | Non-TXV | 6.41%
Chico | CA | 95973-0911 |  | 2013-08-21 | 2013-08-21 16:34 | 2013-08-21 16:34 | PAYNE - PY1PNB024060AAAA | 77 | 0 | Yes | Yes | 14.8 | 17.7 | -2.9 | B116E09B8F3B4663B380FBB9494F08D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-6914 |  | 2013-06-05 | 2013-06-05 08:57 | 2013-06-05 10:30 | PAYNE - PY2PNB024040ABAA | 55 | -5.2 | Yes | Yes | 22.4 | 20.4 | 2 | B416BFAADC294CCF8A8298B657436D92 |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Gridley | CA | 95948-9559 |  | 2013-09-09 | 2013-09-09 12:03 | 2013-09-09 12:24 | RUUD - 10AJB2401 | 70 | 3.4 | Yes | Yes | 17.5 | 16.6 | 0.9 | B0C26AE3C52C4F8DA3392E64B07EE968 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Los Banos | CA | 93635-9489 |  | 2013-07-30 | 2013-07-30 12:55 | 2013-07-30 12:58 | BRYANT - 561CJ036-F | 70 | 3.4 | Yes | Yes | 18.1 | 19.2 | -1.1 | AB177E64879B4D8594FD213894F658DA |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Yuba City | CA | 95991-6661 |  | 2013-06-07 | 2013-06-07 10:51 | 2013-06-07 11:21 | DAY & NIGHT - 585HJ024040ABAE | 68 | -6.4 | Yes | Yes | 18 | 19.2 | -1.2 | 3EDD298292AD4CC38F1DB7E4D9FAB572 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Clovis | CA | 93611-4587 |  | 2013-06-15 | 2013-06-15 08:57 | 2013-06-15 09:21 | BDP - 585EJW030050AAAF | 58 | 3.8 | Yes | Yes | 20.3 | 20.4 | -0.1 | 783ACD0C979B4A5C9A700E2993D24590 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.552% | 0.93448 | 12.59% | [5 empty] | Non-TXV | 6.552%
Clovis | CA | 93612-2688 |  | 2013-06-19 | 2013-06-19 10:23 | 2013-06-19 10:23 | RHEEM - RRNL-B030JK06X | 76 | 0 | Yes | Yes | 23.5 | 21.2 | 2.3 | AF2384B6FC6648ABBE9E7B74F228DE1A |  | R410A | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-6732 |  | 2013-06-07 | 2013-06-07 14:54 | 2013-06-07 15:11 | LENNOX - 10ACC-00-230-04 | 130 | 4.1 | Yes | Yes | 18 | 20.9 | -2.9 | B8192AA140BB445B9063636FC24679C6 |  | R22 | Non-TXV |  | 3.154% | 0.96846 | 6.061% | [5 empty] | Non-TXV | 3.154%
Fresno | CA | 93703-4161 |  | 2013-10-26 | 2013-10-26 09:38 | 2013-10-26 10:27 | BDP - 588ANE036080ABAF | 67 | 6.8 | Yes | Yes | 21 | 21 | 0 | 10264A38923D453D99006437981B7C38 |  | R22 | Non-TXV |  | 10.15% | 0.89851 | 19.5% | [5 empty] | Non-TXV | 10.15%
Tracy | CA | 95377-8745 |  | 2013-06-07 | 2013-06-07 17:26 | 2013-06-07 17:48 | DAY & NIGHT - 562AJX042-A | 168 | 9.7 | Yes | Yes | 24.7 | 18.8 | 6 | F1DC14B171714B8E8ED495712F0553FA |  | R22 | Non-TXV |  | 5.774% | 0.94226 | 11.1% | [5 empty] | Non-TXV | 5.774%
Manteca | CA | 95336-7075 |  | 2013-05-28 | 2013-05-28 11:24 | 2013-05-28 11:42 | YORK - H1RC036SO6D | 98 | 2.9 | Yes | Yes | 19.7 | 22 | -2.3 | 5E60F146F4AC4CBE9E0D25B64BBCCBF6 |  | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.687% | [5 empty] | Non-TXV | 2.959%
Tracy | CA | 95376-2620 |  | 2013-06-07 | 2013-06-07 10:02 | 2013-06-07 10:31 | RHEEM - RRAA-08E37AR | 85 | 4.2 | Yes | Yes | 22.5 | 19 | 3.5 | 6B7D25722D4947FAA55D5F114ECC27BB |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Merced | CA | 95340-4516 |  | 2013-06-17 | 2013-06-17 09:14 | 2013-06-17 09:17 | CARRIER - 48SS048080301 | 101 | 9.6 | Yes | Yes | 21.1 | 18.8 | 2.3 | F8C9D619399549E4BAE980859C3974BB |  | R22 | Non-TXV |  | 9.505% | 0.90495 | 18.27% | [5 empty] | Non-TXV | 9.505%
Chico | CA | 95926-2413 |  | 2013-08-01 | 2013-08-01 09:03 | 2013-08-01 09:22 | LENNOX - 12ACB36-1P | 116 | 4.1 | Yes | Yes | 21.4 | 19.9 | 1.5 | 0A425FFD2190445BA81A388C0ABC3705 |  | R22 | Non-TXV |  | 3.534% | 0.96466 | 6.792% | [5 empty] | Non-TXV | 3.534%
Fresno | CA | 93726-2208 |  | 2013-05-31 | 2013-05-31 14:32 | 2013-05-31 15:00 | YORK - DCYZ-F036N070A | 64 | 4 | Yes | Yes | 21.7 | 19.5 | 2.2 | B3AFF3AA54D847A48756B2420785F39A |  | R410A | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Granite Bay | CA | 95746-6646 |  | 2013-08-23 | 2013-08-23 16:36 | 2013-08-23 17:00 | OTHER - AC1BNO60-A | 180 | -10.6 | Yes | Yes | 24.5 | 20.4 | 4.1 | 412B8C8005CD4C4D989B0139DB9E85FD |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Oroville | CA | 95966-9425 |  | 2013-07-29 | 2013-07-29 14:50 | 2013-07-29 21:28 | TRANE - TTB036C1000A2 | 90 | 3 | Yes | Yes | 17.5 | 20.4 | -2.9 | 23752ABF8B6146C28DA9009FA12F39FD |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93703-2051 |  | 2013-06-05 | 2013-06-05 14:16 | 2013-06-05 14:45 | AMERICAN STANDARD - YCP048F1H0AB | 70 | 3.1 | Yes | Yes | 16.6 | 19.3 | -2.7 | 10C51F5C93F94AF8829B81ED0E3A1A04 |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Chico | CA | 95926-1520 |  | 2013-07-12 | 2013-07-12 17:32 | 2013-07-12 17:50 | LENNOX - HS16-311V-4P | 112 | 5.5 | Yes | Yes | 15.8 | 17.4 | -1.6 | 123E66B637394254A833A6F7E2DDA13D |  | R22 | Non-TXV |  | 4.911% | 0.95089 | 9.437% | [5 empty] | Non-TXV | 4.911%
Red Bluff | CA | 96080-8825 |  | 2013-09-18 | 2013-09-18 14:38 | 2013-09-18 15:04 | AMERICAN STANDARD - YCY036G1MOAC | 129 | 10.8 | Yes | Yes | 19.9 | 19.9 | 0 | 5DA073B6639B4B629790D752AFEAD10F |  | R22 | Non-TXV |  | 8.372% | 0.91628 | 16.09% | [5 empty] | Non-TXV | 8.372%
Stockton | CA | 95210-2046 |  | 2013-06-18 | 2013-06-18 12:17 | 2013-06-18 12:33 | RUUD - URMA-A036JK08X | 99 | -5.8 | Yes | Yes | 23.1 | 20.4 | 2.7 | 0554E94330054C2A98EF426D1B1B86CF |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Newman | CA | 95360-1458 |  | 2013-06-05 | 2013-06-05 10:01 | 2013-06-05 10:23 | CARRIER - 591ANX0300000AAAA | 65 | 3.3 | Yes | Yes | 20.3 | 19.8 | 0.5 | C13136EF1C5A40678EA8BCE5EA8B17CF |  | R22 | Non-TXV |  | 5.077% | 0.94923 | 9.757% | [5 empty] | Non-TXV | 5.077%
Magalia | CA | 95954-9476 |  | 2013-07-17 | 2013-07-17 13:40 | 2013-07-17 14:22 | TRANE - 4YCZ6048A1096AB | 136 | 10.6 | Yes | Yes | 20.4 | 19.9 | 0.5 | C37D272E9B5941B0B5A789427CF55569 |  | R410A | Non-TXV |  | 7.794% | 0.92206 | 14.98% | [5 empty] | Non-TXV | 7.794%
Magalia | CA | 95954-9520 |  | 2013-07-19 | 2013-07-19 11:49 | 2013-07-19 18:14 | COLEMAN - ERCS0421CAG | 152 | 4.5 | Yes | Yes | 21.4 | 21.4 | 0 | F0C3F3E7797D4AE593434406DA12480B |  | R22 | Non-TXV |  | 2.961% | 0.97039 | 5.689% | [5 empty] | Non-TXV | 2.961%
Stockton | CA | 95210-1261 |  | 2013-06-06 | 2013-06-06 10:49 | 2013-06-06 11:10 | GOODMAN - CM25-1EB | 54 | -3.2 | Yes | Yes | 16.7 | 19.3 | -2.6 | 02C9FCF2C83A4ED2B87CD6511F577DBC |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Chico | CA | 95973-0533 |  | 2013-06-04 | 2013-06-04 10:06 | 2013-06-04 10:22 | TRANE - TTB018C10000A2 | 63 | 6.7 | Yes | Yes | 19.5 | 21.3 | -1.8 | 1A14F53162204D298C8810774A4FDC56 |  | R22 | Non-TXV |  | 10.63% | 0.89365 | 20.44% | [5 empty] | Non-TXV | 10.63%
Placerville | CA | 95667-9227 |  | 2013-05-29 | 2013-05-29 12:50 | 2013-05-29 13:30 | TRANE - TTX036C100A1 | 152 | -14.3 | Yes | Yes | 17.5 | 19.5 | -2 | AEEBCBB451444A5398167172B963EA35 |  | R22 | Non-TXV |  | -9.408% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.408%
Stockton | CA | 95206-4772 |  | 2013-06-17 | 2013-06-17 09:12 | 2013-06-17 09:34 | OTHER - 13ACD-030-230-12 | 77 | -7.2 | Yes | Yes | 20.4 | 18.1 | 2.3 | BEFE39DE559A41938AEC22558BD2A132 |  | R22 | Non-TXV |  | -9.351% | 1.0935 | 2.619% |  |  |  |  | Non-TXV |  |  | -9.351%
Rocklin | CA | 95765-6107 |  | 2013-06-17 | 2013-06-17 14:29 | 2013-06-17 14:52 | CARRIER - 38BRC060 | 200 | 9.2 | Yes | Yes | 20 | 22.1 | -2.1 | D47EC441717D48778396B2F428C9364F |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Clovis | CA | 93611-2034 |  | 2013-06-12 | 2013-06-12 15:29 | 2013-06-12 16:00 | AMANA - SPCG360451A | 120 | 3.7 | Yes | Yes | 27.5 | 22.4 | 5.1 | 7835F9285B6B4FE08517C54432FC8E89 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Auburn | CA | 95603-3307 |  | 2013-06-17 | 2013-06-17 18:17 | 2013-06-17 18:36 | AIRE-FLO - AFAIR10B36-B | 80 | -3.3 | Yes | Yes | 19.6 | 22.5 | -2.9 | 28188734307B436992C8F731DCAD4D09 |  | R22 | TXV |  | -4.125% | 1.0413 | 1.155% |  |  |  |  | TXV |  |  | -4.125%
Tracy | CA | 95304-8418 |  | 2013-05-30 | 2013-05-30 10:19 | 2013-05-30 10:19 | BRYANT - 598ANO48-D | 214 | 0 | Yes | Yes | 27.7 | 22.2 | 5.5 | 34778A9D68D34A94A63B705BA74BDA29 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-7550 |  | 2013-06-21 | 2013-06-21 14:15 | 2013-06-21 14:15 | DAY & NIGHT - 51ANX024000AAAA | 60 | 0 | Yes | Yes | 16 | 18.8 | -2.8 | 08EC97CF7BE04B41B781E787118B4428 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3501 |  | 2013-06-21 | 2013-06-21 13:02 | 2013-06-21 13:21 | YORK - AC060X1223A | 147 | 35.2 | Yes | Yes | 19.5 | 20.6 | -1.1 | E416059EF6E64E639D4384D3170A27B3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 23.95% | 0.76054 | 46.02% | [5 empty] | Non-TXV | 23.95%
Rocklin | CA | 95677-4038 |  | 2013-06-15 | 2013-06-15 08:57 | 2013-06-15 09:16 | GOODMAN - CKL62-1 | 137 | -11.3 | Yes | Yes | 25.4 | 20.1 | 5.3 | 4FE5A8A76AD54FB4942EFA945BF860EE |  | R22 | Non-TXV |  | -8.248% | 1.0825 | 2.31% |  |  |  |  | Non-TXV |  |  | -8.248%
Grass Valley | CA | 95945-5406 |  | 2013-06-04 | 2013-06-04 10:53 | 2013-06-04 11:13 | BRYANT - 552AN036-E | 87 | 10 | Yes | Yes | 23.1 | 18.7 | 4.4 | 968A72F5FCB74A6AB66327B111CB6B2D |  | R410A | TXV |  | 11.49% | 0.88506 | 22.09% | [5 empty] | TXV | 11.49%
Merced | CA | 95341-6852 |  | 2013-06-08 | 2013-06-08 09:27 | 2013-06-08 09:32 | RHEEM - 7777UNK | 80 | 3.2 | Yes | Yes | 16 | 18 | -2 | FE873267ABB34634940823FD006FB0E1 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Dinuba | CA | 93618-1716 |  | 2013-06-21 | 2013-06-21 15:59 | 2013-06-21 16:23 | NORDYNE - N/A | 120 | 4.2 | Yes | Yes | 19.8 | 21.7 | -1.9 | 6962CCF540CA42019C440387F1D1FC6A |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Livingston | CA | 95334-9566 |  | 2013-06-11 | 2013-06-11 13:10 | 2013-06-11 13:31 | YORK - D3NZ030N03606NXA | 85 | 2.6 | Yes | Yes | 22 | 19.5 | 2.5 | F63E1A428ADF447F8818D3C7BCE9A61F |  | R410A | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Yuba City | CA | 95991-4373 |  | 2013-06-06 | 2013-06-06 10:02 | 2013-06-06 10:20 | DAY & NIGHT - 541B028SHP | 90 | 9.1 | Yes | Yes | 20 | 19.5 | 0.5 | BC85925AB6A347CD8A05F2EB53B06868 |  | R22 | Non-TXV |  | 10.11% | 0.89889 | 19.43% | [5 empty] | Non-TXV | 10.11%
Stockton | CA | 95215-8115 |  | 2013-06-05 | 2013-06-05 13:41 | 2013-06-05 13:59 | HEIL - NAC036AKC3 | 94 | 20.7 | Yes | Yes | 20.9 | 19.9 | 1 | 08A0323982A344C0A33F5150559DAADC |  | R22 | Non-TXV |  | 22.02% | 0.77979 | 42.32% | [5 empty] | Non-TXV | 22.02%
Stockton | CA | 95207-3107 |  | 2013-06-13 | 2013-06-13 10:18 | 2013-06-13 10:18 | BRYANT - 561CJX030-D | 70 | 0 | Yes | Yes | 25.1 | 19.9 | 5.2 | 678C17ADBBA64E27AC2FC3504E3FBD8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7027 |  | 2013-06-08 | 2013-06-08 10:57 | 2013-06-08 10:58 | BRYANT - 582ANW042060NAAG | 100 | 4.9 | Yes | Yes | 24.4 | 18.5 | 5.9 | 775058474E0742C193F0615C874CBF75 |  | R22 | Non-TXV |  | 4.9% | 0.951 | 9.417% | [5 empty] | Non-TXV | 4.9%
Fresno | CA | 93703-2675 |  | 2013-07-03 | 2013-07-03 16:45 | 2013-07-03 17:09 | BDP - 585B024050YACR | 51 | 5.8 | Yes | Yes | 18.9 | 16 | 2.9 | 8617EB7DEB214F1FA8D94E6E22FAC16C |  | R22 | Non-TXV |  | 11.37% | 0.88627 | 21.86% | [5 empty] | Non-TXV | 11.37%
Rocklin | CA | 95765-5811 |  | 2013-08-29 | 2013-08-29 11:32 | 2013-08-29 11:52 | NORDYNE - JS5BD-048KA | 126 | 24.7 | Yes | Yes | 23.1 | 18.5 | 4.6 | 5395B92ED47F41D58955F557B5D81881 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.6% | 0.80397 | 37.67% | [5 empty] | Non-TXV | 19.6%
Fresno | CA | 93703-2674 |  | 2013-07-03 | 2013-07-03 17:38 | 2013-07-03 18:02 | BDP - 585B024050YACR | 51 | 14.1 | Yes | Yes | 16.6 | 16.6 | 0 | E40D029DEAFB45F0BAF80F8440726E45 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 27.65% | 0.72353 | 53.13% | [5 empty] | Non-TXV | 27.65%
Granite Bay | CA | 95746-6210 |  | 2013-06-21 | 2013-06-21 10:15 | 2013-06-21 11:09 | UNITARY PRODUCTS GROUP - DAYP-F036N070A | 108 | -5.3 | Yes | Yes | 22.9 | 19.5 | 3.4 | 8AA18640222C45A29CDDC933C771C419 |  | R22 | Non-TXV |  | -4.907% | 1.0491 | 1.374% |  |  |  |  | Non-TXV |  |  | -4.907%
Stockton | CA | 95210-4468 |  | 2013-07-30 | 2013-07-30 11:33 | 2013-07-30 11:59 | DAY & NIGHT - 561CJ048-B | 103 | 3.6 | Yes | Yes | 25.1 | 19.3 | 5.8 | E833A51FA03E415FBA6A62089008C14A |  | R22 | Non-TXV |  | 3.495% | 0.96505 | 6.717% | [5 empty] | Non-TXV | 3.495%
Yuba City | CA | 95991-6143 |  | 2013-07-17 | 2013-07-17 14:06 | 2013-07-17 14:22 | GOODMAN - GSX160601AB | 200 | 6 | Yes | Yes | 19 | 19.3 | -0.3 | 52A85D875F5E4B47B80C673FDF8FEC85 |  | R410A | TXV |  | 3% | 0.97 | 5.765% | [5 empty] | TXV | 3%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 09:39 | 2013-07-30 09:55 | CARRIER - 38TXA042330 | 132 | 5 | Yes | Yes | 25 | 20.9 | 4.1 | E0FE742718284CD7ADE93BFB5FA5C97E |  | R410A | TXV |  | 3.788% | 0.96212 | 7.279% | [5 empty] | TXV | 3.788%
Dinuba | CA | 93618-3473 |  | 2013-07-25 | 2013-07-25 21:45 | 2013-07-25 22:18 | ICP - PGF030K060A | 52 | 1.8 | Yes | Yes | 14.8 | 17 | -2.2 | F24C10FB4DF34467BF13A10C68AF1E36 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Gerber | CA | 96035-9715 |  | 2013-08-19 | 2013-08-19 14:57 | 2013-08-19 16:15 | DAY & NIGHT - PGD324060K001C1 | 72 | 2.5 | Yes | Yes | 20.6 | 16.3 | 4.3 | F6DF437E1AC645A8B37DA133DD0FAA75 |  | R410A | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Rocklin | CA | 95677-1842 |  | 2013-06-17 | 2013-06-17 13:21 | 2013-06-17 13:40 | TRANE - YCX036G1M0AA | 109 | -6.4 | Yes | Yes | 23 | 20.9 | 2.1 | 7BC28C65F713403B8623BCA144F35F47 |  | R22 | Non-TXV |  | -5.872% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.872%
Stockton | CA | 95210-5673 |  | 2013-05-29 | 2013-05-29 09:27 | 2013-05-29 09:27 | CONCORD - 4AC13L36P-7A | 84 | 0 | Yes | Yes | 27.7 | 18.2 | 9.5 | DE367710BA214D679E2CFB5ADFAACF83 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6261 |  | 2013-06-18 | 2013-06-18 16:33 | 2013-06-18 17:34 | CARRIER - 561AJX048000ACAA | 104 | 5.1 | Yes | Yes | 26.5 | 20.8 | 5.7 | 3897B0C174D64E1391536F2459F9AD16 |  | R22 | Non-TXV |  | 4.904% | 0.95096 | 9.424% | [5 empty] | Non-TXV | 4.904%
Manteca | CA | 95337-7921 |  | 2013-05-31 | 2013-05-31 10:36 | 2013-05-31 10:57 | UNITARY PRODUCTS GROUP - H2RC030S06A | 88 | 2.7 | Yes | Yes | 22.4 | 19.8 | 2.6 | DD79F0CB97A94C638B6F8B4960518472 |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Yuba City | CA | 95991-5312 |  | 2013-07-15 | 2013-07-15 09:02 | 2013-07-15 09:25 | RUUD - 13AJN36A01 | 90 | 3.3 | Yes | Yes | 20 | 19.1 | 0.9 | A4EE257F91F841089BA6C116F4DC26C3 |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Rocklin | CA | 95765-6216 |  | 2013-06-15 | 2013-06-15 13:15 | 2013-06-15 13:44 | NORDYNE - JS5BD-030KA | 99 | 9.6 | Yes | Yes | 23.8 | 20.2 | 3.6 | 07D78F9754A84F2F84141EAE7B439CC3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.697% | 0.90303 | 18.64% | [5 empty] | Non-TXV | 9.697%
Paso Robles | CA | 93446-4451 |  | 2013-08-06 | 2013-08-06 10:15 | 2013-08-06 10:40 | DAY & NIGHT - 5658J030 | 78 | 4.2 | Yes | Yes | 21.6 | 19.3 | 2.3 | 128FBFC140E541D096302BD2A4A38F93 |  | R22 | Non-TXV |  | 5.385% | 0.94615 | 10.35% | [5 empty] | Non-TXV | 5.385%
Stockton | CA | 95206-6379 |  | 2013-06-21 | 2013-06-21 10:20 | 2013-06-21 10:20 | GOODMAN - CLJ42-1A | 99 | 0 | Yes | Yes | 18.8 | 18.8 | 0 | 5BFAA0FA589C4285B6BC5F1670BEBA5A |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1435 |  | 2013-06-18 | 2013-06-18 10:55 | 2013-06-18 11:12 | RHEEM - UNK | 96 | -5.6 | Yes | Yes | 24.9 | 21 | 3.9 | 53C02E4BA44844C5A925D5AD75111E72 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95204-2319 |  | 2013-06-01 | 2013-06-01 12:56 | 2013-06-01 13:26 | CARRIER - 38CKC030340 | 67 | 4.3 | Yes | Yes | 18.4 | 19.3 | -0.9 | 29231BC611604F69B6CC072711FD3FFA |  | R22 | TXV |  | 6.418% | 0.93582 | 12.33% | [5 empty] | TXV | 6.418%
Chico | CA | 95926-4377 |  | 2013-06-06 | 2013-06-06 17:19 | 2013-06-06 18:02 | BDP - 585GJ018040 | 55 | 7.6 | Yes | Yes | 18.5 | 19.9 | -1.4 | A9DFF12F05CE4B6D99AA0AE85C11D150 |  | R22 | Non-TXV |  | 13.82% | 0.86182 | 26.56% | [5 empty] | Non-TXV | 13.82%
Chico | CA | 95928-7647 |  | 2013-06-05 | 2013-06-05 12:52 | 2013-06-05 13:31 | BDP - 279507981 | 99 | 3.1 | Yes | Yes | 20.9 | 20.4 | 0.5 | DF89BD4F1C144AD89CAC33F4B526BC35 |  | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Oroville | CA | 95966-9532 |  | 2013-06-21 | 2013-06-21 10:52 | 2013-06-21 11:42 | AMANA - RCC36C2A | 110 | 8.1 | Yes | Yes | 25.2 | 21 | 4.2 | 203B4940B4894682A2FBAF3E36F1CA08 |  | R22 | Non-TXV |  | 7.364% | 0.92636 | 14.15% | [5 empty] | Non-TXV | 7.364%
Hamilton City | CA | 95951-0000 |  | 2013-09-05 | 2013-09-05 11:01 | 2013-09-05 12:48 | YORK - H2RA030S06D | 62 | 4.6 | Yes | Yes | 21.5 | 17.9 | 3.6 | CD311D8B2D53497C8E893EEFC4459B27 |  | R22 | Non-TXV |  | 7.419% | 0.92581 | 14.26% | [5 empty] | Non-TXV | 7.419%
Fresno | CA | 93703-1228 |  | 2013-05-29 | 2013-05-29 18:11 | 2013-05-29 18:41 | CARRIER - 48KL136311BE | 74 | 9.8 | Yes | Yes | 17.5 | 19.2 | -1.7 | CB96052EBAAF4E05BC007B9189A339C1 |  | R22 | Non-TXV |  | 13.24% | 0.86757 | 25.45% | [5 empty] | Non-TXV | 13.24%
Chico | CA | 95973-0445 |  | 2013-07-03 | 2013-07-03 16:31 | 2013-07-03 16:49 | DAY & NIGHT - 5858030075YACR | 50 | 10 | Yes | Yes | 21.3 | 22.6 | -1.3 | 84BD74C1F9B8442FB93E597A66372281 |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Paradise | CA | 95969-5700 |  | 2013-06-13 | 2013-06-13 16:08 | 2013-06-13 17:16 | CARRIER - NA | 85 | 2.5 | Yes | Yes | 21 | 21.3 | -0.3 | 59E57244CD27456CBF4516FBC8E8E12D |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Cameron Park | CA | 95682-9127 |  | 2013-05-30 | 2013-05-30 17:36 | 2013-05-30 17:56 | TRANE - BWX736A100AD | 139 | 5.1 | Yes | Yes | 19 | 21.8 | -2.8 | 04DBE6D4F56B4A569C6B2AFEAD1EFE8B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.669% | 0.96331 | 7.051% | [5 empty] | Non-TXV | 3.669%
Chico | CA | 95926-7757 |  | 2013-06-05 | 2013-06-05 09:35 | 2013-06-05 09:51 | OTHER - 565AJ0423683A00820 | 94 | 5.8 | Yes | Yes | 20 | 19.4 | 0.6 | 2732BCF0D711468C8DEE0B43CA4D73DD |  | R22 | Non-TXV |  | 6.17% | 0.9383 | 11.86% | [5 empty] | Non-TXV | 6.17%
Chico | CA | 95973-8704 |  | 2013-07-10 | 2013-07-10 16:25 | 2013-07-10 16:43 | AMANA - ASX140241CB | 88 | 13.8 | Yes | Yes | 23.9 | 21.5 | 2.4 | 6922E4DEC8464FAA993F89F84A684B2F |  | R410A | Non-TXV |  | 15.68% | 0.84318 | 30.14% | [5 empty] | Non-TXV | 15.68%
Chico | CA | 95926-4050 |  | 2013-06-05 | 2013-06-05 15:11 | 2013-06-05 15:11 | PAYNE - PY1PN036090AA | 56 | 0 | Yes | Yes | 21 | 19.1 | 1.9 | 4F56430DFF4A4262B5877BCE8C1A16CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-6084 |  | 2013-05-31 | 2013-05-31 10:39 | 2013-05-31 10:39 | LENNOX - 10ACC-042-230-03 | 81 | 0 | Yes | Yes | 20.2 | 21.5 | -1.3 | 589D4E01F4784182832434080D86B23C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6254 |  | 2013-06-15 | 2013-06-15 10:47 | 2013-06-15 11:02 | CARRIER - 48KLA136--300E | 102 | 3.5 | Yes | Yes | 24.1 | 21.4 | 2.7 | 988F47E3E4C448B58A9AE2F03D8A4E21 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.431% | 0.96569 | 6.594% | [5 empty] | Non-TXV | 3.431%
Stockton | CA | 95207-7423 |  | 2013-06-14 | 2013-06-14 11:37 | 2013-06-14 11:37 | TRANE - TTX042D100A0 | 130 | 0 | Yes | Yes | 25.5 | 21.8 | 3.7 | CAFC2422B58A4839916C46F596DC82BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2744 |  | 2013-07-11 | 2013-07-11 15:02 | 2013-07-11 15:23 | PAYNE - 591AN018-A | 40 | -3.8 | Yes | Yes | 19.2 | 22.1 | -2.9 | 229BDCE50AA1456F92A15B973FFE2CBD |  | R22 | Non-TXV |  | -9.5% | 1.095 | 2.66% |  |  |  |  | Non-TXV |  |  | -9.5%
Red Bluff | CA | 96080-8976 |  | 2013-08-09 | 2013-08-09 14:59 | 2013-08-09 15:46 | TRANE - 2TTB3036A1000AA | 101 | 9.7 | Yes | Yes | 17.9 | 19.5 | -1.6 | 727376A7CC294FA5B60791402D3F2F96 |  | R22 | Non-TXV |  | 9.604% | 0.90396 | 18.46% | [5 empty] | Non-TXV | 9.604%
Lincoln | CA | 95648-8456 |  | 2013-08-22 | 2013-08-22 10:55 | 2013-08-22 11:20 | YORK - H2RA036S06E | 63 | 4.4 | Yes | Yes | 19.5 | 21.5 | -2 | FFA5BF83C6E041D2972E56D9A5BB31C1 |  | R22 | TXV |  | 6.984% | 0.93016 | 13.42% | [5 empty] | TXV | 6.984%
Manteca | CA | 95337-8009 |  | 2013-05-24 | 2013-05-24 13:47 | 2013-05-24 14:08 | YORK - H2CB042S06A | 108 | 8.4 | Yes | Yes | 25.1 | 21.4 | 3.7 | 601828B7E89941F5938EB0E85B98C010 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Cutler | CA | 93615-9737 |  | 2013-08-21 | 2013-08-21 14:41 | 2013-08-21 15:08 | GOODMAN - GPG13360701AC | 112 | 3.6 | Yes | Yes | 23.5 | 19.4 | 4.1 | 1616218E9923478EB58B7F6ECED9025B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Stockton | CA | 95207-7314 |  | 2013-06-01 | 2013-06-01 10:29 | 2013-06-01 10:29 | TRANE - TTN036C1004 | 93 | 0 | Yes | Yes | 20.5 | 19.7 | 0.8 | 68A93DDB9ABF4B3EA69D640B448EAE8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-2045 |  | 2013-06-12 | 2013-06-12 17:07 | 2013-06-12 17:27 | LENNOX - 10GCS036-75-1PA | 58 | 3.6 | Yes | Yes | 26.4 | 22.1 | 4.4 | 11BA258252B24184B35BF2E21F8F02C3 |  | R22 | Non-TXV |  | 6.207% | 0.93793 | 11.93% | [5 empty] | Non-TXV | 6.207%
Red Bluff | CA | 96080-9268 |  | 2013-05-31 | 2013-05-31 19:18 | 2013-05-31 19:42 | ARMSTRONG - SCU12E36A | 99 | 9.6 | Yes | Yes | 24.2 | 22.6 | 1.6 | 759F42F40853469D934422B51A0EAF47 |  | R22 | Non-TXV |  | 9.697% | 0.90303 | 18.64% | [5 empty] | Non-TXV | 9.697%
Red Bluff | CA | 96080-9268 |  | 2013-05-31 | 2013-05-31 18:50 | 2013-05-31 19:14 | ARMSTRONG - SCU12E36A-1 | 99 | 9 | Yes | Yes | 22.1 | 21.1 | 1 | 49FBF81CCDB848E8A7294DD3AED6524A |  | R22 | Non-TXV |  | 9.091% | 0.90909 | 17.47% | [5 empty] | Non-TXV | 9.091%
Tracy | CA | 95376-2209 |  | 2013-06-25 | 2013-06-25 13:10 | 2013-06-25 13:31 | RHEEM - RACA-036AA0 | 85 | 8.2 | Yes | Yes | 24.6 | 18.8 | 5.9 | 67694766566F4F1FAAFAB490D5BEB0DB |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Stockton | CA | 95203-1304 |  | 2013-05-31 | 2013-05-31 09:25 | 2013-05-31 09:44 | TRANE - YCY024G1M0AD | 104 | 3.9 | Yes | Yes | 15.4 | 17.5 | -2.1 | 7A57B0B1FEAE4ECE896AEFFFC3E44378 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Chico | CA | 95926-4382 |  | 2013-06-11 | 2013-06-11 19:05 | 2013-06-11 19:22 | DAY & NIGHT - 5856JW018040 | 55 | 7.8 | Yes | Yes | 16.7 | 18 | -1.3 | C81344B0933B4719B4EE2A3AFDF50B44 |  | R22 | Non-TXV |  | 14.18% | 0.85818 | 27.25% | [5 empty] | Non-TXV | 14.18%
Clovis | CA | 93611-2037 |  | 2013-06-12 | 2013-06-12 16:03 | 2013-06-12 16:34 | BDP - 5589ANE042120ACBF | 87 | 3 | Yes | Yes | 21.8 | 18.1 | 3.7 | D6760484B91145FF855C0AB89DF5700E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Stockton | CA | 95219-3561 |  | 2013-06-20 | 2013-06-20 11:28 | 2013-06-20 11:51 | DAY & NIGHT - 24760YAC108C | 64 | -3.8 | Yes | Yes | 23.5 | 21.4 | 2.1 | 0207F693B4BE462A8C7C32C410927A3D |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Stockton | CA | 95207-1328 |  | 2013-05-29 | 2013-05-29 17:02 | 2013-05-29 17:19 | LENNOX - PG036K060A | 71 | 10.5 | Yes | Yes | 20.5 | 19.9 | 0.6 | 2B09A4B2C7E64C6BA94E18900E746CE7 |  | R22 | Non-TXV |  | 14.79% | 0.85211 | 28.42% | [5 empty] | Non-TXV | 14.79%
Tracy | CA | 95376-1970 |  | 2013-06-25 | 2013-06-25 12:02 | 2013-06-25 12:22 | DAY & NIGHT - 585HJ018040ABAC | 61 | -5.7 | Yes | Yes | 22 | 16.9 | 5.1 | F0240D489EDA40C69EBF6FA2B83E72E8 |  | R22 | Non-TXV |  | -9.344% | 1.0934 | 2.617% |  |  |  |  | Non-TXV |  |  | -9.344%
Rocklin | CA | 95677-2567 |  | 2013-06-11 | 2013-06-11 08:44 | 2013-06-11 09:01 | PAYNE - PA13NR030-H | 75 | 9.8 | Yes | Yes | 16 | 18.8 | -2.8 | AEDD70542CAC4371BF20C1C68B922EE4 |  | R22 | Non-TXV |  | 13.07% | 0.86933 | 25.11% | [5 empty] | Non-TXV | 13.07%
Merced | CA | 95340-0659 |  | 2013-08-20 | 2013-08-20 12:57 | 2013-08-20 12:59 | GOODMAN - CK42-1C | 92 | 3 | Yes | Yes | 24.3 | 19.6 | 4.7 | 5920A32C2E6B4B829D0F973D2B15C32D |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Stockton | CA | 95204-4244 |  | 2013-05-31 | 2013-05-31 15:13 | 2013-05-31 15:36 | RHEEM - UNK | 64 | 8.2 | Yes | Yes | 23.8 | 19.9 | 3.9 | DBE44AF711E24A4D8360E2D7ABE44BDB |  | R22 | Non-TXV |  | 12.81% | 0.87187 | 24.62% | [5 empty] | Non-TXV | 12.81%
Chico | CA | 95973-8759 |  | 2013-06-03 | 2013-06-03 09:34 | 2013-06-03 10:25 | ALLEGIANCE - 7A036A100A2 | 95 | -5.6 | Yes | Yes | 24.7 | 21.5 | 3.2 | 95D63C7A3CFF41E7B9C51A055F1EC9E1 |  | R22 | Non-TXV |  | -5.895% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Chico | CA | 95928-5758 |  | 2013-07-16 | 2013-07-16 21:38 | 2013-07-16 14:55 | YORK - H2RC036S06A | 83 | 8 | Yes | Yes | 19.4 | 21.5 | -2.1 | 5E8E8EBE06AC4F028F52501DEFD04883 |  | R22 | Non-TXV |  | 9.639% | 0.90361 | 18.52% | [5 empty] | Non-TXV | 9.639%
Oroville | CA | 95966-3834 |  | 2013-06-20 | 2013-06-20 20:37 | 2013-06-20 20:53 | DAY & NIGHT - 542E1X02400AAAC | 100 | 3.6 | Yes | Yes | 23.5 | 20.1 | 3.4 | 7AE1D53307054A7AA91B99245CB1A256 |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
San Miguel | CA | 93451-0000 |  | 2013-08-13 | 2013-08-13 11:09 | 2013-08-13 11:29 | PAYNE - PA10JA036-C | 82 | 3.6 | Yes | Yes | 19.4 | 18.6 | 0.8 | 651F8DF73574472F9659E3903C973D8E |  | R22 | Non-TXV |  | 4.39% | 0.9561 | 8.437% | [5 empty] | Non-TXV | 4.39%
Fresno | CA | 93727-6214 |  | 2013-06-13 | 2013-06-13 13:42 | 2013-06-13 13:45 | RUUD - UAHE-048JAS | 114 | 9.1 | Yes | Yes | 19.4 | 22.1 | -2.7 | 9784239633C64101B729569CC8B880E7 |  | R22 | Non-TXV |  | 7.982% | 0.92018 | 15.34% | [5 empty] | Non-TXV | 7.982%
Lincoln | CA | 95648-3243 |  | 2013-06-18 | 2013-06-18 09:30 | 2013-06-18 09:52 | CARRIER - 38ETG036300 | 133 | 4.9 | Yes | Yes | 18 | 18.8 | -0.8 | 7CDDCA8F715348E5BA046DA899BCD890 |  | R410A | TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | TXV | 3.684%
Paso Robles | CA | 93446-4304 |  | 2013-08-06 | 2013-08-06 15:46 | 2013-08-06 16:04 | OTHER - EES024FBA | 59 | -4.9 | Yes | Yes | 22.4 | 19.3 | 3.1 | E01A6A3B1EAC4A3A82B55364F19B0A21 |  | R22 | Non-TXV |  | -8.305% | 1.0831 | 2.326% |  |  |  |  | Non-TXV |  |  | -8.305%
Manteca | CA | 95337-6686 |  | 2013-05-31 | 2013-05-31 13:44 | 2013-05-31 14:02 | BRYANT - 563CN042-D | 104 | 8.4 | Yes | Yes | 18.5 | 21.4 | -2.9 | DCB9ECD980894AE3B4F2EE65F67704B4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.077% | 0.91923 | 15.52% | [5 empty] | Non-TXV | 8.077%
Auburn | CA | 95603-2848 |  | 2013-06-07 | 2013-06-07 12:24 | 2013-06-07 12:41 | AMANA - PGD42C0902E | 120 | 6.9 | Yes | Yes | 24.7 | 20.1 | 4.6 | 20A2977C623F4066A0DF5E47ED7C59CF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Yuba City | CA | 95991-8857 |  | 2013-08-29 | 2013-08-29 13:08 | 2013-08-29 13:32 | LENNOX - GSC10-41-50-P | 82 | 4 | Yes | Yes | 26 | 20.4 | 5.6 | CD97FB448E654631A77DF2A9ADC58B88 |  | R22 | Non-TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | Non-TXV | 4.878%
Merced | CA | 95348-3798 |  | 2013-07-10 | 2013-07-10 13:54 | 2013-07-10 13:57 | TRANE - TTR024C100A1 | 58 | 3.9 | Yes | Yes | 16.8 | 18.8 | -2 | 42895BB3250246F0AB1A7074B126D28F |  | R22 | Non-TXV |  | 6.724% | 0.93276 | 12.92% | [5 empty] | Non-TXV | 6.724%
Valley Springs | CA | 95252-9358 |  | 2013-09-05 | 2013-09-05 13:11 | 2013-09-05 13:45 | CARRIER - 48GS-042090301 | 100 | 0 | Yes | Yes | 26.1 | 20.4 | 5.7 | 6A67A2919C884C05B19BB71B91C85971 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-1049 |  | 2013-06-10 | 2013-06-10 13:09 | 2013-06-10 13:32 | YORK - D2GH030N04806C | 112 | 4.8 | Yes | Yes | 15.7 | 18.5 | -2.8 | 966459C28D3C4632832C547AE9CF2536 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Paso Robles | CA | 93446-3641 |  | 2013-09-05 | 2013-09-05 14:10 | 2013-09-05 14:27 | CARRIER - 38EB024300 | 53 | 4.4 | Yes | Yes | 17.9 | 19.2 | -1.3 | F2966568A87C431481919E096AFA1B60 |  | R22 | Non-TXV |  | 8.302% | 0.91698 | 15.95% | [5 empty] | Non-TXV | 8.302%
Granite Bay | CA | 95746-6083 |  | 2013-06-21 | 2013-06-21 18:03 | 2013-06-21 18:03 | RHEEM - RAKA-060JAZ | 112 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 3CCA0EB4625D4F409332919A19728EAD |  | R22 | TXV |  | 0% | 1 | 0%
Madera | CA | 93637-4343 |  | 2013-07-11 | 2013-07-11 02:30 | 2013-07-11 02:30 | OTHER - UNK | 85 | 0 | Yes | Yes | 18.6 | 21 | -2.4 | 779EA1CC3BF44ECBA5A95AD164845130 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4560 |  | 2013-06-07 | 2013-06-07 08:42 | 2013-06-07 08:45 | BRYANT - 574DNW036060NA | 146 | 5.1 | Yes | Yes | 20.5 | 18.2 | 2.3 | 9316A4BF49DD4181ABCFC0E991D78EE4 |  | R410A | Non-TXV |  | 3.493% | 0.96507 | 6.713% | [5 empty] | Non-TXV | 3.493%
Fresno | CA | 93703-4136 |  | 2013-06-06 | 2013-06-06 11:20 | 2013-06-06 11:20 | RHEEM - HC9-0-36210 | 83 | 7.3 | Yes | Yes | 18.2 | 19.8 | -1.6 | 93ADB446435B4D8C8DD1FE7D573F92C4 | Add refrigerant: 7.3 oz | R22 | Non-TXV |  | 8.795% | 0.91205 | 16.9% | [5 empty] | Non-TXV | 8.795%
Merced | CA | 95341-6952 |  | 2013-07-03 | 2013-07-03 11:32 | 2013-07-03 11:34 | GOODMAN - GPG1330045M41BA | 78 | 2.4 | Yes | Yes | 18.4 | 19.1 | -0.7 | 6A6AC160815F43A2AC51D37530B5120E |  | R410A | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95210-4458 |  | 2013-06-14 | 2013-06-14 10:03 | 2013-06-14 10:22 | PAYNE - 591ANX060000AAAA | 169 | -9.9 | Yes | Yes | 26.6 | 21.3 | 5.3 | 8633343A14E4467EBAC738DDC79CC8A4 |  | R22 | Non-TXV |  | -5.858% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.858%
Los Banos | CA | 93635-3202 |  | 2013-07-08 | 2013-07-08 12:47 | 2013-07-08 13:06 | PAYNE - PA10JA042000AHAA | 90 | 12.5 | Yes | Yes | 24.7 | 19.3 | 5.4 | 2302036BA8B749AC926961CDD205AC58 |  | R22 | TXV |  | 13.89% | 0.86111 | 26.69% | [5 empty] | TXV | 13.89%
Dinuba | CA | 93618-2748 |  | 2013-06-21 | 2013-06-21 16:41 | 2013-06-21 18:16 | RHEEM - N/A | 90 | 5.9 | Yes | Yes | 18.8 | 20.4 | -1.6 | 4F78458509C04F889F731AC1720417C0 |  | R22 | Non-TXV |  | 6.556% | 0.93444 | 12.6% | [5 empty] | Non-TXV | 6.556%
Stockton | CA | 95219-5483 |  | 2013-06-20 | 2013-06-20 15:13 | 2013-06-20 15:36 | CARRIER - 38EN018310SM | 55 | 2.2 | Yes | Yes | 19.9 | 22.4 | -2.5 | 323D9478542548F1973FACF587E36E7A |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Atwater | CA | 95301-2022 |  | 2013-06-11 | 2013-06-11 16:11 | 2013-06-11 16:13 | CARRIER - 48KLO30300BE | 54 | 2.1 | Yes | Yes | 22.5 | 18.8 | 3.7 | 2D74D980E4714A93B9B5FC2E0876A5D1 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Atwater | CA | 95301-4859 |  | 2013-06-07 | 2013-06-07 09:34 | 2013-06-07 09:43 | AIRE-FLO - UNK | 62 | 9.3 | Yes | Yes | 19.6 | 19 | 0.6 | B7F05AEC01FD4EB5BB387D0AA3686C47 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Stockton | CA | 95209-1190 |  | 2013-05-28 | 2013-05-28 11:02 | 2013-05-28 11:22 | PAYNE - 585CJWO36075AAAF | 84 | 8.4 | Yes | Yes | 18 | 17.7 | 0.3 | 9E1400A43F2B44228E93AEB0E45C71E9 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Atwater | CA | 95301-4865 |  | 2013-06-07 | 2013-06-07 10:46 | 2013-06-07 10:56 | LENNOX - HS93114P | 68 | 7.6 | Yes | Yes | 19.1 | 20.4 | -1.3 | EA9A60911EC947FA866F6CF3113211F9 |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Merced | CA | 95340-4246 |  | 2013-06-05 | 2013-06-05 10:55 | 2013-06-05 10:57 | TRANE - YCC036F1M0BJ | 83 | 2.7 | Yes | Yes | 20.4 | 19.3 | 1.1 | 92B58791BE6B42CD9DE0AABCAC2938CA |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Stockton | CA | 95206-6235 |  | 2013-07-02 | 2013-07-02 10:11 | 2013-07-02 10:38 | BRYANT - 561CJ060-A | 233 | 9.7 | Yes | Yes | 22.7 | 20.1 | 2.6 | 785959B844B44B0B940435B20DCB2B7D |  | R22 | Non-TXV |  | 4.163% | 0.95837 | 8.001% | [5 empty] | Non-TXV | 4.163%
Fresno | CA | 93703-1274 |  | 2013-06-03 | 2013-06-03 11:27 | 2013-06-03 11:47 | YORK - DAY-PF042N080A | 145 | 4.5 | Yes | Yes | 17.6 | 20.4 | -2.8 | BF0C505A2BA34E9D99CCBF155762EC75 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Fresno | CA | 93726-3616 |  | 2013-06-01 | 2013-06-01 14:14 | 2013-06-01 14:48 | CARRIER - 58ANW024040 | 60 | 2.2 | Yes | Yes | 18.4 | 19.1 | -0.7 | 46D3DAE2F93C4186B6A4FBC2E56D3C80 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Fresno | CA | 93703-3112 |  | 2013-06-01 | 2013-06-01 15:12 | 2013-06-01 15:40 | GOODMAN - GPG1324041CB | 74 | 3.3 | Yes | Yes | 17.1 | 19.8 | -2.7 | 2395B7E4D45E46AD92377A6BC3313EEA |  | R22 | Non-TXV |  | 4.459% | 0.95541 | 8.57% | [5 empty] | Non-TXV | 4.459%
Fresno | CA | 93703-1610 |  | 2013-05-29 | 2013-05-29 11:24 | 2013-05-29 12:00 | AMERICAN STANDARD - YCY042G1M0AC | 147 | 6.3 | Yes | Yes | 17.9 | 20.4 | -2.5 | 3A65AE14492149E38D4DADE7C4ADF7E1 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Merced | CA | 95341-5463 |  | 2013-06-12 | 2013-06-12 10:14 | 2013-06-12 10:23 | OTHER - AC024M1021A | 52 | 8.7 | Yes | Yes | 18 | 18.8 | -0.8 | 62D9E16663944205958FE385B1B80C42 |  | R22 | Non-TXV |  | 16.73% | 0.83269 | 32.15% | [5 empty] | Non-TXV | 16.73%
Stockton | CA | 95209-1405 |  | 2013-05-24 | 2013-05-24 11:10 | 2013-05-24 11:10 | YORK - D1NA042N05606C | 76 | 0 | Yes | Yes | 24.1 | 20.1 | 4 | F279812089C244DFA2C6E2012C9263CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2710 |  | 2013-06-03 | 2013-06-03 14:22 | 2013-06-03 14:41 | AMANA - PGB36B0702A | 118 | 7.4 | Yes | Yes | 22.5 | 21 | 1.5 | BCCF1699501C4D0D9D173C8F371AD9B8 |  | R22 | Non-TXV |  | 6.271% | 0.93729 | 12.05% | [5 empty] | Non-TXV | 6.271%
Clovis | CA | 93611-5113 |  | 2013-06-13 | 2013-06-13 16:35 | 2013-06-13 16:35 | LENNOX - 10GCS030X-75-2PA | 51 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | FFA7F4CE900841B3980E714C97D0A37C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-8676 |  | 2013-06-18 | 2013-06-18 10:59 | 2013-06-18 11:22 | YORK - H4TS048S06B | 156 | 5.7 | Yes | Yes | 24 | 19.5 | 4.5 | 77FE644683CA484890999D4F1A07F98C |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Stockton | CA | 95207-2317 |  | 2013-06-03 | 2013-06-03 09:47 | 2013-06-03 10:06 | GOODMAN - GPG1324051CB | 74 | 2.6 | Yes | Yes | 19.4 | 18.3 | 1.1 | 1499DC25323143B7B583BF3BB36B8F5B |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Manteca | CA | 95336-3976 |  | 2013-05-29 | 2013-05-29 10:05 | 2013-05-29 10:29 | BDP - 5850J24C40 | 68 | 11 | Yes | Yes | 21 | 20.4 | 0.6 | A73E75C896BE4C298AAC923911F91C72 |  | R22 | Non-TXV |  | 16.18% | 0.83824 | 31.09% | [5 empty] | Non-TXV | 16.18%
Yuba City | CA | 95991-8867 |  | 2013-06-07 | 2013-06-07 12:29 | 2013-06-07 12:29 | YORK - TCGD036S41S3H | 73 | 0 | Yes | Yes | 23 | 19.5 | 3.5 | 15D347EB42D34F2DA552676DC35AF167 |  | R410A | TXV |  | 0% | 1 | 0%
Rescue | CA | 95672-9570 |  | 2013-08-10 | 2013-08-10 09:54 | 2013-08-10 09:54 | OTHER - UNK | 78 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 222A0B8681B842599FE22523FF69670A |  | R22 | TXV |  | 0% | 1 | 0%
Rescue | CA | 95672-9570 |  | 2013-08-10 | 2013-08-10 10:24 | 2013-08-10 10:24 | BRYANT - UNK | 120 | 0 | Yes | Yes | 23.1 | 19.1 | 4 | 9BE3B39356B94EE6955239AC345843CD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2674 |  | 2013-06-06 | 2013-06-06 15:25 | 2013-06-06 15:25 | OTHER - 585B024050YACR | 191 | 0 | Yes | Yes | 16 | 18.3 | -2.3 | 631201B1790E4BD4B5E420825E93C678 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-1518 |  | 2013-05-28 | 2013-05-28 15:11 | 2013-05-28 15:11 | DAY & NIGHT - 561CJ042-A | 80 | 0 | Yes | Yes | 26.6 | 21 | 5.6 | 06CD00BDB7424D47B08AF8BA8CD045B4 |  | R22 | TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-5235 |  | 2013-05-30 | 2013-05-30 11:38 | 2013-05-30 12:30 | OTHER - SCV10G42A-1 | 87 | 3.2 | Yes | Yes | 23.5 | 20.9 | 2.6 | 45184DE6F5184BA1B8B77552A99856E0 |  | R22 | Non-TXV |  | 3.678% | 0.96322 | 7.069% | [5 empty] | Non-TXV | 3.678%
Stockton | CA | 95206-6175 |  | 2013-06-19 | 2013-06-19 11:39 | 2013-06-19 11:57 | GOODMAN - CLJ60-1 | 142 | 16.7 | Yes | Yes | 23.2 | 19.4 | 3.8 | 3AA107888339411A96FE6DCF459D899C |  | R22 | Non-TXV |  | 11.76% | 0.88239 | 22.6% | [5 empty] | Non-TXV | 11.76%
Rescue | CA | 95672-9465 |  | 2013-08-10 | 2013-08-10 17:36 | 2013-08-10 19:00 | PAYNE - 691ANX042000AAAA | 180 | 12.8 | Yes | Yes | 17.3 | 19.9 | -2.6 | 8CF545F2B6B045B7A18266CC2F256F2A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.111% | 0.92889 | 13.67% | [5 empty] | Non-TXV | 7.111%
Auburn | CA | 95603-3415 |  | 2013-06-07 | 2013-06-07 08:14 | 2013-06-07 08:14 | BRYANT - 582ANW030060AAAD | 59 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | 1651EFEBE0394DA58C40F076BCFA3370 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-7430 |  | 2013-08-22 | 2013-08-22 17:15 | 2013-08-22 18:00 | LENNOX - 12GCS-42-75-3PA | 133 | 4 | Yes | Yes | 24.5 | 19.1 | 5.5 | 5BA862F7C7D143B9BFAC980801672D92 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Yuba City | CA | 95991-8857 |  | 2013-06-10 | 2013-06-10 11:40 | 2013-06-10 12:03 | DAY & NIGHT - UNK | 85 | 2.5 | Yes | Yes | 22.5 | 18.2 | 4.3 | 4BB279B4828E42E588871F81BE8AAA50 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Yuba City | CA | 95991-6732 |  | 2013-06-21 | 2013-06-21 11:55 | 2013-06-21 12:13 | LENNOX - 10ACC-060-230-04 | 130 | 4 | Yes | Yes | 21.8 | 21.5 | 0.3 | 29A68679D0EB49C4842F07E4B69D1F50 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95206-4825 |  | 2013-06-21 | 2013-06-21 13:17 | 2013-06-21 13:42 | GOODMAN - CE25-1EB | 85 | 4.8 | Yes | Yes | 23.8 | 21.2 | 2.7 | 6189F3CB6BC443E9B1AAD55C7BCD6DC4 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Merced | CA | 95340-9448 |  | 2013-08-07 | 2013-08-07 16:31 | 2013-08-07 16:58 | CARRIER - 48KL048300BE | 80 | 17.3 | Yes | Yes | 22.5 | 20.2 | 2.3 | 130DD1E0117141E282F4E68120E1AB9E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.62% | 0.78375 | 41.56% | [5 empty] | Non-TXV | 21.62%
Stockton | CA | 95205-7909 |  | 2013-06-05 | 2013-06-05 14:23 | 2013-06-05 14:23 | GUARDIAN - GCSD36S21S2B | 74 | 0 | Yes | Yes | 22.5 | 21 | 1.5 | A5D5EC50D3B84119A83E0D03552D84C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4744 |  | 2013-06-03 | 2013-06-03 15:45 | 2013-06-03 16:02 | CARRIER - 38TXA036330 | 111 | 3.5 | Yes | Yes | 20.8 | 20.4 | 0.4 | F8D48998602945ABABD75413F707875E |  | R410A | Non-TXV |  | 3.153% | 0.96847 | 6.06% | [5 empty] | Non-TXV | 3.153%
Fresno | CA | 93726-3113 |  | 2013-06-04 | 2013-06-04 17:03 | 2013-06-04 17:13 | RHEEM - RRNA-A036JK06X | 114 | 3.9 | Yes | Yes | 24.2 | 20 | 4.3 | B35F0A6407794FF3AA87B474318EA23B |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Gerber | CA | 96035-9602 |  | 2013-08-19 | 2013-08-19 18:10 | 2013-08-19 18:10 | COLEMAN - ERCQO481BAA | 124 | 0 | Yes | Yes | 27.5 | 22.1 | 5.4 | F168EBC33AF245BDB80AA17E8FB9D10C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-0000 |  | 2013-08-17 | 2013-08-17 09:45 | 2013-08-17 09:45 | CARRIER - 24ABA48A300 | 127 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 909ED27DA6714D84AC94700D843EB210 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6228 |  | 2013-06-13 | 2013-06-13 14:05 | 2013-06-13 14:08 | GOODMAN - GSC130601CB | 131 | 7.9 | Yes | Yes | 19.8 | 22.1 | -2.3 | B16B198CFB954771AA0EF7755C153E0A |  | R22 | Non-TXV |  | 6.031% | 0.93969 | 11.59% | [5 empty] | Non-TXV | 6.031%
Clovis | CA | 93611-0501 |  | 2013-06-12 | 2013-06-12 09:01 | 2013-06-12 09:36 | BDP - 585EJW030050ABAF | 58 | -4.8 | Yes | Yes | 20.1 | 18.4 | 1.8 | 01453A1808EB4C889D5151B1E94B7E44 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Newman | CA | 95360-9635 |  | 2013-07-29 | 2013-07-29 16:10 | 2013-07-29 16:40 | BRYANT - 5CNN036-D | 101 | 3.7 | Yes | Yes | 20.1 | 19.6 | 0.6 | AAA675D0184541A1B22DC9681DEDCF37 |  | R22 | Non-TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | Non-TXV | 3.663%
Atwater | CA | 95301-4861 |  | 2013-06-07 | 2013-06-07 11:09 | 2013-06-07 11:09 | LENNOX - HS93116P | 78 | 0 | Yes | Yes | 15.5 | 18.5 | -3 | 140C3C5E966640A88EFB11E13A75F571 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-9578 |  | 2013-07-03 | 2013-07-03 09:40 | 2013-07-03 09:48 | RUUD - UAKA060JAZ | 112 | 8.9 | Yes | Yes | 24.6 | 18.7 | 5.9 | C827CA15A5A34DFF9514C3D8B081AD3F |  | R22 | Non-TXV |  | 7.946% | 0.92054 | 15.27% | [5 empty] | Non-TXV | 7.946%
Stockton | CA | 95209-5183 |  | 2013-05-24 | 2013-05-24 15:45 | 2013-05-24 15:45 | PAYNE - 565BJ048 | 85 | 0 | Yes | Yes | 27.1 | 21.5 | 5.6 | C171C9C49FDC473DAB279FD1864CCE7D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2649 |  | 2013-06-03 | 2013-06-03 14:14 | 2013-06-03 14:14 | GMC - VSX130301AA | 78 | 4.5 | Yes | Yes | 16.1 | 17.5 | -1.4 | 76B4B53697534683AC10D723BB25E554 | Add refrigerant: 4.5 oz Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 5.769% | 0.94231 | 11.09% | [5 empty] | Non-TXV | 5.769%
Atwater | CA | 95301-4859 |  | 2013-06-07 | 2013-06-07 09:10 | 2013-06-07 09:17 | AIRE-FLO - CL301AB | 69 | 7 | Yes | Yes | 18.1 | 18.7 | -0.6 | 172B32658BB94C5987EA1E7F0C8D7DEB |  | R22 | Non-TXV |  | 10.14% | 0.89855 | 19.5% | [5 empty] | Non-TXV | 10.14%
Livingston | CA | 95334-9677 |  | 2013-06-10 | 2013-06-10 15:50 | 2013-06-10 16:10 | BDP - `588ANW030040ABAD | 69 | 2.8 | Yes | Yes | 18.9 | 20.1 | -1.2 | EA25436626B74AA095764DD6ACF69D7C |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Lincoln | CA | 95648-3212 |  | 2013-08-17 | 2013-08-17 14:18 | 2013-08-17 14:37 | LENNOX - 13ACC-036-230-02 | 115 | 18.7 | Yes | Yes | 17.9 | 20.2 | -2.3 | 8F74462F644546D880E030D2F1077E63 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16.26% | 0.83739 | 31.25% | [5 empty] | Non-TXV | 16.26%
Chowchilla | CA | 93610-2759 |  | 2013-06-02 | 2013-06-02 10:23 | 2013-06-02 10:43 | YORK - CK24-189 | 72 | -6.8 | Yes | Yes | 24.2 | 20.1 | 4.1 | EA550AE52FC54288949D90E661BB6661 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Lincoln | CA | 95648-2836 |  | 2013-06-18 | 2013-06-18 13:19 | 2013-06-18 13:37 | YORK - H1RAO48S060D | 117 | 4.7 | Yes | Yes | 21 | 21.5 | -0.5 | 811BDD73F4224508B9B4B33416264BB0 |  | R22 | Non-TXV |  | 4.017% | 0.95983 | 7.72% | [5 empty] | Non-TXV | 4.017%
Willows | CA | 95988-3408 |  | 2013-06-27 | 2013-06-27 17:52 | 2013-06-27 18:08 | RHEEM - RRKA-A030JK06X | 54 | 9.2 | Yes | Yes | 17.8 | 19.3 | -1.5 | E015B9574B684997830246B3D81ACB9D |  | R22 | Non-TXV |  | 17.04% | 0.82963 | 32.74% | [5 empty] | Non-TXV | 17.04%
Yuba City | CA | 95993-9113 |  | 2013-05-31 | 2013-05-31 12:51 | 2013-05-31 12:51 | CARRIER - 38CKC036350 | 74 | 6.1 | Yes | Yes | 17.7 | 18.8 | -1.1 | EA2B510B6B574527B2FDA795CADC7E4B | Add refrigerant: 6.1 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.243% | 0.91757 | 15.84% | [5 empty] | Non-TXV | 8.243%
Tracy | CA | 95377-8651 |  | 2013-08-12 | 2013-08-12 12:21 | 2013-08-12 12:47 | BRYANT - 563CN060-D | 200 | 17.4 | Yes | Yes | 18.7 | 18.8 | -0.1 | 628E0E81010641A296602B1DD830720D |  | R22 | TXV |  | 8.7% | 0.913 | 16.72% | [5 empty] | TXV | 8.7%
Los Banos | CA | 93635-4503 |  | 2013-07-09 | 2013-07-09 14:24 | 2013-07-09 14:25 | DAY & NIGHT - 589ANW048080ADAG | 88 | 14.2 | Yes | Yes | 25.4 | 21.1 | 4.4 | DA43CED108E94D20BA62872D41841DB1 |  | R22 | Non-TXV |  | 16.14% | 0.83864 | 31.01% | [5 empty] | Non-TXV | 16.14%
Fresno | CA | 93726-0425 |  | 2013-06-05 | 2013-06-05 13:34 | 2013-06-05 13:42 | RUUD - N/A | 90 | 3 | Yes | Yes | 24.6 | 20.7 | 3.9 | 55A3B9A0BAF4430DA6273DFE15185848 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Chico | CA | 95973-0517 |  | 2013-08-21 | 2013-08-21 11:50 | 2013-08-21 20:42 | RHEEM - UAMC-030JAZ | 77 | 4.8 | Yes | Yes | 24 | 19.5 | 4.5 | 9C3AA1FE80D644D08F9140ACD2AC8B52 |  | R22 | Non-TXV |  | 6.234% | 0.93766 | 11.98% | [5 empty] | Non-TXV | 6.234%
Chico | CA | 95928-9117 |  | 2013-06-04 | 2013-06-04 18:48 | 2013-06-04 19:38 | COLEMAN - 7848-801 | 108 | 9.5 | Yes | Yes | 25 | 22.9 | 2.2 | 4B4B432040244F898F6D91D500BF4A87 |  | R22 | Non-TXV |  | 8.796% | 0.91204 | 16.9% | [5 empty] | Non-TXV | 8.796%
Paso Robles | CA | 93446-2407 |  | 2013-08-05 | 2013-08-05 11:35 | 2013-08-05 11:57 | HEIL - NCAB3OB302 | 44 | 1.8 | Yes | Yes | 17.9 | 18.1 | -0.2 | 9636E395AE0B4190AA69B2D5424ABD46 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Manteca | CA | 95337-8801 |  | 2013-05-24 | 2013-05-24 10:41 | 2013-05-24 11:02 | RHEEM - WRKA-A036JK06 | 62 | 2.1 | Yes | Yes | 23.5 | 18.7 | 4.8 | 0184D28D178947A5A51B876F3A4A61BF | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 3.387% | 0.96613 | 6.509% | [5 empty] | Non-TXV | 3.387%
Tracy | CA | 95376-9183 |  | 2013-06-05 | 2013-06-05 16:59 | 2013-06-05 17:26 | BRYANT - 561CJ030-D | 89 | 3.8 | Yes | Yes | 24 | 20.6 | 3.4 | 7AB6E9CDBACD49F3A29C7DA271F074C6 |  | R22 | Non-TXV |  | 4.27% | 0.9573 | 8.205% | [5 empty] | Non-TXV | 4.27%
Clovis | CA | 93611-0636 |  | 2013-06-12 | 2013-06-12 12:21 | 2013-06-12 12:39 | AMERICAN STANDARD - 4YCY4036A1075AA | 108 | 3.9 | Yes | Yes | 18 | 20.1 | -2.1 | 72892BCF9EEB48549A4ED1ABD7431351 |  | R410A | TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | TXV | 3.611%
Loomis | CA | 95650-8930 |  | 2013-10-10 | 2013-10-10 14:54 | 2013-10-10 14:54 | CONCORD - 2AC13L48P-1B | 203 | 0 | Yes | Yes | 20 | 20.3 | -0.3 | 64CA148FD8C8455686F13B850373654C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3226 |  | 2013-06-03 | 2013-06-03 09:10 | 2013-06-03 09:36 | BDP - 585A030060YACR | 50 | 7.5 | Yes | Yes | 17.7 | 20.4 | -2.7 | AB83C8B5AD5A453AACAF0ECF1CD149B3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Gridley | CA | 95948-9706 |  | 2013-08-17 | 2013-08-17 15:23 | 2013-08-17 15:39 | RHEEM - RAKA-037JAZ | 79 | 8.1 | Yes | Yes | 19.5 | 20.8 | -1.3 | B3983EE44FD84B469F5F2BBEB6410D68 |  | R22 | Non-TXV |  | 10.25% | 0.89747 | 19.7% | [5 empty] | Non-TXV | 10.25%
Gridley | CA | 95948-9706 |  | 2013-08-17 | 2013-08-17 15:59 | 2013-08-17 18:21 | RHEEM - RAKA-048JAZ | 103 | 6.5 | Yes | Yes | 22.5 | 20.8 | 1.7 | 61063ADD29E54B23AE238FBC3E5E84B0 |  | R22 | Non-TXV |  | 6.311% | 0.93689 | 12.13% | [5 empty] | Non-TXV | 6.311%
Marysville | CA | 95901-9439 |  | 2013-06-03 | 2013-06-03 15:16 | 2013-06-03 15:16 | OTHER - UNK | 80 | 0 | Yes | Yes | 18 | 20.6 | -2.6 | C6929796991C4F259C97B895BCFB9A7B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-6022 |  | 2013-06-20 | 2013-06-20 19:36 | 2013-06-20 19:53 | CARRIER - 38EH060330 | 230 | 7.7 | Yes | Yes | 23.5 | 20.1 | 3.4 | 9A08CC9CC3934B768E2E5730606BA241 |  | R22 | Non-TXV |  | 3.348% | 0.96652 | 6.434% | [5 empty] | Non-TXV | 3.348%
Rocklin | CA | 95765-4780 |  | 2013-06-15 | 2013-06-15 11:09 | 2013-06-15 11:09 | YORK - HIRA042S06D | 84 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | FB694D6CBFAE4D23BC5B2C3B3CC2F055 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-9193 |  | 2013-06-13 | 2013-06-13 09:46 | 2013-06-13 10:09 | CARRIER - 38QN024300 | 90 | -8.5 | Yes | Yes | 24.4 | 20.1 | 4.3 | E04E12AE70774AC091C2FC9CDF9E93E9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Chowchilla | CA | 93610-2034 |  | 2013-06-14 | 2013-06-14 12:52 | 2013-06-15 02:44 | AMERICAN STANDARD - TTDD748B100A | 116 | 5.2 | Yes | Yes | 18.5 | 20.1 | -1.6 | BA0A0DF4292D46FE90A3ECE336D77468 |  | R22 | Non-TXV |  | 4.483% | 0.95517 | 8.615% | [5 empty] | Non-TXV | 4.483%
Tracy | CA | 95376-1743 |  | 2013-05-24 | 2013-05-24 11:51 | 2013-05-24 12:37 | DAY & NIGHT - 591ANX048000ABAA | 85 | 3.1 | Yes | Yes | 27.9 | 21.9 | 6 | 56C855C06DCE4716BAFD42EF8BD9B714 |  | R22 | Non-TXV |  | 3.647% | 0.876 | 23.83% | [5 empty] | Non-TXV | 3.647%
Stockton | CA | 95207-4672 |  | 2013-06-04 | 2013-06-04 13:19 | 2013-06-04 13:38 | DAY & NIGHT - 597BNX036-A | 144 | -11.9 | Yes | Yes | 19.4 | 18.6 | 0.8 | FF762D9825664EC9908E83B08BE010E9 |  | R22 | Non-TXV |  | -8.264% | 1.0826 | 2.314% |  |  |  |  | Non-TXV |  |  | -8.264%
Stockton | CA | 95206-1857 |  | 2013-06-10 | 2013-06-10 09:14 | 2013-06-10 09:35 | CARRIER - 585HJ030049 | 68 | 9.6 | Yes | Yes | 20 | 19.4 | 0.6 | 3AA032B0B2EC42F08928946E4FB2B503 |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Stockton | CA | 95203-1714 |  | 2013-05-29 | 2013-05-29 10:31 | 2013-05-29 10:50 | RHEEM - UNK | 64 | 3.1 | Yes | Yes | 18.9 | 18.8 | 0.1 | A5EFADDC76D64C86AC99A869B7B32687 |  | R22 | Non-TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | Non-TXV | 4.844%
Fresno | CA | 93727-3414 |  | 2013-07-15 | 2013-07-15 10:33 | 2013-07-15 11:00 | GOODMAN - PGJ042075-1 | 90 | 3.3 | Yes | Yes | 19.1 | 20.4 | -1.3 | 4C55A025673F4C118FCF062F741A4FAA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Stockton | CA | 95202-1554 |  | 2013-07-09 | 2013-07-09 11:08 | 2013-07-09 11:54 | BDP - 567030RCU | 49 | 8.5 | Yes | Yes | 23.7 | 18.5 | 5.2 | 58E7B86AE1394B2DADD8EBC0099F1BCA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.35% | 0.82653 | 33.34% | [5 empty] | Non-TXV | 17.35%
Stockton | CA | 95210-1541 |  | 2013-07-31 | 2013-07-31 11:26 | 2013-07-31 11:43 | DAY & NIGHT - UNK | 88 | -6.2 | Yes | Yes | 21.8 | 18.5 | 3.3 | 57D3FF8094494C4AB7FD1A646A4D2122 |  | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Lodi | CA | 95240-9438 |  | 2013-10-11 | 2013-10-11 12:27 | 2013-10-11 12:58 | BRYANT - 582ANW042090AAAG | 100 | 15.1 | Yes | Yes | 25.9 | 19.9 | 6 | 26E5CEB790234FF18CA652DEFD7CDB9B |  | R22 | Non-TXV |  | 15.1% | 0.849 | 29.02% | [5 empty] | Non-TXV | 15.1%
Magalia | CA | 95954-9715 |  | 2013-07-19 | 2013-07-19 08:49 | 2013-07-19 09:41 | DAY & NIGHT - 5B790ACBF88ANW036 | 67 | 7.5 | Yes | Yes | 18.5 | 19.6 | -1.1 | 593C42308D8447A4945E0614F73D82E4 |  | R22 | Non-TXV |  | 11.19% | 0.88806 | 21.51% | [5 empty] | Non-TXV | 11.19%
Stockton | CA | 95205-7811 |  | 2013-06-12 | 2013-06-12 08:47 | 2013-06-12 08:47 | RUUD - UAKA060-Z | 112 | 0 | Yes | Yes | 22.3 | 19.1 | 3.3 | 6EF6CB04B43A4EFA84F5624C2A1EFCDD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7022 |  | 2013-06-11 | 2013-06-11 12:25 | 2013-06-11 12:31 | GOODMAN - CLJ361A | 109 | 4.6 | Yes | Yes | 24.3 | 20 | 4.3 | 177728994B354BFF9DA80B5066A2EF1D |  | R22 | Non-TXV |  | 4.22% | 0.9578 | 8.11% | [5 empty] | Non-TXV | 4.22%
Clovis | CA | 93612-1041 |  | 2013-06-15 | 2013-06-15 15:47 | 2013-06-15 16:06 | CARRIER - N/A | 60 | 9 | Yes | Yes | 26.6 | 20.7 | 5.9 | 1785AEA8D2E24F939C4256604CFF9222 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Clovis | CA | 93619-9042 |  | 2013-06-26 | 2013-06-26 14:05 | 2013-06-26 14:32 | YORK - D2CG036N04106B | 94 | 3.2 | Yes | Yes | 19.6 | 20.3 | -0.6 | B553A9B084484A539FEBC512F4A65D0E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.404% | 0.96596 | 6.542% | [5 empty] | Non-TXV | 3.404%
Los Banos | CA | 93635-3406 |  | 2013-05-30 | 2013-05-30 12:26 | 2013-05-30 12:31 | YORK - H3DH036S06A | 95 | 13.3 | Yes | Yes | 25.8 | 21.1 | 4.8 | 0E817E64A4674B6FAC181891A465D77A |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Fresno | CA | 93703-2673 |  | 2013-05-31 | 2013-05-31 13:42 | 2013-05-31 14:07 | RHEEM - RRNL-B024JK06X | 78 | 3 | Yes | Yes | 20.5 | 20.8 | -0.3 | 799F62B18C40489D97A13090FA31B732 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Clovis | CA | 93611-0655 |  | 2013-06-12 | 2013-06-12 10:43 | 2013-06-12 11:01 | BDP - 589ANW048100ADBG | 88 | 7 | Yes | Yes | 20 | 20.1 | -0.1 | 01818B8E8B5A46D2944B0DB0CDD1708D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.955% | 0.92045 | 15.29% | [5 empty] | Non-TXV | 7.955%
Stockton | CA | 95206-4721 |  | 2013-06-17 | 2013-06-17 10:52 | 2013-06-17 11:13 | RHEEM - RAHE-042JAS | 85 | -9 | Yes | Yes | 25.3 | 19.9 | 5.5 | F6968186E3F74AAAB548715DB90D4FD4 |  | R22 | Non-TXV |  | -10.59% | 1.1059 | 2.965% |  |  |  |  | Non-TXV |  |  | -10.59%
Lincoln | CA | 95648-2445 |  | 2013-06-14 | 2013-06-14 12:18 | 2013-06-14 12:18 | YORK - H1DE030S06B | 85 | 0 | Yes | Yes | 24.9 | 23.4 | 1.5 | 628CB48C42524D6DBB72A3C58BBD12BD |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3927 |  | 2013-10-10 | 2013-10-10 18:13 | 2013-10-10 19:54 | UNITARY PRODUCTS GROUP - DAYA-F024N045C | 54 | 7 | Yes | Yes | 22.4 | 21.2 | 1.2 | E241A65719274ABCA7B48E30EEA9D2CB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.96% | 0.87037 | 24.91% | [5 empty] | Non-TXV | 12.96%
Clovis | CA | 93612-2339 |  | 2013-06-18 | 2013-06-18 09:58 | 2013-06-18 10:18 | YORK - D2NP048N09006A | 132 | 4 | Yes | Yes | 20 | 20.4 | -0.4 | D99AE9A329F5443EAE02CBB91EEC1F20 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Fresno | CA | 93726-3120 |  | 2013-06-05 | 2013-06-05 14:19 | 2013-06-05 14:38 | GOODMAN - GPG10480901A | 98 | 3 | Yes | Yes | 21.8 | 19.7 | 2.1 | 392CEBA3B5F343249645C2E9DB853C10 |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Yuba City | CA | 95991-8869 |  | 2013-06-06 | 2013-06-06 13:09 | 2013-06-06 13:30 | YORK - CMA03611A | 90 | 6 | Yes | Yes | 27 | 21.5 | 5.5 | 3C2B754A494E409E851805D94E746D4B |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Stockton | CA | 95209-2726 |  | 2013-05-24 | 2013-05-24 16:24 | 2013-05-24 16:47 | GE - BGTA830R1D | 96 | 18.9 | Yes | Yes | 23.8 | 20.8 | 3 | AFB7E2050FD649E6947988CF597509FA |  | R22 | Non-TXV |  | 19.69% | 0.80312 | 37.84% | [5 empty] | Non-TXV | 19.69%
Los Banos | CA | 93635-6323 |  | 2013-08-01 | 2013-08-01 10:48 | 2013-08-01 10:53 | BRYANT - 561CJ048-A | 105 | 3.3 | Yes | Yes | 17.7 | 20.4 | -2.7 | 29482C8B364745D2BB52CE4DC6CF7C19 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Lincoln | CA | 95648-1753 |  | 2013-05-30 | 2013-05-30 13:57 | 2013-05-30 14:33 | TRANE - TTX042C100A1 | 85 | -3.1 | Yes | Yes | 17 | 19.9 | -2.9 | 5422A96EB00F4430BB079460DDEE8F33 |  | R22 | TXV |  | -3.647% | 1.0365 | 1.021% |  |  |  |  | TXV |  |  | -3.647%
Live Oak | CA | 95953-9761 |  | 2013-08-05 | 2013-08-05 15:46 | 2013-08-05 15:46 | YORK - TCGD030S21S2HA | 55 | 0 | Yes | Yes | 23 | 21.3 | 1.7 | DE27898D1DA449D98DB2395ECFEC100F |  | R22 | TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-9631 |  | 2013-07-09 | 2013-07-09 14:02 | 2013-07-09 14:06 | BRYANT - 561CJ042-B | 93 | 3.1 | Yes | Yes | 19.5 | 22.1 | -2.6 | 8258D641600246E8A4031D4F0DA35081 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95207-4805 |  | 2013-06-03 | 2013-06-03 13:30 | 2013-06-03 13:49 | RHEEM - UNK | 96 | 8.5 | Yes | Yes | 25.9 | 22.8 | 3.2 | 506E6675BB234087B8AB14FD2E7278C9 |  | R22 | Non-TXV |  | 8.854% | 0.91146 | 17.02% | [5 empty] | Non-TXV | 8.854%
Tracy | CA | 95376-7784 |  | 2013-05-28 | 2013-05-28 13:17 | 2013-05-28 13:17 | RHEEM - RAKA-048JAS | 85 | 0 | Yes | Yes | 2.4 | 20.7 | -18.3 | ED039F3AD25240C385BF4CF8AC04FAE4 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Granite Bay | CA | 95746-6609 |  | 2013-06-21 | 2013-06-21 12:47 | 2013-06-21 13:12 | PAYNE - 580AN042060 | 102 | 10.1 | Yes | Yes | 23.2 | 20.5 | 2.7 | 63BF0A6D874147D19DFC80009B332678 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.902% | 0.90098 | 19.03% | [5 empty] | Non-TXV | 9.902%
Granite Bay | CA | 95746-6609 |  | 2013-06-21 | 2013-06-21 13:22 | 2013-06-21 13:57 | PAYNE - 591ANX036000AAAA | 86 | 9.2 | Yes | Yes | 23.6 | 21.5 | 2.1 | CC6703B0303149F688EE3E10D9FA2330 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.7% | 0.89302 | 20.56% | [5 empty] | Non-TXV | 10.7%
Madera | CA | 93638-1851 |  | 2013-06-12 | 2013-06-12 17:47 | 2013-06-17 09:08 | GOODMAN - GPH1336M21AA | 161 | 5.3 | Yes | Yes | 19.3 | 21 | -1.7 | 8900691A2B5D42FDAC7DF9B179FCDCB3 |  | R22 | Non-TXV |  | 3.292% | 0.96708 | 6.326% | [5 empty] | Non-TXV | 3.292%
Fresno | CA | 93726-3015 |  | 2013-06-07 | 2013-06-07 16:14 | 2013-06-07 16:14 | GOODMAN - GPG1336070M41AC | 85 | 0 | Yes | Yes | 17 | 18.8 | -1.8 | ADC41AC2E9344D25B34048490C99495D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-2285 |  | 2013-06-08 | 2013-06-08 15:03 | 2013-06-08 18:41 | BDP - 598AN048-B | 197 | 6.1 | Yes | Yes | 20.8 | 19.9 | 0.9 | 1A270F7A343847C49BCFCD661D3A8D5A |  | R22 | Non-TXV |  | 3.096% | 0.96904 | 5.951% | [5 empty] | Non-TXV | 3.096%
Fresno | CA | 93727-5544 |  | 2013-06-18 | 2013-06-18 11:49 | 2013-06-18 11:53 | OTHER - CA5530VKD2 | 74 | 6.2 | Yes | Yes | 23.4 | 21 | 2.4 | FC1DA657A86343EEAF0D86B3D32A610D |  | R22 | Non-TXV |  | 8.378% | 0.91622 | 16.1% | [5 empty] | Non-TXV | 8.378%
Lathrop | CA | 95330-8833 |  | 2013-06-07 | 2013-06-07 11:50 | 2013-06-07 12:09 | GOODMAN - CLJ048-1C | 130 | 4.4 | Yes | Yes | 21.1 | 22 | -0.9 | F89D404B3E9F439AA2368D0E2131DC7C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.385% | 0.96615 | 6.504% | [5 empty] | Non-TXV | 3.385%
Madera | CA | 93637-8825 |  | 2013-07-03 | 2013-07-03 13:53 | 2013-07-04 15:53 | CARRIER - 48GX-03606301 | 85 | 5.5 | Yes | Yes | 19.7 | 19.7 | 0 | 27BFDB6BFD0842C3852B34EAFDE51546 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Atwater | CA | 95301-4724 |  | 2013-06-06 | 2013-06-06 12:34 | 2013-06-06 12:41 | BDP - 561AJ024 | 56 | 4.4 | Yes | Yes | 21.7 | 19.7 | 2 | 986B0411BF1C49878591B771CA37B57C |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Atwater | CA | 95301-2022 |  | 2013-06-05 | 2013-06-05 08:55 | 2013-06-05 08:57 | TRANE - YCP042F1MOAB | 128 | 6.6 | Yes | Yes | 21.7 | 18.7 | 3 | 8AAD1F4E63E74F0BB19387AC91CC1E2C |  | R22 | Non-TXV |  | 5.156% | 0.94844 | 9.909% | [5 empty] | Non-TXV | 5.156%
Newman | CA | 95360-2731 |  | 2013-07-29 | 2013-07-29 09:59 | 2013-07-29 10:24 | BRYANT - 561CJ048-G | 99 | 13.9 | Yes | Yes | 17.1 | 19.2 | -2.1 | 95DECADCC9FE4670A46C0240C9A35739 |  | R22 | Non-TXV |  | 14.04% | 0.8596 | 26.98% | [5 empty] | Non-TXV | 14.04%
Fresno | CA | 93726-3507 |  | 2013-06-05 | 2013-06-05 16:01 | 2013-06-05 16:35 | AMERICAN STANDARD - YCC024F1L0BJ | 66 | 3.8 | Yes | Yes | 18.3 | 18.8 | -0.5 | 26D78532A20249FB8D116167B86B9AED |  | R22 | Non-TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | Non-TXV | 5.758%
Stockton | CA | 95204-1328 |  | 2013-05-30 | 2013-05-30 10:53 | 2013-05-30 10:53 | LENNOX - GCS29X-030-75-2PA | 51 | 0 | Yes | Yes | 17.8 | 18.8 | -1 | 529C113E760E466D8B00EF546F83A942 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Templeton | CA | 93465-5004 |  | 2013-09-05 | 2013-09-05 17:27 | 2013-09-05 18:04 | PAYNE - PA10JA036-G | 77 | 2.3 | Yes | Yes | 26.1 | 20.9 | 5.2 | B2FB3A58B4804D91AEB84C4337C0F0CC |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Fresno | CA | 93727-7973 |  | 2013-07-16 | 2013-07-16 13:42 | 2013-07-16 14:32 | YORK - D1NP036N05606A | 108 | 5.8 | Yes | Yes | 23.3 | 20.3 | 3.1 | B736878FED9E4488AFBC2C91A9C7BF6A |  | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Fresno | CA | 93720-2532 |  | 2013-06-24 | 2013-06-24 14:30 | 2013-06-24 14:33 | TRANE - 4YCZ6048A 1096BA | 136 | 4 | Yes | Yes | 17.2 | 19.7 | -2.5 | 9E8A0C5276C04F518DF23E2EF57572C6 |  | R410A | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93726-4204 |  | 2013-07-29 | 2013-07-29 12:06 | 2013-07-29 12:11 | YORK - TCGD48S21S2HA | 69 | 10.8 | Yes | Yes | 20.4 | 20.4 | 0 | BE2EB22BDE66440583E97CA976EC3A4A |  | R22 | Non-TXV |  | 15.65% | 0.84348 | 30.08% | [5 empty] | Non-TXV | 15.65%
Fresno | CA | 93703-4056 |  | 2013-08-08 | 2013-08-08 15:15 | 2013-08-08 15:17 | ICP - PGD336060K001C1 | 100 | 5.7 | Yes | Yes | 25.2 | 19.9 | 5.3 | BC0E9B3A87CC46B7B63F4C1C5CE82BE7 |  | R410A | Non-TXV |  | 5.7% | 0.943 | 10.95% | [5 empty] | Non-TXV | 5.7%
Clovis | CA | 93611-5120 |  | 2013-06-14 | 2013-06-14 11:27 | 2013-06-14 11:46 | YORK - D1NP036N05606 | 108 | 5.3 | Yes | Yes | 20.9 | 22.1 | -1.2 | 2320D4586B3B47F0B4471A4D3D396C59 |  | R22 | Non-TXV |  | 4.907% | 0.95093 | 9.431% | [5 empty] | Non-TXV | 4.907%
Clovis | CA | 93611-5137 |  | 2013-10-04 | 2013-10-04 10:41 | 2013-10-04 10:42 | YORK - D1NA036N05606C | 67 | 2.8 | Yes | Yes | 25.7 | 20.1 | 5.6 | 015EA4CB82494E30B1D0A8661DA767B7 |  | R22 | Non-TXV |  | 4.179% | 0.95821 | 8.031% | [5 empty] | Non-TXV | 4.179%
Tracy | CA | 95377-7923 |  | 2013-05-30 | 2013-05-30 13:07 | 2013-05-30 13:41 | YORK - H1RA042S06D | 84 | 7.8 | Yes | Yes | 26 | 22.6 | 3.4 | D856C6F195B646E389C3250AEAA07805 |  | R22 | Non-TXV |  | 9.286% | 0.90714 | 17.85% | [5 empty] | Non-TXV | 9.286%
Fresno | CA | 93703-1440 |  | 2013-06-10 | 2013-06-10 23:17 | 2013-06-10 23:17 | AIRE-FLO - 588ANW042080ACAG | 62 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 639045B0AE9C4E8CB762AF3348D9B9C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7531 |  | 2013-06-17 | 2013-06-17 13:48 | 2013-06-17 13:50 | OTHER - 7777UNK | 96 | 3.7 | Yes | Yes | 23 | 21.9 | 1.1 | 3AFF0187533941EEAF587E4AFC74C32B |  | R22 | Non-TXV |  | 3.854% | 0.96146 | 7.407% | [5 empty] | Non-TXV | 3.854%
Fresno | CA | 93727-7531 |  | 2013-06-17 | 2013-06-17 14:00 | 2013-06-17 14:03 | GOODMAN - GPG1330070M41CA | 78 | 4.4 | Yes | Yes | 22.2 | 20.6 | 1.6 | 05FD540B962047B3BB20270743E7AC0C |  | R410A | Non-TXV |  | 5.641% | 0.94359 | 10.84% | [5 empty] | Non-TXV | 5.641%
Clovis | CA | 93612-3534 |  | 2013-06-18 | 2013-06-18 12:12 | 2013-06-18 12:50 | BRYANT - 582ANW036060AAAF | 56 | 1.8 | Yes | Yes | 20.5 | 22.1 | -1.6 | 2AA354B3BAE44A68B98402D95690C8F2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Stockton | CA | 95206-4650 |  | 2013-06-13 | 2013-06-13 09:43 | 2013-06-13 10:07 | RUUD - 13AJA30A01757 | 70 | 3.1 | Yes | Yes | 22.4 | 19.8 | 2.6 | CE47094324AF47008371FC3B94E97D41 |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Clovis | CA | 93611-5350 |  | 2013-06-28 | 2013-06-28 09:32 | 2013-06-28 10:21 | YORK - DBYP-F042N080A | 150 | 5.5 | Yes | Yes | 17.8 | 20.4 | -2.6 | 3BEA9C376569413BA39B393280CB8890 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Los Banos | CA | 93635-6322 |  | 2013-07-10 | 2013-07-10 12:22 | 2013-07-10 12:32 | OTHER - 2AC13B24P2B | 89 | 11.4 | Yes | Yes | 17.5 | 18.1 | -0.6 | 7A0328671DEF46C5BCA1A26EC65191EE |  | R22 | Non-TXV |  | 12.81% | 0.87191 | 24.62% | [5 empty] | Non-TXV | 12.81%
Fresno | CA | 93703-3228 |  | 2013-08-27 | 2013-08-27 10:56 | 2013-08-27 10:58 | YORK - D3YS024N03206A | 62 | 6.9 | Yes | Yes | 23.6 | 22.4 | 1.2 | 949BE5B42E0A4E13A84C82E5EE0C1F1F |  | R22 | Non-TXV |  | 11.13% | 0.88871 | 21.39% | [5 empty] | Non-TXV | 11.13%
Tracy | CA | 95377-8301 |  | 2013-05-31 | 2013-05-31 10:43 | 2013-05-31 11:32 | YORK - H2RC036S06A | 83 | 26.8 | Yes | Yes | 22.2 | 22.4 | -0.1 | 6CD14D3375B34C2AA83EA2F2AD9F156C |  | R22 | Non-TXV |  | 32.29% | 0.67711 | 62.05% | [5 empty] | Non-TXV | 32.29%
Tracy | CA | 95377-8301 |  | 2013-06-03 | 2013-06-03 16:48 | 2013-06-03 17:05 | YORK - H2RC036S06A | 83 | 20.3 | Yes | Yes | 26.9 | 22.5 | 4.4 | 869E2E04A4B647499D940D622A7A09F0 |  | R22 | Non-TXV |  | 24.46% | 0.75542 | 47% | [5 empty] | Non-TXV | 24.46%
Stockton | CA | 95215-7539 |  | 2013-06-06 | 2013-06-06 15:24 | 2013-06-06 15:24 | PAYNE - PA13NR036000ACAA | 128 | 0 | Yes | Yes | 21.4 | 19.9 | 1.5 | 0265E8D3481943DC972E833074952999 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-4634 |  | 2013-06-13 | 2013-06-13 10:25 | 2013-06-13 10:48 | BRYANT - 561CJ024-C | 130 | 4 | Yes | Yes | 23.1 | 19.8 | 3.3 | E96ADBF91DFE42CB93E3C381202E89B5 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95209-4035 |  | 2013-05-22 | 2013-05-22 12:22 | 2013-05-22 12:57 | DAY & NIGHT - 585B024075YACR | 52 | 11 | Yes | Yes | 18.3 | 21.1 | -2.8 | EA2E7FCE18B341E3A5F520C416C454C6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.15% | 0.78846 | 40.65% | [5 empty] | Non-TXV | 21.15%
Fresno | CA | 93720-4463 |  | 2013-06-24 | 2013-06-24 13:53 | 2013-06-24 13:56 | OTHER - FADC-060JAS | 112 | 3.4 | Yes | Yes | 16.5 | 19.3 | -2.8 | D0A901ED9EDD41F9B2B1DB1DCEE9B5D5 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Merced | CA | 95348-1602 |  | 2013-06-17 | 2013-06-17 13:16 | 2013-06-17 13:32 | YORK - D1NA024N05606C | 54 | 4.5 | Yes | Yes | 18.7 | 20.1 | -1.4 | 18D4E03C20424087AA21817F9E226946 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Manteca | CA | 95337-6888 |  | 2013-08-30 | 2013-08-30 13:38 | 2013-08-30 14:00 | TRANE - 2TTB3060A1000AAA | 139 | 6.4 | Yes | Yes | 26.3 | 21.4 | 4.9 | 6156703F7DEA4851A443242A29C37383 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 4.604% | 0.95396 | 8.848% | [5 empty] | TXV | 4.604%
Oakdale | CA | 95361-8420 |  | 2013-07-10 | 2013-07-10 13:27 | 2013-07-10 13:53 | YORK - E1RA024S06D | 80 | 2.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | 8CE6E850CADF4D4199E3B730FA73B59A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Orosi | CA | 93647-2036 |  | 2013-07-26 | 2013-07-26 17:21 | 2013-07-26 18:28 | CARRIER - 48ESN048090301 | 144 | 5.9 | Yes | Yes | 24 | 19.9 | 4.1 | EA8CA7BA5C8C42588628D010F9CE3BA2 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 4.097% | 0.95903 | 7.874% | [5 empty] | TXV | 4.097%
Magalia | CA | 95954-9023 |  | 2013-07-17 | 2013-07-17 08:40 | 2013-07-17 09:14 | DAY & NIGHT - 588ANW03008AAAAD | 100 | 6.9 | Yes | Yes | 20.7 | 22 | -1.3 | A922BDEBC0704F1CA63582100DED0DF2 |  | R22 | Non-TXV |  | 6.9% | 0.931 | 13.26% | [5 empty] | Non-TXV | 6.9%
Los Banos | CA | 93635-3401 |  | 2013-07-09 | 2013-07-09 10:07 | 2013-07-09 10:09 | YORK - D1NP030N05606A | 73 | 10.9 | Yes | Yes | 21.9 | 19.4 | 2.5 | B5E03CB022054D0BBCF43A889BE3BDF2 |  | R22 | Non-TXV |  | 14.93% | 0.85068 | 28.7% | [5 empty] | Non-TXV | 14.93%
Gerber | CA | 96035-9715 |  | 2013-06-01 | 2013-06-01 10:36 | 2013-06-01 11:05 | ECONAIR - EFGM216551 | 225 | 9.5 | Yes | Yes | 24.5 | 20.7 | 3.8 | C60EA6BEDCD741EF97E0A32D21F1FB8B |  | R22 | Non-TXV |  | 4.222% | 0.95778 | 8.114% | [5 empty] | Non-TXV | 4.222%
Stockton | CA | 95210-2123 |  | 2013-06-12 | 2013-06-12 13:32 | 2013-06-12 13:54 | DAY & NIGHT - 567C024RCU | 60 | 5.8 | Yes | Yes | 26.1 | 20.2 | 5.9 | AA36F28748084E5B9066FFF5515DE029 |  | R22 | Non-TXV |  | 9.667% | 0.90333 | 18.58% | [5 empty] | Non-TXV | 9.667%
Fresno | CA | 93710-7002 |  | 2013-08-22 | 2013-08-22 10:56 | 2013-08-22 10:57 | ICP - HAC042AKC3 | 98 | 11.5 | Yes | Yes | 24.9 | 19.3 | 5.6 | 653FF8F2F4A64145B580612C60B77C15 |  | R22 | Non-TXV |  | 11.73% | 0.88265 | 22.55% | [5 empty] | Non-TXV | 11.73%
Stockton | CA | 95207-2103 |  | 2013-06-03 | 2013-06-03 09:03 | 2013-06-03 09:03 | PAYNE - 582ANW030060NAAD | 55 | 0 | Yes | Yes | 25 | 19.6 | 5.5 | 86D91782325F48CE96EAE3A0AD2B722B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-8140 |  | 2013-06-04 | 2013-06-04 09:30 | 2013-06-04 09:52 | CARRIER - 48SS-048100301 | 104 | 10.9 | Yes | Yes | 21.8 | 19.5 | 2.3 | 727C6B8F29FF4AADBD5883A88B776D21 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.48% | 0.89519 | 20.14% | [5 empty] | Non-TXV | 10.48%
Clovis | CA | 93611-1490 |  | 2013-06-12 | 2013-06-12 13:06 | 2013-06-12 13:31 | CARRIER - N/A | 120 | 15.5 | Yes | Yes | 16.1 | 18.8 | -2.7 | C7E26E26DCE148E28FC875D6E2510B92 |  | R22 | Non-TXV |  | 12.92% | 0.87083 | 24.82% | [5 empty] | Non-TXV | 12.92%
Los Banos | CA | 93635-3206 |  | 2013-05-30 | 2013-05-30 14:38 | 2013-05-30 14:43 | YORK - H2DB036S06A | 73 | 11.3 | Yes | Yes | 21.4 | 20.8 | 0.6 | 4F754F4DED1F4304A418494287264ABC |  | R22 | Non-TXV |  | 15.48% | 0.84521 | 29.75% | [5 empty] | Non-TXV | 15.48%
Stockton | CA | 95215-6051 |  | 2013-06-05 | 2013-06-05 12:40 | 2013-06-05 12:40 | RUUD - RRNL-B036JK06X | 92 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 5A54E6DC379D4755B0418BC39B0A637B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Orland | CA | 95963-1945 |  | 2013-09-05 | 2013-09-05 12:50 | 2013-09-05 13:25 | LENNOX - 5175KO1068 | 70 | 5.9 | Yes | Yes | 16.5 | 18.2 | -1.7 | 03822960908C431899A4C3A087A62A8B |  | R22 | Non-TXV |  | 8.429% | 0.91571 | 16.2% | [5 empty] | Non-TXV | 8.429%
Clovis | CA | 93612-3536 |  | 2013-08-22 | 2013-08-22 16:05 | 2013-08-22 17:11 | BDP - 589ANW036060ADAF | 84 | 6.5 | Yes | Yes | 20 | 21.1 | -1.1 | EEEBC8954F2343C8A43F77053723C34A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.738% | 0.92262 | 14.87% | [5 empty] | Non-TXV | 7.738%
Manton | CA | 96059-8623 |  | 2013-09-20 | 2013-09-20 09:45 | 2013-09-20 09:45 | OTHER - SCU12G36A-1 | 99 | 0 | Yes | Yes | 22.9 | 24.4 | -1.5 | 64BD98D750BD45D98B0EF16A36E434B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2103 |  | 2013-05-29 | 2013-05-29 15:28 | 2013-05-29 15:49 | OTHER - 24/75 TP | 72 | 16.3 | Yes | Yes | 21.9 | 18.8 | 3.1 | 787E1EA6079C4A1DAD72247E893314AF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.64% | 0.77361 | 43.51% | [5 empty] | Non-TXV | 22.64%
Gerber | CA | 96035-9613 |  | 2013-06-01 | 2013-06-01 13:53 | 2013-06-01 14:12 | GIBSON - JT3BC-030K | 137 | 12.3 | Yes | Yes | 24.2 | 22.6 | 1.6 | 6264535D74654C838DBADCE5A6E0E8F8 |  | R22 | Non-TXV |  | 8.978% | 0.91022 | 17.25% | [5 empty] | Non-TXV | 8.978%
Stockton | CA | 95210-1750 |  | 2013-06-18 | 2013-06-18 08:49 | 2013-06-18 09:05 | GOODMAN - GPG1336070M41BA | 70 | -4.1 | Yes | Yes | 22.8 | 18.2 | 4.6 | D327EB6A55E242E995180CFD13F92759 |  | R410A | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Fresno | CA | 93727-3137 |  | 2013-06-11 | 2013-06-11 11:57 | 2013-06-11 12:32 | GOODMAN - PGB03675-1 | 60 | 2 | Yes | Yes | 26.1 | 20.2 | 5.9 | 1711917BD89A48CE99595CD349C44995 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95348-1221 |  | 2013-08-09 | 2013-08-09 12:11 | 2013-08-09 12:31 | GE - BTD724A100A0 | 68 | 7.4 | Yes | Yes | 21.4 | 19.8 | 1.6 | 333A078F8BAF4916BA8A09DBE00CE67A |  | R22 | Non-TXV |  | 10.88% | 0.89118 | 20.91% | [5 empty] | Non-TXV | 10.88%
Sonora | CA | 95370-8612 |  | 2013-07-31 | 2013-07-31 14:23 | 2013-07-31 14:57 | LENNOX - HS18-461-7P | 93 | 10.1 | Yes | Yes | 22.7 | 21.5 | 1.2 | 95F423F02DA9403285F3BA4E9E5F22EF |  | R22 | TXV |  | 10.86% | 0.8914 | 20.87% | [5 empty] | TXV | 10.86%
Stockton | CA | 95204-3345 |  | 2013-06-03 | 2013-06-03 08:44 | 2013-06-03 09:03 | RHEEM - RRKA-A030JK08E | 54 | 4.2 | Yes | Yes | 18 | 17.5 | 0.5 | 4262E43F219F4EAFAF6E5DAA6BD5B8E0 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Gerber | CA | 96035-9664 |  | 2013-09-13 | 2013-09-13 15:12 | 2013-09-13 15:31 | COLEMAN - BRCQ0481BD | 114 | 4 | Yes | Yes | 24.6 | 20.1 | 4.5 | 01C3DF31CFDB4F7B8B9E7202128D8BE2 |  | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Stockton | CA | 95210-1516 |  | 2013-06-11 | 2013-06-11 08:41 | 2013-06-11 09:02 | YORK - D1NP030N05606A | 73 | -5.2 | Yes | Yes | 19 | 18.3 | 0.7 | 9221DD5E2BEF49C195DD98B2DFD05F45 |  | R22 | Non-TXV |  | -7.123% | 1.0712 | 1.995% |  |  |  |  | Non-TXV |  |  | -7.123%
Oroville | CA | 95966-7815 |  | 2013-08-02 | 2013-08-02 09:19 | 2013-08-02 10:36 | RHEEM - RAMA-024JAZ | 85 | 6 | Yes | Yes | 18.3 | 21 | -2.7 | 1DDD3ACE46104D698670BA41DD4B01CE |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Somerset | CA | 95684-9204 |  | 2013-08-12 | 2013-08-12 12:24 | 2013-08-12 12:24 | AMANA - SPH042001A | 132.2 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | 2872871709924743AEB219713D4CA58A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3626 |  | 2013-07-25 | 2013-07-25 11:00 | 2013-07-25 11:19 | YORK - D1NA036N07206A | 63 | 2.1 | Yes | Yes | 19.6 | 18.2 | 1.4 | 1056D4B4F1F549D6B286BAD5AAD56519 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Auburn | CA | 95602-2605 |  | 2013-06-17 | 2013-06-17 09:28 | 2013-06-17 09:28 | CARRIER - UNK COVERED BY DISCONNECT SWITCH | 63 | 0 | Yes | Yes | 25 | 19.5 | 5.5 | DE89F13656DB456592232338954AA278 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-2228 |  | 2013-06-14 | 2013-06-14 12:56 | 2013-06-14 13:27 | RUUD - UARL-048JAZ | 154 | 14.7 | Yes | Yes | 22 | 22 | 0 | CE825806B7A449A098548F63A3AA7470 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Stockton | CA | 95205-2576 |  | 2013-06-04 | 2013-06-04 15:07 | 2013-06-04 15:27 | CARRIER - 38EZG048300 | 125 | 6.5 | Yes | Yes | 24.4 | 19.3 | 5.1 | 5498E0FCA33145FE8E4E244627613434 |  | R410A | TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | TXV | 5.2%
Stockton | CA | 95206-5211 |  | 2013-06-20 | 2013-06-20 08:28 | 2013-06-20 08:55 | GOODMAN - CK30-1B | 85 | 8.1 | Yes | Yes | 21.9 | 20.4 | 1.5 | 78C42FE15FB44159869B1936C49C1414 |  | R22 | Non-TXV |  | 9.529% | 0.90471 | 18.31% | [5 empty] | Non-TXV | 9.529%
Live Oak | CA | 95953-2829 |  | 2013-08-05 | 2013-08-05 14:05 | 2013-08-05 14:05 | CARRIER - 38ETG060300 | 210 | 0 | Yes | Yes | 22 | 19.5 | 2.5 | B4C086C32D2942B5AF9D942874B1C1DD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-4636 |  | 2013-07-11 | 2013-07-11 12:29 | 2013-07-11 12:53 | RHEEM - RAFD-042JBS | 85 | 7.3 | Yes | Yes | 23.3 | 22.5 | 0.8 | 25FF6E9A0F5145FB8F9417CB3F83951C |  | R22 | Non-TXV |  | 8.588% | 0.91412 | 16.5% | [5 empty] | Non-TXV | 8.588%
Tracy | CA | 95376-2221 |  | 2013-05-24 | 2013-05-24 10:24 | 2013-05-24 11:17 | GOODMAN - PGB036075-1A | 60 | 2.1 | Yes | Yes | 24 | 20.6 | 3.4 | 8A698A70E87E4F538823FE5FEDFE2045 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Rocklin | CA | 95677-2218 |  | 2013-06-11 | 2013-06-11 10:24 | 2013-06-11 10:46 | HEIL - CA5036VKB1 | 86 | 2.6 | Yes | Yes | 20 | 18.8 | 1.2 | 7E6E0E138D42441F81F16272E57B98EA |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Atwater | CA | 95301-3936 |  | 2013-07-18 | 2013-07-18 18:24 | 2013-07-18 18:26 | AMERICAN STANDARD - YCY036G1MOAD | 130 | 15.6 | Yes | Yes | 24 | 20.6 | 3.4 | AF3BD862F4F34C4DBD6F3B4B5F0B85ED |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Stockton | CA | 95210-1411 |  | 2013-06-10 | 2013-06-10 10:04 | 2013-06-10 10:21 | WESTINGHOUSE - IE030BAAON | 90 | 2.7 | Yes | Yes | 20.8 | 17.7 | 3.1 | CF53BEC7A1254DB1B475706A3208625F |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Tracy | CA | 95376-3188 |  | 2013-05-28 | 2013-05-28 12:21 | 2013-05-28 12:41 | AMERICAN STANDARD - YCC024F1LOBG | 65 | 4.7 | Yes | Yes | 20.7 | 18.8 | 1.9 | 9600944D44E9428F8CDC23346056C47D |  | R22 | Non-TXV |  | 7.231% | 0.92769 | 13.9% | [5 empty] | Non-TXV | 7.231%
Atwater | CA | 95301-0000 |  | 2013-06-05 | 2013-06-05 08:17 | 2013-06-05 08:17 | RHEEM - RAFA030JAQ | 57 | 0 | Yes | Yes | 16.5 | 18.8 | -2.3 | 549F4F04E1B74A74A8271410F2BA609E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-5730 |  | 2013-08-06 | 2013-08-06 11:02 | 2013-08-06 11:23 | GOODMAN - PGB024050-1 | 85 | 3.2 | Yes | Yes | 17.5 | 18.6 | -1.1 | 496ED6EEC58542A193C73AD7DC4EA4BE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Atwater | CA | 95301-2904 |  | 2013-06-05 | 2013-06-05 13:36 | 2013-06-05 13:45 | GOODMAN - GPG13300701BB | 77 | 6.9 | Yes | Yes | 16.7 | 19.3 | -2.6 | 909E5E919B274A15A150ABD1EE95683C |  | R22 | Non-TXV |  | 8.961% | 0.91039 | 17.22% | [5 empty] | Non-TXV | 8.961%
Grass Valley | CA | 95949-6585 |  | 2013-06-13 | 2013-06-13 11:56 | 2013-06-13 11:56 | CARRIER - 50Y030300 | 87 | 0 | Yes | Yes | 22 | 19.5 | 2.5 | C99208749E1B4A19A3841B4DD9A809E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1629 |  | 2013-06-12 | 2013-06-12 16:49 | 2013-06-12 17:10 | OTHER - 22JK | 57 | 8.6 | Yes | Yes | 22 | 22.6 | -0.6 | 943297171B75413794A2BE810470A510 |  | R22 | Non-TXV |  | 15.09% | 0.84912 | 29% | [5 empty] | Non-TXV | 15.09%
Jackson | CA | 95642-2509 |  | 2013-09-04 | 2013-09-04 10:06 | 2013-09-04 10:31 | NORDYNE - JS3BA-048KA | 115 | 4 | Yes | Yes | 23.8 | 19.3 | 4.5 | 513A768F0047470B8FC1CDBAD1402586 |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Stockton | CA | 95210-4309 |  | 2013-05-29 | 2013-05-29 14:18 | 2013-05-29 14:35 | BDP - 585B024050YACR | 51 | 1.6 | Yes | Yes | 18.4 | 20.8 | -2.4 | 24C8A566EBCC4F51A44BAB60B70DBB86 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Nevada City | CA | 95959-9519 |  | 2013-08-27 | 2013-08-27 18:00 | 2013-08-27 20:39 | PAYNE - PA10JC036-C | 78 | 11.6 | Yes | Yes | 18.2 | 20.8 | -2.6 | BAEF0FCF2AE246E188541288130E6AAA |  | R22 | TXV |  | 14.87% | 0.85128 | 28.58% | [5 empty] | TXV | 14.87%
Oroville | CA | 95966-8508 |  | 2013-07-29 | 2013-07-29 21:01 | 2013-07-29 21:26 | LENNOX - 12CH80483PA | 195 | 8.1 | Yes | Yes | 19.1 | 21.4 | -2.3 | C145BA5798F54591A8A30411D27E99C5 |  | R22 | Non-TXV |  | 4.154% | 0.95846 | 7.983% | [5 empty] | Non-TXV | 4.154%
Stockton | CA | 95203-3163 |  | 2013-05-28 | 2013-05-28 11:40 | 2013-05-28 11:59 | LUXAIRE - UNK | 54 | 2.4 | Yes | Yes | 17.1 | 18.5 | -1.4 | 39B0E10DCA0E479C96129675AEA125D5 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Los Banos | CA | 93635-2971 |  | 2013-05-28 | 2013-05-28 12:17 | 2013-05-28 12:21 | OTHER - CA3048VKA1 | 145 | 6.9 | Yes | Yes | 17.7 | 19.7 | -2 | 53BB025114354E788FD2EF3381A8BF62 |  | R22 | Non-TXV |  | 4.759% | 0.95241 | 9.145% | [5 empty] | Non-TXV | 4.759%
Stockton | CA | 95212-3434 |  | 2013-06-17 | 2013-06-17 11:46 | 2013-06-17 12:02 | UNITARY PRODUCTS GROUP - AC048X1222A | 119 | 10.6 | Yes | Yes | 19.1 | 20.7 | -1.6 | 35321B7C32E74D73BF6B0E693C4F9C5F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.908% | 0.91092 | 17.12% | [5 empty] | Non-TXV | 8.908%
Jackson | CA | 95642-0000 |  | 2013-08-20 | 2013-08-20 09:52 | 2013-08-20 10:22 | NORDYNE - GR4GC-060K096X | 85 | 5.5 | Yes | Yes | 20 | 15.2 | 4.8 | F18BDD35FCD144B8B87ACB1691491F02 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Oroville | CA | 95966-9599 |  | 2013-08-02 | 2013-08-02 19:35 | 2013-08-02 19:56 | RUUD - UAKA-036JAS | 75 | 2.5 | Yes | Yes | 19.7 | 19.5 | 0.2 | 5BC4CA97EBC741058B42A1D79BA405D5 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95207-3130 |  | 2013-05-30 | 2013-05-30 15:15 | 2013-05-30 15:36 | GOODMAN - GSX130361BA | 89 | 8.7 | Yes | Yes | 24.9 | 19.9 | 5 | C9AE012ABB634655BC239E8053813A4F |  | R410A | TXV |  | 9.775% | 0.90225 | 18.79% | [5 empty] | TXV | 9.775%
Stockton | CA | 95210-3246 |  | 2013-07-08 | 2013-07-08 10:13 | 2013-07-08 10:36 | GOODMAN - GSX130361BA | 89 | -5.2 | Yes | Yes | 15.2 | 18.2 | -3 | 7DA4B8751C4E4B07AB5E734CA800DD5F |  | R410A | Non-TXV |  | -5.843% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.843%
Auburn | CA | 95602-8403 |  | 2013-06-12 | 2013-06-12 10:50 | 2013-06-12 11:08 | TRANE - TTB018C100A0 | 51 | 5.2 | Yes | Yes | 21.5 | 17.7 | 3.8 | B29D266F3B454381A9831A4CEFE582D0 |  | R22 | Non-TXV |  | 10.2% | 0.89804 | 19.59% | [5 empty] | Non-TXV | 10.2%
Chico | CA | 95973-0447 |  | 2013-06-05 | 2013-06-05 11:32 | 2013-06-05 12:49 | YORK - D1NA036N05606C | 67 | 9.8 | Yes | Yes | 17.6 | 20.4 | -2.8 | 8F320E501E484DD783A34C096D7D741C |  | R22 | Non-TXV |  | 14.63% | 0.85373 | 28.11% | [5 empty] | Non-TXV | 14.63%
Red Bluff | CA | 96080-2254 |  | 2013-09-03 | 2013-09-03 16:08 | 2013-09-03 16:25 | AMERICAN STANDARD - YCY060G1MOAC | 151 | 5.2 | Yes | Yes | 18 | 21 | -3 | 6A343296EBEA4295846BEB08D51704AE |  | R22 | Non-TXV |  | 3.444% | 0.96556 | 6.618% | [5 empty] | Non-TXV | 3.444%
Red Bluff | CA | 96080-4722 |  | 2013-05-30 | 2013-05-30 21:59 | 2013-05-30 22:17 | BRYANT - 574DNW024040NA | 85 | 3.6 | Yes | Yes | 20.5 | 21.5 | -1 | E4A22FB9DE524795A8A76FBF1622C514 |  | R410A | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Mariposa | CA | 95338-9636 |  | 2013-09-11 | 2013-09-11 10:48 | 2013-09-11 10:50 | BDP - 561CJ048B | 99 | 7.6 | Yes | Yes | 22.5 | 18.8 | 3.7 | D8A512716CF14090B949272B480A0743 |  | R22 | TXV |  | 7.677% | 0.92323 | 14.75% | [5 empty] | TXV | 7.677%
Los Banos | CA | 93635-5428 |  | 2013-06-01 | 2013-06-01 11:13 | 2013-06-01 11:22 | TRANE - 2TTB3024A1000AA | 82 | 3.3 | Yes | Yes | 23.6 | 22 | 1.6 | CBF77CB9679F4B8FA1CB1B22A4E6A38B |  | R22 | TXV |  | 4.024% | 0.95976 | 7.734% | [5 empty] | TXV | 4.024%
Fresno | CA | 93727-3605 |  | 2013-08-14 | 2013-08-14 10:58 | 2013-08-14 11:16 | YORK - DAYP-F036N070A | 108 | 3.5 | Yes | Yes | 21.6 | 19.9 | 1.8 | A0248B6A766C467E9A23D8D700E9479F |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Fresno | CA | 93727-3605 |  | 2013-08-14 | 2013-08-14 11:22 | 2013-08-14 11:44 | YORK - UNK | 67 | 2.3 | Yes | Yes | 24.8 | 20.4 | 4.4 | 62C7039AD43744CB9C44B3806D361404 |  | R22 | Non-TXV |  | 3.433% | 0.96567 | 6.597% | [5 empty] | Non-TXV | 3.433%
Pollock Pines | CA | 95726-9226 |  | 2013-07-29 | 2013-07-29 12:47 | 2013-07-29 12:47 | INTERTHERM - S30A-024KA | 64 | 0 | Yes | Yes | 24 | 22.1 | 1.9 | C83D135DE6204EC08FC0650BEC93F8B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5258 |  | 2013-10-26 | 2013-10-26 10:30 | 2013-10-26 11:25 | AMERICAN STANDARD - YCC024F1L0BC | 64 | 5.4 | Yes | Yes | 26 | 21.4 | 4.7 | 9AF1A8F648EA4C38B895F6ED87772D8A |  | R22 | Non-TXV |  | 8.438% | 0.91563 | 16.22% | [5 empty] | Non-TXV | 8.438%
Auburn | CA | 95602-8408 |  | 2013-08-13 | 2013-08-13 17:04 | 2013-08-13 17:04 | TRANE - TTD718B100A0 | 50 | 0 | Yes | Yes | 18.6 | 19 | -0.4 | 71373B8354BF4B8BB34D26A4514AA830 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Dos Palos | CA | 93620-2037 |  | 2013-08-16 | 2013-08-16 10:00 | 2013-08-16 10:03 | GOODMAN - CK49-1B | 97 | 4.6 | Yes | Yes | 23.3 | 17.4 | 5.9 | 865F91AE92B44558BFFBBC0223D3935C |  | R22 | Non-TXV |  | 4.742% | 0.95258 | 9.114% | [5 empty] | Non-TXV | 4.742%
Fresno | CA | 93720-0452 |  | 2013-06-26 | 2013-06-26 09:01 | 2013-06-26 09:07 | OTHER - UNK | 67 | 4.1 | Yes | Yes | 17.3 | 19 | -1.7 | 569EC82918E64C0CA08E605A85E1F6CB |  | R22 | Non-TXV |  | 6.119% | 0.93881 | 11.76% | [5 empty] | Non-TXV | 6.119%
Paso Robles | CA | 93446-4756 |  | 2013-08-06 | 2013-08-06 12:07 | 2013-08-06 12:27 | BRYANT - 561CJ030-A | 76 | 5.2 | Yes | Yes | 23 | 20.4 | 2.6 | F3C69DFA1AAC4BDBB1D0CCD34D33873B |  | R22 | Non-TXV |  | 6.842% | 0.93158 | 13.15% | [5 empty] | Non-TXV | 6.842%
Tracy | CA | 95304-8418 |  | 2013-06-05 | 2013-06-05 09:59 | 2013-06-05 10:25 | RHEEM - RAKA-030JAZ | 85 | 4 | Yes | Yes | 21.7 | 18.8 | 2.9 | CB59A4E9626E4EDFB116B4B90AEAC708 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fresno | CA | 93720-0414 |  | 2013-06-20 | 2013-06-20 10:13 | 2013-06-20 10:19 | YORK - H2DH048SO6A | 190 | 13.6 | Yes | Yes | 22.5 | 20.4 | 2.1 | A2D120164D3B454A9DFA72F7916C1FA1 |  | R22 | Non-TXV |  | 7.158% | 0.92842 | 13.76% | [5 empty] | Non-TXV | 7.158%
Tracy | CA | 95377-7930 |  | 2013-05-31 | 2013-05-31 12:42 | 2013-05-31 13:00 | GOODMAN - CKJ48-1AB | 85 | 5 | Yes | Yes | 21.7 | 22 | -0.3 | 887FB14EFE8348C4A7B9DD4D1CA85FA3 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Auburn | CA | 95602-8405 |  | 2013-08-13 | 2013-08-13 17:50 | 2013-08-13 17:50 | GE - BTB912A800A0 | 36 | 0 | Yes | Yes | 21.2 | 19.4 | 1.8 | 64A283F5FD2B4FA9BC8EBA20A1F8BC20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95202-1749 |  | 2013-07-09 | 2013-07-09 14:52 | 2013-07-09 15:36 | AMANA - RCB48C2B | 116 | 26.5 | Yes | Yes | 29.5 | 23.5 | 6 | 43A5E5DE59524A1EADA3E920BB6651F7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 22.84% | 0.77155 | 43.9% | [5 empty] | Non-TXV | 22.84%
Yuba City | CA | 95991-1562 |  | 2013-06-10 | 2013-06-10 12:23 | 2013-06-10 12:43 | DAY & NIGHT - 541DJ024 | 118 | 15.3 | Yes | Yes | 18.5 | 19.9 | -1.4 | 50E2B13DAE844FE7B66432116325A759 |  | R22 | Non-TXV |  | 12.97% | 0.87034 | 24.92% | [5 empty] | Non-TXV | 12.97%
Clovis | CA | 93612-5064 |  | 2013-08-07 | 2013-08-07 11:43 | 2013-08-07 11:54 | YORK - DAYAF024N045C | 54 | 7.8 | Yes | Yes | 24.1 | 20.8 | 3.3 | 62B27BD2499241D587459FC302673910 |  | R22 | Non-TXV |  | 14.44% | 0.85556 | 27.76% | [5 empty] | Non-TXV | 14.44%
Red Bluff | CA | 96080-0000 |  | 2013-05-29 | 2013-05-29 16:21 | 2013-05-29 16:42 | OTHER - NA | 72 | 3.9 | Yes | Yes | 23.1 | 20.9 | 2.2 | C17BC7B41EFD4407828A64FC40C632B8 |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Fresno | CA | 93720-0445 |  | 2013-10-26 | 2013-10-26 11:28 | 2013-10-26 13:51 | BDP - 563CN042-A | 131 | 4.4 | Yes | Yes | 24.5 | 20.4 | 4.1 | F93C76CC278E493F91843F5CCC70C4C6 |  | R22 | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
Rocklin | CA | 95677-1725 |  | 2013-06-11 | 2013-06-11 09:36 | 2013-06-11 09:58 | CARRIER - 38TK036300 | 117 | 11.8 | Yes | Yes | 18.3 | 19.5 | -1.2 | 1AE1D2DC31E341CDB19F86A86F6449C9 |  | R22 | Non-TXV |  | 10.09% | 0.89915 | 19.38% | [5 empty] | Non-TXV | 10.09%
Tracy | CA | 95376-4813 |  | 2013-05-28 | 2013-05-28 14:46 | 2013-05-28 15:04 | AMERICAN STANDARD - 7A2042A100A2 | 85 | -8 | Yes | Yes | 25.7 | 19.9 | 5.8 | 33669CE313C24F9F9CA79037D7192D79 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95210-2600 |  | 2013-06-12 | 2013-06-12 12:37 | 2013-06-12 12:37 | CARRIER - 24/60YAC108-C | 58 | 0 | Yes | Yes | 21.7 | 20.3 | 1.5 | 6A7A97697EFC40D292F7E0E207EEA92F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-2759 |  | 2013-06-21 | 2013-06-21 10:14 | 2013-06-21 10:34 | CARRIER - 24ABA360A320 | 132 | 7.1 | Yes | Yes | 21.1 | 19.3 | 1.8 | 079884388C1D4F79AA2EAD3DAFB73F3A |  | R410A | TXV |  | 5.379% | 0.94621 | 10.34% | [5 empty] | TXV | 5.379%
Winton | CA | 95388-9634 |  | 2013-06-14 | 2013-06-14 14:29 | 2013-06-14 14:42 | OTHER - UNK | 84 | 5.1 | Yes | Yes | 17.3 | 15.7 | 1.6 | 4E93556A4313467991BBD8F29C5A24C6 |  | R22 | Non-TXV |  | 6.071% | 0.93929 | 11.67% | [5 empty] | Non-TXV | 6.071%
Atwater | CA | 95301-2290 |  | 2013-06-06 | 2013-06-06 08:28 | 2013-06-06 08:31 | BDP - 585HJW030010ABA | 86 | 3.3 | Yes | Yes | 24.6 | 18.8 | 5.9 | 7EC2F84E360F4DACBDF9A2C8CC32CF88 |  | R22 | Non-TXV |  | 3.837% | 0.96163 | 7.374% | [5 empty] | Non-TXV | 3.837%
Clovis | CA | 93612-5003 |  | 2013-08-07 | 2013-08-07 10:13 | 2013-08-07 10:15 | GOODMAN - PGB042075 | 68 | 8.9 | Yes | Yes | 20.1 | 15.2 | 4.9 | 0EB369AF28F24463BC009F34051D198A |  | R22 | Non-TXV |  | 13.09% | 0.86912 | 25.15% | [5 empty] | Non-TXV | 13.09%
Stockton | CA | 95207-6011 |  | 2013-06-04 | 2013-06-04 12:23 | 2013-06-04 12:43 | RUUD - UNK | 85 | 3.2 | Yes | Yes | 17.9 | 18.6 | -0.7 | E57CD23DCF91479CA05A38F06CD68EF3 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Stockton | CA | 95210-1884 |  | 2013-06-11 | 2013-06-11 12:53 | 2013-06-11 13:14 | TRANE - TTB730A100A0 | 66 | 14.8 | Yes | Yes | 19.8 | 16.4 | 3.4 | EE6A9C0709144EE28FB7AB39A53BB63F |  | R22 | Non-TXV |  | 22.42% | 0.77576 | 43.09% | [5 empty] | Non-TXV | 22.42%
Lincoln | CA | 95648-2341 |  | 2013-05-30 | 2013-05-30 13:26 | 2013-05-30 13:45 | YORK - H2RA030S06D | 62 | 1.8 | Yes | Yes | 19 | 21.7 | -2.7 | A8B3E9EC0C7B425DA95A21A6BA48311C |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Live Oak | CA | 95953-0000 |  | 2013-08-05 | 2013-08-05 11:14 | 2013-08-05 11:51 | YORK - H1RE036 | 150 | 5.8 | Yes | Yes | 17 | 19.2 | -2.2 | AAF98C6644C34BF5B93D9DE812D2713D |  | R22 | TXV |  | 3.867% | 0.96133 | 7.431% | [5 empty] | TXV | 3.867%
Stockton | CA | 95210-1503 |  | 2013-06-26 | 2013-06-26 13:07 | 2013-06-26 13:26 | PAYNE - UNK | 64 | -4.5 | Yes | Yes | 20.5 | 14.5 | 6 | 25FFCD5639454F00B3A2DF50F33DB01F |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Clovis | CA | 93611-0320 |  | 2013-06-13 | 2013-06-13 08:58 | 2013-06-13 09:19 | YORK - D3CG048N06206E | 88 | 13.8 | Yes | Yes | 21.8 | 20.4 | 1.4 | 5B539ABFD5B5403ABE450CE747BFA417 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.68% | 0.84318 | 30.14% | [5 empty] | Non-TXV | 15.68%
Chico | CA | 95928-6069 |  | 2013-06-04 | 2013-06-04 11:56 | 2013-06-04 12:48 | BDP - 567C018RCU | 57 | 8.1 | Yes | Yes | 26.2 | 22.1 | 4.1 | 43323205FBB84BFFBCF033ADD20A0C7F |  | R22 | Non-TXV |  | 14.21% | 0.85789 | 27.31% | [5 empty] | Non-TXV | 14.21%
Auburn | CA | 95602-8402 |  | 2013-05-28 | 2013-05-28 12:51 | 2013-05-28 13:21 | TRANE - TTBO18C100A2 | 47 | 1.4 | Yes | Yes | 14 | 15.9 | -1.9 | 03B8C15D62FA4BFD811E08C2F20774F8 |  | R22 | Non-TXV |  | 2.979% | 0.97021 | 5.724% | [5 empty] | Non-TXV | 2.979%
Stockton | CA | 95204-4729 |  | 2013-06-01 | 2013-06-01 14:55 | 2013-06-01 15:14 | DAY & NIGHT - 561CJ030-A | 66 | 6.3 | Yes | Yes | 21.4 | 19.3 | 2.2 | AE98DAEFA8274AB89C02146B16363A21 |  | R22 | TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | TXV | 9.545%
Orland | CA | 95963-1826 |  | 2013-09-05 | 2013-09-05 13:34 | 2013-09-05 14:28 | LENNOX - GCS20R-411-75-2P | 70 | 5.8 | Yes | Yes | 15.8 | 14.2 | 1.6 | 776E3B645CB4424C893E283A6AAF6A74 |  | R22 | Non-TXV |  | 8.286% | 0.91714 | 15.92% | [5 empty] | Non-TXV | 8.286%
Lincoln | CA | 95648-8103 |  | 2013-05-31 | 2013-05-31 09:35 | 2013-05-31 10:00 | YORK - H2RC036S06HA | 83 | 2.5 | Yes | Yes | 21 | 20.2 | 0.8 | 66086B5011F841B4AC06D8CA91A5F2FD |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Stockton | CA | 95206-2266 |  | 2013-06-20 | 2013-06-20 12:25 | 2013-06-20 12:43 | BRYANT - 574ANW030060NA | 130 | -12.2 | Yes | Yes | 26.4 | 22 | 4.4 | 76257A10B7854F19A91B733C871EC1EB |  | R22 | Non-TXV |  | -9.385% | 1.0938 | 2.628% |  |  |  |  | Non-TXV |  |  | -9.385%
Stockton | CA | 95203-3139 |  | 2013-05-29 | 2013-05-29 12:20 | 2013-05-29 12:36 | LUXAIRE - UNK | 54 | 2.5 | Yes | Yes | 18.3 | 17.5 | 0.8 | 541B61AE4B5342F4881E9F961CEA08B3 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Clovis | CA | 93612-1220 |  | 2013-06-17 | 2013-06-17 12:04 | 2013-06-17 12:24 | CARRIER - N/A | 120 | 10.2 | Yes | Yes | 18.7 | 18.3 | 0.4 | DBA07E4A3C0D4B518DCC54CD6B4B0079 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Los Banos | CA | 93635-3014 |  | 2013-07-08 | 2013-07-08 10:07 | 2013-07-08 10:09 | BDP - HE0360DAOA | 129 | 16.8 | Yes | Yes | 20.5 | 19.3 | 1.2 | E6184768942F4AB580438CF9070874E1 |  | R22 | Non-TXV |  | 13.02% | 0.86977 | 25.03% | [5 empty] | Non-TXV | 13.02%
Clovis | CA | 93612-5033 |  | 2013-06-19 | 2013-06-19 12:36 | 2013-06-19 12:52 | ICP - PGC030K060D | 71 | 3.3 | Yes | Yes | 18.5 | 20.3 | -1.8 | 565E9D0E5B3E482C8579A89D04F55254 |  | R22 | Non-TXV |  | 4.648% | 0.95352 | 8.932% | [5 empty] | Non-TXV | 4.648%
Lincoln | CA | 95648-8653 |  | 2013-05-31 | 2013-05-31 14:50 | 2013-05-31 15:21 | YORK - H2RA030S06D | 62 | 1.9 | Yes | Yes | 27 | 21.9 | 5.1 | 206DA953F2F443F584476E555E018F93 |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Madera | CA | 93638-1523 |  | 2013-06-12 | 2013-06-12 13:29 | 2013-06-12 13:29 | RHEEM - RRNA-B030JK06X | 74 | 0 | Yes | Yes | 19.4 | 19.8 | -0.4 | ABB0AF9CC3BD476A9E59B716BAAED6A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-1918 |  | 2013-07-23 | 2013-07-23 09:43 | 2013-07-23 10:09 | HEIL - CBD | 54 | 2.1 | Yes | Yes | 18.6 | 19 | -0.4 | 172466ACF37C49AF8BA4B5910E2EC41E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Los Banos | CA | 93635-3030 |  | 2013-10-17 | 2013-10-17 08:51 | 2013-10-17 08:57 | RUUD - 7777UNK | 80 | 3.4 | Yes | Yes | 20.1 | 19.1 | 1.1 | 75064EF9EDDB44B4B3D8E802DB484440 |  | R22 | Non-TXV |  | 4.25% | 0.9575 | 8.168% | [5 empty] | Non-TXV | 4.25%
Los Banos | CA | 93635-5440 |  | 2013-07-09 | 2013-07-09 15:01 | 2013-07-09 15:11 | BDP - 561AJ036 | 70 | 15.8 | Yes | Yes | 27 | 24.8 | 2.2 | 96F6E3FE1EDE474D8F7EA991497CE06B |  | R22 | TXV |  | 22.57% | 0.77429 | 43.38% | [5 empty] | TXV | 22.57%
Stockton | CA | 95203-3178 |  | 2013-05-28 | 2013-05-28 14:22 | 2013-05-28 14:43 | BDP - 585GJW024040ASAE | 54 | 3.7 | Yes | Yes | 17.8 | 17.4 | 0.4 | 376C2FB620EE42A9919D56D3C30D3658 |  | R22 | Non-TXV |  | 6.852% | 0.93148 | 13.17% | [5 empty] | Non-TXV | 6.852%
Atwater | CA | 95301-4148 |  | 2013-06-06 | 2013-06-06 09:19 | 2013-06-06 09:24 | OTHER - 542GN030 | 128 | 11.8 | Yes | Yes | 18.4 | 18.7 | -0.3 | 1D86055CACD4499C8E0F576E4598D246 |  | R22 | Non-TXV |  | 9.219% | 0.90781 | 17.72% | [5 empty] | Non-TXV | 9.219%
Fresno | CA | 93703-3310 |  | 2013-06-03 | 2013-06-03 14:12 | 2013-06-03 15:07 | GOODMAN - PGJ04075-12 | 93 | 3.7 | Yes | Yes | 18.2 | 20.7 | -2.5 | 0AF2F1847FA64E5B97FEAB40428ACB69 |  | R22 | Non-TXV |  | 3.978% | 0.96022 | 7.646% | [5 empty] | Non-TXV | 3.978%
Stockton | CA | 95206-4680 |  | 2013-06-18 | 2013-06-18 09:55 | 2013-06-18 10:17 | BRYANT - 563CNX036-A | 122 | -8.6 | Yes | Yes | 21.5 | 20.2 | 1.3 | 18A20684B9FC45E3B46DBEAAA8BDD3E2 |  | R22 | Non-TXV |  | -7.049% | 1.0705 | 1.974% |  |  |  |  | Non-TXV |  |  | -7.049%
Fresno | CA | 93727-2613 |  | 2013-06-10 | 2013-06-10 14:59 | 2013-06-10 15:15 | OTHER - CA3036VKA1 | 94 | 2.9 | Yes | Yes | 15 | 14.7 | 0.4 | B279875885CA487E82AD0D2A1430FAA7 |  | R22 | Non-TXV |  | 3.085% | 0.96915 | 5.929% | [5 empty] | Non-TXV | 3.085%
Fresno | CA | 93727-2449 |  | 2013-06-10 | 2013-06-10 14:08 | 2013-06-10 15:10 | TRANE - TTB048C100A0 | 115 | 3.7 | Yes | Yes | 17.8 | 20.2 | -2.4 | 3B5930C8D0CD4909B7859E179B98D0FD |  | R22 | Non-TXV |  | 3.217% | 0.96783 | 6.183% | [5 empty] | Non-TXV | 3.217%
Woodbridge | CA | 95258-9500 |  | 2013-10-01 | 2013-10-01 11:58 | 2013-10-01 13:04 | GOODMAN - CK36-1A | 73 | 5.7 | Yes | Yes | 25.5 | 19.9 | 5.6 | 91C811B83AD249ADB540BDCE40EB29E3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.808% | 0.92192 | 15.01% | [5 empty] | Non-TXV | 7.808%
Stockton | CA | 95209-4242 |  | 2013-05-24 | 2013-05-24 12:35 | 2013-05-24 12:35 | YORK - H2RC036S06G | 83 | 0 | Yes | Yes | 18.7 | 19.8 | -1.1 | 674AEAE227DE4AADBE2A395AFAE7BC60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-7869 |  | 2013-06-03 | 2013-06-03 18:54 | 2013-06-03 19:13 | PAYNE - PA13NR036-E | 95 | 5.4 | Yes | Yes | 22.5 | 22 | 0.5 | 1405CA4AD5F34B33A60461B528AE9492 |  | R22 | Non-TXV |  | 5.684% | 0.94316 | 10.92% | [5 empty] | Non-TXV | 5.684%
Atwater | CA | 95301-2081 |  | 2013-06-05 | 2013-06-05 09:16 | 2013-06-05 09:18 | RHEEM - RRNAB036JK06X | 83 | 5.3 | Yes | Yes | 15.8 | 18.2 | -2.4 | 5BFE9EEA749D41BCB185B7AC50DE1095 |  | R22 | Non-TXV |  | 6.386% | 0.93614 | 12.27% | [5 empty] | Non-TXV | 6.386%
Stockton | CA | 95203-3137 |  | 2013-05-29 | 2013-05-29 11:50 | 2013-05-29 12:08 | LUXAIRE - UNK | 54 | 3.8 | Yes | Yes | 18.8 | 18.2 | 0.6 | 8B0EBE54586D46F7B49F7B9D9C6D53F4 |  | R22 | Non-TXV |  | 7.037% | 0.92963 | 13.52% | [5 empty] | Non-TXV | 7.037%
Fresno | CA | 93720-1453 |  | 2013-06-21 | 2013-06-21 08:54 | 2013-06-21 08:56 | CARRIER - UNK | 85 | 6.8 | Yes | Yes | 19.2 | 17.6 | 1.6 | 43BDC164142244088E885F8667A8D1A9 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Stockton | CA | 95203-3178 |  | 2013-05-29 | 2013-05-29 16:09 | 2013-05-29 16:26 | DAY & NIGHT - 585GJW018040ABAC | 55 | 2.9 | Yes | Yes | 16.1 | 16.4 | -0.3 | 8EB5490B10AA41D9B5A83ED435F275B9 |  | R22 | Non-TXV |  | 5.273% | 0.94727 | 10.13% | [5 empty] | Non-TXV | 5.273%
Auburn | CA | 95602-8177 |  | 2013-08-14 | 2013-08-14 12:48 | 2013-08-14 12:48 | PAYNE - 588ANW060100AEAG | 112 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 7F43648CA96A46B2B69A9478BBD37813 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8732 |  | 2013-08-21 | 2013-08-21 09:12 | 2013-08-21 09:33 | LENNOX - 13ACD-048-230-01 | 204 | 7.4 | Yes | Yes | 17 | 19 | -2 | 0D12C449B43041D685CFE1E2307CED42 |  | R22 | TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | TXV | 3.627%
Stockton | CA | 95203-3179 |  | 2013-05-29 | 2013-05-29 16:28 | 2013-05-29 16:28 | DAY & NIGHT - 585GJW024040ABAC | 54 | 0 | Yes | Yes | 19.8 | 20.2 | -0.4 | 52161DE3B54940229C3E4515459EDDF0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6445 |  | 2013-06-13 | 2013-06-13 08:49 | 2013-06-13 08:49 | MONTGOMERY WARD - SRM-518350 | 49 | 0 | Yes | Yes | 23.1 | 19.9 | 3.2 | 489C17ACEE154EADA70CFB6B270387E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4019 |  | 2013-05-31 | 2013-05-31 14:51 | 2013-05-31 15:10 | YORK - D1NY036N05606A | 120 | 5.4 | Yes | Yes | 21.1 | 21.5 | -0.4 | 142C0DBB7258484A9DB5C063AC360E89 |  | R410A | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Stockton | CA | 95205-7063 |  | 2013-06-05 | 2013-06-05 09:30 | 2013-06-05 09:56 | PAYNE - PA10JA936-C | 73 | 4.7 | Yes | Yes | 18.4 | 18.8 | -0.4 | ABC25C0B99704F069949BB21E0B535B3 |  | R22 | TXV |  | 6.438% | 0.93562 | 12.37% | [5 empty] | TXV | 6.438%
Auburn | CA | 95602-8403 |  | 2013-08-13 | 2013-08-13 18:23 | 2013-08-13 18:23 | GE - BTB912A800A0 | 36 | 0 | Yes | Yes | 18.9 | 21 | -2.1 | 3717907885B84314B67D97CF2C594245 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6335 |  | 2013-07-03 | 2013-07-03 12:08 | 2013-07-03 12:24 | YORK - H2RC042S06A | 107 | -6.3 | Yes | Yes | 16 | 12.8 | 3.2 | 2D2818EDD19142D2A3D815C1FF152645 |  | R22 | Non-TXV |  | -5.888% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.888%
Clovis | CA | 93611-2060 |  | 2013-07-01 | 2013-07-01 15:46 | 2013-07-01 16:22 | LENNOX - HS14-511V-7P | 177 | 12.1 | Yes | Yes | 22 | 16.9 | 5.1 | 0BCC37B34E394EBA8F52D4B27CD457E4 |  | R22 | Non-TXV |  | 6.836% | 0.93164 | 13.14% | [5 empty] | Non-TXV | 6.836%
Dinuba | CA | 93618-3245 |  | 2013-07-26 | 2013-07-26 15:38 | 2013-07-26 17:07 | GOODMAN - GPG13240451AA | 77 | 2.8 | Yes | Yes | 20.5 | 20 | 0.5 | 0E969C02715345DB8FA6C9C103ED0274 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Stockton | CA | 95207-4008 |  | 2013-06-01 | 2013-06-01 08:42 | 2013-06-01 09:03 | TRANE - TTX030D100AQ | 85 | 8.8 | Yes | Yes | 19.3 | 18.3 | 1 | A8E868F65EB446D694DB5079B403EC0A |  | R22 | Non-TXV |  | 10.35% | 0.89647 | 19.9% | [5 empty] | Non-TXV | 10.35%
Orland | CA | 95963-9470 |  | 2013-06-17 | 2013-06-17 16:09 | 2013-06-17 16:09 | GUARDIAN - GHD3621S1A | 145 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | 8428AFB36CF24A71BEA0FCEABEE10028 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-1801 |  | 2013-06-03 | 2013-06-03 15:06 | 2013-06-03 15:40 | AMERICAN STANDARD - YCP030F1M0AB | 106 | 12.8 | Yes | Yes | 21 | 19.9 | 1.1 | 622370E34B3F4D388C4586E0E3266F44 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.08% | 0.87925 | 23.21% | [5 empty] | Non-TXV | 12.08%
Paradise | CA | 95969-3031 |  | 2013-08-08 | 2013-08-08 16:00 | 2013-08-08 19:20 | BRYANT - 582ANW024060AAAD | 53 | -3.7 | Yes | Yes | 22.4 | 20.4 | 2 | 449E75CDBC994906B210DAECDBE8A433 |  | R22 | Non-TXV |  | -6.981% | 1.0698 | 1.955% |  |  |  |  | Non-TXV |  |  | -6.981%
Chico | CA | 95928-4170 |  | 2013-06-06 | 2013-06-06 17:15 | 2013-06-06 17:15 | TRANE - YCCO36F1H0AA | 89 | 0 | Yes | Yes | 22.1 | 20.4 | 1.7 | 1CB8873093B4481A8CF80933C073CA80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3298 |  | 2013-05-30 | 2013-05-30 12:58 | 2013-05-30 13:02 | BDP - 561AJ036B | 72 | 8.9 | Yes | Yes | 19.1 | 20.4 | -1.3 | BDA07C83BBF7482DA66B3920506E7382 |  | R22 | Non-TXV |  | 12.36% | 0.87639 | 23.76% | [5 empty] | Non-TXV | 12.36%
Mariposa | CA | 95338-9601 |  | 2013-07-31 | 2013-07-31 13:45 | 2013-07-31 13:47 | RHEEM - RQKA-A048JK | 141 | 4.4 | Yes | Yes | 24.4 | 20.5 | 4 | EA82207A4F9D4EB887360B053838A3B2 |  | R22 | Non-TXV |  | 3.121% | 0.96879 | 5.997% | [5 empty] | Non-TXV | 3.121%
Stockton | CA | 95212-3830 |  | 2013-06-18 | 2013-06-18 10:18 | 2013-06-18 10:39 | YORK - H2RC030S06A | 88 | 2.7 | Yes | Yes | 19.1 | 20.2 | -1.1 | D34FABBDFD3246C2BDEE7E8581513E62 |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Winton | CA | 95388-9377 |  | 2013-06-14 | 2013-06-14 12:07 | 2013-06-14 12:08 | ARMSTRONG - PGE10B36D075LA | 58 | 8.3 | Yes | Yes | 23.1 | 18.7 | 4.4 | EE40BB8CA299415EB981964E2F155AED |  | R22 | Non-TXV |  | 14.31% | 0.8569 | 27.5% | [5 empty] | Non-TXV | 14.31%
Fresno | CA | 93726-6739 |  | 2013-06-07 | 2013-06-07 13:01 | 2013-06-07 13:09 | BRYANT - 574DNWA4206NA | 97 | 3 | Yes | Yes | 18.4 | 17.5 | 0.9 | C3A383626B5643DFA91002F0ED643402 |  | R410A | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Stockton | CA | 95207-1154 |  | 2013-05-28 | 2013-05-28 12:02 | 2013-05-28 12:19 | RHEEM - RRNA-B024JK06X | 85 | 3.1 | Yes | Yes | 21.7 | 18.7 | 3 | 371111A49FF343F982ACC0B6A4ADA856 |  | R22 | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Stockton | CA | 95203-1845 |  | 2013-05-28 | 2013-05-28 12:31 | 2013-05-28 12:59 | RHEEM - RAKA-024JAZ | 50 | 4.3 | Yes | Yes | 17.4 | 19.3 | -1.9 | EFE264B0D3E24B23B0A5B5B04FD611E2 |  | R22 | Non-TXV |  | 8.6% | 0.914 | 16.53% | [5 empty] | Non-TXV | 8.6%
Clovis | CA | 93612-4941 |  | 2013-07-02 | 2013-07-02 17:42 | 2013-07-02 17:59 | DAY & NIGHT - N/A | 90 | 5.1 | Yes | Yes | 20.7 | 20.7 | 0 | 8508C490C2B143C99A966C93B132BF7E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Stockton | CA | 95210-4249 |  | 2013-07-09 | 2013-07-09 12:42 | 2013-07-09 13:02 | CARRIER - 38TH030310 | 68 | -4 | Yes | Yes | 23.9 | 20.6 | 3.3 | 7E30BC53B8EC4955BA4ED0AE8A593D73 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95203-3139 |  | 2013-05-24 | 2013-05-24 15:12 | 2013-05-24 15:29 | LUXAIRE - UNK | 54 | 2.8 | Yes | Yes | 17.4 | 19.8 | -2.4 | A6AF74D33A0E4FA3B804FE614E0E87AA |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Stockton | CA | 95207-1154 |  | 2013-05-29 | 2013-05-29 14:30 | 2013-05-29 14:48 | RHEEM - RRNA-BO24JKO6X | 70 | 3.8 | Yes | Yes | 22.1 | 19.7 | 2.4 | 105E024E564F4439934EEF21886783CD |  | R22 | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Los Banos | CA | 93635-3042 |  | 2013-07-09 | 2013-07-09 09:08 | 2013-07-09 09:12 | OTHER - BOWR36A1NB | 60 | 8.6 | Yes | Yes | 18.7 | 17.5 | 1.2 | 7143E12A2B9B49698269B2242D24A854 |  | R22 | Non-TXV |  | 14.33% | 0.85667 | 27.55% | [5 empty] | Non-TXV | 14.33%
Fresno | CA | 93710-6410 |  | 2013-06-03 | 2013-06-03 11:58 | 2013-06-03 12:21 | CARRIER - 38TRA042310 | 130 | 4.2 | Yes | Yes | 19.6 | 20.8 | -1.2 | AA9F129F01B94B2E8D4354AAFAEB1A9F |  | R22 | Non-TXV |  | 3.231% | 0.96769 | 6.209% | [5 empty] | Non-TXV | 3.231%
Chico | CA | 95928-6186 |  | 2013-07-08 | 2013-07-08 21:08 | 2013-07-08 21:27 | TRANE - YCYO30G1M0AD | 124 | 5.4 | Yes | Yes | 25.5 | 22.5 | 3 | 1A722D17C1A44A26B7A4E8E352A51239 |  | R22 | Non-TXV |  | 4.355% | 0.95645 | 8.369% | [5 empty] | Non-TXV | 4.355%
Stockton | CA | 95212-3107 |  | 2013-06-25 | 2013-06-25 10:47 | 2013-06-25 11:09 | YORK - AC060X1221A | 147 | -6.1 | Yes | Yes | 24.2 | 18.2 | 6 | 56683206D45749608498FCE189821BA0 |  | R22 | TXV |  | -4.15% | 1.0415 | 1.162% |  |  |  |  | TXV |  |  | -4.15%
Paradise | CA | 95969-3557 |  | 2013-06-13 | 2013-06-13 17:20 | 2013-06-13 17:41 | YORK - D1NACM2N07206C | 76 | 4.4 | Yes | Yes | 24.6 | 21.5 | 3.1 | D7299068B6D446498E7DA95DA995B7E7 |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Clovis | CA | 93611-5140 |  | 2013-06-27 | 2013-06-27 09:39 | 2013-06-27 10:12 | OTHER - 80WR36G1NA | 120 | 3.6 | Yes | Yes | 19.2 | 21.4 | -2.2 | 7A87B0DBB9CF4AEE953CC8DA75DE9D4A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93611-7349 |  | 2013-08-29 | 2013-08-29 11:11 | 2013-08-29 11:20 | CARRIER - 563ANO36-A | 122 | 3.7 | Yes | Yes | 17.5 | 20.4 | -2.9 | 888A3DC9380749F6854340BA625FABA3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.033% | 0.96967 | 5.828% | [5 empty] | Non-TXV | 3.033%
Madera | CA | 93637-2642 |  | 2013-06-14 | 2013-06-14 15:21 | 2013-06-14 15:43 | RHEEM - RRNA-B036JK6X | 85 | 4.8 | Yes | Yes | 19 | 21 | -2 | A222848D8C854C568ABA1B3C87B55B53 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Chico | CA | 95926-1928 |  | 2013-06-06 | 2013-06-06 16:47 | 2013-06-06 17:04 | TEMPSTAR - TCA024AKA1 | 69 | 4.8 | Yes | Yes | 21.7 | 20.4 | 1.3 | 76D5BC6FFB924ADF9BF93E86B2C3C824 |  | R22 | Non-TXV |  | 6.957% | 0.93043 | 13.37% | [5 empty] | Non-TXV | 6.957%
Stockton | CA | 95203-2901 |  | 2013-05-28 | 2013-05-28 13:27 | 2013-05-28 13:55 | WEATHER KING - 10AJA3601 | 80 | 5.7 | Yes | Yes | 16.4 | 16.6 | -0.2 | F920802A36144855B8C890443B4E86DB |  | R22 | Non-TXV |  | 7.125% | 0.92875 | 13.69% | [5 empty] | Non-TXV | 7.125%
Rocklin | CA | 95677-4774 |  | 2013-07-27 | 2013-07-27 10:46 | 2013-07-27 11:21 | OTHER - AA1BJX024-A | 70 | -5.8 | Yes | Yes | 17 | 19.8 | -2.8 | 04E7961A66104EA3B894AA6D886811D8 |  | R22 | TXV |  | -8.286% | 1.0829 | 2.32% |  |  |  |  | TXV |  |  | -8.286%
Stockton | CA | 95207-6504 |  | 2013-06-03 | 2013-06-03 14:12 | 2013-06-03 14:12 | AMANA - PCE36C2A | 120 | 0 | Yes | Yes | 25.6 | 22.1 | 3.6 | 39CC001CE4F7406C8ED18920BD45BCBD |  | R22 | Non-TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-4107 |  | 2013-07-08 | 2013-07-08 09:15 | 2013-07-08 09:15 | CARRIER - 50YQ036310 | 93 | 0 | Yes | Yes | 21 | 21.5 | -0.5 | 2F425B48F47D4039912718E471249C15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-6303 |  | 2013-06-19 | 2013-06-19 13:43 | 2013-06-19 13:43 | YORK - H2RA060S06D | 118 | 0 | Yes | Yes | 20.3 | 20.6 | -0.3 | E82D8DD8792C4BC9AB83959F826B8C40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-0318 |  | 2013-06-12 | 2013-06-12 12:06 | 2013-06-12 16:30 | BDP - 5856JM03060ABAF | 80 | -4.7 | Yes | Yes | 19.1 | 19.8 | -0.7 | 91CB7ED0ED654DA3913098BD1A83B615 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Marysville | CA | 95901-9727 |  | 2013-06-03 | 2013-06-03 16:06 | 2013-06-03 16:26 | GOODMAN - GPG13300761AB | 77 | -6.3 | Yes | Yes | 16 | 18.5 | -2.5 | 937D6885715D44A6AFB38624FD7CE566 |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Marysville | CA | 95901-9727 |  | 2013-06-03 | 2013-06-03 16:29 | 2013-06-03 16:51 | GOODMAN - GPG13240451BA | 77 | 2.3 | Yes | Yes | 20 | 18.5 | 1.5 | EE02F0CDD3524332B56DC37497DB10C2 |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Chico | CA | 95926-2037 |  | 2013-07-12 | 2013-07-12 19:37 | 2013-07-12 19:37 | PAYNE - PY3GNAAA42090NA | 97 | 0 | Yes | Yes | 19.1 | 18.3 | 0.9 | ED9C873D9CDF4335ABCCFA60C99DC7F5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-3136 |  | 2013-05-24 | 2013-05-24 14:43 | 2013-05-24 15:00 | LUXAIRE - UNK | 54 | 5.5 | Yes | Yes | 18.1 | 19.4 | -1.3 | DA0E351720E541E58CC474B3F55ED908 |  | R22 | Non-TXV |  | 10.19% | 0.89815 | 19.57% | [5 empty] | Non-TXV | 10.19%
Stockton | CA | 95207-6536 |  | 2013-06-04 | 2013-06-04 15:05 | 2013-06-04 15:05 | RHEEM - RRNL-B042JK08X | 112 | 0 | Yes | Yes | 22.7 | 19.6 | 3.1 | 5D568EFEFF584C9E91214A28D3F4C6CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-9286 |  | 2013-06-25 | 2013-06-25 14:40 | 2013-06-25 14:51 | LENNOX - 13ACD-036-230-03 | 111 | 8.2 | Yes | Yes | 20 | 18.4 | 1.6 | 42C500033FB24B75A3DFB912DDF38DFB |  | R22 | Non-TXV |  | 7.387% | 0.92613 | 14.2% | [5 empty] | Non-TXV | 7.387%
Clovis | CA | 93619-9286 |  | 2013-06-25 | 2013-06-25 14:54 | 2013-06-25 15:19 | LENNOX - 13ACD-030-230-03 | 95 | 4.4 | Yes | Yes | 20.8 | 20.1 | 0.7 | 4319DCBE104D40EC875D00A6BF9D06F0 |  | R22 | Non-TXV |  | 4.632% | 0.95368 | 8.901% | [5 empty] | Non-TXV | 4.632%
Loomis | CA | 95650-7616 |  | 2013-09-09 | 2013-09-09 20:16 | 2013-09-09 20:37 | CARRIER - 38TXA048330 | 159 | 16.5 | Yes | Yes | 21.8 | 21.9 | -0.1 | 1BFE56B1EA2C4FF0A782C978698E30B3 |  | R410A | TXV |  | 10.38% | 0.89623 | 19.94% | [5 empty] | TXV | 10.38%
Live Oak | CA | 95953-9432 |  | 2013-08-05 | 2013-08-05 13:18 | 2013-08-05 13:35 | CARRIER - 38CKC060370 | 135 | -8.1 | Yes | Yes | 17 | 19.9 | -2.9 | 7BEF55707ACB4E479499DF0EBA97EA2B |  | R22 | TXV |  | -6% | 1.06 | 1.68% |  |  |  |  | TXV |  |  | -6%
Olivehurst | CA | 95961-0000 |  | 2013-08-30 | 2013-08-30 15:44 | 2013-09-03 00:36 | BDP - 565BJ042 | 82 | 7 | Yes | Yes | 22.8 | 19.6 | 3.3 | B3EDAD52CB1B472F943AA7E193E116EE |  | R22 | Non-TXV |  | 8.537% | 0.91463 | 16.41% | [5 empty] | Non-TXV | 8.537%
Stockton | CA | 95206-3889 |  | 2013-07-08 | 2013-07-08 11:00 | 2013-07-08 11:00 | CARRIER - 38EZG02430 | 80 | 0 | Yes | Yes | 19.8 | 19.9 | -0.1 | D09913C3263046A08B34514B31162D56 |  | R410A | TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1797 |  | 2013-06-13 | 2013-06-13 14:06 | 2013-06-13 14:06 | BRYANT - 574BNW03040NG | 97 | 0 | Yes | Yes | 18.7 | 20.7 | -2 | 4CF91E318096423697AF13B8AA8D36C5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3638 |  | 2013-07-19 | 2013-07-19 12:03 | 2013-07-19 12:24 | LENNOX - 10GCS036X-75-3PA | 58 | 5.8 | Yes | Yes | 19.7 | 19.5 | 0.2 | 160795E8881E48CF9653EF1E50BB5CA8 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95205-7870 |  | 2013-06-05 | 2013-06-05 11:47 | 2013-06-05 12:03 | HEIL - UNK | 54 | 4.4 | Yes | Yes | 18.3 | 18.8 | -0.5 | 0FBF845E2D5B4E95A524095BC346E853 |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Livingston | CA | 95334-9557 |  | 2013-06-10 | 2013-06-10 14:35 | 2013-06-10 15:03 | RHEEM - RRNL-B030JK06X | 77 | 2.5 | Yes | Yes | 20 | 19.7 | 0.3 | 8440090245A542838477C38BA08ED7B0 |  | R410A | Non-TXV |  | 3.247% | 0.96753 | 6.24% | [5 empty] | Non-TXV | 3.247%
Stockton | CA | 95205-7798 |  | 2013-06-05 | 2013-06-05 10:04 | 2013-06-05 10:04 | CARRIER - 38TH024300 | 53 | 0 | Yes | Yes | 25 | 20.1 | 5 | 0A29B76B9D6C4A519DEBBA1BC9EB6EF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-6354 |  | 2013-06-01 | 2013-06-01 12:23 | 2013-06-01 12:28 | BRYANT - 561CJ036 | 70 | 12.6 | Yes | Yes | 25 | 21.4 | 3.6 | C6C83D9CE4D24B5382F71FFBB676D0F9 |  | R22 | TXV |  | 18% | 0.82 | 34.59% | [5 empty] | TXV | 18%
Stockton | CA | 95205-7850 |  | 2013-07-10 | 2013-07-10 09:18 | 2013-07-10 10:08 | HEIL - NRGF36DBB02 | 85 | 3.4 | Yes | Yes | 22.9 | 21 | 1.9 | 11C166EBA8D9451AB5B06D1CC5C16F0E |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Rocklin | CA | 95765-4776 |  | 2013-06-17 | 2013-06-17 10:17 | 2013-06-17 10:52 | YORK - H1RA042D06D | 84 | -7.9 | Yes | Yes | 16 | 18.8 | -2.8 | 879A2412CE594223B2C7981CAED2B7B5 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Diamond Springs | CA | 95619-9321 |  | 2013-07-05 | 2013-07-05 11:33 | 2013-07-05 11:55 | TRANE - DPHH0361BA | 117 | 3.6 | Yes | Yes | 24 | 19.9 | 4.1 | CB61B31343194A29BB15A349A984096A |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Lincoln | CA | 95648-2827 |  | 2013-07-06 | 2013-07-06 09:33 | 2013-07-06 09:53 | YORK - AC036X1221A | 98 | 3.7 | Yes | Yes | 20.5 | 19.9 | 0.6 | 4FB3C807EBE1448E854E7B1FAB48B469 |  | R22 | TXV |  | 3.776% | 0.96224 | 7.256% | [5 empty] | TXV | 3.776%
El Dorado Hills | CA | 95762-3725 |  | 2013-06-20 | 2013-06-20 15:47 | 2013-06-20 15:47 | LENNOX - YCY048F1H0AA | 178 | 0 | Yes | Yes | 26.9 | 21.2 | 5.7 | E4ABAA3D8A6348DCA5FB6005E3984210 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-3908 |  | 2013-06-21 | 2013-06-21 16:04 | 2013-06-22 04:29 | AMANA - RCC48A2E | 132 | 5.4 | Yes | Yes | 17.9 | 20.5 | -2.6 | E0B863E814C1477897B7D6EE034CDE0A |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Cameron Park | CA | 95682-9164 |  | 2013-06-13 | 2013-06-13 09:05 | 2013-06-13 09:05 | PAYNE - PH13NR030-F | 102 | 0 | Yes | Yes | 20.4 | 20.1 | 0.3 | D692E61536794E93A407CA48D020F01F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4612 |  | 2013-07-10 | 2013-07-10 12:33 | 2013-07-10 12:50 | CARRIER - 38EB024300 | 53 | 1.6 | Yes | Yes | 27 | 22.4 | 4.7 | B14D17D1E27247E29014E52E69002968 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
El Dorado Hills | CA | 95762-6903 |  | 2013-10-01 | 2013-10-01 14:17 | 2013-10-01 14:17 | OTHER - UNK | 86 | 0 | Yes | Yes | 17.5 | 19.8 | -2.3 | 4A1325C97E3C4EF08CC4EBF800589303 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-9780 |  | 2013-06-13 | 2013-06-13 14:51 | 2013-06-13 14:55 | INTERTHERM - ACC048BAYAA | 76 | 14.4 | Yes | Yes | 23.9 | 20.4 | 3.5 | 03C2085582744979844F7A7CB95A3FDA |  | R22 | Non-TXV |  | 18.95% | 0.81053 | 36.41% | [5 empty] | Non-TXV | 18.95%
Riverbank | CA | 95367-3010 |  | 2013-06-03 | 2013-06-03 13:09 | 2013-06-03 13:32 | GOODMAN - GSC130481BA | 102 | 8.4 | Yes | Yes | 20.1 | 20.4 | -0.3 | 590792D535F04D2E9EBBED814A40ED1E |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Somerset | CA | 95684-9347 |  | 2013-08-12 | 2013-08-12 15:40 | 2013-08-12 16:08 | DAY & NIGHT - UNK | 86 | 19.6 | Yes | Yes | 26.1 | 21.7 | 4.4 | 4714CFA1B2C540A2940001712FC530A0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.79% | 0.77209 | 43.8% | [5 empty] | Non-TXV | 22.79%
Stockton | CA | 95206-6256 |  | 2013-06-20 | 2013-06-20 13:29 | 2013-06-20 13:48 | GOODMAN - CKJ36-1AB | 97 | -9.1 | Yes | Yes | 22 | 18.8 | 3.2 | 8ED411CD7EFD4CA3898FE1BE4921BD73 |  | R22 | Non-TXV |  | -9.381% | 1.0938 | 2.627% |  |  |  |  | Non-TXV |  |  | -9.381%
Stockton | CA | 95206-5211 |  | 2013-09-13 | 2013-09-13 14:43 | 2013-09-13 15:14 | GOODMAN - CK30-1B | 76 | 5 | Yes | Yes | 24.1 | 22.1 | 2 | A94C95DFDBA446829DE302BA67BBB40E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Stockton | CA | 95210-1262 |  | 2013-06-06 | 2013-06-06 11:34 | 2013-06-06 11:50 | TRANE - TTX030C100A3 | 120 | 4.6 | Yes | Yes | 20.2 | 19.3 | 0.9 | 48D1206982AE403B8D83768EEDEC03AC |  | R22 | Non-TXV |  | 3.833% | 0.96167 | 7.367% | [5 empty] | Non-TXV | 3.833%
Ripon | CA | 95366-3201 |  | 2013-05-31 | 2013-05-31 15:54 | 2013-05-31 16:22 | DAY & NIGHT - UNK | 62 | 4.2 | Yes | Yes | 17.7 | 19.9 | -2.2 | 497A4B54E72B4186BE712AA75398D5A2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.774% | 0.93226 | 13.02% | [5 empty] | Non-TXV | 6.774%
Stockton | CA | 95206-6223 |  | 2013-06-19 | 2013-06-19 10:15 | 2013-06-19 10:32 | CARRIER - 561CJX036000ACAA | 72 | -6.2 | Yes | Yes | 22.1 | 18.3 | 3.8 | 7369EA47809745429059F7660CD48101 |  | R22 | TXV |  | -8.611% | 1.0861 | 2.412% |  |  |  |  | TXV |  |  | -8.611%
Tracy | CA | 95376-4478 |  | 2013-05-29 | 2013-05-29 11:13 | 2013-05-29 11:56 | RUUD - UARL-048JAZ | 85 | 4.6 | Yes | Yes | 25.2 | 19.3 | 5.9 | 020FCB65CB7249C7BE74E2F506DADCC6 |  | R410A | TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | TXV | 5.412%
Fresno | CA | 93727-3317 |  | 2013-07-15 | 2013-07-15 11:13 | 2013-07-15 11:55 | YORK - D1NA036N0560C | 67 | 2.3 | Yes | Yes | 21 | 20.2 | 0.9 | 3F54BDB897BE4F33BFFA22170C9D24C0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.433% | 0.96567 | 6.597% | [5 empty] | Non-TXV | 3.433%
Fresno | CA | 93727-3317 |  | 2013-07-15 | 2013-07-15 11:58 | 2013-07-15 12:34 | GOODMAN - GPG0 | 120 | 4.5 | Yes | Yes | 17.2 | 19.5 | -2.3 | 2765D875AE324E859D0D25C8AD184BB9 | OK: Verified Refrigerant Charge Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Placerville | CA | 95667-5325 |  | 2013-05-29 | 2013-05-29 12:49 | 2013-05-29 12:49 | OTHER - UNK | 107 | 0 | Yes | Yes | 25.2 | 20.2 | 5.1 | 939B99CCB6F9449FBB091ADE0739DFAB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-6503 |  | 2013-07-30 | 2013-07-30 10:31 | 2013-07-30 10:32 | YORK - AC042X1021A | 84 | 11.1 | Yes | Yes | 19.5 | 18.1 | 1.4 | 2E6E72232FC04C1E9300B7F0DED03812 |  | R22 | Non-TXV |  | 13.21% | 0.86786 | 25.39% | [5 empty] | Non-TXV | 13.21%
Stockton | CA | 95219-3152 |  | 2013-06-20 | 2013-06-20 09:08 | 2013-06-20 09:27 | RUUD - 13AJA24A01757 | 64 | 6.1 | Yes | Yes | 21.4 | 19.1 | 2.3 | 0EC03630D928483B88FA5DB554701303 |  | R22 | Non-TXV |  | 9.531% | 0.90469 | 18.32% | [5 empty] | Non-TXV | 9.531%
Fresno | CA | 93726-3507 |  | 2013-06-05 | 2013-06-05 16:37 | 2013-06-05 16:59 | RHEEM - RRNL-B024J06X | 77 | 7.9 | Yes | Yes | 18.7 | 19.9 | -1.2 | 03A819929C434FE29B46E1820B68422F |  | R410A | Non-TXV |  | 10.26% | 0.8974 | 19.72% | [5 empty] | Non-TXV | 10.26%
Lincoln | CA | 95648-3220 |  | 2013-05-30 | 2013-05-30 12:38 | 2013-05-30 12:38 | LENNOX - 13ACD-036-230-01 | 111 | 0 | Yes | Yes | 17 | 19.2 | -2.2 | BC1979EB14EF4DD08AD935D4BFA51908 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-9449 |  | 2013-06-06 | 2013-06-06 15:03 | 2013-06-06 15:03 | LENNOX - 10ACC-048-230-04 | 96 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | EE9D2740D1C44CB4A8CD50DE34366738 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2327 |  | 2013-05-28 | 2013-05-28 12:49 | 2013-05-28 13:13 | PAYNE - PY1PNB036090ABAA | 68 | 5.7 | Yes | Yes | 20.4 | 18.2 | 2.2 | 02F86EA7DB17437B8A1EE318B0EA2951 |  | R22 | TXV |  | 8.382% | 0.91618 | 16.11% | [5 empty] | TXV | 8.382%
Chico | CA | 95928-9401 |  | 2013-06-11 | 2013-06-11 11:33 | 2013-06-11 11:51 | COLEMAN - BRCS030430 | 62 | 4.1 | Yes | Yes | 22.5 | 18.4 | 4.1 | AC9CC4721FAF4D6E8B8C6DFA6825DD79 |  | R22 | Non-TXV |  | 6.613% | 0.93387 | 12.71% | [5 empty] | Non-TXV | 6.613%
Clovis | CA | 93612-4941 |  | 2013-06-19 | 2013-06-19 10:25 | 2013-06-19 10:47 | GOODMAN - GPG12300701A | 73 | 6.3 | Yes | Yes | 20.9 | 20.3 | 0.6 | 33025BECD4D14193826D2C0618E1B624 |  | R22 | Non-TXV |  | 8.63% | 0.9137 | 16.59% | [5 empty] | Non-TXV | 8.63%
Stockton | CA | 95207-3147 |  | 2013-05-31 | 2013-05-31 10:52 | 2013-05-31 11:19 | AMERICAN STANDARD - 4YCC3024B1064AA | 93 | 8.1 | Yes | Yes | 24.1 | 20.1 | 4 | 38EA570D72954ACE8843CB3EDAECD61A |  | R22 | Non-TXV |  | 8.71% | 0.9129 | 16.74% | [5 empty] | Non-TXV | 8.71%
Stockton | CA | 95210-4486 |  | 2013-06-07 | 2013-06-07 10:13 | 2013-06-07 10:26 | DAY & NIGHT - 561AJ048-C | 110 | -6.5 | Yes | Yes | 16.4 | 19.3 | -2.9 | 23162CDE04E94774A7E0F1E5FF9F47D8 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Red Bluff | CA | 96080-3669 |  | 2013-05-29 | 2013-05-29 14:20 | 2013-05-29 16:19 | YORK - H1RA024S06D | 59 | 0 | Yes | Yes | 23.8 | 19.9 | 4 | 55B845D60C0342AC9D81B739F34A3689 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-6852 |  | 2013-06-07 | 2013-06-07 10:10 | 2013-06-07 10:38 | TRANE - CA5548VKD1 | 134 | -7.7 | Yes | Yes | 16 | 18.2 | -2.2 | 8F242C7F688B48BBB2D32C40C2210531 |  | R22 | Non-TXV |  | -5.746% | 1.0575 | 1.609% |  |  |  |  | Non-TXV |  |  | -5.746%
Riverbank | CA | 95367-3307 |  | 2013-07-22 | 2013-07-22 12:28 | 2013-07-22 12:45 | RHEEM - RAPC-060JAZ | 85 | 2.6 | Yes | Yes | 20.3 | 19.5 | 0.8 | 7C4663DC99B5474597C2DE647765EB70 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Stockton | CA | 95210-3113 |  | 2013-06-13 | 2013-06-13 14:42 | 2013-06-13 15:04 | DAY & NIGHT - 588ANW024060ADAD | 41 | -2.4 | Yes | Yes | 23.1 | 22.1 | 1 | C400A17F13764A52B2BB0EBF6FC57813 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Clovis | CA | 93612-4938 |  | 2013-08-16 | 2013-08-16 21:34 | 2013-08-16 21:54 | BDP - 585A018050YAC | 52 | 3 | Yes | Yes | 15.5 | 18.5 | -3 | 9D8D5ADD02A04E77B09327C746A995F2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.769% | 0.94231 | 11.09% | [5 empty] | Non-TXV | 5.769%
Stockton | CA | 95207-1205 |  | 2013-06-13 | 2013-06-13 11:38 | 2013-06-13 12:03 | TRANE - 4TTX6048B1000BA | 120 | 18.5 | Yes | Yes | 25.1 | 19.6 | 5.5 | 096B593834254672A669145E242952F1 |  | R410A | Non-TXV |  | 15.42% | 0.84583 | 29.63% | [5 empty] | Non-TXV | 15.42%
Stockton | CA | 95209-1114 |  | 2013-05-24 | 2013-05-24 15:08 | 2013-05-24 15:27 | DAY & NIGHT - 585C030 | 55 | 7.9 | Yes | Yes | 24.2 | 22 | 2.2 | B4EB792E70C044C49680A852E179C9FE |  | R22 | Non-TXV |  | 14.36% | 0.85636 | 27.6% | [5 empty] | Non-TXV | 14.36%
Rocklin | CA | 95765-4974 |  | 2013-08-29 | 2013-08-29 12:27 | 2013-08-29 12:46 | CARRIER - 38TXA060340 | 192 | 8.9 | Yes | Yes | 25.9 | 22 | 3.9 | 198E103876DB457C8AC5AC3870AF472A |  | R410A | Non-TXV |  | 4.635% | 0.95365 | 8.908% | [5 empty] | Non-TXV | 4.635%
Lincoln | CA | 95648-1571 |  | 2013-06-03 | 2013-06-03 11:56 | 2013-06-03 12:33 | AIRE-FLO - AFAIR10B30-A | 75 | 6.9 | Yes | Yes | 17.7 | 19.8 | -2.1 | D72F553D331D4E038B5A11EE116A176D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.2% | 0.908 | 17.68% | [5 empty] | Non-TXV | 9.2%
Yuba City | CA | 95993-8283 |  | 2013-06-20 | 2013-06-20 09:38 | 2013-06-20 10:01 | YORK - H2RD030S06B | 93 | 2.7 | Yes | Yes | 18 | 20.8 | -2.8 | 66336AA1D9014FF18E976F5E8D46C40F |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Merced | CA | 95340-3865 |  | 2013-06-28 | 2013-06-28 16:58 | 2013-06-28 17:06 | AMERICAN STANDARD - YCC042F1MOBH | 101 | 9.7 | Yes | Yes | 23.1 | 20.2 | 2.9 | 8F93D01710BB43D886A37C231A4CB74A |  | R22 | Non-TXV |  | 9.604% | 0.90396 | 18.46% | [5 empty] | Non-TXV | 9.604%
Stockton | CA | 95207-1338 |  | 2013-05-28 | 2013-05-28 13:46 | 2013-05-28 14:04 | HEIL - A4S530B3V1 | 80 | 11 | Yes | Yes | 19.6 | 19.9 | -0.3 | 3F00E85369D14A8FB870E231BE46CCE6 |  | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Stockton | CA | 95206-5510 |  | 2013-06-20 | 2013-06-20 10:47 | 2013-06-20 11:05 | CARRIER - 38TH042310 | 112 | 6.5 | Yes | Yes | 21.6 | 18.6 | 3 | 565581D1B1C64B0796F5B5AC0F330B8B |  | R22 | TXV |  | 5.804% | 0.94196 | 11.15% | [5 empty] | TXV | 5.804%
Stockton | CA | 95207-3227 |  | 2013-06-05 | 2013-06-05 17:00 | 2013-06-05 17:18 | PAYNE - 597AN024000AAAA | 87 | 7.2 | Yes | Yes | 17.3 | 16.8 | 0.5 | 85FCB8EA71974B48B8D796B02AEC6498 |  | R22 | Non-TXV |  | 8.276% | 0.91724 | 15.9% | [5 empty] | Non-TXV | 8.276%
Olivehurst | CA | 95961-0000 |  | 2013-08-30 | 2013-08-30 15:08 | 2013-08-30 15:30 | AMANA - PGD36C07020 | 110 | 3.6 | Yes | Yes | 23.2 | 20.1 | 3.1 | 31E19746E685477CB79AF302811AA176 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Stockton | CA | 95203-3160 |  | 2013-06-07 | 2013-06-07 09:30 | 2013-06-07 09:47 | GOODMAN - GPG1324045M41AB | 80 | 5.4 | Yes | Yes | 18.9 | 19.4 | -0.5 | 9575D6D1524143C79612E9097B0C07FF |  | R410A | Non-TXV |  | 6.75% | 0.9325 | 12.97% | [5 empty] | Non-TXV | 6.75%
Fresno | CA | 93726-5701 |  | 2013-06-10 | 2013-06-10 12:19 | 2013-06-10 12:19 | GOODMAN - CLQ42-1B | 223 | 0 | Yes | Yes | 19.4 | 20.7 | -1.3 | 5819FE817CDD483DAF0D1BB6868C1510 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-3147 |  | 2013-05-31 | 2013-05-31 10:08 | 2013-05-31 10:31 | OTHER - 55AW24-106 | 69 | 3.6 | Yes | Yes | 20.4 | 20.1 | 0.3 | E3653AA04A7D44838B7CCEA9891E8D32 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.217% | 0.94783 | 10.03% | [5 empty] | Non-TXV | 5.217%
Los Banos | CA | 93635-3836 |  | 2013-08-01 | 2013-08-01 14:08 | 2013-08-01 14:10 | DAY & NIGHT - 7777UNK | 100 | 3.2 | Yes | Yes | 26 | 20.4 | 5.6 | EC822A994D1B4892BE05DA05D6EC1411 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95219-3119 |  | 2013-07-08 | 2013-07-08 16:37 | 2013-07-08 16:37 | BRYANT - 561CJ030-D | 66 | 0 | Yes | Yes | 20.4 | 20.5 | -0.1 | 4BFDE1F29137446594D02DC03C163684 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-3496 |  | 2013-08-14 | 2013-08-14 12:52 | 2013-08-14 13:09 | DAY & NIGHT - 565BJ036-A | 105 | 4.9 | Yes | Yes | 19.7 | 18.6 | 1.1 | BFED58C3D8FC462BA86D12110241A311 |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Stockton | CA | 95210-1427 |  | 2013-06-10 | 2013-06-10 08:18 | 2013-06-10 08:38 | BRYANT - 585A030080YAC | 50 | -2.9 | Yes | Yes | 24.8 | 18.8 | 6 | C428D8B9E29A4B779EC7C373869E6B20 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Orosi | CA | 93647-9708 |  | 2013-07-29 | 2013-07-29 14:23 | 2013-07-29 14:50 | AMERICAN STANDARD - YCY036G1M0AC | 129 | 7 | Yes | Yes | 16.1 | 18.4 | -2.3 | 6388390025DA414BAAC06BD513B823C1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.426% | 0.94574 | 10.43% | [5 empty] | Non-TXV | 5.426%
Manteca | CA | 95336-8650 |  | 2013-05-29 | 2013-05-29 11:39 | 2013-05-29 11:58 | GOODMAN - CKT60-1A | 123 | 4.1 | Yes | Yes | 22.1 | 20.2 | 1.9 | 7A0111E8A407418CB7A0AD50425C5B82 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Lincoln | CA | 95648-0000 |  | 2013-05-31 | 2013-05-31 12:34 | 2013-05-31 13:03 | BDP - 114ANA048-A | 176 | 8.9 | Yes | Yes | 22 | 20.4 | 1.6 | 050785111BF043E79073AC4AB4F4936A |  | R410A | TXV |  | 5.057% | 0.94943 | 9.718% | [5 empty] | TXV | 5.057%
Tracy | CA | 95377-8813 |  | 2013-06-05 | 2013-06-05 09:08 | 2013-06-05 09:42 | YORK - H1RA048S06D | 117 | -8.3 | Yes | Yes | 21.3 | 20.4 | 0.9 | A52BDC3AC2634B9BB3CE5B8CB21D6745 |  | R22 | Non-TXV |  | -7.094% | 1.0709 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.094%
Stockton | CA | 95204-3752 |  | 2013-06-03 | 2013-06-03 11:59 | 2013-06-03 12:28 | PAYNE - 585B024050YACR | 51 | 4.3 | Yes | Yes | 16.5 | 18.3 | -1.8 | 09CB11DA222E44FDBEE5F16635CABE87 |  | R22 | Non-TXV |  | 8.431% | 0.91569 | 16.2% | [5 empty] | Non-TXV | 8.431%
Merced | CA | 95348-8715 |  | 2013-07-12 | 2013-07-12 15:01 | 2013-07-12 15:06 | GOODMAN - CKL60-1L | 115 | 5.5 | Yes | Yes | 18.7 | 21 | -2.3 | 2DBBC614CEC2452EA2C6D467F38A0B1A |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Red Bluff | CA | 96080-0000 |  | 2013-05-28 | 2013-05-28 12:56 | 2013-05-28 13:20 | ARMSTRONG - 2SCU13LB160P-1 | 214 | 9.3 | Yes | Yes | 19 | 20.7 | -1.7 | F684188C84A64480857B71FBEC5C6108 |  | R22 | Non-TXV |  | 4.346% | 0.95654 | 8.352% | [5 empty] | Non-TXV | 4.346%
Red Bluff | CA | 96080-0000 |  | 2013-05-28 | 2013-05-28 13:23 | 2013-05-28 13:23 | ARMSTRONG - 2SCU13LB160P-1 | 85 | 0 | Yes | Yes | 21.9 | 21.8 | 0.1 | 63EF0E1C5BCD4D0FB7FF4C3C426CE570 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-3160 |  | 2013-05-30 | 2013-05-30 09:45 | 2013-05-30 10:03 | LUXAIRE - UNK | 54 | 4.9 | Yes | Yes | 16.3 | 18.3 | -2 | DB01C45F1E344EA7B25372F6BE3018B0 |  | R22 | Non-TXV |  | 9.074% | 0.90926 | 17.44% | [5 empty] | Non-TXV | 9.074%
Clovis | CA | 93612-4934 |  | 2013-08-29 | 2013-08-29 14:13 | 2013-08-29 14:37 | BDP - 585A02405YAC | 51 | 1.7 | Yes | Yes | 17 | 19 | -2 | F74F2970F7C8464C9966A806943788DE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95348-8715 |  | 2013-08-09 | 2013-08-09 14:38 | 2013-08-09 14:59 | GOODMAN - CKL60-1A | 117 | 3.7 | Yes | Yes | 21 | 21.4 | -0.4 | B96AB13104E9473AA644E9053498CF7E |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Chico | CA | 95926-4378 |  | 2013-06-05 | 2013-06-05 12:46 | 2013-06-05 13:13 | DAY & NIGHT - 585GJ018040 | 55 | 7.3 | Yes | Yes | 18 | 20.4 | -2.4 | 4CEB9EEAAF1D46F88CCC3F62D14E9B6F |  | R22 | Non-TXV |  | 13.27% | 0.86727 | 25.51% | [5 empty] | Non-TXV | 13.27%
Chico | CA | 95973-0422 |  | 2013-08-06 | 2013-08-06 08:21 | 2013-08-06 08:45 | BDP - 567C0306CU | 49 | 3.6 | Yes | Yes | 24.5 | 19.1 | 5.4 | 38E6DAB5D3204F4998229E7C93233A83 |  | R22 | Non-TXV |  | 7.347% | 0.92653 | 14.12% | [5 empty] | Non-TXV | 7.347%
Stockton | CA | 95206-5207 |  | 2013-08-13 | 2013-08-13 10:00 | 2013-08-13 10:17 | PAYNE - 561AJ024-B | 57 | 5.7 | Yes | Yes | 16.3 | 16.5 | -0.1 | A6EFE11E6118458A9B944F5875777E66 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Oroville | CA | 95965-3581 |  | 2013-06-19 | 2013-06-19 17:55 | 2013-06-19 18:20 | ECONAIR - AC036X1021G | 64 | 2.1 | Yes | Yes | 21.9 | 19.5 | 2.4 | CBFE1E24C1A14B2AA446BEA1D3CF6396 |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Chico | CA | 95928-9173 |  | 2013-06-04 | 2013-06-04 11:12 | 2013-06-04 11:54 | YORK - MHXM254298 | 65 | 11.8 | Yes | Yes | 21.7 | 21.8 | -0.1 | 2DD76275CDD84B87A644B2E43C64E1B3 |  | R22 | Non-TXV |  | 18.15% | 0.81846 | 34.89% | [5 empty] | Non-TXV | 18.15%
Stockton | CA | 95210-3680 |  | 2013-06-05 | 2013-06-05 09:24 | 2013-06-05 09:41 | PAYNE - 591ANX036000AAAA | 85 | -5 | Yes | Yes | 17.1 | 19.9 | -2.8 | CD04399934564DD2ADC7DD41E642888A |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Chico | CA | 95973-7804 |  | 2013-06-03 | 2013-06-03 18:34 | 2013-06-03 18:51 | LENNOX - M/NH529-30-ZP | 85 | 2.6 | Yes | Yes | 24.9 | 20.8 | 4.1 | 8DA53AA999724A7E80239414894647F1 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Paradise | CA | 95969-6308 |  | 2013-06-29 | 2013-06-29 09:15 | 2013-06-29 09:48 | PAYNE - PYPNB030060AA | 55 | 2 | Yes | Yes | 21 | 21.5 | -0.5 | D603A780DA5742E6AA0916916342F656 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Oroville | CA | 95965-3522 |  | 2013-06-21 | 2013-06-21 18:10 | 2013-06-21 18:27 | DAY & NIGHT - 5858024050YACR | 51 | 2 | Yes | Yes | 18.3 | 20.4 | -2.1 | 53D1FD3EBDCE46E2BA50954712027707 |  | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Stockton | CA | 95206-4635 |  | 2013-07-30 | 2013-07-30 11:07 | 2013-07-30 11:28 | YORK - H2RA036S06D | 63 | -3.7 | Yes | Yes | 23.6 | 19.6 | 4.1 | 5C212784E8BA494C90D1724B701FAFC4 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Stockton | CA | 95204-4260 |  | 2013-05-31 | 2013-05-31 16:27 | 2013-05-31 16:52 | BRYANT - 582ANW036090AAAF | 56 | 6.7 | Yes | Yes | 20.9 | 19.7 | 1.2 | 7884405F886E4A9696A074E59FA365A7 |  | R22 | Non-TXV |  | 11.96% | 0.88036 | 22.99% | [5 empty] | Non-TXV | 11.96%
Oakdale | CA | 95361-3125 |  | 2013-07-09 | 2013-07-09 12:19 | 2013-07-09 12:40 | CARRIER - 38EH030300SM | 115 | 3.4 | Yes | Yes | 26.5 | 20.8 | 5.7 | 607C7FEC27294989B8743DEBEE6684FA |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Live Oak | CA | 95953-9424 |  | 2013-08-05 | 2013-08-05 14:42 | 2013-08-05 15:16 | TRANE - 2TTB0036A1000AA | 76 | 3.4 | Yes | Yes | 15.5 | 18 | -2.5 | 214171875E394AC69ACB8D9594589E4B |  | R22 | TXV |  | 4.474% | 0.95526 | 8.597% | [5 empty] | TXV | 4.474%
Stockton | CA | 95210-1868 |  | 2013-06-12 | 2013-06-12 08:37 | 2013-06-12 09:05 | OTHER - AR7-24 | 90 | 5.8 | Yes | Yes | 15.3 | 18.2 | -2.9 | B0B74AC4901A4B6496068AA26E6CA8DE |  | R22 | Non-TXV |  | 6.444% | 0.93556 | 12.38% | [5 empty] | Non-TXV | 6.444%
Merced | CA | 95341-6873 |  | 2013-07-02 | 2013-07-02 12:49 | 2013-07-02 12:54 | YORK - H10B024S06A | 67 | 3 | Yes | Yes | 22.6 | 18.6 | 4 | 5F8F7B226CBF44A1827660E228FDA0C4 |  | R22 | Non-TXV |  | 4.478% | 0.95522 | 8.605% | [5 empty] | Non-TXV | 4.478%
Red Bluff | CA | 96080-7743 |  | 2013-05-31 | 2013-05-31 10:07 | 2013-05-31 10:28 | BRYANT - 602BNX036000AAAF | 150 | 11.5 | Yes | Yes | 24.8 | 20.7 | 4.1 | 21BCD090C96D498185C469A2C5E7BC20 |  | R410A | TXV |  | 7.667% | 0.92333 | 14.73% | [5 empty] | TXV | 7.667%
El Dorado Hills | CA | 95762-9730 |  | 2013-06-19 | 2013-06-19 11:46 | 2013-06-19 11:46 | RUUD - 15PJL36A01 | 138 | 0 | Yes | Yes | 19.3 | 15.2 | 4.1 | 383FD019CCA34F8BAB2E5FDEDE7B99F5 |  | R410A | TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-5122 |  | 2013-06-03 | 2013-06-03 12:20 | 2013-06-03 12:37 | BRYANT - 583ANW04890AAHF | 114 | 3.6 | Yes | Yes | 26 | 21 | 5 | D230D2F8D70D4B44B6C805DB4154AC69 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Stockton | CA | 95210-1467 |  | 2013-06-07 | 2013-06-07 11:53 | 2013-06-07 12:10 | RHEEM - RRNA-B036JK08X | 83 | 2.6 | Yes | Yes | 23.4 | 19.5 | 3.9 | D77B207D6D094211AB434DAF09EB30EA |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Stockton | CA | 95206-4843 |  | 2013-06-17 | 2013-06-17 12:43 | 2013-06-17 13:04 | ALLEGIANCE - 2A7A1048A100AA | 109 | 12.6 | Yes | Yes | 27.4 | 21.4 | 6 | 4E57974A05224F1DB4DAEAC6997D9EEE |  | R22 | Non-TXV |  | 11.56% | 0.8844 | 22.22% | [5 empty] | Non-TXV | 11.56%
Dinuba | CA | 93618-9502 |  | 2013-07-26 | 2013-07-26 14:32 | 2013-07-26 14:55 | BDP - 588ANW036060ADAF | 67 | 8.6 | Yes | Yes | 18.4 | 18.4 | 0 | FED871378CDF4051AAC9F072FECE75CC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.84% | 0.87164 | 24.67% | [5 empty] | Non-TXV | 12.84%
Manteca | CA | 95337-8569 |  | 2013-05-29 | 2013-05-29 16:53 | 2013-05-29 17:15 | BRYANT - 563CN048-F | 165 | 46.6 | Yes | Yes | 23.9 | 20.9 | 3 | A69D0A853F4A4ED3BE44E580546C4733 |  | R22 | Non-TXV |  | 28.24% | 0.71758 | 54.28% | [5 empty] | Non-TXV | 28.24%
Stockton | CA | 95207-7420 |  | 2013-06-05 | 2013-06-05 09:13 | 2013-06-05 09:13 | OTHER - NAC0336AKA5 | 130 | 0 | Yes | Yes | 23.8 | 19.1 | 4.8 | 72A315C16DE44067AA8EA4AA8C93E6C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-6710 |  | 2013-06-07 | 2013-06-07 08:49 | 2013-06-07 09:10 | GOODMAN - CJ24-1AB | 101 | -5.9 | Yes | Yes | 21.6 | 18.3 | 3.3 | 774F963F0706416FAC6E0984079E0729 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Stockton | CA | 95204-2528 |  | 2013-06-11 | 2013-06-11 12:58 | 2013-06-11 13:16 | LENNOX - HS22-311V-3P | 129 | 14.3 | Yes | Yes | 19 | 18 | 1 | 33367297A9314C1BA0A115E2F65FB380 |  | R22 | TXV |  | 11.09% | 0.88915 | 21.3% | [5 empty] | TXV | 11.09%
Stockton | CA | 95205-3110 |  | 2013-06-04 | 2013-06-04 13:36 | 2013-06-04 13:54 | ICP - R2A330GKR1 | 75 | 3 | Yes | Yes | 20.7 | 18.8 | 1.9 | 460355BFA43C4C708631AC06FEA67164 |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Fresno | CA | 93727-4401 |  | 2013-06-18 | 2013-06-18 10:09 | 2013-06-18 10:11 | PAYNE - 7777UNK | 96 | 6.6 | Yes | Yes | 21.7 | 20.7 | 1 | 3B673F513D96450D8D174A226A567310 |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Auburn | CA | 95602-8403 |  | 2013-08-14 | 2013-08-14 13:50 | 2013-08-14 14:09 | GE - BTB912A800A0 | 36 | 4.3 | Yes | Yes | 15 | 17.7 | -2.7 | D596E86CBB1A4C7DA4C60237C5BA6FE3 |  | R22 | Non-TXV |  | 11.94% | 0.88056 | 22.95% | [5 empty] | Non-TXV | 11.94%
Foresthill | CA | 95631-9717 |  | 2013-08-14 | 2013-08-14 13:35 | 2013-08-14 13:35 | GOODMAN - CLJ48-1A | 130 | 0 | Yes | Yes | 29.6 | 23.8 | 5.8 | CF4A87DA9A1542189D9AB54FEC2CD9FE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1756 |  | 2013-06-19 | 2013-06-19 09:22 | 2013-06-19 09:44 | DAY & NIGHT - 585A030080YACR | 85 | -5 | Yes | Yes | 24.6 | 18.7 | 5.9 | 5EDF5FEB4BD348AFA52963B1759A7DA8 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Clovis | CA | 93611-3118 |  | 2013-06-13 | 2013-06-13 12:39 | 2013-06-13 13:23 | LENNOX - GCS20R-411-100-2P | 70 | 2.1 | Yes | Yes | 24.4 | 19.8 | 4.6 | 1B93251307594FCA86AC5439B8C47723 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-3427 |  | 2013-06-01 | 2013-06-01 09:25 | 2013-06-01 09:53 | DAY & NIGHT - 591ANX030000AAAA | 76 | 6.2 | Yes | Yes | 21.9 | 19.3 | 2.6 | 83400D5882DD4F5E9B4CFCC594C55974 |  | R22 | Non-TXV |  | 8.158% | 0.91842 | 15.68% | [5 empty] | Non-TXV | 8.158%
Stockton | CA | 95206-2886 |  | 2013-06-18 | 2013-06-18 11:13 | 2013-06-18 11:36 | BRYANT - 561CJ030-B | 110 | 12.2 | Yes | Yes | 23.9 | 21 | 2.9 | 381926B1A3E8401EB520CAF9F453CC55 |  | R22 | Non-TXV |  | 11.09% | 0.88909 | 21.31% | [5 empty] | Non-TXV | 11.09%
Fresno | CA | 93720-0468 |  | 2013-06-21 | 2013-06-21 11:53 | 2013-06-21 11:57 | YORK - H108042S06A | 89 | 3.5 | Yes | Yes | 18.9 | 20.2 | -1.3 | B493E8BCF2804A26AA341695E3657C46 |  | R22 | Non-TXV |  | 3.933% | 0.96067 | 7.558% | [5 empty] | Non-TXV | 3.933%
Stockton | CA | 95203-2215 |  | 2013-05-30 | 2013-05-30 09:09 | 2013-05-30 09:09 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 21.5 | 18.8 | 2.7 | B47AF66225874147AE6DC2370B73ADEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-2611 |  | 2013-06-06 | 2013-06-06 09:18 | 2013-06-06 09:20 | RHEEM - RRNA-B042JK08X | 104 | 4.3 | Yes | Yes | 19.7 | 18.8 | 0.9 | 9DDCC8A434034B0091793E5510F10AA6 |  | R22 | Non-TXV |  | 4.135% | 0.95865 | 7.946% | [5 empty] | Non-TXV | 4.135%
Tracy | CA | 95376-3410 |  | 2013-05-29 | 2013-05-29 15:38 | 2013-05-29 16:02 | PAYNE - PA10JA030-C | 85 | -8 | Yes | Yes | 24 | 23.2 | 0.8 | 75DF0FBB1BCD41D1BAAAAE176CF0504E |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95206-4507 |  | 2013-06-13 | 2013-06-13 12:00 | 2013-06-13 12:26 | GOODMAN - CKL36-1H | 85 | 4.6 | Yes | Yes | 20 | 21.2 | -1.2 | 5A00FF1B6F67496BA03466F387ED5384 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Merced | CA | 95341-7512 |  | 2013-06-12 | 2013-06-12 08:35 | 2013-06-12 08:42 | TRANE - TTR048C100A2 | 114 | 9.3 | Yes | Yes | 21.2 | 19.4 | 1.8 | BBE7EF42450B4E7989FA8C4C0E323D6C |  | R22 | Non-TXV |  | 8.158% | 0.91842 | 15.68% | [5 empty] | Non-TXV | 8.158%
Auburn | CA | 95602-8401 |  | 2013-05-28 | 2013-05-28 17:06 | 2013-05-28 17:23 | GOODMAN - CKL18-1D | 83 | 2.5 | Yes | Yes | 19 | 19.9 | -0.9 | 165D04606F584A7985D177E00125322D |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Stockton | CA | 95210-1440 |  | 2013-06-07 | 2013-06-07 11:16 | 2013-06-07 11:34 | TRANE - 2YCX3030A1064AA | 88 | 2.8 | Yes | Yes | 22.1 | 17.7 | 4.4 | 99F622367C19457DB1A2777A0F0DA4CA |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Stockton | CA | 95210-4485 |  | 2013-05-28 | 2013-05-28 11:43 | 2013-05-28 11:43 | BDP - 561AJ060-C | 145 | 0 | Yes | Yes | 20.5 | 18.7 | 1.8 | 6573C2B274CB424FBF87956CF7CC7F83 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-8402 |  | 2013-05-28 | 2013-05-28 16:21 | 2013-05-28 16:43 | GE - UNK | 36 | 2.5 | Yes | Yes | 17 | 19.9 | -2.9 | 932019DB880048109D9DB53129EE8E69 |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Red Bluff | CA | 96080-3014 |  | 2013-05-28 | 2013-05-28 16:54 | 2013-05-28 17:10 | RHEEM - RAFD-036JAS | 80 | 8 | Yes | Yes | 17.7 | 18.8 | -1.1 | F1C8F43D54454556B596A35A1FE993E1 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Dinuba | CA | 93618-1719 |  | 2013-06-24 | 2013-06-24 14:01 | 2013-06-24 14:15 | OTHER - AD042G | 135 | 4.1 | Yes | Yes | 19.4 | 19.9 | -0.5 | 991FC0EF3869478AA785FA2C3D93F6A3 |  | R22 | Non-TXV |  | 3.037% | 0.96963 | 5.837% | [5 empty] | Non-TXV | 3.037%
Stockton | CA | 95205-7838 |  | 2013-06-05 | 2013-06-05 13:21 | 2013-06-05 13:49 | GE - BGTA824R1A | 48 | 2.1 | Yes | Yes | 19.5 | 17.5 | 2 | 84583619B0F44F6D9DFCE561440438F1 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Clovis | CA | 93611-5304 |  | 2013-07-01 | 2013-07-01 12:19 | 2013-07-01 12:34 | AMERICAN STANDARD - YCC024F1L0BG | 65 | 2.4 | Yes | Yes | 19.6 | 22.5 | -2.9 | 5BA9C6841C774313AD8032161DDD2ABD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.692% | 0.96308 | 7.096% | [5 empty] | Non-TXV | 3.692%
Clovis | CA | 93611-5304 |  | 2013-07-01 | 2013-07-01 12:34 | 2013-07-01 13:04 | AMERICAN STANDARD - YCC024F1L0BG | 65 | 2.9 | Yes | Yes | 20.1 | 19.1 | 1 | BBFFACB1260044B0BA2368C7A65A99DD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | Non-TXV | 4.462%
Fresno | CA | 93720-4115 |  | 2013-08-29 | 2013-08-29 13:57 | 2013-08-29 13:59 | YORK - DAYP-F036N070A | 108 | 3.2 | Yes | Yes | 23.4 | 18.8 | 4.6 | 49A2D858A8F4426790C6AAD2C8BABEB6 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Penn Valley | CA | 95946-9105 |  | 2013-09-05 | 2013-09-05 10:24 | 2013-09-05 10:50 | LENNOX - HS29-048-1P | 91 | 8.6 | Yes | Yes | 16 | 18.7 | -2.7 | CF23D23EA0A04DF1B775C972A3A881AD |  | R22 | TXV |  | 9.451% | 0.90549 | 18.16% | [5 empty] | TXV | 9.451%
Fresno | CA | 93727-6511 |  | 2013-06-17 | 2013-06-17 13:11 | 2013-06-17 13:14 | GOODMAN - GSC130481BB | 102 | 5.5 | Yes | Yes | 21.9 | 21.5 | 0.4 | B5F8ECF3C05D4AC394AC56C9083FB42A |  | R22 | Non-TXV |  | 5.392% | 0.94608 | 10.36% | [5 empty] | Non-TXV | 5.392%
Yuba City | CA | 95991-5449 |  | 2013-06-10 | 2013-06-10 10:34 | 2013-06-10 10:34 | BRYANT - 113ANA036-E | 90 | 0 | Yes | Yes | 21 | 18.7 | 2.3 | 808AFB1FD8874E9DA4C31247ED81CD87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-9026 |  | 2013-07-24 | 2013-07-24 13:08 | 2013-07-24 13:26 | RUUD - UAJC-042JAS | 99 | 7.9 | Yes | Yes | 27.2 | 21.7 | 5.5 | 5A455803E2F74FCA9FF947B96B2FD573 |  | R22 | Non-TXV |  | 7.98% | 0.9202 | 15.34% | [5 empty] | Non-TXV | 7.98%
Los Banos | CA | 93635-6418 |  | 2013-06-01 | 2013-06-01 11:44 | 2013-06-01 11:52 | BRYANT - 563CN060 | 200 | 8.2 | Yes | Yes | 24.1 | 22.5 | 1.6 | 9856202A061A4C71985A3CFA35C1AA6F |  | R22 | TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | TXV | 4.1%
Fresno | CA | 93710-6412 |  | 2013-06-10 | 2013-06-10 21:25 | 2013-06-10 21:25 | YORK - D1NPO36N05606A | 108 | 0 | Yes | Yes | 16.1 | 18.5 | -2.4 | 707311852CD74C1CA507818202E595E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-8401 |  | 2013-06-12 | 2013-06-12 12:20 | 2013-06-12 12:41 | GE - BTB912A800A0 | 36 | 19.3 | Yes | Yes | 19.5 | 20.4 | -0.9 | C3C8171962944835A88BF42BF3A5B150 |  | R22 | Non-TXV |  | 53.61% | 0.46389 | 103% | [5 empty] | Non-TXV | 53.61%
Stockton | CA | 95210-2616 |  | 2013-06-05 | 2013-06-05 14:09 | 2013-06-05 14:26 | BRYANT - 574DNWA24040NA | 77 | -4.5 | Yes | Yes | 24.5 | 19.3 | 5.3 | 9F110477F6C449DCA80B59560434DF70 |  | R410A | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Fresno | CA | 93720-4495 |  | 2013-08-08 | 2013-08-08 11:18 | 2013-08-08 11:18 | LENNOX - 12ACB36-5P | 102 | 4.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | 4090A3BAED83444FAC088EE49C68758A | Add refrigerant: 4.9 oz | R22 | Non-TXV |  | 4.804% | 0.95196 | 9.232% | [5 empty] | Non-TXV | 4.804%
Fresno | CA | 93727-7553 |  | 2013-07-16 | 2013-07-16 12:54 | 2013-07-16 13:14 | BDP - 585EJW048100AAAF | 86 | 2.8 | Yes | Yes | 21 | 21.7 | -0.7 | B59B8F5DC545464F85FE37B37F2CCE98 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
Stockton | CA | 95212-3802 |  | 2013-06-18 | 2013-06-18 10:59 | 2013-06-18 11:19 | CARRIER - 38CKC048370 | 99 | 3 | Yes | Yes | 20.8 | 20.3 | 0.5 | CC4FCBD3D30740F4A76CC583DBED357B |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Marysville | CA | 95901-3247 |  | 2013-08-21 | 2013-08-21 13:10 | 2013-08-21 13:32 | DAY & NIGHT - UNK | 99 | 3.5 | Yes | Yes | 18 | 18.2 | -0.2 | 461E72C22AE248848097B2B1FF7764EA |  | R22 | Non-TXV |  | 3.535% | 0.96465 | 6.794% | [5 empty] | Non-TXV | 3.535%
Oroville | CA | 95966-5211 |  | 2013-06-21 | 2013-06-21 17:45 | 2013-06-21 18:07 | DAY & NIGHT - DAYA-F036N090C | 67 | 8.4 | Yes | Yes | 22.8 | 21 | 1.8 | F352CFDC3C774DC88C512B477D9FA370 |  | R22 | Non-TXV |  | 12.54% | 0.87463 | 24.09% | [5 empty] | Non-TXV | 12.54%
Colusa | CA | 95932-3344 |  | 2013-09-17 | 2013-09-17 12:20 | 2013-09-17 12:36 | LENNOX - 12GCS024X-50-3PA | 72 | 3.2 | Yes | Yes | 18 | 18.8 | -0.8 | E796A62FB82F4C58862BAA4A452746EF |  | R22 | TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | TXV | 4.444%
Clovis | CA | 93612-4244 |  | 2013-06-18 | 2013-06-18 12:53 | 2013-06-18 13:12 | RUUD - URG-0KR7E36 | 75 | 2.2 | Yes | Yes | 19.9 | 20.4 | -0.5 | 6DB7AEAE6BEA43ECB169326D8222F3F9 |  | R22 | Non-TXV |  | 2.933% | 0.97067 | 5.637% | [5 empty] | Non-TXV | 2.933%
Stockton | CA | 95205-3820 |  | 2013-07-17 | 2013-07-17 11:30 | 2013-07-17 12:05 | RHEEM - HC-100-42-21C | 72 | 4.3 | Yes | Yes | 21 | 18.2 | 2.8 | 68CA9B2BEEAF451AB2D170EA37868DBE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.972% | 0.94028 | 11.48% | [5 empty] | Non-TXV | 5.972%
Stockton | CA | 95207-0000 |  | 2013-05-29 | 2013-05-29 09:43 | 2013-05-29 10:03 | RHEEM - RRMA-A024JK06X | 70 | 3.1 | Yes | Yes | 19.3 | 19.3 | 0 | 2FDD85CAA4744759A61F30A34445CDC5 |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Clovis | CA | 93611-5113 |  | 2013-06-13 | 2013-06-13 19:45 | 2013-06-13 20:26 | OTHER - 80WE36C1NA | 125 | 4 | Yes | Yes | 21.6 | 20.9 | 0.7 | 07D328F39E30478D90BA0B3D0171E266 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95210-1108 |  | 2013-06-06 | 2013-06-06 10:08 | 2013-06-06 10:25 | RUUD - RRKA-A030JK06X | 54 | -3.2 | Yes | Yes | 21.3 | 18.8 | 2.5 | B007D94FE067434EADF7B3ED9B33D0B9 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Stockton | CA | 95207-1157 |  | 2013-07-26 | 2013-07-26 12:20 | 2013-07-26 12:38 | CARRIER - 48GS024040301 | 56 | 3.9 | Yes | Yes | 16.5 | 18.8 | -2.3 | F832E7857EC844BBA2B611BEE503966E |  | R22 | Non-TXV |  | 6.964% | 0.93036 | 13.38% | [5 empty] | Non-TXV | 6.964%
Fresno | CA | 93720-2519 |  | 2013-06-21 | 2013-06-21 16:47 | 2013-06-21 16:49 | DAY & NIGHT - UNK | 67 | 5 | Yes | Yes | 22.8 | 21.3 | 1.5 | 5E71C3C0473A4C71821A72F94E15638F |  | R22 | Non-TXV |  | 7.463% | 0.92537 | 14.34% | [5 empty] | Non-TXV | 7.463%
Olivehurst | CA | 95961-4643 |  | 2013-10-02 | 2013-10-02 16:02 | 2013-10-02 16:22 | CARRIER - UNK | 197 | 5.9 | Yes | Yes | 18 | 18.8 | -0.8 | 1242E5BCB1C64B0ABFC1D56DDFE1CB9F |  | R22 | Non-TXV |  | 2.995% | 0.97005 | 5.756% | [5 empty] | Non-TXV | 2.995%
Tracy | CA | 95377-7904 |  | 2013-06-04 | 2013-06-04 15:15 | 2013-06-04 15:46 | YORK - H1RC042S06B | 85 | 4.6 | Yes | Yes | 23.8 | 21 | 2.8 | B3762FC1631D4A3E9D01D2F5EBFD74C7 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Oroville | CA | 95965-4049 |  | 2013-06-19 | 2013-06-19 13:02 | 2013-06-19 13:02 | YORK - H2RE042506A | 224 | 0 | Yes | Yes | 22.2 | 21.3 | 1 | A0D7DA2949894A439955117C8EBDA19A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-5908 |  | 2013-06-01 | 2013-06-01 16:32 | 2013-06-01 16:50 | RUUD - URMA-A030JK06E | 80 | 8.6 | Yes | Yes | 21.7 | 19.9 | 1.8 | 30CCF5328E964239A09FDC5A1DCCAD99 |  | R22 | Non-TXV |  | 10.75% | 0.8925 | 20.66% | [5 empty] | Non-TXV | 10.75%
Atwater | CA | 95301-2666 |  | 2013-07-10 | 2013-07-10 09:59 | 2013-07-10 10:01 | CARRIER - 48GS-042060301 | 100 | 5.7 | Yes | Yes | 22.6 | 19.9 | 2.7 | A6C7D3FFEB884B4F8C6C34A4BD3C8E33 |  | R22 | Non-TXV |  | 5.7% | 0.943 | 10.95% | [5 empty] | Non-TXV | 5.7%
Diamond Springs | CA | 95619-9436 |  | 2013-06-26 | 2013-06-26 09:32 | 2013-06-26 09:32 | COLEMAN - 2442-901 | 64 | 0 | Yes | Yes | 22.7 | 17 | 5.7 | B919AC93F4F2437FB836AB34FC32E8B7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-8219 |  | 2013-05-31 | 2013-05-31 13:26 | 2013-05-31 13:48 | RHEEM - RAHE-036JAS | 85 | 8.6 | Yes | Yes | 26.6 | 23.4 | 3.2 | B8CA05A4AFC24307AAEAD34AA7064303 |  | R22 | Non-TXV |  | 10.12% | 0.89882 | 19.44% | [5 empty] | Non-TXV | 10.12%
Manteca | CA | 95337-9656 |  | 2013-09-06 | 2013-09-06 11:04 | 2013-09-06 11:23 | RUUD - UAHE-048JAS | 114 | 3.4 | Yes | Yes | 20.2 | 20.2 | 0 | F5F74844841B407280EE0AF6FC80ED95 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Atwater | CA | 95301-2215 |  | 2013-06-07 | 2013-06-07 15:41 | 2013-06-07 15:46 | GOODMAN - CE421EB | 101 | 7.3 | Yes | Yes | 22.4 | 17.5 | 4.9 | F81E37D24A7B41DC82972EA2AAD673E3 |  | R22 | Non-TXV |  | 7.228% | 0.92772 | 13.89% | [5 empty] | Non-TXV | 7.228%
Fresno | CA | 93726-6052 |  | 2013-06-07 | 2013-06-07 16:40 | 2013-06-07 17:46 | GOODMAN - PGB036075-1 | 60 | 1.8 | Yes | Yes | 22 | 21 | 1 | 1BF4DD60EE5F4A0A92F2C71FA8CB1AA9 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Yuba City | CA | 95991-9446 |  | 2013-07-18 | 2013-07-18 08:34 | 2013-07-18 08:50 | LENNOX - 13ACC-036-230-0 | 115 | 12.3 | Yes | Yes | 23 | 19.8 | 3.2 | 3A04CED259884655BFFA0943C6210AC8 |  | R22 | TXV |  | 10.7% | 0.89304 | 20.55% | [5 empty] | TXV | 10.7%
Stockton | CA | 95203-3022 |  | 2013-05-29 | 2013-05-29 11:17 | 2013-05-29 11:35 | YORK - D1NP036N05606A | 108 | 5.9 | Yes | Yes | 17.7 | 19.3 | -1.6 | A4057179F2C24D0F854FCABD6415F9AE |  | R22 | Non-TXV |  | 5.463% | 0.94537 | 10.5% | [5 empty] | Non-TXV | 5.463%
Fresno | CA | 93703-1101 |  | 2013-07-03 | 2013-07-03 09:45 | 2013-07-03 10:06 | CARRIER - 48NLT080300 | 85 | 2.9 | Yes | Yes | 20 | 21.3 | -1.3 | 1E9316B49FC044CDB9EC673A8F6550D3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Paradise | CA | 95969-5510 |  | 2013-06-12 | 2013-06-12 19:12 | 2013-06-12 19:29 | DAY & NIGHT - NA | 60 | 4.8 | Yes | Yes | 15.9 | 18.2 | -2.3 | 2C0C65294D2C4ABA85B3045B09BAD914 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Chico | CA | 95928-6858 |  | 2013-07-03 | 2013-07-03 18:13 | 2013-07-03 18:31 | YORK - D5YS036N08006A | 80 | 9.2 | Yes | Yes | 16 | 16.4 | -0.4 | 3D70673EA6F54015AC1B88366221CDC6 |  | R22 | Non-TXV |  | 11.5% | 0.885 | 22.1% | [5 empty] | Non-TXV | 11.5%
Chico | CA | 95926-4802 |  | 2013-08-30 | 2013-08-30 10:24 | 2013-08-30 10:42 | BDP - 585B024050YACR | 51 | 1.9 | Yes | Yes | 19.5 | 18.6 | 0.9 | F94AB92F6035400BBA70EDD651055FAE |  | R22 | Non-TXV |  | 3.725% | 0.96275 | 7.16% | [5 empty] | Non-TXV | 3.725%
Chico | CA | 95928-4112 |  | 2013-08-01 | 2013-08-01 11:42 | 2013-08-01 12:01 | AMANA - PGA36C0702F | 64 | 4.3 | Yes | Yes | 24.6 | 18.7 | 5.9 | C3EC2B1891FD484D8E49202AB47E374F |  | R22 | Non-TXV |  | 6.719% | 0.93281 | 12.91% | [5 empty] | Non-TXV | 6.719%
Stockton | CA | 95206-6352 |  | 2013-06-18 | 2013-06-18 11:27 | 2013-06-18 11:27 | YORK - H2RC048S06A | 120 | 0 | Yes | Yes | 18.7 | 19.7 | -1 | E3F3B9A349BB4D8BBE1CF459223C463B |  | R22 | TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9122 |  | 2013-07-17 | 2013-07-17 14:25 | 2013-07-17 15:15 | CARRIER - 38GSO42310 | 84 | 3.3 | Yes | Yes | 18.7 | 20.7 | -2 | C181A63AF3DA40B28C98DF4D8703FA98 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Placerville | CA | 95667-3126 |  | 2013-05-29 | 2013-05-29 14:11 | 2013-05-29 14:11 | LENNOX - HP13-030-230-01 | 132 | 0 | Yes | Yes | 23.8 | 19.1 | 4.7 | F404766147D6401298B1BF2513200921 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4211 |  | 2013-07-18 | 2013-07-18 08:32 | 2013-07-18 08:48 | OTHER - JS3BA-024KA | 64 | 14.2 | Yes | Yes | 22.5 | 18.8 | 3.8 | A7371E2622814477B209E44FCF5933F9 |  | R22 | Non-TXV |  | 22.19% | 0.77812 | 42.64% | [5 empty] | Non-TXV | 22.19%
Fresno | CA | 93726-5807 |  | 2013-06-10 | 2013-06-10 09:38 | 2013-06-10 09:54 | ICP - PGF0300K060A | 52 | 4.8 | Yes | Yes | 25.9 | 19.9 | 6 | 0CEE7E2830DC471382954DE610C5D754 |  | R22 | Non-TXV |  | 9.231% | 0.90769 | 17.74% | [5 empty] | Non-TXV | 9.231%
Stockton | CA | 95207-4293 |  | 2013-05-31 | 2013-05-31 14:10 | 2013-05-31 14:28 | PAYNE - PA13NR024000AEAA | 91 | 4.8 | Yes | Yes | 20.7 | 22.6 | -1.9 | 6BE99232FA22406D95875977C834118E |  | R22 | TXV |  | 5.275% | 0.94725 | 10.14% | [5 empty] | TXV | 5.275%
Tracy | CA | 95376-1453 |  | 2013-06-07 | 2013-06-07 11:22 | 2013-06-07 11:44 | RHEEM - RAFD-042JAS | 85 | -8 | Yes | Yes | 22.2 | 21 | 1.2 | C826ABE697C3400C98A6AF21BA123991 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Madera | CA | 93637-4972 |  | 2013-07-16 | 2013-07-16 12:23 | 2013-07-21 13:06 | YORK - HA4H048S064 | 138 | -8.1 | Yes | Yes | 21.8 | 19.7 | 2.1 | 5F4D0CAC4B2F45BD8C7596C2F9B1C279 |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Fresno | CA | 93720-4690 |  | 2013-06-21 | 2013-06-21 12:20 | 2013-06-21 12:24 | LENNOX - 12ACB48-5P | 171 | 5.1 | Yes | Yes | 17.8 | 19.9 | -2.1 | F2BB950931034055866F22592FD33621 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Stockton | CA | 95207-4291 |  | 2013-06-14 | 2013-06-14 08:25 | 2013-06-14 08:44 | RHEEM - URKA-A030JK06X | 55 | -3.2 | Yes | Yes | 23.9 | 20.1 | 3.8 | BF57A83DA19646DE88C88917967F4124 |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Stockton | CA | 95204-2644 |  | 2013-05-31 | 2013-05-31 10:59 | 2013-05-31 11:17 | CARRIER - 48SX-024060331AA | 57 | 3.5 | Yes | Yes | 19 | 19.9 | -0.9 | 5E613336B16348F6A4CBDFC932E982F2 |  | R22 | Non-TXV |  | 6.14% | 0.9386 | 11.8% | [5 empty] | Non-TXV | 6.14%
Tracy | CA | 95376-5647 |  | 2013-07-11 | 2013-07-11 09:06 | 2013-07-11 09:31 | BRYANT - 113RNA048-B | 185 | 8.2 | Yes | Yes | 20 | 18.8 | 1.2 | C9961461D0814C6395CFF5F8B5DA481E |  | R22 | Non-TXV |  | 4.432% | 0.95568 | 8.518% | [5 empty] | Non-TXV | 4.432%
Loomis | CA | 95650-9540 |  | 2013-09-13 | 2013-09-13 12:30 | 2013-09-13 12:30 | RHEEM - UNK | 53 | 0 | Yes | Yes | 21.9 | 20.1 | 1.8 | DB3AC3BCF22B4B629648A7BA7BC958B7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-8901 |  | 2013-06-04 | 2013-06-04 14:41 | 2013-06-04 15:05 | YORK - AC048X1021A | 117 | 6.8 | Yes | Yes | 24.4 | 18.5 | 5.9 | 37D1FE51942F4A5DAA0D325F0D10419D |  | R22 | Non-TXV |  | 5.812% | 0.94188 | 11.17% | [5 empty] | Non-TXV | 5.812%
Stockton | CA | 95210-6764 |  | 2013-05-30 | 2013-05-30 09:02 | 2013-05-30 09:24 | YORK - H2RC042S06A | 107 | 3.9 | Yes | Yes | 16.3 | 18.3 | -2 | 6601EEE09CC54AE99FA673741FCB6FA0 |  | R22 | TXV |  | 3.645% | 0.96355 | 7.005% | [5 empty] | TXV | 3.645%
Clovis | CA | 93612-1506 |  | 2013-08-06 | 2013-08-06 15:52 | 2013-08-06 15:54 | CARRIER - 568EBX060000AFAA | 197 | 22.2 | Yes | Yes | 16.5 | 18.6 | -2.1 | 56C9FC7D59074F25AB10FC86F9F94A6A |  | R22 | Non-TXV |  | 11.27% | 0.88731 | 21.66% | [5 empty] | Non-TXV | 11.27%
Fresno | CA | 93726-5241 |  | 2013-06-06 | 2013-06-06 18:06 | 2013-06-06 18:25 | CARRIER - 48SX-042100331AA | 87 | 2.8 | Yes | Yes | 18.9 | 13.9 | 5 | 9C957FC3946949CB9173C1CAE4E52708 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.218% | 0.96782 | 6.185% | [5 empty] | Non-TXV | 3.218%
Stockton | CA | 95215-6003 |  | 2013-06-06 | 2013-06-06 10:09 | 2013-06-06 10:09 | AMANA - RCC30C2C | 85 | 0 | Yes | Yes | 16.4 | 18.3 | -1.9 | 1795A884F45245659ACB403C1ABC76E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5722 |  | 2013-07-03 | 2013-07-03 11:20 | 2013-07-03 12:39 | RHEEM - RRGH-05N30JKR | 77 | 4.2 | Yes | Yes | 18.9 | 20.7 | -1.8 | A9B470B52E5D4511B13B2EA8FC63B771 |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Corning | CA | 96021-2159 |  | 2013-06-14 | 2013-06-14 11:14 | 2013-06-14 11:58 | RUUD - LMAMC-036JAS | 93 | 6.3 | Yes | Yes | 21 | 19.8 | 1.2 | D845425CCDA948D1ACDE30D125556DBB |  | R22 | Non-TXV |  | 6.774% | 0.93226 | 13.02% | [5 empty] | Non-TXV | 6.774%
Newcastle | CA | 95658-9659 |  | 2013-08-08 | 2013-08-08 17:26 | 2013-08-08 17:26 | RHEEM - RRMA-A048JK08X | 117 | 0 | Yes | Yes | 22.9 | 19.8 | 3.1 | 6C011CE6E1DA4E2F85DFFD2A8D4ACACF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-0235 |  | 2013-05-29 | 2013-05-29 14:13 | 2013-05-29 14:36 | CARRIER - N/A | 120 | 6.4 | Yes | Yes | 22.4 | 21.4 | 1 | 6E27FFFADBE14EC28EE50EE3378D30FE |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Thornton | CA | 95686-0000 |  | 2013-09-25 | 2013-09-25 11:00 | 2013-09-25 11:19 | AMANA - PGB30C0702E | 64 | 8 | Yes | Yes | 25.6 | 20.1 | 5.5 | 92AEAA9DBE664BF29FBE325E94F08421 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Dinuba | CA | 93618-3492 |  | 2013-07-29 | 2013-07-29 11:08 | 2013-07-29 11:26 | ICP - PGF036K060B | 71 | 8.3 | Yes | Yes | 15.8 | 18.6 | -2.8 | 27296E5C88154F68836740D974E97E88 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.69% | 0.8831 | 22.47% | [5 empty] | Non-TXV | 11.69%
Ione | CA | 95640-9684 |  | 2013-06-26 | 2013-06-26 13:35 | 2013-06-26 13:55 | HEIL - PGAA36C1K1 | 77 | 12.6 | Yes | Yes | 23.2 | 19.3 | 3.9 | 49B3A89DF70442A38D78A3A1B9457A1D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.36% | 0.83636 | 31.45% | [5 empty] | Non-TXV | 16.36%
Stockton | CA | 95203-3137 |  | 2013-05-29 | 2013-05-29 13:46 | 2013-05-29 14:07 | LUXAIRE - UNK | 54 | 4.5 | Yes | Yes | 19.4 | 18.7 | 0.7 | A55B8ADF1ECE4CF9A7C7A53EBA705296 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Merced | CA | 95341-7511 |  | 2013-06-14 | 2013-06-14 17:21 | 2013-06-14 17:24 | TRANE - TTR030C100A2 | 74 | 12 | Yes | Yes | 23.2 | 19.9 | 3.3 | 1DF6951B2188412D904B3089808AD6B0 |  | R22 | Non-TXV |  | 16.22% | 0.83784 | 31.16% | [5 empty] | Non-TXV | 16.22%
Yuba City | CA | 95993-5002 |  | 2013-06-06 | 2013-06-06 11:34 | 2013-06-06 11:55 | LENNOX - 10ACC-060-230-02 | 130 | 4.4 | Yes | Yes | 21 | 19.7 | 1.3 | 233E3B3460B94ECBA54EA6A556DEB0C5 |  | R22 | Non-TXV |  | 3.385% | 0.96615 | 6.504% | [5 empty] | Non-TXV | 3.385%
Thornton | CA | 95686-0000 |  | 2013-09-25 | 2013-09-25 10:39 | 2013-09-25 10:57 | BRYANT - 113ANA036-E | 83 | 3.2 | Yes | Yes | 21.7 | 18.7 | 3 | 9200D889BDC24B208578D081FCFB6695 |  | R410A | TXV |  | 3.855% | 0.96145 | 7.409% | [5 empty] | TXV | 3.855%
Marysville | CA | 95901-3717 |  | 2013-06-04 | 2013-06-04 10:07 | 2013-06-04 10:54 | BRYANT - 38ED036300 | 130 | 18.1 | Yes | Yes | 16.8 | 19.3 | -2.5 | 1B456D624BFB432F89A8E2EA1F1F15D9 |  | R22 | Non-TXV |  | 13.92% | 0.86077 | 26.76% | [5 empty] | Non-TXV | 13.92%
Mariposa | CA | 95338-9249 |  | 2013-09-11 | 2013-09-11 12:25 | 2013-09-11 12:26 | YORK - H1RA042S06A | 84 | 5.5 | Yes | Yes | 25 | 19.9 | 5.1 | 2902286865D440C189E8ED23E5D16E39 |  | R22 | Non-TXV |  | 6.548% | 0.93452 | 12.58% | [5 empty] | Non-TXV | 6.548%
Manteca | CA | 95336-2956 |  | 2013-05-31 | 2013-05-31 12:22 | 2013-05-31 12:48 | RUUD - UAKA-042JAZ | 79 | 8.9 | Yes | Yes | 21.8 | 21.4 | 0.4 | 21DB05A6DB9746B2B76A91FE8E0BE514 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.27% | 0.88734 | 21.65% | [5 empty] | Non-TXV | 11.27%
Stockton | CA | 95204-5824 |  | 2013-06-03 | 2013-06-03 09:32 | 2013-06-03 09:53 | GOODMAN - CKL49-1 | 109 | 7.3 | Yes | Yes | 15.7 | 17.5 | -1.8 | 2D3DB2B44366459BB96C40BAF9DF5D1E |  | R22 | Non-TXV |  | 6.697% | 0.93303 | 12.87% | [5 empty] | Non-TXV | 6.697%
Fresno | CA | 93726-5207 |  | 2013-06-06 | 2013-06-06 10:32 | 2013-06-06 12:09 | OTHER - 80WR36A1AD | 56 | 5.9 | Yes | Yes | 16.3 | 18.3 | -2 | E5472F9899514DD886F45BF8A2ED5A44 |  | R22 | Non-TXV |  | 10.54% | 0.89464 | 20.25% | [5 empty] | Non-TXV | 10.54%
Lincoln | CA | 95648-9615 |  | 2013-06-18 | 2013-06-18 14:16 | 2013-06-18 14:40 | COLEMAN - BRCQ0361BDG | 52 | -4.9 | Yes | Yes | 25 | 21.4 | 3.6 | 695BD83BE4ED48D4B761AC5E649AFC35 |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Fresno | CA | 93726-5806 |  | 2013-06-18 | 2013-06-18 15:13 | 2013-06-18 15:15 | CARRIER - 48KL142300BE | 78 | 2.5 | Yes | Yes | 25.3 | 21.5 | 3.8 | EA2271841D374E8BA53FE89338ECDF50 |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Rocklin | CA | 95677-2449 |  | 2013-08-06 | 2013-08-06 08:50 | 2013-08-06 08:50 | AMANA - PGC24B0702A | 63.7 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | 7959C1C6EB784F59B2807060F6440DED | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Live Oak | CA | 95953-2087 |  | 2013-08-05 | 2013-08-05 17:06 | 2013-08-05 17:26 | GOODMAN - CKL42-1L | 115 | -18.9 | Yes | Yes | 11 | 12.2 | -1.2 | 949CBA59D63446CE9B04EAC689FCF840 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -16.43% | 1.1643 | 4.603% |  |  |  |  | TXV |  |  | -16.43%
Stockton | CA | 95207-4621 |  | 2013-06-13 | 2013-06-13 15:02 | 2013-06-13 15:21 | OTHER - PGC024K040A | 58 | 4.5 | Yes | Yes | 21.7 | 21.2 | 0.6 | 9EF934860E36463DA3DD67CE8ED3D3F4 |  | R22 | Non-TXV |  | 7.759% | 0.92241 | 14.91% | [5 empty] | Non-TXV | 7.759%
Arbuckle | CA | 95912-9542 |  | 2013-07-31 | 2013-07-31 15:03 | 2013-07-31 15:28 | OTHER - 38CKC036350 | 70 | 4.4 | Yes | Yes | 15 | 17.5 | -2.5 | C50F1F2DE4B64E93BF56744CD7BB9330 |  | R22 | TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | TXV | 6.286%
Fresno | CA | 93710-4309 |  | 2013-06-24 | 2013-06-24 11:54 | 2013-06-24 12:14 | CARRIER - 48SX-036080321AA | 83 | 3.6 | Yes | Yes | 19.3 | 21 | -1.7 | 9DCD0AC45BA7450590D7D737B6AAA48F |  | R22 | Non-TXV |  | 4.337% | 0.95663 | 8.335% | [5 empty] | Non-TXV | 4.337%
Stockton | CA | 95204-4947 |  | 2013-06-01 | 2013-06-01 08:41 | 2013-06-01 08:41 | RHEEM - 13AJN48A01 | 116 | 0 | Yes | Yes | 19 | 19.8 | -0.8 | B42AA040E20E48CEAAA13C8168366D4C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1440 |  | 2013-06-03 | 2013-06-03 15:09 | 2013-06-03 15:28 | HEIL - CA5036VKB1 | 86 | 4.7 | Yes | Yes | 27 | 23 | 4 | 7404AFD7255E4305BD5B7E9638FC3596 |  | R22 | Non-TXV |  | 5.465% | 0.94535 | 10.5% | [5 empty] | Non-TXV | 5.465%
Stockton | CA | 95203-3166 |  | 2013-05-30 | 2013-05-30 10:05 | 2013-05-30 10:23 | GOODMAN - GSC130241DA | 83 | 2.9 | Yes | Yes | 15.9 | 18.8 | -2.9 | 5065BC04D06643469C0568ADA6992434 |  | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
Los Banos | CA | 93635-6426 |  | 2013-07-29 | 2013-07-29 15:12 | 2013-07-29 15:21 | BRYANT - 563CN060-G | 204 | 8.7 | Yes | Yes | 20.3 | 19.3 | 1 | 23BDEDCB9F2B4272814CE5E3266D2F24 |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Los Banos | CA | 93635-6426 |  | 2013-06-01 | 2013-06-01 13:36 | 2013-06-01 13:45 | BRYANT - 563CN060 | 200 | 9.4 | Yes | Yes | 23.3 | 21.9 | 1.4 | E590CDA5907340939723597AB25AD641 |  | R22 | TXV |  | 4.7% | 0.953 | 9.032% | [5 empty] | TXV | 4.7%
Clovis | CA | 93611-0612 |  | 2013-06-12 | 2013-06-12 09:46 | 2013-06-12 10:15 | OTHER - DDYZ-F048N110A | 68 | 3.4 | Yes | Yes | 19 | 19.8 | -0.8 | 8915F4EB77674B0FAE76F565AA4462A6 |  | R410A | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Yuba City | CA | 95993-9140 |  | 2013-05-31 | 2013-05-31 13:26 | 2013-05-31 13:43 | CARRIER - 38BRC048370 | 141 | 41.6 | Yes | Yes | 23.3 | 23.1 | 0.2 | 30E87593A1404390A0958ECFBAF14937 |  | R22 | Non-TXV |  | 29.5% | 0.70496 | 56.7% | [5 empty] | Non-TXV | 29.5%
Stockton | CA | 95206-4803 |  | 2013-08-22 | 2013-08-22 14:55 | 2013-08-22 15:18 | DAY & NIGHT - 565J36-D | 76 | 4.6 | Yes | Yes | 26.5 | 20.6 | 5.9 | 82FC22837A36489E983CB2168074527D |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
Oroville | CA | 95965-9672 |  | 2013-06-19 | 2013-06-19 18:41 | 2013-06-19 19:08 | BRYANT - 582AJW048090AAAG | 81 | 3 | Yes | Yes | 23.4 | 19.3 | 4.2 | 3F73099FFE9A4FECA6C14AB72FAEF72F |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Fresno | CA | 93726-1638 |  | 2013-06-06 | 2013-06-06 12:43 | 2013-06-06 13:03 | OTHER - AA5H50E0200AV5610107 | 93 | 3.6 | Yes | Yes | 18.6 | 20.8 | -2.2 | 3397F1F6803540CDA912F00ED996FDA3 |  | R22 | Non-TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | Non-TXV | 3.871%
Stockton | CA | 95210-3720 |  | 2013-06-05 | 2013-06-05 08:35 | 2013-06-05 08:54 | GUARDIAN - GCGD30S41S3A | 62 | -4.4 | Yes | Yes | 22.3 | 18.2 | 4.1 | 54C941DFD729486B913E5ACFAA9A740B |  | R410A | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Los Banos | CA | 93635-2806 |  | 2013-05-28 | 2013-05-28 10:45 | 2013-05-28 10:52 | CARRIER - 38CK030300 | 69 | 10.1 | Yes | Yes | 24.6 | 19.1 | 5.5 | A027B1A72B81411C80CBFD844D7CC60B |  | R22 | Non-TXV |  | 14.64% | 0.85362 | 28.13% | [5 empty] | Non-TXV | 14.64%
Fresno | CA | 93720-2562 |  | 2013-07-11 | 2013-07-11 17:04 | 2013-07-11 18:14 | ICP - CA5042VKA1 | 135 | 10.9 | Yes | Yes | 25.5 | 21.5 | 4.1 | A85E276B65844AF6A4A7BD54326FF0A3 |  | R22 | Non-TXV |  | 8.074% | 0.91926 | 15.52% | [5 empty] | Non-TXV | 8.074%
Auburn | CA | 95602-8403 |  | 2013-06-12 | 2013-06-12 11:28 | 2013-06-12 11:50 | GE - UNK | 36 | 2.6 | Yes | Yes | 19.5 | 19.5 | 0.1 | 5FBA579A9220454982479355106CAE4F |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Stockton | CA | 95203-3177 |  | 2013-05-29 | 2013-05-29 15:27 | 2013-05-29 15:44 | DAY & NIGHT - 585GJA018040ABAC | 55 | 3.6 | Yes | Yes | 20 | 19.6 | 0.4 | D219105CEBDC471CAAB9C4C99B7BE7DE |  | R22 | Non-TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | Non-TXV | 6.545%
Fresno | CA | 93703-1226 |  | 2013-05-29 | 2013-05-29 02:03 | 2013-05-29 02:03 | CARRIER - 480L048=77 | 85 | 0 | Yes | Yes | 26.7 | 21 | 5.7 | BDA66833D2D443488097D676A4C847C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-4451 |  | 2013-08-21 | 2013-08-21 13:34 | 2013-08-21 13:58 | BRYANT - 563CN030-B | 100 | 10.1 | Yes | Yes | 19 | 18.8 | 0.2 | DA10674013844548AA420C13B34657A2 |  | R22 | Non-TXV |  | 10.1% | 0.899 | 19.41% | [5 empty] | Non-TXV | 10.1%
Fresno | CA | 93726-7423 |  | 2013-06-07 | 2013-06-07 13:56 | 2013-06-07 21:11 | AIRE-FLO - N/A | 100 | 3.2 | Yes | Yes | 22.3 | 18.8 | 3.5 | 62B5F67664AA48B1927850B96B71231F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Merced | CA | 95340-3383 |  | 2013-06-17 | 2013-06-17 09:59 | 2013-06-17 10:07 | RHEEM - UNK | 76 | 8.2 | Yes | Yes | 21.7 | 18.8 | 2.9 | 984626674CD4428F87B09D3F65BC06C9 |  | R22 | Non-TXV |  | 10.79% | 0.89211 | 20.73% | [5 empty] | Non-TXV | 10.79%
Stockton | CA | 95210-2600 |  | 2013-06-12 | 2013-06-12 12:48 | 2013-06-12 13:06 | PAYNE - COMPRESSOR/ZP31K5E-PFV-130 | 64 | -4.5 | Yes | Yes | 25 | 20.8 | 4.2 | 48F7D7F2E19D435297F8AD08A0973B52 |  | R410A | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Ione | CA | 95640-5100 |  | 2013-08-01 | 2013-08-01 10:54 | 2013-08-01 10:54 | OTHER - NAMC-F048AB | 116 | 0 | Yes | Yes | 22 | 17.2 | 4.8 | 1D8A3DE53CA74A9FA8EE42B21A2043B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4621 |  | 2013-05-31 | 2013-05-31 15:27 | 2013-05-31 15:45 | RHEEM - RRKA-A024JK06E | 50 | 9.9 | Yes | Yes | 22 | 21.9 | 0.1 | 9B4F32F5272B4C448C443747223B4E0C |  | R22 | Non-TXV |  | 19.8% | 0.802 | 38.05% | [5 empty] | Non-TXV | 19.8%
Merced | CA | 95341-5223 |  | 2013-08-23 | 2013-08-23 14:55 | 2013-08-23 14:56 | RHEEM - RRMA0A036JK08E | 100 | 3.4 | Yes | Yes | 20.9 | 21.2 | -0.3 | 3DE3E354A2CC414C84230D9441EA203C |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
El Dorado Hills | CA | 95762-5916 |  | 2013-06-01 | 2013-06-01 09:41 | 2013-06-01 10:05 | RHEEM - RAFO-031JAS | 64 | 9.7 | Yes | Yes | 20 | 19.3 | 0.7 | 87E1B81CB4574B2BACE180C6C91AEE00 |  | R22 | Non-TXV |  | 15.16% | 0.84844 | 29.13% | [5 empty] | Non-TXV | 15.16%
El Dorado Hills | CA | 95762-5916 |  | 2013-06-01 | 2013-06-01 10:08 | 2013-06-01 10:30 | RHEEM - RAFD-042JBS | 79 | 5.4 | Yes | Yes | 19 | 20.3 | -1.3 | 5CB9023B48D7477E9F380E9ACA43CDAC |  | R22 | Non-TXV |  | 6.835% | 0.93165 | 13.14% | [5 empty] | Non-TXV | 6.835%
Fresno | CA | 93730-5122 |  | 2013-08-12 | 2013-08-12 08:59 | 2013-08-12 09:00 | OTHER - EADC048JAS | 113 | 10.1 | Yes | Yes | 21.8 | 19.2 | 2.6 | 59574A938F50471C8C78A77591BB2637 |  | R22 | Non-TXV |  | 8.938% | 0.91062 | 17.18% | [5 empty] | Non-TXV | 8.938%
Rocklin | CA | 95765-4130 |  | 2013-06-15 | 2013-06-15 15:30 | 2013-06-15 15:30 | CARRIER - 38BRG030300 | 100 | 0 | Yes | Yes | 22.8 | 20.7 | 2.1 | 4DD595AAF66941B499E28265F725AA0A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1713 |  | 2013-06-04 | 2013-06-04 11:38 | 2013-06-04 12:06 | RHEEM - RAHE-048JAS | 114 | 13.6 | Yes | Yes | 21.5 | 20.2 | 1.3 | 24C017744234473DACDF5B7AC87A6507 |  | R22 | Non-TXV |  | 11.93% | 0.8807 | 22.93% | [5 empty] | Non-TXV | 11.93%
Marysville | CA | 95901-5414 |  | 2013-06-03 | 2013-06-03 13:52 | 2013-06-03 14:23 | OTHER - SU12G24A | 73 | 13.1 | Yes | Yes | 28 | 23 | 5 | 8674E37A976941B996E94992D1C10EB7 |  | R22 | Non-TXV |  | 17.95% | 0.82055 | 34.49% | [5 empty] | Non-TXV | 17.95%
Chico | CA | 95926-4389 |  | 2013-09-13 | 2013-09-13 09:20 | 2013-09-13 09:43 | YORK - H4DB024S06A | 50 | 1.6 | Yes | Yes | 20.6 | 17.7 | 2.9 | E909970C6F534D60917ED70482DCC12F |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93726-6080 |  | 2013-06-18 | 2013-06-18 13:35 | 2013-06-18 13:37 | AMANA - PGD24C0452E | 74 | 4.3 | Yes | Yes | 26.3 | 20.3 | 6 | 569839C2CA434876A923593764EF903C |  | R22 | Non-TXV |  | 5.811% | 0.94189 | 11.17% | [5 empty] | Non-TXV | 5.811%
Fresno | CA | 93726-2910 |  | 2013-06-18 | 2013-06-18 14:08 | 2013-06-18 14:10 | ARCOAIRE - HAC036AKA1 | 80 | 2.9 | Yes | Yes | 23.3 | 21.5 | 1.8 | B40BBB906F8C4C06B5B238F32A46ECAF |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Stockton | CA | 95210-3485 |  | 2013-06-13 | 2013-06-13 11:37 | 2013-06-13 11:54 | GOODMAN - GPG13300701BB | 77 | 3.8 | Yes | Yes | 23.4 | 20.6 | 2.8 | A5377FD0580D49E388A88D9DF0D1F8E9 |  | R22 | Non-TXV |  | 4.935% | 0.95065 | 9.484% | [5 empty] | Non-TXV | 4.935%
Clovis | CA | 93611-3806 |  | 2013-07-02 | 2013-07-02 13:11 | 2013-07-02 14:02 | LENNOX - 13ACD-048-230-01 | 204 | 9.2 | Yes | Yes | 21.2 | 20.6 | 0.6 | 06F61A61876446658D83B8963977EF8E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.51% | 0.9549 | 8.667% | [5 empty] | Non-TXV | 4.51%
Dinuba | CA | 93618-1801 |  | 2013-07-26 | 2013-07-26 20:07 | 2013-07-26 22:13 | BDP - 585CJO36075 | 70 | 4.4 | Yes | Yes | 17.3 | 17.1 | 0.2 | 16CEC23F5A1748A7AFB073F0E6E120C1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Lincoln | CA | 95648-8245 |  | 2013-06-14 | 2013-06-14 17:41 | 2013-06-14 18:14 | CARRIER - 38CKC030340 | 68 | 12.6 | Yes | Yes | 19.3 | 21.7 | -2.4 | 658337245F3D445C8B5695A8A2247E77 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.53% | 0.81471 | 35.61% | [5 empty] | Non-TXV | 18.53%
Fresno | CA | 93726-6755 |  | 2013-06-25 | 2013-06-25 12:30 | 2013-06-25 12:34 | AMERICAN STANDARD - 4A7B3036D1000AA | 105 | 3.3 | Yes | Yes | 20.3 | 18.8 | 1.5 | 28864F42FC304E17A9CD0BE6778984A4 |  | R410A | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Marysville | CA | 95901-4442 |  | 2013-06-04 | 2013-06-04 08:40 | 2013-06-04 09:08 | ALLEGIANCE - 581BJV036072AAAA | 90 | 2.7 | Yes | Yes | 25 | 19.7 | 5.3 | 383405455C0B4489967AA899E803DBF6 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93611-6825 |  | 2013-06-15 | 2013-06-15 11:37 | 2013-06-15 12:10 | CARRIER - 38TDA036300 | 184 | 6 | Yes | Yes | 19.8 | 21.4 | -1.6 | EA59D2805B454FC9868360CAB817749A |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Stockton | CA | 95212-3209 |  | 2013-06-17 | 2013-06-17 08:58 | 2013-06-17 09:23 | GOODMAN - CKJ48-1A | 118 | 3.7 | Yes | Yes | 20 | 19.7 | 0.3 | 3638410ACBA14C29A4E126A8FBE978DF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Stockton | CA | 95206-6136 |  | 2013-06-21 | 2013-06-21 14:35 | 2013-06-21 14:52 | YORK - H1RA042S06D | 84 | 5 | Yes | Yes | 19.8 | 18.5 | 1.3 | BFB9304C71E049C6B1C9C88DDC01A23F |  | R22 | TXV |  | 5.952% | 0.94048 | 11.44% | [5 empty] | TXV | 5.952%
Tracy | CA | 95376-2541 |  | 2013-05-24 | 2013-05-24 15:35 | 2013-05-24 15:35 | PAYNE - 3680YAC108C | 66 | 0 | Yes | Yes | 20.8 | 22.9 | -2.1 | 9CF2BB93E95942B1AB407AD12893F668 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakhurst | CA | 93644-9511 |  | 2013-09-16 | 2013-09-16 11:02 | 2013-09-16 11:04 | RUUD - URGG-05E31JKR | 48 | 2.6 | Yes | Yes | 26.1 | 20.4 | 5.7 | 62C240BB84144E2BB7C35DBD410B6E67 |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Tracy | CA | 95376-4444 |  | 2013-05-29 | 2013-05-29 10:20 | 2013-05-29 10:43 | DAY & NIGHT - 568EJX036000AGAA | 190 | 6.7 | Yes | Yes | 24.1 | 18.2 | 5.9 | 52F413686DE8460083F3064BFCC519C1 |  | R22 | Non-TXV |  | 3.526% | 0.96474 | 6.777% | [5 empty] | Non-TXV | 3.526%
Clovis | CA | 93611-3007 |  | 2013-08-06 | 2013-08-06 09:36 | 2013-08-06 09:37 | YORK - D2NP036N05606NXA | 108 | 7.9 | Yes | Yes | 23.6 | 18.2 | 5.4 | 19216FAAED01481CBAA792FFAC1EF1A5 |  | R22 | Non-TXV |  | 7.315% | 0.92685 | 14.06% | [5 empty] | Non-TXV | 7.315%
Fresno | CA | 93727-3674 |  | 2013-07-19 | 2013-07-19 09:27 | 2013-07-19 10:13 | LENNOX - 10GCS036X-75-3PB | 58 | 2.1 | Yes | Yes | 23 | 20.4 | 2.6 | E2948C6F396049CB89D85BC87F4B75C7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.621% | 0.96379 | 6.958% | [5 empty] | Non-TXV | 3.621%
Stockton | CA | 95204-2615 |  | 2013-06-03 | 2013-06-03 15:23 | 2013-06-03 15:50 | YORK - H2DR024S06B | 88 | 4.4 | Yes | Yes | 17 | 17.7 | -0.7 | D7EBCE0174DA431F940A27DA3852DD3A |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Madera | CA | 93637-5003 |  | 2013-07-25 | 2013-07-25 05:06 | 2013-07-25 08:55 | - PGB0242100-1REV A | 85 | 3.9 | Yes | Yes | 19.5 | 20.1 | -0.6 | AD580F6388304519BAB96D7F54268E0E |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Fresno | CA | 93710-4107 |  | 2013-06-07 | 2013-06-07 09:35 | 2013-06-07 09:57 | YORK - D4CG048N06206A | 80 | 3.3 | Yes | Yes | 18.2 | 19.6 | -1.4 | 2662CB0CC4734050A10E7906E44BA0E2 |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Fresno | CA | 93727-3653 |  | 2013-06-13 | 2013-06-13 10:50 | 2013-06-13 10:52 | LENNOX - 10GC036-75-1PA | 58 | 4.3 | Yes | Yes | 27.5 | 21.5 | 6 | 4077109D1ED34D349BFC31653768D773 |  | R22 | Non-TXV |  | 7.414% | 0.92586 | 14.25% | [5 empty] | Non-TXV | 7.414%
Stockton | CA | 95205-7844 |  | 2013-06-05 | 2013-06-05 12:55 | 2013-06-05 13:20 | TRANE - YCC024F1L0BA | 64 | 5 | Yes | Yes | 18.2 | 17.9 | 0.3 | 26069E66250D4BBAAFB89CD4AC23D6A9 |  | R22 | Non-TXV |  | 7.812% | 0.92188 | 15.01% | [5 empty] | Non-TXV | 7.812%
Los Banos | CA | 93635-9431 |  | 2013-06-13 | 2013-06-13 09:31 | 2013-06-13 09:33 | BRYANT - 561CJ060 | 152 | 13.9 | Yes | Yes | 21.1 | 20.2 | 0.9 | B74CFF687C2245AE895213D8D6178A37 |  | R22 | TXV |  | 9.145% | 0.90855 | 17.57% | [5 empty] | TXV | 9.145%
Fresno | CA | 93703-3705 |  | 2013-06-03 | 2013-06-03 16:30 | 2013-06-03 20:31 | YORK - DYCP-F024N045A | 100 | 3 | Yes | Yes | 19 | 21 | -2 | 1A6FB2ECB2D64662A6E35A9B39F9D328 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93727-0000 |  | 2013-06-11 | 2013-06-11 14:42 | 2013-06-11 15:06 | LENNOX - 13ACD-048-230-02 | 204 | 6 | Yes | Yes | 23.6 | 20.1 | 3.5 | 5A640E2B9BAD401E9C72CA005C807D2A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Clovis | CA | 93611-5123 |  | 2013-06-14 | 2013-06-14 11:03 | 2013-06-14 11:45 | ICP - PGF042K0808 | 87 | 2.7 | Yes | Yes | 19.3 | 18.9 | 0.4 | CCFFE95FF4964DD096DEA2457015C2A3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Chico | CA | 95928-6067 |  | 2013-08-01 | 2013-08-01 10:19 | 2013-08-01 10:51 | LUXAIRE - HAMC-F036SA | 92 | 9.5 | Yes | Yes | 18.9 | 18.7 | 0.2 | 865B4A70292944C69DEDC04697E95183 |  | R22 | Non-TXV |  | 10.33% | 0.89674 | 19.84% | [5 empty] | Non-TXV | 10.33%
Atwater | CA | 95301-2287 |  | 2013-06-05 | 2013-06-05 11:38 | 2013-06-05 11:41 | GOODMAN - PGB042075 | 68 | 3.6 | Yes | Yes | 23.6 | 19.9 | 3.7 | 4D885E99684F4AD1A9144F1B71D458BE |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Stockton | CA | 95206-6325 |  | 2013-06-21 | 2013-06-21 14:01 | 2013-06-21 14:01 | YORK - H4DE036S06A | 82 | 0 | Yes | Yes | 20.9 | 20.8 | 0.1 | 4A06A92B665B4A19B1A12F911C956AD1 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-3358 |  | 2013-06-05 | 2013-06-05 09:46 | 2013-06-05 10:06 | GOODMAN - CRT36-1A | 140 | 9.7 | Yes | Yes | 22.7 | 19.6 | 3.1 | 1C06D03C4F8248FEBB9826CD42309DF1 |  | R22 | Non-TXV |  | 6.929% | 0.93071 | 13.32% | [5 empty] | Non-TXV | 6.929%
Stockton | CA | 95212-3100 |  | 2013-06-21 | 2013-06-21 10:55 | 2013-06-21 11:21 | YORK - H1RC060SD | 147 | 4.4 | Yes | Yes | 23.3 | 20.4 | 2.9 | 5C4C4A23462E48058E58CBC025A76087 |  | R22 | Non-TXV |  | 2.993% | 0.97007 | 5.752% | [5 empty] | Non-TXV | 2.993%
Manteca | CA | 95336-2810 |  | 2013-06-28 | 2013-06-28 11:24 | 2013-06-28 11:53 | ARMSTRONG - SCU10G36A-1 | 85 | 12.6 | Yes | Yes | 20.2 | 19.2 | 1.1 | 696640B308524942A0840C0B69EE9399 |  | R22 | Non-TXV |  | 14.82% | 0.85176 | 28.49% | [5 empty] | Non-TXV | 14.82%
Tracy | CA | 95377-2202 |  | 2013-05-31 | 2013-05-31 08:23 | 2013-05-31 08:40 | YORK - H2RA030S06D | 62 | 2.4 | Yes | Yes | 21.9 | 19.8 | 2.1 | 28542D5815A44705A93AB0CE32416A77 |  | R22 | Non-TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | Non-TXV | 3.871%
Stockton | CA | 95210-3137 |  | 2013-07-01 | 2013-07-01 12:43 | 2013-07-01 20:05 | DAY & NIGHT - 77CD030300 | 88 | -5.2 | Yes | Yes | 20.1 | 16.8 | 3.3 | 85D76B468B934DD5BE1041D199716870 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Sutter Creek | CA | 95685-9756 |  | 2013-09-17 | 2013-09-17 10:45 | 2013-09-17 11:32 | RHEEM - RRNA-B036JK08X | 83 | 5.2 | Yes | Yes | 17.6 | 19.9 | -2.3 | ECC5CF2CE56B42FE9B0E4ABCBCD69D43 |  | R22 | Non-TXV |  | 6.265% | 0.93735 | 12.04% | [5 empty] | Non-TXV | 6.265%
Atwater | CA | 95301-4764 |  | 2013-07-10 | 2013-07-10 10:52 | 2013-07-10 10:54 | AMERICAN STANDARD - YCC030F1M0BB | 69 | 4.5 | Yes | Yes | 19.3 | 22.1 | -2.8 | 4E3B170874BC40829F49520A968772EA |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Stockton | CA | 95206-5721 |  | 2013-06-26 | 2013-06-26 08:35 | 2013-06-26 09:02 | BRYANT - 561CJ048-A | 159 | 6.5 | Yes | Yes | 22.4 | 16.6 | 5.8 | 507A311049D9447EB5F43A65EAC450F4 |  | R22 | Non-TXV |  | 4.088% | 0.95912 | 7.856% | [5 empty] | Non-TXV | 4.088%
Tracy | CA | 95377-8239 |  | 2013-06-05 | 2013-06-05 13:47 | 2013-06-05 14:22 | DAY & NIGHT - 598WN036-A | 264 | 9.3 | Yes | Yes | 21.4 | 19.6 | 1.9 | 4F7EC7B2E94448488159F15605B8EB02 |  | R22 | Non-TXV |  | 3.523% | 0.96477 | 6.77% | [5 empty] | Non-TXV | 3.523%
Clovis | CA | 93612-2428 |  | 2013-06-28 | 2013-06-28 15:00 | 2013-06-28 15:33 | AMERICAN STANDARD - YCC042F1M0BF | 101 | 4.7 | Yes | Yes | 17.1 | 18.8 | -1.7 | 416CE2CBC5094252BA52E7373124F03B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.653% | 0.95347 | 8.943% | [5 empty] | Non-TXV | 4.653%
Madera | CA | 93637-5933 |  | 2013-06-18 | 2013-06-18 11:39 | 2013-06-18 12:14 | CARRIER - 38BR048300-- | 161 | 5.5 | Yes | Yes | 19 | 21 | -2 | 3253DD1F2EEA4F3098051D567C09C196 |  | R22 | Non-TXV |  | 3.416% | 0.96584 | 6.565% | [5 empty] | Non-TXV | 3.416%
Tracy | CA | 95377-7067 |  | 2013-05-31 | 2013-05-31 09:07 | 2013-05-31 09:41 | BRYANT - 561CJ060-A | 233 | 14.4 | Yes | Yes | 24 | 21.7 | 2.3 | 323724A312664AE8AA00EA021F02C959 |  | R22 | Non-TXV |  | 6.18% | 0.9382 | 11.88% | [5 empty] | Non-TXV | 6.18%
Grass Valley | CA | 95949-9400 |  | 2013-06-22 | 2013-06-22 13:37 | 2013-06-22 13:37 | TRANE - 2TR2060A1000AA | 125 | 0 | Yes | Yes | 19 | 19.7 | -0.7 | EDDF43421B144BD89E8B6E3A467C8D9B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-9400 |  | 2013-06-22 | 2013-06-22 13:46 | 2013-06-22 14:02 | TRANE - 2TTR2036A1000AA | 96 | 2.8 | Yes | Yes | 22 | 20.2 | 1.8 | 0C4E22C1F0AF41A4953C3DAB14DA3F90 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Stockton | CA | 95206-5528 |  | 2013-06-26 | 2013-06-26 09:52 | 2013-06-26 10:22 | PAYNE - 591ANX042000ABAA | 112 | 10 | Yes | Yes | 19.3 | 19.5 | -0.2 | 97B98BB5618142F1A5770344BAA6F8BF |  | R22 | Non-TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | Non-TXV | 8.929%
Red Bluff | CA | 96080-8859 |  | 2013-08-09 | 2013-08-09 15:48 | 2013-08-09 19:45 | DAY & NIGHT - 56BNN036080BF | 160 | 4.9 | Yes | Yes | 24.2 | 19.8 | 4.4 | 14195D0D3CFD4D7E9475053FD503A860 |  | R22 | Non-TXV |  | 3.062% | 0.96937 | 5.885% | [5 empty] | Non-TXV | 3.062%
Fresno | CA | 93710-3954 |  | 2013-06-11 | 2013-06-11 13:16 | 2013-06-11 14:53 | BDP - 585EJW04205AAAF | 85 | 3.7 | Yes | Yes | 15.8 | 18.5 | -2.7 | 595DB4ABCB2F47028D356FDA0E9EDB37 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Willows | CA | 95988-3329 |  | 2013-08-14 | 2013-08-14 13:18 | 2013-08-14 17:45 | YORK - H4DB036S06A | 73 | 4.1 | Yes | Yes | 22.5 | 21.4 | 1.1 | 79201CF8AB5E423EB007FE533C2AC3CF |  | R22 | Non-TXV |  | 5.616% | 0.94384 | 10.79% | [5 empty] | Non-TXV | 5.616%
Stockton | CA | 95206-5121 |  | 2013-06-21 | 2013-06-21 08:40 | 2013-06-21 09:02 | RUUD - UAFD-048JBS | 85 | 7 | Yes | Yes | 24 | 19.8 | 4.2 | 11A45D316E7A4DC2B4D6868C3FB7E75C |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Paradise | CA | 95969-4865 |  | 2013-08-30 | 2013-08-30 15:58 | 2013-08-30 18:27 | COLEMAN - BRCS0421BDG | 84 | 3.3 | Yes | Yes | 18.1 | 21 | -2.9 | C57A54B156564C34A78EC1536DE71FE5 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Chico | CA | 95973-7688 |  | 2013-06-04 | 2013-06-04 18:45 | 2013-06-04 18:45 | LENNOX - 10ACB36-11P | 80 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | 966A53020EE642C99E67ED803B231E74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-7411 |  | 2013-06-25 | 2013-06-25 13:38 | 2013-06-25 13:40 | RHEEM - RAKA-060JAZ | 112 | 5.5 | Yes | Yes | 24.4 | 18.5 | 5.9 | 645AABFE7DAC4CFE935CC3FBA062EBAC |  | R22 | Non-TXV |  | 4.911% | 0.95089 | 9.437% | [5 empty] | Non-TXV | 4.911%
Stockton | CA | 95206-4835 |  | 2013-06-20 | 2013-06-20 10:42 | 2013-06-20 11:12 | GOODMAN - GSC1330361A | 85 | 10 | Yes | Yes | 18 | 20.2 | -2.2 | 936BEDC787D549EFBE4F3292E9451D0F |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Stockton | CA | 95206-6072 |  | 2013-06-20 | 2013-06-20 08:47 | 2013-06-20 08:51 | GOODMAN - CLJ48-1A | 130 | 12.7 | Yes | Yes | 20.6 | 19.7 | 1 | 158D60C273DC45C38777C9FBBE1E2A90 |  | R22 | TXV |  | 9.769% | 0.90231 | 18.77% | [5 empty] | TXV | 9.769%
Penn Valley | CA | 95946-9325 |  | 2013-09-18 | 2013-09-18 14:05 | 2013-09-18 14:05 | - GR4GA-036K072X | 60 | 0 | Yes | Yes | 24.9 | 21.4 | 3.6 | AB758281354542A4A967A143C6A61E8E |  | R22 | TXV |  | 0% | 1 | 0%
Pollock Pines | CA | 95726-9045 |  | 2013-07-29 | 2013-07-29 09:21 | 2013-07-29 09:21 | OTHER - FAFF-049JAZ | 163 | 0 | Yes | Yes | 22 | 23.1 | -1.1 | 605E802F0BC6452DA13E35A9376F6C2C |  | R22 | TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-4568 |  | 2013-07-08 | 2013-07-08 10:46 | 2013-07-08 11:12 | GOODMAN - CKL36-1H | 71 | -4.2 | Yes | Yes | 20 | 21 | -1 | 8A71CD6C955645DF86F2EA6327676547 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Stockton | CA | 95209-2227 |  | 2013-08-21 | 2013-08-21 11:20 | 2013-08-21 11:43 | PAYNE - UNK | 124 | 16.2 | Yes | Yes | 22 | 19.3 | 2.7 | 6B1A3FBE04454046B1059EC91028D358 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.06% | 0.86935 | 25.11% | [5 empty] | Non-TXV | 13.06%
Oroville | CA | 95966-9008 |  | 2013-06-20 | 2013-06-20 19:14 | 2013-06-20 19:33 | COLEMAN - DRCS0421BE | 109 | 4.4 | Yes | Yes | 17.2 | 19.4 | -2.2 | 3E02E8ED0921440C966815A62DA936D5 |  | R22 | Non-TXV |  | 4.037% | 0.95963 | 7.758% | [5 empty] | Non-TXV | 4.037%
Paradise | CA | 95969-5678 |  | 2013-06-12 | 2013-06-12 09:01 | 2013-06-12 09:24 | YORK - MC24-10A | 54 | 7 | Yes | Yes | 22.2 | 20.1 | 2.2 | 135C735B356947A8B368AA0A1FFC4D76 |  | R22 | Non-TXV |  | 12.96% | 0.87037 | 24.91% | [5 empty] | Non-TXV | 12.96%
Rocklin | CA | 95765-1749 |  | 2013-08-10 | 2013-08-10 09:57 | 2013-08-10 10:14 | TRANE - TTB7448A100A0 | 104 | 16.8 | Yes | Yes | 17 | 18.8 | -1.8 | E56B6EA020244078A609F7E2C2491E7E |  | R22 | TXV |  | 16.15% | 0.83846 | 31.04% | [5 empty] | TXV | 16.15%
Tracy | CA | 95376-2708 |  | 2013-05-28 | 2013-05-28 11:38 | 2013-05-28 11:57 | CARRIER - UNK | 68 | 10 | Yes | Yes | 23.7 | 18.8 | 4.9 | 4E1BDC7687BE4366A9231B08D4047EDC |  | R22 | Non-TXV |  | 14.71% | 0.85294 | 28.26% | [5 empty] | Non-TXV | 14.71%
Auburn | CA | 95603-3427 |  | 2013-06-04 | 2013-06-04 14:28 | 2013-06-04 14:48 | TRANE - 2A7A2048A1000AA | 120 | 10.6 | Yes | Yes | 25.1 | 19.1 | 6 | 69A16FE91AF141B4B0E807BAF33371C6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.833% | 0.91167 | 16.98% | [5 empty] | Non-TXV | 8.833%
El Dorado Hills | CA | 95762-5840 |  | 2013-06-01 | 2013-06-01 12:53 | 2013-06-01 13:14 | YORK - H1DE060S06B | 122 | 3.7 | Yes | Yes | 21 | 21 | 0 | 96DB0347BA6445899AB077277AEC0EA5 |  | R22 | Non-TXV |  | 3.033% | 0.96967 | 5.828% | [5 empty] | Non-TXV | 3.033%
Los Banos | CA | 93635-7427 |  | 2013-06-13 | 2013-06-13 14:00 | 2013-06-13 14:13 | PAYNE - PA13NR030000AEAA | 86 | 8.1 | Yes | Yes | 22.1 | 21.5 | 0.6 | 833698C583DD46A6B9091614A685E68E |  | R22 | TXV |  | 9.419% | 0.90581 | 18.1% | [5 empty] | TXV | 9.419%
Los Banos | CA | 93635-6439 |  | 2013-06-03 | 2013-06-03 14:07 | 2013-06-03 14:25 | BRYANT - 563CN048 | 136 | 6.9 | Yes | Yes | 15.3 | 16.3 | -1 | 73E0DB4799824FBBA621E965A08F7572 |  | R22 | TXV |  | 5.074% | 0.94926 | 9.75% | [5 empty] | TXV | 5.074%
Fresno | CA | 93720-0117 |  | 2013-06-20 | 2013-06-20 14:17 | 2013-06-20 14:26 | RUUD - UAFD042JBS | 60 | 7.7 | Yes | Yes | 24.4 | 22.5 | 1.9 | 668B1732F6A34FC9B4D0A029EA62322B |  | R22 | Non-TXV |  | 12.83% | 0.87167 | 24.66% | [5 empty] | Non-TXV | 12.83%
Auburn | CA | 95602-8401 |  | 2013-06-27 | 2013-06-27 10:39 | 2013-06-27 10:39 | GE - BTB912A800A0 | 36 | 0 | Yes | Yes | 16.5 | 17.7 | -1.2 | F4D97669FDD247CDA7B6A3606113A3B5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-4829 |  | 2013-08-22 | 2013-08-22 15:34 | 2013-08-22 15:51 | GOODMAN - CKT42-1B | 134 | 4.3 | Yes | Yes | 24.1 | 19.1 | 5.1 | 701287679A8047B8AD53026687127B77 |  | R22 | Non-TXV |  | 3.209% | 0.96791 | 6.167% | [5 empty] | Non-TXV | 3.209%
Madera | CA | 93637-5935 |  | 2013-06-18 | 2013-06-18 10:38 | 2013-06-18 11:12 | CARRIER - 48SS-036060331 | 67 | -6.3 | Yes | Yes | 15.8 | 17.4 | -1.6 | B2E49959348E4230B9366C1782347119 |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Pine Grove | CA | 95665-9750 |  | 2013-08-09 | 2013-08-09 10:20 | 2013-08-09 10:20 | CARRIER - 48GS-030060301-- | 59 | 0 | Yes | Yes | 23.6 | 20.1 | 3.5 | 63ED11D45B68498580BAF5AF5FCCD8E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pine Grove | CA | 95665-9750 |  | 2013-08-09 | 2013-08-09 10:43 | 2013-08-09 10:43 | CARRIER - 48SX-042080311AA | 91 | 0 | Yes | Yes | 22.7 | 20.1 | 2.6 | E1BB20E25566472C8A55548744530339 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5246 |  | 2013-06-06 | 2013-06-06 17:20 | 2013-06-06 17:45 | BRYANT - 583ANW036090AAAF | 82 | 9.1 | Yes | Yes | 19.8 | 17.5 | 2.3 | 041F91862B0241EF96CF79C20556E335 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.1% | 0.88902 | 21.33% | [5 empty] | Non-TXV | 11.1%
Stockton | CA | 95212-3425 |  | 2013-06-17 | 2013-06-17 09:25 | 2013-06-17 09:25 | CARRIER - 38CKC048360 | 97 | 0 | Yes | Yes | 17.1 | 18.8 | -1.7 | 6F752434AC264480A1E7A0329E3F20C8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-2350 |  | 2013-08-07 | 2013-08-07 10:23 | 2013-08-07 10:40 | ICP - HAC042AKC3 | 98 | 4.4 | Yes | Yes | 19.6 | 17.7 | 1.9 | 7CF3DC621EA04BE996ACAD924ADE5C79 |  | R22 | Non-TXV |  | 4.49% | 0.9551 | 8.628% | [5 empty] | Non-TXV | 4.49%
Stockton | CA | 95210-4230 |  | 2013-06-10 | 2013-06-10 14:05 | 2013-06-10 14:25 | PAYNE - PA13NR030-C | 117 | 3.6 | Yes | Yes | 24.1 | 20.1 | 4 | 575BDCE3ACB44006A3169C5DBAFBD73E |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Madera | CA | 93637-5954 |  | 2013-06-18 | 2013-06-18 17:40 | 2013-06-18 20:59 | CARRIER - 48GS-042060301 | 95 | 5 | Yes | Yes | 18.6 | 20.1 | -1.5 | B2E2692D757D42FCBBD53F22083FCE74 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Fresno | CA | 93727-7628 |  | 2013-10-09 | 2013-10-09 12:36 | 2013-10-09 13:52 | AMERICAN STANDARD - YCP036F1MOAB | 109 | 3.6 | Yes | Yes | 21.1 | 17.7 | 3.4 | 6AFEB77A527E4B648087EE405773432A |  | R22 | Non-TXV |  | 3.303% | 0.96697 | 6.347% | [5 empty] | Non-TXV | 3.303%
Marysville | CA | 95901-5453 |  | 2013-06-03 | 2013-06-03 12:56 | 2013-06-03 13:17 | OTHER - UNK | 85 | 2.5 | Yes | Yes | 20 | 21.4 | -1.4 | A1BB13CB1D7D4E089166D5DF8AE9D6CC |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Dinuba | CA | 93618-3124 |  | 2013-06-21 | 2013-06-21 14:11 | 2013-06-21 14:39 | UNITARY PRODUCTS GROUP - DBYP-F042N080A | 150 | 5 | Yes | Yes | 26.8 | 22.6 | 4.2 | E4A3279E036D41CCA6CA44C48090023C |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Dinuba | CA | 93618-3124 |  | 2013-06-21 | 2013-06-21 14:43 | 2013-06-21 15:02 | CARRIER - 587AN024060 | 65 | 8.6 | Yes | Yes | 23.1 | 23.2 | 0 | E6DF1744B0434F4DA8C336D20D9FF0CF |  | R22 | Non-TXV |  | 13.23% | 0.86769 | 25.43% | [5 empty] | Non-TXV | 13.23%
Los Banos | CA | 93635-6423 |  | 2013-06-04 | 2013-06-04 09:45 | 2013-06-04 09:53 | YORK - YCJD60S21S2A | 84 | 8 | Yes | Yes | 21.4 | 20.3 | 1.1 | 21507F925DD24C0EA239C2586BC18162 |  | R22 | Non-TXV |  | 9.524% | 0.90476 | 18.3% | [5 empty] | Non-TXV | 9.524%
Paso Robles | CA | 93446-0000 |  | 2013-08-06 | 2013-08-06 08:39 | 2013-08-06 09:05 | RHEEM - RAMB-042JBZ | 96 | -5.6 | Yes | Yes | 20.6 | 19.1 | 1.5 | 4037C18ACE1C4D9797C1C42E823F4553 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Madera | CA | 93637-5912 |  | 2013-07-12 | 2013-07-12 02:18 | 2013-07-12 02:18 | CARRIER - 48SS-0360603 | 70 | 0 | Yes | Yes | 18 | 20.2 | -2.2 | 1ECE7827AA2548A78BCB82380D3280F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6000 |  | 2013-06-27 | 2013-06-27 08:49 | 2013-06-27 09:30 | YORK - H2RA036S06D | 63 | -5.9 | Yes | Yes | 22.2 | 20.4 | 1.8 | EEF2BEA6B842448CBF8E54B1DC477513 |  | R22 | Non-TXV |  | -9.365% | 1.0937 | 2.623% |  |  |  |  | Non-TXV |  |  | -9.365%
Fresno | CA | 93703-3547 |  | 2013-09-04 | 2013-09-04 12:10 | 2013-09-04 12:12 | GOODMAN - GPG10300701A | 50 | 2.6 | Yes | Yes | 19.2 | 19 | 0.2 | 17579B590FF24EBFAEB526C3957865DF |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Dinuba | CA | 93618-1719 |  | 2013-06-24 | 2013-06-24 17:16 | 2013-06-24 17:50 | CARRIER - N/A | 150 | 4.6 | Yes | Yes | 18.3 | 19.9 | -1.6 | 31495004F6054A95AA8AAF3480D50CF5 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Madera | CA | 93636-8522 |  | 2013-07-10 | 2013-07-10 00:57 | 2013-07-10 01:36 | - 48KLA130BE | 85 | 5.3 | Yes | Yes | 20.2 | 22.1 | -1.9 | E9168DA468F44B8C91C318261F14EC57 |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Clovis | CA | 93612-0439 |  | 2013-06-15 | 2013-06-15 13:15 | 2013-06-15 13:48 | CARRIER - 48KLA136-321BE | 102 | 3.2 | Yes | Yes | 21.8 | 22.4 | -0.6 | 7CB48BAF22574BD39683576E425A75D9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Pioneer | CA | 95666-9573 |  | 2013-08-13 | 2013-08-13 11:36 | 2013-08-13 12:09 | CARRIER - 48SS-04210031 | 80 | 4.2 | Yes | Yes | 21.5 | 23.3 | -1.8 | C127509CE75A4BE3BF59A546C852291B |  | R22 | TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | TXV | 5.25%
Fresno | CA | 93720-0118 |  | 2013-07-12 | 2013-07-12 18:52 | 2013-07-12 19:33 | GOODMAN - CKL60-1 | 115 | 13.9 | Yes | Yes | 20.6 | 19.9 | 0.7 | 66E3DDB526B541D4ACF8296449B20E4B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.09% | 0.87913 | 23.23% | [5 empty] | Non-TXV | 12.09%
Livingston | CA | 95334-9618 |  | 2013-07-03 | 2013-07-03 09:04 | 2013-07-03 09:14 | GOODMAN - G8C130481BB | 102 | 7 | Yes | Yes | 23.9 | 19.9 | 4 | 16566F951F954CFB88B8AADF87151A5F |  | R22 | Non-TXV |  | 6.863% | 0.93137 | 13.19% | [5 empty] | Non-TXV | 6.863%
Livingston | CA | 95334-1020 |  | 2013-06-11 | 2013-06-11 13:48 | 2013-06-11 14:25 | GOODMAN - CJ30-1FB | 110 | 15.3 | Yes | Yes | 19.9 | 20.9 | -1 | 6E9AD01B34B34A148E5E7C63C7D6BE7F |  | R22 | Non-TXV |  | 13.91% | 0.86091 | 26.73% | [5 empty] | Non-TXV | 13.91%
Madera | CA | 93637-5932 |  | 2013-08-05 | 2013-08-05 15:11 | 2013-08-05 15:12 | YORK - D1NA042N05606A | 72 | 7.9 | Yes | Yes | 22.9 | 20.8 | 2.1 | D0E6D848FB10404794DD5C738885E7BC |  | R22 | Non-TXV |  | 10.97% | 0.89028 | 21.09% | [5 empty] | Non-TXV | 10.97%
Fresno | CA | 93727-3653 |  | 2013-06-13 | 2013-06-13 11:08 | 2013-06-13 11:10 | LENNOX - 10GCS036-75-1PA | 58 | 1.8 | Yes | Yes | 25.7 | 19.9 | 5.8 | E61E36169CE8459888B00DFBBFAB32EA |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Stockton | CA | 95210-5683 |  | 2013-05-29 | 2013-05-29 11:25 | 2013-05-29 11:51 | PAYNE - 598WN036-A | 190 | 42 | Yes | Yes | 15.5 | 18.5 | -3 | A713F54C691E423DAE36D8A0DDF5696E |  | R22 | Non-TXV |  | 22.11% | 0.77895 | 42.48% | [5 empty] | Non-TXV | 22.11%
Atwater | CA | 95301-4804 |  | 2013-07-12 | 2013-07-12 16:03 | 2013-07-12 16:13 | BDP - 598AN036 | 194 | 19.4 | Yes | Yes | 20.3 | 20.1 | 0.2 | 334B13E243B34245AE1D5F336C098EAA |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Paso Robles | CA | 93446-5042 |  | 2013-08-06 | 2013-08-06 09:30 | 2013-08-06 10:12 | CARRIER - 38EN0243109M | 53 | 6.8 | Yes | Yes | 21.1 | 20.4 | 0.7 | AB7B8A50D1D84D45AC6FEF45CE538D41 |  | R22 | Non-TXV |  | 12.83% | 0.8717 | 24.66% | [5 empty] | Non-TXV | 12.83%
Magalia | CA | 95954-8801 |  | 2013-07-17 | 2013-07-17 11:09 | 2013-07-17 11:09 | CARRIER - 48SDN036090301 | 167 | 0 | Yes | Yes | 19.4 | 18.3 | 1.1 | 621606AD71AE487893429A9546C16620 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-5043 |  | 2013-08-08 | 2013-08-08 13:39 | 2013-08-08 14:02 | CARRIER - 38EN024310SM | 56 | 3.5 | Yes | Yes | 16.3 | 18.8 | -2.5 | BEC95F306ABE425D936F045AC425A6AE |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Farmington | CA | 95230-9539 |  | 2013-10-02 | 2013-10-02 17:26 | 2013-10-02 17:26 | RHEEM - RRKA-A042JK08X | 69 | 0 | Yes | Yes | 25.1 | 21.7 | 3.4 | C51543FC5DAD4C42893367F62DED4D61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5032 |  | 2013-06-19 | 2013-06-19 11:38 | 2013-06-19 12:15 | CARRIER - 48SDN036060311 | 130 | 24.9 | Yes | Yes | 15.3 | 17.9 | -2.6 | 42AFF6486D23474C836D68200E1CD13C |  | R22 | Non-TXV |  | 19.15% | 0.80846 | 36.81% | [5 empty] | Non-TXV | 19.15%
Clovis | CA | 93611-5153 |  | 2013-08-06 | 2013-08-06 14:12 | 2013-08-06 14:14 | BDP - 585HJW030040ABAF | 68 | 8.9 | Yes | Yes | 27.2 | 23.5 | 3.7 | A590BE6C986845559CF3856A803A7FA6 |  | R22 | Non-TXV |  | 13.09% | 0.86912 | 25.15% | [5 empty] | Non-TXV | 13.09%
Yuba City | CA | 95993-5001 |  | 2013-06-06 | 2013-06-06 11:02 | 2013-06-06 11:20 | LENNOX - 10ACC-060-230-02 | 130 | 12 | Yes | Yes | 21 | 19.8 | 1.2 | 48D5B849AD784CE6A93A1E3E977E8009 |  | R22 | Non-TXV |  | 9.231% | 0.90769 | 17.74% | [5 empty] | Non-TXV | 9.231%
Stockton | CA | 95206-6241 |  | 2013-06-21 | 2013-06-21 11:49 | 2013-06-21 12:05 | AIRE-FLO - CR33KF-PFV-230 | 61 | 5.3 | Yes | Yes | 23.9 | 19.9 | 4.1 | 876A5DEF3ECA4C189CA4DAD4D09CBE29 |  | R22 | Non-TXV |  | 8.689% | 0.91311 | 16.7% | [5 empty] | Non-TXV | 8.689%
Clovis | CA | 93612-4844 |  | 2013-06-19 | 2013-06-19 10:50 | 2013-06-19 11:08 | AMERICAN STANDARD - YCC036F1M0BF | 83 | 5 | Yes | Yes | 23.1 | 19 | 4.1 | 55954A5EFE594A0594579EE21E205691 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Rocklin | CA | 95765-4507 |  | 2013-06-15 | 2013-06-15 10:30 | 2013-06-15 10:30 | AMERICAN STANDARD - TTD748B100AD | 116 | 0 | Yes | Yes | 23.6 | 21.7 | 2 | A6D32CBA468341BE8EC76085C3CDD57F | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1978 |  | 2013-09-03 | 2013-09-03 09:36 | 2013-09-03 09:38 | YORK - DAYPF036N070A | 108 | 7.2 | Yes | Yes | 23.7 | 18.7 | 5 | 12C1C321602748C68BD2ED51A0326064 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Merced | CA | 95348-2831 |  | 2013-06-07 | 2013-06-07 10:47 | 2013-06-07 10:50 | GOODMAN - GPG1336070M41AC | 85 | 4 | Yes | Yes | 23.3 | 19.3 | 4.1 | 1329A36719F9445B88FC92344E4A0846 |  | R410A | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Paso Robles | CA | 93446-4469 |  | 2013-08-09 | 2013-08-09 08:23 | 2013-08-09 08:58 | CARRIER - 38EN036320 | 88 | 4.6 | Yes | Yes | 19.5 | 20.9 | -1.4 | 98D07BBEF3B7492EA00AD2D5B81D2591 |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Clovis | CA | 93612-4848 |  | 2013-06-28 | 2013-06-28 15:40 | 2013-06-28 16:05 | CARRIER - 48SX-042080321AA | 87 | 13.3 | Yes | Yes | 20.2 | 23.2 | -3 | 753384D56D00491E859970F15C15AD6D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.29% | 0.84713 | 29.38% | [5 empty] | Non-TXV | 15.29%
Stockton | CA | 95203-1718 |  | 2013-05-31 | 2013-05-31 08:48 | 2013-05-31 09:06 | YORK - D1NH024N05606C | 70 | 2.8 | Yes | Yes | 15.3 | 17.7 | -2.4 | B56902F575A143D79F90BD8BFDE02435 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Magalia | CA | 95954-9394 |  | 2013-07-19 | 2013-07-19 14:24 | 2013-07-19 15:06 | YORK - H4DH042S06A | 104 | 3.7 | Yes | Yes | 19 | 20.4 | -1.4 | DECAC9BB27B041698C93FFEF027DFCD7 |  | R22 | Non-TXV |  | 3.558% | 0.96442 | 6.837% | [5 empty] | Non-TXV | 3.558%
Merced | CA | 95340-2809 |  | 2013-06-06 | 2013-06-06 11:58 | 2013-06-06 12:01 | TRANE - TTX036C100A1 | 152 | 6.3 | Yes | Yes | 22.8 | 18.7 | 4.1 | 623E99A58CAC4E878B6794D4CA190839 |  | R22 | Non-TXV |  | 4.145% | 0.95855 | 7.965% | [5 empty] | Non-TXV | 4.145%
Yuba City | CA | 95993-5009 |  | 2013-06-10 | 2013-06-10 08:20 | 2013-06-10 08:20 | LENNOX - 13ACC-036-230--01 | 115 | 0 | Yes | Yes | 17 | 19.3 | -2.3 | 3113B8F58A734CB4B629EE9A7AE4CCD9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-5009 |  | 2013-06-10 | 2013-06-10 08:33 | 2013-06-10 08:33 | LENNOX - 13ACC-036-230-01 | 115 | 0 | Yes | Yes | 18 | 20.9 | -2.9 | 73F0B7A35EF64F64A07F91DF1AAC60F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4645 |  | 2013-06-10 | 2013-06-10 22:05 | 2013-06-10 22:05 | CARRIER - CA5548VK022 | 131 | 0 | Yes | Yes | 17.6 | 19.8 | -2.2 | 93CD068660F74BB3A86C1290962B53B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-5453 |  | 2013-07-12 | 2013-07-12 10:21 | 2013-07-12 10:44 | OTHER - UNK | 65 | 2.7 | Yes | Yes | 25 | 19.9 | 5.1 | 5360F36721A04883B82F1AE3D7E3FB9A |  | R22 | TXV |  | 4.154% | 0.95846 | 7.983% | [5 empty] | TXV | 4.154%
Oroville | CA | 95966-6007 |  | 2013-06-20 | 2013-06-20 11:43 | 2013-06-20 13:33 | TEMPSTAR - T2A36GKA100 | 131 | 8.5 | Yes | Yes | 22.5 | 20.7 | 1.8 | 196F803742AD412B959AFDF384AD2015 |  | R22 | Non-TXV |  | 6.489% | 0.93511 | 12.47% | [5 empty] | Non-TXV | 6.489%
Riverbank | CA | 95367-2941 |  | 2013-08-20 | 2013-08-20 11:01 | 2013-08-20 11:35 | RHEEM - UNK | 64 | 3.1 | Yes | Yes | 18.8 | 19.9 | -1.1 | 7C5180C85FC944B092F48FE071BE1179 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | Non-TXV | 4.844%
Paso Robles | CA | 93446-5017 |  | 2013-08-08 | 2013-08-08 11:22 | 2013-08-08 11:40 | CARRIER - 38EN024310SM | 56 | 2.7 | Yes | Yes | 20 | 20.1 | -0.1 | DCA28A1630254E98A6D6EFEDDE8CD06A |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Fresno | CA | 93727-6421 |  | 2013-06-14 | 2013-06-14 12:52 | 2013-06-14 12:55 | BRYANT - 38BRB030300 | 106 | 4.5 | Yes | Yes | 16.7 | 19.3 | -2.6 | 00A4AF04B72D496EA1A32E97EB433FD5 |  | R22 | Non-TXV |  | 4.245% | 0.95755 | 8.159% | [5 empty] | Non-TXV | 4.245%
Fresno | CA | 93726-4437 |  | 2013-09-24 | 2013-09-24 08:55 | 2013-09-24 08:58 | NORDYNE - JS5BD048K | 126 | 12.2 | Yes | Yes | 17.8 | 15.9 | 1.9 | D366AF9338514C9EA9BEC1943CEDBF5F |  | R22 | Non-TXV |  | 9.683% | 0.90317 | 18.61% | [5 empty] | Non-TXV | 9.683%
Stockton | CA | 95209-1232 |  | 2013-06-10 | 2013-06-10 15:41 | 2013-06-10 15:41 | PAYNE - PGD32406K001C1 | 72 | 0 | Yes | Yes | 21.4 | 19.5 | 2 | AC4D4F521CC64C0FB60144F87EB997B3 |  | R410A | TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-3664 |  | 2013-08-15 | 2013-08-15 12:16 | 2013-08-15 12:46 | YORK - AC036X1021A | 63 | -5.2 | Yes | Yes | 20.6 | 16.9 | 3.7 | 214A9C7022994B03BE9B40B32EB03751 |  | R22 | Non-TXV |  | -8.254% | 1.0825 | 2.311% |  |  |  |  | Non-TXV |  |  | -8.254%
Live Oak | CA | 95953-9439 |  | 2013-09-10 | 2013-09-10 13:08 | 2013-09-10 13:25 | CARRIER - 24ABA348A300 | 120 | -5.8 | Yes | Yes | 17 | 18.8 | -1.8 | 63555C05B6E04EC9AB9EF958931F0E4B |  | R410A | TXV |  | -4.833% | 1.0483 | 1.354% |  |  |  |  | TXV |  |  | -4.833%
Paso Robles | CA | 93446-5044 |  | 2013-08-07 | 2013-08-07 13:47 | 2013-08-07 14:04 | CARRIER - 38EN0243108M | 56 | 8.9 | Yes | Yes | 25.3 | 23.2 | 2.1 | 60B69DBF78744D68B7C3860540E1BD38 |  | R22 | Non-TXV |  | 15.89% | 0.84107 | 30.54% | [5 empty] | Non-TXV | 15.89%
Marysville | CA | 95901-4804 |  | 2013-06-26 | 2013-06-26 12:59 | 2013-06-26 13:20 | PAYNE - PA10JA030000AGAA | 75 | 7.8 | Yes | Yes | 17.5 | 18.7 | -1.2 | 32280F000D0E4F1AB64E753381B0FD55 |  | R22 | Non-TXV |  | 10.4% | 0.896 | 19.99% | [5 empty] | Non-TXV | 10.4%
Dinuba | CA | 93618-3340 |  | 2013-06-26 | 2013-06-26 17:45 | 2013-06-26 18:17 | GOODMAN - PGB030050-1 | 56 | 1.9 | Yes | Yes | 19.2 | 16.7 | 2.5 | 57C5787DB43B46D3B6A1888EE1C297A0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Stockton | CA | 95210-5651 |  | 2013-07-29 | 2013-07-29 15:30 | 2013-07-29 15:58 | RUUD - 13AJM30A01 | 86 | 9.7 | Yes | Yes | 26.8 | 21 | 5.8 | 1B3B9E31900E4B29B35701A79DE3D9A0 |  | R410A | TXV |  | 11.28% | 0.88721 | 21.68% | [5 empty] | TXV | 11.28%
Fresno | CA | 93710-5625 |  | 2013-06-03 | 2013-06-03 16:24 | 2013-06-03 16:41 | OTHER - UNK | 64 | 1.9 | Yes | Yes | 22.5 | 21.3 | 1.2 | DB31D31ED3CB49B289A29F41A873E7F3 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93710-7104 |  | 2013-10-25 | 2013-10-25 14:08 | 2013-10-25 14:09 | GOODMAN - GSC130421AA | 143 | 4.3 | Yes | Yes | 18 | 18.8 | -0.8 | C1154AE2A1874E8BA8CE8E06359472C9 |  | R22 | Non-TXV |  | 3.007% | 0.96993 | 5.779% | [5 empty] | Non-TXV | 3.007%
Paso Robles | CA | 93446-3250 |  | 2013-08-06 | 2013-08-06 10:52 | 2013-08-06 11:11 | LENNOX - HS18-411-6P | 94 | -5.5 | Yes | Yes | 22.5 | 17.2 | 5.3 | 118C4D401FE14E32A86C7D25595A0A68 |  | R22 | Non-TXV |  | -5.851% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.851%
Stockton | CA | 95210-1430 |  | 2013-06-27 | 2013-06-27 10:12 | 2013-06-27 10:31 | WESTINGHOUSE - UNK | 64 | -4.5 | Yes | Yes | 20.8 | 16.7 | 4.1 | D914EF8E34B54B29B0D4DF1274262785 |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Oakdale | CA | 95361-2932 |  | 2013-06-14 | 2013-06-14 09:22 | 2013-06-14 09:49 | PAYNE - PY3PNA024060NB-- | 89 | 5 | Yes | Yes | 22.6 | 20.1 | 2.5 | 6DEE7B6C491D46A197453F3DED5D942C |  | R22 | Non-TXV |  | 5.618% | 0.94382 | 10.8% | [5 empty] | Non-TXV | 5.618%
Fresno | CA | 93727-3912 |  | 2013-06-14 | 2013-06-14 15:05 | 2013-06-14 15:07 | RUUD - 7777UNK | 85 | 3.9 | Yes | Yes | 19.2 | 17.7 | 1.5 | F9F9528DD198484E9976C55E2A34A432 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Stockton | CA | 95207-7429 |  | 2013-10-09 | 2013-10-09 10:29 | 2013-10-09 11:00 | KENMORE - TCA448AKA1 | 198 | 6.3 | Yes | Yes | 26.6 | 20.6 | 6 | DD9AFAAC74934CB29E542B283DEA26F0 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Tracy | CA | 95377-7937 |  | 2013-06-04 | 2013-06-04 12:09 | 2013-06-04 12:41 | GOODMAN - CKT36-1AD | 85 | -8 | Yes | Yes | 22.7 | 20.2 | 2.5 | 330BBEE842B0430D8CA6FD7FE31D3E0F |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95204-2621 |  | 2013-06-25 | 2013-06-25 11:57 | 2013-06-25 12:16 | RUUD - 13AJA30A01 | 98 | 11.5 | Yes | Yes | 16.2 | 16.3 | -0.1 | 7814E05B10074A9DBF8F9B334EFE2162 |  | R22 | Non-TXV |  | 11.73% | 0.88265 | 22.55% | [5 empty] | Non-TXV | 11.73%
Maxwell | CA | 95955-0000 |  | 2013-09-09 | 2013-09-09 09:15 | 2013-09-09 09:34 | GOODMAN - CK30-1A | 76 | 3 | Yes | Yes | 18.4 | 18.8 | -0.4 | 28E631438925449883C3DB849AB0817A |  | R22 | TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | TXV | 3.947%
Stockton | CA | 95215-5814 |  | 2013-06-05 | 2013-06-05 11:49 | 2013-06-05 12:09 | RHEEM - RRKA-A030JK08E | 54 | 6.8 | Yes | Yes | 20 | 18.8 | 1.2 | 2CFCBC7D74F14291B0240C1E50E82C65 |  | R22 | Non-TXV |  | 12.59% | 0.87407 | 24.2% | [5 empty] | Non-TXV | 12.59%
Fresno | CA | 93727-3031 |  | 2013-06-10 | 2013-06-10 16:35 | 2013-06-10 17:05 | BDP - 585CJW030050AAAF | 75 | 2.3 | Yes | Yes | 23.6 | 19.7 | 3.9 | 6DFD07FD3C8F4FF6B673DA76453EB0E3 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Stockton | CA | 95203-3179 |  | 2013-06-07 | 2013-06-07 08:57 | 2013-06-07 09:17 | DAY & NIGHT - 585GW024040ABAE | 54 | 2.6 | Yes | Yes | 17 | 18.8 | -1.8 | C2D16088ED0A47EEB9F509B1BEAEC108 |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Stockton | CA | 95210-1208 |  | 2013-06-17 | 2013-06-17 10:10 | 2013-06-17 10:28 | RUUD - UAFD-042JBS | 79 | 2.4 | Yes | Yes | 20.3 | 18.7 | 1.6 | 42740E66E3A44FA78A1E92E656028979 |  | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Stockton | CA | 95206-6271 |  | 2013-06-18 | 2013-06-18 13:16 | 2013-06-18 13:16 | OTHER - 38CKC060--301 | 153 | 0 | Yes | Yes | 18.6 | 20.9 | -2.3 | 6A96C87EDBDD4726BDAA3B74FF340146 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-8773 |  | 2013-06-05 | 2013-06-05 10:53 | 2013-06-05 11:38 | BRYANT - 38CK060370 | 159 | 13.3 | Yes | Yes | 19 | 20.4 | -1.4 | 84929072A235452EA9D4259E9927A5EF |  | R22 | Non-TXV |  | 8.365% | 0.91635 | 16.08% | [5 empty] | Non-TXV | 8.365%
Clovis | CA | 93611-4018 |  | 2013-06-28 | 2013-06-28 11:21 | 2013-06-28 11:41 | BDP - 585A036080YAC | 60 | 6.1 | Yes | Yes | 18.3 | 19.7 | -1.4 | E802243DFA514DA9A1631B6953E94311 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.17% | 0.89833 | 19.54% | [5 empty] | Non-TXV | 10.17%
Fresno | CA | 93727-3031 |  | 2013-06-10 | 2013-06-10 17:06 | 2013-06-10 17:40 | BDP - 585CJO30050 | 78 | 2.9 | Yes | Yes | 23.8 | 18.8 | 5 | 2F790E7CFDFB439698529E106C2323B0 |  | R22 | Non-TXV |  | 3.718% | 0.96282 | 7.145% | [5 empty] | Non-TXV | 3.718%
Fresno | CA | 93720-2347 |  | 2013-07-08 | 2013-07-08 10:31 | 2013-07-08 10:52 | TEMPSTAR - CA3048VKA1 | 138 | 4.1 | Yes | Yes | 18.1 | 20.9 | -2.8 | 5CF947044DA04D43A2A0A9253CB127A9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.971% | 0.97029 | 5.71% | [5 empty] | Non-TXV | 2.971%
Red Bluff | CA | 96080-9739 |  | 2013-05-30 | 2013-05-30 13:22 | 2013-05-30 14:18 | BRYANT - | 151 | 5.2 | Yes | Yes | 26.5 | 22.8 | 3.7 | 83D2AEE3F1A3451791E4E14269A08D7C |  | R410A | Non-TXV |  | 3.444% | 0.96556 | 6.618% | [5 empty] | Non-TXV | 3.444%
Stockton | CA | 95205-0000 |  | 2013-06-03 | 2013-06-03 11:14 | 2013-06-03 11:33 | GOODMAN - GSC130481BA | 102 | 3.4 | Yes | Yes | 17.5 | 18.7 | -1.2 | 4613E0276FB94030A9287C3A6FFC036C |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Colfax | CA | 95713-0000 |  | 2013-07-25 | 2013-07-25 16:35 | 2013-07-25 16:35 | COLEMAN - UNK | 100 | 0 | Yes | Yes | 21 | 22.5 | -1.5 | 7C96FAD090554FD2B13D48DB064197A8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-3160 |  | 2013-05-29 | 2013-05-29 13:32 | 2013-05-29 13:32 | PAYNE - PY1PNB024060AAAA | 53 | -5 | Yes | Yes | -0.4 | 16.4 | -16.8 | 34BF2A2B4AAD42DAAF20C0183F455499 | Remove refrigerant: 5 oz Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Fresno | CA | 93703-1542 |  | 2013-06-06 | 2013-06-06 13:16 | 2013-06-10 10:15 | OTHER - GPG1330070M41AC | 160 | 7.8 | Yes | Yes | 18.3 | 20.4 | -2.1 | D4A2BF320D214CEF8150ED64636C8F51 |  | R22 | Non-TXV |  | 4.875% | 0.95125 | 9.369% | [5 empty] | Non-TXV | 4.875%
Stockton | CA | 95206-4605 |  | 2013-06-18 | 2013-06-18 13:18 | 2013-06-18 13:50 | RUUD - UAKA-030JAZ | 85 | -8 | Yes | Yes | 24 | 18.1 | 5.9 | 5D4C126D122549178AD872C915AEBCEE |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Oroville | CA | 95966-8045 |  | 2013-06-20 | 2013-06-20 10:13 | 2013-06-20 11:41 | DAY & NIGHT - 589ANW0360ADBF | 100 | 3 | Yes | Yes | 22 | 20 | 2.1 | 21EFF3CBE27F41988F0297DE1C5C31FF |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95212-2859 |  | 2013-06-12 | 2013-06-12 12:56 | 2013-06-12 13:21 | CARRIER - 38CKC042351 | 81 | 2.4 | Yes | Yes | 16.8 | 19.7 | -2.9 | 733BD65514EC469D9BA4834582000EA9 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95203-3164 |  | 2013-05-29 | 2013-05-29 12:38 | 2013-05-29 12:56 | DAY & NIGHT - 585GJW024040ABAE | 54 | 3.3 | Yes | Yes | 18.3 | 18.8 | -0.5 | 44A5E81315A64B808A39636AD3D1FD02 |  | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Stockton | CA | 95207-3059 |  | 2013-05-30 | 2013-05-30 13:23 | 2013-05-30 13:46 | DAY & NIGHT - 588ANW042100ADAG | 82 | 5.8 | Yes | Yes | 25 | 22 | 3 | AD708E8814DD4907806BE466E17ECD34 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.073% | 0.92927 | 13.59% | [5 empty] | Non-TXV | 7.073%
Fresno | CA | 93726-4011 |  | 2013-06-04 | 2013-06-04 13:24 | 2013-06-04 13:47 | RUUD - URMA-A036JK08E | 99 | 3.6 | Yes | Yes | 21.8 | 21.2 | 0.6 | F25E6218D1D84343A1228117765E3A70 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Auburn | CA | 95603-9730 |  | 2013-06-07 | 2013-06-07 09:23 | 2013-06-07 09:23 | TRANE - 4YCY4060A1120AA | 156 | 0 | Yes | Yes | 22.5 | 18.7 | 3.8 | 5345A6C6F6E8435188E6A22970BF96B4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-9603 |  | 2013-09-05 | 2013-09-05 12:36 | 2013-09-05 12:37 | CARRIER - 38B036300 | 117 | 3.6 | Yes | Yes | 27.5 | 22.4 | 5.1 | 48E8B5FFD4B949AEB3A049CF5EF6072A |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Los Banos | CA | 93635-6408 |  | 2013-07-10 | 2013-07-10 13:28 | 2013-07-10 13:37 | NORDYNE - FS5BD060KA | 160 | 15.7 | Yes | Yes | 25.6 | 23 | 2.6 | 8310B9F531894311A8B24F95E0F1A076 |  | R22 | Non-TXV |  | 9.812% | 0.90187 | 18.86% | [5 empty] | Non-TXV | 9.812%
Clovis | CA | 93612-0133 |  | 2013-06-27 | 2013-06-27 11:01 | 2013-06-27 11:22 | BDP - 589ANW036060ADBF | 84 | 8.8 | Yes | Yes | 19.2 | 20.4 | -1.2 | F2572FA59D5F4C32B2593749C8700EF8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.48% | 0.89524 | 20.13% | [5 empty] | Non-TXV | 10.48%
Fresno | CA | 93726-4011 |  | 2013-06-04 | 2013-06-04 12:41 | 2013-06-04 13:45 | GOODMAN - GPG1336070M41BA | 70 | 2.1 | Yes | Yes | 23.6 | 18.5 | 5.2 | 7217154BB9254B50B32C7D4A81155B10 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93612-0118 |  | 2013-06-21 | 2013-06-21 11:57 | 2013-06-21 12:16 | BDP - 589ANW024040ACBD | 57 | 1.8 | Yes | Yes | 22.7 | 20.7 | 2 | A7299D290EC5428C8739EBD6246C6998 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Merced | CA | 95348-3778 |  | 2013-09-06 | 2013-09-06 09:58 | 2013-09-06 10:17 | AMERICAN STANDARD - TTD730B100AO | 69 | 8.1 | Yes | Yes | 22.6 | 17.9 | 4.7 | FAC2097E5A1A45E386158BEBAECA16DF |  | R22 | Non-TXV |  | 11.74% | 0.88261 | 22.56% | [5 empty] | Non-TXV | 11.74%
Maxwell | CA | 95955-0000 |  | 2013-09-09 | 2013-09-09 10:43 | 2013-09-09 11:08 | LENNOX - 12GCS048-100-2PA | 167 | 4.9 | Yes | Yes | 22 | 19.3 | 2.7 | B18BAED581B64D8FBD6B87F9C6DFC206 |  | R22 | Non-TXV |  | 2.934% | 0.97066 | 5.639% | [5 empty] | Non-TXV | 2.934%
Clovis | CA | 93612-0906 |  | 2013-06-21 | 2013-06-21 09:22 | 2013-06-21 09:56 | CARRIER - 48GP--30060311US | 85 | 3.4 | Yes | Yes | 19.3 | 20.7 | -1.4 | D5A859FDF8E241A1B3917E1150A87F5E | OK: Verified Refrigerant Charge Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Fresno | CA | 93703-1620 |  | 2013-06-06 | 2013-06-06 14:10 | 2013-06-10 23:19 | OTHER - PY3GNNA48090NA | 131 | 6.4 | Yes | Yes | 18.8 | 17.4 | 1.4 | 7CBEF1C7DB054DCBBF95BF863B23E3A5 |  | R22 | Non-TXV |  | 4.885% | 0.95115 | 9.389% | [5 empty] | Non-TXV | 4.885%
Sutter Creek | CA | 95685-9748 |  | 2013-09-17 | 2013-09-17 10:04 | 2013-09-17 10:27 | CARRIER - 48SS-018040301 | 38 | 4.1 | Yes | Yes | 26 | 20.3 | 5.8 | C8D1E3E3C8A846DE83D0988C5BE40950 |  | R22 | Non-TXV |  | 10.79% | 0.89211 | 20.73% | [5 empty] | Non-TXV | 10.79%
Nevada City | CA | 95959-2428 |  | 2013-08-27 | 2013-08-27 11:11 | 2013-08-27 11:11 | CARRIER - 38GA001300 | 58 | 0 | Yes | Yes | 16.8 | 18.9 | -2.1 | 11AF0465C11C4C66BFD41196CDA6F4E3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4840 |  | 2013-06-11 | 2013-06-11 15:33 | 2013-06-11 15:36 | BRYANT - 561CJ024-C | 72 | 2.2 | Yes | Yes | 17.2 | 18.3 | -1.1 | C4F5D4F797004158AB625B0E59C0F81C |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Rough & Ready | CA | 95975-9736 |  | 2013-08-26 | 2013-08-26 12:06 | 2013-08-26 12:06 | LENNOX - HS29-048-2P | 88 | 0 | Yes | Yes | 25.3 | 20.4 | 4.9 | D8EF2B50C5EE49299630DA0EE59C0A87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-4806 |  | 2013-06-28 | 2013-06-28 09:47 | 2013-06-28 10:18 | UNITARY PRODUCTS GROUP - GCGD36S41S3A | 73 | 8.1 | Yes | Yes | 17.8 | 17.6 | 0.2 | D1C8F419D6E84B638AD505BA23296891 |  | R410A | Non-TXV |  | 11.1% | 0.88904 | 21.32% | [5 empty] | Non-TXV | 11.1%
Clovis | CA | 93612-2645 |  | 2013-06-17 | 2013-06-17 14:57 | 2013-06-17 15:15 | GOODMAN - CLQ030-1B | 131 | 4.4 | Yes | Yes | 18.6 | 19.5 | -0.9 | 10F68C36AD5A4E22B3B28211A5899219 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
Fresno | CA | 93726-5626 |  | 2013-08-13 | 2013-08-13 10:43 | 2013-08-13 11:01 | YORK - D1NP042N06506A | 150 | 4.9 | Yes | Yes | 19.7 | 18.8 | 0.9 | 27177906A90A4D3685E03984C441135F |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.278% | [5 empty] | Non-TXV | 3.267%
Auburn | CA | 95603-3423 |  | 2013-06-12 | 2013-06-12 14:53 | 2013-06-12 15:15 | TRANE - WCY030G100BB | 140 | 4.1 | Yes | Yes | 27 | 23.1 | 3.9 | 68E2B6B508224170B8C644A28F40AB89 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.628% | [5 empty] | Non-TXV | 2.929%
Jackson | CA | 95642-9594 |  | 2013-09-10 | 2013-09-10 13:53 | 2013-09-10 13:53 | UNITARY PRODUCTS GROUP - BRC00301BE | 41 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | F8966E7E20D44CE7AFFC9FAB27E57907 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Jackson | CA | 95642-9574 |  | 2013-09-04 | 2013-09-04 13:05 | 2013-09-04 13:05 | YORK - BRCQ0361BD | 52 | 0 | Yes | Yes | 26.1 | 23.1 | 3 | 88480A8F19E941BEBE055C9251B194D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4805 |  | 2013-06-11 | 2013-06-11 15:10 | 2013-06-11 15:12 | BRYANT - 598AN036-B | 196 | 6 | Yes | Yes | 18.1 | 17.7 | 0.4 | 1AEBAEF06BC54B13878DCC0A3EB59869 |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Dinuba | CA | 93618-1845 |  | 2013-06-24 | 2013-06-24 18:23 | 2013-06-24 18:42 | PAYNE - PY3GNAA30060NA | 98 | 4.8 | Yes | Yes | 25.7 | 20.9 | 4.8 | 8CF7299C7C98491BBBF305F1FA27F03A |  | R410A | TXV |  | 4.898% | 0.95102 | 9.413% | [5 empty] | TXV | 4.898%
Stockton | CA | 95212-0000 |  | 2013-06-13 | 2013-06-13 09:47 | 2013-06-13 10:09 | CARRIER - 38CKC024340 | 51 | 3.7 | Yes | Yes | 17.9 | 20.4 | -2.5 | 80CDC6D69BFE46F08B3D7B7EB9F3E27B |  | R22 | Non-TXV |  | 7.255% | 0.92745 | 13.94% | [5 empty] | Non-TXV | 7.255%
Atwater | CA | 95301-4206 |  | 2013-06-06 | 2013-06-06 11:03 | 2013-06-06 11:17 | ICP - HAC042AKA1 | 98 | 6.9 | Yes | Yes | 15.9 | 17.9 | -2 | 3EF2E7A7790645059CD18CED50CB29C6 |  | R22 | Non-TXV |  | 7.041% | 0.92959 | 13.53% | [5 empty] | Non-TXV | 7.041%
French Camp | CA | 95231-9717 |  | 2013-08-29 | 2013-08-29 14:57 | 2013-08-29 15:15 | DAY & NIGHT - 597BNX048-A | 73 | 7.4 | Yes | Yes | 23.3 | 19.4 | 3.9 | 3B46C30CE190451FBCA9D4B1A292A8AA |  | R22 | Non-TXV |  | 10.14% | 0.89863 | 19.48% | [5 empty] | Non-TXV | 10.14%
Tracy | CA | 95376-2610 |  | 2013-05-28 | 2013-05-28 16:10 | 2013-05-28 16:41 | YORK - H2RA036S06E | 63 | 2.8 | Yes | Yes | 22.6 | 18.7 | 4 | 55A807B4829441F0819063BEEB3E5968 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Stockton | CA | 95206-4853 |  | 2013-06-17 | 2013-06-17 13:59 | 2013-06-17 14:35 | JANITROL - UNK | 85 | -7 | Yes | Yes | 26.8 | 21.6 | 5.2 | CD831263AACA4E0C965D05C8A8D88F51 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Manteca | CA | 95337-6527 |  | 2013-05-31 | 2013-05-31 09:40 | 2013-05-31 10:09 | BDP - 585CJ02450 | 72 | 2.8 | Yes | Yes | 20.3 | 20.2 | 0.1 | C3123B3228B4489C932AC7EB8CB56650 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Clovis | CA | 93612-1963 |  | 2013-08-23 | 2013-08-23 11:00 | 2013-08-23 11:25 | BDP - 585EJWO24040ABAE | 54 | 4.6 | Yes | Yes | 22 | 20.2 | 1.9 | C413FEDA735745A9ABC6C8C2AD648478 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.519% | 0.91481 | 16.37% | [5 empty] | Non-TXV | 8.519%
Merced | CA | 95348-1339 |  | 2013-08-08 | 2013-08-08 15:42 | 2013-08-08 16:07 | LENNOX - 10ACB30-7P | 69 | 2.1 | Yes | Yes | 20.5 | 20.2 | 0.3 | E05DB3A4B7034B2D9CEA91F51E2856CA |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Manteca | CA | 95336-8426 |  | 2013-05-29 | 2013-05-29 14:14 | 2013-05-29 14:31 | GOODMAN - GPG1342070M41AB | 105 | 5.1 | Yes | Yes | 19.5 | 19.3 | 0.2 | 3F7632D27EAC4434821A638EACF082DB |  | R410A | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Yuba City | CA | 95993-5009 |  | 2013-06-10 | 2013-06-10 08:50 | 2013-06-10 09:09 | LENNOX - 10AC-036-230-02 | 96 | 16.3 | Yes | Yes | 16 | 18.8 | -2.8 | D4C35EA0711A44519CF09A2032A6F16D |  | R22 | Non-TXV |  | 16.98% | 0.83021 | 32.63% | [5 empty] | Non-TXV | 16.98%
Placerville | CA | 95667-7753 |  | 2013-09-03 | 2013-09-03 18:36 | 2013-09-03 18:36 | UNITARY PRODUCTS GROUP - AM024M1021G | 52 | 0 | Yes | Yes | 23.2 | 21.7 | 1.5 | 5DE28538BA2E4071B056551A8D195776 | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2905 |  | 2013-06-10 | 2013-06-10 10:32 | 2013-06-10 10:50 | LENNOX - HS13-411V-5P | 149 | 15.2 | Yes | Yes | 21.9 | 19.4 | 2.5 | B9B5A9C716574E79B9A40E874BE873EE |  | R22 | Non-TXV |  | 10.2% | 0.89799 | 19.6% | [5 empty] | Non-TXV | 10.2%
Dinuba | CA | 93618-1851 |  | 2013-06-24 | 2013-06-24 15:25 | 2013-06-24 15:27 | RHEEM - N/A | 75 | 2.5 | Yes | Yes | 25.1 | 19.6 | 5.5 | FD91FCCA541F4BB7A46B5A01E29CCA71 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Manteca | CA | 95336-8428 |  | 2013-05-30 | 2013-05-30 14:45 | 2013-05-30 15:08 | YORK - D2NP024N05606A | 100 | 3.1 | Yes | Yes | 17.4 | 18 | -0.6 | 740F5EF60D064995947E8E36F2DBF130 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Fresno | CA | 93703-1658 |  | 2013-10-25 | 2013-10-25 11:56 | 2013-10-25 11:57 | BDP - 588ANW048100AFAG | 101 | 4.3 | Yes | Yes | 19.7 | 19.1 | 0.6 | 2E102579C87941ED9B1E340A5F9BEB8C |  | R22 | Non-TXV |  | 4.257% | 0.95743 | 8.182% | [5 empty] | Non-TXV | 4.257%
Rocklin | CA | 95677-2670 |  | 2013-08-23 | 2013-08-23 08:52 | 2013-08-23 08:52 | RHEEM - RAFD-042JBS | 79 | 0 | Yes | Yes | 21 | 19.4 | 1.6 | 3BEAE21B180F4F88A9E2746B717AD263 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-2848 |  | 2013-09-09 | 2013-09-09 10:52 | 2013-09-09 10:54 | GOODMAN - GPH1336M21AB | 165 | 21.2 | Yes | Yes | 18.8 | 18.2 | 0.6 | CCD56953F189460EA403FB071BA493AA |  | R22 | Non-TXV |  | 12.85% | 0.87152 | 24.69% | [5 empty] | Non-TXV | 12.85%
Stockton | CA | 95207-2091 |  | 2013-05-29 | 2013-05-29 13:25 | 2013-05-29 13:44 | LENNOX - UNK | 96 | 4.9 | Yes | Yes | 19.6 | 20.2 | -0.5 | 00B0CF446AFF49669B98D4231910BC2A |  | R410A | Non-TXV |  | 5.104% | 0.94896 | 9.809% | [5 empty] | Non-TXV | 5.104%
Fresno | CA | 93726-0434 |  | 2013-05-30 | 2013-05-30 12:13 | 2013-05-30 12:34 | OTHER - N/A | 120 | 13.6 | Yes | Yes | 20.3 | 20.1 | 0.2 | F41C688CA9C8403FBD53A2F09630F64D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Auburn | CA | 95603-3546 |  | 2013-06-17 | 2013-06-17 17:15 | 2013-06-17 17:35 | RUUD - UAHE-030JAS | 78 | -7.3 | Yes | Yes | 20.7 | 20.9 | -0.2 | A572B7BAC631466C8B91B1D482DC06D6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.359% | 1.0936 | 2.621% |  |  |  |  | Non-TXV |  |  | -9.359%
Stockton | CA | 95210-4198 |  | 2013-05-29 | 2013-05-29 15:06 | 2013-05-29 15:26 | RUUD - UAHE-048JAS | 114 | 25.5 | Yes | Yes | 23.7 | 21.2 | 2.6 | B744AA42CB5D4F02B7FAEF693AFAA154 |  | R22 | Non-TXV |  | 22.37% | 0.77632 | 42.99% | [5 empty] | Non-TXV | 22.37%
Lincoln | CA | 95648-2980 |  | 2013-08-23 | 2013-08-23 10:48 | 2013-08-23 11:10 | YORK - H1BD042S06G | 98 | 3.9 | Yes | Yes | 16 | 18.8 | -2.8 | D710CEC2AC4F4FCBBC8FEFCCC6A6C4DF |  | R22 | Non-TXV |  | 3.98% | 0.9602 | 7.648% | [5 empty] | Non-TXV | 3.98%
Manteca | CA | 95336-8426 |  | 2013-05-30 | 2013-05-30 14:43 | 2013-05-30 15:03 | BDP - 585A024055YAC | 51 | 2.1 | Yes | Yes | 21.2 | 23.1 | -1.9 | D04A33D0082E4DCDA48F5EAEBCED75A0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Dinuba | CA | 93618-1740 |  | 2013-06-26 | 2013-06-26 18:33 | 2013-06-26 18:54 | NORDYNE - N/A | 90 | 2.6 | Yes | Yes | 23.5 | 18.3 | 5.2 | A73823EA23E94E949145A0B5C1ECD61F |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Yuba City | CA | 95991-7510 |  | 2013-06-20 | 2013-06-20 12:24 | 2013-06-20 12:44 | LENNOX - 10AC36-1P | 92 | 6 | Yes | Yes | 21 | 20.1 | 0.9 | FAAEDF9BDD3144948474BEA1B01A5B05 |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Dinuba | CA | 93618-1850 |  | 2013-06-20 | 2013-06-20 14:30 | 2013-06-20 20:08 | BDP - 585ANW3606A | 86 | 2.7 | Yes | Yes | 24.3 | 21.9 | 2.4 | 68D17A26BD214563BCCA8A9108D76A15 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.14% | 0.9686 | 6.033% | [5 empty] | Non-TXV | 3.14%
Madera | CA | 93638-2808 |  | 2013-06-19 | 2013-06-19 18:03 | 2013-06-19 18:21 | DAY & NIGHT - 542DJKD07H | 114 | 3.8 | Yes | Yes | 17 | 18.5 | -1.5 | 6099078590F749F18AC16BA7F6AF7A21 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95207-8811 |  | 2013-06-03 | 2013-06-03 10:28 | 2013-06-03 10:45 | RUUD - UNK | 117 | 15.4 | Yes | Yes | 19.6 | 18.8 | 0.8 | 8AD070C10FF14429B48DBAF3FC3C4246 |  | R22 | Non-TXV |  | 13.16% | 0.86838 | 25.3% | [5 empty] | Non-TXV | 13.16%
Stockton | CA | 95215-7336 |  | 2013-06-06 | 2013-06-06 12:13 | 2013-06-06 12:13 | YORK - D3NZ030N056606NXA | 64 | 0 | Yes | Yes | 22.3 | 18.7 | 3.6 | 0299647331CF437EAC181DB00367416D |  | R22 | TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9262 |  | 2013-06-11 | 2013-06-11 10:13 | 2013-06-11 10:15 | YORK - D3NZ030N05606NXA | 64 | 2.8 | Yes | Yes | 24.2 | 18.3 | 6 | AF61821470994159A2DB42572DB62518 |  | R410A | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Stockton | CA | 95204-1637 |  | 2013-05-30 | 2013-05-30 11:40 | 2013-05-30 12:02 | COLEMAN - ERCS0361BBB | 96 | 7.6 | Yes | Yes | 16.5 | 18.7 | -2.2 | B0C25A62EB6443AA862ACFF22B3B36CA |  | R22 | Non-TXV |  | 7.917% | 0.92083 | 15.21% | [5 empty] | Non-TXV | 7.917%
Stockton | CA | 95212-2845 |  | 2013-07-15 | 2013-07-15 10:31 | 2013-07-15 10:51 | CARRIER - 38CKC048360 | 97 | 3 | Yes | Yes | 22.2 | 21 | 1.2 | AD2935DCBED04B008C07E1E96C4BF16B |  | R22 | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Tracy | CA | 95377-6651 |  | 2013-06-05 | 2013-06-05 08:20 | 2013-06-05 08:55 | DAY & NIGHT - BRCS0421BD | 84 | -7.9 | Yes | Yes | 20.3 | 19.8 | 0.5 | 3DA98EB284CC424E9DBFC4C22C6E72A5 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Winton | CA | 95388-9548 |  | 2013-07-25 | 2013-07-25 17:56 | 2013-07-25 17:57 | TRANE - UNK | 86 | 19.9 | Yes | Yes | 31.3 | 25.9 | 5.4 | E9AD17AE30DB4BF0A0CCA2B60E26E501 |  | R22 | Non-TXV |  | 23.14% | 0.7686 | 44.47% | [5 empty] | Non-TXV | 23.14%
Columbia | CA | 95310-9436 |  | 2013-10-03 | 2013-10-03 15:44 | 2013-10-03 16:43 | PAYNE - PA10JA048000ACAA | 96 | -9 | Yes | Yes | 18.5 | 17.2 | 1.3 | 82EB2ED41C9940119740F4A7E20DDFEE | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Sonora | CA | 95370-9173 |  | 2013-07-31 | 2013-07-31 12:13 | 2013-07-31 12:54 | NORDYNE - JS3BA-036KA | 69 | 6.7 | Yes | Yes | 25.9 | 20.6 | 5.3 | 0D011BCDD2A4420E987DD46F4F36BFC6 |  | R22 | Non-TXV |  | 9.71% | 0.9029 | 18.66% | [5 empty] | Non-TXV | 9.71%
Fresno | CA | 93727-2041 |  | 2013-06-08 | 2013-06-08 14:25 | 2013-06-08 14:41 | DAY & NIGHT - 24/60 YAC108-C | 54 | 1.8 | Yes | Yes | 19.8 | 17.5 | 2.3 | 0AC00816EF6443CC8479C5BC19F69442 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93710-6310 |  | 2013-06-03 | 2013-06-03 11:19 | 2013-06-03 11:40 | DAY & NIGHT - 36/80YAC-106C | 66 | 2.1 | Yes | Yes | 17.9 | 20.2 | -2.3 | CC099DCE535240A6B331D635A81B90C2 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Lincoln | CA | 95648-2102 |  | 2013-05-31 | 2013-05-31 11:32 | 2013-05-31 11:52 | AMERICAN STANDARD - PGC048K080A | 102 | 3 | Yes | Yes | 19 | 20.6 | -1.6 | C1794610D0B04BF1AD7F2BDD212372C1 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Valley Springs | CA | 95252-9254 |  | 2013-08-20 | 2013-08-20 14:05 | 2013-08-20 14:22 | BRYANT - 582ANW036090AAAF | 56 | 2.3 | Yes | Yes | 21.5 | 21.3 | 0.2 | A20FD48347D44FE686757A670C10ABAD |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Stockton | CA | 95219-3137 |  | 2013-06-25 | 2013-06-25 12:13 | 2013-06-25 12:30 | RHEEM - AT-30B1F | 58 | -4.1 | Yes | Yes | 18 | 16.1 | 1.9 | 8BB77243B5F4475D98A7AEAAFFDAED01 |  | R22 | Non-TXV |  | -7.069% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.069%
Cameron Park | CA | 95682-8931 |  | 2013-06-13 | 2013-06-13 10:58 | 2013-06-13 10:58 | WEATHER KING - 13AJA48A01 | 85 | 0 | Yes | Yes | 25.7 | 19.9 | 5.8 | D61F23B2DF5A4145B2DA6985318F4352 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-3522 |  | 2013-08-20 | 2013-08-20 09:12 | 2013-08-20 09:33 | OTHER - NAC036AKAS | 87 | 3.9 | Yes | Yes | 22 | 19.5 | 2.5 | 41A22099F40A4C9A9A8EAA8E1987391C |  | R22 | Non-TXV |  | 4.483% | 0.95517 | 8.615% | [5 empty] | Non-TXV | 4.483%
Stockton | CA | 95209-2003 |  | 2013-06-17 | 2013-06-17 11:32 | 2013-06-17 11:51 | RHEEM - HC-100-36-21C | 49 | 10.6 | Yes | Yes | 22.6 | 18.6 | 4 | 26812A01E0D74801B33DEB84F6CD3E9B |  | R22 | Non-TXV |  | 21.63% | 0.78367 | 41.57% | [5 empty] | Non-TXV | 21.63%
Placerville | CA | 95667-4031 |  | 2013-05-29 | 2013-05-29 15:07 | 2013-05-29 15:31 | TRANE - 2TWB0018A1000AB | 69 | 8.3 | Yes | Yes | 17.8 | 19.3 | -1.5 | 74EA453B2BF3423D94DB1352FBC565A8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.03% | 0.87971 | 23.12% | [5 empty] | Non-TXV | 12.03%
Oakdale | CA | 95361-2814 |  | 2013-07-10 | 2013-07-10 09:29 | 2013-07-10 09:56 | BARD - 568EJ036 | 138 | -24.4 | Yes | Yes | 19.4 | 22.1 | -2.7 | 0D497A6AB9FD49F59E59351BE981B36B |  | R22 | TXV |  | -17.68% | 1.1768 | 4.952% |  |  |  |  | TXV |  |  | -17.68%
Fresno | CA | 93720-2528 |  | 2013-06-21 | 2013-06-21 11:17 | 2013-06-21 11:21 | LENNOX - 12GCS036X-75-5PB | 110 | 4.5 | Yes | Yes | 25.2 | 22 | 3.2 | BC5AB8C86FFC4249B47EFE087BE74107 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Chico | CA | 95926-2327 |  | 2013-06-06 | 2013-06-06 08:56 | 2013-06-06 09:24 | AMANA - RCB36B2A | 85 | 3.6 | Yes | Yes | 18 | 19.3 | -1.3 | 33FFFD4AD2C545EBA65731FB06C9A485 |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Fresno | CA | 93727-7141 |  | 2013-07-16 | 2013-07-16 11:01 | 2013-07-16 11:20 | AMANA - PGB42B0902A | 112 | 3.4 | Yes | Yes | 23.5 | 21.1 | 2.5 | EE37E2EC902346F38C0594031D48033C |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
El Dorado | CA | 95623-4249 |  | 2013-08-15 | 2013-08-15 12:40 | 2013-08-15 12:40 | OTHER - 2A7B2036A1000AA | 96 | 0 | Yes | Yes | 19.1 | 21.4 | -2.3 | 62B9F592C19C47649C5825A1865B9A7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-2219 |  | 2013-05-30 | 2013-05-30 12:27 | 2013-05-30 12:48 | GOODMAN - UNK | 84 | 4.6 | Yes | Yes | 17.1 | 18.6 | -1.5 | C2F719CC0C794C3CAA5DE1BD19470576 |  | R22 | Non-TXV |  | 5.476% | 0.94524 | 10.52% | [5 empty] | Non-TXV | 5.476%
Dos Palos | CA | 93620-9633 |  | 2013-08-05 | 2013-08-05 15:28 | 2013-08-05 15:33 | OTHER - BRC00481BD | 103 | 3.4 | Yes | Yes | 24.3 | 20.4 | 3.9 | 4CA8C79FEB624CF2BF92C7BB8193261D |  | R22 | Non-TXV |  | 3.301% | 0.96699 | 6.344% | [5 empty] | Non-TXV | 3.301%
Stockton | CA | 95206-5245 |  | 2013-06-20 | 2013-06-20 14:03 | 2013-06-20 14:37 | BRYANT - 563CN042-A | 166 | 7.1 | Yes | Yes | 20.4 | 21.4 | -1 | CCAE1370411149FD9BCC772BC30FB068 |  | R22 | Non-TXV |  | 4.277% | 0.95723 | 8.22% | [5 empty] | Non-TXV | 4.277%
Stockton | CA | 95206-5245 |  | 2013-06-20 | 2013-06-20 14:41 | 2013-06-20 14:58 | BRYANT - 563CN030-A | 159 | 9.3 | Yes | Yes | 18.4 | 19.6 | -1.2 | 5724FBB066C14F7A9CAF2A0DE531EE41 |  | R22 | Non-TXV |  | 5.849% | 0.94151 | 11.24% | [5 empty] | Non-TXV | 5.849%
Fresno | CA | 93710-5367 |  | 2013-06-24 | 2013-06-24 14:45 | 2013-06-24 15:01 | PAYNE - PY3PNA02406NA | 123 | -8.7 | Yes | Yes | 16 | 16.3 | -0.3 | 9DE9A67802B140A2AAAE3B11AD5FD1DF |  | R22 | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Yuba City | CA | 95993-9431 |  | 2013-06-19 | 2013-06-19 08:30 | 2013-06-19 08:49 | OTHER - 38BRC036330 | 101 | 3 | Yes | Yes | 15 | 17.7 | -2.7 | 136036E04D024F278B1B7A4B649EF1BF |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Merced | CA | 95341-7038 |  | 2013-06-11 | 2013-06-11 11:14 | 2013-06-11 11:20 | KENMORE - 13ACD036230 | 111 | 6.5 | Yes | Yes | 18.6 | 18.5 | 0.1 | B8230C242264494DABCB1D266366ED07 |  | R22 | Non-TXV |  | 5.856% | 0.94144 | 11.25% | [5 empty] | Non-TXV | 5.856%
Stockton | CA | 95210-3331 |  | 2013-06-05 | 2013-06-05 13:06 | 2013-06-05 13:24 | RUUD - UAKA-048JAZ | 103 | 3.3 | Yes | Yes | 25.9 | 19.9 | 6 | 53EAAF44D77A46178102F1417695B732 |  | R22 | Non-TXV |  | 3.204% | 0.96796 | 6.157% | [5 empty] | Non-TXV | 3.204%
Oroville | CA | 95966-9492 |  | 2013-06-21 | 2013-06-21 11:44 | 2013-06-21 12:01 | CARRIER - 50JS-048-301- | 120 | 6.1 | Yes | Yes | 22.5 | 20.4 | 2.1 | CFA622739777459DBA867C7354CF2E6F |  | R22 | Non-TXV |  | 5.083% | 0.94917 | 9.769% | [5 empty] | Non-TXV | 5.083%
Livingston | CA | 95334-9679 |  | 2013-06-11 | 2013-06-11 09:46 | 2013-06-11 10:17 | BDP - 588ANW030040ACAD | 53 | 6.9 | Yes | Yes | 15.9 | 18.7 | -2.8 | CF040E04137E464EA443997D02C3CCF8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.02% | 0.86981 | 25.02% | [5 empty] | Non-TXV | 13.02%
Corning | CA | 96021-9205 |  | 2013-07-22 | 2013-07-22 19:01 | 2013-07-22 19:01 | GUARDIAN - 6HRP3654151A | 120 | 3.6 | Yes | Yes | 20.4 | 22.3 | -1.9 | 9CA3E0F6E89A4EFB9B960933C266F5FB | Add refrigerant: 3.6 oz | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Oroville | CA | 95966-9423 |  | 2013-07-29 | 2013-07-29 08:59 | 2013-07-29 08:59 | LENNOX - GCS20R-411-75-2P | 70 | 0 | Yes | Yes | 16.3 | 19.1 | -2.8 | C5C30FD6A7224180A993DE285F26234D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3235 |  | 2013-05-29 | 2013-05-29 11:58 | 2013-05-29 12:13 | AIRE-FLO - UNK | 86 | 6.7 | Yes | Yes | 18.5 | 19.3 | -0.8 | D8671DF342B048349FBB8B2BC46809A8 |  | R22 | Non-TXV |  | 7.791% | 0.92209 | 14.97% | [5 empty] | Non-TXV | 7.791%
Clovis | CA | 93611-2407 |  | 2013-06-13 | 2013-06-13 11:57 | 2013-06-13 12:09 | LENNOX - 13ACC-048-230-02 | 159 | 5 | Yes | Yes | 20 | 20.4 | -0.4 | 6E25F37E1E514260986ED086C2515FAA |  | R22 | Non-TXV |  | 3.145% | 0.96855 | 6.043% | [5 empty] | Non-TXV | 3.145%
Los Banos | CA | 93635-6360 |  | 2013-06-03 | 2013-06-03 12:33 | 2013-06-03 12:44 | BRYANT - 561CJ36 | 70 | 10.6 | Yes | Yes | 20.6 | 21 | -0.4 | 8EE2F5CDE37B4C2FA9F2D7E4860B2E46 |  | R22 | TXV |  | 15.14% | 0.84857 | 29.1% | [5 empty] | TXV | 15.14%
Chico | CA | 95926-7320 |  | 2013-06-05 | 2013-06-05 13:50 | 2013-06-05 14:16 | LENNOX - 14ACX-036-230-10 | 107 | -4.3 | Yes | Yes | 20.1 | 19.8 | 0.3 | C9B4299496404CE3B0816A0FAA1CDB6A |  | R410A | TXV |  | -4.019% | 1.0402 | 1.125% |  |  |  |  | TXV |  |  | -4.019%
Fresno | CA | 93720-3685 |  | 2013-06-25 | 2013-06-25 11:27 | 2013-06-25 11:31 | YORK - H1DE036S06A | 84 | 6.9 | Yes | Yes | 23.1 | 20.6 | 2.5 | 0535009A7B594BE384CFE80D91E348B3 |  | R22 | Non-TXV |  | 8.214% | 0.91786 | 15.79% | [5 empty] | Non-TXV | 8.214%
Tracy | CA | 95377-7976 |  | 2013-06-04 | 2013-06-04 12:51 | 2013-06-04 13:31 | GOODMAN - CLT30-1A | 85 | -7 | Yes | Yes | 24.3 | 18.5 | 5.8 | 37C8484581844610AE36F7290301A986 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Paradise | CA | 95969-5231 |  | 2013-06-29 | 2013-06-29 09:54 | 2013-06-29 11:38 | RHEEM - RRNA-A030JK06E | 112 | 12.1 | Yes | Yes | 25.6 | 19.9 | 5.7 | 1D253FB6F1B14414A63ACD231976694F |  | R22 | Non-TXV |  | 10.8% | 0.89196 | 20.76% | [5 empty] | Non-TXV | 10.8%
Auburn | CA | 95603-3020 |  | 2013-06-04 | 2013-06-04 12:57 | 2013-06-04 12:57 | TRANE - 4YCY4036B1075AA | 85 | 0 | Yes | Yes | 25.8 | 20.4 | 5.4 | AD7F4B072C384918B486B0754AA8D00D |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-9680 |  | 2013-06-06 | 2013-06-06 14:49 | 2013-06-06 14:49 | LENNOX - HP14311-511V-11P | 224 | 0 | Yes | Yes | 23.1 | 17.3 | 5.8 | E48FA00E00564C89B10982CFD50DFF43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1145 |  | 2013-08-05 | 2013-08-05 14:32 | 2013-08-05 14:50 | BDP - 585A030080YACR | 50 | 4.2 | Yes | Yes | 29 | 23 | 6 | 8C291D464CC748AAB846D87A0013D2DE |  | R22 | Non-TXV |  | 8.4% | 0.916 | 16.14% | [5 empty] | Non-TXV | 8.4%
Merced | CA | 95340-3439 |  | 2013-06-17 | 2013-06-17 13:50 | 2013-06-17 13:57 | RHEEM - UNK | 67 | 9 | Yes | Yes | 25.5 | 20.9 | 4.6 | 76BBE9DA675A4C56B55DAA4D2218F2C4 |  | R22 | Non-TXV |  | 13.43% | 0.86567 | 25.81% | [5 empty] | Non-TXV | 13.43%
Stockton | CA | 95207-1145 |  | 2013-05-29 | 2013-05-29 12:46 | 2013-05-29 12:46 | YORK - D1NA030N05606C | 85 | 0 | Yes | Yes | 19.8 | 18.8 | 1 | BC3C35A0BFA242998CC0A0EBF2E1749A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-4489 |  | 2013-08-12 | 2013-08-12 11:41 | 2013-08-12 12:03 | RHEEM - RAKA018JAZ | 85 | 6.2 | Yes | Yes | 24.7 | 21.7 | 3 | 23B593EC0FBF46DAB41EBCFEE7F54200 |  | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Tracy | CA | 95376-3103 |  | 2013-05-29 | 2013-05-29 14:18 | 2013-05-29 14:38 | AMERICAN STANDARD - YCC036F1MOBF | 83 | -8 | Yes | Yes | 20.9 | 19.3 | 1.6 | 04D9A7C5957F40268D59AA332E0700E3 |  | R22 | Non-TXV |  | -9.639% | 1.0964 | 2.699% |  |  |  |  | Non-TXV |  |  | -9.639%
Placerville | CA | 95667-8802 |  | 2013-07-10 | 2013-07-10 09:26 | 2013-07-10 09:48 | YORK - YMA04211A | 140 | 5.1 | Yes | Yes | 26 | 22 | 4 | 425D9317E8984A37B5CF21657313797D |  | R22 | TXV |  | 3.643% | 0.96357 | 7.001% | [5 empty] | TXV | 3.643%
Stockton | CA | 95204-2007 |  | 2013-06-28 | 2013-06-28 11:17 | 2013-06-28 11:21 | OTHER - N2A336AKB300 | 86 | -8.1 | Yes | Yes | 18.4 | 19.3 | -0.9 | F1BA557A774145058799114C2AC57631 |  | R22 | Non-TXV |  | -9.419% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.419%
Paso Robles | CA | 93446-4489 |  | 2013-08-12 | 2013-08-12 11:20 | 2013-08-12 11:38 | RUUD - UNK | 60 | 4.8 | Yes | Yes | 23.5 | 20.4 | 3.1 | B3310AD0764A41ECA70F1C169EF9680A |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Stockton | CA | 95206-5233 |  | 2013-06-20 | 2013-06-20 09:11 | 2013-06-20 09:37 | RHEEM - UNK | 85 | 5 | Yes | Yes | 23.8 | 21 | 2.8 | 1D01AB1E775D413AB0A998CAD4F73065 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Clovis | CA | 93611-5158 |  | 2013-06-15 | 2013-06-15 09:52 | 2013-06-15 10:17 | BDP - 585GJW036060ABAF | 82 | 2.6 | Yes | Yes | 22.9 | 20.9 | 2 | DB034425A8204C6F97D75D9844172C03 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Stockton | CA | 95207-1146 |  | 2013-05-29 | 2013-05-29 16:19 | 2013-05-29 16:37 | PAYNE - 585A030080YACR | 85 | 5 | Yes | Yes | 24.4 | 20.4 | 4 | E31BB91CF8824D7F9DF5F5A68C9AE122 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
El Dorado Hills | CA | 95762-5385 |  | 2013-10-01 | 2013-10-01 15:59 | 2013-10-01 15:59 | CARRIER - 38EN036320 | 93 | 0 | Yes | Yes | 23.7 | 20.2 | 3.5 | 5E04EA90128140CF992E21D36519CFFE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3229 |  | 2013-05-29 | 2013-05-29 11:32 | 2013-05-29 11:38 | DAY & NIGHT - 588ANW024040AAAD | 41 | 4.5 | Yes | Yes | 24.8 | 20.6 | 4.2 | 084DD5BEC76446A184801BF15FC52B90 |  | R22 | Non-TXV |  | 10.98% | 0.89024 | 21.09% | [5 empty] | Non-TXV | 10.98%
Stockton | CA | 95210-2011 |  | 2013-06-12 | 2013-06-12 11:01 | 2013-06-12 11:19 | PAYNE - PA12NA036-B | 101 | -5.9 | Yes | Yes | 18.9 | 18.8 | 0.1 | D9CD4360CC834D158EDB59A98CA391C7 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Stockton | CA | 95209-1762 |  | 2013-06-10 | 2013-06-10 14:22 | 2013-06-10 14:39 | OTHER - N2A342AKA300 | 106 | -10 | Yes | Yes | 26.3 | 20.6 | 5.7 | 192BD39A10194982B12E4F029780A3AE |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Orland | CA | 95963-1420 |  | 2013-06-17 | 2013-06-17 08:40 | 2013-06-17 09:43 | LENNOX - HS29-030-1P | 68 | 2 | Yes | Yes | 20.1 | 19.3 | 0.8 | 4A0FFA5E02894FB4A3CCD774D90314AB |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95210-3325 |  | 2013-06-06 | 2013-06-06 08:37 | 2013-06-06 08:55 | HEIL - NAC042AKA1 | 105 | -6.2 | Yes | Yes | 21.7 | 18.2 | 3.5 | 241B9C76AC204688891E948C73A8BF66 |  | R22 | Non-TXV |  | -5.905% | 1.059 | 1.654% |  |  |  |  | Non-TXV |  |  | -5.905%
Stockton | CA | 95204-2016 |  | 2013-05-30 | 2013-05-30 13:52 | 2013-05-30 13:52 | RHEEM - AT-38B1 Q | 45 | 0 | Yes | Yes | 19.4 | 19.3 | 0.1 | 526C4AA84C4F4AF5A5A62C9016605256 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-4036 |  | 2013-08-06 | 2013-08-06 14:38 | 2013-08-06 14:57 | WEATHER KING - 10AJA4801 | 90 | 2.6 | Yes | Yes | 17.3 | 19.8 | -2.5 | 4ED2220B3A964CB5AFF9791AB88C41BD |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Clovis | CA | 93612-5880 |  | 2013-06-19 | 2013-06-19 17:51 | 2013-06-19 18:10 | CARRIER - 48BR042300 | 131 | 11.4 | Yes | Yes | 23.2 | 21.7 | 1.5 | 56942BD0748A419EB7E3099E4AE08689 |  | R22 | Non-TXV |  | 8.702% | 0.91298 | 16.72% | [5 empty] | Non-TXV | 8.702%
Marysville | CA | 95901-7204 |  | 2013-06-03 | 2013-06-03 09:20 | 2013-06-03 09:40 | AMANA - PGD420902D | 105 | 5.4 | Yes | Yes | 27 | 21.3 | 5.7 | CE421BBF3F9F4214B8846C08A3EE9E50 |  | R22 | Non-TXV |  | 5.143% | 0.94857 | 9.883% | [5 empty] | Non-TXV | 5.143%
Tracy | CA | 95377-1150 |  | 2013-07-19 | 2013-07-19 12:52 | 2013-07-19 13:14 | CARRIER - 38BRC042-341 | 110 | 7.6 | Yes | Yes | 26 | 21.9 | 4.1 | 97E3F48CF360464285C0A13BA6548928 |  | R22 | Non-TXV |  | 6.909% | 0.93091 | 13.28% | [5 empty] | Non-TXV | 6.909%
Stockton | CA | 95204-2030 |  | 2013-06-01 | 2013-06-01 12:11 | 2013-06-01 12:42 | GE - BTN930A100A2 | 150 | 9.3 | Yes | Yes | 27.1 | 21.2 | 5.9 | C1771A95FE844059A7D5EDC82041754F |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Fresno | CA | 93703-1404 |  | 2013-06-07 | 2013-06-07 10:30 | 2013-06-07 11:51 | BRYANT - 582ANW048090AAAG | 83 | 2.5 | Yes | Yes | 16.7 | 19.2 | -2.5 | 91C42C366AFE4862A18D7A30B1C408EC |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Los Banos | CA | 93635-3042 |  | 2013-10-17 | 2013-10-17 09:01 | 2013-10-17 09:02 | YORK - 777UNK | 90 | 3.4 | Yes | Yes | 21.8 | 19.1 | 2.7 | A4F8B204B1684E4984F200302F806FE0 |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Stockton | CA | 95207-1124 |  | 2013-05-29 | 2013-05-29 11:34 | 2013-05-29 11:58 | PAYNE - 585A030080YACR | 50 | 2.1 | Yes | Yes | 21.8 | 18.3 | 3.5 | A562325A3960461087DD254CFD39856F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Los Banos | CA | 93635-9452 |  | 2013-06-13 | 2013-06-13 09:50 | 2013-06-13 09:55 | BRYANT - 561CJ036 | 70 | 10.2 | Yes | Yes | 23.5 | 20.4 | 3.1 | 563468E3396C4EE98CDD002941F3651D |  | R22 | TXV |  | 14.57% | 0.85429 | 28% | [5 empty] | TXV | 14.57%
Los Banos | CA | 93635-9452 |  | 2013-06-13 | 2013-06-13 09:58 | 2013-06-13 10:25 | BRYANT - 561CJ036 | 70 | 8.3 | Yes | Yes | 19.5 | 22.2 | -2.7 | 3DDA3CA985684A1A9BC0C7DE6DAEA765 |  | R22 | TXV |  | 11.86% | 0.88143 | 22.79% | [5 empty] | TXV | 11.86%
Stockton | CA | 95207-2210 |  | 2013-06-13 | 2013-06-13 12:41 | 2013-06-13 12:41 | AMANA - PGB24C0452E | 64 | 0 | Yes | Yes | 24.2 | 20.4 | 3.8 | 5C0DC6D32F824F9885A166254C3E759D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-9426 |  | 2013-06-04 | 2013-06-04 13:47 | 2013-06-04 13:55 | BRYANT - 561CJ042 | 80 | 3.7 | Yes | Yes | 17.3 | 19.3 | -2 | C1CFEEA93A3048BDA3D640C8D32487A7 |  | R22 | TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | TXV | 4.625%
Fresno | CA | 93726-0948 |  | 2013-05-31 | 2013-05-31 13:27 | 2013-05-31 13:46 | DAY & NIGHT - N/A | 60 | 3.7 | Yes | Yes | 19.3 | 17.3 | 2.1 | 5F6743F2F5C0429B9F735D4887239913 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.167% | 0.93833 | 11.85% | [5 empty] | Non-TXV | 6.167%
Stockton | CA | 95207-1157 |  | 2013-05-31 | 2013-05-31 09:13 | 2013-05-31 09:33 | DAY & NIGHT - 535A030080YACR | 50 | 8.9 | Yes | Yes | 20.2 | 19.8 | 0.4 | CF9C2AE82C5C486DA1CE804F38DBCE79 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.8% | 0.822 | 34.21% | [5 empty] | Non-TXV | 17.8%
Rocklin | CA | 95677-2273 |  | 2013-06-17 | 2013-06-17 15:31 | 2013-06-17 15:31 | RHEEM - UNK | 90 | 0 | Yes | Yes | 20 | 22 | -2 | DDB08B8BC4584B6A8E795922108E1F54 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-2273 |  | 2013-06-17 | 2013-06-17 15:51 | 2013-06-17 15:51 | AMANA - RCE60C2A | 245 | 0 | Yes | Yes | 21 | 22.4 | -1.4 | 3BA2A97B714342DFBC2B5821E173AE4D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2868 |  | 2013-07-16 | 2013-07-16 14:02 | 2013-07-16 14:22 | RHEEM - 13AJA36A01757 | 66 | 2.3 | Yes | Yes | 24.2 | 18.8 | 5.5 | EA74C43175EE45279C7D413A43816087 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Merced | CA | 95341-7008 |  | 2013-06-11 | 2013-06-11 13:26 | 2013-06-11 13:34 | GOODMAN - CLJ301 | 96 | 4.6 | Yes | Yes | 16.4 | 16.4 | 0 | 28000740F4414E2FA1BE6A098D099BFA |  | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Los Banos | CA | 93635-5402 |  | 2013-06-03 | 2013-06-03 10:13 | 2013-06-03 10:15 | AIRE-FLO - UNK | 82 | 4.8 | Yes | Yes | 20.6 | 20.4 | 0.2 | 7D92CA2CF21C481D840586FD130A2EC9 |  | R22 | Non-TXV |  | 5.854% | 0.94146 | 11.25% | [5 empty] | Non-TXV | 5.854%
Madera | CA | 93637-5659 |  | 2013-06-18 | 2013-06-18 16:54 | 2013-06-18 21:16 | YORK - 2400E26460 | 100 | 3 | Yes | Yes | 18.5 | 20.1 | -1.6 | 4B1B588BED61490993F5A62ACB3D6683 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Magalia | CA | 95954-8816 |  | 2013-07-17 | 2013-07-17 09:34 | 2013-07-17 10:07 | WHIRLPOOL - P67220-12065251188 | 102 | 4 | Yes | Yes | 17.6 | 15.9 | 1.7 | 19E5D3AB68CF48A08160853346D531E9 |  | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Dinuba | CA | 93618-3016 |  | 2013-08-10 | 2013-08-10 14:59 | 2013-08-10 16:06 | RHEEM - RRNL-B024JK06X | 77 | 3.4 | Yes | Yes | 16.5 | 19 | -2.5 | AB3279D7644D4ED7AB519C4CB4561B88 |  | R410A | TXV |  | 4.416% | 0.95584 | 8.486% | [5 empty] | TXV | 4.416%
Gustine | CA | 95322-1360 |  | 2013-09-05 | 2013-09-05 18:23 | 2013-09-05 18:25 | GOODMAN - CK36A1-A | 73 | 2.3 | Yes | Yes | 18.7 | 19.3 | -0.6 | CCE8879471804470A7869A48A4937CF4 |  | R22 | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Dinuba | CA | 93618-1820 |  | 2013-07-25 | 2013-07-25 15:21 | 2013-07-25 15:54 | BRYANT - 582ANW042060AAAF | 117 | 5.7 | Yes | Yes | 16.4 | 19.3 | -2.9 | BB7DFF4AB8734D41868B0B7112311E95 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.872% | 0.95128 | 9.363% | [5 empty] | Non-TXV | 4.872%
Clovis | CA | 93612-4327 |  | 2013-08-15 | 2013-08-15 16:36 | 2013-08-15 17:01 | DAY & NIGHT - N/A | 90 | 4.1 | Yes | Yes | 20 | 19.7 | 0.3 | 125237CE0ED049CD89489A86D4DED814 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.556% | 0.95444 | 8.755% | [5 empty] | Non-TXV | 4.556%
Somerset | CA | 95684-0000 |  | 2013-08-12 | 2013-08-12 10:02 | 2013-08-12 10:02 | OTHER - 13AJA42A01 | 121 | 0 | Yes | Yes | 26.4 | 21.1 | 5.4 | 06506EEAD069428398200845E4CBEEB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6559 |  | 2013-08-05 | 2013-08-05 10:04 | 2013-08-05 10:23 | YORK - D3NZ030N05606NXB | 64 | 1.9 | Yes | Yes | 25.3 | 19.4 | 5.9 | 50DBF5A5D1E240C783ECCC039CE2AC7B |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Yuba City | CA | 95993-6034 |  | 2013-08-28 | 2013-08-28 17:43 | 2013-08-28 18:01 | OTHER - HAA8-F024SA | 118 | 5 | Yes | Yes | 18 | 17.1 | 0.9 | 9849EED202E2476A984336E049587691 |  | R22 | Non-TXV |  | 4.237% | 0.95763 | 8.143% | [5 empty] | Non-TXV | 4.237%
Rocklin | CA | 95677-2200 |  | 2013-07-27 | 2013-07-27 12:23 | 2013-07-27 12:40 | AMERICAN STANDARD - 2A7B3060A1000AA | 139 | 9 | Yes | Yes | 18 | 20.8 | -2.8 | 99EBDB2C5D874CBDA376440408E4EE3F |  | R22 | TXV |  | 6.475% | 0.93525 | 12.44% | [5 empty] | TXV | 6.475%
Lathrop | CA | 95330-8833 |  | 2013-06-07 | 2013-06-07 11:25 | 2013-06-07 11:47 | GOODMAN - CKL036-1 | 88 | 7.9 | Yes | Yes | 19.6 | 20.4 | -0.8 | B251CC83281E47D292B833469B66D62B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.977% | 0.91023 | 17.25% | [5 empty] | Non-TXV | 8.977%
Fresno | CA | 93710-6452 |  | 2013-06-03 | 2013-06-03 09:44 | 2013-06-03 10:07 | CARRIER - 38TH036300 | 86 | -5.1 | Yes | Yes | 22.1 | 19.4 | 2.7 | 2A3D4FB0A30349649BCCA7098F6F45FD |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
El Dorado | CA | 95623-4304 |  | 2013-08-15 | 2013-08-15 11:18 | 2013-08-15 11:18 | BRYANT - 60ANX030000AAAD | 93 | 0 | Yes | Yes | 26.1 | 21.8 | 4.3 | A2347D35C8714D5AB5286968D4066514 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3016 |  | 2013-06-17 | 2013-06-17 11:08 | 2013-06-17 11:26 | TRANE - YCY042F1MOAB | 133 | 4.3 | Yes | Yes | 19.5 | 19.3 | 0.2 | 742FA3C85D904298841A8B79E5970A48 |  | R22 | Non-TXV |  | 3.233% | 0.96767 | 6.213% | [5 empty] | Non-TXV | 3.233%
Stockton | CA | 95210-1605 |  | 2013-06-10 | 2013-06-10 09:01 | 2013-06-10 09:18 | AMANA - PGD30C0702G | 70 | -4.1 | Yes | Yes | 16.5 | 19.1 | -2.6 | 2AB1F5A5444049C8891A17D84345F94D |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Fresno | CA | 93726-2644 |  | 2013-06-03 | 2013-06-03 13:35 | 2013-06-03 13:59 | CARRIER - 48GS-036060301 | 56 | 1.9 | Yes | Yes | 15.3 | 17.5 | -2.2 | DEEA052912614BDA973FF77446E30079 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Stockton | CA | 95207-1143 |  | 2013-05-29 | 2013-05-29 12:14 | 2013-05-29 12:14 | PAYNE - 585A024055YACR | 51 | 0 | Yes | Yes | 22.2 | 19.8 | 2.4 | 18C394A9CDC54C8999D65D9EA91319FD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6514 |  | 2013-05-31 | 2013-05-31 14:21 | 2013-05-31 15:05 | BDP - 565BJ024 | 70 | 13.2 | Yes | Yes | 23.9 | 21.5 | 2.4 | 473D9A0EAD8741659BADF84C3E7DF09C |  | R22 | Non-TXV |  | 18.86% | 0.81143 | 36.24% | [5 empty] | Non-TXV | 18.86%
Los Banos | CA | 93635-3087 |  | 2013-05-29 | 2013-05-29 10:11 | 2013-05-29 10:24 | NORDYNE - UNK | 78 | 6.7 | Yes | Yes | 17.9 | 19.3 | -1.4 | 77017EB6CA9B41318D336793320EA6D0 |  | R22 | Non-TXV |  | 8.59% | 0.9141 | 16.51% | [5 empty] | Non-TXV | 8.59%
Los Banos | CA | 93635-5307 |  | 2013-06-03 | 2013-06-03 10:55 | 2013-06-03 11:07 | RUUD - UAHE042JAS | 101 | 10 | Yes | Yes | 18.8 | 20.4 | -1.6 | 6ABD2D6B2EAF40058B8AC87C9F2A61DB |  | R22 | Non-TXV |  | 9.901% | 0.90099 | 19.03% | [5 empty] | Non-TXV | 9.901%
Cameron Park | CA | 95682-8642 |  | 2013-05-30 | 2013-05-30 16:15 | 2013-05-30 16:15 | LENNOX - HPXA19-048-230-01 | 206 | 0 | Yes | Yes | 25.8 | 21.5 | 4.3 | C9517B3240D44886AD86C218D07935C6 |  | R410A | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-6107 |  | 2013-06-19 | 2013-06-19 14:38 | 2013-06-19 15:03 | BRYANT - 563CN042-E | 105 | 4.4 | Yes | Yes | 20 | 17.9 | 2.1 | D955A104B22449468061C3ED10E105FC |  | R22 | Non-TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | Non-TXV | 4.19%
Yuba City | CA | 95993-6107 |  | 2013-06-19 | 2013-06-19 14:50 | 2013-06-19 15:10 | BRYANT - UNK | 85 | 3 | Yes | Yes | 21 | 20.4 | 0.6 | F1BCF93AD83D4BE7BBAD5CDFD58A5D32 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Merced | CA | 95340-3380 |  | 2013-07-11 | 2013-07-11 12:30 | 2013-07-11 12:31 | RHEEM - UNK | 64 | 7.4 | Yes | Yes | 22.2 | 20.4 | 1.8 | DE1F966EB8C94C39B84E92C0478DBB5C |  | R22 | Non-TXV |  | 11.56% | 0.88438 | 22.22% | [5 empty] | Non-TXV | 11.56%
Stockton | CA | 95207-2839 |  | 2013-05-30 | 2013-05-30 14:27 | 2013-05-30 14:47 | GOODMAN - CKL36-1D | 72 | 7 | Yes | Yes | 26.9 | 21 | 5.9 | 2107DDC25D1E4738BEFC407B9D65CA84 |  | R22 | Non-TXV |  | 9.722% | 0.90278 | 18.68% | [5 empty] | Non-TXV | 9.722%
Stockton | CA | 95210-3332 |  | 2013-06-05 | 2013-06-05 12:25 | 2013-06-05 12:43 | CARRIER - 38EN048300 | 122 | -7.2 | Yes | Yes | 22.6 | 19.6 | 3 | B7EC70CA57FD4EEF986FDC61E18F4FCE |  | R22 | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Stockton | CA | 95210-3608 |  | 2013-07-12 | 2013-07-12 10:19 | 2013-07-12 10:44 | CARRIER - 38CKC048370 | 100 | -5.9 | Yes | Yes | 26 | 20.4 | 5.6 | F0E8764170FF4417B52EDD44483E0BD6 |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Yuba City | CA | 95993-5907 |  | 2013-06-10 | 2013-06-10 13:30 | 2013-06-10 13:52 | BRYANT - 563CN030-0 | 101 | -8.3 | Yes | Yes | 19 | 18.2 | 0.8 | AFCD5E99229F4582A854FC10EEE5A06A |  | R22 | Non-TXV |  | -8.218% | 1.0822 | 2.301% |  |  |  |  | Non-TXV |  |  | -8.218%
Yuba City | CA | 95993-5907 |  | 2013-06-10 | 2013-06-10 13:53 | 2013-06-10 14:14 | BRYANT - UNK | 101 | 9 | Yes | Yes | 18 | 21 | -3 | 17885F2A1A154F2CBE2765D0F59C0DBB |  | R22 | Non-TXV |  | 8.911% | 0.91089 | 17.12% | [5 empty] | Non-TXV | 8.911%
Stevinson | CA | 95374-9767 |  | 2013-09-17 | 2013-09-17 12:50 | 2013-09-17 12:54 | OTHER - BRC0301BD | 52 | 2.6 | Yes | Yes | 17.6 | 20.5 | -2.9 | 00FA6F61A1724968BBE5F9A7405E74B9 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93726-1108 |  | 2013-05-29 | 2013-05-29 17:00 | 2013-05-29 17:21 | ICP - PGAD42D1K3 | 180 | 5.4 | Yes | Yes | 22.6 | 19.5 | 3.1 | 334D1ACBECA946FDBE262D5FD054CC9D |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95973-7660 |  | 2013-07-11 | 2013-07-11 10:05 | 2013-07-11 10:37 | OTHER - 3294E10280 | 102 | 6.3 | Yes | Yes | 17.5 | 20.3 | -2.8 | 150F2B4803D7447AA3D4394C5E3EBE3E |  | R22 | Non-TXV |  | 6.176% | 0.93824 | 11.87% | [5 empty] | Non-TXV | 6.176%
Dinuba | CA | 93618-1855 |  | 2013-06-20 | 2013-06-20 13:10 | 2013-06-20 13:28 | RHEEM - N/A | 85 | 6 | Yes | Yes | 20.5 | 19.4 | 1.1 | C84EEC95862A4B638911AB66892A719F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Manteca | CA | 95337-6527 |  | 2013-05-29 | 2013-05-29 15:03 | 2013-05-29 15:30 | DAY & NIGHT - 565BJ018 | 50 | 1.5 | Yes | Yes | 21.6 | 19.7 | 1.9 | CB6583A1377845B5A32762CBE2724C2E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93726-0967 |  | 2013-05-29 | 2013-05-29 13:16 | 2013-05-29 13:37 | YORK - D3NP024N03606A | 100 | 3.1 | Yes | Yes | 20.1 | 19.3 | 0.8 | F050574568DD41F4B70581B9AAFF5E5F |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Chico | CA | 95926-2413 |  | 2013-08-01 | 2013-08-01 09:39 | 2013-08-01 09:39 | ICP - N2A448GKA100 | 234 | 0 | Yes | Yes | 17.7 | 19.3 | -1.6 | 9342458F4996430380FE7D04E6F14D90 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-8337 |  | 2013-07-17 | 2013-07-17 10:35 | 2013-07-17 10:55 | YORK - H2RC042S06HA | 109 | 20.6 | Yes | Yes | 17 | 19.2 | -2.2 | 05BD0F1F2B7741458C850927F76608AC |  | R22 | Non-TXV |  | 18.9% | 0.81101 | 36.32% | [5 empty] | Non-TXV | 18.9%
Yuba City | CA | 95993-5147 |  | 2013-06-20 | 2013-06-20 15:05 | 2013-06-20 15:28 | BRYANT - 561J030- | 75 | 11.9 | Yes | Yes | 31 | 25.3 | 5.7 | 91186AB2933042EE94B2595CDE14535A |  | R22 | Non-TXV |  | 15.87% | 0.84133 | 30.49% | [5 empty] | Non-TXV | 15.87%
Stockton | CA | 95212-1812 |  | 2013-06-12 | 2013-06-12 09:55 | 2013-06-12 10:22 | LENNOX - UNK | 64 | 2.1 | Yes | Yes | 21.6 | 18.9 | 2.7 | 6337AC8BE74F4E919929C08672091A68 |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Stockton | CA | 95210-2324 |  | 2013-06-19 | 2013-06-19 11:25 | 2013-06-19 11:46 | CARRIER - 48SS024040321 | 38 | 17.6 | Yes | Yes | 20.2 | 22.4 | -2.2 | 483886325AD242D68BCD25E0318BC363 |  | R22 | Non-TXV |  | 46.32% | 0.53684 | 89.01% | [5 empty] | Non-TXV | 46.32%
Merced | CA | 95348-1547 |  | 2013-06-11 | 2013-06-11 09:47 | 2013-06-11 09:50 | OTHER - UNK | 65 | 7 | Yes | Yes | 24.9 | 19.1 | 5.9 | FE50733C03394FBFB0E0101378A6D1C8 |  | R22 | Non-TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | Non-TXV | 10.77%
Yuba City | CA | 95993-6095 |  | 2013-06-19 | 2013-06-19 13:08 | 2013-06-19 13:30 | BRYANT - 563CN042-D | 105 | 3.1 | Yes | Yes | 20 | 19.4 | 0.6 | 33C651A4DFF54717B70AD5976CF3720F |  | R22 | Non-TXV |  | 2.952% | 0.97048 | 5.674% | [5 empty] | Non-TXV | 2.952%
Yuba City | CA | 95993-5002 |  | 2013-06-06 | 2013-06-06 09:17 | 2013-06-06 09:37 | LENNOX - 10ACC-060-230-02 | 130 | 9.4 | Yes | Yes | 20 | 19.3 | 0.7 | 7638B5EFF4FF4542B15108EA8AAE8777 |  | R22 | Non-TXV |  | 7.231% | 0.92769 | 13.9% | [5 empty] | Non-TXV | 7.231%
Merced | CA | 95341-7027 |  | 2013-06-08 | 2013-06-08 11:15 | 2013-06-08 11:17 | BRYANT - 582ANW042060NAAG | 100 | 4.1 | Yes | Yes | 21.8 | 19.5 | 2.3 | 7C972D16AA534B359F958894294FFBB5 |  | R22 | Non-TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | Non-TXV | 4.1%
Oroville | CA | 95966-6738 |  | 2013-07-29 | 2013-07-29 13:00 | 2013-07-29 13:33 | TRANE - 2TTB3030A10000AA | 88 | 5.6 | Yes | Yes | 22.5 | 20.9 | 1.6 | 0696A6F0756440C08D336026FA3FA530 |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Stockton | CA | 95206-6395 |  | 2013-06-18 | 2013-06-18 14:27 | 2013-06-18 14:46 | GOODMAN - CLJ42-1A | 99 | 5.8 | Yes | Yes | 23.3 | 19.8 | 3.5 | 48D8664CE1AC4D58A343244771BCE71F |  | R22 | TXV |  | 5.859% | 0.94141 | 11.26% | [5 empty] | TXV | 5.859%
Winton | CA | 95388-9787 |  | 2013-06-24 | 2013-06-24 17:20 | 2013-06-24 17:33 | ICP - PGF036K060D | 71 | 3.1 | Yes | Yes | 21.5 | 18.8 | 2.7 | 0CA088837A50497BB226D54ABA08DAFF |  | R22 | Non-TXV |  | 4.366% | 0.95634 | 8.391% | [5 empty] | Non-TXV | 4.366%
Santa Maria | CA | 93458-9068 |  | 2013-10-10 | 2013-10-10 11:07 | 2013-10-10 11:23 | YORK - H2DB036S06A | 73 | -7.3 | Yes | Yes | 21.8 | 19.5 | 2.3 | 7D52122509834B2588516F0F40EDD665 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Live Oak | CA | 95953-2419 |  | 2013-08-05 | 2013-08-05 17:45 | 2013-08-05 18:06 | BRYANT - 563CN036-D | 100 | 4.5 | Yes | Yes | 18 | 21 | -3 | D124FB48E9C148269CC6E6EBAF9EF7A9 |  | R22 | TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | TXV | 4.5%
Stockton | CA | 95210-2039 |  | 2013-06-17 | 2013-06-17 15:01 | 2013-06-17 15:01 | RHEEM - A1-38B10 | 50 | 0 | Yes | Yes | 17.3 | 19.6 | -2.3 | B5A8B16A90564C489FC47665466D3E9E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-3145 |  | 2013-08-02 | 2013-08-02 13:36 | 2013-08-02 13:58 | TRANE - YCX036F1M0BB | 116 | 3.4 | Yes | Yes | 19.3 | 18.8 | 0.5 | 68363C6B63AC421D924243D54EC87556 |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Granite Bay | CA | 95746-9618 |  | 2013-06-22 | 2013-06-22 10:14 | 2013-06-22 10:14 | RUUD - UPKA-049JAZ | 130 | 0 | Yes | Yes | 21.3 | 20.1 | 1.2 | E353F97239EA4E6F95BD96C957F118B6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-4328 |  | 2013-05-29 | 2013-05-29 12:10 | 2013-05-29 12:43 | DAY & NIGHT - CA5536UKVC1 | 85 | 8.4 | Yes | Yes | 21.1 | 19.6 | 1.5 | 502A9CFCE40442318A77BAEF7D22EB9A |  | R22 | Non-TXV |  | 9.882% | 0.90118 | 18.99% | [5 empty] | Non-TXV | 9.882%
Lincoln | CA | 95648-9436 |  | 2013-06-22 | 2013-06-22 12:21 | 2013-06-22 12:21 | CARRIER - 38CKC048360 | 98 | 0 | Yes | Yes | 19.1 | 18.9 | 0.2 | 4BEC32BDF6B548779565E0F6D5FBAEA7 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8330 |  | 2013-06-19 | 2013-06-19 11:34 | 2013-06-19 11:55 | BRYANT - 561CJ060-A | 135 | 4.9 | Yes | Yes | 17 | 19.9 | -2.9 | 05E955FD235D4260837978E179F6A0D0 |  | R22 | Non-TXV |  | 3.63% | 0.9637 | 6.975% | [5 empty] | Non-TXV | 3.63%
Lincoln | CA | 95648-1687 |  | 2013-06-18 | 2013-06-18 11:42 | 2013-06-18 11:42 | RUUD - 14AJM48A01 | 215 | 0 | Yes | Yes | 23.9 | 21 | 2.9 | 55D9BD880D49441098C6CD1C8589C8C4 |  | R22 | TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-4607 |  | 2013-06-04 | 2013-06-04 13:09 | 2013-06-04 13:40 | BRYANT - 583ANW036060AAAF | 85 | 2.5 | Yes | Yes | 18 | 19.1 | -1.1 | 1FE12D69BD2045FDAE50E56CBA88246C |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95206-6137 |  | 2013-07-02 | 2013-07-02 09:26 | 2013-07-02 09:56 | GOODMAN - CKJ36-1AB | 85 | 10.7 | Yes | Yes | 20.4 | 20.1 | 0.3 | DAD414ABF6A9492F9B44C72F9399C8E5 |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Dinuba | CA | 93618-3717 |  | 2013-07-30 | 2013-07-30 15:38 | 2013-07-30 15:56 | CARRIER - 48XP-060115311 | 210 | 7.7 | Yes | Yes | 23 | 18.7 | 4.3 | 20C875C85DAA47058D3157356F6F342C |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Paradise | CA | 95969-3407 |  | 2013-06-12 | 2013-06-12 19:55 | 2013-06-12 20:13 | CARRIER - NA | 53 | -5 | Yes | Yes | 25.6 | 21.9 | 3.7 | A7FC57FF0AC645E69A6B5108E3CF3A58 |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Chico | CA | 95973-1145 |  | 2013-08-07 | 2013-08-07 09:19 | 2013-08-07 10:00 | PAYNE - PY1PNB036090AAAA | 56 | 7.6 | Yes | Yes | 24.3 | 20.5 | 3.8 | 575C995137C040EA9E4ECD4561A0707C |  | R22 | Non-TXV |  | 13.57% | 0.86429 | 26.08% | [5 empty] | Non-TXV | 13.57%
Stockton | CA | 95204-2424 |  | 2013-05-31 | 2013-05-31 13:24 | 2013-05-31 13:24 | DAY & NIGHT - PGF336080K01A1 | 176 | 0 | Yes | Yes | 21.4 | 19.9 | 1.5 | 96D62E3685844D1B939067AAB3338C08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Granite Bay | CA | 95746-9331 |  | 2013-06-21 | 2013-06-21 14:48 | 2013-06-21 14:48 | PAYNE - PA12NA036-A | 100 | 0 | Yes | Yes | 23.1 | 21 | 2.1 | D9A1C66D9F3044519F83B1F53F461242 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-9597 |  | 2013-06-07 | 2013-06-07 10:38 | 2013-06-07 10:38 | PAYNE - 584AN042060 | 102 | 0 | Yes | Yes | 21.9 | 19.3 | 2.6 | 34E6315022A042E4BAF3B3F81122D1A4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Mariposa | CA | 95338-0000 |  | 2013-09-11 | 2013-09-11 15:45 | 2013-09-11 15:46 | DUCANE - AC10B36 | 96 | 9.3 | Yes | Yes | 29.1 | 24 | 5.1 | 985C97D18CF0488E90DCED726D8431CC |  | R22 | Non-TXV |  | 9.688% | 0.90312 | 18.62% | [5 empty] | Non-TXV | 9.688%
E Palo Alto | CA | 94303-2531 |  | 2013-11-20 | 2013-11-20 09:32 | 2013-11-20 09:32 | TRANE - 2TTB0048A1000AA | 109 | 0 | Yes | Yes | 23.6 | 19.3 | 4.3 | C4F8F3C0111E4F81B896FF6A756DCAD4 |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2403 |  | 2013-06-17 | 2013-06-17 15:36 | 2013-06-17 15:59 | BDP - 5858036075YACR | 60 | 2.8 | Yes | Yes | 28.3 | 22.6 | 5.7 | 308CB01485D047E6A3C9FD0392D4FD19 |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Stockton | CA | 95219-3436 |  | 2013-06-20 | 2013-06-20 10:50 | 2013-06-20 11:11 | RHEEM - AT24BIS | 85 | -6 | Yes | Yes | 20.2 | 18.8 | 1.4 | EB357FD17FA64BA3AAB5E9425EFAF719 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93726-3504 |  | 2013-06-05 | 2013-06-05 21:08 | 2013-06-05 21:08 | ICP - PGF036K080D | 71 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 75E9BBC0021049D9B417B3009F511824 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9255 |  | 2013-06-14 | 2013-06-14 12:42 | 2013-06-14 12:44 | GOODMAN - PGB0240501 | 54 | 6.8 | Yes | Yes | 16.7 | 17.7 | -1 | F3E9590D19CE46979CAC937ADA418729 |  | R22 | Non-TXV |  | 12.59% | 0.87407 | 24.2% | [5 empty] | Non-TXV | 12.59%
Stockton | CA | 95209-3732 |  | 2013-06-10 | 2013-06-10 13:37 | 2013-06-10 13:54 | GOODMAN - CKJ48-1B | 110 | -10.4 | Yes | Yes | 21.5 | 18.6 | 2.9 | 839B6EE280A448A9BC17A93313E9F3D7 |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Chico | CA | 95926-6512 |  | 2013-06-05 | 2013-06-05 10:25 | 2013-06-05 10:45 | OTHER - JS3BA-024KA | 64 | 7.9 | Yes | Yes | 15 | 17.6 | -2.6 | 3812CF8CB552436189F48B86D55EF29F |  | R22 | Non-TXV |  | 12.34% | 0.87656 | 23.72% | [5 empty] | Non-TXV | 12.34%
Clovis | CA | 93611-5378 |  | 2013-06-14 | 2013-06-14 13:57 | 2013-06-14 14:14 | OTHER - TZAA-342-2A757 | 105 | 3.5 | Yes | Yes | 19.2 | 21.6 | -2.4 | 85C3D640071C47A3A21C9BD752A1D05B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Chico | CA | 95973-0227 |  | 2013-07-16 | 2013-07-16 21:33 | 2013-07-16 19:52 | YORK - H2RA036506A | 63 | 0 | Yes | Yes | 17.5 | 19 | -1.5 | F196AD673A8C4F26A225409E4CCD9DC7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2640 |  | 2013-06-01 | 2013-06-01 08:24 | 2013-06-01 08:48 | OTHER - PGHA042G075AIN | 93 | 4.7 | Yes | Yes | 19.5 | 21.5 | -2 | 9CF4F169D77D46609A9C74A9A81203E3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.054% | 0.94946 | 9.712% | [5 empty] | Non-TXV | 5.054%
Manteca | CA | 95337-6529 |  | 2013-05-29 | 2013-05-29 15:34 | 2013-05-29 16:04 | OTHER - TZAA-330-2A | 98 | 3.2 | Yes | Yes | 22.5 | 20.4 | 2.1 | 9C4067C24F94443B8338FFBB1FF0311E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.265% | 0.96735 | 6.275% | [5 empty] | Non-TXV | 3.265%
Fresno | CA | 93726-3416 |  | 2013-06-01 | 2013-06-01 11:56 | 2013-06-01 12:32 | BRYANT - 583ANW042090NBAF | 102 | 3.1 | Yes | Yes | 18.2 | 20.4 | -2.2 | 38A6E209B82E4CDE95A58F54B5A17D62 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Stockton | CA | 95204-2943 |  | 2013-06-01 | 2013-06-01 13:53 | 2013-06-01 14:20 | CARRIER - 48DL003 | 49 | 5.3 | Yes | Yes | 21 | 20.1 | 0.9 | 897C28F096444886ACBB2BDA832984F8 |  | R22 | Non-TXV |  | 10.82% | 0.89184 | 20.79% | [5 empty] | Non-TXV | 10.82%
Hamilton City | CA | 95951-0000 |  | 2013-09-23 | 2013-09-23 09:53 | 2013-09-23 10:31 | YORK - H2RD0360S06B | 96 | 2.9 | Yes | Yes | 22 | 20.2 | 1.9 | 4B92BD60CC184214B7A50C19AE838CDF |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Stockton | CA | 95210-1885 |  | 2013-07-11 | 2013-07-11 09:17 | 2013-07-11 09:37 | GOODMAN - CM30-1EB | 67 | -3.9 | Yes | Yes | 15.9 | 18 | -2.1 | 238075D417FA49E5BB015D19DCA001E1 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Fresno | CA | 93726-2546 |  | 2013-07-29 | 2013-07-29 10:52 | 2013-07-29 10:54 | OTHER - UNK | 85 | 10.6 | Yes | Yes | 23.4 | 22.3 | 1.1 | 705A8B4A0CE34284BCD321CE9E50AC8A |  | R22 | Non-TXV |  | 12.47% | 0.87529 | 23.97% | [5 empty] | Non-TXV | 12.47%
Chico | CA | 95928-7637 |  | 2013-06-05 | 2013-06-05 13:33 | 2013-06-05 13:33 | LENNOX - HS25-411-1P | 129 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 472309198F354DA5BD5127CD6994CA6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-2219 |  | 2013-05-30 | 2013-05-30 13:12 | 2013-05-30 13:12 | BDP - 561AJ024-E | 54 | 0 | Yes | Yes | 25.7 | 21.5 | 4.2 | C8E525BDC9D346289F3611ED457C647B |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-7169 |  | 2013-06-19 | 2013-06-19 12:28 | 2013-06-19 12:56 | OTHER - CA9036VKD3 | 124 | -8.2 | Yes | Yes | 22 | 19.9 | 2.1 | C75AEDE549E74FE5B73471E8EEFEC8E2 |  | R22 | Non-TXV |  | -6.613% | 1.0661 | 1.852% |  |  |  |  | Non-TXV |  |  | -6.613%
Rocklin | CA | 95765-0000 |  | 2013-09-26 | 2013-09-26 18:05 | 2013-09-26 18:35 | NORDYNE - JS5BD-030KA | 99 | -19.5 | Yes | Yes | 24 | 20.7 | 3.3 | 700B0734F806426DA143ABBAFDEB619C |  | R22 | TXV |  | -19.7% | 1.197 | 5.516% |  |  |  |  | TXV |  |  | -19.7%
Riverbank | CA | 95367-3051 |  | 2013-07-11 | 2013-07-11 12:36 | 2013-07-11 12:57 | BRYANT - 561CJ036-E | 70 | 2.5 | Yes | Yes | 22.1 | 20.1 | 2 | 7A275B8297964E088FD553E471BECA56 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Ione | CA | 95640-5217 |  | 2013-06-26 | 2013-06-26 16:03 | 2013-06-26 16:03 | CARRIER - 38BRC036330 | 104 | 0 | Yes | Yes | 17.6 | 18.5 | -0.9 | 87ED699E95694BA0AA1B2A22D0B9E2FD |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1353 |  | 2013-06-28 | 2013-06-28 09:27 | 2013-06-28 09:27 | YORK - D3NZ036N05606NXA | 64 | 0 | Yes | Yes | 22.1 | 16.4 | 5.7 | D6C460AF70384A04A1111A4C5579FC6B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-5616 |  | 2013-07-16 | 2013-07-16 15:42 | 2013-07-16 16:04 | AMANA - RCB42A2B | 96 | 15.4 | Yes | Yes | 21.7 | 20.1 | 1.7 | A550DB8EF279409DB8CA94AC9314A527 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.04% | 0.83958 | 30.83% | [5 empty] | Non-TXV | 16.04%
Lincoln | CA | 95648-8240 |  | 2013-05-31 | 2013-05-31 10:25 | 2013-05-31 10:47 | CARRIER - 38CKC036350 | 73 | 2.1 | Yes | Yes | 18 | 20.4 | -2.4 | 3D6C8B50D4D149B98FE5D3865F6B634E |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Lincoln | CA | 95648-8212 |  | 2013-06-03 | 2013-06-03 10:33 | 2013-06-03 10:53 | YORK - H1RA042S06D | 84 | -7.9 | Yes | Yes | 17.1 | 19.9 | -2.8 | 83E62A7FD7AB459EA5B6B13D410706E6 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Stockton | CA | 95210-3719 |  | 2013-06-13 | 2013-06-13 13:19 | 2013-06-13 13:39 | RHEEM - RAKB-036JAZ | 79 | -4.6 | Yes | Yes | 18.2 | 19.7 | -1.5 | 7A1B0D7D09B94472B4E89C63722EB4E8 |  | R22 | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Clovis | CA | 93612-1239 |  | 2013-06-17 | 2013-06-17 12:48 | 2013-06-17 18:28 | ICP - PGF042KD080 | 87 | 10.8 | Yes | Yes | 0.4 | 20.4 | -20 | A8733F00AAD94327AAC7619884D8BF12 |  | R22 | Non-TXV |  | 12.41% | 0.87586 | 23.86% | [5 empty] | Non-TXV | 12.41%
Stockton | CA | 95207-3446 |  | 2013-06-13 | 2013-06-13 09:42 | 2013-06-13 09:42 | OTHER - NAC036AKA5 | 87 | 0 | Yes | Yes | 24.9 | 20.2 | 4.8 | B0A9EAABDF574B16A1F36BD96594FD34 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-3751 |  | 2013-06-25 | 2013-06-25 12:40 | 2013-06-25 12:57 | BRYANT - 561CJ030-E | 66 | 2.2 | Yes | Yes | 20.5 | 19.3 | 1.2 | BF7F49A8327E429CB78F115C4311A4FA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Paso Robles | CA | 93446-1274 |  | 2013-08-14 | 2013-08-14 16:06 | 2013-08-14 16:37 | PAYNE - UNK | 77 | 3.1 | Yes | Yes | 21.5 | 21.1 | 0.4 | 40D16C283B904ED286443D3484DF4FF6 |  | R22 | Non-TXV |  | 4.026% | 0.95974 | 7.737% | [5 empty] | Non-TXV | 4.026%
Stockton | CA | 95204-2807 |  | 2013-07-02 | 2013-07-02 09:51 | 2013-07-02 10:12 | OTHER - YCG030 | 64 | 15.9 | Yes | Yes | 20.2 | 19 | 1.2 | B40CEB291B05444CACB1DA3823152A6A |  | R22 | Non-TXV |  | 24.84% | 0.75156 | 47.74% | [5 empty] | Non-TXV | 24.84%
Tracy | CA | 95376-0753 |  | 2013-07-23 | 2013-07-23 12:10 | 2013-07-23 12:29 | GOODMAN - SSX140361BA | 98 | 4.4 | Yes | Yes | 23.6 | 19.3 | 4.3 | AC794F8D9BE94034B78BD1D73A1DAB12 |  | R410A | TXV |  | 4.49% | 0.9551 | 8.628% | [5 empty] | TXV | 4.49%
Tracy | CA | 95376-0753 |  | 2013-07-23 | 2013-07-23 12:28 | 2013-07-23 12:50 | YORK - H1CB024A06B | 60 | 1.8 | Yes | Yes | 21.3 | 19.2 | 2.1 | 7C104870922A4753B081200B3EDFEFEA |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-1914 |  | 2013-06-25 | 2013-06-25 10:13 | 2013-06-25 10:33 | GOODMAN - CKL36-1H | 71 | 7.6 | Yes | Yes | 18.6 | 18.5 | 0.1 | 13B881DB5DFD48BD90FF56F3CCB861DC |  | R22 | Non-TXV |  | 10.7% | 0.89296 | 20.57% | [5 empty] | Non-TXV | 10.7%
Stockton | CA | 95210-3737 |  | 2013-06-19 | 2013-06-19 12:53 | 2013-06-19 13:13 | YORK - H2RA036S06G | 63 | 4 | Yes | Yes | 18.2 | 19.3 | -1.1 | 5C74384E14E546ADBAC9B3E395665344 |  | R22 | Non-TXV |  | 6.349% | 0.93651 | 12.2% | [5 empty] | Non-TXV | 6.349%
Fresno | CA | 93726-0959 |  | 2013-05-29 | 2013-05-29 15:09 | 2013-05-29 15:45 | AMERICAN STANDARD - YCC024F1L0BG | 96 | 4.3 | Yes | Yes | 17.7 | 20.7 | -3 | DBCFE1F65A9F4EE48B2DFCF4803AF627 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.479% | 0.95521 | 8.608% | [5 empty] | Non-TXV | 4.479%
Dinuba | CA | 93618-3010 |  | 2013-08-10 | 2013-08-10 14:08 | 2013-08-10 14:08 | ICP - PGD330060K001C1 | 98 | 0 | Yes | Yes | 19 | 20.7 | -1.7 | 24AD346714E74BEBB5CC7E150AFDFAA0 |  | R410A | TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1623 |  | 2013-06-04 | 2013-06-04 10:46 | 2013-06-04 11:10 | RHEEM - 13AJN24A01 | 68 | 11.2 | Yes | Yes | 19.9 | 20.4 | -0.5 | FC1EBD76299F4F8489D2EB65C9EC0C38 |  | R410A | Non-TXV |  | 16.47% | 0.83529 | 31.65% | [5 empty] | Non-TXV | 16.47%
Stockton | CA | 95206-6401 |  | 2013-06-19 | 2013-06-19 08:53 | 2013-06-19 09:13 | GOODMAN - CJL48=1A | 130 | 7.6 | Yes | Yes | 20.1 | 18.3 | 1.8 | 744FEBA77A2F44F79A767A2A56B15232 |  | R22 | Non-TXV |  | 5.846% | 0.94154 | 11.24% | [5 empty] | Non-TXV | 5.846%
Marysville | CA | 95901-4630 |  | 2013-06-26 | 2013-06-26 09:05 | 2013-06-26 09:28 | LENNOX - 13GCSXA-42-2301A | 181 | 5.4 | Yes | Yes | 19 | 18.1 | 0.9 | 784363034D3B4DE1B7A10156A3094C13 |  | R22 | Non-TXV |  | 2.983% | 0.97017 | 5.733% | [5 empty] | Non-TXV | 2.983%
Williams | CA | 95987-0000 |  | 2013-08-03 | 2013-08-03 08:50 | 2013-08-03 09:09 | RHEEM - RRNL-B024JK06X | 77 | 2.8 | Yes | Yes | 18 | 18.2 | -0.2 | 0ED3E6C081764AB49891761A82C14305 |  | R410A | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Los Banos | CA | 93635-3810 |  | 2013-05-31 | 2013-05-31 14:55 | 2013-05-31 14:57 | OTHER - UNK | 87 | 8.9 | Yes | Yes | 30 | 24.2 | 5.8 | 9B78B787F935460F90F97734EFCA1560 |  | R22 | Non-TXV |  | 10.23% | 0.8977 | 19.66% | [5 empty] | Non-TXV | 10.23%
Clovis | CA | 93612-3402 |  | 2013-06-18 | 2013-06-18 11:26 | 2013-06-18 11:46 | ICP - PGC030K060D | 52 | 5.7 | Yes | Yes | 18.2 | 20.1 | -1.9 | 95E66450E85947888574582C96BFAB42 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.96% | 0.89038 | 21.07% | [5 empty] | Non-TXV | 10.96%
Fresno | CA | 93726-2039 |  | 2013-05-31 | 2013-05-31 18:51 | 2013-05-31 19:49 | ICP - PGF342080K01 | 184 | 5.5 | Yes | Yes | 20.5 | 15.9 | 4.6 | CABC5BB109314F9DACC9C7CEFA4FF4F4 |  | R22 | Non-TXV |  | 2.989% | 0.97011 | 5.744% | [5 empty] | Non-TXV | 2.989%
Auburn | CA | 95602-8104 |  | 2013-06-12 | 2013-06-12 08:52 | 2013-06-12 08:52 | LENNOX - 10ACC-048-230-02 | 99 | 0 | Yes | Yes | 23 | 18.7 | 4.3 | 6BF672C76F0F4DABB7A46A7F12DDB3A6 |  | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6529 |  | 2013-06-11 | 2013-06-11 16:00 | 2013-06-11 16:27 | DAY & NIGHT - 565BJ018 | 52 | 4.1 | Yes | Yes | 21.7 | 18.9 | 2.8 | C95F004D7888407DB1D080EB0E81A832 |  | R22 | Non-TXV |  | 7.885% | 0.92115 | 15.15% | [5 empty] | Non-TXV | 7.885%
Stockton | CA | 95205-7779 |  | 2013-06-06 | 2013-06-06 12:31 | 2013-06-06 12:48 | RUUD - UAKA-024JAZ | 50 | 4.5 | Yes | Yes | 21.9 | 18.6 | 3.3 | CA22F36CDBEE44F3BF016BF3D28AF83E |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Stockton | CA | 95204-1231 |  | 2013-06-06 | 2013-06-06 14:37 | 2013-06-06 14:57 | BRYANT - 588ANW030060ADAD | 53 | 4 | Yes | Yes | 24.1 | 19.3 | 4.8 | 1A8B8DF1A3A848D8B4F6CEC88A9A69E4 |  | R22 | Non-TXV |  | 7.547% | 0.92453 | 14.5% | [5 empty] | Non-TXV | 7.547%
Stockton | CA | 95203-2024 |  | 2013-07-15 | 2013-07-15 09:59 | 2013-07-15 10:22 | RHEEM - RRMA-A030JK08X | 80 | 2.8 | Yes | Yes | 21.5 | 19.1 | 2.4 | 6B1C77360C29473C93E6E6901AAEDA61 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Lincoln | CA | 95648-2078 |  | 2013-06-18 | 2013-06-18 17:01 | 2013-06-18 17:01 | PAYNE - UNK | 95 | 11.7 | Yes | Yes | 0 | 20.2 | -20.2 | BD1BFF62F34840BEA8BB6D6B3D8A8161 | Add refrigerant: 11.7 oz Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.32% | 0.87684 | 23.67% | [5 empty] | Non-TXV | 12.32%
Stockton | CA | 95206-6292 |  | 2013-06-26 | 2013-06-26 10:59 | 2013-06-26 11:26 | CARRIER - 38CKC060370 | 159 | 5.5 | Yes | Yes | 22.3 | 20.9 | 1.4 | 7DE11E2C717444CD8DE60EDF9467C4BB |  | R22 | Non-TXV |  | 3.459% | 0.96541 | 6.648% | [5 empty] | Non-TXV | 3.459%
Lincoln | CA | 95648-8274 |  | 2013-06-18 | 2013-06-18 15:07 | 2013-06-18 15:30 | CARRIER - 38CK036350 | 75 | -4.4 | Yes | Yes | 18 | 20.9 | -2.9 | 0CD2F607AAED4F89BA05FD992E183F52 |  |  |  |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | 0 |  |  | -5.867%
Stockton | CA | 95210-3714 |  | 2013-06-19 | 2013-06-19 14:50 | 2013-06-19 15:11 | LENNOX - HS260422P | 107 | 3.5 | Yes | Yes | 25.4 | 19.9 | 5.5 | FE4C8025263942B19F717630E1868377 |  | R22 | Non-TXV |  | 3.271% | 0.96729 | 6.286% | [5 empty] | Non-TXV | 3.271%
Clovis | CA | 93612-0261 |  | 2013-08-06 | 2013-08-06 15:06 | 2013-08-06 15:10 | CARRIER - 48NLT030300 | 85 | 13.2 | Yes | Yes | 23.4 | 22 | 1.4 | 13A92B2DE4504A618E5599C1B07E7A29 |  | R22 | Non-TXV |  | 15.53% | 0.84471 | 29.84% | [5 empty] | Non-TXV | 15.53%
Chowchilla | CA | 93610-8463 |  | 2013-09-09 | 2013-09-09 15:01 | 2013-09-09 15:04 | GOODMAN - CKL491A | 112 | 17.6 | Yes | Yes | 20.9 | 22.6 | -1.7 | F49DA491BCC3497DA9E508F23C19EE42 |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Stockton | CA | 95204-3507 |  | 2013-06-12 | 2013-06-12 13:11 | 2013-06-12 13:11 | PAYNE - 574DNWA30040NATP | 98 | 0 | Yes | Yes | 22.2 | 19.4 | 2.8 | 2A2988B0733D4E0287D1DA8DD34E4D03 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1439 |  | 2013-06-10 | 2013-06-10 17:53 | 2013-06-10 18:28 | LENNOX - 13ACD-042-230-01 | 111 | 13.2 | Yes | Yes | 18.8 | 12.8 | 6 | ED3D6FB74CB34F3B8F653B33737F46AF |  | R22 | Non-TXV |  | 11.89% | 0.88108 | 22.85% | [5 empty] | Non-TXV | 11.89%
Manteca | CA | 95336-8608 |  | 2013-06-06 | 2013-06-06 13:07 | 2013-06-06 13:28 | GOODMAN - GSC130361DF | 120 | 3.7 | Yes | Yes | 18.8 | 20.4 | -1.6 | 9785150E3AC04000BC4F652214A7E0B4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Stockton | CA | 95207-7721 |  | 2013-06-14 | 2013-06-14 12:50 | 2013-06-14 13:05 | HEIL - ACS024A2C1 | 62 | 5.5 | Yes | Yes | 19.2 | 19 | 0.2 | 0F360499FE0845869D52F7BC958CAE1F |  | R22 | Non-TXV |  | 8.871% | 0.91129 | 17.05% | [5 empty] | Non-TXV | 8.871%
Madera | CA | 93637-6708 |  | 2013-07-12 | 2013-07-12 10:11 | 2013-07-12 11:08 | YORK - H2RD060S06B | 162 | 5.3 | Yes | Yes | 17.2 | 19.8 | -2.6 | B5A0E767787A4326827BDA5534B0F818 |  | R22 | Non-TXV |  | 3.272% | 0.96728 | 6.287% | [5 empty] | Non-TXV | 3.272%
Yuba City | CA | 95993-8126 |  | 2013-09-09 | 2013-09-09 14:44 | 2013-09-09 15:02 | TRANE - 4TT0483D1000BA | 109 | 3.9 | Yes | Yes | 18.3 | 19.8 | -1.5 | E3139DEE783F426F98D10FEEB8ABC02F |  | R410A | Non-TXV |  | 3.578% | 0.96422 | 6.876% | [5 empty] | Non-TXV | 3.578%
Lincoln | CA | 95648-2491 |  | 2013-06-14 | 2013-06-14 11:27 | 2013-06-14 11:27 | YORK - H2RA036S06E | 63 | 0 | Yes | Yes | 23.3 | 21 | 2.3 | 63078741BC044749B2FE086CB2F4050B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-4478 |  | 2013-06-24 | 2013-06-24 15:27 | 2013-06-24 15:32 | LENNOX - 13ACC-042-230-01 | 126 | 3.9 | Yes | Yes | 18.1 | 18.8 | -0.7 | 398D132578A64545A50477F0CB91D004 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Grass Valley | CA | 95945-4532 |  | 2013-08-22 | 2013-08-22 15:55 | 2013-08-22 16:47 | CARRIER - 38BQ006310 | 50 | 6.6 | Yes | Yes | 25.1 | 19.7 | 5.4 | EBC7FDDD94EA4AEEA431474C439D1CCF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.2% | 0.868 | 25.37% | [5 empty] | Non-TXV | 13.2%
Fresno | CA | 93726-3735 |  | 2013-08-16 | 2013-08-16 08:17 | 2013-08-16 08:34 | DAY & NIGHT - UNK | 55 | 2.4 | Yes | Yes | 22.3 | 19 | 3.3 | 3ED2561D400F430795F5AB1165B4A5F5 |  | R22 | Non-TXV |  | 4.364% | 0.95636 | 8.386% | [5 empty] | Non-TXV | 4.364%
Stockton | CA | 95205-7872 |  | 2013-06-06 | 2013-06-06 12:49 | 2013-06-06 13:15 | HEIL - UNK | 54 | 2.8 | Yes | Yes | 18.8 | 18 | 0.8 | B7C554EF4BBF4DAEAEDEEEA930BC2007 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Los Banos | CA | 93635-5454 |  | 2013-06-04 | 2013-06-04 08:48 | 2013-06-04 08:54 | BRYANT - 561CJX048000AAA | 102 | 5.2 | Yes | Yes | 17.6 | 19.1 | -1.5 | 565A2C83FF7A425F8E6257632690EEA2 |  | R22 | TXV |  | 5.098% | 0.94902 | 9.797% | [5 empty] | TXV | 5.098%
Stockton | CA | 95207-5842 |  | 2013-06-07 | 2013-06-07 14:44 | 2013-06-07 14:44 | GE - BTN924A100A3 | 92 | 0 | Yes | Yes | 23.9 | 19.3 | 4.6 | 1ADCD9AFDCC04B6A85A14A0D2CDC39F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Diamond Springs | CA | 95619-9376 |  | 2013-07-05 | 2013-07-05 14:59 | 2013-07-05 14:59 | RHEEM - UNK | 95 | 0 | Yes | Yes | 14.5 | 17.4 | -2.9 | FF3B81EE6A7845B4A9A14EB3633BC735 |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3047 |  | 2013-05-29 | 2013-05-29 09:04 | 2013-05-29 09:16 | AMANA - ARCF36U01D | 112 | 5.2 | Yes | Yes | 18.8 | 12.8 | 6 | 55B0B86F0C3E480D8CB8E1F722B2C7D0 |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Mariposa | CA | 95338-9660 |  | 2013-08-02 | 2013-08-02 10:19 | 2013-08-02 10:21 | BRYANT - 583ANW030060NADD | 68 | 2.7 | Yes | Yes | 26.5 | 20.7 | 5.8 | 52C698F8711749EA845B0FD6F2A6123A |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Stockton | CA | 95219-3135 |  | 2013-06-21 | 2013-06-21 11:01 | 2013-06-21 11:23 | RHEEM - HC-80-24-21C | 49 | -3.5 | Yes | Yes | 21.3 | 18.8 | 2.5 | 10063F312D8A4E228DDD795B7AE37F6A |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Yuba City | CA | 95993-8132 |  | 2013-06-20 | 2013-06-20 09:10 | 2013-06-20 09:34 | GOODMAN - CM30-1EB | 67 | -6.3 | Yes | Yes | 19 | 20.1 | -1.1 | B0F6EE571B184155A0C3096B5467159C |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Stockton | CA | 95206-4680 |  | 2013-06-18 | 2013-06-18 10:26 | 2013-06-18 10:52 | BRYANT - 563CN042-A | 166 | 5.8 | Yes | Yes | 23.5 | 21.3 | 2.2 | E276D4A0992F425F8B426AAC1A1F5E41 |  | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
Los Banos | CA | 93635-5471 |  | 2013-08-15 | 2013-08-15 11:05 | 2013-08-15 11:07 | YORK - H2RA030SO6D | 62 | 7.3 | Yes | Yes | 17.8 | 16.6 | 1.2 | C3764DFF167F4489B941C0C6FBF73E62 |  | R22 | Non-TXV |  | 11.77% | 0.88226 | 22.63% | [5 empty] | Non-TXV | 11.77%
Los Banos | CA | 93635-5471 |  | 2013-08-15 | 2013-08-15 11:25 | 2013-08-15 11:27 | YORK - H2RA030SO6D | 62 | 7.7 | Yes | Yes | 17 | 17.1 | -0.1 | E6D17054AF17480ABE69FEA07D444735 |  | R22 | Non-TXV |  | 12.42% | 0.87581 | 23.87% | [5 empty] | Non-TXV | 12.42%
Chico | CA | 95926-3825 |  | 2013-08-23 | 2013-08-23 13:27 | 2013-08-23 18:44 | DAY & NIGHT - PGD324060K001C1 | 65 | 2.1 | Yes | Yes | 22.4 | 20.6 | 1.8 | CF93A88D1D18427E974138B34E597896 |  | R410A | Non-TXV |  | 3.231% | 0.96769 | 6.209% | [5 empty] | Non-TXV | 3.231%
Madera | CA | 93638-2135 |  | 2013-06-13 | 2013-06-13 11:32 | 2013-06-16 02:03 | CARRIER - 48MT030-301BE | 91 | -8.6 | Yes | Yes | 17.4 | 20.1 | -2.7 | BD2D4A7DC1ED41BE88365668B87EAF7B |  | R22 | Non-TXV |  | -9.451% | 1.0945 | 2.647% |  |  |  |  | Non-TXV |  |  | -9.451%
Oroville | CA | 95966-3960 |  | 2013-06-20 | 2013-06-20 19:57 | 2013-06-20 20:13 | PAYNE - PH10JAO48-E | 121 | 4.8 | Yes | Yes | 20.8 | 20.1 | 0.7 | CAE4DFA4E2344EFC92793EA2AB1D3766 |  | R22 | Non-TXV |  | 3.967% | 0.96033 | 7.624% | [5 empty] | Non-TXV | 3.967%
Fresno | CA | 93710-5618 |  | 2013-06-04 | 2013-06-04 10:12 | 2013-06-04 10:32 | PAYNE - UNK | 96 | -5.6 | Yes | Yes | 22.9 | 20.1 | 2.9 | F22D99A4D0154847A88F06DEC4E6FBEE |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Los Banos | CA | 93635-8810 |  | 2013-06-13 | 2013-06-13 10:50 | 2013-06-13 11:09 | BRYANT - 113RNA060 | 170 | 12.2 | Yes | Yes | 26.3 | 21.9 | 4.4 | 033C7C154EED40C8AF5951066E06CB90 |  | R22 | TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | TXV | 7.176%
Atwater | CA | 95301-3521 |  | 2013-06-14 | 2013-06-14 10:59 | 2013-06-14 11:04 | YORK - H30H042S06A | 140 | 10.6 | Yes | Yes | 22.3 | 17.7 | 4.6 | 00A6FDE8F8944EF8A4A37E5CD01E4ECE |  | R22 | Non-TXV |  | 7.571% | 0.92429 | 14.55% | [5 empty] | Non-TXV | 7.571%
Fresno | CA | 93726-2807 |  | 2013-06-03 | 2013-06-03 16:08 | 2013-06-03 16:30 | BRYANT - 563CNX0600000AGAA | 120 | 4.1 | Yes | Yes | 18.3 | 20.6 | -2.3 | F20D3E0CB8564299888B19ED8233CA65 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.417% | 0.96583 | 6.566% | [5 empty] | Non-TXV | 3.417%
Stockton | CA | 95210-1519 |  | 2013-06-17 | 2013-06-17 10:47 | 2013-06-17 11:05 | AMANA - PGD30C0702G | 74 | -4.4 | Yes | Yes | 21.1 | 19.9 | 1.2 | 02D1DA78CF2A4475AEAF876AF37E5614 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Valley Springs | CA | 95252-9131 |  | 2013-09-12 | 2013-09-12 15:01 | 2013-09-12 22:35 | BRYANT - 561CJ036-E | 76 | 3.8 | Yes | Yes | 21.5 | 19.8 | 1.7 | 4CB0F5DF65484688BB5CCB3768A577B8 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Lathrop | CA | 95330-9757 |  | 2013-06-07 | 2013-06-07 09:15 | 2013-06-07 09:50 | LUXAIRE - TCGD048S21S1HA | 75 | 2.7 | Yes | Yes | 18.4 | 18.7 | -0.3 | 9CD26D6C2297427B93296318EBA41A35 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Valley Springs | CA | 95252-9280 |  | 2013-08-14 | 2013-08-14 15:15 | 2013-08-14 15:34 | BRYANT - 582AJW048115AAAG | 81 | 6 | Yes | Yes | 22.2 | 19.6 | 2.6 | 5368FF51DAEF4FE58C21D39816FEF22A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
Willows | CA | 95988-2056 |  | 2013-06-26 | 2013-06-26 18:52 | 2013-06-26 19:10 | GOODMAN - CK30-1A | 76 | 2.3 | Yes | Yes | 21.4 | 20.1 | 1.4 | D7F0546FE70548D08BCD3AD10A1962CB |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Rocklin | CA | 95677-2024 |  | 2013-06-11 | 2013-06-11 11:37 | 2013-06-11 11:58 | TRANE - YCC036F1M0BF | 83 | 2.7 | Yes | Yes | 19 | 19.3 | -0.3 | 01E44DA64AF14DBF8612CEEC3DB69B95 |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Stockton | CA | 95202-1544 |  | 2013-07-09 | 2013-07-09 13:58 | 2013-07-09 13:58 | PAYNE - PA13NR036-D | 114 | 0 | Yes | Yes | 18.5 | 18.9 | -0.4 | BF41456B75544E0ABF9949F4002DCCED |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4039 |  | 2013-05-31 | 2013-05-31 13:07 | 2013-05-31 13:09 | BRYANT - 589ANW048080ADAG | 87 | 7.7 | Yes | Yes | 19.7 | 21 | -1.3 | EB5AD699EA564DAEA06D67B5A3CA0162 |  | R22 | Non-TXV |  | 8.851% | 0.91149 | 17.01% | [5 empty] | Non-TXV | 8.851%
Tracy | CA | 95377-9172 |  | 2013-06-06 | 2013-06-06 10:27 | 2013-06-06 10:49 | TRANE - UNK | 85 | 14.6 | Yes | Yes | 17 | 18.2 | -1.2 | 37569C5E2563458DBF6F7DD6FD79A9CE |  | R22 | Non-TXV |  | 17.18% | 0.82824 | 33.01% | [5 empty] | Non-TXV | 17.18%
Atwater | CA | 95301-0000 |  | 2013-06-05 | 2013-06-05 14:36 | 2013-06-05 14:36 | BDP - 60RCU108C | 134 | 0 | Yes | Yes | 21.6 | 21.6 | 0 | D8D82BE2D3B44A6EB01F0A3DBE8A74AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-4516 |  | 2013-06-06 | 2013-06-06 10:20 | 2013-06-06 10:42 | RUUD - AUND-042JAZ | 136 | 4.8 | Yes | Yes | 20.1 | 18.2 | 1.9 | EC1242777DE445B78B922FFBE831929C |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Orland | CA | 95963-2130 |  | 2013-09-05 | 2013-09-05 15:28 | 2013-09-05 15:45 | TEMPSTAR - FBA030GC1 | 71 | 3.8 | Yes | Yes | 18.5 | 19.2 | -0.7 | 4562A0A251FC4DB493E141D66D26E9B5 |  | R22 | Non-TXV |  | 5.352% | 0.94648 | 10.29% | [5 empty] | Non-TXV | 5.352%
Lincoln | CA | 95648-2357 |  | 2013-06-18 | 2013-06-18 12:41 | 2013-06-18 12:58 | CARRIER - 38ETG036 | 133 | -4.9 | Yes | Yes | 22 | 23.6 | -1.6 | 37834E0D3874455CBBC70FD591EC9AFA |  | R410A | TXV |  | -3.684% | 1.0368 | 1.032% |  |  |  |  | TXV |  |  | -3.684%
Yuba City | CA | 95993-7611 |  | 2013-08-07 | 2013-08-07 09:48 | 2013-08-07 10:09 | DAY & NIGHT - N2A324AKC200 | 55 | 2.2 | Yes | Yes | 18 | 18.8 | -0.8 | 745A06D64ACA4D8A90ADD356093DF3B5 |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Tracy | CA | 95376-2739 |  | 2013-06-06 | 2013-06-06 13:17 | 2013-06-06 13:36 | CARRIER - 49NXM048--301BE | 151 | 12.3 | Yes | Yes | 21.6 | 18.5 | 3.1 | FDF80B411EBC4CD8B6765F1379B287C7 |  | R22 | Non-TXV |  | 8.146% | 0.91854 | 15.65% | [5 empty] | Non-TXV | 8.146%
Stockton | CA | 95210-5616 |  | 2013-06-14 | 2013-06-14 13:09 | 2013-06-14 13:09 | PAYNE - 593ANX042000AAAA | 164 | 0 | Yes | Yes | 28.5 | 22.6 | 5.9 | E75F3ACDD28B4AF6946B48BE81E56E23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-5616 |  | 2013-06-14 | 2013-06-14 13:19 | 2013-06-14 13:19 | PAYNE - 591ANX024000AAAA | 53 | 0 | Yes | Yes | 23.7 | 22.5 | 1.2 | 4B853AF5D926467ABD7EB90E6A7BA446 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3536 |  | 2013-06-11 | 2013-06-11 15:28 | 2013-06-11 15:52 | UNITARY PRODUCTS GROUP - DAYQ-F042N080A | 72 | 2.8 | Yes | Yes | 18.3 | 19.5 | -1.2 | 62769C8278C74EB2BA0870A8C610DBF7 |  | R410A | TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | TXV | 3.889%
Stockton | CA | 95212-3412 |  | 2013-06-21 | 2013-06-21 12:33 | 2013-06-21 12:58 | YORK - H2RC048S06A | 120 | 3.6 | Yes | Yes | 22.5 | 20.4 | 2.1 | 6CDD202759AC4CC4A051CCE1AE4D27AB |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93726-1511 |  | 2013-05-31 | 2013-05-31 12:47 | 2013-05-31 13:07 | GE - 21TA036H1D | 101 | 3.6 | Yes | Yes | 19.1 | 18.1 | 1 | FF402EE1FC9745EDB3D464EF03EE9B08 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.564% | 0.96436 | 6.85% | [5 empty] | Non-TXV | 3.564%
Marysville | CA | 95901-3324 |  | 2013-06-27 | 2013-06-27 10:12 | 2013-06-27 10:34 | RHEEM - RAC-030ABQ | 35 | 23.6 | Yes | Yes | 15 | 17.4 | -2.4 | A5F37D460EDE46AAB1CF97A2AAF94A12 |  | R22 | Non-TXV |  | 67.43% | 0.32571 | 129.6% | [5 empty] | Non-TXV | 67.43%
Riverbank | CA | 95367-2649 |  | 2013-07-11 | 2013-07-11 16:48 | 2013-07-11 17:22 | HEIL - CA5056VKB1 | 86 | 2.9 | Yes | Yes | 24.5 | 21.5 | 3 | 5D3105EB0B1A4148A05B8FB124C4F576 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.372% | 0.96628 | 6.48% | [5 empty] | Non-TXV | 3.372%
Los Banos | CA | 93635-2626 |  | 2013-07-02 | 2013-07-02 10:05 | 2013-07-02 10:14 | GOODMAN - CK361B | 76 | 5.8 | Yes | Yes | 27.4 | 22.4 | 5 | FA4F7230237B44D79A1260BA1343E58A |  | R22 | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
Chico | CA | 95928-7654 |  | 2013-06-07 | 2013-06-07 10:45 | 2013-06-07 11:23 | PAYNE - 3396E20354 | 102 | 6.4 | Yes | Yes | 20.8 | 20.4 | 0.4 | D4691E76FC4F448D9164C01F0F7A97BA |  | R22 | Non-TXV |  | 6.275% | 0.93725 | 12.06% | [5 empty] | Non-TXV | 6.275%
Applegate | CA | 95703-0000 |  | 2013-08-19 | 2013-08-19 12:21 | 2013-08-19 12:21 | NORDYNE - S5BD-030KA | 99 | 0 | Yes | Yes | 25.2 | 22.1 | 3.1 | F4A74849D98146209D7E9400735C3674 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1451 |  | 2013-06-08 | 2013-06-08 12:29 | 2013-06-08 12:37 | LENNOX - 13ACD-036-230-03 | 111 | 3.5 | Yes | Yes | 22.2 | 18.8 | 3.4 | 0CDFCDAD76844531A246FA84A6367671 |  | R22 | Non-TXV |  | 3.153% | 0.96847 | 6.06% | [5 empty] | Non-TXV | 3.153%
Stockton | CA | 95205-4640 |  | 2013-06-06 | 2013-06-06 09:35 | 2013-06-06 09:53 | RUUD - URKA-A030JK06E | 54 | 2.1 | Yes | Yes | 18.8 | 18.7 | 0.1 | 3BFF0F88FF6B45AD8EB5C15BFC48389F |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Willows | CA | 95988-3337 |  | 2013-08-14 | 2013-08-14 12:53 | 2013-08-14 13:44 | BRYANT - 552ANO42-E | 83 | 3.5 | Yes | Yes | 15.2 | 18 | -2.8 | DD9F3B969F9C46D686E9CBE2A4543BBB |  | R410A | TXV |  | 4.217% | 0.95783 | 8.104% | [5 empty] | TXV | 4.217%
Willows | CA | 95988-0000 |  | 2013-06-26 | 2013-06-26 13:02 | 2013-06-26 13:19 | LENNOX - 12CHP036-3PA | 176 | 8.5 | Yes | Yes | 19.3 | 19.6 | -0.3 | 64313FD12EC34CC9BD5788FE0638FDEC |  | R22 | Non-TXV |  | 4.83% | 0.9517 | 9.281% | [5 empty] | Non-TXV | 4.83%
Los Banos | CA | 93635-7420 |  | 2013-06-03 | 2013-06-03 13:29 | 2013-06-03 13:40 | NORDYNE - JS3BC036KA | 82 | 8.7 | Yes | Yes | 21.6 | 20.9 | 0.7 | FE7E1309BA48473EBA89D59B8F5768C2 |  | R22 | Non-TXV |  | 10.61% | 0.8939 | 20.39% | [5 empty] | Non-TXV | 10.61%
Stockton | CA | 95204-2918 |  | 2013-06-11 | 2013-06-11 12:02 | 2013-06-11 12:19 | LENNOX - HS13481J-SP | 158 | 16.2 | Yes | Yes | 20.6 | 17.4 | 3.2 | A548251713E440D6BC12454032594037 |  | R22 | TXV |  | 10.25% | 0.89747 | 19.7% | [5 empty] | TXV | 10.25%
El Dorado Hills | CA | 95762-9792 |  | 2013-07-08 | 2013-07-08 12:05 | 2013-07-08 12:37 | RHEEM - PRFB-036JAS | 94 | 2.8 | Yes | Yes | 22 | 22.2 | -0.2 | 79B5E23B86104FD7822CBEB77C128A1B |  | R22 | Non-TXV |  | 2.979% | 0.97021 | 5.724% | [5 empty] | Non-TXV | 2.979%
El Dorado Hills | CA | 95762-9792 |  | 2013-07-08 | 2013-07-08 12:29 | 2013-07-08 12:50 | RHEEM - RPCA-036JAO | 82 | 21.6 | Yes | Yes | 19 | 21.2 | -2.2 | 2FEAF8F2D78C43D4B54316E23FD664EF |  | R22 | Non-TXV |  | 26.34% | 0.73659 | 50.62% | [5 empty] | Non-TXV | 26.34%
El Dorado Hills | CA | 95762-9792 |  | 2013-07-08 | 2013-07-08 13:02 | 2013-07-08 13:35 | RHEEM - RAFD-019JAS | 45 | 1.3 | Yes | Yes | 20 | 22.6 | -2.6 | 57A7A644DC7647D285B4FE7192DC84B0 |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Stockton | CA | 95207-7766 |  | 2013-06-14 | 2013-06-14 13:21 | 2013-06-14 13:41 | OTHER - CM18 4TT | 36 | 7.5 | Yes | Yes | 25 | 24 | 1.1 | 6CE753F05A2241158C9290DE6548D7A9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.83% | 0.79167 | 40.04% | [5 empty] | Non-TXV | 20.83%
Fresno | CA | 93720-4048 |  | 2013-06-25 | 2013-06-25 10:38 | 2013-06-25 10:41 | CARRIER - 7777UNK | 108 | 4.1 | Yes | Yes | 19.8 | 17.9 | 1.9 | 429EA5D84D174D56A777C795E69BBD1F |  | R22 | Non-TXV |  | 3.796% | 0.96204 | 7.296% | [5 empty] | Non-TXV | 3.796%
Paso Robles | CA | 93446-4752 |  | 2013-08-06 | 2013-08-06 10:43 | 2013-08-06 11:06 | BRYANT - 561J030-C | 85 | 3.7 | Yes | Yes | 23.5 | 19.9 | 3.6 | B834911F103140DE8DE3298282229333 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Paso Robles | CA | 93446-4491 |  | 2013-09-04 | 2013-09-04 15:21 | 2013-09-04 15:46 | RUUD - UNK | 51 | 19.3 | Yes | Yes | 21.5 | 19.5 | 2 | B2F9065B78794754A26E28816EFF0A3C |  | R22 | Non-TXV |  | 37.84% | 0.62157 | 72.73% | [5 empty] | Non-TXV | 37.84%
Manteca | CA | 95337-6525 |  | 2013-06-19 | 2013-06-19 09:02 | 2013-06-19 09:29 | DAY & NIGHT - 565BJ018 | 82 | 2.5 | Yes | Yes | 19.2 | 19.1 | 0.1 | 3FF71F6B63454973AEA1F8F8CDA83EC8 |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Stockton | CA | 95210-3136 |  | 2013-06-12 | 2013-06-12 14:12 | 2013-06-12 14:37 | YORK - D1NA024N05606C | 54 | 1.7 | Yes | Yes | 23.2 | 21 | 2.3 | F52ACFEC96504EEB97F2384F8D800909 |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Sutter Creek | CA | 95685-0000 |  | 2013-07-24 | 2013-07-24 09:28 | 2013-07-24 09:58 | OTHER - BRHS0361BD | 92 | 2.8 | Yes | Yes | 20.4 | 22.9 | -2.5 | A825F006B13E4B32ADE3A8FF4070F7F7 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Yuba City | CA | 95991-6946 |  | 2013-06-18 | 2013-06-18 08:50 | 2013-06-18 08:50 | TRANE - 2TTB2060A1000AA | 125 | 0 | Yes | Yes | 22.9 | 19.2 | 3.7 | 305B265ED7B14545B6A8DB310DCDD5B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3136 |  | 2013-06-13 | 2013-06-13 08:20 | 2013-06-13 08:41 | RHEEM - UNK | 64 | -6 | Yes | Yes | 19 | 17.7 | 1.3 | 9038D200B17744C9B772F7214D2853E7 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Stockton | CA | 95203-2611 |  | 2013-06-07 | 2013-06-07 11:04 | 2013-06-07 11:23 | YORK - SA36G080-6G | 53 | 3.1 | Yes | Yes | 19 | 18.1 | 0.9 | 9727468FDDEE433ABE13096F4BE1842F |  | R22 | Non-TXV |  | 5.849% | 0.94151 | 11.24% | [5 empty] | Non-TXV | 5.849%
Merced | CA | 95341-5371 |  | 2013-07-02 | 2013-07-02 15:47 | 2013-07-02 15:52 | YORK - H0B030S03A | 71 | 2.5 | Yes | Yes | 22.3 | 18.6 | 3.7 | 4F15BBFC20544FD4A7654B42E8D91375 |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Clovis | CA | 93612-1547 |  | 2013-08-15 | 2013-08-15 15:42 | 2013-08-15 16:33 | GOODMAN - CK24-1B | 71 | 6.8 | Yes | Yes | 21.5 | 17.9 | 3.7 | DA24F09967DA4B6FA11FBE5C48F20E15 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.577% | 0.90423 | 18.41% | [5 empty] | Non-TXV | 9.577%
Placerville | CA | 95667-8438 |  | 2013-06-18 | 2013-06-18 12:04 | 2013-06-18 12:04 | UNITARY PRODUCTS GROUP - BRQ0301BD | 48 | 0 | Yes | Yes | 22 | 20.1 | 1.9 | 81C8F21080B749FF99C650728EEB16E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-3843 |  | 2013-07-15 | 2013-07-15 14:58 | 2013-07-15 14:58 | TEMPSTAR - PGAD42E1K5 | 180 | 0 | Yes | Yes | 17.8 | 20.4 | -2.6 | 3CA7D9CC490343BFA0A8F68D884C60BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9740 |  | 2013-06-21 | 2013-06-21 13:39 | 2013-06-21 14:00 | OTHER - UNK | 90 | 16.8 | Yes | Yes | 17 | 19.9 | -2.9 | 19702821E82644BEA3EE5FE7A237491A |  | R22 | Non-TXV |  | 18.67% | 0.81333 | 35.87% | [5 empty] | Non-TXV | 18.67%
Oakdale | CA | 95361-2750 |  | 2013-06-14 | 2013-06-14 09:51 | 2013-06-14 10:05 | OTHER - UNK | 54 | 1.9 | Yes | Yes | 17.5 | 20.1 | -2.6 | 85C594115CD74280A262FBE4320E8054 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Stockton | CA | 95207-2726 |  | 2013-06-07 | 2013-06-07 08:56 | 2013-06-07 09:16 | GOODMAN - CM30 | 67 | -6.7 | Yes | Yes | 20.4 | 18.3 | 2.1 | 986DA908DAF9402DBA19E168F3C2CF53 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Merced | CA | 95348-1503 |  | 2013-06-11 | 2013-06-11 10:14 | 2013-06-11 10:17 | OTHER - 585EJ030050 | 58 | 4.4 | Yes | Yes | 16.9 | 18.3 | -1.4 | 71DF246A13BB4CD38D812B7368C417C4 |  | R22 | Non-TXV |  | 7.586% | 0.92414 | 14.58% | [5 empty] | Non-TXV | 7.586%
Paso Robles | CA | 93446-4429 |  | 2013-08-06 | 2013-08-06 14:32 | 2013-08-06 14:54 | RHEEM - 13JA24A01 | 77 | 2.6 | Yes | Yes | 24.7 | 19.7 | 5 | 5ABE435CC953400996B8E878E00DC63F |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Live Oak | CA | 95953-9650 |  | 2013-10-02 | 2013-10-02 13:46 | 2013-10-02 14:04 | CARRIER - UNK | 100 | 4.1 | Yes | Yes | 20 | 23 | -3 | 374A1A237BBD47C8AFCFFBB2C733DC67 |  | R22 | Non-TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | Non-TXV | 4.1%
Madera | CA | 93638-1876 |  | 2013-06-13 | 2013-06-13 13:00 | 2013-06-13 13:00 | PAYNE - PY1PNBB03606BAA | 68 | 0 | Yes | Yes | 18.2 | 19.8 | -1.6 | C5785833D8D34CC887E6536F19994ABE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-4429 |  | 2013-09-05 | 2013-09-05 14:40 | 2013-09-05 14:59 | WEATHER KING - 13AJA24A01 | 77 | 4.3 | Yes | Yes | 19.3 | 22.3 | -3 | 0B2D8BC032C1441A98B592CF35610478 |  | R22 | Non-TXV |  | 5.584% | 0.94416 | 10.73% | [5 empty] | Non-TXV | 5.584%
Willows | CA | 95988-2054 |  | 2013-09-09 | 2013-09-09 11:03 | 2013-09-09 11:38 | TRANE - TTD73013100A1 | 69 | 2.4 | Yes | Yes | 21.4 | 21.8 | -0.4 | BC5BB75DFDEE4F09AB2B10CA31D503C0 |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Stockton | CA | 95206-6431 |  | 2013-06-21 | 2013-06-21 09:25 | 2013-06-21 09:41 | CARRIER - 38CKC036350 | 70 | 2.9 | Yes | Yes | 20.3 | 19.4 | 0.9 | 219247D6C6B4413FA6DD0F4090FAE5C4 |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Marysville | CA | 95901-3324 |  | 2013-06-27 | 2013-06-27 09:48 | 2013-06-27 10:07 | BRYANT - 561CJO30-E | 75 | 6.5 | Yes | Yes | 17.5 | 17.7 | -0.2 | 7CB2AE7642C14B9D83E87972D28917C0 |  | R22 | Non-TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | Non-TXV | 8.667%
Corning | CA | 96021-2014 |  | 2013-07-22 | 2013-07-22 13:11 | 2013-07-22 15:02 | GOODMAN - GSC130241AE | 93 | 2.8 | Yes | Yes | 16.8 | 18.8 | -2 | 7FD1DA7F8686488C94B20DF67EEBA76B |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Stockton | CA | 95219-3109 |  | 2013-06-20 | 2013-06-20 12:08 | 2013-06-20 12:28 | RHEEM - AT-30B1F | 88 | -5.2 | Yes | Yes | 20.2 | 19 | 1.2 | C1F9FD2021D54814BA180FA384CE45D2 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Manteca | CA | 95337-7917 |  | 2013-06-19 | 2013-06-19 11:00 | 2013-06-19 11:20 | YORK - H2RA036S06E | 67 | 2.4 | Yes | Yes | 17.1 | 18.8 | -1.7 | 7E0862F341A34559912F7BB44433D801 |  | R22 | Non-TXV |  | 3.582% | 0.96418 | 6.884% | [5 empty] | Non-TXV | 3.582%
Corning | CA | 96021-3002 |  | 2013-06-14 | 2013-06-14 10:00 | 2013-06-14 10:18 | YORK - H1DB018S06A | 62 | 2 | Yes | Yes | 21.5 | 19.3 | 2.2 | E1553010C8684BCABEBEFF8E20C57E23 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Grass Valley | CA | 95945-4848 |  | 2013-06-13 | 2013-06-13 13:51 | 2013-06-13 13:51 | BRYANT - 563CN036-D | 101 | 0 | Yes | Yes | 21 | 19.5 | 1.5 | 3773B05F1B8944E4B520FED29AD70A27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2704 |  | 2013-06-07 | 2013-06-07 14:06 | 2013-06-07 14:06 | AMANA - PHB36C02E1 | 135 | 0 | Yes | Yes | 24.1 | 18.7 | 5.4 | E506BFC1885E44609DE020738FBD7F35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-3222 |  | 2013-06-22 | 2013-06-22 10:35 | 2013-06-22 10:35 | GOODMAN - PGJ036075-1 | 81 | 0 | Yes | Yes | 19 | 18.7 | 0.3 | 119F8336F8A84E88A2C76CA98E9AFB72 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2734 |  | 2013-06-06 | 2013-06-06 09:03 | 2013-06-06 09:21 | PAYNE - 561CJ024-C | 69 | 4.8 | Yes | Yes | 17 | 18.1 | -1.1 | 180022EBFA3A4922954D971A23CB1711 |  | R22 | TXV |  | 6.957% | 0.93043 | 13.37% | [5 empty] | TXV | 6.957%
Gridley | CA | 95948-9760 |  | 2013-08-17 | 2013-08-17 13:24 | 2013-08-17 13:24 | TRANE - 4K26036A1075BA | 101 | 0 | Yes | Yes | 22.2 | 18.3 | 3.9 | 721EFF95948D4FA8B99C8D56DDBA76A2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-3602 |  | 2013-06-26 | 2013-06-26 15:56 | 2013-06-26 15:56 | PAYNE - PY3GNAA30060NA | 98 | 0 | Yes | Yes | 25 | 19.3 | 5.7 | A9C0CF84479C425BA96208C690E711A6 |  | R410A | TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-4108 |  | 2013-06-15 | 2013-06-15 17:48 | 2013-06-15 18:04 | DAY & NIGHT - 597CN036-D | 100 | 4.5 | Yes | Yes | 27.5 | 22.3 | 5.2 | B65340DB2EE547489CF831259B7135B7 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Tracy | CA | 95376-0788 |  | 2013-06-06 | 2013-06-06 11:38 | 2013-06-06 14:05 | TRANE - TTR048SC100A0 | 116 | 5.2 | Yes | Yes | 19.8 | 20.1 | -0.3 | C935330035754C56A8E998DD214B1860 |  | R22 | Non-TXV |  | 4.483% | 0.95517 | 8.615% | [5 empty] | Non-TXV | 4.483%
Merced | CA | 95340-3953 |  | 2013-06-18 | 2013-06-18 08:23 | 2013-06-18 08:25 | RHEEM - RRKAA036JK08X | 62 | 5 | Yes | Yes | 23.6 | 17.6 | 6 | 617E134E366448DA88E51582FDF1AC65 |  | R22 | Non-TXV |  | 8.065% | 0.91935 | 15.5% | [5 empty] | Non-TXV | 8.065%
Fresno | CA | 93703-1312 |  | 2013-05-29 | 2013-05-29 22:44 | 2013-05-29 23:02 | CARRIER - UNK | 83 | -4.9 | Yes | Yes | 28 | 22.6 | 5.4 | F2A6E17955374FC784AA2438D6B6F239 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Lincoln | CA | 95648-2808 |  | 2013-06-22 | 2013-06-22 13:10 | 2013-06-22 13:10 | YORK - H1RC048S06D | 122 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 18A642FCB388402D83017596A50033B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-5218 |  | 2013-06-07 | 2013-06-07 11:36 | 2013-06-07 11:57 | YORK - H2RC048S06A | 120 | 8.3 | Yes | Yes | 23.4 | 20.1 | 3.3 | 74CCBBD0661C4808B0F92DE5E6C045C6 |  | R22 | Non-TXV |  | 6.917% | 0.93083 | 13.29% | [5 empty] | Non-TXV | 6.917%
Marysville | CA | 95901-3528 |  | 2013-08-20 | 2013-08-20 09:41 | 2013-08-20 10:09 | TRANE - 2TTZ9048B100BA | 252 | 9.8 | Yes | Yes | 16 | 18.2 | -2.2 | 42AB859C42134A3384318B3D08AFF47C |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Riverbank | CA | 95367-3157 |  | 2013-07-11 | 2013-07-11 13:25 | 2013-07-11 13:49 | RUUD - CBD | 136 | 4.1 | Yes | Yes | 23.2 | 20.7 | 2.5 | E42C037B62214B84BA1763C6C7D7728A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.015% | 0.96985 | 5.794% | [5 empty] | Non-TXV | 3.015%
El Dorado Hills | CA | 95762-7303 |  | 2013-06-19 | 2013-06-19 09:48 | 2013-06-19 09:48 | PAYNE - 591ANX048000ACAA | 128 | 0 | Yes | Yes | 22.2 | 20.1 | 2.1 | D7BCDC9FB75147D284F4F5D6366EF480 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93636-8453 |  | 2013-06-19 | 2013-06-19 17:05 | 2013-06-19 17:59 | RUUD - UNK | 66 | 2.4 | Yes | Yes | 18.8 | 20.6 | -1.8 | 749EDC2277194B9BB1C5162EB5325063 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Atwater | CA | 95301-0000 |  | 2013-06-06 | 2013-06-06 14:27 | 2013-06-06 14:34 | AIRE-FLO - TTB060C100AOM062S71HF | 146 | 14 | Yes | Yes | 20.8 | 20.9 | -0.1 | A44541E04FC3446E9B8A734ABB69B7DB |  | R22 | Non-TXV |  | 9.589% | 0.90411 | 18.43% | [5 empty] | Non-TXV | 9.589%
Atwater | CA | 95301-0000 |  | 2013-06-06 | 2013-06-06 14:37 | 2013-06-06 14:57 | AIRE-FLO - TTB060C100AOM062S71HF | 146 | 12.8 | Yes | Yes | 17.8 | 20.2 | -2.4 | 094AC12E1EA5412C96AB63706DC37F6A |  | R22 | Non-TXV |  | 8.767% | 0.91233 | 16.85% | [5 empty] | Non-TXV | 8.767%
Riverbank | CA | 95367-9621 |  | 2013-06-11 | 2013-06-11 08:46 | 2013-06-11 09:12 | TRANE - TTL036C100A0 | 149 | 5.8 | Yes | Yes | 23 | 19.3 | 3.7 | 1E2911F5147547F7A755C7F2CC756C71 |  | R22 | Non-TXV |  | 3.893% | 0.96107 | 7.481% | [5 empty] | Non-TXV | 3.893%
Madera | CA | 93638-1892 |  | 2013-07-17 | 2013-07-17 11:05 | 2013-07-17 11:22 | BRYANT - 582ANW036060NBAF | 70 | -4.1 | Yes | Yes | 17.6 | 18.6 | -0.9 | 624CE224F0314458AB0C47F17330ABBF |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Yuba City | CA | 95991-9442 |  | 2013-06-21 | 2013-06-21 14:50 | 2013-06-21 15:11 | LENNOX - 13ACC-036-230-02 | 115 | 7.6 | Yes | Yes | 26 | 23.7 | 2.3 | 04815147E9404E7783413607F7B8F2D3 |  | R22 | Non-TXV |  | 6.609% | 0.93391 | 12.7% | [5 empty] | Non-TXV | 6.609%
Yuba City | CA | 95991-9442 |  | 2013-06-21 | 2013-06-21 15:14 | 2013-06-21 15:35 | LENNOX - 13ACC-036-230-02 | 115 | 4.2 | Yes | Yes | 22 | 22.6 | -0.6 | 84212D099A1E48EEB58242432E765157 |  | R22 | TXV |  | 3.652% | 0.96348 | 7.019% | [5 empty] | TXV | 3.652%
Fresno | CA | 93726-0959 |  | 2013-05-29 | 2013-05-29 15:48 | 2013-05-29 16:22 | DAY & NIGHT - N/A | 60 | 1.9 | Yes | Yes | 23.2 | 19.1 | 4.2 | 42498A43984947158F08EC912E7D6248 |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Clovis | CA | 93612-1541 |  | 2013-06-25 | 2013-06-25 15:35 | 2013-06-25 16:01 | UNITARY PRODUCTS GROUP - DBYP-F024N045A | 100 | 3.2 | Yes | Yes | 24.6 | 20.4 | 4.2 | 11738A6E6A2A40C89727ED608DABA0E9 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Merced | CA | 95341-8993 |  | 2013-07-03 | 2013-07-03 10:14 | 2013-07-03 10:16 | ICP - PGC024K060E | 54 | 3.8 | Yes | Yes | 17.7 | 19.6 | -1.9 | B3E98B440AC24321992F3C6743791EE0 |  | R22 | Non-TXV |  | 7.037% | 0.92963 | 13.52% | [5 empty] | Non-TXV | 7.037%
Fresno | CA | 93720-0876 |  | 2013-08-13 | 2013-08-13 08:43 | 2013-08-13 08:57 | BDP - 568EJ030 | 118 | 10.2 | Yes | Yes | 23.4 | 17.7 | 5.7 | 53ABAC9D52DB46D8B12F9C5FD829A1E5 |  | R22 | Non-TXV |  | 8.644% | 0.91356 | 16.61% | [5 empty] | Non-TXV | 8.644%
Fresno | CA | 93720-0876 |  | 2013-08-13 | 2013-08-13 09:06 | 2013-08-13 09:27 | BDP - 568EJ030 | 118 | 10.8 | Yes | Yes | 18.9 | 17.2 | 1.7 | A72509BF359F47F98A7B7AF73FBF0B42 |  | R22 | Non-TXV |  | 9.153% | 0.90847 | 17.59% | [5 empty] | Non-TXV | 9.153%
Stockton | CA | 95206-6409 |  | 2013-06-18 | 2013-06-18 09:41 | 2013-06-18 09:58 | GOODMAN - CKL-301F | 72 | 5.8 | Yes | Yes | 20.7 | 19.7 | 1.1 | 24B9729351FF4D33B11025671B4E600B |  | R22 | Non-TXV |  | 8.056% | 0.91944 | 15.48% | [5 empty] | Non-TXV | 8.056%
Clovis | CA | 93611-1436 |  | 2013-06-12 | 2013-06-12 11:17 | 2013-06-12 11:40 | AMANA - PGD48C0902E | 139 | 4.1 | Yes | Yes | 22.8 | 20.2 | 2.7 | 3203F2EAD74F481B950514288E25C853 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.95% | 0.9705 | 5.669% | [5 empty] | Non-TXV | 2.95%
Yuba City | CA | 95993-8257 |  | 2013-06-20 | 2013-06-20 13:49 | 2013-06-20 14:10 | OTHER - 561AJ042-A | 90 | 2.7 | Yes | Yes | 27 | 21 | 6 | 29B207FCEF4845F087E85D2B3A666E28 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95928-6817 |  | 2013-07-16 | 2013-07-16 20:17 | 2013-07-16 20:34 | TEMPSTAR - PGF33606BK01A1 | 176 | 5.9 | Yes | Yes | 17.8 | 20.4 | -2.6 | 99F5F0ACD15141EFAD38D7891D4B61C4 |  | R22 | Non-TXV |  | 3.352% | 0.96648 | 6.442% | [5 empty] | Non-TXV | 3.352%
Stockton | CA | 95203-1507 |  | 2013-07-15 | 2013-07-15 09:22 | 2013-07-15 09:41 | RHEEM - RAKA-030JAZ | 66 | -5.4 | Yes | Yes | 15.2 | 17.7 | -2.5 | 01F3EB23F9FF4577A19AC111D56388F0 |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Stockton | CA | 95204-2905 |  | 2013-06-11 | 2013-06-11 13:48 | 2013-06-11 13:48 | RHEEM - RRNA-B036JK06X | 83 | 0 | Yes | Yes | 17.5 | 18.5 | -1 | 174C04B7F01A4CCB8CBC3A248943271B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2892 |  | 2013-06-12 | 2013-06-12 13:34 | 2013-06-12 13:59 | GOODMAN - GSC130301EA | 85 | 6.5 | Yes | Yes | 23.5 | 21 | 2.5 | 28158D274B5E4BA69743F5DC9CD818BF |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Stockton | CA | 95206-6216 |  | 2013-08-12 | 2013-08-12 12:13 | 2013-08-12 12:37 | BDP - 561CJ036-D | 82 | -7.7 | Yes | Yes | 25 | 19.5 | 5.5 | 5A829C37EB474838BDB2EA76F485E33B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.39% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.39%
Manteca | CA | 95337-6512 |  | 2013-06-06 | 2013-06-06 15:43 | 2013-06-06 16:11 | BDP - 565BJ024 | 70 | 2.3 | Yes | Yes | 15.7 | 18.4 | -2.7 | 82150F09338D497EB7BF02D8928F207A |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Fresno | CA | 93710-6837 |  | 2013-07-01 | 2013-07-01 14:57 | 2013-07-01 15:01 | RUUD - URKAA024JK04E | 50 | 5.4 | Yes | Yes | 22.7 | 22 | 0.7 | 6F29F5DB7228494DAE1F689EAC929277 |  | R22 | Non-TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | Non-TXV | 10.8%
Yuba City | CA | 95993-5002 |  | 2013-06-21 | 2013-06-21 09:46 | 2013-06-21 10:04 | LENNOX - 13ACD-036-230-01 | 111 | 9.1 | Yes | Yes | 20 | 20.9 | -0.9 | BA6AD326C81E403BA1065D477B831EA9 |  | R22 | Non-TXV |  | 8.198% | 0.91802 | 15.76% | [5 empty] | Non-TXV | 8.198%
Yuba City | CA | 95993-5002 |  | 2013-06-21 | 2013-06-21 10:07 | 2013-06-21 10:24 | LENNOX - 13ACD-036-230-01 | 111 | 29.2 | Yes | Yes | 18 | 20.4 | -2.4 | CBBBC8E0947F4D5EAD28C58821B82859 |  | R22 | Non-TXV |  | 26.31% | 0.73694 | 50.55% | [5 empty] | Non-TXV | 26.31%
Yuba City | CA | 95993-6107 |  | 2013-07-18 | 2013-07-18 09:26 | 2013-07-18 09:51 | BRYANT - 563CN042000AEAA | 103 | 4.1 | Yes | Yes | 24 | 20.4 | 3.6 | 7AAD0D1599C9466CA0D0FAC07A9EF79D |  | R22 | TXV |  | 3.981% | 0.96019 | 7.65% | [5 empty] | TXV | 3.981%
Yuba City | CA | 95993-6107 |  | 2013-07-18 | 2013-07-18 09:52 | 2013-07-18 10:10 | BRYANT - 563N030-C | 100 | 3.6 | Yes | Yes | 20 | 18.8 | 1.2 | 2576A9EDD2A244748581C057C305C515 |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Willows | CA | 95988-3342 |  | 2013-06-27 | 2013-06-27 18:16 | 2013-06-27 18:38 | LENNOX - HS26-030-3P | 78 | 10.9 | Yes | Yes | 15.3 | 14.7 | 0.6 | 1C18DD9751C845B1889741CF77F189C5 |  | R22 | Non-TXV |  | 13.97% | 0.86026 | 26.86% | [5 empty] | Non-TXV | 13.97%
Artois | CA | 95913-0000 |  | 2013-09-11 | 2013-09-11 10:12 | 2013-09-11 10:31 | AMANA - PGD24C0452X | 74 | 6.4 | Yes | Yes | 20.5 | 21 | -0.5 | 925B185E4D0C4E54B15C3C27FAD525BD |  | R22 | Non-TXV |  | 8.649% | 0.91351 | 16.62% | [5 empty] | Non-TXV | 8.649%
Artois | CA | 95913-0000 |  | 2013-09-11 | 2013-09-11 10:31 | 2013-09-11 10:49 | TRANE - TTRO18BC100A0 | 51 | 6.2 | Yes | Yes | 19.5 | 19.9 | -0.4 | F76613818D2E454CB651B229A71F03E3 |  | R22 | Non-TXV |  | 12.16% | 0.87843 | 23.36% | [5 empty] | Non-TXV | 12.16%
Fresno | CA | 93726-5423 |  | 2013-06-07 | 2013-06-07 10:27 | 2013-06-07 10:48 | BRYANT - 583ANW042090AAAF | 118 | 6.8 | Yes | Yes | 20.8 | 19.7 | 1.1 | 41D88A2683BD483CB4B21535C619F54B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.763% | 0.94237 | 11.07% | [5 empty] | Non-TXV | 5.763%
Fresno | CA | 93720-4415 |  | 2013-09-16 | 2013-09-16 08:43 | 2013-09-16 08:45 | LENNOX - 10ACB425P | 89 | 7.4 | Yes | Yes | 22.7 | 18.2 | 4.5 | 72FD1352AAF64C7B873555470F59A3C3 |  | R22 | Non-TXV |  | 8.315% | 0.91685 | 15.98% | [5 empty] | Non-TXV | 8.315%
Madera | CA | 93638-0905 |  | 2013-06-13 | 2013-06-13 13:28 | 2013-06-13 13:28 | RHEEM - URGG-07E43JKR | 89 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | EDC1204347EE46AEB3FE5B7A68ACB33A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-6094 |  | 2013-06-19 | 2013-06-19 10:12 | 2013-06-19 10:29 | BRYANT - 563CN036-F | 103 | 3.2 | Yes | Yes | 19 | 19.3 | -0.3 | 654E06428E6C40D79080F1C0163FDB39 |  | R22 | Non-TXV |  | 3.107% | 0.96893 | 5.971% | [5 empty] | Non-TXV | 3.107%
Stockton | CA | 95206-6243 |  | 2013-06-21 | 2013-06-21 12:27 | 2013-06-21 12:46 | GOODMAN - CKJ36-1AE | 97 | 9.3 | Yes | Yes | 20.9 | 18.8 | 2.2 | E66282DE1C3A459082CC0C2125F2E76C |  | R22 | Non-TXV |  | 9.588% | 0.90412 | 18.43% | [5 empty] | Non-TXV | 9.588%
Atwater | CA | 95301-3227 |  | 2013-07-10 | 2013-07-10 09:31 | 2013-07-10 09:33 | RHEEM - HC-80-24-21C | 49 | 2.2 | Yes | Yes | 20.6 | 19.4 | 1.2 | 4ABA44F816BB4BF585A21091D6871C4A |  | R22 | Non-TXV |  | 4.49% | 0.9551 | 8.628% | [5 empty] | Non-TXV | 4.49%
Chico | CA | 95926-1230 |  | 2013-06-11 | 2013-06-11 18:45 | 2013-06-11 19:02 | BDP - BPGM0240451AA | 50 | 6.3 | Yes | Yes | 24.5 | 19.9 | 4.6 | 608009F25C104059A7B34C0AE4E99D71 |  | R22 | Non-TXV |  | 12.6% | 0.874 | 24.21% | [5 empty] | Non-TXV | 12.6%
Magalia | CA | 95954-9447 |  | 2013-07-18 | 2013-07-18 12:47 | 2013-07-18 14:00 | GE - BWC030B100B0 | 128 | 13.8 | Yes | Yes | 18.5 | 21 | -2.5 | 16F2618D31BD47309CC50A8D5E6CD704 |  | R22 | Non-TXV |  | 10.78% | 0.89219 | 20.72% | [5 empty] | Non-TXV | 10.78%
Rescue | CA | 95672-9548 |  | 2013-08-10 | 2013-08-10 14:09 | 2013-08-10 14:09 | DAY & NIGHT - UNK | 67 | 0 | Yes | Yes | 18.9 | 18.7 | 0.2 | A0C264C78AF64320A6ED9FF5BA613666 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-9770 |  | 2013-06-06 | 2013-06-06 12:50 | 2013-06-06 13:09 | CARRIER - 38TH048320 | 128 | 19.7 | Yes | Yes | 20.6 | 16.6 | 4 | 2676059F7C3F49BEAA9D4567D71C0924 |  | R22 | Non-TXV |  | 15.39% | 0.84609 | 29.58% | [5 empty] | Non-TXV | 15.39%
Stockton | CA | 95210-6708 |  | 2013-07-29 | 2013-07-29 14:02 | 2013-07-29 14:25 | YORK - H1DE030S06B | 80 | -12 | Yes | Yes | 23.4 | 20.3 | 3.2 | DFFAF866587E42CE942E609AC07AF306 |  | R22 | TXV |  | -15% | 1.15 | 4.201% |  |  |  |  | TXV |  |  | -15%
Ione | CA | 95640-4500 |  | 2013-07-24 | 2013-07-24 16:06 | 2013-07-24 16:32 | YORK - H2RD030S068 | 93 | 8.3 | Yes | Yes | 17 | 19.8 | -2.8 | D70A75D3DFEC4214BC5DE5B050598C5C |  | R22 | TXV |  | 8.925% | 0.91075 | 17.15% | [5 empty] | TXV | 8.925%
Stockton | CA | 95205-3843 |  | 2013-06-06 | 2013-06-06 08:37 | 2013-06-06 08:37 | RHEEM - RRNL-B036JK06X | 93 | 0 | Yes | Yes | 22.8 | 18.8 | 4 | AC957F9F812F456B96BB643D567E8936 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Orland | CA | 95963-1583 |  | 2013-06-17 | 2013-06-17 12:46 | 2013-06-17 13:39 | YORK - P1NP036N072 | 108 | 5.3 | Yes | Yes | 20.1 | 20.2 | 0 | D73E8A9DE7C44D13B00ED69535501A6E |  | R22 | Non-TXV |  | 4.907% | 0.95093 | 9.431% | [5 empty] | Non-TXV | 4.907%
Willows | CA | 95988-3331 |  | 2013-06-27 | 2013-06-27 19:08 | 2013-06-27 19:27 | PAYNE - PY1NB036090ABAA | 68 | 2.8 | Yes | Yes | 21.9 | 19.5 | 2.4 | 2BD5272AB4CF4CBBBA822A9EA7805E29 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Merced | CA | 95348-2842 |  | 2013-09-04 | 2013-09-04 09:32 | 2013-09-04 09:36 | BRYANT - 582ANW030040AAAD | 55 | 5.8 | Yes | Yes | 22.3 | 18.2 | 4.1 | F085115A7BFE41FD8AC7D9301BEF7116 |  | R22 | Non-TXV |  | 10.55% | 0.89455 | 20.27% | [5 empty] | Non-TXV | 10.55%
Chico | CA | 95926-8661 |  | 2013-06-07 | 2013-06-07 17:19 | 2013-06-07 17:43 | ALLEGIANCE - 7APD48B100A1 | 97 | 10.2 | Yes | Yes | 24 | 20.7 | 3.3 | FFE6E039D82E4126A47A4FC9F09F2C64 |  | R22 | Non-TXV |  | 10.52% | 0.89485 | 20.21% | [5 empty] | Non-TXV | 10.52%
Los Banos | CA | 93635-3426 |  | 2013-07-08 | 2013-07-08 09:34 | 2013-07-08 09:36 | BDP - 589ANW036060ACAF | 84 | 8.6 | Yes | Yes | 18.1 | 18.1 | 0 | D52834D9360C4E1892C786837B1B93DC |  | R22 | Non-TXV |  | 10.24% | 0.89762 | 19.68% | [5 empty] | Non-TXV | 10.24%
Yuba City | CA | 95993-9032 |  | 2013-06-20 | 2013-06-20 14:23 | 2013-06-20 14:45 | AMANA - ARCF30V01D | 109 | 18 | Yes | Yes | 19 | 20.4 | -1.4 | D3218F61DA4B4E688E11B09798446C54 |  | R22 | Non-TXV |  | 16.51% | 0.83486 | 31.74% | [5 empty] | Non-TXV | 16.51%
Merced | CA | 95348-3024 |  | 2013-07-11 | 2013-07-11 15:36 | 2013-07-11 15:38 | YORK - D1NA030N05606C | 76 | 4 | Yes | Yes | 23.5 | 21.3 | 2.2 | F10EC7F5FBE64F7392C63BAAF90F6174 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Placerville | CA | 95667-3033 |  | 2013-06-18 | 2013-06-18 16:26 | 2013-06-18 16:26 | TRANE - UNK PGE SHUTOFF OVER DATAPLATE | 187 | 0 | Yes | Yes | 26.4 | 20.6 | 5.8 | ED61126A6FC24AC581941D38A2B3C7A7 |  | R22 | TXV |  | 0% | 1 | 0%
Willows | CA | 95988-2053 |  | 2013-06-27 | 2013-06-27 12:31 | 2013-06-27 12:31 | GOODMAN - CK30-1T | 76 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | E54AE64C1976417997F73BC8117408B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1554 |  | 2013-06-13 | 2013-06-13 14:44 | 2013-06-13 14:44 | DAY & NIGHT - UNK | 74 | 0 | Yes | Yes | 17.5 | 19.5 | -2 | 60F46C47075B4B06B03907BA75876C67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-5506 |  | 2013-07-30 | 2013-07-30 18:18 | 2013-07-31 09:34 | YORK - D1NA036NO5606C | 66 | 3 | Yes | Yes | 16.8 | 19.7 | -2.9 | BAFCFE47463241ABA22731AAA5FA8B52 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Oroville | CA | 95966-3942 |  | 2013-06-19 | 2013-06-19 10:02 | 2013-06-19 10:02 | CARRIER - 25HPA442A300 | 56 | 0 | Yes | Yes | 20.7 | 18.6 | 2.1 | 172FCAD596914C6E94357F9B71EC042F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-3912 |  | 2013-06-26 | 2013-06-26 12:14 | 2013-06-26 12:32 | YORK - D3NZ036N05606NXB | 64 | 2.9 | Yes | Yes | 19 | 17.2 | 1.8 | C9D932F62411499B8166853DDBE86A39 |  | R22 | TXV |  | 4.531% | 0.95469 | 8.708% | [5 empty] | TXV | 4.531%
Stockton | CA | 95210-4438 |  | 2013-06-17 | 2013-06-17 09:31 | 2013-06-17 09:48 | PAYNE - 591ANX060000AAAA | 170 | -12 | Yes | Yes | 25.5 | 19.6 | 5.9 | EF5ECE1FD1734A8E86787A6CF4A12859 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Lincoln | CA | 95648-2983 |  | 2013-06-14 | 2013-06-14 14:46 | 2013-06-14 14:46 | YORK - H1RD030S06G | 121 | 0 | Yes | Yes | 17.2 | 20.2 | -3 | DCC4929FCB6E4501B2F1CDD4B7CCDE21 |  | R22 | TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-2419 |  | 2013-06-20 | 2013-06-20 15:49 | 2013-06-20 16:08 | NORDYNE - N/A | 90 | 4.9 | Yes | Yes | 17.6 | 19.9 | -2.3 | 95C6CC66EE2A49209CF056484AF54097 |  | R22 | Non-TXV |  | 5.444% | 0.94556 | 10.46% | [5 empty] | Non-TXV | 5.444%
Clovis | CA | 93611-5128 |  | 2013-06-14 | 2013-06-14 12:16 | 2013-06-14 12:52 | BDP - 585EJW042075ABAF | 84 | 5.2 | Yes | Yes | 24.7 | 20.7 | 4 | 17E8CFC7D5414B79AD8C4F1722F9F1D0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | Non-TXV | 6.19%
Stockton | CA | 95212-2736 |  | 2013-06-25 | 2013-06-25 14:03 | 2013-06-25 14:33 | CARRIER - 38CKC036350 | 70 | 2.4 | Yes | Yes | 17.6 | 15.8 | 1.8 | C4F14481DA8C47609C200AE35022BAF0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Willows | CA | 95988-3032 |  | 2013-06-26 | 2013-06-26 18:28 | 2013-06-26 18:46 | RUUD - NA | 100 | 4.9 | Yes | Yes | 16.4 | 18.6 | -2.2 | 7C2FD93C0B574F6A9D50F9A0F44E6C81 |  | R22 | Non-TXV |  | 4.9% | 0.951 | 9.417% | [5 empty] | Non-TXV | 4.9%
Stockton | CA | 95205-6140 |  | 2013-06-06 | 2013-06-06 15:42 | 2013-06-06 16:10 | LENNOX - HS26-311-1P | 129 | 9.2 | Yes | Yes | 21.7 | 19.2 | 2.5 | E3B09E77BC7245ECA83D0495F0689B89 |  | R22 | Non-TXV |  | 7.132% | 0.92868 | 13.71% | [5 empty] | Non-TXV | 7.132%
Manteca | CA | 95337-6887 |  | 2013-06-11 | 2013-06-11 14:49 | 2013-06-11 15:13 | TRANE - TTN030C100C4 | 87 | 4.6 | Yes | Yes | 24.8 | 19.7 | 5.1 | 70371F2722B04AEB8AE9917BCF05D876 |  | R22 | Non-TXV |  | 5.287% | 0.94713 | 10.16% | [5 empty] | Non-TXV | 5.287%
Stockton | CA | 95207-2820 |  | 2013-06-07 | 2013-06-07 09:29 | 2013-06-07 09:48 | PAYNE - 561CJX024000ACAA | 70 | 8 | Yes | Yes | 18.9 | 17.9 | 1.1 | D3C46DE1C89B42398735BBDEF3CA944A |  | R22 | Non-TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | Non-TXV | 11.43%
Stockton | CA | 95206-2743 |  | 2013-06-12 | 2013-06-12 09:12 | 2013-06-12 09:46 | HEIL - HAC224AKA4 | 85 | -7 | Yes | Yes | 23.2 | 19.3 | 3.9 | 6464A14E8F424210A9FE05B2D4CF25D5 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Manteca | CA | 95336-6907 |  | 2013-06-19 | 2013-06-19 13:31 | 2013-06-19 14:00 | DAY & NIGHT - 585GJ030040 | 58 | 5.6 | Yes | Yes | 18 | 20.7 | -2.7 | 89F76450AE5141D5AE8FBE25FC5C2B35 |  | R22 | Non-TXV |  | 9.655% | 0.90345 | 18.56% | [5 empty] | Non-TXV | 9.655%
Stockton | CA | 95206-6418 |  | 2013-07-30 | 2013-07-30 14:00 | 2013-07-30 14:21 | GOODMAN - CKL36-1L | 84 | 5.4 | Yes | Yes | 19.3 | 19.2 | 0.1 | E8060FA70170466383D4828CD0C97284 |  | R22 | Non-TXV |  | 6.429% | 0.93571 | 12.35% | [5 empty] | Non-TXV | 6.429%
Clovis | CA | 93612-2336 |  | 2013-06-18 | 2013-06-18 14:17 | 2013-06-18 14:44 | CARRIER - 48GX-042090301AD | 118 | 8.6 | Yes | Yes | 25.1 | 19.1 | 6 | 89F244163A0140BBAE6B4FDD60212BF0 |  | R22 | Non-TXV |  | 7.288% | 0.92712 | 14.01% | [5 empty] | Non-TXV | 7.288%
Clovis | CA | 93612-4450 |  | 2013-06-18 | 2013-06-18 15:07 | 2013-06-18 15:25 | ICP - NPGAD36D1K6 | 102 | 4.5 | Yes | Yes | 27.2 | 22.1 | 5.1 | FF48C60023D2466886935EA0EF53B1F6 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Livingston | CA | 95334-1818 |  | 2013-08-21 | 2013-08-21 15:08 | 2013-08-21 15:38 | TRANE - 4TTX3030A1000AA | 66 | 11.9 | Yes | Yes | 17.3 | 19.1 | -1.8 | 5925B7947C23404A8B9B38A9FBD1B321 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 18.03% | 0.8197 | 34.65% | [5 empty] | Non-TXV | 18.03%
Fresno | CA | 93703-1822 |  | 2013-08-13 | 2013-08-13 11:47 | 2013-08-13 11:48 | GOODMAN - GPG13360701AB | 112 | 16.8 | Yes | Yes | 23.3 | 17.9 | 5.4 | C73586D7493840B399E2637EBCD3DB0B |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Atwater | CA | 95301-4810 |  | 2013-06-07 | 2013-06-07 12:34 | 2013-06-07 12:40 | BDP - 598AN036 | 194 | 8 | Yes | Yes | 20.9 | 18.3 | 2.6 | E9B67CDE896546A595B983EB580E4A29 |  | R22 | Non-TXV |  | 4.124% | 0.95876 | 7.925% | [5 empty] | Non-TXV | 4.124%
Atwater | CA | 95301-3722 |  | 2013-06-07 | 2013-06-07 13:39 | 2013-06-07 13:52 | GOODMAN - PGB0300751A | 56 | 4.7 | Yes | Yes | 21.6 | 20.6 | 1 | EC74A33DE100401EA022FA9ADD31E54B |  | R22 | Non-TXV |  | 8.393% | 0.91607 | 16.13% | [5 empty] | Non-TXV | 8.393%
Valley Springs | CA | 95252-9573 |  | 2013-07-16 | 2013-07-16 10:40 | 2013-07-16 11:02 | BRYANT - 577CNWA30060NA | 86 | 4 | Yes | Yes | 22.5 | 20.9 | 1.6 | DB6E6886C1714B1F928A10249B2E1820 | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 4.651% | 0.95349 | 8.939% | [5 empty] | TXV | 4.651%
Clovis | CA | 93612-0704 |  | 2013-06-21 | 2013-06-21 11:14 | 2013-06-21 11:54 | UNITARY PRODUCTS GROUP - DCYZ-F030N070B | 64 | 3.4 | Yes | Yes | 26 | 21.5 | 4.5 | 486CBE6F005D4FF883D4F0B9222D7E1B | OK: Verified Refrigerant Charge Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 5.312% | 0.94688 | 10.21% | [5 empty] | TXV | 5.312%
Atwater | CA | 95301-4838 |  | 2013-06-06 | 2013-06-06 13:32 | 2013-06-06 13:43 | AIRE-FLO - 561CJ030 | 71 | 14.8 | Yes | Yes | 19.9 | 20.2 | -0.3 | 76425408CC77442EACA543273853C196 |  | R22 | TXV |  | 20.85% | 0.79155 | 40.06% | [5 empty] | TXV | 20.85%
Newman | CA | 95360-9709 |  | 2013-06-05 | 2013-06-05 14:45 | 2013-06-05 15:34 | ICP - CA9048VKA2 | 206 | 12.2 | Yes | Yes | 22.7 | 20.4 | 2.3 | 7EB940B095CA47DFA15E38DF5F7C5E6B |  | R22 | Non-TXV |  | 5.922% | 0.94078 | 11.38% | [5 empty] | Non-TXV | 5.922%
Manteca | CA | 95337-4215 |  | 2013-06-06 | 2013-06-06 12:23 | 2013-06-06 12:44 | RHEEM - RRNA-B024JK06X | 70 | 2.2 | Yes | Yes | 17.3 | 19.3 | -2 | 8541041E04C840C3A95725783C7B0B5B |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Stockton | CA | 95210-3744 |  | 2013-06-13 | 2013-06-13 13:53 | 2013-06-13 14:12 | TRANE - TTP036C100A2 | 140 | 37.8 | Yes | Yes | 20.3 | 21 | -0.7 | 008403185653468E8073A58665ECD0CE |  | R22 | Non-TXV |  | 27% | 0.73 | 51.89% | [5 empty] | Non-TXV | 27%
Fresno | CA | 93726-1120 |  | 2013-05-30 | 2013-05-30 13:14 | 2013-05-30 13:32 | BRYANT - 583ANW060115AAAG | 129 | -9.1 | Yes | Yes | 22.5 | 19.8 | 2.7 | D565DCAA414840BBBF4714863264CF8F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -7.054% | 1.0705 | 1.976% |  |  |  |  | Non-TXV |  |  | -7.054%
Fresno | CA | 93726-5840 |  | 2013-06-10 | 2013-06-10 11:30 | 2013-06-10 11:48 | BDP - 585HJW048080ABAF | 118 | 7.1 | Yes | Yes | 18.7 | 19.9 | -1.2 | 1343A3EC44554AE4B345552465B8A085 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.017% | 0.93983 | 11.56% | [5 empty] | Non-TXV | 6.017%
Lincoln | CA | 95648-2802 |  | 2013-06-18 | 2013-06-18 15:53 | 2013-06-18 16:14 | YORK - HIRC036S06B | 98 | -9.2 | Yes | Yes | 19 | 21.4 | -2.4 | 3CD5448568A4446B97BE5C4F189F7253 |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Auburn | CA | 95603-3235 |  | 2013-08-19 | 2013-08-19 15:17 | 2013-08-19 15:17 | PAYNE - 597CN036-D | 100 | 0 | Yes | Yes | 26.4 | 20.7 | 5.8 | 9601A4D0656F4B9EBC27AE4FEE573462 |  | R22 | TXV |  | 0% | 1 | 0%
Live Oak | CA | 95953-2148 |  | 2013-08-05 | 2013-08-05 10:02 | 2013-08-05 10:46 | CARRIER - 38CK042350 | 90 | 6.4 | Yes | Yes | 21 | 20.4 | 0.6 | D3CB5F662278413DBAC0D3AD86811FDB |  | R22 | TXV |  | 7.111% | 0.92889 | 13.67% | [5 empty] | TXV | 7.111%
Gerber | CA | 96035-9798 |  | 2013-09-13 | 2013-09-13 16:34 | 2013-09-13 16:55 | RHEEM - RRNA-A036JK08E | 114 | 3.5 | Yes | Yes | 20 | 20.1 | -0.1 | D2A29FAC9BAE4197BBAFE94552F3E132 |  | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
Gerber | CA | 96035-9798 |  | 2013-09-13 | 2013-09-13 17:37 | 2013-09-13 17:54 | RHEEM - RRMA-A036JK08E | 99 | 4.1 | Yes | Yes | 16.4 | 19.3 | -2.9 | A5A0CD25EA8D4626906A6667C0CA06E8 |  | R22 | Non-TXV |  | 4.141% | 0.95859 | 7.959% | [5 empty] | Non-TXV | 4.141%
Los Banos | CA | 93635-5124 |  | 2013-05-31 | 2013-05-31 13:32 | 2013-05-31 13:39 | GOODMAN - SSX140421BA | 170 | 9.2 | Yes | Yes | 21.3 | 21.5 | -0.2 | 38058D64A3584ED6B8D258301C816406 |  | R410A | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Tracy | CA | 95376-7915 |  | 2013-06-06 | 2013-06-06 08:11 | 2013-06-06 08:56 | BRYANT - 561CJ060-A | 233 | -13.7 | Yes | Yes | 20 | 20.3 | -0.3 | 399D748D233C4FBB8E1FCAA5B98AE821 |  | R22 | Non-TXV |  | -5.88% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.88%
Fresno | CA | 93727-3329 |  | 2013-07-22 | 2013-07-22 10:22 | 2013-07-22 10:25 | CARRIER - 38TH060300 | 169 | 5 | Yes | Yes | 23.4 | 20.1 | 3.3 | CC94AFDDEFD74B70B4C7E1EACD8BE50E |  | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.686% | [5 empty] | Non-TXV | 2.959%
Gerber | CA | 96035-9721 |  | 2013-08-19 | 2013-08-19 18:37 | 2013-08-19 18:54 | YORK - CMA03611A | 95 | 2.8 | Yes | Yes | 20.4 | 21.5 | -1.1 | 3C3DEAC858A447B7B749E75AB9AA9C09 |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Stockton | CA | 95203-1131 |  | 2013-06-07 | 2013-06-07 15:23 | 2013-06-07 15:40 | GOODMAN - CKL18-1 | 50 | 4.3 | Yes | Yes | 20.6 | 18.5 | 2.1 | 509D12425DDD4EA58204C61A45BA7B3E |  | R22 | Non-TXV |  | 8.6% | 0.914 | 16.53% | [5 empty] | Non-TXV | 8.6%
Granite Bay | CA | 95746-9649 |  | 2013-06-22 | 2013-06-22 09:26 | 2013-06-22 09:26 | RHEEM - RRGG-12E61JKR | 136 | 0 | Yes | Yes | 22 | 19.5 | 2.5 | 1D12291C0ACD40B5B7EDD505A0E42B61 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-6912 |  | 2013-08-21 | 2013-08-21 17:17 | 2013-08-21 17:37 | BRYANT - 113RNA036-B | 90 | 4.1 | Yes | Yes | 23.5 | 20.7 | 2.8 | 61F98E911DAE4D23A1BA3FEC3464A958 |  | R22 | TXV |  | 4.556% | 0.95444 | 8.755% | [5 empty] | TXV | 4.556%
Los Banos | CA | 93635-6375 |  | 2013-08-05 | 2013-08-05 11:35 | 2013-08-05 11:39 | BRYANT - 563CN048-H | 140 | 4.2 | Yes | Yes | 21.4 | 19.7 | 1.7 | E1AA00C444004C469E9B8E0A0F1DE9FF |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-5223 |  | 2013-06-03 | 2013-06-03 12:05 | 2013-06-03 12:12 | CARRIER - 38TH042310 | 112 | 5.6 | Yes | Yes | 27.4 | 21.5 | 5.9 | DF513984293D4A0BBEA22C21E8F3B019 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95206-6412 |  | 2013-06-18 | 2013-06-18 08:57 | 2013-06-18 09:17 | AMANA - GSC130361GA | 77 | -26.2 | Yes | Yes | 19.6 | 19.4 | 0.2 | F280A102B90541D8B60E648F376174CA | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -34.03% | 1.3403 | 9.529% |  |  |  |  | TXV |  |  | -34.03%
Fresno | CA | 93726-2324 |  | 2013-06-18 | 2013-06-18 13:08 | 2013-06-18 13:10 | CARRIER - 38CKB030C300 | 68 | 3.8 | Yes | Yes | 21 | 20.7 | 0.3 | B5CEE9D9C2844C0091D0AD5B08DF0C0C |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Atwater | CA | 95301-2228 |  | 2013-06-05 | 2013-06-05 09:54 | 2013-06-05 09:57 | RHEEM - HC802421C | 49 | 4.4 | Yes | Yes | 24 | 18.2 | 5.8 | 8797A1AE40FC473A9F4435A3AE721E8D |  | R22 | Non-TXV |  | 8.98% | 0.9102 | 17.26% | [5 empty] | Non-TXV | 8.98%
Atwater | CA | 95301-2228 |  | 2013-06-05 | 2013-06-05 10:13 | 2013-06-05 10:15 | RHEEM - HC802421C | 49 | 3.1 | Yes | Yes | 25.8 | 19.9 | 5.9 | 242BB804ADE74D5F9F8E809A929393C1 |  | R22 | Non-TXV |  | 6.327% | 0.93673 | 12.16% | [5 empty] | Non-TXV | 6.327%
Fresno | CA | 93710-5243 |  | 2013-06-10 | 2013-06-10 21:20 | 2013-06-10 21:20 | CARRIER - UNK | 62 | 0 | Yes | Yes | 17 | 19.8 | -2.8 | 9E9F9A1262CE499DAB3D547DCC1C152A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-3170 |  | 2013-07-25 | 2013-07-25 19:08 | 2013-07-25 19:28 | ICP - NAC060AKC3 | 124 | 3.7 | Yes | Yes | 17.6 | 16.3 | 1.3 | 346BBE18D2E947159102239A24107CBE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.984% | 0.97016 | 5.734% | [5 empty] | Non-TXV | 2.984%
Tracy | CA | 95376-2559 |  | 2013-06-06 | 2013-06-06 14:43 | 2013-06-06 15:01 | - 585HJ018040 | 61 | 12.9 | Yes | Yes | 19.5 | 20.4 | -0.9 | F53F92AF3C404D2CA4D99DC1BD5918B9 |  | R22 | Non-TXV |  | 21.15% | 0.78852 | 40.64% | [5 empty] | Non-TXV | 21.15%
Los Banos | CA | 93635-7422 |  | 2013-06-03 | 2013-06-03 13:06 | 2013-06-03 13:12 | NORDYNE - JS3BC036KA | 82 | 5.2 | Yes | Yes | 22.8 | 20.4 | 2.4 | 5B71437E09704064B2E27F22071E1374 |  | R22 | Non-TXV |  | 6.341% | 0.93659 | 12.19% | [5 empty] | Non-TXV | 6.341%
Lincoln | CA | 95648-8139 |  | 2013-06-18 | 2013-06-18 10:06 | 2013-06-18 10:42 | YORK - H2RC030S06G | 88 | 2.6 | Yes | Yes | 20 | 19.8 | 0.2 | 094BD91ECFB44FD5B52701772AD8EC92 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Orland | CA | 95963-1500 |  | 2013-09-05 | 2013-09-05 14:03 | 2013-09-05 18:20 | TRANE - 4YCY4060A0A112GAB | 156 | 6.3 | Yes | Yes | 17.8 | 18 | -0.2 | E6C4549C7F364D2D9D61CAA5B36565C8 |  | R410A | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
Tracy | CA | 95376-2559 |  | 2013-06-07 | 2013-06-07 13:03 | 2013-06-07 13:19 | AMERICAN STANDARD - 585HJ024040 | 66 | 9.9 | Yes | Yes | 22 | 19.8 | 2.2 | F96A7D4CB1AB4EFF8C77D2901F8ADBE3 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Yuba City | CA | 95993-8907 |  | 2013-07-22 | 2013-07-22 15:44 | 2013-07-22 16:11 | GIBSON - JS3BC-060-KA | 155 | 5.8 | Yes | Yes | 22.5 | 20.7 | 1.8 | A7266484E54B4003A359B87F09C6128E |  | R22 | TXV |  | 3.742% | 0.96258 | 7.191% | [5 empty] | TXV | 3.742%
Willows | CA | 95988-2062 |  | 2013-06-26 | 2013-06-26 10:40 | 2013-06-26 10:40 | GOODMAN - CK30-1A | 76 | 0 | Yes | Yes | 20.9 | 19.9 | 1 | 8A7377463EB2459C9FC8C0B91BCC8B30 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-8394 |  | 2013-09-04 | 2013-09-04 13:53 | 2013-09-04 14:19 | OTHER - DAYH-F030N070A | 69 | 2.5 | Yes | Yes | 17 | 19.9 | -2.9 | 17DDD103CBEF4F16ABD8A3C1062BD681 |  | R22 | TXV |  | 3.623% | 0.96377 | 6.963% | [5 empty] | TXV | 3.623%
Fresno | CA | 93727-6846 |  | 2013-06-14 | 2013-06-14 13:35 | 2013-06-14 13:37 | LENNOX - 10GCS042-75-3PA | 73 | 3.8 | Yes | Yes | 25.9 | 20.2 | 5.8 | 31AA3808D0EE4D449DBE5FEBDE09D51B |  | R22 | Non-TXV |  | 5.205% | 0.94795 | 10% | [5 empty] | Non-TXV | 5.205%
Atwater | CA | 95301-2211 |  | 2013-06-25 | 2013-06-25 16:26 | 2013-06-25 16:27 | RHEEM - RRMA-A048JK10X | 115 | 5.2 | Yes | Yes | 23.9 | 21.2 | 2.7 | 2D4918A548284189B2AFD5410A70A915 |  | R22 | Non-TXV |  | 4.522% | 0.95478 | 8.69% | [5 empty] | Non-TXV | 4.522%
Dinuba | CA | 93618-3125 |  | 2013-06-21 | 2013-06-21 15:22 | 2013-06-21 15:42 | YORK - 03CG036N04106B | 94 | 3.2 | Yes | Yes | 20.9 | 21.5 | -0.6 | 7B98038A68BE41D7BD563B825DA3DB45 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.404% | 0.96596 | 6.542% | [5 empty] | Non-TXV | 3.404%
Riverbank | CA | 95367-2204 |  | 2013-06-11 | 2013-06-11 11:26 | 2013-06-11 11:53 | RHEEM - RAND-036JAZ | 85 | -8 | Yes | Yes | 22.4 | 18.8 | 3.6 | F537ADB9DFF243CAA07A332ED2C5E676 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95206-4803 |  | 2013-06-17 | 2013-06-17 09:48 | 2013-06-17 10:22 | YORK - H2RD036S06B | 85 | 16 | Yes | Yes | 18.2 | 20.4 | -2.2 | CF7D5408AAEA43ED8439E18904E9F72B |  | R22 | Non-TXV |  | 18.82% | 0.81176 | 36.17% | [5 empty] | Non-TXV | 18.82%
Live Oak | CA | 95953-2279 |  | 2013-09-09 | 2013-09-09 13:27 | 2013-09-09 13:43 | DAY & NIGHT - 561AJ024B | 65 | -4.6 | Yes | Yes | 19.3 | 15.7 | 3.6 | BD08C83F10B146398B608482F93E9E23 |  | R22 | Non-TXV |  | -7.077% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.077%
Tracy | CA | 95377-7917 |  | 2013-06-07 | 2013-06-07 09:04 | 2013-06-07 09:42 | GOODMAN - CLJ48-1A | 85 | 9.2 | Yes | Yes | 19.1 | 19 | 0.1 | 2D3CBA3275704DA6ADE61EE089C6A0E6 |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
Willows | CA | 95988-2446 |  | 2013-06-27 | 2013-06-27 09:04 | 2013-06-27 09:25 | YORK - D1NA048N0906B | 88 | 9.9 | Yes | Yes | 16.8 | 16.2 | 0.6 | F3CCB98B52464BAAB96986B9A839A42A |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Stockton | CA | 95207-7538 |  | 2013-06-14 | 2013-06-14 12:26 | 2013-06-14 12:26 | OTHER - 60WR24A1F | 48 | 0 | Yes | Yes | 22.1 | 23.6 | -1.5 | EE4BAB1AFF564E47A065D95386049BC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-2431 |  | 2013-08-14 | 2013-08-14 08:40 | 2013-08-14 08:40 | AMERICAN STANDARD - 7A2036A100A0 | 118 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | 7DD8774407AA424FBA7A5E3701EEFAB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-5229 |  | 2013-06-14 | 2013-06-14 10:57 | 2013-06-14 11:24 | DAY & NIGHT - 56581018 | 50 | -3.5 | Yes | Yes | 20.8 | 20.8 | 0 | 4AF337ADD981432EB883516E1EF5B654 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Corning | CA | 96021-3703 |  | 2013-06-14 | 2013-06-14 17:48 | 2013-06-14 17:48 | GOODMAN - VSX13C361AA | 89 | 0 | Yes | Yes | 22.2 | 21 | 1.2 | 3766308516C0411FB0F9749DFF954490 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93636-8272 |  | 2013-07-02 | 2013-07-02 12:59 | 2013-07-21 12:57 | GOODMAN - PGJ042075-1B | 78 | 3.2 | Yes | Yes | 17.2 | 19 | -1.8 | 697FFDBEBE93418B9B7B54F08DC892CB |  | R22 | Non-TXV |  | 4.103% | 0.95897 | 7.884% | [5 empty] | Non-TXV | 4.103%
Atascadero | CA | 93422-4105 |  | 2013-08-08 | 2013-08-08 15:22 | 2013-08-08 15:39 | NORDYNE - FS3BA-030KA | 68 | 3.7 | Yes | Yes | 20.1 | 21.3 | -1.2 | AAC8B2FF64CF43F1A2F5768C873974DD |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Stockton | CA | 95215-6808 |  | 2013-08-13 | 2013-08-13 14:42 | 2013-08-13 15:04 | GIBSON - JS5BD-024KA | 94 | 5.8 | Yes | Yes | 22.7 | 18.9 | 3.8 | 7558A06C293546EAAA500BE1D11DD2E2 |  | R22 | TXV |  | 6.17% | 0.9383 | 11.86% | [5 empty] | TXV | 6.17%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 09:59 | 2013-07-30 10:21 | PAYNE - PA13NAD042000ACAA | 100 | 3.6 | Yes | Yes | 21 | 18.8 | 2.2 | C83740D3C2024B3296A25547CC062AD7 |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Pine Grove | CA | 95665-9619 |  | 2013-08-13 | 2013-08-13 15:26 | 2013-08-13 15:26 | CARRIER - 38TH042310 | 112 | 0 | Yes | Yes | 27 | 24.8 | 2.2 | 2111C98368414BE1AB05AB44C2C939F0 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-4947 |  | 2013-06-20 | 2013-06-20 13:35 | 2013-06-20 13:57 | RHEEM - UNK | 64 | -4.5 | Yes | Yes | 22.2 | 19.3 | 2.9 | B4A0295DA9DB443BA1BAA9AB6A3EA4ED |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Willows | CA | 95988-2949 |  | 2013-08-15 | 2013-08-15 09:16 | 2013-08-15 10:48 | PAYNE - NA | 89 | 3.3 | Yes | Yes | 19.2 | 21.5 | -2.3 | 1F0CF89345974087B440284169258C52 |  | R22 | Non-TXV |  | 3.708% | 0.96292 | 7.126% | [5 empty] | Non-TXV | 3.708%
Stockton | CA | 95212-3066 |  | 2013-06-25 | 2013-06-25 16:11 | 2013-06-25 16:42 | CARRIER - UNK | 65 | 4 | Yes | Yes | 14.4 | 17 | -2.6 | C71DD1D7185B418589AC27CA2F9B7A85 |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Orland | CA | 95963-1133 |  | 2013-06-17 | 2013-06-17 09:45 | 2013-06-17 10:38 | LENNOX - HS14-411V-5P | 164 | 6.1 | Yes | Yes | 16.7 | 19.1 | -2.4 | F2F31377C8B4469EBD9F815716871460 |  | R22 | Non-TXV |  | 3.72% | 0.9628 | 7.148% | [5 empty] | Non-TXV | 3.72%
Magalia | CA | 95954-9435 |  | 2013-07-19 | 2013-07-19 15:11 | 2013-07-19 18:10 | AMERICAN STANDARD - WCC030F100BG | 120 | 4.3 | Yes | Yes | 19 | 21.8 | -2.8 | 7001B868A8434713BDD430CE748C66F4 |  | R22 | Non-TXV |  | 3.583% | 0.96417 | 6.886% | [5 empty] | Non-TXV | 3.583%
Stockton | CA | 95212-3218 |  | 2013-06-17 | 2013-06-17 13:47 | 2013-06-17 14:05 | CARRIER - 38BRC030310 | 99 | 19 | Yes | Yes | 24 | 21.5 | 2.5 | C35445BA6B6941CD97BBBE986E762B7A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.19% | 0.80808 | 36.88% | [5 empty] | Non-TXV | 19.19%
Stockton | CA | 95212-2120 |  | 2013-06-12 | 2013-06-12 09:16 | 2013-06-12 09:37 | BDP - 588ANW024040ACAD | 38 | 6.1 | Yes | Yes | 21.3 | 19.5 | 1.8 | 08BA293EF4D44DABBDC01535742E30AA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.05% | 0.83947 | 30.85% | [5 empty] | Non-TXV | 16.05%
Atwater | CA | 95301-2715 |  | 2013-06-07 | 2013-06-07 11:54 | 2013-06-07 12:00 | ECONAIR - 38BRC036330 | 101 | 5.7 | Yes | Yes | 24.1 | 19.6 | 4.5 | BAE2B136338940048AEDA6344E4F5B68 |  | R22 | Non-TXV |  | 5.644% | 0.94356 | 10.85% | [5 empty] | Non-TXV | 5.644%
Chico | CA | 95926-2921 |  | 2013-06-11 | 2013-06-11 08:48 | 2013-06-11 09:06 | RHEEM - RAFD-025 JAS | 51 | 3.4 | Yes | Yes | 19.8 | 17.9 | 1.9 | 9132CF71C5144AF895D001344BDAEAF5 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 16:08 | 2013-07-30 16:34 | AMERICAN STANDARD - 2A7A3030A1000AA | 88 | 3.3 | Yes | Yes | 22 | 19.9 | 2.1 | 85BF0379D6A64E73981C3290445F87D4 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Paradise | CA | 95969-3707 |  | 2013-06-28 | 2013-06-28 19:40 | 2013-06-28 19:56 | CARRIER - NA | 89 | 5.2 | Yes | Yes | 16.3 | 14.9 | 1.5 | 3F611020444D4302BC065A7040843B65 |  | R22 | Non-TXV |  | 5.843% | 0.94157 | 11.23% | [5 empty] | Non-TXV | 5.843%
Stockton | CA | 95210-1514 |  | 2013-06-11 | 2013-06-11 09:14 | 2013-06-11 09:36 | YORK - D1NA030N05606C | 76 | 2.4 | Yes | Yes | 17.6 | 18.5 | -0.9 | E1CD04F38DAA49509D5EEB1FCEF4AD21 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Chico | CA | 95926-8040 |  | 2013-09-25 | 2013-09-25 17:26 | 2013-09-25 17:47 | RHEEM - RAFD-024 | 60 | 6.8 | Yes | Yes | 20 | 19.9 | 0.1 | BF2F23E4963942AF80CB44666312A9F6 |  | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Chico | CA | 95973-5336 |  | 2013-06-06 | 2013-06-06 18:06 | 2013-06-06 18:23 | BDP - 561CJ042-A | 81 | 9 | Yes | Yes | 21.9 | 21.1 | 0.8 | F90D909B9433413695D5ED11471CF821 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Gridley | CA | 95948-9608 |  | 2013-08-17 | 2013-08-17 17:21 | 2013-08-17 17:21 | TRANE - 4TTX042B1000AA | 103 | 0 | Yes | Yes | 22.7 | 20.7 | 2 | 63E2322FD41E42A3BF3403F4E0EDD584 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95965-4724 |  | 2013-07-25 | 2013-07-25 14:35 | 2013-07-25 19:55 | DAY & NIGHT - PGD34209001C1 | 90 | 3.3 | Yes | Yes | 27 | 22.8 | 4.2 | 3D76C8F7EAC14B5988C3DE6520C92508 |  | R410A | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Fresno | CA | 93726-2446 |  | 2013-08-21 | 2013-08-21 12:04 | 2013-08-21 12:24 | TEMPSTAR - PGAD42D1K3 | 179 | 6.6 | Yes | Yes | 21.8 | 17.5 | 4.3 | 5FAB9F4FB1674FABB263263B7230BA8C |  | R22 | Non-TXV |  | 3.687% | 0.96313 | 7.086% | [5 empty] | Non-TXV | 3.687%
Oroville | CA | 95966-9459 |  | 2013-06-20 | 2013-06-20 08:51 | 2013-06-20 10:09 | OTHER - 80 VE 2A | 66 | 6.3 | Yes | Yes | 20.5 | 18.5 | 2 | AE372483F38C41E185D239322BA7CB1C |  | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Clovis | CA | 93611-7306 |  | 2013-08-22 | 2013-08-22 12:05 | 2013-08-22 12:05 | CARRIER - 48NLT0480300 | 149 | 0 | Yes | Yes | 24.5 | 21.2 | 3.3 | 358180B877A043D4929AF11B6F77EA6D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-8284 |  | 2013-08-07 | 2013-08-07 15:11 | 2013-08-07 15:29 | LENNOX - 13AD-030-230-02 | 85 | 6.5 | Yes | Yes | 17.1 | 18.7 | -1.6 | ECD9254156A549C4BBCD05DB12FB6F6E |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Chico | CA | 95973-0550 |  | 2013-06-07 | 2013-06-07 09:15 | 2013-06-07 10:42 | UNK - UNK | 85 | 14.6 | Yes | Yes | 20.5 | 20.7 | -0.2 | 9CC754DABB0E42E7AD8A0A0CB8AD0FA4 |  |  |  |  | 17.18% | 0.82824 | 33.01% | [5 empty] | 0 | 17.18%
Stockton | CA | 95207-2302 |  | 2013-06-07 | 2013-06-07 13:05 | 2013-06-07 13:29 | PAYNE - PY3GNAA24060NA | 73 | 3.2 | Yes | Yes | 18.2 | 15.9 | 2.3 | B952275080E442CBB2C1BD6F1AD12661 |  | R410A | TXV |  | 4.384% | 0.95616 | 8.424% | [5 empty] | TXV | 4.384%
Chico | CA | 95973-7204 |  | 2013-07-11 | 2013-07-11 09:14 | 2013-07-11 10:02 | PAYNE - PA18N00X6835536-C | 70 | 4.2 | Yes | Yes | 19.2 | 18.5 | 0.7 | 86C82995D446420FA092BF3C311AF180 |  | R410A | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Chico | CA | 95928-4131 |  | 2013-07-09 | 2013-07-09 09:38 | 2013-07-09 18:45 | DAY & NIGHT - 58ANW024040ACBD | 38 | 15.8 | Yes | Yes | 17.1 | 19.4 | -2.3 | 549AF09869AA427CA67454CC0473C1EA |  | R22 | Non-TXV |  | 41.58% | 0.58421 | 79.91% | [5 empty] | Non-TXV | 41.58%
Red Bluff | CA | 96080-3953 |  | 2013-06-15 | 2013-06-15 18:49 | 2013-06-15 19:10 | OTHER - TCA036AKA1 | 80 | 3.7 | Yes | Yes | 27.8 | 22.5 | 5.3 | CC141546CEDA4A3AAFC8B50CE0496960 |  | R22 | Non-TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | Non-TXV | 4.625%
Stockton | CA | 95212-3034 |  | 2013-06-18 | 2013-06-18 11:21 | 2013-06-18 11:43 | UNITARY PRODUCTS GROUP - H2RO36S06G | 85 | 2.5 | Yes | Yes | 19.5 | 18.8 | 0.7 | E2FDA9A362F641898ED8FD6AC9C10FC5 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Paradise | CA | 95969-2420 |  | 2013-08-05 | 2013-08-05 09:42 | 2013-08-05 10:17 | CARRIER - 38BRG048310 | 136 | 8.6 | Yes | Yes | 22 | 21.5 | 0.5 | C0C879F91D5F41129FF277361DE72A0A |  | R22 | Non-TXV |  | 6.324% | 0.93676 | 12.15% | [5 empty] | Non-TXV | 6.324%
Stockton | CA | 95207-2145 |  | 2013-06-14 | 2013-06-14 14:49 | 2013-06-14 14:52 | RHEEM - RAKA-037JAS | 79 | 19.9 | Yes | Yes | 22.5 | 18.4 | 4.2 | B40828F5F27743E1B3D55FC363E8F5DB |  | R22 | Non-TXV |  | 25.19% | 0.7481 | 48.41% | [5 empty] | Non-TXV | 25.19%
Fresno | CA | 93726-2443 |  | 2013-06-03 | 2013-06-03 11:14 | 2013-06-03 11:35 | CARRIER - 48GX-036060301AD | 82 | 2.5 | Yes | Yes | 15 | 17.2 | -2.2 | D85987AD58CF4E7BB547B5135E27B96C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Paradise | CA | 95969-3030 |  | 2013-06-12 | 2013-06-12 19:32 | 2013-06-12 19:53 | CARRIER - 48NMX036300 | 70 | 8.8 | Yes | Yes | 22.4 | 20.7 | 1.7 | 367ADC04DD95486CAB1C275746FC8BFE |  | R22 | Non-TXV |  | 12.57% | 0.87429 | 24.16% | [5 empty] | Non-TXV | 12.57%
Stockton | CA | 95203-1018 |  | 2013-06-07 | 2013-06-07 14:24 | 2013-06-07 14:52 | GMC - VSC130181BA | 67 | 2 | Yes | Yes | 17 | 17.4 | -0.4 | 459F4E288E7F4D62A0BE27C1D4F07EE0 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Willows | CA | 95988-2722 |  | 2013-08-14 | 2013-08-14 12:15 | 2013-08-14 12:50 | GOODMAN - CLO30-1B | 131 | 4 | Yes | Yes | 15.7 | 17.5 | -1.8 | 6789B669CA8B4A3C843078AA10BC87D0 |  | R22 | Non-TXV |  | 3.053% | 0.96947 | 5.868% | [5 empty] | Non-TXV | 3.053%
Atwater | CA | 95301-2251 |  | 2013-06-05 | 2013-06-05 12:02 | 2013-06-05 12:06 | TRANE - TTD742B100AO | 97 | 8.7 | Yes | Yes | 20.3 | 20.4 | -0.1 | A87334E534494D419E6C351974F20EB8 |  | R22 | Non-TXV |  | 8.969% | 0.91031 | 17.24% | [5 empty] | Non-TXV | 8.969%
Chico | CA | 95973-9144 |  | 2013-06-07 | 2013-06-07 11:33 | 2013-06-07 11:50 | TEMPSTAR - T2A324GKB200 | 82 | 2.5 | Yes | Yes | 23.1 | 20.6 | 2.5 | A0F5A5A7C156424FAF934F70DA6CF9D5 |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Los Banos | CA | 93635-6393 |  | 2013-07-29 | 2013-07-29 11:37 | 2013-07-29 11:43 | BRYANT - 563CN048-H | 140 | 4.6 | Yes | Yes | 21 | 18.7 | 2.3 | 7DDD3976C1A2433CA0B995348970A3D1 |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Stockton | CA | 95206-6130 |  | 2013-07-30 | 2013-07-30 10:12 | 2013-07-30 10:36 | YORK - H1RA042506A | 84 | 3 | Yes | Yes | 16.9 | 18.8 | -1.9 | 843A7F78E9E24EF59617F3F6152CBFA3 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Los Banos | CA | 93635-8563 |  | 2013-06-04 | 2013-06-04 11:57 | 2013-06-04 12:04 | AMERICAN STANDARD - 2A7B00601000AA | 126 | 10.5 | Yes | Yes | 21.9 | 20.9 | 1 | C6D8C3E12D884324BDC448B7A15088D7 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Los Banos | CA | 93635-9234 |  | 2013-06-04 | 2013-06-04 15:52 | 2013-06-04 16:01 | NORDYNE - JS5BD036K | 138 | 7.5 | Yes | Yes | 20.1 | 18.6 | 1.6 | CF72A1F394FC46EA929015872F9CE677 |  | R22 | Non-TXV |  | 5.435% | 0.94565 | 10.44% | [5 empty] | Non-TXV | 5.435%
Stockton | CA | 95206-2607 |  | 2013-06-26 | 2013-06-26 14:34 | 2013-06-26 15:04 | GOODMAN - GSC130361GA | 85 | 7.9 | Yes | Yes | 19.6 | 20.5 | -0.9 | F7998E209E804C07BC20783614B26407 |  | R22 | Non-TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | Non-TXV | 9.294%
Fresno | CA | 93726-3418 |  | 2013-06-05 | 2013-06-05 10:23 | 2013-06-05 12:24 | AMERICAN STANDARD - YCY042G1M0AC | 147 | 4.7 | Yes | Yes | 18.1 | 20.6 | -2.5 | FF940CED310D421388CD38F4B66C8FA4 |  | R22 | Non-TXV |  | 3.197% | 0.96803 | 6.144% | [5 empty] | Non-TXV | 3.197%
Willows | CA | 95988-3247 |  | 2013-06-27 | 2013-06-27 09:36 | 2013-06-27 10:20 | OTHER - 38CK03030340 | 69 | 2.2 | Yes | Yes | 21.7 | 20.4 | 1.3 | 94D0CDA7CD164ECB86A4EA88EAEE5554 |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Paso Robles | CA | 93446-3260 |  | 2013-08-05 | 2013-08-05 12:16 | 2013-08-05 12:43 | RHEEM - RAHE036JAS | 93 | 10.9 | Yes | Yes | 19.3 | 13.6 | 5.7 | ED696078FA66466A80DE72F988B74C35 |  | R22 | Non-TXV |  | 11.72% | 0.8828 | 22.52% | [5 empty] | Non-TXV | 11.72%
Stockton | CA | 95215-4002 |  | 2013-06-20 | 2013-06-20 10:03 | 2013-06-20 10:28 | CARRIER - 591ANX048000ACAA | 128 | 3.8 | Yes | Yes | 19.7 | 19.8 | -0.1 | F117A39B1415472B84F9430AE3CBA570 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Stockton | CA | 95206-6400 |  | 2013-08-28 | 2013-08-28 09:58 | 2013-08-28 10:20 | GOODMAN - CLJ36-1A | 109 | 3.3 | Yes | Yes | 20 | 19.3 | 0.7 | C68BC04FB3514F46BCA59FCED5CCFECD |  | R22 | Non-TXV |  | 3.028% | 0.96972 | 5.818% | [5 empty] | Non-TXV | 3.028%
Copperopolis | CA | 95228-9562 |  | 2013-08-13 | 2013-08-13 09:58 | 2013-08-13 10:23 | RHEEM - RRNA-BO48JK100X | 85 | 7.6 | Yes | Yes | 21.4 | 19.9 | 1.5 | 433FCA787CF84A74AF62C851DE1E801A |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Stockton | CA | 95212-3805 |  | 2013-08-07 | 2013-08-07 14:20 | 2013-08-07 14:20 | YORK - H2RC036S06A | 83 | 0 | Yes | Yes | 17.4 | 19.3 | -1.9 | D2E66F8A583B49F09919F18A1846951E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-4092 |  | 2013-07-10 | 2013-07-10 08:47 | 2013-07-10 09:55 | RHEEM - RRNA-B036JK06X | 83 | 3.8 | Yes | Yes | 18.4 | 21 | -2.6 | 3CE33910EF6A4393B7904B7CF97327BA |  | R22 | Non-TXV |  | 4.578% | 0.95422 | 8.799% | [5 empty] | Non-TXV | 4.578%
Yuba City | CA | 95993-7676 |  | 2013-06-20 | 2013-06-20 10:14 | 2013-06-20 10:59 | TRANE - TTP048C100A2 | 156 | 5 | Yes | Yes | 21 | 20.8 | 0.2 | 3A29129B47D14A3784B5BE6C35E19C6E |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Orland | CA | 95963-9551 |  | 2013-09-05 | 2013-09-05 11:22 | 2013-09-05 18:47 | BRYANT - 661CJX030-A | 86 | 9.5 | Yes | Yes | 13.6 | 16.5 | -2.9 | 0B080A8EA0DB4AE68AD70762B01C0BB0 |  | R22 | Non-TXV |  | 11.05% | 0.88953 | 21.23% | [5 empty] | Non-TXV | 11.05%
Orland | CA | 95963-9551 |  | 2013-09-05 | 2013-09-05 11:25 | 2013-09-05 11:46 | YORK - NA | 71 | 2.5 | Yes | Yes | 15.6 | 17 | -1.4 | 6516F6C0997B4D4F8F8A61A68F3561F3 |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Stockton | CA | 95206-6098 |  | 2013-07-05 | 2013-07-05 10:15 | 2013-07-05 10:42 | GOODMAN - CLJ36-1A | 85 | -5 | Yes | Yes | 21 | 18.6 | 2.5 | 504F20BF77384FF288A06C8FA386C6A0 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Corning | CA | 96021-9201 |  | 2013-07-22 | 2013-07-22 18:39 | 2013-07-22 18:58 | YORK - D1NH036N07206C | 98 | 9.5 | Yes | Yes | 20.6 | 20.6 | 0 | F7E3A2AEEDB84222B5A077A805852F0C |  | R22 | Non-TXV |  | 9.694% | 0.90306 | 18.63% | [5 empty] | Non-TXV | 9.694%
Stockton | CA | 95206-2802 |  | 2013-06-12 | 2013-06-12 12:45 | 2013-06-12 13:17 | CARRIER - 38CKC042350 | 93 | 3.8 | Yes | Yes | 23.4 | 20.4 | 3 | 1673C8AC62D14C7BB6C7FA4B3841C19E |  | R22 | Non-TXV |  | 4.086% | 0.95914 | 7.852% | [5 empty] | Non-TXV | 4.086%
Paso Robles | CA | 93446-3209 |  | 2013-08-14 | 2013-08-14 11:51 | 2013-08-14 18:11 | RHEEM - RRPLB036JK06X | 92 | 3.6 | Yes | Yes | 18.4 | 21 | -2.6 | 037CA198617543248F960A5983A1CC37 |  | R410A | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Fresno | CA | 93726-3634 |  | 2013-06-04 | 2013-06-04 11:57 | 2013-06-04 11:57 | RHEEM - RRNL-B030JK06 | 76 | 0 | Yes | Yes | 17.6 | 20.4 | -2.8 | 56983A4CA2254B328E6BF5BEB39826D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-4092 |  | 2013-07-26 | 2013-07-26 09:34 | 2013-07-26 09:55 | RHEEM - RRNA-B036JK06X | 83 | 3.1 | Yes | Yes | 15.9 | 18.7 | -2.8 | 5A27155D2FAE40F8A3773C9136948A51 |  | R22 | Non-TXV |  | 3.735% | 0.96265 | 7.178% | [5 empty] | Non-TXV | 3.735%
Fresno | CA | 93722-2762 |  | 2013-06-20 | 2013-06-20 11:57 | 2013-06-20 12:19 | CARRIER - 428SS-042060331 | 83 | 2.8 | Yes | Yes | 21.1 | 19.5 | 1.6 | CEF920A9694F4DEA9F1DB1F0B84A95C3 |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Willows | CA | 95988-2024 |  | 2013-08-14 | 2013-08-14 09:24 | 2013-08-14 10:18 | YORK - H1RC030S06D | 76 | 3.5 | Yes | Yes | 16.6 | 19.3 | -2.7 | F9244E879BFC49DD9C95998C6EF3BD9F |  | R22 | Non-TXV |  | 4.605% | 0.95395 | 8.85% | [5 empty] | Non-TXV | 4.605%
Yuba City | CA | 95993-6427 |  | 2013-06-19 | 2013-06-19 10:54 | 2013-06-19 11:14 | TRANE - YCY024F1MOAA | 102 | 3.1 | Yes | Yes | 19 | 19.3 | -0.3 | 0648C5107CF949329353E48DB241017A |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Paso Robles | CA | 93446-3243 |  | 2013-08-08 | 2013-08-08 16:47 | 2013-08-08 17:14 | TRANE - 2TTB3048A1000AA | 140 | 4.8 | Yes | Yes | 23.7 | 19.3 | 4.4 | 21BE3652C736437DB7686EC4B87DD14A |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Fresno | CA | 93726-2523 |  | 2013-06-03 | 2013-06-03 10:27 | 2013-06-03 10:48 | CARRIER - 48DL045-6 | 70 | 11.8 | Yes | Yes | 17.5 | 20.4 | -2.9 | 138F5C1EE8A0418F9C7A7AF213E3242A |  | R22 | Non-TXV |  | 16.86% | 0.83143 | 32.4% | [5 empty] | Non-TXV | 16.86%
Rescue | CA | 95672-9350 |  | 2013-09-04 | 2013-09-04 11:03 | 2013-09-04 11:03 | RUUD - URGG-07N36JKR | 75 | 0 | Yes | Yes | 24.5 | 20.1 | 4.4 | D8C1FA5C3FD2446B88D0CA0DE441EDDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3506 |  | 2013-06-07 | 2013-06-07 13:23 | 2013-06-07 13:23 | WHIRLPOOL - DXB-29B | 43 | 0 | Yes | Yes | 17.5 | 19.3 | -1.8 | 2A796125DFB24F4D98665D66CD2723C3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3503 |  | 2013-06-24 | 2013-06-24 12:58 | 2013-06-24 13:02 | GOODMAN - PGJ036075 | 81 | 6.3 | Yes | Yes | 16.2 | 15.7 | 0.5 | CCEF7491525A40CB8A4B3A6E43C9EF51 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Merced | CA | 95341-5336 |  | 2013-06-12 | 2013-06-12 14:57 | 2013-06-12 14:58 | GOODMAN - GPG13600901AA | 145 | 15.3 | Yes | Yes | 26.2 | 21.4 | 4.8 | 31D09B281CF747C9B7B73340716EC286 |  | R22 | Non-TXV |  | 10.55% | 0.89448 | 20.28% | [5 empty] | Non-TXV | 10.55%
Fresno | CA | 93705-2841 |  | 2013-06-18 | 2013-06-18 12:32 | 2013-06-18 12:37 | WESTINGHOUSE - UNK | 88 | 9.4 | Yes | Yes | 16.3 | 16.8 | -0.5 | 7D4AD1855C164208BD70A2C262D81E34 |  | R22 | Non-TXV |  | 10.68% | 0.89318 | 20.53% | [5 empty] | Non-TXV | 10.68%
Stockton | CA | 95209-1204 |  | 2013-07-03 | 2013-07-03 08:54 | 2013-07-03 09:13 | PAYNE - 565A042RCUL | 114 | 9.8 | Yes | Yes | 19.9 | 19.6 | 0.3 | 7834B23F0FF14E97BA9F8A27081529A8 |  | R22 | Non-TXV |  | 8.596% | 0.91404 | 16.52% | [5 empty] | Non-TXV | 8.596%
Willows | CA | 95988-2105 |  | 2013-06-26 | 2013-06-26 09:26 | 2013-06-26 09:56 | BRYANT - 597CN036-G | 100 | 7.6 | Yes | Yes | 20.9 | 19.9 | 1 | 34E7512A652243FA885CB2876D9FC7AD |  | R22 | Non-TXV |  | 7.6% | 0.924 | 14.61% | [5 empty] | Non-TXV | 7.6%
Gustine | CA | 95322-1232 |  | 2013-09-05 | 2013-09-05 10:18 | 2013-09-05 10:20 | TEMPSTAR - PGAD24B1K8 | 70 | 4.4 | Yes | Yes | 16.4 | 18.8 | -2.4 | 7FF5E6A2FAF245A29D296F4D6926E615 |  | R22 | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Stockton | CA | 95210-4430 |  | 2013-07-09 | 2013-07-09 13:25 | 2013-07-09 13:47 | PAYNE - 591ANX060000AAAA | 168 | 5.9 | Yes | Yes | 18.9 | 20.7 | -1.8 | 42B6727B17494428BCB07D09AC366B62 |  | R22 | Non-TXV |  | 3.512% | 0.96488 | 6.749% | [5 empty] | Non-TXV | 3.512%
Fresno | CA | 93726-2640 |  | 2013-06-03 | 2013-06-03 14:25 | 2013-06-03 14:38 | ICP - PGAD36D1K4 | 102 | 4.1 | Yes | Yes | 21.8 | 20.4 | 1.4 | E0317667635E49FAAF82FB4F1083EE6D |  | R22 | Non-TXV |  | 4.02% | 0.9598 | 7.725% | [5 empty] | Non-TXV | 4.02%
Lincoln | CA | 95648-3237 |  | 2013-06-14 | 2013-06-14 08:55 | 2013-06-14 09:20 | LENNOX - UNK MISSING | 108 | 7.5 | Yes | Yes | 17.3 | 20.1 | -2.8 | 145F8083444E41E1916C48495CF0A32E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Arbuckle | CA | 95912-0000 |  | 2013-07-31 | 2013-07-31 10:19 | 2013-07-31 10:43 | OTHER - UNK | 85 | 2.5 | Yes | Yes | 22 | 19.9 | 2.1 | 55E9D46AF1A540E6B4CDA7F873C3EB62 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Templeton | CA | 93465-0000 |  | 2013-09-05 | 2013-09-05 15:21 | 2013-09-05 15:38 | CARRIER - 38EN036320 | 93 | 3.7 | Yes | Yes | 21.4 | 19.8 | 1.6 | 5F88099648154E938A84B47905B16359 |  | R22 | Non-TXV |  | 3.978% | 0.96022 | 7.646% | [5 empty] | Non-TXV | 3.978%
Fresno | CA | 93704-5301 |  | 2013-06-19 | 2013-06-19 15:04 | 2013-06-19 15:06 | BRYANT - 574BNW060090NB | 210 | 6.3 | Yes | Yes | 28.4 | 22.6 | 5.8 | 6840D94A20144258BCDA4CDCE7AED5EF |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Newman | CA | 95360-1748 |  | 2013-06-04 | 2013-06-04 14:08 | 2013-06-04 14:27 | UNITARY PRODUCTS GROUP - H2RC042S06A | 107 | 3.3 | Yes | Yes | 19.9 | 21.4 | -1.5 | A0E4AFBA97634789BA8F527A4306626C |  | R22 | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Stockton | CA | 95207-7628 |  | 2013-06-14 | 2013-06-14 15:46 | 2013-06-14 16:03 | PAYNE - SF018OAA | 28 | 3.9 | Yes | Yes | 24.2 | 19.8 | 4.4 | 9FB65FCD8AD34AAFA676F04160355D25 |  | R22 | Non-TXV |  | 13.93% | 0.86071 | 26.77% | [5 empty] | Non-TXV | 13.93%
Fresno | CA | 93727-6928 |  | 2013-07-18 | 2013-07-18 11:20 | 2013-07-18 12:55 | - | 85 | 9.7 | Yes | Yes | 18.8 | 19.5 | -0.7 | CDD4A498931345FA94B03C6BD8CA6506 |  | R22 | Non-TXV |  | 11.41% | 0.88588 | 21.93% | [5 empty] | Non-TXV | 11.41%
Madera | CA | 93637-6224 |  | 2013-06-18 | 2013-06-18 13:48 | 2013-06-18 14:17 | CARRIER - 3505E28281 | 100 | 3.2 | Yes | Yes | 19.1 | 20 | -0.8 | 0F58B3A7D971468AADDCF8BDA45EFD63 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Paso Robles | CA | 93446-5434 |  | 2013-10-07 | 2013-10-07 12:33 | 2013-10-07 12:53 | CARRIER - 38EZG030300 | 88 | 2.6 | Yes | Yes | 16.7 | 18.5 | -1.8 | F9254C58DDD945B3ADEBE495DDA15287 |  | R410A | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Fresno | CA | 93725-1639 |  | 2013-06-20 | 2013-06-20 11:00 | 2013-06-20 11:04 | BDP - 585CJ042100 | 104 | 5.3 | Yes | Yes | 25.8 | 20.3 | 5.5 | 2EE3FE57E2924C1ABA21A69509ACD640 |  | R22 | Non-TXV |  | 5.096% | 0.94904 | 9.794% | [5 empty] | Non-TXV | 5.096%
Fresno | CA | 93725-1849 |  | 2013-06-20 | 2013-06-20 13:03 | 2013-06-20 13:06 | COLEMAN - BRCS0481BD | 117 | 4.5 | Yes | Yes | 22.2 | 20.7 | 1.5 | 27DDA1F669C1425399102A0DE66C76C7 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Stockton | CA | 95210-3262 |  | 2013-06-14 | 2013-06-14 12:22 | 2013-06-14 12:43 | PAYNE - PA10JA024-C | 64 | 10.6 | Yes | Yes | 28.5 | 22.6 | 5.9 | D05E1F1EDBA34C31B6DBFFB23016151A |  | R22 | Non-TXV |  | 16.56% | 0.83437 | 31.83% | [5 empty] | Non-TXV | 16.56%
Chico | CA | 95926-7752 |  | 2013-07-01 | 2013-07-01 13:57 | 2013-07-01 18:16 | BDP - 585CJ036075 | 84 | 2.7 | Yes | Yes | 20.2 | 22.1 | -1.9 | BF9035489EB34C3EAC04914738574D37 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Fresno | CA | 93726-1538 |  | 2013-05-30 | 2013-05-30 17:01 | 2013-05-30 17:27 | AMERICAN STANDARD - YCC03601MOBJ | 87 | 2.9 | Yes | Yes | 20.2 | 18.5 | 1.7 | 06480AEA8C1642B69E9E40A4A9EBBC50 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Placerville | CA | 95667-6727 |  | 2013-08-16 | 2013-08-16 14:33 | 2013-08-16 14:33 | TRANE - 2TTR2042B1000AA | 86 | 0 | Yes | Yes | 23.3 | 21.9 | 1.4 | BB2A957353C143A3AFE62FB8942FE992 |  | R22 | TXV |  | 0% | 1 | 0%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 11:21 | 2013-07-30 11:21 | AMERICAN STANDARD - 4YCC3042A11096AA | 109 | 0 | Yes | Yes | 20 | 18.5 | 1.5 | 0C95B14C4EB740ADB1793C93DF284BC8 |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5200 |  | 2013-07-03 | 2013-07-03 14:18 | 2013-07-03 14:37 | TRANE - 2TTR2036A1000AA | 96 | 14.8 | Yes | Yes | 19.4 | 20.4 | -1 | C977DE9F46A140248F22B70B0AE846F5 |  | R22 | Non-TXV |  | 15.42% | 0.84583 | 29.63% | [5 empty] | Non-TXV | 15.42%
Stockton | CA | 95206-4694 |  | 2013-06-17 | 2013-06-17 11:27 | 2013-06-17 11:27 | GOODMAN - CKJ60-1C | 85 | 0 | Yes | Yes | 25.9 | 20.9 | 5 | FB8BAA846F144157B935BE5FB717A719 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1851 |  | 2013-06-20 | 2013-06-20 13:24 | 2013-06-20 13:26 | GOODMAN - CKL30-1 | 76 | 3.3 | Yes | Yes | 26.5 | 21.5 | 5 | BAAEB2A4EC5C42FFBBBAC2E83A953270 |  | R22 | Non-TXV |  | 4.342% | 0.95658 | 8.345% | [5 empty] | Non-TXV | 4.342%
Williams | CA | 95987-0000 |  | 2013-09-12 | 2013-09-12 09:41 | 2013-09-12 09:58 | AMERICAN STANDARD - 2A7A40048B100AA | 150 | 5.8 | Yes | Yes | 23 | 18.2 | 4.8 | 91B54E1E96BA4A34800B728B3FFBE174 |  | R22 | TXV |  | 3.867% | 0.96133 | 7.431% | [5 empty] | TXV | 3.867%
Fresno | CA | 93726-1514 |  | 2013-05-31 | 2013-05-31 11:39 | 2013-05-31 12:41 | GE - 2TC036F1B | 112 | 9 | Yes | Yes | 22.2 | 18 | 4.2 | 624DE92950894652AD26523BD6EF1E36 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.036% | 0.91964 | 15.44% | [5 empty] | Non-TXV | 8.036%
Clovis | CA | 93619-5069 |  | 2013-06-25 | 2013-06-25 13:45 | 2013-06-25 14:09 | BRYANT - 114ANA042-A | 164 | 6.8 | Yes | Yes | 21.3 | 19.9 | 1.4 | 95D0F872B28E44FC9F0DBF41B5FC164D |  | R410A | TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | TXV | 4.146%
Merced | CA | 95340-8590 |  | 2013-06-17 | 2013-06-17 12:38 | 2013-06-17 12:54 | AMERICAN STANDARD - WCC036F100BF | 131 | 11.8 | Yes | Yes | 19.1 | 17.5 | 1.6 | E4C4B53CC65A41978A0689A300A54DD1 |  | R22 | Non-TXV |  | 9.008% | 0.90992 | 17.31% | [5 empty] | Non-TXV | 9.008%
Fresno | CA | 93725-1740 |  | 2013-06-20 | 2013-06-20 11:22 | 2013-06-20 11:25 | HEIL - PGAA30C1K4 | 79 | 3.7 | Yes | Yes | 21 | 20.2 | 0.9 | 99EBB578DCAC4152A70333AF8104BE2F |  | R22 | Non-TXV |  | 4.684% | 0.95316 | 9.001% | [5 empty] | Non-TXV | 4.684%
Stockton | CA | 95205-4656 |  | 2013-06-06 | 2013-06-06 11:03 | 2013-06-06 11:03 | GOODMAN - PGB048125-1A | 86 | 0 | Yes | Yes | 22.9 | 18.8 | 4.1 | 6D8FBFE275234C4DB54DD57885DC7904 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-2959 |  | 2013-06-06 | 2013-06-06 09:01 | 2013-06-06 09:01 | YORK - D3NZ024N05606NXC | 58 | 0 | Yes | Yes | 17 | 19.1 | -2 | 1A18080FA68E440790BEFA7CDC8A60DE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-7699 |  | 2013-10-11 | 2013-10-11 15:11 | 2013-10-11 15:38 | LENNOX - 13ACD-030-230-02 | 85 | 8 | Yes | Yes | 19.9 | 21 | -1.1 | 8495CB3B6BE84A2AA364956443545BBB |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 10:45 | 2013-07-30 11:06 | OTHER - SCU13H48A-1 | 217 | 7 | Yes | Yes | 22 | 16.6 | 5.4 | B4D010140C294E61829D3295293F0329 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Fresno | CA | 93726-3419 |  | 2013-06-01 | 2013-06-01 12:34 | 2013-06-01 12:53 | AMERICAN STANDARD - YCC036F1M0BF | 90 | 4.1 | Yes | Yes | 23 | 21.3 | 1.7 | EB422312A5814BB29719DEBBC3BC3E86 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.556% | 0.95444 | 8.755% | [5 empty] | Non-TXV | 4.556%
Stockton | CA | 95206-2614 |  | 2013-08-22 | 2013-08-22 10:00 | 2013-08-22 10:18 | BDP - 588ANW018040ABAD | 38 | 2.5 | Yes | Yes | 19.9 | 19.2 | 0.7 | E85240EF37484163976867C5A5A4A58A |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Cameron Park | CA | 95682-8227 |  | 2013-06-13 | 2013-06-13 12:02 | 2013-06-13 12:02 | CARRIER - 38TDB048300 | 184 | 0 | Yes | Yes | 19.2 | 21.3 | -2.1 | B5ECE7B4532948F9A8A4008D55334396 |  | R410A | TXV |  | 0% | 1 | 0%
San Joaquin | CA | 93660-0000 |  | 2013-08-28 | 2013-08-28 10:55 | 2013-08-28 10:56 | GOODMAN - GCS130421AD | 143 | 5.2 | Yes | Yes | 21.5 | 19.2 | 2.3 | EB33E6D9A73540C7958372E336615613 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Yuba City | CA | 95991-3623 |  | 2013-06-18 | 2013-06-18 17:04 | 2013-06-18 17:20 | GOODMAN - GPG13480901AC | 145 | 4.4 | Yes | Yes | 20.5 | 19.7 | 0.8 | D82A7E2C7A6D4EE494CA7964DD5E2B3C |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.832% | [5 empty] | Non-TXV | 3.034%
San Joaquin | CA | 93660-0000 |  | 2013-08-15 | 2013-08-15 10:24 | 2013-08-15 10:43 | COLEMAN - GSC130421AB | 143 | 4.3 | Yes | Yes | 17.8 | 20.2 | -2.4 | 84D42D6B67E74368A5385CCA4217486D |  | R22 | Non-TXV |  | 3.007% | 0.96993 | 5.779% | [5 empty] | Non-TXV | 3.007%
Merced | CA | 95348-3754 |  | 2013-06-07 | 2013-06-07 15:20 | 2013-06-07 15:22 | RHEEM - RRPL-B060JK10X | 172 | 5.5 | Yes | Yes | 20.8 | 19.5 | 1.3 | E9343EE556234CBA9FE193EBC5E53007 |  | R410A | Non-TXV |  | 3.198% | 0.96802 | 6.145% | [5 empty] | Non-TXV | 3.198%
Manteca | CA | 95337-6528 |  | 2013-07-17 | 2013-07-17 17:22 | 2013-07-17 17:41 | BDP - 565BJ024 | 70 | 2.4 | Yes | Yes | 23.4 | 20.8 | 2.6 | 2233F9FCFF14406781B91F4ABB1369C0 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Fresno | CA | 93722-5163 |  | 2013-08-12 | 2013-08-12 13:48 | 2013-08-12 13:49 | CARRIER - 48KLA136-300BE | 102 | 4.5 | Yes | Yes | 25.3 | 19.8 | 5.5 | 084EED54CE23465D9B9816781A22E189 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Fresno | CA | 93727-2621 |  | 2013-06-10 | 2013-06-10 15:33 | 2013-06-10 15:56 | RHEEM - RRKA030J06E | 54 | 4.4 | Yes | Yes | 20 | 19.5 | 0.5 | 349429920D4E4D7EAE0144D1D596DF73 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Fresno | CA | 93726-0643 |  | 2013-11-20 | 2013-11-20 09:48 | 2013-11-20 09:48 | CARRIER - 48KLA136-321BE | 116 | 0 | Yes | Yes | 29.7 | 20.4 | 9.3 | 3D5F98D52D23463895CDF4EDF05A7695 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-3901 |  | 2013-08-28 | 2013-08-28 14:59 | 2013-08-28 21:29 | GOODMAN - GPH1324H21AB | 102 | 3.7 | Yes | Yes | 21.1 | 20.4 | 0.7 | 361447B20C1F4E69B4881D901BC21054 |  | R22 | Non-TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | Non-TXV | 3.627%
Atwater | CA | 95301-4434 |  | 2013-06-06 | 2013-06-06 11:32 | 2013-06-06 11:35 | AMERICAN STANDARD - YCC036F1MOBJ | 83 | 4.5 | Yes | Yes | 18.7 | 18.7 | 0 | 4CFFEF717390411A97396E1A05B592C5 |  | R22 | Non-TXV |  | 5.422% | 0.94578 | 10.42% | [5 empty] | Non-TXV | 5.422%
Livingston | CA | 95334-1235 |  | 2013-06-11 | 2013-06-11 13:00 | 2013-06-11 13:17 | RHEEM - RRNL-B036JK06X | 93 | 2.7 | Yes | Yes | 21.2 | 19.8 | 1.4 | 5F5F2705CE8448DC9B3E7FEFC89C92FA |  | R410A | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Los Banos | CA | 93635-3017 |  | 2013-05-28 | 2013-05-28 12:56 | 2013-05-28 13:02 | YORK - H2CB042S06A | 108 | 8.3 | Yes | Yes | 17.1 | 19.2 | -2.1 | 8FE3A2F0C3ED45E58B78F7D0263577C9 |  | R22 | Non-TXV |  | 7.685% | 0.92315 | 14.77% | [5 empty] | Non-TXV | 7.685%
Yuba City | CA | 95993-6087 |  | 2013-06-19 | 2013-06-19 09:10 | 2013-06-19 09:32 | LENNOX - 10ACC-036-230-02 | 74 | 6.1 | Yes | Yes | 19 | 19.8 | -0.8 | E99EC2B7B68A489D919F080A7EEEE8A5 |  | R22 | TXV |  | 8.243% | 0.91757 | 15.84% | [5 empty] | TXV | 8.243%
Fresno | CA | 93720-0138 |  | 2013-06-20 | 2013-06-20 10:44 | 2013-06-20 10:52 | RUUD - UAFD036JAS | 80 | 15.2 | Yes | Yes | 22.8 | 22 | 0.8 | AC4E8C59F3E647819F54855267DE34C7 |  | R22 | Non-TXV |  | 19% | 0.81 | 36.51% | [5 empty] | Non-TXV | 19%
Marysville | CA | 95901-4747 |  | 2013-06-26 | 2013-06-26 16:29 | 2013-06-26 16:52 | BRYANT - 114ANA036-B | 117 | 10.5 | Yes | Yes | 16 | 19 | -3 | 76F43CCFA29440F9AF9BB2A6F42BB923 |  | R410A | TXV |  | 8.974% | 0.91026 | 17.25% | [5 empty] | TXV | 8.974%
Stockton | CA | 95210-3410 |  | 2013-06-19 | 2013-06-19 12:05 | 2013-06-19 12:24 | TRANE - 2TTB3030A1000AA | 88 | -5.2 | Yes | Yes | 16.6 | 19.3 | -2.7 | 416635496F8040A19F1B5A2927910468 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Madera | CA | 93637-2914 |  | 2013-09-05 | 2013-09-05 10:33 | 2013-09-05 10:34 | TRANE - YCY048G1HOAC | 183 | 18.1 | Yes | Yes | 21.5 | 18.2 | 3.3 | 7868F09FF8CC448891A56DD967D647FA |  | R22 | Non-TXV |  | 9.891% | 0.90109 | 19.01% | [5 empty] | Non-TXV | 9.891%
Madera | CA | 93637-5665 |  | 2013-06-19 | 2013-06-19 13:49 | 2013-06-19 18:22 | CARRIER - 24ABB330W0031010 | 68 | 2 | Yes | Yes | 19.2 | 20.4 | -1.2 | 3DFB230F030D42CDBF8B3192B3C898C1 |  | R410A | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95207-5416 |  | 2013-06-27 | 2013-06-27 08:54 | 2013-06-27 08:54 | RHEEM - RRKA-A036JK06E | 62 | 0 | Yes | Yes | 20.1 | 17.7 | 2.5 | 7692DA416A16402282C8CF184505BA69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Joaquin | CA | 93660-0000 |  | 2013-08-15 | 2013-08-15 12:58 | 2013-08-15 21:41 | GOODMAN - GSC130421AB | 143 | -8.4 | Yes | Yes | 22.9 | 20.4 | 2.5 | AEE7CC69A6A2409AB2FD9B73F4E8407B |  | R22 | Non-TXV |  | -5.874% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.874%
Fresno | CA | 93726-1511 |  | 2013-05-30 | 2013-05-30 16:01 | 2013-05-30 16:20 | GOODMAN - GSC130361DF | 120 | -8.5 | Yes | Yes | 13.4 | 16 | -2.6 | FB34A3819C5B41428A45242725930DB8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Stockton | CA | 95206-2818 |  | 2013-06-18 | 2013-06-18 09:21 | 2013-06-18 09:47 | BRYANT - 561CJ030-C | 139 | 6.8 | Yes | Yes | 21.8 | 19.3 | 2.5 | 46BC5E389A494C17A0E04348F07CD6FD |  | R22 | Non-TXV |  | 4.892% | 0.95108 | 9.402% | [5 empty] | Non-TXV | 4.892%
Newcastle | CA | 95658-9769 |  | 2013-09-03 | 2013-09-03 13:48 | 2013-09-03 14:06 | BRYANT - 563CN042-E | 100 | 4.5 | Yes | Yes | 15 | 16.4 | -1.4 | 402AB3670BD040EF8CE208813B00EAB6 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Chico | CA | 95973-0675 |  | 2013-06-11 | 2013-06-11 19:24 | 2013-06-11 19:24 | COLEMAN - DRCS0361BEG | 83 | 0 | Yes | Yes | 25.2 | 20.7 | 4.5 | 1B0122E699024A1BA543ECE0ED8BF9CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-1510 |  | 2013-06-07 | 2013-06-07 11:44 | 2013-06-07 12:00 | CARRIER - UNK | 64 | 5.2 | Yes | Yes | 20.4 | 18.7 | 1.7 | 7E597F9517D14BFE9F05F78E97C4410F |  | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Stockton | CA | 95210-6755 |  | 2013-06-14 | 2013-06-14 13:47 | 2013-06-14 14:07 | BDP - 561CJ036-C | 78 | 2.6 | Yes | Yes | 24.8 | 22.8 | 2 | 23A3A3AA6A33448FB214584A789EBDDE |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95210-2142 |  | 2013-06-14 | 2013-06-14 08:58 | 2013-06-14 09:19 | AMANA - GSC130301CA | 106 | -6.2 | Yes | Yes | 18.5 | 20.4 | -1.9 | 9FD968D8F4DC430E9729B853323FF578 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Lincoln | CA | 95648-3260 |  | 2013-07-06 | 2013-07-06 11:41 | 2013-07-06 12:09 | LENNOX - 13AC-048-230-02 | 158 | 4.7 | Yes | Yes | 22 | 20.4 | 1.6 | 6763D143394A4E29A97B2FF3F4509F8A |  | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.717% | [5 empty] | Non-TXV | 2.975%
Red Bluff | CA | 96080-3628 |  | 2013-06-14 | 2013-06-14 18:33 | 2013-06-14 19:09 | BDP - 561CJ030-A | 73 | 4 | Yes | Yes | 22.6 | 18.5 | 4.1 | B8E4BAD8314C4ED9A4EC57D7207E501B |  | R22 | Non-TXV |  | 5.479% | 0.94521 | 10.53% | [5 empty] | Non-TXV | 5.479%
Oroville | CA | 95966-6401 |  | 2013-06-21 | 2013-06-21 09:02 | 2013-06-21 10:13 | BRYANT - 124ANA048-C | 177 | 8.3 | Yes | Yes | 23.3 | 19.6 | 3.7 | 597D077F58BA4EA789B5830CF3BA96D7 |  | R410A | TXV |  | 4.689% | 0.95311 | 9.012% | [5 empty] | TXV | 4.689%
Mariposa | CA | 95338-9123 |  | 2013-07-31 | 2013-07-31 12:07 | 2013-07-31 12:09 | BRYANT - 574ANW0480N0NA | 193 | 6.9 | Yes | Yes | 25.6 | 22.1 | 3.5 | 89E5F2A08D044640B7632826ECBE9544 |  | R22 | Non-TXV |  | 3.575% | 0.96425 | 6.871% | [5 empty] | Non-TXV | 3.575%
Madera | CA | 93637-9258 |  | 2013-06-19 | 2013-06-19 14:56 | 2013-06-19 15:20 | PAYNE - 4811 | 106 | -6.2 | Yes | Yes | 16.2 | 18.5 | -2.3 | E55214ADC952490F9CC9FF200C5D6547 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Yuba City | CA | 95991-2962 |  | 2013-06-07 | 2013-06-07 13:12 | 2013-06-07 13:36 | OTHER - 561AJ030-B | 70 | -6.6 | Yes | Yes | 16 | 18 | -2 | 4B9CD93EF5234EC68A1EE4B6B5E16040 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Lincoln | CA | 95648-8103 |  | 2013-06-14 | 2013-06-14 13:28 | 2013-06-14 13:50 | YORK - H2RC042S06B | 109 | 8.8 | Yes | Yes | 18.6 | 20.8 | -2.2 | 1759626219C747438089474B3BD1E391 |  | R22 | TXV |  | 8.073% | 0.91927 | 15.52% | [5 empty] | TXV | 8.073%
Corning | CA | 96021-8631 |  | 2013-07-23 | 2013-07-23 11:30 | 2013-07-23 12:18 | YORK - H3RA060506G | 98 | 4.4 | Yes | Yes | 20 | 19.3 | 0.7 | A35144FBFE074CA0A465143B642F6497 |  | R22 | Non-TXV |  | 4.49% | 0.9551 | 8.628% | [5 empty] | Non-TXV | 4.49%
Yuba City | CA | 95991-6259 |  | 2013-07-15 | 2013-07-15 10:08 | 2013-07-15 10:29 | OTHER - UNK | 95 | 2.9 | Yes | Yes | 20 | 18.1 | 1.9 | 82C45750617B49AABAEB38B2CF0F0A54 |  | R22 | Non-TXV |  | 3.053% | 0.96947 | 5.866% | [5 empty] | Non-TXV | 3.053%
Kerman | CA | 93630-1440 |  | 2013-10-03 | 2013-10-03 10:40 | 2013-10-03 10:41 | GOODMAN - GPG1348070M41AC | 125 | 3.9 | Yes | Yes | 25.9 | 20.1 | 5.8 | 140164BDEF80475A9CCBE6F405DA9940 |  | R410A | Non-TXV |  | 3.12% | 0.9688 | 5.996% | [5 empty] | Non-TXV | 3.12%
Granite Bay | CA | 95746-6246 |  | 2013-06-21 | 2013-06-21 16:11 | 2013-06-21 16:47 | GOODMAN - PGB042075-1A | 68 | 9.8 | Yes | Yes | 28.1 | 22.8 | 5.3 | 9F18B89F077F4DE2811B19C58964B9BA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.41% | 0.85588 | 27.7% | [5 empty] | Non-TXV | 14.41%
Stockton | CA | 95210-1484 |  | 2013-06-07 | 2013-06-07 13:19 | 2013-06-07 13:38 | PAYNE - 585A024055YAC | 51 | -3 | Yes | Yes | 26 | 21.3 | 4.7 | 778241DCA2CB4A59932C291AC731AC5C |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95205-7871 |  | 2013-06-12 | 2013-06-12 09:23 | 2013-06-12 09:23 | HEIL - UNK | 97 | 0 | Yes | Yes | 21.6 | 18.8 | 2.8 | 7D023929E70143FDB70A61F277E6642C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-1533 |  | 2013-06-20 | 2013-06-20 10:55 | 2013-06-20 11:15 | CARRIER - 48GX-048115301AD | 114 | 3.6 | Yes | Yes | 19.6 | 19.8 | -0.2 | 940900A6786A4BB0AE586B4DCD65BB0C |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Madera | CA | 93638-2636 |  | 2013-06-13 | 2013-06-13 22:44 | 2013-06-17 09:09 | CARRIER - CA5548VK022 | 134 | -9.5 | Yes | Yes | 17.5 | 19.9 | -2.4 | 941CE6E0A5D54AC98263DC5680E1EF26 |  | R22 | Non-TXV |  | -7.09% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.09%
Lincoln | CA | 95648-2948 |  | 2013-08-17 | 2013-08-17 16:34 | 2013-08-17 16:53 | CARRIER - 38CKC048370 | 100 | 8.2 | Yes | Yes | 17.5 | 19.9 | -2.4 | BB005E1245264E749F010D043629E969 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.2% | 0.918 | 15.76% | [5 empty] | Non-TXV | 8.2%
Clovis | CA | 93612-5812 |  | 2013-08-07 | 2013-08-07 11:14 | 2013-08-07 11:15 | BDP - 585HJW036060ABAF | 102 | 11.4 | Yes | Yes | 25 | 19.3 | 5.7 | 31EF18D3342F4C7AA4CCB34D1E220240 |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Fresno | CA | 93722-4779 |  | 2013-07-18 | 2013-07-18 08:47 | 2013-07-18 08:53 | CARRIER - UNK | 68 | 8.6 | Yes | Yes | 22.8 | 18.8 | 4 | 156B733226674E4C905D30ADD41A4EB5 |  | R22 | Non-TXV |  | 12.65% | 0.87353 | 24.3% | [5 empty] | Non-TXV | 12.65%
Fresno | CA | 93704-4728 |  | 2013-06-19 | 2013-06-19 12:12 | 2013-06-19 12:15 | CARRIER - 48KL124300BE | 50 | 7.9 | Yes | Yes | 19.9 | 18.3 | 1.6 | EDDFFA2A3D1A4A9C8F3F0B81A304B85A |  | R22 | Non-TXV |  | 15.8% | 0.842 | 30.36% | [5 empty] | Non-TXV | 15.8%
Fresno | CA | 93710-5919 |  | 2013-06-03 | 2013-06-03 14:11 | 2013-06-03 14:29 | DAY & NIGHT - 585A042100YAC | 90 | -5.3 | Yes | Yes | 23.5 | 20.4 | 3.1 | E2AF2533B0ED40AA933E3A4404564220 |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Clovis | CA | 93612-3878 |  | 2013-06-18 | 2013-06-18 13:32 | 2013-06-18 15:03 | CARRIER - 48SS-030040321 | 53 | 3.4 | Yes | Yes | 23.1 | 19.6 | 3.5 | 1EF59C44FDFE4E9193D06A14E60C7B2F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.415% | 0.93585 | 12.33% | [5 empty] | Non-TXV | 6.415%
Stockton | CA | 95207-5284 |  | 2013-07-30 | 2013-07-30 09:08 | 2013-07-30 09:27 | CARRIER - 24ABS324A0030010 | 72 | 16.3 | Yes | Yes | 16.5 | 19.1 | -2.6 | BC43DC0AD115452388CEBFBE237F987B |  | R22 | Non-TXV |  | 22.64% | 0.77361 | 43.51% | [5 empty] | Non-TXV | 22.64%
Stockton | CA | 95206-4822 |  | 2013-06-17 | 2013-06-17 13:23 | 2013-06-17 13:41 | RUUD - UNK | 85 | 3.5 | Yes | Yes | 25.6 | 20.8 | 4.8 | 8523AAB1085542AA9ABCD951B8F5C827 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Kerman | CA | 93630-1980 |  | 2013-07-31 | 2013-07-31 13:33 | 2013-07-31 13:34 | CARRIER - 48GX042060311 | 118 | 13.5 | Yes | Yes | 23 | 19.8 | 3.2 | 5E11DC4C32BF4B18BB8E1A81E522F097 |  | R22 | Non-TXV |  | 11.44% | 0.88559 | 21.99% | [5 empty] | Non-TXV | 11.44%
Fresno | CA | 93726-3420 |  | 2013-06-04 | 2013-06-04 11:06 | 2013-06-04 11:20 | CARRIER - 48SX-042080321AA | 87 | 2.7 | Yes | Yes | 20.7 | 20.8 | -0.1 | CB06A15F64854B0B850D5CDAEFF9D006 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Merced | CA | 95348-2157 |  | 2013-06-05 | 2013-06-05 15:11 | 2013-06-05 15:14 | OTHER - TZAA-336-2A757 | 100 | 3.7 | Yes | Yes | 19.2 | 19 | 0.2 | 364FB97E785441ABB13991CCBD34A761 |  | R22 | Non-TXV |  | 3.7% | 0.963 | 7.111% | [5 empty] | Non-TXV | 3.7%
Stockton | CA | 95212-3407 |  | 2013-06-21 | 2013-06-21 12:09 | 2013-06-21 12:31 | UNITARY PRODUCTS GROUP - H2RC036S06A | 83 | 2.5 | Yes | Yes | 21.3 | 19.9 | 1.4 | 8ADFBE1364E040C4A1D23E773F9988EF |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Fresno | CA | 93705-3660 |  | 2013-06-24 | 2013-06-24 13:29 | 2013-06-24 13:29 | BRYANT - 583ANW024040NDAD | 55 | 0 | Yes | Yes | 17.8 | 20.4 | -2.6 | 65D531BE862B44B193207954EE12BA66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-3962 |  | 2013-08-09 | 2013-08-09 13:08 | 2013-08-09 13:59 | LENNOX - HS14-511-9P | 177 | 5.9 | Yes | Yes | 17.2 | 19.9 | -2.7 | 66017E8EFFA24A5798AD64378A90642B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95206-5823 |  | 2013-07-11 | 2013-07-11 14:56 | 2013-07-11 14:56 | RHEEM - RAFD-031JAS | 64 | 0 | Yes | Yes | 22.1 | 20.2 | 2 | 8730FE295D174ECA98F3E5C1272621EA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6704 |  | 2013-08-08 | 2013-08-08 13:36 | 2013-08-08 13:48 | GOODMAN - GSC130361DF | 120 | 3.9 | Yes | Yes | 22.6 | 18 | 4.6 | CB185204F80149199833C38E5D95941B |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Clovis | CA | 93611-5468 |  | 2013-08-07 | 2013-08-07 08:44 | 2013-08-07 08:50 | HEIL - NRGF36DKB04 | 90 | 11.9 | Yes | Yes | 21.7 | 17 | 4.7 | 0F4982D690E64EB4874E543A67B5A998 |  | R22 | Non-TXV |  | 13.22% | 0.86778 | 25.41% | [5 empty] | Non-TXV | 13.22%
Stockton | CA | 95212-3541 |  | 2013-06-17 | 2013-06-17 15:04 | 2013-06-17 15:24 | GOODMAN - CLJ42-1A | 135 | 4.1 | Yes | Yes | 19 | 20.9 | -1.9 | 4E215401A0944EDDA8A098EF8E5A444E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.037% | 0.96963 | 5.837% | [5 empty] | Non-TXV | 3.037%
Sanger | CA | 93657-2823 |  | 2013-09-12 | 2013-09-12 18:08 | 2013-09-12 18:32 | CARRIER - 38TXA036---331 | 104 | 8.3 | Yes | Yes | 17 | 17.5 | -0.5 | A9960D4FF95748B795AF04A14E8D92AC |  | R410A | TXV |  | 7.981% | 0.92019 | 15.34% | [5 empty] | TXV | 7.981%
Los Banos | CA | 93635-3235 |  | 2013-05-30 | 2013-05-30 10:42 | 2013-05-30 10:46 | BDP - 563AN036A | 85 | 12.3 | Yes | Yes | 26.5 | 23.6 | 2.9 | E2D9E27C72074055B0335367F7969D12 |  | R22 | Non-TXV |  | 14.47% | 0.85529 | 27.81% | [5 empty] | Non-TXV | 14.47%
Livingston | CA | 95334-1020 |  | 2013-06-10 | 2013-06-10 10:09 | 2013-06-10 10:29 | RHEEM - RRNA-B036JK06X | 83 | 2.6 | Yes | Yes | 21.1 | 20.7 | 0.4 | 6A4AB06E3D8F4777AF2057079DB4819D |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Los Banos | CA | 93635-6328 |  | 2013-06-01 | 2013-06-01 10:15 | 2013-06-01 10:20 | GOODMAN - CK241B | 71 | 3.7 | Yes | Yes | 20.5 | 20.9 | -0.4 | 0B048B4CED5F4E2A80463298CEC28565 |  | R22 | Non-TXV |  | 5.211% | 0.94789 | 10.01% | [5 empty] | Non-TXV | 5.211%
Jackson | CA | 95642-9570 |  | 2013-08-20 | 2013-08-20 11:45 | 2013-08-20 12:27 | RUUD - 13AJN42A01 | 106 | 7.5 | Yes | Yes | 23.7 | 19.8 | 4 | 5B9BDBB1E2504495AFA232B9DD7A3973 |  | R410A | TXV |  | 7.075% | 0.92925 | 13.6% | [5 empty] | TXV | 7.075%
Fresno | CA | 93728-2907 |  | 2013-07-15 | 2013-07-15 11:27 | 2013-07-15 11:29 | LENNOX - GCS29-036-75-2PA | 58 | 2.6 | Yes | Yes | 25.7 | 20.9 | 4.8 | 8520DF5139294A1DA84BB5EC6FFE2337 |  | R22 | Non-TXV |  | 4.483% | 0.95517 | 8.615% | [5 empty] | Non-TXV | 4.483%
Merced | CA | 95348-3368 |  | 2013-06-12 | 2013-06-12 09:46 | 2013-06-12 09:48 | RHEEM - 7777UNK | 74 | 3.4 | Yes | Yes | 24 | 19.9 | 4.1 | 8A7BF9B4F5CE4ED89B96E2769ECECC28 |  | R22 | Non-TXV |  | 4.595% | 0.95405 | 8.83% | [5 empty] | Non-TXV | 4.595%
Yuba City | CA | 95993-5121 |  | 2013-06-10 | 2013-06-10 14:28 | 2013-06-10 14:28 | BRYANT - 574ANW036090NA | 167 | 0 | Yes | Yes | 24 | 19.8 | 4.2 | E2216E3BE2B0408BA3AFEB2198DFF03A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1866 |  | 2013-06-20 | 2013-06-20 11:55 | 2013-06-20 12:01 | LENNOX - HS25-411-1P | 129 | 5.8 | Yes | Yes | 22.6 | 21 | 1.6 | 451489E48BAC48AD9264690AA3087F72 |  | R22 | Non-TXV |  | 4.496% | 0.95504 | 8.641% | [5 empty] | Non-TXV | 4.496%
Merced | CA | 95348-2116 |  | 2013-08-19 | 2013-08-19 14:15 | 2013-08-19 14:16 | RHEEM - RRNA0042JK08X | 104 | 3.2 | Yes | Yes | 23.6 | 19.2 | 4.4 | 9934CDCBC5024FA08BCE736B7DCC43AA |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Fresno | CA | 93725-1847 |  | 2013-06-20 | 2013-06-20 14:04 | 2013-06-20 14:08 | COLEMAN - BRCS0361BGD | 63 | 3.9 | Yes | Yes | 26.6 | 21 | 5.6 | 89A6975AECF7453780ADA38EE3B59705 |  | R22 | Non-TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | Non-TXV | 6.19%
Sanger | CA | 93657-9785 |  | 2013-08-03 | 2013-08-03 11:04 | 2013-08-03 11:29 | YORK - D2NA060N06506D | 84 | 7.9 | Yes | Yes | 22.8 | 20.4 | 2.4 | 5AA70744D11F4E4A8320335F28C0E6FE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.405% | 0.90595 | 18.07% | [5 empty] | Non-TXV | 9.405%
Stockton | CA | 95210-4235 |  | 2013-06-19 | 2013-06-19 13:24 | 2013-06-19 13:44 | DAY & NIGHT - 588ANW024060ABAD | 40 | -2.4 | Yes | Yes | 22.1 | 20.9 | 1.2 | 15EE669F5F9D4ED5B05AC34EFA935B43 |  | R22 | Non-TXV |  | -6% | 1.06 | 1.68% |  |  |  |  | Non-TXV |  |  | -6%
Placerville | CA | 95667-0000 |  | 2013-07-19 | 2013-07-19 15:58 | 2013-07-19 16:19 | OTHER - BRCQ0361BD | 52 | 2.1 | Yes | Yes | 16 | 17.7 | -1.7 | 7891C69083AE4E8CB4909529ECA8B1F9 |  | R22 | TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | TXV | 4.038%
Stockton | CA | 95206-2635 |  | 2013-07-08 | 2013-07-08 08:27 | 2013-07-08 08:49 | RHEEM - UAKB-036JAZ | 79 | 8.9 | Yes | Yes | 24.3 | 18.3 | 6 | 77656D95E03342CDB63C98BD1165A2E6 |  | R22 | Non-TXV |  | 11.27% | 0.88734 | 21.65% | [5 empty] | Non-TXV | 11.27%
Placerville | CA | 95667-9403 |  | 2013-06-18 | 2013-06-18 09:20 | 2013-06-18 09:39 | GOODMAN - CK36-1C | 80 | 8 | Yes | Yes | 18.5 | 19.7 | -1.2 | B3E31F2B05BB4BB1960E03AB74EBA74C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Placerville | CA | 95667-9403 |  | 2013-06-18 | 2013-06-18 10:12 | 2013-06-18 10:35 | LENNOX - 14ACX-036-20-14 | 107 | 12.1 | Yes | Yes | 19.7 | 19.9 | -0.2 | 73C2FB4DFFC74836A725F6CCAB9AC68A |  | R410A | TXV |  | 11.31% | 0.88692 | 21.73% | [5 empty] | TXV | 11.31%
Dinuba | CA | 93618-9581 |  | 2013-06-24 | 2013-06-24 12:08 | 2013-06-24 12:31 | CARRIER - 38BRC048330 | 164 | 5.2 | Yes | Yes | 15.9 | 18.7 | -2.8 | E3A4009D829843C19AA4D83F2633FD11 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Fresno | CA | 93720-2207 |  | 2013-06-20 | 2013-06-20 12:38 | 2013-06-20 12:40 | GOODMAN - GPG1360090M41BA | 91 | 2.7 | Yes | Yes | 23 | 20.9 | 2.1 | D8979060B3E24D9B8DE2F9020F0A971A |  | R410A | Non-TXV |  | 2.967% | 0.97033 | 5.702% | [5 empty] | Non-TXV | 2.967%
Los Banos | CA | 93635-4321 |  | 2013-06-03 | 2013-06-03 16:08 | 2013-06-03 16:21 | OTHER - UNK | 66 | 3.3 | Yes | Yes | 21.3 | 21.5 | -0.2 | EE7BA9943C1D430DA210EE9B032A8643 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Yuba City | CA | 95993-8254 |  | 2013-08-28 | 2013-08-28 10:40 | 2013-08-28 11:01 | TRANE - TTN036C100B2 | 117 | 4.5 | Yes | Yes | 22 | 19 | 3 | E45ED2DA95E14263B7D7A13F40C53524 |  | R22 | TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | TXV | 3.846%
Marysville | CA | 95901-6248 |  | 2013-06-26 | 2013-06-26 14:51 | 2013-06-26 15:13 | CARRIER - 585EJW02050ABAF | 54 | 3.6 | Yes | Yes | 23 | 17.9 | 5.1 | EFA8F575955D41CF801F2FD204BDAFC7 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Shingle Springs | CA | 95682-8756 |  | 2013-09-13 | 2013-09-13 11:28 | 2013-09-13 11:59 | TRANE - 4WCK4048A1000AA | 124 | 9.5 | Yes | Yes | 17.6 | 19.5 | -1.9 | E0043DE40CCF4CEF8527601DF2547A09 |  | R410A | Non-TXV |  | 7.661% | 0.92339 | 14.72% | [5 empty] | Non-TXV | 7.661%
Fresno | CA | 93726-0872 |  | 2013-05-28 | 2013-05-28 14:26 | 2013-05-28 14:58 | PAYNE - N/A | 60 | 13.1 | Yes | Yes | 16.4 | 19.4 | -3 | B7DB6B2682584995B074D5B906F26862 |  | R22 | Non-TXV |  | 21.83% | 0.78167 | 41.96% | [5 empty] | Non-TXV | 21.83%
Arbuckle | CA | 95912-0000 |  | 2013-09-17 | 2013-09-17 15:07 | 2013-09-17 15:27 | AMANA - PGB36C0902E | 64 | 2.4 | Yes | Yes | 27 | 22.1 | 4.9 | 41FE6C475C5D4656BF8BB67E5572C582 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Kerman | CA | 93630-1350 |  | 2013-07-31 | 2013-07-31 14:34 | 2013-07-31 14:36 | YORK - DAYPF048N110A | 132 | 21.5 | Yes | Yes | 22.4 | 21.3 | 1.1 | FBE7EEA0D7304F19A3D7EBD626336ACB |  | R22 | Non-TXV |  | 16.29% | 0.83712 | 31.3% | [5 empty] | Non-TXV | 16.29%
Kerman | CA | 93630-1350 |  | 2013-07-31 | 2013-07-31 14:37 | 2013-07-31 14:50 | YORK - DAYPF048N110A | 132 | 15.6 | Yes | Yes | 21.8 | 22.1 | -0.3 | 21E29870716C4BC0AE8685459C030D8A |  | R22 | Non-TXV |  | 11.82% | 0.88182 | 22.71% | [5 empty] | Non-TXV | 11.82%
Jackson | CA | 95642-2565 |  | 2013-09-04 | 2013-09-04 12:01 | 2013-09-04 12:22 | YORK - H2RC036S06A | 83 | 20.1 | Yes | Yes | 25.4 | 22.8 | 2.6 | 0083C17A93D246239EF6FB60ACFE8CCA |  | R22 | Non-TXV |  | 24.22% | 0.75783 | 46.54% | [5 empty] | Non-TXV | 24.22%
Clovis | CA | 93611-8126 |  | 2013-07-01 | 2013-07-01 14:47 | 2013-07-01 15:04 | BRYANT - 563CN042-D | 103 | 3.5 | Yes | Yes | 20.6 | 20.8 | -0.2 | 1ACD3923686D4776B63A2B9557EB14BC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.398% | 0.96602 | 6.53% | [5 empty] | Non-TXV | 3.398%
Fresno | CA | 93710-3816 |  | 2013-06-07 | 2013-06-07 12:34 | 2013-06-07 12:55 | PAYNE - PA10JA0360000AGAA | 74 | 7.6 | Yes | Yes | 17.8 | 19.9 | -2.1 | BC6A623AA1664D369677B830C436F087 |  | R22 | Non-TXV |  | 10.27% | 0.8973 | 19.74% | [5 empty] | Non-TXV | 10.27%
Stockton | CA | 95210-1760 |  | 2013-06-10 | 2013-06-10 13:23 | 2013-06-10 13:45 | RHEEM - RRMA-A030JK06X35 | 80 | -4.7 | Yes | Yes | 24.1 | 19.9 | 4.2 | A60338178E424793B33E2B66E24B390D |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Gustine | CA | 95322-9528 |  | 2013-09-05 | 2013-09-05 13:38 | 2013-09-05 13:40 | DAY & NIGHT - 7777UNK | 64 | 3.1 | Yes | Yes | 16.6 | 19.3 | -2.7 | B292138FF19F47098A6CC1FB780D30C5 |  | R22 | Non-TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | Non-TXV | 4.844%
Fresno | CA | 93726-2503 |  | 2013-05-31 | 2013-05-31 17:23 | 2013-05-31 17:40 | CARRIER - N/A | 90 | 4 | Yes | Yes | 18.2 | 12.3 | 5.9 | 21D2666247894394A6BAAC4EB3CC4C89 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Los Banos | CA | 93635-3425 |  | 2013-05-30 | 2013-05-30 13:27 | 2013-05-30 13:29 | TEMPSTAR - PGAA36C1K2 | 81 | 4.6 | Yes | Yes | 26.8 | 22.3 | 4.5 | 5C34617B05E4453181F7D250A249D6FD |  | R22 | Non-TXV |  | 5.679% | 0.94321 | 10.91% | [5 empty] | Non-TXV | 5.679%
Paradise | CA | 95969-4845 |  | 2013-06-12 | 2013-06-12 11:26 | 2013-06-12 12:10 | DAY & NIGHT - 58ANW024060ABBD | 145 | 5 | Yes | Yes | 21 | 20.4 | 0.6 | F91030CB4C634FEA86F3152513BE297A |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Fresno | CA | 93737-9761 |  | 2013-09-04 | 2013-09-04 13:15 | 2013-09-04 14:05 | TRANE - TWP048C100A4 | 147 | 21.3 | Yes | Yes | 18.5 | 20.1 | -1.6 | 2F86BFF15E14499E988AC375A79375F8 |  | R22 | Non-TXV |  | 14.49% | 0.8551 | 27.85% | [5 empty] | Non-TXV | 14.49%
Merced | CA | 95340-2621 |  | 2013-06-06 | 2013-06-06 13:18 | 2013-06-06 13:20 | GOODMAN - GBG13480901AC | 145 | 5.2 | Yes | Yes | 23.9 | 19.3 | 4.6 | F9E397ECA6364ED9B978DADE9A7BC82E |  | R22 | Non-TXV |  | 3.586% | 0.96414 | 6.892% | [5 empty] | Non-TXV | 3.586%
Willows | CA | 95988-3439 |  | 2013-06-27 | 2013-06-27 13:12 | 2013-06-27 13:34 | LENNOX - GCSV-511-125-1P | 104 | 8.9 | Yes | Yes | 17.6 | 18.8 | -1.2 | E276F893D7424252998CB71B6025AF85 |  | R22 | Non-TXV |  | 8.558% | 0.91442 | 16.45% | [5 empty] | Non-TXV | 8.558%
Diamond Springs | CA | 95619-9723 |  | 2013-09-18 | 2013-09-18 11:53 | 2013-09-18 12:15 | LENNOX - GCS20R-411-75-2P | 70 | 3.7 | Yes | Yes | 23 | 22.2 | 0.8 | D3D2AAD8245F4B9BBB52847C13EFAD0A |  | R22 | TXV |  | 5.286% | 0.94714 | 10.16% | [5 empty] | TXV | 5.286%
Fresno | CA | 93728-1642 |  | 2013-07-15 | 2013-07-15 10:32 | 2013-07-15 10:37 | JANITROL - CK42-1B | 92 | 4.4 | Yes | Yes | 22.1 | 20.7 | 1.4 | 17DBAB0C25EC40EEBAB5099FCB0103CA |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Fresno | CA | 93726-0437 |  | 2013-06-18 | 2013-06-18 15:36 | 2013-06-18 15:37 | OTHER - 7777UNK | 80 | 3.5 | Yes | Yes | 26.2 | 22 | 4.2 | 52AF5FE3441B4A0DAFBFE0D584E35500 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Marysville | CA | 95901-6236 |  | 2013-06-26 | 2013-06-26 10:34 | 2013-06-26 11:03 | PAYNE - UNK | 85 | 10 | Yes | Yes | 22 | 16.9 | 5.1 | EC6E5AFF86624CEE83695BD1ABA80756 |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Stockton | CA | 95210-5127 |  | 2013-06-14 | 2013-06-14 11:35 | 2013-06-14 12:02 | CARRIER - 38CXC048320 | 100 | -5.9 | Yes | Yes | 25.6 | 20.4 | 5.2 | E09F06E14A8943EE8BA372333FD10BAA |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Penn Valley | CA | 95946-9697 |  | 2013-08-15 | 2013-08-15 16:47 | 2013-08-15 17:03 | TRANE - TTN060C100A2 | 201 | 7.8 | Yes | Yes | 24 | 23.1 | 0.9 | F8DD78DE0A224CB3A997E1985EA579BF |  | R22 | TXV |  | 3.881% | 0.96119 | 7.458% | [5 empty] | TXV | 3.881%
Manteca | CA | 95337-6816 |  | 2013-06-11 | 2013-06-11 13:09 | 2013-06-11 13:30 | TRANE - R2A336GKC1 | 115 | 11.2 | Yes | Yes | 22.9 | 23.1 | -0.2 | 8DFEB94A1C0043C3B543D2F199C37E64 |  | R22 | Non-TXV |  | 9.739% | 0.90261 | 18.72% | [5 empty] | Non-TXV | 9.739%
Stockton | CA | 95203-3008 |  | 2013-07-25 | 2013-07-25 18:32 | 2013-07-25 18:51 | ICP - PGAD36D1K5 | 102 | -6 | Yes | Yes | 18.4 | 19.9 | -1.5 | 9D5C0BF9C90749A69C058A9F0CCAF4C9 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Rocklin | CA | 95765-4235 |  | 2013-07-27 | 2013-07-27 12:57 | 2013-07-27 12:57 | GOODMAN - CK36--1D | 73 | 0 | Yes | Yes | 17 | 18.5 | -1.5 | 508FF4C3FCC84EA3B4027D84F330667D |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2426 |  | 2013-06-21 | 2013-06-21 10:09 | 2013-06-21 10:26 | LENNOX - GCS16H-311-75-1P | 51 | -3.6 | Yes | Yes | 20.1 | 19.9 | 0.2 | C8DECB6F5F7A47E8A620663A41B77018 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Orland | CA | 95963-9501 |  | 2013-06-17 | 2013-06-17 11:42 | 2013-06-17 11:59 | YORK - D1NH036N05606C | 108 | 7 | Yes | Yes | 22.8 | 19.8 | 3 | C098376060314DF58C49E81E49390723 |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Manteca | CA | 95337-6685 |  | 2013-07-17 | 2013-07-17 14:36 | 2013-07-17 15:00 | BRYANT - 563CN036-D | 101 | 5.7 | Yes | Yes | 21 | 19.7 | 1.3 | 63571858A2164DD3B929C54351C4DD93 |  | R22 | TXV |  | 5.644% | 0.94356 | 10.85% | [5 empty] | TXV | 5.644%
Merced | CA | 95340-6423 |  | 2013-06-17 | 2013-06-17 08:39 | 2013-06-17 08:42 | RHEEM - RRNAB036JK08X | 83 | 7 | Yes | Yes | 19.1 | 17.2 | 1.9 | 7420394DFE8B4621B62B2CD3D1FE1D0F |  | R22 | Non-TXV |  | 8.434% | 0.91566 | 16.21% | [5 empty] | Non-TXV | 8.434%
Madera | CA | 93638-1791 |  | 2013-09-06 | 2013-09-06 12:16 | 2013-09-06 12:17 | BRYANT - 574BNW042060NB | 165 | 4.9 | Yes | Yes | 17.7 | 18.3 | -0.5 | 3BAEA9D937EA41D6971312213BA6BBB3 |  | R410A | Non-TXV |  | 2.97% | 0.9703 | 5.707% | [5 empty] | Non-TXV | 2.97%
Marysville | CA | 95901-9757 |  | 2013-06-26 | 2013-06-26 17:20 | 2013-06-26 17:44 | OTHER - BRCQ0421BD | 66 | -5.4 | Yes | Yes | 17 | 19.2 | -2.2 | 26C0B357335C4E50A8F95764314650DF |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Pollock Pines | CA | 95726-0000 |  | 2013-09-19 | 2013-09-19 10:35 | 2013-09-19 10:35 | PAYNE - 591ANX042000ADAA | 96 | 0 | Yes | Yes | 21.3 | 20.6 | 0.7 | E57156F6B60F410F925C4D069DD2A20F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-5408 |  | 2013-07-23 | 2013-07-23 09:04 | 2013-07-23 09:27 | TRANE - TTR748A100A0 | 140 | 7 | Yes | Yes | 26.6 | 20.9 | 5.7 | FD7A0EF8C50E4C3C9CDFF79D4D9A4211 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Clovis | CA | 93612-4327 |  | 2013-08-26 | 2013-08-26 10:32 | 2013-08-26 10:50 | YORK - D1NH036N05606C | 108 | 5.3 | Yes | Yes | 20.6 | 20.4 | 0.2 | 1B4E3F87C0D2454CBA11753930652CAD |  | R22 | Non-TXV |  | 4.907% | 0.95093 | 9.431% | [5 empty] | Non-TXV | 4.907%
Manteca | CA | 95337-6511 |  | 2013-06-06 | 2013-06-06 15:48 | 2013-06-06 16:05 | BDP - 565BJ018 | 50 | 1.5 | Yes | Yes | 17.5 | 20.4 | -2.9 | 2868F31DFED4479E8202AFA7568A9808 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 12:01 | 2013-07-30 12:23 | COLEMAN - 9348A901 | 70 | 4.9 | Yes | Yes | 21 | 18.8 | 2.2 | E66E0774EEAC45BE8EFA2929601DCE7F |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Lincoln | CA | 95648-3248 |  | 2013-06-14 | 2013-06-14 16:29 | 2013-06-14 16:29 | GOODMAN - CLQ36-1C | 131 | 0 | Yes | Yes | 20.9 | 21 | -0.1 | FAC89434808546EAB08BD7AC428B68B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-8533 |  | 2013-08-02 | 2013-08-02 15:15 | 2013-08-02 18:49 | CARRIER - 386SD42310 | 84 | 2.5 | Yes | Yes | 20.5 | 21.6 | -1.1 | E2F3FA6052F14535B4775869B62FA462 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Los Banos | CA | 93635-3241 |  | 2013-05-30 | 2013-05-30 10:07 | 2013-05-30 10:10 | OTHER - 80WR36A1 | 76 | 10 | Yes | Yes | 20.3 | 20.1 | 0.2 | 2F62DB412B174251B180977396B6E4ED |  | R22 | Non-TXV |  | 13.16% | 0.86842 | 25.29% | [5 empty] | Non-TXV | 13.16%
Auburn | CA | 95602-9337 |  | 2013-06-08 | 2013-06-08 12:19 | 2013-06-08 12:43 | GOODMAN - SSZ140481AD | 85 | 5.8 | Yes | Yes | 18 | 20.6 | -2.6 | D599AA4AFD514060BDD34AA43D1D34F4 |  | R410A | TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | TXV | 6.824%
Fresno | CA | 93726-0869 |  | 2013-06-06 | 2013-06-06 15:48 | 2013-06-06 16:19 | PAYNE - 30/80 YAC 106T | 65 | 8.7 | Yes | Yes | 18.6 | 17.9 | 0.7 | 02B4E1252190440B9EE8BEED36E3C370 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.38% | 0.86615 | 25.72% | [5 empty] | Non-TXV | 13.38%
Fresno | CA | 93726-2443 |  | 2013-06-06 | 2013-06-06 09:56 | 2013-06-06 10:09 | ICP - GPF042K080D | 87 | 3 | Yes | Yes | 20.5 | 18.2 | 2.3 | A62F010D19D445FA9A00FD253B6FB481 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Atascadero | CA | 93422-6321 |  | 2013-08-09 | 2013-08-09 10:33 | 2013-08-09 10:54 | NORDYNE - FS3BA-060KB | 114 | 10.6 | Yes | Yes | 24.6 | 18.8 | 5.8 | 59D17B9D11034C098EB2B4299AFAC565 |  | R22 | Non-TXV |  | 9.298% | 0.90702 | 17.87% | [5 empty] | Non-TXV | 9.298%
Olivehurst | CA | 95961-0000 |  | 2013-06-28 | 2013-06-28 10:22 | 2013-06-28 10:22 | MILLER - UNK | 90 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 5159E9859916406B8AEE7E73A7DFEFB8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-4208 |  | 2013-06-10 | 2013-06-10 09:32 | 2013-06-10 09:32 | YORK - H2RC036S06A | 83 | 0 | Yes | Yes | 15.8 | 18.7 | -2.9 | E8C4B48C60884B5F873141116E1074FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-2614 |  | 2013-08-09 | 2013-08-09 10:02 | 2013-08-09 11:09 | BRYANT - 550AN036-F | 104 | 8.7 | Yes | Yes | 18.8 | 19.9 | -1.1 | 8ADAACD4F01B48D18CBB84B42FAE7B1A |  | R410A | Non-TXV |  | 8.365% | 0.91635 | 16.08% | [5 empty] | Non-TXV | 8.365%
Lincoln | CA | 95648-3259 |  | 2013-06-14 | 2013-06-14 15:40 | 2013-06-14 15:40 | LENNOX - 13ACD-048-230-01 | 204 | 0 | Yes | Yes | 18.1 | 20.7 | -2.6 | 102E409681BA49DB932EB679CFFD2C38 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3020 |  | 2013-06-13 | 2013-06-13 10:40 | 2013-06-13 11:02 | YORK - H2RD048S06B | 134 | 7.4 | Yes | Yes | 19.3 | 19.3 | 0 | 5E3D7187686A4F8786D837780767D538 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.522% | 0.94478 | 10.61% | [5 empty] | Non-TXV | 5.522%
Merced | CA | 95341-8819 |  | 2013-08-05 | 2013-08-05 11:13 | 2013-08-05 11:36 | AMANA - PGD60C0905C | 139 | 4.1 | Yes | Yes | 24.5 | 19.8 | 4.7 | C602268943C843FCB2BBD43C3E45A12F |  | R22 | Non-TXV |  | 2.95% | 0.9705 | 5.669% | [5 empty] | Non-TXV | 2.95%
Diamond Springs | CA | 95619-9427 |  | 2013-07-05 | 2013-07-05 12:20 | 2013-07-05 12:42 | DAY & NIGHT - N2H342AKB200 | 147 | 5.4 | Yes | Yes | 21 | 20.4 | 0.6 | F9FB0387EDFA4D7397EF106E6374A7F1 |  | R22 | TXV |  | 3.673% | 0.96327 | 7.06% | [5 empty] | TXV | 3.673%
Manteca | CA | 95337-4213 |  | 2013-06-08 | 2013-06-08 10:06 | 2013-06-08 10:29 | HEIL - PGAD24D1K | 70 | 8.2 | Yes | Yes | 17.5 | 19.7 | -2.2 | B623E881A2444F8095B422BCAE9804A5 |  | R22 | Non-TXV |  | 11.71% | 0.88286 | 22.51% | [5 empty] | Non-TXV | 11.71%
Corning | CA | 96021-2340 |  | 2013-06-14 | 2013-06-14 17:52 | 2013-06-14 18:31 | WHIRLPOOL - W2GC336A-3 | 92 | 5.1 | Yes | Yes | 21.2 | 20.8 | 0.4 | E1506703740E4267A0B2762EF8BD5160 |  | R22 | Non-TXV |  | 5.543% | 0.94457 | 10.65% | [5 empty] | Non-TXV | 5.543%
Stockton | CA | 95210-5697 |  | 2013-06-14 | 2013-06-14 14:19 | 2013-06-14 14:44 | PAYNE - 598ANX036-B | 196 | 6.2 | Yes | Yes | 17.9 | 20.4 | -2.5 | 096CF23819A047BC9390DE2365DDB05C |  | R22 | Non-TXV |  | 3.163% | 0.96837 | 6.079% | [5 empty] | Non-TXV | 3.163%
Fresno | CA | 93727-8713 |  | 2013-06-17 | 2013-06-17 12:00 | 2013-06-17 12:06 | YORK - D1NA036N03606C | 67 | 5.2 | Yes | Yes | 21.1 | 21.4 | -0.3 | 922D6A4E1B9F415FB465DB7BF92CD46C |  | R22 | Non-TXV |  | 7.761% | 0.92239 | 14.92% | [5 empty] | Non-TXV | 7.761%
Fresno | CA | 93705-3249 |  | 2013-06-19 | 2013-06-19 08:38 | 2013-06-19 08:54 | BDP - 567C048RCU | 76 | 12.7 | Yes | Yes | 22.8 | 19.3 | 3.5 | 112489F164D44399A1DB44DE3FC87078 |  | R22 | Non-TXV |  | 16.71% | 0.83289 | 32.11% | [5 empty] | Non-TXV | 16.71%
Manteca | CA | 95337-4452 |  | 2013-06-06 | 2013-06-06 14:29 | 2013-06-06 14:52 | TRANE - YCX024G1L0BB | 99 | 42 | Yes | Yes | 18.2 | 20.9 | -2.7 | 4CCC6740E4DE4F1F8F9651CEDCA430B2 |  | R22 | Non-TXV |  | 42.42% | 0.57576 | 81.53% | [5 empty] | Non-TXV | 42.42%
Auburn | CA | 95602-8200 |  | 2013-06-08 | 2013-06-08 11:10 | 2013-06-08 11:10 | CARRIER - 38TKB048300 | 115 | 0 | Yes | Yes | 18 | 18.2 | -0.2 | 9708D714BEB04232ADDD22F0374B48BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4514 |  | 2013-07-18 | 2013-07-18 14:43 | 2013-07-18 14:44 | BRYANT - 574BNW036060NB | 149 | 10.1 | Yes | Yes | 23.4 | 22 | 1.4 | A64313D35C9F478ABB32E8F0F746FC83 |  | R410A | Non-TXV |  | 6.779% | 0.93221 | 13.03% | [5 empty] | Non-TXV | 6.779%
Nevada City | CA | 95959-3707 |  | 2013-06-22 | 2013-06-22 11:10 | 2013-06-22 11:10 | BRYANT - 588NW024060ADAD | 42 | 0 | Yes | Yes | 19 | 19.9 | -0.9 | 215BBDFD277C48069F199A0E0144391B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-0000 |  | 2013-06-26 | 2013-06-26 17:28 | 2013-06-26 17:52 | BRYANT - 585A042125YAC | 90 | 3.2 | Yes | Yes | 12.9 | 15.9 | -3 | 428454620A384CC0AF3307B596D2EF76 |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Marysville | CA | 95901-5028 |  | 2013-07-12 | 2013-07-12 11:00 | 2013-07-12 11:00 | LENNOX - UNK | 90 | 0 | Yes | Yes | 17 | 19.3 | -2.3 | E5B6A3CA1DF243E591E46F97822204D8 |  | R22 | TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-0000 |  | 2013-06-29 | 2013-06-29 10:00 | 2013-06-29 10:21 | OTHER - 113RNA036-E | 95 | 3.6 | Yes | Yes | 17 | 18.8 | -1.8 | 81211011733D4C5A863ECF50836F1D46 |  | R22 | TXV |  | 3.789% | 0.96211 | 7.283% | [5 empty] | TXV | 3.789%
Fresno | CA | 93703-2326 |  | 2013-05-30 | 2013-05-30 14:36 | 2013-05-30 15:05 | GOODMAN - PGB036075-1A | 61 | 2.6 | Yes | Yes | 20.6 | 20.1 | 0.5 | 8160D63ABA134A02A25CBA7B62D7C915 |  | R22 | Non-TXV |  | 4.262% | 0.95738 | 8.191% | [5 empty] | Non-TXV | 4.262%
Clovis | CA | 93612-0438 |  | 2013-06-17 | 2013-06-17 08:46 | 2013-06-17 09:12 | CARRIER - 48KLA136---321BE | 102 | 3.1 | Yes | Yes | 22.5 | 20.7 | 1.9 | 3251CBFFA1C6465C886017817EC86997 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Red Bluff | CA | 96080-3509 |  | 2013-06-15 | 2013-06-15 18:29 | 2013-06-15 18:45 | AMANA - PGD36C0702D | 110 | 15.4 | Yes | Yes | 23.1 | 23.4 | -0.3 | 732CD0B8F0E641EF81B8EC06F992AFE7 |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Stockton | CA | 95206-5125 |  | 2013-06-18 | 2013-06-18 15:08 | 2013-06-18 15:47 | PAYNE - 598WN036-A | 264 | 7.9 | Yes | Yes | 23.3 | 20.1 | 3.2 | F0BBBBCDEBAC4D6AB5112EB3A9BFCE55 |  | R22 | Non-TXV |  | 2.992% | 0.97008 | 5.751% | [5 empty] | Non-TXV | 2.992%
Fresno | CA | 93728-3127 |  | 2013-06-19 | 2013-06-19 11:04 | 2013-06-19 11:07 | ICP - PGF030K060E | 50 | 3.4 | Yes | Yes | 17.1 | 19.9 | -2.8 | 28A422F558FA46D0B217EE6E04898CAD |  | R22 | Non-TXV |  | 6.8% | 0.932 | 13.07% | [5 empty] | Non-TXV | 6.8%
Merced | CA | 95340-2730 |  | 2013-06-05 | 2013-06-05 13:59 | 2013-06-05 14:02 | GOODMAN - GPG13480701AB | 145 | 6.1 | Yes | Yes | 24.2 | 19 | 5.2 | B7549D411DC0465BBA1BF1C4C90DCAAF |  | R22 | Non-TXV |  | 4.207% | 0.95793 | 8.085% | [5 empty] | Non-TXV | 4.207%
Stockton | CA | 95207-4676 |  | 2013-06-13 | 2013-06-13 15:42 | 2013-06-13 16:01 | DAY & NIGHT - 567C024RCU | 85 | 6 | Yes | Yes | 24.6 | 21.8 | 2.9 | 548601A41D2743FB82FAAAF9C404B462 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Grass Valley | CA | 95949-6523 |  | 2013-06-22 | 2013-06-22 11:57 | 2013-06-22 11:57 | LENNOX - 15GCSXAV-48-110-230-1A | 189 | 0 | Yes | Yes | 20 | 21.7 | -1.7 | 0145C1E24F1449BFBB87FC77FDDFC245 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-6362 |  | 2013-07-24 | 2013-07-24 16:14 | 2013-07-24 16:14 | AIRE-FLO - 561CJ048-A | 103 | 0 | Yes | Yes | 18.9 | 17.8 | 1.1 | F6270D517F404D81AEB37CC74D158A08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3719 |  | 2013-07-30 | 2013-07-30 12:33 | 2013-07-30 13:08 | BRYANT - 561CJ042-B | 81 | 2.7 | Yes | Yes | 20.6 | 20.6 | 0 | 2D612612618D44D5B0EE5347D2983EB7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95210-1755 |  | 2013-06-19 | 2013-06-19 08:15 | 2013-06-19 08:39 | DAY & NIGHT - 585B024050YACR | 51 | -3 | Yes | Yes | 22 | 19.3 | 2.7 | 43CD568F0644499FB51BB43EA26463B3 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Marysville | CA | 95901-3627 |  | 2013-07-01 | 2013-07-01 11:46 | 2013-07-01 11:46 | LENNOX - 13GEP30075ALP-3A | 68 | 0 | Yes | Yes | 17 | 18.8 | -1.8 | 1BC6B292436F48BD8FE9774E58A5DE13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-8512 |  | 2013-06-13 | 2013-06-13 10:35 | 2013-06-13 10:51 | YORK - H2RA036S06A | 53 | 8.5 | Yes | Yes | 17 | 19.5 | -2.5 | F681B876011848DC8B0E5F22D1C1F61C |  | R22 | Non-TXV |  | 16.04% | 0.83962 | 30.82% | [5 empty] | Non-TXV | 16.04%
Manteca | CA | 95336-3738 |  | 2013-06-06 | 2013-06-06 09:35 | 2013-06-06 10:03 | ICP - GPCM036K080D | 85 | 7.6 | Yes | Yes | 24.3 | 20.4 | 3.9 | 7FB92E3EB3C3441AB2A57F4A2335072B |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Stockton | CA | 95219-7200 |  | 2013-09-04 | 2013-09-04 13:08 | 2013-09-04 13:08 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 21 | 19.1 | 2 | 80FF7C2350A2449E983B0EE51F97359C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1329 |  | 2013-06-18 | 2013-06-18 10:24 | 2013-06-18 10:41 | PAYNE - PA10JA048-D | 98 | -5.8 | Yes | Yes | 22.4 | 18.7 | 3.7 | 70DB1E3E530849F3B142647FD60D69EA |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Stockton | CA | 95210-4181 |  | 2013-06-13 | 2013-06-13 09:13 | 2013-06-13 09:36 | RUUD - UAFD-036JAS | 80 | 10.4 | Yes | Yes | 17.5 | 19.9 | -2.4 | A1A0607502674E2390CB5370CF06F9F4 |  | R22 | Non-TXV |  | 13% | 0.87 | 24.98% | [5 empty] | Non-TXV | 13%
Fresno | CA | 93723-9204 |  | 2013-09-12 | 2013-09-12 15:23 | 2013-09-12 15:26 | TRANE - YCC048F1HOBE | 128 | 16.2 | Yes | Yes | 25 | 21.5 | 3.5 | 6EA9B4B23ADA46DEA28817534D827555 |  | R22 | Non-TXV |  | 12.66% | 0.87344 | 24.32% | [5 empty] | Non-TXV | 12.66%
Atascadero | CA | 93422-2541 |  | 2013-08-08 | 2013-08-08 11:54 | 2013-08-08 12:17 | RHEEM - RACA-048AAO | 47 | 3.6 | Yes | Yes | 17.6 | 19.6 | -2 | C204ED135D704120B44B52126A33D5D2 |  | R22 | Non-TXV |  | 7.66% | 0.9234 | 14.72% | [5 empty] | Non-TXV | 7.66%
Stockton | CA | 95210-1633 |  | 2013-06-10 | 2013-06-10 10:45 | 2013-06-10 11:07 | RHEEM - RRNA-B030JK06X | 72 | -4.2 | Yes | Yes | 24.3 | 18.5 | 5.9 | 54E5FCCB91B54CE38E7FEA7BBD01EF8C |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93726-0728 |  | 2013-05-28 | 2013-05-28 13:24 | 2013-05-28 13:45 | CARRIER - 38BRC03620 | 104 | 18.5 | Yes | Yes | 25.7 | 20.2 | 5.5 | 3528EFF801D44A9EA62E4E3A7E356197 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.79% | 0.82212 | 34.19% | [5 empty] | Non-TXV | 17.79%
Fresno | CA | 93726-0728 |  | 2013-08-23 | 2013-08-23 12:00 | 2013-08-23 13:48 | ARCOAIRE - 38BRC036320 | 104 | 3.9 | Yes | Yes | 18.2 | 19.8 | -1.6 | 891F95DFDF54409CBABAB0D49F115296 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Fresno | CA | 93726-0915 |  | 2013-05-28 | 2013-05-28 15:43 | 2013-05-28 16:01 | UNITARY PRODUCTS GROUP - BRCS0361BD | 63 | 1.9 | Yes | Yes | 18.4 | 20.9 | -2.5 | B1DE8737F3B94CABB563D1419D325017 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Colfax | CA | 95713-9623 |  | 2013-07-26 | 2013-07-26 13:41 | 2013-07-26 14:00 | TRANE - 2TTB3042A1000AA | 109 | 4.6 | Yes | Yes | 25.5 | 20.4 | 5.1 | 2AA0A5CA0D7747AF968C3D4880E6C228 |  | R22 | TXV |  | 4.22% | 0.9578 | 8.11% | [5 empty] | TXV | 4.22%
Yuba City | CA | 95991-1825 |  | 2013-08-06 | 2013-08-06 12:25 | 2013-08-06 12:25 | AMERICAN STANDARD - 4A7B3018A1000AA | 84 | 0 | Yes | Yes | 17 | 17.2 | -0.2 | CEA3EF056D8E46EFBC629913206B2588 |  | R410A | TXV |  | 0% | 1 | 0%
Madera | CA | 93637-2809 |  | 2013-08-05 | 2013-08-05 16:19 | 2013-08-05 16:20 | PAYNE - 575100YAC107 | 68 | 9.5 | Yes | Yes | 24.8 | 24.5 | 0.3 | 8C0A76E5AFA941FF980C143FA84420BD |  | R22 | Non-TXV |  | 13.97% | 0.86029 | 26.85% | [5 empty] | Non-TXV | 13.97%
Stockton | CA | 95204-3921 |  | 2013-07-26 | 2013-07-26 10:36 | 2013-07-26 11:25 | GOODMAN - 13ACD-048-230-15 | 120 | 3.8 | Yes | Yes | 24.7 | 19.9 | 4.8 | AF6168260EA3476197A9ADF76D7E808D |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Colfax | CA | 95713-9002 |  | 2013-07-25 | 2013-07-25 11:18 | 2013-07-25 11:35 | OTHER - 588ANW030080ACD | 53 | 2.1 | Yes | Yes | 25 | 21.3 | 3.7 | 3399869407FD4B39B381920EA332D9C6 |  | R22 | Non-TXV |  | 3.962% | 0.96038 | 7.615% | [5 empty] | Non-TXV | 3.962%
Marysville | CA | 95901-3702 |  | 2013-06-27 | 2013-06-27 08:55 | 2013-06-27 09:19 | OTHER - R2A330GKR2 | 75 | -10.1 | Yes | Yes | 13 | 15.5 | -2.5 | 212994D55C754909942AAC3F3053638E |  | R22 | Non-TXV |  | -13.47% | 1.1347 | 3.771% |  |  |  |  | Non-TXV |  |  | -13.47%
Madera | CA | 93638-1795 |  | 2013-06-12 | 2013-06-12 16:33 | 2013-06-17 09:04 | BRYANT - 574BNW036060NB | 149 | 4.6 | Yes | Yes | 19.1 | 19.8 | -0.7 | 4725172AA078460FB29E4514686A912C |  | R22 | Non-TXV |  | 3.087% | 0.96913 | 5.933% | [5 empty] | Non-TXV | 3.087%
Stockton | CA | 95212-3816 |  | 2013-08-08 | 2013-08-08 14:49 | 2013-08-08 15:13 | GOODMAN - CKL42-1L | 115 | 3.4 | Yes | Yes | 25.1 | 21 | 4.1 | 02815E5386484AEE9674B4A47E634202 |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Fresno | CA | 93728-2229 |  | 2013-06-20 | 2013-06-20 14:36 | 2013-06-20 14:39 | BDP - 588ANW036080ABAF | 66 | 3.6 | Yes | Yes | 29.7 | 24 | 5.8 | 8DB388B9B7104FE5BE1EE1ABE4471E74 |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Stockton | CA | 95212-3534 |  | 2013-06-17 | 2013-06-17 13:54 | 2013-06-17 14:13 | GOODMAN - CLJ48-1A | 130 | 7.7 | Yes | Yes | 21.9 | 21.2 | 0.7 | B4E14FBC72F04FBEBB43F57B7BD52823 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.923% | 0.94077 | 11.38% | [5 empty] | Non-TXV | 5.923%
Los Banos | CA | 93635-3428 |  | 2013-05-31 | 2013-05-31 14:09 | 2013-05-31 14:16 | NORDYNE - JS5BD042K | 170 | 12.3 | Yes | Yes | 27 | 22.6 | 4.4 | 8B0E8559A8964F2F84F8368AEB295BD4 |  | R22 | Non-TXV |  | 7.235% | 0.92765 | 13.9% | [5 empty] | Non-TXV | 7.235%
Madera | CA | 93638-1785 |  | 2013-09-06 | 2013-09-06 11:40 | 2013-09-06 11:42 | BRYANT - 574BNW042060NB | 165 | 5.1 | Yes | Yes | 25 | 19.1 | 6 | 353FD6D809BA417B842602D29CD4D490 |  | R410A | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Selma | CA | 93662-4287 |  | 2013-08-01 | 2013-08-01 09:10 | 2013-08-01 19:59 | LENNOX - 12ACB48-5P | 171 | 5.2 | Yes | Yes | 19 | 20.4 | -1.4 | 14692F08FCED4B73BD2FFF8E25BB8FD6 |  | R22 | Non-TXV |  | 3.041% | 0.96959 | 5.844% | [5 empty] | Non-TXV | 3.041%
Valley Springs | CA | 95252-8880 |  | 2013-07-16 | 2013-07-16 16:33 | 2013-07-16 17:03 | RUUD - UAKA-030JAZ | 66 | 15.9 | Yes | Yes | 18.9 | 21.3 | -2.4 | 4364ADF0FC4D4ADC903A61CD465E1E86 |  | R22 | Non-TXV |  | 24.09% | 0.75909 | 46.3% | [5 empty] | Non-TXV | 24.09%
Dinuba | CA | 93618-4068 |  | 2013-06-24 | 2013-06-24 15:58 | 2013-06-24 16:18 | WEATHER KING - 13AJA30A01 | 98 | 7.6 | Yes | Yes | 19.8 | 19.1 | 0.7 | DBA201E924AF4D3EBC84ABE3FBD418A1 |  | R22 | Non-TXV |  | 7.755% | 0.92245 | 14.9% | [5 empty] | Non-TXV | 7.755%
Los Banos | CA | 93635-4564 |  | 2013-05-31 | 2013-05-31 11:23 | 2013-05-31 11:29 | BRYANT - 561CJ042E | 80 | 8.2 | Yes | Yes | 18.7 | 20.8 | -2.1 | 34A63DF4E5444F1D80FD73C8CC1494F0 |  | R22 | TXV |  | 10.25% | 0.8975 | 19.7% | [5 empty] | TXV | 10.25%
Marysville | CA | 95901-4751 |  | 2013-06-29 | 2013-06-29 10:53 | 2013-06-29 11:17 | BRYANT - 114ANA036-B | 115 | 4.2 | Yes | Yes | 18 | 20.4 | -2.4 | BACD55C289A64F82A67F31D90A8028E4 |  | R410A | TXV |  | 3.652% | 0.96348 | 7.019% | [5 empty] | TXV | 3.652%
Manteca | CA | 95336-7119 |  | 2013-06-06 | 2013-06-06 11:37 | 2013-06-06 12:01 | YORK - UNK | 85 | 5.2 | Yes | Yes | 23.7 | 19.7 | 4 | 8F2A00BE4ECF45DCA47AC396CA4D9DFD |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Fresno | CA | 93720-4471 |  | 2013-06-21 | 2013-06-21 12:53 | 2013-06-21 12:56 | LENNOX - 12ACB42-5P | 125 | 5.4 | Yes | Yes | 19.1 | 21.5 | -2.4 | 565BC67A9AD0484D978EE7939B47A3D0 |  | R22 | Non-TXV |  | 4.32% | 0.9568 | 8.302% | [5 empty] | Non-TXV | 4.32%
Penn Valley | CA | 95946-9465 |  | 2013-08-15 | 2013-08-15 13:30 | 2013-08-15 13:57 | TRANE - 4TTX060B1000AA | 160 | 11.3 | Yes | Yes | 19 | 19.3 | -0.3 | E38149CA414643B2886E7AF9BB71292A |  | R410A | Non-TXV |  | 7.062% | 0.92937 | 13.57% | [5 empty] | Non-TXV | 7.062%
Penn Valley | CA | 95946-9465 |  | 2013-08-15 | 2013-08-15 13:49 | 2013-08-15 14:07 | TRANE - YCC030F1M0BJ | 69 | 3.2 | Yes | Yes | 17 | 19.1 | -2.1 | 058DD72261BD43439D776C33740F5D61 |  | R22 | TXV |  | 4.638% | 0.95362 | 8.913% | [5 empty] | TXV | 4.638%
Dinuba | CA | 93618-8816 |  | 2013-06-24 | 2013-06-24 11:15 | 2013-06-24 12:08 | LENNOX - 13ACD-036-230-02 | 111 | 3.7 | Yes | Yes | 16.1 | 19 | -2.9 | CC3F698957BE441A817BF41F3A9D1C82 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Plumas Lake | CA | 95961-9082 |  | 2013-08-19 | 2013-08-19 16:42 | 2013-08-19 16:58 | CARRIER - UNK | 70 | -6.6 | Yes | Yes | 14 | 17 | -3 | 63B52226AB994F21AC9B937218CB7EE7 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Fresno | CA | 93726-0901 |  | 2013-06-06 | 2013-06-06 16:41 | 2013-06-06 16:59 | GOODMAN - CK30-18 | 76 | 7.4 | Yes | Yes | 19.8 | 21.3 | -1.5 | 56DFF409C8804E89AD5381D6E629CA61 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.737% | 0.90263 | 18.71% | [5 empty] | Non-TXV | 9.737%
Rocklin | CA | 95677-2730 |  | 2013-06-11 | 2013-06-11 12:27 | 2013-06-11 12:27 | GOODMAN - GSX130421BA | 121 | 0 | Yes | Yes | 21 | 18.3 | 2.7 | 2C969E02A9F54F7297EEB874F45946EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4766 |  | 2013-06-20 | 2013-06-20 20:06 | 2013-06-20 20:06 | RHEEM - 1RMA-B042JK08 | 116 | 0 | Yes | Yes | 18.3 | 20.9 | -2.6 | C833D2DA408C4BA7ACE972C94300AB45 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ione | CA | 95640-9715 |  | 2013-09-10 | 2013-09-10 15:21 | 2013-09-10 15:40 | PAYNE - PA10JA0488-A | 99 | 13.3 | Yes | Yes | 26.6 | 20.9 | 5.7 | 42B4BD4B3E77469099654A6DB40E79EF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.43% | 0.86566 | 25.82% | [5 empty] | Non-TXV | 13.43%
Stockton | CA | 95206-6307 |  | 2013-06-21 | 2013-06-21 15:13 | 2013-06-21 15:30 | GOODMAN - CKJ42-1AB | 106 | 6.7 | Yes | Yes | 21.9 | 19.4 | 2.6 | 1564ABBBFE5544578F9E9BB6745E65F6 |  | R22 | Non-TXV |  | 6.321% | 0.93679 | 12.15% | [5 empty] | Non-TXV | 6.321%
Stockton | CA | 95206-5729 |  | 2013-06-20 | 2013-06-20 12:12 | 2013-06-20 12:33 | PAYNE - 38CKC042---311 | 89 | 18.1 | Yes | Yes | 21.6 | 18.7 | 2.9 | FF3C69A429DC4C18BB813C182EBA6720 |  | R22 | Non-TXV |  | 20.34% | 0.79663 | 39.08% | [5 empty] | Non-TXV | 20.34%
Fresno | CA | 93726-6216 |  | 2013-08-08 | 2013-08-08 09:48 | 2013-08-08 09:49 | GOODMAN - PGJ036075-1B | 72 | 3.3 | Yes | Yes | 19.1 | 18.5 | 0.6 | 2050B3B064134AA38DEEA7EB56E22360 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Ione | CA | 95640-5421 |  | 2013-08-01 | 2013-08-01 15:48 | 2013-08-01 16:14 | RHEEM - RAMB-048JBZ | 162 | 6.3 | Yes | Yes | 18 | 20.3 | -2.3 | 0A5191A4FDDC438AA26B07B92A6CC395 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Ione | CA | 95640-5212 |  | 2013-06-26 | 2013-06-26 11:02 | 2013-06-26 11:02 | NORDYNE - GS3BA-036KA | 69 | 0 | Yes | Yes | 16.9 | 17 | -0.1 | 2DD81E5BFA494C3FB0122CA26E40958B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6086 |  | 2013-06-08 | 2013-06-08 10:55 | 2013-06-08 11:19 | CARRIER - 593ANX042000AAAA | 163 | 5 | Yes | Yes | 20.1 | 19.9 | 0.2 | E34F2E6ADDCD422AB956932038A8DB7E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.895% | [5 empty] | Non-TXV | 3.067%
Yuba City | CA | 95991-1924 |  | 2013-06-07 | 2013-06-07 11:55 | 2013-06-07 12:13 | OTHER - SRM 51211A | 95 | -7.8 | Yes | Yes | 17 | 19.5 | -2.5 | 53D189BE7DC14EE38B23D150FD6D81AE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.211% | 1.0821 | 2.299% |  |  |  |  | Non-TXV |  |  | -8.211%
Fresno | CA | 93728-2203 |  | 2013-06-19 | 2013-06-19 11:29 | 2013-06-19 11:32 | PAYNE - 585HJ036060 | 102 | 5.4 | Yes | Yes | 26.1 | 20.1 | 6 | 7228920E2C9C4660A1E1EE1BB7670219 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Stockton | CA | 95206-4748 |  | 2013-07-12 | 2013-07-12 11:35 | 2013-07-12 11:54 | GOODMAN - CKL30-10 | 70 | 4.8 | Yes | Yes | 18.8 | 19.6 | -0.8 | CE065B1521EA498D8FF9378056727761 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.857% | 0.93143 | 13.18% | [5 empty] | Non-TXV | 6.857%
Fresno | CA | 93726-6747 |  | 2013-06-25 | 2013-06-25 11:52 | 2013-06-25 11:54 | BRYANT - 574BNW048090NB | 178 | 5.5 | Yes | Yes | 16.6 | 13.9 | 2.7 | BA13DE8FCAA7491894A38A00CA0E8F05 |  | R410A | Non-TXV |  | 3.09% | 0.9691 | 5.938% | [5 empty] | Non-TXV | 3.09%
Manteca | CA | 95336-3417 |  | 2013-06-07 | 2013-06-07 13:58 | 2013-06-07 14:17 | TRANE - 2TTZ906A1000AA | 224 | 6.9 | Yes | Yes | 21.8 | 19.9 | 1.9 | 6EA65970327E451F9C1EC0FF17BBCD57 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.08% | 0.9692 | 5.92% | [5 empty] | Non-TXV | 3.08%
Shingle Springs | CA | 95682-7311 |  | 2013-09-13 | 2013-09-13 10:35 | 2013-09-13 10:53 | CARRIER - 38CKC036340 | 70 | 2.1 | Yes | Yes | 18.6 | 18.5 | 0.1 | 911BD62CEF044C7E99BA3167FB42CE94 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Arbuckle | CA | 95912-0000 |  | 2013-07-31 | 2013-07-31 10:58 | 2013-07-31 11:21 | TEMPSTAR - GPC036K060F | 85 | 6.4 | Yes | Yes | 16 | 18.8 | -2.8 | DEC18C3623B94062A8A0B4EB83271FD6 |  | R22 | TXV |  | 7.529% | 0.92471 | 14.47% | [5 empty] | TXV | 7.529%
Fresno | CA | 93722-6701 |  | 2013-06-21 | 2013-06-21 12:21 | 2013-06-21 12:27 | BDP - 585HJW030040ABAF | 68 | 6.6 | Yes | Yes | 19.9 | 18.6 | 1.3 | CA78DEB52BFC4E768681CA07C48F8BEA |  | R22 | Non-TXV |  | 9.706% | 0.90294 | 18.65% | [5 empty] | Non-TXV | 9.706%
Madera | CA | 93638-1795 |  | 2013-06-12 | 2013-06-12 15:48 | 2013-06-12 15:48 | BRYANT - 574BNW 0360600NB | 149 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 12AFED0154E043E58D715D0D3F63E866 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Penryn | CA | 95663-0000 |  | 2013-09-19 | 2013-09-19 14:48 | 2013-09-19 15:25 | YORK - H1RA024S06D | 59 | 2.6 | Yes | Yes | 19 | 21.5 | -2.5 | A5963DB4D03A472BA44BC1D69594354A |  | R22 | Non-TXV |  | 4.407% | 0.95593 | 8.469% | [5 empty] | Non-TXV | 4.407%
Madera | CA | 93637-4245 |  | 2013-09-05 | 2013-09-05 11:00 | 2013-09-05 11:02 | CARRIER - 38TKB036300 | 83 | 5.9 | Yes | Yes | 22.8 | 19.7 | 3.1 | 363F889D4BAB4A23A103B87BCF4433B6 |  | R22 | TXV |  | 7.108% | 0.92892 | 13.66% | [5 empty] | TXV | 7.108%
Willows | CA | 95988-9791 |  | 2013-06-27 | 2013-06-27 19:29 | 2013-06-27 19:29 | COLEMAN - 7830-901 | 41 | 0 | Yes | Yes | 19.6 | 20.7 | -1.1 | E6B05D5482834A189AC38D3E488CD73A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Colfax | CA | 95713-0000 |  | 2013-07-25 | 2013-07-25 08:16 | 2013-07-25 08:34 | ARMSTRONG - UNK | 85 | 19.4 | Yes | Yes | 18 | 20.2 | -2.2 | 021A0FF047E44F6A90B7A87734C4392F |  | R22 | Non-TXV |  | 22.82% | 0.77176 | 43.86% | [5 empty] | Non-TXV | 22.82%
Fresno | CA | 93726-0947 |  | 2013-05-29 | 2013-05-29 12:21 | 2013-05-29 12:42 | GOODMAN - GPG13420701AA | 107 | 3.3 | Yes | Yes | 24.6 | 18.7 | 5.9 | 4C3E1B78F595488097D9C856B1AE2512 |  | R22 | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Yuba City | CA | 95993-4638 |  | 2013-06-10 | 2013-06-10 15:22 | 2013-06-10 15:50 | ARMSTRONG - 2SCU13LB148-1 | 156 | 5 | Yes | Yes | 16 | 18.8 | -2.8 | B1D7B1E6D7284138AFF9178C592780F2 |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Fresno | CA | 93726-1138 |  | 2013-05-30 | 2013-05-30 17:45 | 2013-05-30 18:09 | AMERICAN STANDARD - YCC036F1M0BJ | 83 | 6.8 | Yes | Yes | 18.4 | 14.3 | 4.1 | F4A9C1A8C12B4E8FBC8CE875F860804E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.193% | 0.91807 | 15.74% | [5 empty] | Non-TXV | 8.193%
Dinuba | CA | 93618-8816 |  | 2013-07-30 | 2013-07-30 13:08 | 2013-07-30 13:28 | LENNOX - 13ACD-036-230-02 | 111 | 4.7 | Yes | Yes | 17.5 | 19.1 | -1.6 | 28C4DAAA6EF2407E95CDCBF4E576C8F4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.234% | 0.95766 | 8.137% | [5 empty] | Non-TXV | 4.234%
Stockton | CA | 95207-3529 |  | 2013-06-07 | 2013-06-07 10:15 | 2013-06-07 10:15 | HEIL - PGAD36D1K4 | 86 | 0 | Yes | Yes | 19.2 | 18 | 1.2 | 07B7804076074F6DAE713CAC25E96F26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9714 |  | 2013-09-25 | 2013-09-25 16:17 | 2013-09-25 16:38 | DAY & NIGHT - 48PAC-103C | 71 | 2.4 | Yes | Yes | 24.5 | 19.9 | 4.6 | DF196F5525C842A5B52838A6538B0E9D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.38% | 0.9662 | 6.496% | [5 empty] | Non-TXV | 3.38%
Chico | CA | 95928-7633 |  | 2013-06-11 | 2013-06-11 12:26 | 2013-06-11 12:59 | TEMPSTAR - NCA9030UKC1 | 85 | 13.7 | Yes | Yes | 22.5 | 20.9 | 1.6 | 6D4728F2F6F7407E9C83AC7F9507B181 |  | R22 | Non-TXV |  | 16.12% | 0.83882 | 30.97% | [5 empty] | Non-TXV | 16.12%
Rocklin | CA | 95677-4712 |  | 2013-06-15 | 2013-06-15 12:13 | 2013-06-15 12:13 | GOODMAN - CJ60-1EB | 202 | 0 | Yes | Yes | 16.9 | 19.8 | -2.9 | 0AAA6B8826EC4981BC42DA4AB7182DF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2743 |  | 2013-06-17 | 2013-06-17 10:20 | 2013-06-17 10:48 | DAY & NIGHT - 585A024055YACR | 51 | 12.4 | Yes | Yes | 17.2 | 18.8 | -1.6 | 076366F4781946B6AA6271F022939F6B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 24.31% | 0.75686 | 46.73% | [5 empty] | Non-TXV | 24.31%
Stockton | CA | 95212-2852 |  | 2013-07-15 | 2013-07-15 09:56 | 2013-07-15 10:28 | CARRIER - 38CKC042340 | 80 | 8.9 | Yes | Yes | 23.2 | 20.4 | 2.8 | 1E304D92CDBA4D0F8759C16C3B2F02A6 |  | R22 | Non-TXV |  | 11.12% | 0.88875 | 21.38% | [5 empty] | Non-TXV | 11.12%
Corning | CA | 96021-0000 |  | 2013-07-22 | 2013-07-22 09:48 | 2013-07-22 11:17 | COLEMAN - NA | 70 | 0 | Yes | Yes | 23.1 | 22.6 | 0.5 | 8F9AE6EE9358492C99FA083BA01BF7FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9217 |  | 2013-06-20 | 2013-06-20 13:20 | 2013-06-20 13:44 | OTHER - PA13NR036-J | 85 | -5 | Yes | Yes | 20 | 20.4 | -0.4 | 74CF8DE978584E25925203C2E1B332E3 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Chico | CA | 95926-2102 |  | 2013-08-01 | 2013-08-01 17:08 | 2013-08-01 18:53 | BRYANT - 582ANW030060AAD | 55 | 2.5 | Yes | Yes | 23.1 | 21 | 2.1 | F8180B3C691D408D8A6FC5A5960E1033 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93726-1223 |  | 2013-05-30 | 2013-05-30 14:09 | 2013-05-30 14:30 | DAY & NIGHT - N/A | 120 | 14.7 | Yes | Yes | 23.7 | 20.4 | 3.3 | 3DB50ED0201F49CFB668B212DD6AE0A0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.25% | 0.8775 | 23.54% | [5 empty] | Non-TXV | 12.25%
Dinuba | CA | 93618-8815 |  | 2013-07-26 | 2013-07-26 12:29 | 2013-07-26 13:26 | LENNOX - 13ACD-036-230-05 | 92 | 4.6 | Yes | Yes | 17.9 | 19.7 | -1.8 | 7C8946F8A2B941178FF1F869DE66E2B8 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93722-4752 |  | 2013-06-21 | 2013-06-21 13:00 | 2013-06-21 13:03 | ARCOAIRE - 867815025 | 53 | 4.9 | Yes | Yes | 24.6 | 20.4 | 4.2 | 2A4059F39B864A44AEBCCBB789A4244F |  | R410A | Non-TXV |  | 9.245% | 0.90755 | 17.77% | [5 empty] | Non-TXV | 9.245%
Yuba City | CA | 95991-2812 |  | 2013-08-30 | 2013-08-30 09:26 | 2013-08-30 09:55 | OTHER - UNK | 85 | -6 | Yes | Yes | 25 | 19.1 | 5.9 | 5E593D4D94D84A6CBFB613A4D8D5F4FC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Sutter Creek | CA | 95685-4114 |  | 2013-07-24 | 2013-07-24 10:02 | 2013-07-24 10:39 | COLEMAN - BRCS0361BD | 63 | 12.9 | Yes | Yes | 24 | 22.6 | 1.4 | 9E243316105D4ED5A90D2DF44051030E |  | R22 | Non-TXV |  | 20.48% | 0.79524 | 39.35% | [5 empty] | Non-TXV | 20.48%
Fresno | CA | 93726-0620 |  | 2013-06-05 | 2013-06-05 12:54 | 2013-06-05 13:32 | BDP - 585EJW036075ABAF | 82 | 2.7 | Yes | Yes | 25.4 | 20.1 | 5.3 | 6E1B1C985A8A4492814AAA8D7E9527C8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Yuba City | CA | 95991-8473 |  | 2013-06-18 | 2013-06-18 18:03 | 2013-06-18 18:20 | CARRIER - 68CK048370 | 101 | 3.1 | Yes | Yes | 24.5 | 19.2 | 5.3 | E81A34846C6B4D83AA24AAF5E2B6FC86 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Paso Robles | CA | 93446-5436 |  | 2013-08-14 | 2013-08-14 15:11 | 2013-08-14 15:36 | CARRIER - UNK | 102 | 4.1 | Yes | Yes | 18.8 | 20.4 | -1.6 | 8253ABC750244DA8B7B9181D3226FC91 |  | R410A | Non-TXV |  | 4.02% | 0.9598 | 7.725% | [5 empty] | Non-TXV | 4.02%
Paso Robles | CA | 93446-5436 |  | 2013-08-09 | 2013-08-09 12:33 | 2013-08-09 12:50 | CARRIER - 38EZG024300 | 80 | 8.9 | Yes | Yes | 16.5 | 18.2 | -1.7 | C66FEB1128BC4287894C48A5B9755FFD |  | R410A | Non-TXV |  | 11.12% | 0.88875 | 21.38% | [5 empty] | Non-TXV | 11.12%
Fresno | CA | 93722-4750 |  | 2013-06-20 | 2013-06-20 22:03 | 2013-06-20 22:03 | OTHER - NRGE36DOB03 | 91 | 0 | Yes | Yes | 19.5 | 21.4 | -1.9 | C1D25FCD08CB48CA9EEDDB47D570395C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-7719 |  | 2013-06-13 | 2013-06-13 13:04 | 2013-06-13 13:04 | RHEEM - RQPL-B048K 000 | 183 | 0 | Yes | Yes | 21.2 | 19.7 | 1.6 | B8C38644917A46EBAAD7356910115CF6 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-3130 |  | 2013-07-22 | 2013-07-22 11:45 | 2013-07-22 11:47 | BDP - 561AJ048 | 102 | 15.2 | Yes | Yes | 20.5 | 22.1 | -1.6 | B7D8985C53474C5097F9FB395B4C2BD8 |  | R22 | TXV |  | 14.9% | 0.85098 | 28.64% | [5 empty] | TXV | 14.9%
Stockton | CA | 95207-5323 |  | 2013-06-13 | 2013-06-13 16:29 | 2013-06-13 16:49 | RHEEM - 13AJN | 68 | 4 | Yes | Yes | 20.5 | 20.8 | -0.3 | 62AD728314BC47D2A9CFB7426FFC5804 |  | R410A | TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | TXV | 5.882%
Madera | CA | 93637-2764 |  | 2013-06-17 | 2013-06-17 10:32 | 2013-06-17 11:19 | CARRIER - 48KLA36-300B E | 102 | 3.2 | Yes | Yes | 20.2 | 19.8 | 0.4 | 874496FED40D49A8A23B2527BB1F662E |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Yuba City | CA | 95991-8235 |  | 2013-06-19 | 2013-06-19 13:48 | 2013-06-19 14:15 | LENNOX - NK | 117 | 3.7 | Yes | Yes | 21 | 21.8 | -0.8 | 3CD9C5D772124D35BB417B8E49CB3F91 |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Manteca | CA | 95336-4721 |  | 2013-06-07 | 2013-06-07 14:39 | 2013-06-07 15:01 | HEIL - CA7036VKA2 | 140 | 4.2 | Yes | Yes | 19.5 | 20.3 | -0.8 | 3DF41E837ADA41A38C627E3447E17DF2 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-2621 |  | 2013-07-17 | 2013-07-17 15:26 | 2013-07-17 15:28 | CARRIER - UNK | 68 | 10.1 | Yes | Yes | 21.4 | 21 | 0.4 | C658A55E64C6449B83F0C484B252C968 |  | R22 | Non-TXV |  | 14.85% | 0.85147 | 28.54% | [5 empty] | Non-TXV | 14.85%
Madera | CA | 93637-5648 |  | 2013-07-10 | 2013-07-10 03:15 | 2013-07-10 07:45 | - 48NLTO3---321BE | 85 | 5.5 | Yes | Yes | 23.9 | 21.8 | 2.2 | CF5235BBCFF34EAFA64DEF44EA190D8A |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Parlier | CA | 93648-2208 |  | 2013-07-23 | 2013-07-23 16:22 | 2013-07-23 16:44 | RUUD - URKA-A030JKO6E | 54 | 6.5 | Yes | Yes | 19.3 | 19.1 | 0.2 | 0DD3211D650B47079EB9718F7CA21155 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.04% | 0.87963 | 23.13% | [5 empty] | Non-TXV | 12.04%
Clovis | CA | 93612-4246 |  | 2013-07-02 | 2013-07-02 16:11 | 2013-07-02 16:44 | BDP - 585ANZ042080AAAF | 82 | 5.2 | Yes | Yes | 21.2 | 17.8 | 3.4 | F39CF2DA180E47AA88965C0ED8D469F3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.341% | 0.93659 | 12.19% | [5 empty] | Non-TXV | 6.341%
Madera | CA | 93636-1429 |  | 2013-06-19 | 2013-06-19 16:14 | 2013-06-19 18:02 | CARRIER - 48KL-036-311BE | 102 | -6 | Yes | Yes | 18.9 | 20.9 | -2 | 220AB14969ED4DD384398A01F93B5A21 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Madera | CA | 93637-2960 |  | 2013-10-08 | 2013-10-08 11:18 | 2013-10-08 11:20 | CARRIER - 48ESN036060301 | 146 | 5.9 | Yes | Yes | 24.9 | 19.1 | 5.8 | 67D5DCFBF84E4C3FBFF9EB1B96E2AF18 |  | R410A | Non-TXV |  | 4.041% | 0.95959 | 7.766% | [5 empty] | Non-TXV | 4.041%
Stockton | CA | 95206-6431 |  | 2013-06-18 | 2013-06-18 08:30 | 2013-06-18 08:30 | CARRIER - 38CKC036--351 | 70 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | E0D9FCC22BE046C2AE00EEC9C7D6B1EA |  | R22 | TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-5520 |  | 2013-06-29 | 2013-06-29 11:42 | 2013-06-29 12:16 | BRYANT - 598BN036-A | 136 | 16 | Yes | Yes | 16 | 18.9 | -2.9 | CE2C5A21005844ADBDC51AB1CECBAFEB |  | R410A | TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | TXV | 11.76%
Marysville | CA | 95901-5520 |  | 2013-06-29 | 2013-06-29 12:02 | 2013-06-29 12:28 | BRYANT - 598BNO036-A | 135 | -37.2 | Yes | Yes | 17 | 19.9 | -2.9 | 78E20DEF98804D6DA75B6B22FEE22E57 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R410A | TXV |  | -27.56% | 1.2756 | 7.717% |  |  |  |  | TXV |  |  | -27.56%
Magalia | CA | 95954-9576 |  | 2013-08-29 | 2013-08-29 12:34 | 2013-08-29 13:18 | YORK - E1RA042S060 | 110 | 7.6 | Yes | Yes | 23.4 | 22.9 | 0.6 | 0DAAC83DE4B94560B807979977650F64 |  | R22 | Non-TXV |  | 6.909% | 0.93091 | 13.28% | [5 empty] | Non-TXV | 6.909%
Sutter Creek | CA | 95685-9626 |  | 2013-07-24 | 2013-07-24 11:05 | 2013-07-24 11:05 | AMERICAN STANDARD - WCH036C100AA | 112 | 0 | Yes | Yes | 25 | 20.4 | 4.6 | B89496782391416395AA5A1584F8B26F |  | R22 | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3141 |  | 2013-08-05 | 2013-08-05 16:12 | 2013-08-05 17:14 | RHEEM - RRNA-C048JK10X | 97 | 6.3 | Yes | Yes | 24.1 | 20.6 | 3.5 | 55FA24B431D14BA5B887CA23BB17F81E |  | R22 | Non-TXV |  | 6.495% | 0.93505 | 12.48% | [5 empty] | Non-TXV | 6.495%
Stockton | CA | 95206-1912 |  | 2013-07-17 | 2013-07-17 16:06 | 2013-07-17 16:06 | CARRIER - 38CKC042350 | 93 | 0 | Yes | Yes | 20.4 | 23.2 | -2.8 | 1195B31373384F9B8A0399178A6F16E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ripon | CA | 95366-3630 |  | 2013-09-04 | 2013-09-04 14:17 | 2013-09-04 14:36 | TRANE - TTN036C100B2 | 115 | 6.2 | Yes | Yes | 21.7 | 20.6 | 1.1 | 504813F2FA0F4D88A09F15309D0D8697 |  | R22 | TXV |  | 5.391% | 0.94609 | 10.36% | [5 empty] | TXV | 5.391%
Oakdale | CA | 95361-2843 |  | 2013-07-09 | 2013-07-09 10:17 | 2013-07-09 10:17 | RHEEM - RRNA-A036JK06X | 114 | 0 | Yes | Yes | 20.4 | 19.8 | 0.6 | A46BA7848F234485A3A672E9F6075A2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5820 |  | 2013-07-30 | 2013-07-30 09:25 | 2013-07-30 09:25 | COMFORT AIRE - N4A348AKB200 | 112 | 0 | Yes | Yes | 21.8 | 18.7 | 3.1 | 7CC64BBBC45C43139272643ADEF182C5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1842 |  | 2013-06-25 | 2013-06-25 09:02 | 2013-06-25 09:13 | GOODMAN - PGB036075 | 60 | 7.2 | Yes | Yes | 22.5 | 18.7 | 3.8 | 072F22C26F314001889E4B57A4BB42E6 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Chico | CA | 95973-0670 |  | 2013-08-08 | 2013-08-08 17:00 | 2013-08-08 17:41 | COLEMAN - UNK | 49 | 6.1 | Yes | Yes | 23.7 | 21.3 | 2.4 | 788B76D18CEA4AC98AC6ED703D061604 |  | R22 | Non-TXV |  | 12.45% | 0.87551 | 23.92% | [5 empty] | Non-TXV | 12.45%
Oroville | CA | 95966-5517 |  | 2013-07-29 | 2013-07-29 08:35 | 2013-07-29 08:35 | RUUD - 10AJB36A01 | 80 | 0 | Yes | Yes | 16.9 | 19.4 | -2.5 | C21A2DAD37F84CFD9151EC5FFB9C7D9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5726 |  | 2013-09-01 | 2013-09-01 00:16 | 2013-09-01 00:32 | LENNOX - UNK' | 70 | 3.1 | Yes | Yes | 18.1 | 15.9 | 2.2 | C25FAA4C126145AF86D8CA0656B42BCB |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Fresno | CA | 93726-1515 |  | 2013-06-07 | 2013-06-07 09:41 | 2013-06-07 09:41 | YORK - DCCW-F36N100A | 125 | 0 | Yes | Yes | 25 | 19.6 | 5.4 | 9556535D97FD41A38BDFA94A20A7979E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-5109 |  | 2013-06-19 | 2013-06-19 16:02 | 2013-06-19 16:22 | RUUD - UAFD042JBS | 79 | 14.5 | Yes | Yes | 21 | 21 | 0 | 7497E484CA97472EAF26227AAD4F39E9 |  | R22 | Non-TXV |  | 18.35% | 0.81646 | 35.27% | [5 empty] | Non-TXV | 18.35%
Red Bluff | CA | 96080-3208 |  | 2013-06-15 | 2013-06-15 17:27 | 2013-06-15 17:46 | RUUD - RRNA-B042JK08E | 104 | 4 | Yes | Yes | 22.7 | 18.8 | 3.9 | 3851B93030224CFF95147AE85F9180E4 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Clovis | CA | 93612-0453 |  | 2013-06-17 | 2013-06-17 11:08 | 2013-06-17 11:27 | CARRIER - N/A | 85 | 5.4 | Yes | Yes | 18.6 | 21.2 | -2.6 | 670EFAE3C08C437D930B86E11F3158E3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Stockton | CA | 95209-1810 |  | 2013-06-10 | 2013-06-10 15:18 | 2013-06-10 15:34 | OTHER - 2PGE13E36068LP-1A | 101 | 4.9 | Yes | Yes | 21.6 | 19.3 | 2.3 | 1934229EC9E64B4C9CC2D74574626910 |  | R22 | Non-TXV |  | 4.851% | 0.95149 | 9.323% | [5 empty] | Non-TXV | 4.851%
Stockton | CA | 95209-1800 |  | 2013-07-16 | 2013-07-16 12:00 | 2013-07-16 12:00 | OTHER - 2PGE13E36068LP-1A | 101 | 0 | Yes | Yes | 18.8 | 18.3 | 0.5 | EF6C4241273444D8B30380508E3E18DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-3916 |  | 2013-06-24 | 2013-06-24 17:07 | 2013-06-25 01:22 | AMERICAN STANDARD - YCP06F1MDOAB | 66 | 1.9 | Yes | Yes | 18.8 | 20.7 | -1.9 | 90EAD21B488E4FF29835B940732296A8 |  | R22 | Non-TXV |  | 2.879% | 0.97121 | 5.532% | [5 empty] | Non-TXV | 2.879%
Mendota | CA | 93640-0000 |  | 2013-08-13 | 2013-08-13 10:53 | 2013-08-13 11:12 | AMERICAN STANDARD - 2A7B3036A1000AA | 101 | 3.8 | Yes | Yes | 17.1 | 19.8 | -2.7 | FA2667F518A2480B91269B2B6FAFE109 |  | R22 | Non-TXV |  | 3.762% | 0.96238 | 7.23% | [5 empty] | Non-TXV | 3.762%
Merced | CA | 95340-2751 |  | 2013-07-02 | 2013-07-02 14:29 | 2013-07-02 14:36 | GOODMAN - GPG10360701A | 75 | 11.6 | Yes | Yes | 25.5 | 19.7 | 5.8 | D44BF0A6A0804AB2AC0532533CB7A7BE |  | R22 | Non-TXV |  | 15.47% | 0.84533 | 29.72% | [5 empty] | Non-TXV | 15.47%
Fresno | CA | 93704-1812 |  | 2013-06-19 | 2013-06-19 10:11 | 2013-06-19 10:11 | YORK - D1NA036N05606C | 67 | 0 | Yes | Yes | 18.2 | 20.4 | -2.2 | 243D2E262C2D4922939D071F4BCA2FA0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4201 |  | 2013-06-04 | 2013-06-04 14:09 | 2013-06-04 14:51 | CARRIER - 48ES-A4811530TP | 100 | 3.2 | Yes | Yes | 24.1 | 20.6 | 3.5 | 132BB5BC399343A0ADB5B99C09F334A9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93722-4725 |  | 2013-06-21 | 2013-06-21 13:42 | 2013-06-21 13:44 | OTHER - GR4GD036K072X | 100 | 6 | Yes | Yes | 27.3 | 22.1 | 5.3 | 9FB21D6A03FF41CC95C927709FAE7E33 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Madera | CA | 93637-5707 |  | 2013-06-19 | 2013-06-19 11:10 | 2013-06-19 11:37 | PAYNE - PA10JA030-A | 80 | 3.8 | Yes | Yes | 18.2 | 21 | -2.8 | 95E50F4E5BA94FADA45D60AA6BE2C02C |  | R22 | Non-TXV |  | 4.75% | 0.9525 | 9.128% | [5 empty] | Non-TXV | 4.75%
Fresno | CA | 93705-1741 |  | 2013-06-24 | 2013-06-24 12:02 | 2013-06-24 12:09 | DAY & NIGHT - UNK | 70 | 9.9 | Yes | Yes | 20.9 | 20.4 | 0.5 | 11157739270B4FB3A3283A48ABA3254E |  | R22 | Non-TXV |  | 14.14% | 0.85857 | 27.18% | [5 empty] | Non-TXV | 14.14%
Merced | CA | 95348-3361 |  | 2013-07-15 | 2013-07-15 15:42 | 2013-07-15 15:44 | RHEEM - RRMA-A036 | 99 | 3.7 | Yes | Yes | 22.9 | 21.5 | 1.4 | 684BAD074F76432088006B18F8C426B1 |  | R22 | Non-TXV |  | 3.737% | 0.96263 | 7.182% | [5 empty] | Non-TXV | 3.737%
Fresno | CA | 93722-4721 |  | 2013-06-20 | 2013-06-20 10:39 | 2013-06-20 11:43 | BDP - 585HJW0360ABAH | 44 | -3.1 | Yes | Yes | 15.3 | 17.2 | -1.9 | 9157573D81014EDF8DCF0F10D8061650 |  | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Fresno | CA | 93722-5476 |  | 2013-07-16 | 2013-07-16 19:34 | 2013-07-16 20:04 | CARRIER - N/A | 85 | 2.5 | Yes | Yes | 18.4 | 18.6 | -0.2 | 9B5289AAA7CF4AF69E390921DE8EFEE1 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Riverbank | CA | 95367-2658 |  | 2013-07-11 | 2013-07-11 16:07 | 2013-07-11 16:30 | CARRIER - 591ANOX042000ABAA | 112 | 8.4 | Yes | Yes | 18.8 | 20.1 | -1.3 | 0768E3AFD24E401687E1E0212A4248C5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95212-2852 |  | 2013-06-12 | 2013-06-12 11:08 | 2013-06-12 11:28 | CARRIER - 38CKC042 | 80 | 5.3 | Yes | Yes | 18.9 | 18.7 | 0.2 | DDCD32417F444E75A56D8517B85650AB |  | R22 | Non-TXV |  | 6.625% | 0.93375 | 12.73% | [5 empty] | Non-TXV | 6.625%
Fresno | CA | 93722-3007 |  | 2013-07-30 | 2013-07-30 15:48 | 2013-07-30 15:49 | TEMPSTAR - CA5036VKB1 | 86 | 14.5 | Yes | Yes | 16.7 | 16.1 | 0.6 | 0C0177A05D4B433495A19DEE1BFDF664 |  | R22 | Non-TXV |  | 16.86% | 0.8314 | 32.4% | [5 empty] | Non-TXV | 16.86%
Granite Bay | CA | 95746-6273 |  | 2013-06-21 | 2013-06-21 17:25 | 2013-06-21 17:25 | TRANE - TTD760B100A0 | 129 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | F9539C374BB5447789994ED3374ACBAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1740 |  | 2013-06-18 | 2013-06-18 11:19 | 2013-06-18 11:28 | DAY & NIGHT - 3680YAC107C | 66 | 12 | Yes | Yes | 24 | 19.9 | 4.1 | F30321D1B554414EA3A45F6F261ACF6C |  | R22 | Non-TXV |  | 18.18% | 0.81818 | 34.94% | [5 empty] | Non-TXV | 18.18%
Chico | CA | 95928-9617 |  | 2013-07-08 | 2013-07-08 20:40 | 2013-07-08 21:06 | OTHER - RCC36R12B | 114 | 16.2 | Yes | Yes | 17.2 | 20.1 | -2.9 | DF8704B51C424BDB9C8B4CD36AD4E6BC |  | R22 | Non-TXV |  | 14.21% | 0.85789 | 27.31% | [5 empty] | Non-TXV | 14.21%
Stockton | CA | 95212-3803 |  | 2013-06-18 | 2013-06-18 12:43 | 2013-06-18 13:03 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 18.9 | 19.3 | -0.4 | E23323462D23438A8169910EDC359809 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-4946 |  | 2013-06-07 | 2013-06-07 15:17 | 2013-06-07 15:17 | DAY & NIGHT - 30/80YAC-106T-C | 65 | 0 | Yes | Yes | 22 | 21 | 1 | E071DA7EB12747A3895CAFCFBCC549ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-5364 |  | 2013-08-27 | 2013-08-27 16:26 | 2013-08-27 16:26 | GOODMAN - GSC13042 | 95 | 0 | Yes | Yes | 19 | 20.6 | -1.6 | A19E1957CB664562B18D7DB7339850EB |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6402 |  | 2013-06-18 | 2013-06-18 12:01 | 2013-06-18 12:23 | GOODMAN - CLJ36-1A | 109 | -18.2 | Yes | Yes | 20 | 18.9 | 1.2 | AE7CB871E19540409EFF7FACE9E281E8 |  | R22 | TXV |  | -16.7% | 1.167 | 4.676% |  |  |  |  | TXV |  |  | -16.7%
Manteca | CA | 95336-9125 |  | 2013-06-08 | 2013-06-08 08:40 | 2013-06-08 09:05 | TRANE - BTD736A100B0 | 92 | 2.8 | Yes | Yes | 22.7 | 19.9 | 2.8 | 974CBAA220524A6BB7D7DC6E6D44721F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Tracy | CA | 95377-7969 |  | 2013-07-23 | 2013-07-23 15:48 | 2013-07-23 16:07 | UNITARY PRODUCTS GROUP - H1DE042S06B | 99 | 2.9 | Yes | Yes | 23.1 | 20.2 | 2.9 | 7A7F0137A0A94C0F83FF0BCD91182919 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Fresno | CA | 93728-2219 |  | 2013-07-16 | 2013-07-16 09:59 | 2013-07-16 10:01 | YORK - D3YS036N0456C | 78 | 3.2 | Yes | Yes | 21.5 | 19.3 | 2.2 | B6294F4A10AF4CEAB7FF481B63CF8267 |  | R22 | Non-TXV |  | 4.103% | 0.95897 | 7.884% | [5 empty] | Non-TXV | 4.103%
Copperopolis | CA | 95228-9603 |  | 2013-08-29 | 2013-08-29 10:39 | 2013-08-29 10:55 | RHEEM - 13AJA36A01 | 108 | 13 | Yes | Yes | 20 | 19.6 | 0.4 | 3F799F8846A249979C3B91121FC7650A |  | R22 | Non-TXV |  | 12.04% | 0.87963 | 23.13% | [5 empty] | Non-TXV | 12.04%
Copperopolis | CA | 95228-9603 |  | 2013-08-29 | 2013-08-29 10:58 | 2013-08-29 10:58 | WEATHER KING - 13AJA30A01 | 98 | 0 | Yes | Yes | 23.6 | 19.8 | 3.8 | EA808A7E21A0486CB2C1D468B75BF4F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1334 |  | 2013-06-18 | 2013-06-18 10:48 | 2013-06-18 10:51 | BRYANT - 583ANW036060AAAF | 82 | 7.4 | Yes | Yes | 21.9 | 20.2 | 1.7 | C5C9FA262B9F468D9FF9F5B33EFA6752 |  | R22 | Non-TXV |  | 9.024% | 0.90976 | 17.34% | [5 empty] | Non-TXV | 9.024%
Merced | CA | 95341-5710 |  | 2013-06-12 | 2013-06-12 11:22 | 2013-06-12 11:26 | RHEEM - RRNLB030JK06X | 76 | 2.3 | Yes | Yes | 23.5 | 21.3 | 2.2 | 0AED4FB8CBFD498480AE8C298C62C1DA |  | R410A | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
San Andreas | CA | 95249-9460 |  | 2013-08-20 | 2013-08-20 11:52 | 2013-08-20 12:10 | WESTINGHOUSE - FS3BA-024KA | 64 | 2.8 | Yes | Yes | 21.9 | 20.6 | 1.3 | 5376B6E5CC924168AAFCF6C024C37D5F |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Rocklin | CA | 95765-4243 |  | 2013-06-15 | 2013-06-15 14:12 | 2013-06-15 14:12 | GOODMAN - CKJ60-1C | 149 | 0 | Yes | Yes | 22.1 | 21.8 | 0.3 | B8944F4493444CA585DCFE36AD218240 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1523 |  | 2013-06-12 | 2013-06-12 13:04 | 2013-06-12 13:27 | RUUD - 92-20841-02-02 | 64 | 2.3 | Yes | Yes | 18.6 | 19.2 | -0.6 | D461C6404FF3411FB45853C658466E4C |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Stockton | CA | 95207-5832 |  | 2013-06-14 | 2013-06-14 10:36 | 2013-06-14 11:00 | HEIL - CA3036VKA1 | 94 | 19.1 | Yes | Yes | 25.5 | 20.3 | 5.2 | 9A7984FAAB094BD1A516E8D4E8A3357F |  | R22 | Non-TXV |  | 20.32% | 0.79681 | 39.05% | [5 empty] | Non-TXV | 20.32%
Stockton | CA | 95206-5710 |  | 2013-06-20 | 2013-06-20 09:28 | 2013-06-20 09:45 | CARRIER - 38CKB036320 | 72 | 8.8 | Yes | Yes | 18.6 | 18.3 | 0.3 | CF121AD83B7A40CFA8F5F478E6368DC1 |  | R22 | TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | TXV | 12.22%
Pollock Pines | CA | 95726-9510 |  | 2013-07-29 | 2013-07-29 11:07 | 2013-07-29 11:31 | CARRIER - 48SS-030040321 | 56 | 2.3 | Yes | Yes | 26 | 21 | 5 | 9258FDF6179E462286BA5DF692E97A39 |  | R22 | TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | TXV | 4.107%
Orland | CA | 95963-8149 |  | 2013-08-15 | 2013-08-15 12:39 | 2013-08-15 13:10 | YORK - H1RD036S06G | 145 | 12.8 | Yes | Yes | 19.7 | 20.9 | -1.2 | 88230D7B52B246C681ED4F0AF75BE1C8 |  | R22 | Non-TXV |  | 8.828% | 0.91172 | 16.96% | [5 empty] | Non-TXV | 8.828%
Fresno | CA | 93705-3118 |  | 2013-06-18 | 2013-06-18 12:55 | 2013-06-18 12:58 | TRANE - YCC036F1MOBF | 83 | 7.3 | Yes | Yes | 18.5 | 16.8 | 1.7 | 805B6B327063406F9F156E81A62CAB2B |  | R22 | Non-TXV |  | 8.795% | 0.91205 | 16.9% | [5 empty] | Non-TXV | 8.795%
Stockton | CA | 95206-4698 |  | 2013-06-13 | 2013-06-13 14:24 | 2013-06-13 14:47 | GOODMAN - GSC130601CB | 85 | 4 | Yes | Yes | 25.3 | 22.8 | 2.5 | DC1E415F4D36403587916AF2963AAF91 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fresno | CA | 93705-1341 |  | 2013-07-01 | 2013-07-01 11:08 | 2013-07-01 11:18 | AMANA - PGD36C0702E | 110 | 9.1 | Yes | Yes | 24.4 | 19.7 | 4.7 | B5C25CCB8C2445178BCC841B7DB6EA00 |  | R22 | Non-TXV |  | 8.273% | 0.91727 | 15.9% | [5 empty] | Non-TXV | 8.273%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 14:52 | 2013-07-30 14:52 | LENNOX - GCS20R-411-100-1P | 70 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 365E2499F80F40D1825B4FFA174AE546 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4753 |  | 2013-06-20 | 2013-06-20 20:03 | 2013-06-20 20:03 | RHEEM - RRNL-B036K06K | 91 | 0 | Yes | Yes | 17.4 | 19.9 | -2.5 | 8B2632C0E1404B52994B8BCA7E77FF33 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2704 |  | 2013-06-05 | 2013-06-05 13:13 | 2013-06-05 13:15 | GOODMAN - PGB042100-1 | 68 | 3.1 | Yes | Yes | 20.7 | 19.3 | 1.4 | 8C47F3C7AC5D45D0AE067CD8089D4CC2 |  | R22 | Non-TXV |  | 4.559% | 0.95441 | 8.761% | [5 empty] | Non-TXV | 4.559%
Stockton | CA | 95204-4610 |  | 2013-06-25 | 2013-06-25 11:09 | 2013-06-25 11:29 | CARRIER - 38EN036320 | 88 | 10.1 | Yes | Yes | 20.2 | 17.1 | 3.1 | D8919EAEA01446D38E342660BC7D1C57 |  | R22 | Non-TXV |  | 11.48% | 0.88523 | 22.06% | [5 empty] | Non-TXV | 11.48%
Oakdale | CA | 95361-2607 |  | 2013-07-09 | 2013-07-09 09:43 | 2013-07-09 10:03 | GUARDIAN - TCGD42S21S2HA | 66 | 7.5 | Yes | Yes | 18.6 | 20.4 | -1.8 | 4772250492CC41AFBBF835EF8CAF76F8 |  | R22 | Non-TXV |  | 11.36% | 0.88636 | 21.84% | [5 empty] | Non-TXV | 11.36%
Kerman | CA | 93630-1457 |  | 2013-08-28 | 2013-08-28 12:28 | 2013-08-28 12:30 | LENNOX - GCS29X-030-75-2PA | 60 | 3.2 | Yes | Yes | 22.1 | 20.2 | 1.9 | E710C6C14F914E769F278D4502AECF6C |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Fresno | CA | 93722-3319 |  | 2013-07-25 | 2013-07-25 12:05 | 2013-07-25 12:06 | CARRIER - UNK | 68 | 8.6 | Yes | Yes | 25.8 | 22.5 | 3.4 | 3D959BA8E0624B54839A78067659A712 |  | R22 | Non-TXV |  | 12.65% | 0.87353 | 24.3% | [5 empty] | Non-TXV | 12.65%
Stockton | CA | 95209-2605 |  | 2013-07-24 | 2013-07-24 13:55 | 2013-07-24 14:12 | TRANE - TTX030C100A3 | 111 | 3.3 | Yes | Yes | 23.1 | 20.7 | 2.4 | 997327D3B227473AAC4F4FC31BC214D6 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
San Joaquin | CA | 93660-9733 |  | 2013-09-12 | 2013-09-12 09:46 | 2013-09-12 09:49 | OTHER - UNK | 98 | 8.4 | Yes | Yes | 30.1 | 24.2 | 5.9 | BE86121840F644F0B1C921C12C428D62 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Riverbank | CA | 95367-2641 |  | 2013-07-22 | 2013-07-22 15:57 | 2013-07-22 16:18 | RHEEM - RAFD-036JA | 80 | 2.4 | Yes | Yes | 18.8 | 19 | -0.2 | A7CF0AE1DD02472AB73918B6BF78CA17 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-4039 |  | 2013-07-09 | 2013-07-09 12:59 | 2013-07-09 13:01 | AMERICAN STANDARD - YCZ050F1HOAE | 189 | 24.3 | Yes | Yes | 19.7 | 18.2 | 1.5 | E9061F36374C4553B952CC5F76B71272 |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Stockton | CA | 95206-2614 |  | 2013-06-12 | 2013-06-12 08:30 | 2013-06-12 08:56 | BRYANT - 583ANW042090NBAF | 118 | -11.1 | Yes | Yes | 22.3 | 21 | 1.3 | 31F82F2FFC124DD2AC02B40314C0B62A |  | R22 | Non-TXV |  | -9.407% | 1.0941 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.407%
Marysville | CA | 95901-4417 |  | 2013-07-11 | 2013-07-11 08:23 | 2013-07-11 08:58 | GOODMAN - GPG1324045M41AA | 80 | 2.9 | Yes | Yes | 22 | 18.8 | 3.2 | 2A2AE02FBFF84BF28F8EF01FFC642D50 |  | R410A | TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | TXV | 3.625%
Ione | CA | 95640-9306 |  | 2013-08-01 | 2013-08-01 12:11 | 2013-08-01 12:11 | PAYNE - UNK | 85 | 0 | Yes | Yes | 29 | 23.1 | 5.9 | 675E4737A35F43E78437010994E5F145 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-3603 |  | 2013-06-18 | 2013-06-18 17:44 | 2013-06-18 18:01 | CARRIER - NA | 83 | 3.6 | Yes | Yes | 23.9 | 19 | 4.9 | DB6D223AB6A7434F88A90300172D76D4 |  | R22 | Non-TXV |  | 4.337% | 0.95663 | 8.335% | [5 empty] | Non-TXV | 4.337%
Biola | CA | 93606-0000 |  | 2013-08-28 | 2013-08-28 13:26 | 2013-08-28 13:27 | RHEEM - RRMA-A030JK06X | 80 | 4.5 | Yes | Yes | 17 | 19.9 | -2.9 | E02498933430485E8DC946847BEBA326 |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Chico | CA | 95926-3402 |  | 2013-07-01 | 2013-07-01 18:22 | 2013-07-01 18:50 | LENNOX - GCS10X-50-1P | 71 | 10.4 | Yes | Yes | 21.5 | 17.7 | 3.8 | 17F0A8344C144053A014427C99C9C87D |  | R22 | Non-TXV |  | 14.65% | 0.85352 | 28.15% | [5 empty] | Non-TXV | 14.65%
Fresno | CA | 93728-2206 |  | 2013-07-19 | 2013-07-19 09:41 | 2013-07-19 09:55 | BRYANT - 561036-E | 70 | 5 | Yes | Yes | 17.3 | 20.2 | -2.8 | 58C1CA32C5CB45D59F231D69EA43434E |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Stockton | CA | 95206-2408 |  | 2013-06-12 | 2013-06-12 15:06 | 2013-06-12 15:33 | BRYANT - 561CJ030-D | 89 | 4.4 | Yes | Yes | 21.9 | 22 | -0.1 | BB5F2909049C409287D2C8E0D44184A7 |  | R22 | Non-TXV |  | 4.944% | 0.95056 | 9.501% | [5 empty] | Non-TXV | 4.944%
Yuba City | CA | 95993-5127 |  | 2013-06-19 | 2013-06-19 15:23 | 2013-06-19 15:23 | BRYANT - 583BNW042090NC | 144 | 0 | Yes | Yes | 18 | 19.3 | -1.3 | FB8644555B6B4ABB8F5698A28ECBF3B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Williams | CA | 95987-0000 |  | 2013-09-09 | 2013-09-09 13:34 | 2013-09-09 13:34 | BRYANT - 589ANW060120ABAG | 106 | 0 | Yes | Yes | 17 | 19.1 | -2.1 | 70DE902F52AC468B981368F2C536CBE2 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-9523 |  | 2013-07-13 | 2013-07-13 10:18 | 2013-07-13 10:18 | BRYANT - 563CN048-F | 165 | 0 | Yes | Yes | 18 | 19.8 | -1.8 | F2E56923C0C34871979EF48E50509A2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1706 |  | 2013-08-21 | 2013-08-21 10:07 | 2013-08-21 10:09 | RHEEM - RRNA-B030JK06X | 65 | 4.1 | Yes | Yes | 18.8 | 18.9 | -0.1 | 3CC4137238204A37BB0A040D85914D5C |  | R22 | Non-TXV |  | 6.308% | 0.93692 | 12.12% | [5 empty] | Non-TXV | 6.308%
Plumas Lake | CA | 95961-9071 |  | 2013-08-19 | 2013-08-19 13:55 | 2013-08-19 14:19 | CARRIER - UNK | 95 | 4.5 | Yes | Yes | 16 | 17.7 | -1.7 | C12C25559E12496C95D91472F70871BB |  | R22 | TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | TXV | 4.737%
Rocklin | CA | 95765-5804 |  | 2013-08-12 | 2013-08-12 11:16 | 2013-08-12 11:38 | GOODMAN - CLJ60-1 | 141 | 5.1 | Yes | Yes | 15 | 17.9 | -2.9 | 4D3EB595F3EB4204AE1315F4DE28068E |  | R22 | TXV |  | 3.617% | 0.96383 | 6.951% | [5 empty] | TXV | 3.617%
Stockton | CA | 95207-7624 |  | 2013-06-14 | 2013-06-14 15:22 | 2013-06-14 15:22 | GOODMAN - CKL18-1 | 53 | 0 | Yes | Yes | 18.2 | 20.2 | -2 | FB396D5939D54381941356C4DAFE080C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4298 |  | 2013-08-09 | 2013-08-09 10:57 | 2013-08-09 11:21 | GOODMAN - CKL49-1 | 109 | 12.7 | Yes | Yes | 17.5 | 20.1 | -2.6 | 7663731F313744A1B10F9636110C1CAB |  | R22 | Non-TXV |  | 11.65% | 0.88349 | 22.39% | [5 empty] | Non-TXV | 11.65%
Fresno | CA | 93703-4390 |  | 2013-10-25 | 2013-10-25 12:43 | 2013-10-25 12:45 | BDP - 777UNK | 64 | 2.8 | Yes | Yes | 20 | 19.5 | 0.5 | 7DF8907FE6834B11947AC119E184AA3E |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Auburn | CA | 95602-8151 |  | 2013-07-27 | 2013-07-27 08:22 | 2013-07-27 08:46 | PAYNE - 542EJ036 | 132 | 4.8 | Yes | Yes | 22 | 20.4 | 1.6 | 60405F4AA32C494B89B2F08073AFA5C7 |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Merced | CA | 95348-3206 |  | 2013-06-07 | 2013-06-07 12:03 | 2013-06-07 12:06 | OTHER - H1RC04206A | 105 | 3.7 | Yes | Yes | 18.1 | 18.5 | -0.4 | FE3FAB193B3E4C31A81651968B6523EE |  | R22 | Non-TXV |  | 3.524% | 0.96476 | 6.772% | [5 empty] | Non-TXV | 3.524%
Placerville | CA | 95667-9001 |  | 2013-06-18 | 2013-06-18 15:24 | 2013-06-18 15:24 | TRANE - WCH030B100CA | 140 | 0 | Yes | Yes | 26.9 | 21 | 5.9 | F8DA35EA85634E5D94F1901E9B4A070E |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3010 |  | 2013-06-01 | 2013-06-01 09:41 | 2013-06-01 10:09 | PAYNE - N/A | 90 | -6.4 | Yes | Yes | 18.2 | 20.7 | -2.5 | 8832FB4B65C8426E83CA4060C85A136F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.111% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.111%
Merced | CA | 95348-3206 |  | 2013-06-07 | 2013-06-07 12:30 | 2013-06-07 12:32 | CARRIER - 38BRC048320 | 165 | 6.4 | Yes | Yes | 20.1 | 18.6 | 1.6 | 2F3250F09205416495E35CCCE1399F18 |  | R22 | Non-TXV |  | 3.879% | 0.96121 | 7.454% | [5 empty] | Non-TXV | 3.879%
San Andreas | CA | 95249-0000 |  | 2013-08-20 | 2013-08-20 11:13 | 2013-08-20 11:37 | RHEEM - RRNL-B048CK10E | 161 | 5.8 | Yes | Yes | 24.8 | 20.4 | 4.4 | ED4D5AE083E74E8399BCD6A2D806397F |  | R410A | Non-TXV |  | 3.602% | 0.96398 | 6.923% | [5 empty] | Non-TXV | 3.602%
Clovis | CA | 93612-2465 |  | 2013-06-19 | 2013-06-19 15:55 | 2013-06-19 16:17 | BDP - 565BJX030000AAAA | 72 | 20 | Yes | Yes | 19.2 | 20.8 | -1.6 | 74DED556DD9A4580A6AE093086EB6431 |  | R22 | Non-TXV |  | 27.78% | 0.72222 | 53.38% | [5 empty] | Non-TXV | 27.78%
Fresno | CA | 93710-7833 |  | 2013-06-11 | 2013-06-11 09:51 | 2013-06-11 09:51 | AMERICAN STANDARD - YCC030F1MOBG | 66 | 0 | Yes | Yes | 19.7 | 21 | -1.3 | 1A398C4455304E9B928716D6CF7C6727 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-7124 |  | 2013-08-28 | 2013-08-28 11:52 | 2013-08-28 12:15 | YORK - H4DB 036S06A | 73 | -6.9 | Yes | Yes | 20 | 21.3 | -1.3 | 77C0570161A54F2191B66EA02A031193 |  | R22 | Non-TXV |  | -9.452% | 1.0945 | 2.647% |  |  |  |  | Non-TXV |  |  | -9.452%
Stockton | CA | 95206-2414 |  | 2013-06-20 | 2013-06-20 13:11 | 2013-06-20 13:34 | LENNOX - UNK | 85 | 6.1 | Yes | Yes | 26.7 | 21.5 | 5.2 | 902C988EF3F3433586FB75C0887B8FC6 |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Stockton | CA | 95205-3355 |  | 2013-07-12 | 2013-07-12 14:50 | 2013-07-12 15:13 | WHIRLPOOL - UNK | 85 | 8 | Yes | Yes | 26.1 | 20.1 | 6 | 2D6ED2087CBE45D19262F0B1F04BFC25 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Paradise | CA | 95969-3130 |  | 2013-07-15 | 2013-07-15 14:46 | 2013-07-15 14:46 | DAY & NIGHT - N4A318KB200 | 53 | 0 | Yes | Yes | 19.5 | 19.6 | -0.1 | BCEC710CD6EF422C815D93336D6BA3F3 |  | R410A | TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-2935 |  | 2013-06-12 | 2013-06-12 20:15 | 2013-06-12 20:32 | CARRIER - 38CKC030340 | 72 | 9.2 | Yes | Yes | 19.1 | 19.5 | -0.4 | 5E4DB33CC96B4405AE5B2556A24B22D9 |  | R22 | Non-TXV |  | 12.78% | 0.87222 | 24.56% | [5 empty] | Non-TXV | 12.78%
Clovis | CA | 93612-2343 |  | 2013-06-17 | 2013-06-17 14:10 | 2013-06-17 14:10 | PAYNE - PYG3NAA36060NA | 100 | 0 | Yes | Yes | 26.8 | 22.1 | 4.7 | 1111A61C03754791ACC10976CEE9587F | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-9229 |  | 2013-06-04 | 2013-06-04 14:39 | 2013-06-04 14:45 | NORDYNE - JS5BD042K | 170 | 9 | Yes | Yes | 20.6 | 18.5 | 2.1 | 6A6AE1C4712242F3882CC11F9ADE5B94 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Red Bluff | CA | 96080-2039 |  | 2013-06-15 | 2013-06-15 09:23 | 2013-06-15 10:08 | NORDYNE - R4GE-X48K120X | 224 | 8.8 | Yes | Yes | 21 | 19.3 | 1.7 | 91355FF1279A4C31BBE08A395B61C0BD |  | R410A | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Oakdale | CA | 95361-3627 |  | 2013-07-10 | 2013-07-10 12:56 | 2013-07-10 13:22 | DAY & NIGHT - 584BNW036080B | 80 | 2.5 | Yes | Yes | 18.1 | 20.4 | -2.3 | DF49444BA6D64F93833B39AD6E4521AB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93710-7125 |  | 2013-06-27 | 2013-06-27 14:51 | 2013-06-27 14:57 | AMANA - SRCF36U01D | 118 | 3.7 | Yes | Yes | 24.3 | 20.1 | 4.2 | 4FF034E7B9E64C3DA594F568D06A4118 |  | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Merced | CA | 95348-1642 |  | 2013-08-13 | 2013-08-13 16:29 | 2013-08-13 16:29 | OTHER - 7777UNK | 74 | 0 | Yes | Yes | 18.6 | 20.6 | -2 | F74C5DC4DACB41DDA64D588F3BB1AB09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-4755 |  | 2013-08-06 | 2013-08-06 11:42 | 2013-08-06 12:00 | BRYANT - 561J030 | 76 | 3.3 | Yes | Yes | 20.1 | 19.4 | 0.7 | 214432A316F14787ACF8D321FD1ED639 |  | R22 | Non-TXV |  | 4.342% | 0.95658 | 8.345% | [5 empty] | Non-TXV | 4.342%
Marysville | CA | 95901-4444 |  | 2013-06-27 | 2013-06-27 13:56 | 2013-06-27 14:20 | TEMPSTAR - PGAA36C1K3 | 81 | 4.2 | Yes | Yes | 15 | 17.9 | -2.9 | CCBE5FDEE61D4788A6BF416B32C52676 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Newcastle | CA | 95658-9426 |  | 2013-08-08 | 2013-08-08 15:35 | 2013-08-08 15:35 | AMANA - RCE48C2C | 185 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | 739559B17C4A43E49A64BCDC5B5BDD26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-3229 |  | 2013-06-14 | 2013-06-14 09:18 | 2013-06-14 09:36 | RHEEM - RACA-018AAQ | 34 | -8 | Yes | Yes | 23.3 | 18.7 | 4.6 | 7254EE1DFDF74626AE4805817987E37A |  | R22 | Non-TXV |  | -23.53% | 1.2353 | 6.589% |  |  |  |  | Non-TXV |  |  | -23.53%
Sonora | CA | 95370-9702 |  | 2013-07-31 | 2013-07-31 09:02 | 2013-07-31 09:32 | YORK - H2CB048S06A | 162 | 15.1 | Yes | Yes | 25.6 | 20.1 | 5.5 | 407EA21E3B224453A98ACB5674C284BF |  | R22 | Non-TXV |  | 9.321% | 0.90679 | 17.91% | [5 empty] | Non-TXV | 9.321%
Atwater | CA | 95301-4062 |  | 2013-07-10 | 2013-07-10 10:23 | 2013-07-10 10:24 | GOODMAN - GPG1324-451BA | 77 | 5.3 | Yes | Yes | 21 | 19.6 | 1.4 | EABFD3C44EC94DFE8033684CEC752949 |  | R22 | Non-TXV |  | 6.883% | 0.93117 | 13.23% | [5 empty] | Non-TXV | 6.883%
Paso Robles | CA | 93446-4756 |  | 2013-08-12 | 2013-08-12 12:48 | 2013-08-12 13:09 | BRYANT - 561CJX030000ADAA | 85 | 9.1 | Yes | Yes | 25.6 | 21.8 | 3.8 | 1BFF38C1331C4CFFBBF7593E9B803C28 |  | R22 | Non-TXV |  | 10.71% | 0.89294 | 20.57% | [5 empty] | Non-TXV | 10.71%
Fresno | CA | 93711-0583 |  | 2013-06-21 | 2013-06-21 13:47 | 2013-06-22 04:28 | CARRIER - 38EN03600 | 95 | 4.5 | Yes | Yes | 18.6 | 21.4 | -2.8 | A2F12E816E674026A4DA0A637B2E20F9 |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Paradise | CA | 95969-3242 |  | 2013-06-12 | 2013-06-12 19:08 | 2013-06-12 19:08 | RHEEM - RRNA-B042JK08E | 104 | 0 | Yes | Yes | 18.7 | 14.7 | 4 | C34B156040D84B2EBB9206FC01C86598 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-2031 |  | 2013-06-20 | 2013-06-20 08:17 | 2013-06-20 08:38 | GOODMAN - CKJ60-1 | 142 | -11.7 | Yes | Yes | 18.3 | 19.7 | -1.4 | 5275BCBDC7814E56A29946B2648FC4B8 |  | R22 | Non-TXV |  | -8.239% | 1.0824 | 2.307% |  |  |  |  | Non-TXV |  |  | -8.239%
Merced | CA | 95348-1684 |  | 2013-06-14 | 2013-06-14 08:27 | 2013-06-14 08:33 | YORK - UNK | 58 | 8.2 | Yes | Yes | 25.1 | 19.1 | 6 | 4B8959187B1541D1B11DA817880E1B35 |  | R22 | Non-TXV |  | 14.14% | 0.85862 | 27.17% | [5 empty] | Non-TXV | 14.14%
Los Banos | CA | 93635-5427 |  | 2013-06-01 | 2013-06-01 08:32 | 2013-06-01 08:40 | BDP - 561AJ024B | 56 | 5.9 | Yes | Yes | 27.9 | 22 | 5.9 | 836DC63612D24738B8FB8F0E398A3700 |  | R22 | TXV |  | 10.54% | 0.89464 | 20.25% | [5 empty] | TXV | 10.54%
Livingston | CA | 95334-1140 |  | 2013-06-10 | 2013-06-10 09:43 | 2013-06-10 09:43 | RHEEM - RRNL-B036JK06X | 93 | 0 | Yes | Yes | 21.4 | 18.6 | 2.8 | 422F50B5FD03466AABE83E91B6A6A9A1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-2658 |  | 2013-07-12 | 2013-07-12 12:39 | 2013-07-12 12:56 | PAYNE - 591ANX042000ABAA | 112 | 4.2 | Yes | Yes | 19.2 | 20.4 | -1.2 | EFBF5BAB481645949729E5A7E9446A6C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Fresno | CA | 93703-1230 |  | 2013-05-28 | 2013-05-28 22:51 | 2013-05-28 22:51 | BRYANT - 58ANW036090ABAF | 85 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | 5973BE1CEEAB4F54B859E090B9F544D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-9636 |  | 2013-07-30 | 2013-07-30 13:55 | 2013-07-30 14:53 | LENNOX - 13ACD-048-230-03 | 152 | 7.9 | Yes | Yes | 17.3 | 20.1 | -2.8 | F74EC4528C41465A8C7ACB313E7AE3AA |  | R22 | Non-TXV |  | 5.197% | 0.94803 | 9.988% | [5 empty] | Non-TXV | 5.197%
Fresno | CA | 93728-3833 |  | 2013-06-19 | 2013-06-19 12:23 | 2013-06-19 12:27 | COPELAND - GSX130601BA | 125 | 4.5 | Yes | Yes | 20.3 | 19.6 | 0.7 | E523D5B5CD9749849584D27FF10D72B0 |  | R410A | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Fresno | CA | 93710-7121 |  | 2013-06-04 | 2013-06-04 11:28 | 2013-06-04 11:48 | GOODMAN - GPG13420701AA | 107 | -6.3 | Yes | Yes | 21.8 | 20.2 | 1.6 | A155D23E5FCC4F2BA531F1CBB886F088 |  | R22 | Non-TXV |  | -5.888% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.888%
Fresno | CA | 93705-2429 |  | 2013-06-20 | 2013-06-20 13:22 | 2013-06-20 13:24 | PAYNE - UNK | 58 | 7.7 | Yes | Yes | 23 | 21 | 2 | 364E69D7C2B74DC18349415784EC06A5 |  | R22 | Non-TXV |  | 13.28% | 0.86724 | 25.51% | [5 empty] | Non-TXV | 13.28%
Marysville | CA | 95901-4601 |  | 2013-07-11 | 2013-07-11 13:38 | 2013-07-11 13:54 | LENNOX - 12GCS036X-75-5PB | 110 | 4.3 | Yes | Yes | 23 | 20.1 | 2.9 | 8C38377203B24FFEBEA34846BCB3A3EE |  | R22 | TXV |  | 3.909% | 0.96091 | 7.512% | [5 empty] | TXV | 3.909%
Marysville | CA | 95901-3621 |  | 2013-06-27 | 2013-06-27 10:55 | 2013-06-27 11:17 | DAY & NIGHT - 585HJ024040ABAE | 68 | 5 | Yes | Yes | 20 | 17.9 | 2.1 | C5C774DA0DED426D822E95A8704EDDC0 |  | R22 | Non-TXV |  | 7.353% | 0.92647 | 14.13% | [5 empty] | Non-TXV | 7.353%
Mendota | CA | 93640-4011 |  | 2013-08-21 | 2013-08-21 12:47 | 2013-08-21 12:49 | BRYANT - 113RNA36-B | 93 | 5.3 | Yes | Yes | 26.1 | 20.2 | 6 | BF7D173DC1EC4A439F624976FF74022C |  | R22 | Non-TXV |  | 5.699% | 0.94301 | 10.95% | [5 empty] | Non-TXV | 5.699%
Fresno | CA | 93706-5948 |  | 2013-07-18 | 2013-07-18 11:17 | 2013-07-18 11:20 | DAY & NIGHT - 7777UNK | 100 | 3.2 | Yes | Yes | 16.9 | 19.8 | -2.9 | 0C4659FEB79A42ED9AB291894CFE8744 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Mendota | CA | 93640-4012 |  | 2013-08-21 | 2013-08-21 12:17 | 2013-08-21 12:19 | BRYANT - 7777UNK | 84 | 2.8 | Yes | Yes | 23 | 19.8 | 3.3 | 0C6198F37EBE4E12A5C0A8512910A8A0 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93706-5924 |  | 2013-07-17 | 2013-07-17 12:06 | 2013-07-17 12:14 | CARRIER - 38BRB036300 | 122 | 4.4 | Yes | Yes | 19.9 | 18.2 | 1.7 | 70AAA6963629474692CD0404D69F08FA |  | R22 | Non-TXV |  | 3.607% | 0.96393 | 6.931% | [5 empty] | Non-TXV | 3.607%
Fresno | CA | 93710-5304 |  | 2013-06-07 | 2013-06-07 16:51 | 2013-06-07 16:51 | RHEEM - HC-80-36-210 | 108 | 0 | Yes | Yes | 20.3 | 21 | -0.7 | CD905CD775B64F50BE31B93BE70A0786 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-7217 |  | 2013-07-10 | 2013-07-10 13:58 | 2013-07-10 14:30 | CARRIER - UNK | 81 | 3.4 | Yes | Yes | 27.6 | 22.1 | 5.5 | 2D20F0EF5F964285A5264CB7BA99CF7C |  | R22 | Non-TXV |  | 4.198% | 0.95802 | 8.067% | [5 empty] | Non-TXV | 4.198%
Fresno | CA | 93722-1121 |  | 2013-06-20 | 2013-06-20 22:06 | 2013-06-20 23:30 | CARRIER - UNK | 81 | 2.8 | Yes | Yes | 19.7 | 20.4 | -0.7 | C8004CB70BC54D6E8E42F2D07B43E2F2 |  | R22 | Non-TXV |  | 3.457% | 0.96543 | 6.643% | [5 empty] | Non-TXV | 3.457%
Fresno | CA | 93720-0117 |  | 2013-06-26 | 2013-06-26 10:41 | 2013-06-26 10:46 | RHEEM - RAKB-036JAZ | 79 | 2.6 | Yes | Yes | 17.5 | 19.2 | -1.6 | 4FDF1412A89B438CB1EE0988D6A943B2 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Fresno | CA | 93705-2013 |  | 2013-06-24 | 2013-06-24 12:29 | 2013-06-24 12:34 | YORK - D1NH036N05606C | 108 | 6.5 | Yes | Yes | 22.1 | 18.6 | 3.5 | C8B6C8047D9B4AD09BFF830C6E380753 |  | R22 | Non-TXV |  | 6.019% | 0.93981 | 11.57% | [5 empty] | Non-TXV | 6.019%
Stockton | CA | 95210-3671 |  | 2013-06-17 | 2013-06-17 12:54 | 2013-06-17 13:18 | PAYNE - 591ANX036000AAAA | 92 | -5.4 | Yes | Yes | 24.6 | 20.4 | 4.2 | 7BF83CF6BCC54924BB3A4E466BEA390D |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Fresno | CA | 93726-3411 |  | 2013-06-01 | 2013-06-01 11:16 | 2013-06-01 11:52 | YORK - D3CG036N08206D | 94 | 2.9 | Yes | Yes | 23 | 20.1 | 2.9 | FC77C32051DB405FB9910CFDB8063027 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.085% | 0.96915 | 5.929% | [5 empty] | Non-TXV | 3.085%
Marysville | CA | 95901-3624 |  | 2013-08-20 | 2013-08-20 13:24 | 2013-08-20 14:09 | PAYNE - PA133NR042-E | 150 | 8.8 | Yes | Yes | 21 | 19.3 | 1.7 | 1EAB5D37750949E28CC1FD1B4CED0E79 |  | R22 | TXV |  | 5.867% | 0.94133 | 11.27% | [5 empty] | TXV | 5.867%
Fresno | CA | 93705-1743 |  | 2013-06-24 | 2013-06-24 11:32 | 2013-06-24 11:36 | CARRIER - 48GS036090311 | 68 | 5.2 | Yes | Yes | 23.2 | 18.5 | 4.7 | BB5DE1B37DDE443D86DCC82DE9795B9F |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Arbuckle | CA | 95912-9724 |  | 2013-07-31 | 2013-07-31 12:52 | 2013-07-31 13:10 | AMERICAN STANDARD - 4TTB3060D1000BA | 128 | -5.6 | Yes | Yes | 23 | 19.1 | 3.9 | CB076739222149C4AECEF4422F08A393 |  | R410A | TXV |  | -4.375% | 1.0437 | 1.225% |  |  |  |  | TXV |  |  | -4.375%
Fresno | CA | 93710-6331 |  | 2013-06-24 | 2013-06-24 13:00 | 2013-06-24 13:00 | HEIL - NRGHA23DB01 | 89 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | 26710815AC074787A4D3DDEFC5F79945 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1851 |  | 2013-08-06 | 2013-08-06 15:17 | 2013-08-06 15:23 | OTHER - DRCS0481BEG | 119 | 3.7 | Yes | Yes | 27.6 | 23 | 4.6 | 7D47ADB2DB83429F81DEBA2E559E693C |  | R22 | Non-TXV |  | 3.109% | 0.96891 | 5.975% | [5 empty] | Non-TXV | 3.109%
Merced | CA | 95340-1315 |  | 2013-06-17 | 2013-06-17 10:38 | 2013-06-17 11:04 | GE - BTB824A100A | 43 | 7.1 | Yes | Yes | 19.6 | 19.9 | -0.3 | 1367D4D66F0041068072DC7C27418D4E |  | R22 | Non-TXV |  | 16.51% | 0.83488 | 31.73% | [5 empty] | Non-TXV | 16.51%
Chico | CA | 95928-6471 |  | 2013-08-06 | 2013-08-06 13:07 | 2013-08-06 13:26 | BDP - 585CJ02450 | 72 | 5.7 | Yes | Yes | 20.1 | 19.6 | 0.6 | E27FD210847642008DDBF4561C0F11B9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.917% | 0.92083 | 15.21% | [5 empty] | Non-TXV | 7.917%
Fresno | CA | 93725-1842 |  | 2013-06-20 | 2013-06-20 13:45 | 2013-06-20 13:49 | GOODMAN - GSC130421AA | 148 | 4.4 | Yes | Yes | 23.5 | 23.5 | 0 | 8605EC37960C48F38912AACB94AAC76B |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Pine Grove | CA | 95665-0000 |  | 2013-08-13 | 2013-08-13 14:39 | 2013-08-13 15:10 | PAYNE - PA13NR030-K | 75 | 2.7 | Yes | Yes | 16.5 | 19.1 | -2.6 | D1436C817D194D25A022EE533F48D6AE |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 16:58 | 2013-07-30 17:38 | CARRIER - 38TKB030300 | 70 | 2.6 | Yes | Yes | 25 | 21.2 | 3.8 | 350B23FA3D9C45158B2EB5B4DCCD5510 |  | R22 | TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | TXV | 3.714%
Yuba City | CA | 95991-8318 |  | 2013-07-15 | 2013-07-15 11:07 | 2013-07-15 11:37 | LENNOX - 10ACC-048-230-02 | 99 | 11.2 | Yes | Yes | 19 | 19.3 | -0.3 | 188C6CAD61654A78A108FB0DEB7B85F6 |  | R22 | Non-TXV |  | 11.31% | 0.88687 | 21.74% | [5 empty] | Non-TXV | 11.31%
Fresno | CA | 93726-1511 |  | 2013-08-16 | 2013-08-16 08:55 | 2013-08-16 09:17 | AMANA - RCB42C2C | 90 | 10 | Yes | Yes | 21.8 | 19.2 | 2.6 | FA9CBA9D79E64BE19E5A5F8BC128BBF8 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Fresno | CA | 93725-1851 |  | 2013-06-21 | 2013-06-21 10:44 | 2013-06-21 10:44 | LENNOX - 10ACB48-5P | 99 | 0 | Yes | Yes | 21.9 | 23.1 | -1.2 | 559D56CA8E764545881D57A480BECBA2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-4069 |  | 2013-07-30 | 2013-07-30 14:45 | 2013-07-30 15:28 | WEATHER KING - 13AJA30A01 | 98 | 3.1 | Yes | Yes | 18.5 | 20.8 | -2.3 | 610908519BEC43A89410F8D9C4E99450 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.163% | 0.96837 | 6.079% | [5 empty] | Non-TXV | 3.163%
Selma | CA | 93662-4801 |  | 2013-07-31 | 2013-07-31 16:57 | 2013-07-31 17:28 | ICP - PGAD30D1KA3 | 78 | 8.6 | Yes | Yes | 20.9 | 19.8 | 1.1 | 070F6BD17ABA4503B2E369BEEC495061 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.03% | 0.88974 | 21.19% | [5 empty] | Non-TXV | 11.03%
Grass Valley | CA | 95949-7341 |  | 2013-10-23 | 2013-10-23 16:56 | 2013-10-23 17:35 | RUUD - URKA-A042JK10E | 69 | 17.6 | Yes | Yes | 26.4 | 20.9 | 5.5 | B24385988919492281740952D1878A30 |  | R22 | Non-TXV |  | 25.51% | 0.74493 | 49.02% | [5 empty] | Non-TXV | 25.51%
Fresno | CA | 93725-1842 |  | 2013-09-10 | 2013-09-10 12:21 | 2013-09-10 12:22 | UNITARY PRODUCTS GROUP - HBBD-F036SB | 96 | 5.3 | Yes | Yes | 18 | 20.7 | -2.7 | FA912FAE4825456E907132A7D2839820 |  | R22 | Non-TXV |  | 5.521% | 0.94479 | 10.61% | [5 empty] | Non-TXV | 5.521%
Fresno | CA | 93703-3596 |  | 2013-08-08 | 2013-08-08 13:20 | 2013-08-08 13:21 | GOODMAN - GPG0300701A | 50 | 6.2 | Yes | Yes | 19.9 | 16.8 | 3.1 | 5DD57E60DA124A5ABC568BCEA0665C03 |  | R22 | Non-TXV |  | 12.4% | 0.876 | 23.83% | [5 empty] | Non-TXV | 12.4%
Cameron Park | CA | 95682-9223 |  | 2013-06-13 | 2013-06-13 13:56 | 2013-06-13 14:23 | PAYNE - PH13NA036-B | 100 | -8.2 | Yes | Yes | 21.6 | 20.2 | 1.5 | 46F6B97D8310464C9DEC36DEDA3DC041 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | -8.2% | 1.082 | 2.296% |  |  |  |  | Non-TXV |  |  | -8.2%
Tracy | CA | 95376-9621 |  | 2013-07-11 | 2013-07-11 10:15 | 2013-07-11 10:40 | RHEEM - RAFD-048JBS | 85 | 10.4 | Yes | Yes | 18.7 | 19.9 | -1.2 | CB4EA353437D440FA59939AAE691DE69 |  | R22 | Non-TXV |  | 12.24% | 0.87765 | 23.51% | [5 empty] | Non-TXV | 12.24%
Fresno | CA | 93705-3359 |  | 2013-08-02 | 2013-08-02 13:23 | 2013-08-02 13:44 | BDP - 58A030080YAC | 50 | 1.6 | Yes | Yes | 16.2 | 19 | -2.8 | 4979849BF33F4631992CE09371D2A00C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93727-2297 |  | 2013-06-08 | 2013-06-08 11:29 | 2013-06-08 11:48 | BDP - 598N036-B | 197 | 13.2 | Yes | Yes | 24.5 | 20.8 | 3.7 | 51BE320730074C2D9FD6E8035D12D3F1 |  | R22 | TXV |  | 6.701% | 0.93299 | 12.88% | [5 empty] | TXV | 6.701%
Olivehurst | CA | 95961-4218 |  | 2013-06-28 | 2013-06-28 08:21 | 2013-06-28 08:40 | AMANA - PGD30C0702D | 74 | 2.2 | Yes | Yes | 21 | 17.5 | 3.5 | 62A4F94F9FEC47FD993198DF495BE736 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Dinuba | CA | 93618-2003 |  | 2013-06-20 | 2013-06-20 13:58 | 2013-06-20 13:58 | RHEEM - RRPL-B042JK08X | 112 | 0 | Yes | Yes | 20.1 | 20.2 | -0.1 | E3256A8FAC7A4E929F2F0DC751B20276 |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3206 |  | 2013-06-27 | 2013-06-27 15:02 | 2013-06-27 15:07 | GOODMAN - CLJ421B | 84 | 10.7 | Yes | Yes | 19.3 | 20.2 | -0.9 | B2071CB7BBC241C59EB8CC272D4BB710 |  | R22 | Non-TXV |  | 12.74% | 0.87262 | 24.48% | [5 empty] | Non-TXV | 12.74%
Fresno | CA | 93701-0000 |  | 2013-07-12 | 2013-07-12 10:56 | 2013-07-12 10:59 | GOODMAN - GSC130301DA | 87 | 3.2 | Yes | Yes | 17 | 17.6 | -0.6 | 360E3E50D05C4F2C8A58CB2BB3453E38 |  | R22 | Non-TXV |  | 3.678% | 0.96322 | 7.069% | [5 empty] | Non-TXV | 3.678%
Rocklin | CA | 95677-2922 |  | 2013-06-17 | 2013-06-17 12:46 | 2013-06-17 13:13 | OTHER - TZAA-342-2A | 121 | 3.6 | Yes | Yes | 20 | 20.4 | -0.4 | 43277C75DD82476E97E1E41A252FC620 |  | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.718% | [5 empty] | Non-TXV | 2.975%
Oroville | CA | 95966-9446 |  | 2013-06-20 | 2013-06-20 18:54 | 2013-06-20 19:10 | OTHER - MX230TN2 | 138 | 4.2 | Yes | Yes | 25 | 20.4 | 4.6 | 3DA52AE75BF4460F91CF0013DA2820AB |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Parlier | CA | 93648-2632 |  | 2013-08-28 | 2013-08-28 10:15 | 2013-08-28 10:46 | GOODMAN - PGB048075-1 | 86 | 4.2 | Yes | Yes | 20.6 | 20.4 | 0.2 | 9D04AD829D67436DB0023F7ECA626D32 |  | R22 | Non-TXV |  | 4.884% | 0.95116 | 9.385% | [5 empty] | Non-TXV | 4.884%
Fresno | CA | 93705-2322 |  | 2013-06-18 | 2013-06-18 12:03 | 2013-06-18 12:14 | CARRIER - 48DL004 | 70 | 6.9 | Yes | Yes | 18.5 | 15.2 | 3.3 | 54AB1DEE896F41BEBCBE0D961B1F2D2E |  | R22 | Non-TXV |  | 9.857% | 0.90143 | 18.94% | [5 empty] | Non-TXV | 9.857%
Fresno | CA | 93720-2444 |  | 2013-06-24 | 2013-06-24 12:32 | 2013-06-24 12:36 | AIRE-FLO - TGCD60S41S3A | 86 | 4.6 | Yes | Yes | 25.4 | 20.4 | 5 | 1DEFA997C9C644BA9A11B64740CC8218 |  | R410A | Non-TXV |  | 5.349% | 0.94651 | 10.28% | [5 empty] | Non-TXV | 5.349%
Pine Grove | CA | 95665-9677 |  | 2013-08-09 | 2013-08-09 15:53 | 2013-08-09 15:53 | RHEEM - RPNA-025J 000 | 54 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 80460C7616F84270922D8C4628E2C8F2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Pine Grove | CA | 95665-9677 |  | 2013-08-09 | 2013-08-09 16:10 | 2013-08-09 16:38 | RHEEM - UNK | 96 | 11.4 | Yes | Yes | 28 | 22.6 | 5.4 | BB63C406224B45C3903E89D9DD4793AA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.88% | 0.88125 | 22.82% | [5 empty] | Non-TXV | 11.88%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 15:04 | 2013-07-30 15:32 | LUXAIRE - TCGD36S21S1HA | 65 | 2.4 | Yes | Yes | 23 | 19.9 | 3.1 | F175CBAA4CD3461BBD8502CD1EF20F45 |  | R22 | TXV |  | 3.692% | 0.96308 | 7.096% | [5 empty] | TXV | 3.692%
Riverbank | CA | 95367-2820 |  | 2013-06-11 | 2013-06-11 10:13 | 2013-06-11 10:32 | - 1E030BA00N | 145 | 8.7 | Yes | Yes | 19.7 | 19.2 | 0.5 | 67B886D6A1D44CEEBD805C79B717C223 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Parlier | CA | 93648-2616 |  | 2013-08-07 | 2013-08-07 16:58 | 2013-08-07 17:49 | GOODMAN - GPG1336045M41CA | 108 | 4.6 | Yes | Yes | 19 | 20.2 | -1.2 | 9C5578D407AC4235B1257FA45F702B53 |  | R410A | TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | TXV | 4.259%
Fresno | CA | 93728-2212 |  | 2013-06-19 | 2013-06-19 11:49 | 2013-06-19 11:52 | DAY & NIGHT - 585GJ048080 | 86 | 3.8 | Yes | Yes | 23.8 | 20.4 | 3.4 | 6DD4ACA3DC4346AFB8DDA257A46B16BD |  | R22 | Non-TXV |  | 4.419% | 0.95581 | 8.492% | [5 empty] | Non-TXV | 4.419%
Riverbank | CA | 95367-2322 |  | 2013-07-11 | 2013-07-11 14:12 | 2013-07-11 14:33 | BDP - 563CN0X48000ACAA | 165 | 4.9 | Yes | Yes | 26.3 | 20.4 | 5.9 | 3E0A30B9C73C4D408ACDCDAE57BC06D3 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.707% | [5 empty] | Non-TXV | 2.97%
Fresno | CA | 93705-3820 |  | 2013-06-18 | 2013-06-18 13:23 | 2013-06-18 13:31 | AIRE-FLO - 38CKC036350 | 70 | 7.1 | Yes | Yes | 17.9 | 20.4 | -2.5 | B91FB293D4C94B6785209B8FE998B1E5 |  | R22 | TXV |  | 10.14% | 0.89857 | 19.49% | [5 empty] | TXV | 10.14%
Fresno | CA | 93723-8113 |  | 2013-06-24 | 2013-06-24 10:58 | 2013-06-24 11:04 | LENNOX - 13ACC048230 | 158 | 7.2 | Yes | Yes | 24.4 | 19.3 | 5.1 | 584ACCE110F94040BA4361FC17179AFA |  | R22 | Non-TXV |  | 4.557% | 0.95443 | 8.757% | [5 empty] | Non-TXV | 4.557%
Fresno | CA | 93722-5458 |  | 2013-07-16 | 2013-07-16 18:26 | 2013-07-16 18:47 | COLEMAN - N/A | 120 | 14.4 | Yes | Yes | 22.5 | 19.8 | 2.8 | 5CE9E7D202884213992C66B567488E5A | Add refrigerant: 10.3 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Placerville | CA | 95667-7966 |  | 2013-09-03 | 2013-09-03 13:55 | 2013-09-03 14:14 | GOODMAN - CK30-1B | 76 | 6.7 | Yes | Yes | 25.7 | 22.5 | 3.2 | BBE87A1361A745C1822C35487211D94B |  | R22 | Non-TXV |  | 8.816% | 0.91184 | 16.94% | [5 empty] | Non-TXV | 8.816%
Stockton | CA | 95206-4777 |  | 2013-07-12 | 2013-07-12 09:40 | 2013-07-12 10:10 | RHEEM - RAKA-036JAS | 75 | 8.6 | Yes | Yes | 23.8 | 18.2 | 5.6 | 74845C562AB64BDE8FF82E37003D62B7 |  | R22 | Non-TXV |  | 11.47% | 0.88533 | 22.04% | [5 empty] | Non-TXV | 11.47%
San Joaquin | CA | 93660-0000 |  | 2013-08-15 | 2013-08-15 13:46 | 2013-08-15 15:55 | CARRIER - 48SS--030040311 | 53 | 2 | Yes | Yes | 19.2 | 21.5 | -2.3 | 37465E62546140C08BAB546C55FCBC4D |  | R22 | Non-TXV |  | 3.774% | 0.96226 | 7.252% | [5 empty] | Non-TXV | 3.774%
Grass Valley | CA | 95949-6591 |  | 2013-06-13 | 2013-06-13 11:15 | 2013-06-13 11:35 | GE - UNK | 85 | 2.6 | Yes | Yes | 20 | 18.7 | 1.3 | 8868F9B7CF3E4173B3B46516433E7556 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93726-2626 |  | 2013-06-03 | 2013-06-03 12:20 | 2013-06-03 12:24 | AMERICAN STANDARD - YCC036F1M0BJ | 83 | 7.9 | Yes | Yes | 20 | 20 | 0.1 | 3F3402F1C98B4468B07F52D93EBDA9A0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.518% | 0.90482 | 18.29% | [5 empty] | Non-TXV | 9.518%
Grass Valley | CA | 95945-7557 |  | 2013-06-22 | 2013-06-22 12:36 | 2013-06-22 12:36 | OTHER - UNK | 70 | 9.8 | Yes | Yes | 19 | 20.4 | -1.4 | 53923C5FC6274D678B9708D414E43DD6 | Add refrigerant: 9.8 oz | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Stockton | CA | 95210-1790 |  | 2013-06-11 | 2013-06-11 10:40 | 2013-06-11 11:02 | LUXAIRE - 60WE24G1 | 55 | 1.9 | Yes | Yes | 16.4 | 18.2 | -1.8 | B88356AEC3A2418096F61CD3ACC8B365 |  | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Yuba City | CA | 95993-8012 |  | 2013-10-31 | 2013-10-31 12:37 | 2013-10-31 12:59 | OTHER - 77CD024300 | 76 | 2.8 | Yes | Yes | 19 | 19.5 | -0.5 | 728AB1D2FEE14ACD917B6F6445844D54 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Stockton | CA | 95206-5528 |  | 2013-06-26 | 2013-06-26 09:18 | 2013-06-26 09:42 | PAYNE - 591ANX060000AAAA | 222 | 6.8 | Yes | Yes | 24.4 | 18.5 | 5.9 | 5EE226CC5D9042D0BC73360F85CBA6CE |  | R22 | Non-TXV |  | 3.063% | 0.96937 | 5.887% | [5 empty] | Non-TXV | 3.063%
Fresno | CA | 93706-5916 |  | 2013-07-17 | 2013-07-17 13:01 | 2013-07-17 13:03 | OTHER - 7777UNK | 100 | 4.3 | Yes | Yes | 23.4 | 18.7 | 4.7 | 25F3D596163E4FDF82F93D5315F185C1 |  | R22 | Non-TXV |  | 4.3% | 0.957 | 8.264% | [5 empty] | Non-TXV | 4.3%
Willows | CA | 95988-3044 |  | 2013-06-27 | 2013-06-27 18:43 | 2013-06-27 19:01 | YORK - D1NH036N05606C | 108 | 13.8 | Yes | Yes | 21.7 | 20.1 | 1.6 | 273EC5FEBD9043049A829AA046B2C189 |  | R22 | Non-TXV |  | 12.78% | 0.87222 | 24.56% | [5 empty] | Non-TXV | 12.78%
Selma | CA | 93662-3313 |  | 2013-07-31 | 2013-07-31 11:56 | 2013-07-31 12:15 | GOODMAN - CK36-1A | 73 | 6 | Yes | Yes | 18.8 | 20.6 | -1.8 | 292F7F7171A64094B7AF8FDF220432C8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.219% | 0.91781 | 15.8% | [5 empty] | Non-TXV | 8.219%
Stockton | CA | 95210-1790 |  | 2013-06-11 | 2013-06-11 11:52 | 2013-06-11 12:15 | LUXAIRE - 60NE24G1 | 55 | 2.5 | Yes | Yes | 17.4 | 19.2 | -1.8 | 4F1E2E6341494D158427DD6176CC0B42 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93705-2427 |  | 2013-06-24 | 2013-06-24 13:59 | 2013-06-24 14:09 | GOODMAN - PGB030050 | 56 | 3.7 | Yes | Yes | 24.4 | 18.8 | 5.6 | 6DDAA0BE6BF44C56954FB86410F36CE1 |  | R22 | Non-TXV |  | 6.607% | 0.93393 | 12.7% | [5 empty] | Non-TXV | 6.607%
Stockton | CA | 95207-6917 |  | 2013-07-29 | 2013-07-29 09:16 | 2013-07-29 09:16 | RHEEM - HC-80-30-21CC03 | 48 | 0 | Yes | Yes | 21.4 | 18.2 | 3.2 | 8BBDCB25B06E45C5B2B3D4A117EE67D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3302 |  | 2013-05-30 | 2013-05-30 11:29 | 2013-05-30 11:31 | AIRE-FLO - YCY036F1MOAA | 136 | 12.5 | Yes | Yes | 19.6 | 20.3 | -0.7 | 55D6C75DD8804163949E18581948D242 |  | R22 | Non-TXV |  | 9.191% | 0.90809 | 17.66% | [5 empty] | Non-TXV | 9.191%
Stockton | CA | 95206-2517 |  | 2013-06-12 | 2013-06-12 10:06 | 2013-06-12 10:33 | YORK - GCGD36S21S2B | 85 | 12.1 | Yes | Yes | 19.2 | 18.8 | 0.4 | 7D1F9853BE24487B858FE3BD75E6EE44 |  | R22 | Non-TXV |  | 14.24% | 0.85765 | 27.36% | [5 empty] | Non-TXV | 14.24%
Lathrop | CA | 95330-8836 |  | 2013-06-20 | 2013-06-20 13:08 | 2013-06-20 13:29 | GOODMAN - CLJ30-1C | 105 | 4.8 | Yes | Yes | 20.7 | 21.5 | -0.8 | 105FBF05D5284A6CA057CE261F722564 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Fresno | CA | 93710-4241 |  | 2013-06-07 | 2013-06-07 14:54 | 2013-06-07 14:54 | PAYNE - 80YAC-10-C | 89 | 0 | Yes | Yes | 17.8 | 19.8 | -2 | C8177340FF644758A09E84F58EF17CCD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-0420 |  | 2013-05-28 | 2013-05-28 12:17 | 2013-05-28 12:43 | AMERICAN STANDARD - YCX036G1MOAA | 93 | 2.9 | Yes | Yes | 23.3 | 20.2 | 3.2 | 09E1AF9DF559496CB4AAF5A3C808B052 |  | R22 | Non-TXV |  | 3.118% | 0.96882 | 5.993% | [5 empty] | Non-TXV | 3.118%
Selma | CA | 93662-2103 |  | 2013-09-05 | 2013-09-05 12:13 | 2013-09-05 12:46 | CARRIER - 48SS-036080321 | 67 | 9.7 | Yes | Yes | 17.5 | 20.4 | -2.9 | 0DD56BFAB516419FB71FE1B1A5ECC395 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.48% | 0.85522 | 27.82% | [5 empty] | Non-TXV | 14.48%
Yuba City | CA | 95993-6040 |  | 2013-06-21 | 2013-06-21 13:13 | 2013-06-21 13:13 | LENNOX - HS22-411V-3P | 129 | 0 | Yes | Yes | 20 | 19.2 | 0.8 | 5FA149E6A8ED41AEB1C6A46C4D8D1D0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-8854 |  | 2013-06-20 | 2013-06-20 14:35 | 2013-06-20 15:01 | - 38EZG042 | 88 | 4.6 | Yes | Yes | 19.4 | 20.9 | -1.5 | AF7220DF9AB54B85842EC810A46C5322 |  | R410A | TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | TXV | 5.227%
West Point | CA | 95255-0000 |  | 2013-09-17 | 2013-09-17 10:09 | 2013-09-17 10:24 | BRYANT - 561CJ030-D | 68 | 2.2 | Yes | Yes | 20.4 | 17.6 | 2.8 | 2796FD43388E4520B2C349191BCD51C7 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Stockton | CA | 95212-3430 |  | 2013-06-17 | 2013-06-17 10:56 | 2013-06-17 11:20 | UNITARY PRODUCTS GROUP - AC060X122A | 136 | 4.2 | Yes | Yes | 20 | 20.9 | -0.9 | BB7A90AB51B043B4931CFA47B4BDD9CB |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Fresno | CA | 93727-5827 |  | 2013-06-13 | 2013-06-13 12:32 | 2013-06-13 12:34 | CARRIER - 48SX-048100341AA | 84 | 4.4 | Yes | Yes | 18.4 | 20.4 | -2 | C18A5734E0AE476CB01D2C05565CC63D |  | R22 | Non-TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | Non-TXV | 5.238%
Fresno | CA | 93726-3616 |  | 2013-06-01 | 2013-06-01 17:27 | 2013-06-01 17:27 | YORK - D1NQ036N036NXA | 58 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | 0E707829D3CB43B8A11F05403AA3634B |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2226 |  | 2013-07-17 | 2013-07-17 08:07 | 2013-07-17 08:18 | CARRIER - 38BRC048330 | 164 | 9.1 | Yes | Yes | 22.4 | 20.3 | 2.1 | D90E4E0E3008464B8A03151C9CB76ABC |  | R22 | Non-TXV |  | 5.549% | 0.94451 | 10.66% | [5 empty] | Non-TXV | 5.549%
Merced | CA | 95348-3611 |  | 2013-06-07 | 2013-06-07 14:18 | 2013-06-07 14:21 | GOODMAN - PGB0300501 | 56 | 1.7 | Yes | Yes | 21.6 | 18.6 | 3 | 5037F5A1A0D84E4BAE7F002A4B9D921B |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Clovis | CA | 93612-5747 |  | 2013-07-02 | 2013-07-02 14:47 | 2013-07-02 15:17 | RHEEM - RRGG-05N25JKR | 39 | 2.6 | Yes | Yes | 27.7 | 22.1 | 5.6 | 7B4185DA6CF54003A0710637FB7366D0 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Clovis | CA | 93612-5703 |  | 2013-06-19 | 2013-06-19 13:11 | 2013-06-19 13:29 | YORK - D1NP048N09006A | 132 | 5.6 | Yes | Yes | 24.2 | 21 | 3.2 | 315A3AE76FC74108A79F3449AFE0B31D |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Clovis | CA | 93612-5747 |  | 2013-08-15 | 2013-08-15 14:51 | 2013-08-15 15:40 | RHEEM - RRGG-05N25JKR | 60 | 2.1 | Yes | Yes | 24.5 | 18.7 | 5.9 | 175B6178B904433F86D45FF90A1BF272 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Parlier | CA | 93648-2609 |  | 2013-07-23 | 2013-07-23 19:46 | 2013-07-23 20:45 | GOODMAN - GPG1324045M41AB | 80 | 3.7 | Yes | Yes | 20.7 | 20.1 | 0.6 | 95423CF95B4A41E89EBD8F99D14489C1 |  | R410A | TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | TXV | 4.625%
Clovis | CA | 93612-5701 |  | 2013-06-19 | 2013-06-19 15:03 | 2013-06-19 15:23 | UNITARY PRODUCTS GROUP - H2RE060S06A | 253 | 7.5 | Yes | Yes | 22.6 | 21.4 | 1.2 | 7B6C5A5EA00349E9831E401724E034A9 |  | R22 | Non-TXV |  | 2.964% | 0.97036 | 5.697% | [5 empty] | Non-TXV | 2.964%
Stockton | CA | 95205-7785 |  | 2013-06-12 | 2013-06-12 09:55 | 2013-06-12 10:13 | CARRIER - 38TH024300 | 54 | 7.7 | Yes | Yes | 25.1 | 21 | 4.1 | 34E087F28F6C4A1FA8D5A96F4C832D98 |  | R22 | Non-TXV |  | 14.26% | 0.85741 | 27.4% | [5 empty] | Non-TXV | 14.26%
Yuba City | CA | 95993-9272 |  | 2013-06-21 | 2013-06-21 08:17 | 2013-06-21 08:36 | GIBSON - JS3B-060KA | 155 | 19.1 | Yes | Yes | 22 | 20.9 | 1.1 | 27C92D5DD28346138B7F92EE97186E66 |  | R22 | Non-TXV |  | 12.32% | 0.87677 | 23.68% | [5 empty] | Non-TXV | 12.32%
Willows | CA | 95988-3547 |  | 2013-08-14 | 2013-08-14 17:22 | 2013-08-14 17:45 | GOODMAN - GSC130181CA | 67 | -3.9 | Yes | Yes | 18.7 | 20.4 | -1.7 | FAAA3D360DFB484492C7A025738F777C |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Oroville | CA | 95966-9609 |  | 2013-06-21 | 2013-06-21 18:29 | 2013-06-21 18:47 | LENNOX - GLS20H-311-75-3P | 48 | 3.7 | Yes | Yes | 21.6 | 20.4 | 1.2 | BE0F79EBB6BB4E11AED8B79367116CEC |  | R22 | Non-TXV |  | 7.708% | 0.92292 | 14.81% | [5 empty] | Non-TXV | 7.708%
Manteca | CA | 95336-3009 |  | 2013-06-19 | 2013-06-19 11:38 | 2013-06-19 11:56 | GE - BTB936A100C0 | 82 | 2.5 | Yes | Yes | 26.6 | 21.4 | 5.2 | 8E3FE03E69F84A30A59DDB942C1D8D24 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Fresno | CA | 93720-5460 |  | 2013-06-25 | 2013-06-25 12:39 | 2013-06-25 12:46 | AIRE-FLO - 13ACC036230 | 115 | 8.2 | Yes | Yes | 23.1 | 19.3 | 3.8 | B6009E3159F549978A724BC2772AAEA1 |  | R22 | Non-TXV |  | 7.13% | 0.9287 | 13.7% | [5 empty] | Non-TXV | 7.13%
Sonora | CA | 95370-9180 |  | 2013-09-24 | 2013-09-24 10:06 | 2013-09-24 10:31 | UNITARY PRODUCTS GROUP - DAYA-F042N090C | 76 | 5.5 | Yes | Yes | 25 | 19.9 | 5.1 | 14ED4BDF23FC45BDB723A00FC560B3B1 |  | R22 | Non-TXV |  | 7.237% | 0.92763 | 13.91% | [5 empty] | Non-TXV | 7.237%
Lathrop | CA | 95330-8654 |  | 2013-06-20 | 2013-06-20 13:54 | 2013-06-20 14:14 | CARRIER - 24ABA348A300 | 122 | 14.1 | Yes | Yes | 20.6 | 21 | -0.4 | 9A47592DA1104479BF4DD6C3C3B572F1 |  | R410A | Non-TXV |  | 11.56% | 0.88443 | 22.21% | [5 empty] | Non-TXV | 11.56%
Selma | CA | 93662-9636 |  | 2013-08-01 | 2013-08-01 12:45 | 2013-08-01 13:06 | RHEEM - RRNA-A030JK06X | 112 | 3.7 | Yes | Yes | 19.3 | 19.3 | 0 | 9F6BF08DDB22424AA5F76BEEBFA2AD28 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Selma | CA | 93662-9636 |  | 2013-08-01 | 2013-08-01 13:07 | 2013-08-01 13:26 | RHEEM - RRNA-A030JK06X | 112 | 6.9 | Yes | Yes | 20 | 18.8 | 1.2 | 1101993AB8754FF4A0A5824BC76F137E |  | R22 | Non-TXV |  | 6.161% | 0.93839 | 11.84% | [5 empty] | Non-TXV | 6.161%
Fresno | CA | 93725-1848 |  | 2013-09-23 | 2013-09-23 18:13 | 2013-09-23 18:44 | COLEMAN - N/A | 120 | 9.2 | Yes | Yes | 26 | 21 | 5.1 | B233BF73FC7D4927A30EECAF204C89CB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.667% | 0.92333 | 14.73% | [5 empty] | Non-TXV | 7.667%
Manteca | CA | 95336-8545 |  | 2013-06-19 | 2013-06-19 12:17 | 2013-06-19 12:38 | YORK - `H1RA048S06D | 117 | 3.5 | Yes | Yes | 19.5 | 20.4 | -0.9 | F318DA2E8DB5444EABF18A39EDD5BE1C |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Clovis | CA | 93612-5701 |  | 2013-07-02 | 2013-07-02 15:22 | 2013-07-02 16:08 | BDP - 585GJW048080ABAF | 86 | 16.7 | Yes | Yes | 18.3 | 21 | -2.7 | C4C8216F11514CA5ADEE1DAE55D8A165 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.42% | 0.80581 | 37.32% | [5 empty] | Non-TXV | 19.42%
Corning | CA | 96021-9257 |  | 2013-06-14 | 2013-06-14 09:15 | 2013-06-14 09:15 | YORK - H4D1C48S06A | 101 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 470940A02B1C4955BD90161E033D6B72 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-3011 |  | 2013-07-23 | 2013-07-23 10:19 | 2013-07-23 11:13 | RUUD - VAMC-036JAZ | 93 | 3 | Yes | Yes | 23 | 18.5 | 4.5 | 5E762C67881645A49AFBC67D2309BAF0 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Fresno | CA | 93726-4216 |  | 2013-06-04 | 2013-06-04 14:53 | 2013-06-04 15:14 | GOODMAN - N/A | 68 | 2.3 | Yes | Yes | 20.4 | 19.6 | 0.8 | 0DA56C721B654E2FAB16F2FF94709986 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Fresno | CA | 93704-4217 |  | 2013-06-19 | 2013-06-19 09:35 | 2013-06-19 09:40 | RHEEM - RRNAB036JK08X | 83 | 4.2 | Yes | Yes | 21.8 | 16.4 | 5.4 | F8129643B6734345B846630E0117A8CD |  | R22 | Non-TXV |  | 5.06% | 0.9494 | 9.725% | [5 empty] | Non-TXV | 5.06%
Stockton | CA | 95210-1161 |  | 2013-06-17 | 2013-06-17 14:07 | 2013-06-17 14:26 | TEMPSTAR - CA9642VKA1 | 156 | 4.9 | Yes | Yes | 21.3 | 19.9 | 1.4 | 027496DAC948443F8D38F02E9900CF36 |  | R22 | Non-TXV |  | 3.141% | 0.96859 | 6.036% | [5 empty] | Non-TXV | 3.141%
Fresno | CA | 93726-2314 |  | 2013-05-31 | 2013-05-31 16:15 | 2013-05-31 16:41 | UNITARY PRODUCTS GROUP - TCGD36S41S3HA | 73 | -8.2 | Yes | Yes | 17.3 | 13.4 | 3.9 | 4A1DB7D703294561BE73826DDAD72AF1 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | -11.23% | 1.1123 | 3.146% |  |  |  |  | Non-TXV |  |  | -11.23%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 13:40 | 2013-07-30 14:02 | CARRIER - 38CKC060370 | 130 | 4.1 | Yes | Yes | 16 | 18.8 | -2.8 | 997B94F18C044CE5B4EC4E44CD795A40 |  | R22 | Non-TXV |  | 3.154% | 0.96846 | 6.061% | [5 empty] | Non-TXV | 3.154%
Yuba City | CA | 95993-8243 |  | 2013-08-29 | 2013-08-29 10:10 | 2013-08-29 10:36 | HEIL - CA9036VKC1 | 97 | 3.5 | Yes | Yes | 17 | 18.6 | -1.6 | 0E5FD887A6DC4DC4A1CB9EE82D9E46FB |  | R22 | Non-TXV |  | 3.608% | 0.96392 | 6.934% | [5 empty] | Non-TXV | 3.608%
Fresno | CA | 93704-5930 |  | 2013-06-19 | 2013-06-19 14:07 | 2013-06-19 14:32 | BDP - 568B036RCUHL | 96 | 12.9 | Yes | Yes | 18.7 | 15.9 | 2.8 | DACC5C3C2709440CB8A70F153625FE6A |  | R22 | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
Yuba City | CA | 95991-8215 |  | 2013-06-18 | 2013-06-18 16:42 | 2013-06-18 17:00 | - 563AN048-A | 164 | 6.9 | Yes | Yes | 22.5 | 19.5 | 3 | D8202492572A499ABFDF5C8D22D1E9FC |  | R22 | Non-TXV |  | 4.207% | 0.95793 | 8.086% | [5 empty] | Non-TXV | 4.207%
Manteca | CA | 95336-2718 |  | 2013-06-19 | 2013-06-19 14:57 | 2013-06-19 15:25 | PAYNE - PA13NR030-H | 65 | 2 | Yes | Yes | 20.1 | 19.8 | 0.3 | 1108E1A18B32415D91238FEB568D3B7D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95206-2308 |  | 2013-06-12 | 2013-06-12 11:36 | 2013-06-12 11:58 | TRANE - YCY036G1M0AB | 129 | 6.6 | Yes | Yes | 25.4 | 20.4 | 5 | FC3F497FC4F74F7E8BA413464E1DD7BC |  | R22 | Non-TXV |  | 5.116% | 0.94884 | 9.832% | [5 empty] | Non-TXV | 5.116%
Parlier | CA | 93648-2247 |  | 2013-07-23 | 2013-07-23 18:23 | 2013-07-23 19:03 | RHEEM - RRNA-B042JK08X | 104 | 3.7 | Yes | Yes | 20.9 | 19.1 | 1.9 | 016EFF1C56954CB3AD1C506469FD7FDB |  | R22 | Non-TXV |  | 3.558% | 0.96442 | 6.837% | [5 empty] | Non-TXV | 3.558%
Los Banos | CA | 93635-4119 |  | 2013-06-03 | 2013-06-03 16:49 | 2013-06-03 16:54 | CARRIER - PA13NR030K | 75 | 7.3 | Yes | Yes | 24.2 | 21.5 | 2.7 | A623DD1CFBD74EE2B8465746087E0299 |  | R22 | TXV |  | 9.733% | 0.90267 | 18.71% | [5 empty] | TXV | 9.733%
Yuba City | CA | 95991-8325 |  | 2013-07-17 | 2013-07-17 12:31 | 2013-07-17 13:03 | YORK - AC042X1221A | 107 | -4.2 | Yes | Yes | 17 | 19.5 | -2.5 | 6CB738AF32534B139D262AFDCF685BA1 |  | R22 | TXV |  | -3.925% | 1.0393 | 1.099% |  |  |  |  | TXV |  |  | -3.925%
Merced | CA | 95348-3030 |  | 2013-09-19 | 2013-09-19 22:50 | 2013-09-19 22:51 | BDP - 565BJ018 | 50 | 1.8 | Yes | Yes | 20.1 | 20 | 0.1 | 40B3EA874DFA47AAA583AA3F38231E27 |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Merced | CA | 95341-6873 |  | 2013-07-02 | 2013-07-02 12:19 | 2013-07-02 12:27 | YORK - H1DB030S06A | 70 | 3.3 | Yes | Yes | 14.9 | 17.2 | -2.3 | C605468D624D4873B63C321ECAE4F1C4 |  | R22 | Non-TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | Non-TXV | 4.714%
Fresno | CA | 93710-6841 |  | 2013-08-12 | 2013-08-12 11:58 | 2013-08-12 19:14 | FRESCHI - BOWE30G1NA | 87 | 0 | Yes | Yes | 14 | 18.4 | -4.4 | CD1E93AF49A548B9BDBA124CE2A3DA1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3236 |  | 2013-06-19 | 2013-06-19 15:40 | 2013-06-19 15:47 | AIRE-FLO - AC13036230 | 111 | 11.6 | Yes | Yes | 26.7 | 20.9 | 5.8 | 9866EE000233411DA712B89F9880124A |  | R22 | Non-TXV |  | 10.45% | 0.8955 | 20.08% | [5 empty] | Non-TXV | 10.45%
Dinuba | CA | 93618-1858 |  | 2013-06-20 | 2013-06-20 16:35 | 2013-06-20 18:15 | BDP - 585HJW030040ABAF | 68 | 16.2 | Yes | Yes | 20.6 | 23.4 | -2.8 | F7ABB64F115948D3A2DF33C4C2390C7E |  | R22 | Non-TXV |  | 23.82% | 0.76176 | 45.78% | [5 empty] | Non-TXV | 23.82%
Fresno | CA | 93705-4821 |  | 2013-08-02 | 2013-08-02 19:04 | 2013-08-02 21:20 | BRYANT - 583ANW042090AAAF | 118 | 11.8 | Yes | Yes | 20.1 | 19.7 | 0.4 | 8FC2FCC7F4524764916534358278B7B7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95206-6408 |  | 2013-06-18 | 2013-06-18 10:25 | 2013-06-18 10:43 | - CKL-42-1L | 115 | -10.8 | Yes | Yes | 20.5 | 19.7 | 0.8 | 59F40552651B408595C11C9E74CF35D9 |  | R22 | Non-TXV |  | -9.391% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.391%
Manteca | CA | 95337-6025 |  | 2013-06-19 | 2013-06-19 10:16 | 2013-06-19 10:43 | GOODMAN - GPG13360701AC | 112 | 3.4 | Yes | Yes | 22.2 | 19.3 | 2.9 | 19B6CA4784A64FE696FAD068DC64ED22 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Fresno | CA | 93722-6888 |  | 2013-07-15 | 2013-07-15 14:23 | 2013-07-15 14:24 | CARRIER - 38CKC048370 | 98 | 15.1 | Yes | Yes | 21 | 22.4 | -1.4 | 06871100E1EA4261A319E97F88344D84 |  | R22 | TXV |  | 15.41% | 0.84592 | 29.61% | [5 empty] | TXV | 15.41%
Stockton | CA | 95210-6616 |  | 2013-08-16 | 2013-08-16 14:51 | 2013-08-16 15:11 | YORK - D5YS024N04506A | 70 | 5.3 | Yes | Yes | 22.3 | 19.9 | 2.4 | DDBAF6DE974B410191CE5A2E1ECA0286 |  | R22 | Non-TXV |  | 7.571% | 0.92429 | 14.55% | [5 empty] | Non-TXV | 7.571%
Stockton | CA | 95207-2720 |  | 2013-06-13 | 2013-06-13 13:56 | 2013-06-13 14:18 | RHEEM - RRPL-B042JK08X | 85 | 13.4 | Yes | Yes | 23 | 20.4 | 2.6 | DF2A0433A3E74FAB85FA7BDCD565B653 |  | R410A | TXV |  | 15.76% | 0.84235 | 30.3% | [5 empty] | TXV | 15.76%
Yuba City | CA | 95993-0000 |  | 2013-09-11 | 2013-09-11 13:02 | 2013-09-11 13:35 | LENNOX - UNK | 130 | 4.9 | Yes | Yes | 18 | 18.7 | -0.7 | 86D437FBCA05404F96630718FC964B37 |  | R22 | TXV |  | 3.769% | 0.96231 | 7.244% | [5 empty] | TXV | 3.769%
Stockton | CA | 95215-7430 |  | 2013-06-20 | 2013-06-20 10:47 | 2013-06-20 11:15 | AMANA - RCE36C2A | 225 | 30 | Yes | Yes | 19.2 | 19.4 | -0.2 | 99CB67780D334ED3836D6B785FD83961 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Fresno | CA | 93720-4240 |  | 2013-06-24 | 2013-06-24 15:02 | 2013-06-24 15:08 | CARRIER - 38TDA048300 | 172 | 5.5 | Yes | Yes | 18.2 | 19.7 | -1.5 | 30C19A576B0B40FEAAE2CC7ACAA179C5 |  | R22 | Non-TXV |  | 3.198% | 0.96802 | 6.145% | [5 empty] | Non-TXV | 3.198%
Red Bluff | CA | 96080-3135 |  | 2013-06-15 | 2013-06-15 15:27 | 2013-06-15 16:58 | YORK - NA | 58 | 12.7 | Yes | Yes | 26.7 | 21.3 | 5.4 | E50B70F5F1494C8480F1766BFDC9F00B |  | R22 | Non-TXV |  | 21.9% | 0.78103 | 42.08% | [5 empty] | Non-TXV | 21.9%
Fresno | CA | 93703-1437 |  | 2013-06-01 | 2013-06-01 15:05 | 2013-06-01 15:05 | DAY & NIGHT - GCS26-048-100-2PA | 117 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | 301E8AD17464492DA1BD82154EADBF2D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-6860 |  | 2013-07-03 | 2013-07-03 18:36 | 2013-07-03 18:54 | AMANA - PG036C07020 | 110 | 10.6 | Yes | Yes | 19.1 | 18.3 | 0.8 | 4A03537A69134B9BB68D680ACA2DF32B |  | R22 | Non-TXV |  | 9.636% | 0.90364 | 18.52% | [5 empty] | Non-TXV | 9.636%
Fresno | CA | 93726-0422 |  | 2013-05-28 | 2013-05-28 17:43 | 2013-05-28 22:05 | ICP - HAC042AKA5 | 98 | 5.1 | Yes | Yes | 19.6 | 21 | -1.4 | 3093C26042DE44E5AD61465186DE1F95 |  | R22 | Non-TXV |  | 5.204% | 0.94796 | 10% | [5 empty] | Non-TXV | 5.204%
Newman | CA | 95360-1756 |  | 2013-06-05 | 2013-06-05 11:15 | 2013-06-05 11:32 | UNITARY PRODUCTS GROUP - H2RA030S06D | 62 | 5.8 | Yes | Yes | 18.8 | 20.4 | -1.6 | 3C3723594F7A457F945BCC7F030614B9 |  | R22 | Non-TXV |  | 9.355% | 0.90645 | 17.98% | [5 empty] | Non-TXV | 9.355%
Los Banos | CA | 93635-3074 |  | 2013-05-29 | 2013-05-29 09:39 | 2013-05-29 09:55 | NORDYNE - JS3BC030KA | 68 | 6.6 | Yes | Yes | 13.9 | 16.5 | -2.6 | A0B6FEF57217497688CBC36271A955C5 |  | R22 | Non-TXV |  | 9.706% | 0.90294 | 18.65% | [5 empty] | Non-TXV | 9.706%
Stockton | CA | 95207-7430 |  | 2013-06-14 | 2013-06-14 12:00 | 2013-06-14 12:00 | GOODMAN - PGB030050-1-REV A | 56 | 0 | Yes | Yes | 27.3 | 21.9 | 5.4 | 16F7829A0294462D9FDEA4B245186F8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-0000 |  | 2013-07-18 | 2013-07-18 16:46 | 2013-07-18 17:15 | GOODMAN - GSC130301DA | 87 | 9.7 | Yes | Yes | 21 | 22.1 | -1.1 | E6407309FEC74AEDBAB33447A8BB1027 |  | R22 | Non-TXV |  | 11.15% | 0.88851 | 21.43% | [5 empty] | Non-TXV | 11.15%
Stockton | CA | 95206-4728 |  | 2013-06-17 | 2013-06-17 12:06 | 2013-06-17 12:30 | RHEEM - RAHE-042JAS | 85 | -8 | Yes | Yes | 26 | 20.1 | 5.9 | 0092248205AE4D609C865617E2523EFD |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Selma | CA | 93662-4139 |  | 2013-08-09 | 2013-08-09 12:41 | 2013-08-09 13:27 | BDP - 561CJ048-A | 102 | 3.1 | Yes | Yes | 22.5 | 20.4 | 2.1 | 74D3202C7B434AE58A9635A834DE0500 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Merced | CA | 95341-5860 |  | 2013-06-19 | 2013-06-19 15:18 | 2013-06-19 15:20 | YORK - DAYA-F024N045C | 54 | 2.2 | Yes | Yes | 22 | 21.7 | 0.4 | 6490E4E5122E459AB4446609148F0C2E |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Stockton | CA | 95210-6606 |  | 2013-07-12 | 2013-07-12 09:35 | 2013-07-12 09:54 | YORK - D3YS024N03206B | 62 | 10 | Yes | Yes | 22.6 | 19.8 | 2.8 | 31A96611FA8B409BB04407E62D5736BB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.13% | 0.83871 | 31% | [5 empty] | Non-TXV | 16.13%
Sonora | CA | 95370-9265 |  | 2013-07-31 | 2013-07-31 11:21 | 2013-07-31 12:00 | CARRIER - 48GS-036090301 | 56 | 3.8 | Yes | Yes | 18.6 | 19.2 | -0.6 | B382E37181534C39A1979158A5179088 |  | R22 | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Paso Robles | CA | 93446-5435 |  | 2013-08-09 | 2013-08-09 11:44 | 2013-08-09 12:05 | CARRIER - 38EZG030300 | 88 | 13.8 | Yes | Yes | 16.2 | 18.2 | -2 | 6647EA7A9D21470DB01D6C8EDF85E098 |  | R410A | Non-TXV |  | 15.68% | 0.84318 | 30.14% | [5 empty] | Non-TXV | 15.68%
Fresno | CA | 93725-9415 |  | 2013-07-18 | 2013-07-18 17:51 | 2013-07-18 18:20 | HEIL - N/A | 120 | 17.2 | Yes | Yes | 26.1 | 22.2 | 3.9 | 0FA18CF529114536A8CD9B00A0C1EEFD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.33% | 0.85667 | 27.55% | [5 empty] | Non-TXV | 14.33%
Paso Robles | CA | 93446-5433 |  | 2013-08-09 | 2013-08-09 12:12 | 2013-08-09 12:30 | GOODMAN - VSX130241DA | 76 | -4.5 | Yes | Yes | 18.7 | 18.2 | 0.5 | 96EB8CE23F24457AAB1394EC6DAF242A |  | R410A | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Parlier | CA | 93648-2831 |  | 2013-07-24 | 2013-07-24 11:44 | 2013-07-24 12:28 | LENNOX - 10GCS030-75-3PA | 51 | 3.5 | Yes | Yes | 19.3 | 20.7 | -1.4 | A881B87324154D69A18DB14F3AB63FF8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.863% | 0.93137 | 13.19% | [5 empty] | Non-TXV | 6.863%
Paradise | CA | 95969-6651 |  | 2013-06-13 | 2013-06-13 12:12 | 2013-06-13 15:57 | COLEMAN - DAYP-F042N080A | 150 | 9.4 | Yes | Yes | 27 | 21 | 6 | 6D324808C3384D24BF9122322DCAA829 |  | R22 | Non-TXV |  | 6.267% | 0.93733 | 12.04% | [5 empty] | Non-TXV | 6.267%
Selma | CA | 93662-4107 |  | 2013-07-31 | 2013-07-31 15:23 | 2013-07-31 15:46 | CARRIER - 580AN042060 | 100 | 8.9 | Yes | Yes | 21 | 20.7 | 0.3 | 6294AB8393EE490084BBE159DEFAD8B1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.9% | 0.911 | 17.1% | [5 empty] | Non-TXV | 8.9%
Fresno | CA | 93726-5903 |  | 2013-06-07 | 2013-06-07 13:18 | 2013-06-07 13:39 | CARRIER - N/A | 90 | 8.3 | Yes | Yes | 22.6 | 19 | 3.6 | 677864570C294261937CC62514AD8C5A |  | R22 | Non-TXV |  | 9.222% | 0.90778 | 17.72% | [5 empty] | Non-TXV | 9.222%
Los Banos | CA | 93635-5142 |  | 2013-06-03 | 2013-06-03 09:28 | 2013-06-03 09:35 | GOODMAN - CJ481GB | 149 | 12.4 | Yes | Yes | 22.2 | 19.9 | 2.3 | 5AAB08446C784086A31035C7761F93B1 |  | R22 | Non-TXV |  | 8.322% | 0.91678 | 15.99% | [5 empty] | Non-TXV | 8.322%
Yuba City | CA | 95993-8880 |  | 2013-08-09 | 2013-08-09 13:34 | 2013-08-09 14:10 | LENNOX - 13ACC-048-230-01 | 158 | 5.8 | Yes | Yes | 21 | 17.7 | 3.3 | C33A21D37E1246EC8CAF2BCFC7674716 |  | R22 | TXV |  | 3.671% | 0.96329 | 7.055% | [5 empty] | TXV | 3.671%
Merced | CA | 95340-1629 |  | 2013-07-10 | 2013-07-10 11:38 | 2013-07-10 11:42 | AMERICAN STANDARD - TTD730B100A1 | 69 | 2.8 | Yes | Yes | 17.2 | 16.6 | 0.6 | 46F853BB3AC54F2DBD9C1078E2F2C02A |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Yuba City | CA | 95993-9255 |  | 2013-07-22 | 2013-07-22 13:15 | 2013-07-22 13:40 | OTHER - JS3BC-060KA | 85 | 8.7 | Yes | Yes | 17 | 19.9 | -2.9 | 218DBC7E5171431DB8C78CE70017420F |  | R22 | TXV |  | 10.24% | 0.89765 | 19.67% | [5 empty] | TXV | 10.24%
Placerville | CA | 95667-8187 |  | 2013-06-18 | 2013-06-18 13:01 | 2013-06-18 13:01 | AMERICAN STANDARD - WCY042G100AB | 149 | 0 | Yes | Yes | 26.3 | 20.8 | 5.5 | E37ADE7C8FF046F6B71DC033501FD187 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3040 |  | 2013-06-13 | 2013-06-13 11:07 | 2013-06-13 11:35 | GUARDIAN - GCGD30S21S2B | 85 | 16.5 | Yes | Yes | 18.3 | 20.3 | -2 | 46764ED79EEA44ED9A88CD99796839F8 |  | R22 | Non-TXV |  | 19.41% | 0.80588 | 37.31% | [5 empty] | Non-TXV | 19.41%
Los Banos | CA | 93635-5453 |  | 2013-06-04 | 2013-06-04 09:21 | 2013-06-04 09:26 | BRYANT - 561CJ060 | 152 | 6.4 | Yes | Yes | 19.5 | 20.4 | -0.9 | 3713DC664EB347BFAF680907A1D0912D |  | R22 | TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | TXV | 4.211%
Dinuba | CA | 93618-3614 |  | 2013-06-24 | 2013-06-24 10:04 | 2013-06-24 10:29 | RUUD - N/A | 90 | 4.8 | Yes | Yes | 25 | 19.3 | 5.7 | BAE5FC1281924D94A3540E44EC79D802 |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Fresno | CA | 93726-5723 |  | 2013-06-10 | 2013-06-10 15:49 | 2013-06-10 21:11 | BDP - 585ANE036080YAC | 60 | 1.8 | Yes | Yes | 19.3 | 21 | -1.7 | 06ECA076B7CE48CB8FDDED427D9E5FED |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93726-3511 |  | 2013-06-28 | 2013-06-28 10:24 | 2013-06-28 10:26 | RHEEM - RRNL-B024JK06X | 78 | 3.7 | Yes | Yes | 20 | 18.8 | 1.3 | 8BB79BCFEF694E80BF18A737B885A846 |  | R410A | Non-TXV |  | 4.744% | 0.95256 | 9.116% | [5 empty] | Non-TXV | 4.744%
Marysville | CA | 95901-8213 |  | 2013-07-02 | 2013-07-02 13:49 | 2013-07-02 13:49 | OTHER - 561CJ036-E | 80 | 0 | Yes | Yes | 16 | 18.3 | -2.3 | C5E2D8843FCC4EA9B04C2CBE4518EB57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2220 |  | 2013-07-10 | 2013-07-10 15:34 | 2013-07-10 15:57 | AMANA - PGA360702C | 112 | 3.8 | Yes | Yes | 25.3 | 20.2 | 5.1 | 6BEF744DC508420982BCFA4984C02EAC |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Manteca | CA | 95337-6528 |  | 2013-06-19 | 2013-06-19 09:31 | 2013-06-19 09:56 | DAY & NIGHT - 565BJ024 | 59 | 15 | Yes | Yes | 17.5 | 20.2 | -2.7 | DCAC3664C7FE4BD881DBB3E57E30239A |  | R22 | Non-TXV |  | 25.42% | 0.74576 | 48.86% | [5 empty] | Non-TXV | 25.42%
Yuba City | CA | 95991-5027 |  | 2013-09-06 | 2013-09-06 12:27 | 2013-09-06 12:46 | BDP - 655ANX024000ABBD | 65 | 13.9 | Yes | Yes | 18 | 19.8 | -1.8 | 6D6429C3A2C64EDCA0CC6B7173B9E821 |  | R22 | Non-TXV |  | 21.38% | 0.78615 | 41.1% | [5 empty] | Non-TXV | 21.38%
Winton | CA | 95388-9423 |  | 2013-06-14 | 2013-06-14 15:08 | 2013-06-14 15:21 | OTHER - BRCQ0421BD | 66 | 7.8 | Yes | Yes | 22.1 | 21.3 | 0.8 | 546376DD786447CF9DA5D727F9A6C0DF |  | R22 | Non-TXV |  | 11.82% | 0.88182 | 22.71% | [5 empty] | Non-TXV | 11.82%
Marysville | CA | 95901-8233 |  | 2013-06-29 | 2013-06-29 13:48 | 2013-06-29 13:48 | YORK - H2RA036S06E | 63 | 0 | Yes | Yes | 13 | 15.8 | -2.8 | 0CD39C55931B40AA91BE1EFF83548442 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-3215 |  | 2013-07-08 | 2013-07-08 17:34 | 2013-07-08 17:34 | BRYANT - 567C036ROU | 67 | 0 | Yes | Yes | 0 | 19.5 | -19.5 | B09C142CC5944135932C2518BD7ED133 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-3215 |  | 2013-07-08 | 2013-07-08 18:12 | 2013-07-08 18:12 | BRYANT - 567C024ROU | 60 | 0 | Yes | Yes | 24.7 | 20.9 | 3.9 | 5DB1679D8EAC42C8A3CF4C2540C768D4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Pinedale | CA | 93650-1385 |  | 2013-09-03 | 2013-09-03 12:39 | 2013-09-03 12:40 | GOODMAN - GPG1330045M41AD | 80 | 5.7 | Yes | Yes | 23.5 | 19.3 | 4.2 | 88D75648833E44E683A59C1B8A917CC3 |  | R410A | Non-TXV |  | 7.125% | 0.92875 | 13.69% | [5 empty] | Non-TXV | 7.125%
Chico | CA | 95973-5859 |  | 2013-08-07 | 2013-08-07 09:46 | 2013-08-07 10:07 | TRANE - 2TTB2036A1000AA | 96 | 3.1 | Yes | Yes | 21.2 | 17.7 | 3.5 | 87FB3BFCDF9B43D5894E3E195F7FC2EA |  | R22 | TXV |  | 3.229% | 0.96771 | 6.206% | [5 empty] | TXV | 3.229%
Cameron Park | CA | 95682-9266 |  | 2013-07-19 | 2013-07-19 10:00 | 2013-07-19 10:27 | OTHER - 5410J030 | 102 | -9.6 | Yes | Yes | 19 | 21 | -2 | F5DEF7197AD94BA3A658067ADFCD1D5B |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95212-3043 |  | 2013-06-26 | 2013-06-26 09:35 | 2013-06-26 09:55 | CARRIER - 38CKC036350 | 70 | 5.3 | Yes | Yes | 16.3 | 18.8 | -2.5 | A99D5A30935C436B84583D419166EB08 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.571% | 0.92429 | 14.55% | [5 empty] | Non-TXV | 7.571%
Merced | CA | 95348-3606 |  | 2013-06-12 | 2013-06-12 10:30 | 2013-06-12 10:32 | TRANE - YCC030F1M0BC | 69 | 3.5 | Yes | Yes | 22.5 | 21.5 | 1 | A1C45750444446CB8B5EAB29DB92DBAC |  | R22 | Non-TXV |  | 5.072% | 0.94928 | 9.748% | [5 empty] | Non-TXV | 5.072%
Fresno | CA | 93705-4809 |  | 2013-06-19 | 2013-06-19 12:39 | 2013-06-19 12:41 | CARRIER - 48GX030060311 | 68 | 5.7 | Yes | Yes | 21.2 | 20.2 | 1 | 25C1300563A74F96810F751B3B1BF94C |  | R22 | Non-TXV |  | 8.382% | 0.91618 | 16.11% | [5 empty] | Non-TXV | 8.382%
Los Banos | CA | 93635-8808 |  | 2013-06-04 | 2013-06-04 13:18 | 2013-06-04 13:24 | BRYANT - 561CJ048 | 72 | 4.7 | Yes | Yes | 23.4 | 18.1 | 5.3 | 1C9672137B434604BA480FB59C500221 |  | R22 | TXV |  | 6.528% | 0.93472 | 12.54% | [5 empty] | TXV | 6.528%
Chowchilla | CA | 93610-9373 |  | 2013-06-27 | 2013-06-27 01:09 | 2013-06-27 01:39 | BARD - 48GS-04809B01 | 74 | 2.2 | Yes | Yes | 19 | 19.7 | -0.7 | F31E8DE5A1934449B894761D84DE93A9 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Firebaugh | CA | 93622-2731 |  | 2013-08-14 | 2013-08-14 12:43 | 2013-08-14 12:44 | LENNOX - 10GCS030-75-1PA | 51 | 2.1 | Yes | Yes | 26.1 | 21.9 | 4.2 | 5F85ED1F64CC425AAD1B424094AF8779 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fresno | CA | 93706-5941 |  | 2013-07-17 | 2013-07-17 12:35 | 2013-07-17 12:37 | RHEEM - RRKA-A042JK08X | 69 | 2.5 | Yes | Yes | 19.6 | 18.6 | 1 | C5C81FA86D1146988FB9F947C4744D0A |  | R22 | Non-TXV |  | 3.623% | 0.96377 | 6.963% | [5 empty] | Non-TXV | 3.623%
Merced | CA | 95348-3606 |  | 2013-06-08 | 2013-06-08 11:44 | 2013-06-08 11:46 | TRANE - YCC030F1M0BC | 70 | 5.8 | Yes | Yes | 18.2 | 20.2 | -2 | 4FB4FDA75B5B4884B3F6EA17AC897FE3 |  | R22 | Non-TXV |  | 8.286% | 0.91714 | 15.92% | [5 empty] | Non-TXV | 8.286%
Red Bluff | CA | 96080-2031 |  | 2013-06-15 | 2013-06-15 18:07 | 2013-06-15 18:25 | AMERICAN STANDARD - 2H7A2042810000AA | 86 | 15 | Yes | Yes | 22.7 | 21.3 | 1.4 | 560AF644950E4CF8B7054A7DF093D5F5 |  | R22 | Non-TXV |  | 17.44% | 0.82558 | 33.52% | [5 empty] | Non-TXV | 17.44%
Marysville | CA | 95901-3123 |  | 2013-07-11 | 2013-07-11 09:04 | 2013-07-11 09:25 | TEMPSTAR - CA5548VKD2 | 134 | 10.4 | Yes | Yes | 21 | 19.3 | 1.7 | DA4C9BAD089849F895338F3C9A919702 |  | R22 | Non-TXV |  | 7.761% | 0.92239 | 14.92% | [5 empty] | Non-TXV | 7.761%
Manteca | CA | 95336-3337 |  | 2013-07-09 | 2013-07-09 13:20 | 2013-07-09 13:41 | GOODMAN - GPG154811541AB | 85 | 5.1 | Yes | Yes | 24.3 | 19.3 | 5 | 86575EEEBC084D4D94C82D76174416A4 |  | R410A | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Selma | CA | 93662-4331 |  | 2013-09-05 | 2013-09-05 15:12 | 2013-09-05 15:30 | UNITARY PRODUCTS GROUP - H1RD3606G | 145 | 13.8 | Yes | Yes | 19.5 | 21.5 | -2 | 6099A755C7A04D6FABD04983F56980CC |  | R22 | Non-TXV |  | 9.517% | 0.90483 | 18.29% | [5 empty] | Non-TXV | 9.517%
Madera | CA | 93637-4615 |  | 2013-07-10 | 2013-07-10 10:40 | 2013-07-17 03:07 | OTHER - UNK | 95 | 3.1 | Yes | Yes | 17.4 | 20.2 | -2.8 | 2FCC177557A347B195F0413DFEC398BE |  | R22 | Non-TXV |  | 3.263% | 0.96737 | 6.271% | [5 empty] | Non-TXV | 3.263%
Red Bluff | CA | 96080-2545 |  | 2013-06-15 | 2013-06-15 17:04 | 2013-06-15 17:24 | AMANA - PGB030C0702E | 64 | 13 | Yes | Yes | 22.4 | 19.8 | 2.6 | 1C537E82D08449D583D6DB60B64DDAD8 |  | R22 | Non-TXV |  | 20.31% | 0.79688 | 39.04% | [5 empty] | Non-TXV | 20.31%
Stockton | CA | 95210-2160 |  | 2013-06-19 | 2013-06-19 10:49 | 2013-06-19 11:08 | ICP - HAC030AKA4 | 74 | 5 | Yes | Yes | 20.6 | 19.3 | 1.3 | 88D0078D2540482499D830E42A19CF20 |  | R22 | Non-TXV |  | 6.757% | 0.93243 | 12.98% | [5 empty] | Non-TXV | 6.757%
Fresno | CA | 93726-3408 |  | 2013-06-04 | 2013-06-04 10:26 | 2013-06-04 10:41 | GOODMAN - PGB048075-1 | 86 | 2.8 | Yes | Yes | 22.9 | 19.6 | 3.4 | 185BBC096E94451E9F68332C30B30549 |  | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
Yuba City | CA | 95993-5901 |  | 2013-06-18 | 2013-06-18 17:23 | 2013-06-18 17:41 | LENNOX - 10ACC-060-320-02 | 130 | 4.7 | Yes | Yes | 24.2 | 21 | 3.2 | 03748834308A4D2B9B5D1A6B52F33992 |  | R22 | Non-TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | Non-TXV | 3.615%
Fresno | CA | 93710-5410 |  | 2013-06-13 | 2013-06-13 10:04 | 2013-06-13 10:06 | CARRIER - 585H36060 | 100 | 3.9 | Yes | Yes | 23.5 | 20.4 | 3.1 | 8BA256D956BB49E69D8704E69A0E398F |  | R22 | Non-TXV |  | 3.9% | 0.961 | 7.495% | [5 empty] | Non-TXV | 3.9%
Willows | CA | 95988-3531 |  | 2013-06-27 | 2013-06-27 19:03 | 2013-06-27 19:03 | GOODMAN - GSC30181CA | 67 | 0 | Yes | Yes | 24.2 | 20.7 | 3.5 | 3A31200B190F41BE9655878BC19A302F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-5120 |  | 2013-06-10 | 2013-06-10 11:30 | 2013-06-10 11:46 | PAYNE - 565B-JO36 | 84 | 7.5 | Yes | Yes | 21.6 | 18.1 | 3.5 | 98308D436DC442BB85869D7A94E77EFD |  | R22 | Non-TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | Non-TXV | 8.929%
Manteca | CA | 95336-2918 |  | 2013-07-09 | 2013-07-09 11:18 | 2013-07-09 11:36 | GOODMAN - PGB036075 | 85 | 8 | Yes | Yes | 23.8 | 20.1 | 3.7 | 801B13E956514F3B91640F37F107957A |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Arbuckle | CA | 95912-0000 |  | 2013-07-31 | 2013-07-31 11:45 | 2013-07-31 12:23 | LENNOX - 13ACX-030-230-17 | 82 | -4.1 | Yes | Yes | 14 | 16.3 | -2.3 | 5ADB40B395664EA0B35FB5A18BFFCB1E |  | R410A | TXV |  | -5% | 1.05 | 1.4% |  |  |  |  | TXV |  |  | -5%
Fresno | CA | 93711-2751 |  | 2013-07-22 | 2013-07-22 10:14 | 2013-07-22 10:16 | RHEEM - RRMAA042JK08X | 114 | 14.8 | Yes | Yes | 23.8 | 20.4 | 3.4 | A9AAD33D0DDB404DB4845B566DFCA6CC |  | R22 | Non-TXV |  | 12.98% | 0.87018 | 24.95% | [5 empty] | Non-TXV | 12.98%
Fresno | CA | 93711-2751 |  | 2013-07-22 | 2013-07-22 10:17 | 2013-07-22 10:32 | RHEEM - RRMAA042JK08X | 114 | 12 | Yes | Yes | 23 | 18.8 | 4.2 | 4EDDA7AD5E7646F993A846EAF4F048BE |  | R22 | Non-TXV |  | 10.53% | 0.89474 | 20.23% | [5 empty] | Non-TXV | 10.53%
Arbuckle | CA | 95912-9758 |  | 2013-07-31 | 2013-07-31 17:04 | 2013-07-31 17:29 | OTHER - UNK | 85 | 10.5 | Yes | Yes | 18 | 19.5 | -1.5 | D059B6DBF46940BD945CAE5E2E5E0E5D |  | R22 | Non-TXV |  | 12.35% | 0.87647 | 23.74% | [5 empty] | Non-TXV | 12.35%
Stockton | CA | 95210-4438 |  | 2013-06-18 | 2013-06-18 08:17 | 2013-06-18 08:35 | PAYNE - 591ANX042000ABAA | 112 | -7.9 | Yes | Yes | 17.2 | 19.1 | -1.9 | 2DDDAAC2DC73418DBFA1E8BA598EB5AA |  | R22 | Non-TXV |  | -7.054% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.054%
Stockton | CA | 95212-3458 |  | 2013-06-17 | 2013-06-17 10:22 | 2013-06-17 10:41 | BRYANT - 561CJ048-F | 97 | 3.9 | Yes | Yes | 17.9 | 20.4 | -2.5 | 9EAA3CD251B540EA813FE18CD50F9F14 |  | R22 | Non-TXV |  | 4.021% | 0.95979 | 7.727% | [5 empty] | Non-TXV | 4.021%
Stockton | CA | 95210-2054 |  | 2013-06-27 | 2013-06-27 13:51 | 2013-06-27 14:12 | DAY & NIGHT - 585A024055YACR | 50 | -3.5 | Yes | Yes | 18.8 | 18.1 | 0.7 | 4FCD8342BC6344BE85CAD67AFBF93E66 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93726-1834 |  | 2013-05-30 | 2013-05-30 18:40 | 2013-05-30 18:40 | BDP - 563CN036-B | 122 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 809A704062FF4AB4885579B03A7E0D8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9431 |  | 2013-09-06 | 2013-09-06 14:41 | 2013-09-06 15:09 | CARRIER - 38BRC042330 | 101 | 7.6 | Yes | Yes | 18 | 19.9 | -1.9 | 01C2FE8635C94B27BF16C03D602C294C |  | R22 | TXV |  | 7.525% | 0.92475 | 14.46% | [5 empty] | TXV | 7.525%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 13:06 | 2013-07-30 13:27 | CARRIER - 38CKC042350 | 90 | 2.6 | Yes | Yes | 15 | 17.9 | -2.9 | 134587B4C16E4662A33AB42E05BCE424 |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Tracy | CA | 95376-2728 |  | 2013-06-25 | 2013-06-25 10:04 | 2013-06-25 10:24 | YORK - D1NH042N06506A | 90 | 4.1 | Yes | Yes | 21.6 | 17.1 | 4.5 | BC41A7DB21724234AAD05631BFB5C2B9 |  | R22 | Non-TXV |  | 4.556% | 0.95444 | 8.755% | [5 empty] | Non-TXV | 4.556%
Fresno | CA | 93703-1612 |  | 2013-05-29 | 2013-05-29 23:04 | 2013-05-29 23:04 | OTHER - UNK | 70 | 0 | Yes | Yes | 21 | 16.1 | 4.9 | F670AB18D1A1474CAE40DE00E5AD76D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-9369 |  | 2013-08-27 | 2013-08-27 12:13 | 2013-08-27 12:34 | GOODMAN - GPG13240701BA | 77 | 17.3 | Yes | Yes | 19.5 | 20.9 | -1.4 | E278C235C94A44F891DC7E952F9E32DE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.47% | 0.77532 | 43.18% | [5 empty] | Non-TXV | 22.47%
Stockton | CA | 95206-6357 |  | 2013-06-20 | 2013-06-20 14:57 | 2013-06-20 15:14 | GOODMAN - CLJ48-1 | 116 | 8.1 | Yes | Yes | 23.9 | 19.3 | 4.7 | 51FA1D3B048B47C58D3850B039EA0DA4 |  | R22 | Non-TXV |  | 6.983% | 0.93017 | 13.42% | [5 empty] | Non-TXV | 6.983%
Clovis | CA | 93612-4491 |  | 2013-08-15 | 2013-08-15 13:26 | 2013-08-15 14:04 | GOODMAN - PGB036075-1A | 60 | 3.3 | Yes | Yes | 19 | 20.2 | -1.2 | 9719FFD420A141B485CE30CC057E28FC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Fresno | CA | 93722-8714 |  | 2013-07-15 | 2013-07-15 14:55 | 2013-07-15 15:00 | CARRIER - 24ABA342A300 | 98 | 9.5 | Yes | Yes | 22 | 21.6 | 0.4 | 587408E4B30147BDAF8B484A1CC4F6B6 |  | R22 | TXV |  | 9.694% | 0.90306 | 18.63% | [5 empty] | TXV | 9.694%
Selma | CA | 93662-4214 |  | 2013-07-31 | 2013-07-31 12:49 | 2013-07-31 13:19 | OTHER - N/A | 90 | 8.5 | Yes | Yes | 14.8 | 17.7 | -2.9 | 4F463F1B69F6458295FB6A2D56747391 |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Arbuckle | CA | 95912-9806 |  | 2013-07-31 | 2013-07-31 14:20 | 2013-07-31 14:44 | GOODMAN - GSC120301AE | 117 | 4.3 | Yes | Yes | 14 | 16.5 | -2.5 | 91A51CBA53224AC887E553E368592641 |  | R22 | TXV |  | 3.675% | 0.96325 | 7.063% | [5 empty] | TXV | 3.675%
Arbuckle | CA | 95912-0000 |  | 2013-07-31 | 2013-07-31 16:10 | 2013-07-31 16:31 | LENNOX - GSC20R-036-75-6P | 82 | 4.4 | Yes | Yes | 20 | 19.9 | 0.1 | BC6147F2A2C64DDF8D0CF29F8B90D6A7 |  | R22 | Non-TXV |  | 5.366% | 0.94634 | 10.31% | [5 empty] | Non-TXV | 5.366%
Escalon | CA | 95320-2114 |  | 2013-09-26 | 2013-09-26 14:42 | 2013-09-26 15:01 | RUUD - URKA-A036JK08E | 62 | 3.3 | Yes | Yes | 25.2 | 20.1 | 5.1 | 1782DDAEA0B04D0A8B263832F46059CA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.323% | 0.94677 | 10.23% | [5 empty] | Non-TXV | 5.323%
Stockton | CA | 95203-2812 |  | 2013-07-15 | 2013-07-15 14:57 | 2013-07-15 14:57 | ICP - PGC024K060E | 54 | 0 | Yes | Yes | 17.4 | 17.6 | -0.2 | DA3FF178D79742A0A57FADC27E2F439E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2146 |  | 2013-07-10 | 2013-07-10 12:55 | 2013-07-10 13:14 | GE - BTB936A100A0 | 70 | 7.1 | Yes | Yes | 18.3 | 18.5 | -0.2 | 288F7F10B68C423AA08E1CB36AC9315A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.14% | 0.89857 | 19.49% | [5 empty] | Non-TXV | 10.14%
Fresno | CA | 93705-1744 |  | 2013-06-18 | 2013-06-18 11:44 | 2013-06-18 11:47 | YORK - D1NA036N05606C | 67 | 7.4 | Yes | Yes | 20.4 | 19.7 | 0.7 | BD41B2AD76764DC1AF89D8B903DD265E |  | R22 | Non-TXV |  | 11.04% | 0.88955 | 21.23% | [5 empty] | Non-TXV | 11.04%
Los Banos | CA | 93635-3075 |  | 2013-07-02 | 2013-07-02 10:44 | 2013-07-02 11:02 | YORK - TCGD48S21S2A | 69 | 8.6 | Yes | Yes | 28 | 22.4 | 5.6 | 77D8A34D7A6E4E1DA9D982CE884942D9 |  | R22 | Non-TXV |  | 12.46% | 0.87536 | 23.95% | [5 empty] | Non-TXV | 12.46%
Merced | CA | 95348-3805 |  | 2013-06-07 | 2013-06-07 16:13 | 2013-06-07 16:15 | TRANE - YCC030F1M0BA | 69 | 4.3 | Yes | Yes | 20.7 | 19.3 | 1.4 | E8775D6DACCC487DA43F0516A832B240 |  | R22 | Non-TXV |  | 6.232% | 0.93768 | 11.98% | [5 empty] | Non-TXV | 6.232%
Los Banos | CA | 93635-5410 |  | 2013-06-01 | 2013-06-01 09:07 | 2013-06-01 09:12 | BDP - 561AJ042 | 88 | 6.8 | Yes | Yes | 23.9 | 23.2 | 0.7 | 07B58BEEDBB642BA93ABE6ED7A84F505 |  | R22 | TXV |  | 7.727% | 0.92273 | 14.85% | [5 empty] | TXV | 7.727%
Chico | CA | 95973-1069 |  | 2013-07-11 | 2013-07-11 19:18 | 2013-07-11 19:35 | AIRE-FLO - AFA1R12B30-A | 48 | 4.4 | Yes | Yes | 25.5 | 20 | 5.6 | 7E2023E48F844805897508AF0C50D5D9 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Merced | CA | 95348-3793 |  | 2013-06-07 | 2013-06-07 14:55 | 2013-06-07 14:58 | PAYNE - 591ANX030000ABAA | 69 | 2.3 | Yes | Yes | 17.8 | 17.9 | -0.1 | D1025401D06C4527A448A0B92245BD6A |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93726-3508 |  | 2013-10-03 | 2013-10-03 12:10 | 2013-10-03 12:11 | OTHER - 7777UNK | 54 | 2.2 | Yes | Yes | 16.9 | 19.9 | -3 | 738B9E8AEC024D2FAE8902C7E79D004A |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Nevada City | CA | 95959-9301 |  | 2013-09-12 | 2013-09-12 11:47 | 2013-09-12 11:47 | NORDYNE - R4GD-030K072X | 93.5 | 0 | Yes | Yes | 18.9 | 18.9 | 0 | 18A329B16A36444F88CD7183670F97C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-4369 |  | 2013-09-19 | 2013-09-19 13:09 | 2013-09-19 13:30 | DAY & NIGHT - 1889E83641 | 93 | 3.5 | Yes | Yes | 18.7 | 21 | -2.3 | 4EFCCFF93D11474C9A24097049BD2207 |  | R22 | Non-TXV |  | 3.763% | 0.96237 | 7.233% | [5 empty] | Non-TXV | 3.763%
Mendota | CA | 93640-4013 |  | 2013-08-13 | 2013-08-13 14:39 | 2013-08-13 15:07 | BRYANT - 113RNA030 B | 82 | 2.8 | Yes | Yes | 21.4 | 17.3 | 4.2 | 242A90C32D174B64A57D4E4D32C8C117 |  | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Fresno | CA | 93704-1031 |  | 2013-06-25 | 2013-06-25 14:51 | 2013-06-25 14:55 | ICP - HAC036AKA4 | 80 | 4.4 | Yes | Yes | 23.9 | 18.3 | 5.6 | BA0244C31DBE437EB2BDDCB9C7BD8923 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Fresno | CA | 93725-1429 |  | 2013-08-06 | 2013-08-06 16:48 | 2013-08-06 16:50 | CARRIER - 48SDN048090311 | 196 | 8.6 | Yes | Yes | 17.2 | 20.2 | -3 | 8BD1CA0ECC154B419DE952D48C830D37 |  | R22 | Non-TXV |  | 4.388% | 0.95612 | 8.432% | [5 empty] | Non-TXV | 4.388%
Fresno | CA | 93720-2002 |  | 2013-06-20 | 2013-06-20 12:06 | 2013-06-20 12:10 | RHEEM - RRNLB042JK08X | 112 | 3.4 | Yes | Yes | 20 | 19.8 | 0.2 | C4B948D23B22454BB3FF481C4AB04A4D |  | R410A | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Yuba City | CA | 95991-6901 |  | 2013-07-15 | 2013-07-15 13:06 | 2013-07-15 13:28 | CARRIER - 38TXA048330 | 150 | 5.5 | Yes | Yes | 22 | 24.1 | -2.1 | 0710BE84E5D94951AAB6D436FFED52DE |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Chico | CA | 95973-0914 |  | 2013-08-07 | 2013-08-07 10:42 | 2013-08-07 10:59 | GOODMAN - PGB060100-1 | 82 | 10.8 | Yes | Yes | 26.2 | 20.3 | 5.9 | DCD652EE96564ECB9F6C14F1437869D1 |  | R22 | Non-TXV |  | 13.17% | 0.86829 | 25.31% | [5 empty] | Non-TXV | 13.17%
Mendota | CA | 93640-4004 |  | 2013-08-13 | 2013-08-13 13:29 | 2013-08-13 13:48 | AMERICAN STANDARD - 4A7B3036B1000BA | 126 | 4.7 | Yes | Yes | 19 | 20.5 | -1.5 | F5CCF08BCC2C4893BA7A83EC8D056092 |  | R410A | TXV |  | 3.73% | 0.9627 | 7.169% | [5 empty] | TXV | 3.73%
Stockton | CA | 95206-1230 |  | 2013-07-13 | 2013-07-13 10:33 | 2013-07-13 10:56 | BDP - UNK | 66 | 2.3 | Yes | Yes | 18.9 | 18.7 | 0.2 | A95B97484CE240A79ED2152CC2D2D343 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Livingston | CA | 95334-9411 |  | 2013-06-10 | 2013-06-10 13:55 | 2013-06-10 14:16 | PAYNE - 591ANX030000ABAA | 67 | 2.6 | Yes | Yes | 18 | 19.6 | -1.6 | CE36DE21ABA14F268A879407AF1D9F70 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.881% | 0.96119 | 7.458% | [5 empty] | Non-TXV | 3.881%
Stockton | CA | 95219-3535 |  | 2013-08-27 | 2013-08-27 11:53 | 2013-08-27 12:19 | GOODMAN - CK24-1B | 71 | 13.7 | Yes | Yes | 23.9 | 19.3 | 4.6 | EA030FA18D5C45E6963DF3437FFC5684 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.3% | 0.80704 | 37.08% | [5 empty] | Non-TXV | 19.3%
Fresno | CA | 93705-2547 |  | 2013-07-01 | 2013-07-01 10:43 | 2013-07-01 10:46 | RHEEM - RRPLB030JK06X | 76 | 6.3 | Yes | Yes | 19 | 18.6 | 0.4 | 1A67EF8486DC4CF9BE51AABEB2CD8690 |  | R22 | Non-TXV |  | 8.289% | 0.91711 | 15.93% | [5 empty] | Non-TXV | 8.289%
Fresno | CA | 93711-0000 |  | 2013-07-25 | 2013-07-25 10:10 | 2013-07-25 10:11 | RHEEM - UNK | 77 | 12.4 | Yes | Yes | 25.2 | 24.2 | 1 | 283214E95CAC4297997D2CB93EDF033F |  | R22 | Non-TXV |  | 16.1% | 0.83896 | 30.95% | [5 empty] | Non-TXV | 16.1%
Fresno | CA | 93705-4023 |  | 2013-07-09 | 2013-07-09 15:22 | 2013-07-09 15:44 | PAYNE - PA13NR060-C | 275 | 13.7 | Yes | Yes | 20 | 19.3 | 0.7 | 8776727FCFB24B59B70DB1117CDF4EE2 |  | R22 | Non-TXV |  | 4.982% | 0.95018 | 9.574% | [5 empty] | Non-TXV | 4.982%
Yuba City | CA | 95993-9288 |  | 2013-08-07 | 2013-08-07 11:34 | 2013-08-07 11:56 | LENNOX - 13ACC-060-230-01 | 168 | 6.7 | Yes | Yes | 22 | 19.3 | 2.7 | 96BAA0769C9647FDBCAC280943163EFB |  | R22 | TXV |  | 3.988% | 0.96012 | 7.664% | [5 empty] | TXV | 3.988%
Merced | CA | 95348-1522 |  | 2013-08-08 | 2013-08-08 14:06 | 2013-08-08 14:36 | GOODMAN - GPG1330070M41AA | 80 | 6.1 | Yes | Yes | 25.7 | 20.2 | 5.5 | 15B6358E66A8442489954FC7CB34B65D |  | R410A | Non-TXV |  | 7.625% | 0.92375 | 14.65% | [5 empty] | Non-TXV | 7.625%
Fresno | CA | 93706-3512 |  | 2013-07-17 | 2013-07-17 10:47 | 2013-07-17 10:50 | HEIL - NRGF30DDB04 | 53 | 2.3 | Yes | Yes | 17.6 | 20.6 | -3 | 66CCA827CC69471BB1DD213FA00CB029 |  | R22 | Non-TXV |  | 4.34% | 0.9566 | 8.34% | [5 empty] | Non-TXV | 4.34%
Stockton | CA | 95207-4332 |  | 2013-06-27 | 2013-06-27 12:49 | 2013-06-27 13:06 | OTHER - 10AJB30A05 | 68 | 12.7 | Yes | Yes | 19.2 | 19.3 | 0 | 2D537D25ED734884BE05B43CAC7517CE |  | R22 | Non-TXV |  | 18.68% | 0.81324 | 35.89% | [5 empty] | Non-TXV | 18.68%
Yuba City | CA | 95993-8322 |  | 2013-08-07 | 2013-08-07 12:28 | 2013-08-07 12:51 | OTHER - CA5542VKD1 | 98 | -4.7 | Yes | Yes | 22 | 19 | 3 | A1085C8204384AC695FFDAD7264FCAAC |  | R22 | TXV |  | -4.796% | 1.048 | 1.343% |  |  |  |  | TXV |  |  | -4.796%
Mariposa | CA | 95338-9786 |  | 2013-07-31 | 2013-07-31 15:40 | 2013-07-31 15:44 | GOODMAN - GSC130421AA | 143 | 4.2 | Yes | Yes | 19.2 | 19.6 | -0.4 | 016F77A2CB7049D8BED0D0E1AFCF2FAB |  | R22 | Non-TXV |  | 2.937% | 0.97063 | 5.644% | [5 empty] | Non-TXV | 2.937%
Madera | CA | 93638-5505 |  | 2013-07-18 | 2013-07-18 19:58 | 2013-07-18 19:58 | YORK - D1NA036NO5606C | 67 | 0 | Yes | Yes | 18.8 | 21.5 | -2.7 | 80161C4B75F94BFDAD795626785FA968 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mendota | CA | 93640-2110 |  | 2013-08-13 | 2013-08-13 12:33 | 2013-08-13 12:53 | CARRIER - 48SX-024060331AA | 57 | 5.8 | Yes | Yes | 20 | 19.4 | 0.6 | 231AAD74EFEC4E558C115AE69FD7E6DB |  | R22 | Non-TXV |  | 10.18% | 0.89825 | 19.55% | [5 empty] | Non-TXV | 10.18%
Stockton | CA | 95207-2302 |  | 2013-07-17 | 2013-07-17 15:32 | 2013-07-17 15:54 | HEIL - GPCM030K060 | 51 | 5.6 | Yes | Yes | 20.7 | 18.8 | 1.9 | 59373D17A14F438AB551830121117298 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.98% | 0.8902 | 21.1% | [5 empty] | Non-TXV | 10.98%
Stockton | CA | 95212-2114 |  | 2013-06-26 | 2013-06-26 10:59 | 2013-06-26 11:30 | COPELAND - 588ANW042080ACAG | 82 | 2.8 | Yes | Yes | 21.1 | 16.8 | 4.3 | ED04F6892CB545B9A48CAE897F19ECFA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Merced | CA | 95340-3508 |  | 2013-07-22 | 2013-07-22 16:00 | 2013-07-22 16:02 | RHEEM - RRMA-A042JK08X | 114 | 5.1 | Yes | Yes | 24.2 | 20.7 | 3.5 | CF29D84660364BFF8E31C1CD4C2C00B8 |  | R22 | Non-TXV |  | 4.474% | 0.95526 | 8.597% | [5 empty] | Non-TXV | 4.474%
Fresno | CA | 93705-3266 |  | 2013-08-02 | 2013-08-02 17:49 | 2013-08-02 18:15 | WESTINGHOUSE - 352A473G01 | 92 | 13.3 | Yes | Yes | 17.9 | 20.1 | -2.2 | D47B60ED4AF244E6865204802D3FF49B |  | R22 | Non-TXV |  | 14.46% | 0.85543 | 27.78% | [5 empty] | Non-TXV | 14.46%
Gustine | CA | 95322-1424 |  | 2013-10-21 | 2013-10-21 11:01 | 2013-10-21 11:15 | PAYNE - PA13NA024B | 63 | 3.9 | Yes | Yes | 26.3 | 20.4 | 5.9 | 177FC6F5DD464DC59C9F95B9D48CBF1E |  | R410A | TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | TXV | 6.19%
Stockton | CA | 95207-4426 |  | 2013-06-25 | 2013-06-25 13:30 | 2013-06-25 14:08 | OTHER - 80AW24-106 | 69 | 8.6 | Yes | Yes | 18.3 | 15.9 | 2.4 | 182204FDEB3B4842AB9316138378190C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.46% | 0.87536 | 23.95% | [5 empty] | Non-TXV | 12.46%
Madera | CA | 93638-5512 |  | 2013-07-22 | 2013-07-22 10:39 | 2013-07-22 11:49 | YORK - D1NP030N05606A | 73 | 2.2 | Yes | Yes | 20 | 20.7 | -0.7 | 15F26811293948E8B990668F3DC27539 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Stockton | CA | 95206-3806 |  | 2013-07-03 | 2013-07-03 13:06 | 2013-07-03 13:24 | YORK - D1NQ048N09006NXA | 70 | 6.3 | Yes | Yes | 20.5 | 21.4 | -0.9 | CCA2E5598966455380D3B9C3F61FA7F3 |  | R410A | TXV |  | 9% | 0.91 | 17.3% | [5 empty] | TXV | 9%
Fresno | CA | 93720-3018 |  | 2013-08-13 | 2013-08-13 02:49 | 2013-08-13 02:49 | GOODMAN - GPG1549115411AA | 170 | 0 | Yes | Yes | 20.8 | 19.8 | 1 | A525F9E4A9904AA2BB60F55C1C65AA18 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6447 |  | 2013-07-03 | 2013-07-03 08:10 | 2013-07-03 08:30 | GOODMAN - CKL36-1K | 84 | -7.9 | Yes | Yes | 21.2 | 16.6 | 4.6 | B655A9764ECE4B709C6066AF30AA333B |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Fresno | CA | 93703-3210 |  | 2013-06-06 | 2013-06-06 10:47 | 2013-06-06 11:05 | ICP - PGC030K00E | 55 | -3.9 | Yes | Yes | 23.3 | 20.4 | 2.9 | 5029F66E79DD41C6A4B80215C52355AB |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Fresno | CA | 93703-2068 |  | 2013-05-31 | 2013-05-31 15:51 | 2013-06-01 14:58 | YORK - AC042X1021A | 87 | 15.7 | Yes | Yes | 20 | 20.4 | -0.4 | 3A93573E2E754D70BC692F89834D8F73 |  | R22 | Non-TXV |  | 18.05% | 0.81954 | 34.68% | [5 empty] | Non-TXV | 18.05%
Fresno | CA | 93720-0000 |  | 2013-06-24 | 2013-06-24 11:21 | 2013-06-24 11:25 | AIRE-FLO - 13ACC-026-230-025805G112787 | 115 | 3.6 | Yes | Yes | 18.5 | 18.3 | 0.3 | C7F7C422272F41E5AECD228249FAFF9B |  | R22 | Non-TXV |  | 3.13% | 0.9687 | 6.016% | [5 empty] | Non-TXV | 3.13%
Stockton | CA | 95210-3500 |  | 2013-07-10 | 2013-07-10 10:45 | 2013-07-10 11:05 | GOODMAN - CLT36-1B | 140 | 4.3 | Yes | Yes | 22.2 | 18.3 | 3.9 | B24F64F686E84FB2A1CCB05F620CEBFA |  | R22 | Non-TXV |  | 3.071% | 0.96929 | 5.903% | [5 empty] | Non-TXV | 3.071%
San Andreas | CA | 95249-9664 |  | 2013-08-20 | 2013-08-20 10:36 | 2013-08-20 10:55 | RUUD - UAKA-036JAZ | 79 | 5.1 | Yes | Yes | 20 | 20.4 | -0.4 | 77F27FCEE5EA491E94DD8F110008EDC7 |  | R22 | Non-TXV |  | 6.456% | 0.93544 | 12.41% | [5 empty] | Non-TXV | 6.456%
Fresno | CA | 93725-0910 |  | 2013-07-18 | 2013-07-18 13:03 | 2013-07-18 13:09 | GOODMAN - VSC130301BA | 87 | 2.6 | Yes | Yes | 18.7 | 20 | -1.3 | 4064A0E70B00414CB83E0F1BB1FD341D |  | R22 | Non-TXV |  | 2.989% | 0.97011 | 5.743% | [5 empty] | Non-TXV | 2.989%
Fresno | CA | 93727-7121 |  | 2013-06-14 | 2013-06-14 11:49 | 2013-06-14 11:51 | AMERICAN STANDARD - 2YCC30421075AA | 131 | 6.5 | Yes | Yes | 19.5 | 18.2 | 1.3 | CF143F1369E94471B9647BBDA8BFE363 |  | R22 | Non-TXV |  | 4.962% | 0.95038 | 9.536% | [5 empty] | Non-TXV | 4.962%
Fresno | CA | 93726-5529 |  | 2013-07-30 | 2013-07-30 10:05 | 2013-07-30 10:07 | GOODMAN - PGB036075 | 67 | 10.6 | Yes | Yes | 25.2 | 20.9 | 4.3 | C1606F2A3D1941B0850F7E31ABCB8238 |  | R22 | Non-TXV |  | 15.82% | 0.84179 | 30.4% | [5 empty] | Non-TXV | 15.82%
Fresno | CA | 93703-1641 |  | 2013-05-29 | 2013-05-29 12:23 | 2013-05-29 12:42 | CARRIER - 48SZ-042080311AA | 87 | -5.1 | Yes | Yes | 21.6 | 19.5 | 2.1 | 5117167F84D44EC1835A1F4866566C5F |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Fresno | CA | 93720-2362 |  | 2013-06-24 | 2013-06-24 13:22 | 2013-06-24 13:26 | HEIL - CA3048VKA1 | 145 | 5 | Yes | Yes | 21.7 | 18.6 | 3.1 | 7AEF363B279E4F139F5C35DAFE52CE58 |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Merced | CA | 95348-9542 |  | 2013-06-18 | 2013-06-18 14:59 | 2013-06-18 15:07 | LENNOX - 060 | 214 | 8.1 | Yes | Yes | 16.8 | 16.6 | 0.2 | 43304064F8644E35910EDBB790D50583 |  | R22 | Non-TXV |  | 3.785% | 0.96215 | 7.274% | [5 empty] | Non-TXV | 3.785%
Merced | CA | 95348-3371 |  | 2013-06-12 | 2013-06-12 11:20 | 2013-06-12 11:22 | GOODMAN - PGB030050-1 | 56 | 3.7 | Yes | Yes | 18.5 | 18.5 | 0 | D0EE37F8405D4EDE9AB3F7CC8E7E27B4 |  | R22 | Non-TXV |  | 6.607% | 0.93393 | 12.7% | [5 empty] | Non-TXV | 6.607%
Fresno | CA | 93703-1653 |  | 2013-05-30 | 2013-05-30 12:37 | 2013-05-30 13:00 | RUUD - URKA-A042JK083 | 130 | 4 | Yes | Yes | 18.5 | 20.4 | -1.9 | 7D3F89A3629748A4802DCE5DC7DD069B |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Clovis | CA | 93612-5047 |  | 2013-09-25 | 2013-09-25 10:15 | 2013-09-25 10:17 | AMERICAN STANDARD - YCY036G1MOAD | 130 | 10.5 | Yes | Yes | 23.8 | 18.7 | 5.1 | BAF26E708C644501A74E80468E7DC46E |  | R22 | Non-TXV |  | 8.077% | 0.91923 | 15.52% | [5 empty] | Non-TXV | 8.077%
Yuba City | CA | 95993-2305 |  | 2013-08-29 | 2013-08-29 12:11 | 2013-08-29 12:33 | CARRIER - 38CKC048-371 | 101 | 4.1 | Yes | Yes | 19 | 16.6 | 2.4 | F5010A01487E44309096D21EA0FAA57D |  | R22 | Non-TXV |  | 4.059% | 0.95941 | 7.801% | [5 empty] | Non-TXV | 4.059%
Pinedale | CA | 93650-1385 |  | 2013-09-03 | 2013-09-03 13:01 | 2013-09-03 13:02 | CARRIER - 48SDN030060311 | 96 | 16.3 | Yes | Yes | 21.1 | 17.4 | 3.7 | F4A4C4C0CD4E4A6DB594D4CB74D14288 |  | R22 | Non-TXV |  | 16.98% | 0.83021 | 32.63% | [5 empty] | Non-TXV | 16.98%
Los Banos | CA | 93635-3623 |  | 2013-05-31 | 2013-05-31 10:00 | 2013-05-31 10:08 | DUCANE - 2AC13B30P1A | 129 | 8.8 | Yes | Yes | 23.6 | 23.1 | 0.5 | 82B47C261FC04FA0B86B315E42E8698F |  | R22 | Non-TXV |  | 6.822% | 0.93178 | 13.11% | [5 empty] | Non-TXV | 6.822%
Stockton | CA | 95209-4013 |  | 2013-07-17 | 2013-07-17 11:15 | 2013-07-17 11:32 | GUARDIAN - CA42K- | 87 | 12.8 | Yes | Yes | 21.2 | 17.6 | 3.7 | 8C639F2C6BF24AD7B0BF7224148D2700 |  | R22 | Non-TXV |  | 14.71% | 0.85287 | 28.27% | [5 empty] | Non-TXV | 14.71%
Stockton | CA | 95210-3679 |  | 2013-07-09 | 2013-07-09 09:58 | 2013-07-09 10:16 | CARRIER - 591ANX036000AAAA | 85 | -5 | Yes | Yes | 26.1 | 20.1 | 6 | E7D00F298D3D4A2D9B345F36D6FEAB58 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93728-1634 |  | 2013-07-15 | 2013-07-15 12:03 | 2013-07-15 12:05 | ICP - PGD342090K001C1 | 106 | 3.6 | Yes | Yes | 22.3 | 20.4 | 1.9 | B1C7940C48CE45EBA4A6C9D33703F04B |  | R410A | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Fresno | CA | 93705-3238 |  | 2013-07-01 | 2013-07-01 13:43 | 2013-07-01 13:50 | CARRIER - 593ANX036000ACAA | 71 | 6.2 | Yes | Yes | 26.9 | 21.5 | 5.4 | A70700B930154D75B9FB79D7BFEE540F |  | R22 | Non-TXV |  | 8.732% | 0.91268 | 16.78% | [5 empty] | Non-TXV | 8.732%
Yuba City | CA | 95993-1728 |  | 2013-08-21 | 2013-08-21 10:45 | 2013-08-21 11:05 | YORK - H3DH048S06A | 104 | 4.3 | Yes | Yes | 22 | 20.1 | 1.9 | 253D3F38AF0146B99B875BEA95BA647C |  | R22 | TXV |  | 4.135% | 0.95865 | 7.946% | [5 empty] | TXV | 4.135%
Plumas Lake | CA | 95961-9028 |  | 2013-08-19 | 2013-08-19 10:59 | 2013-08-19 11:19 | YORK - H2RA036S06E | 63 | 11.8 | Yes | Yes | 17 | 19.9 | -2.9 | 43ED41D9F49E404298713E7D2D07526B |  | R22 | TXV |  | 18.73% | 0.8127 | 36% | [5 empty] | TXV | 18.73%
Coalinga | CA | 93210-9770 |  | 2013-08-17 | 2013-08-17 13:32 | 2013-08-17 13:53 | GOODMAN - 561AJ048-C | 104 | 6.2 | Yes | Yes | 16.8 | 19 | -2.2 | BD41237304DC4A1C9D3AA79A374F9AA0 |  | R22 | Non-TXV |  | 5.962% | 0.94038 | 11.46% | [5 empty] | Non-TXV | 5.962%
Atascadero | CA | 93422-7648 |  | 2013-08-07 | 2013-08-07 10:25 | 2013-08-07 10:44 | YORK - D1NA024N03606C | 54 | -3.8 | Yes | Yes | 19.7 | 18.7 | 1 | 852A37C5E44E44B997FE44A878E8276C |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Fresno | CA | 93705-2829 |  | 2013-07-01 | 2013-07-01 12:20 | 2013-07-01 12:35 | CARRIER - UNK | 67 | 12.2 | Yes | Yes | 19.2 | 21.7 | -2.5 | 5E3D7EC9BC7A4D44A6EC988CB4B6A9B0 |  | R22 | Non-TXV |  | 18.21% | 0.81791 | 34.99% | [5 empty] | Non-TXV | 18.21%
Los Banos | CA | 93635-5217 |  | 2013-06-04 | 2013-06-04 10:53 | 2013-06-04 10:58 | BRYANT - 561CJ048 | 99 | 5.1 | Yes | Yes | 17.6 | 20.4 | -2.8 | 754A4836F401467B88E37E7911C9CE08 |  | R22 | TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | TXV | 5.152%
Atwater | CA | 95301-4129 |  | 2013-06-06 | 2013-06-06 08:54 | 2013-06-06 08:59 | OTHER - 14AJM36A01 | 130 | 4.1 | Yes | Yes | 16 | 18.5 | -2.5 | 967AB2D50A2C4F04A0C95DE9C1044E7D |  | R410A | Non-TXV |  | 3.154% | 0.96846 | 6.061% | [5 empty] | Non-TXV | 3.154%
Yuba City | CA | 95993-7167 |  | 2013-07-18 | 2013-07-18 12:24 | 2013-07-18 12:42 | TRANE - TTN036C100B3 | 117 | 6.7 | Yes | Yes | 18 | 17.7 | 0.3 | 96D6B8712E4F453B8FAD7B40B74BE385 |  | R22 | TXV |  | 5.726% | 0.94274 | 11.01% | [5 empty] | TXV | 5.726%
Stockton | CA | 95207-7625 |  | 2013-06-25 | 2013-06-25 15:10 | 2013-06-25 15:23 | GOODMAN - GSC130181FA | 75 | -8.7 | Yes | Yes | 20.2 | 18.6 | 1.6 | 25F3EDFA780446AFB31C6B41DB88DCB5 |  | R22 | Non-TXV |  | -11.6% | 1.116 | 3.249% |  |  |  |  | Non-TXV |  |  | -11.6%
Stockton | CA | 95215-7917 |  | 2013-07-02 | 2013-07-02 12:30 | 2013-07-02 13:01 | TRANE - TTD736A100A0 | 70 | 2.6 | Yes | Yes | 14.7 | 14.8 | -0.1 | C104190227004B4F9664CF5BD64F3526 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | Non-TXV | 3.714%
Cutler | CA | 93615-9771 |  | 2013-08-14 | 2013-08-14 11:49 | 2013-08-14 12:10 | UNITARY PRODUCTS GROUP - TCD060S21S1A | 90 | 10.7 | Yes | Yes | 17.5 | 20.4 | -2.9 | 29BBC2B087C249C5B6D28E5587475E12 |  | R22 | Non-TXV |  | 11.89% | 0.88111 | 22.85% | [5 empty] | Non-TXV | 11.89%
Cutler | CA | 93615-9771 |  | 2013-08-14 | 2013-08-14 12:12 | 2013-08-14 12:58 | UNITARY PRODUCTS GROUP - N/A | 90 | 19.9 | Yes | Yes | 15.2 | 18.2 | -3 | 0D6C051386DE4CF88FBB914E856492EE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 22.11% | 0.77889 | 42.49% | [5 empty] | Non-TXV | 22.11%
Fresno | CA | 93720-1614 |  | 2013-06-21 | 2013-06-21 15:23 | 2013-06-21 15:38 | CARRIER - 38GS048310 | 86 | 15.2 | Yes | Yes | 20.1 | 21 | -0.9 | DE7AA725EA224891B2E0F7311B4B48CB |  | R22 | Non-TXV |  | 17.67% | 0.82326 | 33.97% | [5 empty] | Non-TXV | 17.67%
Fresno | CA | 93720-1614 |  | 2013-06-21 | 2013-06-21 15:39 | 2013-06-21 15:50 | CARRIER - 38GS048310 | 86 | 9.2 | Yes | Yes | 22.5 | 21.4 | 1.1 | DB120C3E161E41728DC495CE91C443F4 |  | R22 | Non-TXV |  | 10.7% | 0.89302 | 20.56% | [5 empty] | Non-TXV | 10.7%
Grass Valley | CA | 95945-7949 |  | 2013-06-29 | 2013-06-29 16:30 | 2013-06-29 16:51 | OTHER - UNK | 86 | 13.9 | Yes | Yes | 22 | 16.4 | 5.6 | A2EB893053A54ED0A2B0B6195A18CD1E |  | R22 | Non-TXV |  | 16.16% | 0.83837 | 31.06% | [5 empty] | Non-TXV | 16.16%
Live Oak | CA | 95953-2205 |  | 2013-08-05 | 2013-08-05 11:53 | 2013-08-05 12:09 | WESTINGHOUSE - FS3BC-030KA | 68 | 2.9 | Yes | Yes | 18 | 21 | -3 | 73606E1020844ECFB6BE27AF396DEC6E |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Paso Robles | CA | 93446-5044 |  | 2013-08-08 | 2013-08-08 14:12 | 2013-08-08 14:32 | - 38EN0310SM | 56 | -4.6 | Yes | Yes | 20.6 | 18.5 | 2.1 | 5CB5334DE2CF4A919CD2894FACDBE1F8 |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Atascadero | CA | 93422-5876 |  | 2013-08-08 | 2013-08-08 16:29 | 2013-08-08 16:51 | RHEEM - UNK | 49 | 1.5 | Yes | Yes | 17.2 | 19.9 | -2.7 | 9AF293BF33CA499CA0E040641CE2F00B |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Stockton | CA | 95209-1782 |  | 2013-07-16 | 2013-07-16 11:35 | 2013-07-16 11:35 | TRANE - YCZ060F1MOBD | 195 | 0 | Yes | Yes | 16.4 | 19.1 | -2.7 | FBC36E4FB60149DE898407E43B1E599E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-3012 |  | 2013-08-09 | 2013-08-09 11:52 | 2013-08-09 12:32 | RHEEM - RAKB-036JAZ | 79 | 2.7 | Yes | Yes | 21.5 | 20.4 | 1.1 | 0A3FB6FF70404848B1519D7453B7D749 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Paso Robles | CA | 93446-5010 |  | 2013-09-04 | 2013-09-04 17:57 | 2013-09-04 18:15 | CARRIER - 38EN024310SM | 62 | 2.1 | Yes | Yes | 17.5 | 17.9 | -0.4 | 1D1432EF5D684A00953FCBD8866EFF07 |  | R22 | Non-TXV |  | 3.387% | 0.96613 | 6.509% | [5 empty] | Non-TXV | 3.387%
Lotus | CA | 95651-0000 |  | 2013-10-03 | 2013-10-03 11:57 | 2013-10-03 12:29 | OTHER - UNK | 65 | 7.3 | Yes | Yes | 20 | 20.6 | -0.6 | 9A1307B44CE64DD79952DAEF9CC0DA1C |  | R22 | TXV |  | 11.23% | 0.88769 | 21.58% | [5 empty] | TXV | 11.23%
Fresno | CA | 93720-5355 |  | 2013-08-09 | 2013-08-09 12:12 | 2013-08-09 12:29 | RHEEM - RAKA-048JAZ | 103 | 4.6 | Yes | Yes | 17.4 | 19 | -1.6 | DE3897397EFE4873A937BF78379FF98B |  | R22 | Non-TXV |  | 4.466% | 0.95534 | 8.583% | [5 empty] | Non-TXV | 4.466%
Los Banos | CA | 93635-6407 |  | 2013-06-03 | 2013-06-03 14:43 | 2013-06-03 14:51 | BRYANT - 563CN048 | 164 | 6.8 | Yes | Yes | 21 | 21.4 | -0.4 | 9A31A9E5C3DA4835B2CC67A1179C185A |  | R22 | TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | TXV | 4.146%
Nevada City | CA | 95959-9782 |  | 2013-08-27 | 2013-08-27 14:00 | 2013-08-27 14:00 | - 584BNW042080B | 75 | 0 | Yes | Yes | 22.5 | 20.6 | 1.9 | E600662782124D98845FBF5BCB0BAEEA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-3920 |  | 2013-08-09 | 2013-08-09 09:26 | 2013-08-09 10:52 | BDP - 585HJ036060ACAF | 102 | 16.1 | Yes | Yes | 17.6 | 20.4 | -2.8 | F741029D9A444A71B3A61960F7583243 |  | R22 | Non-TXV |  | 15.78% | 0.84216 | 30.33% | [5 empty] | Non-TXV | 15.78%
Red Bluff | CA | 96080-3546 |  | 2013-07-20 | 2013-07-20 08:31 | 2013-07-20 08:56 | COLEMAN - 9656F801 | 88 | 10 | Yes | Yes | 17.5 | 20.2 | -2.7 | D89DCE33B3344FBFA80787F629EF4E14 |  | R22 | Non-TXV |  | 11.36% | 0.88636 | 21.84% | [5 empty] | Non-TXV | 11.36%
Stockton | CA | 95212-2891 |  | 2013-06-25 | 2013-06-25 11:42 | 2013-06-25 12:15 | CARRIER - 38CKC042350 | 81 | 2.7 | Yes | Yes | 22.8 | 18.7 | 4.1 | AC6A3FDCEF75479DAEC2E5B4AD7EADDA |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Manteca | CA | 95337-7926 |  | 2013-07-30 | 2013-07-30 14:32 | 2013-07-30 14:59 | YORK - H1RA048S06D | 117 | 4.1 | Yes | Yes | 19.6 | 20.1 | -0.5 | 514FCA0A8BBC439E8D67215D8B079DC3 |  | R22 | Non-TXV |  | 3.504% | 0.96496 | 6.734% | [5 empty] | Non-TXV | 3.504%
Stockton | CA | 95207-2805 |  | 2013-06-25 | 2013-06-25 12:47 | 2013-06-25 13:05 | YORK - UNK | 96 | 11.7 | Yes | Yes | 19.7 | 17.5 | 2.3 | C165D22B4D2743F5B8D837CC6343396E |  | R22 | Non-TXV |  | 12.19% | 0.87813 | 23.42% | [5 empty] | Non-TXV | 12.19%
Stockton | CA | 95210-3107 |  | 2013-07-10 | 2013-07-10 11:25 | 2013-07-10 11:42 | HEIL - CA9036VKC1 | 97 | 5 | Yes | Yes | 22.5 | 19.8 | 2.7 | 3784FC2E10DA4D0BAC92224414781F5B |  | R22 | Non-TXV |  | 5.155% | 0.94845 | 9.906% | [5 empty] | Non-TXV | 5.155%
Stockton | CA | 95212-3021 |  | 2013-07-22 | 2013-07-22 12:55 | 2013-07-22 13:15 | YORK - H2RD036S06B | 96 | 6.9 | Yes | Yes | 21.1 | 18.8 | 2.4 | AC0816A83AF54B01B02EE7857690DA2E |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Nevada City | CA | 95959-8638 |  | 2013-08-07 | 2013-08-07 13:12 | 2013-08-07 13:30 | DAY & NIGHT - 585HJW036060ABAF | 102 | 13.6 | Yes | Yes | 25.8 | 21 | 4.8 | 33CEB8AC731A4081865AB171989B10EA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Los Banos | CA | 93635-9465 |  | 2013-06-13 | 2013-06-13 11:30 | 2013-06-13 11:34 | BRYANT - 561CJ042 | 80 | 10.6 | Yes | Yes | 23.8 | 22 | 1.8 | 99D38579346E46F19659345B198BEF4D |  | R22 | TXV |  | 13.25% | 0.8675 | 25.46% | [5 empty] | TXV | 13.25%
Los Banos | CA | 93635-9465 |  | 2013-06-13 | 2013-06-13 11:36 | 2013-06-13 11:49 | BRYANT - 561CJ042 | 80 | 10.1 | Yes | Yes | 22 | 20.9 | 1.1 | 0823A6F2DAE543E3B2AC46821C1B7419 |  | R22 | TXV |  | 12.62% | 0.87375 | 24.26% | [5 empty] | TXV | 12.62%
Stockton | CA | 95210-3458 |  | 2013-07-09 | 2013-07-09 11:33 | 2013-07-09 11:51 | PAYNE - PA10JA036-C | 77 | -4.5 | Yes | Yes | 15.7 | 17.2 | -1.5 | 27CCED3040BA4A0F90340BFE717FD33D |  | R22 | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Red Bluff | CA | 96080-3674 |  | 2013-07-24 | 2013-07-24 21:06 | 2013-07-24 21:25 | BRYANT - 563CNX060000ACAA | 115 | 7.1 | Yes | Yes | 18 | 17.4 | 0.6 | A07E867637F6450DBFE953FC1B67FAB2 |  | R22 | Non-TXV |  | 6.174% | 0.93826 | 11.86% | [5 empty] | Non-TXV | 6.174%
Fresno | CA | 93702-4321 |  | 2013-07-17 | 2013-07-17 03:11 | 2013-07-17 03:11 | BDP - 585C1036075 | 70 | 0 | Yes | Yes | 18.8 | 20.7 | -1.9 | DBD48FF7AC6C497E9BB3B45114893D4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2616 |  | 2013-07-11 | 2013-07-11 10:19 | 2013-07-11 10:22 | LENNOX - 12GCSO36-75-3PA | 110 | 4.7 | Yes | Yes | 21.8 | 19.9 | 1.9 | CDA41647F89E43528506390C606BAA45 |  | R22 | Non-TXV |  | 4.273% | 0.95727 | 8.211% | [5 empty] | Non-TXV | 4.273%
Gustine | CA | 95322-9648 |  | 2013-07-09 | 2013-07-09 15:00 | 2013-07-09 15:03 | BRYANT - 561CJ042- | 80 | 3.2 | Yes | Yes | 23.3 | 20.3 | 3 | EA9E2642A98647348A24DEAA46CDBEF1 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Arbuckle | CA | 95912-0000 |  | 2013-09-12 | 2013-09-12 13:20 | 2013-09-12 13:43 | LENNOX - GCS29X048-100-2PA | 93 | 4.5 | Yes | Yes | 19 | 16.9 | 2.1 | 669762FC807140D8BED0190288DB1BA1 |  | R22 | TXV |  | 4.839% | 0.95161 | 9.299% | [5 empty] | TXV | 4.839%
Plumas Lake | CA | 95961-9044 |  | 2013-08-19 | 2013-08-19 14:26 | 2013-08-19 14:50 | CARRIER - 38CK042350 | 90 | -9 | Yes | Yes | 14.8 | 16.8 | -2 | D28CA37C736A467594A0A8AB260B4436 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Merced | CA | 95348-1335 |  | 2013-06-05 | 2013-06-05 12:27 | 2013-06-05 12:30 | LENNOX - 10ACB30-7P | 69 | 2.2 | Yes | Yes | 17.8 | 19.8 | -2 | E2DB0F0FA78C43FA960A377A5D15DBE1 |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Fresno | CA | 93702-4476 |  | 2013-07-12 | 2013-07-12 10:22 | 2013-07-12 10:24 | GOODMAN - GPG13360701A | 112 | 5 | Yes | Yes | 25 | 19.9 | 5.1 | CAB71E98A09A453EB819614F17F2DD12 |  | R22 | Non-TXV |  | 4.464% | 0.95536 | 8.579% | [5 empty] | Non-TXV | 4.464%
Merced | CA | 95348-3659 |  | 2013-06-07 | 2013-06-07 13:57 | 2013-06-07 13:58 | AMANA - PGD30C0702E | 74 | 3.7 | Yes | Yes | 20.1 | 18.6 | 1.6 | 04E4204123294F4BBF7B5FDA4697B093 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95209-2316 |  | 2013-08-02 | 2013-08-02 08:55 | 2013-08-02 09:14 | RUUD - UAMB-036JBZ | 94 | 3.2 | Yes | Yes | 20.1 | 18.5 | 1.6 | 012BF877C6D34D178D4BEAF08D2FA065 |  | R22 | Non-TXV |  | 3.404% | 0.96596 | 6.542% | [5 empty] | Non-TXV | 3.404%
Chico | CA | 95973-0227 |  | 2013-07-08 | 2013-07-08 20:03 | 2013-07-08 20:27 | COLEMAN - NA | 72 | 12.2 | Yes | Yes | 21.5 | 19.1 | 2.5 | 4AD2CA21F7D948AAB32FB5DA825674FD |  | R22 | Non-TXV |  | 16.94% | 0.83056 | 32.56% | [5 empty] | Non-TXV | 16.94%
Olivehurst | CA | 95961-0000 |  | 2013-06-28 | 2013-06-28 09:55 | 2013-06-28 10:16 | CARRIER - 38TH036300 | 90 | 3.9 | Yes | Yes | 20 | 18 | 2 | A68741C0887143B19CAA89DD3A57EB9C |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Merced | CA | 95348-3799 |  | 2013-06-07 | 2013-06-07 15:52 | 2013-06-07 15:54 | TRANE - 2TTB3030A1000AA | 88 | 4.9 | Yes | Yes | 21.5 | 18.5 | 3 | 99B4D94FA50046B38F2376685327ADD9 |  | R22 | Non-TXV |  | 5.568% | 0.94432 | 10.7% | [5 empty] | Non-TXV | 5.568%
Tracy | CA | 95376-2028 |  | 2013-06-25 | 2013-06-25 13:51 | 2013-06-25 14:13 | YORK - BRCS0361BD | 63 | 3 | Yes | Yes | 25.7 | 19.8 | 5.9 | 46A62B4E1EA3484392FF380D15CA8E7E |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Fresno | CA | 93726-5611 |  | 2013-08-14 | 2013-08-14 10:18 | 2013-08-14 10:36 | OTHER - UNK | 64 | 4.7 | Yes | Yes | 20.7 | 20.4 | 0.3 | F3CDFEB7DDDC4F968769B0855489ADB6 |  | R22 | Non-TXV |  | 7.344% | 0.92656 | 14.11% | [5 empty] | Non-TXV | 7.344%
Plumas Lake | CA | 95961-9011 |  | 2013-08-19 | 2013-08-19 10:09 | 2013-08-19 10:30 | CARRIER - 38CKC030340 | 70 | 2.2 | Yes | Yes | 17 | 19.3 | -2.3 | B762BF3A5D15442DA200DE91C808C40E |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Clovis | CA | 93612-1958 |  | 2013-06-19 | 2013-06-19 18:30 | 2013-06-19 19:01 | BDP - 585HJW030040ABAF | 84 | 9.1 | Yes | Yes | 28.3 | 23.5 | 4.8 | 18B5AB7028EB4545979745695886479B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Madera | CA | 93638-5508 |  | 2013-07-22 | 2013-07-22 19:09 | 2013-07-22 19:09 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 15.8 | 18.7 | -2.9 | 52A3EAEFABC446C5B167711451B8749B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8327 |  | 2013-08-30 | 2013-08-30 11:07 | 2013-08-30 11:40 | CARRIER - 187ANA036-B | 157 | -15.3 | Yes | Yes | 17.5 | 19.1 | -1.6 | C0E42E4D0D1A4B5FB6D82789455F5F4F |  | R410A | TXV |  | -9.745% | 1.0975 | 2.729% |  |  |  |  | TXV |  |  | -9.745%
Fresno | CA | 93702-4637 |  | 2013-06-25 | 2013-06-25 14:38 | 2013-06-26 09:30 | BARD - 563CNOX048000AFAAA | 100 | 6.9 | Yes | Yes | 18.6 | 20.2 | -1.6 | 4FD483D7FF7B40FBAE501BF3072301D5 |  | R22 | Non-TXV |  | 6.9% | 0.931 | 13.26% | [5 empty] | Non-TXV | 6.9%
Riverbank | CA | 95367-4217 |  | 2013-07-12 | 2013-07-12 10:46 | 2013-07-12 11:08 | AMANA - VCA48B2A | 85 | 3.1 | Yes | Yes | 25.5 | 19.8 | 5.7 | B14A862366EB4F33AD42E967FD36E600 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Fresno | CA | 93726-3409 |  | 2013-06-01 | 2013-06-01 13:10 | 2013-06-01 13:23 | CARRIER - 48SX-048100341AA | 88 | 6.3 | Yes | Yes | 22.3 | 18.3 | 4 | F552C13277B74A43B2FD90E7DA499ECD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.159% | 0.92841 | 13.76% | [5 empty] | Non-TXV | 7.159%
Marysville | CA | 95901-4277 |  | 2013-08-20 | 2013-08-20 12:48 | 2013-08-20 13:17 | DAY & NIGHT - 540JJ018 | 83 | 5.4 | Yes | Yes | 17 | 19.5 | -2.5 | 85FB63F5E085455BAB08632007CEB3EA |  | R22 | Non-TXV |  | 6.506% | 0.93494 | 12.5% | [5 empty] | Non-TXV | 6.506%
Plumas Lake | CA | 95961-9019 |  | 2013-10-23 | 2013-10-23 16:00 | 2013-10-23 16:16 | CARRIER - 38CKC030340 | 68 | 6.1 | Yes | Yes | 17.3 | 19.8 | -2.5 | 02585413FD4F405D962EB1571BAA10FA |  | R22 | Non-TXV |  | 8.971% | 0.91029 | 17.24% | [5 empty] | Non-TXV | 8.971%
Merced | CA | 95348-3808 |  | 2013-08-20 | 2013-08-20 14:44 | 2013-08-20 14:46 | YORK - DBYP-F03070A | 73 | 2.7 | Yes | Yes | 19 | 18.6 | 0.4 | 55C3D62B48E4414FACF021DAA48D56EB |  | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Fresno | CA | 93705-3203 |  | 2013-07-01 | 2013-07-01 14:06 | 2013-07-01 14:20 | KENMORE - CA5548VKD2 | 134 | 7.9 | Yes | Yes | 21.8 | 21.3 | 0.5 | 34F9B9387D1F4D98A4948B5DC6CBDFED |  | R22 | Non-TXV |  | 5.896% | 0.94104 | 11.33% | [5 empty] | Non-TXV | 5.896%
Fresno | CA | 93720-2345 |  | 2013-08-08 | 2013-08-08 11:55 | 2013-08-08 11:55 | OTHER - CA3048VKA1 | 138 | -9.7 | Yes | Yes | 18.5 | 20.4 | -1.9 | 99168E5E3261481E927CEE6D7B572EE4 | Remove refrigerant: 9.7 oz | R22 | Non-TXV |  | -7.029% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.029%
Yuba City | CA | 95993-7687 |  | 2013-08-07 | 2013-08-07 13:45 | 2013-08-07 14:07 | BRYANT - 561CJ060-A | 150 | 5.5 | Yes | Yes | 22.5 | 20.7 | 1.8 | 734669BE13A54E0C82EC0CCB96A15A29 |  | R22 | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Plumas Lake | CA | 95961-9062 |  | 2013-08-19 | 2013-08-19 12:46 | 2013-08-19 13:01 | CARRIER - 38CKC036350 | 70 | 3.4 | Yes | Yes | 19 | 18.8 | 0.2 | 9CFD178281A543E89EFD66EFE45E2DB4 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Fresno | CA | 93720-1940 |  | 2013-06-21 | 2013-06-21 09:31 | 2013-06-21 09:33 | BRYANT - 574DNWA36060NATP | 100 | 3.1 | Yes | Yes | 21.5 | 19.5 | 2 | D8065BD0F44C4C55AE8110335A5B4A88 |  | R410A | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Fresno | CA | 93710-6418 |  | 2013-06-03 | 2013-06-03 10:20 | 2013-06-03 10:37 | ARCOAIRE - PGF048Y080A | 102 | -6 | Yes | Yes | 26.9 | 21.2 | 5.7 | F0EC9A9E41674D6EB4F0FED03B7410EF |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Lincoln | CA | 95648-8336 |  | 2013-07-06 | 2013-07-06 12:20 | 2013-07-06 12:47 | YORK - H3RA060S06A | 106 | 5.5 | Yes | Yes | 18 | 21 | -3 | DBF63E1FFC8748E1B79FB7C3B295B831 |  | R22 | Non-TXV |  | 5.189% | 0.94811 | 9.971% | [5 empty] | Non-TXV | 5.189%
Lincoln | CA | 95648-8336 |  | 2013-07-06 | 2013-07-06 12:50 | 2013-07-06 13:08 | YORK - H1RA018S06D | 54 | 3 | Yes | Yes | 19 | 20.6 | -1.6 | 776B6E64417843E3A7300FF6FD34EC32 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Stockton | CA | 95212-3832 |  | 2013-06-27 | 2013-06-27 14:46 | 2013-06-27 15:03 | CARRIER - 38CKC048370 | 131 | 7.6 | Yes | Yes | 16.2 | 18.8 | -2.6 | ECF5A21D097C4FD1AAF2AA990CF40365 |  | R22 | Non-TXV |  | 5.802% | 0.94198 | 11.15% | [5 empty] | Non-TXV | 5.802%
Fresno | CA | 93705-3407 |  | 2013-07-09 | 2013-07-09 13:17 | 2013-07-09 13:37 | LENNOX - 12GCS030X-75-3PA | 85 | 3.8 | Yes | Yes | 18.7 | 21.3 | -2.6 | A2ECE90F7B5B4210A011B97164C924FB |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Chico | CA | 95926-3049 |  | 2013-07-31 | 2013-07-31 12:00 | 2013-07-31 12:19 | DAY & NIGHT - 591ANX030000ABAA | 66 | 4.1 | Yes | Yes | 21.1 | 18.6 | 2.5 | 5A20662187124781B8F983BFE016AD48 |  | R22 | Non-TXV |  | 6.212% | 0.93788 | 11.94% | [5 empty] | Non-TXV | 6.212%
Fresno | CA | 93726-2724 |  | 2013-08-09 | 2013-08-09 11:02 | 2013-08-09 11:04 | YORK - D1NH036N03606A | 104 | 4.2 | Yes | Yes | 17.8 | 19.9 | -2.1 | B7469ABFA309482FAD39EBAF6935C8BB |  | R22 | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
Fresno | CA | 93705-3423 |  | 2013-07-01 | 2013-07-01 12:55 | 2013-07-01 12:57 | GOODMAN - GPG1336070M41CA | 108 | 4.9 | Yes | Yes | 22.2 | 16.6 | 5.6 | C3FC5536A041417AA7DF369D62F29AF6 |  | R410A | Non-TXV |  | 4.537% | 0.95463 | 8.719% | [5 empty] | Non-TXV | 4.537%
Paso Robles | CA | 93446-3511 |  | 2013-08-06 | 2013-08-06 12:00 | 2013-08-06 12:19 | RHEEM - UNK | 77 | 2.6 | Yes | Yes | 16.4 | 18.2 | -1.8 | B1F06319C6E3411089E8074A3BD64B2D |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Fresno | CA | 93703-1649 |  | 2013-06-05 | 2013-06-05 13:33 | 2013-06-05 14:46 | AIRE-FLO - YCY042F1MOAA | 98 | 4.4 | Yes | Yes | 17.9 | 20.1 | -2.2 | F5C9EC3D3BCF458E908A72ABF78E8831 |  | R22 | Non-TXV |  | 4.49% | 0.9551 | 8.628% | [5 empty] | Non-TXV | 4.49%
Yuba City | CA | 95991-8401 |  | 2013-07-17 | 2013-07-17 13:16 | 2013-07-17 13:35 | TRANE - TTL036C100A0 | 152 | 4.5 | Yes | Yes | 23 | 18.2 | 4.8 | D9A7E410DE93448D811693CD9B1245DB |  | R22 | TXV |  | 2.961% | 0.97039 | 5.689% | [5 empty] | TXV | 2.961%
Fresno | CA | 93702-4221 |  | 2013-07-11 | 2013-07-11 11:14 | 2013-07-11 11:17 | GOODMAN - PGP03005701 | 56 | 2.7 | Yes | Yes | 19.4 | 22 | -2.6 | 9803399DA22E4937AD9757EE6F03DC59 |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Chico | CA | 95926-1657 |  | 2013-07-01 | 2013-07-01 19:56 | 2013-07-01 20:22 | LENNOX - GCS29X-036-75-1A | 58 | 4.6 | Yes | Yes | 18.8 | 20.4 | -1.6 | AF0E8C802FDD468CA68D5F756B5896E8 |  | R22 | Non-TXV |  | 7.931% | 0.92069 | 15.24% | [5 empty] | Non-TXV | 7.931%
Tracy | CA | 95376-8609 |  | 2013-07-19 | 2013-07-19 11:44 | 2013-07-19 12:14 | BDP - PA13NRO60-J | 168 | 6.5 | Yes | Yes | 25.5 | 20.2 | 5.3 | 7840006B3CA04CC096DE2B75F5342639 |  | R22 | Non-TXV |  | 3.869% | 0.96131 | 7.435% | [5 empty] | Non-TXV | 3.869%
Manteca | CA | 95336-3419 |  | 2013-07-08 | 2013-07-08 12:02 | 2013-07-08 12:26 | BRYANT - AC035X1021A | 63 | 5.6 | Yes | Yes | 22.7 | 20.2 | 2.5 | 2686DE18E33B495DB88490869FED1EE1 |  | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Atascadero | CA | 93422-5824 |  | 2013-08-09 | 2013-08-09 09:41 | 2013-08-09 09:59 | RHEEM - UNK | 50 | 1.7 | Yes | Yes | 22.3 | 17.7 | 4.6 | 7958036EE64C4E81969AD0A89BB3AC80 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Madera | CA | 93638-1206 |  | 2013-07-25 | 2013-07-25 02:28 | 2013-07-25 02:45 | AMANA - ABA1242070AA | 107 | 3.6 | Yes | Yes | 17.3 | 19.7 | -2.4 | 12E55117A528464CB0067B01E239B32E |  | R22 | Non-TXV |  | 3.364% | 0.96636 | 6.466% | [5 empty] | Non-TXV | 3.364%
Stockton | CA | 95204-3445 |  | 2013-06-25 | 2013-06-25 15:42 | 2013-06-25 16:01 | WESTINGHOUSE - ID024MOA | 69 | 8.6 | Yes | Yes | 18.5 | 16.4 | 2.2 | B0611EBCCD784663B28929C5A9947553 |  | R22 | Non-TXV |  | 12.46% | 0.87536 | 23.95% | [5 empty] | Non-TXV | 12.46%
Los Banos | CA | 93635-8565 |  | 2013-06-04 | 2013-06-04 11:32 | 2013-06-04 11:39 | AMERICAN STANDARD - 2A7B0060A1000AA | 126 | 12.1 | Yes | Yes | 18.5 | 19.8 | -1.3 | FE35B7F7239A4D3091854EFA6E58021D |  | R22 | Non-TXV |  | 9.603% | 0.90397 | 18.46% | [5 empty] | Non-TXV | 9.603%
Madera | CA | 93638-1783 |  | 2013-07-16 | 2013-07-16 20:40 | 2013-07-16 23:36 | - 574BNWO360600NB | 149 | 4.5 | Yes | Yes | 18 | 20.4 | -2.4 | FD2DBE978DE246DBBCB52859D43397F2 |  | R22 | Non-TXV |  | 3.02% | 0.9698 | 5.804% | [5 empty] | Non-TXV | 3.02%
Fresno | CA | 93726-2612 |  | 2013-06-03 | 2013-06-03 12:56 | 2013-06-03 13:12 | YORK - D1NA030N03606C | 76 | 2.3 | Yes | Yes | 21.9 | 18.3 | 3.6 | 8484068262F5467A8B7138C7FFA19FA7 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Marysville | CA | 95901-4055 |  | 2013-06-27 | 2013-06-27 13:12 | 2013-06-27 13:34 | GOODMAN - CPKE18-1A | 75 | 2.8 | Yes | Yes | 15 | 18 | -3 | 4038C6A98A104F7E90CF79CCD239EE67 |  | R22 | TXV |  | 3.733% | 0.96267 | 7.175% | [5 empty] | TXV | 3.733%
Chico | CA | 95928-6817 |  | 2013-07-03 | 2013-07-03 16:53 | 2013-07-03 17:20 | GOODMAN - GPG10360701A | 75 | 2.5 | Yes | Yes | 17 | 19.7 | -2.7 | AB0BB6DBCE4D42A185C3928C1580CC0A |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93705-2214 |  | 2013-07-09 | 2013-07-09 08:45 | 2013-07-09 09:27 | YORK - 22JK | 69 | 5.7 | Yes | Yes | 24.2 | 20.4 | 3.8 | 45FEE048AB914391A2BF46B832FD8430 |  | R22 | Non-TXV |  | 8.261% | 0.91739 | 15.88% | [5 empty] | Non-TXV | 8.261%
Stockton | CA | 95206-6263 |  | 2013-08-19 | 2013-08-19 10:17 | 2013-08-19 10:37 | BRYANT - 38CKC048300 | 102 | 4.6 | Yes | Yes | 23.3 | 18.3 | 5 | 11FAA57F65ED4798822D2E5073713A9D |  | R22 | Non-TXV |  | 4.51% | 0.9549 | 8.667% | [5 empty] | Non-TXV | 4.51%
Fresno | CA | 93726-5518 |  | 2013-07-29 | 2013-07-29 12:58 | 2013-07-29 12:59 | OTHER - RRNAA036JK08X | 114 | 12.3 | Yes | Yes | 22.5 | 19.7 | 2.8 | CD274B16AC62451A86B17442B7FB7190 |  | R22 | Non-TXV |  | 10.79% | 0.89211 | 20.73% | [5 empty] | Non-TXV | 10.79%
Willows | CA | 95988-2062 |  | 2013-08-14 | 2013-08-14 11:33 | 2013-08-14 12:03 | GOODMAN - CK30-1A | 76 | 2.4 | Yes | Yes | 22.1 | 20.4 | 1.7 | 1AA3771228C24308A70352B9932FFEB7 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Fresno | CA | 93725-9793 |  | 2013-07-18 | 2013-07-18 19:06 | 2013-07-18 20:43 | RHEEM - RRGG-07N49JKR | 136 | 4 | Yes | Yes | 24.5 | 18.5 | 6 | 17C7B484823D4FEF964F899B7B62FECB |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95210-1884 |  | 2013-08-14 | 2013-08-14 12:46 | 2013-08-14 13:07 | PAYNE - 5858024050YAC | 51 | 8.6 | Yes | Yes | 20.4 | 21 | -0.6 | AC462301EAA445E7829C3B212A73F59D |  | R22 | Non-TXV |  | 16.86% | 0.83137 | 32.41% | [5 empty] | Non-TXV | 16.86%
Fresno | CA | 93710-4512 |  | 2013-06-07 | 2013-06-07 15:59 | 2013-06-07 16:18 | ARCOAIRE - TCGF4S21S1A | 89 | 3.2 | Yes | Yes | 17.1 | 19 | -1.9 | 237BDD0295634F5BB6FA2AF368D9A671 |  | R22 | Non-TXV |  | 3.596% | 0.96404 | 6.91% | [5 empty] | Non-TXV | 3.596%
Fresno | CA | 93706-5230 |  | 2013-07-17 | 2013-07-17 11:16 | 2013-07-17 11:18 | CARRIER - 48SS-036080321 | 67 | 3.5 | Yes | Yes | 22.7 | 20.1 | 2.7 | 0489067085514C3AAB4B377C9FE82956 |  | R22 | Non-TXV |  | 5.224% | 0.94776 | 10.04% | [5 empty] | Non-TXV | 5.224%
Fresno | CA | 93722-6157 |  | 2013-07-18 | 2013-07-18 12:07 | 2013-07-18 12:08 | OTHER - UNK | 65 | 9 | Yes | Yes | 15.7 | 18.2 | -2.5 | E5FA7FA3E31A4E0487544AEA48F936D7 |  | R22 | Non-TXV |  | 13.85% | 0.86154 | 26.61% | [5 empty] | Non-TXV | 13.85%
Fresno | CA | 93720-1933 |  | 2013-06-25 | 2013-06-25 10:36 | 2013-06-25 10:51 | CARRIER - 48NLT036300 | 96 | 13.2 | Yes | Yes | 23.3 | 19.1 | 4.2 | E884C1551D0345F8811B546EA3B02140 |  | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Stockton | CA | 95207-7520 |  | 2013-06-26 | 2013-06-26 08:54 | 2013-06-26 09:20 | RHEEM - AT-30B10 | 70 | -6.6 | Yes | Yes | 16.4 | 15.3 | 1.1 | 54FA38459E2143EA9C7C1F4838062131 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Marysville | CA | 95901-6860 |  | 2013-06-29 | 2013-06-29 08:40 | 2013-06-29 09:03 | RUUD - UAFD-031JAS | 64 | 2.6 | Yes | Yes | 17.1 | 19.2 | -2.1 | 3A5C0DE7C42B44869CFF98FFAF5F59C6 |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Arbuckle | CA | 95912-9552 |  | 2013-07-31 | 2013-07-31 08:55 | 2013-07-31 08:55 | CARRIER - 38BRC060360 | 200 | 0 | Yes | Yes | 16.5 | 17.7 | -1.2 | 4BE42DEDA771457F87B3552B7FFC31C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-1946 |  | 2013-06-20 | 2013-06-20 11:19 | 2013-06-20 11:24 | CARRIER - UNK | 86 | 15.6 | Yes | Yes | 21.3 | 19.3 | 2 | 3BEEE066C9AB4907A19FAA6B02024450 |  | R410A | Non-TXV |  | 18.14% | 0.8186 | 34.86% | [5 empty] | Non-TXV | 18.14%
Fresno | CA | 93726-0209 |  | 2013-05-28 | 2013-05-28 16:30 | 2013-05-28 16:48 | BRYANT - 585ANW036090AAAF | 82 | 3 | Yes | Yes | 17.6 | 20.4 | -2.8 | DDE9ED2BED064D84944C0D143DA49654 |  | R22 | Non-TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | Non-TXV | 3.659%
Paso Robles | CA | 93446-3207 |  | 2013-09-05 | 2013-09-05 12:00 | 2013-09-05 12:21 | GOODMAN - GSX130361BA | 89 | -6.3 | Yes | Yes | 25.8 | 19.9 | 5.9 | B15E31652F954691A3FB0036932E5548 |  | R410A | Non-TXV |  | -7.079% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.079%
Paso Robles | CA | 93446-5183 |  | 2013-08-12 | 2013-08-12 12:17 | 2013-08-12 12:44 | CARRIER - 38EN024310M | 56 | 3.7 | Yes | Yes | 18.3 | 16.1 | 2.2 | C4D2633B6E7D495ABE682559B9A17DC3 |  | R22 | Non-TXV |  | 6.607% | 0.93393 | 12.7% | [5 empty] | Non-TXV | 6.607%
Stockton | CA | 95219-0000 |  | 2013-07-24 | 2013-07-24 09:54 | 2013-07-24 10:32 | LENNOX - 13ACD-042-230-02 | 111 | 5 | Yes | Yes | 19.7 | 19.9 | -0.1 | 7A37948629F445A58256604F296CB01C |  | R22 | Non-TXV |  | 4.505% | 0.95495 | 8.657% | [5 empty] | Non-TXV | 4.505%
Fresno | CA | 93727-6427 |  | 2013-06-13 | 2013-06-13 15:23 | 2013-06-13 15:26 | BRYANT - 38BR030300 | 100 | 6.2 | Yes | Yes | 19.9 | 19.9 | 0 | FC16238502534573948B6C4DF709BC67 |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Fresno | CA | 93727-5183 |  | 2013-06-14 | 2013-06-14 10:44 | 2013-06-14 10:48 | PAYNE - PA13NRO30-E | 86 | 5.8 | Yes | Yes | 19.9 | 20.4 | -0.5 | 13059FBF242447CBB4C9BA452AE91A52 |  | R22 | Non-TXV |  | 6.744% | 0.93256 | 12.96% | [5 empty] | Non-TXV | 6.744%
Paso Robles | CA | 93446-5080 |  | 2013-08-08 | 2013-08-08 14:46 | 2013-08-08 15:07 | CARRIER - 38EN024310SM | 56 | 3.5 | Yes | Yes | 18.5 | 20.2 | -1.7 | 1F2C1EB3AA414B0482DE26B469F2B7F5 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Merced | CA | 95348-3606 |  | 2013-06-17 | 2013-06-17 11:31 | 2013-06-17 11:34 | AMERICAN STANDARD - YCC030F1MOBC | 69 | 8.9 | Yes | Yes | 19.1 | 19.8 | -0.7 | 4AD442D03BCC44F4929B0166B392EC38 |  | R22 | Non-TXV |  | 12.9% | 0.87101 | 24.79% | [5 empty] | Non-TXV | 12.9%
Grass Valley | CA | 95945-7629 |  | 2013-07-01 | 2013-07-01 11:04 | 2013-07-01 11:04 | CARRIER - 50HS-042---311-- | 128 | 0 | Yes | Yes | 19 | 18.7 | 0.3 | 1C26B6025989449BB09378C20A510927 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-1941 |  | 2013-06-21 | 2013-06-21 16:07 | 2013-06-21 16:10 | RHEEM - RRPLB036JK08X | 92 | 3.1 | Yes | Yes | 23.7 | 21.3 | 2.4 | AB3ADB944096420980FF710559CD13F3 |  | R410A | Non-TXV |  | 3.37% | 0.9663 | 6.476% | [5 empty] | Non-TXV | 3.37%
Fresno | CA | 93727-6486 |  | 2013-07-19 | 2013-07-19 11:08 | 2013-07-19 11:30 | LENNOX - 12ACB42-5P | 125 | 5.8 | Yes | Yes | 18.3 | 20.1 | -1.7 | BAB30027790D41CE83DF241EF48DF563 |  | R22 | Non-TXV |  | 4.64% | 0.9536 | 8.917% | [5 empty] | Non-TXV | 4.64%
Stockton | CA | 95206-6027 |  | 2013-06-27 | 2013-06-27 14:15 | 2013-06-27 14:40 | GOODMAN - CKJ42-1AB | 85 | 19.3 | Yes | Yes | 23.5 | 17.5 | 6 | 7AEAEDA5ED3146489A97212C8F1A761A |  | R22 | Non-TXV |  | 22.71% | 0.77294 | 43.64% | [5 empty] | Non-TXV | 22.71%
Fresno | CA | 93722-4359 |  | 2013-07-16 | 2013-07-16 10:29 | 2013-07-16 10:31 | AMANA - APG13360701C | 112 | 12.4 | Yes | Yes | 20.9 | 18.8 | 2.1 | AB8BA0DC33FB46918C5744BC72DA4A25 |  | R22 | Non-TXV |  | 11.07% | 0.88929 | 21.28% | [5 empty] | Non-TXV | 11.07%
Merced | CA | 95348-3553 |  | 2013-06-11 | 2013-06-11 08:37 | 2013-06-11 08:44 | GOODMAN - CK491B | 97 | 3.5 | Yes | Yes | 25.4 | 19.4 | 6 | CF14CFEC7B954EB19DA66A88F7E91CB0 |  | R22 | Non-TXV |  | 3.608% | 0.96392 | 6.934% | [5 empty] | Non-TXV | 3.608%
Fresno | CA | 93704-2141 |  | 2013-06-25 | 2013-06-25 13:20 | 2013-06-25 13:32 | AMERICAN STANDARD - YCP060F1MOAC | 160 | 20.2 | Yes | Yes | 24.7 | 20.3 | 4.4 | 9FC0E356BBD64D048D695AFBBD8ED21B |  | R22 | Non-TXV |  | 12.62% | 0.87375 | 24.26% | [5 empty] | Non-TXV | 12.62%
Fresno | CA | 93725-1617 |  | 2013-07-18 | 2013-07-18 12:04 | 2013-07-18 13:02 | BDP - 585GJW030040ABAF | 58 | 1.9 | Yes | Yes | 17.1 | 20.1 | -3 | AC321F6022764966AD6C001E47E3F343 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.276% | 0.96724 | 6.295% | [5 empty] | Non-TXV | 3.276%
Marysville | CA | 95901-8297 |  | 2013-07-01 | 2013-07-01 10:43 | 2013-07-01 11:09 | CARRIER - 38CKC042350 | 90 | 2.7 | Yes | Yes | 16 | 18.8 | -2.8 | 63D7E76C5BC347EEBBCAF44C095496CE |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95203-1311 |  | 2013-08-15 | 2013-08-15 08:07 | 2013-08-15 08:07 | LENNOX - GCS20R-411-50-1P | 85 | 0 | Yes | Yes | 18 | 18.6 | -0.6 | 645B8C929AA447AA8AF515300004D553 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2725 |  | 2013-06-01 | 2013-06-01 09:14 | 2013-06-01 09:38 | YORK - D1NH030N05606C | 73 | 2.3 | Yes | Yes | 23 | 20.2 | 2.9 | DA1E01E9E442435393BA903022B5A438 |  | R22 | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Fresno | CA | 93706-5741 |  | 2013-07-17 | 2013-07-17 13:34 | 2013-07-17 13:41 | BRYANT - 563CN042-A | 134 | 4 | Yes | Yes | 21.9 | 20.3 | 1.7 | FFC197295C3D45E0BE0D4B30D1C26350 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Marysville | CA | 95901-3609 |  | 2013-06-27 | 2013-06-27 11:31 | 2013-06-27 11:31 | CARRIER - 585A024055YACR | 51 | 0 | Yes | Yes | 19 | 17.2 | 1.8 | 03B432646B0D4B989D5B207C68A241AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-8200 |  | 2013-07-01 | 2013-07-01 15:10 | 2013-07-01 15:10 | OTHER - CJ36-163 | 106 | 0 | Yes | Yes | 21.5 | 19.6 | 1.9 | 34820BF3C0774ACBA912D17A14D1FA09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3469 |  | 2013-07-25 | 2013-07-25 11:11 | 2013-07-25 11:13 | BDP - 587ANZ024040AAAE | 65 | 10.5 | Yes | Yes | 19.4 | 21.5 | -2.1 | 149140AC95674A279A4DAEF7FAA1CF5F |  | R22 | Non-TXV |  | 16.15% | 0.83846 | 31.04% | [5 empty] | Non-TXV | 16.15%
Fresno | CA | 93722-3469 |  | 2013-07-25 | 2013-07-25 11:14 | 2013-07-25 11:27 | BDP - 587ANZ024040AAAE | 65 | 7.5 | Yes | Yes | 23 | 18.8 | 4.2 | 52A6C834B75D493B901F3DAAA57A3E55 |  | R22 | Non-TXV |  | 11.54% | 0.88462 | 22.17% | [5 empty] | Non-TXV | 11.54%
Clovis | CA | 93612-0790 |  | 2013-08-15 | 2013-08-15 10:43 | 2013-08-15 11:09 | BDP - 585GJW024040ABAE | 54 | 2.7 | Yes | Yes | 18.5 | 20.4 | -1.9 | 3C3F2F1E42B24DABA67ADD1096955D7B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Merced | CA | 95348-3813 |  | 2013-06-12 | 2013-06-12 10:50 | 2013-06-12 10:52 | TRANE - YCC030F1M0BC | 69 | 3.8 | Yes | Yes | 20.9 | 19.1 | 1.9 | F3597DF1395C49F1B1BB2C1825C5610C |  | R22 | Non-TXV |  | 5.507% | 0.94493 | 10.58% | [5 empty] | Non-TXV | 5.507%
Manteca | CA | 95336-8209 |  | 2013-07-18 | 2013-07-18 12:57 | 2013-07-18 13:22 | OTHER - CM 42-13 0 | 80 | 6 | Yes | Yes | 18.7 | 19.3 | -0.6 | BB70A69E096E4DC78016A8D40D25078C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Merced | CA | 95340-2429 |  | 2013-06-06 | 2013-06-06 15:12 | 2013-06-06 15:16 | PAYNE - PA13N0R42-C | 188 | 5.7 | Yes | Yes | 27.8 | 22.1 | 5.7 | 68D81E70ED9F41C58CB8FB91D6ACC0A4 |  | R22 | Non-TXV |  | 3.032% | 0.96968 | 5.827% | [5 empty] | Non-TXV | 3.032%
Parlier | CA | 93648-9667 |  | 2013-07-24 | 2013-07-24 14:54 | 2013-07-24 15:58 | LENNOX - 13ACD-048-230-02 | 204 | 32 | Yes | Yes | 19.5 | 19.1 | 0.4 | 9E8982ACBB27457495B6AB97FD5391E2 | Add refrigerant: 28.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.69% | 0.84314 | 30.15% | [5 empty] | Non-TXV | 15.69%
Stockton | CA | 95205-2572 |  | 2013-07-11 | 2013-07-11 08:48 | 2013-07-11 09:08 | ICP - GPCM36K060F | 85 | 3.8 | Yes | Yes | 15.9 | 13.4 | 2.5 | 0AAB965CC0D64C77B9527626822603E7 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Merced | CA | 95348-3771 |  | 2013-06-08 | 2013-06-08 12:05 | 2013-06-08 12:07 | RHEEM - RRNA-B024JK06X | 70 | 4.2 | Yes | Yes | 18.5 | 18.8 | -0.3 | 3607FDFD7ACC42D2959A827D70AABEC6 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93703-2633 |  | 2013-05-31 | 2013-05-31 12:58 | 2013-05-31 13:16 | GOODMAN - PGB048075-1REVA | 86 | 3.2 | Yes | Yes | 17.2 | 20.1 | -2.9 | F057F4E065044A49AC04E69C1EE183C9 |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Manteca | CA | 95336-7039 |  | 2013-07-30 | 2013-07-30 13:58 | 2013-07-30 14:19 | BRYANT - 563CN036-C | 101 | 3 | Yes | Yes | 18.5 | 18.3 | 0.2 | B09249629B1A4C7EB7B7736496DF9AE3 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Willows | CA | 95988-3543 |  | 2013-08-15 | 2013-08-15 11:03 | 2013-08-15 11:24 | GOODMAN - GSC130181AE | 89 | 6.5 | Yes | Yes | 21.5 | 19.9 | 1.7 | E30D6FA3A0C247FCB8D944D20526B276 |  | R22 | Non-TXV |  | 7.303% | 0.92697 | 14.04% | [5 empty] | Non-TXV | 7.303%
Fresno | CA | 93722-2741 |  | 2013-07-22 | 2013-07-22 09:39 | 2013-07-22 09:42 | CARRIER - 38VKB036330 | 82 | 4.6 | Yes | Yes | 17 | 19.3 | -2.3 | 09D0BCF9D0504D64A8FEDD09D68BAD34 |  | R22 | TXV |  | 5.61% | 0.9439 | 10.78% | [5 empty] | TXV | 5.61%
Fresno | CA | 93726-2723 |  | 2013-06-18 | 2013-06-18 14:32 | 2013-06-18 14:34 | RUUD - URMA-A036JK08E | 99 | 4.5 | Yes | Yes | 21.1 | 20.4 | 0.7 | 13F8CAD74BF343269661D333EDC61A37 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93725-9719 |  | 2013-07-18 | 2013-07-18 10:13 | 2013-07-18 11:19 | CARRIER - 48SS-048030180 | 101 | 24.8 | Yes | Yes | 17.9 | 20.7 | -2.8 | C10DCDFDD2434C34B6684782E15D7C61 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 24.55% | 0.75446 | 47.19% | [5 empty] | Non-TXV | 24.55%
Fresno | CA | 93726-2722 |  | 2013-07-26 | 2013-07-26 08:29 | 2013-07-26 08:43 | OTHER - 48SX036080321 | 84 | 14.2 | Yes | Yes | 23.2 | 20.4 | 2.8 | 5D3C6A959D6D4AF8918920BEC3226C2D |  | R22 | Non-TXV |  | 16.9% | 0.83095 | 32.49% | [5 empty] | Non-TXV | 16.9%
Tracy | CA | 95376-3130 |  | 2013-08-16 | 2013-08-16 10:40 | 2013-08-16 10:58 | BRYANT - 113ANA0330000BEAA | 74 | 10.1 | Yes | Yes | 16.5 | 18.8 | -2.3 | 20CF4627DB0C4A768C27F9ECF15E2295 |  | R410A | Non-TXV |  | 13.65% | 0.86351 | 26.23% | [5 empty] | Non-TXV | 13.65%
Tracy | CA | 95376-3130 |  | 2013-08-16 | 2013-08-16 12:11 | 2013-08-16 12:11 | YORK - UNK | 85 | 0 | Yes | Yes | 16.4 | 18.2 | -1.8 | 7E01678391A447E5ABE78F986F258976 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6334 |  | 2013-07-03 | 2013-07-03 13:24 | 2013-07-03 13:58 | DUCANE - 2AC14L42P1A | 204 | 6.1 | Yes | Yes | 19.9 | 19.1 | 0.8 | E09B138684C84CE7BEFC95D4E74D5B8F |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Oroville | CA | 95966-6622 |  | 2013-08-29 | 2013-08-29 09:32 | 2013-08-29 09:52 | CARRIER - 48GS-036060311 | 70 | -4.1 | Yes | Yes | 20.3 | 18.2 | 2.1 | 41BCEED3C0E84D61B1CA0EDF433F8387 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Stockton | CA | 95205-4312 |  | 2013-07-10 | 2013-07-10 12:17 | 2013-07-10 12:49 | OTHER - 2AC13L18P-A1 | 67 | 4 | Yes | Yes | 22.5 | 22.7 | -0.1 | F8D61496C4774C5E89848762E846C086 |  | R22 | Non-TXV |  | 5.97% | 0.9403 | 11.47% | [5 empty] | Non-TXV | 5.97%
Isleton | CA | 95641-0000 |  | 2013-08-27 | 2013-08-27 08:35 | 2013-08-27 09:16 | NORDYNE - FS3CB-030KA | 68 | 4.1 | Yes | Yes | 20.8 | 16.5 | 4.3 | DD34D93470C1436EB3F8227B2DD00548 |  | R22 | Non-TXV |  | 6.029% | 0.93971 | 11.59% | [5 empty] | Non-TXV | 6.029%
Fresno | CA | 93722-3312 |  | 2013-07-18 | 2013-07-18 12:36 | 2013-07-18 12:47 | CARRIER - UNK | 68 | 14.8 | Yes | Yes | 20.1 | 17.6 | 2.5 | 775918FB45C6480D9E9AFB476C14B039 |  | R22 | Non-TXV |  | 21.76% | 0.78235 | 41.83% | [5 empty] | Non-TXV | 21.76%
Merced | CA | 95340-1560 |  | 2013-06-06 | 2013-06-06 10:28 | 2013-06-06 10:31 | GOODMAN - GPG13360701A | 112 | 4.4 | Yes | Yes | 24.5 | 18.8 | 5.7 | AE9597507E0F45F8865F090AD8D97100 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Oroville | CA | 95965-4505 |  | 2013-07-25 | 2013-07-25 13:00 | 2013-07-25 15:12 | BRYANT - 555AMX63000ABBA | 53 | 15.1 | Yes | Yes | 23.4 | 24.8 | -1.4 | 52EB61E5EBA44E41BC5DAE64322F31B2 |  | R410A | Non-TXV |  | 28.49% | 0.71509 | 54.75% | [5 empty] | Non-TXV | 28.49%
Madera | CA | 93637-5399 |  | 2013-07-09 | 2013-07-09 11:49 | 2013-07-09 13:29 | LENNOX - PGE10A30D075-1PA | 55 | -5.2 | Yes | Yes | 18.5 | 20.2 | -1.7 | 022AA765680B49728C737F6D038DB6D1 |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Fresno | CA | 93705-3519 |  | 2013-07-09 | 2013-07-09 12:02 | 2013-07-09 12:30 | PAYNE - 584AN030040AD | 67 | 4 | Yes | Yes | 22.3 | 21.5 | 0.8 | 90DE3A46A2EB4E958C8CE9C8E78A12F5 |  | R22 | Non-TXV |  | 5.97% | 0.9403 | 11.47% | [5 empty] | Non-TXV | 5.97%
Fresno | CA | 93710-7110 |  | 2013-06-04 | 2013-06-04 12:07 | 2013-06-04 12:23 | BRYANT - 550AN042-E | 140 | -8.2 | Yes | Yes | 22.3 | 18.8 | 3.6 | 837B0424CD56458AB66EB684E311C25B |  | R410A | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Willows | CA | 95988-2228 |  | 2013-08-15 | 2013-08-15 08:39 | 2013-08-15 09:15 | BRYANT - 574BNW048090NA | 179 | 15.5 | Yes | Yes | 23.4 | 20 | 3.5 | 120F7E1B28594D23B282E6E45199047B |  | R410A | Non-TXV |  | 8.659% | 0.91341 | 16.64% | [5 empty] | Non-TXV | 8.659%
Stockton | CA | 95206-6214 |  | 2013-07-25 | 2013-07-25 15:52 | 2013-07-25 16:32 | BDP - 598WN036-A | 184 | 13.5 | Yes | Yes | 18.1 | 19.3 | -1.2 | 1B9F1AF5EBE34F4490D776E2DDB62E26 |  | R22 | Non-TXV |  | 7.337% | 0.92663 | 14.1% | [5 empty] | Non-TXV | 7.337%
Manteca | CA | 95336-3450 |  | 2013-07-10 | 2013-07-10 08:10 | 2013-07-10 08:37 | GE - BG7A730B1A0 | 51 | 8.1 | Yes | Yes | 17.7 | 19.2 | -1.5 | A3FB9E2AE44942F4882D1FCDECE2CBCD |  | R22 | Non-TXV |  | 15.88% | 0.84118 | 30.52% | [5 empty] | Non-TXV | 15.88%
Fresno | CA | 93703-3260 |  | 2013-08-08 | 2013-08-08 11:24 | 2013-08-08 11:26 | LENNOX - 13ACX03023002 | 86 | 3.5 | Yes | Yes | 24.5 | 20.6 | 3.9 | 33B502D4E4B54E569C564796DF09D95A |  | R410A | Non-TXV |  | 4.07% | 0.9593 | 7.821% | [5 empty] | Non-TXV | 4.07%
Fresno | CA | 93705-4430 |  | 2013-07-19 | 2013-07-19 11:19 | 2013-07-19 11:22 | OTHER - GR6GD-X42K096X | 115 | 5.4 | Yes | Yes | 21.8 | 19.3 | 2.5 | 5F19CBD2A0DF4667B3066A9A041C6834 |  | R410A | TXV |  | 4.696% | 0.95304 | 9.024% | [5 empty] | TXV | 4.696%
Fresno | CA | 93727-3200 |  | 2013-06-11 | 2013-06-11 12:35 | 2013-06-11 12:35 | DAY & NIGHT - N/A | 90 | 0 | Yes | Yes | 19.5 | 18.8 | 0.7 | F3EC3DA56E1542DBBCFF841AD5B64A35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-4832 |  | 2013-07-10 | 2013-07-10 11:38 | 2013-07-10 12:05 | GOODMAN - CK36-1B | 85 | 16 | Yes | Yes | 19.7 | 19.9 | -0.2 | E4BCB14BF9944513A8FB1BA2311DC506 |  | R22 | Non-TXV |  | 18.82% | 0.81176 | 36.17% | [5 empty] | Non-TXV | 18.82%
Fresno | CA | 93703-3229 |  | 2013-06-03 | 2013-06-03 15:29 | 2013-06-04 03:19 | LENNOX - 13ACX-02 | 70 | 2.9 | Yes | Yes | 21 | 21.1 | -0.1 | 1B6F9927F05645C9ABE514B9955D994D |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Stockton | CA | 95206-6442 |  | 2013-07-30 | 2013-07-30 12:37 | 2013-07-30 12:56 | CARRIER - 38CKC030340 | 66 | 2.3 | Yes | Yes | 18.9 | 19.7 | -0.8 | 7AD863995F04401796B15ACC74FC9C4A |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Marysville | CA | 95901-8067 |  | 2013-07-12 | 2013-07-12 09:09 | 2013-07-12 09:33 | YORK - H3RD042S06G | 152 | -5.5 | Yes | Yes | 21 | 17 | 4 | 4CA45DCF921A487E9F1A2BFFCC7A93F0 |  | R22 | TXV |  | -3.618% | 1.0362 | 1.013% |  |  |  |  | TXV |  |  | -3.618%
Fresno | CA | 93727-6492 |  | 2013-06-17 | 2013-06-17 12:39 | 2013-06-17 12:42 | LENNOX - 12ACB48-5P | 171 | 7.1 | Yes | Yes | 20.2 | 20.7 | -0.5 | 3EC9F74A417E46C899ACCBED261264E8 |  | R22 | Non-TXV |  | 4.152% | 0.95848 | 7.979% | [5 empty] | Non-TXV | 4.152%
Nevada City | CA | 95959-9730 |  | 2013-09-10 | 2013-09-10 12:01 | 2013-09-10 12:01 | NORDYNE - GS3BA-048KA | 115 | 0 | Yes | Yes | 18.1 | 17.7 | 0.4 | 912541D3A0C0463F9110EB0995716A69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-4346 |  | 2013-07-12 | 2013-07-12 12:35 | 2013-07-12 13:16 | UNITARY PRODUCTS GROUP - DAYA-F036N070CNNJM157735 | 85 | 2.8 | Yes | Yes | 21.5 | 18.7 | 2.8 | DDFD87CB8D28411F83A337FA45598344 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Stockton | CA | 95210-1702 |  | 2013-06-27 | 2013-06-27 10:43 | 2013-06-27 11:01 | RHEEM - RRNA-B036JK06X | 83 | -4.9 | Yes | Yes | 21.4 | 19.2 | 2.2 | 4BB658D05B754656BA795A059BC4C79C |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Selma | CA | 93662-2128 |  | 2013-07-31 | 2013-07-31 09:51 | 2013-07-31 09:51 | ICP - PGCO42K080B | 87 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | D08E922D6F6F48F9B5A58321DEDA9D74 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-8230 |  | 2013-07-17 | 2013-07-17 12:00 | 2013-07-17 12:24 | LENNOX - HS25-11-2P | 216 | 8.4 | Yes | Yes | 20 | 19.2 | 0.8 | 302F8A69839844E79D8067EA201B396F |  | R22 | TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | TXV | 3.889%
Plumas Lake | CA | 95961-9106 |  | 2013-08-19 | 2013-08-19 15:35 | 2013-08-19 15:58 | CARRIER - 38CK042350 | 90 | -8.5 | Yes | Yes | 14 | 16.8 | -2.8 | 483113378E624FA5A89BCE9D1600C2C5 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Kingsburg | CA | 93631-1739 |  | 2013-08-01 | 2013-08-01 15:41 | 2013-08-01 16:00 | - | 80 | 2.5 | Yes | Yes | 23.5 | 20.8 | 2.7 | 5D2CA829C8F04C1AAB0B2F7C8C66ACAC |  | R22 | Non-TXV |  | 3.125% | 0.5 | 96.09% | [5 empty] | Non-TXV | 3.125%
Selma | CA | 93662-9730 |  | 2013-08-01 | 2013-08-01 12:00 | 2013-08-01 12:42 | GOODMAN - CKL24-1K | 76 | 2.7 | Yes | Yes | 16.5 | 18.9 | -2.4 | 20A243200AB647D6A72A7A0052917471 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Clovis | CA | 93612-3326 |  | 2013-08-15 | 2013-08-15 17:32 | 2013-08-15 17:51 | LENNOX - 10GCS030X-75-3PA | 51 | 2.4 | Yes | Yes | 17.7 | 20.7 | -3 | B9CC6674BF2541F58CD8604465CE33D7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Atascadero | CA | 93422-5827 |  | 2013-08-07 | 2013-08-07 16:00 | 2013-08-07 16:19 | GOODMAN - GPG1324045M41AB | 80 | 2.4 | Yes | Yes | 25.4 | 19.5 | 6 | 181E7DC598CA49D7B0945D273CE3F89F |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93703-0000 |  | 2013-08-27 | 2013-08-27 09:09 | 2013-08-27 09:13 | TRANE - 2TTR4060A1000AA | 211 | 15.5 | Yes | Yes | 25.4 | 20.4 | 5 | 6A6969A1D75B40A4BC324794CF4EF2D5 |  | R22 | Non-TXV |  | 7.346% | 0.92654 | 14.12% | [5 empty] | Non-TXV | 7.346%
Plumas Lake | CA | 95961-9069 |  | 2013-08-19 | 2013-08-19 13:02 | 2013-08-19 13:24 | CARRIER - 38CKC036350 | 70 | 8.3 | Yes | Yes | 14.5 | 17.2 | -2.7 | A29287289F494114961567A59D49426C |  | R22 | Non-TXV |  | 11.86% | 0.88143 | 22.79% | [5 empty] | Non-TXV | 11.86%
Atascadero | CA | 93422-7633 |  | 2013-08-07 | 2013-08-07 16:52 | 2013-08-07 17:09 | PAYNE - PA10JA030-G | 66 | -3.9 | Yes | Yes | 21.3 | 19.7 | 1.6 | 8BD3744675A6467AB0F69EAE0D3B4737 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Los Banos | CA | 93635-9300 |  | 2013-06-03 | 2013-06-03 17:27 | 2013-06-03 17:31 | NORDYNE - JS3BA030KA | 68 | 5.8 | Yes | Yes | 18.2 | 19.9 | -1.7 | 8937ABA92DEE4471BF23A3C13B12CB64 |  | R22 | Non-TXV |  | 8.529% | 0.91471 | 16.39% | [5 empty] | Non-TXV | 8.529%
Stockton | CA | 95219-3547 |  | 2013-07-24 | 2013-07-24 11:18 | 2013-07-24 11:40 | RHEEM - UNK | 64 | 5.5 | Yes | Yes | 16.9 | 19.4 | -2.5 | DD1F83EBA6EC4A4FBAFBF3FCCB325E86 |  | R22 | Non-TXV |  | 8.594% | 0.91406 | 16.52% | [5 empty] | Non-TXV | 8.594%
Madera | CA | 93637-2810 |  | 2013-07-24 | 2013-07-24 23:33 | 2013-07-24 23:54 | BDP - 58ANW036080ACF | 67 | 2.2 | Yes | Yes | 16.8 | 19.7 | -2.9 | 94F570E5712D469A9E7B1BEC01972240 |  | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Sonora | CA | 95370-9298 |  | 2013-09-06 | 2013-09-06 13:08 | 2013-09-06 13:26 | YORK - H1RA048S06D | 117 | 17.1 | Yes | Yes | 20.2 | 20.4 | -0.2 | C9CD25B7B18744948DC9E4442D77AA24 |  | R22 | Non-TXV |  | 14.62% | 0.85385 | 28.09% | [5 empty] | Non-TXV | 14.62%
Marysville | CA | 95901-4287 |  | 2013-08-30 | 2013-08-30 10:08 | 2013-08-30 10:25 | BDP - 540JJ018 | 83 | 2.8 | Yes | Yes | 15.6 | 17.1 | -1.5 | A9ADAE30A7BF41C5849E9073D15189A1 |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Oroville | CA | 95966-6401 |  | 2013-08-29 | 2013-08-29 08:35 | 2013-08-29 08:57 | TRANE - 2YCX3042A1075AA | 131 | -9.2 | Yes | Yes | 25.1 | 19.6 | 5.6 | 76FF8075F1424B239D99C34DF6F3A298 |  | R22 | Non-TXV |  | -7.023% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.023%
Ione | CA | 95640-0000 |  | 2013-07-24 | 2013-07-24 14:43 | 2013-07-24 15:09 | TRANE - 2TTB0030A1000AA | 64 | 5.9 | Yes | Yes | 16 | 18.7 | -2.7 | C8CDDBF2101A4CC4B6C06DA0F4E5832A |  | R22 | Non-TXV |  | 9.219% | 0.90781 | 17.72% | [5 empty] | Non-TXV | 9.219%
Fresno | CA | 93710-3820 |  | 2013-06-08 | 2013-06-08 08:56 | 2013-06-08 09:20 | PAYNE - N/A | 69 | 3 | Yes | Yes | 18.2 | 20.1 | -1.9 | 2983019F8A6949C2B82363038E97795A |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Chico | CA | 95928-6471 |  | 2013-08-05 | 2013-08-05 15:52 | 2013-08-05 16:17 | BDP - 585CJ02450 | 72 | 4.5 | Yes | Yes | 23.8 | 19.5 | 4.3 | 46945B1AE3D149ACA7954F5D821143C4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Plumas Lake | CA | 95961-9027 |  | 2013-08-19 | 2013-08-19 15:04 | 2013-08-19 15:28 | CARRIER - 38CKC036350 | 75 | -3.8 | Yes | Yes | 15 | 17.2 | -2.2 | ABA80816AE8A44E2B133604DE3C1D61E |  | R22 | TXV |  | -5.067% | 1.0507 | 1.419% |  |  |  |  | TXV |  |  | -5.067%
Atascadero | CA | 93422-7633 |  | 2013-08-14 | 2013-08-14 17:28 | 2013-08-14 17:51 | YORK - H4DU030S06A | 80 | 3.8 | Yes | Yes | 18.8 | 20.8 | -2 | ED8036E075414F589AE3AC2A7D835DE6 |  | R22 | Non-TXV |  | 4.75% | 0.9525 | 9.128% | [5 empty] | Non-TXV | 4.75%
Olivehurst | CA | 95961-0000 |  | 2013-06-28 | 2013-06-28 09:06 | 2013-06-28 09:28 | TEMPSTAR - PGAA36C1K4 | 69 | 13.6 | Yes | Yes | 20.5 | 20.7 | -0.2 | 6C905DAC0CF14D248FBDBC07F367CE6E |  | R22 | Non-TXV |  | 19.71% | 0.8029 | 37.88% | [5 empty] | Non-TXV | 19.71%
Los Banos | CA | 93635-6368 |  | 2013-06-13 | 2013-06-13 13:16 | 2013-06-13 13:21 | PAYNE - PA10JA036 | 72 | 10.3 | Yes | Yes | 19.1 | 19.3 | -0.2 | 14F749B7E9F74AAF983C098507B89DBF |  | R22 | TXV |  | 14.31% | 0.85694 | 27.49% | [5 empty] | TXV | 14.31%
Dinuba | CA | 93618-3346 |  | 2013-06-26 | 2013-06-26 17:10 | 2013-06-26 17:43 | RHEEM - RRMA-A036JK08X | 99 | 2.9 | Yes | Yes | 20.8 | 17.5 | 3.3 | 19CCEE961F644980A9B43AA27FB661B3 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Fresno | CA | 93726-1139 |  | 2013-06-10 | 2013-06-10 13:18 | 2013-06-10 14:28 | GOODMAN - PGB03606075-1 | 60 | 2.5 | Yes | Yes | 17.4 | 19.5 | -2.1 | DA4793D2B80E4A02BC1DC218149C05EA |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Merced | CA | 95348-2842 |  | 2013-06-07 | 2013-06-07 11:18 | 2013-06-07 11:20 | BRYANT - 582ANW030040AAAD | 55 | 4.5 | Yes | Yes | 23.8 | 19.1 | 4.8 | 9AFB558AD836478AAB6821FF648D96BE |  | R22 | Non-TXV |  | 8.182% | 0.91818 | 15.72% | [5 empty] | Non-TXV | 8.182%
Grass Valley | CA | 95945-5606 |  | 2013-08-22 | 2013-08-22 09:57 | 2013-08-22 09:57 | BDP - 588ANW030060ADAD | 56 | 0 | Yes | Yes | 25.2 | 20.4 | 4.8 | CDEC34BD2DBC452288E8E4964DBDB654 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-8492 |  | 2013-09-24 | 2013-09-24 13:19 | 2013-09-24 13:40 | BARD - PH31 | 82 | 9.8 | Yes | Yes | 19.9 | 19.9 | 0 | DCE4C3310ED846F2974B0DF44C17A6E1 |  | R22 | Non-TXV |  | 11.95% | 0.88049 | 22.97% | [5 empty] | Non-TXV | 11.95%
Paradise | CA | 95969-3666 |  | 2013-06-28 | 2013-06-28 20:31 | 2013-06-28 20:59 | YORK - 16BNA030-A | 73 | 4.4 | Yes | Yes | 21 | 19.2 | 1.8 | 10BF6E989CA1480FBF9CA0EA1AEECABB |  | R22 | TXV |  | 6.027% | 0.93973 | 11.58% | [5 empty] | TXV | 6.027%
Stockton | CA | 95206-6111 |  | 2013-07-08 | 2013-07-08 13:55 | 2013-07-08 14:14 | RUUD - UAMA036JB2 | 96 | 7.6 | Yes | Yes | 20.4 | 18.5 | 1.9 | B652FDB3F4374CA2B17AACAFF2D4865E |  | R22 | Non-TXV |  | 7.917% | 0.92083 | 15.21% | [5 empty] | Non-TXV | 7.917%
Tracy | CA | 95377-7933 |  | 2013-08-12 | 2013-08-12 13:26 | 2013-08-12 13:45 | GOODMAN - CKT42-1AB | 125 | 5.7 | Yes | Yes | 20.4 | 19.1 | 1.4 | 0954DF5D1D1B4267BE680BE1E37CC25D |  | R22 | Non-TXV |  | 4.56% | 0.9544 | 8.763% | [5 empty] | Non-TXV | 4.56%
Livingston | CA | 95334-1864 |  | 2013-06-10 | 2013-06-10 11:59 | 2013-06-10 12:22 | GOODMAN - GP1336070M41AB | 85 | 2.5 | Yes | Yes | 21.8 | 18.7 | 3.1 | 75840182862A4AD18A896E8D3264C018 |  | R410A | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95209-2345 |  | 2013-07-12 | 2013-07-12 12:06 | 2013-07-12 12:25 | RHEEM - UNK | 96 | 8 | Yes | Yes | 23.4 | 19.7 | 3.7 | 508CDB908B82410F946345FEED5E7D74 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Camino | CA | 95709-9636 |  | 2013-07-29 | 2013-07-29 15:56 | 2013-07-29 16:22 | TRANE - YCX048F1H0BA | 161 | 5.9 | Yes | Yes | 24 | 21.9 | 2.1 | 731A06D7BAA74E5196DA5602FC3F95C4 |  | R22 | TXV |  | 3.665% | 0.96335 | 7.043% | [5 empty] | TXV | 3.665%
Tracy | CA | 95377-8416 |  | 2013-07-23 | 2013-07-23 16:30 | 2013-07-23 16:57 | CARRIER - 38EZG036310 | 99 | 3.4 | Yes | Yes | 18.8 | 19.9 | -1.1 | D347CCB53FD44E83B0DD812D1389F247 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.434% | 0.96566 | 6.6% | [5 empty] | Non-TXV | 3.434%
Winton | CA | 95388-9573 |  | 2013-06-14 | 2013-06-14 13:28 | 2013-06-14 13:32 | RHEEM - UNK | 56 | 4.6 | Yes | Yes | 20.2 | 17.7 | 2.5 | 476E9BB97BC648E5961BC7C625E5F2A6 |  | R22 | Non-TXV |  | 8.214% | 0.91786 | 15.79% | [5 empty] | Non-TXV | 8.214%
Merced | CA | 95340-3349 |  | 2013-06-06 | 2013-06-06 14:25 | 2013-06-06 14:35 | OTHER - GR6GD-X36K072X | 112 | 5.4 | Yes | Yes | 22.9 | 20.3 | 2.7 | E5C981EA77A541BBB857BD4F964D9752 |  | R410A | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Camino | CA | 95709-0000 |  | 2013-07-29 | 2013-07-29 14:57 | 2013-07-29 14:57 | DAY & NIGHT - 691ANX042000AAAA | 180 | 0 | Yes | Yes | 20.5 | 23.3 | -2.8 | 3D35D4BBDCA34A03A98A9E04282BCDB4 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4922 |  | 2013-06-18 | 2013-06-18 12:31 | 2013-06-18 12:33 | DAY & NIGHT - 7777UNK | 96 | 4.2 | Yes | Yes | 22.8 | 20.4 | 2.4 | A05822F2E6F04B6E98EB2427893A08A3 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Merced | CA | 95348-2727 |  | 2013-07-03 | 2013-07-03 13:30 | 2013-07-03 13:35 | YORK - H1RD036S06G | 145 | 20.6 | Yes | Yes | 23.5 | 19 | 4.5 | F051CFC917CE4036931FB46528C32B06 |  | R22 | Non-TXV |  | 14.21% | 0.85793 | 27.3% | [5 empty] | Non-TXV | 14.21%
Fresno | CA | 93710-6224 |  | 2013-06-03 | 2013-06-03 13:20 | 2013-06-03 13:41 | DAY & NIGHT - UNK | 96 | 6.9 | Yes | Yes | 23.2 | 20.4 | 2.8 | 47380FA573E14850A45A9CED92F370DB |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Stockton | CA | 95209-2044 |  | 2013-09-19 | 2013-09-19 11:47 | 2013-09-19 12:05 | HEIL - ACS036A2C1 | 83 | 3 | Yes | Yes | 20.6 | 19.9 | 0.7 | A21D68EE05864DE480F63CE40AAF172D |  | R22 | Non-TXV |  | 3.614% | 0.96386 | 6.946% | [5 empty] | Non-TXV | 3.614%
Dinuba | CA | 93618-3616 |  | 2013-07-30 | 2013-07-30 16:23 | 2013-07-30 16:43 | RUUD - N/A | 90 | 4.5 | Yes | Yes | 21.9 | 19.3 | 2.6 | 8781CA82988941F3874C83691764306B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Los Banos | CA | 93635-9696 |  | 2013-07-12 | 2013-07-12 10:41 | 2013-07-12 10:56 | AMERICAN STANDARD - 2A7B0036A1000AA | 76 | 10.6 | Yes | Yes | 17 | 17.6 | -0.6 | 659AB5E397EC4FE0B547BABD5A5F3C8F |  | R22 | Non-TXV |  | 13.95% | 0.86053 | 26.8% | [5 empty] | Non-TXV | 13.95%
Los Banos | CA | 93635-9696 |  | 2013-07-12 | 2013-07-12 11:19 | 2013-07-12 11:20 | AMERICAN STANDARD - 2A7B0036A1000AA | 76 | 8.2 | Yes | Yes | 17.6 | 17.6 | 0 | 2D3046BD41E141A396EDF52E13A26DA6 |  | R22 | Non-TXV |  | 10.79% | 0.89211 | 20.73% | [5 empty] | Non-TXV | 10.79%
Yuba City | CA | 95991-6414 |  | 2013-07-16 | 2013-07-16 13:35 | 2013-07-16 13:54 | LENNOX - 10AC-036-230-02 | 74 | 2.9 | Yes | Yes | 17 | 19.3 | -2.3 | 20CBD1717DFF4D63BA8274C97B210867 |  | R22 | TXV |  | 3.919% | 0.96081 | 7.531% | [5 empty] | TXV | 3.919%
Rocklin | CA | 95765-5430 |  | 2013-08-22 | 2013-08-22 15:19 | 2013-08-22 15:39 | GOODMAN - CKJ48-1A | 109 | 8.1 | Yes | Yes | 27 | 22.8 | 4.2 | 934A2055278C434E9190AC655FD094BA |  | R22 | Non-TXV |  | 7.431% | 0.92569 | 14.28% | [5 empty] | Non-TXV | 7.431%
Lincoln | CA | 95648-8129 |  | 2013-08-06 | 2013-08-06 16:49 | 2013-08-06 17:09 | YORK - H2RC036S06G | 83 | 9.3 | Yes | Yes | 18.4 | 19.9 | -1.5 | 771494080E5B4ACFAD3F6C6671E71688 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.2% | 0.88795 | 21.53% | [5 empty] | Non-TXV | 11.2%
Lincoln | CA | 95648-8129 |  | 2013-08-06 | 2013-08-06 17:15 | 2013-08-06 17:15 | YORK - E1RC018S06G | 93 | 0 | Yes | Yes | 20.3 | 22.6 | -2.3 | 25E93F5AA8284B2A8E4561ED3539CC5E |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3412 |  | 2013-07-02 | 2013-07-02 16:48 | 2013-07-02 18:00 | DAY & NIGHT - N/A | 90 | 3.1 | Yes | Yes | 20 | 18.8 | 1.3 | C8CA7D904E6140B1ACA03C8B3559256A |  | R22 | Non-TXV |  | 3.444% | 0.96556 | 6.619% | [5 empty] | Non-TXV | 3.444%
Paradise | CA | 95969-5218 |  | 2013-08-05 | 2013-08-05 12:22 | 2013-08-05 12:52 | BRYANT - 561CJ036-C | 71 | 2.6 | Yes | Yes | 20 | 21 | -1 | 6B54999EC25542E9B3E68FD096864A12 |  | R22 | TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | TXV | 3.662%
Stockton | CA | 95212-3819 |  | 2013-06-25 | 2013-06-25 15:20 | 2013-06-25 15:40 | CARRIER - 38CKC030340 | 67 | 10.1 | Yes | Yes | 16.7 | 19.5 | -2.8 | 09ABCF9FC71B475A9D7E73AFF7340C26 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.07% | 0.84925 | 28.97% | [5 empty] | Non-TXV | 15.07%
Fresno | CA | 93703-1339 |  | 2013-06-01 | 2013-06-01 15:42 | 2013-06-01 15:42 | LENNOX - RRPL-B036JK06X | 91 | 0 | Yes | Yes | 21.7 | 20.3 | 1.4 | 0E9459C2193647078B0F767A4AEAC72A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-7416 |  | 2013-06-26 | 2013-06-26 15:07 | 2013-06-26 15:25 | DAY & NIGHT - 36DNR108C | 74 | 2.4 | Yes | Yes | 19.6 | 17.4 | 2.2 | C0627938E39B428184BC91D25F732BB9 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Stockton | CA | 95215-6032 |  | 2013-06-28 | 2013-06-28 14:02 | 2013-06-28 14:33 | OTHER - 60WE24G1 | 55 | 4.2 | Yes | Yes | 22.1 | 19.5 | 2.7 | DE80E1FC5FC646938BC979D0916E574C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.636% | 0.92364 | 14.68% | [5 empty] | Non-TXV | 7.636%
Tracy | CA | 95376-1961 |  | 2013-08-01 | 2013-08-01 09:33 | 2013-08-01 09:49 | BRYANT - 563CN036-F | 104 | 3.1 | Yes | Yes | 23.7 | 19.8 | 3.9 | 1BAE54A5B7594F858CECC93C1AB7BCEA |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Clovis | CA | 93612-0908 |  | 2013-09-10 | 2013-09-10 09:55 | 2013-09-10 10:26 | GOODMAN - PGB030050-1 | 56 | 4.2 | Yes | Yes | 19.6 | 20.8 | -1.2 | 434872E8F672416A8B0FFFF669002056 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Olivehurst | CA | 95961-0000 |  | 2013-10-22 | 2013-10-22 13:09 | 2013-10-22 13:27 | TRANE - 4TTM303A1000BA | 66 | 3.2 | Yes | Yes | 20 | 20.1 | -0.1 | 72B7D91649F84326AD5F675A6A83D08C |  | R410A | TXV |  | 4.848% | 0.95152 | 9.318% | [5 empty] | TXV | 4.848%
Manteca | CA | 95336-3062 |  | 2013-07-08 | 2013-07-08 09:51 | 2013-07-08 10:14 | RHEEM - 13AJM30A01 | 85 | 4.5 | Yes | Yes | 20.7 | 19.8 | 0.9 | 88EDD19161224A0BBB5B91EC838A4ED4 |  | R410A | TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | TXV | 5.294%
Manteca | CA | 95336-4063 |  | 2013-07-12 | 2013-07-12 08:57 | 2013-07-12 09:15 | HEIL - UNK | 85 | -6 | Yes | Yes | 22.7 | 19.8 | 2.9 | 656B13130A66410F9067445A1BEF7796 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Stockton | CA | 95206-2251 |  | 2013-07-03 | 2013-07-03 08:53 | 2013-07-03 09:13 | RHEEM - RRNA-B030JK06X | 85 | 5.7 | Yes | Yes | 18.6 | 18.1 | 0.5 | 654799F850534A878B2A4B24B4525A13 |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Stockton | CA | 95209-4041 |  | 2013-07-12 | 2013-07-12 11:36 | 2013-07-12 11:36 | GOODMAN - GPG1342070M41AB | 105 | 0 | Yes | Yes | 22.1 | 18.6 | 3.5 | 13BF81841DAE4BD9B381AC6C5BBC06C1 |  | R410A | TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-8699 |  | 2013-09-10 | 2013-09-10 19:46 | 2013-09-10 20:15 | LENNOX - HS22-311U-3P | 129 | 11.2 | Yes | Yes | 25.8 | 24.2 | 1.6 | A5550677988E4D59ADB5787196D1EB69 |  | R22 | TXV |  | 8.682% | 0.91318 | 16.69% | [5 empty] | TXV | 8.682%
Clovis | CA | 93611-6136 |  | 2013-08-29 | 2013-08-29 12:11 | 2013-08-29 12:21 | BDP - 561AJX030-A | 65 | 3.8 | Yes | Yes | 18 | 20.4 | -2.4 | 52BB0CE668EA4A2693CE709B058AFB51 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.846% | 0.94154 | 11.24% | [5 empty] | Non-TXV | 5.846%
Clovis | CA | 93611-6136 |  | 2013-08-29 | 2013-08-29 13:13 | 2013-08-29 13:15 | BDP - 561AJ036-C | 68 | 2.3 | Yes | Yes | 20 | 20.7 | -0.6 | 73666BBC45004009BE634E099A2747A8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Stockton | CA | 95210-2048 |  | 2013-07-11 | 2013-07-11 09:55 | 2013-07-11 10:14 | WESTINGHOUSE - ID036CEAON | 125 | -7.4 | Yes | Yes | 18.3 | 18.2 | 0.1 | 18DAFD5F0FF9401C8E681B9EC82ED750 |  | R22 | Non-TXV |  | -5.92% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.92%
Madera | CA | 93638-0244 |  | 2013-07-16 | 2013-07-16 15:53 | 2013-07-16 15:54 | YORK - D3NZ042N06506NXA | 78 | 2.4 | Yes | Yes | 26.4 | 21 | 5.5 | D61140AED3034C4598717FA7B1D7D4D0 |  | R410A | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Fresno | CA | 93726-1623 |  | 2013-08-12 | 2013-08-12 12:13 | 2013-08-12 12:31 | DAY & NIGHT - 585GJ036060 | 82 | 9 | Yes | Yes | 20.4 | 19.2 | 1.2 | C3D0589BEBFB4B7D9058F31FED181D37 |  | R22 | Non-TXV |  | 10.98% | 0.89024 | 21.09% | [5 empty] | Non-TXV | 10.98%
Los Banos | CA | 93635-6425 |  | 2013-06-01 | 2013-06-01 13:06 | 2013-06-01 13:16 | CARRIER - 24ABA36AO300 | 135 | 7.8 | Yes | Yes | 22.6 | 20.6 | 2 | FA7B3AF13D60444FA83129F8C286B6F4 |  | R410A | TXV |  | 5.778% | 0.94222 | 11.1% | [5 empty] | TXV | 5.778%
Oroville | CA | 95965-4193 |  | 2013-07-26 | 2013-07-26 15:55 | 2013-07-26 22:21 | DAY & NIGHT - 0176C00144 | 84 | 9.4 | Yes | Yes | 25 | 21 | 4 | 981963B064BF4055AA131D6F11B2E768 |  | R22 | Non-TXV |  | 11.19% | 0.8881 | 21.51% | [5 empty] | Non-TXV | 11.19%
Stockton | CA | 95210-1145 |  | 2013-06-26 | 2013-06-26 13:36 | 2013-06-26 13:57 | HEIL - CA5036VKB1 | 86 | 21.4 | Yes | Yes | 19.7 | 16.3 | 3.4 | 150AB0FC39EC4481A26E34F8638E1BF1 |  | R22 | Non-TXV |  | 24.88% | 0.75116 | 47.82% | [5 empty] | Non-TXV | 24.88%
Stockton | CA | 95219-4941 |  | 2013-06-25 | 2013-06-25 10:08 | 2013-06-25 10:26 | PAYNE - 591ANX042000ADAA | 91 | 7.5 | Yes | Yes | 12.7 | 14.6 | -1.9 | 947652B96CBE40EDB6507432ADA2B1D4 |  | R22 | Non-TXV |  | 8.242% | 0.91758 | 15.84% | [5 empty] | Non-TXV | 8.242%
Chico | CA | 95928-8256 |  | 2013-08-02 | 2013-08-02 15:00 | 2013-08-02 15:20 | TRANE - 2YCC3024A1040AA | 72 | 5.5 | Yes | Yes | 19.7 | 19 | 0.7 | 03425E56F89140B8B4F0DAB943EADC6C |  | R22 | Non-TXV |  | 7.639% | 0.92361 | 14.68% | [5 empty] | Non-TXV | 7.639%
Fresno | CA | 93703-3229 |  | 2013-08-08 | 2013-08-08 10:56 | 2013-08-08 11:03 | LENNOX - 13ACX02423002 | 70 | 4.4 | Yes | Yes | 22 | 19 | 3 | 96ACD99861D64A4DAC0A2D995BA87D87 |  | R410A | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Yuba City | CA | 95991-6732 |  | 2013-07-15 | 2013-07-15 08:13 | 2013-07-15 08:39 | LENNOX - 10AC-060-230-04 | 130 | 3.9 | Yes | Yes | 19 | 20.4 | -1.4 | 10C63F59286A4422BD482A2E8F6C5EF4 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Rocklin | CA | 95677-2856 |  | 2013-08-06 | 2013-08-06 09:36 | 2013-08-06 09:57 | BRYANT - 561CJ024-C | 72 | 11.6 | Yes | Yes | 18.4 | 19.5 | -1.1 | 55A0F9793BCE4177993A72AE59665EDB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Stockton | CA | 95212-3804 |  | 2013-06-25 | 2013-06-25 13:10 | 2013-06-25 13:57 | YORK - H2RC036S06G | 83 | 5 | Yes | Yes | 16.7 | 16.9 | -0.2 | FAF86BB7B3DE4265B3D84E6734AA30C5 |  | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Madera | CA | 93638-1780 |  | 2013-07-16 | 2013-07-16 16:42 | 2013-07-16 16:42 | BRYANT - 574BNMO42060NB--- | 167 | 0 | Yes | Yes | 18.1 | 21 | -2.9 | 123D1B5C84574D8FAE3C9806A9E2411C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2217 |  | 2013-06-12 | 2013-06-12 14:05 | 2013-06-12 14:07 | YORK - D1MP036N05606A | 108 | 5.1 | Yes | Yes | 22.4 | 21.4 | 1 | 0B872DCD4D4D45D5AA101DE8F6AB2919 |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Fresno | CA | 93727-2436 |  | 2013-06-17 | 2013-06-17 11:02 | 2013-06-17 11:04 | TRANE - YCX036F1M0BC | 114 | 6 | Yes | Yes | 21.2 | 20.4 | 0.8 | 9CE678A9DF664BC8A37B6A3EEB86206C |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Riverbank | CA | 95367-2104 |  | 2013-07-12 | 2013-07-12 10:17 | 2013-07-12 10:45 | AMANA - PGD60C0902E | 139 | 4.3 | Yes | Yes | 19 | 18.3 | 0.7 | 046DA21BC8304F509205FA7105D27564 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.094% | 0.96906 | 5.945% | [5 empty] | Non-TXV | 3.094%
Olivehurst | CA | 95961-4626 |  | 2013-06-28 | 2013-06-28 11:08 | 2013-06-28 11:26 | TRANE - YCY030F1L0AA | 148 | 4.5 | Yes | Yes | 21 | 20.3 | 0.7 | 9BCD9B257E414ADC9D6BFACAA48A668C |  | R22 | Non-TXV |  | 3.041% | 0.96959 | 5.843% | [5 empty] | Non-TXV | 3.041%
Yuba City | CA | 95993-0000 |  | 2013-07-16 | 2013-07-16 09:11 | 2013-07-16 09:33 | LENNOX - 10AC-060-230-02 | 130 | 4 | Yes | Yes | 17 | 19.3 | -2.3 | C84AEC8AAC794B7995797EA3B93F0C94 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Oroville | CA | 95966-9515 |  | 2013-08-29 | 2013-08-29 12:30 | 2013-08-29 12:47 | TRANE - YCY036G1MOAC | 130 | -7.6 | Yes | Yes | 22.3 | 18.8 | 3.5 | 870D8A9B6102474CAB2A05DF430DF5B6 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Stockton | CA | 95203-2234 |  | 2013-07-15 | 2013-07-15 13:33 | 2013-07-15 14:01 | OTHER - UNK | 66 | -3.9 | Yes | Yes | 22.4 | 18.7 | 3.7 | 3C0E2DA8CE86448994596DCE27B9A0EB |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Lockeford | CA | 95237-9697 |  | 2013-08-20 | 2013-08-20 14:09 | 2013-08-20 14:30 | GOODMAN - CK42-1A | 86 | 10.7 | Yes | Yes | 18.6 | 18.1 | 0.5 | 6FEEA57A0FAE4ED8B88AD72F3AF1928E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.44% | 0.87558 | 23.91% | [5 empty] | Non-TXV | 12.44%
Fresno | CA | 93703-1617 |  | 2013-05-29 | 2013-05-29 13:55 | 2013-05-29 14:29 | AIRE-FLO - JHMNT036 300 | 83 | 3.3 | Yes | Yes | 15.3 | 17.5 | -2.2 | 73F6F6B10D004CB6890EAF467D9EA159 |  | R22 | Non-TXV |  | 3.976% | 0.96024 | 7.641% | [5 empty] | Non-TXV | 3.976%
Stockton | CA | 95209-3786 |  | 2013-07-12 | 2013-07-12 10:17 | 2013-07-12 10:31 | CARRIER - 38ETG042300 | 135 | 9.5 | Yes | Yes | 16.7 | 18.2 | -1.5 | EB62402180FB47C5879B5625B8FA9AF3 |  | R410A | TXV |  | 7.037% | 0.92963 | 13.52% | [5 empty] | TXV | 7.037%
Stockton | CA | 95215-5904 |  | 2013-07-23 | 2013-07-23 13:55 | 2013-07-23 14:12 | PAYNE - PY1PNB030060AAAA | 55 | 3.3 | Yes | Yes | 21.6 | 21 | 0.6 | C054C8B2C9864A54B7C58F244DCEE72A |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93726-3014 |  | 2013-06-05 | 2013-06-05 15:02 | 2013-06-05 15:18 | AMANA - PGB3680702C | 118 | 4.1 | Yes | Yes | 20.5 | 19.1 | 1.4 | 42897D00E5994EB8ADC89C44393904DC |  | R22 | Non-TXV |  | 3.475% | 0.96525 | 6.677% | [5 empty] | Non-TXV | 3.475%
Jamestown | CA | 95327-9668 |  | 2013-08-01 | 2013-08-01 10:21 | 2013-08-01 10:52 | GOODMAN - CJK48-1B | 110 | 4.7 | Yes | Yes | 27.6 | 21.7 | 5.9 | 67010421181E48EFA5E5571A8722B685 |  | R22 | Non-TXV |  | 4.273% | 0.95727 | 8.211% | [5 empty] | Non-TXV | 4.273%
Stockton | CA | 95203-1226 |  | 2013-07-23 | 2013-07-23 10:26 | 2013-07-23 10:51 | ICP - N2A336AKA300 | 88 | 4.1 | Yes | Yes | 21.3 | 19.1 | 2.3 | E81C44B1842D4494BA7023A979FEDC2D |  | R22 | Non-TXV |  | 4.659% | 0.95341 | 8.954% | [5 empty] | Non-TXV | 4.659%
Oroville | CA | 95965-4843 |  | 2013-08-28 | 2013-08-28 12:23 | 2013-08-28 12:23 | TRANE - WCC030F1OOBB | 128 | 0 | Yes | Yes | 20.6 | 23.3 | -2.7 | AE2DF6A412D2466DB0E6479447A8A031 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-1812 |  | 2013-07-12 | 2013-07-12 09:30 | 2013-07-12 09:53 | DAY & NIGHT - N4A430GKA100 | 122 | 7.9 | Yes | Yes | 22 | 20.4 | 1.6 | 0275A23A57CE463283DFFF171AD5DB3F |  | R410A | TXV |  | 6.475% | 0.93525 | 12.44% | [5 empty] | TXV | 6.475%
Fresno | CA | 93727-5919 |  | 2013-06-13 | 2013-06-13 11:55 | 2013-06-13 11:57 | LENNOX - GCS16R-511-125-5P | 96 | 4.7 | Yes | Yes | 25.2 | 22 | 3.2 | 57E07B5DE8974F7D843BAA2637064B5C |  | R22 | Non-TXV |  | 4.896% | 0.95104 | 9.409% | [5 empty] | Non-TXV | 4.896%
Stockton | CA | 95209-4221 |  | 2013-07-16 | 2013-07-16 10:34 | 2013-07-16 10:34 | YORK - AC036X1222A | 83 | 0 | Yes | Yes | 19.8 | 19.1 | 0.7 | DEE9BE7A814946F3B86F8D5E18D54737 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-4513 |  | 2013-07-24 | 2013-07-24 09:15 | 2013-07-24 09:39 | YORK - D3NZ030N03606NXA | 64 | 6.9 | Yes | Yes | 21.1 | 17.7 | 3.4 | 46B0D4C8668D4601B8C66F3E09919761 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 10.78% | 0.89219 | 20.72% | [5 empty] | Non-TXV | 10.78%
Stockton | CA | 95206-5426 |  | 2013-06-26 | 2013-06-26 12:45 | 2013-06-26 13:04 | RUUD - UAKB-36JAZ | 85 | 18 | Yes | Yes | 22 | 18.8 | 3.2 | 60D6800F849B476B87FB368E5E631E86 |  | R22 | Non-TXV |  | 21.18% | 0.78824 | 40.7% | [5 empty] | Non-TXV | 21.18%
Olivehurst | CA | 95961-4708 |  | 2013-10-23 | 2013-10-23 15:20 | 2013-10-23 15:20 | OTHER - HAC048AKA5 | 123 | 0 | Yes | Yes | 22 | 20.1 | 1.9 | 00EC08444D2B4388ACCB0DF9B4EBF78E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2612 |  | 2013-07-08 | 2013-07-08 10:10 | 2013-07-08 10:29 | RHEEM - UNK | 96 | -9 | Yes | Yes | 21.3 | 18 | 3.3 | 9A3DBC4830814F64A7266699CA5D0FC6 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Paso Robles | CA | 93446-4077 |  | 2013-08-08 | 2013-08-08 15:52 | 2013-08-08 16:34 | BRYANT - PA10JA060000 | 147 | -8.6 | Yes | Yes | 22.5 | 19.3 | 3.2 | F07C5C942791424EA52B29838F00228F |  | R22 | Non-TXV |  | -5.85% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.85%
Chico | CA | 95928-6382 |  | 2013-08-05 | 2013-08-05 13:09 | 2013-08-05 13:29 | YORK - H1CB024S06B | 71 | 9.9 | Yes | Yes | 20.6 | 20.4 | 0.2 | 674D83E18B1A46E89037022496617D6B |  | R22 | Non-TXV |  | 13.94% | 0.86056 | 26.8% | [5 empty] | Non-TXV | 13.94%
Merced | CA | 95348-2827 |  | 2013-06-05 | 2013-06-05 14:39 | 2013-06-05 14:42 | TRANE - TTR0300100A0 | 74 | 5.2 | Yes | Yes | 17.6 | 18.7 | -1.1 | 7BEC44DB23DA45F08D94DD38A3947573 |  | R22 | Non-TXV |  | 7.027% | 0.92973 | 13.5% | [5 empty] | Non-TXV | 7.027%
Chico | CA | 95928-5645 |  | 2013-07-03 | 2013-07-03 08:47 | 2013-07-03 16:28 | LENNOX - HS16-311V-4P | 112 | 6 | Yes | Yes | 22 | 19.5 | 2.5 | C5FAFACE8CC74A5883ABD4094663911B |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Paradise | CA | 95969-2313 |  | 2013-06-28 | 2013-06-28 20:20 | 2013-06-28 20:20 | BRYANT - 116BNA030-A | 97 | 0 | Yes | Yes | 23 | 20.4 | 2.6 | 342F917FB1734C20BBB94C7F08B1DB92 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Plumas Lake | CA | 95961-8928 |  | 2013-08-19 | 2013-08-19 08:45 | 2013-08-19 09:12 | YORK - H2RD048S06B | 134 | 5.2 | Yes | Yes | 15 | 17.5 | -2.5 | 3AE0DAD12C4E4951B82516194AA57AD5 |  | R22 | TXV |  | 3.881% | 0.96119 | 7.458% | [5 empty] | TXV | 3.881%
Merced | CA | 95341-5560 |  | 2013-06-13 | 2013-06-13 08:27 | 2013-06-13 08:29 | RHEEM - UNK | 76 | 13.6 | Yes | Yes | 22.5 | 18.9 | 3.6 | 8A4AD29C7F504596B9B67E12F5AA96D7 |  | R22 | Non-TXV |  | 17.89% | 0.82105 | 34.39% | [5 empty] | Non-TXV | 17.89%
Stockton | CA | 95219-5488 |  | 2013-06-25 | 2013-06-25 11:40 | 2013-06-25 11:56 | RUUD - 10AJB18A01 | 52 | -3.7 | Yes | Yes | 17.9 | 17.2 | 0.7 | 1B31D4C486954F2DB963F8745D0E75CD |  | R22 | Non-TXV |  | -7.115% | 1.0712 | 1.993% |  |  |  |  | Non-TXV |  |  | -7.115%
Stockton | CA | 95205-3224 |  | 2013-07-11 | 2013-07-11 12:27 | 2013-07-11 12:48 | RHEEM - UNK | 85 | 4.1 | Yes | Yes | 16 | 18.8 | -2.8 | 7C8DECE2FF614B0BB15D3E995980891D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Merced | CA | 95341-5585 |  | 2013-07-01 | 2013-07-01 10:23 | 2013-07-01 10:24 | RUUD - 7777UNK | 96 | 3.2 | Yes | Yes | 23.8 | 20.4 | 3.4 | CC83F16745444BD2A082B0D8E43DB8E6 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Manteca | CA | 95337-6514 |  | 2013-07-17 | 2013-07-17 17:05 | 2013-07-17 17:26 | OTHER - R2A330GKC1 | 68 | 2.3 | Yes | Yes | 21.7 | 18.7 | 3 | 0811CA5BAFAD45B0A1845C6423258EF8 |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Fresno | CA | 93727-1937 |  | 2013-06-11 | 2013-06-11 16:11 | 2013-06-11 16:39 | CARRIER - 48SX-030060331AA | 69 | -4.1 | Yes | Yes | 13.8 | 14.9 | -1.1 | 9BEC5198AB8C40379D2DD323F7EAFED6 |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Clovis | CA | 93612-0790 |  | 2013-08-22 | 2013-08-22 13:03 | 2013-08-22 13:33 | BDP - 585GJWO24040ABAF | 54 | 21.6 | Yes | Yes | 16.5 | 19.5 | -3 | 6CA0125306DE4F729D02514C7D289A87 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 40% | 0.6 | 76.87% | [5 empty] | Non-TXV | 40%
Chico | CA | 95926-1514 |  | 2013-07-12 | 2013-07-12 18:15 | 2013-07-12 18:33 | PAYNE - PY3GNAA30060NA | 98 | 4.8 | Yes | Yes | 18.8 | 21.5 | -2.7 | FE0008E0087143A58E6ED5529032630D |  | R410A | Non-TXV |  | 4.898% | 0.95102 | 9.413% | [5 empty] | Non-TXV | 4.898%
Fresno | CA | 93727-2456 |  | 2013-08-12 | 2013-08-12 12:12 | 2013-08-12 12:12 | BDP - 585EJW030050ABAF | 58 | 0 | Yes | Yes | 19.2 | 20.4 | -1.2 | DD81FB09CC054E48ADAC54FE9A105E18 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5238 |  | 2013-06-06 | 2013-06-06 13:28 | 2013-06-06 13:40 | YORK - DARA-F036N080B | 80 | 4.6 | Yes | Yes | 24.7 | 22.1 | 2.7 | 173341DC895941CEB653637244989E86 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.75% | 0.77 | 44.2% | [5 empty] | Non-TXV | 5.75%
Fresno | CA | 93710-5745 |  | 2013-06-03 | 2013-06-03 14:52 | 2013-06-03 15:10 | BDP - 589ANW048100AEBG | 93 | 3 | Yes | Yes | 20.6 | 21.2 | -0.6 | E3B54D35F754475794F42DB8CF5CA36D |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Lathrop | CA | 95330-9362 |  | 2013-07-08 | 2013-07-08 14:26 | 2013-07-08 14:44 | CARRIER - 38BRC048370 | 136 | 24.2 | Yes | Yes | 18.2 | 19.5 | -1.3 | CDFD305966B64106BF6FCF7051030F22 |  | R22 | Non-TXV |  | 17.79% | 0.82206 | 34.2% | [5 empty] | Non-TXV | 17.79%
Clovis | CA | 93611-6735 |  | 2013-08-16 | 2013-08-16 15:09 | 2013-08-16 15:53 | CARRIER - 591ANX036000AAAA | 83 | 2.5 | Yes | Yes | 20 | 17.6 | 2.4 | 3903786D88C340B58F7EBA2ACDFB31B6 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Clovis | CA | 93612-3875 |  | 2013-08-29 | 2013-08-29 09:45 | 2013-08-29 10:32 | GOODMAN - PGB024050-1 | 54 | 3.7 | Yes | Yes | 16.5 | 19.5 | -3 | 3C8308144DD7454F9DE1D7FFF5E362E6 |  | R22 | Non-TXV |  | 6.852% | 0.93148 | 13.17% | [5 empty] | Non-TXV | 6.852%
Magalia | CA | 95954-9654 |  | 2013-07-18 | 2013-07-18 16:17 | 2013-07-18 19:14 | BRYANT - 604ANX03000AA | 132 | 4.1 | Yes | Yes | 19.7 | 21 | -1.3 | 3D0D2E64BCBE4E73ABD4AED7C058AD57 |  | R22 | Non-TXV |  | 3.106% | 0.96894 | 5.969% | [5 empty] | Non-TXV | 3.106%
Atwater | CA | 95301-3860 |  | 2013-06-24 | 2013-06-24 16:48 | 2013-06-24 16:51 | GOODMAN - GPG13420701AA | 107 | 4.2 | Yes | Yes | 24.4 | 19.5 | 4.9 | 0278799A37FE4661B44E4C76F0D2F28F |  | R22 | Non-TXV |  | 3.925% | 0.96075 | 7.543% | [5 empty] | Non-TXV | 3.925%
Madera | CA | 93636-8857 |  | 2013-07-09 | 2013-07-09 15:01 | 2013-07-09 20:12 | RHEEM - RJMA-A060JL 000 | 161 | 5.3 | Yes | Yes | 17.8 | 20.2 | -2.4 | 07E23AA015414AB2A4A787CB45F59125 |  | R22 | Non-TXV |  | 3.292% | 0.96708 | 6.326% | [5 empty] | Non-TXV | 3.292%
Madera | CA | 93638-1575 |  | 2013-07-15 | 2013-07-15 09:43 | 2013-07-15 10:16 | CARRIER - 5955W0330060ABAF | 55 | -5.5 | Yes | Yes | 14.7 | 16.7 | -2 | 0C6C06071FAC475A8E4EE90E869ED47A |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Stockton | CA | 95215-7343 |  | 2013-07-01 | 2013-07-01 13:14 | 2013-07-01 13:31 | MAYTAG - PPG1GDX42K100X | 192 | 7.2 | Yes | Yes | 20.4 | 22.8 | -2.4 | 1FB6E79F11E14B009BE3B510634D1BDF |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Fresno | CA | 93710-6117 |  | 2013-06-04 | 2013-06-04 09:40 | 2013-06-04 09:57 | ICP - PGF336060K01A1 | 176 | -10.4 | Yes | Yes | 23.7 | 20.4 | 3.3 | A49A6890BA294FFE85C5D2C24B915F6C |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Clovis | CA | 93612-3876 |  | 2013-08-29 | 2013-08-29 13:16 | 2013-08-29 13:39 | GOODMAN - PGB024050-1 | 54 | 2.2 | Yes | Yes | 19 | 20 | -0.9 | 82EE552D63FE431E8FED0E6D8C9576E7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Stockton | CA | 95215-6092 |  | 2013-07-01 | 2013-07-01 09:13 | 2013-07-01 09:51 | RHEEM - RAKA-024JAZ | 50 | 4.2 | Yes | Yes | 17.3 | 19.3 | -2 | 546308748A204018A18AB1F8C9833B6E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.4% | 0.916 | 16.14% | [5 empty] | Non-TXV | 8.4%
Atwater | CA | 95301-3303 |  | 2013-06-17 | 2013-06-17 12:03 | 2013-06-17 12:13 | RHEEM - RRMAA042JK10X | 114 | 12.1 | Yes | Yes | 20.3 | 18.8 | 1.5 | 9143AC67709A4EF98D59B9DEEA5C441A |  | R22 | Non-TXV |  | 10.61% | 0.89386 | 20.4% | [5 empty] | Non-TXV | 10.61%
Fresno | CA | 93710-6207 |  | 2013-06-03 | 2013-06-03 12:43 | 2013-06-03 13:01 | ICP - PGAD471K7 | 215 | -12.6 | Yes | Yes | 23.3 | 20.6 | 2.7 | 2E1A6CAB0CC84A79AB1B98042D687819 |  | R22 | Non-TXV |  | -5.86% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.86%
Merced | CA | 95348-2838 |  | 2013-06-07 | 2013-06-07 10:22 | 2013-06-07 10:24 | TRANE - TTR030C100A1 | 74 | 5 | Yes | Yes | 18.8 | 18.9 | -0.1 | A8DEA8AA9C1E465496E878E2DD10FD70 |  | R22 | Non-TXV |  | 6.757% | 0.93243 | 12.98% | [5 empty] | Non-TXV | 6.757%
Paradise | CA | 95969-4028 |  | 2013-08-05 | 2013-08-05 10:19 | 2013-08-05 11:06 | CARRIER - 48SX-036060301AA | 84 | 5.2 | Yes | Yes | 22.9 | 21.6 | 1.3 | CF8ADDBBC69F40C4AB48F1F74C9B1528 |  | R22 | Non-TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | Non-TXV | 6.19%
Fresno | CA | 93726-4431 |  | 2013-06-04 | 2013-06-04 16:05 | 2013-06-04 16:23 | ALLEGIANCE - N/A | 101 | 3.1 | Yes | Yes | 20.5 | 18.5 | 2 | 9ACC22A5061E42BFB4B848E9F61BA114 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Acampo | CA | 95220-9340 |  | 2013-09-10 | 2013-09-10 16:48 | 2013-09-10 17:08 | LENNOX - HS25-411-1P | 129 | -18.7 | Yes | Yes | 20.8 | 19.8 | 1 | 57DDD2FC947F4E448525DAD7BBF0449A |  | R22 | TXV |  | -14.5% | 1.145 | 4.06% |  |  |  |  | TXV |  |  | -14.5%
Twain Harte | CA | 95383-9768 |  | 2013-09-12 | 2013-09-12 09:40 | 2013-09-12 10:05 | YORK - H1DH060S06B | 260 | 10.4 | Yes | Yes | 26.1 | 20.1 | 6 | 47BE126757584095AC50B4BEC65DBE9B |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95206-6241 |  | 2013-07-02 | 2013-07-02 11:17 | 2013-07-02 11:44 | GOODMAN - KJ42-1AB | 85 | 5.4 | Yes | Yes | 23.1 | 17.2 | 5.9 | 001ED147F5DC474DA8F81E925E59C3EF |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Ione | CA | 95640-9757 |  | 2013-06-26 | 2013-06-26 13:02 | 2013-06-26 13:29 | BRYANT - 563CN036-D | 104 | 19.9 | Yes | Yes | 13.6 | 15.9 | -2.3 | 1D4325B2069B4CFA883E8478F6F7E96F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.13% | 0.80865 | 36.77% | [5 empty] | Non-TXV | 19.13%
Dos Palos | CA | 93620-2640 |  | 2013-07-08 | 2013-07-08 10:16 | 2013-07-08 10:18 | ICP - GPCM036K060F | 86 | 3.3 | Yes | Yes | 23.4 | 20.8 | 2.6 | 2C73A1A3296E41E7B4F065FAA64F3E94 |  | R22 | Non-TXV |  | 3.837% | 0.96163 | 7.374% | [5 empty] | Non-TXV | 3.837%
Merced | CA | 95341-5560 |  | 2013-06-12 | 2013-06-12 10:47 | 2013-06-12 10:48 | RHEEM - UNK | 78 | 5.7 | Yes | Yes | 22.9 | 21.4 | 1.5 | 633A6108672840DF9A1A718581F0FD6F |  | R22 | Non-TXV |  | 7.308% | 0.92692 | 14.04% | [5 empty] | Non-TXV | 7.308%
Los Banos | CA | 93635-8550 |  | 2013-06-04 | 2013-06-04 12:30 | 2013-06-04 12:43 | AMERICAN STANDARD - 2A7B0060A1000AA | 126 | 6.2 | Yes | Yes | 20.1 | 20.2 | -0.1 | 1C9006245FE0403CB0BE327973AA33D6 |  | R22 | Non-TXV |  | 4.921% | 0.95079 | 9.456% | [5 empty] | Non-TXV | 4.921%
Clovis | CA | 93611-4508 |  | 2013-06-17 | 2013-06-17 10:22 | 2013-06-17 10:44 | BDP - 588ANW036080ACAF | 67 | 7.1 | Yes | Yes | 20.2 | 20.7 | -0.5 | D3238738081F4A58B86F535B007ADFA5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.6% | 0.89403 | 20.37% | [5 empty] | Non-TXV | 10.6%
Atwater | CA | 95301-8370 |  | 2013-06-25 | 2013-06-25 15:41 | 2013-06-25 15:46 | GOODMAN - CLJ60-1 | 141 | 4.3 | Yes | Yes | 15.3 | 17.3 | -2 | 3236582028574AF9BB2C5F65AA443791 |  | R22 | Non-TXV |  | 3.05% | 0.9695 | 5.861% | [5 empty] | Non-TXV | 3.05%
Stockton | CA | 95205-7896 |  | 2013-07-18 | 2013-07-18 14:37 | 2013-07-18 14:55 | BRYANT - 561CJ042-F | 81 | 4.5 | Yes | Yes | 21.3 | 19.9 | 1.4 | 679101096C3C4721A6162B6442F07969 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Ione | CA | 95640-9535 |  | 2013-08-01 | 2013-08-01 16:33 | 2013-08-01 17:03 | BRYANT - 574DNWA24040NA | 70 | -2.6 | Yes | Yes | 22 | 20.9 | 1.1 | C479A669A9804B99A8270A5C55A7A326 |  | R410A | TXV |  | -3.714% | 1.0371 | 1.04% |  |  |  |  | TXV |  |  | -3.714%
Fresno | CA | 93727-5857 |  | 2013-06-13 | 2013-06-13 13:07 | 2013-06-13 13:10 | LENNOX - 13ACD-060-230-02 | 214 | 6.9 | Yes | Yes | 21.4 | 19.1 | 2.3 | 189F5A7F496240FDAD18C49EEBD3C354 |  | R22 | Non-TXV |  | 3.224% | 0.96776 | 6.196% | [5 empty] | Non-TXV | 3.224%
Fresno | CA | 93726-3121 |  | 2013-06-01 | 2013-06-01 10:34 | 2013-06-01 11:12 | YORK - N/A | 90 | 3 | Yes | Yes | 17.4 | 19.7 | -2.3 | 59A18829FC14490B84784D9B6FEE250C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Paradise | CA | 95969-6342 |  | 2013-10-16 | 2013-10-16 12:38 | 2013-10-16 13:37 | TEMPSTAR - PGAD60E1K7 | 212 | 8.3 | Yes | Yes | 25.1 | 20.7 | 4.4 | 907A875EF85B485ABF7786BB94DFD476 |  | R22 | Non-TXV |  | 3.915% | 0.96085 | 7.524% | [5 empty] | Non-TXV | 3.915%
Plumas Lake | CA | 95961-9028 |  | 2013-10-16 | 2013-10-16 10:55 | 2013-10-16 11:24 | YORK - H1RA042S06D | 84 | 2.5 | Yes | Yes | 21 | 20.1 | 0.9 | 0BF1D1B20D1642108E1755648FE5E28C |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Fresno | CA | 93703-1643 |  | 2013-06-07 | 2013-06-07 11:08 | 2013-06-07 11:53 | YORK - D2NPO42N06506 | 148 | 4.7 | Yes | Yes | 19.7 | 20.1 | -0.4 | 95B7006460264CAD88DFFF7C289AF502 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.103% | [5 empty] | Non-TXV | 3.176%
Merced | CA | 95340-0664 |  | 2013-06-06 | 2013-06-06 10:58 | 2013-06-06 11:02 | GOODMAN - GPG32420701AB | 107 | 4.5 | Yes | Yes | 25.5 | 19.6 | 5.9 | B2C6B54AB1B54157969ADE656AF90557 |  | R22 | Non-TXV |  | 4.206% | 0.95794 | 8.082% | [5 empty] | Non-TXV | 4.206%
Yuba City | CA | 95991-6160 |  | 2013-07-15 | 2013-07-15 09:27 | 2013-07-15 09:47 | RHEEM - RACA-036ABQ | 35 | 8.4 | Yes | Yes | 17 | 19.9 | -2.9 | E8B19B6F7FB2463184976F5D32161473 |  | R22 | Non-TXV |  | 24% | 0.76 | 46.12% | [5 empty] | Non-TXV | 24%
Paradise | CA | 95969-3082 |  | 2013-06-28 | 2013-06-28 08:40 | 2013-06-28 08:40 | BRYANT - 583BNW036090AAAF | 105 | 0 | Yes | Yes | 24.1 | 21 | 3.1 | 3726FDAF3FFA41C6ABBA610A948D6578 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-2720 |  | 2013-08-06 | 2013-08-06 13:35 | 2013-08-06 14:19 | TRANE - TTB042C100A1 | 103 | 3.3 | Yes | Yes | 19.3 | 20.4 | -1.1 | FB8C6D4A83754EF2B40B606EBF783B8F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.204% | 0.96796 | 6.157% | [5 empty] | Non-TXV | 3.204%
Marysville | CA | 95901-8252 |  | 2013-07-12 | 2013-07-12 09:23 | 2013-07-12 09:43 | CARRIER - 38CKC024340 | 60 | 3.9 | Yes | Yes | 16 | 18.6 | -2.6 | A968DF79C4AE4F4794804C1BB580E61E |  | R22 | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Tracy | CA | 95376-1940 |  | 2013-07-17 | 2013-07-17 10:20 | 2013-07-17 10:46 | GOODMAN - CK49-1B | 85 | 4.4 | Yes | Yes | 20 | 19.3 | 0.7 | BEFCE8C092D3453BA38A5CCF259604B3 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Fresno | CA | 93726-5529 |  | 2013-07-29 | 2013-07-29 14:21 | 2013-07-29 14:22 | OTHER - ACS042A2A1 | 97 | 18.5 | Yes | Yes | 21.9 | 19.9 | 2 | E882BD68B7354ADD9966E12AF8E49416 |  | R22 | Non-TXV |  | 19.07% | 0.80928 | 36.65% | [5 empty] | Non-TXV | 19.07%
Colusa | CA | 95932-2340 |  | 2013-09-09 | 2013-09-09 11:56 | 2013-09-09 12:24 | AMANA - ZRCF42V01D | 133 | 10.2 | Yes | Yes | 24 | 19.9 | 4.1 | 2886E09CCFCD4FD386D8113DD8A26D5C |  | R22 | Non-TXV |  | 7.669% | 0.92331 | 14.74% | [5 empty] | Non-TXV | 7.669%
Yuba City | CA | 95993-9006 |  | 2013-07-22 | 2013-07-22 08:43 | 2013-07-22 09:04 | CARRIER - 38BRC024310 | 83 | 2.5 | Yes | Yes | 18 | 19.4 | -1.4 | 872785F993CA4C5BB0C5099803B27BA4 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Merced | CA | 95348-3031 |  | 2013-10-10 | 2013-10-10 14:48 | 2013-10-10 14:49 | BRYANT - 113ANA018E | 53 | 3.4 | Yes | Yes | 21.7 | 17.7 | 4 | 065914792CD949549CA91386CF56153F |  | R410A | TXV |  | 6.415% | 0.93585 | 12.33% | [5 empty] | TXV | 6.415%
Stockton | CA | 95210-1463 |  | 2013-07-02 | 2013-07-02 08:30 | 2013-07-02 08:48 | LENNOX - 13GEP24050ALP-1A | 82 | 2.6 | Yes | Yes | 18.6 | 18.2 | 0.4 | 52054B883FA04F2EB5C382F16249472F |  | R410A | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Chowchilla | CA | 93610-2812 |  | 2013-06-02 | 2013-06-02 10:45 | 2013-06-02 11:25 | ARCOAIRE - PGF042080E | 85 | 3 | Yes | Yes | 16.5 | 19.5 | -3 | 56F6A428A23744758751AFD37FB9CDBF |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Chico | CA | 95973-0743 |  | 2013-08-07 | 2013-08-07 11:26 | 2013-08-07 11:46 | YORK - H4DH042S06A | 108 | 7.7 | Yes | Yes | 17 | 19.4 | -2.4 | E4AFC4AB760443E69EFCB9BD8DE67F07 |  | R22 | Non-TXV |  | 7.13% | 0.9287 | 13.7% | [5 empty] | Non-TXV | 7.13%
Stockton | CA | 95206-4699 |  | 2013-07-11 | 2013-07-11 09:06 | 2013-07-11 09:32 | GUARDIAN - GCGD48S41S3A | 73 | 6.1 | Yes | Yes | 20.4 | 21.5 | -1.1 | 385BE3D099E14BD6B6568130342CB768 |  | R410A | Non-TXV |  | 8.356% | 0.91644 | 16.06% | [5 empty] | Non-TXV | 8.356%
Live Oak | CA | 95953-2123 |  | 2013-09-30 | 2013-09-30 11:30 | 2013-09-30 11:53 | COLEMAN - BRCS036B | 96 | 19.1 | Yes | Yes | 17 | 16.6 | 0.4 | 9BD3F041C3D64832A24B8EF3840B6148 |  | R22 | Non-TXV |  | 19.9% | 0.80104 | 38.24% | [5 empty] | Non-TXV | 19.9%
Fresno | CA | 93727-5884 |  | 2013-07-23 | 2013-07-23 11:48 | 2013-07-23 12:01 | YORK - H2RD036S06B | 96 | 13.4 | Yes | Yes | 16 | 19 | -3 | C804350B91164F47A51B47073469AA2E |  | R22 | Non-TXV |  | 13.96% | 0.86042 | 26.82% | [5 empty] | Non-TXV | 13.96%
Fresno | CA | 93727-5884 |  | 2013-07-23 | 2013-07-23 12:09 | 2013-07-23 12:14 | YORK - H2RD036S06B | 96 | 3.1 | Yes | Yes | 20.1 | 18.7 | 1.4 | BF70309786C34D6E8E6E5CAD8B1F07C9 |  | R22 | Non-TXV |  | 3.229% | 0.96771 | 6.206% | [5 empty] | Non-TXV | 3.229%
Atwater | CA | 95301-4209 |  | 2013-06-06 | 2013-06-06 10:26 | 2013-06-06 10:29 | RHEEM - RRMAA036JK08X | 99 | 8.9 | Yes | Yes | 22.8 | 19.2 | 3.6 | 34A63EDEBD2349B4820C59B9F8BEFF6B |  | R22 | Non-TXV |  | 8.99% | 0.9101 | 17.28% | [5 empty] | Non-TXV | 8.99%
Yuba City | CA | 95993-5233 |  | 2013-07-16 | 2013-07-16 14:34 | 2013-07-16 14:34 | LENNOX - 12ACB36-5P | 103 | 9.7 | Yes | Yes | 17 | 19.8 | -2.8 | 0F08A11DC76F45CBB996E434CBFBE309 | Add refrigerant: 9.7 oz | R22 | TXV |  | 9.417% | 0.90583 | 18.1% | [5 empty] | TXV | 9.417%
Yuba City | CA | 95993-8229 |  | 2013-07-22 | 2013-07-22 13:59 | 2013-07-22 14:32 | BRYANT - 561CJX042-B | 87 | 6.1 | Yes | Yes | 18 | 20.4 | -2.4 | E45880F7EBE342B8B00F8B0F190A1762 |  | R22 | TXV |  | 7.011% | 0.92989 | 13.47% | [5 empty] | TXV | 7.011%
Woodbridge | CA | 95258-9700 |  | 2013-10-03 | 2013-10-03 12:26 | 2013-10-03 12:46 | ICP - PGF336060K01A1 | 176 | 9 | Yes | Yes | 21.9 | 19.1 | 2.8 | EEA984E292024D6BB5245DC2D73DBF13 |  | R22 | Non-TXV |  | 5.114% | 0.94886 | 9.827% | [5 empty] | Non-TXV | 5.114%
Merced | CA | 95340-1642 |  | 2013-06-27 | 2013-06-27 12:25 | 2013-06-27 12:35 | TRANE - YCC048F1MOBG | 100 | 9.2 | Yes | Yes | 20 | 19.3 | 0.7 | A2B0810A4C7F45F999FD00055E4BCD01 |  | R22 | Non-TXV |  | 9.2% | 0.908 | 17.68% | [5 empty] | Non-TXV | 9.2%
Stockton | CA | 95206-6243 |  | 2013-07-02 | 2013-07-02 08:04 | 2013-07-02 08:32 | GOODMAN - CK60-1C | 85 | 4.5 | Yes | Yes | 18.8 | 20.4 | -1.6 | 9F0FD33E609E4A40A1077EE472981A9C |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Stockton | CA | 95204-1739 |  | 2013-07-09 | 2013-07-09 12:29 | 2013-07-09 12:50 | DAY & NIGHT - 36/80YAC-108C | 66 | 8.2 | Yes | Yes | 19.8 | 17 | 2.8 | 80292BF8EC4E48558183627C9B62FD38 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.42% | 0.87576 | 23.88% | [5 empty] | Non-TXV | 12.42%
Yuba City | CA | 95993-8229 |  | 2013-07-22 | 2013-07-22 10:01 | 2013-07-22 10:31 | TRANE - TTB036C100A1 | 90 | 4.9 | Yes | Yes | 18.5 | 20.8 | -2.3 | 6C6EEAC1EF80488086C99DC631FAE497 |  | R22 | TXV |  | 5.444% | 0.94556 | 10.46% | [5 empty] | TXV | 5.444%
Manteca | CA | 95337-6690 |  | 2013-07-16 | 2013-07-16 12:59 | 2013-07-16 13:18 | BRYANT - 563CN048-F | 165 | 5 | Yes | Yes | 20.3 | 19.8 | 0.5 | C70500DA3CFF419A8B85BB06356D355B |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Fresno | CA | 93726-2605 |  | 2013-09-24 | 2013-09-24 09:30 | 2013-09-24 09:31 | GOODMAN - PGB0360751A | 60 | 4.6 | Yes | Yes | 18.8 | 16.5 | 2.3 | 85A8697172994A89B69D747D574A3C2E |  | R22 | Non-TXV |  | 7.667% | 0.92333 | 14.73% | [5 empty] | Non-TXV | 7.667%
Murphys | CA | 95247-0000 |  | 2013-08-22 | 2013-08-22 13:14 | 2013-08-22 13:36 | CARRIER - 38CK048-301 | 105 | 7 | Yes | Yes | 18.4 | 20.9 | -2.5 | 13E4EF32811548A691CC1DBD2A4CED99 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93710-5734 |  | 2013-06-10 | 2013-06-10 21:28 | 2013-06-10 21:50 | CARRIER - SK4P39FG | 59 | 2.3 | Yes | Yes | 17.7 | 19.2 | -1.5 | D3559C25FC7F4ADBB75F5355F449FAFF |  | R22 | Non-TXV |  | 3.898% | 0.96102 | 7.492% | [5 empty] | Non-TXV | 3.898%
N San Juan | CA | 95960-9620 |  | 2013-10-23 | 2013-10-23 13:32 | 2013-10-23 13:32 | TEMPSTAR - TCA036AKC4 | 96 | 0 | Yes | Yes | 26.3 | 20.9 | 5.4 | E8B849A67DD047D38C72BC392CC91F19 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95965-4183 |  | 2013-08-06 | 2013-08-06 14:16 | 2013-08-06 16:00 | TRANE - 2TTR2030A1000AA | 68 | 6.7 | Yes | Yes | 21.3 | 22 | -0.7 | A500A55B5DD64B77B65AD7F105623A77 |  | R22 | Non-TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | Non-TXV | 9.853%
Fresno | CA | 93726-5402 |  | 2013-06-06 | 2013-06-06 14:51 | 2013-06-06 15:09 | WEATHER KING - 10AJA3001 | 80 | 3.7 | Yes | Yes | 19.5 | 21.1 | -1.6 | D70B47BA53B64553BAF5B8DE338CABA4 |  | R22 | Non-TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | Non-TXV | 4.625%
Fresno | CA | 93726-2139 |  | 2013-06-05 | 2013-06-05 17:18 | 2013-06-05 18:00 | YORK - DAYP-F042NO80A | 150 | 8.6 | Yes | Yes | 21.6 | 20.6 | 1 | 28EA85ED15A740A09C9EB523FE19FAFC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.733% | 0.94267 | 11.02% | [5 empty] | Non-TXV | 5.733%
Yuba City | CA | 95993-6087 |  | 2013-07-18 | 2013-07-18 11:43 | 2013-07-18 12:15 | LENNOX - 10ACC-0360230-02 | 74 | 6.4 | Yes | Yes | 17 | 19.9 | -2.9 | 8D228E6ADE4048868DBE556F0E83F224 |  | R22 | TXV |  | 8.649% | 0.91351 | 16.62% | [5 empty] | TXV | 8.649%
Merced | CA | 95341-5504 |  | 2013-06-12 | 2013-06-12 09:03 | 2013-06-12 09:17 | ARCOAIRE - HAC030AKA1 | 74 | 7.1 | Yes | Yes | 24.1 | 18.2 | 5.9 | 4BC7B7FD6CE24CF4981986D80BC44540 |  | R22 | Non-TXV |  | 9.595% | 0.90405 | 18.44% | [5 empty] | Non-TXV | 9.595%
Tracy | CA | 95376-1433 |  | 2013-07-16 | 2013-07-16 13:23 | 2013-07-16 13:51 | GOODMAN - CKL49-1A | 112 | 3.8 | Yes | Yes | 21.3 | 18.7 | 2.6 | 03CF696C5E06407E8E63D9674D77E93F |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Kerman | CA | 93630-9162 |  | 2013-08-21 | 2013-08-21 10:50 | 2013-08-21 10:52 | BRYANT - 574BNW042060NB | 164 | 4.9 | Yes | Yes | 19.4 | 17.4 | 2 | 99B44649703C473589448DE139912B82 |  | R410A | Non-TXV |  | 2.988% | 0.97012 | 5.742% | [5 empty] | Non-TXV | 2.988%
Fresno | CA | 93726-2722 |  | 2013-06-03 | 2013-06-03 15:01 | 2013-06-03 15:09 | GOODMAN - PGJ042100-1 | 90 | 3.4 | Yes | Yes | 24.1 | 21 | 3.1 | 4A312862087340619FD68648DD4BFD39 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Kerman | CA | 93630-0000 |  | 2013-07-31 | 2013-07-31 08:46 | 2013-07-31 08:47 | TRANE - 2YCC3036A1064AB | 82 | 6.7 | Yes | Yes | 22.4 | 18.5 | 3.9 | 5D66E20CA75A499A9F5B1C9475783F73 |  | R22 | Non-TXV |  | 8.171% | 0.91829 | 15.7% | [5 empty] | Non-TXV | 8.171%
Fresno | CA | 93720-4133 |  | 2013-06-25 | 2013-06-25 09:37 | 2013-06-25 09:42 | LENNOX - 12ACB36-5P | 103 | 3.3 | Yes | Yes | 17.6 | 16.8 | 0.8 | 5AC4990F9012498EBEB74C9C01F7DC0A |  | R22 | Non-TXV |  | 3.204% | 0.96796 | 6.157% | [5 empty] | Non-TXV | 3.204%
Sanger | CA | 93657-2198 |  | 2013-10-01 | 2013-10-01 14:35 | 2013-10-01 14:53 | UNITARY PRODUCTS GROUP - H2RC042S06G | 109 | 3.7 | Yes | Yes | 18 | 20.7 | -2.7 | 47ABC7F80874425895E2CC49DDA2D866 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.394% | 0.96606 | 6.523% | [5 empty] | Non-TXV | 3.394%
Newman | CA | 95360-1497 |  | 2013-08-22 | 2013-08-22 13:22 | 2013-08-22 13:44 | PAYNE - PA13NR036-J | 84 | 2.6 | Yes | Yes | 21.8 | 21 | 0.8 | A0CEB451455C4812AF63B5099C274F93 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Paradise | CA | 95969-4505 |  | 2013-08-08 | 2013-08-08 12:15 | 2013-08-08 13:23 | RUUD - RRNA-A036JK08E | 114 | 4.2 | Yes | Yes | 25 | 21.3 | 3.8 | 401F2292706A4B888C5B7802699598DE |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Sanger | CA | 93657-2442 |  | 2013-07-22 | 2013-07-22 12:33 | 2013-07-22 13:15 | YORK - D1NA030N03606C | 76 | 2.8 | Yes | Yes | 19.5 | 20.4 | -0.9 | 270E6B4AB9FB4B149FC87D6418BE2DAC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Clovis | CA | 93611-3007 |  | 2013-08-23 | 2013-08-23 09:16 | 2013-08-23 09:36 | RHEEM - RRPL-B030JKO6X | 76 | 3.7 | Yes | Yes | 17 | 19.9 | -2.9 | 1993D34AB44046069295F61998FB48D8 | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 4.868% | 0.95132 | 9.356% | [5 empty] | TXV | 4.868%
Chowchilla | CA | 93610-2236 |  | 2013-06-14 | 2013-06-14 09:28 | 2013-06-14 09:28 | YORK - D1NQO030N5606NXA | 83 | 0 | Yes | Yes | 18.5 | 19.8 | -1.3 | CB30BE6EDA6A4C79B70EBE238D8C48E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9408 |  | 2013-07-18 | 2013-07-18 12:08 | 2013-07-18 12:34 | YORK - D1NA030N05606C | 66 | 2.5 | Yes | Yes | 17 | 19.9 | -2.9 | 9D0018A65C2249E3BDDACCC40DB3AF03 |  | R22 | Non-TXV |  | 3.788% | 0.96212 | 7.279% | [5 empty] | Non-TXV | 3.788%
Lathrop | CA | 95330-8538 |  | 2013-07-30 | 2013-07-30 09:25 | 2013-07-30 09:43 | CARRIER - 24ABA342A310 | 98 | 2.9 | Yes | Yes | 22 | 18.7 | 3.3 | 6818E182550D4BAF8B3A3E6A33797E2A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 2.959% | 0.97041 | 5.687% | [5 empty] | Non-TXV | 2.959%
Los Banos | CA | 93635-3808 |  | 2013-05-31 | 2013-05-31 10:48 | 2013-05-31 10:50 | BRYANT - 582ANW030040AAAD | 55 | 5.2 | Yes | Yes | 20.7 | 19.6 | 1.1 | CAF2436EEB8944CB9E19385D4D86D5B9 |  | R22 | Non-TXV |  | 9.455% | 0.90545 | 18.17% | [5 empty] | Non-TXV | 9.455%
Stockton | CA | 95210-3433 |  | 2013-07-08 | 2013-07-08 11:45 | 2013-07-08 12:02 | RHEEM - RAMB-036JAZ | 93 | -5.5 | Yes | Yes | 22.9 | 18.6 | 4.3 | D1FE91EFF7714F3CB7AA8D5BB36EA5D9 |  | R22 | Non-TXV |  | -5.914% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.914%
Diamond Springs | CA | 95619-9708 |  | 2013-07-05 | 2013-07-05 14:23 | 2013-07-05 14:39 | CARRIER - 38TRA036330 | 105 | 3.1 | Yes | Yes | 19 | 20.4 | -1.4 | C7C927BA3CB842E291EFC1D32ACB74AA |  | R22 | Non-TXV |  | 2.952% | 0.97048 | 5.674% | [5 empty] | Non-TXV | 2.952%
Newman | CA | 95360-9667 |  | 2013-06-05 | 2013-06-05 13:48 | 2013-06-05 14:17 | GIBSON - JS3BC-030KA | 68 | 10 | Yes | Yes | 18 | 19.3 | -1.3 | 273D73CF5D7540BDB9FCDC2B96271CD1 |  | R22 | Non-TXV |  | 14.71% | 0.85294 | 28.26% | [5 empty] | Non-TXV | 14.71%
Lathrop | CA | 95330-9371 |  | 2013-07-24 | 2013-07-24 09:55 | 2013-07-24 10:29 | AIRE-FLO - 38CKC048370 | 99 | 3.5 | Yes | Yes | 17.2 | 19.9 | -2.7 | 68D981CF51EE436A88BD96418035D341 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.535% | 0.96465 | 6.794% | [5 empty] | Non-TXV | 3.535%
Diamond Springs | CA | 95619-9208 |  | 2013-07-05 | 2013-07-05 13:22 | 2013-07-05 13:41 | TRANE - YCX0361M0AC | 109 | 3.8 | Yes | Yes | 25 | 22 | 3 | E1937C05C1E24E2BA9617E27065CC44C |  | R22 | Non-TXV |  | 3.486% | 0.96514 | 6.7% | [5 empty] | Non-TXV | 3.486%
Newman | CA | 95360-1448 |  | 2013-07-29 | 2013-07-29 12:53 | 2013-07-29 13:30 | UNITARY PRODUCTS GROUP - TCGD30S21HA | 59 | 5.8 | Yes | Yes | 21.5 | 19 | 2.5 | 7698BE0DF7F24EBC84D6D492D5833F55 |  | R22 | Non-TXV |  | 9.831% | 0.90169 | 18.89% | [5 empty] | Non-TXV | 9.831%
Fresno | CA | 93727-5248 |  | 2013-07-15 | 2013-07-15 13:51 | 2013-07-15 13:59 | LENNOX - 13ACC-042-230-7P | 123 | 5.4 | Yes | Yes | 17.8 | 19.7 | -1.9 | 2B13551D737A4E289F693CC8BDC0CEE6 |  | R22 | Non-TXV |  | 4.39% | 0.9561 | 8.437% | [5 empty] | Non-TXV | 4.39%
Fresno | CA | 93727-5248 |  | 2013-07-15 | 2013-07-15 14:02 | 2013-07-15 14:18 | LENNOX - 13ACC-036-230-02 | 114 | 8.8 | Yes | Yes | 18.6 | 20.2 | -1.6 | 0229A42928604D58A98BEF99A9327181 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.719% | 0.92281 | 14.83% | [5 empty] | Non-TXV | 7.719%
Merced | CA | 95341-9760 |  | 2013-06-05 | 2013-06-05 10:00 | 2013-06-05 10:04 | YORK - E1RC036S06D | 116 | 3.9 | Yes | Yes | 16 | 17.7 | -1.7 | CF0D937DE20B48CB942B291787951ACC |  | R22 | Non-TXV |  | 3.362% | 0.96638 | 6.461% | [5 empty] | Non-TXV | 3.362%
Kerman | CA | 93630-1211 |  | 2013-07-31 | 2013-07-31 09:58 | 2013-07-31 10:00 | LENNOX - 12ACB364P | 106 | 9 | Yes | Yes | 22.1 | 19.3 | 2.8 | D2EBADA6553F4EBDB874702F50755ABD |  | R22 | Non-TXV |  | 8.491% | 0.91509 | 16.32% | [5 empty] | Non-TXV | 8.491%
Colfax | CA | 95713-9249 |  | 2013-07-26 | 2013-07-26 09:15 | 2013-07-26 09:42 | WESTINGHOUSE - R4GA-030K072X | 65 | 2.4 | Yes | Yes | 20.5 | 20.7 | -0.2 | 544D434F098A47FC8FA5C726D4BAD9FB |  | R22 | TXV |  | 3.692% | 0.96308 | 7.096% | [5 empty] | TXV | 3.692%
Stockton | CA | 95209-3035 |  | 2013-07-11 | 2013-07-11 12:51 | 2013-07-11 13:11 | DAY & NIGHT - 588ANW03608ACAF | 67 | 5 | Yes | Yes | 22.7 | 20.4 | 2.3 | D9787CADBCBA4F24A4F8ABEF0AD6DBE7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.463% | 0.92537 | 14.34% | [5 empty] | Non-TXV | 7.463%
Stockton | CA | 95209-2345 |  | 2013-07-11 | 2013-07-11 09:39 | 2013-07-11 09:39 | OTHER - 80WR24A1A | 48 | 0 | Yes | Yes | 16.1 | 19 | -2.9 | 662CE413364F444497BC25743D08EAF7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-1820 |  | 2013-07-12 | 2013-07-12 18:54 | 2013-07-12 19:12 | BDP - 541B028SHP | 90 | 5.7 | Yes | Yes | 18.2 | 20.4 | -2.2 | 86540A0C327245068FFB66F92EBC593B |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Stockton | CA | 95205-0000 |  | 2013-07-11 | 2013-07-11 10:58 | 2013-07-11 11:26 | GOODMAN - GSC130361DE | 119 | -8 | Yes | Yes | 18.3 | 20.2 | -1.9 | 38DFA60E6CAB4E1284B9485FC50B47E7 |  | R22 | Non-TXV |  | -6.723% | 1.0672 | 1.883% |  |  |  |  | Non-TXV |  |  | -6.723%
Stockton | CA | 95209-1333 |  | 2013-07-03 | 2013-07-03 10:41 | 2013-07-03 10:58 | PAYNE - 567C042RCU | 74 | 6.2 | Yes | Yes | 22.2 | 19.3 | 2.9 | 48E597D8E13A451C9397988C897DEF22 |  | R22 | TXV |  | 8.378% | 0.91622 | 16.1% | [5 empty] | TXV | 8.378%
Madera | CA | 93637-6310 |  | 2013-07-04 | 2013-07-04 15:54 | 2013-07-04 15:54 | LENNOX - GCS29X306-2PA | 93 | 0 | Yes | Yes | 19.6 | 21.5 | -1.9 | 2E510468B5CA47CCB5F730D86AEACDFE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3541 |  | 2013-07-16 | 2013-07-16 12:49 | 2013-07-16 12:51 | RHEEM - RRKA-A030JK06X | 54 | 2.2 | Yes | Yes | 21 | 20.8 | 0.2 | A3AF9588DBEE46FCA6CC6B9BEBC0EE62 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Madera | CA | 93638-4408 |  | 2013-09-06 | 2013-09-06 12:59 | 2013-09-06 13:01 | YORK - D1NA036N03606C | 63 | 2.8 | Yes | Yes | 19.1 | 19.8 | -0.7 | 0B83086336674C83BFB2C7A895131E7E |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Chowchilla | CA | 93610-2003 |  | 2013-06-02 | 2013-06-02 09:49 | 2013-06-02 10:32 | RHEEM - RRMA-A036JK06X | 98 | -9.2 | Yes | Yes | 18.1 | 21 | -2.9 | 7F366A7E01394B4A91F2D9670EE6190D |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Manteca | CA | 95337-6509 |  | 2013-07-16 | 2013-07-16 17:51 | 2013-07-16 18:14 | UNITARY PRODUCTS GROUP - GCGD30S41S1A | 62 | 2.2 | Yes | Yes | 24.7 | 20.1 | 4.6 | 08EB539960434731A7B2CE3B14F5A1BC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Sonora | CA | 95370-7511 |  | 2013-07-31 | 2013-07-31 13:30 | 2013-07-31 14:03 | RUUD - UAKA-037JAZ | 79 | 6.5 | Yes | Yes | 19.7 | 20.2 | -0.5 | 5DCF3DF73C9549B7988FFF274FBE1264 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.228% | 0.91772 | 15.81% | [5 empty] | Non-TXV | 8.228%
Kerman | CA | 93630-9161 |  | 2013-08-01 | 2013-08-01 09:23 | 2013-08-01 09:25 | BRYANT - 574BNW036060NB | 149 | 12.5 | Yes | Yes | 23.8 | 18.8 | 5 | 69AC4DDEAEF64F1483660EAEB5DB3FC5 |  | R22 | Non-TXV |  | 8.389% | 0.91611 | 16.12% | [5 empty] | Non-TXV | 8.389%
Stockton | CA | 95219-5483 |  | 2013-06-25 | 2013-06-25 09:41 | 2013-06-25 09:59 | CARRIER - 38EN018310SM | 60 | 2.2 | Yes | Yes | 15.4 | 17.6 | -2.2 | 752324B4347346498CE1ADF17B1A6F72 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Oakhurst | CA | 93644-8614 |  | 2013-08-14 | 2013-08-14 15:19 | 2013-08-14 16:06 | LENNOX - 12G CSO 036753 PA | 110 | -10.4 | Yes | Yes | 18.7 | 19.4 | -0.7 | C9B639C13616435D90F5BBC101D3B7D9 |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Plumas Lake | CA | 95961-8706 |  | 2013-10-16 | 2013-10-16 14:01 | 2013-10-16 14:21 | LENNOX - UNK | 111 | 4 | Yes | Yes | 21 | 20.6 | 0.4 | 58AE7C0BEF4A4AE98F7C08E11310F658 |  | R22 | TXV |  | 3.604% | 0.96396 | 6.925% | [5 empty] | TXV | 3.604%
Stockton | CA | 95209-1789 |  | 2013-07-10 | 2013-07-10 10:32 | 2013-07-10 10:53 | PAYNE - 585HJ036060 | 102 | -9.6 | Yes | Yes | 25 | 19.9 | 5.1 | 8E3B333E746C46A9A33C9C15CFC83AB3 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93705-0745 |  | 2013-07-10 | 2013-07-10 12:47 | 2013-07-10 13:10 | ICP - PGAA36C1K4 | 69 | 5.8 | Yes | Yes | 22.9 | 21 | 1.9 | 96B12A2554E746798107D3A893F444F8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.406% | 0.91594 | 16.15% | [5 empty] | Non-TXV | 8.406%
Grass Valley | CA | 95945-6828 |  | 2013-09-11 | 2013-09-11 17:00 | 2013-09-11 17:17 | PAYNE - 565AJ024 | 70 | 2.7 | Yes | Yes | 16.9 | 19.9 | -3 | EC0747E2F0EB43C4A50F708885701318 |  | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
Fresno | CA | 93726-5927 |  | 2013-06-07 | 2013-06-07 11:07 | 2013-06-07 11:17 | UNITARY PRODUCTS GROUP - GCGD36S41S3A | 73 | 4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 9644C3A9B29B46468D08D923A27BDBC3 |  | R410A | Non-TXV |  | 5.479% | 0.94521 | 10.53% | [5 empty] | Non-TXV | 5.479%
Fresno | CA | 93726-5120 |  | 2013-08-13 | 2013-08-13 14:22 | 2013-08-13 14:42 | PAYNE - UNK | 64 | 4 | Yes | Yes | 16.7 | 18.8 | -2.1 | 70A170453AE4435C9E80DE8246F53767 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fresno | CA | 93705-0804 |  | 2013-07-08 | 2013-07-08 13:37 | 2013-07-08 13:55 | RHEEM - RRKA-A030JK06E | 54 | 10.3 | Yes | Yes | 19.2 | 20.2 | -1 | BC9C8CC4491C45EE9D2CF70F0ECCF8E9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.07% | 0.80926 | 36.66% | [5 empty] | Non-TXV | 19.07%
Fresno | CA | 93720-2414 |  | 2013-06-25 | 2013-06-25 12:08 | 2013-06-25 12:10 | OTHER - 48SX042060331AA | 87 | 11.1 | Yes | Yes | 19.3 | 17.3 | 2.1 | AFF4A90420ED4565BBC7442C6A6F5075 |  | R22 | Non-TXV |  | 12.76% | 0.87241 | 24.52% | [5 empty] | Non-TXV | 12.76%
Fresno | CA | 93726-5868 |  | 2013-06-07 | 2013-06-07 14:59 | 2013-06-07 15:05 | BRYANT - 113ANA036000BEAA | 83 | 3 | Yes | Yes | 23.4 | 20 | 3.5 | 9109DF725D40423781ABDD70B76FD56C |  | R410A | Non-TXV |  | 3.614% | 0.96386 | 6.946% | [5 empty] | Non-TXV | 3.614%
Fresno | CA | 93722-6806 |  | 2013-08-09 | 2013-08-09 15:01 | 2013-08-09 15:03 | PAYNE - 7777UNK | 144 | 4.7 | Yes | Yes | 22.4 | 20.9 | 1.5 | 87B15B58B7654E26B69B9EED59123FBC |  | R22 | Non-TXV |  | 3.264% | 0.96736 | 6.272% | [5 empty] | Non-TXV | 3.264%
Fresno | CA | 93722-9782 |  | 2013-07-25 | 2013-07-25 12:59 | 2013-07-25 13:03 | BDP - 585JW036060ABAF | 82 | 14.8 | Yes | Yes | 20.4 | 20.8 | -0.4 | 9CA2A284617C49AF94C2E8E8715C8B34 |  | R22 | Non-TXV |  | 18.05% | 0.81951 | 34.69% | [5 empty] | Non-TXV | 18.05%
Grass Valley | CA | 95945-9338 |  | 2013-06-29 | 2013-06-29 12:14 | 2013-06-29 12:14 | DAY & NIGHT - 567AJ30RCU | 63 | 0 | Yes | Yes | 17.7 | 18.2 | -0.5 | 0DB445DF70B44542A4B2BEEF656CF61C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5413 |  | 2013-06-27 | 2013-06-27 14:03 | 2013-06-27 14:08 | WEATHER KING - 13AJA42A01 | 121 | 4.7 | Yes | Yes | 19.3 | 19.5 | -0.2 | C1E48B512B344F408C8A3A7408266CBF |  | R22 | Non-TXV |  | 3.884% | 0.96116 | 7.465% | [5 empty] | Non-TXV | 3.884%
Sanger | CA | 93657-2164 |  | 2013-08-06 | 2013-08-06 09:18 | 2013-08-06 09:35 | YORK - D1NA030N0360A | 72 | 5.3 | Yes | Yes | 18.5 | 20.4 | -1.9 | CF1F689151BE4632B1C97F8B7D1428A7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.361% | 0.92639 | 14.15% | [5 empty] | Non-TXV | 7.361%
Stockton | CA | 95209-1163 |  | 2013-07-03 | 2013-07-03 09:34 | 2013-07-03 09:34 | BRYANT - 561CJ036-F | 71 | 0 | Yes | Yes | 16.9 | 19.7 | -2.8 | E6BB719D5D72481E96DBB2521C8FADCF |  | R22 | TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-3036 |  | 2013-08-01 | 2013-08-01 15:40 | 2013-08-01 16:13 | OTHER - DAYQ-F024N045A | 57 | -5.4 | Yes | Yes | 17.9 | 18.7 | -0.8 | F2DB858396B046FA9F0F276F538F8C2A |  | R22 | Non-TXV |  | -9.474% | 1.0947 | 2.653% |  |  |  |  | Non-TXV |  |  | -9.474%
Fresno | CA | 93704-4615 |  | 2013-08-12 | 2013-08-12 15:02 | 2013-08-12 15:03 | GOODMAN - PGB0360 | 60 | 9.1 | Yes | Yes | 20.2 | 17.7 | 2.5 | 700182308C9F44D895D9623937D49D5D |  | R22 | Non-TXV |  | 15.17% | 0.84833 | 29.15% | [5 empty] | Non-TXV | 15.17%
Fresno | CA | 93702-4477 |  | 2013-07-11 | 2013-07-11 11:38 | 2013-07-11 11:41 | GOODMAN - GPG13360451AA | 112 | 4.6 | Yes | Yes | 21.4 | 18.8 | 2.6 | 5865958CC7F54FAEBA90180FF5B3B868 |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Fresno | CA | 93710-3606 |  | 2013-08-09 | 2013-08-09 17:32 | 2013-08-09 21:53 | YORK - DCYZ-F024N080A | 76 | 3.8 | Yes | Yes | 20 | 20.4 | -0.4 | 53F5A4CF5A5848DAA14B26B3AF407288 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93710-5744 |  | 2013-08-10 | 2013-08-10 14:56 | 2013-08-10 15:13 | BDP - UNK | 66 | 2.4 | Yes | Yes | 16 | 16.9 | -0.9 | 064007C73E214451AAFA7EBF6C14F9C7 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Manteca | CA | 95336-3140 |  | 2013-07-08 | 2013-07-08 09:05 | 2013-07-08 09:29 | AMANA - RCE60A2D | 85 | -8 | Yes | Yes | 21.1 | 18.2 | 2.9 | 4F636F4C10904CC58C6BFFC2C9D9C71C |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95210-1819 |  | 2013-07-24 | 2013-07-24 10:17 | 2013-07-24 10:34 | GOODMAN - GPG10300701A0404213231 | 56 | 3.3 | Yes | Yes | 22.9 | 20.2 | 2.7 | BB1312355237458682200CF95B230C5E |  | R22 | Non-TXV |  | 5.893% | 0.94107 | 11.32% | [5 empty] | Non-TXV | 5.893%
Stockton | CA | 95207-7546 |  | 2013-06-26 | 2013-06-26 09:36 | 2013-06-26 09:53 | OTHER - N2A330AKA300 | 84 | -8.4 | Yes | Yes | 20 | 16.4 | 3.6 | CDAF2654A86F4BC5B6E8357475E2E7F6 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Fresno | CA | 93726-5805 |  | 2013-06-25 | 2013-06-25 11:14 | 2013-06-25 11:15 | TRANE - YCX036F1M0AB | 96 | 3.1 | Yes | Yes | 22.5 | 18.9 | 3.7 | 2D91536D60514728B6CB0B1F7E4A0A92 |  | R22 | Non-TXV |  | 3.229% | 0.96771 | 6.206% | [5 empty] | Non-TXV | 3.229%
Chico | CA | 95973-7647 |  | 2013-07-09 | 2013-07-09 19:23 | 2013-07-09 19:47 | OTHER - 561A5036-B | 72 | 3.2 | Yes | Yes | 23.8 | 22.4 | 1.5 | B42391EB2188436B819C6BA18165FEDE |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Fresno | CA | 93704-1329 |  | 2013-06-25 | 2013-06-25 14:22 | 2013-06-25 14:26 | TAPPAN - RTA337541 | 62 | 12.5 | Yes | Yes | 26.2 | 24.2 | 2 | 3FCD3B9145784FFD93EBC7A9B344C384 |  | R22 | Non-TXV |  | 20.16% | 0.79839 | 38.75% | [5 empty] | Non-TXV | 20.16%
Fresno | CA | 93704-4158 |  | 2013-06-25 | 2013-06-25 15:29 | 2013-06-25 15:31 | BRYANT - 583BNW060090AB | 160 | 4.9 | Yes | Yes | 25.5 | 21.7 | 3.8 | F64B16783BEA40B497A0BAB7D335AF78 |  | R410A | Non-TXV |  | 3.062% | 0.96937 | 5.885% | [5 empty] | Non-TXV | 3.062%
Chico | CA | 95926-1753 |  | 2013-07-01 | 2013-07-01 08:39 | 2013-07-01 10:38 | YORK - W065484218 | 63 | 2 | Yes | Yes | 25.1 | 20.4 | 4.7 | 06FDB12681F3416FAA381C5520AA51AF |  | R22 | Non-TXV |  | 3.175% | 0.96825 | 6.101% | [5 empty] | Non-TXV | 3.175%
Fresno | CA | 93704-1112 |  | 2013-06-25 | 2013-06-25 09:51 | 2013-06-25 09:53 | YORK - DDYZF048N080A | 68 | 2.3 | Yes | Yes | 21.1 | 16.9 | 4.2 | DD097888ACA7457183DD9D43D9D470A0 |  | R410A | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Selma | CA | 93662-2900 |  | 2013-08-20 | 2013-08-20 16:49 | 2013-08-20 17:40 | BDP - 588ANW030040ACADPO | 53 | 3.6 | Yes | Yes | 18.5 | 18.8 | -0.3 | B0B325611311420C9DBA20D9735C77CC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.792% | 0.93208 | 13.05% | [5 empty] | Non-TXV | 6.792%
Tracy | CA | 95376-3180 |  | 2013-07-23 | 2013-07-23 13:41 | 2013-07-23 14:01 | RHEEM - CBD | 64 | 6.5 | Yes | Yes | 23.5 | 19.2 | 4.3 | B0AB40270E5B4938BFA9D87CE5EEB021 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.16% | 0.89844 | 19.52% | [5 empty] | Non-TXV | 10.16%
Clovis | CA | 93611-0626 |  | 2013-06-25 | 2013-06-25 16:43 | 2013-06-25 17:11 | GOODMAN - GPG13600901BB | 164 | 7.6 | Yes | Yes | 24.6 | 20.6 | 4 | 86A41E29B753478187B97C179F8BFA6B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.634% | 0.95366 | 8.906% | [5 empty] | Non-TXV | 4.634%
Fresno | CA | 93728-2710 |  | 2013-08-15 | 2013-08-15 12:59 | 2013-08-15 13:02 | GOODMAN - GPG13480701AB | 145 | 4.9 | Yes | Yes | 21.5 | 18.1 | 3.4 | E9B3AD5294D445E5AAB3858F1ADDE5ED |  | R22 | Non-TXV |  | 3.379% | 0.96621 | 6.494% | [5 empty] | Non-TXV | 3.379%
Tracy | CA | 95376-7208 |  | 2013-07-11 | 2013-07-11 11:39 | 2013-07-11 12:07 | DAY & NIGHT - 561ANJ042-A | 168 | 8.3 | Yes | Yes | 24.4 | 20.9 | 3.5 | 37AB5EDCA81E43A1874ECFB461232C50 |  | R22 | Non-TXV |  | 4.94% | 0.9506 | 9.495% | [5 empty] | Non-TXV | 4.94%
Fresno | CA | 93705-2318 |  | 2013-07-09 | 2013-07-09 11:20 | 2013-07-09 11:59 | RHEEM - RRKA-A030JK06X | 54 | 3.5 | Yes | Yes | 23.1 | 20.6 | 2.5 | 2045DFF72FC94F59977A51AA8679F104 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Fresno | CA | 93710-3940 |  | 2013-07-23 | 2013-07-23 08:58 | 2013-07-23 09:00 | ICP - CAC042AKA1 | 98 | 14.3 | Yes | Yes | 22.7 | 19.7 | 3 | 14DC6F38E797438198FCD8A2AE618BD6 |  | R22 | Non-TXV |  | 14.59% | 0.85408 | 28.04% | [5 empty] | Non-TXV | 14.59%
Willows | CA | 95988-0000 |  | 2013-06-26 | 2013-06-26 17:58 | 2013-06-26 17:58 | AMANA - PGD36C0702G | 123 | 0 | Yes | Yes | 22.4 | 19.4 | 3.1 | 9087C0CBF4E346B4824BF6F7804B6504 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-0000 |  | 2013-06-26 | 2013-06-26 18:01 | 2013-06-26 18:18 | AMERICAN STANDARD - TTX348C100A0 | 164 | 14.4 | Yes | Yes | 20.9 | 20.6 | 0.4 | 430EA1C559604C4487606FF2E5462B50 |  | R22 | Non-TXV |  | 8.78% | 0.9122 | 16.87% | [5 empty] | Non-TXV | 8.78%
Madera | CA | 93637-5379 |  | 2013-07-10 | 2013-07-10 14:54 | 2013-07-10 15:16 | RHEEM - URKA-A024JK06E | 61 | 3.9 | Yes | Yes | 21.1 | 19.5 | 1.6 | 394CCF11CE7B44CDBBE48695E625C6E1 |  | R22 | Non-TXV |  | 6.393% | 0.93607 | 12.29% | [5 empty] | Non-TXV | 6.393%
Fresno | CA | 93705-3345 |  | 2013-08-12 | 2013-08-12 12:33 | 2013-08-12 12:34 | YORK - D1NA024N03606C | 54 | 3 | Yes | Yes | 18.9 | 18.3 | 0.6 | 855D1A9CFAA94D1B8D75389F0B86C790 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Stockton | CA | 95203-3008 |  | 2013-07-15 | 2013-07-15 11:07 | 2013-07-15 11:26 | BRYANT - 113RNA042-A | 113 | 7.2 | Yes | Yes | 19.3 | 19.9 | -0.6 | 78215AF0EDAF4FCBAF88CC7B7B945978 |  | R22 | Non-TXV |  | 6.372% | 0.93628 | 12.24% | [5 empty] | Non-TXV | 6.372%
Fresno | CA | 93728-1034 |  | 2013-08-12 | 2013-08-12 09:40 | 2013-08-12 10:29 | ICP - GPFM48K080F | 99 | 3.7 | Yes | Yes | 18 | 19.3 | -1.3 | 6D0F5E31E23142DD8F7E6AE8C0CE66FB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.737% | 0.96263 | 7.182% | [5 empty] | Non-TXV | 3.737%
Los Banos | CA | 93635-6420 |  | 2013-08-05 | 2013-08-05 09:30 | 2013-08-05 09:35 | BRYANT - 563CN060-G | 204 | 6 | Yes | Yes | 22.3 | 19.9 | 2.4 | 25BBAACE28CE4DD2978663BA0411C92C |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93728-1038 |  | 2013-07-16 | 2013-07-16 11:25 | 2013-07-16 11:27 | CARRIER - 48XP-030040301 | 128 | 3.9 | Yes | Yes | 22 | 19.9 | 2.1 | B11EB758DC944684A8769B2D6C14178F |  | R410A | Non-TXV |  | 3.047% | 0.96953 | 5.855% | [5 empty] | Non-TXV | 3.047%
Madera | CA | 93637-6310 |  | 2013-09-05 | 2013-09-05 12:37 | 2013-09-05 12:40 | LENNOX - GCS29036752PA | 58 | 7.5 | Yes | Yes | 27.5 | 21.5 | 6 | 3F24BB14C44A45AC8A53346B2022ACB5 |  | R22 | Non-TXV |  | 12.93% | 0.87069 | 24.85% | [5 empty] | Non-TXV | 12.93%
Fresno | CA | 93705-4341 |  | 2013-07-09 | 2013-07-09 17:46 | 2013-07-09 18:03 | YORK - N/A | 90 | 2.9 | Yes | Yes | 16.3 | 18.5 | -2.2 | F06F85F349834F52BC835A0DDB8EDEFE |  | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Tracy | CA | 95377-7011 |  | 2013-07-19 | 2013-07-19 13:56 | 2013-07-19 14:15 | UNITARY PRODUCTS GROUP - AC042X1021A | 84 | 16 | Yes | Yes | 18.7 | 21.5 | -2.8 | 2BAE8B2A6FD743789919A81CF0961047 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.05% | 0.80952 | 36.61% | [5 empty] | Non-TXV | 19.05%
Lathrop | CA | 95330-9446 |  | 2013-07-03 | 2013-07-03 09:25 | 2013-07-03 09:54 | RHEEM - UNK | 64 | 2.4 | Yes | Yes | 21.7 | 19 | 2.7 | F1EA5ABAE35149499B92977D1A94E844 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95209-5038 |  | 2013-07-22 | 2013-07-22 13:03 | 2013-07-22 13:25 | PAYNE - 567GJ042 | 94 | -5.5 | Yes | Yes | 23.3 | 19.3 | 4 | EEDDCBA577734F9A85AA95C4CDD564D7 |  | R22 | Non-TXV |  | -5.851% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.851%
Stockton | CA | 95203-2014 |  | 2013-07-29 | 2013-07-29 08:56 | 2013-07-29 09:20 | LENNOX - HS26-030-2P | 78 | 3.4 | Yes | Yes | 20.7 | 18.2 | 2.5 | AA380D17B1AF4851A7CFCB6F7A1D161F |  | R22 | Non-TXV |  | 4.359% | 0.95641 | 8.377% | [5 empty] | Non-TXV | 4.359%
Chowchilla | CA | 93610-2315 |  | 2013-06-02 | 2013-06-02 12:22 | 2013-06-02 12:45 | AMERICAN STANDARD - YCP06036F1MOAC | 108 | -10.2 | Yes | Yes | 18.6 | 19.8 | -1.2 | 61583FFFED234ECDBE06168F270C2665 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Stockton | CA | 95207-2844 |  | 2013-07-29 | 2013-07-29 12:56 | 2013-07-29 13:18 | YORK - GCGD30S41S3A | 85 | 3 | Yes | Yes | 16.5 | 18.2 | -1.7 | 53187BDD4BB442CE98C4990C10D5B6BA |  | R410A | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Chowchilla | CA | 93610-3032 |  | 2013-06-14 | 2013-06-14 12:05 | 2013-06-14 12:05 | RHEEM - RRPL-B030JK06X | 76 | 0 | Yes | Yes | 20 | 22.1 | -2.1 | 3930EBFA475A4086A8C45D1F235AFA0C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8048 |  | 2013-07-16 | 2013-07-16 16:14 | 2013-07-16 17:15 | GOODMAN - GPG1336045M41AC | 85 | 3.7 | Yes | Yes | 25.4 | 19.6 | 5.8 | 04619AD2C1BA430DAC1A6635F05FD30F | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | TXV | 4.353%
Stockton | CA | 95209-1539 |  | 2013-07-10 | 2013-07-10 09:17 | 2013-07-10 09:17 | PAYNE - 561AJ036-B | 73 | 0 | Yes | Yes | 24.7 | 19 | 5.7 | 09BB90A279C84D0D94962DC0820D5CFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-5906 |  | 2013-08-29 | 2013-08-29 09:20 | 2013-08-29 09:45 | BRYANT - 563CN036-F | 100 | 3.9 | Yes | Yes | 15.5 | 17.1 | -1.6 | EA7E9A81BCF7417CBA2B7545A0FF639F |  | R22 | Non-TXV |  | 3.9% | 0.961 | 7.495% | [5 empty] | Non-TXV | 3.9%
Yuba City | CA | 95993-5906 |  | 2013-08-29 | 2013-08-29 09:30 | 2013-08-29 09:54 | BRYANT - 563CN042-E | 105 | 6.5 | Yes | Yes | 16 | 18.8 | -2.8 | 96156F0E9DAF4C88A6CCFE35E5E4974A |  | R22 | Non-TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | Non-TXV | 6.19%
Stockton | CA | 95210-3226 |  | 2013-07-08 | 2013-07-08 08:53 | 2013-07-08 09:14 | GOODMAN - GSC130241AE | 93 | 4.4 | Yes | Yes | 16.6 | 17.7 | -1.1 | 344243C2C76049798183DD2908A96CB6 |  | R22 | Non-TXV |  | 4.731% | 0.95269 | 9.092% | [5 empty] | Non-TXV | 4.731%
Arbuckle | CA | 95912-9715 |  | 2013-08-08 | 2013-08-08 08:33 | 2013-08-08 08:51 | TRANE - YCP042F1H | 128 | 4.7 | Yes | Yes | 22 | 19.5 | 2.5 | 439ACCD7FA5B49AAA55C8F7C117B5041 |  | R22 | TXV |  | 3.672% | 0.96328 | 7.057% | [5 empty] | TXV | 3.672%
Mariposa | CA | 95338-9373 |  | 2013-07-31 | 2013-07-31 14:31 | 2013-07-31 14:32 | RUUD - 7777UNK | 100 | 3.8 | Yes | Yes | 23.4 | 21.4 | 2 | E278285A943A4092AE88291A55709121 |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Tuolumne | CA | 95379-9721 |  | 2013-09-12 | 2013-09-12 11:05 | 2013-09-12 11:28 | RHEEM - RRNA-BO42JKO8X | 104 | -7.3 | Yes | Yes | 18.3 | 19.5 | -1.2 | 928C032512CD4C41A0BA528E3C74D279 |  | R22 | Non-TXV |  | -7.019% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.019%
Stockton | CA | 95215-7421 |  | 2013-09-12 | 2013-09-12 10:53 | 2013-09-12 11:14 | BRYANT - 561CJ036-F | 76 | 13.3 | Yes | Yes | 22.5 | 18.2 | 4.3 | 9E620CD5A38443C19C1008AC031602AF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Merced | CA | 95341-5550 |  | 2013-06-12 | 2013-06-12 11:55 | 2013-06-12 12:01 | YORK - DBYPF030N070A | 73 | 7.2 | Yes | Yes | 21.5 | 18.5 | 3 | BF948C79A01242769873E40FE04006E3 |  | R22 | Non-TXV |  | 9.863% | 0.90137 | 18.95% | [5 empty] | Non-TXV | 9.863%
Stockton | CA | 95209-2052 |  | 2013-07-10 | 2013-07-10 13:36 | 2013-07-10 13:59 | RHEEM - UAKA-037JAZ | 79 | 4.2 | Yes | Yes | 20.2 | 19.3 | 0.9 | 78B05044262741A78A1C10CDDE213A04 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.316% | 0.94684 | 10.22% | [5 empty] | Non-TXV | 5.316%
Stockton | CA | 95209-2051 |  | 2013-07-22 | 2013-07-22 10:12 | 2013-07-22 10:29 | DAY & NIGHT - 565A042RCUE | 114 | -6.7 | Yes | Yes | 21.6 | 16.8 | 4.8 | 9E56EE78A0AB414EBFF2FA9DC23369D4 |  | R22 | Non-TXV |  | -5.877% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.877%
Marysville | CA | 95901-7239 |  | 2013-07-11 | 2013-07-11 16:02 | 2013-07-11 16:22 | BRYANT - 133RNA030-D | 73 | 2.8 | Yes | Yes | 19 | 21 | -2 | BD844C99E38C4DA1890999D8C7BF3F3D |  | R22 | TXV |  | 3.836% | 0.96164 | 7.371% | [5 empty] | TXV | 3.836%
Plumas Lake | CA | 95961-9162 |  | 2013-10-16 | 2013-10-16 12:39 | 2013-10-16 12:59 | YORK - H2RC036S06G | 83 | -8.2 | Yes | Yes | 18 | 20.6 | -2.6 | E50C7DF7EA834CD0907B5AD6CA420524 |  | R22 | Non-TXV |  | -9.88% | 1.0988 | 2.767% |  |  |  |  | Non-TXV |  |  | -9.88%
Stockton | CA | 95207-7764 |  | 2013-06-26 | 2013-06-26 11:11 | 2013-06-26 11:28 | AMERICAN STANDARD - 2A7B3024A1000AA | 82 | 5.4 | Yes | Yes | 19.4 | 17.9 | 1.5 | 06D36F4C6ED24551B5517E752F3F79BB |  | R22 | Non-TXV |  | 6.585% | 0.93415 | 12.66% | [5 empty] | Non-TXV | 6.585%
Stockton | CA | 95204-2812 |  | 2013-07-09 | 2013-07-09 08:31 | 2013-07-09 09:01 | GE - BGTA836R1A | 100 | -9.4 | Yes | Yes | 18.2 | 18.1 | 0.1 | D5022C6BF2E349B3A707E7F4B2A4F3CA |  | R22 | Non-TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.4%
Chowchilla | CA | 93610-3042 |  | 2013-06-14 | 2013-06-14 13:30 | 2013-06-14 13:30 | BRYANT - 583ANW03606AAAF | 81 | 0 | Yes | Yes | 19.1 | 20.2 | -1.1 | 7181D6BE708D4183A1C694984907BA81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-3822 |  | 2013-08-23 | 2013-08-23 11:33 | 2013-08-23 11:55 | BDP - 585ENW024050 | 54 | 3.6 | Yes | Yes | 24.1 | 18.4 | 5.7 | 9B37204BD4E442228C745C10D0DDC393 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Willows | CA | 95988-3544 |  | 2013-09-09 | 2013-09-09 13:43 | 2013-09-09 19:00 | RHEEM - NA | 59 | 3.8 | Yes | Yes | 16.6 | 19.3 | -2.7 | 66483DE7DDA248CC8DC64C70CD3EF01F |  | R22 | Non-TXV |  | 6.441% | 0.93559 | 12.38% | [5 empty] | Non-TXV | 6.441%
Yuba City | CA | 95993-5906 |  | 2013-09-06 | 2013-09-06 09:21 | 2013-09-06 09:58 | BRYANT - 563CN048-H | 133 | 4.1 | Yes | Yes | 22 | 19.3 | 2.7 | 6503383786C54D27BCDCCAAFEBECF349 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.924% | [5 empty] | Non-TXV | 3.083%
Sonora | CA | 95370-9310 |  | 2013-08-27 | 2013-08-27 10:07 | 2013-08-27 10:26 | YORK - ACP048G1101021C | 92 | 3.8 | Yes | Yes | 22.8 | 21.1 | 1.7 | 5AA22D846473461CB4E2B2664DFD768B |  | R22 | Non-TXV |  | 4.13% | 0.9587 | 7.938% | [5 empty] | Non-TXV | 4.13%
Antelope | CA | 95843-5030 |  | 2013-10-24 | 2013-10-24 18:57 | 2013-10-24 19:18 | GOODMAN - CM30-1EB | 67 | 4.8 | Yes | Yes | 17 | 19.9 | -2.9 | AF37BA55E5FA4795AF7D50B580501045 |  | R22 | Non-TXV |  | 7.164% | 0.92836 | 13.77% | [5 empty] | Non-TXV | 7.164%
Granite Bay | CA | 95746-6517 |  | 2013-10-01 | 2013-10-01 17:09 | 2013-10-01 17:09 | BRYANT - 165ANA036-B | 160 | 0 | Yes | Yes | 17.6 | 20.2 | -2.6 | B796FDB2C17C410AB661A3769605D9CD | Actual Subcooling cannot be negative. Please check entries. Evaporator saturation temperature is <25°F. Please check entries. | R410A | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4815 |  | 2013-05-31 | 2013-05-31 12:24 | 2013-05-31 12:27 | OTHER - RRPLB048JK10X | 161 | 6.1 | Yes | Yes | 26.3 | 21.7 | 4.6 | E0A3DFA7F24741AFBFCA79FC3867AF02 |  | R410A | Non-TXV |  | 3.789% | 0.96211 | 7.281% | [5 empty] | Non-TXV | 3.789%
Stockton | CA | 95206-6515 |  | 2013-07-02 | 2013-07-02 10:24 | 2013-07-02 10:45 | YORK - H3RA360S06A | 82 | 5 | Yes | Yes | 23.9 | 18.1 | 5.8 | 3AB03619496E4E4390B0FAC8717DC399 |  | R22 | Non-TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | Non-TXV | 6.098%
Stockton | CA | 95204-3909 |  | 2013-07-09 | 2013-07-09 13:31 | 2013-07-09 13:49 | LENNOX - GCS29X-030-752PA | 51 | 3.6 | Yes | Yes | 21.2 | 18.6 | 2.7 | A99183B6F603418EAA7740F95D242935 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Stockton | CA | 95206-5657 |  | 2013-06-26 | 2013-06-26 11:55 | 2013-06-26 12:20 | CARRIER - 38TDA036300 | 261 | 12.9 | Yes | Yes | 21.3 | 16.4 | 4.9 | AE76B8D2E94040D496D5BD6B188D48FD |  | R22 | Non-TXV |  | 4.943% | 0.95057 | 9.498% | [5 empty] | Non-TXV | 4.943%
Los Banos | CA | 93635-5143 |  | 2013-06-03 | 2013-06-03 11:36 | 2013-06-03 11:44 | BDP - 563CN036 | 122 | 5.7 | Yes | Yes | 18.6 | 20.3 | -1.7 | CBBD3D9E50C54D279C54BD6F23F20B3C |  | R22 | TXV |  | 4.672% | 0.95328 | 8.979% | [5 empty] | TXV | 4.672%
Stockton | CA | 95203-3237 |  | 2013-07-25 | 2013-07-25 11:30 | 2013-07-25 12:19 | RHEEM - RRKA-A030JK08X | 54 | 2.7 | Yes | Yes | 21.4 | 20.8 | 0.6 | 794C9F789A85444A9D0D2DEA924E1CC8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95219-3587 |  | 2013-07-24 | 2013-07-24 13:46 | 2013-07-24 14:10 | RUUD - UAKA-024JAZ | 50 | 1.8 | Yes | Yes | 17.4 | 19.7 | -2.3 | FA5E848FF7444575A63B4F5D4429A580 |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Chico | CA | 95926-8027 |  | 2013-09-25 | 2013-09-25 09:35 | 2013-09-25 09:52 | OTHER - CA5536VKD2 | 82 | 2.4 | Yes | Yes | 25 | 20.1 | 4.9 | 9552D672AA154CF790C71D9F4BBF8EA8 |  | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Thornton | CA | 95686-0000 |  | 2013-09-25 | 2013-09-25 11:26 | 2013-09-25 11:43 | RHEEM - UNK | 71 | 7.8 | Yes | Yes | 20.9 | 19.5 | 1.4 | 34961721B91A48A8865A8204FC489023 |  | R22 | Non-TXV |  | 10.99% | 0.89014 | 21.11% | [5 empty] | Non-TXV | 10.99%
Stockton | CA | 95206-5552 |  | 2013-06-26 | 2013-06-26 13:57 | 2013-06-26 14:23 | CARRIER - CAC460GKC4 | 85 | 5.3 | Yes | Yes | 23.8 | 18 | 5.8 | FD3C4FDF055C4B0F9C01B45C3E9C2E48 |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Stockton | CA | 95219-3592 |  | 2013-07-26 | 2013-07-26 14:47 | 2013-07-26 15:16 | CARRIER - UNK | 55 | 2.3 | Yes | Yes | 19.4 | 20.1 | -0.7 | C61D9A00B92C4986AED4B42C0F4BFD45 |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
Atwater | CA | 95301-3314 |  | 2013-06-14 | 2013-06-14 10:19 | 2013-06-14 10:19 | DAY & NIGHT - UNK | 78 | 0 | Yes | Yes | 17.8 | 20.4 | -2.6 | 5D80C16F5F82411EADE6DC34340E3259 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-4400 |  | 2013-07-19 | 2013-07-19 12:11 | 2013-07-19 12:33 | BRYANT - 561CJ036-E | 70 | 4.8 | Yes | Yes | 19.5 | 18.7 | 0.8 | 4A65405EBA3A4B398360AF128492B9A2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.857% | 0.93143 | 13.18% | [5 empty] | Non-TXV | 6.857%
Lathrop | CA | 95330-0000 |  | 2013-08-02 | 2013-08-02 11:33 | 2013-08-02 11:52 | RHEEM - RRNL-B030JK06X | 76 | 2.5 | Yes | Yes | 17.3 | 19.3 | -2 | 4F2838256AE142C5A1C412785EE6D1F9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Chico | CA | 95926-8003 |  | 2013-08-28 | 2013-08-28 16:22 | 2013-08-28 16:47 | BDP - 565BJ024 | 70 | 2.4 | Yes | Yes | 24.7 | 20.2 | 4.6 | AFB61F657B4F40E98DB17F96F1DDF97C |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Stockton | CA | 95206-6401 |  | 2013-07-02 | 2013-07-02 08:34 | 2013-07-02 08:34 | GOODMAN - CLJ60-1 | 85 | 0 | Yes | Yes | 19.2 | 17.9 | 1.3 | 8EF623B0096942009756EFDE5C511298 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2009 |  | 2013-08-28 | 2013-08-28 13:26 | 2013-08-28 13:57 | YORK - H1RAO42S06D | 84 | 2.5 | Yes | Yes | 18.5 | 20.7 | -2.2 | 314CDEAFB8BC41E3987B37E877EBFFE3 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Stockton | CA | 95206-6041 |  | 2013-06-27 | 2013-06-27 15:10 | 2013-06-27 15:10 | AMERICAN STANDARD - 2A7B0048A1000AA | 109 | 0 | Yes | Yes | 21.6 | 17.7 | 3.9 | 21BF7AD389CC491A85977DB532738733 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-9652 |  | 2013-06-14 | 2013-06-14 10:27 | 2013-06-15 02:45 | YORK - 94350B 3 | 85 | -5 | Yes | Yes | 15.7 | 17.7 | -2 | D699C1FC18E04D7D808DF0C222F34E52 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95206-6026 |  | 2013-06-27 | 2013-06-27 13:42 | 2013-06-27 14:10 | GOODMAN - CKJ30-1A | 85 | -5 | Yes | Yes | 20.4 | 21.3 | -0.9 | BEA4FE0260E14E48B2CCA18095409022 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95219-3587 |  | 2013-07-26 | 2013-07-26 14:00 | 2013-07-26 14:24 | CARRIER - TCGD24S41S1A | 61 | 2.7 | Yes | Yes | 16.1 | 17.9 | -1.8 | 77B4A50DBC6D45A291BA3E20FCBACD46 |  | R410A | Non-TXV |  | 4.426% | 0.95574 | 8.506% | [5 empty] | Non-TXV | 4.426%
Stockton | CA | 95210-4311 |  | 2013-08-16 | 2013-08-16 13:18 | 2013-08-16 13:37 | OTHER - AC024M1021A | 52 | 7.2 | Yes | Yes | 18.2 | 19.7 | -1.5 | A7462FDE9E1746D8A2EE6A3B4FAF05D6 |  | R22 | Non-TXV |  | 13.85% | 0.86154 | 26.61% | [5 empty] | Non-TXV | 13.85%
Tracy | CA | 95376-1812 |  | 2013-09-10 | 2013-09-10 11:35 | 2013-09-10 12:02 | BRYANT - 63CN036-C | 101 | 7.7 | Yes | Yes | 23.3 | 18.7 | 4.6 | 2EBB6EEE45184762A61B67B64A7A5735 |  | R22 | Non-TXV |  | 7.624% | 0.92376 | 14.65% | [5 empty] | Non-TXV | 7.624%
Tracy | CA | 95376-1812 |  | 2013-09-10 | 2013-09-10 12:04 | 2013-09-10 12:22 | BRYANT - 582ANW042090AAAG | 100 | 3 | Yes | Yes | 23.3 | 20.2 | 3.2 | 794D70868E03420A8C324F7469130E4B |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95928-4930 |  | 2013-09-25 | 2013-09-25 15:21 | 2013-09-25 15:44 | PAYNE - 585EJ034050 | 54 | 2.1 | Yes | Yes | 26.5 | 20.7 | 5.8 | 972BD60CEB8F44748D5241AF97532583 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Tracy | CA | 95376-2344 |  | 2013-07-23 | 2013-07-23 10:28 | 2013-07-23 10:48 | OTHER - 2SCU13LB142P-2 | 102 | 3.1 | Yes | Yes | 20 | 18.6 | 1.4 | 0E74D3EF61754EAFA46CCC28310AD13D |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Chico | CA | 95928-6471 |  | 2013-08-27 | 2013-08-27 13:10 | 2013-08-27 13:30 | BDP - 585CJ02450 | 72 | 2.5 | Yes | Yes | 23.3 | 19.2 | 4.1 | E91ACF3D685B4BC8BFBB2EE47D2B2C07 |  | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Paradise | CA | 95969-4614 |  | 2013-10-24 | 2013-10-24 15:52 | 2013-10-24 16:18 | YORK - H1RA024S06D | 59 | 5.6 | Yes | Yes | 17.5 | 20.4 | -2.9 | 1E961F274AA3480FB93462193340595D |  | R22 | Non-TXV |  | 9.492% | 0.90508 | 18.24% | [5 empty] | Non-TXV | 9.492%
Stockton | CA | 95209-4224 |  | 2013-07-15 | 2013-07-15 10:58 | 2013-07-15 11:19 | YORK - H3RC060S06HA | 144 | 16.6 | Yes | Yes | 23.4 | 17.9 | 5.5 | 1263ABD46F6645058BFE80E03D3717FC |  | R22 | Non-TXV |  | 11.53% | 0.88472 | 22.15% | [5 empty] | Non-TXV | 11.53%
Chowchilla | CA | 93610-8997 |  | 2013-08-22 | 2013-08-22 12:15 | 2013-08-22 12:15 | AIRE-FLO - GCGD300S212B | 51 | 0 | Yes | Yes | 18.5 | 21 | -2.5 | 4E20B2B8400B434FB8D7CA8DBEAC22D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4315 |  | 2013-07-09 | 2013-07-09 14:09 | 2013-07-09 14:27 | LENNOX - LCS13DC-024-230-01 | 67 | -3.9 | Yes | Yes | 20.9 | 19 | 1.9 | FC420DCDE7AB48CC84D1BDA0A59751AA |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Stockton | CA | 95203-1229 |  | 2013-07-23 | 2013-07-23 09:25 | 2013-07-23 09:43 | RUUD - UAKB-024JAZ | 56 | 3.8 | Yes | Yes | 22.6 | 19.1 | 3.5 | 3275B6B208D248EA99F67BEF0DACA539 |  | R22 | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Rocklin | CA | 95677-2856 |  | 2013-07-20 | 2013-07-20 09:23 | 2013-07-20 09:42 | - FADC-030JAS | 70 | 2.6 | Yes | Yes | 20 | 20.4 | -0.4 | A169FF2FE46246E3A7B39E5700932EDB |  | R22 | TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | TXV | 3.714%
Grass Valley | CA | 95949-6512 |  | 2013-06-29 | 2013-06-29 14:38 | 2013-06-29 14:38 | CARRIER - 38TXA042330 | 140 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | CF859A60ED694B388415575460763EB2 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-3611 |  | 2013-07-16 | 2013-07-16 15:27 | 2013-07-16 15:45 | GOODMAN - CLJ36-1 | 90 | 8.3 | Yes | Yes | 20.1 | 19.7 | 0.4 | 967828A9FE85414F882B5C667E3E7E03 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.222% | 0.90778 | 17.72% | [5 empty] | Non-TXV | 9.222%
Stockton | CA | 95209-3611 |  | 2013-07-16 | 2013-07-16 15:52 | 2013-07-16 16:11 | GOODMAN - CLJ36-1 | 90 | 18 | Yes | Yes | 20.9 | 19.6 | 1.3 | 04FBA05FA88041FF8B65B82B75EFA0C7 |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Paso Robles | CA | 93446-3965 |  | 2013-08-06 | 2013-08-06 13:17 | 2013-08-06 13:34 | HEIL - CA3048VKA1 | 145 | -8.5 | Yes | Yes | 24.4 | 20.2 | 4.3 | 29954EF3C40E4A3096C11DF8BFC6003B |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Stockton | CA | 95210-3133 |  | 2013-07-03 | 2013-07-03 09:55 | 2013-07-03 10:12 | HEIL - CA5530VKD2 | 74 | -5.2 | Yes | Yes | 18.9 | 18.6 | 0.3 | FCF9A4BEEC1746D78447EBC646B1EBC8 |  | R22 | Non-TXV |  | -7.027% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.027%
Chowchilla | CA | 93610-9772 |  | 2013-08-21 | 2013-08-21 09:54 | 2013-08-21 15:14 | RHEEM - RRNA-B036JK06X | 83 | -4.9 | Yes | Yes | 21.7 | 18.5 | 3.2 | C6BA9CCE30294A068AD45AEB07A7827A |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Rocklin | CA | 95765-5384 |  | 2013-08-10 | 2013-08-10 08:39 | 2013-08-10 09:44 | GIBSON - JS5RD-030KA | 99 | 3 | Yes | Yes | 21.5 | 19.8 | 1.7 | 7D352E5F70594EE984B3D2FDADDCC952 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Chico | CA | 95926-3537 |  | 2013-07-02 | 2013-07-02 18:49 | 2013-07-02 19:16 | MAYTAG - PPG1GC036K072X | 78 | 6.2 | Yes | Yes | 25.5 | 23.7 | 1.9 | EACA5308DF26491BA03B0384DF4DDF1B |  | R22 | Non-TXV |  | 7.949% | 0.92051 | 15.28% | [5 empty] | Non-TXV | 7.949%
Auburn | CA | 95602-8267 |  | 2013-07-13 | 2013-07-13 09:31 | 2013-07-13 09:31 | OTHER - HP030X1321B | 137 | 0 | Yes | Yes | 18 | 19.1 | -1.1 | 5FEA9EEFB41C426CB68C9D0F6BEDC36F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-9211 |  | 2013-06-11 | 2013-06-11 09:17 | 2013-06-11 09:23 | TRANE - 2YCC3042A1075AA | 131 | 8.9 | Yes | Yes | 17.9 | 18.8 | -0.9 | 6C2720785D7D4BAA990766A0504945C5 |  | R22 | Non-TXV |  | 6.794% | 0.93206 | 13.06% | [5 empty] | Non-TXV | 6.794%
Williams | CA | 95987-9011 |  | 2013-08-03 | 2013-08-03 13:09 | 2013-08-03 13:28 | GIBSON - JS3BA-024KA | 64 | 2 | Yes | Yes | 17 | 19.9 | -2.9 | F1D29E0E29A94F8DA9A06CAFB2522CAD |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Chico | CA | 95926-2669 |  | 2013-07-31 | 2013-07-31 14:33 | 2013-07-31 14:59 | RUUD - N4H330AKE100 | 100 | 6.2 | Yes | Yes | 18 | 19.2 | -1.2 | 6B6F1C8793304967BF9B1C9BA1DB7D3E |  | R410A | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Chico | CA | 95926-1822 |  | 2013-08-05 | 2013-08-05 12:00 | 2013-08-05 12:28 | ICP - N2H324AKA300 | 96 | 10.3 | Yes | Yes | 20.6 | 19.3 | 1.3 | B409D9C2DC1844E68004815AD9527554 |  | R22 | TXV |  | 10.73% | 0.89271 | 20.62% | [5 empty] | TXV | 10.73%
Stockton | CA | 95207-2317 |  | 2013-08-20 | 2013-08-20 10:30 | 2013-08-20 10:30 | GOODMAN - GPG13240451CB | 74 | 0 | Yes | Yes | 17.4 | 17.2 | 0.2 | D762E54F49B64230AA6E997DDDC755BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6041 |  | 2013-07-30 | 2013-07-30 11:56 | 2013-07-30 12:15 | UNK - UNK | 85 | -8 | Yes | Yes | 24.8 | 19.7 | 5.1 | C578CC51694C49429A11AC926DB9FA4D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. |  |  |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | 0 |  |  | -9.412%
Tuolumne | CA | 95379-9679 |  | 2013-09-12 | 2013-09-12 11:47 | 2013-09-12 12:15 | BRYANT - 113RNA042-B | 127 | 5.6 | Yes | Yes | 20.2 | 19.3 | 0.9 | CD8800854F8F44008445C03DD601BE5D |  | R22 | TXV |  | 4.409% | 0.95591 | 8.474% | [5 empty] | TXV | 4.409%
Dinuba | CA | 93618-3171 |  | 2013-06-26 | 2013-06-26 15:36 | 2013-06-26 15:55 | ICP - NAC042AKC3 | 112 | 3.4 | Yes | Yes | 16.5 | 19.3 | -2.8 | EDDD7B528B8B435D95AFCD5E5D3B21D5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Stockton | CA | 95206-6041 |  | 2013-08-13 | 2013-08-13 13:24 | 2013-08-13 13:42 | RUUD - UNK | 96 | 6.9 | Yes | Yes | 23.1 | 19.9 | 3.2 | D563DF5079A7497DB9565BDDDBA5E0FF |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Dinuba | CA | 93618-3161 |  | 2013-07-25 | 2013-07-25 18:13 | 2013-07-25 19:05 | ICP - CA5548VKA1 | 139 | 8 | Yes | Yes | 21.3 | 20.6 | 0.7 | 678C914130B14798A884A008C570DD9E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.755% | 0.94245 | 11.06% | [5 empty] | Non-TXV | 5.755%
Stockton | CA | 95207-7784 |  | 2013-06-26 | 2013-06-26 13:02 | 2013-06-26 13:02 | PAYNE - PY1PNB024060AAAA | 53 | 0 | Yes | Yes | 16.6 | 17.1 | -0.5 | CC2734B21E494774B5AEA55643349B43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-4535 |  | 2013-07-15 | 2013-07-15 09:45 | 2013-07-15 10:02 | CARRIER - 38CKC030340 | 69 | 3.4 | Yes | Yes | 19.9 | 17.5 | 2.4 | C863B43DB3164FC88956D9164AE988CD |  | R22 | Non-TXV |  | 4.928% | 0.95072 | 9.47% | [5 empty] | Non-TXV | 4.928%
Chico | CA | 95926-1933 |  | 2013-08-01 | 2013-08-01 13:18 | 2013-08-01 13:38 | TEMPSTAR - TCA024AKA1 | 69 | 5.3 | Yes | Yes | 20.5 | 19.3 | 1.2 | CAFA104E340B4A599FB2D19FE0C700DE |  | R22 | Non-TXV |  | 7.681% | 0.92319 | 14.76% | [5 empty] | Non-TXV | 7.681%
Stockton | CA | 95215-9776 |  | 2013-07-02 | 2013-07-02 13:06 | 2013-07-02 13:36 | GOODMAN - GSC140481E | 183 | -17.2 | Yes | Yes | 16.4 | 15 | 1.4 | 8B555292754F421C89623B0F43DF2E8E |  | R22 | Non-TXV |  | -9.399% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.399%
Stockton | CA | 95204-3345 |  | 2013-07-01 | 2013-07-01 08:40 | 2013-07-01 08:40 | GMC - VSX130241AA | 76 | 0 | Yes | Yes | 20.7 | 17 | 3.7 | 758F61A22C844CFA9945DFE9CF4C0920 |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95340-0946 |  | 2013-07-09 | 2013-07-09 11:17 | 2013-07-09 11:19 | GOODMAN - GPG1348090M41AC | 125 | 3.8 | Yes | Yes | 24.8 | 19.5 | 5.3 | 7E8FE65704464850A9C24C43C4EE0CE2 |  | R410A | Non-TXV |  | 3.04% | 0.9696 | 5.842% | [5 empty] | Non-TXV | 3.04%
Stockton | CA | 95206-6401 |  | 2013-07-11 | 2013-07-11 14:05 | 2013-07-11 14:27 | GOODMAN - CLJ48-1A | 130 | 4.4 | Yes | Yes | 22.3 | 18.9 | 3.4 | AF92132A8D0A4A82857FC6418DE56A6B |  | R22 | Non-TXV |  | 3.385% | 0.96615 | 6.504% | [5 empty] | Non-TXV | 3.385%
Stockton | CA | 95210-2051 |  | 2013-07-01 | 2013-07-01 10:22 | 2013-07-01 10:39 | BDP - 585A030080YAC | 50 | -4.1 | Yes | Yes | 19.1 | 16.2 | 3 | 0B2CCA8261D540E9B39FFE83A7597C2B |  | R22 | Non-TXV |  | -8.2% | 1.082 | 2.296% |  |  |  |  | Non-TXV |  |  | -8.2%
Manteca | CA | 95337-6013 |  | 2013-07-16 | 2013-07-16 15:02 | 2013-07-16 15:26 | OTHER - 80JR30E1 | 54 | 1.9 | Yes | Yes | 20.1 | 19.5 | 0.6 | 3B1ECCFDEB914F769AE0E5ACA8F819B5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Manteca | CA | 95337-8588 |  | 2013-08-26 | 2013-08-26 09:52 | 2013-08-26 10:12 | BRYANT - 563CN042-E | 104 | 3.9 | Yes | Yes | 23.6 | 19.9 | 3.7 | 6326028F25F64E58A64FF42D026599F0 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95210-2133 |  | 2013-07-01 | 2013-07-01 12:04 | 2013-07-01 12:20 | GOODMAN - GSC130241DA | 83 | -4.9 | Yes | Yes | 17.9 | 17 | 0.9 | 4647090D23FB47C688D26265306A6081 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Corning | CA | 96021-8646 |  | 2013-07-23 | 2013-07-23 08:45 | 2013-07-23 09:25 | YORK - H1DB036S06B | 72 | 3.3 | Yes | Yes | 19.8 | 19.1 | 0.7 | 0DB4CF5D200542C890CB57E24BE32967 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Corning | CA | 96021-3601 |  | 2013-07-23 | 2013-07-23 13:23 | 2013-07-23 13:43 | ALLEGIANCE - 2A7A2036A1000AA | 96 | 2.9 | Yes | Yes | 24 | 20.5 | 3.6 | 053FE2E88D7144BE9548377CC6E613A8 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Stockton | CA | 95206-5665 |  | 2013-06-27 | 2013-06-27 12:11 | 2013-06-27 12:37 | CARRIER - 38TDA036300 | 264 | 9.6 | Yes | Yes | 18.6 | 17.5 | 1.1 | 6DF87D5C0E42431D8C275195AEAA167D |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Soulsbyville | CA | 95372-0000 |  | 2013-09-12 | 2013-09-12 08:57 | 2013-09-12 09:23 | AIRE-FLO - ARAIR12B60 | 136 | 9 | Yes | Yes | 24 | 19.1 | 4.9 | 87D0456151194F1796BA838E61784F94 |  | R22 | Non-TXV |  | 6.618% | 0.93382 | 12.72% | [5 empty] | Non-TXV | 6.618%
Williams | CA | 95987-0000 |  | 2013-09-12 | 2013-09-12 12:07 | 2013-09-12 12:07 | OTHER - 597BN048-A | 165 | 0 | Yes | Yes | 24 | 19.3 | 4.7 | 93387FDE8B624A9AAEF3E84F6D86B796 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-0850 |  | 2013-07-12 | 2013-07-12 13:10 | 2013-07-12 19:12 | CARRIER - UNK | 81 | 3.4 | Yes | Yes | 19.3 | 21.2 | -1.9 | 342943969C594DDB8FA3D05847B4B0EE |  | R22 | Non-TXV |  | 4.198% | 0.95802 | 8.067% | [5 empty] | Non-TXV | 4.198%
Stockton | CA | 95205-7778 |  | 2013-08-14 | 2013-08-14 08:28 | 2013-08-14 08:46 | BRYANT - 561CJ042-F | 93 | 12.7 | Yes | Yes | 24.1 | 20.4 | 3.7 | B9A763FA896A4B8892E1A9F04D9F5AC3 |  | R22 | Non-TXV |  | 13.66% | 0.86344 | 26.24% | [5 empty] | Non-TXV | 13.66%
Madera | CA | 93638-1577 |  | 2013-07-15 | 2013-07-15 10:49 | 2013-07-15 11:09 | YORK - D1NZ030N05606A | 116 | 5.4 | Yes | Yes | 22.4 | 20.1 | 2.3 | 560CD0E097534CD2A3E35670AE247940 |  | R410A | Non-TXV |  | 4.655% | 0.95345 | 8.946% | [5 empty] | Non-TXV | 4.655%
Merced | CA | 95341-6575 |  | 2013-06-08 | 2013-06-08 09:07 | 2013-06-08 09:09 | DAY & NIGHT - 77777UNK | 80 | 2.5 | Yes | Yes | 17.7 | 17.6 | 0.1 | EB850A3CDCD7401993E05A939327D6CF |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Tracy | CA | 95376-2620 |  | 2013-07-23 | 2013-07-23 12:51 | 2013-07-23 13:15 | DAY & NIGHT - CBD | 64 | 1.9 | Yes | Yes | 16.5 | 19.2 | -2.7 | E347B330EC1945519ABC94CAABA54961 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Chowchilla | CA | 93610-2022 |  | 2013-06-02 | 2013-06-02 11:46 | 2013-06-02 11:46 | BDP - 585HJJWO036060 | 102 | 0 | Yes | Yes | 19.6 | 20.4 | -0.8 | 1FB2040655D64A79A66F20A461C5FFF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5380 |  | 2013-07-27 | 2013-07-27 01:57 | 2013-07-27 02:28 | RHEEM - UNK | 68 | -6.4 | Yes | Yes | 18.6 | 20.4 | -1.8 | EFCC3297EF264DCEACCB23185F2B34FE |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Merced | CA | 95341-6757 |  | 2013-08-06 | 2013-08-06 12:30 | 2013-08-06 12:56 | DAY & NIGHT - 588ANW024040ABAD | 40 | 1.9 | Yes | Yes | 20.8 | 20.4 | 0.4 | 10293994C3CA46998C285F2D0F54CE4B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.75% | 0.9525 | 9.128% | [5 empty] | Non-TXV | 4.75%
Chico | CA | 95926-2817 |  | 2013-07-31 | 2013-07-31 13:46 | 2013-07-31 14:03 | OTHER - UNK | 85 | 9 | Yes | Yes | 19.9 | 21 | -1.1 | DC09A23C4D1544FB9BF9B5C22190B702 |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Chico | CA | 95973-8348 |  | 2013-07-11 | 2013-07-11 20:01 | 2013-07-11 20:18 | LENNOX - HS22-311V-3P | 129 | 15.2 | Yes | Yes | 20.9 | 17.5 | 3.4 | ED0247A13050436DBD11912812C30683 |  | R22 | Non-TXV |  | 11.78% | 0.88217 | 22.64% | [5 empty] | Non-TXV | 11.78%
Chico | CA | 95973-4952 |  | 2013-08-08 | 2013-08-08 11:59 | 2013-08-08 12:31 | LENNOX - 12ACB36-4P | 103 | 17.2 | Yes | Yes | 16.6 | 19.3 | -2.7 | 4A311D4A98B243ADA6A479F18F6319CD |  | R22 | Non-TXV |  | 16.7% | 0.83301 | 32.09% | [5 empty] | Non-TXV | 16.7%
Chico | CA | 95926-4766 |  | 2013-08-23 | 2013-08-23 15:35 | 2013-08-23 18:23 | PAYNE - 585CJW024050ARAE | 54 | 2.4 | Yes | Yes | 22.2 | 20.2 | 2.1 | 6EB10639981A42CF9AE54DD4AE4B3C95 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Corning | CA | 96021-0000 |  | 2013-10-25 | 2013-10-25 15:09 | 2013-10-25 15:25 | ARMSTRONG - NA | 75 | 2.3 | Yes | Yes | 23.2 | 20.7 | 2.6 | 1638129D2DA64765BB0E6EC7CBD1B137 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Lathrop | CA | 95330-9717 |  | 2013-07-03 | 2013-07-03 08:53 | 2013-07-03 09:15 | BRYANT - 561CJ036-E | 70 | 2.2 | Yes | Yes | 23.7 | 19.5 | 4.2 | 53561878B27D480EBAE43DC4F67423D7 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Fresno | CA | 93710-4842 |  | 2013-06-27 | 2013-06-27 12:29 | 2013-06-27 12:35 | PAYNE - 42RAC1SAKC | 85 | 3.7 | Yes | Yes | 17 | 16.8 | 0.2 | EBF22CDAA63045C583097F1A6F58A86C |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Stockton | CA | 95209-2164 |  | 2013-07-11 | 2013-07-11 08:23 | 2013-07-11 08:42 | PAYNE - UNK | 52 | 6.1 | Yes | Yes | 16.4 | 18 | -1.6 | D680646A51CF4373ACE9451D19F75E7B |  | R22 | Non-TXV |  | 11.73% | 0.88269 | 22.54% | [5 empty] | Non-TXV | 11.73%
Jamestown | CA | 95327-9729 |  | 2013-08-01 | 2013-08-01 08:20 | 2013-08-01 08:39 | UNITARY PRODUCTS GROUP - H1RA036506A | 85 | 18.5 | Yes | Yes | 26.2 | 20.4 | 5.8 | 94F92D6B60EE44A18FBDB90EE12B52D5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.76% | 0.78235 | 41.83% | [5 empty] | Non-TXV | 21.76%
Manteca | CA | 95337-8582 |  | 2013-08-30 | 2013-08-30 12:59 | 2013-08-30 13:34 | BRYANT - 56CN048-F | 165 | 4.9 | Yes | Yes | 21.9 | 18.5 | 3.4 | 2B8D5BC5FB16413A8BBD01EAEB655B99 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.707% | [5 empty] | Non-TXV | 2.97%
Fresno | CA | 93722-7362 |  | 2013-07-18 | 2013-07-18 16:38 | 2013-07-18 16:40 | LENNOX - 13ACB06023001 | 214 | 18.6 | Yes | Yes | 19.9 | 21.4 | -1.5 | 40BBF9F4D63640A08D861FEF2FF773B3 |  | R22 | Non-TXV |  | 8.692% | 0.91308 | 16.7% | [5 empty] | Non-TXV | 8.692%
Chico | CA | 95926-8003 |  | 2013-09-27 | 2013-09-27 15:15 | 2013-09-27 15:38 | RHEEM - RAKA-024JAZ | 150 | 4.5 | Yes | Yes | 20 | 19.5 | 0.5 | E11AED97499647569BFE9ED6890705C7 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95210-2327 |  | 2013-07-08 | 2013-07-08 08:18 | 2013-07-08 08:36 | YORK - D3NP024N03606NXB | 100 | -7.1 | Yes | Yes | 20.5 | 19.4 | 1.1 | 908C6DA4756042CF87EE378FF4F92E52 |  | R22 | Non-TXV |  | -7.1% | 1.071 | 1.988% |  |  |  |  | Non-TXV |  |  | -7.1%
Fresno | CA | 93722-8643 |  | 2013-07-15 | 2013-07-15 13:33 | 2013-07-15 14:00 | LENNOX - HS290365P | 70 | 10.5 | Yes | Yes | 18.6 | 20.2 | -1.6 | 88E51412E6CA415B9F80E771F4B1B5BA |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Fresno | CA | 93722-4648 |  | 2013-07-16 | 2013-07-16 12:51 | 2013-07-16 12:52 | LENNOX - 12GCS036753PD | 110 | 13.2 | Yes | Yes | 24.3 | 22.1 | 2.2 | B92B54ED1F0F4B93917F7B2CBC33A309 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Stockton | CA | 95209-1881 |  | 2013-07-10 | 2013-07-10 11:44 | 2013-07-10 11:44 | BRYANT - 561CJ024-E | 55 | 0 | Yes | Yes | 18.5 | 17.8 | 0.8 | 4967638EA1D5468B8ECC9C6E935A8938 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-9106 |  | 2013-08-23 | 2013-08-23 08:46 | 2013-08-23 11:15 | LENNOX - 10GCS030X-75-3PA | 51 | 3.5 | Yes | Yes | 21.4 | 19.3 | 2.1 | DE995C68F787404DA510FB3F2C16EBD7 |  | R22 | TXV |  | 6.863% | 0.93137 | 13.19% | [5 empty] | TXV | 6.863%
Merced | CA | 95341-6762 |  | 2013-07-02 | 2013-07-02 10:06 | 2013-07-02 10:08 | DAY & NIGHT - 7777UNK | 72 | 2.3 | Yes | Yes | 19.1 | 18.1 | 1 | 0A95035D08D546FFB4C522F2711D9CFF |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Fresno | CA | 93722-9032 |  | 2013-07-18 | 2013-07-18 11:28 | 2013-07-18 11:29 | LENNOX - 12GCS042753PA | 133 | 15.5 | Yes | Yes | 22.2 | 19.3 | 2.9 | 5FE390A1DB2446C09FA72E6F5008F3DC |  | R22 | Non-TXV |  | 11.65% | 0.88346 | 22.4% | [5 empty] | Non-TXV | 11.65%
Fresno | CA | 93710-4816 |  | 2013-06-27 | 2013-06-27 11:19 | 2013-06-27 11:24 | GOODMAN - CKL-48-1L | 112 | 4.3 | Yes | Yes | 19.3 | 17.4 | 1.9 | 3D508620FBE44A7CAA783FB70BBACB31 |  | R22 | Non-TXV |  | 3.839% | 0.96161 | 7.378% | [5 empty] | Non-TXV | 3.839%
Paradise | CA | 95969-6163 |  | 2013-08-08 | 2013-08-08 14:57 | 2013-08-08 15:15 | PAYNE - PY1PNB060115AAA | 116 | 3.8 | Yes | Yes | 24.3 | 21.4 | 2.9 | E0B3E594446B4AE49C1E6C8DAFDCF75E |  | R22 | Non-TXV |  | 3.276% | 0.96724 | 6.295% | [5 empty] | Non-TXV | 3.276%
Manteca | CA | 95337-0000 |  | 2013-07-24 | 2013-07-24 10:51 | 2013-07-24 11:08 | BRYANT - 113RNA036-B | 88 | 6 | Yes | Yes | 23.6 | 20.4 | 3.2 | FE524122FBA44E948FA5E431B5EA143C |  | R22 | TXV |  | 6.818% | 0.93182 | 13.1% | [5 empty] | TXV | 6.818%
Fresno | CA | 93703-2716 |  | 2013-08-08 | 2013-08-08 09:51 | 2013-08-08 09:52 | YORK - D1NH036N07206C | 108 | 11.7 | Yes | Yes | 25.1 | 19.3 | 5.8 | F867070BB09B42DA8384F198A0A8A7DA |  | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Stockton | CA | 95205-7217 |  | 2013-07-15 | 2013-07-15 16:09 | 2013-07-15 16:40 | ICP - PGC042K080B | 87 | 6.3 | Yes | Yes | 19.9 | 20.4 | -0.5 | 20C78D6F53774B5DA19D05DBB2B27E71 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.241% | 0.92759 | 13.92% | [5 empty] | Non-TXV | 7.241%
Fresno | CA | 93710-4216 |  | 2013-08-12 | 2013-08-12 23:41 | 2013-08-13 00:24 | OTHER - PGAA36C1K1 | 77 | 2.6 | Yes | Yes | 21.9 | 21.8 | 0.1 | AD294A36A72846468E436143971F57FD |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Chico | CA | 95928-6377 |  | 2013-08-06 | 2013-08-06 11:27 | 2013-08-06 11:46 | YORK - K1CB024S06B | 71 | -6.7 | Yes | Yes | 16.5 | 17.4 | -0.9 | 5AB42A85069649589AB8987A08FEF69D |  | R22 | Non-TXV |  | -9.437% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.437%
Madera | CA | 93636-8243 |  | 2013-06-28 | 2013-06-28 15:30 | 2013-06-29 11:11 | RHEEM - UNK | 74 | 2.9 | Yes | Yes | 19.3 | 20.4 | -1.1 | 465A3A2722774637A69FA73F28162069 |  | R22 | Non-TXV |  | 3.919% | 0.96081 | 7.531% | [5 empty] | Non-TXV | 3.919%
Stockton | CA | 95205-7217 |  | 2013-07-23 | 2013-07-23 09:20 | 2013-07-23 09:38 | GOODMAN - GSC130361DE | 119 | -11.2 | Yes | Yes | 20.4 | 17.8 | 2.6 | DDE4394C2BCD4EF68026324CCC6C020B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93726-2219 |  | 2013-08-12 | 2013-08-12 13:40 | 2013-08-12 14:00 | RUUD - URMA-A036JK08E | 99 | 8 | Yes | Yes | 23.5 | 21.4 | 2.1 | 0197C8F04BED47358E59CE20BBB531EE |  | R22 | Non-TXV |  | 8.081% | 0.91919 | 15.53% | [5 empty] | Non-TXV | 8.081%
Fresno | CA | 93720-2792 |  | 2013-07-12 | 2013-07-12 19:35 | 2013-07-12 22:31 | OTHER - NRGF42DDB04 | 90 | 8 | Yes | Yes | 21.3 | 22.1 | -0.8 | 9D50C3BBE29F4D9AA82234F8525C61BC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Fresno | CA | 93720-3628 |  | 2013-09-20 | 2013-09-20 13:39 | 2013-09-20 13:41 | HEIL - NRGF36DDB04 | 98 | 3.9 | Yes | Yes | 18.8 | 17.6 | 1.2 | 8B0EB1449CE9469791996AB35C707ED8 |  | R22 | Non-TXV |  | 3.98% | 0.9602 | 7.648% | [5 empty] | Non-TXV | 3.98%
Stockton | CA | 95204-4966 |  | 2013-07-09 | 2013-07-09 11:15 | 2013-07-09 11:34 | RHEEM - PGAD30D1K3 | 78 | -7.3 | Yes | Yes | 14.9 | 16.1 | -1.2 | 78FC8576E718433E8F274861A471FE8B |  | R22 | Non-TXV |  | -9.359% | 1.0936 | 2.621% |  |  |  |  | Non-TXV |  |  | -9.359%
Fresno | CA | 93710-7126 |  | 2013-06-27 | 2013-06-27 14:28 | 2013-06-27 14:30 | DAY & NIGHT - 7777UNK | 100 | 3.1 | Yes | Yes | 17.7 | 17.4 | 0.3 | 0C3FD8A5B7824BB2B5B9D59B66F1FC1C |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Fresno | CA | 93703-1621 |  | 2013-07-03 | 2013-07-03 11:04 | 2013-07-03 11:29 | WESTINGHOUSE - ID036BBA | 66 | 6.3 | Yes | Yes | 16.4 | 18.5 | -2.1 | AD733D53ACC844418D12923528EC265F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Madera | CA | 93638-1538 |  | 2013-07-12 | 2013-07-12 15:23 | 2013-07-12 16:30 | CARRIER - 56540300B0YC | 197 | 6.3 | Yes | Yes | 18 | 20.4 | -2.4 | E22F9664FBE44E07AEA7BE1DFC9535DD |  | R22 | Non-TXV |  | 3.198% | 0.96802 | 6.146% | [5 empty] | Non-TXV | 3.198%
Sanger | CA | 93657-2139 |  | 2013-08-23 | 2013-08-23 14:12 | 2013-08-23 14:33 | BDP - 585HJW024040ABAE | 68 | 9.3 | Yes | Yes | 19 | 19.9 | -0.9 | 729E65BD9BA74184A4E9035E1EDA9491 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.68% | 0.86324 | 26.28% | [5 empty] | Non-TXV | 13.68%
Valley Springs | CA | 95252-9380 |  | 2013-07-16 | 2013-07-16 14:44 | 2013-07-16 15:11 | RUUD - URGF-05E30JKR | 46 | 4.7 | Yes | Yes | 22.9 | 21.4 | 1.5 | EB2224CFB4D644BF9113757CFEB70C0D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.22% | 0.89783 | 19.64% | [5 empty] | Non-TXV | 10.22%
Coalinga | CA | 93210-9797 |  | 2013-08-17 | 2013-08-17 22:22 | 2013-08-17 23:08 | OTHER - 563ANO052-A | 123 | 4.2 | Yes | Yes | 19.7 | 20.1 | -0.3 | E36EF716F5034485BABFCCE79E1321C0 |  | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Madera | CA | 93637-2757 |  | 2013-07-12 | 2013-07-12 03:28 | 2013-07-12 03:28 | YORK - UNK | 89 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 3404C782465A4F9299088EB275D6DF4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2560 |  | 2013-07-22 | 2013-07-22 13:18 | 2013-07-22 13:18 | RHEEM - RRPL-B036JK06X | 92 | 0 | Yes | Yes | 17.6 | 20.1 | -2.5 | 1A6B5AF0FEB34DDC82CCBDFF434D73CE | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-2592 |  | 2013-08-17 | 2013-08-17 15:23 | 2013-08-17 23:19 | GOODMAN - GB0340-1B | 50 | 2.5 | Yes | Yes | 20.1 | 20.7 | -0.6 | EA9928E8E654447A8960EFEA827B46F9 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93727-3716 |  | 2013-07-15 | 2013-07-15 12:40 | 2013-07-15 13:01 | AMERICAN STANDARD - 2YCC3036A1064AA | 82 | 3.3 | Yes | Yes | 20.5 | 20.4 | 0.1 | 02B01D4F1D794EF281C1695EDD9D0DE3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.024% | 0.95976 | 7.734% | [5 empty] | Non-TXV | 4.024%
Mariposa | CA | 95338-9363 |  | 2013-08-21 | 2013-08-21 11:57 | 2013-08-21 12:00 | RUUD - UNK | 56 | 8.5 | Yes | Yes | 27.8 | 23.7 | 4.1 | 030C468CC09C44C2A69CC89C87DA5F4D |  | R22 | Non-TXV |  | 15.18% | 0.84821 | 29.17% | [5 empty] | Non-TXV | 15.18%
Fresno | CA | 93710-4227 |  | 2013-08-10 | 2013-08-10 12:09 | 2013-08-10 21:19 | BDP - 588ANW03680AAAF | 68 | 5.8 | Yes | Yes | 19.4 | 19.8 | -0.4 | 9CAC2B4A18FE4097A879677D102DD86F |  | R22 | Non-TXV |  | 8.529% | 0.91471 | 16.39% | [5 empty] | Non-TXV | 8.529%
Fresno | CA | 93722-2239 |  | 2013-07-25 | 2013-07-25 13:40 | 2013-07-25 13:41 | OTHER - FADC060JAS | 112 | 17 | Yes | Yes | 22.5 | 21.7 | 0.8 | 58E99477B90B4618AEFE11E99203CD63 |  | R22 | Non-TXV |  | 15.18% | 0.84821 | 29.17% | [5 empty] | Non-TXV | 15.18%
Stockton | CA | 95209-5113 |  | 2013-07-15 | 2013-07-15 12:23 | 2013-07-15 12:45 | DAY & NIGHT - 565BJ036 | 84 | 4.7 | Yes | Yes | 17.3 | 18.1 | -0.8 | 3D4C5943B0D6474698AF88C3BF8B58FC |  | R22 | Non-TXV |  | 5.595% | 0.94405 | 10.75% | [5 empty] | Non-TXV | 5.595%
Fresno | CA | 93704-4826 |  | 2013-08-12 | 2013-08-12 10:26 | 2013-08-12 10:27 | RUUD - URKAA036JK08E | 62 | 7.5 | Yes | Yes | 20.6 | 18.8 | 1.8 | C6B3EF1959B24EF19655AD62F99B8392 |  | R22 | Non-TXV |  | 12.1% | 0.87903 | 23.25% | [5 empty] | Non-TXV | 12.1%
Stockton | CA | 95209-2655 |  | 2013-07-11 | 2013-07-11 12:18 | 2013-07-11 12:36 | RHEEM - AT-38B1F | 68 | 5.8 | Yes | Yes | 22.7 | 18.6 | 4.1 | 3B06BB5B3FCE4166B5DCD5038E96259B |  | R22 | Non-TXV |  | 8.529% | 0.91471 | 16.39% | [5 empty] | Non-TXV | 8.529%
Magalia | CA | 95954-9413 |  | 2013-07-19 | 2013-07-19 11:04 | 2013-07-19 11:35 | TEMPSTAR - NA | 72 | 10 | Yes | Yes | 19.7 | 19.6 | 0.2 | F2DD6188C3324EB9BFC53B6E1F720058 |  | R22 | Non-TXV |  | 13.89% | 0.86111 | 26.69% | [5 empty] | Non-TXV | 13.89%
Fresno | CA | 93722-8500 |  | 2013-07-16 | 2013-07-16 08:26 | 2013-07-16 08:27 | LENNOX - HS260366P | 87 | 7.1 | Yes | Yes | 20.8 | 17.4 | 3.4 | CF03AE124A3649C2AD15407C808FE63D |  | R22 | Non-TXV |  | 8.161% | 0.91839 | 15.68% | [5 empty] | Non-TXV | 8.161%
Fresno | CA | 93704-3860 |  | 2013-06-26 | 2013-06-26 12:38 | 2013-06-26 12:40 | YORK - D1NH036N05606C | 108 | 6.9 | Yes | Yes | 24.2 | 20.1 | 4.1 | 03C0F2A8281749848A51A5355FFB9516 |  | R22 | Non-TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | Non-TXV | 6.389%
Fresno | CA | 93710-4813 |  | 2013-07-19 | 2013-07-19 09:12 | 2013-07-19 09:29 | PAYNE - 42KAC168K | 87 | 9.4 | Yes | Yes | 18.7 | 18.6 | 0.1 | 5D473151E8094B2AB301B2A4AAADEB33 |  | R22 | Non-TXV |  | 10.8% | 0.89195 | 20.76% | [5 empty] | Non-TXV | 10.8%
Paradise | CA | 95969-3025 |  | 2013-06-28 | 2013-06-28 19:59 | 2013-06-28 20:18 | BDP - 588AVW030080ACBD | 53 | 9.1 | Yes | Yes | 19.1 | 19.8 | -0.7 | 3AEBD515B5B748E895EB21ACC8D236EC |  | R22 | Non-TXV |  | 17.17% | 0.8283 | 33% | [5 empty] | Non-TXV | 17.17%
Chowchilla | CA | 93610-8997 |  | 2013-08-22 | 2013-08-22 19:25 | 2013-08-22 21:11 | RUUD - UNK | 53 | 3.1 | Yes | Yes | 18.7 | 21.3 | -2.6 | 39DC67FCD14447D5AE9135F9FA7D17B7 |  | R22 | Non-TXV |  | 5.849% | 0.94151 | 11.24% | [5 empty] | Non-TXV | 5.849%
Tracy | CA | 95377-7229 |  | 2013-07-19 | 2013-07-19 15:07 | 2013-07-19 15:32 | CARRIER - 38EZG0042300 | 104 | 6.5 | Yes | Yes | 22.9 | 20 | 3 | C291041E9794404D976931F2E20A23D6 |  | R410A | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fresno | CA | 93704-6149 |  | 2013-08-09 | 2013-08-09 13:53 | 2013-08-09 13:54 | COLEMAN - AC5B048F1B | 226 | 17.7 | Yes | Yes | 19.5 | 20.9 | -1.4 | C9787FE10D4F491382D4FE79BB3F0D8D |  | R410A | Non-TXV |  | 7.832% | 0.92168 | 15.05% | [5 empty] | Non-TXV | 7.832%
Los Banos | CA | 93635-4522 |  | 2013-07-10 | 2013-07-10 08:18 | 2013-07-10 08:34 | BRYANT - 563CN030 | 98 | 12.2 | Yes | Yes | 26.9 | 21 | 5.9 | 44B5C4277D0346DE8BB2C33472829B49 |  | R22 | TXV |  | 12.45% | 0.87551 | 23.92% | [5 empty] | TXV | 12.45%
Stockton | CA | 95210-1644 |  | 2013-06-27 | 2013-06-27 09:20 | 2013-06-27 09:37 | PAYNE - 585A030080YAC | 50 | -3.5 | Yes | Yes | 21.2 | 16.6 | 4.6 | B054A186AA04475693FA9B0FAE46B4C0 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93705-0207 |  | 2013-07-08 | 2013-07-08 11:29 | 2013-07-08 11:48 | OTHER - 2A7B0030A1000AA | 64 | 9.2 | Yes | Yes | 22.1 | 21.2 | 1 | 4BA09C1091F14402BD7B47501CD98742 |  | R22 | Non-TXV |  | 14.37% | 0.85625 | 27.63% | [5 empty] | Non-TXV | 14.37%
Tracy | CA | 95377-2209 |  | 2013-07-23 | 2013-07-23 14:27 | 2013-07-23 14:51 | YORK - H4DE036S06A | 82 | 9.1 | Yes | Yes | 19 | 19.4 | -0.3 | F228BE5AC7B6431B9E249CB2D37DB083 |  | R22 | Non-TXV |  | 11.1% | 0.88902 | 21.33% | [5 empty] | Non-TXV | 11.1%
Stockton | CA | 95203-2318 |  | 2013-07-15 | 2013-07-15 14:28 | 2013-07-15 14:51 | BRYANT - 561CJ036-E | 70 | -4.1 | Yes | Yes | 25.9 | 20.8 | 5.1 | CA6E5F3E5A7942E2BF8F794C8C1F630D |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Fresno | CA | 93710-4743 |  | 2013-06-27 | 2013-06-27 10:18 | 2013-06-27 10:21 | PAYNE - 7777UNK | 100 | 4.6 | Yes | Yes | 19.1 | 18.3 | 0.9 | 2F05EBE81F1540458EADF3DFCCC78590 |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Orosi | CA | 93647-9407 |  | 2013-07-29 | 2013-07-29 13:35 | 2013-07-29 14:05 | ICP - PGC048K080D | 102 | 11 | Yes | Yes | 18.1 | 17.7 | 0.4 | 793CE67444AD4F62B3257DF3EE9FAD56 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.78% | 0.89216 | 20.73% | [5 empty] | Non-TXV | 10.78%
Fresno | CA | 93720-0251 |  | 2013-07-11 | 2013-07-11 16:11 | 2013-07-11 17:02 | YORK - H1GH036S06A | 127 | 4 | Yes | Yes | 24.1 | 20.4 | 3.7 | 48A71020EFBF4A3BA2ADE921D6E82ECE |  | R22 | Non-TXV |  | 3.15% | 0.9685 | 6.053% | [5 empty] | Non-TXV | 3.15%
Stockton | CA | 95209-2163 |  | 2013-07-22 | 2013-07-22 12:32 | 2013-07-22 12:49 | DAY & NIGHT - UNK | 51 | 2.2 | Yes | Yes | 20.3 | 18.6 | 1.8 | 74C1EFFEDAD84FBEA410F1748BB5B7E7 |  | R22 | Non-TXV |  | 4.314% | 0.95686 | 8.29% | [5 empty] | Non-TXV | 4.314%
Stockton | CA | 95210-5109 |  | 2013-07-11 | 2013-07-11 13:41 | 2013-07-11 14:00 | RUUD - UAFD-030JAS | 69 | -4.1 | Yes | Yes | 21.7 | 20.4 | 1.3 | B299E5E739D543D19AE2C98F606F6C7F |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Winton | CA | 95388-9302 |  | 2013-06-11 | 2013-06-11 10:43 | 2013-06-11 10:45 | CARRIER - 7777UNK | 68 | 4.7 | Yes | Yes | 25.2 | 19.3 | 5.9 | FCC943A0D2754864889AB4839271EF45 |  | R22 | Non-TXV |  | 6.912% | 0.93088 | 13.28% | [5 empty] | Non-TXV | 6.912%
Stockton | CA | 95215-5461 |  | 2013-06-28 | 2013-06-28 13:22 | 2013-06-28 13:47 | PAYNE - PY3PNA030060NA | 130 | 4.7 | Yes | Yes | 21.7 | 19 | 2.8 | 2FFB23585B9842D98AC76AE063F758F1 |  | R22 | Non-TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | Non-TXV | 3.615%
Chico | CA | 95928-8501 |  | 2013-08-02 | 2013-08-02 11:55 | 2013-08-02 12:13 | RHEEM - RAFD-031JAS | 64 | 2.2 | Yes | Yes | 17 | 19.1 | -2.1 | F11A6BFF79AD4CE5B7FC749512221159 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Fresno | CA | 93722-5481 |  | 2013-07-17 | 2013-07-17 08:57 | 2013-07-17 08:59 | CARRIER - 38CK036310 | 72 | 9.6 | Yes | Yes | 23.7 | 19.1 | 4.7 | 97F5E141F6084300BB7E1F50F66BA5AC |  | R22 | TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | TXV | 13.33%
Manteca | CA | 95337-5731 |  | 2013-07-19 | 2013-07-19 12:57 | 2013-07-19 13:31 | LENNOX - GCS16R-411-50-3P | 76 | 12.5 | Yes | Yes | 17.9 | 20.4 | -2.5 | BA9D44566D414B618D1AA4386953B83F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.45% | 0.83553 | 31.61% | [5 empty] | Non-TXV | 16.45%
Manteca | CA | 95337-5731 |  | 2013-07-19 | 2013-07-19 13:34 | 2013-07-19 13:56 | YORK - D5YS018N03206A | 52 | 3.4 | Yes | Yes | 21.4 | 20.4 | 1 | A1F32FEC17A74FD8B1342F1DFDC2F563 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Stockton | CA | 95205-3821 |  | 2013-07-17 | 2013-07-17 10:31 | 2013-07-17 10:53 | AMANA - GSX1303301AD | 76 | 5.8 | Yes | Yes | 18.5 | 17.7 | 0.8 | 8231E0953DD84BCEB5F2ED51AE0A6979 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
Orosi | CA | 93647-9407 |  | 2013-07-30 | 2013-07-30 17:28 | 2013-07-30 18:16 | GOODMAN - GPG13480901A | 90 | 2.9 | Yes | Yes | 16.6 | 19.4 | -2.8 | 955DCE262EC24AEEA320F816AD6E7B20 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Fresno | CA | 93722-3623 |  | 2013-08-10 | 2013-08-10 15:27 | 2013-08-10 15:29 | CARRIER - 7777UNK | 106 | 3.1 | Yes | Yes | 20.9 | 20.2 | 0.8 | D186E5668E904BBAA929716A9A6BD75B |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
Fresno | CA | 93710-4817 |  | 2013-06-27 | 2013-06-27 10:54 | 2013-06-27 10:57 | PAYNE - 7777UNK | 96 | 3.2 | Yes | Yes | 16.6 | 19.5 | -2.9 | 46C3AB9ED0854EBE8A409A20B57CB5DE |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Sanger | CA | 93657-2980 |  | 2013-07-22 | 2013-07-22 15:25 | 2013-07-22 16:10 | ICP - PGC042K080E | 84 | 2.9 | Yes | Yes | 22.3 | 19.2 | 3.1 | BBA0F9C977954126A87B661B9BAF0BEA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Stockton | CA | 95209-2133 |  | 2013-07-11 | 2013-07-11 08:55 | 2013-07-11 09:22 | FRESCHI - 60WE2461 | 55 | 6.8 | Yes | Yes | 17.5 | 17 | 0.5 | 38AE1B373A5D4CAB8EA06D0466D725CC |  | R22 | Non-TXV |  | 12.36% | 0.87636 | 23.76% | [5 empty] | Non-TXV | 12.36%
Corning | CA | 96021-9235 |  | 2013-07-24 | 2013-07-24 11:59 | 2013-07-24 13:45 | COLEMAN - 9632E60 | 114 | 7.4 | Yes | Yes | 18.2 | 20.4 | -2.2 | 02A04CE08F984404A485B5C0050FE416 |  | R22 | Non-TXV |  | 6.491% | 0.93509 | 12.47% | [5 empty] | Non-TXV | 6.491%
Winton | CA | 95388-9369 |  | 2013-06-11 | 2013-06-11 11:09 | 2013-06-11 11:11 | GOODMAN - GPG13360701AC | 112 | 5 | Yes | Yes | 23 | 17.5 | 5.5 | 3A066935BF6C45D5BD108613F8073A63 |  | R22 | Non-TXV |  | 4.464% | 0.95536 | 8.579% | [5 empty] | Non-TXV | 4.464%
Manteca | CA | 95336-3797 |  | 2013-07-10 | 2013-07-10 10:52 | 2013-07-10 11:16 | CARRIER - 585HJ018040 | 61 | 4.7 | Yes | Yes | 17.6 | 19.3 | -1.7 | D48F45D02892425DB9DF7889A7042A19 |  | R22 | Non-TXV |  | 7.705% | 0.92295 | 14.81% | [5 empty] | Non-TXV | 7.705%
Clovis | CA | 93612-1671 |  | 2013-06-28 | 2013-06-28 12:20 | 2013-06-28 12:38 | AMANA - RCE48C2A | 235 | 9.1 | Yes | Yes | 21.1 | 20.9 | 0.2 | 84577909130D47B195AD1E918FF19FD5 |  | R22 | Non-TXV |  | 3.872% | 0.96128 | 7.442% | [5 empty] | Non-TXV | 3.872%
Manteca | CA | 95336-3701 |  | 2013-07-09 | 2013-07-09 14:10 | 2013-07-09 14:31 | GOODMAN - GPG12300701A | 85 | 5.7 | Yes | Yes | 23.3 | 19.5 | 3.8 | B64BD5467BB44B97A68AE048B7282E51 |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Fresno | CA | 93704-1549 |  | 2013-07-25 | 2013-07-25 09:18 | 2013-07-25 09:19 | RHEEM - RAMB048JBZ | 162 | 23.2 | Yes | Yes | 21.8 | 21.3 | 0.5 | F81C1E0AD47D44319659A63045C0A5D7 |  | R22 | Non-TXV |  | 14.32% | 0.85679 | 27.52% | [5 empty] | Non-TXV | 14.32%
Stockton | CA | 95210-4226 |  | 2013-07-15 | 2013-07-15 13:54 | 2013-07-15 14:23 | TEMPSTAR - T2A32GKB200 | 82 | 3.3 | Yes | Yes | 20.1 | 19.3 | 0.8 | 4DAEE1E225584E11B84000A45A8EB041 |  | R22 | Non-TXV |  | 4.024% | 0.95976 | 7.734% | [5 empty] | Non-TXV | 4.024%
Tracy | CA | 95377-0223 |  | 2013-07-17 | 2013-07-17 13:14 | 2013-07-17 13:37 | BRYANT - 561CJ042-B | 93 | 3 | Yes | Yes | 23.8 | 19 | 4.8 | 9FF97647DD9C4CF29A4FCA28E72FDE3F |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Tracy | CA | 95377-0223 |  | 2013-07-17 | 2013-07-17 13:40 | 2013-07-17 14:01 | BRYANT - 561CJ030-D | 89 | 13.6 | Yes | Yes | 21.9 | 20.4 | 1.5 | D1B592B475C040308BC55AE182801BB6 |  | R22 | Non-TXV |  | 15.28% | 0.84719 | 29.37% | [5 empty] | Non-TXV | 15.28%
Yuba City | CA | 95991-6696 |  | 2013-07-17 | 2013-07-17 15:25 | 2013-07-17 15:46 | LENNOX - UNK | 100 | 3.6 | Yes | Yes | 23.5 | 19.9 | 3.6 | 6DB36F0582D24A1FA92FEA4980EAE0FD |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Fresno | CA | 93650-1320 |  | 2013-09-25 | 2013-09-25 10:57 | 2013-09-25 10:58 | YORK - D1NP030N05606A | 73 | 4.5 | Yes | Yes | 23.2 | 18.8 | 4.4 | 71E9B2D0ED424CC992BAAD1D8BFA7F51 |  | R22 | Non-TXV |  | 6.164% | 0.93836 | 11.85% | [5 empty] | Non-TXV | 6.164%
Los Banos | CA | 93635-3090 |  | 2013-05-29 | 2013-05-29 11:00 | 2013-05-29 11:02 | LENNOX - 12GCS036755PB | 110 | 4.4 | Yes | Yes | 27.5 | 21.5 | 6 | EF8E67CCE71F48C5B26746F219963C05 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Merced | CA | 95340-4203 |  | 2013-06-28 | 2013-06-28 15:21 | 2013-06-28 15:25 | TRANE - TTP036C100A1 | 140 | 4.1 | Yes | Yes | 15 | 18 | -3 | 226B7E19FDDB40FFA5718D5DBE8A6222 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.628% | [5 empty] | Non-TXV | 2.929%
Atwater | CA | 95301-4833 |  | 2013-06-07 | 2013-06-07 14:58 | 2013-06-07 15:10 | ALLEGIANCE - 2A7A1030A1000AA | 64 | 5.7 | Yes | Yes | 20.4 | 21.7 | -1.3 | 4E568A53B18A426183FD040AC868E2EC |  | R22 | Non-TXV |  | 8.906% | 0.91094 | 17.12% | [5 empty] | Non-TXV | 8.906%
Fresno | CA | 93704-4483 |  | 2013-08-13 | 2013-08-13 13:44 | 2013-08-13 13:45 | YORK - D1NA024N03606C | 54 | 7.1 | Yes | Yes | 20.5 | 18.8 | 1.7 | C136786B4BB74C18861066079788CC57 |  | R22 | Non-TXV |  | 13.15% | 0.86852 | 25.27% | [5 empty] | Non-TXV | 13.15%
Fresno | CA | 93706-3529 |  | 2013-07-22 | 2013-07-22 12:46 | 2013-07-22 12:49 | TEMPSTAR - PGD3360K001C1 | 100 | 3 | Yes | Yes | 24.5 | 20.5 | 4.1 | A6546E13414F4D7982A35EF9DB104826 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93702-2612 |  | 2013-07-18 | 2013-07-18 15:35 | 2013-07-18 16:06 | GOODMAN - GPG13240451CB | 74 | 2.5 | Yes | Yes | 20.6 | 21.3 | -0.7 | E6E0D177118048EF8E216F86BBB6CC43 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.378% | 0.96622 | 6.492% | [5 empty] | Non-TXV | 3.378%
Selma | CA | 93662-4509 |  | 2013-07-31 | 2013-07-31 18:01 | 2013-07-31 18:29 | CARRIER - 48SB-036060301AA | 64 | 6.2 | Yes | Yes | 17.6 | 19.6 | -2 | 12C18B5DB0F7488EA1F6AB2C332023F4 |  | R22 | Non-TXV |  | 9.688% | 0.90312 | 18.62% | [5 empty] | Non-TXV | 9.688%
Chico | CA | 95928-8502 |  | 2013-08-28 | 2013-08-28 10:09 | 2013-08-28 10:32 | RHEEM - RAFD-031JAS | 64 | -3.8 | Yes | Yes | 18.3 | 18.2 | 0.1 | B94AA39DC98F4E77B4EC20A35C6B5FA3 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Fresno | CA | 93704-4480 |  | 2013-06-26 | 2013-06-26 14:09 | 2013-06-26 14:12 | YORK - D1NA024N03606C | 54 | 5.3 | Yes | Yes | 20.9 | 20.4 | 0.5 | 3951C86B32344A04A0BE1C2B4A15DE7B |  | R22 | Non-TXV |  | 9.815% | 0.90185 | 18.86% | [5 empty] | Non-TXV | 9.815%
Fresno | CA | 93727-8314 |  | 2013-07-16 | 2013-07-16 17:19 | 2013-07-16 18:11 | YORK - D2NP024N03606Q | 100 | 3.6 | Yes | Yes | 25.8 | 21.3 | 4.6 | A212C21BDB0D427080D16CCF0E331E8B |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Los Banos | CA | 93635-6336 |  | 2013-06-01 | 2013-06-01 10:36 | 2013-06-01 10:39 | GOODMAN - CK361A | 73 | 5.6 | Yes | Yes | 27.3 | 21.5 | 5.8 | 5608A6AD6D7E4B369E46311A8908FA1E |  | R22 | Non-TXV |  | 7.671% | 0.92329 | 14.74% | [5 empty] | Non-TXV | 7.671%
Oroville | CA | 95965-4982 |  | 2013-08-06 | 2013-08-06 09:04 | 2013-08-06 09:22 | TEMPSTAR - CA5536VKD2 | 82 | 12.6 | Yes | Yes | 22.3 | 21.3 | 1.1 | 36349B81EBBF44BBB0AA40E2462B54B9 |  | R22 | Non-TXV |  | 15.37% | 0.84634 | 29.53% | [5 empty] | Non-TXV | 15.37%
Chico | CA | 95926-1051 |  | 2013-07-12 | 2013-07-12 19:34 | 2013-07-12 19:34 | BRYANT - 113ANA036-E | 83 | 0 | Yes | Yes | 17.6 | 20.4 | -2.8 | A86474CBD5F0484DA157F2037061A4DF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1783 |  | 2013-07-17 | 2013-07-17 10:13 | 2013-07-17 10:31 | BRYANT - 574BNW042060NB | 167 | 5 | Yes | Yes | 17.9 | 20.1 | -2.2 | 6933E5AC406E4F279785A2EBF78A5887 |  | R22 | Non-TXV |  | 2.994% | 0.97006 | 5.754% | [5 empty] | Non-TXV | 2.994%
Los Banos | CA | 93635-2807 |  | 2013-05-28 | 2013-05-28 11:11 | 2013-05-28 11:16 | BDP - 561AJX024000ABAA | 56 | 6.7 | Yes | Yes | 18.7 | 18.2 | 0.5 | 23BAE94E72294F3B871088C1865EE081 |  | R22 | TXV |  | 11.96% | 0.88036 | 22.99% | [5 empty] | TXV | 11.96%
Placerville | CA | 95667-9407 |  | 2013-08-29 | 2013-08-29 16:53 | 2013-08-29 17:24 | GE - BWR730A100A0 | 167 | 24.7 | Yes | Yes | 18.8 | 21.3 | -2.5 | 6C764D4380CF4E91B5AA2C3674FA1961 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.79% | 0.8521 | 28.42% | [5 empty] | Non-TXV | 14.79%
Selma | CA | 93662-3837 |  | 2013-10-04 | 2013-10-04 13:49 | 2013-10-04 14:09 | WHIRLPOOL - N/A | 90 | 6.4 | Yes | Yes | 23.5 | 20 | 3.5 | DE452463CA544A45A5E9B6DDCCA26486 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.111% | 0.92889 | 13.67% | [5 empty] | Non-TXV | 7.111%
Fresno | CA | 93710-4922 |  | 2013-06-27 | 2013-06-27 11:53 | 2013-06-27 11:55 | YORK - DAYP-F036N070A | 108 | 4.6 | Yes | Yes | 20.1 | 19.3 | 0.9 | 13EC153259E145B2BD1DD983A0BE33D8 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Fresno | CA | 93710-4922 |  | 2013-06-27 | 2013-06-27 12:01 | 2013-06-27 12:04 | YORK - DAYP-F036N070A | 108 | 5.7 | Yes | Yes | 18.8 | 19.2 | -0.4 | A547F377B9904E86A22C3C53C43651FE |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Paso Robles | CA | 93446-4765 |  | 2013-08-06 | 2013-08-06 13:46 | 2013-08-06 14:18 | DUCANE - AC10B60-A | 160 | 5.4 | Yes | Yes | 20.6 | 19.9 | 0.7 | 0A1300CC08714ED1B216FF6DB951382B |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Fresno | CA | 93727-6237 |  | 2013-07-15 | 2013-07-15 16:35 | 2013-07-15 17:03 | CARRIER - N/A | 120 | 6 | Yes | Yes | 17.8 | 20.5 | -2.7 | 9D6ABE53B8FC4F9CA5F3E8858D08EE42 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93704-5733 |  | 2013-08-09 | 2013-08-09 13:21 | 2013-08-09 13:21 | CARRIER - 48DC004 | 87 | 0 | Yes | Yes | 21.3 | 23.2 | -1.9 | C738FDD4A1784D3281AC1FB495E0E247 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6525 |  | 2013-07-17 | 2013-07-17 16:04 | 2013-07-17 16:41 | BARD - 585BJ024 | 70 | 2.1 | Yes | Yes | 20.1 | 19.4 | 0.7 | D359CA1C507F4016BFA794FD9897F0D8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95341-6711 |  | 2013-07-03 | 2013-07-03 10:59 | 2013-07-03 11:03 | DAY & NIGHT - 7777UNK | 84 | 3 | Yes | Yes | 13.6 | 16.1 | -2.5 | 6926C7FE39194D30869E6831EEC0052B |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Fresno | CA | 93722-5606 |  | 2013-08-16 | 2013-08-16 08:45 | 2013-08-16 08:47 | ICP - PGAD24B1K6 | 73 | 4.4 | Yes | Yes | 24.7 | 18.8 | 5.9 | A6A8BEEF8F9042F9AE5DE8489200B1E1 |  | R22 | Non-TXV |  | 6.027% | 0.93973 | 11.58% | [5 empty] | Non-TXV | 6.027%
Chico | CA | 95926-3201 |  | 2013-08-22 | 2013-08-22 15:57 | 2013-08-22 16:14 | YORK - H2DB030S06A | 71 | 2.2 | Yes | Yes | 22.9 | 18.6 | 4.3 | E3F76BFF9D344457858E1C886EED37D1 |  | R22 | Non-TXV |  | 3.099% | 0.96901 | 5.955% | [5 empty] | Non-TXV | 3.099%
Stockton | CA | 95206-6241 |  | 2013-07-02 | 2013-07-02 10:46 | 2013-07-02 11:10 | GOODMAN - CKJ42-1AB | 85 | 4.1 | Yes | Yes | 22.3 | 19.2 | 3.2 | BB54C6C2D55042A8B25476E0ECE780DA |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Firebaugh | CA | 93622-2147 |  | 2013-09-18 | 2013-09-18 10:15 | 2013-09-18 10:16 | CARRIER - UNK | 68 | 4.2 | Yes | Yes | 16.6 | 17 | -0.4 | F388FD81601C458FA298DFD658B7CE38 |  | R22 | Non-TXV |  | 6.176% | 0.93824 | 11.87% | [5 empty] | Non-TXV | 6.176%
Red Bluff | CA | 96080-4108 |  | 2013-07-20 | 2013-07-20 13:06 | 2013-07-20 16:57 | BRYANT - 56CJ0366-F | 95 | 3.6 | Yes | Yes | 21.9 | 20.4 | 1.5 | 19031635FE0B4E868F8C3AB8E8D0066F |  | R22 | TXV |  | 3.789% | 0.96211 | 7.283% | [5 empty] | TXV | 3.789%
Fresno | CA | 93722-6807 |  | 2013-07-15 | 2013-07-15 11:53 | 2013-07-15 11:57 | CARRIER - 36300 | 72 | 12.4 | Yes | Yes | 20 | 21.4 | -1.4 | 396B52E82D8448848FD857DF22BE884C |  | R22 | Non-TXV |  | 17.22% | 0.82778 | 33.1% | [5 empty] | Non-TXV | 17.22%
Fresno | CA | 93727-8315 |  | 2013-08-14 | 2013-08-14 15:46 | 2013-08-14 16:02 | ICP - PGF030K060E | 51 | 11.2 | Yes | Yes | 22.5 | 20.7 | 1.8 | EE4E76FEAAAF4A54A2DA02C5EE6A950F |  | R22 | Non-TXV |  | 21.96% | 0.78039 | 42.2% | [5 empty] | Non-TXV | 21.96%
Stockton | CA | 95210-2114 |  | 2013-07-03 | 2013-07-03 11:25 | 2013-07-03 11:44 | LENNOX - HS19-311V-4P | 105 | 3.1 | Yes | Yes | 16.8 | 18.8 | -2 | 3B588E8A33784200B9DFE00192853D3C |  | R22 | Non-TXV |  | 2.952% | 0.97048 | 5.674% | [5 empty] | Non-TXV | 2.952%
Sanger | CA | 93657-9382 |  | 2013-08-03 | 2013-08-03 09:12 | 2013-08-03 09:33 | BRYANT - 574DNWA42060NA | 106 | 4 | Yes | Yes | 17.6 | 20.4 | -2.8 | 299831D6E28142F8A345CB0D5494AA2C |  | R410A | TXV |  | 3.774% | 0.96226 | 7.252% | [5 empty] | TXV | 3.774%
Chowchilla | CA | 93610-2612 |  | 2013-06-02 | 2013-06-02 12:47 | 2013-06-02 14:22 | GOODMAN - GPG13300701AC | 78 | 4.7 | Yes | Yes | 18.3 | 20.4 | -2.1 | D5A0EC70E2014133B0919681109D64DA |  | R22 | Non-TXV |  | 6.026% | 0.93974 | 11.58% | [5 empty] | Non-TXV | 6.026%
Stockton | CA | 95202-1245 |  | 2013-07-09 | 2013-07-09 09:49 | 2013-07-09 09:49 | GOODMAN - CKJ-30-1A | 92 | 0 | Yes | Yes | 22.8 | 18.8 | 4 | 48EFB48289154FDF9AC4BFCDB2F8F7A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-9477 |  | 2013-06-07 | 2013-06-07 14:15 | 2013-06-07 14:26 | PAYNE - PA10JA030 | 77 | 12.2 | Yes | Yes | 17.5 | 18.5 | -1 | C976AA17BB4C4F3DAE6190FF76024CD9 |  | R22 | TXV |  | 15.84% | 0.84156 | 30.45% | [5 empty] | TXV | 15.84%
Ione | CA | 95640-9524 |  | 2013-08-23 | 2013-08-23 11:53 | 2013-08-23 12:09 | NORDYNE - S3QA-036K | 69 | 6.4 | Yes | Yes | 20.2 | 20.4 | -0.2 | A1E51B8AA46B420D8D007E83DF2CB6EA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.275% | 0.90725 | 17.83% | [5 empty] | Non-TXV | 9.275%
Stockton | CA | 95209-1523 |  | 2013-07-03 | 2013-07-03 10:01 | 2013-07-03 10:01 | YORK - H2CB036S06A | 91 | 0 | Yes | Yes | 20.4 | 19.3 | 1.1 | 0874D7BCEE8848BFA102532D2B82B47D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5051 |  | 2013-06-06 | 2013-06-06 13:51 | 2013-06-06 13:53 | TRANE - YCP030F1M0AB | 106 | 3.5 | Yes | Yes | 22.1 | 19.2 | 3 | 3B0655C1B33842E1AA66FB0EF5D44998 |  | R22 | Non-TXV |  | 3.302% | 0.96698 | 6.345% | [5 empty] | Non-TXV | 3.302%
Paso Robles | CA | 93446-1061 |  | 2013-08-05 | 2013-08-05 15:57 | 2013-08-05 16:17 | CARRIER - 38EA018300 | 48 | 1.4 | Yes | Yes | 19.8 | 21.3 | -1.5 | A520F1E4A075427CA55247EEC7DD4408 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Stockton | CA | 95219-3585 |  | 2013-07-24 | 2013-07-24 12:55 | 2013-07-24 13:22 | HEIL - ACS018A2C1 | 56 | 10 | Yes | Yes | 16.9 | 19.9 | -3 | 207E5E84E8254BB6A1A9DEFD6A7C64CB |  | R22 | Non-TXV |  | 17.86% | 0.82143 | 34.32% | [5 empty] | Non-TXV | 17.86%
Manteca | CA | 95336-3937 |  | 2013-07-10 | 2013-07-10 09:42 | 2013-07-10 10:06 | YORK - H1RD024S06G | 88 | 6.6 | Yes | Yes | 18.3 | 18.6 | -0.3 | 296191C8D8F0408EB22D85763B30CCCF |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95209-5049 |  | 2013-07-16 | 2013-07-16 14:36 | 2013-07-16 14:57 | PAYNE - 567GJ042 | 94 | 5.9 | Yes | Yes | 18.3 | 19 | -0.7 | 0E45AFA3092B45059EC026AA7281092A |  | R22 | Non-TXV |  | 6.277% | 0.93723 | 12.06% | [5 empty] | Non-TXV | 6.277%
Selma | CA | 93662-4317 |  | 2013-08-09 | 2013-08-09 15:11 | 2013-08-09 16:00 | GOODMAN - CKL42-1B | 115 | 15 | Yes | Yes | 18.6 | 21.1 | -2.5 | C08A3B39B91746C08F30AD1B4E8C1155 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.04% | 0.86957 | 25.07% | [5 empty] | Non-TXV | 13.04%
Manteca | CA | 95336-3936 |  | 2013-07-17 | 2013-07-17 11:25 | 2013-07-17 11:46 | YORK - H1RD024S06G | 88 | 2.8 | Yes | Yes | 21 | 19.3 | 1.7 | 9C1A732C2E684070B1341B6AFB836917 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Oakdale | CA | 95361-4012 |  | 2013-07-10 | 2013-07-10 15:35 | 2013-07-10 15:56 | CARRIER - 38CK036350 | 70 | 2.1 | Yes | Yes | 20.1 | 21 | -0.9 | CED1DEF3CD5040AC888220E3049770EB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95206-4950 |  | 2013-07-20 | 2013-07-20 10:14 | 2013-07-20 10:46 | GOODMAN - CRT48-1 | 145 | 4.9 | Yes | Yes | 22.6 | 16.8 | 5.8 | FF987E61467D4398848EDF33ACC04507 |  | R22 | Non-TXV |  | 3.379% | 0.96621 | 6.494% | [5 empty] | Non-TXV | 3.379%
Stockton | CA | 95210-1924 |  | 2013-07-11 | 2013-07-11 10:30 | 2013-07-11 10:48 | GOODMAN - CT36-1B | 103 | -6.1 | Yes | Yes | 25.5 | 19.6 | 6 | DBA1E08DCABA4E6893C0CDEA7805F698 |  | R22 | Non-TXV |  | -5.922% | 1.0592 | 1.659% |  |  |  |  | Non-TXV |  |  | -5.922%
Willows | CA | 95988-0000 |  | 2013-08-14 | 2013-08-14 10:20 | 2013-08-14 10:20 | GOODMAN - VSX130361AA | 89 | 0 | Yes | Yes | 23 | 21.5 | 1.5 | 2B01224932CC43E4A45413D2668F37C7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0693 |  | 2013-08-22 | 2013-08-22 10:10 | 2013-08-22 10:36 | YORK - H2RD030S06A | 93 | 3.4 | Yes | Yes | 22 | 19 | 3 | 367928AD2DB2438B89D40B8E26BEB777 |  | R22 | Non-TXV |  | 3.656% | 0.96344 | 7.026% | [5 empty] | Non-TXV | 3.656%
Los Banos | CA | 93635-4815 |  | 2013-05-31 | 2013-05-31 11:56 | 2013-05-31 11:59 | AIRE-FLO - PY3PNA03609ONA | 167 | 10.7 | Yes | Yes | 23.6 | 21.5 | 2.1 | D66C23D501B040E78B64CFECA5E86708 |  | R22 | Non-TXV |  | 6.407% | 0.93593 | 12.31% | [5 empty] | Non-TXV | 6.407%
Oakdale | CA | 95361-8217 |  | 2013-07-09 | 2013-07-09 10:59 | 2013-07-09 11:18 | RUUD - UANL-030JAZ | 94 | 10.1 | Yes | Yes | 21.5 | 20.4 | 1.1 | AE1E3D3CB2C54788A0FEE1A2622E5DEE |  | R410A | TXV |  | 10.74% | 0.89255 | 20.65% | [5 empty] | TXV | 10.74%
Colfax | CA | 95713-9568 |  | 2013-07-26 | 2013-07-26 10:41 | 2013-07-26 11:00 | BRYANT - 163ANA060-B | 150 | 5.5 | Yes | Yes | 19 | 18.5 | 0.5 | A07758497FC740E58F98A63A7249C6E5 |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Colfax | CA | 95713-8803 |  | 2013-07-25 | 2013-07-25 09:05 | 2013-07-25 09:35 | PAYNE - PY2PNB030060AAAA | 70 | 3 | Yes | Yes | 21 | 19.9 | 1.1 | D74AE8B5C5074208A085CB4A68AEDDE5 |  | R22 | TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | TXV | 4.286%
Los Banos | CA | 93635-0000 |  | 2013-05-28 | 2013-05-28 09:23 | 2013-05-28 09:30 | AMERICAN STANDARD - 2A7B3060A1000AA | 139 | 18.9 | Yes | Yes | 17 | 19.3 | -2.3 | 2A6E28E4F0B64AD19D75F50D3885FC09 |  | R22 | Non-TXV |  | 13.6% | 0.86403 | 26.13% | [5 empty] | Non-TXV | 13.6%
Chico | CA | 95926-4454 |  | 2013-08-23 | 2013-08-23 13:33 | 2013-08-23 13:53 | OTHER - CA5524VKD3 | 73 | 4.8 | Yes | Yes | 15.2 | 17.2 | -2 | 60ABFB8F0AD247EFB23EEDD91FCBD85D |  | R22 | Non-TXV |  | 6.575% | 0.93425 | 12.64% | [5 empty] | Non-TXV | 6.575%
Los Banos | CA | 93635-8549 |  | 2013-07-12 | 2013-07-12 13:42 | 2013-07-12 13:54 | TRANE - 2A7B0048A1000AA | 109 | 11.7 | Yes | Yes | 21.8 | 21.7 | 0.1 | B568F270FC174D1B9925075A4899DAF8 |  | R22 | Non-TXV |  | 10.73% | 0.89266 | 20.63% | [5 empty] | Non-TXV | 10.73%
Riverbank | CA | 95367-2612 |  | 2013-07-11 | 2013-07-11 11:21 | 2013-07-11 12:17 | CARRIER - 591ANX042000ABAA | 85 | 3.8 | Yes | Yes | 20.8 | 20.4 | 0.4 | 5D6B043818DD4A7D9C1877ADB72DCA0B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Chico | CA | 95928-8851 |  | 2013-08-07 | 2013-08-07 12:26 | 2013-08-07 12:52 | GOODMAN - PGB036075-1A | 60 | 2.2 | Yes | Yes | 23.1 | 18.3 | 4.8 | 55459440F48D43CCA0AF4A2272C3CBB9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Stockton | CA | 95205-5611 |  | 2013-07-17 | 2013-07-17 12:32 | 2013-07-17 12:57 | AIRE-FLO - GPG13360701AA | 112 | 5.1 | Yes | Yes | 25.9 | 20.2 | 5.7 | 51F00EEE7E1748398E7767F753758FE3 |  | R22 | Non-TXV |  | 4.554% | 0.95446 | 8.751% | [5 empty] | Non-TXV | 4.554%
Paradise | CA | 95969-4118 |  | 2013-07-15 | 2013-07-15 18:09 | 2013-07-15 18:26 | COLEMAN - NA | 56 | 1.8 | Yes | Yes | 21.6 | 21 | 0.6 | 0043DAC812AF432BA0877FACFAC9A202 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Stockton | CA | 95215-5424 |  | 2013-06-28 | 2013-06-28 12:02 | 2013-06-28 12:26 | DAY & NIGHT - 588ANW024040ACAD | 38 | 4.2 | Yes | Yes | 13.5 | 8.8 | 4.8 | C0C618A8106A43D5BC0A39448467AC44 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.05% | 0.88947 | 21.24% | [5 empty] | Non-TXV | 11.05%
Stockton | CA | 95210-1932 |  | 2013-07-01 | 2013-07-01 10:59 | 2013-07-01 11:44 | AMANA - RCC48A2D | 138 | -8.1 | Yes | Yes | 21.3 | 17.3 | 4.1 | F9894B3D4AEB466A956E514A0E04B616 |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Stockton | CA | 95219-3586 |  | 2013-08-07 | 2013-08-07 10:52 | 2013-08-07 11:17 | OTHER - UNK | 55 | 10.3 | Yes | Yes | 17.9 | 18.2 | -0.3 | 86E1D3B8E05B42058E293B80D521F22E |  | R22 | Non-TXV |  | 18.73% | 0.81273 | 35.99% | [5 empty] | Non-TXV | 18.73%
Dinuba | CA | 93618-3203 |  | 2013-06-26 | 2013-06-26 16:39 | 2013-06-26 17:09 | BDP - N/A | 102 | 5.3 | Yes | Yes | 19.5 | 18.8 | 0.7 | 2441197B7EF845DDB9FE7F6F2BADB6BF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.196% | 0.94804 | 9.986% | [5 empty] | Non-TXV | 5.196%
Oakdale | CA | 95361-8617 |  | 2013-10-04 | 2013-10-04 12:27 | 2013-10-04 13:01 | DAY & NIGHT - CBD | 51 | 1.6 | Yes | Yes | 23.2 | 20.4 | 2.8 | EBB26EAFC1D34B5B94AD0F2F033BFDBC |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Oakdale | CA | 95361-8617 |  | 2013-10-04 | 2013-10-04 12:40 | 2013-10-04 13:01 | DAY & NIGHT - 585B024050YACR | 51 | 1.6 | Yes | Yes | 24.3 | 19.5 | 4.8 | FF0C862F2ABA465DA30C846B779397ED |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Ione | CA | 95640-9573 |  | 2013-08-02 | 2013-08-02 08:47 | 2013-08-02 09:11 | RHEEM - RAKAB-030JAS | 68 | 10.3 | Yes | Yes | 16 | 18.7 | -2.7 | 8CE324E30EF04058B2F67DAB4457D5E5 |  | R22 | Non-TXV |  | 15.15% | 0.84853 | 29.11% | [5 empty] | Non-TXV | 15.15%
Oroville | CA | 95966-5922 |  | 2013-07-29 | 2013-07-29 21:31 | 2013-07-29 21:46 | WEATHER KING - 12AJB3OA-1 | 96 | 11.6 | Yes | Yes | 20 | 20.4 | -0.4 | DD756ABABDB1426296E5735DAC56B413 |  | R22 | Non-TXV |  | 12.08% | 0.87917 | 23.22% | [5 empty] | Non-TXV | 12.08%
Stockton | CA | 95215-6727 |  | 2013-07-01 | 2013-07-01 11:30 | 2013-07-01 11:47 | OTHER - 13ACD-036-230-16 | 92 | 9.2 | Yes | Yes | 19.3 | 20.9 | -1.6 | 0FFA3786A2F9490D978EE4BD92D5628B |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Los Banos | CA | 93635-0000 |  | 2013-05-28 | 2013-05-28 09:55 | 2013-05-28 10:04 | AMERICAN STANDARD - 2A7B0048A10000AA | 109 | 9.9 | Yes | Yes | 16.8 | 19.5 | -2.7 | 097BD171D9F6456AA625479B12D6C4B5 |  | R22 | Non-TXV |  | 9.083% | 0.90917 | 17.45% | [5 empty] | Non-TXV | 9.083%
Manteca | CA | 95336-6341 |  | 2013-07-25 | 2013-07-25 12:12 | 2013-07-25 12:40 | CARRIER - 585GJ030040 | 58 | 2.8 | Yes | Yes | 25.3 | 19.5 | 5.8 | 06BA61E117ED474AA611D0E84EA69C1A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.828% | 0.95172 | 9.278% | [5 empty] | Non-TXV | 4.828%
Pioneer | CA | 95666-9619 |  | 2013-09-10 | 2013-09-10 09:09 | 2013-09-10 09:27 | HEIL - NRGF48ED803 | 112 | -10.5 | Yes | Yes | 17.1 | 19.6 | -2.5 | FC846ED158D345A69500934317E6DB32 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Red Bluff | CA | 96080-9732 |  | 2013-08-13 | 2013-08-13 15:16 | 2013-08-13 18:41 | LENNOX - CHP20R-511-2P | 168 | 4.9 | Yes | Yes | 24 | 23.1 | 0.9 | F8EC302B8F464459877F4FBF275235A7 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Stockton | CA | 95203-1538 |  | 2013-07-15 | 2013-07-15 11:53 | 2013-07-15 11:53 | RHEEM - RRMA-A042JK08X | 114 | 0 | Yes | Yes | 18 | 19.3 | -1.3 | 79D8A4038DA44569B128A492A58CC575 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-7038 |  | 2013-07-17 | 2013-07-17 10:22 | 2013-07-17 10:38 | BRYANT - 563CN048-D | 165 | 16.1 | Yes | Yes | 19.4 | 19.3 | 0.1 | 34CC3C8587E94D32A2C22B99152CF93A |  | R22 | TXV |  | 9.758% | 0.90242 | 18.75% | [5 empty] | TXV | 9.758%
Chico | CA | 95926-4004 |  | 2013-07-11 | 2013-07-11 20:20 | 2013-07-11 21:01 | RHEEM - RAHE-036JAS | 91 | 7.7 | Yes | Yes | 23.2 | 20.6 | 2.7 | 66BFDB5BAE8D4AF584DFC0DA97223D95 |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Pine Grove | CA | 95665-9722 |  | 2013-08-09 | 2013-08-09 13:27 | 2013-08-09 13:27 | RHEEM - PNA-030J 000 | 79 | 0 | Yes | Yes | 25.4 | 20.6 | 4.8 | 486095C16DCB48688FD4325EAB188EB3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pine Grove | CA | 95665-9671 |  | 2013-09-03 | 2013-09-03 10:56 | 2013-09-03 11:00 | BDP - 561AJ042-A | 88 | 6.8 | Yes | Yes | 26.4 | 20.4 | 6 | 94BDC8B047134FD1A3621F8C456A213E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.727% | 0.92273 | 14.85% | [5 empty] | Non-TXV | 7.727%
Pine Grove | CA | 95665-9671 |  | 2013-09-03 | 2013-09-03 11:09 | 2013-09-03 11:31 | BDP - 561AJ036-B | 72 | 9.5 | Yes | Yes | 25.9 | 20.7 | 5.3 | FC229F6414E84E5D958911B2B028AB3A |  | R22 | Non-TXV |  | 13.19% | 0.86806 | 25.36% | [5 empty] | Non-TXV | 13.19%
Manteca | CA | 95337-6677 |  | 2013-07-16 | 2013-07-16 14:19 | 2013-07-16 14:44 | RHEEM - RAMB-036JBZ | 93 | 3.9 | Yes | Yes | 22.8 | 19.8 | 3 | 254261951EC44A588C1B5206B51828DE |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Manteca | CA | 95337-6677 |  | 2013-07-16 | 2013-07-16 14:25 | 2013-07-16 14:49 | RHEEM - RAMB-036JBZ | 93 | 2.8 | Yes | Yes | 22.8 | 20.4 | 2.4 | A9B3ED31502149908D8A22889D0F6BBF |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Tracy | CA | 95377-8425 |  | 2013-07-19 | 2013-07-19 09:21 | 2013-07-19 09:53 | CARRIER - 38EZG030300 | 88 | 6.7 | Yes | Yes | 18.3 | 20.4 | -2.1 | 966012642C2A4A67BF3384259859D70E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 7.614% | 0.92386 | 14.63% | [5 empty] | Non-TXV | 7.614%
Chico | CA | 95973-9113 |  | 2013-07-10 | 2013-07-10 20:00 | 2013-07-10 20:22 | BRYANT - 563CN036-C | 101 | 5.5 | Yes | Yes | 16.7 | 19.6 | -2.9 | 6D606920F09F4B989780265687871053 |  | R22 | Non-TXV |  | 5.446% | 0.94554 | 10.47% | [5 empty] | Non-TXV | 5.446%
Stockton | CA | 95206-2818 |  | 2013-07-13 | 2013-07-13 09:18 | 2013-07-13 09:40 | BRYANT - 561CJ036-D | 82 | -5.8 | Yes | Yes | 22.6 | 19 | 3.6 | 5DC843174A914B84803EFC5B1ABF0786 |  | R22 | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Nevada City | CA | 95959-9019 |  | 2013-08-07 | 2013-08-07 11:26 | 2013-08-07 11:26 | LENNOX - 10GCS036-75-3P | 58 | 0 | Yes | Yes | 23 | 17.6 | 5.4 | F2B77E064B0641288AC8FF86F797D31F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9406 |  | 2013-07-19 | 2013-07-19 10:25 | 2013-07-19 10:58 | CARRIER - 38QH030300SM | 120 | 9.7 | Yes | Yes | 16.3 | 19 | -2.7 | A9235B9090F04D2D9DFADE6F8AF0D7D1 |  | R22 | Non-TXV |  | 8.083% | 0.91917 | 15.53% | [5 empty] | Non-TXV | 8.083%
Stockton | CA | 95205-4754 |  | 2013-07-15 | 2013-07-15 17:16 | 2013-07-15 17:37 | LENNOX - HS25-331-1P | 129 | 12.9 | Yes | Yes | 18.9 | 21.5 | -2.6 | 49D35B1EAF2F42D9AFD2F576C7317048 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Tracy | CA | 95376-3716 |  | 2013-07-11 | 2013-07-11 14:18 | 2013-07-11 14:38 | BRYANT - DBYP-F030N070A | 73 | 4.3 | Yes | Yes | 20.8 | 22.1 | -1.3 | F4E47BC8EDDE447B964449AF1C20A49A |  | R22 | Non-TXV |  | 5.89% | 0.9411 | 11.32% | [5 empty] | Non-TXV | 5.89%
Copperopolis | CA | 95228-0000 |  | 2013-08-22 | 2013-08-22 15:11 | 2013-08-22 15:35 | GOODMAN - | 110 | 4.6 | Yes | Yes | 23.8 | 25.1 | -1.3 | 00BFFA0EFA884B3A93299F917053468F |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
Tracy | CA | 95377-9501 |  | 2013-07-26 | 2013-07-26 14:57 | 2013-07-26 15:47 | GOODMAN - GSC130601CB | 85 | 2.7 | Yes | Yes | 21.6 | 19.3 | 2.3 | BC9AB148FB9C49A8BB8AABDCCC05BF08 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Merced | CA | 95348-3175 |  | 2013-08-30 | 2013-08-30 10:07 | 2013-08-30 10:09 | CARRIER - 38YCB018310 | 68 | 11.1 | Yes | Yes | 18.5 | 16.9 | 1.6 | F0CFEC70BDDE4F8F9031B0A8784E5BF5 |  | R22 | TXV |  | 16.32% | 0.83676 | 31.37% | [5 empty] | TXV | 16.32%
Manteca | CA | 95336-4906 |  | 2013-07-12 | 2013-07-12 09:25 | 2013-07-12 09:49 | JANITROL - UNK | 85 | 3.8 | Yes | Yes | 18 | 19.3 | -1.3 | D6F5E0DC79C74B01A73745A2C2861A4C |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Stockton | CA | 95212-3506 |  | 2013-06-27 | 2013-06-27 11:44 | 2013-06-27 12:49 | UNITARY PRODUCTS GROUP - AC048X1222A | 119 | 24.1 | Yes | Yes | 18.1 | 19.8 | -1.7 | E2F8BCBD31F644F3A2A743CD2068008F |  | R22 | Non-TXV |  | 20.25% | 0.79748 | 38.92% | [5 empty] | Non-TXV | 20.25%
Bangor | CA | 95914-0000 |  | 2013-09-11 | 2013-09-11 09:28 | 2013-09-11 09:28 | AMANA - PGC4880902A | 135 | 0 | Yes | Yes | 19 | 17.7 | 1.3 | DE00CA9363E840EEB8FF1ECE99EC0EF0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2200 |  | 2013-08-27 | 2013-08-27 10:46 | 2013-08-27 10:46 | GE - BGTA736B1B | 70 | 0 | Yes | Yes | 18.1 | 18.7 | -0.6 | A21A158668FB4B249CB42D5AF5B86F14 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6403 |  | 2013-07-02 | 2013-07-02 09:11 | 2013-07-02 09:30 | OTHER - UNK | 64 | -3.8 | Yes | Yes | 24.2 | 19.1 | 5.2 | C859BA65BED84C6599EC1785C9B18341 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Stockton | CA | 95209-2262 |  | 2013-07-24 | 2013-07-24 10:57 | 2013-07-24 11:14 | YORK - D1NH060N09006C | 140 | -8.2 | Yes | Yes | 24.9 | 19.4 | 5.5 | 1E332CB65F094BC29FC10B0C866C2490 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Manteca | CA | 95336-7703 |  | 2013-07-18 | 2013-07-18 15:35 | 2013-07-18 16:04 | HEIL - CBD | 85 | 2.5 | Yes | Yes | 23 | 20.1 | 2.9 | 175E58ED745A4303BDFED60F5764F714 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Soulsbyville | CA | 95372-9752 |  | 2013-09-24 | 2013-09-24 09:01 | 2013-09-24 09:20 | ICP - N2A336AKA200 | 88 | 7.2 | Yes | Yes | 26 | 20.7 | 5.3 | 7078EABC356E4CE2B7BCBD9A54723ADF |  | R22 | Non-TXV |  | 8.182% | 0.91818 | 15.72% | [5 empty] | Non-TXV | 8.182%
Atwater | CA | 95301-4806 |  | 2013-06-06 | 2013-06-06 13:06 | 2013-06-06 13:20 | BDP - 561CJ030 | 71 | 6.3 | Yes | Yes | 14 | 16.8 | -2.8 | F13532C0C5934EC18683D20374259F0A |  | R22 | TXV |  | 8.873% | 0.91127 | 17.05% | [5 empty] | TXV | 8.873%
Ione | CA | 95640-5213 |  | 2013-08-01 | 2013-08-01 09:37 | 2013-08-01 10:05 | DAY & NIGHT - 563CN030-A19380 | 100 | 13.5 | Yes | Yes | 17 | 19.5 | -2.5 | 61532BECC3BE44B2BF1151D1C93BF5E5 |  | R22 | TXV |  | 13.5% | 0.865 | 25.94% | [5 empty] | TXV | 13.5%
Stockton | CA | 95205-6431 |  | 2013-07-15 | 2013-07-15 15:17 | 2013-07-15 15:41 | ICP - PGC030K060E | 51 | 6.1 | Yes | Yes | 22.6 | 21.3 | 1.3 | 5789C0D4F235476FBCB6EE13F68F3AE4 |  | R22 | Non-TXV |  | 11.96% | 0.88039 | 22.99% | [5 empty] | Non-TXV | 11.96%
Coarsegold | CA | 93614-9232 |  | 2013-09-16 | 2013-09-16 20:42 | 2013-09-16 20:44 | LENNOX - 10ACB36-11P | 80 | 4.2 | Yes | Yes | 22.2 | 21.4 | 0.8 | 07EBBAA6EED84E68B90F546C8D0A6843 |  | R22 | Non-TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | Non-TXV | 5.25%
Fresno | CA | 93726-3408 |  | 2013-07-26 | 2013-07-26 14:40 | 2013-07-26 15:08 | CARRIER - 48KLA136300BE | 102 | 21.7 | Yes | Yes | 23.8 | 20.3 | 3.5 | 1ECF4D43AA8F41BE97B4E9B9B4055177 |  | R22 | Non-TXV |  | 21.27% | 0.78725 | 40.88% | [5 empty] | Non-TXV | 21.27%
Escalon | CA | 95320-1529 |  | 2013-08-29 | 2013-08-29 10:25 | 2013-08-29 10:54 | OTHER - UNK | 64 | 8.6 | Yes | Yes | 15.6 | 17.3 | -1.7 | 92A38029236E4F62ADB3910E0A932DF3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
Fresno | CA | 93703-2664 |  | 2013-07-03 | 2013-07-03 16:04 | 2013-07-03 17:34 | RHEEM - RRNL-B024JK06X | 77 | 3 | Yes | Yes | 19.8 | 22.4 | -2.6 | 1FE96E0AB11E4024BBFA0E6E00266B24 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R410A | TXV |  | 3.896% | 0.96104 | 7.487% | [5 empty] | TXV | 3.896%
Fresno | CA | 93720-4481 |  | 2013-08-09 | 2013-08-09 01:00 | 2013-08-09 01:00 | LENNOX - 12ACB485E | 171 | 6.5 | Yes | Yes | 16.7 | 19 | -2.3 | 01A59B6DEAB94135BF615BACA1AFFFA9 | Add refrigerant: 6.5 oz | R22 | Non-TXV |  | 3.801% | 0.96199 | 7.305% | [5 empty] | Non-TXV | 3.801%
Atwater | CA | 95301-2239 |  | 2013-06-27 | 2013-06-27 10:22 | 2013-06-27 10:31 | AIRE-FLO - RCE42A2D | 150 | 13.2 | Yes | Yes | 20.1 | 20.4 | -0.3 | B8730F7AA15B4FE1AD60B757DDD33CBB |  | R22 | Non-TXV |  | 8.8% | 0.912 | 16.91% | [5 empty] | Non-TXV | 8.8%
Stockton | CA | 95210-1650 |  | 2013-07-01 | 2013-07-01 09:05 | 2013-07-01 09:22 | RUUD - UAFD-060JBS | 118 | 3.7 | Yes | Yes | 24.3 | 18.8 | 5.5 | F2D55497521748D3A8E527D1CB9D7345 |  | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Riverbank | CA | 95367-3313 |  | 2013-08-20 | 2013-08-20 14:31 | 2013-08-20 15:00 | BDP - 598AN036-B | 195 | 7.8 | Yes | Yes | 21.1 | 20.6 | 0.5 | 6EAC13CC0BD64C658FCDAF89FC63DFF2 |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Fresno | CA | 93725-4001 |  | 2013-07-18 | 2013-07-18 13:42 | 2013-07-18 14:40 | GOODMAN - GPG13360451AB | 112 | 10.9 | Yes | Yes | 25 | 20.1 | 4.9 | E092572DCD424DF98C233DC83E6436E8 |  | R22 | Non-TXV |  | 9.732% | 0.90268 | 18.7% | [5 empty] | Non-TXV | 9.732%
Fresno | CA | 93720-0334 |  | 2013-06-28 | 2013-06-28 12:17 | 2013-06-28 12:23 | LENNOX - 12ACB48-4P | 171 | 5.3 | Yes | Yes | 22.3 | 19.7 | 2.6 | CCAA6FA21EDE451AA58AE60E452D1A10 |  | R22 | Non-TXV |  | 3.099% | 0.96901 | 5.956% | [5 empty] | Non-TXV | 3.099%
Fresno | CA | 93726-1636 |  | 2013-07-29 | 2013-07-29 10:24 | 2013-07-29 10:26 | ICP - PGAD36D1K6 | 102 | 15.2 | Yes | Yes | 24 | 21.9 | 2.1 | F5FCD19A868842E38D37972DE04B75CA |  | R22 | Non-TXV |  | 14.9% | 0.85098 | 28.64% | [5 empty] | Non-TXV | 14.9%
Stockton | CA | 95202-1703 |  | 2013-07-09 | 2013-07-09 12:58 | 2013-07-09 13:20 | UNITARY PRODUCTS GROUP - DAYA-F036N070C | 67 | 3 | Yes | Yes | 22.4 | 18.5 | 3.9 | 1D47B725E83343C6AFCCC857E718E929 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.478% | 0.95522 | 8.605% | [5 empty] | Non-TXV | 4.478%
Stockton | CA | 95204-1342 |  | 2013-07-09 | 2013-07-09 14:01 | 2013-07-09 14:22 | PAYNE - PY1PNB030060AAAA | 55 | 1.8 | Yes | Yes | 23.1 | 20.7 | 2.4 | 7AAC314E77D9475BA3FBBFC23C5F2BC7 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Fowler | CA | 93625-2906 |  | 2013-08-20 | 2013-08-20 09:35 | 2013-08-20 09:50 | LENNOX - 10GCS048X-100-3PA | 93 | 3.3 | Yes | Yes | 17 | 19.3 | -2.3 | D52083BDE34A49D99412032E27F86D95 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Riverbank | CA | 95367-0000 |  | 2013-07-11 | 2013-07-11 09:09 | 2013-07-11 09:32 | TRANE - 2TTX4060A1000AA | 211 | 6.6 | Yes | Yes | 22.8 | 19.7 | 3.1 | 7D6359585AFA4FAFA0FBA47DBD736656 |  | R22 | Non-TXV |  | 3.128% | 0.96872 | 6.011% | [5 empty] | Non-TXV | 3.128%
Sanger | CA | 93657-8835 |  | 2013-07-23 | 2013-07-23 10:55 | 2013-07-23 11:33 | RUUD - N/A | 120 | 3.8 | Yes | Yes | 15.1 | 17.7 | -2.6 | 71399314216940929A3774B67E95ECFA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Fresno | CA | 93704-1526 |  | 2013-06-26 | 2013-06-26 11:28 | 2013-06-26 11:40 | OTHER - UNK | 76 | 5.5 | Yes | Yes | 15.3 | 17.2 | -1.9 | E5F9ECAB58B445AC9F037F3F47AAF7B1 |  | R22 | Non-TXV |  | 7.237% | 0.92763 | 13.91% | [5 empty] | Non-TXV | 7.237%
Yuba City | CA | 95993-6104 |  | 2013-07-18 | 2013-07-18 10:14 | 2013-07-18 10:35 | BRYANT - UNK | 89 | 7.2 | Yes | Yes | 17 | 18.5 | -1.5 | DD81426A4F1B4EB98533EB3F4B395CE0 |  | R22 | TXV |  | 8.09% | 0.9191 | 15.55% | [5 empty] | TXV | 8.09%
Yuba City | CA | 95993-6104 |  | 2013-07-18 | 2013-07-18 10:21 | 2013-07-18 10:46 | BRYANT - 563CN02-D | 83 | 9.3 | Yes | Yes | 18 | 18.7 | -0.7 | 1DA34EA66E9246A89282F7E387C06CD8 |  | R22 | TXV |  | 11.2% | 0.88795 | 21.53% | [5 empty] | TXV | 11.2%
Chico | CA | 95973-1251 |  | 2013-07-09 | 2013-07-09 08:38 | 2013-07-09 09:03 | RHEEM - RAHE060JAS | 176 | 16.1 | Yes | Yes | 25 | 22 | 3 | A7DE76D4D7AD48949A73AFDF6DD0D93B |  | R22 | Non-TXV |  | 9.148% | 0.90852 | 17.58% | [5 empty] | Non-TXV | 9.148%
Stockton | CA | 95209-5003 |  | 2013-07-16 | 2013-07-16 13:18 | 2013-07-16 13:35 | PAYNE - PY1PNB030060AAAA | 55 | -5.2 | Yes | Yes | 19.2 | 18.6 | 0.7 | 404BC52C070045D7926E04DE3C0065E8 |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Fresno | CA | 93704-5730 |  | 2013-07-23 | 2013-07-23 12:51 | 2013-07-23 12:52 | GOODMAN - 0300751 | 68 | 6.5 | Yes | Yes | 20.1 | 20.4 | -0.3 | 670E95D8CA98483E81D1B67F20878A0B |  | R22 | Non-TXV |  | 9.559% | 0.90441 | 18.37% | [5 empty] | Non-TXV | 9.559%
Live Oak | CA | 95953-9658 |  | 2013-09-09 | 2013-09-09 12:44 | 2013-09-09 13:01 | CARRIER - UNK | 93 | 3 | Yes | Yes | 19.2 | 18.3 | 1 | 69B8E7FA7BD7462A8C519EE62CA5BBD0 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Paso Robles | CA | 93446-1738 |  | 2013-10-09 | 2013-10-09 14:27 | 2013-10-09 14:51 | PAYNE - 585B024050YACR | 51 | -3 | Yes | Yes | 22.9 | 18.7 | 4.2 | F3EC650FBBAD46FDA8EB0BFB6FB9ED74 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Kerman | CA | 93630-1954 |  | 2013-07-31 | 2013-07-31 14:04 | 2013-07-31 14:05 | CARRIER - 48GS036060301 | 56 | 7.8 | Yes | Yes | 26.3 | 20.9 | 5.4 | B3B9B95C56664685BEE427375A63536E |  | R22 | Non-TXV |  | 13.93% | 0.86071 | 26.77% | [5 empty] | Non-TXV | 13.93%
Merced | CA | 95348-9352 |  | 2013-07-08 | 2013-07-08 15:10 | 2013-07-08 15:13 | AMANA - PGD24C0452E | 74 | 3 | Yes | Yes | 25.7 | 20.4 | 5.3 | DBE4A5BB86BB44ADA70F78BBFF3A024E |  | R22 | Non-TXV |  | 4.054% | 0.95946 | 7.791% | [5 empty] | Non-TXV | 4.054%
Paso Robles | CA | 93446-1738 |  | 2013-08-05 | 2013-08-05 14:15 | 2013-08-05 14:36 | ICP - PGD324040K001C1 | 77 | -4.5 | Yes | Yes | 23.8 | 22.6 | 1.2 | 273B98F179B4422E94A9CEFD46B28DAC |  | R410A | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Manteca | CA | 95336-9268 |  | 2013-07-12 | 2013-07-12 12:33 | 2013-07-12 12:55 | YORK - BRC0036-1BD | 52 | 11.2 | Yes | Yes | 18.9 | 20.4 | -1.5 | F28931EFF3334F2B88FE3D0DB02499E2 |  | R22 | Non-TXV |  | 21.54% | 0.78462 | 41.39% | [5 empty] | Non-TXV | 21.54%
Fresno | CA | 93705-2427 |  | 2013-07-08 | 2013-07-08 17:08 | 2013-07-08 17:32 | AMANA - PGA36C0702F | 64 | 3 | Yes | Yes | 23 | 21 | 2 | 865B91DFF5614AD0821F7E461CBD8A2D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Manteca | CA | 95336-4562 |  | 2013-07-12 | 2013-07-12 10:13 | 2013-07-12 10:41 | GOODMAN - CKL18-1 | 85 | 5.9 | Yes | Yes | 18.6 | 19.9 | -1.3 | 7401F1B38DA64EDB997A20868D8FA0E9 |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
Paso Robles | CA | 93446-1767 |  | 2013-08-05 | 2013-08-05 14:39 | 2013-08-05 14:59 | PAYNE - 585FJ018050 | 55 | 1.9 | Yes | Yes | 20.9 | 18.8 | 2.1 | 8D382BA66FCE493BADD2688B5A6166A1 |  | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Manteca | CA | 95336-3642 |  | 2013-07-17 | 2013-07-17 15:35 | 2013-07-17 16:01 | GOODMAN - GPG1336070M41AC | 85 | 2.7 | Yes | Yes | 23.5 | 18.7 | 4.8 | E8ED5E6874FD4AB6B44E63B25E8E78DE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Manteca | CA | 95337-5657 |  | 2013-07-16 | 2013-07-16 16:17 | 2013-07-16 16:40 | TRANE - TTR030C100A4 | 66 | 2.4 | Yes | Yes | 21.8 | 19.9 | 2 | 3D50FF890DD04BDAB135C79A6845088D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Fresno | CA | 93728-1608 |  | 2013-07-17 | 2013-07-17 10:09 | 2013-07-17 10:11 | DAY & NIGHT - 7777UNK | 68 | 2.9 | Yes | Yes | 20.7 | 19.9 | 0.8 | DC1C9086E083415F85698EBD1A464849 |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Paso Robles | CA | 93446-1018 |  | 2013-08-05 | 2013-08-05 15:19 | 2013-08-05 15:42 | CARRIER - 38EA018300 | 50 | 2.3 | Yes | Yes | 21 | 23.2 | -2.2 | F70F4633800C4734885AFC6225AB5EFF |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Stockton | CA | 95205-7738 |  | 2013-07-18 | 2013-07-18 09:19 | 2013-07-18 09:39 | PAYNE - PY1PNB036060ABAA | 68 | 2.4 | Yes | Yes | 23.6 | 20.3 | 3.4 | 299382B27F00470293C3F82A1A325996 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93710-6834 |  | 2013-06-27 | 2013-06-27 16:57 | 2013-06-27 17:00 | RHEEM - RRCE-05N24JKR | 42 | 2 | Yes | Yes | 17.7 | 16.6 | 1.1 | 1B302A309B3F428D863D027C9E6B2052 |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Fresno | CA | 93704-1407 |  | 2013-06-26 | 2013-06-26 10:58 | 2013-06-26 11:13 | NORDYNE - S3QC042KA | 102 | 10.1 | Yes | Yes | 20.4 | 18.5 | 1.9 | FB15C09FCC8E495795D5CF7C40533D9A |  | R22 | Non-TXV |  | 9.902% | 0.90098 | 19.03% | [5 empty] | Non-TXV | 9.902%
Fresno | CA | 93725-4001 |  | 2013-08-06 | 2013-08-06 15:46 | 2013-08-06 15:48 | GOODMAN - GPG13360451AB | 112 | 3.8 | Yes | Yes | 23.7 | 18.5 | 5.2 | 2175698A55E34FE09515E3559C6B949E |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Chico | CA | 95973-0478 |  | 2013-08-09 | 2013-08-09 11:52 | 2013-08-09 12:20 | CARRIER - 48ESNA3606030 | 100 | -12.4 | Yes | Yes | 20.6 | 18.2 | 2.4 | EF8A2B6016564D8E8938E18CBD526F9E |  | R410A | TXV |  | -12.4% | 1.124 | 3.473% |  |  |  |  | TXV |  |  | -12.4%
Colfax | CA | 95713-9421 |  | 2013-08-27 | 2013-08-27 12:18 | 2013-08-27 12:18 | BRYANT - 561CJ036-F | 70 | 0 | Yes | Yes | 19 | 18.2 | 0.8 | 190AC9110E2046BB9735A64F89B4DB50 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6839 |  | 2013-09-24 | 2013-09-24 16:36 | 2013-09-24 17:05 | RHEEM - RRGG-05N25JKR | 39 | 8 | Yes | Yes | 25 | 20.1 | 4.9 | 0A520A1AE7F6483988EF70BD5A072735 |  | R22 | Non-TXV |  | 20.51% | 0.79487 | 39.42% | [5 empty] | Non-TXV | 20.51%
Fresno | CA | 93722-1113 |  | 2013-07-15 | 2013-07-15 08:16 | 2013-07-15 08:17 | BRYANT - 583ANW030060AAAD | 68 | 9.8 | Yes | Yes | 25.9 | 20.7 | 5.3 | DB9900366549403E858F5E44443E4750 |  | R22 | Non-TXV |  | 14.41% | 0.85588 | 27.7% | [5 empty] | Non-TXV | 14.41%
Fresno | CA | 93705-3339 |  | 2013-07-09 | 2013-07-09 10:47 | 2013-07-09 11:17 | CARRIER - N/A | 75 | 2.5 | Yes | Yes | 19.1 | 19.8 | -0.7 | D8CFD4C9052241078C5F7CCBDE532259 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93726-2129 |  | 2013-08-20 | 2013-08-20 14:23 | 2013-08-20 14:40 | YORK - DAYAF36NO90C | 67 | 5.4 | Yes | Yes | 21.1 | 20.7 | 0.5 | 728280F7322F43F1B054C020894E51DD |  | R22 | Non-TXV |  | 8.06% | 0.9194 | 15.49% | [5 empty] | Non-TXV | 8.06%
Kerman | CA | 93630-9354 |  | 2013-08-01 | 2013-08-01 12:04 | 2013-08-01 12:13 | LENNOX - 13ACC04823001 | 158 | 17.9 | Yes | Yes | 20.7 | 21 | -0.3 | 519490F2AF554292A43E09C658D0F3C1 |  | R22 | Non-TXV |  | 11.33% | 0.88671 | 21.77% | [5 empty] | Non-TXV | 11.33%
Cool | CA | 95614-2142 |  | 2013-09-13 | 2013-09-13 09:27 | 2013-09-13 09:27 | DAY & NIGHT - 542BJ024 | 100 | 0 | Yes | Yes | 20.5 | 20.1 | 0.4 | B13E5BECB4384F1E9CD0F970E81888AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Firebaugh | CA | 93622-4403 |  | 2013-08-13 | 2013-08-13 23:45 | 2013-08-14 00:06 | OTHER - GSX1303618A | 89 | 2.7 | Yes | Yes | 16.6 | 19.6 | -3 | A72C6154981B47AB8362B02F5C563F60 |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Stockton | CA | 95210-3248 |  | 2013-07-08 | 2013-07-08 09:34 | 2013-07-08 09:52 | PAYNE - 585B024050YACR | 51 | -3 | Yes | Yes | 17.5 | 18.8 | -1.3 | 68B60A4287EA402F8C906B20AB74DB38 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Merced | CA | 95341-6971 |  | 2013-08-08 | 2013-08-08 11:17 | 2013-08-08 11:37 | RHEEM - RRGG-05N24JKR | 42 | 1.8 | Yes | Yes | 15.2 | 17.7 | -2.5 | 37A03323D13248F4B4357EDC1DEE7937 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Chowchilla | CA | 93610-8989 |  | 2013-08-22 | 2013-08-22 01:00 | 2013-08-22 01:49 | - | 85 | 5.2 | Yes | Yes | 24.9 | 20.7 | 4.2 | 0BF73629C2324EA384DBC01A06AB6FC1 |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Merced | CA | 95340-2318 |  | 2013-06-28 | 2013-06-28 17:34 | 2013-06-28 17:36 | PAYNE - PY3PNA036060NA | 167 | 5 | Yes | Yes | 23.9 | 19.3 | 4.6 | AFB792E7FE29413F926CCBE71B151FC5 |  | R22 | Non-TXV |  | 2.994% | 0.97006 | 5.754% | [5 empty] | Non-TXV | 2.994%
Manteca | CA | 95337-7314 |  | 2013-07-19 | 2013-07-19 17:05 | 2013-07-19 17:24 | DAY & NIGHT - 565BJ024-A | 70 | 3.4 | Yes | Yes | 19.2 | 19.3 | -0.1 | 12A1A29EDACD4ADBB7977A9A1F836573 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Stockton | CA | 95209-4193 |  | 2013-07-12 | 2013-07-12 12:49 | 2013-07-12 13:06 | YORK - AC036X1222A | 83 | 4 | Yes | Yes | 20.5 | 19.1 | 1.4 | 4DF505551C8B496287E9598988D6B276 |  | R22 | Non-TXV |  | 4.819% | 0.95181 | 9.262% | [5 empty] | Non-TXV | 4.819%
Firebaugh | CA | 93622-0000 |  | 2013-09-18 | 2013-09-18 08:19 | 2013-09-18 08:21 | OTHER - UNK | 76 | 4.1 | Yes | Yes | 21.4 | 16.5 | 4.9 | 44447E122123435393403BD97B18B7BA |  | R22 | Non-TXV |  | 5.395% | 0.94605 | 10.37% | [5 empty] | Non-TXV | 5.395%
Fresno | CA | 93705-4966 |  | 2013-07-11 | 2013-07-11 12:04 | 2013-07-11 12:40 | GOODMAN - GPG | 60 | 2.3 | Yes | Yes | 17.5 | 20.4 | -2.9 | 09EF9605B0344F2CA966CBB70E7A1807 |  | R410A | TXV |  | 3.833% | 0.96167 | 7.367% | [5 empty] | TXV | 3.833%
Colfax | CA | 95713-9574 |  | 2013-08-27 | 2013-08-27 11:25 | 2013-08-27 11:42 | AMANA - SPCG420901A | 119 | 9.6 | Yes | Yes | 20 | 20.6 | -0.6 | 2580F7A0CE18477CBD47CBCC82E79EE9 |  | R22 | Non-TXV |  | 8.067% | 0.91933 | 15.5% | [5 empty] | Non-TXV | 8.067%
Magalia | CA | 95954-9670 |  | 2013-07-19 | 2013-07-19 13:23 | 2013-07-19 13:42 | RHEEM - RA036J0ASDD | 80 | 13.4 | Yes | Yes | 17.4 | 19.9 | -2.5 | 8F04684C15AE4E5AB4FE805EA1ED2D5E |  | R22 | Non-TXV |  | 16.75% | 0.8325 | 32.19% | [5 empty] | Non-TXV | 16.75%
Merced | CA | 95340-4159 |  | 2013-06-28 | 2013-06-28 14:57 | 2013-06-28 14:59 | TRANE - YCX060F1MOBA | 168 | 5.1 | Yes | Yes | 19.2 | 15.6 | 3.6 | 57BAF4A4B49341BE83A96CE5FABEAF43 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Fresno | CA | 93703-4360 |  | 2013-08-08 | 2013-08-08 14:45 | 2013-08-08 14:46 | YORK - D2NP024N03606A | 100 | 14.6 | Yes | Yes | 19.6 | 17.4 | 2.2 | 702AE1484087480185164CA278A42F48 |  | R22 | Non-TXV |  | 14.6% | 0.854 | 28.06% | [5 empty] | Non-TXV | 14.6%
Kerman | CA | 93630-9354 |  | 2013-08-01 | 2013-08-01 12:39 | 2013-08-01 12:41 | LENNOX - 13ACC03623001 | 115 | 20.5 | Yes | Yes | 22.6 | 22.5 | 0.1 | 6A9A346FE5774A599AFF47AD98710398 |  | R22 | Non-TXV |  | 17.83% | 0.82174 | 34.26% | [5 empty] | Non-TXV | 17.83%
Stockton | CA | 95215-5909 |  | 2013-09-04 | 2013-09-04 10:47 | 2013-09-04 11:12 | UNITARY PRODUCTS GROUP - BRCQ0421BD | 66 | 2.2 | Yes | Yes | 18.5 | 17.7 | 0.8 | 4E6D6B76D89748EDAFA230CAD3E53199 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95210-6756 |  | 2013-07-11 | 2013-07-11 12:09 | 2013-07-11 12:27 | BDP - 561CJ030-C | 76 | -4.5 | Yes | Yes | 24.1 | 19.7 | 4.4 | 9D56AF91BBC64146B8A2B0E2B3DC066A |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Fresno | CA | 93704-1811 |  | 2013-08-17 | 2013-08-17 10:58 | 2013-08-17 11:31 | RHEEM - RRPL-B048JK10X | 161 | 5.9 | Yes | Yes | 17.3 | 19.8 | -2.5 | AD5B8E3A2F114899A11D3686982F84F4 | OK: Verified Refrigerant Charge Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 3.665% | 0.96335 | 7.043% | [5 empty] | TXV | 3.665%
Fresno | CA | 93705-3611 |  | 2013-07-09 | 2013-07-09 14:07 | 2013-07-09 14:35 | CARRIER - KLA124-321BE | 68 | 8.6 | Yes | Yes | 18.9 | 18.5 | 0.4 | 725368E6600F4CC4AAB401EB27E6173B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.65% | 0.87353 | 24.3% | [5 empty] | Non-TXV | 12.65%
Stockton | CA | 95207-7779 |  | 2013-06-26 | 2013-06-26 12:22 | 2013-06-26 12:39 | DAY & NIGHT - 565AJ018 | 50 | 7.1 | Yes | Yes | 20.1 | 19.6 | 0.5 | D29E0165CD01483FBA99513FD4CAA0FD |  | R22 | Non-TXV |  | 14.2% | 0.858 | 27.29% | [5 empty] | Non-TXV | 14.2%
Los Banos | CA | 93635-3171 |  | 2013-07-08 | 2013-07-08 12:08 | 2013-07-08 12:23 | RUUD - UAKA030JAS | 68 | 14.4 | Yes | Yes | 20.2 | 20.9 | -0.7 | 082A82D80E334EEBAC8F28B435D31FE9 |  | R22 | Non-TXV |  | 21.18% | 0.78824 | 40.7% | [5 empty] | Non-TXV | 21.18%
Fresno | CA | 93722-6810 |  | 2013-08-08 | 2013-08-08 14:51 | 2013-08-08 14:53 | CARRIER - 7777UHK | 114 | 4.1 | Yes | Yes | 18.7 | 19.8 | -1.1 | E2CA1D59D92F4B48A8851453DA901489 |  | R22 | Non-TXV |  | 3.596% | 0.96404 | 6.912% | [5 empty] | Non-TXV | 3.596%
Stockton | CA | 95202-1248 |  | 2013-08-28 | 2013-08-28 13:30 | 2013-08-28 13:54 | CARRIER - N2A348AKA200 | 119 | 6.2 | Yes | Yes | 23 | 18.2 | 4.8 | 1AE20F5B58254725B22F971A7198E08C |  | R22 | TXV |  | 5.21% | 0.9479 | 10.01% | [5 empty] | TXV | 5.21%
Los Banos | CA | 93635-9427 |  | 2013-07-12 | 2013-07-12 12:26 | 2013-07-12 12:42 | GOODMAN - CKJ361AB | 90 | 13.3 | Yes | Yes | 18.9 | 20.8 | -1.9 | BAB0B8CD5A1F4FF7BB683C3F77F98567 |  | R22 | Non-TXV |  | 14.78% | 0.85222 | 28.4% | [5 empty] | Non-TXV | 14.78%
Paso Robles | CA | 93446-1077 |  | 2013-08-09 | 2013-08-09 10:41 | 2013-08-09 11:15 | DAY & NIGHT - UNK | 57 | 2.3 | Yes | Yes | 17.6 | 17.4 | 0.3 | 6D01EB25C51147D09DAE589FA6B30846 |  | R22 | Non-TXV |  | 4.035% | 0.95965 | 7.755% | [5 empty] | Non-TXV | 4.035%
Paso Robles | CA | 93446-1077 |  | 2013-08-05 | 2013-08-05 12:28 | 2013-08-05 12:46 | GUARDIAN - GCGD24S41S3A | 61 | 2.8 | Yes | Yes | 19.3 | 18.8 | 0.5 | 450500FB930A436FAD183111CF54798A |  | R410A | Non-TXV |  | 4.59% | 0.9541 | 8.821% | [5 empty] | Non-TXV | 4.59%
Los Banos | CA | 93635-7411 |  | 2013-07-12 | 2013-07-12 11:41 | 2013-07-12 12:03 | NORDYNE - JS5BD036K | 138 | 15.8 | Yes | Yes | 13.9 | 15.5 | -1.6 | 3989784396AE4043A9EC40F3448ADDEC |  | R22 | Non-TXV |  | 11.45% | 0.88551 | 22% | [5 empty] | Non-TXV | 11.45%
Fresno | CA | 93722-4102 |  | 2013-07-16 | 2013-07-16 11:27 | 2013-07-16 11:28 | GOODMAN - GPG036075 | 60 | 9.2 | Yes | Yes | 24.8 | 19.7 | 5.2 | E50E40E9B672470B8F9104CF6E141A3C |  | R22 | Non-TXV |  | 15.33% | 0.84667 | 29.47% | [5 empty] | Non-TXV | 15.33%
Pioneer | CA | 95666-9566 |  | 2013-09-10 | 2013-09-10 10:07 | 2013-09-10 10:33 | BRYANT - 583ANW036090AAHF | 82 | 5.4 | Yes | Yes | 23.7 | 21.5 | 2.2 | 215D758D7A6C46DDB751EFA7688A4941 |  | R22 | Non-TXV |  | 6.585% | 0.93415 | 12.66% | [5 empty] | Non-TXV | 6.585%
Fresno | CA | 93710-7033 |  | 2013-06-27 | 2013-06-27 13:34 | 2013-06-27 13:37 | GOODMAN - GPG10480901A | 98 | 3.4 | Yes | Yes | 26.6 | 20.9 | 5.8 | FE18CB1A6C554FC4A8C9C1FC982A658E |  | R22 | Non-TXV |  | 3.469% | 0.96531 | 6.667% | [5 empty] | Non-TXV | 3.469%
Magalia | CA | 95954-9413 |  | 2013-08-29 | 2013-08-29 10:29 | 2013-08-29 11:02 | COLEMAN - 9536-901 | 56 | 4.3 | Yes | Yes | 18.2 | 21 | -2.8 | 5B39D44687EB4FF78FB208AB610A0E73 |  | R22 | Non-TXV |  | 7.679% | 0.92321 | 14.76% | [5 empty] | Non-TXV | 7.679%
Selma | CA | 93662-2703 |  | 2013-09-05 | 2013-09-05 13:19 | 2013-09-05 14:17 | GOODMAN - PGB036075-1 | 60 | 3.5 | Yes | Yes | 19.1 | 19.8 | -0.7 | F8330CB6487B41C6B9B8753712843DB3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Pinedale | CA | 93650-1137 |  | 2013-08-15 | 2013-08-15 13:40 | 2013-08-15 13:41 | OTHER - TCGD3621S1A | 65 | 3.6 | Yes | Yes | 21.7 | 22 | -0.3 | D438B20D2AA3407AA16CFD317A196D0B |  | R22 | Non-TXV |  | 5.538% | 0.94462 | 10.64% | [5 empty] | Non-TXV | 5.538%
Lincoln | CA | 95648-2827 |  | 2013-07-06 | 2013-07-06 09:08 | 2013-07-06 09:30 | YORK - AC036X1221A | 98 | 7.4 | Yes | Yes | 16.5 | 18.5 | -2 | 950FD473CB1D480C999E2C1FFB4FBB75 |  | R22 | TXV |  | 7.551% | 0.92449 | 14.51% | [5 empty] | TXV | 7.551%
Copperopolis | CA | 95228-9359 |  | 2013-08-01 | 2013-08-01 16:35 | 2013-08-01 16:53 | CARRIER - 38BRC036350 | 103 | 18.8 | Yes | Yes | 18 | 21 | -3 | 82BF8AFA53904806929E5DDFAAA919B2 |  | R22 | TXV |  | 18.25% | 0.81748 | 35.08% | [5 empty] | TXV | 18.25%
Stockton | CA | 95206-2108 |  | 2013-07-25 | 2013-07-25 12:15 | 2013-07-25 12:38 | GOODMAN - GSC130301AA | 123 | 5.6 | Yes | Yes | 20.6 | 19.6 | 1 | 1D9FD106231142AEB0206A5ADDE9B570 |  | R22 | Non-TXV |  | 4.553% | 0.95447 | 8.75% | [5 empty] | Non-TXV | 4.553%
Stockton | CA | 95205-3432 |  | 2013-07-17 | 2013-07-17 09:41 | 2013-07-17 10:06 | YORK - D1H036N05606C | 124 | 11.1 | Yes | Yes | 22.5 | 19.3 | 3.2 | 599FDEA37C5A46A393ADF16EE913F1EA |  | R22 | Non-TXV |  | 8.952% | 0.91048 | 17.2% | [5 empty] | Non-TXV | 8.952%
Chico | CA | 95973-0743 |  | 2013-07-16 | 2013-07-16 01:15 | 2013-07-16 13:36 | COLEMAN - 9536-901 | 88 | 5.7 | Yes | Yes | 20.8 | 20.4 | 0.4 | 2E556D95CB444E25AC2AF840541A6DF3 |  | R22 | Non-TXV |  | 6.477% | 0.93523 | 12.45% | [5 empty] | Non-TXV | 6.477%
Stockton | CA | 95212-2912 |  | 2013-06-26 | 2013-06-26 14:58 | 2013-06-26 15:22 | AMANA - UNK | 80 | 2.4 | Yes | Yes | 20 | 18.3 | 1.7 | C14D97D1C97C4916861B17B837058A32 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93704-2636 |  | 2013-07-23 | 2013-07-23 10:51 | 2013-07-23 10:52 | TRANE - YCP060F1MOAB | 160 | 20.1 | Yes | Yes | 24.1 | 20.9 | 3.2 | 4BBC617337BA43A3A77F0FC1C1C3AA3D |  | R22 | Non-TXV |  | 12.56% | 0.87438 | 24.14% | [5 empty] | Non-TXV | 12.56%
Fresno | CA | 93704-2636 |  | 2013-07-23 | 2013-07-23 11:06 | 2013-07-23 11:09 | TRANE - YCP060F1MOAB | 160 | 20.1 | Yes | Yes | 20.3 | 19.4 | 0.9 | 1C98E510E5E6452197F35FC99819F2B0 |  | R22 | Non-TXV |  | 12.56% | 0.87438 | 24.14% | [5 empty] | Non-TXV | 12.56%
Colfax | CA | 95713-0000 |  | 2013-10-18 | 2013-10-18 11:30 | 2013-10-18 11:30 | TRANE - TTP042C100A4 | 147 | 0 | Yes | Yes | 26.1 | 20.9 | 5.2 | 96417414C2644A3E96352D583F8B12F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-5270 |  | 2013-07-30 | 2013-07-30 09:56 | 2013-07-30 10:22 | BDP - 567024R00 | 60 | -5.6 | Yes | Yes | 25.3 | 19.4 | 5.9 | 781BF1CEF55F4FCFAD82B562F097A5BC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Los Banos | CA | 93635-8563 |  | 2013-07-30 | 2013-07-30 11:51 | 2013-07-30 12:08 | AMERICAN STANDARD - 2A7B0042A1000AA | 95 | 7.5 | Yes | Yes | 16.5 | 18.9 | -2.4 | 18727B9FE2674ECEBCDC6AF77B5A5B5E |  | R22 | Non-TXV |  | 7.895% | 0.92105 | 15.17% | [5 empty] | Non-TXV | 7.895%
Stockton | CA | 95206-4778 |  | 2013-07-11 | 2013-07-11 10:06 | 2013-07-11 10:06 | RHEEM - RAKA-036JAS | 75 | 0 | Yes | Yes | 21.1 | 19.1 | 2 | 5C85D3DF556D470084CEC9F0A6CFEDCC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Ione | CA | 95640-9578 |  | 2013-08-02 | 2013-08-02 14:34 | 2013-08-02 14:53 | OTHER - S30A-036KA | 69 | 3.2 | Yes | Yes | 22 | 21 | 1 | 665F36D20CF9464CAF3049283266CC8B |  | R22 | Non-TXV |  | 4.638% | 0.95362 | 8.913% | [5 empty] | Non-TXV | 4.638%
Tracy | CA | 95376-2066 |  | 2013-07-16 | 2013-07-16 11:29 | 2013-07-16 11:53 | BRYANT - 561CJ048-A | 159 | 6.8 | Yes | Yes | 21.4 | 19.4 | 2 | 2FE1089721064207A57776C4F94B299C |  | R22 | Non-TXV |  | 4.277% | 0.95723 | 8.219% | [5 empty] | Non-TXV | 4.277%
Stockton | CA | 95215-5118 |  | 2013-06-28 | 2013-06-28 10:34 | 2013-06-28 11:07 | WEATHER KING - WEMA-A036JK06E | 85 | 4.4 | Yes | Yes | 12.2 | 11.2 | 1 | 03C79EC34A7A4232B9CB3134F736C176 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Merced | CA | 95340-3430 |  | 2013-06-28 | 2013-06-28 15:06 | 2013-06-28 15:14 | YORK - 03GH036N07006A | 112 | 17.6 | Yes | Yes | 21.1 | 21.3 | -0.2 | EA44C95124C34BC6B64B39F8855784B2 |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Copperopolis | CA | 95228-9415 |  | 2013-08-29 | 2013-08-29 09:44 | 2013-08-29 10:02 | HEIL - CA5542VKA1 | 138 | 5.2 | Yes | Yes | 21 | 20.9 | 0.1 | 39AEBDA34DA64015BABF612B79D0F1F1 |  |  |  |  | 3.768% | 0.96232 | 7.241% | [5 empty] | 0 | 3.768%
Chico | CA | 95926-2931 |  | 2013-07-10 | 2013-07-10 18:41 | 2013-07-10 18:59 | PAYNE - 1008X61191 | 159 | 8 | Yes | Yes | 20 | 19 | 1 | 5506277BFFB643B5B418DDA7A4BDF2CD |  | R22 | Non-TXV |  | 5.031% | 0.94969 | 9.669% | [5 empty] | Non-TXV | 5.031%
Kingsburg | CA | 93631-2302 |  | 2013-08-08 | 2013-08-08 22:17 | 2013-08-08 22:35 | CARRIER - 48XPN036090311 | 149 | 5.4 | Yes | Yes | 18 | 20.2 | -2.2 | 86B26A67C04B49799ED800A5DE08D22A |  | R410A | TXV |  | 3.624% | 0.96376 | 6.965% | [5 empty] | TXV | 3.624%
Auburn | CA | 95602-7839 |  | 2013-06-27 | 2013-06-27 13:54 | 2013-06-27 13:54 | AMERICAN STANDARD - YCC030F1A0BC | 72 | 0 | Yes | Yes | 21.8 | 19.6 | 2.2 | C04248D279564E50963A8E39C9D64FE4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-7112 |  | 2013-08-15 | 2013-08-15 12:55 | 2013-08-15 13:16 | GOODMAN - GSC130361BA | 125 | 10.8 | Yes | Yes | 24.2 | 19.2 | 5 | 0C3D252C3F2D4351AF92211B19AB46E2 |  | R22 | Non-TXV |  | 8.64% | 0.9136 | 16.6% | [5 empty] | Non-TXV | 8.64%
Chico | CA | 95926-4807 |  | 2013-08-28 | 2013-08-28 16:48 | 2013-08-28 17:07 | DAY & NIGHT - UNK | 50 | -2.9 | Yes | Yes | 21.2 | 19.6 | 1.6 | E20EC21FC9304B3F95EC0B58FDDB1780 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Lathrop | CA | 95330-9703 |  | 2013-07-24 | 2013-07-24 08:41 | 2013-07-24 09:04 | RUUD - UANNL-42JAZ | 130 | 10 | Yes | Yes | 21.9 | 19.6 | 2.3 | 093205DCB71B497F862261D213F51630 |  | R410A | Non-TXV |  | 7.692% | 0.92308 | 14.78% | [5 empty] | Non-TXV | 7.692%
Sanger | CA | 93657-3413 |  | 2013-07-23 | 2013-07-23 10:36 | 2013-07-23 10:54 | PAYNE - PYG3NAA24040NA | 72 | 2.9 | Yes | Yes | 17.1 | 20.1 | -3 | 274BBC97A34F4CB5AD46DD9D97D28962 |  | R410A | TXV |  | 4.028% | 0.95972 | 7.741% | [5 empty] | TXV | 4.028%
Oakdale | CA | 95361-3117 |  | 2013-07-10 | 2013-07-10 10:18 | 2013-07-10 10:39 | PAYNE - PY3GNAA24060NA | 72 | 3 | Yes | Yes | 20.4 | 19.9 | 0.5 | A26405A72FF04FA5B0EE52420E6E135A |  | R410A | TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | TXV | 4.167%
Stockton | CA | 95206-2929 |  | 2013-07-13 | 2013-07-13 13:02 | 2013-07-13 13:36 | BDP - 585CJ02450 | 72 | 8.1 | Yes | Yes | 26.6 | 21 | 5.6 | C3727F846487442788E741D4E35D22F2 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Copperopolis | CA | 95228-9617 |  | 2013-08-13 | 2013-08-13 08:28 | 2013-08-13 08:51 | CARRIER - 48SX-042060331AA | 87 | 3.4 | Yes | Yes | 25.7 | 19.9 | 5.8 | ABD267B19258478B9083B9ACF68ACD5B |  | R22 | Non-TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | Non-TXV | 3.908%
Colfax | CA | 95713-9634 |  | 2013-09-03 | 2013-09-03 08:25 | 2013-09-03 08:50 | RUUD - URKA-A036JK06E | 62 | 1.9 | Yes | Yes | 16 | 17.7 | -1.7 | 347B0672A351456F84226A3A735F97CA |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Kerman | CA | 93630-1210 |  | 2013-08-01 | 2013-08-01 13:01 | 2013-08-01 13:03 | DAY & NIGHT - UNK | 68 | 9.7 | Yes | Yes | 22.1 | 19.3 | 2.8 | 49262344591148BDA6FE4CFC151A4940 |  | R22 | Non-TXV |  | 14.26% | 0.85735 | 27.41% | [5 empty] | Non-TXV | 14.26%
Fresno | CA | 93725-1421 |  | 2013-07-22 | 2013-07-22 12:06 | 2013-07-22 12:08 | OTHER - DCYZ-F030N070C | 64 | 2.6 | Yes | Yes | 19.3 | 20.4 | -1.1 | 78A7E34240234279BB22A8A6384AE348 |  | R410A | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Fresno | CA | 93726-1156 |  | 2013-07-26 | 2013-07-26 12:03 | 2013-07-26 12:04 | BDP - 567C030RCU | 63 | 11.4 | Yes | Yes | 22.3 | 23.1 | -0.8 | DF56E7F617734230A31720370727F681 |  | R22 | Non-TXV |  | 18.1% | 0.81905 | 34.78% | [5 empty] | Non-TXV | 18.1%
Fresno | CA | 93726-1156 |  | 2013-07-26 | 2013-07-26 12:12 | 2013-07-26 12:13 | BDP - 567C030RCU | 63 | 12.1 | Yes | Yes | 16.1 | 18.3 | -2.2 | FCEF79C20A434FDBA6D2390CD1D8EA26 |  | R22 | Non-TXV |  | 19.21% | 0.80794 | 36.91% | [5 empty] | Non-TXV | 19.21%
Fresno | CA | 93726-3420 |  | 2013-08-07 | 2013-08-07 16:29 | 2013-08-07 16:31 | YORK - D1NP042N09006A | 150 | 4.4 | Yes | Yes | 23.3 | 21.3 | 2 | 6293D46141BE4F59AC927CF828615C29 |  | R22 | Non-TXV |  | 2.933% | 0.97067 | 5.637% | [5 empty] | Non-TXV | 2.933%
Copperopolis | CA | 95228-9549 |  | 2013-08-01 | 2013-08-01 13:23 | 2013-08-01 13:57 | LENNOX - HS18-511-4P | 126 | 20.5 | Yes | Yes | 30.5 | 24.7 | 5.8 | F88D16B8375C468CB2A4F58EFDEECEC9 |  | R22 | TXV |  | 16.27% | 0.8373 | 31.27% | [5 empty] | TXV | 16.27%
Mendota | CA | 93640-2074 |  | 2013-08-13 | 2013-08-13 11:45 | 2013-08-13 12:30 | AMERICAN STANDARD - 4A7B036D1000AA | 105 | 4.9 | Yes | Yes | 18.5 | 20.7 | -2.2 | 9FB8F5325D42474D94B42B654A0870C8 |  | R410A | TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | TXV | 4.667%
Madera | CA | 93637-8819 |  | 2013-07-08 | 2013-07-08 10:39 | 2013-07-08 14:18 | LENNOX - 10GCS042X-75 | 85 | 4.2 | Yes | Yes | 16 | 18.5 | -2.5 | 5D57D182F4E240DAAAE3C8DE4DFCF816 |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Fresno | CA | 93703-2664 |  | 2013-07-03 | 2013-07-03 15:20 | 2013-07-03 16:03 | BDP - 24-YAC60-108C | 53 | 2.9 | Yes | Yes | 26.9 | 21.9 | 5 | A3D370B6F158454385ED52911644D80E |  | R22 | Non-TXV |  | 5.472% | 0.94528 | 10.52% | [5 empty] | Non-TXV | 5.472%
Manteca | CA | 95336-4564 |  | 2013-07-30 | 2013-07-30 13:10 | 2013-07-30 13:32 | GOODMAN - CKL18-1 | 53 | 1.7 | Yes | Yes | 16.6 | 18 | -1.4 | 1E1738F81B7D4A4380DF3043C2FAB2F9 |  | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Copperopolis | CA | 95228-9515 |  | 2013-08-01 | 2013-08-01 15:45 | 2013-08-01 16:08 | ICP - GPCM048KO8OD | 85 | 5 | Yes | Yes | 19.6 | 22.6 | -3 | F7B05EB0B74F45FAB2DB43B85D6B75B7 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Kerman | CA | 93630-0000 |  | 2013-07-31 | 2013-07-31 09:15 | 2013-07-31 09:16 | AMERICAN STANDARD - 2YCC3036A1064AA | 82 | 10 | Yes | Yes | 19 | 18.2 | 0.8 | EE1ECE066122403D8C5450E2954C88F5 |  | R22 | Non-TXV |  | 12.2% | 0.87805 | 23.44% | [5 empty] | Non-TXV | 12.2%
Stockton | CA | 95207-1422 |  | 2013-07-26 | 2013-07-26 12:54 | 2013-07-26 13:28 | PAYNE - PY1PNB04209AAAA | 100 | -9.4 | Yes | Yes | 21.5 | 21.3 | 0.2 | 98412664D3E74D03B4B48A5413F6C179 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.4%
Fresno | CA | 93726-0881 |  | 2013-07-26 | 2013-07-26 10:47 | 2013-07-26 10:49 | PAYNE - 3080YAC | 65 | 11.1 | Yes | Yes | 19.4 | 20.4 | -1 | 4BC38240DB4A4D1782A30215F6426FAE |  | R22 | Non-TXV |  | 17.08% | 0.82923 | 32.82% | [5 empty] | Non-TXV | 17.08%
Kerman | CA | 93630-9208 |  | 2013-08-01 | 2013-08-01 10:06 | 2013-08-01 10:08 | TRANE - 2WCC3042A1000AA | 122 | 13.9 | Yes | Yes | 21 | 18.8 | 2.2 | B68FB918E17D454198DEDA0BDF49FBB9 |  | R22 | Non-TXV |  | 11.39% | 0.88607 | 21.9% | [5 empty] | Non-TXV | 11.39%
Magalia | CA | 95954-9323 |  | 2013-08-30 | 2013-08-30 08:54 | 2013-08-30 08:54 | GOODMAN - GPG13300701AB | 77 | 0 | Yes | Yes | 27.9 | 22.3 | 5.6 | 799939A58522467C998B181395B19EF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-5200 |  | 2013-07-02 | 2013-07-02 18:28 | 2013-07-02 18:46 | PAYNE - 56EJX042000AGAA | 150 | 9.8 | Yes | Yes | 25.3 | 23.9 | 1.4 | 56BD72B9837541EC8DCEE5EBED5B7499 |  | R22 | Non-TXV |  | 6.533% | 0.93467 | 12.56% | [5 empty] | Non-TXV | 6.533%
Atwater | CA | 95301-4829 |  | 2013-07-29 | 2013-07-29 17:22 | 2013-07-29 17:33 | BDP - 598WN036 | 184 | 20.2 | Yes | Yes | 19 | 18.6 | 0.4 | 530D0F6AC23E468D84146005493DBB7F |  | R22 | Non-TXV |  | 10.98% | 0.89022 | 21.1% | [5 empty] | Non-TXV | 10.98%
Ripon | CA | 95366-2810 |  | 2013-10-16 | 2013-10-16 15:48 | 2013-10-16 16:22 | BRYANT - 58ANW024060AADA | 53 | 1.6 | Yes | Yes | 21.8 | 20.7 | 1.1 | 7113CCCD403846DB89444CFACB31CFE7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Kerman | CA | 93630-0000 |  | 2013-07-31 | 2013-07-31 10:39 | 2013-07-31 10:40 | YORK - BRCS0361BD | 63 | 9.7 | Yes | Yes | 18.5 | 16.8 | 1.7 | 3C66D0B3E782484EB793AA1CFBAA50DC |  | R22 | Non-TXV |  | 15.4% | 0.84603 | 29.59% | [5 empty] | Non-TXV | 15.4%
Clovis | CA | 93612-1988 |  | 2013-06-28 | 2013-06-28 13:33 | 2013-06-28 13:55 | GOODMAN - GPG13420701AB | 107 | 3.1 | Yes | Yes | 20.1 | 20.1 | 0 | D5E2D35354A04D6DB0930662F55586BD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.897% | 0.97103 | 5.568% | [5 empty] | Non-TXV | 2.897%
Copperopolis | CA | 95228-9712 |  | 2013-08-13 | 2013-08-13 11:40 | 2013-08-13 12:01 | PAYNE - PA13NR060-C | 85 | 10.3 | Yes | Yes | 26.5 | 20.8 | 5.7 | 365DEAA5FD8544DAA008B7188C313D46 |  | R22 | TXV |  | 12.12% | 0.87882 | 23.29% | [5 empty] | TXV | 12.12%
Clovis | CA | 93612-1983 |  | 2013-06-28 | 2013-06-28 13:00 | 2013-06-28 13:31 | LENNOX - 12GCS036X-75-3PB | 110 | 6 | Yes | Yes | 25.4 | 20.9 | 4.5 | 43A0F5F70A9E4C319CB9F04A2428727C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Riverbank | CA | 95367-3317 |  | 2013-07-12 | 2013-07-12 13:52 | 2013-07-12 14:16 | COPELAND - 598AN036-B | 180 | 6.8 | Yes | Yes | 24.1 | 20.6 | 3.5 | 4D0B74B7A72B44FE96E5B541787C3591 |  | R22 | TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | TXV | 3.778%
Stockton | CA | 95206-3533 |  | 2013-07-16 | 2013-07-16 11:00 | 2013-07-16 11:00 | PAYNE - PA12NA030-H | 96 | 0 | Yes | Yes | 18.6 | 19.6 | -1 | DB2E3006A37B4B3292184E113D3B8426 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-8882 |  | 2013-07-24 | 2013-07-24 08:26 | 2013-07-24 08:26 | DAY & NIGHT - PGD348090K0014 | 100 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | 4346916778614FF993965D629EEF525C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Copperopolis | CA | 95228-9567 |  | 2013-08-22 | 2013-08-22 16:17 | 2013-08-22 16:36 | YORK - D1NA036NO5606C | 67 | 4.6 | Yes | Yes | 21.8 | 21.5 | 0.3 | 177225328953416BA0FCD99837002760 |  | R22 | Non-TXV |  | 6.866% | 0.93134 | 13.19% | [5 empty] | Non-TXV | 6.866%
Kerman | CA | 93630-9631 |  | 2013-09-12 | 2013-09-12 11:26 | 2013-09-12 11:39 | BDP - 597AN048A | 178 | 14.6 | Yes | Yes | 21.6 | 19.9 | 1.7 | D6CAC5C557F040D09677E7E4297402D0 |  | R22 | Non-TXV |  | 8.202% | 0.91798 | 15.76% | [5 empty] | Non-TXV | 8.202%
Clovis | CA | 93612-5019 |  | 2013-07-02 | 2013-07-02 14:04 | 2013-07-02 16:46 | GOODMAN - GPG1236070AB | 85 | -7 | Yes | Yes | 21.6 | 18.8 | 2.8 | 957E06DC597342B398A1E4DBCE227CA4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Yuba City | CA | 95991-9103 |  | 2013-07-16 | 2013-07-16 10:57 | 2013-07-16 11:23 | YORK - H1RA042S06D | 84 | -7 | Yes | Yes | 18 | 18.2 | -0.2 | BFF0419951014444B1015C904224790B |  | R22 | TXV |  | -8.333% | 1.0833 | 2.334% |  |  |  |  | TXV |  |  | -8.333%
Copperopolis | CA | 95228-9342 |  | 2013-08-01 | 2013-08-01 12:18 | 2013-08-01 12:48 | GOODMAN - CKL36-1L | 84 | 6.3 | Yes | Yes | 21.3 | 22.1 | -0.8 | 647FB6B665CB46B383C5B3404335AC46 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Fresno | CA | 93728-3425 |  | 2013-07-15 | 2013-07-15 13:44 | 2013-07-15 13:48 | CARRIER - 38CKB060300 | 157 | 5.4 | Yes | Yes | 21.2 | 21.5 | -0.3 | 6DB2D203687B47A3BC6C5B8804F48014 |  | R22 | Non-TXV |  | 3.439% | 0.96561 | 6.61% | [5 empty] | Non-TXV | 3.439%
Oakdale | CA | 95361-2715 |  | 2013-07-10 | 2013-07-10 10:52 | 2013-07-10 11:14 | GOODMAN - VSC130361AA | 119 | 3.6 | Yes | Yes | 19.7 | 21.3 | -1.6 | F6E76ECA6B5B4FA7A97234FA37B52A30 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.025% | 0.96975 | 5.814% | [5 empty] | Non-TXV | 3.025%
Stockton | CA | 95215-7328 |  | 2013-07-01 | 2013-07-01 12:03 | 2013-07-01 12:18 | LENNOX - GCS26X-030-75-2PA | 85 | 2.6 | Yes | Yes | 19.8 | 15 | 4.8 | 3D4F1EFA379C4527A09161DCC038BFAC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93705-3613 |  | 2013-07-10 | 2013-07-10 11:22 | 2013-07-10 11:39 | YORK - D1NA024N03606C | 54 | 2.3 | Yes | Yes | 18.9 | 17.3 | 1.7 | EDE05B7C02B248C69BF96E127D047505 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Nevada City | CA | 95959-8718 |  | 2013-08-07 | 2013-08-07 10:46 | 2013-08-07 10:46 | GOODMAN - CJ42-1C | 92 | 0 | Yes | Yes | 19.9 | 19.1 | 0.8 | EEAEAECAFA594BFFA1E9EE8593FE9295 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-9607 |  | 2013-06-27 | 2013-06-27 12:37 | 2013-06-27 12:37 | CARRIER - 4855-060120331-- | 112 | 0 | Yes | Yes | 18 | 17.2 | 0.8 | D4F21DF9D96F4E6684C520C667C7770E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-0000 |  | 2013-07-17 | 2013-07-17 03:09 | 2013-07-17 03:09 | SINGER - 48SDN030040311 | 97 | 0 | Yes | Yes | 19.6 | 20.1 | -0.5 | 1F731BE66C6347DF8A82CEF234286B7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-4107 |  | 2013-08-08 | 2013-08-08 12:33 | 2013-08-08 13:23 | LENNOX - 12GCS030-75-3PA | 85 | 5.8 | Yes | Yes | 16.8 | 19.5 | -2.7 | C04FB611D6C140A68156C08FBDF1AC20 |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Stockton | CA | 95210-1704 |  | 2013-08-02 | 2013-08-02 14:36 | 2013-08-02 14:58 | RHEEM - URMAA036JK06E | 98 | 3 | Yes | Yes | 19.8 | 19.4 | 0.4 | 9F68789C91344AFFA61C6F7B9DDFAD8B |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Stockton | CA | 95207-4713 |  | 2013-06-27 | 2013-06-27 10:23 | 2013-06-27 10:23 | PAYNE - PY1PNB042090AAAA | 100 | 0 | Yes | Yes | 15.7 | 17.8 | -2.1 | 23F5D1CD819A48A6BDF65357D9745441 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3625 |  | 2013-07-08 | 2013-07-08 14:05 | 2013-07-08 14:27 | DAY & NIGHT - UNK | 85 | 8 | Yes | Yes | 18.2 | 19.5 | -1.3 | E2FCF720A75444C9AD5DA92EF99CE029 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Merced | CA | 95340-4125 |  | 2013-06-28 | 2013-06-28 16:13 | 2013-06-28 16:19 | GOODMAN - PGB0360751 | 60 | 6.3 | Yes | Yes | 23.7 | 18.1 | 5.6 | E80F661D0C594EF9A2006545C5F07AE3 |  | R22 | Non-TXV |  | 10.5% | 0.895 | 20.18% | [5 empty] | Non-TXV | 10.5%
Stockton | CA | 95206-6148 |  | 2013-07-05 | 2013-07-05 11:18 | 2013-07-05 11:43 | GOODMAN - CLJ48-1 | 85 | -6 | Yes | Yes | 18.6 | 20.9 | -2.3 | 52C71ACCF3FE4C0B87CB5C977AFAC87A |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93704-4704 |  | 2013-07-23 | 2013-07-23 12:21 | 2013-07-23 12:23 | RHEEM - 24JGK | 50 | 8.1 | Yes | Yes | 22.8 | 20.9 | 1.9 | F6798835502D489A8D52AB1D131E0393 |  | R22 | Non-TXV |  | 16.2% | 0.838 | 31.13% | [5 empty] | Non-TXV | 16.2%
Fresno | CA | 93725-9746 |  | 2013-09-04 | 2013-09-04 13:03 | 2013-09-04 13:04 | CARRIER - 7777UNK | 84 | 3.3 | Yes | Yes | 22 | 19.4 | 2.6 | AA5BC1FC33014762B0ED3C52B256DDD5 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Los Banos | CA | 93635-0000 |  | 2013-07-08 | 2013-07-08 08:26 | 2013-07-08 08:35 | NORDYNE - JS3BA030KA | 68 | 5.9 | Yes | Yes | 19.2 | 20.1 | -0.9 | 618C0DA0D4584E53A82BDD243301D4EC |  | R22 | Non-TXV |  | 8.676% | 0.91324 | 16.67% | [5 empty] | Non-TXV | 8.676%
Fresno | CA | 93728-3103 |  | 2013-07-15 | 2013-07-15 12:29 | 2013-07-15 12:34 | GOODMAN - CKL24-1A | 72 | 3.3 | Yes | Yes | 17 | 19.8 | -2.8 | EF02AAE3A5DF43B3AD6372C7FB130BC0 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Kerman | CA | 93630-1274 |  | 2013-09-12 | 2013-09-12 13:16 | 2013-09-12 13:17 | ICP - CA5036VKB1 | 86 | 11.6 | Yes | Yes | 24.4 | 22.6 | 1.8 | 5D7D59A526D9472394CFB0E323A2691B |  | R22 | Non-TXV |  | 13.49% | 0.86512 | 25.92% | [5 empty] | Non-TXV | 13.49%
Stockton | CA | 95204-3731 |  | 2013-08-05 | 2013-08-05 13:46 | 2013-08-05 14:04 | LENNOX - HS19-311V-4P | 105 | 3.4 | Yes | Yes | 18.2 | 18.7 | -0.5 | 19454A69695A4CC2A3FA014B32DC523B |  | R22 | Non-TXV |  | 3.238% | 0.96762 | 6.223% | [5 empty] | Non-TXV | 3.238%
Fresno | CA | 93726-5107 |  | 2013-07-30 | 2013-07-30 09:44 | 2013-07-30 09:44 | OTHER - 55AW24106 | 69 | 0 | Yes | Yes | -9 | 20.4 | -29.4 | 6D8B08C421224FC48EB36294F97C2EB0 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-5365 |  | 2013-08-26 | 2013-08-26 11:33 | 2013-08-26 12:14 | YORK - D1NAO48N09006C | 92 | 7 | Yes | Yes | 23 | 19.1 | 3.9 | 8F5BFBB439AF44EE90CA20B799E74961 |  | R22 | Non-TXV |  | 7.609% | 0.92391 | 14.62% | [5 empty] | Non-TXV | 7.609%
Stockton | CA | 95215-6092 |  | 2013-07-01 | 2013-07-01 09:53 | 2013-07-01 10:23 | ALLEGIANCE - 7A0036A100A2 | 88 | 2.7 | Yes | Yes | 23.2 | 19.9 | 3.3 | 162DD0D6897A43D4993BC8A4B917800C |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Fresno | CA | 93703-1524 |  | 2013-07-03 | 2013-07-03 08:54 | 2013-07-03 09:21 | CARRIER - 48SX-042080321 | 87 | 4.9 | Yes | Yes | 20.8 | 20.7 | 0.1 | EDEE1C8D3FD347A39561D42FEFB6E4E0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.632% | 0.94368 | 10.82% | [5 empty] | Non-TXV | 5.632%
Chico | CA | 95926-1612 |  | 2013-07-01 | 2013-07-01 10:40 | 2013-07-01 10:40 | DAY & NIGHT - 593CJ036-B | 95 | 0 | Yes | Yes | 22.8 | 21.5 | 1.3 | FE38463541B04BB98DE275B49AC5E661 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4010 |  | 2013-07-23 | 2013-07-23 10:59 | 2013-07-23 11:01 | YORK - D1NH048N09006C | 128 | 3.8 | Yes | Yes | 19.4 | 19.4 | 0 | EB35EBFF344F4A81B5E41339C6EDE548 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Meadow Vista | CA | 95722-0000 |  | 2013-08-27 | 2013-08-27 14:06 | 2013-08-27 14:19 | RHEEM - UNK | 83 | -3.7 | Yes | Yes | 18 | 21 | -3 | EB13B211668F4D808B0832872D5104F3 |  | R22 | TXV |  | -4.458% | 1.0446 | 1.248% |  |  |  |  | TXV |  |  | -4.458%
Los Banos | CA | 93635-6328 |  | 2013-07-10 | 2013-07-10 14:39 | 2013-07-10 14:52 | GOODMAN - CK361A | 73 | 10.4 | Yes | Yes | 24.2 | 22.2 | 2.1 | 793FDCFD7BA546A5AEF17552B81923C2 |  | R22 | Non-TXV |  | 14.25% | 0.85753 | 27.38% | [5 empty] | Non-TXV | 14.25%
Clovis | CA | 93612-4913 |  | 2013-06-28 | 2013-06-28 17:00 | 2013-06-28 17:28 | YORK - D1NA030N03606A | 75 | 9.1 | Yes | Yes | 20.4 | 20.3 | 0.2 | E896C613E6434BD4B60EF315137F40A0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.13% | 0.87867 | 23.32% | [5 empty] | Non-TXV | 12.13%
Kerman | CA | 93630-9320 |  | 2013-08-01 | 2013-08-01 13:27 | 2013-08-01 13:30 | LENNOX - 10ACB3611P | 80 | 10.6 | Yes | Yes | 26.9 | 22.5 | 4.4 | FA60B48D4EF946BC934CB0E58A3F40CC |  | R22 | Non-TXV |  | 13.25% | 0.8675 | 25.46% | [5 empty] | Non-TXV | 13.25%
Clovis | CA | 93612-5044 |  | 2013-07-11 | 2013-07-11 09:09 | 2013-07-11 09:37 | DAY & NIGHT - 36/80 YAC 107C | 67 | 2.5 | Yes | Yes | 22.6 | 21 | 1.6 | 44FA0DDD770A4D9FBAF8E94A6B42B32A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.731% | 0.96269 | 7.171% | [5 empty] | Non-TXV | 3.731%
Fresno | CA | 93725-1889 |  | 2013-07-22 | 2013-07-22 11:38 | 2013-07-22 11:41 | GOODMAN - GPG13360451AB | 112 | 3.6 | Yes | Yes | 23 | 17.2 | 5.8 | CF82CDE3B9444F1BADD4BD5907262F53 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Los Banos | CA | 93635-9493 |  | 2013-07-12 | 2013-07-12 14:48 | 2013-07-12 14:49 | BRYANT - 561CJ060 | 131 | 17 | Yes | Yes | 18.3 | 20.7 | -2.3 | 44592974BDCB45659F259FA2CB6DAD2B |  | R22 | TXV |  | 12.98% | 0.87023 | 24.94% | [5 empty] | TXV | 12.98%
Stockton | CA | 95205-6411 |  | 2013-07-15 | 2013-07-15 11:35 | 2013-07-15 12:03 | ICP - PGC06K060D | 92 | 3.5 | Yes | Yes | 20.9 | 18.6 | 2.3 | 6447CEEE012D4A4B814EE084E474DECE |  | R22 | Non-TXV |  | 3.804% | 0.96196 | 7.311% | [5 empty] | Non-TXV | 3.804%
Paradise | CA | 95969-3610 |  | 2013-06-28 | 2013-06-28 18:51 | 2013-06-28 19:10 | CARRIER - 48TMX030-34- | 100 | 9.8 | Yes | Yes | 19.6 | 20.4 | -0.8 | 95823CC91ECF41ADBB114C9F1381BF02 |  | R22 | Non-TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | Non-TXV | 9.8%
Stockton | CA | 95209-2436 |  | 2013-07-11 | 2013-07-11 11:07 | 2013-07-11 11:07 | GOODMAN - CK42-1C | 92 | 0 | Yes | Yes | 19.1 | 18.2 | 0.9 | 547678F156CF4AE08C9CEE5456DF27FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1889 |  | 2013-08-07 | 2013-08-07 10:20 | 2013-08-07 10:28 | GOODMAN - GPG13360451AB | 112 | 3.6 | Yes | Yes | 24.6 | 18.6 | 6 | 08F6A28F6BC943E386F58FACD0B25DA1 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Los Banos | CA | 93635-3145 |  | 2013-07-08 | 2013-07-08 14:37 | 2013-07-08 14:39 | YORK - H2RE048S061 | 227 | 24.8 | Yes | Yes | 25.7 | 20.4 | 5.3 | 720DEC4876FC40C6BF5960AD783F6B08 |  | R22 | Non-TXV |  | 10.93% | 0.89075 | 21% | [5 empty] | Non-TXV | 10.93%
Madera | CA | 93637-5636 |  | 2013-08-06 | 2013-08-06 11:22 | 2013-08-06 11:51 | NORDYNE - GR6GD-X30K045X | 93 | 3.9 | Yes | Yes | 22.7 | 20.7 | 2.1 | A272092B7E3F4ABFB766C9FBF0372010 |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Fresno | CA | 93704-1540 |  | 2013-07-23 | 2013-07-23 10:12 | 2013-07-23 10:13 | CARRIER - UNK | 68 | 10.4 | Yes | Yes | 23.6 | 21 | 2.6 | 605B12D9934B40F18E906A2EEA0D9837 |  | R22 | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
Madera | CA | 93637-5614 |  | 2013-10-01 | 2013-10-01 15:43 | 2013-10-01 15:45 | CARRIER - 48KL130300BE | 54 | 2.8 | Yes | Yes | 21.8 | 19.1 | 2.8 | 3FEDE497FE374A82A9CFEAFA23F04B77 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Fresno | CA | 93726-4610 |  | 2013-07-29 | 2013-07-29 15:07 | 2013-07-29 15:08 | RHEEM - RAMB036JBZ | 93 | 11.9 | Yes | Yes | 25.4 | 22.5 | 2.9 | 03B59EF8773B4ECD81A3DA88DD96A1D1 |  | R22 | Non-TXV |  | 12.8% | 0.87204 | 24.59% | [5 empty] | Non-TXV | 12.8%
Clovis | CA | 93611-4538 |  | 2013-06-26 | 2013-06-26 12:53 | 2013-06-26 13:14 | PAYNE - Y3GNAA42090 | 100 | 4 | Yes | Yes | 21.3 | 21.7 | -0.4 | 004C4D34124040E48EE76F968C77172E |  | R410A | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Chico | CA | 95926-2049 |  | 2013-07-30 | 2013-07-30 14:27 | 2013-07-30 14:55 | DAY & NIGHT - 58BR4050YNCR | 75 | 8.4 | Yes | Yes | 18.1 | 20.9 | -2.8 | EB5EC8043FE34F59A2D51214F629E0CA |  | R22 | Non-TXV |  | 11.2% | 0.888 | 21.52% | [5 empty] | Non-TXV | 11.2%
Fresno | CA | 93705-0235 |  | 2013-07-08 | 2013-07-08 12:42 | 2013-07-08 13:05 | PAYNE - N/A | 75 | 5.9 | Yes | Yes | 20 | 19.1 | 0.9 | 7820CE46FF5E41DEA136B0FAE011AC4C |  | R22 | Non-TXV |  | 7.867% | 0.92133 | 15.12% | [5 empty] | Non-TXV | 7.867%
Camino | CA | 95709-9611 |  | 2013-07-29 | 2013-07-29 13:57 | 2013-07-29 13:57 | CARRIER - 50HX-042-301AA | 100 | 0 | Yes | Yes | 24 | 22.3 | 1.7 | C0731A4EBF71413F9213BA494521D593 |  | R22 | TXV |  | 0% | 1 | 0%
Williams | CA | 95987-9009 |  | 2013-08-03 | 2013-08-03 13:50 | 2013-08-03 14:18 | GIBSON - JS3BA-024KA | 64 | 2.2 | Yes | Yes | 18 | 19.6 | -1.6 | 8400B19958B244AFB02FCBBCE55C18CE |  | R22 | TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | TXV | 3.438%
Red Bluff | CA | 96080-9781 |  | 2013-07-24 | 2013-07-24 10:57 | 2013-07-24 11:51 | DAY & NIGHT - 585GJW056060ABAF | 85 | 3.5 | Yes | Yes | 18.6 | 20.3 | -1.7 | 548CDD67CA4D4F0091F3FD53137A8049 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fresno | CA | 93703-1542 |  | 2013-08-07 | 2013-08-07 12:30 | 2013-08-07 12:32 | RHEEM - RRKAA036JK08E | 62 | 8 | Yes | Yes | 18.8 | 17.5 | 1.3 | 6A3047C0910D4B7688AEB3D6A0104EC2 |  | R22 | Non-TXV |  | 12.9% | 0.87097 | 24.8% | [5 empty] | Non-TXV | 12.9%
Fresno | CA | 93726-0313 |  | 2013-07-26 | 2013-07-26 11:23 | 2013-07-26 11:24 | OTHER - 36RCU108C | 67 | 10.7 | Yes | Yes | 22.2 | 19.3 | 2.9 | 2065C8D4BB2D4241B351BDC80A2EC4A4 |  | R22 | Non-TXV |  | 15.97% | 0.8403 | 30.69% | [5 empty] | Non-TXV | 15.97%
Stockton | CA | 95210-1311 |  | 2013-06-26 | 2013-06-26 11:47 | 2013-06-26 12:06 | COLEMAN - BRC0421BB | 112 | 3.7 | Yes | Yes | 19.7 | 16.4 | 3.4 | 2C4DF6CB57D843C3B79E311A6CFCC0F6 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Stockton | CA | 95206-5917 |  | 2013-07-16 | 2013-07-16 09:58 | 2013-07-16 09:58 | CARRIER - 38CKC060360 | 131 | 0 | Yes | Yes | 19 | 20.2 | -1.2 | 9082DEB4B6EB45FA8D5237353CD18CED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-2308 |  | 2013-07-15 | 2013-07-15 12:54 | 2013-07-15 12:57 | ARCOAIRE - PGF042K080A | 87 | 4.5 | Yes | Yes | 20.7 | 23.5 | -2.8 | CC5227866ADF4D86B78D2BB972771EA2 |  | R22 | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Reedley | CA | 93654-4107 |  | 2013-07-25 | 2013-07-25 13:15 | 2013-07-25 14:08 | LENNOX - 10GCS036-75-3PA | 58 | 2.7 | Yes | Yes | 20.5 | 21.4 | -0.9 | 7CAC971B21F34D2E9CAC341291B2B7D7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.655% | 0.95345 | 8.946% | [5 empty] | Non-TXV | 4.655%
Fresno | CA | 93711-1458 |  | 2013-07-26 | 2013-07-26 16:43 | 2013-07-26 16:45 | YORK - D1NH048N09006C | 128 | 18.6 | Yes | Yes | 26.6 | 23.6 | 3 | D18BA62492614E828C3C71F17B1E5319 |  | R22 | Non-TXV |  | 14.53% | 0.85469 | 27.93% | [5 empty] | Non-TXV | 14.53%
Fresno | CA | 93711-1458 |  | 2013-07-22 | 2013-07-22 12:19 | 2013-07-22 12:21 | TRANE - YCX048G1HOAA | 166 | 29.6 | Yes | Yes | 21.7 | 20.4 | 1.3 | 6BF5CCCD8C7848D6845D7EEBB0C4B121 |  | R22 | Non-TXV |  | 17.83% | 0.82169 | 34.27% | [5 empty] | Non-TXV | 17.83%
Fresno | CA | 93720-0232 |  | 2013-08-22 | 2013-08-22 14:10 | 2013-08-22 14:15 | CARRIER - UNK | 56 | 6.9 | Yes | Yes | 25.1 | 23.1 | 2 | 5B584C95872445C8976F7BD3814FB093 |  | R22 | Non-TXV |  | 12.32% | 0.87679 | 23.68% | [5 empty] | Non-TXV | 12.32%
Fresno | CA | 93705-2812 |  | 2013-07-08 | 2013-07-08 17:54 | 2013-07-08 18:09 | AMANA - PGB36C07020 | 67 | 6.9 | Yes | Yes | 22.3 | 18.8 | 3.5 | 76B89C3E4E654B4F954162DB2F646D15 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.3% | 0.89701 | 19.79% | [5 empty] | Non-TXV | 10.3%
Grass Valley | CA | 95945-8809 |  | 2013-09-04 | 2013-09-04 11:52 | 2013-09-04 12:18 | DAY & NIGHT - 588ANW030080ACAD | 50 | 1.9 | Yes | Yes | 20 | 18.2 | 1.8 | B5EBEBDD85264ECAAD4B6250C3E05AB1 |  | R22 | TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | TXV | 3.8%
Magalia | CA | 95954-9504 |  | 2013-07-17 | 2013-07-17 15:59 | 2013-07-17 19:58 | BRYANT - 602SDNX036000A3 | 147 | 13.7 | Yes | Yes | 18 | 19.6 | -1.6 | 0E5588B465004205906968FAAE65B261 |  | R410A | Non-TXV |  | 9.32% | 0.9068 | 17.91% | [5 empty] | Non-TXV | 9.32%
Atascadero | CA | 93422-5516 |  | 2013-08-08 | 2013-08-08 17:03 | 2013-08-08 17:22 | HEIL - NAC218AKC3 | 80 | 2.8 | Yes | Yes | 23 | 19.4 | 3.6 | 1517829A640D499F87F5CAD6E3650BB1 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Stockton | CA | 95212-0000 |  | 2013-06-27 | 2013-06-27 09:40 | 2013-06-27 09:59 | BRYANT - 4ABA348A300 | 121 | 7.3 | Yes | Yes | 15.9 | 18.8 | -2.9 | 4913FE36FA194B42922914206F0AA843 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 6.033% | 0.93967 | 11.59% | [5 empty] | Non-TXV | 6.033%
Grass Valley | CA | 95945-5405 |  | 2013-08-23 | 2013-08-23 16:26 | 2013-08-23 16:26 | BDP - 561CJ030-A | 67 | 0 | Yes | Yes | 24.3 | 20.3 | 4 | 7C38A252A1EB466AAC32DDF3741CFAAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-4304 |  | 2013-07-09 | 2013-07-09 13:18 | 2013-07-09 13:37 | RUUD - CBD | 48 | 1.7 | Yes | Yes | 25.6 | 20.4 | 5.2 | 55EAD49FEE6B418D95DA84F97F1B9BEF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Ione | CA | 95640-9111 |  | 2013-07-24 | 2013-07-24 13:41 | 2013-07-24 14:10 | PAYNE - PA13NR042-H | 112 | 9.1 | Yes | Yes | 18.5 | 19.7 | -1.2 | EC40122E04E445A092461757E4960C8F |  | R22 | TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | TXV | 8.125%
Williams | CA | 95987-5120 |  | 2013-08-03 | 2013-08-03 12:13 | 2013-08-03 12:13 | - GQ4SD-048K | 293 | 0 | Yes | Yes | 17 | 19.4 | -2.4 | 2ADB44632CA84B39B3C794E963796E15 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2665 |  | 2013-07-03 | 2013-07-03 13:31 | 2013-07-03 14:11 | BDP - 24/60YAC108C | 53 | 7.8 | Yes | Yes | 18.3 | 18.6 | -0.3 | 78EB8A5322454C5FBCBB9FE2B085B5FD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.72% | 0.85283 | 28.28% | [5 empty] | Non-TXV | 14.72%
Cameron Park | CA | 95682-8211 |  | 2013-07-05 | 2013-07-05 09:02 | 2013-07-05 09:32 | OTHER - N2H330AKB100 | 100 | 9.3 | Yes | Yes | 16 | 18.7 | -2.7 | 10B170287DF64F9C8748655220D642E5 |  | R22 | TXV |  | 9.3% | 0.907 | 17.87% | [5 empty] | TXV | 9.3%
Los Banos | CA | 93635-3164 |  | 2013-07-08 | 2013-07-08 11:18 | 2013-07-08 11:25 | BDP - 561AJ024B | 56 | 8.5 | Yes | Yes | 20.4 | 20.2 | 0.2 | 4334C957B63B467CA12D4A7C58F35EEC |  | R22 | Non-TXV |  | 15.18% | 0.84821 | 29.17% | [5 empty] | Non-TXV | 15.18%
Fresno | CA | 93704-2129 |  | 2013-06-26 | 2013-06-26 13:07 | 2013-06-26 13:11 | BDP - 561AJ036 | 72 | 4.3 | Yes | Yes | 19.9 | 18.5 | 1.4 | 88144D464E274F74BCADD521732F66C2 |  | R22 | Non-TXV |  | 5.972% | 0.94028 | 11.48% | [5 empty] | Non-TXV | 5.972%
Kerman | CA | 93630-1943 |  | 2013-07-31 | 2013-07-31 13:08 | 2013-07-31 13:11 | CARRIER - 48GS036060301 | 56 | 8.3 | Yes | Yes | 26.1 | 23.1 | 3 | C1954322458F4324B73C164975E552DE |  | R22 | Non-TXV |  | 14.82% | 0.85179 | 28.48% | [5 empty] | Non-TXV | 14.82%
Dos Palos | CA | 93620-2524 |  | 2013-09-18 | 2013-09-18 09:48 | 2013-09-18 09:50 | GOODMAN - XK30-1B | 76 | 4.5 | Yes | Yes | 17.3 | 20 | -2.7 | 43F50B5186544FFAA657F9C7875DF024 |  | R22 | Non-TXV |  | 5.921% | 0.94079 | 11.38% | [5 empty] | Non-TXV | 5.921%
Stockton | CA | 95206-6340 |  | 2013-07-12 | 2013-07-12 12:16 | 2013-07-12 12:39 | YORK - H1RD036S06A | 145 | 4.7 | Yes | Yes | 22.3 | 18.5 | 3.8 | B27E7563C5F942149782AFC3B44D125D |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.229% | [5 empty] | Non-TXV | 3.241%
Stockton | CA | 95207-7772 |  | 2013-06-26 | 2013-06-26 11:45 | 2013-06-26 12:03 | GOODMAN - GSC130241EA | 77 | 6.8 | Yes | Yes | 19.7 | 20.5 | -0.8 | 7193E0E8206F4BFB9CCC4F17BB9B9FC6 |  | R22 | Non-TXV |  | 8.831% | 0.91169 | 16.97% | [5 empty] | Non-TXV | 8.831%
Merced | CA | 95341-6983 |  | 2013-07-01 | 2013-07-01 15:09 | 2013-07-01 15:11 | PAYNE - PY1PNB042060AAAA | 100 | 4.4 | Yes | Yes | 24.4 | 21 | 3.5 | 35BD8259E694457D9449A2FCCCEF2D88 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Cameron Park | CA | 95682-7401 |  | 2013-07-08 | 2013-07-08 15:15 | 2013-07-08 15:39 | TRANE - TWN036C100B4 | 135 | 7.7 | Yes | Yes | 18 | 20.9 | -2.9 | B422AF6A0DA446738121BB322641ADDB |  | R22 | Non-TXV |  | 5.704% | 0.94296 | 10.96% | [5 empty] | Non-TXV | 5.704%
Placerville | CA | 95667-5339 |  | 2013-07-10 | 2013-07-10 12:28 | 2013-07-10 12:44 | CARRIER - 48GX-042090301AD | 120 | 3.6 | Yes | Yes | 24 | 22.1 | 1.9 | 95ED31FA91BE403EB6467FD1AB89C40C |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95348-1127 |  | 2013-07-10 | 2013-07-10 12:47 | 2013-07-10 12:49 | GOODMAN - GPG1342070M41AB | 105 | 3.3 | Yes | Yes | 26 | 20.9 | 5.1 | 0F6BC9251DCB4166B22DD1AC475FC641 |  | R410A | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Ripon | CA | 95366-3150 |  | 2013-07-24 | 2013-07-24 14:19 | 2013-07-24 14:55 | RUUD - UAKA-042JAZ | 79 | 2.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | E84B0622B03D439F8278E69C01FBE1A1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Clovis | CA | 93611-3038 |  | 2013-06-26 | 2013-06-26 13:20 | 2013-06-26 14:02 | ICP - PGAD36D1KB | 102 | 3.5 | Yes | Yes | 18.7 | 18.3 | 0.4 | 8030335764B940D5AE5486F936794A6D |  | R22 | Non-TXV |  | 3.431% | 0.96569 | 6.594% | [5 empty] | Non-TXV | 3.431%
Paradise | CA | 95969-3816 |  | 2013-06-29 | 2013-06-29 18:22 | 2013-06-29 18:40 | PAYNE - PY3938G42PNA040NB | 112 | 5.4 | Yes | Yes | 23.2 | 22.1 | 1.1 | FA129C72FB454FD8AEA8BE4A7C503F30 |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Stockton | CA | 95205-5548 |  | 2013-07-15 | 2013-07-15 10:17 | 2013-07-15 10:43 | GOODMAN - GPG1324045M41AD | 85 | 5.5 | Yes | Yes | 20.6 | 20.4 | 0.2 | C4B5392C4EDD42508BE2F05B4C65EDDA |  | R410A | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Atascadero | CA | 93422-5516 |  | 2013-08-13 | 2013-08-13 15:14 | 2013-08-13 15:35 | HEIL - EO42553481 | 80 | 7.4 | Yes | Yes | 23.3 | 19.7 | 3.6 | EF3726240F7448C0853EB399FB78BE33 |  | R22 | Non-TXV |  | 9.25% | 0.9075 | 17.78% | [5 empty] | Non-TXV | 9.25%
Kerman | CA | 93630-2501 |  | 2013-08-01 | 2013-08-01 08:07 | 2013-08-01 08:09 | CARRIER - 48GX036060301 | 82 | 4.3 | Yes | Yes | 21.2 | 18.3 | 2.9 | E84BED17FA4843E88BA021529C84EBC0 |  | R22 | Non-TXV |  | 5.244% | 0.94756 | 10.08% | [5 empty] | Non-TXV | 5.244%
Kerman | CA | 93630-1959 |  | 2013-08-13 | 2013-08-13 18:20 | 2013-08-13 19:00 | LENNOX - 10GCS036X-75-1PA | 58 | 4.6 | Yes | Yes | 22 | 20.4 | 1.6 | E1E2078D88A94017822D75E80180348D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.931% | 0.92069 | 15.24% | [5 empty] | Non-TXV | 7.931%
Chico | CA | 95928-6069 |  | 2013-08-28 | 2013-08-28 09:23 | 2013-08-28 09:45 | BDP - 567C018RCU | 37 | 19.1 | Yes | Yes | 19.7 | 18.2 | 1.5 | B4B482B9E89144D1B959BA17DCAE1661 |  | R22 | Non-TXV |  | 51.62% | 0.48378 | 99.21% | [5 empty] | Non-TXV | 51.62%
Stockton | CA | 95206-4748 |  | 2013-08-13 | 2013-08-13 09:04 | 2013-08-13 09:21 | YORK - BRCS03016D | 62 | -7.3 | Yes | Yes | 16.9 | 16.8 | 0.1 | 8E9BA8ACD9EF44B2B86C8480D042581A |  | R22 | Non-TXV |  | -11.77% | 1.1177 | 3.297% |  |  |  |  | Non-TXV |  |  | -11.77%
Marysville | CA | 95901-3835 |  | 2013-07-17 | 2013-07-17 17:31 | 2013-07-17 17:31 | YORK - D2PN04206506A | 150 | 0 | Yes | Yes | 28 | 22.1 | 5.9 | 352786E5D76D4AF992E74FFF64BDCAA4 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2125 |  | 2013-06-26 | 2013-06-26 11:59 | 2013-06-26 12:07 | YORK - DBRHF036N080C | 112 | 9.9 | Yes | Yes | 19.2 | 17.7 | 1.5 | A09714E259A0440499F6A8BC9EFAB288 |  | R22 | Non-TXV |  | 8.839% | 0.91161 | 16.99% | [5 empty] | Non-TXV | 8.839%
El Dorado | CA | 95623-4874 |  | 2013-08-15 | 2013-08-15 10:08 | 2013-08-15 10:30 | WESTINGHOUSE - HR036SA | 65 | 13.2 | Yes | Yes | 18.5 | 21.3 | -2.8 | 4F6644865C354EBBBB40D2EA5FA31F1F |  | R22 | Non-TXV |  | 20.31% | 0.79692 | 39.03% | [5 empty] | Non-TXV | 20.31%
Kerman | CA | 93630-1980 |  | 2013-08-16 | 2013-08-16 15:03 | 2013-08-16 17:31 | CARRIER - 48GX-042060311 | 117 | 3.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | 69098045F6D64798B42B8A28F2349D53 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95205-4355 |  | 2013-07-12 | 2013-07-12 15:41 | 2013-07-12 17:25 | BDP - 589ANW024040ABCD | 57 | -4 | Yes | Yes | 17.5 | 19.3 | -1.8 | D846B251FCBB487D87B67CEB2786BE1A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.018% | 1.0702 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.018%
Fresno | CA | 93710-3927 |  | 2013-07-22 | 2013-07-22 13:06 | 2013-07-22 13:07 | YORK - H2RD036S06B | 96 | 11.6 | Yes | Yes | 23.6 | 20.4 | 3.2 | DA96A9942D17448D81400B45354B72A0 |  | R22 | Non-TXV |  | 12.08% | 0.87917 | 23.22% | [5 empty] | Non-TXV | 12.08%
Wheatland | CA | 95692-9445 |  | 2013-09-11 | 2013-09-11 14:58 | 2013-09-11 15:29 | BDP - 588ANW03060ADAD | 55 | 4.3 | Yes | Yes | 20 | 19.9 | 0.1 | 92D1B66E9C284B9DBA7EEB8DD07CAC1F |  | R22 | Non-TXV |  | 7.818% | 0.92182 | 15.02% | [5 empty] | Non-TXV | 7.818%
Stockton | CA | 95210-3246 |  | 2013-07-09 | 2013-07-09 08:36 | 2013-07-09 08:54 | DAY & NIGHT - 567C030RCU | 63 | -3.7 | Yes | Yes | 22.9 | 19.2 | 3.7 | 4447D51E6F8F44B9BA23617872CB81F5 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Ripon | CA | 95366-2019 |  | 2013-08-23 | 2013-08-23 16:58 | 2013-08-23 17:23 | GOODMAN - GSC130361D | 120 | 6.8 | Yes | Yes | 19.7 | 19.7 | 0 | 088C581C8624457FA6419768A8430A8E |  | R22 | TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | TXV | 5.667%
Fresno | CA | 93737-9254 |  | 2013-09-04 | 2013-09-04 11:48 | 2013-09-04 12:01 | LENNOX - 13ACX-048-230-02 | 120 | 7.5 | Yes | Yes | 17.5 | 20.4 | -2.9 | 8B7CEC0B6AC14CB4893A049B83094617 |  | R410A | TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | TXV | 6.25%
Stockton | CA | 95205-6554 |  | 2013-07-18 | 2013-07-18 10:10 | 2013-07-18 10:38 | CARRIER - 24ABA348A300 | 121 | 18.2 | Yes | Yes | 23.3 | 18.8 | 4.5 | FD26BB1B12A34FB6AA8417B9E904C756 |  | R410A | Non-TXV |  | 15.04% | 0.84959 | 28.91% | [5 empty] | Non-TXV | 15.04%
Fresno | CA | 93722-3022 |  | 2013-07-18 | 2013-07-18 09:38 | 2013-07-18 09:38 | OTHER - CA5036VKB1 | 86 | 0 | Yes | Yes | 15.2 | 25.3 | -10.1 | 8135B67F08604EC58CB6360FAD6D0ED1 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6563 |  | 2013-07-16 | 2013-07-16 12:08 | 2013-07-16 12:33 | LENNOX - 13ACC-048-230-02 | 158 | 7.2 | Yes | Yes | 15.9 | 18.9 | -3 | 63D792FF70904E53BFE322D16598CAB5 |  | R22 | Non-TXV |  | 4.557% | 0.95443 | 8.757% | [5 empty] | Non-TXV | 4.557%
Los Banos | CA | 93635-3441 |  | 2013-07-09 | 2013-07-09 12:26 | 2013-07-09 12:29 | NORDYNE - FS3BA036KA | 69 | 11.1 | Yes | Yes | 26 | 20.8 | 5.2 | 25D0666F120640619DC46897B8AB6AC1 |  | R22 | Non-TXV |  | 16.09% | 0.83913 | 30.92% | [5 empty] | Non-TXV | 16.09%
Chico | CA | 95928-6886 |  | 2013-08-05 | 2013-08-05 16:34 | 2013-08-05 16:51 | LENNOX - GCS29X-024-50-2PA | 52 | 2.2 | Yes | Yes | 22.8 | 20.4 | 2.4 | B658F701A5C449B1ACC6437E1C9A0524 |  | R22 | Non-TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | Non-TXV | 4.231%
Stockton | CA | 95210-4631 |  | 2013-07-30 | 2013-07-30 09:18 | 2013-07-30 09:38 | BRYANT - 563CN018-B | 80 | 10.7 | Yes | Yes | 16.4 | 18.2 | -1.8 | 24C96F858DED46D29F1D755EE8D09B4D |  | R22 | Non-TXV |  | 13.38% | 0.86625 | 25.7% | [5 empty] | Non-TXV | 13.38%
Chowchilla | CA | 93610-2054 |  | 2013-06-27 | 2013-06-27 09:25 | 2013-06-27 10:27 | NORDYNE - JSC38C-042KA | 103 | 3.3 | Yes | Yes | 19.4 | 19.8 | -0.4 | 863389AE48D34152AEFB0A84B248579C |  | R22 | Non-TXV |  | 3.204% | 0.96796 | 6.157% | [5 empty] | Non-TXV | 3.204%
Valley Springs | CA | 95252-9452 |  | 2013-07-16 | 2013-07-16 13:04 | 2013-07-16 13:46 | AMERICAN STANDARD - 2WCX3030A1000AA | 99 | 5.1 | Yes | Yes | 17 | 18.5 | -1.5 | 23F3C05C7B3D4CF38C10977F5EDC7320 |  | R22 | Non-TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | Non-TXV | 5.152%
Los Banos | CA | 93635-3282 |  | 2013-07-09 | 2013-07-09 09:35 | 2013-07-09 09:43 | DAY & NIGHT - UNK | 68 | 8.3 | Yes | Yes | 22.7 | 19.8 | 2.9 | D9A04E355F2C40E29F4295A8251DBCE7 |  | R22 | Non-TXV |  | 12.21% | 0.87794 | 23.46% | [5 empty] | Non-TXV | 12.21%
Chico | CA | 95926-8027 |  | 2013-09-27 | 2013-09-27 13:02 | 2013-09-27 13:23 | BDP - 565BJ024 | 70 | 2.1 | Yes | Yes | 22 | 20.6 | 1.4 | 661E9179F6434B188C7C004FF2006FEC |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93704-1914 |  | 2013-06-26 | 2013-06-26 10:27 | 2013-06-26 10:39 | YORK - D1GH024N03206A | 132 | 19.3 | Yes | Yes | 17.2 | 14.4 | 2.8 | D728998EE0F249D0AE93D408D00D3B14 |  | R22 | Non-TXV |  | 14.62% | 0.85379 | 28.1% | [5 empty] | Non-TXV | 14.62%
Chico | CA | 95926-3129 |  | 2013-07-02 | 2013-07-02 17:55 | 2013-07-02 18:25 | TRANE - YCP030F1MOAA | 107 | 11 | Yes | Yes | 20.6 | 21.7 | -1.1 | 0C2A9055DE5C4B7689466601AFE5E9E3 |  | R22 | Non-TXV |  | 10.28% | 0.8972 | 19.76% | [5 empty] | Non-TXV | 10.28%
Stockton | CA | 95212-2761 |  | 2013-06-26 | 2013-06-26 11:54 | 2013-06-26 12:17 | CARRIER - 24ABA360A320 | 132 | 9.5 | Yes | Yes | 21.8 | 18 | 3.8 | 86C7369DAC624C05A998D5CEC20E0A44 |  | R410A | TXV |  | 7.197% | 0.92803 | 13.83% | [5 empty] | TXV | 7.197%
Fresno | CA | 93704-1003 |  | 2013-06-26 | 2013-06-26 09:42 | 2013-06-26 10:08 | CARRIER - 38TKB036300 | 88 | 10.8 | Yes | Yes | 17.9 | 17.5 | 0.4 | BA97F5511EC04E12ADE0CF142614DCF1 |  | R22 | Non-TXV |  | 12.27% | 0.87727 | 23.59% | [5 empty] | Non-TXV | 12.27%
Burson | CA | 95225-0000 |  | 2013-10-01 | 2013-10-01 10:23 | 2013-10-01 10:23 | DAY & NIGHT - 591ANX048000ABAA | 114 | 0 | Yes | Yes | 22.9 | 19.5 | 3.4 | 34361711666443698ABADF1007B7248C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Burson | CA | 95225-0000 |  | 2013-10-01 | 2013-10-01 10:49 | 2013-10-01 11:16 | NORDYNE - JS5BD-030KA | 99 | 4.7 | Yes | Yes | 26.1 | 20.1 | 6 | 8EB2B080F17A417F8EFDAAF80E2ED75C |  | R22 | Non-TXV |  | 4.747% | 0.95253 | 9.124% | [5 empty] | Non-TXV | 4.747%
Merced | CA | 95340-2368 |  | 2013-06-28 | 2013-06-28 14:20 | 2013-06-28 14:27 | COLEMAN - 2036911 | 86 | 11.2 | Yes | Yes | 21.9 | 20.4 | 1.5 | 4F459251D08E48BD8A526CD63154688A |  | R22 | Non-TXV |  | 13.02% | 0.86977 | 25.03% | [5 empty] | Non-TXV | 13.02%
Chico | CA | 95973-8315 |  | 2013-08-20 | 2013-08-20 13:08 | 2013-08-20 13:08 | RUUD - UAFD-025JAS4727 F0490 4040 | 51 | 0 | Yes | Yes | 22 | 22.8 | -0.8 | 12BC7EE7A3A043CBBF6E546D710AA6C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-5319 |  | 2013-08-14 | 2013-08-14 13:27 | 2013-08-14 16:40 | CARRIER - 38CKB036330 | 82 | 9 | Yes | Yes | 20 | 19.7 | 0.3 | 0D01CDC6CF6D4265BE9EB3BAF25C1F3F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.98% | 0.89024 | 21.09% | [5 empty] | Non-TXV | 10.98%
Manteca | CA | 95336-3441 |  | 2013-07-09 | 2013-07-09 11:49 | 2013-07-09 12:13 | COLEMAN - UNK | 85 | 6 | Yes | Yes | 20.9 | 20.2 | 0.8 | 1B30B1DD948D48318710FA2D9B48152D |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Chowchilla | CA | 93610-2044 |  | 2013-07-30 | 2013-07-30 11:29 | 2013-08-02 03:14 | CARRIER - 38CK060370 | 135 | 5.5 | Yes | Yes | 19.9 | 20.2 | -0.3 | FC0603D169A947F790BBD309AF9F7373 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Stockton | CA | 95209-3004 |  | 2013-07-11 | 2013-07-11 11:35 | 2013-07-11 11:53 | RHEEM - RRAA-08E30AR | 45 | 3.8 | Yes | Yes | 25.2 | 20.6 | 4.6 | 86FA67A8530F4029B9BFF67D60E7E710 |  | R22 | Non-TXV |  | 8.444% | 0.91556 | 16.23% | [5 empty] | Non-TXV | 8.444%
Fresno | CA | 93727-6316 |  | 2013-07-23 | 2013-07-23 09:47 | 2013-07-23 09:49 | DAY & NIGHT - 585A036060YAC | 60 | 2.6 | Yes | Yes | 20.4 | 19.3 | 1.1 | F3010F8E23AA4F8A90BAC2AB183FE168 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Fresno | CA | 93727-6316 |  | 2013-07-23 | 2013-07-23 10:09 | 2013-07-23 10:11 | DAY & NIGHT - 585A036060YAC | 60 | 2.1 | Yes | Yes | 20.8 | 19.4 | 1.5 | 140C3ECF4AF5468083AF36C30DA24C31 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Chico | CA | 95926-2581 |  | 2013-07-01 | 2013-07-01 18:53 | 2013-07-01 19:13 | LENNOX - 13ACC-60-230-01 | 169 | 11 | Yes | Yes | 20 | 17.9 | 2.2 | 16A2792BB7E84F23A6C82FC872B66ACD |  | R22 | Non-TXV |  | 6.509% | 0.93491 | 12.51% | [5 empty] | Non-TXV | 6.509%
Madera | CA | 93637-5354 |  | 2013-07-09 | 2013-07-09 11:12 | 2013-07-09 11:12 | ARCOAIRE - PGAD36D1KB | 61 | 0 | Yes | Yes | 19.6 | 19.2 | 0.4 | 98E9ADE48DA2498D9B2BC2D5A2518413 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3210 |  | 2013-07-23 | 2013-07-23 13:26 | 2013-07-23 13:28 | CARRIER - 48SS-0420B0321 | 82 | 3.6 | Yes | Yes | 22 | 20.6 | 1.4 | 6809852BC6214021A3D29E38E9BE2DC7 |  | R22 | Non-TXV |  | 4.39% | 0.9561 | 8.437% | [5 empty] | Non-TXV | 4.39%
Madera | CA | 93638-5505 |  | 2013-07-24 | 2013-07-24 20:14 | 2013-07-24 20:39 | YORK - D1NA030N3606C | 85 | 4.1 | Yes | Yes | 19.4 | 21 | -1.6 | 3AF760A2B89C4CA9A5E15747997B39F3 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fresno | CA | 93703-3596 |  | 2013-09-23 | 2013-09-23 11:41 | 2013-09-23 11:42 | GOODMAN - GPG10300701A | 50 | 2.5 | Yes | Yes | 21.2 | 19.4 | 1.8 | 48024619BF274270A412C257F8113181 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Paradise | CA | 95969-2816 |  | 2013-08-26 | 2013-08-26 09:39 | 2013-08-26 09:39 | DAY & NIGHT - N2A336AKB300 | 84 | 0 | Yes | Yes | 20.5 | 19.3 | 1.2 | 4676E3A076D94956987FABF7AFEF8751 |  | R22 | TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9429 |  | 2013-07-11 | 2013-07-11 10:24 | 2013-07-11 10:25 | CARRIER - 48GS024040301 | 53 | 5.7 | Yes | Yes | 26.7 | 21 | 5.7 | BAFB2355C966403C8D74A94E5611083D |  | R22 | Non-TXV |  | 10.75% | 0.89245 | 20.67% | [5 empty] | Non-TXV | 10.75%
Stockton | CA | 95206-4640 |  | 2013-07-08 | 2013-07-08 12:39 | 2013-07-08 12:39 | PAYNE - PA13NA024-1B | 63 | 0 | Yes | Yes | 20.9 | 20.5 | 0.4 | 89026FAA6A50476BBA4912CB23D8C03C |  | R410A | TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1347 |  | 2013-07-31 | 2013-07-31 11:19 | 2013-07-31 11:21 | YORK - D1NA048N06506C | 92 | 12.6 | Yes | Yes | 20.4 | 18.2 | 2.2 | 3625136B7BE34476A7BC24901236A5B7 |  | R22 | Non-TXV |  | 13.7% | 0.86304 | 26.32% | [5 empty] | Non-TXV | 13.7%
Chico | CA | 95928-6898 |  | 2013-08-07 | 2013-08-07 17:49 | 2013-08-07 18:06 | CARRIER - 24ABA324A310 | 65 | 3.7 | Yes | Yes | 18.3 | 20.4 | -2.1 | 5A8F2DEF5A7B4CAE999C705B89B16856 |  | R410A | Non-TXV |  | 5.692% | 0.94308 | 10.94% | [5 empty] | Non-TXV | 5.692%
Placerville | CA | 95667-7761 |  | 2013-07-09 | 2013-07-09 11:44 | 2013-07-09 12:10 | GOODMAN - CK24-1B | 71 | -6.7 | Yes | Yes | 18 | 20.1 | -2.1 | F47AFFB9CF884F4EA35CFAB223117389 |  | R22 | Non-TXV |  | -9.437% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.437%
Chico | CA | 95926-2640 |  | 2013-07-31 | 2013-07-31 09:26 | 2013-07-31 09:42 | AMANA - PGB36C0702E | 64 | 2.2 | Yes | Yes | 21.5 | 18.7 | 2.8 | 5169A202CAA44B25B8F0F547D6B73A43 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Red Bluff | CA | 96080-8862 |  | 2013-08-13 | 2013-08-13 14:27 | 2013-08-13 14:27 | ARMSTRONG - 2PGE13E36068-1A | 101 | 0 | Yes | Yes | 20.8 | 20.4 | 0.4 | 63A46256169D4794BB77779A5C58ECF3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-2232 |  | 2013-08-22 | 2013-08-22 14:34 | 2013-08-22 15:53 | DAY & NIGHT - PHD324000K00C1 | 150 | 4.5 | Yes | Yes | 27.2 | 22 | 5.2 | 4BB4AEACC11948F8994B80E6C3D9EA22 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Orland | CA | 95963-1540 |  | 2013-08-15 | 2013-08-15 16:37 | 2013-08-15 18:17 | CARRIER - 48ESNA2406030TP | 72 | 2.2 | Yes | Yes | 19.1 | 20.4 | -1.3 | 47005FB47DA24F108595E40FD3DD936C |  | R410A | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Burson | CA | 95225-0000 |  | 2013-09-05 | 2013-09-05 16:09 | 2013-09-05 16:29 | TRANE - 4TTB4048E1000AA | 133 | 4.1 | Yes | Yes | 26.4 | 20.4 | 6 | 45A34A5EF95D46769AAA6149B0F62E27 |  | R410A | Non-TXV |  | 3.083% | 0.96917 | 5.924% | [5 empty] | Non-TXV | 3.083%
Fresno | CA | 93703-1734 |  | 2013-07-03 | 2013-07-03 12:38 | 2013-07-03 12:59 | GOODMAN - N/A | 90 | 3.6 | Yes | Yes | 23 | 20 | 3 | CB7659D013584BDDA2DEFB65BC3A5027 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95210-1162 |  | 2013-06-28 | 2013-06-28 09:26 | 2013-06-28 09:45 | AMANA - RCE24A2D | 150 | -8.8 | Yes | Yes | 20.8 | 17.9 | 2.9 | 1654C9A4258B481F84DCB0FA1D3708A7 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Nevada City | CA | 95959-9639 |  | 2013-09-11 | 2013-09-11 15:18 | 2013-09-11 15:18 | LENNOX - 10GCS042-100-1PA | 73 | 0 | Yes | Yes | 19.2 | 20.7 | -1.5 | E8E652584306490395DB0C61E81888B9 |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-6354 |  | 2013-07-10 | 2013-07-10 15:12 | 2013-07-10 15:14 | BRYANT - 561CJ036 | 70 | 13 | Yes | Yes | 21.1 | 21.5 | -0.4 | 2A7305DC021F4FD0BC5F8F38B60A3040 |  | R22 | TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | TXV | 18.57%
Diamond Springs | CA | 95619-9709 |  | 2013-09-06 | 2013-09-06 10:26 | 2013-09-06 10:26 | AMANA - RCB36B2A | 85 | 0 | Yes | Yes | 25.3 | 20.4 | 4.9 | FC06A1A737304EE3BC7724A761A987D9 |  | R22 | TXV |  | 0% | 1 | 0%
Mariposa | CA | 95338-9439 |  | 2013-08-21 | 2013-08-21 09:33 | 2013-08-21 09:37 | RHEEM - RRMAA036JK08X | 99 | 11.1 | Yes | Yes | 19.2 | 16.5 | 2.7 | 01AF6F4938284FC282E1B5B604F60A37 |  | R22 | Non-TXV |  | 11.21% | 0.88788 | 21.55% | [5 empty] | Non-TXV | 11.21%
Oroville | CA | 95965-4260 |  | 2013-08-06 | 2013-08-06 16:02 | 2013-08-06 20:40 | OTHER - CN421780C30S-01 | 77 | 15.7 | Yes | Yes | 19 | 20.4 | -1.4 | FC1BB53A551D444FA51A986943406953 |  | R22 | Non-TXV |  | 20.39% | 0.7961 | 39.18% | [5 empty] | Non-TXV | 20.39%
Wallace | CA | 95254-0000 |  | 2013-08-23 | 2013-08-23 13:56 | 2013-08-23 14:26 | BRYANT - 561CJ048-A | 99 | 13.6 | Yes | Yes | 19.6 | 19.8 | -0.2 | AEEFE7D896F84F1DA7DD8843AF324CD2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.74% | 0.86263 | 26.4% | [5 empty] | Non-TXV | 13.74%
Stockton | CA | 95210-1630 |  | 2013-06-27 | 2013-06-27 08:49 | 2013-06-27 09:07 | OTHER - UNK | 80 | 2.6 | Yes | Yes | 16.5 | 16.4 | 0.1 | B4D3A9B7757A468EB7E15F9D2858A676 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Stockton | CA | 95202-2719 |  | 2013-07-25 | 2013-07-25 13:39 | 2013-07-25 13:59 | BRYANT - 213RNA024-A | 96 | 5.8 | Yes | Yes | 19.5 | 19.9 | -0.4 | 1092B4015427457DAA7242275B7D9800 |  | R22 | Non-TXV |  | 6.042% | 0.93958 | 11.61% | [5 empty] | Non-TXV | 6.042%
Nevada City | CA | 95959-9342 |  | 2013-08-07 | 2013-08-07 09:25 | 2013-08-07 09:56 | HEIL - HAC248AKA1 | 148 | 41.4 | Yes | Yes | 18.5 | 20.8 | -2.3 | 7F2676AA7B48439A879724A8374D3368 |  | R22 | Non-TXV |  | 27.97% | 0.72027 | 53.76% | [5 empty] | Non-TXV | 27.97%
Fresno | CA | 93728-1505 |  | 2013-07-18 | 2013-07-18 10:21 | 2013-07-18 10:33 | OTHER - NRGF36DDB04 | 90 | 10 | Yes | Yes | 24.5 | 20.2 | 4.4 | 35A80B846B9746E9B93DAA279D8A0617 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Wallace | CA | 95254-0000 |  | 2013-10-01 | 2013-10-01 14:36 | 2013-10-01 14:56 | LENNOX - UNK | 71 | 7.5 | Yes | Yes | 20.5 | 19.7 | 0.8 | EBFEC9A4DC384EBA94C4FA2A10810D33 |  | R22 | Non-TXV |  | 10.56% | 0.89437 | 20.3% | [5 empty] | Non-TXV | 10.56%
Manteca | CA | 95336-3709 |  | 2013-07-17 | 2013-07-17 12:52 | 2013-07-17 13:12 | GOODMAN - GSC14346830241FA | 77 | 14.4 | Yes | Yes | 13.7 | 16.4 | -2.7 | 581CB7B2013F48FAB65D0C3D3AFCEA68 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.7% | 0.81299 | 35.94% | [5 empty] | Non-TXV | 18.7%
Madera | CA | 93638-1577 |  | 2013-07-25 | 2013-07-25 00:02 | 2013-07-25 01:14 | BDP - 595EA03075ABAP | 53 | 1.7 | Yes | Yes | 17.5 | 19.7 | -2.2 | 8688571892794B92BA7D16B02F56FB5A |  | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Madera | CA | 93637-4945 |  | 2013-07-09 | 2013-07-09 10:24 | 2013-07-10 07:46 | CARRIER - 563AN042-A | 136 | 10 | Yes | Yes | 21.5 | 18.1 | 3.4 | 2B11E76EA533408384983038565D58AB |  | R22 | Non-TXV |  | 7.353% | 0.92647 | 14.13% | [5 empty] | Non-TXV | 7.353%
Chico | CA | 95928-6815 |  | 2013-07-03 | 2013-07-03 17:22 | 2013-07-03 17:47 | YORK - D1NP036N05606A | 108 | 8.2 | Yes | Yes | 20.8 | 20.1 | 0.7 | 9999C0918CC041FB86B7AF0F592577BD |  | R22 | Non-TXV |  | 7.593% | 0.92407 | 14.59% | [5 empty] | Non-TXV | 7.593%
Madera | CA | 93638-7814 |  | 2013-07-25 | 2013-07-25 23:44 | 2013-07-26 00:02 | BRYANT - 583BNW042060NB | 146 | 5.3 | Yes | Yes | 19.5 | 20.4 | -0.9 | E39C7D2506EB496A9410673A8104A1BD |  | R22 | Non-TXV |  | 3.63% | 0.9637 | 6.976% | [5 empty] | Non-TXV | 3.63%
Manteca | CA | 95336-3431 |  | 2013-07-08 | 2013-07-08 13:21 | 2013-07-08 13:50 | AMANA - RCE30A2D | 53 | 1.9 | Yes | Yes | 17.4 | 19.2 | -1.8 | 05397B1954D74978B3418517FE81FD0C |  | R22 | Non-TXV |  | 3.585% | 0.96415 | 6.889% | [5 empty] | Non-TXV | 3.585%
Stockton | CA | 95210-3216 |  | 2013-08-14 | 2013-08-14 14:16 | 2013-08-14 14:34 | GOODMAN - CKL36-1D | 72 | 9.7 | Yes | Yes | 23.3 | 21.2 | 2.1 | A90E5FD8C54D43A7BF40623683034823 |  | R22 | Non-TXV |  | 13.47% | 0.86528 | 25.89% | [5 empty] | Non-TXV | 13.47%
Tracy | CA | 95376-2928 |  | 2013-07-11 | 2013-07-11 13:19 | 2013-07-11 13:36 | CARRIER - UNK | 85 | 6.3 | Yes | Yes | 23 | 21 | 2 | 4F3C457CAAFD4055A49AC256AE30419B |  | R22 | Non-TXV |  | 7.412% | 0.92588 | 14.24% | [5 empty] | Non-TXV | 7.412%
Fresno | CA | 93703-1733 |  | 2013-07-03 | 2013-07-03 12:02 | 2013-07-03 12:59 | YORK - DAYP-F048N080A | 132 | 5.1 | Yes | Yes | 18.1 | 20.4 | -2.3 | 1192B8708EF44BBB8B78053490773110 |  | R22 | Non-TXV |  | 3.864% | 0.96136 | 7.425% | [5 empty] | Non-TXV | 3.864%
Madera | CA | 93638-9635 |  | 2013-07-27 | 2013-07-27 00:04 | 2013-07-27 00:54 | GUARDIAN - PGB042075-REV A | 72 | 8 | Yes | Yes | 20 | 19.8 | 0.2 | A4BD0A84D62C412A925801679CD86C47 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Reedley | CA | 93654-2558 |  | 2013-08-08 | 2013-08-08 10:45 | 2013-08-08 11:06 | YORK - D1GA030N04806A | 80 | 7.2 | Yes | Yes | 20.6 | 20.4 | 0.2 | 2DBCC24C49B243068F38F86186365E84 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Madera | CA | 93638-7809 |  | 2013-07-26 | 2013-07-26 13:40 | 2013-07-26 14:04 | CARRIER - 48GX-03606301 | 81 | 4.2 | Yes | Yes | 20.4 | 21 | -0.6 | BEFFB8FAE38E47B188918627EDC26429 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Fresno | CA | 93726-0884 |  | 2013-07-26 | 2013-07-26 10:21 | 2013-07-26 10:23 | PAYNE - UNK | 56 | 8.1 | Yes | Yes | 22.6 | 19.9 | 2.7 | 13AC4320F7C84078A565A4FE11A8C7E3 |  | R22 | Non-TXV |  | 14.46% | 0.85536 | 27.8% | [5 empty] | Non-TXV | 14.46%
Reedley | CA | 93654-2558 |  | 2013-07-24 | 2013-07-24 16:00 | 2013-07-24 16:26 | YORK - D1GA030N03206B | 80 | 9 | Yes | Yes | 19.9 | 19.2 | 0.7 | 31C168176A694A939FDB3B205E14DCD6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Fresno | CA | 93722-5259 |  | 2013-07-16 | 2013-07-16 15:38 | 2013-07-16 15:39 | CARRIER - 585CJ030040 | 68 | 10.7 | Yes | Yes | 22.3 | 19.3 | 3 | 4FF8A421F72B4292A5204F163A60BE04 |  | R22 | Non-TXV |  | 15.74% | 0.84265 | 30.24% | [5 empty] | Non-TXV | 15.74%
Cool | CA | 95614-9533 |  | 2013-08-13 | 2013-08-13 09:28 | 2013-08-13 09:54 | YORK - B1SP030A06A | 81 | 7.4 | Yes | Yes | 20.6 | 20.1 | 0.5 | 503D9F449ABA4DAD96186BA4A4D3A5A2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.136% | 0.90864 | 17.56% | [5 empty] | Non-TXV | 9.136%
Fresno | CA | 93726-1249 |  | 2013-08-12 | 2013-08-12 12:49 | 2013-08-12 13:08 | RHEEM - RRNL-B024JK06X | 77 | 4.8 | Yes | Yes | 19.2 | 19.2 | 0 | 545D4B8E1DA942BC8B7725118CF06774 |  | R410A | Non-TXV |  | 6.234% | 0.93766 | 11.98% | [5 empty] | Non-TXV | 6.234%
Chico | CA | 95926-2050 |  | 2013-08-01 | 2013-08-01 14:02 | 2013-08-01 19:00 | ICP - PGC024K060D | 58 | 3 | Yes | Yes | 17.5 | 20.4 | -2.9 | C62ECB10990343068C67C3E2359C6F33 |  | R22 | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Corning | CA | 96021-0000 |  | 2013-10-25 | 2013-10-25 15:27 | 2013-10-25 15:43 | DUCANE - AC10B4B48 | 71 | 7.5 | Yes | Yes | 19.8 | 20.9 | -1.1 | 66F75F713F964306954A779B7764BB56 |  | R22 | Non-TXV |  | 10.56% | 0.89437 | 20.3% | [5 empty] | Non-TXV | 10.56%
Meadow Vista | CA | 95722-9705 |  | 2013-08-14 | 2013-08-14 10:46 | 2013-08-14 11:05 | COLEMAN - DRCS0361BB | 100 | 3.1 | Yes | Yes | 17 | 19.1 | -2.1 | 3D2519E682104E8D91FE371E31641D5A |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Los Banos | CA | 93635-6354 |  | 2013-07-12 | 2013-07-12 10:05 | 2013-07-12 10:11 | BRYANT - 561CJ048 | 99 | 14.3 | Yes | Yes | 20.2 | 21 | -0.8 | 8D22455ACF2A46E9AACF1E7C367441D4 |  | R22 | TXV |  | 14.44% | 0.85556 | 27.76% | [5 empty] | TXV | 14.44%
Stockton | CA | 95206-5819 |  | 2013-08-28 | 2013-08-28 10:50 | 2013-08-28 11:11 | RUUD - UAFD-048JBS | 101 | 4.7 | Yes | Yes | 19.9 | 18 | 1.9 | 4A6FDCD31E754B75BFA546A5E3B5DC88 |  | R22 | Non-TXV |  | 4.653% | 0.95347 | 8.943% | [5 empty] | Non-TXV | 4.653%
Fresno | CA | 93722-2286 |  | 2013-07-18 | 2013-07-18 13:24 | 2013-07-18 13:26 | WEATHER KING - 10AJA4801 | 106 | 14.6 | Yes | Yes | 17.7 | 19.8 | -2.1 | 7CA21FE4032E45439D94840F19CE4145 |  | R22 | Non-TXV |  | 13.77% | 0.86226 | 26.47% | [5 empty] | Non-TXV | 13.77%
Magalia | CA | 95954-9436 |  | 2013-07-18 | 2013-07-18 08:52 | 2013-07-18 09:18 | CARRIER - NA | 114 | 3.5 | Yes | Yes | 23.5 | 17.9 | 5.6 | 0057BB7DF33E4E93BAE41EFFC475FB96 |  | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
Stockton | CA | 95215-6076 |  | 2013-07-02 | 2013-07-02 09:02 | 2013-07-02 09:29 | OTHER - 60WE24G1NA | 52 | 2.8 | Yes | Yes | 16.2 | 18.8 | -2.6 | BA9D3552285342ACA9E6E0FC80909024 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.385% | 0.94615 | 10.35% | [5 empty] | Non-TXV | 5.385%
Stockton | CA | 95212-3838 |  | 2013-07-23 | 2013-07-23 14:58 | 2013-07-23 14:58 | CARRIER - 38CKC060370 | 99 | 0 | Yes | Yes | 22.1 | 21.2 | 0.9 | 5B07A77D626C4BEBB7DF107EA4F08073 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1500 |  | 2013-07-23 | 2013-07-23 16:02 | 2013-07-23 16:02 | TRANE - TTD724B100B0 | 60 | 0 | Yes | Yes | 21.6 | 20.1 | 1.6 | 400C61D4AC894FF99D972522BF3E233E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1500 |  | 2013-07-23 | 2013-07-23 16:16 | 2013-07-23 16:22 | TRANE - TTD724B100B0 | 60 | 2.9 | Yes | Yes | 21 | 19.2 | 1.8 | 80EA9D1460F941A0928ABDFA2A489B46 |  | R22 | Non-TXV |  | 4.833% | 0.95167 | 9.289% | [5 empty] | Non-TXV | 4.833%
Stockton | CA | 95215-5225 |  | 2013-06-28 | 2013-06-28 11:16 | 2013-06-28 11:46 | ICP - PGC030K060E | 85 | 3.4 | Yes | Yes | 16.3 | 18.5 | -2.2 | 57F0FDD46AA548C0B1EE19099A95EFF0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Chico | CA | 95973-7871 |  | 2013-09-04 | 2013-09-04 00:57 | 2013-09-04 11:30 | TRANE - 2TTRO42A1000AA | 109 | 8.9 | Yes | Yes | 26.4 | 20.8 | 5.6 | E0A4B43869854F2EBCC60E600F38D3BD |  | R22 | Non-TXV |  | 8.165% | 0.91835 | 15.69% | [5 empty] | Non-TXV | 8.165%
Orange Cove | CA | 93646-2209 |  | 2013-08-14 | 2013-08-14 10:38 | 2013-08-14 11:47 | UNITARY PRODUCTS GROUP - DBYP-F036N070A | 108 | 3.4 | Yes | Yes | 18 | 20.7 | -2.7 | C75699B8133F43228FAAB7EF8D68F908 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Chowchilla | CA | 93610-9770 |  | 2013-06-28 | 2013-06-28 19:42 | 2013-06-28 20:02 | CARRIER - UNK | 76 | 5 | Yes | Yes | 19 | 17.7 | 1.3 | 52FBF824F3BE48A4B5C561926F54FC38 |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Merced | CA | 95341-6621 |  | 2013-07-12 | 2013-07-12 16:19 | 2013-07-12 16:21 | GOODMAN - PGB024050-1 | 54 | 2.1 | Yes | Yes | 18 | 17.5 | 0.5 | 8A01EECEE9064BC59B89534F3D82B96B |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Stockton | CA | 95215-5435 |  | 2013-09-12 | 2013-09-12 12:50 | 2013-09-12 13:09 | YORK - D3GH036N07006A | 115 | 5.3 | Yes | Yes | 17 | 18.1 | -1.1 | 513F722A3F4241AFB6A494AE8E42A7CD |  | R22 | Non-TXV |  | 4.609% | 0.95391 | 8.857% | [5 empty] | Non-TXV | 4.609%
Stockton | CA | 95207-1533 |  | 2013-07-17 | 2013-07-17 12:55 | 2013-07-17 13:15 | RHEEM - RRNL-BO30JK06X | 77 | 3.6 | Yes | Yes | 18.7 | 18.6 | 0.1 | 41F8811EFDD04CD2AB0D0E5B85297238 |  | R410A | TXV |  | 4.675% | 0.95325 | 8.985% | [5 empty] | TXV | 4.675%
Stockton | CA | 95210-4131 |  | 2013-07-09 | 2013-07-09 11:03 | 2013-07-09 11:19 | RHEEM - RRGF-05E30JKR | 46 | -2.7 | Yes | Yes | 25.6 | 19.7 | 5.9 | 4A98B942A95448C7A03434C54B908650 |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Stockton | CA | 95206-4686 |  | 2013-07-12 | 2013-07-12 10:41 | 2013-07-12 11:06 | YORK - H1RA048S06D | 117 | 3.6 | Yes | Yes | 28.6 | 23.7 | 4.9 | 8849DE14579A4DA8B63F1A639FE919A4 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Winton | CA | 95388-9429 |  | 2013-07-11 | 2013-07-11 10:50 | 2013-07-11 10:51 | CARRIER - 48GS030040301 | 55 | 4.9 | Yes | Yes | 22.7 | 19.7 | 3 | 29B921EA85FD48038B3A2C7EDD3442AD |  | R22 | Non-TXV |  | 8.909% | 0.91091 | 17.12% | [5 empty] | Non-TXV | 8.909%
Fresno | CA | 93703-3598 |  | 2013-08-09 | 2013-08-09 09:34 | 2013-08-09 09:34 | GOODMAN - GPG10300701A | 50 | 0 | Yes | Yes | 22.7 | 20.4 | 2.3 | B9B0C93856D94E19BCDE4A63CD24A879 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1989 |  | 2013-07-31 | 2013-07-31 15:25 | 2013-07-31 15:26 | CARRIER - 48SDN036060301 | 167 | 25.4 | Yes | Yes | 18 | 17.9 | 0.1 | 840A1CF5C2B844B8B7C32E603938411E |  | R22 | Non-TXV |  | 15.21% | 0.8479 | 29.23% | [5 empty] | Non-TXV | 15.21%
Stockton | CA | 95206-5719 |  | 2013-06-27 | 2013-06-27 11:20 | 2013-06-27 11:57 | YORK - H1RA036S06A | 69 | 9.1 | Yes | Yes | 18.5 | 19.7 | -1.2 | 6D3601D69A5B4968ACBF2ABAF1EC5877 |  | R22 | Non-TXV |  | 13.19% | 0.86812 | 25.35% | [5 empty] | Non-TXV | 13.19%
Cameron Park | CA | 95682-8626 |  | 2013-07-05 | 2013-07-05 09:45 | 2013-07-05 10:24 | TRANE - TWP048C100A3 | 157 | 12.4 | Yes | Yes | 20.5 | 19.7 | 0.8 | 8C17F3D1E527443FB62143066CD2262B |  | R22 | Non-TXV |  | 7.898% | 0.92102 | 15.18% | [5 empty] | Non-TXV | 7.898%
Oakdale | CA | 95361-3206 |  | 2013-07-09 | 2013-07-09 14:12 | 2013-07-09 14:35 | PAYNE - PA10JA036-C | 73 | 9.1 | Yes | Yes | 25.7 | 20.4 | 5.3 | 6E0BE78925BA485EB64BB081E9B32462 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.47% | 0.87534 | 23.96% | [5 empty] | Non-TXV | 12.47%
Fresno | CA | 93703-4045 |  | 2013-08-08 | 2013-08-08 12:21 | 2013-08-08 12:23 | GOODMAN - GSZ130361BB | 128 | 9.2 | Yes | Yes | 20.1 | 21.5 | -1.4 | 759DF4437ECB4408B159C60DD60DE2D3 |  | R410A | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Stockton | CA | 95212-3207 |  | 2013-07-15 | 2013-07-15 11:46 | 2013-07-15 12:07 | GOODMAN - CLJ36-1A | 109 | 4 | Yes | Yes | 23.1 | 21 | 2.1 | 6C9310DB76A046369F927808803A79F3 |  | R22 | Non-TXV |  | 3.67% | 0.9633 | 7.052% | [5 empty] | Non-TXV | 3.67%
Kerman | CA | 93630-1511 |  | 2013-08-13 | 2013-08-13 19:02 | 2013-08-13 19:53 | YORK - D1NP03605606A | 108 | 3.2 | Yes | Yes | 18.5 | 20.7 | -2.2 | 505F3FC5FC87481895F2DB1217FBAC06 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93711-1424 |  | 2013-08-10 | 2013-08-10 11:29 | 2013-08-10 11:29 | BDP - 367C042RCU | 116 | 0 | Yes | Yes | 18.4 | 19.3 | -0.9 | 220B36F4067B4BA3B26F60D9A75EE7CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1439 |  | 2013-06-27 | 2013-06-27 13:01 | 2013-06-27 13:20 | GE - BGYC036A1B08 | 124 | 11.4 | Yes | Yes | 18 | 18.9 | -0.9 | 4EA1A2E2023247CEA32D13EFA33BF0C7 |  | R22 | Non-TXV |  | 9.194% | 0.90806 | 17.67% | [5 empty] | Non-TXV | 9.194%
Kerman | CA | 93630-1221 |  | 2013-08-13 | 2013-08-13 17:06 | 2013-08-13 22:26 | BDP - 585HJW042060ABAF | 80 | 2.6 | Yes | Yes | 22.5 | 19.6 | 2.9 | 6EA0E46C1922442D85C69DBF9146311C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Stockton | CA | 95215-5208 |  | 2013-07-02 | 2013-07-02 09:37 | 2013-07-02 10:03 | AMANA - PGB24C0452E | 64 | 11.1 | Yes | Yes | 24.9 | 19.5 | 5.4 | 953D464F9FC049FCBE853CA5865B4161 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.34% | 0.82656 | 33.33% | [5 empty] | Non-TXV | 17.34%
Atascadero | CA | 93422-5567 |  | 2013-09-06 | 2013-09-06 12:54 | 2013-09-06 13:14 | HEIL - NAC218AKA2 | 71 | 2.1 | Yes | Yes | 25.1 | 19.1 | 6 | E32D779CEF73484DAF9B5DCFCD888CCF |  | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Fresno | CA | 93711-3045 |  | 2013-07-22 | 2013-07-22 11:00 | 2013-07-22 11:01 | GOODMAN - PGB024050 | 54 | 8.4 | Yes | Yes | 23.4 | 21.4 | 2 | E6FE7B2BB3A34462820CDAF1D82C0C50 |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Fresno | CA | 93711-3045 |  | 2013-07-22 | 2013-07-22 11:11 | 2013-07-22 11:13 | GOODMAN - PGB024050 | 54 | 6.9 | Yes | Yes | 25.3 | 20.4 | 4.9 | A2A409559C1444FDB5B6DA254ED310D9 |  | R22 | Non-TXV |  | 12.78% | 0.87222 | 24.56% | [5 empty] | Non-TXV | 12.78%
Magalia | CA | 95954-9568 |  | 2013-07-18 | 2013-07-18 14:06 | 2013-07-18 14:48 | DAY & NIGHT - 50QQ024340 | 119 | 12.5 | Yes | Yes | 15.4 | 17.8 | -2.4 | A961F48707334FC991FE829B4CB22722 |  | R22 | Non-TXV |  | 10.5% | 0.89496 | 20.19% | [5 empty] | Non-TXV | 10.5%
Fresno | CA | 93727-1828 |  | 2013-07-16 | 2013-07-16 10:07 | 2013-07-16 10:38 | GOODMAN - GPG13420701AB | 107 | 3.4 | Yes | Yes | 20.5 | 20.2 | 0.4 | 3E96A36C125B488381A9595F442E0218 |  | R22 | Non-TXV |  | 3.178% | 0.96822 | 6.107% | [5 empty] | Non-TXV | 3.178%
Atascadero | CA | 93422-5567 |  | 2013-08-13 | 2013-08-13 15:38 | 2013-08-13 15:54 | HEIL - NAC218AKC3 | 80 | 4.5 | Yes | Yes | 19.4 | 20.7 | -1.3 | 495E4AE0601B4535A79797E5263F9589 |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Fresno | CA | 93726-1838 |  | 2013-07-30 | 2013-07-30 08:46 | 2013-07-30 08:47 | BDP - 589ANW048080ADBG | 88 | 6.6 | Yes | Yes | 22.7 | 20.4 | 2.3 | D792A0BEF20E4CB49D4016CE0C04C35D |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Atascadero | CA | 93422-5516 |  | 2013-08-08 | 2013-08-08 13:47 | 2013-08-08 14:08 | NORDYNE - JS5BD-024KB | 53 | 1.7 | Yes | Yes | 18.5 | 19.1 | -0.6 | 2257B4DE41754407B8F511B6290DF41C |  | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Manteca | CA | 95336-5034 |  | 2013-07-12 | 2013-07-12 11:15 | 2013-07-12 11:43 | GE - UNK | 85 | -8 | Yes | Yes | 25 | 20.2 | 4.8 | 9947399238FB47A1853F00C7DFBB4D5F |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Tracy | CA | 95376-2453 |  | 2013-07-16 | 2013-07-16 14:11 | 2013-07-16 14:34 | RHEEM - RAHE-048JAS | 85 | 8.3 | Yes | Yes | 17.2 | 16.8 | 0.4 | 18A53FFF3CB148F98FC103EFAA0B57A6 |  | R22 | Non-TXV |  | 9.765% | 0.90235 | 18.77% | [5 empty] | Non-TXV | 9.765%
Chowchilla | CA | 93610-0000 |  | 2013-08-28 | 2013-08-28 14:50 | 2013-08-28 15:15 | CARRIER - UNK | 66 | 3 | Yes | Yes | 17.6 | 20.1 | -2.5 | 35F08F6510D548F382BDEC963B494304 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Manteca | CA | 95336-6200 |  | 2013-08-16 | 2013-08-16 13:06 | 2013-08-16 13:27 | TRANE - TTD748A100A0 | 118 | 3.5 | Yes | Yes | 23.9 | 19.1 | 4.8 | 0039B839591145769693B39375C10E95 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Fresno | CA | 93703-4736 |  | 2013-09-23 | 2013-09-23 12:09 | 2013-09-23 12:11 | RUUD - 7777UNK | 80 | 3.3 | Yes | Yes | 20.1 | 19.9 | 0.2 | 68AB37B94CE840BB855174DAF7A9DE44 |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Manteca | CA | 95336-2930 |  | 2013-07-09 | 2013-07-09 10:32 | 2013-07-09 10:56 | GOODMAN - GSC130361GA | 85 | 3 | Yes | Yes | 19.4 | 19.3 | 0.1 | 4CE545D37E7D467CA49588D7C9948289 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Le Grand | CA | 95333-9790 |  | 2013-08-14 | 2013-08-14 15:38 | 2013-08-14 15:39 | DAY & NIGHT - UNK | 68 | 10.6 | Yes | Yes | 24.6 | 21.9 | 2.7 | 0B38C4E87B82400FBE531D804C4CD1EB |  | R22 | Non-TXV |  | 15.59% | 0.84412 | 29.96% | [5 empty] | Non-TXV | 15.59%
Fresno | CA | 93722-6758 |  | 2013-07-15 | 2013-07-15 11:19 | 2013-07-15 11:21 | YORK - D5YS036N04506A | 80 | 8.8 | Yes | Yes | 26.4 | 23.7 | 2.7 | 7FB5BC67BC7047539B7004D41C7DFF3E |  | R22 | Non-TXV |  | 11% | 0.89 | 21.14% | [5 empty] | Non-TXV | 11%
Reedley | CA | 93654-3029 |  | 2013-08-26 | 2013-08-26 16:53 | 2013-08-26 19:36 | CARRIER - 48GS-024040301 | 53 | 1.7 | Yes | Yes | 16.7 | 19.3 | -2.6 | 05D5A57450F4494C98FAA2CDB21C171F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Le Grand | CA | 95333-0000 |  | 2013-08-14 | 2013-08-14 14:59 | 2013-08-14 15:00 | YORK - DAYPF036N070A | 108 | 12.6 | Yes | Yes | 28.2 | 23.5 | 4.7 | 0491CA7AF43945B1BC9B60004618A6FD |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Fresno | CA | 93722-5528 |  | 2013-07-25 | 2013-07-25 14:42 | 2013-07-25 14:44 | ICP - GPCM042K080D | 84 | 14.3 | Yes | Yes | 24.5 | 21.5 | 3 | 530791073F5E4EE9A133A2EBB0299DAB |  | R22 | Non-TXV |  | 17.02% | 0.82976 | 32.72% | [5 empty] | Non-TXV | 17.02%
Fresno | CA | 93726-1009 |  | 2013-08-07 | 2013-08-07 16:00 | 2013-08-07 16:03 | GOODMAN - CK24-1B | 71 | 3.6 | Yes | Yes | 20.8 | 20.4 | 0.4 | 539D3BE52E544383BE6A5A4F11864552 |  | R22 | Non-TXV |  | 5.07% | 0.9493 | 9.744% | [5 empty] | Non-TXV | 5.07%
Fresno | CA | 93720-0506 |  | 2013-06-26 | 2013-06-26 11:35 | 2013-06-26 11:40 | OTHER - FADC-036JAS | 80 | 3.3 | Yes | Yes | 14.7 | 16.8 | -2.1 | 387DC356A7EB417F93840C664A1E208E |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Atascadero | CA | 93422-5896 |  | 2013-08-07 | 2013-08-07 11:15 | 2013-08-07 11:40 | RHEEM - UNK | 51 | -3 | Yes | Yes | 23.4 | 18 | 5.5 | 1753A098C6954535819BA6B872784A16 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Parlier | CA | 93648-2127 |  | 2013-07-25 | 2013-07-25 09:06 | 2013-07-25 10:13 | RUUD - N/A | 90 | 4.6 | Yes | Yes | 18.1 | 21 | -2.9 | 3CCA6A89D0674FD6B9C625A8E29A424A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.111% | 0.94889 | 9.822% | [5 empty] | Non-TXV | 5.111%
Fresno | CA | 93710-4323 |  | 2013-07-23 | 2013-07-23 09:39 | 2013-07-23 09:40 | GOODMAN - GPG13360701A | 112 | 9.7 | Yes | Yes | 24.5 | 19.3 | 5.2 | CC72F9D7697B448DAAA53AF8DABA9DE1 |  | R22 | Non-TXV |  | 8.661% | 0.91339 | 16.64% | [5 empty] | Non-TXV | 8.661%
Fresno | CA | 93722-6346 |  | 2013-07-17 | 2013-07-17 11:44 | 2013-07-17 11:46 | DAY & NIGHT - UNK | 68 | 11.2 | Yes | Yes | 18.1 | 19.5 | -1.4 | 77736F98868F4A8C920479DA57A90C65 |  | R22 | Non-TXV |  | 16.47% | 0.83529 | 31.65% | [5 empty] | Non-TXV | 16.47%
Fresno | CA | 93703-3307 |  | 2013-08-16 | 2013-08-16 10:27 | 2013-08-16 10:29 | YORK - D1NP036N05606A | 108 | 16.4 | Yes | Yes | 21.8 | 17.6 | 4.2 | 1C6335C2F2004582B7F5689797DA2C3C |  | R22 | Non-TXV |  | 15.19% | 0.84815 | 29.18% | [5 empty] | Non-TXV | 15.19%
Atwater | CA | 95301-2470 |  | 2013-06-26 | 2013-06-26 15:59 | 2013-06-26 16:22 | COLEMAN - UNK | 56 | 7.4 | Yes | Yes | 24.2 | 22.4 | 1.8 | 0514D6A2A51C4A1C82EE2FFD7FACBE83 |  | R22 | Non-TXV |  | 13.21% | 0.86786 | 25.39% | [5 empty] | Non-TXV | 13.21%
Corning | CA | 96021-9631 |  | 2013-07-23 | 2013-07-23 18:51 | 2013-07-23 19:09 | PAYNE - 542E1X0360DAAAE | 132 | 6 | Yes | Yes | 12.3 | 15.2 | -2.9 | C2AAC0A710034816A89954C42242761F |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Oakdale | CA | 95361-2814 |  | 2013-09-11 | 2013-09-11 10:48 | 2013-09-11 11:17 | DAY & NIGHT - CBD | 64 | 6 | Yes | Yes | 18.8 | 18.8 | 0 | 9DC6C81421E2479795546EA70C5E8C33 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Kelsey | CA | 95667-0000 |  | 2013-10-03 | 2013-10-03 13:57 | 2013-10-03 14:25 | AMERICAN STANDARD - 2A7B036A1000AA | 101 | -5.9 | Yes | Yes | 26.9 | 21.1 | 5.9 | 13D832D89BE54D16AFD111061EAD8B62 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Durham | CA | 95938-9615 |  | 2013-09-06 | 2013-09-06 09:32 | 2013-09-06 10:46 | LENNOX - GCS20H-311-75-3P | 48 | 2.2 | Yes | Yes | 21.8 | 20.8 | 1 | 4CF03D9BC32444F8AB5044A478FBF4A1 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Manteca | CA | 95336-2876 |  | 2013-06-28 | 2013-06-28 10:50 | 2013-06-28 11:15 | DAY & NIGHT - 585HJ018040 | 61 | 9.8 | Yes | Yes | 19.8 | 18 | 1.8 | E6A17B6D1D0142DFB9F65246FF76A581 |  | R22 | Non-TXV |  | 16.07% | 0.83934 | 30.87% | [5 empty] | Non-TXV | 16.07%
Stockton | CA | 95215-7538 |  | 2013-07-02 | 2013-07-02 11:34 | 2013-07-02 12:11 | GOODMAN - GPG103007?? | 55 | 4 | Yes | Yes | 22.3 | 18.6 | 3.7 | 56DE877B525A4EC2ACCEB77631282250 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Merced | CA | 95341-6627 |  | 2013-07-09 | 2013-07-09 11:56 | 2013-07-09 11:58 | GOODMAN - GBG13360701AB | 112 | 6.4 | Yes | Yes | 26.1 | 20.1 | 6 | 2CB5E651A077453DA38B185E84B69A30 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Grass Valley | CA | 95945-9768 |  | 2013-06-29 | 2013-06-29 13:01 | 2013-06-29 13:01 | CARRIER - 24ABA342A300 | 99 | 0 | Yes | Yes | 16.8 | 18.6 | -1.8 | 2A49B09F7C65413E8B8F2439269DD692 |  | R410A | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-2615 |  | 2013-07-08 | 2013-07-08 12:49 | 2013-07-08 13:11 | RHEEM - RRNA-B042JK08X | 85 | 6.1 | Yes | Yes | 27.5 | 21.5 | 6 | 860F861026C14B62887587087D6F6922 |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Grass Valley | CA | 95945-6622 |  | 2013-08-23 | 2013-08-23 12:39 | 2013-08-23 12:39 | CARRIER - 585CJ02450 | 69 | 0 | Yes | Yes | 19.4 | 19.7 | -0.3 | D15146850C1D4CBA9B76D08AF25089C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6653 |  | 2013-07-16 | 2013-07-16 17:07 | 2013-07-16 17:34 | - 563CN036-C | 101 | 8.2 | Yes | Yes | 21.3 | 19.7 | 1.6 | EAA47CE4CB2142DD9857C9DED2EEA905 |  | R22 | Non-TXV |  | 8.119% | 0.91881 | 15.6% | [5 empty] | Non-TXV | 8.119%
Manteca | CA | 95337-6653 |  | 2013-07-16 | 2013-07-16 17:24 | 2013-07-16 17:48 | - 563CN036-C | 101 | 3.5 | Yes | Yes | 21.2 | 19.2 | 2 | D224F8E36FC74303B92774F6FAF1618A |  | R22 | Non-TXV |  | 3.465% | 0.96535 | 6.66% | [5 empty] | Non-TXV | 3.465%
Lodi | CA | 95242-9621 |  | 2013-08-20 | 2013-08-20 15:08 | 2013-08-20 15:58 | TRANE - YCC030F1M0BH | 69 | 6.7 | Yes | Yes | 23.4 | 21.7 | 1.7 | E9AC69071B83452A9BBF821CAFB1BDE0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.71% | 0.9029 | 18.66% | [5 empty] | Non-TXV | 9.71%
San Miguel | CA | 93451-0000 |  | 2013-08-13 | 2013-08-13 12:14 | 2013-08-13 12:41 | GOODMAN - CK301A | 76 | 5 | Yes | Yes | 22.6 | 19.6 | 3 | DFCB2F55FE1A4C0E8C5105F04FBCA144 |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Merced | CA | 95341-6627 |  | 2013-07-01 | 2013-07-01 13:35 | 2013-07-01 13:37 | OTHER - 7777UNK | 84 | 3.3 | Yes | Yes | 23.3 | 20.8 | 2.5 | 2A85E30614834DBABE13F0483D0A790A |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Chowchilla | CA | 93610-8011 |  | 2013-07-29 | 2013-07-29 12:04 | 2013-07-30 10:49 | BRYANT - 561CJ060-H | 53 | 5.3 | Yes | Yes | 18.1 | 20.2 | -2.1 | BB93A8D5878F43CB9AF75535075BC83F |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Willows | CA | 95988-3536 |  | 2013-08-14 | 2013-08-14 17:26 | 2013-08-14 17:44 | WEATHER KING - 10AJB18401 | 52 | 3 | Yes | Yes | 19.5 | 21.2 | -1.7 | CE3057F69A0B4414B56477C85F675A3C |  | R22 | Non-TXV |  | 5.769% | 0.94231 | 11.09% | [5 empty] | Non-TXV | 5.769%
Colfax | CA | 95713-9690 |  | 2013-07-26 | 2013-07-26 12:50 | 2013-07-26 13:16 | DAY & NIGHT - UNK | 95 | 4.8 | Yes | Yes | 26 | 20.9 | 5.1 | A464BA2909A34F42800A78583B7CD5AE |  | R22 | TXV |  | 5.053% | 0.94947 | 9.71% | [5 empty] | TXV | 5.053%
Chico | CA | 95926-1662 |  | 2013-07-31 | 2013-07-31 15:26 | 2013-07-31 15:50 | COLEMAN - 9530C901 | 51 | 14.7 | Yes | Yes | 21.4 | 20.4 | 1 | 0CE587CBF18846D0B22A9F236E1BC610 |  | R22 | Non-TXV |  | 28.82% | 0.71176 | 55.39% | [5 empty] | Non-TXV | 28.82%
Yuba City | CA | 95993-9126 |  | 2013-08-07 | 2013-08-07 17:35 | 2013-08-07 17:59 | CARRIER - 24ABA336A310 | 85 | 9.7 | Yes | Yes | 18 | 20.4 | -2.4 | D2E56FE62B7D46C5BA0878CEDEB0A7D3 |  | R410A | TXV |  | 11.41% | 0.88588 | 21.93% | [5 empty] | TXV | 11.41%
Atascadero | CA | 93422-5875 |  | 2013-09-03 | 2013-09-03 13:54 | 2013-09-03 14:16 | RHEEM - UNK | 50 | 2.6 | Yes | Yes | 15.9 | 17 | -1.1 | BDE543A8EF7D46AC89408AABEF436895 |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Los Banos | CA | 93635-3273 |  | 2013-08-21 | 2013-08-21 14:48 | 2013-08-21 14:49 | DAY & NIGHT - 7777UNK | 86 | 4.1 | Yes | Yes | 22.6 | 21.2 | 1.4 | 8F0EC69695414D3889EE22B47666A804 |  | R22 | Non-TXV |  | 4.767% | 0.95233 | 9.162% | [5 empty] | Non-TXV | 4.767%
Paso Robles | CA | 93446-3523 |  | 2013-08-06 | 2013-08-06 12:34 | 2013-08-06 12:52 | YORK - D1NH042N06506C | 94 | -5.5 | Yes | Yes | 26.3 | 20.4 | 5.9 | C9990B55384849798B2041770AAA7EF5 |  | R22 | Non-TXV |  | -5.851% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.851%
Corning | CA | 96021-2415 |  | 2013-07-22 | 2013-07-22 18:34 | 2013-07-22 18:34 | RUUD - RRPL-B036JK08E | 92 | 0 | Yes | Yes | 22 | 22.2 | -0.1 | B7C3193D95B5496B85D49C938E175E33 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-4331 |  | 2013-07-15 | 2013-07-15 10:24 | 2013-07-15 10:24 | CARRIER - 38CKC060--371-- | 62 | 0 | Yes | Yes | 18.7 | 17.8 | 1 | 7F655F7D3B274D0883780E920E853FEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-5485 |  | 2013-07-29 | 2013-07-29 10:51 | 2013-07-29 11:08 | CARRIER - 36EN018310 | 55 | 2.9 | Yes | Yes | 23.2 | 17.6 | 5.6 | A577AECCB1F54A78BDD1A716E2028870 |  | R22 | Non-TXV |  | 5.273% | 0.94727 | 10.13% | [5 empty] | Non-TXV | 5.273%
Dinuba | CA | 93618-3356 |  | 2013-07-26 | 2013-07-26 11:23 | 2013-07-26 11:43 | CARRIER - 585HJW030040ACAF | 68 | -4 | Yes | Yes | 20 | 20.9 | -0.9 | 480FAC6FC2584D1F8E9F7A8B569EBEB7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Atwater | CA | 95301-2341 |  | 2013-08-13 | 2013-08-13 09:42 | 2013-08-13 10:11 | TRANE - YCC036F1M0BA | 83 | 2.8 | Yes | Yes | 18 | 18.8 | -0.8 | 6B98CF1AEB054A308A8467601A629ECB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Chowchilla | CA | 93610-8024 |  | 2013-09-10 | 2013-09-10 16:05 | 2013-09-10 16:07 | CARRIER - 38CKC060370 | 131 | 16 | Yes | Yes | 21.4 | 17.4 | 4 | 8F6FFAE7EAEA4048B3D13BF5839E2895 |  | R22 | TXV |  | 12.21% | 0.87786 | 23.47% | [5 empty] | TXV | 12.21%
Merced | CA | 95341-6608 |  | 2013-07-19 | 2013-07-19 16:56 | 2013-07-19 16:56 | ICP - PGC036K080E | 68 | 2.9 | Yes | Yes | 16.3 | 19.6 | -3.3 | E39F0241655844F79FB97217C58B1FB1 | Add refrigerant: 2.9 oz | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Stockton | CA | 95212-2932 |  | 2013-06-26 | 2013-06-26 14:28 | 2013-06-26 14:54 | BDP - 561CJ042-A | 80 | 2.4 | Yes | Yes | 12 | 14.7 | -2.7 | 2F8D6B8AF81F4F39AB0015A6CA28FAFB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Paso Robles | CA | 93446-1841 |  | 2013-08-06 | 2013-08-06 10:06 | 2013-08-06 10:24 | HEIL - CA5042VKA1 | 135 | -9.5 | Yes | Yes | 21.5 | 18.2 | 3.3 | 003C07565B694504805EB8D3A2A4A4AA |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Chico | CA | 95973-9122 |  | 2013-09-06 | 2013-09-06 16:15 | 2013-09-06 19:32 | TRANE - YCC024F1LOBH | 65 | 2.6 | Yes | Yes | 16.1 | 17.5 | -1.4 | D6523C02D405459DBAF625F23F366D43 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Manteca | CA | 95337-9363 |  | 2013-07-16 | 2013-07-16 09:35 | 2013-07-16 09:58 | ICP - N4A460AKA100 | 217 | 9.9 | Yes | Yes | 25.9 | 20.2 | 5.7 | 93B9C330022C462DBFF77117C695D608 |  | R410A | Non-TXV |  | 4.562% | 0.95438 | 8.768% | [5 empty] | Non-TXV | 4.562%
Dinuba | CA | 93618-3708 |  | 2013-07-26 | 2013-07-26 10:28 | 2013-07-26 11:19 | AMERICAN STANDARD - YCY036G1M0AC | 129 | 4 | Yes | Yes | 20.2 | 18.9 | 1.3 | 9DDF00B100B34610B93068963300EDCC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.101% | 0.96899 | 5.959% | [5 empty] | Non-TXV | 3.101%
Stockton | CA | 95209-2344 |  | 2013-07-17 | 2013-07-17 11:59 | 2013-07-17 11:59 | OTHER - H23B243ABCA | 85 | 0 | Yes | Yes | 19 | 20.2 | -1.2 | 35941703FC424321881FF13037175EB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-9118 |  | 2013-08-07 | 2013-08-07 14:14 | 2013-08-07 15:01 | HEIL - YCC024F1L0BH | 65 | 2.7 | Yes | Yes | 17.9 | 19.8 | -1.9 | E67A84F1C39C4521B75EEF973AE7B2F5 |  | R22 | Non-TXV |  | 4.154% | 0.95846 | 7.983% | [5 empty] | Non-TXV | 4.154%
Tracy | CA | 95304-9324 |  | 2013-07-16 | 2013-07-16 12:37 | 2013-07-16 13:01 | YORK - UNK | 85 | 7.3 | Yes | Yes | 23 | 19.8 | 3.2 | DE60E7F1B96348B0BDEDBE65BC0DB8CB |  | R22 | Non-TXV |  | 8.588% | 0.91412 | 16.5% | [5 empty] | Non-TXV | 8.588%
Foresthill | CA | 95631-9222 |  | 2013-08-14 | 2013-08-14 10:11 | 2013-08-14 10:11 | TRANE - TTR036C100A0 | 97 | 0 | Yes | Yes | 26.4 | 20.9 | 5.5 | 05B8C60BD92A4C5394B645EE6B546A71 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-5215 |  | 2013-07-02 | 2013-07-02 19:18 | 2013-07-02 19:47 | AMANA - RCC48A2B | 138 | 12.3 | Yes | Yes | 22.3 | 23.7 | -1.4 | 2293942FF2A34264867981653157BBF3 |  | R22 | Non-TXV |  | 8.913% | 0.91087 | 17.13% | [5 empty] | Non-TXV | 8.913%
N San Juan | CA | 95960-9518 |  | 2013-09-09 | 2013-09-09 09:24 | 2013-09-09 09:24 | AMANA - VCB30A2A | 70 | 0 | Yes | Yes | 19.7 | 19.5 | 0.2 | E3934A7907724A08832057424D53DC40 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Colfax | CA | 95713-9215 |  | 2013-07-25 | 2013-07-25 14:19 | 2013-07-25 14:54 | AMERICAN STANDARD - 2A7A2042A1000AA | 95 | 10.2 | Yes | Yes | 20 | 20.4 | -0.4 | B858BE8CC51C453EA284FF902FE7BBE8 |  | R22 | TXV |  | 10.74% | 0.89263 | 20.63% | [5 empty] | TXV | 10.74%
Stockton | CA | 95206-4824 |  | 2013-07-10 | 2013-07-10 11:39 | 2013-07-10 12:01 | RHEEM - RAFD-030JAS | 64 | -4.5 | Yes | Yes | 17.7 | 19.7 | -2 | 7D234E82CDBA43CEA5A0371F09DBB8C5 |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Oakdale | CA | 95361-9629 |  | 2013-08-28 | 2013-08-28 14:04 | 2013-08-28 14:25 | CARRIER - 38CK048310 | 102 | 22.4 | Yes | Yes | 17.7 | 19.9 | -2.2 | 13429A3966784FF2AC77073059C24BFD |  | R22 | Non-TXV |  | 21.96% | 0.78039 | 42.2% | [5 empty] | Non-TXV | 21.96%
Chico | CA | 95926-2820 |  | 2013-07-10 | 2013-07-10 21:17 | 2013-07-10 21:34 | DAY & NIGHT - 588ANW042080AAA6 | 82 | 8.9 | Yes | Yes | 21.6 | 23 | -1.4 | CB1507FE313B4286B25C76FA3C5ADFD0 |  | R22 | Non-TXV |  | 10.85% | 0.89146 | 20.86% | [5 empty] | Non-TXV | 10.85%
Arbuckle | CA | 95912-0000 |  | 2013-07-31 | 2013-07-31 09:42 | 2013-07-31 10:05 | WESTINGHOUSE - FS3BA-042KA | 87 | 2.8 | Yes | Yes | 19 | 19.3 | -0.3 | 33A23796DC96485DA0951875494F2A82 |  | R22 | TXV |  | 3.218% | 0.96782 | 6.185% | [5 empty] | TXV | 3.218%
Atascadero | CA | 93422-5897 |  | 2013-08-07 | 2013-08-07 11:56 | 2013-08-07 12:14 | RHEEM - RACC-024JAS | 49 | 2 | Yes | Yes | 19.4 | 18.2 | 1.2 | AAA9B7C28C9B4822B3EF841E744BC63A |  | R22 | Non-TXV |  | 4.082% | 0.95918 | 7.844% | [5 empty] | Non-TXV | 4.082%
Somerset | CA | 95684-9248 |  | 2013-08-12 | 2013-08-12 17:13 | 2013-08-12 17:13 | YORK - D1NA036N05606C | 67 | 0 | Yes | Yes | 22.7 | 24.2 | -1.5 | 0D1B2BF45A924571A9602970A2718A85 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Jackson | CA | 95642-2656 |  | 2013-08-20 | 2013-08-20 10:45 | 2013-08-20 11:07 | OTHER - CA5030VKB1 | 79 | 13.1 | Yes | Yes | 25 | 21 | 4 | C13978A320CE48758BD0311F222A61D3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.58% | 0.83418 | 31.87% | [5 empty] | Non-TXV | 16.58%
Stockton | CA | 95210-6767 |  | 2013-08-21 | 2013-08-21 10:56 | 2013-08-21 11:19 | YORK - H2RA036S06D | 63 | 6.4 | Yes | Yes | 26.5 | 21 | 5.5 | BD7B43D7F19640F19E44D9DB94F833D3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.16% | 0.89841 | 19.52% | [5 empty] | Non-TXV | 10.16%
Madera | CA | 93637-4739 |  | 2013-07-11 | 2013-07-11 00:51 | 2013-07-11 02:07 | ALLEGIANCE - E3063042863 | 85 | 2.7 | Yes | Yes | 16.2 | 19.1 | -2.9 | FC8706A85B6A45C08DC3610CE1FF8767 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Stockton | CA | 95210-3648 |  | 2013-08-16 | 2013-08-16 09:27 | 2013-08-16 09:45 | GOODMAN - GSC130361DE | 119 | 7.8 | Yes | Yes | 16.9 | 17.9 | -1 | BDB4B5B05C60443196683126904D7A4B |  | R22 | Non-TXV |  | 6.555% | 0.93445 | 12.6% | [5 empty] | Non-TXV | 6.555%
Placerville | CA | 95667-4668 |  | 2013-07-09 | 2013-07-09 11:14 | 2013-07-09 11:14 | LENNOX - HS19-311V-4P | 105 | 0 | Yes | Yes | 26 | 21 | 5 | 7BCCF971F5414B05BD5ABCAE112084AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93636-8225 |  | 2013-08-23 | 2013-08-23 14:55 | 2013-08-23 15:46 | YORK - DAY80CF042NO8O | 95 | 2.8 | Yes | Yes | 20.8 | 21.5 | -0.7 | 09ECE4E61B47494D97346A6EFD58815F |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Chico | CA | 95973-9118 |  | 2013-09-04 | 2013-09-04 15:49 | 2013-09-04 17:31 | TRANE - YCCO24F1LOBH | 65 | 3 | Yes | Yes | 20 | 19.3 | 0.7 | 4E20AF68FB87461C857EE06F11707F97 |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Chico | CA | 95973-9119 |  | 2013-08-07 | 2013-08-07 17:59 | 2013-08-07 18:24 | TRANE - YCCO24F1LOBH | 65 | 4 | Yes | Yes | 21.3 | 20.8 | 0.5 | C13BBD8016454C4BBAEB9B6379FE9A69 |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Stockton | CA | 95210-2273 |  | 2013-08-16 | 2013-08-16 15:39 | 2013-08-16 16:14 | OTHER - FS3BA-030KA | 68 | 10.3 | Yes | Yes | 21.9 | 19.8 | 2.1 | AE6173812CD64109BB2B904CD128FED7 |  | R22 | Non-TXV |  | 15.15% | 0.84853 | 29.11% | [5 empty] | Non-TXV | 15.15%
Chico | CA | 95926-4427 |  | 2013-09-24 | 2013-09-24 10:17 | 2013-09-24 10:38 | DAY & NIGHT - N2A324AKC200 | 53 | 2.2 | Yes | Yes | 16 | 18.8 | -2.8 | 4E831F9F91B6454A9773BA09046014D8 |  | R22 | Non-TXV |  | 4.151% | 0.95849 | 7.977% | [5 empty] | Non-TXV | 4.151%
Tracy | CA | 95376-2715 |  | 2013-07-26 | 2013-07-26 11:42 | 2013-07-26 12:07 | BDP - 5J5A030YAC | 60 | 2.1 | Yes | Yes | 18.7 | 18.6 | 0.1 | 9E29A7A09959494B922414DAA17895D1 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Tracy | CA | 95377-7202 |  | 2013-07-19 | 2013-07-19 16:59 | 2013-07-19 17:16 | YORK - H2RA030S06D | 62 | 6.7 | Yes | Yes | 20.2 | 19.7 | 0.5 | FE237343F1B04459AB008D324DF53A28 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.81% | 0.89194 | 20.77% | [5 empty] | Non-TXV | 10.81%
Tracy | CA | 95377-7202 |  | 2013-07-19 | 2013-07-19 17:18 | 2013-07-19 17:39 | YORK - H2RA030S06D | 62 | 3.5 | Yes | Yes | 20.1 | 19 | 1.1 | 7D122A704DD4479DA9295A7327B77966 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.645% | 0.94355 | 10.85% | [5 empty] | Non-TXV | 5.645%
Tracy | CA | 95377-8711 |  | 2013-07-26 | 2013-07-26 16:47 | 2013-07-26 17:16 | CARRIER - 38CKC042300 | 80 | 5.9 | Yes | Yes | 18.6 | 20.4 | -1.8 | A95D064A5AD8423D9656185F363BD982 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.375% | 0.92625 | 14.17% | [5 empty] | Non-TXV | 7.375%
Stockton | CA | 95215-6738 |  | 2013-07-08 | 2013-07-08 08:52 | 2013-07-08 09:18 | CARRIER - 38CK036350 | 70 | 20.9 | Yes | Yes | 14.4 | 17 | -2.6 | 8308293F5C2644DBBEA54E36E7F65D56 |  | R22 | Non-TXV |  | 29.86% | 0.70143 | 57.38% | [5 empty] | Non-TXV | 29.86%
Colfax | CA | 95713-0000 |  | 2013-07-25 | 2013-07-25 15:34 | 2013-07-25 15:34 | GOODMAN - CKL36-1H | 71 | 0 | Yes | Yes | 12 | 15 | -3 | 554D7827D92E4D7EAA8C3C9BE166A352 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6452 |  | 2013-07-02 | 2013-07-02 11:27 | 2013-07-02 11:48 | OTHER - UNK | 68 | 2.1 | Yes | Yes | 17 | 19.3 | -2.3 | FD6A264D4732482CB22FF24DC0F4EAD5 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Stockton | CA | 95206-2911 |  | 2013-08-16 | 2013-08-16 16:40 | 2013-08-16 17:02 | GOODMAN - GSC130301AE | 176 | 27.3 | Yes | Yes | 23.9 | 19.6 | 4.3 | 190DD4567EFC4521839761D2F90D5E0E |  | R22 | Non-TXV |  | 15.51% | 0.84489 | 29.81% | [5 empty] | Non-TXV | 15.51%
Stockton | CA | 95205-6418 |  | 2013-07-17 | 2013-07-17 14:12 | 2013-07-17 14:32 | RUUD - URKA-A036JK06E | 62 | 7.4 | Yes | Yes | 23.1 | 21.3 | 1.8 | 2C9E641234704069AB08A3FB7C8F8D80 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.94% | 0.88065 | 22.94% | [5 empty] | Non-TXV | 11.94%
Los Banos | CA | 93635-4039 |  | 2013-07-24 | 2013-07-24 13:19 | 2013-07-24 13:22 | HEIL - NRGE30SAK02 | 47 | 3.1 | Yes | Yes | 16.8 | 19.7 | -2.9 | 3768FE0F2672439AA8335576CFFC5AB6 |  | R22 | Non-TXV |  | 6.596% | 0.93404 | 12.68% | [5 empty] | Non-TXV | 6.596%
Merced | CA | 95348-1814 |  | 2013-07-17 | 2013-07-17 15:56 | 2013-07-17 16:00 | GE - BTD724A100A0 | 68 | 2.4 | Yes | Yes | 19.2 | 17.2 | 2 | AA1C72083B0742F4AC827F6FF3165B3C |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Los Banos | CA | 93635-3233 |  | 2013-07-08 | 2013-07-08 13:45 | 2013-07-08 13:47 | TRANE - SFHA301 | 65 | 9.3 | Yes | Yes | 25.8 | 22 | 3.8 | CFAD2B3D066C434F9059F40FE71AED67 |  | R22 | Non-TXV |  | 14.31% | 0.85692 | 27.5% | [5 empty] | Non-TXV | 14.31%
Foresthill | CA | 95631-9746 |  | 2013-10-14 | 2013-10-14 13:37 | 2013-10-14 13:37 | PAYNE - PY2PNB048090AAAA | 115 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | 5845570E802D4A6387DDBCF1D770181B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pioneer | CA | 95666-9582 |  | 2013-08-13 | 2013-08-13 09:59 | 2013-08-13 10:31 | GE - BGTA936EIA | 85 | 3.7 | Yes | Yes | 20 | 20.7 | -0.7 | B30A15BC71514D2F923F753367BE2D5B |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Stockton | CA | 95207-1208 |  | 2013-07-31 | 2013-07-31 13:40 | 2013-07-31 14:09 | GUARDIAN - GSC130361DE | 119 | 3.6 | Yes | Yes | 20.2 | 19.5 | 0.8 | 78ED515CBF934B7DA2DB8E420134C9EB |  | R22 | Non-TXV |  | 3.025% | 0.96975 | 5.814% | [5 empty] | Non-TXV | 3.025%
Stockton | CA | 95207-2850 |  | 2013-06-27 | 2013-06-27 14:28 | 2013-06-27 14:56 | RHEEM - RRNA-B024JK06X | 70 | 3.5 | Yes | Yes | 14.9 | 16.6 | -1.7 | 178087CB82764F7FB711D98F0AE9C462 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Los Banos | CA | 93635-0000 |  | 2013-07-08 | 2013-07-08 08:56 | 2013-07-08 09:07 | NORDYNE - JS3BA030KA | 68 | 6.8 | Yes | Yes | 21 | 20.4 | 0.6 | 7B0B4B652C064C29B1AB7DF4D2BE4126 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95212-3419 |  | 2013-06-27 | 2013-06-27 11:02 | 2013-06-27 11:19 | CARRIER - 38CKC048300 | 85 | 7.6 | Yes | Yes | 18.7 | 19 | -0.3 | 6CC02D3CA98C4B74B0F08B9754AC73BA |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
San Miguel | CA | 93451-0000 |  | 2013-08-16 | 2013-08-16 12:45 | 2013-08-16 13:07 | UNK - UNK | 85 | 3.2 | Yes | Yes | 23.2 | 20.7 | 2.5 | D860911B149C4AEBA9FACD2027AC606D |  |  |  |  | 3.765% | 0.96235 | 7.235% | [5 empty] | 0 | 3.765%
Stockton | CA | 95204-1223 |  | 2013-07-01 | 2013-07-01 09:15 | 2013-07-01 09:35 | PAYNE - 585EJM030075ABHE | 58 | 8.6 | Yes | Yes | 21.5 | 17.5 | 4 | E75223889F7442869BFD81F8EFA0A4D2 |  | R22 | TXV |  | 14.83% | 0.85172 | 28.5% | [5 empty] | TXV | 14.83%
Stockton | CA | 95219-3588 |  | 2013-07-26 | 2013-07-26 13:35 | 2013-07-26 13:58 | CARRIER - 38EN018300 | 54 | 3.6 | Yes | Yes | 15 | 17.5 | -2.5 | B81CD5DECB6A4E939AD70E973D739EB6 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Los Banos | CA | 93635-6407 |  | 2013-07-29 | 2013-07-29 12:15 | 2013-07-29 12:19 | BRYANT - 563CN036-D | 104 | 5 | Yes | Yes | 16.5 | 19.3 | -2.8 | 8EAA85F1D7E548348EC9DE566EFFDDD1 |  | R22 | Non-TXV |  | 4.808% | 0.95192 | 9.239% | [5 empty] | Non-TXV | 4.808%
Merced | CA | 95348-1815 |  | 2013-08-15 | 2013-08-15 16:09 | 2013-08-15 16:13 | GE - BTD724A100A0 | 68 | 2.7 | Yes | Yes | 20.8 | 18.8 | 2 | 44AFC1E5CB604941B6FC554D9F7F46D9 |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Foresthill | CA | 95631-9362 |  | 2013-08-14 | 2013-08-14 10:58 | 2013-08-14 10:58 | PAYNE - PY3GNAA36060NA-- | 102 | 0 | Yes | Yes | 24.7 | 21.2 | 3.5 | A6357D16C9A8400EB5CF735206F0178E |  | R410A | TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0915 |  | 2013-07-11 | 2013-07-11 19:38 | 2013-07-11 19:59 | PAYNE - PY1PA036060NB | 114 | 3.6 | Yes | Yes | 20.8 | 18.8 | 2 | 9D254CCA7F4E490396E8319C55584535 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Los Banos | CA | 93635-6322 |  | 2013-08-20 | 2013-08-20 11:07 | 2013-08-20 11:09 | GOODMAN - CK42-1AB | 106 | 3.2 | Yes | Yes | 18.4 | 21.3 | -2.9 | EA6FCA61052143069C05E447CA4D345E |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Valley Springs | CA | 95252-9559 |  | 2013-07-16 | 2013-07-16 15:38 | 2013-07-16 15:55 | GOODMAN - PG030075-1AB REV C | 60 | 4.6 | Yes | Yes | 17.9 | 20.9 | -3 | BFC76A2B4F694113B599A1091670BCF7 |  | R22 | Non-TXV |  | 7.667% | 0.92333 | 14.73% | [5 empty] | Non-TXV | 7.667%
Stockton | CA | 95203-1651 |  | 2013-07-25 | 2013-07-25 15:05 | 2013-07-25 15:23 | GOODMAN - CKL36-1H | 71 | 13.9 | Yes | Yes | 15 | 17.6 | -2.5 | D8A5BD697CF5433D96F6C28877B85668 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.58% | 0.80423 | 37.62% | [5 empty] | Non-TXV | 19.58%
Manteca | CA | 95336-7040 |  | 2013-07-25 | 2013-07-25 11:37 | 2013-07-25 11:57 | BRYANT - 563CN048-D | 165 | 18 | Yes | Yes | 19.9 | 19.3 | 0.6 | 2541CA4A336E4AA1A68A483D6B0AB35E |  | R22 | Non-TXV |  | 10.91% | 0.89091 | 20.96% | [5 empty] | Non-TXV | 10.91%
Stockton | CA | 95203-1723 |  | 2013-07-19 | 2013-07-19 12:35 | 2013-07-19 12:35 | AMERICAN STANDARD - 2A7A536A1000AA | 137 | 0 | Yes | Yes | 29.7 | 17.3 | 12.4 | A78F1AA3B7F84BB483915649D64DB736 | Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6601 |  | 2013-08-05 | 2013-08-05 12:02 | 2013-08-05 12:21 | RHEEM - RRNL-B030JK06X | 77 | 2.4 | Yes | Yes | 19.1 | 19.3 | -0.2 | 960EF6123D3549C980BC95C47A7B021D |  | R410A | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Madera | CA | 93638-1809 |  | 2013-07-16 | 2013-07-16 14:37 | 2013-07-21 20:15 | - 38CK024-- | 55 | 4.4 | Yes | Yes | 17.1 | 20.1 | -3 | F5139BDAA89843148574EC165CADDDB4 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Cameron Park | CA | 95682-8150 |  | 2013-08-28 | 2013-08-28 11:20 | 2013-08-28 11:40 | KENMORE - HHP024AKA1 | 104 | 13.4 | Yes | Yes | 18.7 | 21.5 | -2.8 | 4B5B22277DAF4B73BDEC8B1F73138978 |  | R22 | Non-TXV |  | 12.88% | 0.87115 | 24.76% | [5 empty] | Non-TXV | 12.88%
West Point | CA | 95255-9759 |  | 2013-09-05 | 2013-09-05 12:02 | 2013-09-05 12:23 | LUXAIRE - F036P100 | 80 | 3 | Yes | Yes | 22.3 | 20.4 | 1.9 | 6032A185C9714F40B9530BD8FC0A2244 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Paradise | CA | 95969-5991 |  | 2013-09-04 | 2013-09-04 14:44 | 2013-09-04 17:30 | DAY & NIGHT - NA | 65 | 3 | Yes | Yes | 17.5 | 20.4 | -2.9 | D24064DD40FB4A25AA48A5BC82E9A524 |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Oroville | CA | 95965-4262 |  | 2013-07-25 | 2013-07-25 15:01 | 2013-07-25 21:01 | COLEMAN - TCD3652152A | 63 | 7.5 | Yes | Yes | 18.6 | 21.3 | -2.7 | BC3ED3FAF6E7409EBC5190FC1EB4BDCF |  | R22 | Non-TXV |  | 11.9% | 0.88095 | 22.88% | [5 empty] | Non-TXV | 11.9%
Atwater | CA | 95301-4530 |  | 2013-08-13 | 2013-08-13 12:00 | 2013-08-13 12:22 | INTERTHERM - ACC 036BAVAA | 47 | 2.2 | Yes | Yes | 19.1 | 19.7 | -0.6 | AB91686E235240BCA5A3CC50AA3F6A72 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.681% | 0.95319 | 8.996% | [5 empty] | Non-TXV | 4.681%
Chico | CA | 95926-2453 |  | 2013-08-16 | 2013-08-16 15:26 | 2013-08-16 20:49 | PAYNE - NA | 59 | 2.4 | Yes | Yes | 17.9 | 20.9 | -3 | 94CB1C9C5EF54862812B566409AA8D1D |  | R22 | Non-TXV |  | 4.068% | 0.95932 | 7.817% | [5 empty] | Non-TXV | 4.068%
Dos Palos | CA | 93620-0000 |  | 2013-08-14 | 2013-08-14 15:28 | 2013-08-14 15:32 | OTHER - TZAA-3422A757 | 100 | 4.2 | Yes | Yes | 25.9 | 22.1 | 3.8 | E47692628B7A4A5F8F719D8D1D04AEB2 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Atascadero | CA | 93422-6057 |  | 2013-08-09 | 2013-08-09 09:01 | 2013-08-09 09:19 | LENNOX - 13ACD-042-230-02 | 111 | -6.5 | Yes | Yes | 18 | 19.3 | -1.3 | EF6D77CD036A4B03824FC6142F8FB391 |  | R22 | Non-TXV |  | -5.856% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.856%
Oroville | CA | 95966-7151 |  | 2013-08-02 | 2013-08-02 19:14 | 2013-08-02 11:31 | PAYNE - 585HJ0240 | 91 | 5.8 | Yes | Yes | 17.4 | 20.4 | -3 | 3BA41CD842314E32B308538081A6D9C1 |  | R22 | Non-TXV |  | 6.374% | 0.93626 | 12.25% | [5 empty] | Non-TXV | 6.374%
Paradise | CA | 95969-4817 |  | 2013-08-05 | 2013-08-05 18:19 | 2013-08-05 18:19 | BRYANT - 30-579A | 46 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | BF434846978E4E21823579885478E05D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-1603 |  | 2013-07-08 | 2013-07-08 14:02 | 2013-07-08 14:04 | RHEEM - RRKA-A036K06E | 62 | 4.4 | Yes | Yes | 21.7 | 20.7 | 1.1 | 96E177C9A9584ECB84B65F088B5883EA |  | R22 | Non-TXV |  | 7.097% | 0.92903 | 13.64% | [5 empty] | Non-TXV | 7.097%
Merced | CA | 95341-5237 |  | 2013-07-01 | 2013-07-01 09:41 | 2013-07-01 09:50 | RUUD - UKA-036JAS | 96 | 8.7 | Yes | Yes | 20.4 | 19.5 | 0.9 | D7B8D5039FB14F33A60789D622B8888F |  | R22 | Non-TXV |  | 9.062% | 0.90938 | 17.42% | [5 empty] | Non-TXV | 9.062%
Stockton | CA | 95206-2885 |  | 2013-07-03 | 2013-07-03 13:38 | 2013-07-03 14:04 | CARRIER - 561CJ048-B | 134 | 5.5 | Yes | Yes | 22.8 | 19.3 | 3.5 | FEB6A0D0AAD3490D8AC602202680B475 |  | R22 | Non-TXV |  | 4.104% | 0.95896 | 7.888% | [5 empty] | Non-TXV | 4.104%
Merced | CA | 95348-1603 |  | 2013-07-08 | 2013-07-08 14:35 | 2013-07-08 14:37 | TAPPAN - 7777UNK | 80 | 5.6 | Yes | Yes | 20.4 | 20.8 | -0.4 | FA2131DEC7434BD8862DD7A39F56C4C5 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Corning | CA | 96021-3608 |  | 2013-07-23 | 2013-07-23 14:04 | 2013-07-23 18:49 | AMANA - RCC30A2B | 95 | 10.5 | Yes | Yes | 17.9 | 20.2 | -2.3 | 348E4D6D8B8641349BDE60582E8FD9F5 |  | R22 | Non-TXV |  | 11.05% | 0.88947 | 21.24% | [5 empty] | Non-TXV | 11.05%
Oroville | CA | 95966-7160 |  | 2013-08-02 | 2013-08-02 18:54 | 2013-08-02 19:12 | PAYNE - 5870J030-B | 80 | 3 | Yes | Yes | 22 | 22 | 0 | 8E97A14E1E3F4121866A99F2CD18EB60 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Merced | CA | 95341-5215 |  | 2013-07-02 | 2013-07-02 09:38 | 2013-07-02 09:39 | TRANE - 2YCC3048A1075AA | 144 | 4.2 | Yes | Yes | 19.3 | 18.8 | 0.5 | 65661DD78261467D9316AA1E16E615AF |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Valley Springs | CA | 95252-9241 |  | 2013-09-16 | 2013-09-16 11:31 | 2013-09-16 12:09 | BRYANT - 582ANW036060AAAF | 56 | 2 | Yes | Yes | 22.7 | 20.4 | 2.3 | 4FDD715ACCF94999AE03824605232D4C |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Sutter Creek | CA | 95685-4106 |  | 2013-07-24 | 2013-07-24 11:36 | 2013-07-24 12:03 | RUUD - UPFB-018JAS | 52 | 5.1 | Yes | Yes | 20 | 18.2 | 1.8 | C818814F4DC2433B85B517F8EDC45663 |  | R22 | Non-TXV |  | 9.808% | 0.90192 | 18.85% | [5 empty] | Non-TXV | 9.808%
Merced | CA | 95348-1603 |  | 2013-07-08 | 2013-07-08 14:19 | 2013-07-08 14:21 | GOODMAN - PGB030050-1 REV A | 56 | 4.5 | Yes | Yes | 18 | 20.9 | -2.9 | 898C237F3AE74B17A19E25557BD307AD |  | R22 | Non-TXV |  | 8.036% | 0.91964 | 15.44% | [5 empty] | Non-TXV | 8.036%
Madera | CA | 93637-8825 |  | 2013-08-15 | 2013-08-15 17:32 | 2013-08-15 18:06 | CARRIER - 48GX-03606301 | 82 | 3.4 | Yes | Yes | 17.2 | 19.9 | -2.7 | F12CCD018AD84D9CB8306DF0C8381D5D |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Manteca | CA | 95336-2633 |  | 2013-06-28 | 2013-06-28 10:11 | 2013-06-28 10:34 | YORK - UNK | 96 | 7.2 | Yes | Yes | 23.2 | 17.4 | 5.8 | 53FC5A66D04D4014B7E52AE9CBCB6B57 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Lincoln | CA | 95648-2146 |  | 2013-07-06 | 2013-07-06 10:13 | 2013-07-06 10:39 | RHEEM - RAKB-024JAZ | 56 | -5.3 | Yes | Yes | 18 | 19.9 | -1.9 | 6FA3D9A8C04A432CAF88C30EAD253B64 |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
Stockton | CA | 95212-3832 |  | 2013-08-08 | 2013-08-08 13:44 | 2013-08-08 14:05 | CARRIER - 38CKC048370 | 85 | 4.2 | Yes | Yes | 25.3 | 19.3 | 6 | 8371894C7240478CB6E318393CF57916 |  | R22 | TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | TXV | 4.941%
Lincoln | CA | 95648-8000 |  | 2013-08-23 | 2013-08-23 13:15 | 2013-08-23 13:15 | OTHER - 38CKC0603803E27805370 | 131 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 802E2EE9BCE244A88D505333BC1B5E63 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-7932 |  | 2013-08-01 | 2013-08-01 13:20 | 2013-08-01 13:40 | GOODMAN - GSC130421AC | 137 | 4.4 | Yes | Yes | 21 | 19.9 | 1.1 | 0C6F772798044BD4BAC7175C4EB87A4F |  | R22 | Non-TXV |  | 3.212% | 0.96788 | 6.172% | [5 empty] | Non-TXV | 3.212%
Stockton | CA | 95209-1227 |  | 2013-07-12 | 2013-07-12 08:55 | 2013-07-12 08:55 | PAYNE - 567C6RCU | 67 | 0 | Yes | Yes | 21.8 | 18.8 | 3.1 | 704C67DE6AF14594AE37071C517586D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-5651 |  | 2013-07-01 | 2013-07-01 09:03 | 2013-07-01 09:04 | ICP - PGD336060K001C1 | 100 | 4.4 | Yes | Yes | 20 | 18.3 | 1.8 | 86433AC6AA164B71B2BFA5D83B7F437E |  | R410A | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Madera | CA | 93637-6219 |  | 2013-07-10 | 2013-07-10 18:20 | 2013-07-10 19:19 | LENNOX - 10GS030X-75-6PA | 85 | 3.4 | Yes | Yes | 19.2 | 21.3 | -2.1 | D6D02981D8F24CFD8F7CEE0005F8D369 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Chico | CA | 95926-4380 |  | 2013-08-23 | 2013-08-23 13:57 | 2013-08-23 14:25 | DAY & NIGHT - 585GJW018040ABAC | 55 | 10.6 | Yes | Yes | 14.4 | 17.4 | -3 | 148D3262B8174277AE12002D7ACDEA20 |  | R22 | Non-TXV |  | 19.27% | 0.80727 | 37.04% | [5 empty] | Non-TXV | 19.27%
Chico | CA | 95928-3937 |  | 2013-08-01 | 2013-08-01 12:35 | 2013-08-01 12:53 | PAYNE - 591ANX048000ACAA | 128 | 9.3 | Yes | Yes | 25.8 | 19.9 | 5.9 | 211527E2A36D45519867921826B2F829 |  | R22 | Non-TXV |  | 7.266% | 0.92734 | 13.96% | [5 empty] | Non-TXV | 7.266%
Stockton | CA | 95212-2744 |  | 2013-07-15 | 2013-07-15 09:17 | 2013-07-15 09:40 | CARRIER - 38CKC036350 | 70 | 5.2 | Yes | Yes | 21.5 | 21 | 0.5 | 64BFF7972C44458783E9C71B4365AB10 |  | R22 | Non-TXV |  | 7.429% | 0.92571 | 14.28% | [5 empty] | Non-TXV | 7.429%
Stockton | CA | 95210-3302 |  | 2013-07-09 | 2013-07-09 09:07 | 2013-07-09 09:24 | GE - UNK | 53 | -3.1 | Yes | Yes | 20.3 | 17.9 | 2.4 | 83CA7409B04346F6B0DDF5ECF98FE892 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Manteca | CA | 95336-2849 |  | 2013-06-28 | 2013-06-28 09:20 | 2013-06-28 09:43 | GOODMAN - CKL36-1K | 85 | 4.8 | Yes | Yes | 16.4 | 17.1 | -0.7 | 0B5621715E4B4048A201D7F0E032D867 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Manteca | CA | 95336-6312 |  | 2013-09-24 | 2013-09-24 15:34 | 2013-09-24 16:00 | BDP - 585CJ030050 | 78 | 2.4 | Yes | Yes | 18.9 | 17.6 | 1.3 | 2C645C17D69745199565A650564C3FFC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Penn Valley | CA | 95946-9108 |  | 2013-09-18 | 2013-09-18 10:38 | 2013-09-18 10:38 | RHEEM - RQPL-B048JK 000 | 183 | 0 | Yes | Yes | 19.2 | 20.1 | -0.9 | 9F1B248F8F9649A98EFFEEE971C5E8A4 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-4512 |  | 2013-07-26 | 2013-07-26 10:25 | 2013-07-26 11:00 | OTHER - NAC018AKB2 | 57 | 4.6 | Yes | Yes | 17.6 | 18.2 | -0.6 | 65B26A62E818413FAE35FAC3EF2978BA |  | R22 | Non-TXV |  | 8.07% | 0.9193 | 15.51% | [5 empty] | Non-TXV | 8.07%
Chowchilla | CA | 93610-8009 |  | 2013-08-22 | 2013-08-22 21:30 | 2013-08-22 23:52 | CARRIER - 38CKC060370 | 131 | 4 | Yes | Yes | 17.9 | 20.1 | -2.1 | 4084939093184873ADD2AA9FF3640E88 |  | R22 | Non-TXV |  | 3.053% | 0.96947 | 5.868% | [5 empty] | Non-TXV | 3.053%
Corning | CA | 96021-2612 |  | 2013-07-22 | 2013-07-22 11:25 | 2013-07-22 12:03 | TRANE - 4TTX6024B10000AA | 89 | 10.2 | Yes | Yes | 18.4 | 20.9 | -2.5 | 8C502E94D9C24CDF966E8629FCAA392B |  | R410A | Non-TXV |  | 11.46% | 0.88539 | 22.02% | [5 empty] | Non-TXV | 11.46%
Stockton | CA | 95215-9780 |  | 2013-08-29 | 2013-08-29 13:38 | 2013-08-29 13:55 | YORK - D1NP036N05606A | 108 | 3.8 | Yes | Yes | 24 | 20.2 | 3.8 | F7267827DE05459A86D525996137C5B1 |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Oakdale | CA | 95361-3106 |  | 2013-09-11 | 2013-09-11 11:28 | 2013-09-11 11:49 | RHEEM - CBD | 64 | 2.1 | Yes | Yes | 17.7 | 18.3 | -0.6 | 8741AA2665B1497FB74ABFEADEE114F7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Durham | CA | 95938-9731 |  | 2013-09-06 | 2013-09-06 10:51 | 2013-09-06 11:42 | COLEMAN - 3848-901 | 135 | 7.1 | Yes | Yes | 17.2 | 19.3 | -2.1 | DA7174689A4F475F96FE152597CBCD88 |  | R22 | Non-TXV |  | 5.259% | 0.94741 | 10.11% | [5 empty] | Non-TXV | 5.259%
Stockton | CA | 95215-5310 |  | 2013-07-02 | 2013-07-02 10:44 | 2013-07-02 11:08 | YORK - H2RD036S06B | 96 | 9.9 | Yes | Yes | 21.3 | 23.5 | -2.2 | B5AF3BEF9A82491EBE498B8BF319FC7E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.31% | 0.89687 | 19.82% | [5 empty] | Non-TXV | 10.31%
Chowchilla | CA | 93610-8009 |  | 2013-06-28 | 2013-06-28 09:51 | 2013-06-28 10:47 | CARRIER - 38CKC048370 | 101 | 3.6 | Yes | Yes | 18.8 | 21.4 | -2.6 | B9B4A1F00416417EAA6EEFC266688541 |  | R22 | Non-TXV |  | 3.564% | 0.96436 | 6.85% | [5 empty] | Non-TXV | 3.564%
Merced | CA | 95341-6700 |  | 2013-07-01 | 2013-07-01 14:43 | 2013-07-01 14:47 | GOODMAN - CKL30-1G | 74 | 3.2 | Yes | Yes | 16.9 | 19.9 | -3 | D149B52D782E475B8E47988A06D2BA17 |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
Grass Valley | CA | 95945-5225 |  | 2013-09-30 | 2013-09-30 12:50 | 2013-09-30 12:50 | CARRIER - 38CKC024340 | 58 | 0 | Yes | Yes | 23.5 | 20.2 | 3.3 | 6A3B0E18A66D44DBB72227B0F0F86CA5 |  | R22 | TXV |  | 0% | 1 | 0%
Chico | CA | 95926-2787 |  | 2013-07-31 | 2013-07-31 12:36 | 2013-07-31 12:56 | BDP - 5658J018 | 50 | 10.3 | Yes | Yes | 18.5 | 19.3 | -0.8 | F5F55C83894D46B8B808F134EF303E85 |  | R22 | Non-TXV |  | 20.6% | 0.794 | 39.59% | [5 empty] | Non-TXV | 20.6%
Atascadero | CA | 93422-0000 |  | 2013-08-13 | 2013-08-13 15:59 | 2013-08-13 16:16 | HEIL - NAC218AKC3 | 80 | -7.5 | Yes | Yes | 17.1 | 15.5 | 1.6 | 900B0AB35AD944129F2B58433520BDC1 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Madera | CA | 93638-9611 |  | 2013-08-23 | 2013-08-23 12:12 | 2013-08-23 12:38 | CARRIER - UNK | 138 | 4.1 | Yes | Yes | 17.6 | 19.8 | -2.2 | FD4D4E5BDDEA478984EC10B157A78445 |  | R22 | Non-TXV |  | 2.971% | 0.97029 | 5.71% | [5 empty] | Non-TXV | 2.971%
Merced | CA | 95341-6700 |  | 2013-07-02 | 2013-07-02 14:01 | 2013-07-02 14:04 | TRANE - TTR30C100A0 | 74 | 4.4 | Yes | Yes | 19.5 | 20.1 | -0.6 | F14F560143E44A7E88ABADA951EA249F |  | R22 | Non-TXV |  | 5.946% | 0.94054 | 11.43% | [5 empty] | Non-TXV | 5.946%
Madera | CA | 93637-2970 |  | 2013-07-01 | 2013-07-01 21:44 | 2013-07-01 22:20 | YORK - D1AP036N05606A | 85 | -5 | Yes | Yes | 18.1 | 19.3 | -1.2 | 578EBB27ACF14F52BA4A04895D7F547A |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Lincoln | CA | 95648-8216 |  | 2013-07-13 | 2013-07-13 13:00 | 2013-07-13 13:00 | GMC - VSX130361BA | 89 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 29FCB18DBA694E8FB626351A1A93D03E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-9503 |  | 2013-08-14 | 2013-08-14 12:23 | 2013-08-14 12:42 | LENNOX - 12ACB30-4P | 101 | 9.5 | Yes | Yes | 20.7 | 22.6 | -1.9 | A37557A944E64DDFB3DCF0FF3C0ED1C3 |  | R22 | Non-TXV |  | 9.406% | 0.90594 | 18.08% | [5 empty] | Non-TXV | 9.406%
Chowchilla | CA | 93610-2043 |  | 2013-07-29 | 2013-07-29 15:04 | 2013-08-02 02:18 | YORK - JS3BD-042K | 131 | 4.2 | Yes | Yes | 18.1 | 20.4 | -2.3 | 4490CB1D6E48433ABA6454922BADC9FF |  | R22 | Non-TXV |  | 3.206% | 0.96794 | 6.161% | [5 empty] | Non-TXV | 3.206%
Merced | CA | 95341-6700 |  | 2013-07-02 | 2013-07-02 13:30 | 2013-07-02 13:37 | GOODMAN - GSC130301EA | 82 | 3.4 | Yes | Yes | 15.9 | 18.8 | -2.9 | C35A0F94E76F429E864ADF6036418D23 |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Stockton | CA | 95219-2042 |  | 2013-07-29 | 2013-07-29 12:40 | 2013-07-29 13:05 | GOODMAN - CKJ48-1A | 118 | 8.5 | Yes | Yes | 17.5 | 20.4 | -2.9 | D24B8435582248EBA9C490E4919BB77A |  | R22 | Non-TXV |  | 7.203% | 0.92797 | 13.84% | [5 empty] | Non-TXV | 7.203%
Pollock Pines | CA | 95726-9705 |  | 2013-09-03 | 2013-09-03 10:39 | 2013-09-03 10:39 | CARRIER - 48GX-048115311AD | 132 | 0 | Yes | Yes | 23.5 | 19.5 | 4 | EF11C5BA4D724D4C8C3BA5BA79B2377D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3423 |  | 2013-07-01 | 2013-07-01 10:20 | 2013-07-01 10:49 | RUUD - UNK | 96 | -9 | Yes | Yes | 21.6 | 15.7 | 5.9 | 5708FB940DAA49ED8896E4024743C67B |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Grass Valley | CA | 95945-9747 |  | 2013-08-05 | 2013-08-05 12:47 | 2013-08-05 12:47 | CARRIER - 48KLA148K300 I THINK | 118 | 0 | Yes | Yes | 25.4 | 20.2 | 5.2 | C26D7C4DBC5341598B75164A2FA6DF4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8013 |  | 2013-07-22 | 2013-07-22 14:47 | 2013-07-22 15:21 | OTHER - JX030000ABAA | 65 | -7 | Yes | Yes | 26 | 21.3 | 4.7 | 28A3B875DD5B4B88B7C874FEA69BA347 |  | R22 | Non-TXV |  | -10.77% | 1.1077 | 3.016% |  |  |  |  | Non-TXV |  |  | -10.77%
Placerville | CA | 95667-9650 |  | 2013-08-29 | 2013-08-29 10:27 | 2013-08-29 10:27 | RHEEM - UNK | 85 | 0 | Yes | Yes | 24.9 | 21.7 | 3.2 | F4C07EDE69994992A25B46214C415D11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4558 |  | 2013-07-03 | 2013-07-03 13:12 | 2013-07-03 13:18 | COLEMAN - BRCQ0361CB | 96 | 3.3 | Yes | Yes | 20 | 19 | 1 | 0435CFEC62E147DE92A06248BDD50350 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Stockton | CA | 95206-6027 |  | 2013-07-05 | 2013-07-05 09:42 | 2013-07-05 10:09 | GOODMAN - CKJ42-1AB | 85 | 4.4 | Yes | Yes | 20 | 19.2 | 0.8 | 7AE23C4FD1FA48C5A1D32E0BEC608C24 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Merced | CA | 95348-3206 |  | 2013-08-09 | 2013-08-09 15:40 | 2013-08-09 15:56 | AMANA - RCB36B2D | 85 | 2.7 | Yes | Yes | 22.6 | 19 | 3.6 | 07AC3ECB44264B879366D56036BC4631 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Nevada City | CA | 95959-9015 |  | 2013-08-27 | 2013-08-27 10:05 | 2013-08-27 10:05 | CARRIER - 38CKC036350 | 74 | 0 | Yes | Yes | 19.1 | 20.9 | -1.8 | D4D6F18D111F484586C0DBA6797164D3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2242 |  | 2013-06-26 | 2013-06-26 16:49 | 2013-06-26 16:51 | TRANE - TTR030C100A2 | 74 | 4.9 | Yes | Yes | 24.3 | 19.9 | 4.4 | BA7E0B5496254BB9ABF52F901B1C60DE |  | R22 | Non-TXV |  | 6.622% | 0.93378 | 12.73% | [5 empty] | Non-TXV | 6.622%
Foresthill | CA | 95631-9680 |  | 2013-10-25 | 2013-10-25 15:37 | 2013-10-25 15:37 | CARRIER - 48GS-048090301-- | 82 | 0 | Yes | Yes | 26.6 | 20.9 | 5.7 | 5F3EB762513546748CA5FC3D30B3D5A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-9680 |  | 2013-10-25 | 2013-10-25 15:58 | 2013-10-25 15:58 | TRANE - YCC030F1M0BC | 72 | 0 | Yes | Yes | 27.7 | 21.9 | 5.8 | 567587099AC243E59CBB957C051AC6BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-3414 |  | 2013-06-28 | 2013-06-28 19:17 | 2013-06-28 19:36 | CARRIER - 4BNLX036300 | 70 | 10 | Yes | Yes | 17.8 | 20.4 | -2.6 | 3D75E9F7EC1F4469BEC75A30DE790988 |  | R22 | Non-TXV |  | 14.29% | 0.85714 | 27.45% | [5 empty] | Non-TXV | 14.29%
Madera | CA | 93638-1817 |  | 2013-07-16 | 2013-07-16 15:32 | 2013-07-16 15:32 | YORK - D1NP048N09006A | 132 | 0 | Yes | Yes | 20.7 | 22.3 | -1.6 | AD8D16D56190450BA5545BBBF806A196 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-6837 |  | 2013-07-17 | 2013-07-17 09:49 | 2013-07-17 10:13 | YORK - H4DH060S06A | 125 | 13.9 | Yes | Yes | 16 | 17.7 | -1.7 | 0600E1EFF7C94512AEDE3EE5F669788A |  | R22 | Non-TXV |  | 11.12% | 0.8888 | 21.37% | [5 empty] | Non-TXV | 11.12%
Biggs | CA | 95917-9710 |  | 2013-09-09 | 2013-09-09 11:16 | 2013-09-09 11:36 | RHEEM - RGAAA030JK06X | 80 | 5.6 | Yes | Yes | 19.3 | 17.7 | 1.6 | 8E91D28374A84AEAB190054A5DFFE324 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Chowchilla | CA | 93610-9664 |  | 2013-08-19 | 2013-08-19 10:43 | 2013-08-19 10:45 | YORK - D1NP048N09006A | 132 | 14.5 | Yes | Yes | 26.9 | 23.7 | 3.2 | BECF6E3E0BEC4EED8C8BC4180241EFC8 |  | R22 | Non-TXV |  | 10.98% | 0.89015 | 21.11% | [5 empty] | Non-TXV | 10.98%
Stockton | CA | 95207-9218 |  | 2013-07-30 | 2013-07-30 15:21 | 2013-07-30 15:51 | GE - BTD718A100A0 | 46 | -4.3 | Yes | Yes | 19 | 16.9 | 2.1 | 142CAD2E197A4711A3923ED68B42F118 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.348% | 1.0935 | 2.618% |  |  |  |  | Non-TXV |  |  | -9.348%
Stockton | CA | 95207-6956 |  | 2013-07-29 | 2013-07-29 10:55 | 2013-07-29 11:12 | OTHER - UNK | 64 | -5.3 | Yes | Yes | 21.4 | 18.9 | 2.5 | 99042F3542F24389891D377DB4219E98 |  | R22 | Non-TXV |  | -8.281% | 1.0828 | 2.319% |  |  |  |  | Non-TXV |  |  | -8.281%
Atwater | CA | 95301-2571 |  | 2013-07-10 | 2013-07-10 08:44 | 2013-07-10 08:47 | GOODMAN - GSH130301AA | 153 | 4.6 | Yes | Yes | 17.9 | 19.9 | -2 | 812E3884B5F04B05ADBF9DCB8CFDE5B7 |  | R22 | Non-TXV |  | 3.007% | 0.96993 | 5.778% | [5 empty] | Non-TXV | 3.007%
Stockton | CA | 95207-4274 |  | 2013-07-18 | 2013-07-18 10:23 | 2013-07-18 10:40 | GE - BTD724A100A0 | 68 | 14.3 | Yes | Yes | 20.8 | 19.2 | 1.6 | AA138EE40BEB45698D706716DCC03B00 |  | R22 | Non-TXV |  | 21.03% | 0.78971 | 40.41% | [5 empty] | Non-TXV | 21.03%
Chowchilla | CA | 93610-8988 |  | 2013-08-19 | 2013-08-19 14:48 | 2013-08-19 14:50 | YORK - D2YS024N04506A | 62 | 7.7 | Yes | Yes | 19.1 | 18.8 | 0.3 | FB65A71A4BED482D9EB603CC5FFFB657 |  | R22 | Non-TXV |  | 12.42% | 0.87581 | 23.87% | [5 empty] | Non-TXV | 12.42%
Stockton | CA | 95215-7306 |  | 2013-07-08 | 2013-07-08 09:42 | 2013-07-08 10:09 | BDP - 561CJ018-B | 52 | 1.7 | Yes | Yes | 21.7 | 20.7 | 1 | 904A6878661F4B03B8E2EB9C205E812A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.269% | 0.96731 | 6.283% | [5 empty] | Non-TXV | 3.269%
Stockton | CA | 95219-4513 |  | 2013-07-26 | 2013-07-26 11:16 | 2013-07-26 11:39 | WEATHER KING - 13AJA18A01 | 67 | 2.9 | Yes | Yes | 24.7 | 19.1 | 5.7 | 99A378EE9B654ABB8CBFCD73FEDF02F4 |  | R22 | Non-TXV |  | 4.328% | 0.95672 | 8.318% | [5 empty] | Non-TXV | 4.328%
Los Banos | CA | 93635-6355 |  | 2013-07-12 | 2013-07-12 09:43 | 2013-07-12 09:45 | BRYANT - 561CJ036 | 70 | 11.9 | Yes | Yes | 24.7 | 19.7 | 5 | 749476A072EB4FA2BA88F2F817F12420 |  | R22 | TXV |  | 17% | 0.83 | 32.67% | [5 empty] | TXV | 17%
Los Banos | CA | 93635-6322 |  | 2013-08-01 | 2013-08-01 11:18 | 2013-08-01 11:24 | GOODMAN - CK30-1A | 76 | 3.1 | Yes | Yes | 18.9 | 18.8 | 0.1 | C141A396100E440BADF11833DCFF1326 |  | R22 | Non-TXV |  | 4.079% | 0.95921 | 7.839% | [5 empty] | Non-TXV | 4.079%
Los Banos | CA | 93635-6378 |  | 2013-07-24 | 2013-07-24 15:43 | 2013-07-24 15:47 | AIRE-FLO - 12GCS036X-75-3PA | 110 | 4.9 | Yes | Yes | 22.9 | 20.4 | 2.5 | 8ADAA40FC1964778ABB8E7A9DE9F144D |  | R22 | Non-TXV |  | 4.455% | 0.95545 | 8.561% | [5 empty] | Non-TXV | 4.455%
Stockton | CA | 95219-3505 |  | 2013-07-24 | 2013-07-24 11:59 | 2013-07-24 12:16 | DAY & NIGHT - UNK | 80 | 10 | Yes | Yes | 19.4 | 19.3 | 0.1 | FFBC250971B34ED29A41FF348FEC4B7A |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Merced | CA | 95341-5710 |  | 2013-07-01 | 2013-07-01 12:16 | 2013-07-01 12:18 | ICP - PGD336060K001C1 | 100 | 3.7 | Yes | Yes | 22.6 | 18.3 | 4.3 | 903611FC45334DD68DD11DAC1F4BFFFD |  | R410A | Non-TXV |  | 3.7% | 0.963 | 7.111% | [5 empty] | Non-TXV | 3.7%
Madera | CA | 93637-2729 |  | 2013-07-01 | 2013-07-01 20:50 | 2013-07-01 21:41 | CARRIER - 48KA1G03008E | 151 | 6.7 | Yes | Yes | 17.8 | 18.1 | -0.3 | 683870F76C2A41D9B5D852333557A754 |  | R22 | Non-TXV |  | 4.437% | 0.95563 | 8.527% | [5 empty] | Non-TXV | 4.437%
Stockton | CA | 95209-1758 |  | 2013-07-10 | 2013-07-10 15:42 | 2013-07-10 15:59 | RHEEM - UNK | 112 | 13.6 | Yes | Yes | 22.2 | 19.9 | 2.4 | 849BE8CCD26F40F1B663352DC2379B0E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.14% | 0.87857 | 23.34% | [5 empty] | Non-TXV | 12.14%
Penryn | CA | 95663-9665 |  | 2013-09-19 | 2013-09-19 14:05 | 2013-09-19 14:24 | ARCOAIRE - UNK | 90 | 15.7 | Yes | Yes | 19 | 21.7 | -2.7 | 014084154A3B434C8CCF23B44140FF28 |  | R22 | Non-TXV |  | 17.44% | 0.82556 | 33.52% | [5 empty] | Non-TXV | 17.44%
Los Banos | CA | 93635-6435 |  | 2013-07-30 | 2013-07-30 09:48 | 2013-07-30 09:53 | BRYANT - 563CN060-G | 202 | 5.9 | Yes | Yes | 17.6 | 20.4 | -2.8 | 4518DAAE2B164F27A5D10A9A509B2321 |  | R22 | Non-TXV |  | 2.921% | 0.97079 | 5.613% | [5 empty] | Non-TXV | 2.921%
Rough & Ready | CA | 95975-9604 |  | 2013-08-26 | 2013-08-26 13:23 | 2013-08-26 13:42 | RHEEM - RAND-048JBZ | 146 | -19.2 | Yes | Yes | 20.1 | 21.7 | -1.6 | C238C74A0B14471A83DA75E5801E4097 |  | R22 | TXV |  | -13.15% | 1.1315 | 3.683% |  |  |  |  | TXV |  |  | -13.15%
Atascadero | CA | 93422-5251 |  | 2013-08-08 | 2013-08-08 15:57 | 2013-08-08 16:14 | BDP - 585A030080YAC | 50 | 2.1 | Yes | Yes | 24.5 | 20.1 | 4.4 | C979672848AE4233AA7F187243C9739D |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Chico | CA | 95926-2010 |  | 2013-07-01 | 2013-07-01 19:36 | 2013-07-01 19:53 | YORK - H2RA030606A | 62 | 13.5 | Yes | Yes | 21.9 | 21.4 | 0.5 | 24E49A98FC3845A7A9083B81C90267CE |  | R22 | Non-TXV |  | 21.77% | 0.78226 | 41.85% | [5 empty] | Non-TXV | 21.77%
Meadow Vista | CA | 95722-9555 |  | 2013-10-07 | 2013-10-07 12:15 | 2013-10-07 12:35 | TRANE - 2TTR2060B1000AA | 146 | 8.6 | Yes | Yes | 26 | 20.9 | 5.1 | 7A1AD2CDBD1C414189E4E6873889A6EA |  | R22 | TXV |  | 5.89% | 0.9411 | 11.32% | [5 empty] | TXV | 5.89%
Stockton | CA | 95204-2423 |  | 2013-06-28 | 2013-06-28 13:29 | 2013-06-28 13:29 | OTHER - NAC048AKC3 | 112 | 0 | Yes | Yes | 19.3 | 18.8 | 0.5 | EFFB8449CF7D40A9B06DE8F60D06C6C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-9183 |  | 2013-07-08 | 2013-07-08 12:58 | 2013-07-08 13:17 | GOODMAN - CKJ30-1A | 92 | 14.2 | Yes | Yes | 19.3 | 19.8 | -0.5 | AA0FA52FB74544B5B7AA60C22EA835BF |  | R22 | Non-TXV |  | 15.43% | 0.84565 | 29.66% | [5 empty] | Non-TXV | 15.43%
Meadow Vista | CA | 95722-9549 |  | 2013-08-14 | 2013-08-14 11:07 | 2013-08-14 11:30 | BRYANT - 556ANO36-A | 150 | 5.5 | Yes | Yes | 21 | 19.1 | 1.9 | 07A04E5E19204AE38C5F2DC079BE1AA4 |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Sonora | CA | 95370-5748 |  | 2013-07-31 | 2013-07-31 16:18 | 2013-07-31 16:40 | NORDYNE - UNK | 104 | 16 | Yes | Yes | 21.7 | 23.1 | -1.4 | A85E71D468D1459695C9D605CE93C1F9 |  | R22 | Non-TXV |  | 15.38% | 0.84615 | 29.57% | [5 empty] | Non-TXV | 15.38%
Foresthill | CA | 95631-0000 |  | 2013-10-25 | 2013-10-25 12:28 | 2013-10-25 12:28 | TRANE - YCC048F1H0BA | 128 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | 59519DDD635E41EF9C600903EA1612DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-9139 |  | 2013-07-08 | 2013-07-08 15:52 | 2013-07-08 16:15 | AMANA - PGD30C0702E | 74 | 2.4 | Yes | Yes | 22.9 | 19.5 | 3.4 | 1E289DFD0E7F46E48C37EDCBECF9FE96 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Los Banos | CA | 93635-7423 |  | 2013-07-29 | 2013-07-29 14:45 | 2013-07-29 14:49 | OTHER - JS5BD-030KA | 99 | 3.1 | Yes | Yes | 19.8 | 19.6 | 0.2 | 7416DC13A117474EBF2DBDCEECE6192F |  | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Chico | CA | 95928-8804 |  | 2013-07-08 | 2013-07-08 09:37 | 2013-07-08 15:17 | AMANA - PGB2404520 | 64 | 9.1 | Yes | Yes | 27 | 22 | 5 | 62C133504FA0436CA45E86A0B4C3564E |  | R22 | Non-TXV |  | 14.22% | 0.85781 | 27.33% | [5 empty] | Non-TXV | 14.22%
Stockton | CA | 95219-3502 |  | 2013-07-08 | 2013-07-08 15:42 | 2013-07-08 15:42 | HEIL - PGC036K0B0B | 71 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | EC564AA6B22B4BA0A83925F7A7F0DD7A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-7348 |  | 2013-07-01 | 2013-07-01 13:53 | 2013-07-01 14:27 | YORK - DAA-F030N070C | 76 | 2.8 | Yes | Yes | 15.3 | 17.6 | -2.3 | 0BFDF7F133ED4A09BE22DC377CCDB652 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Chico | CA | 95928-9406 |  | 2013-07-31 | 2013-07-31 11:00 | 2013-07-31 11:27 | YORK - BRCS0301BD | 62 | 8 | Yes | Yes | 19.3 | 20.2 | -0.9 | E55502297FDB4EA69A629CCD1434A406 |  | R22 | Non-TXV |  | 12.9% | 0.87097 | 24.8% | [5 empty] | Non-TXV | 12.9%
Stockton | CA | 95210-2342 |  | 2013-07-03 | 2013-07-03 10:50 | 2013-07-03 11:11 | GE - 21TA030H1A01 | 102 | 3.1 | Yes | Yes | 21.2 | 17.4 | 3.8 | 7CBB31DD34514E39B1880240B647C637 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Auburn | CA | 95603-9408 |  | 2013-06-28 | 2013-06-28 08:44 | 2013-06-28 09:13 | AMERICAN STANDARD - YCC036F1M0BC | 85 | 5.3 | Yes | Yes | 18.8 | 17.7 | 1.1 | D2A6DE042B3E4A8AB34CB9D2737DB2E3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Los Banos | CA | 93635-6322 |  | 2013-07-12 | 2013-07-12 08:29 | 2013-07-12 08:46 | GOODMAN - CK361A | 73 | 4.7 | Yes | Yes | 24.7 | 18.7 | 6 | EC4356BAA51A4FE386C317391CC33E3D |  | R22 | Non-TXV |  | 6.438% | 0.93562 | 12.37% | [5 empty] | Non-TXV | 6.438%
Penryn | CA | 95663-0000 |  | 2013-09-19 | 2013-09-19 15:41 | 2013-09-19 15:41 | AMANA - RCE36C2A | 230 | 0 | Yes | Yes | 22 | 19.9 | 2.1 | 3B84AA1E9B7044229FFE707E39E9AB84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5238 |  | 2013-07-12 | 2013-07-12 14:14 | 2013-07-12 14:16 | BRYANT - 561CJ060 | 152 | 18.1 | Yes | Yes | 24.5 | 22.1 | 2.4 | 2997BCC212854C74841A53A764B7956E |  | R22 | TXV |  | 11.91% | 0.88092 | 22.88% | [5 empty] | TXV | 11.91%
Madera | CA | 93637-5655 |  | 2013-07-09 | 2013-07-09 13:30 | 2013-07-10 00:17 | LENNOX - 10GCS036X-75-1PA | 159 | 7.6 | Yes | Yes | 20 | 21.5 | -1.5 | C6A6B9266CDD40FB9A61AAEDD6C8EBAA |  | R22 | Non-TXV |  | 4.78% | 0.9522 | 9.186% | [5 empty] | Non-TXV | 4.78%
Tracy | CA | 95377-9577 |  | 2013-08-12 | 2013-08-12 16:26 | 2013-08-12 16:26 | YORK - UNK | 96 | 0 | Yes | Yes | 15.2 | 17.5 | -2.3 | FC50596E97384F09BD747A37831B2854 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6513 |  | 2013-07-10 | 2013-07-10 13:13 | 2013-07-10 13:41 | YORK - H2RA036S06E | 63 | 2.7 | Yes | Yes | 25.9 | 19.9 | 6 | 362A03988920423D957CD7928ACF33AB |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95207-9220 |  | 2013-07-31 | 2013-07-31 09:20 | 2013-07-31 09:56 | OTHER - DAB1025J | 85 | 2.8 | Yes | Yes | 19.2 | 19.1 | 0.1 | 45365EC264BF4057A906C607C0A9DF7D |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Los Banos | CA | 93635-2629 |  | 2013-07-02 | 2013-07-02 09:41 | 2013-07-02 09:48 | GOODMAN - CK361A | 73 | 6 | Yes | Yes | 24.7 | 20.6 | 4.1 | 833FF84CF8994CF3ABDBA61B6C155E7F |  | R22 | Non-TXV |  | 8.219% | 0.91781 | 15.8% | [5 empty] | Non-TXV | 8.219%
Dinuba | CA | 93618-3240 |  | 2013-08-08 | 2013-08-08 15:32 | 2013-08-08 16:13 | ICP - PGF042K080 | 84 | 10 | Yes | Yes | 17 | 19 | -2 | 5166EA30EDF24FF8AB935BC68BE6D732 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.9% | 0.88095 | 22.88% | [5 empty] | Non-TXV | 11.9%
Madera | CA | 93637-8849 |  | 2013-07-03 | 2013-07-03 18:41 | 2013-07-03 21:12 | CARRIER - 0908E20278 | 72 | 4.8 | Yes | Yes | 14.4 | 16.9 | -2.5 | DF54DCE5082F4F36BE5BD71ED320EE33 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Madera | CA | 93637-2930 |  | 2013-07-01 | 2013-07-01 22:45 | 2013-07-02 01:42 | CARRIER - 48GS-048115301- | 81 | 0 | Yes | Yes | 7.3 | 9 | -1.7 | C153CF9CDE5C465EA6328883403BC446 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-4850 |  | 2013-08-27 | 2013-08-27 11:09 | 2013-08-27 11:26 | PAYNE - PY1PNB030040AAAA | 60 | 1.8 | Yes | Yes | 16.9 | 19.2 | -2.3 | 7CD293D1CB194AA9990D05AA62470D47 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95928-7715 |  | 2013-07-16 | 2013-07-16 19:55 | 2013-07-16 10:11 | OTHER - 561CJ030-A | 78 | 3 | Yes | Yes | 16.7 | 18.7 | -2 | 3BF62662C1B74422817044953E247E24 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Stockton | CA | 95206-5302 |  | 2013-07-11 | 2013-07-11 11:55 | 2013-07-11 12:53 | DAY & NIGHT - 591ANY042000ABAA | 112 | -6.6 | Yes | Yes | 21.2 | 19.3 | 1.9 | F220860718514FFC9F5EB2D99857003F |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Madera | CA | 93637-2639 |  | 2013-07-01 | 2013-07-01 11:19 | 2013-07-01 22:21 | CARRIER - 48KLA136---32 | 54 | 3.5 | Yes | Yes | 18.7 | 20.7 | -2 | B246211F04A44B83B665BAEF02972A4B |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Stockton | CA | 95204-3212 |  | 2013-07-02 | 2013-07-02 09:12 | 2013-07-02 09:32 | TRANE - TTR036C10A0 | 92 | -8.7 | Yes | Yes | 18.3 | 18 | 0.3 | BA62EBC1FFE44DBA899850ACA88D2A90 |  | R22 | Non-TXV |  | -9.457% | 1.0946 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.457%
Lincoln | CA | 95648-2435 |  | 2013-08-06 | 2013-08-06 14:47 | 2013-08-06 14:47 | YORK - H1DE030S06B | 80 | 0 | Yes | Yes | 17.6 | 19.6 | -2 | 993278B255A84CBDAEEC518E44EFAB9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-9319 |  | 2013-07-26 | 2013-07-26 03:18 | 2013-07-26 09:18 | CARRIER - 2506E01030 | 121 | 8.5 | Yes | Yes | 17.8 | 19.7 | -1.9 | 8A45C5DD8CBE43EF85F1000EDB1AB4FF |  | R22 | Non-TXV |  | 7.025% | 0.92975 | 13.5% | [5 empty] | Non-TXV | 7.025%
Paradise | CA | 95969-5172 |  | 2013-06-29 | 2013-06-29 19:16 | 2013-06-29 19:35 | DAY & NIGHT - PGD324060K00K1 | 72 | 3.5 | Yes | Yes | 21.9 | 21.9 | 0 | 4AE1BEFE42B54C0BBF69727D6D822826 |  | R410A | Non-TXV |  | 4.861% | 0.95139 | 9.342% | [5 empty] | Non-TXV | 4.861%
Merced | CA | 95340-6700 |  | 2013-07-02 | 2013-07-02 13:42 | 2013-07-02 13:56 | TRANE - TTR036C100AO | 92 | 13.2 | Yes | Yes | 21.6 | 17 | 4.6 | 575DCD9BCA754ED6949778690B62B3EB |  | R22 | Non-TXV |  | 14.35% | 0.85652 | 27.57% | [5 empty] | Non-TXV | 14.35%
Riverbank | CA | 95367-3200 |  | 2013-07-12 | 2013-07-12 09:06 | 2013-07-12 09:27 | RHEEM - RRMA-A024JK06X | 70 | 2.1 | Yes | Yes | 22.5 | 20.3 | 2.3 | 33DF0955586B4BFE88DFCBA9E37012E6 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Placerville | CA | 95667-9398 |  | 2013-07-10 | 2013-07-10 11:38 | 2013-07-10 11:56 | COLEMAN - UNK | 90 | 2.7 | Yes | Yes | 23 | 21 | 2 | 72DF3C0B08F140C59C93D070EF691CEB |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95348-9427 |  | 2013-08-09 | 2013-08-09 10:13 | 2013-08-09 10:34 | GOODMAN - GPG12300701A | 73 | 7.2 | Yes | Yes | 20.1 | 18 | 2.1 | 1C5FBAA1F276488FBB07FBB20913D240 |  | R22 | Non-TXV |  | 9.863% | 0.90137 | 18.95% | [5 empty] | Non-TXV | 9.863%
Applegate | CA | 95703-0000 |  | 2013-08-19 | 2013-08-19 13:39 | 2013-08-19 14:16 | PAYNE - 565BJ048 | 125 | 11.1 | Yes | Yes | 20.2 | 19.9 | 0.3 | 0629358661374CFF86BC009DF3F9319A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.88% | 0.9112 | 17.07% | [5 empty] | Non-TXV | 8.88%
Stockton | CA | 95209-3604 |  | 2013-07-15 | 2013-07-15 08:51 | 2013-07-15 09:09 | GOODMAN - CKJ36-10 | 90 | -10.2 | Yes | Yes | 24.1 | 18.7 | 5.4 | D4FA57C71D094C4897708F915C90DFC3 |  | R22 | TXV |  | -11.33% | 1.1133 | 3.174% |  |  |  |  | TXV |  |  | -11.33%
Stockton | CA | 95207-8803 |  | 2013-07-30 | 2013-07-30 13:59 | 2013-07-30 14:37 | PAYNE - PA13NRO30-E | 86 | 5.5 | Yes | Yes | 20 | 18.6 | 1.4 | F34568D79F5144BFA799968878136BCC |  | R22 | Non-TXV |  | 6.395% | 0.93605 | 12.29% | [5 empty] | Non-TXV | 6.395%
Merced | CA | 95348-9366 |  | 2013-07-08 | 2013-07-08 15:53 | 2013-07-08 15:55 | GOODMAN - PGB036100-1 REV A | 57 | 2 | Yes | Yes | 27.1 | 22.1 | 5 | 736D97DAE4EE4FA69B81159225D9EB5F |  | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Chowchilla | CA | 93610-2072 |  | 2013-07-29 | 2013-07-29 21:34 | 2013-07-29 21:34 | GOODMAN - CLK42-11 | 85 | 0 | Yes | Yes | 16.8 | 18.5 | -1.7 | 2CB4ACDE90F64856B938620FCAAA32C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-3247 |  | 2013-07-01 | 2013-07-01 11:17 | 2013-07-01 11:38 | DAY & NIGHT - 24DNR-108C | 48 | 1.5 | Yes | Yes | 21.6 | 17.5 | 4.1 | 3FAFFD03976448DA9619EB42EBD966A1 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Auburn | CA | 95603-3544 |  | 2013-07-13 | 2013-07-13 10:52 | 2013-07-13 11:13 | AMANA - RCB30B2A | 77 | 5.8 | Yes | Yes | 22.5 | 20.6 | 1.9 | 2224B8B664404B62B3442E6D6498FEED |  | R22 | Non-TXV |  | 7.532% | 0.92468 | 14.48% | [5 empty] | Non-TXV | 7.532%
Auburn | CA | 95603-3544 |  | 2013-07-13 | 2013-07-13 11:03 | 2013-07-13 11:25 | GOODMAN - CRT30-1 | 107 | 3.2 | Yes | Yes | 19 | 22 | -3 | BCD9F3390AE34021B391962374993220 |  | R22 | TXV |  | 2.991% | 0.97009 | 5.747% | [5 empty] | TXV | 2.991%
Madera | CA | 93637-1901 |  | 2013-07-02 | 2013-07-02 11:05 | 2013-07-17 03:15 | YORK - AC048X1021A | 117 | 4 | Yes | Yes | 19.9 | 20.7 | -0.8 | A7896693A63449E3A134A8ECBE7CB88C |  | R22 | Non-TXV |  | 3.419% | 0.96581 | 6.57% | [5 empty] | Non-TXV | 3.419%
Riverbank | CA | 95367-2921 |  | 2013-08-20 | 2013-08-20 10:27 | 2013-08-20 10:44 | AMERICAN STANDARD - YCY036F1M0AA | 136 | 4.2 | Yes | Yes | 19.4 | 19.3 | 0.1 | 8A18E87C729148BC83D6DF43A698AF5E |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Riverbank | CA | 95367-3816 |  | 2013-07-12 | 2013-07-12 11:18 | 2013-07-12 11:44 | PAYNE - 484ANW024040ACAE | 64 | 2.1 | Yes | Yes | 19.7 | 19.5 | 0.2 | 79D6BC300BED4168B85708597E627076 |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Stockton | CA | 95219-7245 |  | 2013-07-29 | 2013-07-29 09:26 | 2013-07-29 09:46 | LENNOX - 13ACC-042-230-02 | 123 | 4.3 | Yes | Yes | 16.2 | 18.2 | -2 | 3D8B5B98234F474AA3FC179EE0615324 |  | R22 | Non-TXV |  | 3.496% | 0.96504 | 6.718% | [5 empty] | Non-TXV | 3.496%
Lincoln | CA | 95648-3221 |  | 2013-07-13 | 2013-07-13 13:56 | 2013-07-13 14:17 | LENNOX - 13ACD-0480230-01 | 204 | 6 | Yes | Yes | 17 | 19.4 | -2.4 | C85EE2C2A63E4F4D9C9A27787671ED08 |  | R22 | TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | TXV | 2.941%
Lathrop | CA | 95330-9198 |  | 2013-07-03 | 2013-07-03 12:36 | 2013-07-03 12:55 | CARRIER - 38CMC060300 | 160 | 4.9 | Yes | Yes | 18 | 19.3 | -1.3 | C2683D1EC627440EB2F6EB13AFACC85D |  | R22 | Non-TXV |  | 3.062% | 0.96937 | 5.885% | [5 empty] | Non-TXV | 3.062%
Merced | CA | 95348-1810 |  | 2013-06-27 | 2013-06-27 13:54 | 2013-06-27 14:00 | CARRIER - 38CKC024340 | 54 | 4.6 | Yes | Yes | 20.1 | 18.5 | 1.6 | E45114F0B6B84866AEF3723E3ADCD9EF |  | R22 | TXV |  | 8.519% | 0.91481 | 16.37% | [5 empty] | TXV | 8.519%
Somerset | CA | 95684-0000 |  | 2013-08-12 | 2013-08-12 13:23 | 2013-08-12 13:23 | DAY & NIGHT - 691ANX03000AAAA | 126 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | 71F4B6B3CCE14AF3ABD9E0311343D14A |  | R22 | TXV |  | 0% | 1 | 0%
Somerset | CA | 95684-0000 |  | 2013-08-12 | 2013-08-12 13:55 | 2013-08-12 14:18 | DAY & NIGHT - 691ANX018000AAAA | 116 | 7.6 | Yes | Yes | 20.7 | 22.1 | -1.4 | FD4E232AF6E34391A7C7D3D2186823E7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.552% | 0.93448 | 12.59% | [5 empty] | Non-TXV | 6.552%
Stockton | CA | 95219-3120 |  | 2013-07-01 | 2013-07-01 10:50 | 2013-07-01 11:07 | RUUD - UAKA-024JAZ | 50 | 3.4 | Yes | Yes | 14.9 | 17.9 | -3 | 796BEC29F41F4D22BEFD823E9F2D3EAC |  | R22 | Non-TXV |  | 6.8% | 0.932 | 13.07% | [5 empty] | Non-TXV | 6.8%
Stockton | CA | 95207-1833 |  | 2013-07-18 | 2013-07-18 09:35 | 2013-07-18 09:55 | RHEEM - HC-80-24-21C | 85 | 6.4 | Yes | Yes | 23.3 | 19 | 4.4 | 0015807FB1D54F759FD6F6B3339F4D3E |  | R22 | Non-TXV |  | 7.529% | 0.92471 | 14.47% | [5 empty] | Non-TXV | 7.529%
Stockton | CA | 95207-4274 |  | 2013-07-31 | 2013-07-31 09:58 | 2013-07-31 10:31 | GE - BTD724A100A0 | 68 | 6.5 | Yes | Yes | 18.2 | 18.7 | -0.5 | B503F372DCCE44089CAF497952DAEBF0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.559% | 0.90441 | 18.37% | [5 empty] | Non-TXV | 9.559%
Stockton | CA | 95207-1834 |  | 2013-07-17 | 2013-07-17 14:22 | 2013-07-17 14:44 | RHEEM - HC-80-24-21C | 49 | 8.7 | Yes | Yes | 19.2 | 17.3 | 1.9 | 028FB5B5C379495D8F3C1C82514F6992 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.76% | 0.82245 | 34.12% | [5 empty] | Non-TXV | 17.76%
Los Banos | CA | 93635-6399 |  | 2013-08-01 | 2013-08-01 12:56 | 2013-08-01 13:00 | GIBSON - JS5BD-060K | 232 | 12.7 | Yes | Yes | 21.5 | 20.4 | 1.1 | 2EA60F8A285D4AFAA31E267563D18C04 |  | R22 | Non-TXV |  | 5.474% | 0.94526 | 10.52% | [5 empty] | Non-TXV | 5.474%
Chico | CA | 95973-0508 |  | 2013-08-09 | 2013-08-09 14:46 | 2013-08-09 15:40 | ICP - NXA624GKA100 | 96 | 9.9 | Yes | Yes | 18.8 | 21 | -2.2 | A2E3383D73564619868D1395C6F63749 |  | R410A | TXV |  | 10.31% | 0.89687 | 19.82% | [5 empty] | TXV | 10.31%
Stockton | CA | 95207-8103 |  | 2013-06-26 | 2013-06-26 13:54 | 2013-06-26 14:16 | PAYNE - PY3GNAA24060NA | 74 | 4.2 | Yes | Yes | 20.7 | 15.8 | 4.9 | 315B1B6EBA2A4FDEA167A9F579CB32C0 |  | R410A | TXV |  | 5.676% | 0.94324 | 10.91% | [5 empty] | TXV | 5.676%
Somerset | CA | 95684-9374 |  | 2013-08-12 | 2013-08-12 16:20 | 2013-08-12 16:20 | BDP - 542D042HP | 181 | 0 | Yes | Yes | 18.6 | 20.2 | -1.6 | 13B923828D32498B9264FA3AE98A07C6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-0000 |  | 2013-07-11 | 2013-07-11 09:44 | 2013-07-11 10:02 | PAYNE - PA10JA036-A | 84 | 2.8 | Yes | Yes | 19.9 | 18.7 | 1.2 | 638AD46DC70A411D99C529122DB4D02B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95209-1579 |  | 2013-07-12 | 2013-07-12 11:06 | 2013-07-12 11:06 | GOODMAN - GPG13240451CB | 74 | 0 | Yes | Yes | 16.4 | 18.6 | -2.2 | DF13F60F0AB74ECAB8B58E56F51A1300 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3665 |  | 2013-06-27 | 2013-06-27 08:56 | 2013-06-27 09:17 | CARRIER - 561AJ036-B | 78 | -7.5 | Yes | Yes | 17.3 | 18.2 | -0.9 | 8C38141E4BC8479588EAA1CF4819C85A |  | R22 | TXV |  | -9.615% | 1.0962 | 2.693% |  |  |  |  | TXV |  |  | -9.615%
Los Banos | CA | 93635-6456 |  | 2013-07-29 | 2013-07-29 13:18 | 2013-07-29 13:22 | YORK - H2RD048S06B | 134 | 4.1 | Yes | Yes | 16.1 | 18.5 | -2.4 | 1764F67AD3FF49D68E3486AF3FD54372 |  | R22 | Non-TXV |  | 3.06% | 0.9694 | 5.88% | [5 empty] | Non-TXV | 3.06%
Stockton | CA | 95206-5134 |  | 2013-07-10 | 2013-07-10 14:09 | 2013-07-10 14:33 | CARRIER - 38CKC036350 | 70 | -4.9 | Yes | Yes | 20.7 | 16.6 | 4.1 | 4510498777634F77ADFD9ED1E115654F |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Stockton | CA | 95212-1123 |  | 2013-06-26 | 2013-06-26 10:19 | 2013-06-26 10:39 | YORK - BRCS0361BD | 63 | 14.2 | Yes | Yes | 16.8 | 17.4 | -0.6 | 3982D75CE8E54B0487307E1F243A012A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.54% | 0.7746 | 43.32% | [5 empty] | Non-TXV | 22.54%
Lathrop | CA | 95330-9540 |  | 2013-07-30 | 2013-07-30 11:33 | 2013-07-30 11:59 | GE - BGTA730B1B | 53 | 2.2 | Yes | Yes | 20.4 | 18.7 | 1.7 | D776D809F29448619004D9421D5744E7 |  | R22 | Non-TXV |  | 4.151% | 0.95849 | 7.977% | [5 empty] | Non-TXV | 4.151%
Stockton | CA | 95204-2747 |  | 2013-06-28 | 2013-06-28 11:58 | 2013-06-28 11:58 | OTHER - 18JQ105 | 40 | 0 | Yes | Yes | 18.8 | 19.5 | -0.7 | 45610F4F41D14F418C0605FB4AFBB635 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0536 |  | 2013-08-21 | 2013-08-21 12:58 | 2013-08-21 13:33 | YORK - 62DB024506B | 48 | 2.6 | Yes | Yes | 25.5 | 22.1 | 3.4 | FB4E42620F3C49ABAD2D3A92C9F21364 |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Lathrop | CA | 95330-9540 |  | 2013-07-03 | 2013-07-03 10:23 | 2013-07-03 10:48 | OTHER - UNK | 64 | 2.3 | Yes | Yes | 16.1 | 18.8 | -2.7 | 690287FB33B849718A956D1A43150C00 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Madera | CA | 93638-5914 |  | 2013-07-22 | 2013-07-22 12:48 | 2013-07-22 14:00 | YORK - D1NP036N05606A | 108 | 3.6 | Yes | Yes | 18.3 | 18.6 | -0.3 | E3A3F2D9AB6C440EA2A1E90846F7B52E |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95209-1118 |  | 2013-07-10 | 2013-07-10 08:41 | 2013-07-10 09:02 | GOODMAN - CK-361B | 76 | 12 | Yes | Yes | 23.4 | 19.3 | 4.1 | E182DF1D031843F1BA534D063B9FF4AC |  | R22 | Non-TXV |  | 15.79% | 0.84211 | 30.34% | [5 empty] | Non-TXV | 15.79%
Madera | CA | 93637-1906 |  | 2013-07-01 | 2013-07-01 17:58 | 2013-07-01 20:48 | YORK - D1AN036N03606C | 68 | 3.7 | Yes | Yes | 17.5 | 18.4 | -0.9 | 742EEDA1E01144AE9EE88C3CC6A924F8 |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Stockton | CA | 95207-5945 |  | 2013-07-29 | 2013-07-29 11:31 | 2013-07-29 11:48 | DAY & NIGHT - UNK | 54 | 1.7 | Yes | Yes | 19 | 19.3 | -0.3 | B4906EA3F1B04B2ABE67AE225870E86D |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Stockton | CA | 95212-3506 |  | 2013-07-22 | 2013-07-22 12:00 | 2013-07-22 12:26 | YORK - AC060X1223A | 147 | 15.2 | Yes | Yes | 17.4 | 19.3 | -1.9 | 675C9CAF6CA546EEB1BCF25C1876EA33 |  | R22 | Non-TXV |  | 10.34% | 0.8966 | 19.87% | [5 empty] | Non-TXV | 10.34%
Stockton | CA | 95204-2748 |  | 2013-07-26 | 2013-07-26 11:28 | 2013-07-26 11:45 | PAYNE - PA10JA018000ACAA | 60 | 3.4 | Yes | Yes | 15.8 | 19.3 | -3.5 | 13F9BA9763644C20B74EE78CC55C8D5F |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Valley Springs | CA | 95252-9682 |  | 2013-08-14 | 2013-08-14 09:18 | 2013-08-14 09:48 | DAY & NIGHT - 541DB048 | 174 | 7.5 | Yes | Yes | 25.8 | 20.3 | 5.5 | DA2066896CFA464898D17CFAF1CF49A0 |  | R22 | Non-TXV |  | 4.31% | 0.9569 | 8.284% | [5 empty] | Non-TXV | 4.31%
Newman | CA | 95360-1100 |  | 2013-08-22 | 2013-08-22 09:30 | 2013-08-22 09:55 | DAY & NIGHT - 591ANX036000AAAA | 84 | 2.9 | Yes | Yes | 24.1 | 19.8 | 4.3 | 538159538BC34E4C92CC2E8ACF784ADF |  | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Magalia | CA | 95954-8820 |  | 2013-07-17 | 2013-07-17 10:22 | 2013-07-17 10:40 | AMERICAN STANDARD - 2WCX3042A1000AA | 122 | 5 | Yes | Yes | 16.8 | 19.6 | -2.8 | 4D39E86372AB4E038B09C9374B96ED31 |  | R22 | Non-TXV |  | 4.098% | 0.95902 | 7.876% | [5 empty] | Non-TXV | 4.098%
Chico | CA | 95973-7807 |  | 2013-07-09 | 2013-07-09 19:49 | 2013-07-09 20:08 | OTHER - PH13NR036-H | 101 | 4.3 | Yes | Yes | 19 | 21.8 | -2.8 | BECE1EC217284F78A043F986599B7603 |  | R22 | TXV |  | 4.257% | 0.95743 | 8.182% | [5 empty] | TXV | 4.257%
Yuba City | CA | 95993-7100 |  | 2013-07-18 | 2013-07-18 13:14 | 2013-07-18 13:30 | CARRIER - 24ACR36A300 | 106 | 3.2 | Yes | Yes | 18 | 18.5 | -0.5 | FD3DA20C9ECD49EDA35DAC8DDA83010C |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Stockton | CA | 95209-1545 |  | 2013-07-10 | 2013-07-10 09:43 | 2013-07-10 10:05 | GUARDIAN - GCGD36S41S38 | 73 | 4.3 | Yes | Yes | 24 | 18.7 | 5.3 | 91114D57E31844978F77D320D83A074A |  | R410A | Non-TXV |  | 5.89% | 0.9411 | 11.32% | [5 empty] | Non-TXV | 5.89%
Stockton | CA | 95212-3020 |  | 2013-07-15 | 2013-07-15 11:08 | 2013-07-15 11:33 | YORK - H2RD036S06B | 96 | 11.9 | Yes | Yes | 20.4 | 19.3 | 1.1 | 8D36E6A3A035419B8F1AAACF5D1623E0 |  | R22 | Non-TXV |  | 12.4% | 0.87604 | 23.82% | [5 empty] | Non-TXV | 12.4%
Madera | CA | 93638-5508 |  | 2013-07-22 | 2013-07-22 16:18 | 2013-07-22 16:48 | YORK - D1NP036N056060A | 108 | 3.5 | Yes | Yes | 18.4 | 20.4 | -2 | F0189D150DCC405CA67B07DCC9FBE085 |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Merced | CA | 95340-1611 |  | 2013-07-09 | 2013-07-09 09:44 | 2013-07-09 09:46 | AMERICAN STANDARD - 2YCX3048A1096AA | 144 | 7.3 | Yes | Yes | 19.4 | 19.9 | -0.5 | 6AD5248B19FC4821B812C3E063AA293B |  | R22 | Non-TXV |  | 5.069% | 0.94931 | 9.742% | [5 empty] | Non-TXV | 5.069%
San Andreas | CA | 95249-9646 |  | 2013-09-05 | 2013-09-05 10:11 | 2013-09-05 10:29 | BRYANT - 552AN060-A | 128 | 4.8 | Yes | Yes | 17.9 | 20.7 | -2.8 | CE1BCAEC9EF440A38E762265CCA207EC |  | R410A | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Merced | CA | 95348-1818 |  | 2013-09-06 | 2013-09-06 11:47 | 2013-09-06 11:48 | GE - BTD724A100AO | 68 | 6.6 | Yes | Yes | 22.3 | 19.9 | 2.4 | AF123A64961F4A919B86B910130959A2 |  | R22 | Non-TXV |  | 9.706% | 0.90294 | 18.65% | [5 empty] | Non-TXV | 9.706%
Stockton | CA | 95212-3543 |  | 2013-06-27 | 2013-06-27 13:33 | 2013-06-27 13:58 | GOODMAN - CLJ48-1A | 130 | 3.8 | Yes | Yes | 17 | 17.7 | -0.7 | 7FEA6F29E54045CA95CD8B58B5958F4B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Stockton | CA | 95210-3329 |  | 2013-07-31 | 2013-07-31 13:00 | 2013-07-31 13:23 | INTERTHERM - A00C48BAYRA | 76 | -5.4 | Yes | Yes | 25.5 | 20.9 | 4.6 | E96B41269C5943FCB4608CC23117D34F |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Oakdale | CA | 95361-9558 |  | 2013-07-10 | 2013-07-10 15:13 | 2013-07-10 15:45 | COLEMAN - CBD | 72 | 7.9 | Yes | Yes | 24.4 | 21.3 | 3.2 | 92A59693A7FA47EFBDA6578B69AB0BFA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.97% | 0.89028 | 21.09% | [5 empty] | Non-TXV | 10.97%
Madera | CA | 93638-5507 |  | 2013-07-25 | 2013-07-25 10:17 | 2013-07-25 12:22 | YORK - D1NA030N3606C | 76 | 2.5 | Yes | Yes | 18.4 | 20.2 | -1.8 | A5CA4961BD9543A5B6D45186314DE3C1 |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Angels Camp | CA | 95222-0000 |  | 2013-10-15 | 2013-10-15 11:40 | 2013-10-15 12:01 | YORK - D2NY036N05606A | 120 | -9.6 | Yes | Yes | 18.5 | 20.1 | -1.6 | E2C2E25F18F049D3BBE2F1DD9CC90EBC |  | R410A | TXV |  | -8% | 1.08 | 2.24% |  |  |  |  | TXV |  |  | -8%
Madera | CA | 93638-2833 |  | 2013-07-18 | 2013-07-18 01:58 | 2013-07-18 03:04 | RHEEM - RRNA-A036JKOE | 70 | 2.7 | Yes | Yes | 17.2 | 19.8 | -2.6 | FFB4387E40E8481B9A45BD4896F2350B |  | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
Newman | CA | 95360-1637 |  | 2013-09-05 | 2013-09-05 10:41 | 2013-09-05 11:20 | HEIL - NRGE30SAK02 | 47 | 6.3 | Yes | Yes | 17.6 | 20.3 | -2.7 | AEBF916927D94A61B5C47930F77B4A40 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.4% | 0.86596 | 25.76% | [5 empty] | Non-TXV | 13.4%
Merced | CA | 95348-2818 |  | 2013-07-15 | 2013-07-15 17:09 | 2013-07-15 17:10 | ICP - GPCM042K080D | 84 | 17.6 | Yes | Yes | 21.9 | 21 | 0.9 | BADA3FC0053C4F929355A97353991C43 |  | R22 | Non-TXV |  | 20.95% | 0.79048 | 40.27% | [5 empty] | Non-TXV | 20.95%
Merced | CA | 95348-4360 |  | 2013-08-19 | 2013-08-19 12:50 | 2013-08-19 12:54 | RHEEM - RAKA-024JAS | 51 | 2.2 | Yes | Yes | 16.6 | 18.3 | -1.7 | C6426D2C5B044FE18CA82CC5DC0B0769 |  | R22 | Non-TXV |  | 4.314% | 0.95686 | 8.29% | [5 empty] | Non-TXV | 4.314%
Fresno | CA | 93727-0000 |  | 2013-07-15 | 2013-07-15 19:34 | 2013-07-15 20:06 | GOODMAN - GPG13360701AB | 112 | 4.2 | Yes | Yes | 20.1 | 18.1 | 2 | 9D8E761DEE974295BEF3AEA28F0733D8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95209-2410 |  | 2013-07-11 | 2013-07-11 10:09 | 2013-07-11 10:37 | RHEEM - RAHE-060JAS | 176 | 20 | Yes | Yes | 21.9 | 17.6 | 4.3 | 9895BDD01041403F8F189AB10A87E87C |  | R22 | Non-TXV |  | 11.36% | 0.88636 | 21.84% | [5 empty] | Non-TXV | 11.36%
Chico | CA | 95926-3860 |  | 2013-08-06 | 2013-08-06 16:06 | 2013-08-06 16:35 | CARRIER - 48KL124300BF | 50 | 6.5 | Yes | Yes | 25.9 | 22 | 3.9 | 1858FEEF4A50451C82082202E2B721FC |  | R22 | Non-TXV |  | 13% | 0.87 | 24.98% | [5 empty] | Non-TXV | 13%
Fresno | CA | 93705-4639 |  | 2013-07-11 | 2013-07-11 14:28 | 2013-07-11 14:55 | YORK - D3NZ036N05606NXA | 64 | 2.3 | Yes | Yes | 21.7 | 19.8 | 1.9 | 26C9F527A8264B0AB2414EE0E5C9CF2B |  | R410A | TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | TXV | 3.594%
Merced | CA | 95348-2818 |  | 2013-07-15 | 2013-07-15 16:49 | 2013-07-15 16:50 | ICP - PGD342090K001C1 | 106 | 10.1 | Yes | Yes | 26.5 | 24.2 | 2.3 | 07BD87609387479BAB7A7E97035FC68F |  | R410A | Non-TXV |  | 9.528% | 0.90472 | 18.31% | [5 empty] | Non-TXV | 9.528%
Parlier | CA | 93648-2167 |  | 2013-07-23 | 2013-07-23 18:16 | 2013-07-23 18:18 | GOODMAN - GPG1330045M41AC | 80 | 3.5 | Yes | Yes | 18.8 | 20.2 | -1.4 | 44E6C09C9DE34010B3D98191925F43AE | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | TXV | 4.375%
Fresno | CA | 93728-1313 |  | 2013-07-15 | 2013-07-15 14:14 | 2013-07-15 14:15 | HEIL - NRGF36DDB03 | 90 | 3.1 | Yes | Yes | 20.3 | 21.5 | -1.2 | 3E61E75B6F91416AA75DA66DF647E357 |  | R22 | Non-TXV |  | 3.444% | 0.96556 | 6.619% | [5 empty] | Non-TXV | 3.444%
Madera | CA | 93638-0516 |  | 2013-07-19 | 2013-07-19 14:45 | 2013-07-28 21:33 | OTHER - 50Y0030300 | 59 | 3.3 | Yes | Yes | 17.7 | 20.6 | -2.9 | FEF54A51B08C4C26AADD90C93086B819 |  | R22 | Non-TXV |  | 5.593% | 0.94407 | 10.75% | [5 empty] | Non-TXV | 5.593%
Livingston | CA | 95334-9739 |  | 2013-09-05 | 2013-09-05 12:29 | 2013-09-05 13:11 | RHEEM - RRNA-B024JK06X | 70 | 2.8 | Yes | Yes | 18.2 | 20.2 | -2 | 4A539F3B66A14FCAAB42B695A8BF7452 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Parlier | CA | 93648-9624 |  | 2013-07-24 | 2013-07-24 13:18 | 2013-07-24 13:37 | RUUD - N/A | 60 | 2 | Yes | Yes | 16.6 | 19.5 | -2.9 | FAF77A730EA24E2582DA0F0E73E14D8D |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Madera | CA | 93637-3133 |  | 2013-07-01 | 2013-07-01 16:18 | 2013-07-01 22:20 | LENNOX - JS4BD-030KB | 42 | 2.3 | Yes | Yes | 20.2 | 20.4 | -0.2 | E391E9755300404183EBF533D60CF9F6 |  | R22 | Non-TXV |  | 5.476% | 0.94524 | 10.52% | [5 empty] | Non-TXV | 5.476%
Fresno | CA | 93722-3120 |  | 2013-07-17 | 2013-07-17 12:30 | 2013-07-17 12:35 | CARRIER - UNK | 68 | 11.8 | Yes | Yes | 20.4 | 20.2 | 0.2 | 0CE1D4242C4541F2B60E54B054CEAB4B |  | R22 | Non-TXV |  | 17.35% | 0.82647 | 33.35% | [5 empty] | Non-TXV | 17.35%
Merced | CA | 95348-1567 |  | 2013-07-03 | 2013-07-03 11:45 | 2013-07-03 11:46 | OTHER - 80R36G1AA | 120 | 12.5 | Yes | Yes | 20.8 | 17.7 | 3.1 | 415E857400DD4044A94C9BD51D3BB05B |  | R22 | Non-TXV |  | 10.42% | 0.89583 | 20.02% | [5 empty] | Non-TXV | 10.42%
Coalinga | CA | 93210-9635 |  | 2013-08-17 | 2013-08-17 12:07 | 2013-08-17 12:28 | GOODMAN - CKLJ30-1A | 92 | 2.8 | Yes | Yes | 19.8 | 20.7 | -0.9 | EFEF6961BCF74EB68366E053B96C17C4 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Parlier | CA | 93648-0000 |  | 2013-07-23 | 2013-07-23 14:21 | 2013-07-23 14:39 | LENNOX - 10GCS030X-75-2PA | 51 | 3.7 | Yes | Yes | 18.6 | 21.2 | -2.6 | 579565165C904D6DA45A245DEA81560C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.255% | 0.92745 | 13.94% | [5 empty] | Non-TXV | 7.255%
Parlier | CA | 93648-2832 |  | 2013-07-24 | 2013-07-24 12:30 | 2013-07-24 12:49 | LENNOX - 10GCS030-75-3PA | 51 | 2.6 | Yes | Yes | 20.9 | 20.2 | 0.8 | C8C1C354C40F4661A5767B87C77BE3BD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.098% | 0.94902 | 9.797% | [5 empty] | Non-TXV | 5.098%
Sanger | CA | 93657-3020 |  | 2013-08-07 | 2013-08-07 14:31 | 2013-08-07 15:09 | BDP - 589ANW030060ADBD | 69 | 8.9 | Yes | Yes | 17.5 | 19.8 | -2.3 | 904B1A9D71954BED9AC36FD4980D6B46 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.9% | 0.87101 | 24.79% | [5 empty] | Non-TXV | 12.9%
Sanger | CA | 93657-3020 |  | 2013-08-07 | 2013-08-07 15:13 | 2013-08-07 15:41 | BDP - 589ANW030060ADBD | 69 | 4.1 | Yes | Yes | 23.5 | 19.7 | 3.8 | 5C7C4923752B4EAAAACDC8C580276B40 |  | R22 | Non-TXV |  | 5.942% | 0.94058 | 11.42% | [5 empty] | Non-TXV | 5.942%
Sanger | CA | 93657-3407 |  | 2013-08-06 | 2013-08-06 15:39 | 2013-08-06 16:01 | BDP - 585A036060YACR | 60 | 5 | Yes | Yes | 19 | 20.2 | -1.2 | 570EB03A617446688E353D62664D9DA0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Fresno | CA | 93727-3018 |  | 2013-07-12 | 2013-07-12 15:29 | 2013-07-12 15:29 | RHEEM - RRNL-B036JK08X | 92 | 0 | Yes | Yes | 29.6 | 23.7 | 5.9 | 0CE86E220271488E9EFB5705E7C2C350 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3156 |  | 2013-07-17 | 2013-07-17 14:51 | 2013-07-17 14:52 | CARRIER - UNK | 68 | 9.3 | Yes | Yes | 19 | 20.1 | -1.1 | BCB8F61B82DC4686B02628F78FB01EEA |  | R22 | Non-TXV |  | 13.68% | 0.86324 | 26.28% | [5 empty] | Non-TXV | 13.68%
Parlier | CA | 93648-9628 |  | 2013-09-03 | 2013-09-03 11:20 | 2013-09-03 11:21 | RUUD - N/A | 60 | 2.1 | Yes | Yes | 15.5 | 18.4 | -2.9 | 7743AD1B73CE498AB65DE05A2DBBDB67 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Stockton | CA | 95205-8422 |  | 2013-07-23 | 2013-07-23 13:10 | 2013-07-23 13:31 | ICP - GPCM048K080D | 100 | 5.9 | Yes | Yes | 17.5 | 19.9 | -2.4 | 24471A7E6E7E4FC8A5BB9E33FA54E522 |  | R22 | Non-TXV |  | 5.9% | 0.941 | 11.34% | [5 empty] | Non-TXV | 5.9%
Fresno | CA | 93705-4342 |  | 2013-07-10 | 2013-07-10 16:30 | 2013-07-10 18:01 | RUUD - UAKA-037JAZ | 79 | 3.8 | Yes | Yes | 23 | 19 | 4 | E71EFEE2AF684B2AB60970E16FF27D8D |  | R22 | Non-TXV |  | 4.81% | 0.9519 | 9.244% | [5 empty] | Non-TXV | 4.81%
Manteca | CA | 95336-2932 |  | 2013-07-08 | 2013-07-08 08:22 | 2013-07-08 08:48 | ARCOAIRE - AG048GB2 | 85 | -8 | Yes | Yes | 20.5 | 19.9 | 0.6 | 2839F589D7AD482EBCCD64FC331E73D3 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95209-2338 |  | 2013-07-10 | 2013-07-10 15:10 | 2013-07-10 15:27 | PAYNE - PA10JA024-C | 64 | 6.6 | Yes | Yes | 21.4 | 18.8 | 2.6 | 77AA44F8FFEC4708A1E74C5727CFD112 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.31% | 0.89687 | 19.82% | [5 empty] | Non-TXV | 10.31%
Stockton | CA | 95207-8806 |  | 2013-07-30 | 2013-07-30 14:40 | 2013-07-30 15:01 | BDP - 565BJO42 | 94 | 4.4 | Yes | Yes | 21.8 | 19 | 2.8 | AEA79CBB5D9940D495D486F870C57248 |  | R22 | Non-TXV |  | 4.681% | 0.95319 | 8.996% | [5 empty] | Non-TXV | 4.681%
Fresno | CA | 93705-0235 |  | 2013-07-08 | 2013-07-08 12:14 | 2013-07-08 12:40 | AMERICAN STANDARD - YCX036F1M0AC | 114 | 6 | Yes | Yes | 18.4 | 20.1 | -1.6 | 39A73E58F55F4A3192E4618DC2B47BE5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Marysville | CA | 95901-0000 |  | 2013-06-26 | 2013-06-26 09:53 | 2013-06-26 10:22 | CARRIER - 38CKC042350 | 95 | 3.5 | Yes | Yes | 17 | 16.4 | 0.6 | A39FED69743A42D89F62BFC782F2311F |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Parlier | CA | 93648-2038 |  | 2013-07-23 | 2013-07-23 15:29 | 2013-07-23 16:19 | LENNOX - 13ACD-048-230 | 204 | 14.6 | Yes | Yes | 17.1 | 17.2 | -0.1 | AE3BC5543364454D8EF933A98CF77ED8 |  | R22 | Non-TXV |  | 7.157% | 0.92843 | 13.75% | [5 empty] | Non-TXV | 7.157%
Hamilton City | CA | 95951-0000 |  | 2013-09-05 | 2013-09-05 09:50 | 2013-09-05 10:56 | BRYANT - ACO24M1021A | 54 | 1.9 | Yes | Yes | 13.9 | 16.6 | -2.7 | E4351A24FF3E47CFA631A7FA90F09577 |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Fresno | CA | 93720-2451 |  | 2013-08-09 | 2013-08-09 14:52 | 2013-08-09 16:29 | YORK - HIRA02496A | 63 | 2.7 | Yes | Yes | 19.6 | 21.8 | -2.2 | 1A10D3593FB248A9AC1D11DFF116472E |  | R22 | Non-TXV |  | 4.286% | 0.82 | 34.59% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95210-1940 |  | 2013-06-28 | 2013-06-28 10:37 | 2013-06-28 10:55 | OTHER - 3TCA-OH-1 | 99 | -8.2 | Yes | Yes | 13.5 | 15.5 | -2 | F1E59155EDBD4DD8BE2FA6F646211877 |  | R22 | Non-TXV |  | -8.283% | 1.0828 | 2.32% |  |  |  |  | Non-TXV |  |  | -8.283%
Oroville | CA | 95965-3128 |  | 2013-07-26 | 2013-07-26 08:51 | 2013-07-26 08:51 | COLEMAN - F042N080A | 150 | 0 | Yes | Yes | 24.7 | 19.9 | 4.9 | CC55BEAED6394E27ADA1161720007AF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-0305 |  | 2013-08-13 | 2013-08-13 15:02 | 2013-08-13 15:21 | OTHER - UNK | 93 | 6.3 | Yes | Yes | 19.8 | 18.8 | 1 | F3B30E7BA7394E29A8936D8B860B01CC |  | R22 | Non-TXV |  | 6.774% | 0.93226 | 13.02% | [5 empty] | Non-TXV | 6.774%
Stockton | CA | 95205-2591 |  | 2013-07-12 | 2013-07-12 09:06 | 2013-07-12 09:31 | GOODMAN - CRT60-1 | 139 | -13.1 | Yes | Yes | 21.3 | 20.3 | 1 | 541B897A8375458FAA67FC1FCADFD428 |  | R22 | Non-TXV |  | -9.424% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.424%
Livingston | CA | 95334-9659 |  | 2013-08-21 | 2013-08-21 17:23 | 2013-08-21 18:04 | OTHER - BRCS036B | 96 | 2.9 | Yes | Yes | 21.5 | 19.5 | 2 | 22022307F05D4075B6176F52CE9406B2 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Fresno | CA | 93710-6333 |  | 2013-06-28 | 2013-06-28 11:02 | 2013-06-28 11:04 | CARRIER - 48SDN036060311 | 130 | 4.3 | Yes | Yes | 21.4 | 18.8 | 2.6 | 1529EFE9F52C414D943716C08EAEF5B1 |  | R22 | Non-TXV |  | 3.308% | 0.96692 | 6.357% | [5 empty] | Non-TXV | 3.308%
Fresno | CA | 93720-2453 |  | 2013-08-29 | 2013-08-29 20:45 | 2013-08-29 20:48 | OTHER - 591ANX024-A | 54 | 2.1 | Yes | Yes | 18.7 | 19.9 | -1.2 | 9519C877B26E466693A5A72733C3E238 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Fresno | CA | 93711-0894 |  | 2013-07-19 | 2013-07-19 13:13 | 2013-07-19 13:16 | LENNOX - HS22411V2P | 129 | 23.3 | Yes | Yes | 20.7 | 20.6 | 0.1 | 39B10D844FF544BE9692DB82409D8E72 |  | R22 | Non-TXV |  | 18.06% | 0.81938 | 34.71% | [5 empty] | Non-TXV | 18.06%
Parlier | CA | 93648-9628 |  | 2013-09-03 | 2013-09-03 12:06 | 2013-09-03 12:49 | RUUD - UAMA-024JAZ | 85 | 3 | Yes | Yes | 16.5 | 19.5 | -3 | F19D3BEC80454BD5B2B27FE6F60409B5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Yuba City | CA | 95991-8223 |  | 2013-07-15 | 2013-07-15 11:56 | 2013-07-15 12:17 | DAY & NIGHT - AC1CNX036000ABAA | 120 | 5.2 | Yes | Yes | 21 | 21 | 0 | 066240E566124BD68849ABD9E38ECE42 |  | R22 | TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | TXV | 4.333%
Parlier | CA | 93648-9625 |  | 2013-08-14 | 2013-08-14 14:27 | 2013-08-14 15:04 | RHEEM - N/A | 60 | 3.1 | Yes | Yes | 18.5 | 20.9 | -2.4 | C5FBE398F34E42B6B7ADCBE8A1107F1D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Ione | CA | 95640-9777 |  | 2013-08-23 | 2013-08-23 10:34 | 2013-08-23 10:52 | CARRIER - 584BNW0360B0AABF | 64 | -5.3 | Yes | Yes | 18.9 | 21 | -2.1 | 5B2B8884B8C643DFA335D4D18E21EBAB |  | R22 | Non-TXV |  | -8.281% | 1.0828 | 2.319% |  |  |  |  | Non-TXV |  |  | -8.281%
Avery | CA | 95224-0000 |  | 2013-09-04 | 2013-09-04 13:39 | 2013-09-04 13:56 | PAYNE - PA13NR06000AAA | 161 | -11.4 | Yes | Yes | 21 | 16.8 | 4.2 | 2D60B9ED79A44411BF5547A9065F665A |  | R22 | Non-TXV |  | -7.081% | 1.0708 | 1.983% |  |  |  |  | Non-TXV |  |  | -7.081%
Merced | CA | 95348-4360 |  | 2013-07-10 | 2013-07-10 13:23 | 2013-07-10 13:28 | RHEEM - RRKA-024JAS | 51 | 2.8 | Yes | Yes | 17.8 | 19.7 | -1.9 | F903FC57EB9C4316A13AE3998A213500 |  | R22 | Non-TXV |  | 5.49% | 0.9451 | 10.55% | [5 empty] | Non-TXV | 5.49%
Stockton | CA | 95210-1641 |  | 2013-06-28 | 2013-06-28 09:59 | 2013-06-28 10:19 | TRANE - YCC036F1MOBJ | 83 | -4.9 | Yes | Yes | 21.6 | 15.6 | 6 | 17D6F282EF784B72BFB61628E2F972B5 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Madera | CA | 93636-8567 |  | 2013-06-28 | 2013-06-28 17:25 | 2013-06-28 17:49 | YORK - UNK | 87 | 8.1 | Yes | Yes | 18.4 | 19.9 | -1.5 | 185604E889204F18AC71708771CB538E |  | R22 | Non-TXV |  | 9.31% | 0.9069 | 17.89% | [5 empty] | Non-TXV | 9.31%
Yuba City | CA | 95993-5133 |  | 2013-07-16 | 2013-07-16 08:06 | 2013-07-16 08:28 | TRANE - TTL048C100A0 | 160 | 5.8 | Yes | Yes | 24 | 19.3 | 4.7 | 386FCA53ACAF42149D4D476AC70F7A40 |  | R22 | TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | TXV | 3.625%
Fresno | CA | 93701-0000 |  | 2013-07-12 | 2013-07-12 11:31 | 2013-07-12 11:33 | OTHER - DBYP-F024N045A | 100 | 4.2 | Yes | Yes | 16.5 | 18.8 | -2.3 | 6C3205A666674460A7AF96F56E9CA213 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Stockton | CA | 95210-2502 |  | 2013-07-03 | 2013-07-03 12:23 | 2013-07-03 12:46 | DAY & NIGHT - 24/60YAC-108C | 58 | 15.1 | Yes | Yes | 21.6 | 18.1 | 3.5 | B245BCF7662445B6B91905C44DBDB2ED |  | R22 | Non-TXV |  | 26.03% | 0.73966 | 50.03% | [5 empty] | Non-TXV | 26.03%
Merced | CA | 95340-5843 |  | 2013-07-02 | 2013-07-02 13:14 | 2013-07-02 13:16 | GOODMAN - GPG13300451AB | 77 | 7.9 | Yes | Yes | 25 | 21.3 | 3.7 | E858BE9D813D49968806318A0804D1A0 |  | R22 | Non-TXV |  | 10.26% | 0.8974 | 19.72% | [5 empty] | Non-TXV | 10.26%
Kingsburg | CA | 93631-1045 |  | 2013-08-01 | 2013-08-01 14:11 | 2013-08-01 14:46 | RUUD - N/A | 60 | -3.5 | Yes | Yes | 16.5 | 19.1 | -2.6 | 54643B4670134F809395C8B746CDA627 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95207-9220 |  | 2013-07-30 | 2013-07-30 15:55 | 2013-07-30 16:31 | CARRIER - 38EN024300 | 56 | 4.8 | Yes | Yes | 20.1 | 18.8 | 1.3 | B7F66F2BAE054D3F9C3F0E231026D149 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Parlier | CA | 93648-9664 |  | 2013-07-30 | 2013-07-30 10:22 | 2013-07-30 11:14 | LENNOX - 10ACC-042-230-04 | 81 | 4.6 | Yes | Yes | 17.3 | 19.9 | -2.6 | ACF0234F0050444FA06561DECB53A0CD |  | R22 | Non-TXV |  | 5.679% | 0.94321 | 10.91% | [5 empty] | Non-TXV | 5.679%
Parlier | CA | 93648-9631 |  | 2013-09-03 | 2013-09-03 11:23 | 2013-09-03 12:48 | RUUD - N/A | 60 | 5.2 | Yes | Yes | 16 | 18.7 | -2.7 | 77FC49575CFB4416AAAE6AA5987464B4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | Non-TXV | 8.667%
Stockton | CA | 95210-1401 |  | 2013-07-01 | 2013-07-01 08:28 | 2013-07-01 08:48 | DAY & NIGHT - 585B024050YACR | 51 | 1.8 | Yes | Yes | 18.8 | 16.4 | 2.5 | C07A35214DEF4EF38F8D8B58458A0253 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Placerville | CA | 95667-4560 |  | 2013-07-10 | 2013-07-10 13:13 | 2013-07-10 13:32 | COLEMAN - UNK | 64 | 8 | Yes | Yes | 23 | 21.4 | 1.6 | 59EF35C602B149A4B18DB6C5AF6FEAB9 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Fresno | CA | 93726-2719 |  | 2013-07-26 | 2013-07-26 15:25 | 2013-07-26 15:26 | RUUD - UNK | 61 | 13.7 | Yes | Yes | 24.9 | 23 | 1.9 | 76E5BBA9D1CB4BF0B01680D614E25A56 |  | R22 | Non-TXV |  | 22.46% | 0.77541 | 43.16% | [5 empty] | Non-TXV | 22.46%
Atascadero | CA | 93422-6813 |  | 2013-08-07 | 2013-08-07 12:28 | 2013-08-07 12:47 | RHEEM - UNK | 49 | 1.9 | Yes | Yes | 20 | 17.5 | 2.5 | 4B06A1A93D324BA981254418CFEA0A9D |  | R22 | Non-TXV |  | 3.878% | 0.96122 | 7.452% | [5 empty] | Non-TXV | 3.878%
Chico | CA | 95928-9145 |  | 2013-07-16 | 2013-07-16 14:58 | 2013-07-16 22:18 | PAYNE - PYZPNBO36060AAAA | 82 | 6.6 | Yes | Yes | 22.6 | 21.5 | 1.1 | CC87B1126ADE4ADF8CC71367B275DEE2 |  | R22 | Non-TXV |  | 8.049% | 0.91951 | 15.47% | [5 empty] | Non-TXV | 8.049%
Chico | CA | 95928-9145 |  | 2013-07-16 | 2013-07-16 22:20 | 2013-07-16 22:39 | CARRIER - 48GS-024040301 | 53 | 2.5 | Yes | Yes | 19.6 | 20.9 | -1.3 | 22ABD5AC2A2C433BB8E2E4A28BA24B49 |  | R22 | Non-TXV |  | 4.717% | 0.95283 | 9.065% | [5 empty] | Non-TXV | 4.717%
Chico | CA | 95928-9145 |  | 2013-07-16 | 2013-07-16 16:43 | 2013-07-16 16:43 | PAYNE - PY2PNB036060AAAA | 82 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 13FD928290004D2E8608866F6FA634A6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3723 |  | 2013-07-09 | 2013-07-09 12:27 | 2013-07-09 12:46 | GOODMAN - PGAD30D1K5 | 78 | 4.9 | Yes | Yes | 22.2 | 20.1 | 2.1 | 842AC6547F514737BEDF99BAB53277F7 |  | R22 | Non-TXV |  | 6.282% | 0.93718 | 12.07% | [5 empty] | Non-TXV | 6.282%
Chico | CA | 95928-6933 |  | 2013-07-08 | 2013-07-08 19:07 | 2013-07-08 19:27 | AMANA - YCY060G1M0AC | 151 | 5.9 | Yes | Yes | 23.8 | 21.5 | 2.3 | 271A9A110FE844AD973F1BDB369BD187 |  | R22 | Non-TXV |  | 3.907% | 0.96093 | 7.509% | [5 empty] | Non-TXV | 3.907%
Chico | CA | 95928-4848 |  | 2013-08-27 | 2013-08-27 10:44 | 2013-08-27 11:04 | PAYNE - PY1PNB030040AAAA | 59 | -3.5 | Yes | Yes | 23.6 | 19.9 | 3.7 | B14D46FCDE7E4BF392EB238C8A5CC7DF |  | R22 | Non-TXV |  | -5.932% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.932%
Manteca | CA | 95337-6602 |  | 2013-07-17 | 2013-07-17 08:34 | 2013-07-17 09:12 | GE - BTR748A100A1 | 154 | 4.6 | Yes | Yes | 18.8 | 19.1 | -0.3 | A8D67195DE1049988A703A902D6C9548 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Ione | CA | 95640-9629 |  | 2013-08-02 | 2013-08-02 10:21 | 2013-08-02 10:21 | OTHER - BRCS0481BD | 117 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | CCE8521309FD4D6CB66A0BF0B175088E |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2723 |  | 2013-09-20 | 2013-09-20 10:23 | 2013-09-20 10:41 | GOODMAN - LT36-1B | 140 | -25 | Yes | Yes | 22.8 | 19 | 3.8 | 10112710C9364E65B578F1A4BBEDB0DC |  | R22 | TXV |  | -17.86% | 1.1786 | 5.001% |  |  |  |  | TXV |  |  | -17.86%
Oroville | CA | 95966-7716 |  | 2013-08-02 | 2013-08-02 10:39 | 2013-08-02 18:50 | OTHER - NA | 85 | 9.5 | Yes | Yes | 17.9 | 20.1 | -2.2 | EC2CF5594CFD486B8AA2FD13E173CE0F |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Parlier | CA | 93648-9626 |  | 2013-08-14 | 2013-08-14 15:08 | 2013-08-14 16:38 | OTHER - TZAA-330-2A | 98 | 2.9 | Yes | Yes | 21.3 | 17.9 | 3.4 | 8ACC98D3CE224A688A49C981192E6F53 |  | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.687% | [5 empty] | Non-TXV | 2.959%
Fresno | CA | 93711-1348 |  | 2013-08-22 | 2013-08-22 10:25 | 2013-08-22 10:26 | TAPPAN - 7777UNK | 100 | 4.8 | Yes | Yes | 19.7 | 18.7 | 1 | 0409FBB8842949ACA0871BA7BADDEEA4 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Paradise | CA | 95969-5921 |  | 2013-06-29 | 2013-06-29 19:39 | 2013-06-29 19:39 | LENNOX - 13GCSXA-42-110-230-1A | 181 | 0 | Yes | Yes | 23.4 | 22.1 | 1.3 | ED6EDBC89E9E4D24AE2C2E2542F61315 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-2009 |  | 2013-07-12 | 2013-07-12 17:53 | 2013-07-12 18:12 | LENNOX - GCS20R-411-100-3P | 70 | 4 | Yes | Yes | 17.5 | 18.8 | -1.3 | 50B854A78B4D4FB499CF2BC21D613E1F |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Merced | CA | 95348-1338 |  | 2013-07-11 | 2013-07-11 14:08 | 2013-07-11 14:14 | LENNOX - 10ACB30 | 64 | 9.1 | Yes | Yes | 21.2 | 21.3 | -0.1 | 5222BA8ECF954FCD8C689A695F88CF41 |  | R22 | Non-TXV |  | 14.22% | 0.85781 | 27.33% | [5 empty] | Non-TXV | 14.22%
Fresno | CA | 93704-1749 |  | 2013-06-26 | 2013-06-26 12:41 | 2013-06-26 12:44 | GOODMAN - GPG13300701BB | 77 | 3.5 | Yes | Yes | 14.5 | 17.4 | -2.9 | 05FE9BE2A9E844A087899E21CDE4E271 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Placerville | CA | 95667-9070 |  | 2013-10-18 | 2013-10-18 12:56 | 2013-10-18 13:15 | BRYANT - 561CJ030-D | 65 | 1.9 | Yes | Yes | 23.5 | 21.2 | 2.4 | 239660C6EEA540DE94B59032FBEA3CB2 |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Placerville | CA | 95667-9070 |  | 2013-10-18 | 2013-10-18 13:08 | 2013-10-18 13:29 | BRYANT - 561CJ03000ADAA | 65 | 2 | Yes | Yes | 26 | 20.9 | 5.1 | 2DBAA81995024C718C23FD9D063DBE5D |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Placerville | CA | 95667-9070 |  | 2013-10-18 | 2013-10-18 13:25 | 2013-10-18 13:54 | BRYANT - 561CJ024000ADAA | 54 | 2.2 | Yes | Yes | 26 | 20.9 | 5.1 | 036CC414CD7243228F361A49CD7F9A12 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Placerville | CA | 95667-9070 |  | 2013-10-18 | 2013-10-18 13:36 | 2013-10-18 13:55 | BRYANT - 561CJX030000ADAA | 65 | 3.9 | Yes | Yes | 24 | 20.9 | 3.1 | 13F4D6D9663E44128FD62BAD32E681C0 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Stockton | CA | 95210-3333 |  | 2013-07-31 | 2013-07-31 13:32 | 2013-07-31 13:51 | CARRIER - 38EB048350 | 115 | 3.8 | Yes | Yes | 24.2 | 21.6 | 2.6 | 4E147446CB4D43AF9513532A7FCA1D46 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.35% | [5 empty] | Non-TXV | 3.304%
Stockton | CA | 95212-2725 |  | 2013-06-26 | 2013-06-26 15:47 | 2013-06-26 16:06 | BRYANT - 563CN030 | 98 | 3 | Yes | Yes | 20.3 | 14.4 | 5.9 | 500B05DF4AD04568B4D678F85AC0470F |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Fresno | CA | 93722-1151 |  | 2013-07-19 | 2013-07-19 12:25 | 2013-07-19 12:26 | YORK - H2DB024S06B | 58 | 10 | Yes | Yes | 24.1 | 22.4 | 1.7 | 29C8CAA43EAF43078BEEAA59CB283448 |  | R22 | Non-TXV |  | 17.24% | 0.82759 | 33.13% | [5 empty] | Non-TXV | 17.24%
Fresno | CA | 93706-2854 |  | 2013-07-16 | 2013-07-16 13:16 | 2013-07-16 13:19 | LENNOX - 12GCS042-100-3PA | 133 | 4.1 | Yes | Yes | 19.6 | 22.1 | -2.5 | DEC9948D7375476888E860B1CDB491A2 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.924% | [5 empty] | Non-TXV | 3.083%
Merced | CA | 95341-5801 |  | 2013-07-02 | 2013-07-02 14:38 | 2013-07-02 14:40 | CARRIER - 48GS-042060301 | 100 | 3.1 | Yes | Yes | 17.4 | 17.7 | -0.3 | 51AA653D672C4B5EB7453D23657A5E60 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Arbuckle | CA | 95912-0000 |  | 2013-08-08 | 2013-08-08 10:18 | 2013-08-08 10:42 | LENNOX - HS25-461-1P | 133 | 4.9 | Yes | Yes | 15.5 | 18.2 | -2.7 | 7ACE78B290024482AF3FE2C03A8FCFF9 |  | R22 | TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | TXV | 3.684%
Parlier | CA | 93648-9624 |  | 2013-07-30 | 2013-07-30 11:16 | 2013-07-30 11:35 | RUUD - N/A | 60 | 2.2 | Yes | Yes | 18.7 | 21 | -2.3 | 30560DF63D3A46BC9CB667B7BDB33D82 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Madera | CA | 93637-5675 |  | 2013-08-05 | 2013-08-05 14:17 | 2013-08-05 14:18 | CARRIER - 48GS030040301 | 55 | 8.9 | Yes | Yes | 23.7 | 22.5 | 1.2 | 4A0DEEF6B23D4D87993204F3FC7D4590 |  | R22 | Non-TXV |  | 16.18% | 0.83818 | 31.1% | [5 empty] | Non-TXV | 16.18%
Orosi | CA | 93647-2137 |  | 2013-07-29 | 2013-07-29 12:59 | 2013-07-29 13:33 | GOODMAN - GSC130361DF | 120 | 3.5 | Yes | Yes | 18.1 | 20.9 | -2.8 | F660D860247F4ABFB5253BDED71EBA08 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Stockton | CA | 95206-6272 |  | 2013-07-10 | 2013-07-10 14:56 | 2013-07-10 15:17 | CARRIER - 38CKC048300 | 102 | 7.3 | Yes | Yes | 25.8 | 19.9 | 5.9 | 6C14D7361CCB425FA7FE2B4CBE9B3846 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.157% | 0.92843 | 13.75% | [5 empty] | Non-TXV | 7.157%
Stockton | CA | 95210-1873 |  | 2013-06-27 | 2013-06-27 13:19 | 2013-06-27 13:40 | RHEEM - RAKA-037JAZ | 79 | 2.7 | Yes | Yes | 16.1 | 17.2 | -1.1 | 0B47099E76CB4193919F9108575086EF |  | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Madera | CA | 93637-5677 |  | 2013-07-10 | 2013-07-10 14:09 | 2013-07-10 14:52 | CARRIER - 4895E06407 | 78 | -4.6 | Yes | Yes | 19.5 | 22 | -2.5 | E01FE51DF1D24255AA05541451D8BC5A |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Stockton | CA | 95210-4440 |  | 2013-07-10 | 2013-07-10 13:34 | 2013-07-10 13:53 | PAYNE - 591ANX036000AAAA | 85 | -5 | Yes | Yes | 28.2 | 22.3 | 5.9 | 9AB287C4028A4BF882C00A202D5642B9 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Tracy | CA | 95376-5293 |  | 2013-07-17 | 2013-07-17 11:15 | 2013-07-17 11:38 | BRYANT - 563C036-B | 122 | -8.6 | Yes | Yes | 18.8 | 21 | -2.2 | D0ABAFE1651C4638A2CF776D7775FADB |  | R22 | Non-TXV |  | -7.049% | 1.0705 | 1.974% |  |  |  |  | Non-TXV |  |  | -7.049%
Stockton | CA | 95219-7168 |  | 2013-08-06 | 2013-08-06 12:54 | 2013-08-06 13:12 | WEATHER KING - 12AJB60A01 | 76 | 2.8 | Yes | Yes | 22.4 | 19.6 | 2.8 | F0F74E6C52094E449EF783A2DF02C3B4 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Cool | CA | 95614-2535 |  | 2013-09-20 | 2013-09-20 10:55 | 2013-09-20 10:55 | CARRIER - 48GS-036090301-- | 61 | 0 | Yes | Yes | 27.2 | 22.2 | 5 | D17899D1BE8147A094340617DE102FDA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-6190 |  | 2013-08-27 | 2013-08-27 15:24 | 2013-08-27 15:43 | RUUD - UAFD-024JAS | 67 | 2 | Yes | Yes | 15.9 | 18.3 | -2.4 | D94DEDC897E24E9EA9A1530A4A52BC6B |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Chico | CA | 95926-4491 |  | 2013-08-23 | 2013-08-23 15:31 | 2013-08-23 18:24 | OTHER - NA | 70 | 4.6 | Yes | Yes | 16.2 | 19.2 | -3 | E1D8755B4ACC4F5FBB9F194E6CDA4CA1 |  | R22 | Non-TXV |  | 6.571% | 0.93429 | 12.63% | [5 empty] | Non-TXV | 6.571%
Merced | CA | 95340-3572 |  | 2013-06-28 | 2013-06-28 15:33 | 2013-06-28 15:36 | BDP - 585A036080YAC | 60 | 6.5 | Yes | Yes | 27 | 21 | 6 | AD404C8273B340B0A29340CE1FDE4FA6 |  | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Chico | CA | 95973-9120 |  | 2013-08-20 | 2013-08-20 11:10 | 2013-08-20 20:22 | TRANE - YCC024F1LOBH | 85 | 3.6 | Yes | Yes | 17.3 | 19.9 | -2.6 | E20A618D882648139675233105459E7B |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Stockton | CA | 95207-3140 |  | 2013-06-27 | 2013-06-27 11:15 | 2013-06-27 11:36 | RHEEM - RRKA-AO30JK06X | 54 | -5.1 | Yes | Yes | 21.4 | 17.2 | 4.2 | 99B94A31F0794C3D99AB71000BDCC904 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Chico | CA | 95973-7667 |  | 2013-08-07 | 2013-08-07 12:04 | 2013-08-07 13:10 | PAYNE - 561AJ030-A | 79 | 8.8 | Yes | Yes | 20.9 | 21.7 | -0.8 | E26093D4873C449BB4148722771AE108 |  | R22 | Non-TXV |  | 11.14% | 0.88861 | 21.41% | [5 empty] | Non-TXV | 11.14%
Stockton | CA | 95205-6610 |  | 2013-07-15 | 2013-07-15 14:28 | 2013-07-15 14:48 | BRYANT - 582ANW030060AAAD | 55 | 2.6 | Yes | Yes | 12 | 14.3 | -2.3 | 489637C107204ADB9344188938791734 |  | R22 | Non-TXV |  | 4.727% | 0.95273 | 9.085% | [5 empty] | Non-TXV | 4.727%
Auburn | CA | 95603-9443 |  | 2013-06-28 | 2013-06-28 15:08 | 2013-06-28 15:08 | RHEEM - RRKA-A048JK10X | 78 | 0 | Yes | Yes | 15.3 | 18.2 | -2.9 | B16F27E7553B4FC59872F901AB470333 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-4022 |  | 2013-08-09 | 2013-08-09 09:59 | 2013-08-09 13:49 | WESTINGHOUSE - F53BD-048K | 143 | 13.7 | Yes | Yes | 18.1 | 20.4 | -2.3 | DA80B1BA71BB4F7286BC3C487A438678 |  | R22 | Non-TXV |  | 9.58% | 0.9042 | 18.41% | [5 empty] | Non-TXV | 9.58%
Los Banos | CA | 93635-0000 |  | 2013-07-02 | 2013-07-02 09:07 | 2013-07-02 09:20 | NORDYNE - JS3BA030KA | 68 | 12.6 | Yes | Yes | 24.2 | 19.5 | 4.7 | 5D328A3D7DA04B86A388007BABE8E0E4 |  | R22 | Non-TXV |  | 18.53% | 0.81471 | 35.61% | [5 empty] | Non-TXV | 18.53%
Stockton | CA | 95204-3129 |  | 2013-07-02 | 2013-07-02 11:42 | 2013-07-02 12:01 | YORK - BRCS0361BD | 63 | 10.5 | Yes | Yes | 16.6 | 17.9 | -1.3 | C900DF49AF7C4A8699846C4582354E1C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Madera | CA | 93637-5678 |  | 2013-07-24 | 2013-07-24 22:46 | 2013-07-24 22:46 | CARRIER - 48G5-03004001 | 55 | 0 | Yes | Yes | 18.4 | 21.2 | -2.8 | 4752248664F34226ABF7FB682D06C7E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3712 |  | 2013-07-10 | 2013-07-10 09:30 | 2013-07-10 09:33 | BRYANT - 556AN042-F | 210 | 14.1 | Yes | Yes | 17.5 | 19.9 | -2.4 | C89E1C26EE7B43D6822914E5AD2BAA00 |  | R410A | Non-TXV |  | 6.714% | 0.93286 | 12.9% | [5 empty] | Non-TXV | 6.714%
Corning | CA | 96021-2740 |  | 2013-08-13 | 2013-08-13 09:59 | 2013-08-13 10:31 | WEATHER KING - 12AJB36A01 | 117 | 7.1 | Yes | Yes | 21.1 | 21 | 0.1 | 4A3041DC83394F4CA14E5521A04AB4C8 |  | R22 | Non-TXV |  | 6.068% | 0.93932 | 11.66% | [5 empty] | Non-TXV | 6.068%
Madera | CA | 93638-1320 |  | 2013-07-16 | 2013-07-16 11:41 | 2013-07-16 11:41 | GOODMAN - CLLJ48-1C | 85 | 0 | Yes | Yes | 17.4 | 19.9 | -2.5 | 08B172C24C7A4082A686815AF6AFBC2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-3981 |  | 2013-07-28 | 2013-07-28 00:46 | 2013-07-28 01:12 | YORK - H2R036S068 | 106 | 3.4 | Yes | Yes | 18.9 | 20.1 | -1.2 | 5235D9A01A5D4005B12F81FCD6DEABA1 |  | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Madera | CA | 93637-5666 |  | 2013-07-11 | 2013-07-11 02:07 | 2013-07-11 02:27 | ALLEGIANCE - 561CJ036000ADAAAA | 104 | 3.2 | Yes | Yes | 18.8 | 21.5 | -2.7 | DA9F041F1A3440E1B89218EF48B492CF |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95210-5695 |  | 2013-07-15 | 2013-07-15 12:50 | 2013-07-15 13:23 | BDP - 598AN036-B | 85 | 8.2 | Yes | Yes | 25.5 | 20.2 | 5.3 | 9087CBE535E9428E9C0CE9D6CEAE7646 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Madera | CA | 93638-0553 |  | 2013-07-12 | 2013-07-12 13:13 | 2013-07-17 03:08 | YORK - B1HPO36A06A | 132 | 4.7 | Yes | Yes | 18 | 20.4 | -2.4 | CAC597A42E2E403F8BF23F87FC0191CD |  | R22 | Non-TXV |  | 3.561% | 0.96439 | 6.843% | [5 empty] | Non-TXV | 3.561%
Merced | CA | 95340-2409 |  | 2013-06-28 | 2013-06-28 13:06 | 2013-06-28 13:23 | PAYNE - PA13NR042E | 150 | 7.8 | Yes | Yes | 28.6 | 23.1 | 5.5 | 46A13F0BAC3145CF889206304F85ABF0 |  | R22 | TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | TXV | 5.2%
Riverbank | CA | 95367-2280 |  | 2013-07-12 | 2013-07-12 13:16 | 2013-07-12 13:41 | DAY & NIGHT - 585B024050AACR` | 51 | 2.1 | Yes | Yes | 15.5 | 18.2 | -2.7 | 3C21C78784DE4877B7F3EA86EB1B1CFB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Los Banos | CA | 93635-3078 |  | 2013-08-05 | 2013-08-05 10:59 | 2013-08-05 11:07 | YORK - GS3BA036KA | 69 | 4 | Yes | Yes | 17 | 19.9 | -2.9 | BEB3A55E492C4BFFBEF6200EFBA23C21 |  | R22 | Non-TXV |  | 5.797% | 0.94203 | 11.14% | [5 empty] | Non-TXV | 5.797%
Marysville | CA | 95901-8295 |  | 2013-07-01 | 2013-07-01 08:37 | 2013-07-01 08:55 | CARRIER - 38CKC030340 | 75 | 10.6 | Yes | Yes | 16 | 18.5 | -2.5 | A8507A8E312447CEBA020B89193A2F3B |  | R22 | Non-TXV |  | 14.13% | 0.85867 | 27.16% | [5 empty] | Non-TXV | 14.13%
Merced | CA | 95340-0000 |  | 2013-07-12 | 2013-07-12 14:15 | 2013-07-12 14:17 | BRYANT - 582ANW042060NAAG | 100 | 4.2 | Yes | Yes | 26.1 | 21.2 | 4.9 | B5ED87ED055747E1842D267519150C51 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Stockton | CA | 95205-4724 |  | 2013-07-15 | 2013-07-15 08:48 | 2013-07-15 09:08 | WEATHER KING - UNK | 72 | 3 | Yes | Yes | 23 | 17.6 | 5.4 | EA11EEE1A8A144568B167BD8E4CD572F |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Merced | CA | 95348-3555 |  | 2013-07-03 | 2013-07-03 12:43 | 2013-07-03 12:58 | OTHER - BRCS0361BD | 63 | 11.3 | Yes | Yes | 21.4 | 21.9 | -0.5 | 1416EF2C867E42FFBE2A5A53CA15D765 |  | R22 | Non-TXV |  | 17.94% | 0.82063 | 34.47% | [5 empty] | Non-TXV | 17.94%
Lathrop | CA | 95330-8900 |  | 2013-07-24 | 2013-07-24 13:50 | 2013-07-24 14:10 | CARRIER - 38CKB030320 | 74 | -5.2 | Yes | Yes | 23 | 19.3 | 3.7 | 919D3BCEA08E4316AFCBBFF8754BC186 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.027% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.027%
Chico | CA | 95926-2318 |  | 2013-07-12 | 2013-07-12 19:14 | 2013-07-12 19:31 | OTHER - 561AJ030=A | 65 | 3.1 | Yes | Yes | 20.6 | 20.7 | -0.1 | 3B7C5863BF6F49529086DAF3ABAE2D66 |  | R22 | Non-TXV |  | 4.769% | 0.95231 | 9.165% | [5 empty] | Non-TXV | 4.769%
Stockton | CA | 95206-5400 |  | 2013-06-26 | 2013-06-26 13:19 | 2013-06-26 13:42 | DAY & NIGHT - 591AN048-C | 128 | 5.3 | Yes | Yes | 17.7 | 18.5 | -0.8 | 453614CBF3DF4AC980AC76620986CDDA |  | R22 | Non-TXV |  | 4.141% | 0.95859 | 7.957% | [5 empty] | Non-TXV | 4.141%
Madera | CA | 93638-5511 |  | 2013-07-22 | 2013-07-22 15:36 | 2013-07-22 15:36 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | FD1FC71AA7FA43D292784D1704EF35B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-9633 |  | 2013-07-29 | 2013-07-29 09:01 | 2013-07-29 09:24 | BRYANT - 563CN042-D | 104 | 3.2 | Yes | Yes | 21.9 | 19.1 | 2.8 | F5EC42719B624CAAA692EA15EF64890D |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Madera | CA | 93637-4321 |  | 2013-07-08 | 2013-07-08 14:03 | 2013-07-08 14:36 | BRYANT - 547BNW04209NG | 163 | 4.9 | Yes | Yes | 21.1 | 21.5 | -0.4 | C72B025EEF464445B382C976D1CB3895 |  | R410A | Non-TXV |  | 3.006% | 0.96994 | 5.777% | [5 empty] | Non-TXV | 3.006%
Marysville | CA | 95901-4286 |  | 2013-08-20 | 2013-08-20 17:15 | 2013-08-20 17:15 | DAY & NIGHT - 5540JJ018 | 83 | 0 | Yes | Yes | 18 | 17.2 | 0.8 | A2C69E8233714B03AC0A994BCA324BC0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6049 |  | 2013-07-02 | 2013-07-02 12:10 | 2013-07-02 12:41 | GOODMAN - K60-1C | 85 | 6.5 | Yes | Yes | 21.1 | 20.5 | 0.6 | 2222488AAD2A4C348C3992AF7AE3D028 |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Chico | CA | 95973-9523 |  | 2013-08-20 | 2013-08-20 11:12 | 2013-08-20 12:36 | TRANE - 2TTR1024A1000AA | 62 | 2.3 | Yes | Yes | 16.7 | 17.8 | -1.1 | 2B153A8301C8458C98779A7989C09770 |  | R22 | Non-TXV |  | 3.71% | 0.9629 | 7.129% | [5 empty] | Non-TXV | 3.71%
Nevada City | CA | 95959-9697 |  | 2013-09-12 | 2013-09-12 09:47 | 2013-09-12 09:47 | CARRIER - 38TXA036320 | 110 | 0 | Yes | Yes | 25.9 | 21.4 | 4.5 | B5FA0DAC7DE74B08ACEBFB7F169ED809 |  | R410A | TXV |  | 0% | 1 | 0%
Pine Grove | CA | 95665-9486 |  | 2013-08-09 | 2013-08-09 14:56 | 2013-08-09 14:56 | DAY & NIGHT - 588ANW048100AEBG | 104 | 0 | Yes | Yes | 18.9 | 18.8 | 0.1 | 727B45CC9B0E4CF3AEC665739F2A8D02 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-6177 |  | 2013-07-10 | 2013-07-10 16:43 | 2013-07-11 00:24 | GOODMAN - PBG048075-1B | 87 | 3.4 | Yes | Yes | 18 | 19.8 | -1.8 | CF7B40148A9746888528CC27D03831E2 |  | R22 | Non-TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | Non-TXV | 3.908%
Madera | CA | 93638-1759 |  | 2013-07-15 | 2013-07-15 15:29 | 2013-07-15 21:25 | GOODMAN - UNK | 64 | -6 | Yes | Yes | 15.7 | 18.3 | -2.6 | 37E35B1F3F784476ACFD77FE2C4511FB |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Stockton | CA | 95205-6200 |  | 2013-07-15 | 2013-07-15 12:23 | 2013-07-15 12:42 | LENNOX - GCS10-261-50-1P | 62 | 7 | Yes | Yes | 22.6 | 20.4 | 2.2 | 4534325037454B0BBB22A496C36DDAC1 |  | R22 | TXV |  | 11.29% | 0.8871 | 21.7% | [5 empty] | TXV | 11.29%
Riverbank | CA | 95367-2754 |  | 2013-07-11 | 2013-07-11 15:20 | 2013-07-11 15:45 | DAY & NIGHT - 585GJW024040ABAE | 54 | 17.6 | Yes | Yes | 20.7 | 22.1 | -1.4 | 4737D50A108D4ED79C064BA6083F5307 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 32.59% | 0.67407 | 62.64% | [5 empty] | Non-TXV | 32.59%
Stockton | CA | 95209-5133 |  | 2013-07-16 | 2013-07-16 13:58 | 2013-07-16 14:19 | LENNOX - 14ACX-030-230-10 | 107 | 6.3 | Yes | Yes | 19.8 | 19.7 | 0.1 | 77AD31DB93B54C1EAF75A24576FBC60F |  | R22 | TXV |  | 5.888% | 0.94112 | 11.32% | [5 empty] | TXV | 5.888%
Pioneer | CA | 95666-9159 |  | 2013-08-13 | 2013-08-13 09:30 | 2013-08-13 09:53 | OTHER - FS3BA-048KA | 102 | 4.7 | Yes | Yes | 24 | 19.7 | 4.3 | 1CB168BCEE9A42CDB4B5AE6E86821D7B |  | R22 | TXV |  | 4.608% | 0.95392 | 8.855% | [5 empty] | TXV | 4.608%
Marysville | CA | 95901-0000 |  | 2013-08-08 | 2013-08-08 13:43 | 2013-08-08 14:19 | YORK - H2RD036S06B | 96 | 5 | Yes | Yes | 19 | 19.8 | -0.8 | FA4729CDFEF64A9B9F3CDA1AE500EE2E |  | R22 | TXV |  | 5.208% | 0.94792 | 10.01% | [5 empty] | TXV | 5.208%
Madera | CA | 93638-5512 |  | 2013-07-22 | 2013-07-22 14:46 | 2013-07-22 19:05 | YORK - D1NP0305606A | 73 | 2.4 | Yes | Yes | 18.9 | 20.4 | -1.5 | D29FC317CBEA4982B83161A094C9DCF9 |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Foresthill | CA | 95631-9605 |  | 2013-10-14 | 2013-10-14 14:33 | 2013-10-14 14:33 | PAYNE - PY3GNAA42090NA- | 98 | 0 | Yes | Yes | 26.7 | 20.9 | 5.8 | 165B2C53CEF54825A78BD602E564D1CF |  | R410A | TXV |  | 0% | 1 | 0%
Madera | CA | 93637-4251 |  | 2013-07-08 | 2013-07-08 20:41 | 2013-07-08 20:58 | CARRIER - 48VKNA360630TP | 149 | 6.4 | Yes | Yes | 13.5 | 13.4 | 0.1 | B2DF17290CAB450498E985468D08C55D |  | R22 | Non-TXV |  | 4.295% | 0.95705 | 8.255% | [5 empty] | Non-TXV | 4.295%
Stockton | CA | 95203-3608 |  | 2013-07-15 | 2013-07-15 12:40 | 2013-07-15 13:01 | YORK - D1NA024N05606C | 54 | -3.2 | Yes | Yes | 22.7 | 17.5 | 5.2 | 2EFA9C0552C8470F8CC4B7E0D7D600E9 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Manteca | CA | 95336-3842 |  | 2013-09-06 | 2013-09-06 08:53 | 2013-09-06 09:12 | ICP - HAC230AKC4 | 95 | 2.8 | Yes | Yes | 19.6 | 18.8 | 0.8 | 9C52D8D832EA434185E3790F6FA9A8AE |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Pollock Pines | CA | 95726-9580 |  | 2013-07-29 | 2013-07-29 10:38 | 2013-07-29 11:05 | DAY & NIGHT - UNK | 92 | 3 | Yes | Yes | 23 | 21.5 | 1.5 | 1EB087ADBB474F998ABC49F761F113E9 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Dos Palos | CA | 93620-2688 |  | 2013-07-08 | 2013-07-08 10:49 | 2013-07-08 10:54 | LENNOX - 7777UNK | 111 | 3.9 | Yes | Yes | 15.3 | 18.1 | -2.8 | 64841A1D5AE84C58AA386ACE2B1A73FE |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Madera | CA | 93638-0137 |  | 2013-08-06 | 2013-08-06 12:56 | 2013-08-06 13:11 | AMERICAN STANDARD - YCY48G1H0AC | 104 | 5.3 | Yes | Yes | 16 | 18.3 | -2.3 | 2E2DC41DDB2C4997BB35FD4D6FEAFAF3 |  | R22 | Non-TXV |  | 5.096% | 0.94904 | 9.794% | [5 empty] | Non-TXV | 5.096%
Grass Valley | CA | 95949-6727 |  | 2013-07-01 | 2013-07-01 09:45 | 2013-07-01 09:45 | BARD - 2H36-2 | 91 | 0 | Yes | Yes | 20.1 | 19.6 | 0.6 | 69EE20AC74F247F08A9B601E68139FB5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-4264 |  | 2013-07-01 | 2013-07-01 15:35 | 2013-07-21 13:00 | LENNOX - HS22-411U-2P | 134 | 5.8 | Yes | Yes | 18.9 | 20.4 | -1.5 | 47599976216A4EF693B609AB1FF4BA51 |  | R22 | Non-TXV |  | 4.328% | 0.95672 | 8.318% | [5 empty] | Non-TXV | 4.328%
Oroville | CA | 95966-3926 |  | 2013-08-06 | 2013-08-06 13:06 | 2013-08-06 14:14 | GE - NA | 65 | 2 | Yes | Yes | 17.8 | 20.4 | -2.6 | B7F10BC1B96A49EC9A8C59DB0F57DD47 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Magalia | CA | 95954-9539 |  | 2013-08-03 | 2013-08-03 13:05 | 2013-08-03 13:38 | PAYNE - PH10JA042-C | 115 | 6.5 | Yes | Yes | 18 | 19.8 | -1.8 | 22252668E1E544439321E5143D79FEA8 |  | R22 | TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | TXV | 5.652%
Tracy | CA | 95377-8731 |  | 2013-07-23 | 2013-07-23 16:59 | 2013-07-23 17:20 | CARRIER - 38CKC060300 | 153 | 4.7 | Yes | Yes | 22.1 | 20.4 | 1.7 | 7C089AA8FCB045ADB7BCDC52819947BD |  | R22 | Non-TXV |  | 3.072% | 0.96928 | 5.904% | [5 empty] | Non-TXV | 3.072%
Grass Valley | CA | 95945-5173 |  | 2013-08-23 | 2013-08-23 14:02 | 2013-08-23 14:24 | CARRIER - PA13NA042-B | 99 | -11.1 | Yes | Yes | 21.7 | 19.9 | 1.8 | 745DF5AD17284BA39C1EAD337EF6C784 |  | R410A | TXV |  | -11.21% | 1.1121 | 3.14% |  |  |  |  | TXV |  |  | -11.21%
Magalia | CA | 95954-9312 |  | 2013-07-18 | 2013-07-18 11:17 | 2013-07-18 11:59 | INTERTHERM - ACSD-042B-01 | 68 | -5.6 | Yes | Yes | 23 | 21.5 | 1.5 | FEE4EC8F4C904598BDB341C461ECE674 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Grass Valley | CA | 95945-4572 |  | 2013-06-29 | 2013-06-29 09:53 | 2013-06-29 09:53 | BRYANT - 563CN042-C | 108 | 0 | Yes | Yes | 21 | 19.3 | 1.7 | 4519A51FA98C42ADB37A7EF35B636C13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-3222 |  | 2013-09-27 | 2013-09-27 08:38 | 2013-09-27 08:38 | LENNOX - 13ACD-060-230-01 | 214 | 0 | Yes | Yes | 24.2 | 20.8 | 3.4 | 752AECCA74774AD9983E627F9742288A |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5237 |  | 2013-07-10 | 2013-07-10 09:18 | 2013-07-10 09:35 | BRYANT - 563CN060 | 200 | 13.2 | Yes | Yes | 22.6 | 19.6 | 3.1 | 60FB6FCB999D48CE9EAE472EE3A27D6A |  | R22 | TXV |  | 6.6% | 0.934 | 12.68% | [5 empty] | TXV | 6.6%
Manteca | CA | 95337-8224 |  | 2013-07-16 | 2013-07-16 10:52 | 2013-07-16 11:11 | BRYANT - 51CJX060-A | 153 | 4.6 | Yes | Yes | 22.5 | 19.3 | 3.2 | ED63FF1C190F4C7B988B2170CE8D094F |  | R22 | Non-TXV |  | 3.007% | 0.96993 | 5.778% | [5 empty] | Non-TXV | 3.007%
Stockton | CA | 95204-2807 |  | 2013-06-28 | 2013-06-28 12:34 | 2013-06-28 12:34 | RHEEM - HC-100-36-21C | 85 | 0 | Yes | Yes | 20.1 | 20.3 | -0.2 | B9257439D7A245F9BF7C4F12046D3977 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-6458 |  | 2013-08-17 | 2013-08-17 11:53 | 2013-08-17 12:10 | YORK - H2RD048S06B | 134 | 16.7 | Yes | Yes | 25.2 | 22.3 | 2.9 | 61C228A8ED714E68A300CE802AD68709 |  | R22 | Non-TXV |  | 12.46% | 0.87537 | 23.95% | [5 empty] | Non-TXV | 12.46%
Auburn | CA | 95603-7930 |  | 2013-06-28 | 2013-06-28 11:37 | 2013-06-28 11:37 | BDP - 589ANW060100ACAG | 104 | 0 | Yes | Yes | 15.7 | 18.5 | -2.8 | ED7C244AFE404C2482B0E959413DD5C5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Ione | CA | 95640-9182 |  | 2013-08-23 | 2013-08-23 08:49 | 2013-08-23 09:42 | ICP - NAC30AKC3 | 75 | 19.6 | Yes | Yes | 21.5 | 19.5 | 2 | 672E60D0089246B683CAE2F2E72543E7 |  | R22 | Non-TXV |  | 26.13% | 0.73867 | 50.22% | [5 empty] | Non-TXV | 26.13%
Grass Valley | CA | 95945-3902 |  | 2013-07-03 | 2013-07-03 09:23 | 2013-07-03 09:39 | CARRIER - UNK | 60 | 2.5 | Yes | Yes | 24 | 20.1 | 3.9 | D8A8781A953B41C9945259B6073186FE |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Williams | CA | 95987-5175 |  | 2013-08-03 | 2013-08-03 11:09 | 2013-08-03 11:26 | CARRIER - 38CKC030340 | 70 | 3.5 | Yes | Yes | 18 | 21 | -3 | 7A0650FBF87A4862BE8AF7E585E9B43E |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Los Banos | CA | 93635-3202 |  | 2013-07-30 | 2013-07-30 13:55 | 2013-07-30 13:57 | HEIL - 7777UNK | 90 | 3.6 | Yes | Yes | 24.7 | 18.7 | 6 | FC71946B619F4C408EA481F6EAF6CC77 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95210-1639 |  | 2013-06-27 | 2013-06-27 09:44 | 2013-06-27 10:02 | DAY & NIGHT - 585A030080YAC | 50 | -2.9 | Yes | Yes | 18.2 | 18.1 | 0.1 | 20EA75CDEE74469FBB924DDDE522DB4B |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Madera | CA | 93638-1751 |  | 2013-07-15 | 2013-07-15 13:06 | 2013-07-15 13:34 | PAYNE - PY1PN0300AAAA | 121 | 3.6 | Yes | Yes | 16 | 18.6 | -2.6 | 0828A094BE0B4EEEBE974F6414EF48B7 |  | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.718% | [5 empty] | Non-TXV | 2.975%
Pollock Pines | CA | 95726-9534 |  | 2013-07-29 | 2013-07-29 09:59 | 2013-07-29 09:59 | OTHER - HO602E5 | 186 | 0 | Yes | Yes | 28 | 22.6 | 5.4 | C0A5772B089F458B994D6225FF4BB593 |  | R22 | TXV |  | 0% | 1 | 0%
Chico | CA | 95928-5444 |  | 2013-09-24 | 2013-09-24 14:06 | 2013-09-24 14:24 | DAY & NIGHT - 585HJW024040ABAE | 68 | 4.8 | Yes | Yes | 22 | 17.7 | 4.3 | 1989E5F3D0754DE99976965D721A8E40 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Grass Valley | CA | 95945-5850 |  | 2013-11-20 | 2013-11-20 10:05 | 2013-11-20 10:05 | DAY & NIGHT - UNK | 81 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 0E83A13508634CD38320A6B687B25ECE | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Ione | CA | 95640-9177 |  | 2013-08-23 | 2013-08-23 09:39 | 2013-08-23 09:57 | RHEEM - RRKA-A036JK06X | 62 | 8.4 | Yes | Yes | 20.7 | 19.9 | 0.8 | 43DDA19C3DF84928BD0CDC901F0B011A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.55% | 0.86452 | 26.04% | [5 empty] | Non-TXV | 13.55%
Los Banos | CA | 93635-3626 |  | 2013-07-09 | 2013-07-09 10:33 | 2013-07-09 10:38 | NORDYNE - GS3BA024KA | 64 | 5.9 | Yes | Yes | 17 | 19.5 | -2.5 | CE18429963F24443B0015DA68D7CFE5E |  | R22 | Non-TXV |  | 9.219% | 0.90781 | 17.72% | [5 empty] | Non-TXV | 9.219%
Stockton | CA | 95215-4016 |  | 2013-06-28 | 2013-06-28 09:11 | 2013-06-28 09:33 | OTHER - UNK | 67 | 3.1 | Yes | Yes | 17.4 | 17 | 0.4 | B1DAE89944D64D30945C091D8125A26A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.627% | 0.95373 | 8.892% | [5 empty] | Non-TXV | 4.627%
Stockton | CA | 95210-3539 |  | 2013-07-09 | 2013-07-09 10:29 | 2013-07-09 10:46 | NORDYNE - R6GF-X48K120X | 240 | 7.6 | Yes | Yes | 22 | 18.6 | 3.4 | D723E56000564904BF19BE926D5842C1 |  | R410A | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Merced | CA | 95348-1339 |  | 2013-07-03 | 2013-07-03 11:18 | 2013-07-03 11:28 | GOODMAN - GSC1303301A | 117 | 14.1 | Yes | Yes | 21.7 | 23.1 | -1.4 | B0A6E9F698AD46F59A766C7AB3ADAF71 |  | R22 | Non-TXV |  | 12.05% | 0.87949 | 23.16% | [5 empty] | Non-TXV | 12.05%
Ione | CA | 95640-9153 |  | 2013-08-01 | 2013-08-01 13:31 | 2013-08-01 13:55 | OTHER - UNK | 80 | 20 | Yes | Yes | 20 | 22.6 | -2.6 | 17726E040BA4448E9FC48021E96E08C4 |  | R22 | Non-TXV |  | 25% | 0.75 | 48.04% | [5 empty] | Non-TXV | 25%
Los Banos | CA | 93635-3149 |  | 2013-07-08 | 2013-07-08 11:40 | 2013-07-08 11:52 | CARRIER - 591ANX030000ABAA | 69 | 10.7 | Yes | Yes | 25.4 | 21.4 | 4 | D1ACBC6C1A5F4A8E921B12C2665544E8 |  | R22 | Non-TXV |  | 15.51% | 0.84493 | 29.8% | [5 empty] | Non-TXV | 15.51%
Merced | CA | 95348-3144 |  | 2013-09-04 | 2013-09-04 10:04 | 2013-09-04 10:05 | GOODMAN - GPG1324045M41AB | 80 | 4.8 | Yes | Yes | 24.1 | 19.4 | 4.7 | 9A903405594E4088B2147DECC2422B2F |  | R410A | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Chowchilla | CA | 93610-2047 |  | 2013-08-28 | 2013-08-28 12:13 | 2013-08-28 12:41 | CARRIER - 24ABA33360A330 | 169 | 5.7 | Yes | Yes | 17.2 | 20.1 | -2.9 | F5838D8F36124BB4BDA2AB6311AFF624 |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.482% | [5 empty] | Non-TXV | 3.373%
Fresno | CA | 93704-6042 |  | 2013-07-23 | 2013-07-23 13:19 | 2013-07-23 13:37 | HEIL - PGAA36D1K1 | 77 | 10.9 | Yes | Yes | 22.4 | 20.3 | 2.2 | 6DAE8F651E1B4FDE9191DB2A6B5E77F1 |  | R22 | Non-TXV |  | 14.16% | 0.85844 | 27.2% | [5 empty] | Non-TXV | 14.16%
Paradise | CA | 95969-5693 |  | 2013-07-15 | 2013-07-15 17:49 | 2013-07-15 18:07 | YORK - MC2410A | 54 | 13.9 | Yes | Yes | 18.9 | 20.1 | -1.2 | 9BA92A6A5512456E889FCA535B22AB85 |  | R22 | Non-TXV |  | 25.74% | 0.74259 | 49.47% | [5 empty] | Non-TXV | 25.74%
Red Bluff | CA | 96080-0000 |  | 2013-07-20 | 2013-07-20 19:24 | 2013-07-20 19:42 | YORK - H2RD036S06B | 96 | 4.5 | Yes | Yes | 20.6 | 21.9 | -1.3 | FED092E3078647EBB14075E0DE7A8E87 |  | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Parlier | CA | 93648-9632 |  | 2013-08-21 | 2013-08-21 11:38 | 2013-08-21 11:54 | RHEEM - N/A | 60 | 3.3 | Yes | Yes | 18 | 20.7 | -2.7 | 589975424AEA49F69437A96908B2D05C |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Fresno | CA | 93727-2492 |  | 2013-08-16 | 2013-08-16 10:28 | 2013-08-16 10:47 | GOODMAN - CKL24-1L | 64 | 6.7 | Yes | Yes | 19.3 | 20.4 | -1.1 | 8699EECC6DE14E348BBF291C808F890D |  | R22 | Non-TXV |  | 10.47% | 0.89531 | 20.12% | [5 empty] | Non-TXV | 10.47%
Stockton | CA | 95212-3205 |  | 2013-06-27 | 2013-06-27 15:16 | 2013-06-27 15:39 | UNITARY PRODUCTS GROUP - AC036X1222A | 83 | -30.5 | Yes | Yes | 23.8 | 18.5 | 5.3 | C6762926262B491E894E7CFE7E39C086 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -36.75% | 1.3675 | 10.29% |  |  |  |  | TXV |  |  | -36.75%
Los Banos | CA | 93635-3626 |  | 2013-07-24 | 2013-07-24 10:09 | 2013-07-24 10:23 | OTHER - GS3BA-024KA | 64 | 4.7 | Yes | Yes | 17.9 | 20.8 | -2.9 | 130F4B2DB3884191B1E510121C202E4C |  | R22 | Non-TXV |  | 7.344% | 0.92656 | 14.11% | [5 empty] | Non-TXV | 7.344%
Marysville | CA | 95901-8270 |  | 2013-07-01 | 2013-07-01 12:38 | 2013-07-01 12:58 | CARRIER - 2ABA336A310 | 85 | 3.1 | Yes | Yes | 16 | 18.3 | -2.3 | C783FCD104E448D789D86052DF117C1D |  | R410A | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Tracy | CA | 95304-9460 |  | 2013-07-16 | 2013-07-16 10:54 | 2013-07-16 11:15 | RHEEM - RRNL-B030JK06X | 85 | 9.6 | Yes | Yes | 21.1 | 19.9 | 1.2 | 461542F7DA9C464CB688CF56BA680BAF |  | R410A | Non-TXV |  | 11.29% | 0.88706 | 21.7% | [5 empty] | Non-TXV | 11.29%
Corning | CA | 96021-3034 |  | 2013-08-13 | 2013-08-13 18:21 | 2013-08-13 15:39 | YORK - D1NA83N05606C | 67 | 5.5 | Yes | Yes | 20.2 | 21.2 | -1 | 99C1EF6006EA40CB89289FEE6B293DF7 |  | R22 | Non-TXV |  | 8.209% | 0.91791 | 15.78% | [5 empty] | Non-TXV | 8.209%
Watsonville | CA | 95076-0315 |  | 2013-10-21 | 2013-10-21 12:34 | 2013-10-21 12:55 | BRYANT - 561CJ060-A | 158 | -11.2 | Yes | Yes | 16.4 | 18.7 | -2.3 | 3556C3E64FCA42798B6D29CFB217BFF7 |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Arnold | CA | 95223-0000 |  | 2013-09-04 | 2013-09-04 11:43 | 2013-09-04 12:04 | PAYNE - PA10JA036-A | 85 | 4.1 | Yes | Yes | 24.8 | 18.8 | 6 | 018DF2DB7359446394E5F1DEA24C1528 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fresno | CA | 93701-1626 |  | 2013-07-12 | 2013-07-12 12:51 | 2013-07-12 12:54 | GOODMAN - GSC130601CA | 131 | 4.8 | Yes | Yes | 22.6 | 19.9 | 2.7 | 6E370471FCB4425585F7015DBE6B336F |  | R22 | Non-TXV |  | 3.664% | 0.96336 | 7.042% | [5 empty] | Non-TXV | 3.664%
Reedley | CA | 93654-3605 |  | 2013-07-24 | 2013-07-24 21:56 | 2013-07-24 21:58 | COLEMAN - 9548-901 | 68 | 2.9 | Yes | Yes | 24.2 | 20.3 | 4 | 67FF2695C7E74618B156AFC5FF485ECB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Los Banos | CA | 93635-3626 |  | 2013-07-09 | 2013-07-09 10:56 | 2013-07-09 11:11 | NORDYNE - GS3BA024KA | 64 | 7.4 | Yes | Yes | 24.8 | 22.8 | 2 | 0941CEA34F724FCF8B19B5E9C0E39DE2 |  | R22 | Non-TXV |  | 11.56% | 0.88438 | 22.22% | [5 empty] | Non-TXV | 11.56%
Stockton | CA | 95209-2516 |  | 2013-07-17 | 2013-07-17 10:54 | 2013-07-17 10:54 | AMERICAN STANDARD - 2YCX36A1096AA | 82 | 0 | Yes | Yes | 19.3 | 18.5 | 0.8 | AF94EA75F7F144DC93E62ACB98EE9D77 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4111 |  | 2013-07-09 | 2013-07-09 13:23 | 2013-07-09 13:25 | BRYANT - 582AJW048090AAAG | 81 | 10.5 | Yes | Yes | 18.3 | 17 | 1.3 | 05419F0117F845319DE1B6CDF31D7064 |  | R22 | Non-TXV |  | 12.96% | 0.87037 | 24.91% | [5 empty] | Non-TXV | 12.96%
Fresno | CA | 93727-3145 |  | 2013-07-12 | 2013-07-12 14:26 | 2013-07-12 14:52 | ICP - PGC048K080A | 102 | 15.8 | Yes | Yes | 19.1 | 22 | -2.9 | 3475E616C6FD45AF9980C9738992FFE8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.49% | 0.8451 | 29.77% | [5 empty] | Non-TXV | 15.49%
Chico | CA | 95973-8355 |  | 2013-07-10 | 2013-07-10 20:27 | 2013-07-10 20:27 | YORK - N2CB0245068 | 65 | 0 | Yes | Yes | 23.6 | 21.2 | 2.4 | 7984EFB43A9648378FD25E6A99D6BD42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-2490 |  | 2013-08-14 | 2013-08-14 14:29 | 2013-08-14 14:50 | RUUD - UNK | 64 | 7 | Yes | Yes | 19.3 | 19.1 | 0.2 | 2317FAECAB654434B824CA8DD18C06F8 |  | R22 | Non-TXV |  | 10.94% | 0.89062 | 21.02% | [5 empty] | Non-TXV | 10.94%
Madera | CA | 93638-1752 |  | 2013-07-16 | 2013-07-16 10:34 | 2013-07-16 11:43 | PAYNE - PY1PNB036060AAA | 56 | 2 | Yes | Yes | 19.7 | 19.2 | 0.5 | 40D3A095B7E94F7C98937D52339C915E |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Auburn | CA | 95603-5437 |  | 2013-06-28 | 2013-06-28 13:04 | 2013-06-28 13:24 | TEMPSTAR - CA3036VKA1 | 94 | -8.8 | Yes | Yes | 16.9 | 19.3 | -2.4 | ADC9C85E6E8D4E28B0A281870F7D7D4D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.362% | 1.0936 | 2.622% |  |  |  |  | Non-TXV |  |  | -9.362%
Stockton | CA | 95219-3139 |  | 2013-07-01 | 2013-07-01 11:50 | 2013-07-01 12:14 | RHEEM - RRNL-B036JK06X | 80 | 3.2 | Yes | Yes | 20.3 | 19 | 1.3 | 4B4A3CF167264F178F310A3F41ACE50C |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Riverbank | CA | 95367-2279 |  | 2013-08-20 | 2013-08-20 08:55 | 2013-08-20 08:55 | BDP - 585B024050YACR | 51 | 0 | Yes | Yes | 20 | 19.2 | 0.8 | 3095D0ADF62C403CAA8313B8E41D8B6F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0718 |  | 2013-07-19 | 2013-07-19 11:08 | 2013-07-19 11:10 | DAY & NIGHT - 3680YAC10CG | 66 | 14.6 | Yes | Yes | 25.2 | 21.3 | 3.9 | 42B3EF0ABE41424F9D0FE2C9045B9900 |  | R22 | Non-TXV |  | 22.12% | 0.77879 | 42.51% | [5 empty] | Non-TXV | 22.12%
Merced | CA | 95340-3267 |  | 2013-07-09 | 2013-07-09 10:43 | 2013-07-09 10:44 | AMERICAN STANDARD - YCY048G1H0AC | 183 | 5.6 | Yes | Yes | 25.8 | 20.2 | 5.6 | DB26B93A32FB43C2A4DA06A971714540 |  | R22 | Non-TXV |  | 3.06% | 0.9694 | 5.881% | [5 empty] | Non-TXV | 3.06%
Fresno | CA | 93727-2492 |  | 2013-08-14 | 2013-08-14 15:03 | 2013-08-14 15:21 | CARRIER - 38CKC030330 | 66 | 2.8 | Yes | Yes | 19.6 | 21.5 | -1.9 | 55D73ECE412E4BD18286898D259CB2EB |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Madera | CA | 93638-1776 |  | 2013-07-15 | 2013-07-15 16:22 | 2013-07-15 18:46 | BRYANT - 582ANWW4206NAAG | 100 | 7.3 | Yes | Yes | 16.2 | 17.7 | -1.5 | 538585A23C664A9C86EA21377299BE07 |  | R22 | Non-TXV |  | 7.3% | 0.927 | 14.03% | [5 empty] | Non-TXV | 7.3%
Dinuba | CA | 93618-9634 |  | 2013-07-29 | 2013-07-29 10:14 | 2013-07-29 11:00 | LENNOX - 13ACD-0420230-02 | 111 | 3.8 | Yes | Yes | 14.2 | 17 | -2.8 | 75C34D39937E42A7902159621F75D7C1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.423% | 0.96577 | 6.579% | [5 empty] | Non-TXV | 3.423%
Stockton | CA | 95212-3539 |  | 2013-06-27 | 2013-06-27 13:06 | 2013-06-27 13:24 | GOODMAN - CLJ42-1B | 84 | 4.1 | Yes | Yes | 27 | 21.3 | 5.7 | DE3768AEE2FF46D7B972A4139149285A |  | R22 | Non-TXV |  | 4.881% | 0.95119 | 9.38% | [5 empty] | Non-TXV | 4.881%
Chico | CA | 95973-8353 |  | 2013-08-21 | 2013-08-21 11:46 | 2013-08-21 12:40 | YORK - H2CB024506B | 65 | 7.6 | Yes | Yes | 20 | 18.6 | 1.4 | D6BE6EF9B4E2492AA76EBE1995F208B8 |  | R22 | Non-TXV |  | 11.69% | 0.88308 | 22.47% | [5 empty] | Non-TXV | 11.69%
Murphys | CA | 95247-0000 |  | 2013-08-22 | 2013-08-22 10:45 | 2013-08-22 11:35 | GOODMAN - CK4918 | 97 | 11.9 | Yes | Yes | 20.8 | 18.4 | 2.4 | E5E9A4B97FDA47249CF3781B1A6E71CC |  | R22 | Non-TXV |  | 12.27% | 0.87732 | 23.58% | [5 empty] | Non-TXV | 12.27%
Tracy | CA | 95376-1454 |  | 2013-07-17 | 2013-07-17 08:07 | 2013-07-17 08:32 | WEATHER KING - 13AJA42A01 | 85 | 3.5 | Yes | Yes | 21 | 18.8 | 2.2 | FB78D1C6ABA948D5B1C3B6BCF91C2FEF |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Parlier | CA | 93648-9633 |  | 2013-08-07 | 2013-08-07 17:51 | 2013-08-07 17:51 | RHEEM - N/A | 60 | 0 | Yes | Yes | 20.5 | 20 | 0.6 | ACDB6FA70A124CE2B11DAF5B356091A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-8259 |  | 2013-07-12 | 2013-07-12 12:22 | 2013-07-12 12:41 | CARRIER - 38KC042350 | 95 | 9.9 | Yes | Yes | 17 | 19.8 | -2.8 | E868B2A078C24E30B4AF41AD707DF4C5 |  | R22 | TXV |  | 10.42% | 0.89579 | 20.03% | [5 empty] | TXV | 10.42%
Marysville | CA | 95901-8261 |  | 2013-07-01 | 2013-07-01 14:29 | 2013-07-01 14:55 | CARRIER - 38CKC048370 | 100 | 5.4 | Yes | Yes | 19 | 21.7 | -2.7 | 2160D46D52F344D7B52C595AF40B55CD |  | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Fresno | CA | 93727-6149 |  | 2013-07-15 | 2013-07-15 15:39 | 2013-07-15 16:08 | LENNOX - 13ACC=-060-230-01 | 168 | 21.3 | Yes | Yes | 18 | 19.8 | -1.8 | F5A86E0F26D04DB5B1BFCCF68306133B |  | R22 | Non-TXV |  | 12.68% | 0.87321 | 24.37% | [5 empty] | Non-TXV | 12.68%
Madera | CA | 93638-0177 |  | 2013-07-17 | 2013-07-17 14:39 | 2013-07-17 14:42 | PAYNE - 7777UNK | 100 | 3.6 | Yes | Yes | 22.1 | 19.8 | 2.3 | DFC7E22D6D044F69B67095D301BFF046 |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Chico | CA | 95973-1015 |  | 2013-07-08 | 2013-07-08 22:00 | 2013-07-08 22:00 | LENNOX - 10HPB36-7P | 104 | 0 | Yes | Yes | 19.1 | 22.1 | -3 | BB47E4AF93A34304A36F2E19DF6D5519 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9627 |  | 2013-09-03 | 2013-09-03 14:26 | 2013-09-03 15:06 | RUUD - UAMA-024JAZ | 85 | 2.8 | Yes | Yes | 19 | 20.7 | -1.7 | BB1E300A0A4E4CC3BB5AC739E0257F03 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Stockton | CA | 95212-3539 |  | 2013-06-27 | 2013-06-27 12:51 | 2013-06-27 16:09 | GOODMAN - CLJ48-1A | 130 | 3.9 | Yes | Yes | 18.9 | 19.5 | -0.6 | BC9B150D14FA496EA9A4A0C73B8BB8F3 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93725-1851 |  | 2013-09-09 | 2013-09-09 14:57 | 2013-09-09 16:00 | UNITARY PRODUCTS GROUP - BRCQ0481BD | 103 | 3.4 | Yes | Yes | 17.5 | 20.1 | -2.6 | 88B09DC507A74CAEA769C954D00F4DC1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.301% | 0.96699 | 6.344% | [5 empty] | Non-TXV | 3.301%
Auburn | CA | 95603-5732 |  | 2013-06-28 | 2013-06-28 12:30 | 2013-06-28 12:30 | PAYNE - 597BN030-A | 110 | 0 | Yes | Yes | 17.1 | 19.7 | -2.6 | 0842CDD850954BE59BD497DA34D422E3 |  | R22 | TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9631 |  | 2013-10-02 | 2013-10-02 16:41 | 2013-10-02 17:00 | RHEEM - N/A | 60 | 4.1 | Yes | Yes | 21.5 | 19.6 | 2 | 89845140E1154AD4B65CCBE2E90C6772 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.833% | 0.93167 | 13.13% | [5 empty] | Non-TXV | 6.833%
Valley Springs | CA | 95252-9508 |  | 2013-07-16 | 2013-07-16 12:07 | 2013-07-16 12:36 | PAYNE - UNK | 85 | 5.6 | Yes | Yes | 20.9 | 18.8 | 2.1 | 182C74A89E914AFAA9BDB1A31F373BBF |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Fresno | CA | 93706-4835 |  | 2013-07-16 | 2013-07-16 14:49 | 2013-07-16 14:51 | OTHER - 7777UNK | 104 | 4.7 | Yes | Yes | 19.6 | 19.9 | -0.3 | 1E0016AFB96F481C9CC947A2E1381813 |  | R22 | Non-TXV |  | 4.519% | 0.95481 | 8.685% | [5 empty] | Non-TXV | 4.519%
Madera | CA | 93638-2518 |  | 2013-07-18 | 2013-07-18 10:55 | 2013-07-18 10:55 | RHEEM - UNK | 66 | 0 | Yes | Yes | 20.8 | 18.8 | 2 | D9F75B387E0C4B67B491FF2722F6A3BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-7836 |  | 2013-07-16 | 2013-07-16 23:39 | 2013-07-16 21:01 | GIBSON - 661CJ018-13 | 68 | 10.5 | Yes | Yes | 18.5 | 20.9 | -2.4 | 903DE30EAFC34D7F9D0ED13CA1669C13 |  | R22 | TXV |  | 15.44% | 0.84559 | 29.67% | [5 empty] | TXV | 15.44%
Madera | CA | 93638-1776 |  | 2013-08-07 | 2013-08-07 15:07 | 2013-08-07 15:37 | BARD - 582ANW4206ONAAG | 100 | 3.8 | Yes | Yes | 19.9 | 20.7 | -0.8 | A1ADDBCBC06A4FE8B34ADF6DB312E6FD |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Fresno | CA | 93727-5522 |  | 2013-07-22 | 2013-07-22 10:54 | 2013-07-22 10:56 | PAYNE - PY1PJ048090AAAA | 81 | 2.8 | Yes | Yes | 19.5 | 20.8 | -1.3 | E87CC41B2C5444328FDCAE9BC3477B05 |  | R22 | Non-TXV |  | 3.457% | 0.96543 | 6.643% | [5 empty] | Non-TXV | 3.457%
Kingsburg | CA | 93631-1049 |  | 2013-08-01 | 2013-08-01 14:48 | 2013-08-01 15:40 | RUUD - N/A | 60 | 5.4 | Yes | Yes | 25 | 20.9 | 4.1 | 9FF3DD04C2CD4205882FEEFB5EF9353F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Stockton | CA | 95207-3133 |  | 2013-07-26 | 2013-07-26 15:01 | 2013-07-26 15:01 | ARMSTRONG - SCU12E36A-2 | 99 | 0 | Yes | Yes | 24.1 | 18.5 | 5.6 | 28B5937AD2AE424596F3FC8DFF7085B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-2287 |  | 2013-07-17 | 2013-07-17 13:01 | 2013-07-17 13:22 | CARRIER - 585E1038075ABAF | 82 | 6.4 | Yes | Yes | 18.2 | 20.4 | -2.2 | 3DCCBE068E5141758835551291136ADA |  | R22 | Non-TXV |  | 7.805% | 0.92195 | 15% | [5 empty] | Non-TXV | 7.805%
Fowler | CA | 93625-2012 |  | 2013-08-20 | 2013-08-20 14:42 | 2013-08-20 15:09 | RHEEM - RRNA0B036JK08X | 83 | 2.6 | Yes | Yes | 17 | 17.2 | -0.2 | 36957E6633D94761995BEC8FFC2D2AFD |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Stockton | CA | 95207-3133 |  | 2013-06-27 | 2013-06-27 13:33 | 2013-06-27 13:53 | GOODMAN - CLJ36-1A | 109 | -10.3 | Yes | Yes | 12.5 | 15 | -2.5 | CF40E898AD2D4F8D9BC6079958C4A389 |  | R22 | Non-TXV |  | -9.45% | 1.0945 | 2.646% |  |  |  |  | Non-TXV |  |  | -9.45%
Galt | CA | 95632-8235 |  | 2013-08-21 | 2013-08-21 09:57 | 2013-08-21 10:15 | BRYANT - 563CN042-C | 103 | 3.6 | Yes | Yes | 18 | 18.7 | -0.7 | E091AEC0819340C1BDB321775A800098 |  | R22 | Non-TXV |  | 3.495% | 0.96505 | 6.717% | [5 empty] | Non-TXV | 3.495%
Diamond Springs | CA | 95619-9308 |  | 2013-10-01 | 2013-10-01 12:45 | 2013-10-01 12:45 | GOODMAN - GPG1330070M41BA | 78 | 0 | Yes | Yes | 16.2 | 19.1 | -2.9 | 8C6EA5D429CE40DC9C28B4DE03744CB5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-4747 |  | 2013-07-09 | 2013-07-09 13:02 | 2013-07-09 13:23 | AMERICAN STANDARD - 6H2036A100A3 | 135 | 14.4 | Yes | Yes | 19 | 22 | -3 | CDC61CF3BF3C4D519FA4E1D76871073D |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Parlier | CA | 93648-9624 |  | 2013-08-28 | 2013-08-28 13:44 | 2013-08-28 14:33 | RUUD - N/A | 60 | 3.1 | Yes | Yes | 19.5 | 20.2 | -0.7 | 4207BF01CFAD420095A6205CDD4EA41A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Oroville | CA | 95966-7713 |  | 2013-07-29 | 2013-07-29 13:35 | 2013-07-29 13:59 | GOODMAN - PC036-18 REV E | 63 | 5 | Yes | Yes | 16.4 | 18.8 | -2.4 | AEE7CC9FBC8142D79D8748BBF096F838 |  | R22 | Non-TXV |  | 7.937% | 0.92063 | 15.25% | [5 empty] | Non-TXV | 7.937%
Fresno | CA | 93722-5708 |  | 2013-07-17 | 2013-07-17 10:13 | 2013-07-17 10:27 | YORK - H2RA036S06 | 63 | 8.2 | Yes | Yes | 21.3 | 20.4 | 0.9 | 567606D4FC9C47D78A0CD23067AE3D36 |  | R22 | Non-TXV |  | 13.02% | 0.86984 | 25.01% | [5 empty] | Non-TXV | 13.02%
Olivehurst | CA | 95961-7454 |  | 2013-10-22 | 2013-10-22 13:29 | 2013-10-22 13:54 | OTHER - UNK | 84 | 3.6 | Yes | Yes | 21 | 21.4 | -0.4 | 3C88BD4A22314B5A8AB9228D534DBE5E |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Sanger | CA | 93657-2961 |  | 2013-08-05 | 2013-08-05 12:53 | 2013-08-05 13:31 | BDP - 585HJ036060ABAF | 102 | 8.2 | Yes | Yes | 18.2 | 20.4 | -2.2 | 7D7CB4444B4541B58E0D64D673C6EAC0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.039% | 0.91961 | 15.45% | [5 empty] | Non-TXV | 8.039%
Marysville | CA | 95901-6558 |  | 2013-06-29 | 2013-06-29 09:19 | 2013-06-29 09:19 | OTHER - 561CJ036-D | 85 | 0 | Yes | Yes | 15.5 | 18 | -2.5 | 4F9C44566683494281CCDE29476630B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4374 |  | 2013-07-16 | 2013-07-16 13:56 | 2013-07-16 13:57 | YORK - D1NH042N06506C | 94 | 11.7 | Yes | Yes | 25.8 | 23.1 | 2.7 | C614F22D1AB441F786A5F6E7CC3F2384 |  | R22 | Non-TXV |  | 12.45% | 0.87553 | 23.92% | [5 empty] | Non-TXV | 12.45%
Stockton | CA | 95207-4833 |  | 2013-06-27 | 2013-06-27 09:54 | 2013-06-27 09:54 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 16.9 | 15.5 | 1.4 | 214A4C0F81D14E79ABEB2A5D8EEF1B5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-9564 |  | 2013-07-13 | 2013-07-13 14:49 | 2013-07-13 15:05 | TRANE - UNK | 95 | 3.5 | Yes | Yes | 23 | 20.4 | 2.6 | B6A0A8807D904BB791145C6577AC8A5D |  | R22 | TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | TXV | 3.684%
Stockton | CA | 95206-4958 |  | 2013-07-16 | 2013-07-16 11:49 | 2013-07-16 12:15 | GOODMAN - GSC130361DF | 120 | 3.6 | Yes | Yes | 18.7 | 19.6 | -0.9 | 49AD2FD562654B18AFDB3F202CD04251 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Reedley | CA | 93654-3656 |  | 2013-07-25 | 2013-07-25 12:13 | 2013-07-25 13:13 | GOODMAN - CKL30-1L | 74 | 4.2 | Yes | Yes | 22.6 | 20.8 | 1.8 | 858FFD07192C4F46892D3F45757C87E7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.676% | 0.94324 | 10.91% | [5 empty] | Non-TXV | 5.676%
Fresno | CA | 93711-2055 |  | 2013-07-25 | 2013-07-25 08:35 | 2013-07-25 08:37 | ICP - HAC248AKA4 | 148 | 18.5 | Yes | Yes | 26 | 20.4 | 5.6 | 6ED13F53CCC5496EA86F8CC51E7BBEB9 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Fresno | CA | 93727-2461 |  | 2013-08-12 | 2013-08-12 11:13 | 2013-08-12 12:08 | CARRIER - 38CKC024---341 | 54 | 1.9 | Yes | Yes | 15.3 | 18.3 | -3 | E824FFAAEA824B74BC5741B51B0C1B7B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Pioneer | CA | 95666-9386 |  | 2013-08-13 | 2013-08-13 13:03 | 2013-08-13 13:03 | CARRIER - 48GX-042090301AD | 118 | 0 | Yes | Yes | 30 | 24.2 | 5.8 | 29F7CB5132A74EF8B78B4055C307C0C5 |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3154 |  | 2013-07-24 | 2013-07-24 12:12 | 2013-07-24 12:17 | GOODMAN - CK24-1B | 71 | 2.3 | Yes | Yes | 17.4 | 18.3 | -0.9 | 22F640585BBE4C9D8A8CDB2957403D86 |  | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.225% | [5 empty] | Non-TXV | 3.239%
Oroville | CA | 95965-4101 |  | 2013-07-25 | 2013-07-25 15:15 | 2013-07-25 15:48 | BRYANT - BRCS0361BD | 63 | 3.5 | Yes | Yes | 20.5 | 20.8 | -0.3 | B6AEC511E92A48129E0847DC1DCB5D61 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Sanger | CA | 93657-3722 |  | 2013-08-05 | 2013-08-05 14:14 | 2013-08-05 15:06 | LENNOX - 12GCS030X-75-3PA | 85 | 3.1 | Yes | Yes | 19 | 19.3 | -0.3 | DAD64A50EB624DEEAE4B3424316B5F26 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Marysville | CA | 95901-7441 |  | 2013-06-29 | 2013-06-29 14:31 | 2013-06-29 14:52 | WESTINGHOUSE - FS5BD-036KA | 110 | 6.4 | Yes | Yes | 20 | 19.9 | 0.1 | E8A7678C2A024E30BB58F55C95F781A2 |  | R22 | Non-TXV |  | 5.818% | 0.94182 | 11.18% | [5 empty] | Non-TXV | 5.818%
Pioneer | CA | 95666-9395 |  | 2013-09-20 | 2013-09-20 10:41 | 2013-09-20 11:04 | RHEEM - RRGG-07N48JKR | 136 | 4 | Yes | Yes | 22 | 19.1 | 2.9 | 18AF5625DA7941BBA22E80C8EBBA2D47 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Winton | CA | 95388-9249 |  | 2013-07-11 | 2013-07-11 09:25 | 2013-07-11 09:27 | GOODMAN - PGB030050 | 56 | 7.6 | Yes | Yes | 26 | 20.6 | 5.4 | FDEE6FBC605F4BC2ABFE9B33AF44CCD2 |  | R22 | Non-TXV |  | 13.57% | 0.86429 | 26.08% | [5 empty] | Non-TXV | 13.57%
Marysville | CA | 95901-0000 |  | 2013-07-11 | 2013-07-11 14:26 | 2013-07-11 14:26 | CARRIER - 48ESN042090311 | 105 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | C6DF36F2C0B34C43A5AD44CE159EEFC9 |  | R410A | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-2979 |  | 2013-07-08 | 2013-07-08 10:24 | 2013-07-08 10:54 | BRYANT - 563CN048-F | 205 | 6.3 | Yes | Yes | 22.6 | 20.1 | 2.5 | 95D2DCC7AD5347E7B293BAB664A8097D |  | R22 | Non-TXV |  | 3.073% | 0.96927 | 5.906% | [5 empty] | Non-TXV | 3.073%
Stockton | CA | 95209-3922 |  | 2013-07-15 | 2013-07-15 11:46 | 2013-07-15 12:04 | CARRIER - 38CKC042---352-- | 88 | 8.3 | Yes | Yes | 21.6 | 18.4 | 3.2 | 3FD34B8BE5D545BC9AE8CD844636E5D0 |  | R22 | Non-TXV |  | 9.432% | 0.90568 | 18.13% | [5 empty] | Non-TXV | 9.432%
Sanger | CA | 93657-9230 |  | 2013-07-23 | 2013-07-23 11:35 | 2013-07-23 12:09 | ICP - PGF042K080B | 87 | 3.4 | Yes | Yes | 17 | 19.8 | -2.8 | 40BA8545B1BA4455AA2C50F5BE3502C0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | Non-TXV | 3.908%
Fresno | CA | 93705-0638 |  | 2013-07-11 | 2013-07-11 10:11 | 2013-07-11 10:25 | GOODMAN - GPG12300701A | 75 | 2.6 | Yes | Yes | 18 | 20.7 | -2.7 | DD6EAF256ECC4F2DB029735431FED23F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.467% | 0.96533 | 6.662% | [5 empty] | Non-TXV | 3.467%
Fresno | CA | 93705-0638 |  | 2013-07-11 | 2013-07-11 10:28 | 2013-07-11 10:50 | GOODMAN - GPG12300701A | 78 | 3 | Yes | Yes | 24.4 | 21 | 3.4 | 610B003D74C94DAC9032595BD4E9404B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Sanger | CA | 93657-3736 |  | 2013-08-03 | 2013-08-03 18:06 | 2013-08-03 19:17 | GOODMAN - PGJ036075-1 | 81 | 5.1 | Yes | Yes | 21.7 | 20.1 | 1.7 | 2049F18A306042C6B3280453D9354CDC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Parlier | CA | 93648-0000 |  | 2013-08-21 | 2013-08-21 10:38 | 2013-08-21 10:56 | CONCORD - CCU10A24A-1 | 50 | 4.1 | Yes | Yes | 19.5 | 20.5 | -1 | F477ECA1970D4D5AAC6160A7C1C6A357 |  | R22 | Non-TXV |  | 8.2% | 0.918 | 15.76% | [5 empty] | Non-TXV | 8.2%
Shingle Springs | CA | 95682-9674 |  | 2013-08-30 | 2013-08-30 16:43 | 2013-08-30 17:02 | CARRIER - 38CKB036330 | 85 | 6.4 | Yes | Yes | 23 | 20.4 | 2.6 | 23C001CCC2AB4647890D31684338F244 |  | R22 | TXV |  | 7.529% | 0.92471 | 14.47% | [5 empty] | TXV | 7.529%
Lathrop | CA | 95330-9200 |  | 2013-07-03 | 2013-07-03 13:25 | 2013-07-03 13:56 | YORK - D2NP036N05606A | 108 | 8.1 | Yes | Yes | 16.5 | 19.5 | -3 | A759397EF2924D57A25FFC63D9F718B6 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Los Banos | CA | 93635-4078 |  | 2013-07-09 | 2013-07-09 13:58 | 2013-07-09 13:59 | NORDYNE - GS3BA024KA | 64 | 11.4 | Yes | Yes | 23.6 | 21.7 | 1.9 | 281FC2E94B544F06BF1326C34D88D387 |  | R22 | Non-TXV |  | 17.81% | 0.82188 | 34.23% | [5 empty] | Non-TXV | 17.81%
Colfax | CA | 95713-9533 |  | 2013-08-16 | 2013-08-16 12:24 | 2013-08-16 12:40 | BRYANT - 552AN048-E | 87 | 3.6 | Yes | Yes | 19 | 21.5 | -2.5 | 13FA7F63E8E8405ABC8E37EE69592CC5 |  | R410A | TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | TXV | 4.138%
Fresno | CA | 93705-0217 |  | 2013-07-16 | 2013-07-16 09:07 | 2013-07-16 10:05 | BDP - 585A036060YACR | 75 | 2.3 | Yes | Yes | 22 | 20.4 | 1.6 | EE66D86CFAE34382ADEE11118BBD3C62 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Clovis | CA | 93612-4450 |  | 2013-08-15 | 2013-08-15 12:21 | 2013-08-15 14:05 | PAYNE - N/A | 90 | 6.4 | Yes | Yes | 19 | 20.4 | -1.4 | 9025E17A76C44B9BB7F2DB88546B4EFF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.111% | 0.92889 | 13.67% | [5 empty] | Non-TXV | 7.111%
Merced | CA | 95340-3206 |  | 2013-06-28 | 2013-06-28 17:04 | 2013-06-28 17:07 | GOODMAN - GPG13360701AB | 112 | 3.6 | Yes | Yes | 21 | 15.5 | 5.5 | CF5E29C8EFD44A269F8987C2D2D32450 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Madera | CA | 93638-0594 |  | 2013-07-12 | 2013-07-12 11:15 | 2013-07-12 12:26 | YORK - B1HP042A06A | 158 | 5.5 | Yes | Yes | 19.2 | 20.1 | -0.9 | 14826B76C12747BFA244EB302C81320F |  | R22 | Non-TXV |  | 3.481% | 0.96519 | 6.69% | [5 empty] | Non-TXV | 3.481%
Fresno | CA | 93726-4513 |  | 2013-07-29 | 2013-07-29 13:39 | 2013-07-29 13:40 | RHEEM - RRGH07N36JKR | 81 | 12.1 | Yes | Yes | 27.5 | 23 | 4.5 | 3087BF3119144AD9ABB18655F0589A39 |  | R22 | Non-TXV |  | 14.94% | 0.85062 | 28.71% | [5 empty] | Non-TXV | 14.94%
Rough & Ready | CA | 95975-9778 |  | 2013-10-23 | 2013-10-23 16:09 | 2013-10-23 16:09 | TRANE - 2TTR2036A1000AA | 96 | 0 | Yes | Yes | 27.8 | 23.5 | 4.3 | 2309CB0621C942DA93477688647DED3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-3609 |  | 2013-06-28 | 2013-06-28 19:14 | 2013-06-28 19:14 | AMANA - APG152407041AA | 51 | 0 | Yes | Yes | 20 | 21 | -1 | E604E93C6F964707A373C3D1BBC4BAC2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3205 |  | 2013-06-27 | 2013-06-27 16:01 | 2013-06-27 16:41 | YORK - H1RC060S06D | 85 | 2.6 | Yes | Yes | 24.3 | 20.4 | 3.9 | D529F731692F451596AE8E9AB075184E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Acampo | CA | 95220-9532 |  | 2013-08-21 | 2013-08-21 12:32 | 2013-08-21 12:51 | AMANA - PGD42C0902E | 120 | 4 | Yes | Yes | 25.5 | 19.5 | 6 | B425D085B6A54838BF68902C0B869A04 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Marysville | CA | 95901-8304 |  | 2013-07-02 | 2013-07-02 13:02 | 2013-07-02 13:02 | CARRIER - 24ABA336A310 | 85 | 0 | Yes | Yes | 16 | 17.5 | -1.5 | B700A0C796674E7D95B0067ED205C56A |  | R410A | TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-4725 |  | 2013-08-06 | 2013-08-06 08:34 | 2013-08-06 09:09 | DAY & NIGHT - 561CJ048-A | 110 | -7.8 | Yes | Yes | 22.5 | 18.7 | 3.8 | F43100BC5CE2461A9E8F309F8AAB1804 |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Corning | CA | 96021-9669 |  | 2013-08-13 | 2013-08-13 12:36 | 2013-08-13 12:53 | RUUD - 13AJA60A01 | 119 | 4.5 | Yes | Yes | 22.5 | 21.5 | 1 | D24CC477E4EB4595A3AF60CE9C6E9886 |  | R22 | Non-TXV |  | 3.782% | 0.96218 | 7.267% | [5 empty] | Non-TXV | 3.782%
Stockton | CA | 95205-4334 |  | 2013-09-04 | 2013-09-04 13:42 | 2013-09-04 13:59 | YORK - D1NP030N05606A | 73 | 3.2 | Yes | Yes | 22.8 | 17.6 | 5.2 | 387023E6E9FE496BAA152DE0B27AA44C |  | R22 | Non-TXV |  | 4.384% | 0.95616 | 8.424% | [5 empty] | Non-TXV | 4.384%
Chico | CA | 95973-0428 |  | 2013-08-21 | 2013-08-21 09:10 | 2013-08-21 09:47 | COLEMAN - 62858901 | 96 | 9.8 | Yes | Yes | 19.5 | 20.6 | -1.1 | 5FE277A322C9410D85B7D2D28BB9ECD8 |  | R22 | Non-TXV |  | 10.21% | 0.89792 | 19.62% | [5 empty] | Non-TXV | 10.21%
Kerman | CA | 93630-1986 |  | 2013-08-01 | 2013-08-01 08:43 | 2013-08-01 08:44 | CARRIER - 48SDN042060301 | 168 | 11.7 | Yes | Yes | 23.1 | 18.2 | 4.9 | 45C676FAA9C5424D95EBD3D220339010 |  | R22 | Non-TXV |  | 6.964% | 0.93036 | 13.38% | [5 empty] | Non-TXV | 6.964%
Fresno | CA | 93710-6116 |  | 2013-06-27 | 2013-06-27 13:10 | 2013-06-27 13:12 | RHEEM - RRNA-A036JK06X | 114 | 3.4 | Yes | Yes | 20.2 | 19.1 | 1.1 | 0611BEB4C7DB463B9BD3ED05CEFF7A1C |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Fresno | CA | 93711-6543 |  | 2013-08-10 | 2013-08-10 14:58 | 2013-08-10 15:01 | AMERICAN STANDARD - YCC024F1L0BJ | 65 | 1.9 | Yes | Yes | 18.7 | 17.6 | 1.1 | 0C73A4D3DAA54C2A9F3CC41E9E44641C |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Stockton | CA | 95209-4154 |  | 2013-07-16 | 2013-07-16 11:07 | 2013-07-16 11:07 | PAYNE - 563AN042-A | 132 | 0 | Yes | Yes | 16.3 | 17.8 | -1.5 | 57E426AC6A0F44C9A262AEAAE5FB20C6 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-3236 |  | 2013-07-23 | 2013-07-23 11:43 | 2013-07-23 11:45 | RUUD - UAFD048JBS | 101 | 11.6 | Yes | Yes | 19.7 | 20.9 | -1.2 | DAFC72AD0A914185A56A085137233622 |  | R22 | Non-TXV |  | 11.49% | 0.88515 | 22.07% | [5 empty] | Non-TXV | 11.49%
Stockton | CA | 95210-1851 |  | 2013-06-27 | 2013-06-27 14:28 | 2013-06-27 14:52 | ICP - PGF330060K01 | 95 | -5.6 | Yes | Yes | 23.4 | 18.1 | 5.3 | 0901DE90C9C04AC3A87247332DC62E60 |  | R22 | Non-TXV |  | -5.895% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Paso Robles | CA | 93446-3476 |  | 2013-08-05 | 2013-08-05 14:34 | 2013-08-05 14:54 | YORK - UNK | 119 | 3.6 | Yes | Yes | 18.4 | 18.8 | -0.4 | 4A9E2DE01E2F4FC39081C8BD1F7127CA |  | R22 | Non-TXV |  | 3.025% | 0.96975 | 5.814% | [5 empty] | Non-TXV | 3.025%
Manteca | CA | 95337-6526 |  | 2013-07-19 | 2013-07-19 16:24 | 2013-07-19 16:47 | DAY & NIGHT - 565BJ024 | 70 | 9.8 | Yes | Yes | 19.5 | 18.2 | 1.3 | FE7BFC18D4214B39B35FD144DF4C3498 |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Auburn | CA | 95603-9793 |  | 2013-06-29 | 2013-06-29 18:10 | 2013-06-29 18:10 | DAY & NIGHT - 542D037HP | 115 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | 4BA9F2582F0242C98464D0D609D30C94 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2047 |  | 2013-06-27 | 2013-06-27 02:26 | 2013-06-27 03:10 | CARRIER - 24AB3448A30 | 114 | 6.4 | Yes | Yes | 17.9 | 20 | -2.1 | 7226F0E87E904E17A40A795A7143EABA |  | R22 | Non-TXV |  | 5.614% | 0.94386 | 10.79% | [5 empty] | Non-TXV | 5.614%
Marysville | CA | 95901-8235 |  | 2013-07-01 | 2013-07-01 09:30 | 2013-07-01 10:01 | YORK - H1RA048S06D | 117 | -6.9 | Yes | Yes | 19 | 20.4 | -1.4 | CF0EE25582884534A3E3B498DFA0527C |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Fresno | CA | 93720-2452 |  | 2013-07-15 | 2013-07-15 09:34 | 2013-07-15 10:02 | YORK - CMA02411A | 91 | 4.1 | Yes | Yes | 16.8 | 19.8 | -3 | 683AA4ABDEAC4A01BFF29D2AA3CB245E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.505% | 0.95495 | 8.659% | [5 empty] | Non-TXV | 4.505%
Tracy | CA | 95376-3453 |  | 2013-08-01 | 2013-08-01 10:30 | 2013-08-01 10:56 | GOODMAN - CBD | 64 | 6.3 | Yes | Yes | 17.4 | 19.5 | -2.1 | 2E8925CE7BBC4F98B25655FDF43E1ED0 |  | R22 | Non-TXV |  | 9.844% | 0.90156 | 18.92% | [5 empty] | Non-TXV | 9.844%
Fresno | CA | 93711-0714 |  | 2013-07-19 | 2013-07-19 11:45 | 2013-07-19 11:47 | OTHER - UNK | 68 | 11.5 | Yes | Yes | 20.8 | 18.1 | 2.7 | 763C42CD8B3A493196926015D3B83B99 |  | R22 | Non-TXV |  | 16.91% | 0.83088 | 32.5% | [5 empty] | Non-TXV | 16.91%
Merced | CA | 95340-3262 |  | 2013-07-09 | 2013-07-09 10:16 | 2013-07-09 10:19 | GOODMAN - GCS130361GB | 77 | 2.6 | Yes | Yes | 21 | 21.3 | -0.3 | E0B6DC3C48564951B7BCDAF8C04F4BA4 |  | R410A | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Fresno | CA | 93705-1915 |  | 2013-10-02 | 2013-10-02 08:07 | 2013-10-02 08:09 | OTHER - 7777UNK | 64 | 2.1 | Yes | Yes | 26 | 20.1 | 5.9 | 5931561E51E64866ACF67D24FD066A9D |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Stockton | CA | 95219-2424 |  | 2013-07-01 | 2013-07-01 10:22 | 2013-07-01 10:47 | RUUD - UAKA-042JAZ | 79 | 2.6 | Yes | Yes | 21.8 | 18.9 | 2.9 | 6AB3595D24914834BA668052C455BCB1 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Colfax | CA | 95713-0000 |  | 2013-07-25 | 2013-07-25 11:42 | 2013-07-25 11:58 | RUUD - URGG-07E36JKR | 75 | 3 | Yes | Yes | 25.5 | 21.5 | 4.1 | C2365F581A7148B8B13F1D0AC7DEBB19 |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Oroville | CA | 95965-4181 |  | 2013-08-12 | 2013-08-12 09:34 | 2013-08-12 09:52 | TRANE - 2TTR2036A1000AA | 96 | 7 | Yes | Yes | 20.8 | 20.2 | 0.6 | 2E010389BEEA4225A64F119E80042B96 |  | R22 | Non-TXV |  | 7.292% | 0.92708 | 14.01% | [5 empty] | Non-TXV | 7.292%
Merced | CA | 95341-6889 |  | 2013-07-02 | 2013-07-02 11:49 | 2013-07-02 11:52 | YORK - H1DB024S06A | 67 | 2.2 | Yes | Yes | 19.2 | 16.6 | 2.6 | 0EB9AA5BDE734C12B6FCDDF67A3CCB6C |  | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Madera | CA | 93638-3305 |  | 2013-08-10 | 2013-08-10 09:48 | 2013-08-11 01:53 | - | 85 | 2.8 | Yes | Yes | 16.4 | 17.2 | -0.8 | 50B0E24F8F4744ECA390B28574F916C8 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fresno | CA | 93705-0129 |  | 2013-07-30 | 2013-07-30 13:07 | 2013-07-30 13:09 | CARRIER - 38CKC024340 | 54 | 6.3 | Yes | Yes | 21.3 | 22.8 | -1.5 | 7761D966B8AD434CBD4921B849D0EF60 |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Stockton | CA | 95212-3491 |  | 2013-06-27 | 2013-06-27 10:56 | 2013-06-27 11:18 | BDP - 561CJ042-E | 80 | -37.3 | Yes | Yes | 16.4 | 16.6 | -0.2 | E206E60BF2AB464486474433C3A2A22F |  | R22 | TXV |  | -46.62% | 1.4663 | 13.06% |  |  |  |  | TXV |  |  | -46.62%
Fresno | CA | 93720-2469 |  | 2013-08-12 | 2013-08-12 11:00 | 2013-08-12 11:38 | GOODMAN - CK30-1A | 78 | 2.9 | Yes | Yes | 16 | 18.3 | -2.3 | E973EF13836148928B95A08B6B346652 |  | R22 | Non-TXV |  | 3.718% | 0.96282 | 7.145% | [5 empty] | Non-TXV | 3.718%
Stockton | CA | 95206-6345 |  | 2013-07-03 | 2013-07-03 10:59 | 2013-07-03 11:20 | UNITARY PRODUCTS GROUP - H2RC036S06A | 83 | 4 | Yes | Yes | 19.7 | 20 | -0.3 | 3E27D4CD6BB048269A9D75F96ADCA355 |  | R22 | TXV |  | 4.819% | 0.95181 | 9.262% | [5 empty] | TXV | 4.819%
Fresno | CA | 93722-4344 |  | 2013-07-18 | 2013-07-18 14:08 | 2013-07-18 14:15 | OTHER - 585CJ030075 | 78 | 12.4 | Yes | Yes | 20.9 | 19.3 | 1.6 | 9635E30BEC9F4512822243F0BF714B9C |  | R22 | Non-TXV |  | 15.9% | 0.84103 | 30.55% | [5 empty] | Non-TXV | 15.9%
Merced | CA | 95340-3317 |  | 2013-11-20 | 2013-11-20 09:44 | 2013-11-20 09:44 | GOODMAN - PGB036075-1 | 60 | 0 | Yes | Yes | 30.1 | 19.1 | 11 | F45B7275B2114D199304CB07AC70B06E | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-2577 |  | 2013-07-17 | 2013-07-17 18:00 | 2013-07-17 18:00 | YORK - D2NX036N065-6X | 156 | 0 | Yes | Yes | 17.6 | 19.5 | -1.9 | 33C354ADD5054F408995D7FD72FC692C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-9741 |  | 2013-08-09 | 2013-08-09 16:23 | 2013-08-09 16:23 | CARRIER - 48GP-048090301 | 150 | 0 | Yes | Yes | 20 | 20.2 | -0.2 | AD2FBFDF850C4DEF8A5AA96B554296B3 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-3206 |  | 2013-07-11 | 2013-07-11 13:16 | 2013-07-11 13:41 | RHEEM - RRNL-B036JK06X | 92 | 4.8 | Yes | Yes | 21.9 | 21.5 | 0.4 | AB6E97A3FC784FA58B666C6292A97B23 |  | R410A | Non-TXV |  | 5.217% | 0.94783 | 10.03% | [5 empty] | Non-TXV | 5.217%
Manteca | CA | 95337-6677 |  | 2013-07-19 | 2013-07-19 15:10 | 2013-07-19 15:26 | BRYANT - 563CN036-D | 101 | 3.1 | Yes | Yes | 20.2 | 19.7 | 0.5 | E0D01EC7E5B14504B1B30E4849A873D3 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Atwater | CA | 95301-4235 |  | 2013-07-11 | 2013-07-11 08:21 | 2013-07-11 08:23 | YORK - D1NH030N05606A | 69 | 6.3 | Yes | Yes | 23.5 | 19.4 | 4.1 | AA5131F3DB9641BE803486D9A0011F8B |  | R22 | Non-TXV |  | 9.13% | 0.9087 | 17.55% | [5 empty] | Non-TXV | 9.13%
Fresno | CA | 93705-1913 |  | 2013-08-07 | 2013-08-07 11:28 | 2013-08-07 11:33 | OTHER - BRCS0181BD | 54 | 1.7 | Yes | Yes | 21.6 | 20.1 | 1.5 | 26607E160FC044BB9CA5C9DE88D8C67D |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Manteca | CA | 95336-4562 |  | 2013-07-10 | 2013-07-10 12:41 | 2013-07-10 13:08 | GOODMAN - CKL18-1B | 85 | 3.6 | Yes | Yes | 18.4 | 20.6 | -2.2 | 63581325F9344B60B0D4740FA3DF1800 |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Stockton | CA | 95206-6346 |  | 2013-07-03 | 2013-07-03 09:37 | 2013-07-03 09:57 | YORK - H2RC042S06A | 107 | 3.6 | Yes | Yes | 22.6 | 19.8 | 2.8 | 1FEA872254184EF3836B4B8706639717 |  | R22 | Non-TXV |  | 3.364% | 0.96636 | 6.466% | [5 empty] | Non-TXV | 3.364%
Fresno | CA | 93722-6758 |  | 2013-07-19 | 2013-07-19 08:15 | 2013-07-19 08:17 | YORK - D2GA036N04806C | 84 | 10.6 | Yes | Yes | 20.7 | 19.3 | 1.4 | 1AEE6CE4836C4ED88DFBB909CED8DDEA |  | R22 | Non-TXV |  | 12.62% | 0.87381 | 24.25% | [5 empty] | Non-TXV | 12.62%
Fresno | CA | 93727-3128 |  | 2013-07-12 | 2013-07-12 10:47 | 2013-07-12 11:25 | PAYNE - N/A | 120 | 8.6 | Yes | Yes | 17.9 | 20.8 | -2.9 | 8CDAA9C29E7040908060F55E5F708F2F |  | R22 | Non-TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | Non-TXV | 7.167%
Marysville | CA | 95901-9597 |  | 2013-07-02 | 2013-07-02 08:51 | 2013-07-02 08:51 | BRYANT - 539GN060-A | 210 | 0 | Yes | Yes | 22 | 17.9 | 4.1 | D372B0F13D754AD294E65528D1DBC5F6 |  | R410A | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3103 |  | 2013-07-19 | 2013-07-19 10:24 | 2013-07-19 10:49 | UNITARY PRODUCTS GROUP - `AC030M1021A | 57 | 1.7 | Yes | Yes | 23 | 18.7 | 4.3 | 8FAF2B8E70244DBF9C8226D9B376C4EC |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Stockton | CA | 95206-6041 |  | 2013-06-27 | 2013-06-27 15:37 | 2013-06-27 16:03 | YORK - H2RA030S06D | 62 | 4.8 | Yes | Yes | 17.3 | 18.3 | -1 | 121713B6993C4E0F9BCCC72B7DCE0DFF |  | R22 | Non-TXV |  | 7.742% | 0.92258 | 14.88% | [5 empty] | Non-TXV | 7.742%
Fresno | CA | 93703-2619 |  | 2013-08-08 | 2013-08-08 09:13 | 2013-08-08 09:16 | RHEEM - RRPLB030JK06X | 76 | 3.2 | Yes | Yes | 18.4 | 18.2 | 0.2 | 45B96597F8934247A15EA4ECC52FEC24 |  | R410A | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Oroville | CA | 95965-4213 |  | 2013-07-26 | 2013-07-26 08:23 | 2013-07-26 08:41 | RUUD - 13AJA42A01757 | 87 | 3 | Yes | Yes | 23.1 | 19.3 | 3.8 | 2283D7BE241B472A9AB824B188DE26F4 |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Los Banos | CA | 93635-3213 |  | 2013-07-08 | 2013-07-08 14:08 | 2013-07-08 14:11 | CARRIER - 48SDN042060311 | 120 | 16.7 | Yes | Yes | 29.4 | 24.2 | 5.2 | D1680B2AADA54E278A85C3D6FFF3E2F0 |  | R22 | Non-TXV |  | 13.92% | 0.86083 | 26.74% | [5 empty] | Non-TXV | 13.92%
Sanger | CA | 93657-2004 |  | 2013-07-22 | 2013-07-22 12:04 | 2013-07-22 12:24 | BDP - 585B0428100YACR | 89 | 2.8 | Yes | Yes | 20 | 21.2 | -1.2 | 1C29EBF5E6304480A8E4E782AAAE9EA9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.146% | 0.96854 | 6.046% | [5 empty] | Non-TXV | 3.146%
Fresno | CA | 93711-1308 |  | 2013-07-19 | 2013-07-19 14:35 | 2013-07-19 14:35 | TRANE - 4TTX3036A1000AA | 78 | 0 | Yes | Yes | 17.2 | 19.9 | -2.7 | 065A4EA9A18345E7AC117098A5C1E458 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6566 |  | 2013-07-17 | 2013-07-17 10:51 | 2013-07-17 10:53 | BDP - 598AN036 | 182 | 15.2 | Yes | Yes | 20 | 19.9 | 0.1 | C587FC0B581341E3A953A147E7A7BC6F |  | R22 | Non-TXV |  | 8.352% | 0.91648 | 16.05% | [5 empty] | Non-TXV | 8.352%
Stockton | CA | 95210-3120 |  | 2013-08-16 | 2013-08-16 12:28 | 2013-08-16 12:48 | WHIRLPOOL - UNK | 68 | 6.2 | Yes | Yes | 20.3 | 21.1 | -0.8 | 7EE20876AAC64A9396436392BC9D6220 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.118% | 0.90882 | 17.52% | [5 empty] | Non-TXV | 9.118%
Fresno | CA | 93702-3837 |  | 2013-07-11 | 2013-07-11 10:45 | 2013-07-11 10:49 | GOODMAN - GPG13480701AC | 145 | 6.7 | Yes | Yes | 26 | 20.4 | 5.6 | 97A9B5D7EDB04EBF877AA242A6970F12 |  | R22 | Non-TXV |  | 4.621% | 0.95379 | 8.88% | [5 empty] | Non-TXV | 4.621%
Fresno | CA | 93722-4363 |  | 2013-07-16 | 2013-07-16 12:13 | 2013-07-16 12:15 | HEIL - PGAA36C1K1 | 77 | 8.7 | Yes | Yes | 22.4 | 19.8 | 2.6 | B522626172FD4FD6BDA29848A4EBCB49 |  | R22 | Non-TXV |  | 11.3% | 0.88701 | 21.71% | [5 empty] | Non-TXV | 11.3%
Marysville | CA | 95901-8235 |  | 2013-07-01 | 2013-07-01 10:06 | 2013-07-01 10:27 | YORK - UNK | 85 | 2.9 | Yes | Yes | 19 | 19.5 | -0.5 | C83545D26F4243B1A89A3FE80408684A |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Reedley | CA | 93654-3511 |  | 2013-08-08 | 2013-08-08 11:48 | 2013-08-08 12:46 | BDP - 585ANW030060YACR | 50 | 3.9 | Yes | Yes | 18.5 | 21 | -2.5 | 772B783199984D6DA09E851FB95DC586 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.8% | 0.922 | 14.99% | [5 empty] | Non-TXV | 7.8%
Placerville | CA | 95667-8179 |  | 2013-08-28 | 2013-08-28 14:12 | 2013-08-28 14:12 | GOODMAN - CL048-1B | 225 | 0 | Yes | Yes | 21.9 | 20.2 | 1.8 | C75BBA4E38944B98B24C56D795F4BC19 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-3814 |  | 2013-07-12 | 2013-07-12 10:42 | 2013-07-12 11:10 | GOODMAN - GSX130241DA | 76 | -7.2 | Yes | Yes | 16.1 | 18.7 | -2.6 | D9ED52EDB52F4EB988FB1F4C41BAB327 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | -9.474% | 1.0947 | 2.653% |  |  |  |  | Non-TXV |  |  | -9.474%
Auburn | CA | 95603-0000 |  | 2013-06-28 | 2013-06-28 14:16 | 2013-06-28 14:16 | OTHER - UNK | 64 | 0 | Yes | Yes | 18.2 | 21 | -2.8 | 73BCAFC7666D4FD69628DF535F42AD8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1214 |  | 2013-07-12 | 2013-07-12 14:02 | 2013-07-12 14:21 | YORK - D1NP036N05606A | 106 | 3.6 | Yes | Yes | 16.2 | 19.1 | -2.9 | 5007127B3600423EAF07CF0CCD021750 |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Oroville | CA | 95965-3900 |  | 2013-07-26 | 2013-07-26 20:54 | 2013-07-26 21:11 | TRANE - 2TTB2036A1000AA | 102 | 17.6 | Yes | Yes | 17.5 | 20.1 | -2.6 | EB3C8024CD3646589A1C543402173141 |  | R22 | Non-TXV |  | 17.25% | 0.82745 | 33.16% | [5 empty] | Non-TXV | 17.25%
Marysville | CA | 95901-8338 |  | 2013-08-09 | 2013-08-09 10:09 | 2013-08-09 10:36 | YORK - H2RD042S06B | 141 | 5.1 | Yes | Yes | 17 | 18.8 | -1.8 | FD2AEBE9F8314B1286E75CC85B8495C5 |  | R22 | TXV |  | 3.617% | 0.96383 | 6.951% | [5 empty] | TXV | 3.617%
Parlier | CA | 93648-2862 |  | 2013-08-28 | 2013-08-28 11:47 | 2013-08-28 12:22 | DUCANE - 2AC13B24P-1A | 89 | 6.6 | Yes | Yes | 18 | 20.4 | -2.4 | CA21C62FACBD4459A74AE51B516B4809 |  | R22 | Non-TXV |  | 7.416% | 0.92584 | 14.25% | [5 empty] | Non-TXV | 7.416%
Stockton | CA | 95210-1540 |  | 2013-06-26 | 2013-06-26 12:13 | 2013-06-26 12:35 | PAYNE - UNK | 80 | 2.8 | Yes | Yes | 18 | 16.6 | 1.4 | 6CAF7A7688C144DF9BEF8DD1A89ABE7C |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Selma | CA | 93662-2804 |  | 2013-09-05 | 2013-09-05 14:19 | 2013-09-05 15:09 | RHEEM - N/A | 85 | 2.7 | Yes | Yes | 18.5 | 20.1 | -1.6 | 408B744F516744C29FDB70F6494C2AC2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Chico | CA | 95973-0427 |  | 2013-08-21 | 2013-08-21 11:44 | 2013-08-21 22:02 | BRYANT - 552AND48-E | 87 | 3.4 | Yes | Yes | 22 | 21 | 1 | 8DC8339409CC46ABBC01E9CF5D2F1AD1 |  | R410A | Non-TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | Non-TXV | 3.908%
Madera | CA | 93638-3124 |  | 2013-07-17 | 2013-07-17 16:01 | 2013-07-17 16:01 | YORK - DCYZ-F024NO45A | 58 | 0 | Yes | Yes | 15.7 | 17.5 | -1.8 | 8A9AB40A49C64EA6A7941AC3AD9D2B0D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Laton | CA | 93242-9542 |  | 2013-09-11 | 2013-09-11 13:51 | 2013-09-11 15:53 | RHEEM - RRKA0A042JK08X | 69 | 3.1 | Yes | Yes | 15.5 | 18 | -2.5 | CE2AEEF181BC4FAEBF3510D06ACBC7CA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.493% | 0.95507 | 8.634% | [5 empty] | Non-TXV | 4.493%
Fresno | CA | 93705-0118 |  | 2013-07-30 | 2013-07-30 14:00 | 2013-07-30 14:02 | GOODMAN - CE251EB | 66 | 12.2 | Yes | Yes | 25.4 | 21 | 4.4 | C083FAF8B1AB4AF5BDCE569A954AE0DB |  | R22 | Non-TXV |  | 18.48% | 0.81515 | 35.52% | [5 empty] | Non-TXV | 18.48%
Madera | CA | 93638-5506 |  | 2013-08-19 | 2013-08-19 09:56 | 2013-08-19 09:58 | YORK - D1NA030N03606C | 76 | 10 | Yes | Yes | 24.3 | 20.4 | 3.9 | A11798DBCDE244949411C71FCD0877A5 |  | R22 | Non-TXV |  | 13.16% | 0.86842 | 25.29% | [5 empty] | Non-TXV | 13.16%
Los Banos | CA | 93635-2969 |  | 2013-07-02 | 2013-07-02 08:24 | 2013-07-02 08:35 | DAY & NIGHT - UNK | 70 | 8.2 | Yes | Yes | 26 | 20.1 | 5.9 | 51B7D044C98640B3911269B44E9B6E83 |  | R22 | Non-TXV |  | 11.71% | 0.88286 | 22.51% | [5 empty] | Non-TXV | 11.71%
Fresno | CA | 93705-2715 |  | 2013-08-06 | 2013-08-06 10:59 | 2013-08-06 11:01 | RUUD - 7777UNK | 90 | 4.3 | Yes | Yes | 22 | 19.9 | 2.1 | D224D45A5BAF4C8DB786E691A538CD21 |  | R22 | Non-TXV |  | 4.778% | 0.95222 | 9.182% | [5 empty] | Non-TXV | 4.778%
Stockton | CA | 95206-6109 |  | 2013-07-02 | 2013-07-02 08:56 | 2013-07-02 09:19 | RUUD - UAKA-048JAZ | 85 | 2.8 | Yes | Yes | 23.9 | 18 | 5.9 | E3B127CC68AA4356AC09266C0B0C59BC |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fresno | CA | 93727-6483 |  | 2013-07-12 | 2013-07-12 09:58 | 2013-07-12 10:18 | LENNOX - 12ACB36-4P | 103 | 4.6 | Yes | Yes | 18.1 | 20.7 | -2.6 | D3AAE1FE301B4DBB85120DBA3335CD95 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.466% | 0.95534 | 8.583% | [5 empty] | Non-TXV | 4.466%
Cameron Park | CA | 95682-7405 |  | 2013-07-08 | 2013-07-08 14:24 | 2013-07-08 14:51 | PAYNE - 540AJ018 | 83 | -5.9 | Yes | Yes | 20.5 | 20.9 | -0.4 | 5ADC1E3FFFA24C419A25FC9111C61C3D |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Stockton | CA | 95204-4203 |  | 2013-07-01 | 2013-07-01 11:52 | 2013-07-01 12:11 | RHEEM - RRKA-A024JK06E | 50 | 2.8 | Yes | Yes | 21.1 | 18.3 | 2.9 | 344DD2528D6D4BBB88FF8A20B6294B97 |  | R22 | Non-TXV |  | 5.6% | 0.944 | 10.76% | [5 empty] | Non-TXV | 5.6%
Clovis | CA | 93612-2190 |  | 2013-06-28 | 2013-06-28 16:03 | 2013-06-28 16:25 | DAY & NIGHT - N/A | 60 | 4.4 | Yes | Yes | 21.7 | 18.8 | 2.9 | 85493C200765455C8BC1712DF673F949 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Sanger | CA | 93657-1926 |  | 2013-07-22 | 2013-07-22 10:56 | 2013-07-22 11:07 | UNITARY PRODUCTS GROUP - TCGD48S41S3HA | 73 | 3.8 | Yes | Yes | 17 | 19.8 | -2.8 | 798789DF1FB5465DBF04C9ED961C39AB |  | R410A | TXV |  | 5.205% | 0.94795 | 10% | [5 empty] | TXV | 5.205%
Fresno | CA | 93727-2027 |  | 2013-07-12 | 2013-07-12 13:25 | 2013-07-12 14:22 | UNITARY PRODUCTS GROUP - DAYP-F048N110A | 132 | 8.5 | Yes | Yes | 17.4 | 20.2 | -2.8 | 93801F1D7D784BC1938A10696C2FD62D |  | R22 | Non-TXV |  | 6.439% | 0.93561 | 12.38% | [5 empty] | Non-TXV | 6.439%
Sutter Creek | CA | 95685-4318 |  | 2013-09-10 | 2013-09-10 12:53 | 2013-09-10 13:34 | TRANE - TTR042C100A0 | 110 | 10.7 | Yes | Yes | 25.7 | 21.5 | 4.2 | 31115B8483FE4C23B4B9EA0958A794A3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.727% | 0.90273 | 18.69% | [5 empty] | Non-TXV | 9.727%
Kingsburg | CA | 93631-1114 |  | 2013-08-09 | 2013-08-09 17:15 | 2013-08-09 17:40 | LENNOX - PGE10B36D075A-3A | 58 | 8.5 | Yes | Yes | 18.6 | 19 | -0.4 | 54017B9B36C64424937F8194FC8D273E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.66% | 0.85345 | 28.16% | [5 empty] | Non-TXV | 14.66%
Fresno | CA | 93726-7416 |  | 2013-07-30 | 2013-07-30 11:41 | 2013-07-30 11:56 | LENNOX - HS254111P | 129 | 16.3 | Yes | Yes | 22.6 | 19.2 | 3.4 | BF53E1163548475CB1ED9C1C66C79B15 |  | R22 | Non-TXV |  | 12.64% | 0.87364 | 24.28% | [5 empty] | Non-TXV | 12.64%
Stockton | CA | 95210-4487 |  | 2013-07-31 | 2013-07-31 08:43 | 2013-07-31 09:06 | PAYNE - 563AN030-A | 101 | -5.9 | Yes | Yes | 18.8 | 18.2 | 0.6 | 6F87CF57E2D74964B14913138EC8EAC4 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Merced | CA | 95348-9521 |  | 2013-07-24 | 2013-07-24 10:18 | 2013-07-24 10:33 | GOODMAN - CKL421B | 115 | 15.2 | Yes | Yes | 19.5 | 21.5 | -2 | A30288919B034D98B1C09FC63C3D3664 |  | R22 | Non-TXV |  | 13.22% | 0.86783 | 25.4% | [5 empty] | Non-TXV | 13.22%
Stockton | CA | 95206-4672 |  | 2013-07-17 | 2013-07-17 12:29 | 2013-07-17 12:50 | PAYNE - PA13NR042-J | 112 | 5.2 | Yes | Yes | 17.9 | 19.3 | -1.4 | 2D3E7666945E4275A71B04884634DC21 |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
El Dorado | CA | 95623-4232 |  | 2013-08-15 | 2013-08-15 11:56 | 2013-08-15 12:34 | YORK - FADED UNK | 67 | 8.7 | Yes | Yes | 26.6 | 23 | 3.6 | EA8D87F9130F480CBE78E1F5D6D426DC |  | R22 | Non-TXV |  | 12.99% | 0.87015 | 24.95% | [5 empty] | Non-TXV | 12.99%
Madera | CA | 93637-5421 |  | 2013-07-26 | 2013-07-26 11:20 | 2013-07-26 11:37 | YORK - DINA 030403606 | 76 | 3.8 | Yes | Yes | 17.9 | 19.7 | -1.8 | 11F54C8DDDBA497FB0BCB6F4A6BE57A8 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Merced | CA | 95340-3245 |  | 2013-07-01 | 2013-07-01 17:54 | 2013-07-01 17:59 | PAYNE - 2460YAC1081 | 56 | 8.7 | Yes | Yes | 22.1 | 22.1 | 0 | 02942843816F4BC6AD4A0D4A1273E1B2 |  | R22 | Non-TXV |  | 15.54% | 0.84464 | 29.86% | [5 empty] | Non-TXV | 15.54%
Fresno | CA | 93727-6479 |  | 2013-07-15 | 2013-07-15 17:40 | 2013-07-15 17:40 | LENNOX - 12ACB42-4P | 125 | 0 | Yes | Yes | 22 | 20.2 | 1.8 | A28D18A59C084240A600B79A259D4099 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-7405 |  | 2013-07-08 | 2013-07-08 14:53 | 2013-07-08 15:11 | PAYNE - 540AJ018 | 83 | 5.5 | Yes | Yes | 18 | 20.2 | -2.2 | 73DD16147878447B881C1FF9CAEF1613 |  | R22 | Non-TXV |  | 6.627% | 0.93373 | 12.73% | [5 empty] | Non-TXV | 6.627%
Fresno | CA | 93728-2222 |  | 2013-08-12 | 2013-08-12 10:31 | 2013-08-12 12:05 | RHEEM - RRNA-B030JK6X | 72 | 3.6 | Yes | Yes | 23.4 | 19.9 | 3.5 | 8068C71DF02E4CEBAF36A51A4C8CF83D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95205-4712 |  | 2013-07-12 | 2013-07-12 13:21 | 2013-07-12 14:11 | BDP - B88ANW024060ADAD | 61 | 13.4 | Yes | Yes | 17.8 | 20.4 | -2.6 | A23B275C1E284B629FA220DA9C19903C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.97% | 0.78033 | 42.22% | [5 empty] | Non-TXV | 21.97%
Stockton | CA | 95206-6140 |  | 2013-07-10 | 2013-07-10 09:19 | 2013-07-10 09:47 | GOODMAN - CKJ36-1AB | 97 | -5.7 | Yes | Yes | 22.9 | 20.6 | 2.4 | 13084C590A8841B281D852C45B69BD38 |  | R22 | Non-TXV |  | -5.876% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.876%
Merced | CA | 95340-2210 |  | 2013-06-28 | 2013-06-28 12:45 | 2013-06-28 12:47 | LUXAIRE - 60WE24G1 | 55 | 11.9 | Yes | Yes | 25.2 | 20.2 | 5 | B712DE03A938467C943EBF098AA7A037 |  | R22 | Non-TXV |  | 21.64% | 0.78364 | 41.58% | [5 empty] | Non-TXV | 21.64%
Greenwood | CA | 95635-0000 |  | 2013-08-16 | 2013-08-16 09:35 | 2013-08-16 09:35 | YORK - BRCS0421BD | 84 | 0 | Yes | Yes | 24.2 | 20.1 | 4.1 | B45C416EC1244D16A743CA093F420B5B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3271 |  | 2013-07-08 | 2013-07-08 15:20 | 2013-07-08 15:35 | RUUD - UAKA060JAS | 112 | 16.3 | Yes | Yes | 28.1 | 24.2 | 3.9 | 875A2D6893E34A6FB71E51A20A915B9D |  | R22 | Non-TXV |  | 14.55% | 0.85446 | 27.97% | [5 empty] | Non-TXV | 14.55%
Stockton | CA | 95210-1527 |  | 2013-08-21 | 2013-08-21 08:48 | 2013-08-21 09:05 | RHEEM - RRPL-B030JK06X | 76 | 3 | Yes | Yes | 18.4 | 17.7 | 0.7 | 43046FD1186A4311854B466C2235667F |  | R410A | TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | TXV | 3.947%
Stockton | CA | 95203-1033 |  | 2013-07-25 | 2013-07-25 14:30 | 2013-07-25 15:25 | PAYNE - PAA110JA024-A | 72 | -7.2 | Yes | Yes | 17.4 | 16.1 | 1.3 | 0FD44FDFE16E483E928F03BADE20150E |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Clovis | CA | 93612-2395 |  | 2013-08-29 | 2013-08-29 16:49 | 2013-08-29 17:18 | BDP - 585EJW030050ABAF | 58 | 8.8 | Yes | Yes | 22 | 20.7 | 1.3 | A856C68592A141F1BB0FE309E32A7355 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.17% | 0.84828 | 29.16% | [5 empty] | Non-TXV | 15.17%
Stockton | CA | 95204-1802 |  | 2013-07-09 | 2013-07-09 15:22 | 2013-07-09 15:22 | DAY & NIGHT - 585HBW060100ABAG | 160 | 0 | Yes | Yes | 24.8 | 21.2 | 3.7 | D8D01971C422474EA839EA7E04232BCA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Escalon | CA | 95320-8550 |  | 2013-07-12 | 2013-07-12 15:20 | 2013-07-12 15:56 | BDP - 563CN030-A | 103 | 3 | Yes | Yes | 25.8 | 23.4 | 2.5 | 61DA153AF38742CEA01049B3AC58FE85 |  | R22 | Non-TXV |  | 2.913% | 0.97087 | 5.597% | [5 empty] | Non-TXV | 2.913%
Kingsburg | CA | 93631-2073 |  | 2013-08-01 | 2013-08-01 16:37 | 2013-08-01 16:58 | PAYNE - N/A | 90 | 3.6 | Yes | Yes | 17 | 18 | -1 | 7D1244BFB4C5460498CC2BF4C3631EDA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Yuba City | CA | 95993-9286 |  | 2013-08-07 | 2013-08-07 08:51 | 2013-08-07 09:15 | LENNOX - 13ACC-036-230-01 | 115 | 4.2 | Yes | Yes | 16.8 | 19.3 | -2.5 | 5F4264DB32D74616B0F656542C357D8C |  | R22 | TXV |  | 3.652% | 0.96348 | 7.019% | [5 empty] | TXV | 3.652%
Fresno | CA | 93726-1245 |  | 2013-07-29 | 2013-07-29 09:47 | 2013-07-29 09:48 | GOODMAN - GPG13240451CB | 74 | 7.1 | Yes | Yes | 22.8 | 19.3 | 3.5 | E586E6DC4A66411BB194E7120D1714F8 |  | R22 | Non-TXV |  | 9.595% | 0.90405 | 18.44% | [5 empty] | Non-TXV | 9.595%
Stockton | CA | 95210-2113 |  | 2013-07-01 | 2013-07-01 09:40 | 2013-07-01 09:58 | CARRIER - 38EB024300 | 53 | -3.1 | Yes | Yes | 23.2 | 18.8 | 4.4 | 652A122233F8492DB546F3B82728328C |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Foresthill | CA | 95631-9356 |  | 2013-10-14 | 2013-10-14 12:41 | 2013-10-14 12:41 | PAYNE - PA13R024-C | 112 | 0 | Yes | Yes | 26.1 | 20.9 | 5.2 | 5A1A0CA8E9534680B51EF4A63AF6C635 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9627 |  | 2013-08-07 | 2013-08-07 14:38 | 2013-08-07 15:08 | CARRIER - 48TEX036-301 | 104 | 3.8 | Yes | Yes | 17 | 18.7 | -1.7 | 43FFAEF1665C498E9C3D2B6634D01AD7 |  | R22 | TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | TXV | 3.654%
Stockton | CA | 95219-5486 |  | 2013-07-29 | 2013-07-29 11:58 | 2013-07-29 12:22 | CARRIER - 3EN018310SM | 55 | 2.9 | Yes | Yes | 20.8 | 18.8 | 2 | AD6700027B534AC8B1E50AE3E11D1025 |  | R22 | Non-TXV |  | 5.273% | 0.94727 | 10.13% | [5 empty] | Non-TXV | 5.273%
Red Bluff | CA | 96080-4537 |  | 2013-09-20 | 2013-09-20 12:11 | 2013-09-20 12:30 | CARRIER - 38TXA060350 | 181 | 6.8 | Yes | Yes | 24.4 | 18.7 | 5.7 | 5F45A1AE6C144E27859BC2C1FEBD9A3E |  | R410A | TXV |  | 3.757% | 0.96243 | 7.22% | [5 empty] | TXV | 3.757%
Marysville | CA | 95901-4010 |  | 2013-07-12 | 2013-07-12 13:30 | 2013-07-12 13:30 | BRYANT - 582ANW0360907634-1 | 60 | 0 | Yes | Yes | 22 | 20.2 | 1.8 | 247F671081674534B85A393A24DF5A79 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1242 |  | 2013-08-23 | 2013-08-23 17:06 | 2013-08-23 17:07 | ICP - PGF024K060A | 58 | 6.9 | Yes | Yes | 24.1 | 23.1 | 1 | 3E7CACABD3FA4DD2B40F4CF7B51BA90E |  | R22 | Non-TXV |  | 11.9% | 0.88103 | 22.86% | [5 empty] | Non-TXV | 11.9%
Stockton | CA | 95206-3868 |  | 2013-07-16 | 2013-07-16 15:41 | 2013-07-16 15:41 | GOODMAN - CLJ42-1A | 98 | 0 | Yes | Yes | 21.6 | 19.6 | 2.1 | 0EF8BE3F6C474A3C9CEA5FDF93695283 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6673 |  | 2013-06-29 | 2013-06-29 18:43 | 2013-06-29 19:13 | LENNOX - 12CHP042-3PA | 172 | 6.1 | Yes | Yes | 24.7 | 18.8 | 5.9 | 6ADF250CB5424CB680EBE399FFC6BB31 |  | R22 | Non-TXV |  | 3.547% | 0.96453 | 6.816% | [5 empty] | Non-TXV | 3.547%
Los Banos | CA | 93635-3125 |  | 2013-07-08 | 2013-07-08 10:59 | 2013-07-08 11:03 | BRYANT - 113ANA048 | 112 | 5.4 | Yes | Yes | 27.6 | 23 | 4.6 | DDB04D56493042FF871CA29920EE6A4A |  | R410A | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Loomis | CA | 95650-9227 |  | 2013-09-13 | 2013-09-13 09:44 | 2013-09-13 09:44 | LENNOX - HP13-030-230-01 | 132 | 0 | Yes | Yes | 20.6 | 18.7 | 1.9 | 35C5421C124B40128FA43A9585A48BF3 |  | R22 | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-5451 |  | 2013-07-15 | 2013-07-15 12:30 | 2013-07-15 12:51 | RUUD - URKA-A030JK06K | 54 | 2.6 | Yes | Yes | 21 | 19.7 | 1.3 | 7CC287DBAB4B439FAFEAE2FDEBE7FE4B |  | R22 | TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | TXV | 4.815%
Fresno | CA | 93727-6335 |  | 2013-07-15 | 2013-07-15 18:24 | 2013-07-15 18:33 | GOODMAN - GSC130481AA | 158 | 5.1 | Yes | Yes | 23 | 17.5 | 5.6 | A9F390CC5B4F4B5AABC0C4E09C0EBBB6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.228% | 0.96772 | 6.203% | [5 empty] | Non-TXV | 3.228%
Fresno | CA | 93727-6335 |  | 2013-07-15 | 2013-07-15 18:35 | 2013-07-15 23:14 | GOODMAN - GSC130481AA | 158 | 5.7 | Yes | Yes | 20.8 | 17 | 3.8 | 7891CC2C80684DFAAA689F4B08504E9E |  | R22 | Non-TXV |  | 3.608% | 0.96392 | 6.933% | [5 empty] | Non-TXV | 3.608%
Stockton | CA | 95209-4006 |  | 2013-07-24 | 2013-07-24 13:09 | 2013-07-24 13:28 | BDP - 567C042RCU | 112 | 4.1 | Yes | Yes | 23.9 | 19.7 | 4.2 | A6DC1299EA9E47248F40A473F2BDB16E |  | R22 | Non-TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | Non-TXV | 3.661%
Merced | CA | 95340-5463 |  | 2013-07-02 | 2013-07-02 12:07 | 2013-07-02 12:21 | OTHER - DRCS0301BD | 76 | 9.3 | Yes | Yes | 21.2 | 20.6 | 0.6 | 60C101EBB4644BD8AF48F321CF1C5A4C |  | R22 | Non-TXV |  | 12.24% | 0.87763 | 23.52% | [5 empty] | Non-TXV | 12.24%
Ione | CA | 95640-4502 |  | 2013-08-02 | 2013-08-02 15:08 | 2013-08-02 15:32 | YORK - H1RD043S06G | 152 | 12.5 | Yes | Yes | 20 | 22.5 | -2.5 | D5DA0B83CED745E7B45EA205423BB09B |  | R22 | TXV |  | 8.224% | 0.91776 | 15.8% | [5 empty] | TXV | 8.224%
Los Banos | CA | 93635-3288 |  | 2013-08-14 | 2013-08-14 10:30 | 2013-08-14 10:33 | GOODMAN - CK36-1B | 76 | 5 | Yes | Yes | 21.5 | 20.4 | 1.1 | 61B800FCC6D64F11BA5147EE90F5BFC5 |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Fresno | CA | 93705-5137 |  | 2013-07-19 | 2013-07-19 12:57 | 2013-07-19 12:59 | WESTINGHOUSE - 1E036QDA0N | 130 | 4 | Yes | Yes | 19.9 | 17 | 2.9 | 55CE16F5E1504B05BB8F8DADB990B9D8 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Fresno | CA | 93705-2334 |  | 2013-07-08 | 2013-07-08 18:26 | 2013-07-08 19:52 | GOODMAN - PGB036075-1A | 60 | 5 | Yes | Yes | 27.6 | 21.7 | 5.9 | D70DABF44E88405585848384682E7488 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Winton | CA | 95388-0000 |  | 2013-07-25 | 2013-07-25 18:15 | 2013-07-25 18:31 | DAY & NIGHT - UNK | 57 | 9.4 | Yes | Yes | 19.2 | 22.1 | -2.9 | 6F64E283B0134364A25C08268AA3DF07 |  | R22 | Non-TXV |  | 16.49% | 0.83509 | 31.69% | [5 empty] | Non-TXV | 16.49%
Marysville | CA | 95901-3223 |  | 2013-07-11 | 2013-07-11 15:32 | 2013-07-11 15:50 | GOODMAN - GPG13360701AB | 112 | 4.3 | Yes | Yes | 27 | 21.4 | 5.6 | 842CA039965E45A9A0C25078BFFDA4FB |  | R22 | TXV |  | 3.839% | 0.96161 | 7.378% | [5 empty] | TXV | 3.839%
Magalia | CA | 95954-9341 |  | 2013-07-17 | 2013-07-17 12:27 | 2013-07-17 13:04 | RHEEM - RCGG-05E36JKR | 75 | 7.2 | Yes | Yes | 17.2 | 18.8 | -1.6 | BA85506D9DF14D6CA0219BBA7F88F608 |  | R22 | Non-TXV |  | 9.6% | 0.904 | 18.45% | [5 empty] | Non-TXV | 9.6%
Auburn | CA | 95603-3598 |  | 2013-06-27 | 2013-06-27 09:40 | 2013-06-27 09:40 | DAY & NIGHT - AC1CN042-A | 134 | 0 | Yes | Yes | 23.4 | 19.7 | 3.8 | 8A732940FE174A96BFDDC360D81C9091 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-1814 |  | 2013-07-18 | 2013-07-18 17:22 | 2013-07-18 17:25 | GE - BTD724A100A0 | 68 | 2 | Yes | Yes | 19.9 | 19.6 | 0.3 | BF283119B6EF4EC68087D451DBF30335 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95212-2899 |  | 2013-06-26 | 2013-06-26 12:20 | 2013-06-26 12:41 | YORK - H2RC036S06G | 83 | 3.3 | Yes | Yes | 19.1 | 20.8 | -1.7 | B345C7BF2FC0476AA5CED21B110A062C |  | R22 | Non-TXV |  | 3.976% | 0.96024 | 7.641% | [5 empty] | Non-TXV | 3.976%
Stockton | CA | 95210-1419 |  | 2013-06-27 | 2013-06-27 08:16 | 2013-06-27 08:37 | DAY & NIGHT - 585EJ030050 | 58 | 2.6 | Yes | Yes | 18.5 | 16.4 | 2.1 | 6EB91814F7CF4710A22DDB147DAB1F59 |  | R22 | Non-TXV |  | 4.483% | 0.95517 | 8.615% | [5 empty] | Non-TXV | 4.483%
Stockton | CA | 95205-0000 |  | 2013-07-11 | 2013-07-11 09:54 | 2013-07-11 10:38 | GMC - GSC130601BC | 169 | 9.4 | Yes | Yes | 23.6 | 19.9 | 3.7 | A2C5465E592B42B1816640CFCFB48B48 |  | R22 | Non-TXV |  | 5.562% | 0.94438 | 10.69% | [5 empty] | Non-TXV | 5.562%
Stockton | CA | 95210-3640 |  | 2013-07-08 | 2013-07-08 13:55 | 2013-07-08 14:21 | RUUD - UAMA-036JAZ | 96 | 3.3 | Yes | Yes | 20 | 21 | -1 | FBF3AC6D2B784C929F2392DFAAF8E9FC |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Merced | CA | 95340-3352 |  | 2013-07-23 | 2013-07-23 18:15 | 2013-07-23 18:17 | TRANE - TTX036C100A | 152 | 5.3 | Yes | Yes | 19.4 | 19.7 | -0.3 | 7389560669EA46828CA272A73A4B8C4A |  | R22 | Non-TXV |  | 3.487% | 0.96513 | 6.701% | [5 empty] | Non-TXV | 3.487%
Chico | CA | 95973-0370 |  | 2013-07-09 | 2013-07-09 20:10 | 2013-07-09 20:28 | COLEMAN - BRC0030B | 56 | 0 | Yes | Yes | 20.6 | 22.4 | -1.8 | 487B613E80C44EF2B0325615F80ACEB3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3596 |  | 2013-08-16 | 2013-08-16 09:51 | 2013-08-16 09:53 | GOODMAN - GPG10300701A | 50 | 4.9 | Yes | Yes | 21.7 | 18.2 | 3.5 | 4D551FC40ED3422EB1F77A1DAD6DF1E3 |  | R22 | Non-TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | Non-TXV | 9.8%
Merced | CA | 95340-0707 |  | 2013-06-26 | 2013-06-26 15:04 | 2013-06-26 15:06 | TRANE - TTX048C100A | 160 | 5.4 | Yes | Yes | 24.7 | 19 | 5.7 | 463A8B9076584A7FA009810A964F8C8E |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Marysville | CA | 95901-6859 |  | 2013-07-11 | 2013-07-11 12:24 | 2013-07-11 12:46 | GOODMAN - GSC130301EB | 66 | 9 | Yes | Yes | 17 | 19.9 | -2.9 | F42BC7E262DD4A7C9DFEB2133C5F614A |  | R22 | Non-TXV |  | 13.64% | 0.86364 | 26.21% | [5 empty] | Non-TXV | 13.64%
Fresno | CA | 93726-1247 |  | 2013-07-29 | 2013-07-29 11:29 | 2013-07-29 11:30 | GOODMAN - GPG1324045M41AD | 80 | 7.9 | Yes | Yes | 21.2 | 21 | 0.2 | EB77BB6FA51A47A2BF85CB032EA4FC52 |  | R410A | Non-TXV |  | 9.875% | 0.90125 | 18.98% | [5 empty] | Non-TXV | 9.875%
Chico | CA | 95973-7838 |  | 2013-08-09 | 2013-08-09 14:15 | 2013-08-09 14:34 | ICP - R2H324GKR4 | 70 | 6.8 | Yes | Yes | 18 | 19.6 | -1.6 | 7F146E901E68491480241D23B018E749 |  | R22 | Non-TXV |  | 9.714% | 0.90286 | 18.67% | [5 empty] | Non-TXV | 9.714%
Merced | CA | 95340-3349 |  | 2013-07-11 | 2013-07-11 12:08 | 2013-07-11 12:11 | RHEEM - RRNLB036JK06X | 92 | 8.1 | Yes | Yes | 22.8 | 19.3 | 3.5 | 2CAD01852B9B4770B68E228924B72C4C |  | R410A | Non-TXV |  | 8.804% | 0.91196 | 16.92% | [5 empty] | Non-TXV | 8.804%
Manteca | CA | 95337-8771 |  | 2013-07-24 | 2013-07-24 13:29 | 2013-07-24 13:51 | CARRIER - 24ABA348A310 | 122 | -15 | Yes | Yes | 20.4 | 19.2 | 1.2 | 210DD118270E49FF91EC7447DBDBABEC |  | R410A | TXV |  | -12.3% | 1.123 | 3.443% |  |  |  |  | TXV |  |  | -12.3%
Fresno | CA | 93727-8018 |  | 2013-07-16 | 2013-07-16 15:33 | 2013-07-16 16:11 | CARRIER - 38BRC042340 | 103 | 9.4 | Yes | Yes | 22.8 | 19.8 | 3 | 39BDB08C84534736B453753982F98CE6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.126% | 0.90874 | 17.54% | [5 empty] | Non-TXV | 9.126%
Auburn | CA | 95603-9505 |  | 2013-07-13 | 2013-07-13 11:48 | 2013-07-13 11:48 | AMANA - GSX130601AB | 187 | 0 | Yes | Yes | 22.5 | 22.4 | 0.1 | 8B4E574EFED64454B4DBAE85BF9EFD0C |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0143 |  | 2013-07-30 | 2013-07-30 14:56 | 2013-07-30 14:57 | GOODMAN - CKL241K | 76 | 10.9 | Yes | Yes | 24.6 | 21.7 | 2.9 | FEBA7DA650F44E6EB368CC81B3D9D04F |  | R22 | Non-TXV |  | 14.34% | 0.85658 | 27.56% | [5 empty] | Non-TXV | 14.34%
Fresno | CA | 93726-6038 |  | 2013-07-30 | 2013-07-30 11:08 | 2013-07-30 11:09 | LENNOX - HS94113P | 84 | 6 | Yes | Yes | 23.5 | 20.4 | 3.1 | 44F637D5D61142F78C2F8ADE16D9CB82 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Magalia | CA | 95954-9671 |  | 2013-07-19 | 2013-07-19 09:43 | 2013-07-19 10:17 | PAYNE - PA10JA036A | 83 | 6.4 | Yes | Yes | 24.6 | 19.9 | 4.7 | E6BEA5203946466898E0FFDA1243B0A4 |  | R22 | TXV |  | 7.711% | 0.92289 | 14.82% | [5 empty] | TXV | 7.711%
Red Bluff | CA | 96080-2601 |  | 2013-08-09 | 2013-08-09 19:49 | 2013-08-09 19:49 | RHEEM - RAK-024JAS | 51 | 0 | Yes | Yes | 19.4 | 19.8 | -0.4 | B95DF230718C4473B7C33D56A1DBCE79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-6300 |  | 2013-06-29 | 2013-06-29 14:13 | 2013-06-29 14:29 | LENNOX - 10ACC-030-230-03 | 58 | 7 | Yes | Yes | 15 | 17.6 | -2.6 | 41CEDA3E96FE448DBFD5D9AC07BFFCEA |  | R22 | Non-TXV |  | 12.07% | 0.87931 | 23.19% | [5 empty] | Non-TXV | 12.07%
Los Banos | CA | 93635-6439 |  | 2013-08-05 | 2013-08-05 09:55 | 2013-08-05 09:59 | BRYANT - 563CN048-H | 140 | 4.7 | Yes | Yes | 17 | 18.7 | -1.7 | 02A2B86A3A074C4F909948E3EBE97032 |  | R22 | Non-TXV |  | 3.357% | 0.96643 | 6.452% | [5 empty] | Non-TXV | 3.357%
Clovis | CA | 93611-5184 |  | 2013-06-27 | 2013-06-27 11:54 | 2013-06-27 12:13 | BDP - 585HJW042060ABAF | 80 | 11.8 | Yes | Yes | 18.5 | 19.3 | -0.8 | 1F183A5C3BEE42AD80C737B6D0756DAE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.75% | 0.8525 | 28.35% | [5 empty] | Non-TXV | 14.75%
Los Banos | CA | 93635-5211 |  | 2013-07-10 | 2013-07-10 08:55 | 2013-07-10 08:58 | CARRIER - 38TH048320 | 128 | 12.3 | Yes | Yes | 26.4 | 20.4 | 6 | 0A609471369E42FDBEA1BD27B4FFD794 |  | R22 | Non-TXV |  | 9.609% | 0.90391 | 18.47% | [5 empty] | Non-TXV | 9.609%
Stockton | CA | 95210-3335 |  | 2013-07-08 | 2013-07-08 11:05 | 2013-07-08 11:23 | CARRIER - 38EB036300 | 120 | 3.7 | Yes | Yes | 22.8 | 19.3 | 3.5 | 4DA764FA381C4EF6BB54A33A05E3A689 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Madera | CA | 93638-1753 |  | 2013-07-15 | 2013-07-15 13:36 | 2013-07-15 14:31 | PAYNE - PY1P NB2060AAAA | 104 | 5.5 | Yes | Yes | 18.6 | 19.8 | -1.2 | 858E6C5DA6C9495D90C26C57537B4A2C |  | R22 | Non-TXV |  | 5.288% | 0.94712 | 10.16% | [5 empty] | Non-TXV | 5.288%
Stockton | CA | 95206-3878 |  | 2013-07-05 | 2013-07-05 13:38 | 2013-07-05 14:05 | CARRIER - 24ABA336A300 | 105 | 4.6 | Yes | Yes | 24 | 21 | 3 | FD6E7047A5364EDE8136E8F389FFF152 |  | R410A | Non-TXV |  | 4.381% | 0.95619 | 8.419% | [5 empty] | Non-TXV | 4.381%
Los Banos | CA | 93635-5444 |  | 2013-07-10 | 2013-07-10 14:01 | 2013-07-10 14:03 | RUUD - UNK | 66 | 8.5 | Yes | Yes | 23.1 | 23.1 | 0 | 9CE4548E0B2D42B8B75577624D20D818 |  | R22 | Non-TXV |  | 12.88% | 0.87121 | 24.75% | [5 empty] | Non-TXV | 12.88%
Madera | CA | 93637-5013 |  | 2013-07-26 | 2013-07-26 10:17 | 2013-07-26 11:39 | CARRIER - 48GS-02404301 | 53 | 1.9 | Yes | Yes | 21.5 | 20.4 | 1.1 | E96F8E8AA856429BA64636244AFDCDDE |  | R22 | Non-TXV |  | 3.585% | 0.96415 | 6.889% | [5 empty] | Non-TXV | 3.585%
Stockton | CA | 95207-7759 |  | 2013-06-26 | 2013-06-26 10:37 | 2013-06-26 10:53 | CARRIER - 38CKC024340 | 57 | 11 | Yes | Yes | 17.6 | 16.4 | 1.2 | D96536341F70453F96650D8191DAC928 |  | R22 | Non-TXV |  | 19.3% | 0.80702 | 37.09% | [5 empty] | Non-TXV | 19.3%
Fresno | CA | 93703-1444 |  | 2013-07-03 | 2013-07-03 10:20 | 2013-07-03 10:44 | YORK - D1NP036N05606A | 108 | 3.7 | Yes | Yes | 20.1 | 21 | -0.9 | F9743D89B0B2418485E8CCCE7B9D35CF |  | R22 | Non-TXV |  | 3.426% | 0.96574 | 6.584% | [5 empty] | Non-TXV | 3.426%
Watsonville | CA | 95076-4196 |  | 2013-10-22 | 2013-10-22 11:28 | 2013-10-22 11:45 | BRYANT - 561CJ024-D | 59 | -4.2 | Yes | Yes | 20.2 | 18.2 | 2 | A25CC9CE6A14453599FE51426D5B5AB3 |  | R22 | Non-TXV |  | -7.119% | 1.0712 | 1.994% |  |  |  |  | Non-TXV |  |  | -7.119%
Marysville | CA | 95901-8236 |  | 2013-09-10 | 2013-09-10 17:01 | 2013-09-10 17:20 | YORK - H2RA030S06D | 62 | -2.8 | Yes | Yes | 23 | 19.9 | 3.1 | 870CFB0BF6584243891707E2113E5409 |  | R22 | TXV |  | -4.516% | 1.0452 | 1.265% |  |  |  |  | TXV |  |  | -4.516%
Fresno | CA | 93720-2451 |  | 2013-08-09 | 2013-08-09 16:33 | 2013-08-09 21:58 | CARRIER - 38E AOL 430 | 59 | 3.4 | Yes | Yes | 16.8 | 19.5 | -2.7 | 2448BB56875D4050B505B284DA2DE49B |  | R22 | Non-TXV |  | 5.763% | 0.94237 | 11.07% | [5 empty] | Non-TXV | 5.763%
Stockton | CA | 95205-0000 |  | 2013-07-17 | 2013-07-17 16:15 | 2013-07-17 16:44 | GOODMAN - GSC130481AF | 152 | 8 | Yes | Yes | 21.2 | 17.5 | 3.8 | 4C37608772A44E1BAF8C820CF91E7890 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Stockton | CA | 95206-3811 |  | 2013-07-16 | 2013-07-16 12:39 | 2013-07-16 12:57 | OTHER - UNK | 98 | 12.2 | Yes | Yes | 24 | 19.3 | 4.7 | 29E294CEDB834769B617AE4E01E18F6C |  | R22 | Non-TXV |  | 12.45% | 0.87551 | 23.92% | [5 empty] | Non-TXV | 12.45%
Fresno | CA | 93705-1114 |  | 2013-07-10 | 2013-07-10 14:13 | 2013-07-10 14:39 | CARRIER - 48GX-030060301 | 68 | 2.2 | Yes | Yes | 20 | 21 | -1 | 62994C35F1824C46B67E4BC394DD6B8A |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Stockton | CA | 95205-2540 |  | 2013-07-23 | 2013-07-23 15:51 | 2013-07-23 16:30 | GOODMAN - CKL36-1K | 84 | 5 | Yes | Yes | 20.9 | 21.7 | -0.8 | 8E5B344AB71648C49E96838E8FE2E2D5 |  | R22 | Non-TXV |  | 5.952% | 0.94048 | 11.44% | [5 empty] | Non-TXV | 5.952%
Gerber | CA | 96035-0000 |  | 2013-09-13 | 2013-09-13 13:03 | 2013-09-13 14:18 | GOODMAN - DLT4Z01R | 125 | 6.9 | Yes | Yes | 17.4 | 17.9 | -0.5 | 6983B6035727432F97AE54B77E07A8F3 |  | R22 | Non-TXV |  | 5.52% | 0.9448 | 10.61% | [5 empty] | Non-TXV | 5.52%
Magalia | CA | 95954-9615 |  | 2013-07-18 | 2013-07-18 14:54 | 2013-07-18 15:45 | BDP - 542EJX036 | 132 | 4.5 | Yes | Yes | 18.3 | 20.4 | -2.1 | 401CCAEE22CE4EFC87F97B6237E93502 |  | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Oroville | CA | 95965-0000 |  | 2013-07-26 | 2013-07-26 12:14 | 2013-07-26 21:32 | TRANE - 2TTB3036A1000AA | 101 | 8.9 | Yes | Yes | 20.5 | 19.2 | 1.4 | 482B82BBBC994AC4A04FDD032E460949 |  | R22 | Non-TXV |  | 8.812% | 0.91188 | 16.93% | [5 empty] | Non-TXV | 8.812%
Corning | CA | 96021-9390 |  | 2013-07-24 | 2013-07-24 20:03 | 2013-07-24 20:22 | COLEMAN - BRC00481BDG | 103 | 4.8 | Yes | Yes | 25 | 23.1 | 1.9 | 6CB1A3667AC2455A88E08A1118C82179 |  | R22 | Non-TXV |  | 4.66% | 0.9534 | 8.956% | [5 empty] | Non-TXV | 4.66%
Los Banos | CA | 93635-9452 |  | 2013-08-13 | 2013-08-13 11:16 | 2013-08-13 11:21 | BRYANT - 561CJ036-E | 73 | 2.3 | Yes | Yes | 18.3 | 20.8 | -2.5 | F2A1755070E741A8935A6E0E9801E0AC |  | R22 | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Los Banos | CA | 93635-9452 |  | 2013-08-13 | 2013-08-13 11:24 | 2013-08-13 11:28 | BRYANT - 561CJ042-A | 80 | 4.3 | Yes | Yes | 18.7 | 21.1 | -2.4 | D7EA94D9393140CAB2FF333832ED931B |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Fresno | CA | 93726-2307 |  | 2013-08-21 | 2013-08-21 09:46 | 2013-08-21 10:16 | CARRIER - 48DL004 | 81 | 2.5 | Yes | Yes | 20.5 | 20.7 | -0.2 | C4F418BB76724EE79C270B22B9B49085 |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Jamestown | CA | 95327-9670 |  | 2013-07-31 | 2013-07-31 17:12 | 2013-07-31 17:31 | COLEMAN - UNK | 57 | 9.7 | Yes | Yes | 26.8 | 22.1 | 4.7 | 77B0BB88E27340DC80DD0B134481DC64 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.02% | 0.82982 | 32.7% | [5 empty] | Non-TXV | 17.02%
Jamestown | CA | 95327-9670 |  | 2013-09-24 | 2013-09-24 14:11 | 2013-09-24 14:55 | GUARDIAN - GCGD42S41S3A | 69 | 5.6 | Yes | Yes | 20.7 | 19.5 | 1.2 | 363F070D50624A0A82413A02ED7843D5 |  | R410A | Non-TXV |  | 8.116% | 0.91884 | 15.6% | [5 empty] | Non-TXV | 8.116%
Stockton | CA | 95204-4011 |  | 2013-07-01 | 2013-07-01 12:25 | 2013-07-01 12:25 | TRANE - YCZO5OF1HOAE | 189 | 0 | Yes | Yes | 18.7 | 20.6 | -1.9 | 00319A5D290E4F3196063405E0A72DBB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5805 |  | 2013-11-20 | 2013-11-20 09:50 | 2013-11-20 09:50 | DAY & NIGHT - 585HJW042060ABAF | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | DE6FAD879CDD4CE3B8A0ECC64768A9C3 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4713 |  | 2013-07-30 | 2013-07-30 11:04 | 2013-07-30 11:34 | BRYANT - 574DNWA42060NA | 106 | 6 | Yes | Yes | 22.8 | 18.3 | 4.5 | F975F1D092CB4ECC90BB9496385A5589 |  | R410A | TXV |  | 5.66% | 0.9434 | 10.88% | [5 empty] | TXV | 5.66%
Valley Springs | CA | 95252-8884 |  | 2013-08-14 | 2013-08-14 08:30 | 2013-08-14 08:49 | RUUD - URMA-A036JK08E | 99 | 10.6 | Yes | Yes | 22.7 | 19.5 | 3.2 | ED6C397F8B4F4C7192DD562EB9040CF8 |  | R22 | Non-TXV |  | 10.71% | 0.89293 | 20.58% | [5 empty] | Non-TXV | 10.71%
Fresno | CA | 93702-3961 |  | 2013-08-17 | 2013-08-17 14:30 | 2013-08-17 16:28 | UNITARY PRODUCTS GROUP - GCGD24S21S2A | 61 | 2 | Yes | Yes | 18 | 20.4 | -2.4 | 4E38C0A1B3454854A9E68D16E0FC27F9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.279% | 0.96721 | 6.301% | [5 empty] | Non-TXV | 3.279%
Fresno | CA | 93711-0544 |  | 2013-08-15 | 2013-08-15 10:56 | 2013-08-15 10:56 | PAYNE - 589ANW03606A0CBF | 84 | -7.9 | Yes | Yes | 12.1 | 15.5 | -3.4 | A4EC9FFB1C8B499F857D25AC9A7F9C66 | Remove refrigerant: 7.9 oz Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Fresno | CA | 93705-0164 |  | 2013-08-06 | 2013-08-06 11:46 | 2013-08-06 11:50 | OTHER - TTB018C100A0 | 51 | 3.4 | Yes | Yes | 18.3 | 21.2 | -2.9 | 95BC5FCECDAC4169A99133561E9A15A3 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93706-4731 |  | 2013-07-16 | 2013-07-16 13:48 | 2013-07-16 13:50 | OTHER - GR4GC-036K6072X | 78 | 2.3 | Yes | Yes | 23.7 | 20.7 | 3 | AA9D27D648D743CC8C936794769710C9 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Reedley | CA | 93654-2273 |  | 2013-08-08 | 2013-08-08 09:41 | 2013-08-08 10:05 | RHEEM - N/A | 90 | 3.9 | Yes | Yes | 21 | 20.4 | 0.6 | 594284F2DA99433196455367D8675EB0 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Fresno | CA | 93722-5170 |  | 2013-07-16 | 2013-07-16 15:02 | 2013-07-16 15:04 | CARRIER - 48KLA130300BE | 68 | 8.8 | Yes | Yes | 24.5 | 23.1 | 1.4 | 03FCA08CB86A4B05B070E6EAFBE8CF06 |  | R22 | Non-TXV |  | 12.94% | 0.87059 | 24.87% | [5 empty] | Non-TXV | 12.94%
Parlier | CA | 93648-2822 |  | 2013-07-30 | 2013-07-30 09:24 | 2013-07-30 09:48 | LENNOX - 10ACB36-12P | 80 | 2.4 | Yes | Yes | 18.4 | 20.4 | -2 | E2BC166DAF6146FFAC026C4B61247694 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Orosi | CA | 93647-9756 |  | 2013-07-29 | 2013-07-29 12:13 | 2013-07-29 12:57 | NORDYNE - FS3BA-048KA | 102 | 4.4 | Yes | Yes | 17.5 | 19.8 | -2.3 | DD84E5C1BCB94B338FA0D4BD72797756 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.314% | 0.95686 | 8.29% | [5 empty] | Non-TXV | 4.314%
Fresno | CA | 93722-3037 |  | 2013-07-15 | 2013-07-15 10:32 | 2013-07-15 10:33 | RUUD - UAMA060JBZ | 192 | 19 | Yes | Yes | 27 | 21.4 | 5.6 | 6E66A0A9BEA04E2B8DFFC426E2547A88 |  | R22 | Non-TXV |  | 9.896% | 0.90104 | 19.02% | [5 empty] | Non-TXV | 9.896%
Marysville | CA | 95901-8802 |  | 2013-07-11 | 2013-07-11 11:50 | 2013-07-11 12:08 | BRYANT - 116BNA036-A | 100 | 4.1 | Yes | Yes | 17 | 19.9 | -2.9 | 2DE9D1B1F1BE422F9D461E3F0F6D66A6 |  | R410A | TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | TXV | 4.1%
Fresno | CA | 93702-3143 |  | 2013-07-18 | 2013-07-18 14:42 | 2013-07-18 15:03 | PAYNE - N/A | 85 | 8 | Yes | Yes | 23.6 | 19.9 | 3.7 | 207BB956E2A44971BAFF4966D914DC46 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Clovis | CA | 93611-6114 |  | 2013-07-01 | 2013-07-01 13:57 | 2013-07-01 14:22 | OTHER - CA9036UKC1 | 97 | 3 | Yes | Yes | 21 | 18.1 | 2.9 | 216FE8BD0F694C7A959912F0780F4D77 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Stockton | CA | 95205-4346 |  | 2013-07-12 | 2013-07-12 11:15 | 2013-07-12 11:35 | YORK - D1NQ024N03606NXA | 85 | 6.9 | Yes | Yes | 21.6 | 19.1 | 2.5 | 2A03C209A6634672AD80C8F98D3550A8 |  | R410A | Non-TXV |  | 8.118% | 0.91882 | 15.6% | [5 empty] | Non-TXV | 8.118%
Fresno | CA | 93705-5126 |  | 2013-07-12 | 2013-07-12 08:49 | 2013-07-12 09:12 | ICP - 588ANW036080ACAF | 67 | 2.9 | Yes | Yes | 21 | 22 | -1 | 72BCFF04CCA841AD91EA033A40BA250A |  | R22 | Non-TXV |  | 4.328% | 0.95672 | 8.318% | [5 empty] | Non-TXV | 4.328%
Riverbank | CA | 95367-0000 |  | 2013-07-11 | 2013-07-11 10:21 | 2013-07-11 10:52 | RHEEM - RAJB-036JAS | 93 | 3 | Yes | Yes | 22.3 | 18.8 | 3.5 | A17C905C1BBF4117B471E262F81644D5 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Fresno | CA | 93722-3323 |  | 2013-07-16 | 2013-07-16 09:51 | 2013-07-16 09:53 | RHEEM - RRNLB030JK06X | 76 | 4.5 | Yes | Yes | 20.1 | 21.7 | -1.6 | 59EF8D712C024B3C930646B79BA35B38 |  | R410A | Non-TXV |  | 5.921% | 0.94079 | 11.38% | [5 empty] | Non-TXV | 5.921%
Fresno | CA | 93728-1905 |  | 2013-07-15 | 2013-07-15 09:45 | 2013-07-15 09:47 | YORK - D1NH036N05606C | 108 | 5 | Yes | Yes | 20.9 | 19.1 | 1.9 | 52DE62300C3A46188A72E566D578996A |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Lathrop | CA | 95330-8827 |  | 2013-07-08 | 2013-07-08 16:57 | 2013-07-08 16:59 | GOODMAN - CKL36-1L | 84 | 5.4 | Yes | Yes | 17.6 | 19 | -1.4 | F9CB8642BB1E4A3DA30C6827BF859657 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 6.429% | 0.93571 | 12.35% | [5 empty] | TXV | 6.429%
Sanger | CA | 93657-4113 |  | 2013-07-24 | 2013-07-24 13:52 | 2013-07-24 14:18 | LENNOX - 10GCS030X-75-3PA | 51 | 7.5 | Yes | Yes | 17.2 | 19.7 | -2.5 | 4A80EC5E00EC4C8CBD10D82C3725444B |  | R22 | Non-TXV |  | 14.71% | 0.85294 | 28.26% | [5 empty] | Non-TXV | 14.71%
Merced | CA | 95348-1122 |  | 2013-07-18 | 2013-07-18 17:00 | 2013-07-18 17:02 | RHEEM - RRMA-A030JK06X | 80 | 4.6 | Yes | Yes | 21.3 | 21.5 | -0.2 | E6E85DF87B42419A9358140BEB275763 |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Jamestown | CA | 95327-9670 |  | 2013-09-06 | 2013-09-06 10:19 | 2013-09-06 10:26 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 9 | Yes | Yes | 24.8 | 20.4 | 4.4 | 5C927C68076E43F8A116238103FE1D78 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Kerman | CA | 93630-9261 |  | 2013-08-01 | 2013-08-01 11:21 | 2013-08-01 11:23 | RHEEM - RRGE05E18JKR | 56 | 8.4 | Yes | Yes | 20.1 | 19.3 | 0.8 | FA29326B171E4A828915514C73C6CEA4 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Atwater | CA | 95301-4542 |  | 2013-07-03 | 2013-07-03 13:37 | 2013-07-03 13:40 | TRANE - 4YCC3030A1075AA | 97 | 3.5 | Yes | Yes | 22.7 | 20.4 | 2.3 | 111F7E70C7A64319B4BA1A6035E0176C |  | R410A | Non-TXV |  | 3.608% | 0.96392 | 6.934% | [5 empty] | Non-TXV | 3.608%
Los Banos | CA | 93635-5232 |  | 2013-08-01 | 2013-08-01 12:07 | 2013-08-01 12:12 | BRYANT - 561CJ060-A | 158 | 6.1 | Yes | Yes | 22.9 | 19.2 | 3.7 | 7E99733811F34060958A2173730C0CE0 |  | R22 | Non-TXV |  | 3.861% | 0.96139 | 7.42% | [5 empty] | Non-TXV | 3.861%
Stockton | CA | 95209-4220 |  | 2013-07-12 | 2013-07-12 13:29 | 2013-07-12 13:50 | YORK - AC60X1223A | 147 | 10.4 | Yes | Yes | 20.9 | 20.1 | 0.8 | 31DAD473C83D4463AF3EE363D3BD1834 |  | R22 | TXV |  | 7.075% | 0.92925 | 13.6% | [5 empty] | TXV | 7.075%
Lathrop | CA | 95330-9156 |  | 2013-07-24 | 2013-07-24 11:54 | 2013-07-24 12:28 | GOODMAN - CJK30-1A | 92 | 5.8 | Yes | Yes | 16.8 | 18.5 | -1.7 | 2FB3415919BA4217AD7875F36B0F8867 |  | R22 | Non-TXV |  | 6.304% | 0.93696 | 12.12% | [5 empty] | Non-TXV | 6.304%
Madera | CA | 93638-1700 |  | 2013-07-15 | 2013-07-15 12:03 | 2013-07-15 12:36 | CARRIER - 48SS-024040301 | 87 | -7.2 | Yes | Yes | 15.9 | 18.8 | -2.9 | A5CB880127464C84AA9BAB2F90C6AAD4 |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Fresno | CA | 93727-5257 |  | 2013-07-15 | 2013-07-15 14:55 | 2013-07-15 15:14 | GOODMAN - GSC130481AA | 150 | 4.9 | Yes | Yes | 18 | 20.9 | -2.9 | CD465FDDEE32499D83234DBDDF2D220E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.278% | [5 empty] | Non-TXV | 3.267%
Selma | CA | 93662-4800 |  | 2013-08-05 | 2013-08-05 11:19 | 2013-08-05 12:27 | ICP - PGAD36D1K3 | 78 | 4.4 | Yes | Yes | 22 | 20.4 | 1.6 | FFF7D5D02F2645A0B437C4B63B5C53BD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.641% | 0.94359 | 10.84% | [5 empty] | Non-TXV | 5.641%
Penn Valley | CA | 95946-9382 |  | 2013-09-05 | 2013-09-05 14:19 | 2013-09-05 14:39 | PAYNE - PH13NR036-C | 128 | 7.2 | Yes | Yes | 18 | 20.4 | -2.4 | 52337A4E047C408F8B7BF25B6AE10DA7 |  | R22 | TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | TXV | 5.625%
El Dorado Hills | CA | 95762-5845 |  | 2013-07-08 | 2013-07-08 11:33 | 2013-07-08 11:52 | YORK - H10E060S06B | 122 | 3.6 | Yes | Yes | 19 | 19.3 | -0.3 | 7D4823A16F5641C997E360624C8CBBDA |  | R22 | Non-TXV |  | 2.951% | 0.97049 | 5.671% | [5 empty] | Non-TXV | 2.951%
Copperopolis | CA | 95228-9537 |  | 2013-08-01 | 2013-08-01 15:14 | 2013-08-01 15:43 | TRANE - 2TTB0048A1000AA | 109 | 6.5 | Yes | Yes | 15.2 | 14.4 | 0.8 | E789E3433F7340FDB85C1B7C8378183C |  | R22 | Non-TXV |  | 5.963% | 0.94037 | 11.46% | [5 empty] | Non-TXV | 5.963%
Atwater | CA | 95301-2133 |  | 2013-07-10 | 2013-07-10 09:06 | 2013-07-10 09:08 | PAYNE - 585HJ030040 | 68 | 2.7 | Yes | Yes | 20.9 | 18.9 | 2 | 46E3A00FE7E2435C9F154E5FDF88AC39 |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Marysville | CA | 95901-8342 |  | 2013-07-02 | 2013-07-02 14:53 | 2013-07-02 15:12 | YORK - H2RD030S06B | 93 | 9.4 | Yes | Yes | 15 | 17.4 | -2.4 | 6495137EFB8E44A1B56A714DEF931B0D |  | R22 | Non-TXV |  | 10.11% | 0.89892 | 19.42% | [5 empty] | Non-TXV | 10.11%
Oakdale | CA | 95361-3005 |  | 2013-07-10 | 2013-07-10 11:50 | 2013-07-10 12:16 | AMANA - RCC36A2D | 114 | 9.6 | Yes | Yes | 19.6 | 22.5 | -2.9 | 737DBE7511934786BDAC09E1FEF3506D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.421% | 0.91579 | 16.18% | [5 empty] | Non-TXV | 8.421%
Oakdale | CA | 95361-3005 |  | 2013-07-10 | 2013-07-10 12:34 | 2013-07-10 12:54 | AMANA - RCC36A2D | 114 | 15.6 | Yes | Yes | 17.8 | 19.9 | -2.1 | 67FDD44BB4E2449D95D8034862A85D0C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.68% | 0.86316 | 26.3% | [5 empty] | Non-TXV | 13.68%
Manteca | CA | 95336-4606 |  | 2013-07-17 | 2013-07-17 12:02 | 2013-07-17 12:24 | PAYNE - 588ANW030060ADAD | 53 | 5.7 | Yes | Yes | 22.9 | 21 | 1.9 | 2876925A563544868672A998044A25B6 |  | R22 | Non-TXV |  | 10.75% | 0.89245 | 20.67% | [5 empty] | Non-TXV | 10.75%
Placerville | CA | 95667-9210 |  | 2013-07-10 | 2013-07-10 10:14 | 2013-07-10 10:35 | YORK - H2RA030S060 | 62 | 2 | Yes | Yes | 19 | 22 | -3 | 78820E13050E444AB7E7E757B836993A |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Newcastle | CA | 95658-9606 |  | 2013-08-08 | 2013-08-08 14:49 | 2013-08-08 14:49 | RHEEM - RRNL-C060JK10X | 172.8 | 0 | Yes | Yes | 22.1 | 19.8 | 2.3 | 840D366D68924DD48667F16AFBA0F675 |  | R410A | TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-9146 |  | 2013-07-16 | 2013-07-16 17:32 | 2013-07-16 17:49 | ICP - N4A360AKC300 | 137 | 12.4 | Yes | Yes | 18.7 | 15 | 3.7 | E7BCBE418180423B9DFAD242A1D9AC60 |  | R410A | Non-TXV |  | 9.051% | 0.90949 | 17.39% | [5 empty] | Non-TXV | 9.051%
Kingsburg | CA | 93631-2122 |  | 2013-08-08 | 2013-08-08 19:39 | 2013-08-08 20:00 | CARRIER - 593ANX048000AAAA | 167 | 4.9 | Yes | Yes | 17 | 19.6 | -2.6 | 278D92757F4E40F185131AD3AB4791BE |  | R22 | Non-TXV |  | 2.934% | 0.97066 | 5.639% | [5 empty] | Non-TXV | 2.934%
Stockton | CA | 95205-2540 |  | 2013-07-11 | 2013-07-11 11:44 | 2013-07-11 12:06 | GOODMAN - CKL36-1K | 84 | 4 | Yes | Yes | 18.7 | 20.2 | -1.5 | DA3DA1B89EA847ED978FC8A099226A1F |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Chico | CA | 95926-2415 |  | 2013-07-01 | 2013-07-01 19:16 | 2013-07-01 19:33 | CARRIER - 48GS-030060301 | 55 | 7.1 | Yes | Yes | 20 | 20.9 | -0.9 | 239E10768B6F48609C25026810C5F2A0 |  | R22 | Non-TXV |  | 12.91% | 0.87091 | 24.81% | [5 empty] | Non-TXV | 12.91%
Fresno | CA | 93728-1913 |  | 2013-07-15 | 2013-07-15 11:05 | 2013-07-15 11:07 | YORK - D1NP048N09006A | 132 | 4.7 | Yes | Yes | 27.4 | 21.4 | 6 | AD050652610B48B38E728ED7E927A4AD |  | R22 | Non-TXV |  | 3.561% | 0.96439 | 6.843% | [5 empty] | Non-TXV | 3.561%
Mariposa | CA | 95338-9787 |  | 2013-08-02 | 2013-08-02 11:41 | 2013-08-02 11:45 | RHEEM - RRKA-A042JK08E | 69 | 4.1 | Yes | Yes | 28.1 | 22.2 | 5.9 | 68AEE32EE69D4FF4B59368068F2293C0 |  | R22 | Non-TXV |  | 5.942% | 0.94058 | 11.42% | [5 empty] | Non-TXV | 5.942%
Marysville | CA | 95901-7220 |  | 2013-07-11 | 2013-07-11 12:59 | 2013-07-11 13:22 | OTHER - 589ANW036100ADAF | 85 | 2.5 | Yes | Yes | 27 | 22 | 5 | D61F1C0802D444F394978D35BA951932 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Los Banos | CA | 93635-5401 |  | 2013-07-10 | 2013-07-10 10:02 | 2013-07-10 10:17 | RUUD - UAKA030JAZ | 66 | 13.5 | Yes | Yes | 20.9 | 20.4 | 0.5 | 52462763D8B14A4C8B4ED32B74E88EA8 |  | R22 | Non-TXV |  | 20.45% | 0.79545 | 39.31% | [5 empty] | Non-TXV | 20.45%
Paradise | CA | 95969-2970 |  | 2013-07-15 | 2013-07-15 12:27 | 2013-07-15 14:42 | COLEMAN - DRCQ0361BE | 64 | 8.1 | Yes | Yes | 18.6 | 21.5 | -2.9 | 3AADAC6C19914626932F7571263227A6 |  | R22 | Non-TXV |  | 12.66% | 0.87344 | 24.32% | [5 empty] | Non-TXV | 12.66%
Madera | CA | 93637-1801 |  | 2013-07-01 | 2013-07-01 10:14 | 2013-07-01 22:21 | GOODMAN - GSG13061DF | 120 | 4.9 | Yes | Yes | 22.5 | 20.9 | 1.6 | 06D6E11076314EA09C17A581D9DF9861 |  | R22 | Non-TXV |  | 4.083% | 0.95917 | 7.847% | [5 empty] | Non-TXV | 4.083%
Stockton | CA | 95210-1758 |  | 2013-06-27 | 2013-06-27 12:05 | 2013-06-27 12:24 | BRYANT - 585A024055YACR | 53 | -3.7 | Yes | Yes | 16 | 17 | -1 | 8358034ED1844061B85A3EF9D8D5676A |  | R22 | Non-TXV |  | -6.981% | 1.0698 | 1.955% |  |  |  |  | Non-TXV |  |  | -6.981%
Marysville | CA | 95901-8262 |  | 2013-07-12 | 2013-07-12 11:45 | 2013-07-12 12:18 | CARRIER - UNK | 90 | 5 | Yes | Yes | 19 | 18.7 | 0.3 | FEFD9A4333944BB8932AD5592DB6B60B |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Colfax | CA | 95713-9513 |  | 2013-08-27 | 2013-08-27 10:34 | 2013-08-27 10:57 | FRIGIDAIRE - FS3BC-060K | 145 | -9.2 | Yes | Yes | 24 | 20.4 | 3.6 | C4BCDD73B7B24D73BE53C069AE3717B1 |  | R22 | TXV |  | -6.345% | 1.0634 | 1.777% |  |  |  |  | TXV |  |  | -6.345%
Stockton | CA | 95206-3869 |  | 2013-07-05 | 2013-07-05 12:13 | 2013-07-05 12:42 | PAYNE - 30RAC58C | 89 | 19.4 | Yes | Yes | 21.1 | 20.2 | 0.9 | BD7DE3171EEC4B4B9EA5D12B78C6315C |  | R22 | Non-TXV |  | 21.8% | 0.78202 | 41.89% | [5 empty] | Non-TXV | 21.8%
Oroville | CA | 95966-3912 |  | 2013-08-06 | 2013-08-06 20:43 | 2013-08-06 21:00 | TRANE - TWYO48A00A2 | 240 | 9.7 | Yes | Yes | 19.3 | 21.5 | -2.2 | 4884455321934BC0AD257D0E17B32766 |  | R22 | Non-TXV |  | 4.042% | 0.95958 | 7.767% | [5 empty] | Non-TXV | 4.042%
Newcastle | CA | 95658-9546 |  | 2013-08-08 | 2013-08-08 09:13 | 2013-08-08 09:46 | NORDYNE - JS3BA-036KA | 69 | 9.1 | Yes | Yes | 22.3 | 19.1 | 3.2 | C348305E38264951BE855BC58AF66991 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.19% | 0.86812 | 25.35% | [5 empty] | Non-TXV | 13.19%
Kerman | CA | 93630-9281 |  | 2013-08-16 | 2013-08-16 17:30 | 2013-08-16 17:30 | RHEEM - UNK | 53 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | D284D6FEF9E04FF4A473F2BFC702012C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9402 |  | 2013-07-11 | 2013-07-11 09:51 | 2013-07-11 09:53 | YORK - D1NH030N05606C | 73 | 6.2 | Yes | Yes | 27.3 | 21.7 | 5.6 | 675DF62D714A4C3CA111656AF3341021 |  | R22 | Non-TXV |  | 8.493% | 0.91507 | 16.32% | [5 empty] | Non-TXV | 8.493%
Stockton | CA | 95204-4505 |  | 2013-07-09 | 2013-07-09 09:41 | 2013-07-09 09:41 | RHEEM - URKA-A024JK04X | 50 | 0 | Yes | Yes | 19 | 18.9 | 0.1 | 45A26F8D5BD44246A92AA4590EFDCFA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2268 |  | 2013-06-26 | 2013-06-26 17:48 | 2013-06-26 17:52 | DAY & NIGHT - UNK | 58 | 5.1 | Yes | Yes | 23.6 | 20.2 | 3.4 | 6635F3FF289B4F08A2893FE85546FB82 |  | R22 | Non-TXV |  | 8.793% | 0.91207 | 16.9% | [5 empty] | Non-TXV | 8.793%
Stockton | CA | 95206-3814 |  | 2013-07-05 | 2013-07-05 13:08 | 2013-07-05 13:25 | RHEEM - RRNA-A036JK08X | 85 | 8.6 | Yes | Yes | 23.6 | 19.8 | 3.8 | D5FBA94551CC476889C4812926FD096D |  | R22 | Non-TXV |  | 10.12% | 0.89882 | 19.44% | [5 empty] | Non-TXV | 10.12%
Madera | CA | 93638-1892 |  | 2013-07-25 | 2013-07-25 21:03 | 2013-07-25 21:03 | BDP - 582ANWO3606ON BAF " | 76 | 0 | Yes | Yes | 16.6 | 19.3 | -2.7 | E64D1D8F2EEC4D389EDD9A2EC434B8FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9286 |  | 2013-08-01 | 2013-08-01 10:43 | 2013-08-01 10:45 | RHEEM - UNK | 56 | 7.5 | Yes | Yes | 21.5 | 17.7 | 3.8 | C60C7DF4EFD742D8A286676E0F7A40F5 |  | R22 | Non-TXV |  | 13.39% | 0.86607 | 25.74% | [5 empty] | Non-TXV | 13.39%
Stockton | CA | 95206-2504 |  | 2013-07-13 | 2013-07-13 09:52 | 2013-07-13 09:52 | RHEEM - RRNL-B030JK06X | 77 | 0 | Yes | Yes | 20.5 | 19.9 | 0.6 | A4B40E358716475B943FA5C11F73383E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-5506 |  | 2013-07-25 | 2013-07-25 22:12 | 2013-07-25 22:59 | YORK - DINA030N0606C | 76 | 0 | Yes | Yes | 18.5 | 21.3 | -2.8 | 5C1EE3BB9CE344F7B7761110AB3F59F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2121 |  | 2013-07-19 | 2013-07-19 13:58 | 2013-07-19 14:03 | YORK - D1NH060N06506C | 140 | 26.7 | Yes | Yes | 21.7 | 19.8 | 1.9 | 02C240098D3C4F9CAFC811B637DB0487 |  | R22 | Non-TXV |  | 19.07% | 0.80929 | 36.65% | [5 empty] | Non-TXV | 19.07%
Kingsburg | CA | 93631-2201 |  | 2013-08-08 | 2013-08-08 18:25 | 2013-08-08 18:38 | RHEEM - RAKA-042JAZ | 79 | 2.5 | Yes | Yes | 18.5 | 21 | -2.5 | 8753082C8C514BF68C941FDCF7012363 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.165% | 0.96835 | 6.082% | [5 empty] | Non-TXV | 3.165%
Kingsburg | CA | 93631-2201 |  | 2013-08-08 | 2013-08-08 19:35 | 2013-08-08 19:36 | TRANE - 4YCC3024B1064AA | 79 | 3.2 | Yes | Yes | 20.3 | 19.2 | 1.1 | A6691039EC724ADEACDAE60D5F3DB582 |  | R410A | TXV |  | 4.051% | 0.95949 | 7.784% | [5 empty] | TXV | 4.051%
Marysville | CA | 95901-8258 |  | 2013-07-12 | 2013-07-12 12:50 | 2013-07-12 13:14 | CARRIER - 38BRC030320 | 99 | -3.8 | Yes | Yes | 20 | 19 | 1 | A03076069A594C1BB07EA9E7947C0752 |  | R22 | TXV |  | -3.838% | 1.0384 | 1.075% |  |  |  |  | TXV |  |  | -3.838%
Madera | CA | 93638-0598 |  | 2013-07-12 | 2013-07-12 17:40 | 2013-07-12 19:10 | DAY & NIGHT - UNK | 116 | 3.8 | Yes | Yes | 19.5 | 20.9 | -1.4 | F01186EB5E4D454F9FE77364AFB5F569 |  | R22 | Non-TXV |  | 3.276% | 0.96724 | 6.295% | [5 empty] | Non-TXV | 3.276%
Jamestown | CA | 95327-9670 |  | 2013-09-06 | 2013-09-06 08:41 | 2013-09-06 09:04 | OTHER - UNK | 85 | 5.1 | Yes | Yes | 25.5 | 19.9 | 5.6 | 55E23178B2F746CC97C1E30BBE276C8F |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93726-2503 |  | 2013-08-12 | 2013-08-12 14:22 | 2013-08-12 14:38 | GOODMAN - CK42-1C | 86 | 2.6 | Yes | Yes | 18.6 | 21.4 | -2.8 | 733E03C5BE9B4D6A91F53E478179CE80 |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
San Andreas | CA | 95249-0000 |  | 2013-08-20 | 2013-08-20 09:22 | 2013-08-20 09:41 | OTHER - BRC0036B | 67 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 23E0CFC085D34A26A7CB87E3E2424774 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1727 |  | 2013-07-28 | 2013-07-28 21:53 | 2013-07-28 22:51 | YORK - D1NA030N0360C | 76 | 2.3 | Yes | Yes | 18.8 | 19 | -0.2 | F021202471814C0E892385CAA288FF26 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Placerville | CA | 95667-4009 |  | 2013-07-09 | 2013-07-09 09:02 | 2013-07-09 09:21 | RHEEM - RQKA-A036JK | 103 | 3.1 | Yes | Yes | 23 | 19.9 | 3.1 | 8846BB0D562D43F98869CB35957BB604 |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Madera | CA | 93637-2673 |  | 2013-07-08 | 2013-07-08 11:32 | 2013-07-08 12:35 | YORK - AC036X102 | 53 | -3.7 | Yes | Yes | 20 | 20.9 | -0.9 | CEA5BD83A6F84FA196707D379942AAE2 |  | R22 | Non-TXV |  | -6.981% | 1.0698 | 1.955% |  |  |  |  | Non-TXV |  |  | -6.981%
Fresno | CA | 93726-1702 |  | 2013-07-26 | 2013-07-26 15:46 | 2013-07-26 15:55 | RUUD - UNK | 67 | 11.9 | Yes | Yes | 23 | 23.1 | -0.1 | EB66767116AB44C7B75FF8E7C2D6C75D |  | R22 | Non-TXV |  | 17.76% | 0.82239 | 34.13% | [5 empty] | Non-TXV | 17.76%
Stockton | CA | 95206-3819 |  | 2013-07-03 | 2013-07-03 11:53 | 2013-07-03 12:23 | CARRIER - 38ETG042300 | 178 | 10.9 | Yes | Yes | 25.4 | 19.7 | 5.7 | 9BEE3A0473204510B0C3902ADCF86A2E |  | R410A | Non-TXV |  | 6.124% | 0.93876 | 11.77% | [5 empty] | Non-TXV | 6.124%
Kerman | CA | 93630-1557 |  | 2013-07-31 | 2013-07-31 12:34 | 2013-07-31 12:36 | CARRIER - 48NLT036300 | 96 | 10.6 | Yes | Yes | 22.7 | 20.1 | 2.6 | F406B9B3D50D42E8BE8F322784B5394B |  | R22 | Non-TXV |  | 11.04% | 0.88958 | 21.22% | [5 empty] | Non-TXV | 11.04%
Kingsburg | CA | 93631-2609 |  | 2013-08-09 | 2013-08-09 18:09 | 2013-08-09 19:34 | RHEEM - N/A | 90 | 3 | Yes | Yes | 20 | 19.1 | 0.9 | BA7740260A2944ED86C1BC8856AAB188 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95340-2647 |  | 2013-06-28 | 2013-06-28 13:42 | 2013-06-28 13:42 | RHEEM - RRMAA048JK10X | 115 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 767DE6E70E9E48ED8DD4E544C6BA3261 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Jamestown | CA | 95327-9670 |  | 2013-08-01 | 2013-08-01 09:04 | 2013-08-01 09:04 | COLEMAN - UNK | 85 | 0 | Yes | Yes | 24.3 | 21.5 | 2.8 | 6B2DD4ECD2A64786B3A473029CAA6A61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3018 |  | 2013-07-30 | 2013-07-30 08:17 | 2013-07-30 08:23 | TRANE - C036F1MOBD | 83 | 9.8 | Yes | Yes | 20.4 | 21 | -0.6 | 485792D908EC406E9C4F95156A56A5B6 |  | R22 | Non-TXV |  | 11.81% | 0.88193 | 22.69% | [5 empty] | Non-TXV | 11.81%
Kingsburg | CA | 93631-2812 |  | 2013-08-08 | 2013-08-08 17:29 | 2013-08-08 18:23 | LENNOX - 10GCS048X-100-3PA | 93 | 3.1 | Yes | Yes | 20 | 20.5 | -0.5 | 849F458F53784DF4841B1C783DA67AD7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93726-2914 |  | 2013-07-26 | 2013-07-26 13:40 | 2013-07-26 13:42 | AMANA - RCC30A2B | 95 | 19.8 | Yes | Yes | 24.5 | 22.3 | 2.2 | C4D6DCDC751148628E33EFE32B8ECB94 |  | R22 | Non-TXV |  | 20.84% | 0.79158 | 40.05% | [5 empty] | Non-TXV | 20.84%
Planada | CA | 95365-0000 |  | 2013-08-26 | 2013-08-26 12:16 | 2013-08-26 12:17 | RHEEM - RQKAA030JK | 70 | 7.7 | Yes | Yes | 26.4 | 23.1 | 3.3 | 639B26A163BA41E28CCE29BBB6023178 |  | R22 | Non-TXV |  | 11% | 0.89 | 21.14% | [5 empty] | Non-TXV | 11%
Planada | CA | 95365-0000 |  | 2013-08-26 | 2013-08-26 12:19 | 2013-08-26 12:36 | RHEEM - RQKAA030JK | 70 | 10 | Yes | Yes | 23.3 | 21.4 | 1.9 | 5EA2DB2E15AD4A50850C915774E41808 |  | R22 | Non-TXV |  | 14.29% | 0.85714 | 27.45% | [5 empty] | Non-TXV | 14.29%
Fresno | CA | 93726-3003 |  | 2013-07-26 | 2013-07-26 13:08 | 2013-07-26 13:09 | RHEEM - RRNAA036JK06X | 114 | 19.7 | Yes | Yes | 21.1 | 20.2 | 0.9 | 79D624008A9D4A319C171454310DF5E7 |  | R22 | Non-TXV |  | 17.28% | 0.82719 | 33.21% | [5 empty] | Non-TXV | 17.28%
Stockton | CA | 95205-3145 |  | 2013-07-11 | 2013-07-11 14:22 | 2013-07-11 14:48 | BRYANT - 574ANW036060NB | 114 | 5.5 | Yes | Yes | 22.9 | 21.8 | 1.2 | BFD76120F61F4E1A851F7896B2393C08 |  | R22 | Non-TXV |  | 4.825% | 0.95175 | 9.272% | [5 empty] | Non-TXV | 4.825%
Pine Grove | CA | 95665-9725 |  | 2013-08-09 | 2013-08-09 11:46 | 2013-08-09 11:46 | OTHER - UNK | 67 | 0 | Yes | Yes | 27.7 | 22.9 | 4.8 | 17F20775C1D74AABA6616EFE5DC3E6E8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-5507 |  | 2013-07-22 | 2013-07-22 17:40 | 2013-07-22 19:02 | YORK - D1NA030N0606C | 76 | 2.9 | Yes | Yes | 17.3 | 20.1 | -2.8 | 6B59F891303348608720AED0D999AB82 |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Stockton | CA | 95209-2255 |  | 2013-07-10 | 2013-07-10 14:35 | 2013-07-10 14:52 | TRANE - TTZ048A100A0 | 234 | 18.7 | Yes | Yes | 16.3 | 18 | -1.7 | 6A319B92B81440F994DFDA796EF0F98A |  | R22 | Non-TXV |  | 7.991% | 0.92009 | 15.36% | [5 empty] | Non-TXV | 7.991%
Lathrop | CA | 95330-9647 |  | 2013-07-03 | 2013-07-03 11:48 | 2013-07-03 12:10 | RUUD - UAFD-030JAS | 69 | 9.5 | Yes | Yes | 12.1 | 14.7 | -2.6 | 5691E516B16E44BAB2466CFEFE8B97F4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.77% | 0.86232 | 26.46% | [5 empty] | Non-TXV | 13.77%
Jamestown | CA | 95327-9670 |  | 2013-08-01 | 2013-08-01 09:39 | 2013-08-01 10:02 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 11.9 | Yes | Yes | 21.8 | 21.6 | 0.2 | 8B5A2DA659D441CCB6E9D044021FF8C8 |  | R22 | Non-TXV |  | 14.17% | 0.85833 | 27.23% | [5 empty] | Non-TXV | 14.17%
Merced | CA | 95340-0638 |  | 2013-07-11 | 2013-07-11 13:00 | 2013-07-11 13:14 | OTHER - 60WR24 | 56 | 9.7 | Yes | Yes | 21.8 | 22.3 | -0.5 | BBA0FC9872794951AEF1BB943E7F864E |  | R22 | Non-TXV |  | 17.32% | 0.82679 | 33.29% | [5 empty] | Non-TXV | 17.32%
Stockton | CA | 95210-1120 |  | 2013-06-26 | 2013-06-26 09:16 | 2013-06-26 09:34 | DAY & NIGHT - 588ANW030060ADAD | 56 | -4 | Yes | Yes | 16.8 | 17.2 | -0.4 | 84DC93BE80264CF4A5B8533B5E0F7B89 |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Fresno | CA | 93704-4404 |  | 2013-06-26 | 2013-06-26 13:42 | 2013-06-26 13:50 | YORK - AC024M1021A | 52 | 3.2 | Yes | Yes | 25 | 19.3 | 5.7 | 285B05B2D2A94113A33FA64AC9D28977 |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Madera | CA | 93637-5638 |  | 2013-08-31 | 2013-08-31 23:23 | 2013-09-01 00:14 | - | 85 | 2.8 | Yes | Yes | 15.8 | 18 | -2.2 | B81F35A83223437F9EE7269C43EC9F4B |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Stockton | CA | 95210-1148 |  | 2013-06-26 | 2013-06-26 14:13 | 2013-06-26 14:34 | RUUD - UNK | 96 | 3.4 | Yes | Yes | 17.5 | 17.9 | -0.4 | E3A9C159B6084A7BA3D4B0041569A48C |  | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Fresno | CA | 93728-1523 |  | 2013-07-15 | 2013-07-15 10:05 | 2013-07-15 10:07 | ARCOAIRE - PGAD42D1K5 | 212 | 6.4 | Yes | Yes | 24.6 | 20.9 | 3.7 | ACB7AF45BD844F86B48CC6111F9156FD |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Laton | CA | 93242-0000 |  | 2013-09-11 | 2013-09-11 13:06 | 2013-09-11 13:25 | OTHER - 867 817920 | 80 | 2.4 | Yes | Yes | 18.5 | 20.4 | -1.9 | 41525F72630A42F3A095A9570479AD3F |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Orange Cove | CA | 93646-2507 |  | 2013-09-17 | 2013-09-17 14:35 | 2013-09-17 15:07 | PAYNE - N/A | 90 | 5.3 | Yes | Yes | 18 | 19.8 | -1.8 | BC1FFC7D8D774772BAA3E691C50FF9B2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.889% | 0.94111 | 11.32% | [5 empty] | Non-TXV | 5.889%
Fresno | CA | 93704-4406 |  | 2013-08-12 | 2013-08-12 09:54 | 2013-08-12 09:55 | GOODMAN - GS130241FA | 77 | 8.2 | Yes | Yes | 20.5 | 19.8 | 0.7 | 8A7F551810E1488895022D98F2BF8C48 |  | R22 | Non-TXV |  | 10.65% | 0.89351 | 20.47% | [5 empty] | Non-TXV | 10.65%
Orange Cove | CA | 93646-2524 |  | 2013-08-14 | 2013-08-14 09:39 | 2013-08-14 09:39 | BDP - 588ANW036060ADAF | 67 | 0 | Yes | Yes | 17 | 19.7 | -2.7 | 071668E09719417E8C583684A38AB0C9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3115 |  | 2013-08-26 | 2013-08-26 11:01 | 2013-08-26 11:04 | OTHER - BWB918A10000 | 77 | 11.6 | Yes | Yes | 18.1 | 17 | 1.1 | 94C5E28C40A64F0085C91DE7539F0EEA |  | R22 | Non-TXV |  | 15.06% | 0.84935 | 28.95% | [5 empty] | Non-TXV | 15.06%
Valley Springs | CA | 95252-9002 |  | 2013-07-16 | 2013-07-16 09:02 | 2013-07-16 09:25 | UNITARY PRODUCTS GROUP - H2RC048S06HA | 120 | 19.9 | Yes | Yes | 22.8 | 20.4 | 2.4 | 1488008C7EC942748F33B2EDFB53B7D9 |  | R22 | Non-TXV |  | 16.58% | 0.83417 | 31.87% | [5 empty] | Non-TXV | 16.58%
El Dorado | CA | 95623-4803 |  | 2013-09-06 | 2013-09-06 09:33 | 2013-09-06 09:33 | UNITARY PRODUCTS GROUP - HRD060S06A | 162 | 0 | Yes | Yes | 26.9 | 21.3 | 5.6 | C48B2643766944C38A981A49C7B0EFDE |  | R22 | TXV |  | 0% | 1 | 0%
Merced | CA | 95340-0757 |  | 2013-06-26 | 2013-06-26 15:23 | 2013-06-26 15:28 | BRYANT - 5636N042-C | 108 | 5 | Yes | Yes | 14 | 14.4 | -0.4 | 861D4735787F46308D30A183923D62C1 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Fresno | CA | 93704-6128 |  | 2013-07-23 | 2013-07-23 13:56 | 2013-07-23 13:58 | YORK - D1NP036N05606A | 108 | 17.3 | Yes | Yes | 22.2 | 19.8 | 2.4 | B290A323DE244E3CA741767C5D82DF95 |  | R22 | Non-TXV |  | 16.02% | 0.83981 | 30.78% | [5 empty] | Non-TXV | 16.02%
Watsonville | CA | 95076-4197 |  | 2013-10-22 | 2013-10-22 12:06 | 2013-10-22 12:35 | BRYANT - 561CJ024-D | 59 | -3.5 | Yes | Yes | 18.1 | 18.2 | -0.1 | 043D3D2899B14C278FD2A469426FA75C |  | R22 | Non-TXV |  | -5.932% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.932%
Ione | CA | 95640-9762 |  | 2013-08-02 | 2013-08-02 13:43 | 2013-08-02 13:43 | GOODMAN - CE36-1GB | 79 | 0 | Yes | Yes | 26 | 21.2 | 4.8 | F1A363EFB8364CC6A48538469B31DB3A |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3344 |  | 2013-07-16 | 2013-07-16 09:22 | 2013-07-16 09:24 | CARRIER - UNK | 96 | 12.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | 656A8372136C46D497BBDEBAECA71959 |  | R22 | Non-TXV |  | 12.92% | 0.87083 | 24.82% | [5 empty] | Non-TXV | 12.92%
Tracy | CA | 95377-8544 |  | 2013-07-26 | 2013-07-26 12:51 | 2013-07-26 13:26 | BRYANT - 561CJ048-F | 97 | -26.4 | Yes | Yes | 21 | 18.5 | 2.5 | 90966F1808344CEFA505431C6EC14536 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -27.22% | 1.2722 | 7.622% |  |  |  |  | TXV |  |  | -27.22%
Tracy | CA | 95377-8544 |  | 2013-07-26 | 2013-07-26 13:11 | 2013-07-26 13:33 | BRYANT - 561CJ036-F | 70 | 8 | Yes | Yes | 22.6 | 19.1 | 3.5 | 6E5DCA698F3D437F82F2F8D5FD2F7683 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | TXV | 11.43%
Fresno | CA | 93726-3010 |  | 2013-07-29 | 2013-07-29 08:34 | 2013-07-29 08:35 | CARRIER - 48NMY030301BE | 68 | 8.6 | Yes | Yes | 16.3 | 18.7 | -2.4 | C30CFFD7B3A243CFBA8952BAB7DA1D2D |  | R22 | Non-TXV |  | 12.65% | 0.87353 | 24.3% | [5 empty] | Non-TXV | 12.65%
Madera | CA | 93637-4460 |  | 2013-07-08 | 2013-07-08 20:58 | 2013-07-08 21:31 | YORK - 38TH036300 | 85 | 3 | Yes | Yes | 14.1 | 15.5 | -1.4 | 299187D317F241EF9AD1AC961743BD62 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Stockton | CA | 95204-3541 |  | 2013-07-02 | 2013-07-02 10:43 | 2013-07-02 11:02 | GUARDIAN - TCGD48S41S3HA | 73 | -5.6 | Yes | Yes | 18.6 | 18.5 | 0.1 | C88A0130D90345458BF2484633C75B29 |  | R410A | TXV |  | -7.671% | 1.0767 | 2.148% |  |  |  |  | TXV |  |  | -7.671%
Stockton | CA | 95203-3529 |  | 2013-07-25 | 2013-07-25 16:08 | 2013-07-25 16:51 | BDP - PHN3NR024-K | 72 | 9.9 | Yes | Yes | 18.1 | 19.9 | -1.8 | C8A6F8BE6AE04A598670824777E2A474 |  | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Marysville | CA | 95901-3329 |  | 2013-06-27 | 2013-06-27 09:21 | 2013-06-27 09:43 | PAYNE - PA13NA036000AEAA | 79 | -3.2 | Yes | Yes | 19 | 17.7 | 1.3 | 55ABD63D557D44309E09B5AB3427B195 |  | R410A | TXV |  | -4.051% | 1.0405 | 1.134% |  |  |  |  | TXV |  |  | -4.051%
Chowchilla | CA | 93610-9503 |  | 2013-06-28 | 2013-06-28 10:46 | 2013-06-28 19:38 | YORK - 1NP060N09006 | 102 | -7.2 | Yes | Yes | 19.8 | 19.7 | 0.1 | 4176F2B9494041A09B96CAC7F0900F3E |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Granite Bay | CA | 95746-9311 |  | 2013-09-27 | 2013-09-27 18:12 | 2013-09-27 18:12 | PAYNE - PY1PNB036090ABAA | 70 | 0 | Yes | Yes | 19.4 | 20.1 | -0.7 | 0BF9085BC019430886C4293F3D5405ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3502 |  | 2013-06-27 | 2013-06-27 14:00 | 2013-06-27 14:23 | YORK - ACO42X1221B | 108 | 13.7 | Yes | Yes | 16.3 | 18.8 | -2.5 | 1CA7835AD64446F9B4C56C2A33DEED2C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.69% | 0.87315 | 24.38% | [5 empty] | Non-TXV | 12.69%
Tracy | CA | 95377-1148 |  | 2013-08-01 | 2013-08-01 14:39 | 2013-08-01 14:56 | CARRIER - 38BRC060360 | 201 | 32.9 | Yes | Yes | 21.7 | 19.8 | 1.9 | F38E70FCE86D4D4BA9E8D3294E34876F |  | R22 | Non-TXV |  | 16.37% | 0.83632 | 31.46% | [5 empty] | Non-TXV | 16.37%
Orange Cove | CA | 93646-2001 |  | 2013-09-17 | 2013-09-17 16:23 | 2013-09-17 17:11 | GOODMAN - GSC130361BA | 125 | 4 | Yes | Yes | 17.7 | 15.9 | 1.8 | 6853B8260BCB47E7827D49BCFB59EA3B |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Merced | CA | 95341-6410 |  | 2013-07-01 | 2013-07-01 11:49 | 2013-07-01 11:51 | GOODMAN - GPG13360701AB | 112 | 4.7 | Yes | Yes | 25.5 | 19.5 | 6 | 5E9178538F6C46ED8EF479475ACC0E58 |  | R22 | Non-TXV |  | 4.196% | 0.95804 | 8.065% | [5 empty] | Non-TXV | 4.196%
Kerman | CA | 93630-9282 |  | 2013-08-16 | 2013-08-16 11:59 | 2013-08-16 13:37 | RHEEM - UNK | 72 | -4.2 | Yes | Yes | 17.2 | 19 | -1.8 | 740837BC692D4C62B0BE9AD6833407DF |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95205-5701 |  | 2013-07-15 | 2013-07-15 13:45 | 2013-07-15 14:06 | PAYNE - PA10JA036-C | 72 | 3.1 | Yes | Yes | 16.9 | 18.6 | -1.7 | 94FE741553E14D0083263EEC89FDB806 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.306% | 0.95694 | 8.274% | [5 empty] | Non-TXV | 4.306%
Stockton | CA | 95206-6072 |  | 2013-07-11 | 2013-07-11 10:58 | 2013-07-11 10:58 | GOODMAN - C1J36-1A | 90 | 0 | Yes | Yes | 18.8 | 19.9 | -1.1 | 7165121E5CB64F1EBD20567FA6C97CBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-5148 |  | 2013-07-11 | 2013-07-11 13:35 | 2013-07-11 14:13 | JANITROL - N/A | 90 | 3.1 | Yes | Yes | 22.9 | 21.7 | 1.2 | EC3AF0C406624821A54E423D8FF1E6CD |  | R22 | Non-TXV |  | 3.444% | 0.96556 | 6.619% | [5 empty] | Non-TXV | 3.444%
Applegate | CA | 95703-9710 |  | 2013-08-19 | 2013-08-19 13:09 | 2013-08-19 13:09 | TRANE - 2YCC3030A1064AA | 88 | 0 | Yes | Yes | 27.5 | 22.6 | 4.9 | 86C57607D3014A65A33922D54295A2DB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-2862 |  | 2013-08-28 | 2013-08-28 14:26 | 2013-08-28 15:48 | CONCORD - CCU10A24A-1 | 50 | 1.9 | Yes | Yes | 20 | 20.5 | -0.5 | 68E947EAB0D74B7FBDFBD6670C8C5556 |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Chico | CA | 95973-9106 |  | 2013-07-12 | 2013-07-12 18:35 | 2013-07-12 18:52 | UNK - UNK | 85 | 7.2 | Yes | Yes | 18.7 | 19.3 | -0.6 | 752BAC9924F847A7A5F907627BAA448C |  |  |  |  | 8.471% | 0.91529 | 16.28% | [5 empty] | 0 | 8.471%
Penn Valley | CA | 95946-9303 |  | 2013-09-16 | 2013-09-16 10:26 | 2013-09-16 10:26 | AMERICAN STANDARD - 6H0018A100A2 | 84 | 0 | Yes | Yes | 19.3 | 20.6 | -1.3 | E71B2CEC0BE040DABA9B638E4DB4FFFF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Penn Valley | CA | 95946-9303 |  | 2013-09-16 | 2013-09-16 10:52 | 2013-09-16 10:52 | GE - BWC024E100A0 | 94 | 0 | Yes | Yes | 18.2 | 19.9 | -1.7 | FD9329153A6D4F32914EE595BEEF0378 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9123 |  | 2013-07-18 | 2013-07-18 10:36 | 2013-07-18 10:37 | BDP - 585EJW030050ABAF | 58 | 10.4 | Yes | Yes | 21.8 | 18.6 | 3.2 | 8AD700B7FB6149919AF07A4B602720CB |  | R22 | Non-TXV |  | 17.93% | 0.82069 | 34.46% | [5 empty] | Non-TXV | 17.93%
Olivehurst | CA | 95961-0000 |  | 2013-06-28 | 2013-06-28 12:14 | 2013-06-28 12:32 | COLEMAN - UNK | 85 | 2.8 | Yes | Yes | 22 | 19 | 3 | 10C44E8CEC0841B294043E48B03A4D2E |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Merced | CA | 95340-0908 |  | 2013-06-26 | 2013-06-26 15:59 | 2013-06-26 16:02 | YORK - D4NZ048N09006NXA | 68 | 2.8 | Yes | Yes | 17.2 | 17.2 | 0 | AF6816091CA5499D84BE9B55D8909368 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Merced | CA | 95340-0908 |  | 2013-06-26 | 2013-06-26 16:10 | 2013-06-26 16:13 | ICP - PGC018K040E | 57 | -4.7 | Yes | Yes | 12.8 | 12.1 | 0.7 | 72965D50BF5F423DBBD96BB7216E26EC |  | R22 | Non-TXV |  | -8.246% | 1.0825 | 2.309% |  |  |  |  | Non-TXV |  |  | -8.246%
Fresno | CA | 93722-3854 |  | 2013-07-25 | 2013-07-25 15:25 | 2013-07-25 15:26 | CARRIER - 38CKC024330 | 54 | 8.3 | Yes | Yes | 24.7 | 23.7 | 1 | 07DBC616E64345E0AB866EECBBCF17A3 |  | R22 | TXV |  | 15.37% | 0.8463 | 29.54% | [5 empty] | TXV | 15.37%
Oroville | CA | 95965-3522 |  | 2013-07-26 | 2013-07-26 10:40 | 2013-07-26 19:58 | DAY & NIGHT - 585B024050YACR | 51 | 7.1 | Yes | Yes | 16.7 | 19.5 | -2.8 | 95626C85D06A4C68A0046029E8A21D7B |  | R22 | Non-TXV |  | 13.92% | 0.86078 | 26.75% | [5 empty] | Non-TXV | 13.92%
Fresno | CA | 93728-1522 |  | 2013-07-16 | 2013-07-16 10:45 | 2013-07-16 10:46 | RHEEM - RRNA-A036JK08X | 114 | 4.7 | Yes | Yes | 20 | 19.3 | 0.7 | 035E8D5AD24E44CB9E260C03459151BD |  | R22 | Non-TXV |  | 4.123% | 0.95877 | 7.923% | [5 empty] | Non-TXV | 4.123%
Colfax | CA | 95713-9662 |  | 2013-09-03 | 2013-09-03 10:41 | 2013-09-03 10:57 | AMANA - APG153009041 | 73 | 3.1 | Yes | Yes | 16 | 18.7 | -2.7 | F470801F757B4AFC92E37FF99085A364 |  | R410A | Non-TXV |  | 4.247% | 0.95753 | 8.161% | [5 empty] | Non-TXV | 4.247%
Colfax | CA | 95713-9662 |  | 2013-09-03 | 2013-09-03 10:30 | 2013-09-03 10:50 | DAY & NIGHT - 591ANX024000AAAA | 53 | 1.6 | Yes | Yes | 19 | 17.2 | 1.8 | 88ACAFE0C71E4DB5A98D80DDC4F59181 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Marysville | CA | 95901-8265 |  | 2013-07-02 | 2013-07-02 11:22 | 2013-07-02 11:22 | CARRIER - 38CKC042350 | 85 | 0 | Yes | Yes | 14 | 17 | -3 | B946745CE0A0439183E286E22F60FB07 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1253 |  | 2013-06-26 | 2013-06-26 10:19 | 2013-06-26 10:37 | LENNOX - GCS20RV-311-75-1P | 72 | 2.5 | Yes | Yes | 16.9 | 15.3 | 1.7 | A2C1DAA6D2ED49F199C2DF99FB85C108 |  | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Fresno | CA | 93704-1406 |  | 2013-08-12 | 2013-08-12 11:27 | 2013-08-12 11:29 | ICP - NAC236MKA1 | 114 | 13.8 | Yes | Yes | 18.7 | 16.6 | 2.1 | 2740BAFCD58240459E86ECBE5A192595 |  | R22 | Non-TXV |  | 12.11% | 0.87895 | 23.26% | [5 empty] | Non-TXV | 12.11%
Stockton | CA | 95212-2872 |  | 2013-06-26 | 2013-06-26 13:23 | 2013-06-26 13:55 | CARRIER - 38CKC060370 | 131 | 4 | Yes | Yes | 23.2 | 23.1 | 0.1 | 74C135BBE04B4C7CA13F9F88627E0F36 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.053% | 0.96947 | 5.868% | [5 empty] | Non-TXV | 3.053%
Chico | CA | 95928-6265 |  | 2013-07-10 | 2013-07-10 20:30 | 2013-07-10 20:49 | YORK - M-H2RC030S06A | 88 | 8.4 | Yes | Yes | 21.5 | 21.5 | 0 | 4D5E0DC85FC74C8994DEC77314E91C61 |  | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Marysville | CA | 95901-6526 |  | 2013-06-29 | 2013-06-29 15:16 | 2013-06-29 15:35 | HEIL - PGC030K060E | 58 | 5.3 | Yes | Yes | 21 | 20.2 | 0.8 | 2F359E577F6744279DF393617869595D |  | R22 | TXV |  | 9.138% | 0.90862 | 17.56% | [5 empty] | TXV | 9.138%
Fresno | CA | 93711-2680 |  | 2013-08-28 | 2013-08-28 09:47 | 2013-08-28 09:50 | RHEEM - UNK | 56 | 6 | Yes | Yes | 22.1 | 20.4 | 1.7 | CDE56369F84B4BAE9991E5C6DF44A1E7 |  | R22 | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Grass Valley | CA | 95945-3901 |  | 2013-07-03 | 2013-07-03 11:30 | 2013-07-03 11:50 | CARRIER - 38CKC024340 | 63 | 1.9 | Yes | Yes | 24 | 19.9 | 4.1 | ECF505DD44344AD59970B210AE4660C6 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Madera | CA | 93637-9115 |  | 2013-07-31 | 2013-07-31 09:36 | 2013-08-02 10:15 | AMANA - NK | 85 | 3.9 | Yes | Yes | 16.3 | 18.8 | -2.5 | FC1A5359507D416D8F52E9CCE64F5F38 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Rocklin | CA | 95677-2856 |  | 2013-07-20 | 2013-07-20 13:44 | 2013-07-20 13:44 | LENNOX - HS26-042-4P | 101 | 0 | Yes | Yes | 23 | 21 | 2 | 911074B5CAFA412B8D8974D5A9E864ED |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1920 |  | 2013-07-08 | 2013-07-08 16:37 | 2013-07-08 16:37 | GOODMAN - GPG13420701AA | 107 | 0 | Yes | Yes | 22.8 | 22.1 | 0.8 | E2ED730AC43C4450B7C53CFDC88ACD90 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-6960 |  | 2013-07-29 | 2013-07-29 10:33 | 2013-07-29 11:08 | RUUD - UAKB-036JAZ | 79 | 11.5 | Yes | Yes | 17.8 | 20.7 | -2.9 | FC71CFDE9F0F455BA2A656E85E7B526B |  | R22 | Non-TXV |  | 14.56% | 0.85443 | 27.98% | [5 empty] | Non-TXV | 14.56%
Stockton | CA | 95210-4613 |  | 2013-07-11 | 2013-07-11 11:05 | 2013-07-11 11:23 | GOODMAN - GSC130241EA | 77 | -4.5 | Yes | Yes | 19.4 | 18.6 | 0.8 | 4DB56DAC41A14CDDB91929DE23466FF1 |  | R22 | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Chowchilla | CA | 93610-3247 |  | 2013-06-27 | 2013-06-27 20:22 | 2013-06-27 20:50 | BDP - DAYQ-F024N080A | 78 | 2.8 | Yes | Yes | 18.3 | 20.4 | -2.1 | 9B115F27DA744161B6933B90999BCF8A |  | R410A | Non-TXV |  | 3.59% | 0.9641 | 6.899% | [5 empty] | Non-TXV | 3.59%
Red Bluff | CA | 96080-4037 |  | 2013-07-20 | 2013-07-20 19:04 | 2013-07-20 19:20 | BRYANT - 1609E0145 | 88 | 3.6 | Yes | Yes | 19.7 | 21.9 | -2.2 | C68EE539549F4F39B94426F0D81BCAD5 |  | R410A | TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | TXV | 4.091%
Merced | CA | 95340-2343 |  | 2013-06-28 | 2013-06-28 16:10 | 2013-06-28 16:13 | TRANE - T7247B100A1 | 67 | 3 | Yes | Yes | 24 | 19.3 | 4.7 | BE79EA03E67C473A956645A0CC403D5C |  | R22 | Non-TXV |  | 4.478% | 0.95522 | 8.605% | [5 empty] | Non-TXV | 4.478%
Marysville | CA | 95901-8051 |  | 2013-08-21 | 2013-08-21 14:35 | 2013-08-21 14:58 | FRIGIDAIRE - FS3BD-030K | 114 | 4.2 | Yes | Yes | 16 | 19 | -3 | C03780A86F754E3D93F563CD10EC3633 |  | R22 | TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | TXV | 3.684%
Grass Valley | CA | 95945-3904 |  | 2013-10-07 | 2013-10-07 10:28 | 2013-10-07 10:53 | CARRIER - 38CKC018340 | 50 | 3.4 | Yes | Yes | 24 | 21 | 3 | 888116E161EC46B7B21FAAD45ECCF29B |  | R22 | Non-TXV |  | 6.8% | 0.932 | 13.07% | [5 empty] | Non-TXV | 6.8%
Marysville | CA | 95901-8215 |  | 2013-07-02 | 2013-07-02 13:31 | 2013-07-02 13:31 | OTHER - 561CJO36-D | 85 | 0 | Yes | Yes | 19 | 20.6 | -1.6 | 76ED264D4D3844ADB35A83C7613CC511 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1214 |  | 2013-06-26 | 2013-06-26 09:50 | 2013-06-26 10:08 | AMANA - RCC36A2D | 114 | -6.7 | Yes | Yes | 15.7 | 15.3 | 0.4 | 5E4B468776124D84A2C03E48ACEC1BEA |  | R22 | Non-TXV |  | -5.877% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.877%
Merced | CA | 95340-2343 |  | 2013-07-10 | 2013-07-10 12:06 | 2013-07-10 12:09 | CARRIER - 38CK30300 | 70 | 3.3 | Yes | Yes | 21.6 | 17.5 | 4.1 | DC167724C02649F9A95EF36A80C76940 |  | R22 | Non-TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | Non-TXV | 4.714%
Fresno | CA | 93711-4032 |  | 2013-08-26 | 2013-08-26 10:34 | 2013-08-26 10:36 | CARRIER - 38CK030340 | 68 | 4.8 | Yes | Yes | 16.9 | 19.8 | -2.9 | CB888A0A55AD4785B4DA760F8FDF2F4A |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Merced | CA | 95340-0925 |  | 2013-06-27 | 2013-06-27 11:51 | 2013-06-27 12:00 | GOODMAN - PGB0420751A | 68 | 7.2 | Yes | Yes | 23.6 | 19.4 | 4.2 | B0F75D289DAF421094588ED7A845A16F |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Los Banos | CA | 93635-3090 |  | 2013-07-08 | 2013-07-08 10:32 | 2013-07-08 10:35 | LENNOX - 12GCS048X1005PD | 167 | 15.4 | Yes | Yes | 19.6 | 19.7 | -0.1 | D9A09050222D4CA3A36BED0B97968AEF |  | R22 | Non-TXV |  | 9.222% | 0.90778 | 17.72% | [5 empty] | Non-TXV | 9.222%
Fresno | CA | 93704-6323 |  | 2013-06-26 | 2013-06-26 12:15 | 2013-06-26 12:17 | OTHER - GR6GD-X24KO45X | 99 | 3.8 | Yes | Yes | 20.6 | 17.6 | 3 | 27C485E3FB9C49F08738D37A7356315F |  | R410A | Non-TXV |  | 3.838% | 0.96162 | 7.377% | [5 empty] | Non-TXV | 3.838%
Mendota | CA | 93640-9724 |  | 2013-08-13 | 2013-08-13 15:38 | 2013-08-13 16:26 | RHEEM - RRGH-05N30JKR | 79 | 3.1 | Yes | Yes | 22 | 21.7 | 0.4 | A24A4C530BD34EE2B4986552E10AF72D |  | R22 | Non-TXV |  | 3.924% | 0.96076 | 7.541% | [5 empty] | Non-TXV | 3.924%
Fresno | CA | 93727-7972 |  | 2013-07-16 | 2013-07-16 14:34 | 2013-07-16 15:27 | CARRIER - N/A | 90 | 3.2 | Yes | Yes | 22.5 | 17.2 | 5.3 | 7A9270FD3C1F40D59F209276E44CD701 |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Stockton | CA | 95206-2351 |  | 2013-07-03 | 2013-07-03 09:55 | 2013-07-03 10:19 | GOODMAN - GPG10360701A | 85 | -8 | Yes | Yes | 25.1 | 19.5 | 5.6 | 98634A9A9CCA4A7DA395B15240E39D49 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Los Banos | CA | 93635-5467 |  | 2013-07-10 | 2013-07-10 11:39 | 2013-07-10 11:43 | TRANE - 2TTM3030A1000AA | 83 | 6.9 | Yes | Yes | 22.8 | 23.6 | -0.8 | 370C7FEBA507469AA9F5A09D1141E015 |  | R22 | Non-TXV |  | 8.313% | 0.91687 | 15.98% | [5 empty] | Non-TXV | 8.313%
Auburn | CA | 95602-9090 |  | 2013-06-27 | 2013-06-27 15:16 | 2013-06-27 15:16 | PAYNE - 591ANX048000ACAA | 128 | 0 | Yes | Yes | 20.1 | 18.8 | 1.3 | 73EE4DB901844066B5E3363C5635FAC5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-6707 |  | 2013-07-11 | 2013-07-11 08:21 | 2013-07-11 08:51 | BRYANT - 561CJ048-A | 159 | 8.7 | Yes | Yes | 23.8 | 19.9 | 3.9 | 0F3DD1E7845144B68B6F27BD489B4A83 |  | R22 | Non-TXV |  | 5.472% | 0.94528 | 10.52% | [5 empty] | Non-TXV | 5.472%
Lathrop | CA | 95330-8950 |  | 2013-07-08 | 2013-07-08 15:04 | 2013-07-08 15:22 | YORK - H1RA042S06D | 84 | 3.5 | Yes | Yes | 19.3 | 21 | -1.7 | A869F148AEC74D20803D68681EB216C1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Fresno | CA | 93711-4049 |  | 2013-08-10 | 2013-08-10 13:46 | 2013-08-10 13:53 | RHEEM - 7777UNK | 86 | 4.8 | Yes | Yes | 20.6 | 20.4 | 0.2 | 567271ADB19B4A3385FC7EF32C026D1F |  | R22 | Non-TXV |  | 5.581% | 0.94419 | 10.73% | [5 empty] | Non-TXV | 5.581%
Stockton | CA | 95204-5619 |  | 2013-07-09 | 2013-07-09 11:57 | 2013-07-09 11:57 | RHEEM - 13AJA2401757 | 68 | 0 | Yes | Yes | 20.8 | 18.4 | 2.4 | 4CAEAD16396A4025B75DCF6C19420DC3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-1611 |  | 2013-07-09 | 2013-07-09 15:37 | 2013-07-09 15:39 | YORK - D2NP036N05606A | 108 | 5.5 | Yes | Yes | 20.4 | 18.8 | 1.6 | D4FD6AE7AD2A46B0B9B8042FDB3575C7 |  | R22 | Non-TXV |  | 5.093% | 0.94907 | 9.787% | [5 empty] | Non-TXV | 5.093%
Auburn | CA | 95602-9660 |  | 2013-06-27 | 2013-06-27 11:30 | 2013-06-27 11:30 | COLEMAN - DAYP-F042N110A | 150 | 0 | Yes | Yes | 15.9 | 17.2 | -1.3 | E6075F3F98234727B00DC18FA65F0876 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3174 |  | 2013-07-12 | 2013-07-12 16:50 | 2013-07-12 16:54 | OTHER - WHC3242GKR2 | 74 | 4 | Yes | Yes | 18.4 | 19.3 | -0.9 | F7FA07AB6FE04CA8AE727BB9094792A6 |  | R22 | Non-TXV |  | 5.405% | 0.94595 | 10.39% | [5 empty] | Non-TXV | 5.405%
Kingsburg | CA | 93631-2630 |  | 2013-08-03 | 2013-08-03 19:20 | 2013-08-03 19:39 | WEATHER KING - WRKA-A036JK06E | 62 | 5.2 | Yes | Yes | 19.1 | 19 | 0.1 | C45CC619887842A8A84F8969FB836C26 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.387% | 0.91613 | 16.12% | [5 empty] | Non-TXV | 8.387%
Stockton | CA | 95206-3873 |  | 2013-07-17 | 2013-07-17 16:42 | 2013-07-17 17:05 | CARRIER - 24ABA336A300 | 82 | 14 | Yes | Yes | 21.3 | 23.6 | -2.3 | 5A955852A8F54A10B081DF23EE7BDFFD |  | R410A | Non-TXV |  | 17.07% | 0.82927 | 32.81% | [5 empty] | Non-TXV | 17.07%
Red Bluff | CA | 96080-2031 |  | 2013-07-20 | 2013-07-20 17:30 | 2013-07-20 18:34 | GIBSON - JS3BC-036KA | 82 | 2.4 | Yes | Yes | 18 | 21 | -3 | B6ECBCC865AC42C49D6FD0B31650F1EE |  | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Marysville | CA | 95901-8045 |  | 2013-07-12 | 2013-07-12 14:05 | 2013-07-12 14:27 | FRIGIDAIRE - FS3BA-030KA | 68 | -6.4 | Yes | Yes | 17 | 18.5 | -1.5 | 54EC818711654F87AA50AFF973B9FB18 |  | R22 | TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | TXV |  |  | -9.412%
Stockton | CA | 95210-5666 |  | 2013-09-05 | 2013-09-05 10:24 | 2013-09-05 10:46 | CARRIER - 38CKC030340 | 71 | 12.3 | Yes | Yes | 21.1 | 17.7 | 3.5 | 17AB14B59A164B97982105009E4F05E6 |  | R22 | Non-TXV |  | 17.32% | 0.82676 | 33.29% | [5 empty] | Non-TXV | 17.32%
Los Banos | CA | 93635-5402 |  | 2013-07-10 | 2013-07-10 10:40 | 2013-07-10 10:51 | PAYNE - UNK | 76 | 10.3 | Yes | Yes | 20.2 | 20.2 | 0 | 42A6D25C15974E9ABEBB382DEEC6771E |  | R22 | Non-TXV |  | 13.55% | 0.86447 | 26.05% | [5 empty] | Non-TXV | 13.55%
Selma | CA | 93662-9730 |  | 2013-08-09 | 2013-08-09 13:33 | 2013-08-09 13:55 | GOODMAN - N/A | 90 | 4.8 | Yes | Yes | 26.5 | 22.2 | 4.3 | E471BD2D182941B3B602F4526BDE803E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Selma | CA | 93662-9730 |  | 2013-08-09 | 2013-08-09 13:56 | 2013-08-09 14:17 | GOODMAN - N/A | 90 | 4.9 | Yes | Yes | 17.5 | 20.4 | -2.9 | 54A749F734F24DFDAFCD4C73E139B3DB |  | R22 | Non-TXV |  | 5.444% | 0.94556 | 10.46% | [5 empty] | Non-TXV | 5.444%
Oroville | CA | 95966-7159 |  | 2013-07-29 | 2013-07-29 09:47 | 2013-07-29 10:31 | ALLEGIANCE - 7A0036A100A1 | 88 | 2.7 | Yes | Yes | 23.5 | 19.4 | 4.1 | B6481659BD1D4B2CBEF8B311D2F83B46 |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Stockton | CA | 95205-2594 |  | 2013-07-17 | 2013-07-17 09:03 | 2013-07-17 09:21 | CARRIER - 38EZ303630 | 100 | 5 | Yes | Yes | 19.1 | 19.9 | -0.8 | 596A50C4AA31448EBC870A42CD57FEC9 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93711-4042 |  | 2013-08-10 | 2013-08-10 14:06 | 2013-08-10 14:11 | CARRIER - 38CK030-341 | 68 | 3.5 | Yes | Yes | 16.4 | 19.4 | -3 | A1543A46CBDA422389F7EC01D3FFB180 |  | R22 | Non-TXV |  | 5.147% | 0.94853 | 9.892% | [5 empty] | Non-TXV | 5.147%
Fresno | CA | 93720-2452 |  | 2013-08-16 | 2013-08-16 11:36 | 2013-08-16 11:38 | CARRIER - 38EA024310 | 55 | 7.9 | Yes | Yes | 16.9 | 17 | -0.1 | A77939E312AC4A84A1B83DC7D390812C |  | R22 | Non-TXV |  | 14.36% | 0.85636 | 27.6% | [5 empty] | Non-TXV | 14.36%
Los Banos | CA | 93635-3626 |  | 2013-07-09 | 2013-07-09 11:28 | 2013-07-09 11:31 | NORDYNE - GS3BKA2A0 | 64 | 5.7 | Yes | Yes | 20.8 | 21.3 | -0.5 | 1C5E479F75AB4375A08FF014D37C13DE |  | R22 | Non-TXV |  | 8.906% | 0.91094 | 17.12% | [5 empty] | Non-TXV | 8.906%
Fresno | CA | 93722-3501 |  | 2013-07-18 | 2013-07-18 15:22 | 2013-07-18 15:29 | CARRIER - 569EBX060000AAAA | 197 | 18.9 | Yes | Yes | 21.4 | 20.8 | 0.6 | BCD71FD39A8040AA82A217E9A98244AB |  | R22 | Non-TXV |  | 9.594% | 0.90406 | 18.44% | [5 empty] | Non-TXV | 9.594%
Grass Valley | CA | 95945-6313 |  | 2013-06-29 | 2013-06-29 10:43 | 2013-06-29 11:02 | BDP - 588ANW048080AEAG | 104 | 8.3 | Yes | Yes | 18.9 | 18.7 | 0.2 | 4A451318CABC4D68808D07B2D33BBEE4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.981% | 0.92019 | 15.34% | [5 empty] | Non-TXV | 7.981%
Stockton | CA | 95206-6047 |  | 2013-08-13 | 2013-08-13 11:27 | 2013-08-13 11:45 | PAYNE - PA10JA030-C | 77 | 11.8 | Yes | Yes | 22.3 | 17.9 | 4.4 | D17B8EAB74BB4E92A31F2BA2AA26E8AD |  | R22 | Non-TXV |  | 15.32% | 0.84675 | 29.45% | [5 empty] | Non-TXV | 15.32%
Fresno | CA | 93725-0000 |  | 2013-08-06 | 2013-08-06 23:44 | 2013-08-06 23:46 | LENNOX - 13ACD-060-230-02 | 214 | 6.3 | Yes | Yes | 16.9 | 18 | -1.1 | 4D2C5E0FBFD04B02B0EB00E8636437D2 |  | R22 | Non-TXV |  | 2.944% | 0.97056 | 5.658% | [5 empty] | Non-TXV | 2.944%
Parlier | CA | 93648-2861 |  | 2013-08-28 | 2013-08-28 11:21 | 2013-08-28 12:18 | CONCORD - CCU10A24A-1 | 50 | 6.5 | Yes | Yes | 18 | 20.4 | -2.4 | 01744DC5E6004A5089DE2D56EB7DD675 |  | R22 | Non-TXV |  | 13% | 0.87 | 24.98% | [5 empty] | Non-TXV | 13%
Manteca | CA | 95337-4460 |  | 2013-07-24 | 2013-07-24 12:08 | 2013-07-24 12:35 | YORK - D3NZ02403606NXA | 58 | 8.1 | Yes | Yes | 17.1 | 19.9 | -2.8 | 139A76EA1880437AACAFDA39447F19A3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 13.97% | 0.86034 | 26.84% | [5 empty] | Non-TXV | 13.97%
Marysville | CA | 95901-8229 |  | 2013-07-02 | 2013-07-02 12:34 | 2013-07-02 12:34 | CARRIER - UNK | 70 | 0 | Yes | Yes | 13.5 | 15.5 | -2 | 8ACF01F46B6A41EFBA92768B883850FA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5463 |  | 2013-08-07 | 2013-08-07 15:39 | 2013-08-07 16:07 | GE - BTV936A100B2 | 144 | 27.9 | Yes | Yes | 22.8 | 24.2 | -1.4 | F0676F27D0B84031B4DBB6A0F708F836 |  | R22 | Non-TXV |  | 19.38% | 0.80625 | 37.23% | [5 empty] | Non-TXV | 19.38%
Fresno | CA | 93722-3846 |  | 2013-07-22 | 2013-07-22 08:35 | 2013-07-22 08:52 | RHEEM - UNK | 50 | 7.4 | Yes | Yes | 15.1 | 17.7 | -2.6 | 81D3EBE2214F4A97B40DB6DFCD745018 |  | R22 | Non-TXV |  | 14.8% | 0.852 | 28.44% | [5 empty] | Non-TXV | 14.8%
Fresno | CA | 93722-2264 |  | 2013-07-15 | 2013-07-15 10:00 | 2013-07-15 10:10 | WEATHER KING - 10AJA6001 | 132 | 14.6 | Yes | Yes | 19 | 21 | -2 | 16E05D4DCC864CC0B728C8F6503A547A |  | R22 | Non-TXV |  | 11.06% | 0.88939 | 21.26% | [5 empty] | Non-TXV | 11.06%
Winton | CA | 95388-9783 |  | 2013-07-22 | 2013-07-22 15:54 | 2013-07-22 15:56 | HEIL - UNK | 60 | 6.7 | Yes | Yes | 16.4 | 19.2 | -2.8 | D7305D2C97284901B961771D98BF78ED |  | R22 | Non-TXV |  | 11.17% | 0.88833 | 21.46% | [5 empty] | Non-TXV | 11.17%
Oakhurst | CA | 93644-8868 |  | 2013-09-12 | 2013-09-12 11:31 | 2013-09-12 11:33 | CARRIER - 542EJ024 | 100 | 5.7 | Yes | Yes | 22 | 19.3 | 2.7 | A83A017F6773446898EC28507B11D3BA |  | R22 | Non-TXV |  | 5.7% | 0.943 | 10.95% | [5 empty] | Non-TXV | 5.7%
Colfax | CA | 95713-9500 |  | 2013-11-20 | 2013-11-20 09:28 | 2013-11-20 09:28 | PAYNE - UNK | 100 | 0 | Yes | Yes | 27.6 | 18.8 | 8.8 | F69E3DFD3E9B46D9AA55CDF98A6B23BE | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6886 |  | 2013-07-16 | 2013-07-16 12:21 | 2013-07-16 12:53 | BDP - 563CN036-B | 113 | 8.6 | Yes | Yes | 22.4 | 20.4 | 2 | 22B86115B1D5417C9C59EF166958B54E |  | R22 | Non-TXV |  | 7.611% | 0.92389 | 14.63% | [5 empty] | Non-TXV | 7.611%
Valley Springs | CA | 95252-8988 |  | 2013-09-30 | 2013-09-30 17:05 | 2013-10-01 09:48 | LENNOX - 13ACD03623001 | 110 | 6.3 | Yes | Yes | 20.4 | 18.8 | 1.6 | A065B5921E734CEF9DBE4E29BAA926B0 |  | R22 | Non-TXV |  | 5.727% | 0.94273 | 11.01% | [5 empty] | Non-TXV | 5.727%
Fresno | CA | 93710-6429 |  | 2013-06-28 | 2013-06-28 11:41 | 2013-06-28 11:47 | RHEEM - RAMA-036JAZ | 96 | 3.2 | Yes | Yes | 18.7 | 18.1 | 0.6 | D3711C1109E94E0CAD199F0D21BC2F4B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93722-3260 |  | 2013-08-12 | 2013-08-12 16:00 | 2013-08-12 16:05 | YORK - H1RA036S06A | 69 | 2.2 | Yes | Yes | 18.5 | 19.9 | -1.4 | 2D18E92DF3A34C569CC18FE6E0284CFB |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Cameron Park | CA | 95682-7423 |  | 2013-07-19 | 2013-07-19 12:17 | 2013-07-19 12:34 | AMERICAN STANDARD - 2A6H3036A10000AA | 118 | 6.4 | Yes | Yes | 23 | 22.8 | 0.2 | 7CA0FB6585F44D4AB1CF03B320AFDDD5 |  | R22 | Non-TXV |  | 5.424% | 0.94576 | 10.42% | [5 empty] | Non-TXV | 5.424%
Chico | CA | 95926-5305 |  | 2013-07-09 | 2013-07-09 19:17 | 2013-07-09 19:17 | PAYNE - NA | 60 | 0 | Yes | Yes | 24.7 | 21 | 3.7 | B7A86E0059EC44EBAB889CD5BD81A2FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9633 |  | 2013-09-30 | 2013-09-30 16:48 | 2013-09-30 17:28 | RUUD - N/A | 60 | 2.1 | Yes | Yes | 17.7 | 20.4 | -2.7 | 80AC1B3DDC9643249ACD32A8AD82AB78 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Marysville | CA | 95901-3046 |  | 2013-06-26 | 2013-06-26 13:48 | 2013-06-26 14:11 | CARRIER - 38CKC036350 | 75 | 13.3 | Yes | Yes | 16 | 18.3 | -2.3 | 53489341D9434806B3DF7BB87D0B8578 |  | R22 | Non-TXV |  | 17.73% | 0.82267 | 34.08% | [5 empty] | Non-TXV | 17.73%
Paso Robles | CA | 93446-3625 |  | 2013-08-06 | 2013-08-06 16:25 | 2013-08-06 16:44 | PAYNE - PA13NR030-C | 120 | 3.7 | Yes | Yes | 20.6 | 19.4 | 1.2 | 82F3210B398146478E14F386C06BD64F |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Los Banos | CA | 93635-9475 |  | 2013-08-17 | 2013-08-17 11:16 | 2013-08-17 11:18 | BRYANT - 561CJ042-E | 80 | 4.6 | Yes | Yes | 20.4 | 20.4 | 0 | 2DE0375BD62242B999EDFCCC2F7C5440 |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Fresno | CA | 93705-0109 |  | 2013-07-09 | 2013-07-09 09:40 | 2013-07-09 09:40 | AMERICAN STANDARD - CM18-41T | 38 | 0 | Yes | Yes | 22 | 22.4 | -0.4 | 9372B7AFAFEC4E658B0F779DBA6B7889 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-4026 |  | 2013-08-27 | 2013-08-27 14:52 | 2013-08-27 14:53 | CARRIER - CK38C030340 | 68 | 2.1 | Yes | Yes | 14.8 | 17.7 | -2.9 | C9772D3A3F4F4DF9B3F9D19D85D36528 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Fresno | CA | 93727-7257 |  | 2013-07-19 | 2013-07-19 13:48 | 2013-07-19 14:10 | PAYNE - N/A | 90 | 8.8 | Yes | Yes | 27 | 21.2 | 5.8 | 62E153389F334158B229EEC0CCCC6423 |  | R22 | Non-TXV |  | 9.778% | 0.90222 | 18.79% | [5 empty] | Non-TXV | 9.778%
Magalia | CA | 95954-9677 |  | 2013-08-29 | 2013-08-29 03:23 | 2013-08-29 15:40 | YORK - D1NH048ND65D6C | 129 | 10.6 | Yes | Yes | 20.3 | 22.9 | -2.6 | D757ED2065E04F6A8F2C40F3BD9493D1 |  | R22 | Non-TXV |  | 8.217% | 0.91783 | 15.79% | [5 empty] | Non-TXV | 8.217%
Fresno | CA | 93711-4034 |  | 2013-08-27 | 2013-08-27 15:16 | 2013-08-27 15:18 | CARRIER - 24ARB330A0031010 | 84 | 4 | Yes | Yes | 20.8 | 23.7 | -2.9 | 9289F8118DCE4CBC91559AFE1A7A85AD |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Stockton | CA | 95207-1566 |  | 2013-07-17 | 2013-07-17 13:30 | 2013-07-17 13:54 | PAYNE - 48GS-024060301 | 53 | 4.3 | Yes | Yes | 21.7 | 19.9 | 1.8 | AB74BD457F834AE184DF9E60ECB0F5DE |  | R22 | Non-TXV |  | 8.113% | 0.91887 | 15.59% | [5 empty] | Non-TXV | 8.113%
Chico | CA | 95973-4957 |  | 2013-07-10 | 2013-07-10 20:55 | 2013-07-10 21:14 | RUUD - 13AJA36A01206913 | 86 | 2.7 | Yes | Yes | 18.2 | 20.4 | -2.2 | ADA6616D0D014E218264A5D0763E1C88 |  | R22 | Non-TXV |  | 3.14% | 0.9686 | 6.033% | [5 empty] | Non-TXV | 3.14%
Newcastle | CA | 95658-9617 |  | 2013-08-08 | 2013-08-08 13:28 | 2013-08-08 13:28 | AMERICAN STANDARD - WCH060F100AB | 171 | 0 | Yes | Yes | 25 | 19.9 | 5.1 | BD63AECF1AAA432C9255DA87C1D19F0E |  | R22 | TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9626 |  | 2013-08-28 | 2013-08-28 13:02 | 2013-08-28 13:19 | RUUD - N/A | 60 | 3.5 | Yes | Yes | 19 | 20.6 | -1.6 | 92BA5CE7083849B7842A402E5868DF8C |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Madera | CA | 93637-5312 |  | 2013-07-22 | 2013-07-22 11:47 | 2013-07-22 12:19 | ICP - PGN430060K1 | 120 | -9.9 | Yes | Yes | 21.3 | 19.1 | 2.3 | 59C6CFDBD68F4B44A3D0A3317FF0EF36 |  | R22 | Non-TXV |  | -8.25% | 1.0825 | 2.31% |  |  |  |  | Non-TXV |  |  | -8.25%
Fresno | CA | 93705-1523 |  | 2013-07-08 | 2013-07-08 15:48 | 2013-07-08 16:10 | LENNOX - HS25-511-2P | 216 | 21.7 | Yes | Yes | 18 | 20.2 | -2.2 | C38972B5C5D34F7F9FC1E903B7E1E283 |  | R22 | Non-TXV |  | 10.05% | 0.89954 | 19.31% | [5 empty] | Non-TXV | 10.05%
Madera | CA | 93637-5017 |  | 2013-08-05 | 2013-08-05 10:27 | 2013-08-05 10:34 | YORK - H1RA024S06G | 59 | 6.3 | Yes | Yes | 19.2 | 18.2 | 1 | DA2ACBBD48B747C9BA3691AEF383F19C |  | R22 | Non-TXV |  | 10.68% | 0.89322 | 20.52% | [5 empty] | Non-TXV | 10.68%
Fresno | CA | 93722-7133 |  | 2013-07-15 | 2013-07-15 12:54 | 2013-07-15 13:13 | LENNOX - HS253111P | 129 | 17.5 | Yes | Yes | 21.7 | 22.5 | -0.8 | F7CE2AE3F18046A0BD672B366DB99051 |  | R22 | Non-TXV |  | 13.57% | 0.86434 | 26.07% | [5 empty] | Non-TXV | 13.57%
Stockton | CA | 95206-6374 |  | 2013-07-03 | 2013-07-03 10:17 | 2013-07-03 10:43 | CARRIER - 38CKC048360 | 98 | -5.8 | Yes | Yes | 15.7 | 18.6 | -2.9 | 236CEAB6EDC44B27A33171C38A86182F |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Fresno | CA | 93705-1523 |  | 2013-07-08 | 2013-07-08 14:29 | 2013-07-08 15:02 | DAY & NIGHT - N/A | 90 | 22.4 | Yes | Yes | 18.3 | 19.1 | -0.8 | 8A5B0442C1224B028B54E8BDC085FB96 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 24.89% | 0.75111 | 47.83% | [5 empty] | Non-TXV | 24.89%
Fresno | CA | 93705-1523 |  | 2013-07-08 | 2013-07-08 15:05 | 2013-07-08 15:41 | DAY & NIGHT - N/A | 90 | 10.9 | Yes | Yes | 21.7 | 21.3 | 0.4 | 888051915B2F4034A092CA09E1C3B77D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.11% | 0.87889 | 23.27% | [5 empty] | Non-TXV | 12.11%
Fresno | CA | 93703-4825 |  | 2013-08-08 | 2013-08-08 14:04 | 2013-08-08 14:12 | GOODMAN - GPG10300701A | 50 | 7.1 | Yes | Yes | 22.9 | 18.5 | 4.4 | 6FDD3EEBA1524990836DB6C950BA1CF5 |  | R22 | Non-TXV |  | 14.2% | 0.858 | 27.29% | [5 empty] | Non-TXV | 14.2%
Fresno | CA | 93711-2600 |  | 2013-08-15 | 2013-08-15 11:52 | 2013-08-15 11:56 | RHEEM - 7777UNK | 68 | 3.4 | Yes | Yes | 17.5 | 20.4 | -2.9 | 4D4CCEA994E24D9B9DABB38D38462CD0 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Manteca | CA | 95337-6601 |  | 2013-09-13 | 2013-09-13 14:06 | 2013-09-13 14:26 | AMERICAN STANDARD - YCY060G1M0AB | 151 | 8 | Yes | Yes | 18.4 | 20.6 | -2.2 | 7AFD17FB36D642A98164200829909116 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.298% | 0.94702 | 10.18% | [5 empty] | Non-TXV | 5.298%
Marysville | CA | 95901-8237 |  | 2013-07-01 | 2013-07-01 15:30 | 2013-07-01 16:02 | YORK - H2RA030S06D | 62 | -4.4 | Yes | Yes | 16 | 18.8 | -2.8 | 06E536BC99C24E41B1E4124E93B353BB |  | R22 | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Chico | CA | 95926-4205 |  | 2013-08-23 | 2013-08-23 09:41 | 2013-08-23 11:15 | PAYNE - PH10JAS030-P | 82 | 4.1 | Yes | Yes | 17.6 | 18.9 | -1.3 | CB19DDEE4D0C43F0B20237C17C0ABDFF |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Fresno | CA | 93705-4129 |  | 2013-07-10 | 2013-07-10 12:04 | 2013-07-10 12:25 | RHEEM - URKA0A036JK06E | 62 | 5.2 | Yes | Yes | 21.6 | 21.6 | 0.1 | 0A627DD62A1B4E5080C821B66845C503 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.387% | 0.91613 | 16.12% | [5 empty] | Non-TXV | 8.387%
Manteca | CA | 95336-3903 |  | 2013-07-18 | 2013-07-18 08:23 | 2013-07-18 08:49 | RHEEM - CBD | 64 | 2.5 | Yes | Yes | 20.1 | 18.8 | 1.3 | 8DB971E7269D4E50B3CDFF1D0A8ACB83 |  | R22 | Non-TXV |  | 3.906% | 0.96094 | 7.507% | [5 empty] | Non-TXV | 3.906%
Ripon | CA | 95366-2810 |  | 2013-07-24 | 2013-07-24 15:14 | 2013-07-24 15:37 | BRYANT - 574ANW030060NB | 39 | 4.3 | Yes | Yes | 19.7 | 18.8 | 0.9 | 984D698CFF8D4BEF8BB19C0ADBC3E313 |  | R22 | Non-TXV |  | 11.03% | 0.88974 | 21.19% | [5 empty] | Non-TXV | 11.03%
Magalia | CA | 95954-9123 |  | 2013-07-18 | 2013-07-18 10:38 | 2013-07-18 11:08 | BRYANT - 561CJX030000AEAA | 69 | 5 | Yes | Yes | 17.1 | 19.9 | -2.8 | F26274EDBECA4B14BC026716CD368175 |  | R22 | TXV |  | 7.246% | 0.92754 | 13.93% | [5 empty] | TXV | 7.246%
Madera | CA | 93637-5013 |  | 2013-07-26 | 2013-07-26 12:19 | 2013-07-26 12:19 | YORK - D1NP024NO5606A | 74 | 0 | Yes | Yes | 18.3 | 20.9 | -2.6 | 7DC66158ABB24A56BA43C8E80F6068C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5004 |  | 2013-07-23 | 2013-07-23 15:35 | 2013-07-23 15:37 | AMERICAN STANDARD - YCC036F1MOBH | 83 | 2.8 | Yes | Yes | 26.3 | 20.6 | 5.7 | 4291CE39B7DB476DA8827FD433A92AE0 |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Manteca | CA | 95336-3940 |  | 2013-07-16 | 2013-07-16 15:12 | 2013-07-16 15:33 | DAY & NIGHT - 591ANX030000ABAA | 85 | 4.2 | Yes | Yes | 20.6 | 20.1 | 0.5 | 45EDF724F3AD44AB922C021499C0490E |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Stockton | CA | 95206-3311 |  | 2013-07-17 | 2013-07-17 09:04 | 2013-07-17 09:04 | BDP - 588ANW060080ADAG | 112 | 0 | Yes | Yes | 24.7 | 18.9 | 5.8 | 29179D3317FC426E844B61BCAE704232 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-3253 |  | 2013-07-31 | 2013-07-31 10:42 | 2013-07-31 10:51 | CARRIER - 38CKC048---371 | 98 | 3.2 | Yes | Yes | 15.8 | 18.6 | -2.8 | 78726EE28665494BA9C17FF28D016626 |  | R22 | Non-TXV |  | 3.265% | 0.96735 | 6.275% | [5 empty] | Non-TXV | 3.265%
Selma | CA | 93662-3253 |  | 2013-07-31 | 2013-07-31 10:53 | 2013-07-31 11:20 | CARRIER - 38CKC036---351B | 70 | 12.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | 99C36B2932FB4C5DAF6FD1EEADADA17D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Fresno | CA | 93722-0000 |  | 2013-07-15 | 2013-07-15 09:07 | 2013-07-15 09:11 | CARRIER - 24ABA342A310 | 98 | 6.2 | Yes | Yes | 26.5 | 20.9 | 5.6 | 8BFB1D3AB4F94CC8A2FA018F5F114713 |  | R410A | TXV |  | 6.327% | 0.93673 | 12.16% | [5 empty] | TXV | 6.327%
Madera | CA | 93638-3981 |  | 2013-07-25 | 2013-07-25 20:41 | 2013-07-25 20:58 | AIRE-FLO - TCGD485211A | 73 | 2.7 | Yes | Yes | 18.7 | 18.8 | -0.1 | 900AD7A00A3743938D94778EAC97CF47 |  | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Fresno | CA | 93722-7114 |  | 2013-07-15 | 2013-07-15 12:28 | 2013-07-15 12:29 | CARRIER - UNK | 67 | 8.6 | Yes | Yes | 21.6 | 22.1 | -0.5 | CEC8ACA7D5C9410D82DC66E1BC99BE25 |  | R22 | Non-TXV |  | 12.84% | 0.87164 | 24.67% | [5 empty] | Non-TXV | 12.84%
Penn Valley | CA | 95946-9568 |  | 2013-09-05 | 2013-09-05 16:00 | 2013-09-05 16:25 | OTHER - CA5530VKA1 | 77 | -3.3 | Yes | Yes | 17 | 19.7 | -2.7 | 833F59FF33AC4A82A3D0D86E8F3985B1 |  | R22 | TXV |  | -4.286% | 1.0429 | 1.2% |  |  |  |  | TXV |  |  | -4.286%
Atwater | CA | 95301-2271 |  | 2013-06-27 | 2013-06-27 08:44 | 2013-06-27 08:48 | BDP - 585HJW030040ABAF | 68 | 5.9 | Yes | Yes | 24.5 | 18.6 | 5.9 | 15463CD4163B43A4B9403474EEADB2A3 |  | R22 | Non-TXV |  | 8.676% | 0.91324 | 16.67% | [5 empty] | Non-TXV | 8.676%
Stockton | CA | 95206-3840 |  | 2013-07-08 | 2013-07-08 09:11 | 2013-07-08 09:27 | RHEEM - UNK | 96 | 4.7 | Yes | Yes | 19.3 | 19 | 0.3 | 1738112110024F2699B0B27D32FD47BC |  | R22 | Non-TXV |  | 4.896% | 0.95104 | 9.409% | [5 empty] | Non-TXV | 4.896%
Grass Valley | CA | 95949-9052 |  | 2013-08-22 | 2013-08-22 19:58 | 2013-08-22 20:18 | CARRIER - 585HJ0480 | 118 | 11.4 | Yes | Yes | 22.9 | 19.1 | 3.8 | 864166D3590E45CFB8380149F1C3CA8A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.661% | 0.90339 | 18.57% | [5 empty] | Non-TXV | 9.661%
Fresno | CA | 93720-0450 |  | 2013-06-26 | 2013-06-26 11:08 | 2013-06-26 11:12 | YORK - 7777UNK | 72 | 3.1 | Yes | Yes | 16.4 | 19.4 | -3 | D78B1B2AA48F43EA9DF7EB19517F5F16 |  | R22 | Non-TXV |  | 4.306% | 0.95694 | 8.274% | [5 empty] | Non-TXV | 4.306%
Fresno | CA | 93705-4120 |  | 2013-07-10 | 2013-07-10 10:23 | 2013-07-10 10:51 | RHEEM - GC-80-36-21C | 49 | 10.4 | Yes | Yes | 20.5 | 21.4 | -0.9 | 323EAC66D44048C69BF7B10AF97C422C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.22% | 0.78776 | 40.79% | [5 empty] | Non-TXV | 21.22%
Paradise | CA | 95969-6530 |  | 2013-08-26 | 2013-08-26 11:04 | 2013-08-26 11:04 | CARRIER - 38TR024300 | 84 | 0 | Yes | Yes | 17.2 | 18.7 | -1.5 | 946DB7E16C4A46F0844C830428FDBBEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Diamond Springs | CA | 95619-9234 |  | 2013-07-05 | 2013-07-05 12:56 | 2013-07-05 12:56 | RHEEM - RQPL-B030JK | 108 | 0 | Yes | Yes | 16 | 18.7 | -2.7 | 49FE3CA174F149969D5B28CB43331BF1 |  | R410A | TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-9108 |  | 2013-07-08 | 2013-07-08 13:43 | 2013-07-08 14:09 | OTHER - CBD | 64 | 8.9 | Yes | Yes | 18.5 | 19.9 | -1.4 | D1E13F173C914837BB99B9BA7BC61618 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.91% | 0.86094 | 26.72% | [5 empty] | Non-TXV | 13.91%
Fresno | CA | 93705-4120 |  | 2013-07-09 | 2013-07-09 16:17 | 2013-07-09 16:54 | PAYNE - PY1PNB030060AAAA | 55 | 3.3 | Yes | Yes | 20 | 17.1 | 2.9 | EBE5934CAD844543B72560E8FC580E00 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93705-4120 |  | 2013-07-09 | 2013-07-09 16:58 | 2013-07-09 17:21 | PAYNE - PY1PNB036060ABAA | 68 | 3.9 | Yes | Yes | 23.7 | 19.9 | 3.8 | DF50542567D74222A122BEE8AC00AFC6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.735% | 0.94265 | 11.02% | [5 empty] | Non-TXV | 5.735%
Grass Valley | CA | 95945-7632 |  | 2013-08-30 | 2013-08-30 09:54 | 2013-08-30 09:54 | PAYNE - PA12NA060-A | 184 | 0 | Yes | Yes | 21.1 | 19.7 | 1.4 | 5B5CF4766C6E4C6EA99E73A7A1E9EAF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-3815 |  | 2013-07-12 | 2013-07-12 11:50 | 2013-07-12 12:13 | RHEEM - RAFD-036JAS | 80 | 3 | Yes | Yes | 23.4 | 19.8 | 3.6 | 976653FCCB4448C19473AFC252875C84 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95215-2248 |  | 2013-08-14 | 2013-08-14 10:03 | 2013-08-14 10:12 | PAYNE - PY3PNA036060NA | 167 | 9.6 | Yes | Yes | 20.7 | 18.2 | 2.5 | 6582ED8E073A4780B08D560FEFF9C089 |  | R22 | Non-TXV |  | 5.749% | 0.94251 | 11.05% | [5 empty] | Non-TXV | 5.749%
Parlier | CA | 93648-2862 |  | 2013-08-30 | 2013-08-30 09:36 | 2013-08-30 09:43 | DUCANE - 2AC13B24P-1A | 89 | 2.8 | Yes | Yes | 17.5 | 20.4 | -2.9 | FFAC5597C50943C3ADF4A41557793007 |  | R22 | Non-TXV |  | 3.146% | 0.96854 | 6.046% | [5 empty] | Non-TXV | 3.146%
Los Banos | CA | 93635-3206 |  | 2013-07-24 | 2013-07-24 12:44 | 2013-07-24 12:46 | RUUD - 7777UNK | 100 | 3.2 | Yes | Yes | 19 | 19.6 | -0.6 | B4432C0A321848F9BDC1DC9CCFEF8875 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Acampo | CA | 95220-9572 |  | 2013-08-21 | 2013-08-21 11:04 | 2013-08-21 11:25 | ALLEGIANCE - 4A7A6048B1000AA | 120 | 6.6 | Yes | Yes | 17.8 | 16.5 | 1.3 | 72E8E94BCC86413794F6A90BA2B03EDB |  | R410A | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Acampo | CA | 95220-9572 |  | 2013-08-21 | 2013-08-21 11:28 | 2013-08-21 11:46 | ALLEGIANCE - 4A7A6036B1000AA | 106 | 3.6 | Yes | Yes | 20.9 | 18.2 | 2.7 | 141C7962AF78470D8AA1A28EEA17CE23 |  | R410A | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Los Banos | CA | 93635-5441 |  | 2013-07-10 | 2013-07-10 11:09 | 2013-07-10 11:19 | RHEEM - UNK | 76 | 14 | Yes | Yes | 22.3 | 22.6 | -0.3 | 5D1F28B803EE4C508DC7AB664377AF47 |  | R22 | Non-TXV |  | 18.42% | 0.81579 | 35.4% | [5 empty] | Non-TXV | 18.42%
Merced | CA | 95340-0612 |  | 2013-06-27 | 2013-06-27 11:21 | 2013-06-27 11:32 | AIRE-FLO - YCC030F1MOBC | 69 | 6.6 | Yes | Yes | 21.3 | 19.5 | 1.8 | 0DACA62189134A8EB999D1AD8D08863E |  | R22 | Non-TXV |  | 9.565% | 0.90435 | 18.38% | [5 empty] | Non-TXV | 9.565%
Ripon | CA | 95366-2809 |  | 2013-07-24 | 2013-07-24 15:57 | 2013-07-24 16:21 | LUXAIRE - `24ECW045GA | 64 | 5.2 | Yes | Yes | 22.4 | 20.4 | 2 | C0E820B4C3BA40B0A2749EA3549403CC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Atwater | CA | 95301-4427 |  | 2013-06-27 | 2013-06-27 09:38 | 2013-06-27 09:45 | RHEEM - RRNLB024JK06X | 78 | 2.7 | Yes | Yes | 19.7 | 17.7 | 2 | 806C714A9F234315A488A46C2AC8D4A9 |  | R410A | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Acampo | CA | 95220-9517 |  | 2013-10-01 | 2013-10-01 09:18 | 2013-10-01 09:47 | UNITARY PRODUCTS GROUP - PGC036K060B | 71 | -6.7 | Yes | Yes | 23.5 | 20.3 | 3.3 | 5105FA381F65451C884A0FD9BDDB6931 |  | R22 | Non-TXV |  | -9.437% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.437%
Merced | CA | 95348-1779 |  | 2013-07-17 | 2013-07-17 16:24 | 2013-07-17 16:26 | RHEEM - 7777UNK | 104 | 4.6 | Yes | Yes | 21.8 | 20.7 | 1.1 | 1EEEA2CADFB44F76A77DDEA802449B5E |  | R22 | Non-TXV |  | 4.423% | 0.95577 | 8.5% | [5 empty] | Non-TXV | 4.423%
Madera | CA | 93637-6134 |  | 2013-07-30 | 2013-07-30 12:59 | 2013-08-01 15:37 | YORK - D2NP030N5606A | 74 | 2.6 | Yes | Yes | 19.9 | 20.7 | -0.8 | 0745F84D73344AADAD95CD09AEE1B150 |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Fresno | CA | 93722-6552 |  | 2013-07-17 | 2013-07-17 16:05 | 2013-07-17 16:07 | ICP - PGAA30C1K1 | 75 | 12.8 | Yes | Yes | 20.2 | 19.9 | 0.3 | E3F90D3278204C6C9CB187E15847DA42 |  | R22 | Non-TXV |  | 17.07% | 0.82933 | 32.8% | [5 empty] | Non-TXV | 17.07%
Riverbank | CA | 95367-3044 |  | 2013-10-24 | 2013-10-24 16:39 | 2013-10-24 16:57 | GOODMAN - GSC130361DE | 119 | 9 | Yes | Yes | 19.7 | 19.9 | -0.2 | 46EE6955DB914BE799D0F5B3D0516FCA |  | R22 | Non-TXV |  | 7.563% | 0.92437 | 14.53% | [5 empty] | Non-TXV | 7.563%
Fresno | CA | 93720-0256 |  | 2013-08-08 | 2013-08-08 10:40 | 2013-08-09 00:46 | YORK - HIDH036S06A | 85 | 3 | Yes | Yes | 18.8 | 21 | -2.2 | 0BE3F5EA43FC4B93B7EA7FC96E861CBB |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Parlier | CA | 93648-9632 |  | 2013-08-28 | 2013-08-28 15:51 | 2013-08-28 16:35 | RUUD - N/A | 60 | 4.2 | Yes | Yes | 21 | 21 | 0 | 4E1402C834424DC9B894773CDB53C6B0 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Sanger | CA | 93657-2141 |  | 2013-08-02 | 2013-08-02 09:41 | 2013-08-02 11:09 | BDP - 585HJW024040BE | 68 | 2.8 | Yes | Yes | 17 | 19.9 | -2.9 | 983D52E071854299851599EA642A1A54 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Stockton | CA | 95206-4619 |  | 2013-07-10 | 2013-07-10 10:26 | 2013-07-10 10:44 | BDP - 563CN030-A | 102 | -6 | Yes | Yes | 20.8 | 19 | 1.8 | A90671BD2A4540759AD37903C0A279DE |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95210-2614 |  | 2013-08-16 | 2013-08-16 11:30 | 2013-08-16 11:30 | RHEEM - GPG1324045M41AD | 80 | 0 | Yes | Yes | 17.8 | 18.6 | -0.8 | 6A706009A82B4BBA8AEF00E24F005B08 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9626 |  | 2013-09-30 | 2013-09-30 10:49 | 2013-09-30 10:49 | PAYNE - PA13NR030-H | 75 | 0 | Yes | Yes | 20.1 | 18.2 | 1.9 | 3634B041850F474E8C1D20C18783CE1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-7824 |  | 2013-07-19 | 2013-07-19 09:28 | 2013-07-19 09:28 | GOODMAN - GSX130601BA | 125 | 0 | Yes | Yes | 26 | 20.9 | 5.1 | A3D2AFF0DC414D7B879732A0723FDCD9 |  | R410A | TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-3804 |  | 2013-07-25 | 2013-07-25 16:38 | 2013-07-25 17:00 | DAY & NIGHT - 591ANX042000ABAA | 112 | 4.1 | Yes | Yes | 18.6 | 20.2 | -1.6 | D02465C755C0440FB9D1250C3723CB0E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | Non-TXV | 3.661%
Sanger | CA | 93657-1931 |  | 2013-09-17 | 2013-09-17 12:54 | 2013-09-17 12:54 | UNITARY PRODUCTS GROUP - TCJF60S41S3A | 89 | 0 | Yes | Yes | 18 | 19.5 | -1.5 | B73891E174DB460695BE53ADDC0A8F90 |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5127 |  | 2013-06-28 | 2013-06-28 15:41 | 2013-06-28 15:44 | GOODMAN - GPG1336045M41AC | 85 | 3.4 | Yes | Yes | 24.6 | 18.8 | 5.8 | 25434B4B6338426CA4E14BB7F4C391BD |  | R410A | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Manteca | CA | 95337-8399 |  | 2013-07-24 | 2013-07-24 11:10 | 2013-07-24 11:29 | YORK - H2RD036S06B | 96 | 3 | Yes | Yes | 22.1 | 20.1 | 2.1 | B94DD17C9AE043DDABE81128CB722F70 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Ione | CA | 95640-9411 |  | 2013-09-03 | 2013-09-03 13:23 | 2013-09-03 13:39 | GOODMAN - GSC130361GB | 77 | 11 | Yes | Yes | 17.4 | 20.4 | -3 | 8790091ED5A9433DBD0C95BA10E4DC37 | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 14.29% | 0.85714 | 27.45% | [5 empty] | TXV | 14.29%
Manteca | CA | 95336-3416 |  | 2013-07-18 | 2013-07-18 09:08 | 2013-07-18 09:33 | AMANA - PGD42C0902E | 120 | 7.3 | Yes | Yes | 20.6 | 18.7 | 1.9 | 26C5DABC8E11476C89AD572D4FC5ED2A |  | R22 | Non-TXV |  | 6.083% | 0.93917 | 11.69% | [5 empty] | Non-TXV | 6.083%
Fresno | CA | 93705-5015 |  | 2013-07-11 | 2013-07-11 12:48 | 2013-07-11 13:30 | CARRIER - 48SS-036080301 | 67 | 2.5 | Yes | Yes | 21.3 | 21.2 | 0.1 | 55A078D44DD54AAAA69E914FA479945E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.731% | 0.96269 | 7.171% | [5 empty] | Non-TXV | 3.731%
Stockton | CA | 95206-6271 |  | 2013-07-19 | 2013-07-19 10:34 | 2013-07-19 10:34 | CARRIER - 38CKC048300 | 102 | 0 | Yes | Yes | 21.2 | 18.8 | 2.4 | 0804160B68644F5BB1F99BA599C0C874 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-8562 |  | 2013-08-02 | 2013-08-02 16:18 | 2013-08-02 16:38 | YORK - H1RA042S06D | 84 | 4.4 | Yes | Yes | 22 | 20.2 | 1.8 | 777EB8B4DFFF4C8AB19F02D2E4D7535D | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | TXV | 5.238%
Fresno | CA | 93703-2405 |  | 2013-08-27 | 2013-08-27 13:41 | 2013-08-27 13:42 | ICP - PGC048K080A | 102 | 19.4 | Yes | Yes | 20.1 | 18.4 | 1.7 | 6E9D399B61834FFEAD15A11ED45ECF76 |  | R22 | Non-TXV |  | 19.02% | 0.8098 | 36.55% | [5 empty] | Non-TXV | 19.02%
Ione | CA | 95640-5212 |  | 2013-08-01 | 2013-08-01 10:24 | 2013-08-01 10:47 | BRYANT - 561CJ036-F | 70 | -4.1 | Yes | Yes | 24 | 20.8 | 3.2 | D415631B856D4F21A12CE4AB05AA214D |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Reedley | CA | 93654-9725 |  | 2013-07-25 | 2013-07-25 14:36 | 2013-07-25 15:19 | UNITARY PRODUCTS GROUP - ERCS0601BBB | 162 | 5.8 | Yes | Yes | 23.3 | 19.6 | 3.7 | 1A1F8D7B85574B3F80E254300CF3F456 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.58% | 0.9642 | 6.88% | [5 empty] | Non-TXV | 3.58%
Parlier | CA | 93648-2863 |  | 2013-08-30 | 2013-08-30 10:36 | 2013-08-30 10:36 | CONCORD - CCU1024A-1A | 50 | 0 | Yes | Yes | 18 | 21 | -3 | 31A48363E264443B9573218D6DC36631 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-5163 |  | 2013-07-22 | 2013-07-22 14:52 | 2013-07-22 14:55 | PAYNE - 7777UNK | 100 | 4 | Yes | Yes | 21.6 | 20.4 | 1.2 | F4C11911D3CE473599089C14C2DA1216 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Williams | CA | 95987-0000 |  | 2013-08-03 | 2013-08-03 10:07 | 2013-08-03 10:23 | OTHER - 561AJ036-D | 69 | 2.1 | Yes | Yes | 16 | 18.3 | -2.3 | E54F2B27E15E4373A8FFD29E02640293 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Fresno | CA | 93728-1634 |  | 2013-07-18 | 2013-07-18 09:50 | 2013-07-18 09:52 | ICP - PGD4240K001C1 | 96 | 3 | Yes | Yes | 23.5 | 19.9 | 3.6 | 852017528AC24FA88B41FC8A66E75C14 |  | R410A | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Paradise | CA | 95969-6167 |  | 2013-08-08 | 2013-08-08 08:46 | 2013-08-08 09:07 | DAY & NIGHT - 591ANX0480000ACAA | 128 | -7.5 | Yes | Yes | 23.5 | 20.7 | 2.8 | 3347CB0B8107405B986FC5A62AAB1E30 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Stockton | CA | 95206-2968 |  | 2013-07-17 | 2013-07-17 11:00 | 2013-07-17 11:19 | ICP - PGF330060K01A1 | 152 | 5.3 | Yes | Yes | 22.9 | 19.9 | 3 | EA009D8CECDE48549DBF29C69E7AD5F2 |  | R22 | Non-TXV |  | 3.487% | 0.96513 | 6.701% | [5 empty] | Non-TXV | 3.487%
Reedley | CA | 93654-9140 |  | 2013-08-08 | 2013-08-08 14:25 | 2013-08-08 15:30 | UNITARY PRODUCTS GROUP - BRCS0361BD | 63 | 7.2 | Yes | Yes | 19 | 20.2 | -1.2 | 15557B4CA43C4122A36B71758AB8DA76 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | Non-TXV | 11.43%
Oroville | CA | 95966-5535 |  | 2013-07-29 | 2013-07-29 12:06 | 2013-07-29 12:22 | OTHER - CA9642VKA1 | 156 | 4.6 | Yes | Yes | 21.5 | 21.5 | 0 | 0278206CCF624B64ADF608FCE1F45E11 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Fresno | CA | 93726-2906 |  | 2013-07-29 | 2013-07-29 09:11 | 2013-07-29 09:13 | ICP - PGAA36D1KA | 69 | 9.1 | Yes | Yes | 22.3 | 19.9 | 2.4 | 333C16EBC1594DC4947E30299ECA963E |  | R22 | Non-TXV |  | 13.19% | 0.86812 | 25.35% | [5 empty] | Non-TXV | 13.19%
Gridley | CA | 95948-9503 |  | 2013-08-17 | 2013-08-17 14:28 | 2013-08-17 17:52 | PAYNE - PY3PNA048090NB | 196 | 6.6 | Yes | Yes | 18.7 | 18.8 | -0.1 | 805FD0B469224707B332E76A8646C414 |  | R22 | Non-TXV |  | 3.367% | 0.96633 | 6.471% | [5 empty] | Non-TXV | 3.367%
Sanger | CA | 93657-8624 |  | 2013-08-06 | 2013-08-06 19:39 | 2013-08-06 21:02 | GOODMAN - CRT36-1A | 140 | 7.7 | Yes | Yes | 17.5 | 19.8 | -2.3 | A684C2DF54154FC89E8381405FD909B0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Placerville | CA | 95667-8993 |  | 2013-08-28 | 2013-08-28 18:48 | 2013-08-28 18:48 | LENNOX - HS20-311-2P | 64 | 0 | Yes | Yes | 23.6 | 22.6 | 1 | BA53097BF1EB4FCDADBE1D701D31E622 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0214 |  | 2013-07-01 | 2013-07-01 11:41 | 2013-07-01 11:42 | OTHER - UNK | 67 | 10.2 | Yes | Yes | 24.9 | 20.9 | 4 | C3410090B37A4022881F1993196A2471 |  | R22 | Non-TXV |  | 15.22% | 0.84776 | 29.26% | [5 empty] | Non-TXV | 15.22%
Newcastle | CA | 95658-9469 |  | 2013-08-08 | 2013-08-08 16:45 | 2013-08-08 17:21 | AMERICAN STANDARD - YCY036F1M0AC | 85 | 9.3 | Yes | Yes | 24.7 | 20.4 | 4.3 | F4D086E6898C4C90B445ECCD8553BC6E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.94% | 0.89059 | 21.03% | [5 empty] | Non-TXV | 10.94%
Chico | CA | 95973-2003 |  | 2013-07-09 | 2013-07-09 18:53 | 2013-07-09 19:13 | PAYNE - PY1PNB036060AAAA | 56 | 4.4 | Yes | Yes | 18.6 | 20.9 | -2.3 | FAC995166892451C8E4830F602FD4B77 |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Fresno | CA | 93701-1218 |  | 2013-07-12 | 2013-07-12 11:58 | 2013-07-12 12:00 | OTHER - DPYB-F036N070A | 108 | 3.5 | Yes | Yes | 22.8 | 20.9 | 1.9 | DB525C3BBD63499D9B76BDA72456C382 |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Stockton | CA | 95209-3912 |  | 2013-07-18 | 2013-07-18 13:51 | 2013-07-18 13:51 | GOODMAN - CKJ36-1AB | 85 | 0 | Yes | Yes | 21.5 | 19.7 | 1.8 | 4BC3B442EC7B42BEA6E740DFBB07EFEE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fowler | CA | 93625-9429 |  | 2013-08-20 | 2013-08-20 13:06 | 2013-08-20 13:51 | LENNOX - 13ACC0060-230-01 | 168 | 9.2 | Yes | Yes | 18 | 20.7 | -2.7 | F9178445763C466598E1100BB0863F86 |  | R22 | Non-TXV |  | 5.476% | 0.94524 | 10.52% | [5 empty] | Non-TXV | 5.476%
Chico | CA | 95928-8504 |  | 2013-08-27 | 2013-08-27 16:12 | 2013-08-27 16:39 | RUUD - RAFD-031JAS | 64 | 2.1 | Yes | Yes | 19 | 20.4 | -1.4 | D5315FD194244194A8133F8DC096E621 |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Parlier | CA | 93648-9631 |  | 2013-09-03 | 2013-09-03 13:45 | 2013-09-03 14:10 | RUUD - N/A | 85 | 2.8 | Yes | Yes | 18.5 | 21.5 | -3 | 7FD7F97F64CD4C6099D54005647CE5A8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Manteca | CA | 95336-4652 |  | 2013-08-12 | 2013-08-12 14:23 | 2013-08-12 14:40 | BRYANT - 114ANA030-D | 88 | 3.6 | Yes | Yes | 23.4 | 20.7 | 2.8 | 5FCAFED406E94E84A878C12C23651F31 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Fresno | CA | 93725-1201 |  | 2013-08-06 | 2013-08-06 16:19 | 2013-08-06 16:21 | DAY & NIGHT - 5858036075YACR | 92 | 3.8 | Yes | Yes | 26.5 | 22.8 | 3.7 | 1320AAC0969B44B0A1E6DAEC7C4A9757 |  | R22 | Non-TXV |  | 4.13% | 0.9587 | 7.938% | [5 empty] | Non-TXV | 4.13%
Mariposa | CA | 95338-9453 |  | 2013-08-21 | 2013-08-21 11:08 | 2013-08-21 11:10 | RUUD - UNK | 57 | 8.1 | Yes | Yes | 20.1 | 18.6 | 1.5 | 8896EBF9B21747F9BB169AF4DDEDF78A |  | R22 | Non-TXV |  | 14.21% | 0.85789 | 27.31% | [5 empty] | Non-TXV | 14.21%
Madera | CA | 93638-3763 |  | 2013-07-19 | 2013-07-19 12:59 | 2013-07-19 12:59 | BDP - 542D024HP | 102 | 0 | Yes | Yes | 20 | 19.5 | 0.5 | 9816954DB4D4480CB8141D6C8CEA7CCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9628 |  | 2013-09-04 | 2013-09-04 15:19 | 2013-09-04 15:43 | RUUD - N/A | 85 | 2.8 | Yes | Yes | 17.5 | 18.6 | -1.1 | 21F2CDEDAE104565B4C373D74C1535AB |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Newman | CA | 95360-1436 |  | 2013-07-29 | 2013-07-29 13:46 | 2013-07-29 14:12 | PAYNE - PA10JA036-C | 73 | 6.6 | Yes | Yes | 19.8 | 20.4 | -0.6 | 94A6508900504C5C966CCDB9B2177358 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.041% | 0.90959 | 17.37% | [5 empty] | Non-TXV | 9.041%
Cameron Park | CA | 95682-8936 |  | 2013-08-15 | 2013-08-15 16:00 | 2013-08-15 16:00 | AMERICAN STANDARD - 4A6B3024A1000BA | 91 | 0 | Yes | Yes | 21.2 | 19.3 | 1.9 | 74FA1C3EBE0C4814B24DB61881C2011B |  | R410A | TXV |  | 0% | 1 | 0%
Ione | CA | 95640-0000 |  | 2013-07-24 | 2013-07-24 12:57 | 2013-07-24 13:29 | CARRIER - 38TXA060350 | 180 | -16.9 | Yes | Yes | 21 | 21.9 | -0.9 | 27E57B5D08EE45CEB0AA4F9E89F7E24B |  | R410A | TXV |  | -9.389% | 1.0939 | 2.629% |  |  |  |  | TXV |  |  | -9.389%
Madera | CA | 93637-4636 |  | 2013-07-28 | 2013-07-28 01:56 | 2013-07-28 21:31 | YORK - D1P036N9556 | 85 | 3.3 | Yes | Yes | 17.1 | 19.8 | -2.7 | 256F7DBC0F124E4CB84CCF0BBCC0C71B |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Cameron Park | CA | 95682-8936 |  | 2013-08-28 | 2013-08-28 10:47 | 2013-08-28 10:47 | - 2A6H1030A1000AB | 73 | 0 | Yes | Yes | 24.9 | 19.9 | 5 | B76D5B325FE2420E95437B989FD90D2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1400 |  | 2013-08-22 | 2013-08-22 11:19 | 2013-08-22 11:36 | RHEEM - UNK | 64 | 2.6 | Yes | Yes | 23 | 19.8 | 3.2 | 5B44728C699B47B996447B8E30486CEC |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Sanger | CA | 93657-2055 |  | 2013-07-22 | 2013-07-22 17:03 | 2013-07-22 17:58 | LENNOX - 10ACC-042-230-03 | 81 | 5.4 | Yes | Yes | 19.8 | 18.7 | 1.1 | 82D927235F524C40BDF264ACDAA68923 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Newman | CA | 95360-1436 |  | 2013-07-29 | 2013-07-29 14:24 | 2013-07-29 14:50 | BRYANT - 561CJ030-E | 67 | 5.9 | Yes | Yes | 19.1 | 19.5 | -0.4 | 5B776D7630E447CDAEAD93F29D3E46F4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.806% | 0.91194 | 16.92% | [5 empty] | Non-TXV | 8.806%
Fresno | CA | 93705-0144 |  | 2013-07-30 | 2013-07-30 14:29 | 2013-07-30 14:30 | ICP - NAC024AKA1 | 60 | 7.7 | Yes | Yes | 25 | 22.4 | 2.6 | 46E14ECBB3344B8592BE1BE96C1CCE54 |  | R22 | Non-TXV |  | 12.83% | 0.87167 | 24.66% | [5 empty] | Non-TXV | 12.83%
Stockton | CA | 95207-4705 |  | 2013-07-29 | 2013-07-29 12:08 | 2013-07-29 12:30 | YORK - GCGD24S21S2XB | 67 | 3 | Yes | Yes | 17.4 | 17.2 | 0.2 | EB6A02FE9113442A87E8EAED892D15B1 |  | R22 | Non-TXV |  | 4.478% | 0.95522 | 8.605% | [5 empty] | Non-TXV | 4.478%
Stockton | CA | 95212-1019 |  | 2013-07-31 | 2013-07-31 16:23 | 2013-07-31 17:52 | UNITARY PRODUCTS GROUP - H3RA060S06G | 98 | 18.2 | Yes | Yes | 23.8 | 20.9 | 2.9 | B4803F52998D4A64928954EFFAF0C088 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Magalia | CA | 95954-9601 |  | 2013-08-03 | 2013-08-03 10:10 | 2013-08-03 10:48 | YORK - D1NA036N05606C | 67 | 2.4 | Yes | Yes | 24.4 | 19.8 | 4.6 | D8B30AECB8464DBA9F383F75102F29C1 |  | R22 | Non-TXV |  | 3.582% | 0.96418 | 6.884% | [5 empty] | Non-TXV | 3.582%
Manteca | CA | 95336-2543 |  | 2013-07-18 | 2013-07-18 11:25 | 2013-07-18 11:47 | TRANE - TTR030C100A0 | 85 | 3.1 | Yes | Yes | 20.4 | 18.6 | 1.8 | E4C724686FBC4B7F9C3C5A9B388C095B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Stockton | CA | 95212-2891 |  | 2013-07-22 | 2013-07-22 10:11 | 2013-07-22 10:36 | CARRIER - 38CKC060370 | 131 | 5 | Yes | Yes | 24 | 19.4 | 4.6 | 3616777CE059432C86E57F832D24AC63 |  | R22 | Non-TXV |  | 3.817% | 0.96183 | 7.335% | [5 empty] | Non-TXV | 3.817%
Merced | CA | 95348-3116 |  | 2013-09-18 | 2013-09-18 11:15 | 2013-09-18 11:16 | GE - BTB924A100A0 | 45 | 2.8 | Yes | Yes | 16.7 | 18.1 | -1.4 | 8E9490D9DDAF41339C4213B3877AA0FF |  | R22 | Non-TXV |  | 6.222% | 0.93778 | 11.96% | [5 empty] | Non-TXV | 6.222%
Magalia | CA | 95954-9670 |  | 2013-08-29 | 2013-08-29 13:59 | 2013-08-29 14:19 | OTHER - DBRH-030N080C | 113 | 3.5 | Yes | Yes | 18.1 | 17.4 | 0.7 | 492C03F41D9544FCBDAB063A93414E11 |  | R22 | Non-TXV |  | 3.097% | 0.96903 | 5.952% | [5 empty] | Non-TXV | 3.097%
Winton | CA | 95388-9428 |  | 2013-07-22 | 2013-07-22 16:26 | 2013-07-22 16:27 | CARRIER - 48GS036060301 | 56 | 6 | Yes | Yes | 22.6 | 21.5 | 1.1 | 0E1B3D977A384E27BA5DBF738521F7DC |  | R22 | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Stockton | CA | 95206-4619 |  | 2013-07-25 | 2013-07-25 14:54 | 2013-07-25 15:21 | BDP - 563CN036-A | 113 | 9.2 | Yes | Yes | 19.2 | 19.3 | -0.1 | 168071122D5F495FABA903DCC4696D8A |  | R22 | TXV |  | 8.142% | 0.91858 | 15.65% | [5 empty] | TXV | 8.142%
Los Banos | CA | 93635-6438 |  | 2013-07-29 | 2013-07-29 13:47 | 2013-07-29 13:53 | BRYANT - 563CN048-H | 140 | 4.6 | Yes | Yes | 21.1 | 18.8 | 2.4 | E3D6E2301075429D86D16CAC6EDEB4A8 |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Merced | CA | 95348-3174 |  | 2013-09-06 | 2013-09-06 13:18 | 2013-09-06 13:19 | GOODMAN - GSC130181F4 | 75 | 8 | Yes | Yes | 20.9 | 18.7 | 2.2 | B31CD72260944240B65658A37AF076C9 |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Cool | CA | 95614-2502 |  | 2013-09-13 | 2013-09-13 10:26 | 2013-09-13 10:49 | RUUD - UAFD-048JBS | 101 | -5.9 | Yes | Yes | 17 | 18.3 | -1.3 | D4C93669603B40F9BCBD66248F671008 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Stockton | CA | 95205-4615 |  | 2013-07-18 | 2013-07-18 11:10 | 2013-07-18 11:47 | AMANA - APG12300701A | 73 | -6.9 | Yes | Yes | 23.6 | 19.5 | 4.1 | B78A75C41D5F4297B20710AB3C9CF025 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.452% | 1.0945 | 2.647% |  |  |  |  | Non-TXV |  |  | -9.452%
Marysville | CA | 95901-8288 |  | 2013-07-01 | 2013-07-01 13:13 | 2013-07-01 13:33 | LENNOX - 13ACD-030-230-02 | 85 | 2.9 | Yes | Yes | 15 | 17.9 | -2.9 | C4328ECD3C1744F3B54BCA923FD613D2 |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Chico | CA | 95973-1030 |  | 2013-08-07 | 2013-08-07 13:45 | 2013-08-07 14:15 | LENNOX - HS26-048-4P | 114 | 9.8 | Yes | Yes | 23.8 | 20.4 | 3.4 | 2A9D604077C54DA79FFC343382115E05 |  | R22 | TXV |  | 8.596% | 0.91404 | 16.52% | [5 empty] | TXV | 8.596%
Stockton | CA | 95210-4214 |  | 2013-07-30 | 2013-07-30 12:37 | 2013-07-30 13:02 | RHEEM - 13AJ24A01 | 77 | 5.3 | Yes | Yes | 19.3 | 18.1 | 1.2 | 77DE87E9BB1F4EFD85E09010B312C619 |  | R22 | Non-TXV |  | 6.883% | 0.93117 | 13.23% | [5 empty] | Non-TXV | 6.883%
Galt | CA | 95632-8215 |  | 2013-09-10 | 2013-09-10 17:42 | 2013-09-10 18:01 | GOODMAN - GSC130481AG | 147 | -42.3 | Yes | Yes | 21.8 | 20 | 1.8 | 71B1B55971E64FBCAC52C61C24007374 |  | R22 | Non-TXV |  | -28.78% | 1.2878 | 8.058% |  |  |  |  | Non-TXV |  |  | -28.78%
Acampo | CA | 95220-9390 |  | 2013-08-21 | 2013-08-21 13:06 | 2013-08-21 13:24 | BDP - 585B030075YACR | 50 | 2.7 | Yes | Yes | 20.3 | 19 | 1.3 | 56F9E1937CAB4F52B1B8E3F5A888F306 |  | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Stockton | CA | 95206-6317 |  | 2013-07-19 | 2013-07-19 12:04 | 2013-07-19 12:04 | YORK - GCGD48S21S2A | 69 | 0 | Yes | Yes | 17.7 | 19 | -1.3 | B64BC7AA47ED47B3B2516FF577443CC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-2761 |  | 2013-07-22 | 2013-07-22 14:52 | 2013-07-22 15:13 | - 585GJ024040ABAE | 54 | -5.1 | Yes | Yes | 26.4 | 22.8 | 3.6 | 70C24C4A25954B2D8233A5C4E438AE43 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Stockton | CA | 95207-4628 |  | 2013-08-09 | 2013-08-09 09:26 | 2013-08-09 09:43 | ICP - PGC024K060A | 58 | 4.8 | Yes | Yes | 15.9 | 17.7 | -1.8 | 03AF26E749904A1E89216944C8F1CD42 |  | R22 | Non-TXV |  | 8.276% | 0.91724 | 15.9% | [5 empty] | Non-TXV | 8.276%
Murphys | CA | 95247-9554 |  | 2013-08-22 | 2013-08-22 11:38 | 2013-08-22 11:59 | AMERICAN STANDARD - 27A1030A100000 | 65 | 4.1 | Yes | Yes | 22.6 | 16.6 | 6 | 8586427834E24FF7B75B8D186DA9A331 |  | R22 | Non-TXV |  | 6.308% | 0.93692 | 12.12% | [5 empty] | Non-TXV | 6.308%
Sutter Creek | CA | 95685-9783 |  | 2013-09-06 | 2013-09-06 12:45 | 2013-09-06 13:07 | BDP - 588ANW042060ACAG | 83 | 5.5 | Yes | Yes | 19.6 | 16.5 | 3.1 | 0406530A224E471CA291BDD2ADC227D7 |  | R22 | Non-TXV |  | 6.627% | 0.93373 | 12.73% | [5 empty] | Non-TXV | 6.627%
Los Banos | CA | 93635-2905 |  | 2013-07-24 | 2013-07-24 10:48 | 2013-07-24 10:50 | DAY & NIGHT - 7777UNK | 100 | 3.5 | Yes | Yes | 25.4 | 21.9 | 3.5 | 07AF44FB90DE46E7800C24F870F953BC |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Merced | CA | 95348-3174 |  | 2013-09-06 | 2013-09-06 10:57 | 2013-09-06 10:58 | RHEEM - RPKA025JAZ | 73 | 6.5 | Yes | Yes | 28 | 23.1 | 4.9 | D52E204E76324FB182E489CB5F341079 |  | R22 | Non-TXV |  | 8.904% | 0.91096 | 17.11% | [5 empty] | Non-TXV | 8.904%
Newman | CA | 95360-9634 |  | 2013-07-29 | 2013-07-29 10:57 | 2013-07-29 11:28 | BRYANT - 563CN036-D | 101 | 3.8 | Yes | Yes | 21.3 | 19.3 | 2 | 504193EDA67F43A48C2CA5E9A41821BB |  | R22 | TXV |  | 3.762% | 0.96238 | 7.23% | [5 empty] | TXV | 3.762%
Merced | CA | 95348-3126 |  | 2013-09-06 | 2013-09-06 08:54 | 2013-09-06 08:55 | OTHER - BTB924A100AO | 45 | 5.1 | Yes | Yes | 20.9 | 20.4 | 0.5 | 8F59436A8C514E69A0BAE016FF896682 |  | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Los Banos | CA | 93635-3103 |  | 2013-08-15 | 2013-08-15 10:00 | 2013-08-15 10:02 | TRANE - YCY036G1MOAC | 129 | 15.3 | Yes | Yes | 24.6 | 18.8 | 5.8 | AF04687345E1494FB0E775E4F017C4A4 |  | R22 | Non-TXV |  | 11.86% | 0.8814 | 22.79% | [5 empty] | Non-TXV | 11.86%
Lodi | CA | 95242-9519 |  | 2013-09-06 | 2013-09-06 16:56 | 2013-09-08 22:09 | COLEMAN - 7848801 | 165 | 10.7 | Yes | Yes | 20.4 | 18.7 | 1.7 | 3D29C743A134454EAD77DB21A54DBFB5 |  | R22 | Non-TXV |  | 6.485% | 0.93515 | 12.46% | [5 empty] | Non-TXV | 6.485%
Madera | CA | 93638-1747 |  | 2013-07-19 | 2013-07-19 11:04 | 2013-07-19 13:01 | PAYNE - PY1NPB024040AAA | 53 | 1.9 | Yes | Yes | 21.2 | 21.5 | -0.3 | 8A1581EF6A0A41B1B93EDFD693A538B8 |  | R22 | Non-TXV |  | 3.585% | 0.96415 | 6.889% | [5 empty] | Non-TXV | 3.585%
Yuba City | CA | 95993-0000 |  | 2013-08-06 | 2013-08-06 08:27 | 2013-08-06 09:03 | LENNOX - 10ACC-036-230-02 | 74 | 5.1 | Yes | Yes | 17 | 19.1 | -2.1 | 0EED388361F240F496A644894B124DF9 |  | R22 | TXV |  | 6.892% | 0.93108 | 13.24% | [5 empty] | TXV | 6.892%
Stockton | CA | 95209-1242 |  | 2013-08-02 | 2013-08-02 13:46 | 2013-08-02 14:07 | GOODMAN - GPG133070M41B | 78 | -7.3 | Yes | Yes | 23.3 | 18.5 | 4.8 | 52446C20C77E410D80ADDD0350814950 |  | R410A | Non-TXV |  | -9.359% | 1.0936 | 2.621% |  |  |  |  | Non-TXV |  |  | -9.359%
Colfax | CA | 95713-9603 |  | 2013-07-26 | 2013-07-26 12:07 | 2013-07-26 12:07 | DAY & NIGHT - 588ANW036080ACAF | 75 | 0 | Yes | Yes | 18 | 18.5 | -0.5 | 5A9B729FC341489EBE80D3C10B24ACAF |  | R22 | TXV |  | 0% | 1 | 0%
Chico | CA | 95926-4812 |  | 2013-08-26 | 2013-08-26 15:30 | 2013-08-26 15:57 | NORDYNE - JS3BA-030KA | 68 | 3 | Yes | Yes | 23.3 | 18.6 | 4.7 | C1E798492EB14315AE50A30BC748F40F |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Ione | CA | 95640-5101 |  | 2013-08-01 | 2013-08-01 08:33 | 2013-08-01 09:02 | RHEEM - RAFD-036JAS | 80 | 3 | Yes | Yes | 18.2 | 20.1 | -1.9 | 12FAF58E48584EF08130F23CE32CB701 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Madera | CA | 93638-3238 |  | 2013-08-05 | 2013-08-05 09:37 | 2013-08-05 09:38 | GOODMAN - GPG13480701AC | 143 | 14.8 | Yes | Yes | 24.6 | 18.8 | 5.8 | 253C539AE5B54F07B675FAC50005F1EB |  | R22 | Non-TXV |  | 10.35% | 0.8965 | 19.89% | [5 empty] | Non-TXV | 10.35%
Grass Valley | CA | 95949-8302 |  | 2013-08-30 | 2013-08-30 11:52 | 2013-08-30 11:52 | OTHER - BRCQ0421BD | 66 | 0 | Yes | Yes | 18.7 | 21.5 | -2.8 | FFAF8DA1B5144A0D90BF74678FA9E74C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Colfax | CA | 95713-0000 |  | 2013-07-26 | 2013-07-26 09:46 | 2013-07-26 10:19 | BRYANT - 582ANW030060AAAD | 55 | 7.4 | Yes | Yes | 18 | 20.4 | -2.4 | D79CCA2F6F954D4F884FAB6B5EBA074B |  | R22 | TXV |  | 13.45% | 0.86545 | 25.86% | [5 empty] | TXV | 13.45%
Los Banos | CA | 93635-3096 |  | 2013-09-09 | 2013-09-09 10:19 | 2013-09-09 10:22 | GIBSON - JS3BC-030KA | 68 | 3.4 | Yes | Yes | 23.2 | 20.4 | 2.8 | 636F2D1972304A9C9CF071F42BE28AF4 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Yuba City | CA | 95991-1816 |  | 2013-08-06 | 2013-08-06 11:26 | 2013-08-06 11:42 | PAYNE - PA13NA024000ABAA | 55 | 4.1 | Yes | Yes | 18 | 19.7 | -1.7 | 215C7FBDA4D64F10B8B78FD23D5AEE1E |  | R410A | TXV |  | 7.455% | 0.92545 | 14.33% | [5 empty] | TXV | 7.455%
Stockton | CA | 95209-5034 |  | 2013-07-22 | 2013-07-22 11:00 | 2013-07-22 11:17 | GOODMAN - CK42-1C | 92 | -5.4 | Yes | Yes | 24 | 18.8 | 5.2 | 62F83C3340064F5DAFFF2C02A6F83820 |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Merced | CA | 95348-3129 |  | 2013-10-16 | 2013-10-16 09:19 | 2013-10-16 09:21 | GE - BWB918A10060 | 52 | 5 | Yes | Yes | 22 | 18.3 | 3.7 | 1495ACFA6A5E4B9EB4AA6C4160C5D2E7 |  | R22 | Non-TXV |  | 9.615% | 0.90385 | 18.48% | [5 empty] | Non-TXV | 9.615%
Stockton | CA | 95204-1704 |  | 2013-07-25 | 2013-07-25 08:49 | 2013-07-25 09:14 | GE - UNK | 66 | 3.7 | Yes | Yes | 19 | 19.3 | -0.3 | 70F8650A74974ED9995475B3AFAC2F1D |  | R22 | Non-TXV |  | 5.606% | 0.94394 | 10.77% | [5 empty] | Non-TXV | 5.606%
Dos Palos | CA | 93620-2682 |  | 2013-08-14 | 2013-08-14 14:23 | 2013-08-14 14:27 | LENNOX - 13ACD-048-230-01 | 111 | 4.9 | Yes | Yes | 22.2 | 18.4 | 3.9 | 908D10B1C2E049A49D1AE73E30C1E38E |  | R22 | Non-TXV |  | 4.414% | 0.95586 | 8.484% | [5 empty] | Non-TXV | 4.414%
Live Oak | CA | 95953-2104 |  | 2013-08-05 | 2013-08-05 09:14 | 2013-08-05 09:33 | TEMPSTAR - PGAA30D1K1 | 75 | 3.1 | Yes | Yes | 20 | 21 | -1 | 6FB85450912042B385D3E9DFC74C794D |  | R22 | Non-TXV |  | 4.133% | 0.95867 | 7.943% | [5 empty] | Non-TXV | 4.133%
Stockton | CA | 95210-4230 |  | 2013-07-31 | 2013-07-31 09:10 | 2013-07-31 09:32 | DAY & NIGHT - CA3024UKA2 | 85 | 12.7 | Yes | Yes | 23 | 17.7 | 5.3 | 7DFE709D657546EA87C8E16B8A50EBD5 |  | R22 | Non-TXV |  | 14.94% | 0.85059 | 28.71% | [5 empty] | Non-TXV | 14.94%
Stockton | CA | 95212-2727 |  | 2013-07-31 | 2013-07-31 15:07 | 2013-07-31 15:33 | GOODMAN - CKJ36-1D | 90 | 7.5 | Yes | Yes | 26.2 | 20.9 | 5.3 | DBBD1CDA0E5440A3B160001183D807D8 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Stockton | CA | 95210-4230 |  | 2013-08-16 | 2013-08-16 10:14 | 2013-08-16 10:32 | OTHER - N4A324AKB200 | 90 | 10.1 | Yes | Yes | 16.4 | 17.9 | -1.5 | 2B4047283D8942FB8A42C6D8F3984899 |  | R410A | TXV |  | 11.22% | 0.88778 | 21.57% | [5 empty] | TXV | 11.22%
Marysville | CA | 95901-8268 |  | 2013-08-08 | 2013-08-08 15:00 | 2013-08-08 15:17 | CARRIER - UNK | 101 | 5.8 | Yes | Yes | 16 | 19 | -3 | 0D0DBB1E6BB948E0971AC497F62093F2 |  | R22 | Non-TXV |  | 5.743% | 0.94257 | 11.04% | [5 empty] | Non-TXV | 5.743%
Dos Palos | CA | 93620-9668 |  | 2013-08-05 | 2013-08-05 15:03 | 2013-08-05 15:04 | RUUD - 7777UNK | 100 | 2.9 | Yes | Yes | 21.8 | 21.3 | 0.5 | 5678590DAB064B14A48F7C6562F4A1A6 |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Stockton | CA | 95209-3806 |  | 2013-07-26 | 2013-07-26 09:21 | 2013-07-26 09:51 | GOODMAN - CKJ60-1C | 149 | -8.8 | Yes | Yes | 22.7 | 20.5 | 2.3 | C8B69C99C19640BCAD51ED41A14ABDB6 |  | R22 | Non-TXV |  | -5.906% | 1.0591 | 1.654% |  |  |  |  | Non-TXV |  |  | -5.906%
Merced | CA | 95348-3402 |  | 2013-09-04 | 2013-09-04 14:08 | 2013-09-04 14:10 | OTHER - UNK | 56 | 10.9 | Yes | Yes | 20.7 | 17.9 | 2.8 | F7268DB3DD1D46F8BE0CCBD9A1B3C334 |  | R22 | Non-TXV |  | 19.46% | 0.80536 | 37.41% | [5 empty] | Non-TXV | 19.46%
Tracy | CA | 95376-2712 |  | 2013-07-17 | 2013-07-17 08:48 | 2013-07-17 09:22 | RUUD - UKAB-030JAZ | 85 | -8 | Yes | Yes | 19.9 | 19.9 | 0 | EB2A0DACA7D74E65A576592D9791FB5D |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Merced | CA | 95348-1568 |  | 2013-07-24 | 2013-07-24 08:32 | 2013-07-24 08:33 | GOODMAN - GPG12360701A | 85 | 9.2 | Yes | Yes | 28.5 | 22.5 | 6 | F3B594C9809548A1B3D9E007AB6DBA48 |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
Tracy | CA | 95376-2713 |  | 2013-07-19 | 2013-07-19 15:50 | 2013-07-19 16:14 | ICP - GPGC042K080B | 87 | 8.3 | Yes | Yes | 20.8 | 20.2 | 0.6 | 749F80B422F04C39A3284C428679DD9B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.54% | 0.9046 | 18.33% | [5 empty] | Non-TXV | 9.54%
Watsonville | CA | 95076-4183 |  | 2013-10-21 | 2013-10-21 14:31 | 2013-10-21 14:50 | BRYANT - 561CJ024-D | 59 | 3.3 | Yes | Yes | 21.3 | 17.5 | 3.8 | D2DA4639283A4538AB5C56DF2E25D107 |  | R22 | Non-TXV |  | 5.593% | 0.94407 | 10.75% | [5 empty] | Non-TXV | 5.593%
Madera | CA | 93637-5471 |  | 2013-09-06 | 2013-09-06 13:36 | 2013-09-06 13:38 | CARRIER - 48GS-030060301 | 55 | 1.9 | Yes | Yes | 23.3 | 20.2 | 3.1 | 7DDFE0BB5F9F4A2FAC9A838369E51984 |  | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Grass Valley | CA | 95949-7632 |  | 2013-08-05 | 2013-08-05 13:54 | 2013-08-05 13:54 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 19.9 | 20.1 | -0.2 | B452223980FC4F13BDD74D7A13FCDD6E |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4231 |  | 2013-07-30 | 2013-07-30 12:07 | 2013-07-30 12:28 | OTHER - NACO24KB2 | 85 | 12.3 | Yes | Yes | 18.9 | 17.9 | 1 | A8568313FADE4FF89AC1AF7E6B55B943 |  | R22 | Non-TXV |  | 14.47% | 0.85529 | 27.81% | [5 empty] | Non-TXV | 14.47%
Stockton | CA | 95206-6450 |  | 2013-07-25 | 2013-07-25 13:13 | 2013-07-25 13:41 | GOODMAN - CKL49-1L | 122 | 4.6 | Yes | Yes | 21.2 | 19.5 | 1.7 | 74CFD8ED0E684BB6B429E1A32D02C491 |  | R22 | Non-TXV |  | 3.77% | 0.9623 | 7.246% | [5 empty] | Non-TXV | 3.77%
Chico | CA | 95928-8504 |  | 2013-08-27 | 2013-08-27 14:34 | 2013-08-27 14:52 | RHEEM - RAFD-031JAS | 64 | 1.9 | Yes | Yes | 18.3 | 19.3 | -1 | 055FDD57DE894C068142A0E3516AD8F4 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Newcastle | CA | 95658-9369 |  | 2013-08-08 | 2013-08-08 10:20 | 2013-08-08 10:20 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 21.5 | 18.2 | 3.3 | 0ECE1E1508124535906810848314FD90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4226 |  | 2013-07-30 | 2013-07-30 13:11 | 2013-07-30 13:33 | GOODMAN - CPKE24 | 100 | 10.1 | Yes | Yes | 22.2 | 17.2 | 5 | 67D4C4EF0A29445EBDD586458DD5590A |  | R22 | Non-TXV |  | 10.1% | 0.899 | 19.41% | [5 empty] | Non-TXV | 10.1%
Madera | CA | 93638-2460 |  | 2013-07-18 | 2013-07-18 14:34 | 2013-07-18 14:34 | BRYANT - 582ANW036060AF | 59 | 0 | Yes | Yes | 18.4 | 20.7 | -2.3 | 6617728C2E5349A6BBF046C1AD53D332 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6411 |  | 2013-07-20 | 2013-07-20 09:28 | 2013-07-20 09:53 | GOODMAN - CKL36-1H | 71 | 7.4 | Yes | Yes | 18.9 | 19.3 | -0.4 | 1D6A89CE102C4DA4B075836643F23491 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.42% | 0.89577 | 20.03% | [5 empty] | Non-TXV | 10.42%
Stockton | CA | 95204-1722 |  | 2013-07-19 | 2013-07-19 08:58 | 2013-07-19 08:58 | TEMPSTAR - PGC036K080E | 68 | 0 | Yes | Yes | 21.2 | 19.1 | 2.2 | 5EF259BF9A844C8286ACD6191EC045C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newcastle | CA | 95658-9640 |  | 2013-08-08 | 2013-08-08 11:57 | 2013-08-08 11:57 | LENNOX - HS21-048-1P | 179 | 0 | Yes | Yes | 25.1 | 19.5 | 5.6 | 915F77FD04C74964847E70F5C3F9D9A7 |  | R22 | TXV |  | 0% | 1 | 0%
Newcastle | CA | 95658-9640 |  | 2013-08-08 | 2013-08-08 12:21 | 2013-08-08 12:47 | LENNOX - HS26-024-2P | 62 | 5.2 | Yes | Yes | 18.7 | 19.5 | -0.8 | 9BE67A36C2B3465EA06A0A6F7AEB55BD |  | R22 | TXV |  | 8.387% | 0.91613 | 16.12% | [5 empty] | TXV | 8.387%
Marysville | CA | 95901-4926 |  | 2013-08-09 | 2013-08-09 08:54 | 2013-08-09 09:16 | AIRE-FLO - 13ACD-024-230-13 | 68 | 2.5 | Yes | Yes | 18 | 18.2 | -0.2 | 9D7DDD2A8FD8491C933DFEFE34ABB8AE |  | R22 | TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | TXV | 3.676%
Yuba City | CA | 95993-9406 |  | 2013-08-07 | 2013-08-07 10:45 | 2013-08-07 11:03 | - 563CN060-A | 200 | 8 | Yes | Yes | 18 | 21 | -3 | 8AEC232D36D749428D919C51D9977854 |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Stockton | CA | 95206-5116 |  | 2013-08-13 | 2013-08-13 12:29 | 2013-08-13 12:47 | RUUD - UAFD-042JBS | 79 | 6 | Yes | Yes | 18.2 | 19.3 | -1.1 | B2793C76CE13420EB15FD0BC3CF37B31 |  | R22 | Non-TXV |  | 7.595% | 0.92405 | 14.6% | [5 empty] | Non-TXV | 7.595%
West Point | CA | 95255-9631 |  | 2013-09-05 | 2013-09-05 11:01 | 2013-09-05 11:28 | PAYNE - PA10JA036000ACAA | 77 | 7.6 | Yes | Yes | 19.6 | 17.5 | 2.2 | 45F6B203A2B14987B64EFC37FC1C7481 |  | R22 | Non-TXV |  | 9.87% | 0.9013 | 18.97% | [5 empty] | Non-TXV | 9.87%
Stockton | CA | 95206-2002 |  | 2013-07-17 | 2013-07-17 15:23 | 2013-07-17 15:41 | RHEEM - UNK | 64 | 8.6 | Yes | Yes | 25.2 | 21.9 | 3.3 | A56A0BDA5CC44958A627FF67CB191508 |  | R22 | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
Yuba City | CA | 95993-5166 |  | 2013-09-06 | 2013-09-06 10:04 | 2013-09-06 10:43 | GIBSON - JSCBC-024KA | 63 | 18.1 | Yes | Yes | 8 | 18.9 | -10.9 | 21E447E937F74D8D90C5F45AEC1FEF30 | Add refrigerant: 11.1 oz | R22 | Non-TXV |  | 28.73% | 0.7127 | 55.21% | [5 empty] | Non-TXV | 28.73%
Yuba City | CA | 95993-5166 |  | 2013-09-06 | 2013-09-06 10:38 | 2013-09-06 10:58 | GIBSON - JS3BC-024KA | 63 | -3.7 | Yes | Yes | 18 | 19.7 | -1.7 | EED0AC74B69A4E44B7A00B6C0E75363D |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Colfax | CA | 95713-0000 |  | 2013-07-26 | 2013-07-26 08:15 | 2013-07-26 08:46 | DAY & NIGHT - UNK | 100 | 4.1 | Yes | Yes | 19 | 19.1 | -0.1 | A9B4641F720C4CE6AB61D4B7A4A571CC |  | R22 | TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | TXV | 4.1%
Oroville | CA | 95965-9226 |  | 2013-07-26 | 2013-07-26 15:35 | 2013-07-26 21:51 | LENNOX - 12ACB48-5P | 169 | 15.6 | Yes | Yes | 20.4 | 20.6 | -0.2 | 95BFFF9612834EDDA03CB7398183C5EA |  | R22 | Non-TXV |  | 9.231% | 0.90769 | 17.74% | [5 empty] | Non-TXV | 9.231%
Stockton | CA | 95210-2448 |  | 2013-07-31 | 2013-07-31 12:21 | 2013-07-31 12:40 | RHEEM - UNK | 51 | -3.6 | Yes | Yes | 22.1 | 20.9 | 1.2 | 906E7676CFD14D55B1E5637170405378 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93705-1751 |  | 2013-08-12 | 2013-08-12 15:27 | 2013-08-12 15:32 | BRYANT - 561AJ048-B | 105 | 4.2 | Yes | Yes | 25.4 | 19.9 | 5.5 | 2753736B69AD488F9B629E7901A50490 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Chico | CA | 95928-6741 |  | 2013-08-02 | 2013-08-02 09:11 | 2013-08-02 09:28 | TRANE - YCC024F1L0BH | 65 | 2.2 | Yes | Yes | 20.7 | 18.7 | 2 | 34136C17A8DC4AC58DDA0B3B952686B8 |  | R22 | Non-TXV |  | 3.385% | 0.96615 | 6.504% | [5 empty] | Non-TXV | 3.385%
Sonora | CA | 95370-9604 |  | 2013-10-14 | 2013-10-14 14:52 | 2013-10-14 15:09 | TRANE - TTX748A10043 | 160 | 14.9 | Yes | Yes | 25.6 | 21.7 | 3.9 | BBEF20F674834E5DAF5B835AFAA2AEE0 |  | R22 | Non-TXV |  | 9.312% | 0.90687 | 17.9% | [5 empty] | Non-TXV | 9.312%
Paradise | CA | 95969-5830 |  | 2013-08-26 | 2013-08-26 13:46 | 2013-08-26 19:02 | MONTGOMERY WARD - SRM1835C | 52 | 8.2 | Yes | Yes | 20.8 | 20.9 | -0.1 | 2EE472375ABC43A89787C9C10E9F43C5 |  | R22 | Non-TXV |  | 15.77% | 0.84231 | 30.3% | [5 empty] | Non-TXV | 15.77%
Grass Valley | CA | 95949-8715 |  | 2013-09-10 | 2013-09-10 16:41 | 2013-09-10 16:41 | TRANE - YCX042F1M0BD | 123 | 0 | Yes | Yes | 24.9 | 22.6 | 2.3 | C6E229F54D0141D1BB968123E23DA9C8 |  | R22 | TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-8715 |  | 2013-09-10 | 2013-09-10 17:39 | 2013-09-10 17:39 | TRANE - YCX036F1M0AB | 119 | 0 | Yes | Yes | 24.3 | 22.6 | 1.7 | B4A430370BCE4F63819BE9BB50DABE99 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-7810 |  | 2013-07-18 | 2013-07-18 13:45 | 2013-07-18 14:02 | PAYNE - PS13NR036000ACAA | 128 | 7.7 | Yes | Yes | 25.9 | 20.4 | 5.5 | 2AD62CDD002641F6BA84EDAB7F784F18 |  | R22 | Non-TXV |  | 6.016% | 0.93984 | 11.56% | [5 empty] | Non-TXV | 6.016%
Newcastle | CA | 95658-0000 |  | 2013-10-02 | 2013-10-02 16:59 | 2013-10-02 16:59 | RHEEM - RRKA-A036JK08X | 62 | 0 | Yes | Yes | 19.2 | 20.6 | -1.3 | 5667AEE471644616B9A81D8E47AE9F78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lodi | CA | 95240-9434 |  | 2013-08-21 | 2013-08-21 13:48 | 2013-08-21 13:48 | TRANE - 4TTX4042A1000AA | 103 | 0 | Yes | Yes | 25.2 | 19.3 | 5.9 | 06A6D9FFA5364E0C9260467286CDE84F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-2851 |  | 2013-07-18 | 2013-07-18 11:03 | 2013-07-18 11:26 | DAY & NIGHT - UNK | 105 | 4.9 | Yes | Yes | 21 | 20.4 | 0.6 | 76D3E45F5D06450285AA41110522B7F7 |  | R22 | TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | TXV | 4.667%
Madera | CA | 93637-2606 |  | 2013-08-07 | 2013-08-07 13:39 | 2013-08-07 13:39 | YORK - D1NP036N05606A | 109 | 0 | Yes | Yes | 19.2 | 20.2 | -0.9 | E7AA66B2AB314B898803354C3730961A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pine Grove | CA | 95665-9723 |  | 2013-08-09 | 2013-08-09 12:35 | 2013-08-09 12:35 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 22.3 | 20.6 | 1.7 | 01AD1DD531954CE8971F8859F18FAA8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8221 |  | 2013-07-22 | 2013-07-22 09:31 | 2013-07-22 10:07 | TRANE - TTNO36C100B2 | 117 | 4.4 | Yes | Yes | 20 | 19.3 | 0.7 | 0C389501990445FFB53D9C09A8F2F223 |  | R22 | TXV |  | 3.761% | 0.96239 | 7.227% | [5 empty] | TXV | 3.761%
Riverbank | CA | 95367-3401 |  | 2013-07-25 | 2013-07-25 15:31 | 2013-07-25 15:51 | RUUD - CBD | 64 | -6 | Yes | Yes | 16.8 | 17.6 | -0.8 | 677F65E9E32C4E5EA41A03B246F58379 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Yuba City | CA | 95993-8905 |  | 2013-07-22 | 2013-07-22 11:19 | 2013-07-22 11:37 | CARRIER - 38BRC042330 | 101 | 3.7 | Yes | Yes | 17 | 19.5 | -2.5 | F18E97EA7D304F508FBEAA38084D139B |  | R22 | TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | TXV | 3.663%
Stockton | CA | 95210-2057 |  | 2013-07-31 | 2013-07-31 09:47 | 2013-07-31 10:10 | WESTINGHOUSE - IE024AAAON | 55 | -3.2 | Yes | Yes | 17.9 | 18 | -0.1 | B948F7E984F24A01827E3ECA10686F41 |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Stockton | CA | 95209-3906 |  | 2013-07-26 | 2013-07-26 12:07 | 2013-07-26 12:25 | GOODMAN - CKJ30-1A | 92 | -5.4 | Yes | Yes | 20.2 | 17.7 | 2.6 | C33366D8F33540589E79BD304560326A |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Grass Valley | CA | 95945-7350 |  | 2013-08-05 | 2013-08-05 10:16 | 2013-08-05 10:42 | AMERICAN STANDARD - YCY036G1M0AC | 130 | 12.5 | Yes | Yes | 24 | 19.9 | 4.1 | 6C5CAB067B004FA4BEC3CF748B884451 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.615% | 0.90385 | 18.48% | [5 empty] | Non-TXV | 9.615%
Madera | CA | 93637-4133 |  | 2013-07-28 | 2013-07-28 01:31 | 2013-07-28 01:55 | AIRE-FLO - | 85 | 5 | Yes | Yes | 17.7 | 19.3 | -1.6 | D6AC24D605044B3FB55706B063D5275A |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Atwater | CA | 95301-4028 |  | 2013-09-09 | 2013-09-09 14:52 | 2013-09-09 15:33 | PAYNE - 591AN024-A | 51 | 2 | Yes | Yes | 21.7 | 21.9 | -0.2 | 526933619652485A936F7E3634139522 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Atwater | CA | 95301-4028 |  | 2013-11-20 | 2013-11-20 10:13 | 2013-11-20 10:13 | PAYNE - 591AN024-A | 51 | 0 | Yes | Yes | 29.5 | 20.4 | 9.1 | 37DCFF087F854745B73DF85F7662EF6B | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-2711 |  | 2013-07-19 | 2013-07-19 10:58 | 2013-07-19 11:20 | BRYANT - 113ANA042-C | 88 | 2.7 | Yes | Yes | 18.4 | 18.2 | 0.2 | 176BB83E9090488FB41EEA8F4B5422D8 |  | R410A | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Stockton | CA | 95209-2149 |  | 2013-07-22 | 2013-07-22 09:37 | 2013-07-22 09:57 | BDP - 561AJ036-B | 77 | 2.4 | Yes | Yes | 21.1 | 17.6 | 3.5 | 961ABE0D70DD4BF2991ECC992D05CFB7 |  | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Madera | CA | 93638-5925 |  | 2013-07-26 | 2013-07-26 15:00 | 2013-07-27 00:03 | CARRIER - 388K (048371 | 100 | 6.4 | Yes | Yes | 18.5 | 21.4 | -2.9 | F19FD54AC38C4CBF8CA97475C082189F |  | R22 | Non-TXV |  | 6.4% | 0.936 | 12.3% | [5 empty] | Non-TXV | 6.4%
Tracy | CA | 95376-0717 |  | 2013-07-26 | 2013-07-26 08:57 | 2013-07-26 09:25 | YORK - H1CF036S06A | 132 | 3.9 | Yes | Yes | 24.5 | 19.8 | 4.7 | 458C354A784E4D45AF8AC1DBC0BC122A |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Stockton | CA | 95210-1419 |  | 2013-07-24 | 2013-07-24 08:25 | 2013-07-24 08:43 | DAY & NIGHT - 585EJ030050 | 58 | -3.4 | Yes | Yes | 22.8 | 18.3 | 4.5 | BB9E42B7BB4D4379911E8050A32A7E93 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Stockton | CA | 95210-3528 |  | 2013-07-30 | 2013-07-30 14:12 | 2013-07-30 14:30 | HEIL - UNK | 80 | 2.6 | Yes | Yes | 18.2 | 19.3 | -1.1 | BC46BE656690400AA8A4A5694900C2BA |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Madera | CA | 93636-8806 |  | 2013-07-23 | 2013-07-23 13:07 | 2013-07-23 13:55 | BRYANT - 582ANW042060NAAG | 100 | 5 | Yes | Yes | 17.9 | 19.7 | -1.8 | EB62E4A002A94AAD8099AB54AD62A082 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Los Banos | CA | 93635-5470 |  | 2013-07-29 | 2013-07-29 10:54 | 2013-07-29 10:59 | YORK - H3RA060S06A | 106 | 3.8 | Yes | Yes | 20.9 | 19.1 | 1.8 | F4CD20AD00EC4B5C97D3D1F5EF748CBC |  | R22 | Non-TXV |  | 3.585% | 0.96415 | 6.889% | [5 empty] | Non-TXV | 3.585%
Stockton | CA | 95215-7534 |  | 2013-09-11 | 2013-09-11 13:57 | 2013-09-11 14:16 | OTHER - LK-0525CC | 92 | 4.5 | Yes | Yes | 22.9 | 19.1 | 3.8 | A772E00EB5574F539F5491E4F887C2FB |  | R22 | Non-TXV |  | 4.891% | 0.95109 | 9.4% | [5 empty] | Non-TXV | 4.891%
Tracy | CA | 95377-8508 |  | 2013-07-26 | 2013-07-26 14:21 | 2013-07-26 14:39 | CARRIER - 38CKC060370 | 131 | -59.2 | Yes | Yes | 25.9 | 20.4 | 5.5 | 3732EC227B204F99AD6CD7429C5DDCAB | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -45.19% | 1.4519 | 12.66% |  |  |  |  | TXV |  |  | -45.19%
Rocklin | CA | 95677-3373 |  | 2013-07-20 | 2013-07-20 13:24 | 2013-07-20 13:24 | DAY & NIGHT - 591ANX048000AAAA | 115 | 0 | Yes | Yes | 25 | 21 | 4 | 65E91267AA3040F79FD0C655D80305A4 |  | R22 | TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-3833 |  | 2013-07-22 | 2013-07-22 10:25 | 2013-07-22 10:48 | RUUD - RAFD-042JBS | 79 | 2.3 | Yes | Yes | 21.1 | 19.9 | 1.2 | 72C7EFC5D3AC4623AA6118DD99FE8CB1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.911% | 0.97089 | 5.595% | [5 empty] | Non-TXV | 2.911%
Chico | CA | 95926-3803 |  | 2013-07-31 | 2013-07-31 13:13 | 2013-07-31 13:33 | DAY & NIGHT - PGD324060K001C1 | 72 | 2.5 | Yes | Yes | 24.6 | 20.2 | 4.5 | DDA3C952E8A74FF19B07F1559553B4E2 |  | R410A | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Corning | CA | 96021-3323 |  | 2013-07-24 | 2013-07-24 13:25 | 2013-07-24 20:42 | LENNOX - GCS020H-311-75-P | 48 | 4.9 | Yes | Yes | 22 | 21 | 1 | C08A3E908A6245A2BB1EE2BC254E7042 |  | R22 | Non-TXV |  | 10.21% | 0.89792 | 19.62% | [5 empty] | Non-TXV | 10.21%
Chico | CA | 95928-3926 |  | 2013-08-05 | 2013-08-05 17:10 | 2013-08-05 17:31 | TRANE - TTP042C100A2 | 156 | 5.8 | Yes | Yes | 26.5 | 21 | 5.5 | 1932539EE0694E649888D13AAD85498D |  | R22 | Non-TXV |  | 3.718% | 0.96282 | 7.145% | [5 empty] | Non-TXV | 3.718%
Madera | CA | 93638-1571 |  | 2013-07-21 | 2013-07-21 13:01 | 2013-07-21 13:01 | GOODMAN - GPG13360701AC | 112 | 0 | Yes | Yes | 16.8 | 19 | -2.2 | A38254E64D144EA582A65D91A0164A68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atascadero | CA | 93422-4663 |  | 2013-08-13 | 2013-08-13 14:38 | 2013-08-13 15:04 | WHIRLPOOL - 10024AEAON | 55 | 5.3 | Yes | Yes | 24 | 23.9 | 0.1 | 5F4AFBDD9864456F89488EA6729D3752 |  | R22 | TXV |  | 9.636% | 0.90364 | 18.52% | [5 empty] | TXV | 9.636%
Jackson | CA | 95642-9504 |  | 2013-09-03 | 2013-09-03 14:42 | 2013-09-03 18:32 | BRYANT - 561CJ024-C | 72 | 5.2 | Yes | Yes | 16.4 | 18.8 | -2.4 | 52C184809D7E4E51B61A29D3E79658B5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Stockton | CA | 95206-6440 |  | 2013-07-30 | 2013-07-30 13:17 | 2013-07-30 13:39 | GUARDIAN - GCGD36S21S2A | 63 | 3.4 | Yes | Yes | 24.4 | 19.4 | 5 | 742C2A4409E94A4B9C89E2AFE324EE44 |  | R22 | Non-TXV |  | 5.397% | 0.94603 | 10.37% | [5 empty] | Non-TXV | 5.397%
Madera | CA | 93637-1405 |  | 2013-08-05 | 2013-08-05 15:54 | 2013-08-05 15:55 | GOODMAN - GPG13360701AC | 112 | 13.4 | Yes | Yes | 23.7 | 19.2 | 4.5 | 9480FD4956A64203BF0840E12316A5A2 |  | R22 | Non-TXV |  | 11.96% | 0.88036 | 22.99% | [5 empty] | Non-TXV | 11.96%
Hilmar | CA | 95324-9433 |  | 2013-10-01 | 2013-10-01 15:17 | 2013-10-01 15:18 | RUUD - UAJC030JAS | 88 | 11.3 | Yes | Yes | 21.7 | 19 | 2.7 | 95798DFC4FFA466C9D9F9A002A7E3EB5 |  | R22 | Non-TXV |  | 12.84% | 0.87159 | 24.68% | [5 empty] | Non-TXV | 12.84%
Arnold | CA | 95223-0000 |  | 2013-09-04 | 2013-09-04 11:02 | 2013-09-04 11:40 | CARRIER - 24ACA348A3000 | 128 | 9.6 | Yes | Yes | 25 | 20.4 | 4.6 | DC5B254996124ED09D5A5E95CC6E95E5 |  | R410A | TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | TXV | 7.5%
Chico | CA | 95926-3216 |  | 2013-08-30 | 2013-08-30 11:34 | 2013-08-30 11:52 | LENNOX - 13ACC-030-230-01 | 109 | 3.6 | Yes | Yes | 16.8 | 18.8 | -2 | 6779791945D54388A6BAE53F0E64D429 |  | R22 | Non-TXV |  | 3.303% | 0.96697 | 6.347% | [5 empty] | Non-TXV | 3.303%
Newman | CA | 95360-1450 |  | 2013-07-29 | 2013-07-29 11:30 | 2013-07-29 11:57 | GOODMAN - GSC130361GA | 77 | 2.3 | Yes | Yes | 24 | 20.4 | 3.6 | 7DFB6536D4E344FE9C2084B758CE4C74 |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Stockton | CA | 95206-4680 |  | 2013-07-17 | 2013-07-17 13:24 | 2013-07-17 13:46 | BDP - 563CN036-B | 113 | 14.1 | Yes | Yes | 21.6 | 21 | 0.6 | 5F3A6CBC9C744F81BB12369AC19FABC2 |  | R22 | Non-TXV |  | 12.48% | 0.87522 | 23.98% | [5 empty] | Non-TXV | 12.48%
Auburn | CA | 95602-8470 |  | 2013-07-27 | 2013-07-27 09:31 | 2013-07-27 09:48 | TRANE - TTR030C100A2 | 74 | 2.7 | Yes | Yes | 16 | 18.2 | -2.2 | 1719821442BE4394AA56F807F2CF555A |  | R22 | TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | TXV | 3.649%
Stockton | CA | 95205-2618 |  | 2013-07-23 | 2013-07-23 11:11 | 2013-07-23 11:36 | RHEEM - RARA-048JAZ | 130 | -7.6 | Yes | Yes | 16.5 | 19 | -2.5 | BD1DD725F42D475FA37D305678C15937 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Lathrop | CA | 95330-9205 |  | 2013-07-24 | 2013-07-24 11:17 | 2013-07-24 11:36 | CARRIER - 38CM060-301 | 160 | 9.4 | Yes | Yes | 17.1 | 19.3 | -2.2 | D68A043D5D964226BCAE7BFC28FE8100 |  | R22 | TXV |  | 5.875% | 0.94125 | 11.29% | [5 empty] | TXV | 5.875%
Merced | CA | 95341-5417 |  | 2013-08-05 | 2013-08-05 09:21 | 2013-08-05 09:40 | GOODMAN - CKL30-1L | 74 | 6.9 | Yes | Yes | 16.8 | 19.3 | -2.5 | 341FD991A8BC483C92694107CEEFA260 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.324% | 0.90676 | 17.92% | [5 empty] | Non-TXV | 9.324%
Stockton | CA | 95204-3916 |  | 2013-07-25 | 2013-07-25 10:25 | 2013-07-25 11:01 | DAY & NIGHT - UNK | 62 | 3.6 | Yes | Yes | 20.3 | 20.4 | -0.1 | 76CD108F6D314D14810BC3B2E31732D4 |  | R22 | Non-TXV |  | 5.806% | 0.94194 | 11.16% | [5 empty] | Non-TXV | 5.806%
Stockton | CA | 95203-1448 |  | 2013-07-23 | 2013-07-23 11:09 | 2013-07-23 11:42 | HEIL - CA3030UKB1 | 66 | 10.6 | Yes | Yes | 14.1 | 17 | -2.9 | ECF8FAAA06F54D44A63686A5671BE021 |  | R22 | Non-TXV |  | 16.06% | 0.83939 | 30.86% | [5 empty] | Non-TXV | 16.06%
Stockton | CA | 95219-3922 |  | 2013-08-06 | 2013-08-06 15:29 | 2013-08-06 15:46 | OTHER - UNK | 64 | 9.8 | Yes | Yes | 18.4 | 19.3 | -0.9 | 4A1435A7A6F64C649A3A741AA8197948 |  | R22 | Non-TXV |  | 15.31% | 0.84688 | 29.43% | [5 empty] | Non-TXV | 15.31%
Lodi | CA | 95240-7300 |  | 2013-08-21 | 2013-08-21 15:11 | 2013-08-21 15:30 | OTHER - UNK | 70 | -4.9 | Yes | Yes | 19.1 | 19.5 | -0.4 | AF3ACEDC97D14C10BB1BD07FB16C147A |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Chico | CA | 95928-4155 |  | 2013-08-08 | 2013-08-08 12:54 | 2013-08-08 13:18 | TRANE - TTB024C100A2 | 54 | 4 | Yes | Yes | 16.5 | 19.4 | -2.9 | 1995C90A4ED14660B55E91E93615E5EF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
Rough & Ready | CA | 95975-9607 |  | 2013-10-02 | 2013-10-02 11:46 | 2013-10-02 12:03 | UNITARY PRODUCTS GROUP - BRCQ0301BE | 41 | 4.7 | Yes | Yes | 17.7 | 20.4 | -2.7 | C369E2A1D41141DA9C940CBD37371C8C |  | R22 | TXV |  | 11.46% | 0.88537 | 22.03% | [5 empty] | TXV | 11.46%
Madera | CA | 93637-5015 |  | 2013-08-02 | 2013-08-02 10:16 | 2013-08-02 10:16 | - 38N030300 | 85 | 0 | Yes | Yes | 19.4 | 20.7 | -1.3 | D55CB7632ABB4B45ADFA9BFCA507969E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3013 |  | 2013-07-25 | 2013-07-25 10:17 | 2013-07-25 10:35 | PAYNE - PA10JA030-C | 65 | 4 | Yes | Yes | 20.6 | 19.1 | 1.5 | 1D885A03E81F4C38A0FE3952581D5D62 |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Stockton | CA | 95219-3712 |  | 2013-07-26 | 2013-07-26 12:08 | 2013-07-26 12:26 | PAYNE - UNK | 80 | 4 | Yes | Yes | 18.5 | 19.3 | -0.8 | 32024737518D440CA78CFE1FFB6DC916 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Merced | CA | 95340-3213 |  | 2013-07-23 | 2013-07-23 17:47 | 2013-07-23 17:49 | TRANE - YCC036F1M0BK | 83 | 3.5 | Yes | Yes | 21.6 | 21.3 | 0.3 | 5CE5966A55EF4AFCAD396AD5DC41B22C |  | R22 | Non-TXV |  | 4.217% | 0.95783 | 8.104% | [5 empty] | Non-TXV | 4.217%
Applegate | CA | 95703-9739 |  | 2013-08-19 | 2013-08-19 11:10 | 2013-08-19 11:10 | TRANE - UNK FADED | 67 | 0 | Yes | Yes | 21.2 | 21.3 | -0.1 | 38B81843E304480D85C483E3BFB705C7 | OK: Verified Refrigerant Charge Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-2921 |  | 2013-08-05 | 2013-08-05 11:23 | 2013-08-05 11:49 | BRYANT - 561CJ030-B | 70 | 2.7 | Yes | Yes | 23.7 | 18 | 5.7 | 44D93AEE3E6E44F9827E1C2811E9C727 |  | R22 | TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | TXV | 3.857%
Merced | CA | 95348-2223 |  | 2013-07-18 | 2013-07-18 16:28 | 2013-07-18 16:29 | TRANE - YCY042F1M0AC | 136 | 4.4 | Yes | Yes | 24.4 | 19.9 | 4.5 | 309A2C829D374A9CA465AC7DCE96FFD8 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Merced | CA | 95348-3408 |  | 2013-07-24 | 2013-07-24 11:25 | 2013-07-24 11:28 | OTHER - 24C80 | 50 | 7.1 | Yes | Yes | 18.8 | 17 | 1.8 | FE3F3D05C1834007BFC8F4F911EEB6CC |  | R22 | Non-TXV |  | 14.2% | 0.858 | 27.29% | [5 empty] | Non-TXV | 14.2%
Chico | CA | 95973-0535 |  | 2013-09-26 | 2013-09-26 18:47 | 2013-09-26 18:47 | TEMPSTAR - TCA024AKA1 | 69 | 0 | Yes | Yes | 21 | 19.3 | 1.7 | BFD0910EB49C4B5F96AD58475BA3F7F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-2605 |  | 2013-07-19 | 2013-07-19 09:41 | 2013-07-19 09:58 | GOODMAN - CKL36-1H | 71 | -6.7 | Yes | Yes | 19.5 | 19.4 | 0.1 | 5BA3DE729DC04F15A529126E47C93B39 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.437% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.437%
Los Banos | CA | 93635-8596 |  | 2013-08-01 | 2013-08-01 13:26 | 2013-08-01 13:30 | LENNOX - 12GCS042-75-5PB | 133 | 4.6 | Yes | Yes | 23 | 18.6 | 4.4 | 14AEDF146D5A4D28982A6FB8F838D420 |  | R22 | Non-TXV |  | 3.459% | 0.96541 | 6.647% | [5 empty] | Non-TXV | 3.459%
El Dorado Hills | CA | 95762-5532 |  | 2013-08-30 | 2013-08-30 14:56 | 2013-08-30 15:17 | YORK - H2RC048S06A | 120 | 5.5 | Yes | Yes | 19 | 21.2 | -2.2 | D505B284D8A54CC0AA0205DDAC31769E |  | R22 | TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | TXV | 4.583%
Stockton | CA | 95205-3623 |  | 2013-07-23 | 2013-07-23 10:20 | 2013-07-23 10:39 | GOODMAN - PGB03005-1 REV A | 56 | 4.6 | Yes | Yes | 17.8 | 19.8 | -2 | DDE2D44DB7974E6DB8E950B2F4712922 |  | R22 | Non-TXV |  | 8.214% | 0.91786 | 15.79% | [5 empty] | Non-TXV | 8.214%
Madera | CA | 93637-6316 |  | 2013-07-23 | 2013-07-23 18:28 | 2013-07-23 18:28 | LENNOX - GCS29X030-752PA | 51 | 1.6 | Yes | Yes | 19.5 | 18.8 | 0.8 | B88AC47DF49A4E54A965015BFBF81E1E | Add refrigerant: 1.6 oz | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Merced | CA | 95348-3179 |  | 2013-08-09 | 2013-08-09 16:14 | 2013-08-09 16:35 | GE - BTB92B100A0 | 56 | 1.9 | Yes | Yes | 20.4 | 20.1 | 0.3 | 3E1B9CF6AF14455FAC75707A727E6F3C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Merced | CA | 95348-3177 |  | 2013-09-03 | 2013-09-03 15:34 | 2013-09-03 16:06 | CARRIER - 38YCA024360 | 72 | 7.2 | Yes | Yes | 18.2 | 17.2 | 1 | F342601CD4424E5D96141CE85F54EC90 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Los Banos | CA | 93635-2957 |  | 2013-07-24 | 2013-07-24 11:14 | 2013-07-24 11:15 | DAY & NIGHT - 7777UNK | 100 | 3.5 | Yes | Yes | 23.4 | 21.1 | 2.3 | 9E17005EBBB046509345B6FE85BEF321 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Merced | CA | 95348-3124 |  | 2013-08-26 | 2013-08-26 14:29 | 2013-08-26 14:31 | BDP - 540JJ030 | 68 | 9.4 | Yes | Yes | 24 | 21.5 | 2.5 | 34C7E87F6AEC444698FEABAC3C20BB90 |  | R22 | Non-TXV |  | 13.82% | 0.86176 | 26.57% | [5 empty] | Non-TXV | 13.82%
El Dorado Hills | CA | 95762-4568 |  | 2013-10-01 | 2013-10-01 15:07 | 2013-10-01 15:07 | GOODMAN - CKL36-1H | 71 | 0 | Yes | Yes | 21.3 | 19.7 | 1.6 | 6C1C74397D3E40A2A757E8ED99FBD4D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Plumas Lake | CA | 95961-9126 |  | 2013-10-16 | 2013-10-16 15:00 | 2013-10-16 15:18 | CARRIER - 38BRC048370 | 120 | 4.8 | Yes | Yes | 23 | 21.2 | 1.8 | E272D90288F340ADBA720065A6A21410 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Madera | CA | 93638-1722 |  | 2013-07-18 | 2013-07-18 12:39 | 2013-07-18 13:18 | RHEEM - UNK | 81 | -5.7 | Yes | Yes | 15 | 17.7 | -2.7 | A301E6A6F81E4697A19E613B9E876C9E |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Copperopolis | CA | 95228-9528 |  | 2013-08-22 | 2013-08-22 16:41 | 2013-08-22 17:37 | PAYNE - PA10NR03600GAJAA | 88 | 4.1 | Yes | Yes | 27.8 | 22.5 | 5.3 | DB92B40B0ADE4CE29026F05E651DFA07 |  | R22 | Non-TXV |  | 4.659% | 0.95341 | 8.954% | [5 empty] | Non-TXV | 4.659%
El Dorado Hills | CA | 95762-7557 |  | 2013-08-30 | 2013-08-30 15:35 | 2013-08-30 15:56 | YORK - H3RA060S06B | 98 | 3.9 | Yes | Yes | 21 | 22.1 | -1.1 | F55F8DDC21DC4FEAA2C799651D9370CF |  | R22 | TXV |  | 3.98% | 0.9602 | 7.648% | [5 empty] | TXV | 3.98%
Watsonville | CA | 95076-4183 |  | 2013-10-21 | 2013-10-21 14:10 | 2013-10-21 14:28 | BRYANT - 561CJ024-D | 59 | 2.7 | Yes | Yes | 19 | 18.7 | 0.3 | 9730712AA84847FBAF169334C65A2FF7 |  | R22 | Non-TXV |  | 4.576% | 0.95424 | 8.795% | [5 empty] | Non-TXV | 4.576%
Stockton | CA | 95206-6356 |  | 2013-07-25 | 2013-07-25 09:56 | 2013-07-25 10:15 | YORK - H2RC048S06A | 120 | 4.5 | Yes | Yes | 21.4 | 19.6 | 1.8 | 4719D4C02CFA4B2BBE6ABDD5E8BEC475 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
San Carlos | CA | 94070-3653 |  | 2013-10-15 | 2013-10-15 14:28 | 2013-10-15 14:50 | CARRIER - 38HDC060321 | 210 | 6.3 | Yes | Yes | 21 | 19.9 | 1.1 | 6C0301D82791468F81A3CC8D3D622A2D |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chowchilla | CA | 93610-2027 |  | 2013-08-02 | 2013-08-02 03:53 | 2013-08-02 06:52 | RHEEM - RR-GG05N36JKR | 45 | 3.9 | Yes | Yes | 20.2 | 20.4 | -0.2 | 9C49C4825E944058A8EFF2F335728AD3 |  | R22 | TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | TXV | 8.667%
Marysville | CA | 95901-8278 |  | 2013-08-09 | 2013-08-09 10:50 | 2013-08-09 11:11 | BRYANT - 561CJ030-E | 70 | 10.4 | Yes | Yes | 18 | 20.4 | -2.4 | 910B16CA71F14EF8AEF51C5998D1A42E |  | R22 | Non-TXV |  | 14.86% | 0.85143 | 28.55% | [5 empty] | Non-TXV | 14.86%
Stockton | CA | 95210-2048 |  | 2013-07-31 | 2013-07-31 11:54 | 2013-07-31 12:11 | LENNOX - PGE10A48D125-1PA | 97 | 3.8 | Yes | Yes | 20.6 | 18.8 | 1.8 | 2AB0E342F3B742C6BBE1E234CCCA4AA1 |  | R22 | Non-TXV |  | 3.918% | 0.96082 | 7.529% | [5 empty] | Non-TXV | 3.918%
Stockton | CA | 95205-7732 |  | 2013-08-02 | 2013-08-02 10:27 | 2013-08-02 10:50 | YORK - UNK | 111 | 23.9 | Yes | Yes | 21.1 | 19.9 | 1.2 | B9F3BEF77FA24F4E8919E1A2FE453C5C |  | R22 | Non-TXV |  | 21.53% | 0.78468 | 41.38% | [5 empty] | Non-TXV | 21.53%
Grass Valley | CA | 95949-9157 |  | 2013-08-23 | 2013-08-23 18:44 | 2013-08-23 18:44 | BRYANT - 114ANA042-A | 166 | 0 | Yes | Yes | 21.9 | 21.4 | 0.5 | 6230B0AA56654977BC8BF38A379F8C45 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1440 |  | 2013-08-23 | 2013-08-23 09:54 | 2013-08-23 10:11 | GOODMAN - CKL36-1D | 72 | 3.9 | Yes | Yes | 18.5 | 18 | 0.6 | A20CB4AD6E0F45379C7491971C1CC6A9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Merced | CA | 95348-3124 |  | 2013-10-16 | 2013-10-16 10:28 | 2013-10-16 10:32 | AIRE-FLO - BWB918A1000 | 77 | 7.7 | Yes | Yes | 23.1 | 17.7 | 5.4 | 9EE3D9ED05B3488DACF701C9C5ADBE0B |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95209-1153 |  | 2013-07-22 | 2013-07-22 09:01 | 2013-07-22 09:18 | PAYNE - 585GJ030040 | 58 | -3.4 | Yes | Yes | 22.4 | 18.1 | 4.3 | FBF8E68CBADA488D8B274F745EFE27C5 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Madera | CA | 93637-8938 |  | 2013-08-06 | 2013-08-06 14:37 | 2013-08-06 15:11 | YORK - D1NQ060NN0906NXA | 85 | 3.2 | Yes | Yes | 19.1 | 20.7 | -1.6 | 06914CB6A1164FA088723C33F1AE0FB9 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Stockton | CA | 95206-2818 |  | 2013-07-17 | 2013-07-17 11:42 | 2013-07-17 12:10 | BRYANT - 561C048-A | 102 | 4.5 | Yes | Yes | 23.4 | 19.3 | 4.1 | F759B9671DE2468AA1A671B6EE18AA04 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Newman | CA | 95360-1436 |  | 2013-07-29 | 2013-07-29 15:23 | 2013-07-29 15:48 | CARRIER - 38EH024320 | 96 | 10.1 | Yes | Yes | 25.5 | 20.7 | 4.8 | 0F7543E07AD445E9A64CA2FD6E0637AF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.52% | 0.89479 | 20.22% | [5 empty] | Non-TXV | 10.52%
Atwater | CA | 95301-3035 |  | 2013-07-19 | 2013-07-19 16:19 | 2013-07-19 16:45 | OTHER - 80WE36G1NA | 86 | 13.6 | Yes | Yes | 19.9 | 19.7 | 0.2 | A7B51B371F3540D4A27349B7EFE0995F |  | R22 | Non-TXV |  | 15.81% | 0.84186 | 30.39% | [5 empty] | Non-TXV | 15.81%
Mariposa | CA | 95338-9361 |  | 2013-07-31 | 2013-07-31 12:54 | 2013-07-31 12:56 | CARRIER - 48KLA136-321BE | 102 | 5.7 | Yes | Yes | 21.1 | 19.7 | 1.5 | 70C6B57898F54E09AA53D44ADF4A8F8A |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Los Banos | CA | 93635-4208 |  | 2013-08-16 | 2013-08-16 12:17 | 2013-08-16 12:19 | COLEMAN - HBBD-F036SB | 96 | 3 | Yes | Yes | 25.5 | 20.4 | 5.1 | C4384AF9B5724693BA45BCA13A6134EB |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Newman | CA | 95360-1411 |  | 2013-08-22 | 2013-08-22 10:38 | 2013-08-22 11:35 | BRYANT - 583BNW048115NB | 149 | 4.5 | Yes | Yes | 22.7 | 20.2 | 2.6 | FA3D33280A6F49A982C37DE59372E440 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.02% | 0.9698 | 5.804% | [5 empty] | Non-TXV | 3.02%
Rocklin | CA | 95677-2856 |  | 2013-07-20 | 2013-07-20 08:42 | 2013-07-20 09:04 | OTHER - UNK | 80 | 19.6 | Yes | Yes | 16 | 18.6 | -2.6 | B1DCE2D022664421B1395CB34402BF9B |  | R22 | Non-TXV |  | 24.5% | 0.755 | 47.08% | [5 empty] | Non-TXV | 24.5%
Riverbank | CA | 95367-3152 |  | 2013-09-12 | 2013-09-12 16:55 | 2013-10-23 17:27 | DAY & NIGHT - 587ANZ024040A???????? | 85 | 2.6 | Yes | Yes | 16.9 | 19.2 | -2.3 | B5722A53AD1941CF9FF7A9633143CB29 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Riverbank | CA | 95367-2720 |  | 2013-08-29 | 2013-08-29 14:22 | 2013-08-29 14:54 | ICP - PGX330060K01A1 | 129 | 3.7 | Yes | Yes | 19 | 18.6 | 0.4 | 335F3B453D6343E4B1E9020F2FA5F635 |  | R410A | TXV |  | 2.868% | 0.97132 | 5.512% | [5 empty] | TXV | 2.868%
Los Banos | CA | 93635-9710 |  | 2013-07-30 | 2013-07-30 11:16 | 2013-07-30 11:18 | BDP - 588ANW02404ACAD | 44 | 2.3 | Yes | Yes | 23.8 | 19.7 | 4.1 | B2C886FEB9FE40308915ED1D74559782 |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Oakdale | CA | 95361-3915 |  | 2013-08-28 | 2013-08-28 11:50 | 2013-08-28 12:32 | HEIL - NRGF24DDB04 | 53 | 4.2 | Yes | Yes | 22.7 | 18.8 | 3.9 | 20143D09C54D4602B1DC25C7D697AB0C |  | R22 | Non-TXV |  | 7.925% | 0.92075 | 15.23% | [5 empty] | Non-TXV | 7.925%
Red Bluff | CA | 96080-4014 |  | 2013-09-20 | 2013-09-20 14:09 | 2013-09-20 14:34 | BRYANT - 582ANW036060ABAF | 68 | 4.1 | Yes | Yes | 17.6 | 20 | -2.4 | E2A6A7D92055460BB120E2A0F1123C9F |  | R22 | Non-TXV |  | 6.029% | 0.93971 | 11.59% | [5 empty] | Non-TXV | 6.029%
Yuba City | CA | 95991-8210 |  | 2013-08-06 | 2013-08-06 14:29 | 2013-08-06 15:14 | OTHER - AC1CN048-A | 165 | 6.4 | Yes | Yes | 18 | 19.2 | -1.2 | B58F14A168B94CD7BDE40AD059E12C33 |  | R22 | TXV |  | 3.879% | 0.96121 | 7.454% | [5 empty] | TXV | 3.879%
Lathrop | CA | 95330-8914 |  | 2013-07-24 | 2013-07-24 12:31 | 2013-07-24 12:52 | GOODMAN - CJK36-1D | 90 | 6.2 | Yes | Yes | 24.8 | 20.2 | 4.6 | FCC783DC726C4221839655CF9CBD008F |  | R22 | Non-TXV |  | 6.889% | 0.93111 | 13.24% | [5 empty] | Non-TXV | 6.889%
Stockton | CA | 95204-5713 |  | 2013-08-22 | 2013-08-22 12:44 | 2013-08-22 13:07 | RHEEM - 14AJM24A01 | 105 | 6.5 | Yes | Yes | 19.3 | 21.5 | -2.2 | BFB97E53D3464966BC0574F5F9390775 |  | R410A | TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | TXV | 6.19%
Los Banos | CA | 93635-9211 |  | 2013-08-05 | 2013-08-05 14:00 | 2013-08-05 14:06 | GIBSON - JS3BC-036KA | 82 | 3.2 | Yes | Yes | 14.7 | 17.7 | -3 | 40AB9121EB71471FA12E8EE61F41C8B1 |  | R22 | Non-TXV |  | 3.902% | 0.96098 | 7.5% | [5 empty] | Non-TXV | 3.902%
Oakdale | CA | 95361-3915 |  | 2013-08-28 | 2013-08-28 12:40 | 2013-08-28 13:01 | HEIL - MRGF24DK804 | 53 | 1.6 | Yes | Yes | 19.2 | 18.8 | 0.4 | 19875EEF4515455DA219EC06026D8710 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Stockton | CA | 95206-4848 |  | 2013-07-20 | 2013-07-20 11:10 | 2013-07-20 11:35 | BRYANT - 562CJ036-C | 96 | -7.9 | Yes | Yes | 16.7 | 19.6 | -2.9 | 86C90B49B4CF4CAA86F1F413C7155185 |  | R22 | Non-TXV |  | -8.229% | 1.0823 | 2.305% |  |  |  |  | Non-TXV |  |  | -8.229%
Stockton | CA | 95206-1444 |  | 2013-07-17 | 2013-07-17 10:26 | 2013-07-17 10:26 | GMC - VSX130361DA | 77 | 0 | Yes | Yes | 22.7 | 18.2 | 4.5 | CD27A5E9F36744728A5EC398BD4CE6BD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-6051 |  | 2013-08-07 | 2013-08-07 08:42 | 2013-08-07 08:42 | DAY & NIGHT - PGD324040K001C1 | 72 | 0 | Yes | Yes | 18.8 | 19.5 | -0.7 | B13EA854D8254F62B0280F905356A9A6 |  | R410A | TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-5712 |  | 2013-08-05 | 2013-08-05 13:58 | 2013-08-05 18:18 | BRYANT - 582AW036060AAF | 56 | 8.1 | Yes | Yes | 20 | 20.8 | -0.8 | 5FA001813F934D83BE0E1A2E9987E602 |  | R22 | Non-TXV |  | 14.46% | 0.85536 | 27.8% | [5 empty] | Non-TXV | 14.46%
Stockton | CA | 95209-4221 |  | 2013-07-26 | 2013-07-26 08:35 | 2013-07-26 08:53 | YORK - AC060X1223A | 147 | 4.3 | Yes | Yes | 19.8 | 18.6 | 1.2 | 501300DAC1C34FAC9CDF46D471D81285 |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.622% | [5 empty] | Non-TXV | 2.925%
Manteca | CA | 95336-4008 |  | 2013-07-18 | 2013-07-18 10:38 | 2013-07-18 11:07 | GOODMAN - CLJ30-1C | 105 | 9.8 | Yes | Yes | 19.9 | 18.7 | 1.2 | B25357EC2D0E4CDF9E0E8F553503D71B |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Chico | CA | 95928-6422 |  | 2013-08-02 | 2013-08-02 10:28 | 2013-08-02 10:47 | LENNOX - HS18-461-4P | 93 | -5.5 | Yes | Yes | 20.3 | 18.3 | 2 | 70C97759A37142418D7D5C4A88901B38 |  | R22 | Non-TXV |  | -5.914% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.914%
Rough & Ready | CA | 95975-9719 |  | 2013-08-26 | 2013-08-26 10:59 | 2013-08-26 11:20 | CARRIER - 48GX-03609030AD | 83 | 12.5 | Yes | Yes | 20.6 | 19.5 | 1.1 | F277A76F67234EC68D6E6A55C32A4CD6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.06% | 0.8494 | 28.94% | [5 empty] | Non-TXV | 15.06%
Stockton | CA | 95206-6337 |  | 2013-07-25 | 2013-07-25 14:07 | 2013-07-25 14:30 | GOODMAN - CKT42-1AB | 132 | 7.5 | Yes | Yes | 23.1 | 19 | 4.1 | 1FF11A56DCBB43C5A1C0378A3225B8EC |  | R22 | Non-TXV |  | 5.682% | 0.94318 | 10.92% | [5 empty] | Non-TXV | 5.682%
Red Bluff | CA | 96080-9725 |  | 2013-09-11 | 2013-09-11 13:44 | 2013-09-11 14:22 | LENNOX - 12GCS042X-100-1PA | 133 | 4.2 | Yes | Yes | 17.3 | 19.3 | -2 | 35A3F782D7DB44369DF70943C4BF97D6 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Stockton | CA | 95209-1316 |  | 2013-08-23 | 2013-08-23 13:29 | 2013-08-23 13:29 | PAYNE - 567C036RCU | 67 | 0 | Yes | Yes | 18.6 | 19 | -0.4 | CF7B05C4040247A79D4DF1A48052AE6A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3814 |  | 2013-07-23 | 2013-07-23 15:32 | 2013-07-23 16:00 | GOODMAN - UNK | 80 | 8 | Yes | Yes | 19.9 | 22.6 | -2.7 | 8C30839696204C2D849C63C916EFBFEE |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Chico | CA | 95926-2031 |  | 2013-08-16 | 2013-08-16 09:52 | 2013-08-16 10:35 | RUUD - URKA-A036JKO6X | 62 | -3.6 | Yes | Yes | 22.7 | 20.7 | 2 | 7C7533E81371452D991037745B4E6F7B |  | R22 | Non-TXV |  | -5.806% | 1.0581 | 1.626% |  |  |  |  | Non-TXV |  |  | -5.806%
Oroville | CA | 95966-5679 |  | 2013-08-06 | 2013-08-06 17:31 | 2013-08-06 17:31 | WESTINGHOUSE - FT3BD-024K | 128 | 0 | Yes | Yes | 21.5 | 21.2 | 0.3 | EDACC25A265A4AC684ECA73FE4E2C6AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1507 |  | 2013-07-18 | 2013-07-18 15:35 | 2013-07-18 15:38 | YORK - H2DA048S06A | 124 | 4.6 | Yes | Yes | 29.1 | 23.1 | 6 | 36B8C8657DD8471FBCF20F4F144DCCF5 |  | R22 | Non-TXV |  | 3.71% | 0.9629 | 7.129% | [5 empty] | Non-TXV | 3.71%
Stockton | CA | 95210-3271 |  | 2013-08-14 | 2013-08-14 14:50 | 2013-08-14 15:15 | GE - BTB936A1000 | 83 | 7.8 | Yes | Yes | 27.3 | 21.9 | 5.4 | A581FCF7CBAB42AD913D4933F132CE38 |  | R22 | Non-TXV |  | 9.398% | 0.90602 | 18.06% | [5 empty] | Non-TXV | 9.398%
Winton | CA | 95388-9214 |  | 2013-07-22 | 2013-07-22 16:56 | 2013-07-22 17:25 | GOODMAN - SSX160301AA | 96 | 13.3 | Yes | Yes | 20.4 | 17.7 | 2.7 | D8DCF3B852CD42D8B5C0DDEB3973118F |  | R410A | Non-TXV |  | 13.85% | 0.86146 | 26.62% | [5 empty] | Non-TXV | 13.85%
Stockton | CA | 95212-3831 |  | 2013-07-23 | 2013-07-23 13:33 | 2013-07-23 13:58 | YORK - H1RA042S06G | 84 | 13.5 | Yes | Yes | 17.6 | 20.4 | -2.8 | 1DE43418FE504FEC82977AEACE589896 |  | R22 | Non-TXV |  | 16.07% | 0.83929 | 30.89% | [5 empty] | Non-TXV | 16.07%
Marysville | CA | 95901-3567 |  | 2013-08-08 | 2013-08-08 12:44 | 2013-08-08 13:07 | LENNOX - HS29-036-2P | 70 | 5.7 | Yes | Yes | 17 | 19.2 | -2.2 | 6D4A15650893482888BC8FD25089BDB3 |  | R22 | TXV |  | 8.143% | 0.91857 | 15.65% | [5 empty] | TXV | 8.143%
Colfax | CA | 95713-9122 |  | 2013-07-25 | 2013-07-25 13:42 | 2013-07-25 14:01 | BRYANT - 563CN048000AFAA | 160 | -7.2 | Yes | Yes | 18 | 19.9 | -1.9 | E67879534BB445F48D2549BF8226A837 |  | R22 | TXV |  | -4.5% | 1.045 | 1.26% |  |  |  |  | TXV |  |  | -4.5%
Stockton | CA | 95205-6502 |  | 2013-07-17 | 2013-07-17 13:20 | 2013-07-17 13:45 | TRANE - YCY036G1M0AD | 133 | 4.4 | Yes | Yes | 23.8 | 17.9 | 5.9 | F5FA9339CAF847BEB72AA46D4212564F |  | R22 | Non-TXV |  | 3.308% | 0.96692 | 6.358% | [5 empty] | Non-TXV | 3.308%
Sanger | CA | 93657-8635 |  | 2013-08-05 | 2013-08-05 18:12 | 2013-08-05 18:58 | GOODMAN - CKL36-1L | 84 | 3 | Yes | Yes | 22.5 | 19.9 | 2.6 | 7D19A76569A14ADB94E1C43F6B2277C7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Ione | CA | 95640-5407 |  | 2013-07-24 | 2013-07-24 15:53 | 2013-07-24 16:10 | PAYNE - PA12NA030000AAAA | 96 | 3.8 | Yes | Yes | 20 | 22.1 | -2.1 | EB86F4C6589F4FD8B3BAB8B325576D9C |  | R22 | TXV |  | 3.958% | 0.96042 | 7.607% | [5 empty] | TXV | 3.958%
Cameron Park | CA | 95682-8601 |  | 2013-07-19 | 2013-07-19 08:53 | 2013-07-19 08:53 | OTHER - Q5RD-036K | 137 | 0 | Yes | Yes | 27 | 21 | 6 | 725990AB8446460483B74BE1B7612EB3 |  | R410A | TXV |  | 0% | 1 | 0%
Chico | CA | 95926-4452 |  | 2013-10-02 | 2013-10-02 10:40 | 2013-10-02 11:00 | RHEEM - RAKA-024JAZ | 53 | 6.1 | Yes | Yes | 18.6 | 21.5 | -2.9 | F2E2CF91EA63474E989385BE380A8164 |  | R22 | Non-TXV |  | 11.51% | 0.88491 | 22.12% | [5 empty] | Non-TXV | 11.51%
Oroville | CA | 95965-8038 |  | 2013-07-29 | 2013-07-29 18:08 | 2013-07-29 20:58 | COLEMAN - BRCSO421BD | 85 | 3.7 | Yes | Yes | 23.7 | 22.1 | 1.6 | 3FCF8B2DA94E4E5E938AF99AB036710E |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Kerman | CA | 93630-9509 |  | 2013-08-01 | 2013-08-01 14:00 | 2013-08-01 14:02 | ICP - PGAB24B1K1 | 80 | 10.1 | Yes | Yes | 27.3 | 22.5 | 4.8 | 7E7F37E306EC418B8EB9B3C8470B1BF7 |  | R22 | Non-TXV |  | 12.62% | 0.87375 | 24.26% | [5 empty] | Non-TXV | 12.62%
Lathrop | CA | 95330-0000 |  | 2013-07-30 | 2013-07-30 09:56 | 2013-07-30 10:21 | CARRIER - 38BRC048370 | 85 | 3.1 | Yes | Yes | 21.9 | 19.3 | 2.6 | 9F07EB347FD9440EB862846194DFB2FC |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Arbuckle | CA | 95912-0000 |  | 2013-07-30 | 2013-07-30 18:12 | 2013-07-30 18:28 | HEIL - N4A336AKB200 | 85 | 3.6 | Yes | Yes | 18 | 21 | -3 | 4EF3D06B1B40406C9BC5D0576ABA2D82 |  | R410A | TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | TXV | 4.235%
Fresno | CA | 93728-2014 |  | 2013-08-15 | 2013-08-15 12:30 | 2013-08-15 12:32 | RHEEM - RRNL-B036JK06X | 93 | 2.7 | Yes | Yes | 22.3 | 20.5 | 1.9 | D0473944E3834AFCA7FA440A10DEACC0 |  | R410A | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Fresno | CA | 93705-4141 |  | 2013-07-19 | 2013-07-19 10:57 | 2013-07-19 10:59 | OTHER - 7777UNK | 80 | 3.3 | Yes | Yes | 21.5 | 20.4 | 1.1 | 5162318A7B824779BBDD6323F52906B5 |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Fresno | CA | 93710-7207 |  | 2013-08-12 | 2013-08-12 15:04 | 2013-08-12 20:17 | AMERICAN STANDARD - YCC0241FLOAH | 104 | 4.5 | Yes | Yes | 17.5 | 20 | -2.5 | 46C27088E010452780C2DB13AE94179D |  | R22 | Non-TXV |  | 4.327% | 0.95673 | 8.315% | [5 empty] | Non-TXV | 4.327%
Stockton | CA | 95206-4807 |  | 2013-07-17 | 2013-07-17 14:16 | 2013-07-17 14:16 | RHEEM - RRKA-A030JK08X | 54 | 0 | Yes | Yes | 18.9 | 17.9 | 1 | ABC211C124564E4B86021D38A4E65E98 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-4636 |  | 2013-07-24 | 2013-07-24 19:21 | 2013-07-24 19:21 | AMERICAN STANDARD - 4YCY4 042B 1096 AA | 85 | 0 | Yes | Yes | 19.9 | 22.1 | -2.2 | E2E8D51C233D4C96BF00F65836550689 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3461 |  | 2013-07-22 | 2013-07-22 11:09 | 2013-07-22 11:36 | BRYANT - 561CJ036-F | 70 | 7.4 | Yes | Yes | 17.5 | 20.1 | -2.6 | 9ED3A8B1571B4371990156DD4EBF9536 |  | R22 | Non-TXV |  | 10.57% | 0.89429 | 20.32% | [5 empty] | Non-TXV | 10.57%
Los Banos | CA | 93635-0000 |  | 2013-07-29 | 2013-07-29 10:23 | 2013-07-29 10:29 | BRYANT - 7777UNK | 100 | 4.9 | Yes | Yes | 20.8 | 19.3 | 1.5 | 83506BCB4BA642D095E8E2AF05A0AE53 |  | R22 | Non-TXV |  | 4.9% | 0.951 | 9.417% | [5 empty] | Non-TXV | 4.9%
Sanger | CA | 93657-8632 |  | 2013-07-24 | 2013-07-24 09:24 | 2013-07-24 09:56 | GOODMAN - CRT42-1 | 125 | 19.7 | Yes | Yes | 18.6 | 20.7 | -2.1 | D204DB1452FF47A288F614B0B50A1421 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.76% | 0.8424 | 30.29% | [5 empty] | Non-TXV | 15.76%
Stockton | CA | 95212-2118 |  | 2013-07-23 | 2013-07-23 16:22 | 2013-07-23 16:45 | DAY & NIGHT - UNK | 96 | 8.1 | Yes | Yes | 23.9 | 22.1 | 1.8 | E46377E6E48143B39EAF24BE4B6AD803 |  | R22 | Non-TXV |  | 8.438% | 0.91563 | 16.22% | [5 empty] | Non-TXV | 8.438%
Durham | CA | 95938-9613 |  | 2013-09-06 | 2013-09-06 11:43 | 2013-09-06 12:45 | DAY & NIGHT - 588ANW048080 | 101 | 9.2 | Yes | Yes | 17.5 | 20.4 | -2.9 | 8C0110BA8FDC4DC2830EC430C2B7E942 |  | R22 | Non-TXV |  | 9.109% | 0.90891 | 17.51% | [5 empty] | Non-TXV | 9.109%
Reedley | CA | 93654-3516 |  | 2013-07-24 | 2013-07-24 17:05 | 2013-07-24 17:24 | CARRIER - 48SS-030060321 | 53 | 8.2 | Yes | Yes | 18.7 | 19.3 | -0.6 | 5907BDCF42F5401D9566F7DA0ABBC30E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.47% | 0.84528 | 29.73% | [5 empty] | Non-TXV | 15.47%
Valley Springs | CA | 95252-9604 |  | 2013-08-14 | 2013-08-14 11:47 | 2013-08-14 12:16 | GIBSON - UNK | 85 | 19.9 | Yes | Yes | 22.1 | 22 | 0.1 | FB08FBF903B54366AC6D2316E24DBBC5 |  | R22 | Non-TXV |  | 23.41% | 0.76588 | 44.99% | [5 empty] | Non-TXV | 23.41%
Stockton | CA | 95215-7309 |  | 2013-09-12 | 2013-09-12 13:27 | 2013-09-12 13:27 | BRYANT - 582ANW036000AAAF | 56 | 0 | Yes | Yes | 17.7 | 18 | -0.3 | EE4AC9A63A1142C3A5CA4681C4ADADEA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-0000 |  | 2013-07-31 | 2013-07-31 11:56 | 2013-07-31 11:57 | YORK - H2RC036S06G | 83 | 9 | Yes | Yes | 19.2 | 19.3 | -0.1 | CE830608690B42ED8AB1056C1633C1D6 |  | R22 | Non-TXV |  | 10.84% | 0.89157 | 20.84% | [5 empty] | Non-TXV | 10.84%
Parlier | CA | 93648-2338 |  | 2013-09-04 | 2013-09-04 17:29 | 2013-09-04 18:00 | CONCORD - CCU10A30A-1 | 60 | 2.4 | Yes | Yes | 19.4 | 20.8 | -1.4 | 0C517E08D37143D7A1605AFFA71A00A6 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Tracy | CA | 95376-1926 |  | 2013-07-23 | 2013-07-23 11:32 | 2013-07-23 11:54 | NORDYNE - JS3BA-036KA | 89 | 2.7 | Yes | Yes | 25.9 | 20 | 6 | 4C6F4B74C9A44F098B6322A1693F3DD6 |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Stockton | CA | 95206-2354 |  | 2013-07-17 | 2013-07-17 09:46 | 2013-07-17 10:04 | BRYANT - 561CJ042-A | 80 | 3.2 | Yes | Yes | 21.1 | 19.5 | 1.6 | 7058D81E2C3F449FBC0BB95151380A78 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Placerville | CA | 95667-7120 |  | 2013-08-29 | 2013-08-29 19:05 | 2013-08-29 19:05 | RHEEM - RAND-036JAZ | 116 | 0 | Yes | Yes | 22.3 | 19.9 | 2.4 | 24F54AF6540E43E2B4D6C9490DCB8CC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9744 |  | 2013-08-01 | 2013-08-01 14:56 | 2013-08-01 14:58 | YORK - D3GA042N06006A | 82 | 12.6 | Yes | Yes | 25.5 | 22.9 | 2.6 | 3ED2C7343BEE4604A8AED0D4BDE73954 |  | R22 | Non-TXV |  | 15.37% | 0.84634 | 29.53% | [5 empty] | Non-TXV | 15.37%
Los Banos | CA | 93635-4507 |  | 2013-07-24 | 2013-07-24 13:47 | 2013-07-24 13:49 | CARRIER - 7777UNK | 60 | 2.4 | Yes | Yes | 23.4 | 21.5 | 1.9 | 5C2DA9368DA243D185AF1FB10087826B |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Reedley | CA | 93654-0000 |  | 2013-07-24 | 2013-07-24 19:25 | 2013-07-24 21:12 | ICP - CA5548VKD2 | 134 | 4 | Yes | Yes | 19.6 | 21.5 | -1.9 | FBDB591ACA914C5CAB71B771A1BF1A7C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Yuba City | CA | 95993-7661 |  | 2013-08-07 | 2013-08-07 15:45 | 2013-08-07 16:09 | RHEEM - RAFD-048JBS | 101 | 3.8 | Yes | Yes | 17.5 | 19.3 | -1.8 | 0FDDACEA6AF94081AC40FABCA40AC2A8 |  | R22 | TXV |  | 3.762% | 0.96238 | 7.23% | [5 empty] | TXV | 3.762%
Fresno | CA | 93710-7107 |  | 2013-07-22 | 2013-07-22 13:43 | 2013-07-22 13:45 | AMERICAN STANDARD - YCC024F1LOBE | 64 | 11.4 | Yes | Yes | 19.4 | 20.4 | -1 | AFFCD5E5CFBA42ACB16F7FB90AA56506 |  | R22 | Non-TXV |  | 17.81% | 0.82188 | 34.23% | [5 empty] | Non-TXV | 17.81%
Madera | CA | 93638-0373 |  | 2013-07-29 | 2013-07-29 09:28 | 2013-07-29 10:20 | CARRIER - 500Q50340 | 165 | 5.1 | Yes | Yes | 17.5 | 19.7 | -2.2 | B014799B67FA4F528B13427E138B48E8 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Grass Valley | CA | 95949-9146 |  | 2013-08-07 | 2013-08-07 16:20 | 2013-08-07 16:20 | BRYANT - 113RNA036-B | 93 | 0 | Yes | Yes | 24.8 | 21.8 | 3 | BF3A914585DB4D78930CD0063647F2AE |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1928 |  | 2013-08-16 | 2013-08-16 12:30 | 2013-08-16 12:32 | AMERICAN STANDARD - YCC030F1MOBC | 69 | 9.9 | Yes | Yes | 20.1 | 20.4 | -0.3 | 063511ACDF4F4DF983782B01611E103F |  | R22 | Non-TXV |  | 14.35% | 0.85652 | 27.57% | [5 empty] | Non-TXV | 14.35%
Grass Valley | CA | 95949-9159 |  | 2013-09-05 | 2013-09-05 12:12 | 2013-09-05 12:29 | COLEMAN - 2430-901 | 111 | 36.9 | Yes | Yes | 20.1 | 20.6 | -0.5 | 153C6CB40EB0400F81DBC7929A1A7A52 |  | R22 | Non-TXV |  | 33.24% | 0.66757 | 63.89% | [5 empty] | Non-TXV | 33.24%
Marysville | CA | 95901-6881 |  | 2013-08-20 | 2013-08-20 16:37 | 2013-08-20 16:53 | GIBSON - GS3BA-036KA | 69 | -5.8 | Yes | Yes | 13 | 16 | -3 | 9439E795317F4EA482BF3A76B800BB6B |  | R22 | TXV |  | -8.406% | 1.0841 | 2.354% |  |  |  |  | TXV |  |  | -8.406%
Corning | CA | 96021-2600 |  | 2013-07-22 | 2013-07-22 18:10 | 2013-07-22 18:26 | BRYANT - 56CJX030-C | 71 | 9.8 | Yes | Yes | 20.2 | 22.6 | -2.4 | 73CE9E146FE8415CB5B7F0C0CB4DAEBB |  | R22 | Non-TXV |  | 13.8% | 0.86197 | 26.53% | [5 empty] | Non-TXV | 13.8%
Fresno | CA | 93726-2616 |  | 2013-08-07 | 2013-08-07 15:23 | 2013-08-07 15:25 | OTHER - DCYZ-F036N070A | 64 | 2.6 | Yes | Yes | 24.1 | 18.5 | 5.6 | 26DDABA2353442F8B760370F0F961041 |  | R410A | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Chico | CA | 95926-1547 |  | 2013-07-30 | 2013-07-30 13:49 | 2013-07-30 14:23 | OTHER - NA | 70 | 11.7 | Yes | Yes | 17.6 | 20.4 | -2.8 | 368954736CCD4918BF66694EEAC513D6 |  | R22 | Non-TXV |  | 16.71% | 0.83286 | 32.12% | [5 empty] | Non-TXV | 16.71%
Fresno | CA | 93705-1117 |  | 2013-07-18 | 2013-07-18 13:31 | 2013-07-18 13:32 | WEATHER KING - WRKA-A030JK06E | 54 | 4 | Yes | Yes | 22 | 20.4 | 1.6 | 69B20782E2D94548802C7A1CF7DA450A |  | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
Riverbank | CA | 95367-2128 |  | 2013-07-22 | 2013-07-22 13:43 | 2013-07-22 14:24 | GOODMAN - GSC130421BB | 95 | 2.8 | Yes | Yes | 21.5 | 19.2 | 2.3 | 5678C6CC048941939820D273ADB20D7B |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Lathrop | CA | 95330-9752 |  | 2013-09-18 | 2013-09-18 11:06 | 2013-09-18 11:25 | RHEEM - UAKA037JAZ | 79 | 3.7 | Yes | Yes | 19.8 | 21.5 | -1.7 | 1CB34CB33A5E46D0B2D263B787F20D87 |  | R22 | Non-TXV |  | 4.684% | 0.95316 | 9.001% | [5 empty] | Non-TXV | 4.684%
San Joaquin | CA | 93660-0000 |  | 2013-08-15 | 2013-08-15 11:44 | 2013-08-15 12:05 | LENNOX - GCS29-030-75-2PA | 53 | -3.7 | Yes | Yes | 16.2 | 12.2 | 4 | 8FF6D505B22A4505988CBB7B07C49CD3 |  | R22 | Non-TXV |  | -6.981% | 1.0698 | 1.955% |  |  |  |  | Non-TXV |  |  | -6.981%
Los Banos | CA | 93635-9433 |  | 2013-08-05 | 2013-08-05 13:08 | 2013-08-05 13:12 | BRYANT - 561CJ060-A | 156 | 4.6 | Yes | Yes | 23.4 | 21.8 | 1.6 | 4D4BE8C193624DFBBDE323B39B4E2941 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Merced | CA | 95348-9204 |  | 2013-07-19 | 2013-07-19 15:42 | 2013-07-19 15:44 | RHEEM - HC-80-36-21C | 50 | 2.1 | Yes | Yes | 20.1 | 20.2 | -0.1 | 2E80DB992E714F87BCFF67ED78099BA5 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Stockton | CA | 95206-1814 |  | 2013-07-25 | 2013-07-25 11:42 | 2013-07-25 12:02 | DAY & NIGHT - UNK | 80 | -5.6 | Yes | Yes | 16.7 | 19.3 | -2.6 | 2954C7952C094029B796B248C424D11E |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Atwater | CA | 95301-9582 |  | 2013-08-14 | 2013-08-14 12:33 | 2013-08-14 12:50 | YORK - D2NY048N09006A | 148 | 12.7 | Yes | Yes | 22.3 | 20.2 | 2.1 | D782A8DFAD044B76819B96D200AC80CE |  | R410A | Non-TXV |  | 8.581% | 0.91419 | 16.49% | [5 empty] | Non-TXV | 8.581%
Sanger | CA | 93657-1922 |  | 2013-07-22 | 2013-07-22 09:35 | 2013-07-22 10:50 | OTHER - HC30A1VAR | 83 | 10.6 | Yes | Yes | 20.5 | 19.9 | 0.6 | B915D6F9F3C74D16ADF374B8535A88B1 |  | R22 | Non-TXV |  | 12.77% | 0.87229 | 24.54% | [5 empty] | Non-TXV | 12.77%
Los Banos | CA | 93635-5316 |  | 2013-08-01 | 2013-08-01 14:55 | 2013-08-01 14:57 | PAYNE - 7777UNK | 110 | 4 | Yes | Yes | 20.7 | 19.8 | 0.9 | 187C79B0E866493E9AB9E9C88F0F845E |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Sanger | CA | 93657-2571 |  | 2013-07-22 | 2013-07-22 16:29 | 2013-07-22 17:02 | PAYNE - N/A | 90 | 3 | Yes | Yes | 20.3 | 18 | 2.3 | C882FD1F3CC94EEF9CA7BBB12CA3014C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Los Banos | CA | 93635-6324 |  | 2013-07-24 | 2013-07-24 14:23 | 2013-07-24 14:25 | LENNOX - 12GCS048X-100-1PA | 167 | 5 | Yes | Yes | 29.3 | 23.5 | 5.8 | 1456DB155F1B45048985702AF8AF4B51 |  | R22 | Non-TXV |  | 2.994% | 0.97006 | 5.754% | [5 empty] | Non-TXV | 2.994%
Fresno | CA | 93705-0838 |  | 2013-08-02 | 2013-08-02 15:22 | 2013-08-02 15:46 | BDP - 585JJ030075 | 68 | 9 | Yes | Yes | 20 | 19.7 | 0.3 | 2C3B9F00075448F7AB571D37020496B5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.24% | 0.86765 | 25.44% | [5 empty] | Non-TXV | 13.24%
Merced | CA | 95341-5560 |  | 2013-08-05 | 2013-08-05 10:43 | 2013-08-05 11:10 | YORK - DCYZ-F036N070A | 64 | 2.2 | Yes | Yes | 24 | 19.8 | 4.2 | 49299159F1214C659EF094F29B7C3F60 |  | R410A | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Stockton | CA | 95209-2746 |  | 2013-07-22 | 2013-07-22 12:06 | 2013-07-22 12:23 | PAYNE - 585A024055YACR | 51 | -3.6 | Yes | Yes | 24.5 | 18.5 | 6 | BE70F58294314FB08EAA99903FA04E94 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93705-0430 |  | 2013-07-18 | 2013-07-18 12:36 | 2013-07-18 12:38 | PAYNE - 585HD036060 | 102 | 5.1 | Yes | Yes | 23.4 | 19.3 | 4.1 | CB6E15B9C92E4AFDA5E1687D8972374F |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Merced | CA | 95341-5400 |  | 2013-07-19 | 2013-07-19 16:23 | 2013-07-19 16:25 | CARRIER - 7777UNK | 100 | 5 | Yes | Yes | 17.5 | 19.3 | -1.8 | 689D92E28E3145A69D10D1C3398AE260 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93711-2802 |  | 2013-08-10 | 2013-08-10 12:26 | 2013-08-10 12:31 | GOODMAN - GSC130481BB | 102 | 4 | Yes | Yes | 18.7 | 18.7 | 0 | C038190FF6124B45BEDA6521DFE8DFC9 |  | R22 | TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | TXV | 3.922%
Stockton | CA | 95204-1233 |  | 2013-07-26 | 2013-07-26 08:47 | 2013-07-26 09:09 | UNITARY PRODUCTS GROUP - H2RD036S06B | 96 | 4.9 | Yes | Yes | 19.2 | 18.3 | 0.9 | 319C550181C44FE6895CFCD1A8C4430D |  | R22 | TXV |  | 5.104% | 0.94896 | 9.809% | [5 empty] | TXV | 5.104%
Stockton | CA | 95204-1233 |  | 2013-07-26 | 2013-07-26 09:15 | 2013-07-26 09:41 | ICP - N4A348AKB200 | 112 | -10.5 | Yes | Yes | 21.7 | 18.8 | 2.9 | AC6FCB530D4544998711ED3DDF72CD4B |  | R410A | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Tracy | CA | 95376-4324 |  | 2013-07-17 | 2013-07-17 11:57 | 2013-07-17 12:22 | GE - BTB930A100A0 | 53 | 3.6 | Yes | Yes | 17.6 | 19.5 | -1.9 | D0491BD315B44828959E28E9FEE228D8 |  | R22 | Non-TXV |  | 6.792% | 0.93208 | 13.05% | [5 empty] | Non-TXV | 6.792%
Stockton | CA | 95206-6258 |  | 2013-07-18 | 2013-07-18 12:21 | 2013-07-18 12:42 | PAYNE - PA13NR036-K | 83 | -8.3 | Yes | Yes | 22.9 | 18.6 | 4.3 | 830DD257A5744BF1B086E0571F6F5895 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Atwater | CA | 95301-3648 |  | 2013-08-27 | 2013-08-27 09:14 | 2013-08-27 09:50 | WHIRLPOOL - HWA36480K | 101 | 3.2 | Yes | Yes | 17.2 | 17.6 | -0.4 | 3F706F11DE9A4E7991914B887CE49E3D |  | R22 | Non-TXV |  | 3.168% | 0.96832 | 6.089% | [5 empty] | Non-TXV | 3.168%
Los Banos | CA | 93635-5424 |  | 2013-07-24 | 2013-07-24 14:55 | 2013-07-24 15:00 | BRYANT - 561CJ036=C | 76 | 2.7 | Yes | Yes | 18.9 | 21.5 | -2.6 | 87EC1476575E4C6F96E429958066848B |  | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Stockton | CA | 95209-4004 |  | 2013-07-18 | 2013-07-18 15:33 | 2013-07-18 15:56 | DAY & NIGHT - 567C042RCU | 74 | 9.7 | Yes | Yes | 21.1 | 17.2 | 3.9 | E134A2FEEA45480FB4671F0142B9F03C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.11% | 0.86892 | 25.19% | [5 empty] | Non-TXV | 13.11%
Clovis | CA | 93611-5206 |  | 2013-08-16 | 2013-08-16 12:12 | 2013-08-16 12:13 | CARRIER - 591ANX042000ABAA | 112 | 6.9 | Yes | Yes | 22 | 18.9 | 3.1 | 3538844BEFD94C5AB2F2A8F8DEF34C3E |  | R22 | Non-TXV |  | 6.161% | 0.93839 | 11.84% | [5 empty] | Non-TXV | 6.161%
Clovis | CA | 93611-5206 |  | 2013-08-16 | 2013-08-16 12:17 | 2013-08-16 12:42 | CARRIER - GCGD030S21SB | 85 | 17.7 | Yes | Yes | 19 | 18.7 | 0.3 | EF2348E26BA34AC7B4A6178047DA3D6B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 20.82% | 0.79176 | 40.02% | [5 empty] | Non-TXV | 20.82%
Paradise | CA | 95969-3110 |  | 2013-08-05 | 2013-08-05 08:44 | 2013-08-05 09:20 | YORK - D1NP036N05506 | 108 | 15.8 | Yes | Yes | 17 | 19.9 | -2.9 | A450B44F05EE4515B39043DE215F142E |  | R22 | Non-TXV |  | 14.63% | 0.8537 | 28.11% | [5 empty] | Non-TXV | 14.63%
Winton | CA | 95388-9385 |  | 2013-08-15 | 2013-08-15 15:44 | 2013-08-15 16:09 | RUUD - URKA-A030JK06E | 54 | 1.6 | Yes | Yes | 22.5 | 19.9 | 2.6 | A8EAFF1AFD924B5BA0AFB5A04FEBF069 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Sanger | CA | 93657-2740 |  | 2013-07-22 | 2013-07-22 14:23 | 2013-07-22 14:52 | YORK - D1NA036N05606C | 67 | 3.8 | Yes | Yes | 20.5 | 21.4 | -0.9 | FD44C98242E14F42B896C429CD44922C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.672% | 0.94328 | 10.9% | [5 empty] | Non-TXV | 5.672%
Coalinga | CA | 93210-1653 |  | 2013-08-17 | 2013-08-17 11:01 | 2013-08-17 11:01 | ICP - PGD330060K001C1 | 97 | 0 | Yes | Yes | 17.2 | 19 | -1.8 | BE1210F436C24851B20E20FCB0663163 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-1653 |  | 2013-08-17 | 2013-08-17 10:34 | 2013-08-17 10:58 | CARRIER - 48GS-030040301 | 55 | 2.4 | Yes | Yes | 20.1 | 21.5 | -1.4 | 528B8FE149E247B0B0403FAA02D2BE53 |  | R22 | Non-TXV |  | 4.364% | 0.95636 | 8.386% | [5 empty] | Non-TXV | 4.364%
Sanger | CA | 93657-9711 |  | 2013-07-23 | 2013-07-23 13:28 | 2013-07-23 13:38 | YORK - D1NP036N05605A | 108 | -10.2 | Yes | Yes | 16.5 | 18 | -1.5 | 853B73B635E94029BE0A7D8A6C4F8B35 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Sanger | CA | 93657-9711 |  | 2013-07-23 | 2013-07-23 13:40 | 2013-07-23 14:39 | YORK - D1NP048N06506A | 132 | 4.7 | Yes | Yes | 18.9 | 18.3 | 0.6 | BAFAF1E4374C4C2594A3EBAFC3638198 |  | R22 | Non-TXV |  | 3.561% | 0.96439 | 6.843% | [5 empty] | Non-TXV | 3.561%
Selma | CA | 93662-4803 |  | 2013-08-01 | 2013-08-01 10:33 | 2013-08-01 11:55 | ICP - PGAD30D1K3 | 78 | 8.2 | Yes | Yes | 21.2 | 20.4 | 0.8 | 69E4071869074E1C898E9CEE2318764A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.51% | 0.89487 | 20.2% | [5 empty] | Non-TXV | 10.51%
Lockeford | CA | 95237-9774 |  | 2013-08-20 | 2013-08-20 15:26 | 2013-08-20 15:46 | YORK - D1NA042N05606C | 76 | 2.4 | Yes | Yes | 25.6 | 21.3 | 4.3 | 031043B6E58040419012F4715135F9E7 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Selma | CA | 93662-2100 |  | 2013-07-31 | 2013-07-31 09:15 | 2013-07-31 09:49 | CARRIER - 48KLA136---321BE | 102 | 3.5 | Yes | Yes | 20 | 20.4 | -0.4 | 6E2C6CA607F74AF2A86E9ECA6C37989C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.431% | 0.96569 | 6.594% | [5 empty] | Non-TXV | 3.431%
Stockton | CA | 95205-4128 |  | 2013-07-18 | 2013-07-18 12:04 | 2013-07-18 12:27 | LUXAIRE - TCGD30S21S2HA | 55 | 3.6 | Yes | Yes | 19.4 | 19.3 | 0.1 | CF3D6D3610C843C28A4CF49A362EA5A0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | Non-TXV | 6.545%
Fresno | CA | 93705-4506 |  | 2013-07-19 | 2013-07-19 11:46 | 2013-07-19 11:48 | RUUD - 7777UNK | 100 | 4 | Yes | Yes | 22.5 | 20.5 | 2.1 | 783BF359DD674C589A8FB61AD9626D2C |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Atwater | CA | 95301-2746 |  | 2013-08-13 | 2013-08-13 10:49 | 2013-08-13 11:19 | RHEEM - RRNA-B030JK06X | 72 | 2.2 | Yes | Yes | 16.9 | 19.1 | -2.2 | FF66DE673D3B4BA886922ABE4CB986ED |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Fresno | CA | 93722-7336 |  | 2013-07-18 | 2013-07-18 11:04 | 2013-07-18 11:05 | GOODMAN - GPG12360701A | 85 | 10.4 | Yes | Yes | 27 | 21.5 | 5.5 | 281C4888956F4030B770D1D31E4E89BD |  | R22 | Non-TXV |  | 12.24% | 0.87765 | 23.51% | [5 empty] | Non-TXV | 12.24%
Stockton | CA | 95204-1833 |  | 2013-08-02 | 2013-08-02 13:12 | 2013-08-02 13:57 | RHEEM - RRKA-A036JK08X | 64 | 3.6 | Yes | Yes | 19.3 | 19.8 | -0.5 | CDC590476278487CB977CBE4A39BFDB9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Fresno | CA | 93705-2202 |  | 2013-08-12 | 2013-08-12 13:00 | 2013-08-12 13:01 | TRANE - YCC036F1MOBF | 83 | 4.4 | Yes | Yes | 23.1 | 21 | 2.1 | 5D2DDE39D5C14582999ED783D0BFFE1E |  | R22 | Non-TXV |  | 5.301% | 0.94699 | 10.19% | [5 empty] | Non-TXV | 5.301%
Los Banos | CA | 93635-2958 |  | 2013-07-24 | 2013-07-24 11:41 | 2013-07-24 11:47 | DAY & NIGHT - F91ANX042000ABAA | 112 | 3.9 | Yes | Yes | 19.6 | 20.1 | -0.5 | A6AF8003EFA0474BBDA14D2354E4FF23 |  | R22 | Non-TXV |  | 3.482% | 0.96518 | 6.692% | [5 empty] | Non-TXV | 3.482%
Stockton | CA | 95206-4816 |  | 2013-07-17 | 2013-07-17 14:43 | 2013-07-17 15:02 | BRYANT - 561CJ036-D | 82 | 5.8 | Yes | Yes | 20.1 | 21.7 | -1.6 | FACCEDA985E14880A8589C3069A2E939 |  | R22 | Non-TXV |  | 7.073% | 0.92927 | 13.59% | [5 empty] | Non-TXV | 7.073%
Madera | CA | 93638-2859 |  | 2013-07-28 | 2013-07-28 00:10 | 2013-07-28 00:43 | CARRIER - 48GX-30606301 | 83 | 2.7 | Yes | Yes | 20.8 | 22.1 | -1.3 | 4640FCA2666C41B5B81D72E30A935559 |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Selma | CA | 93662-4801 |  | 2013-08-09 | 2013-08-09 16:03 | 2013-08-09 16:44 | ICP - PGAD36D1K3 | 77 | 9.9 | Yes | Yes | 17.4 | 20.2 | -2.8 | 285648EB2A5345E6802EC99457ADB114 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Paradise | CA | 95969-2638 |  | 2013-08-26 | 2013-08-26 12:52 | 2013-08-26 18:41 | CARRIER - 3BCKC036350 | 70 | 2.6 | Yes | Yes | 16.3 | 19.3 | -3 | 0B193B248AAF4E488717C771064FF6C1 |  | R22 | TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | TXV | 3.714%
Fresno | CA | 93726-2621 |  | 2013-07-26 | 2013-07-26 12:43 | 2013-07-26 12:46 | PAYNE - UNK | 65 | 8.8 | Yes | Yes | 17.8 | 17.7 | 0.1 | 871AB9F1F39744C5B3765A021CA54CAF |  | R22 | Non-TXV |  | 13.54% | 0.86462 | 26.02% | [5 empty] | Non-TXV | 13.54%
Fresno | CA | 93726-2450 |  | 2013-08-14 | 2013-08-14 12:14 | 2013-08-14 12:31 | GOODMAN - PGJ036075-1 | 81 | 12.6 | Yes | Yes | 24.1 | 20.4 | 3.7 | A996BB64F2144FA2807A15A8641B8FA5 |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Sanger | CA | 93657-2212 |  | 2013-07-22 | 2013-07-22 17:59 | 2013-07-22 18:40 | RHEEM - N/A | 85 | 7.3 | Yes | Yes | 16.3 | 18.5 | -2.2 | D9EF46D81370423883AE8EF484A5466A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.588% | 0.91412 | 16.5% | [5 empty] | Non-TXV | 8.588%
Fresno | CA | 93705-4612 |  | 2013-07-19 | 2013-07-19 13:18 | 2013-07-19 13:19 | GOODMAN - PGB060125-1 | 82 | 3.2 | Yes | Yes | 18.2 | 19.3 | -1.1 | 553B88A198EF416D8365C798BD8BA62D |  | R22 | Non-TXV |  | 3.902% | 0.96098 | 7.5% | [5 empty] | Non-TXV | 3.902%
Fresno | CA | 93711-2660 |  | 2013-08-28 | 2013-08-28 10:20 | 2013-08-28 10:22 | RHEEM - UNK | 56 | 4.7 | Yes | Yes | 21.7 | 22.6 | -0.9 | 8224B3C11DF44130B26077F84DABD470 |  | R22 | Non-TXV |  | 8.393% | 0.91607 | 16.13% | [5 empty] | Non-TXV | 8.393%
Riverbank | CA | 95367-3835 |  | 2013-07-22 | 2013-07-22 09:33 | 2013-07-22 10:03 | RHEEM - RAHE-030JAS | 78 | 2.3 | Yes | Yes | 20.1 | 19.7 | 0.4 | D49CCFB1D6FA44C8B9E17D963F9C67C8 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Fresno | CA | 93726-4112 |  | 2013-07-29 | 2013-07-29 12:38 | 2013-07-29 12:39 | RHEEM - RRNAAB036JK08X | 83 | 9.6 | Yes | Yes | 21.9 | 18.2 | 3.7 | 51FC98155C524F46A08D0A90092231FA |  | R22 | Non-TXV |  | 11.57% | 0.88434 | 22.23% | [5 empty] | Non-TXV | 11.57%
Madera | CA | 93637-5017 |  | 2013-08-05 | 2013-08-05 11:04 | 2013-08-05 11:05 | CARRIER - 48ESN024040311 | 72 | 6.9 | Yes | Yes | 25.5 | 20.4 | 5.1 | A09284035F964DF6B083F83B5EFFA9DD |  | R410A | Non-TXV |  | 9.583% | 0.90417 | 18.42% | [5 empty] | Non-TXV | 9.583%
Madera | CA | 93637-4610 |  | 2013-07-23 | 2013-07-23 10:11 | 2013-07-23 10:11 | GOODMAN - GPG1336045M41DA | 85 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | EA09DE5E36844978AEA3EAD4A167EC09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2712 |  | 2013-08-23 | 2013-08-23 15:29 | 2013-08-23 15:31 | PAYNE - PA13NR024-H | 65 | 2.8 | Yes | Yes | 17.5 | 19.1 | -1.6 | B7A1F42CCE334FC084F0963840E9062C |  | R22 | Non-TXV |  | 4.308% | 0.95692 | 8.278% | [5 empty] | Non-TXV | 4.308%
Manteca | CA | 95336-3458 |  | 2013-07-18 | 2013-07-18 09:47 | 2013-07-18 10:07 | PAYNE - PA10JA036-C | 73 | 2.5 | Yes | Yes | 18.8 | 19.3 | -0.5 | 0016C3A1DAB8467C93715B39A3617DE1 |  | R22 | Non-TXV |  | 3.425% | 0.96575 | 6.581% | [5 empty] | Non-TXV | 3.425%
Placerville | CA | 95667-9420 |  | 2013-07-19 | 2013-07-19 14:25 | 2013-07-19 14:25 | LENNOX - UNK | 90 | 0 | Yes | Yes | 20 | 22.1 | -2.1 | B8C22E2369A442BEB42682E296502680 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1233 |  | 2013-07-19 | 2013-07-19 12:17 | 2013-07-19 12:19 | BRYANT - 582ANW030060AAAD | 55 | 3.4 | Yes | Yes | 24 | 22 | 2 | 5E16697F340F4D0BACE2B28EF662596A |  | R22 | Non-TXV |  | 6.182% | 0.93818 | 11.88% | [5 empty] | Non-TXV | 6.182%
Fresno | CA | 93726-1019 |  | 2013-08-13 | 2013-08-13 16:01 | 2013-08-13 16:32 | RUUD - UAKA-030JAZ | 76 | 14.6 | Yes | Yes | 18.3 | 17.6 | 0.7 | 75237481342948888DC1E70CD9455FC7 |  | R22 | Non-TXV |  | 19.21% | 0.80789 | 36.92% | [5 empty] | Non-TXV | 19.21%
Atwater | CA | 95301-9443 |  | 2013-08-14 | 2013-08-14 11:25 | 2013-08-14 11:43 | YORK - H10B042S06B | 89 | 2.7 | Yes | Yes | 18.6 | 19.8 | -1.2 | ED64B70C78AF437EBDA46655FF91CDAA |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Corning | CA | 96021-0000 |  | 2013-07-22 | 2013-07-22 08:44 | 2013-07-22 09:47 | YORK - H4RC060S06G | 143 | 15.1 | Yes | Yes | 18.1 | 20.4 | -2.3 | CA32A1C4F1094140AD6AD8BEF53E3C7C |  | R22 | Non-TXV |  | 10.56% | 0.89441 | 20.29% | [5 empty] | Non-TXV | 10.56%
Fresno | CA | 93722-2375 |  | 2013-07-19 | 2013-07-19 10:09 | 2013-07-19 10:10 | LENNOX - 12ACB364P | 106 | 12.7 | Yes | Yes | 18.4 | 21 | -2.6 | 1EB4960006464DB39F6DE6E3432D3BBA |  | R22 | Non-TXV |  | 11.98% | 0.88019 | 23.03% | [5 empty] | Non-TXV | 11.98%
Fresno | CA | 93703-1508 |  | 2013-08-13 | 2013-08-13 12:21 | 2013-08-13 12:22 | LENNOX - PGE12A42D1001PA | 133 | 17.4 | Yes | Yes | 25.8 | 21.4 | 4.4 | F02C6B3CB5A34DA8BE05AF1EB7CD58D4 |  | R22 | Non-TXV |  | 13.08% | 0.86917 | 25.14% | [5 empty] | Non-TXV | 13.08%
Fresno | CA | 93720-2028 |  | 2013-08-09 | 2013-08-09 10:58 | 2013-08-09 11:16 | YORK - H4DB030S06A | 71 | 6.7 | Yes | Yes | 17.2 | 19.2 | -2 | D5657B4727EA4F26B014816060A94BF4 |  | R22 | Non-TXV |  | 9.437% | 0.90563 | 18.14% | [5 empty] | Non-TXV | 9.437%
Stockton | CA | 95204-1313 |  | 2013-07-25 | 2013-07-25 09:36 | 2013-07-25 10:23 | GMC - VSC130241AA | 83 | 5 | Yes | Yes | 25.1 | 19.3 | 5.8 | FA0568086F724E068A6045CB2A8ECFD7 |  | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Riverbank | CA | 95367-9644 |  | 2013-07-25 | 2013-07-25 14:15 | 2013-07-25 15:13 | RHEEM - CBD | 85 | 2.6 | Yes | Yes | 26.2 | 20.2 | 6 | 0666579E1ED943AB81903324B45A0E69 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Sanger | CA | 93657-8635 |  | 2013-08-05 | 2013-08-05 13:34 | 2013-08-05 13:34 | GOODMAN - CLJ48-1C | 130 | 0 | Yes | Yes | 18.9 | 20.3 | -1.4 | FFD0F556EF02442F87C84A105B03C9C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3250 |  | 2013-08-08 | 2013-08-08 11:50 | 2013-08-08 11:51 | RHEEM - RRNAB060JK10X | 145 | 21.2 | Yes | Yes | 22.1 | 19.9 | 2.2 | C077109CED3E4588A206BF56E9188927 |  | R22 | Non-TXV |  | 14.62% | 0.85379 | 28.1% | [5 empty] | Non-TXV | 14.62%
Merced | CA | 95348-2717 |  | 2013-08-16 | 2013-08-16 15:18 | 2013-08-16 15:19 | GOODMAN - CK24-1B | 71 | 3.4 | Yes | Yes | 22.1 | 19.5 | 2.6 | E14D20C189DF4437A61D7EA7AD7FA127 |  | R22 | Non-TXV |  | 4.789% | 0.95211 | 9.203% | [5 empty] | Non-TXV | 4.789%
Red Bluff | CA | 96080-2130 |  | 2013-07-24 | 2013-07-24 14:45 | 2013-07-24 15:02 | DAY & NIGHT - 584ANW036100ACAG | 93 | 5 | Yes | Yes | 20.2 | 19.8 | 0.4 | 4905E5B70ACF4C8B950898ECE383DF85 |  | R22 | Non-TXV |  | 5.376% | 0.94624 | 10.33% | [5 empty] | Non-TXV | 5.376%
Marysville | CA | 95901-8257 |  | 2013-08-21 | 2013-08-21 11:33 | 2013-08-21 12:06 | CARRIER - 24ABA330A320 | 64 | 3.8 | Yes | Yes | 18 | 19.1 | -1.1 | ED4F55ECB91043AD9892D4F7DC3221C8 |  | R410A | TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | TXV | 5.938%
Paso Robles | CA | 93446-5013 |  | 2013-08-07 | 2013-08-07 16:48 | 2013-08-07 17:26 | CARRIER - 38EN024310SM | 56 | 3.4 | Yes | Yes | 24.3 | 20.2 | 4.1 | 9E9F93FFDCD242F2997DC736ED9A2B2B |  | R22 | Non-TXV |  | 6.071% | 0.93929 | 11.67% | [5 empty] | Non-TXV | 6.071%
Corning | CA | 96021-3423 |  | 2013-07-23 | 2013-07-23 09:28 | 2013-07-23 10:17 | BDP - GPG13300451BB | 77 | 4.7 | Yes | Yes | 15 | 17.9 | -2.9 | 3B78DD0E4C9E43AE8574EFC204FBD933 |  | R22 | Non-TXV |  | 6.104% | 0.93896 | 11.73% | [5 empty] | Non-TXV | 6.104%
Stockton | CA | 95209-1554 |  | 2013-08-21 | 2013-08-21 12:06 | 2013-08-21 12:25 | BDP - 585FJM030050ABAF | 58 | 6.9 | Yes | Yes | 20.2 | 19.5 | 0.7 | 48459FA8752240569381151C331F5FEB |  | R22 | Non-TXV |  | 11.9% | 0.88103 | 22.86% | [5 empty] | Non-TXV | 11.9%
Paso Robles | CA | 93446-5014 |  | 2013-08-07 | 2013-08-07 14:23 | 2013-08-07 14:43 | CARRIER - 38EN024310SM | 56 | 2.5 | Yes | Yes | 20.8 | 19.4 | 1.4 | 292C2DF9DA394217984961A0ED2F8093 |  | R22 | Non-TXV |  | 4.464% | 0.95536 | 8.579% | [5 empty] | Non-TXV | 4.464%
Mariposa | CA | 95338-9765 |  | 2013-08-02 | 2013-08-02 12:57 | 2013-08-02 12:59 | RHEEM - RQMA-A036JK 000 | 106 | 3.6 | Yes | Yes | 25.8 | 23.2 | 2.6 | 9C4D45444BBF4096B256764947F09785 |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Riverbank | CA | 95367-2764 |  | 2013-10-04 | 2013-10-04 15:02 | 2013-10-04 15:31 | BRYANT - 563CN042-E | 104 | 5.1 | Yes | Yes | 23.6 | 21 | 2.6 | 50676D6FD4B2443B926792291748BBF1 |  | R22 | TXV |  | 4.904% | 0.95096 | 9.424% | [5 empty] | TXV | 4.904%
Rocklin | CA | 95677-4749 |  | 2013-08-10 | 2013-08-10 11:33 | 2013-08-10 11:56 | GOODMAN - CH48-1EC | 86 | -3.1 | Yes | Yes | 20 | 20.4 | -0.4 | F9E5D167A65A42D89025A80D19F246F7 |  | R22 | TXV |  | -3.605% | 1.036 | 1.009% |  |  |  |  | TXV |  |  | -3.605%
Madera | CA | 93637-5013 |  | 2013-08-02 | 2013-08-02 02:19 | 2013-08-02 03:12 | YORK - D1NA02403660C | 57 | 5.3 | Yes | Yes | 17.9 | 20.4 | -2.5 | 8EDE9ADE6D3D4DC09F0038BE4B607B84 |  | R22 | Non-TXV |  | 9.298% | 0.90702 | 17.87% | [5 empty] | Non-TXV | 9.298%
Stockton | CA | 95207-3120 |  | 2013-11-06 | 2013-11-06 10:41 | 2013-11-06 10:57 | YORK - D3NZ036N05606NXA | 64 | 7.5 | Yes | Yes | 22.7 | 19.7 | 3 | D5DB691D385F4C7BB0EAECA6DE228824 |  | R410A | TXV |  | 11.72% | 0.88281 | 22.52% | [5 empty] | TXV | 11.72%
Fresno | CA | 93705-0312 |  | 2013-07-18 | 2013-07-18 13:03 | 2013-07-18 13:07 | GOODMAN - CK36-1B | 76 | 2.4 | Yes | Yes | 22.2 | 20.4 | 1.8 | 429CCE579C7F4FF58D21B9FC428D55DA |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Atwater | CA | 95301-4572 |  | 2013-07-19 | 2013-07-19 16:58 | 2013-07-19 16:59 | BDP - 588ANW024040ABAD | 39 | 12.1 | Yes | Yes | 22.1 | 21.2 | 0.9 | 63ED686546B348C08E67EAC3F6118449 |  | R22 | Non-TXV |  | 31.03% | 0.68974 | 59.62% | [5 empty] | Non-TXV | 31.03%
Paso Robles | CA | 93446-5041 |  | 2013-10-07 | 2013-10-07 14:08 | 2013-10-07 14:25 | CARRIER - 38EN024310SM | 61 | 2 | Yes | Yes | 17.9 | 19.8 | -1.9 | C78F36F698104F718253E2856E2F82A1 |  | R22 | Non-TXV |  | 3.279% | 0.96721 | 6.301% | [5 empty] | Non-TXV | 3.279%
Yuba City | CA | 95991-1213 |  | 2013-07-22 | 2013-07-22 12:12 | 2013-07-22 12:39 | OTHER - FS4BE-036K | 136 | 11.4 | Yes | Yes | 23 | 20.4 | 2.6 | CD2842EACD6F462889178A366BB4701D |  | R410A | TXV |  | 8.382% | 0.91618 | 16.11% | [5 empty] | TXV | 8.382%
Yuba City | CA | 95991-1926 |  | 2013-08-30 | 2013-08-30 08:43 | 2013-08-30 09:01 | RHEEM - RSKA-037AZ | 79 | 4.8 | Yes | Yes | 20.4 | 18.7 | 1.7 | 957DAB7EE6AD46C48B8B7A2956F82513 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.076% | 0.93924 | 11.68% | [5 empty] | Non-TXV | 6.076%
Merced | CA | 95340-2948 |  | 2013-08-06 | 2013-08-06 14:48 | 2013-08-06 15:13 | RHEEM - RAHE-030JAS | 78 | 14.1 | Yes | Yes | 17.8 | 19.6 | -1.8 | 0AF51EF45EF74290979EEE1A46AA6C5F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.08% | 0.81923 | 34.74% | [5 empty] | Non-TXV | 18.08%
Paso Robles | CA | 93446-5034 |  | 2013-08-08 | 2013-08-08 12:46 | 2013-08-08 13:11 | CARRIER - 38EN024310SM | 56 | 1.7 | Yes | Yes | 19.4 | 18.2 | 1.2 | 075FB02254CD46429C7F2D783F5E4D5A |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Merced | CA | 95348-2729 |  | 2013-07-24 | 2013-07-24 09:10 | 2013-07-24 09:24 | RHEEM - RAFD025JAS | 51 | 6.6 | Yes | Yes | 23.8 | 18.8 | 5 | C21F1CD5DA77477DADBA37CDD4D2F9C5 |  | R22 | Non-TXV |  | 12.94% | 0.87059 | 24.87% | [5 empty] | Non-TXV | 12.94%
Paso Robles | CA | 93446-5006 |  | 2013-08-07 | 2013-08-07 10:48 | 2013-08-07 11:14 | CARRIER - 38EN024310 | 56 | -5.3 | Yes | Yes | 18 | 19 | -1 | 21649D83ECCF47A19F8592D6EDBED8AD |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
Merced | CA | 95348-2712 |  | 2013-08-20 | 2013-08-20 13:20 | 2013-08-20 13:23 | CARRIER - 38CK0244340 | 61 | 2.2 | Yes | Yes | 17.3 | 19.5 | -2.2 | 5F385594458A48688B8B4CF2D0CCA4B5 |  | R22 | Non-TXV |  | 3.607% | 0.96393 | 6.931% | [5 empty] | Non-TXV | 3.607%
Fresno | CA | 93727-2520 |  | 2013-08-12 | 2013-08-12 13:00 | 2013-08-12 13:23 | RHEEM - N/A | 150 | 5.7 | Yes | Yes | 20 | 19.3 | 0.8 | 98697BE7CBE446C59D5DD3E3DCBF453A |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Ione | CA | 95640-9523 |  | 2013-08-01 | 2013-08-01 14:31 | 2013-08-01 14:54 | OTHER - UNK | 85 | 13 | Yes | Yes | 15.2 | 17.7 | -2.5 | 5BA49CF066564428A3E4E651904E8277 |  | R22 | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
Placerville | CA | 95667-8815 |  | 2013-09-06 | 2013-09-06 17:02 | 2013-09-09 07:30 | GOODMAN - GPG13480901AC | 145 | -6.3 | Yes | Yes | 25.4 | 21.3 | 4.1 | 9225E4636AD24209BF8E54CF215621C7 |  | R22 | TXV |  | -4.345% | 1.0434 | 1.217% |  |  |  |  | TXV |  |  | -4.345%
Paradise | CA | 95969-5440 |  | 2013-10-18 | 2013-10-18 14:13 | 2013-10-18 14:36 | YORK - H4DH048S06A | 138 | 5.6 | Yes | Yes | 17.1 | 19.9 | -2.8 | 78A0FC0C19E64A02A91EC936483EC456 |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Paso Robles | CA | 93446-5930 |  | 2013-08-09 | 2013-08-09 09:52 | 2013-08-09 10:15 | COLEMAN - 9548A801 | 120 | 8.8 | Yes | Yes | 20.9 | 17.7 | 3.2 | D5876CA556F348999A4535ED07E7A1A0 |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Mariposa | CA | 95338-9522 |  | 2013-08-21 | 2013-08-21 14:07 | 2013-08-21 14:08 | GOODMAN - CLJ361C | 109 | 11.6 | Yes | Yes | 28.4 | 22.8 | 5.6 | E3CC3B1272DD48E2AAFE9F174D9930CE |  | R22 | Non-TXV |  | 10.64% | 0.89358 | 20.45% | [5 empty] | Non-TXV | 10.64%
Stockton | CA | 95205-4139 |  | 2013-07-17 | 2013-07-17 14:53 | 2013-07-17 15:13 | GOODMAN - GPG13240701CB | 74 | 2.8 | Yes | Yes | 20.1 | 18.5 | 1.6 | CF9742E1C5254F3898A8B32AEE13B88B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | Non-TXV | 3.784%
Stockton | CA | 95219-3590 |  | 2013-07-26 | 2013-07-26 13:04 | 2013-07-26 13:04 | CARRIER - 38EN018300 | 54 | 0 | Yes | Yes | 16 | 18.5 | -2.5 | 10B94FE352524A85B728E40C4E254D8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-0000 |  | 2013-07-17 | 2013-07-17 16:08 | 2013-07-17 16:30 | LENNOX - 10ACC-042-230-04 | 81 | 3 | Yes | Yes | 21 | 19.3 | 1.7 | 7B3660592C97478EBFF76C560D8227EE |  | R22 | TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | TXV | 3.704%
Chico | CA | 95973-8946 |  | 2013-09-04 | 2013-09-04 16:02 | 2013-09-04 16:02 | BRYANT - 116BNA042-A | 134 | 0 | Yes | Yes | 16.9 | 18.8 | -1.9 | 41E9B5218FB045A9A3B2836D8C77257B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-8946 |  | 2013-09-04 | 2013-09-04 19:05 | 2013-09-04 19:27 | DAY & NIGHT - NA | 77 | 6.2 | Yes | Yes | 21.3 | 18 | 3.3 | 23C24183632F4094BC875560A9CD0ED3 |  | R22 | Non-TXV |  | 8.052% | 0.91948 | 15.47% | [5 empty] | Non-TXV | 8.052%
Fowler | CA | 93625-2806 |  | 2013-09-27 | 2013-09-27 15:24 | 2013-09-27 17:35 | BDP - 588ANW042060 | 82 | 3.3 | Yes | Yes | 25.5 | 20.7 | 4.8 | 2380FA2E5723448D9D8EACD0D963CF4E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.024% | 0.95976 | 7.734% | [5 empty] | Non-TXV | 4.024%
Paso Robles | CA | 93446-3413 |  | 2013-08-07 | 2013-08-07 15:25 | 2013-08-07 15:52 | WHIRLPOOL - UNK | 99 | 3.5 | Yes | Yes | 20.5 | 20.2 | 0.4 | 7C783B213B8D4D5DA296A461893B3A49 |  | R22 | Non-TXV |  | 3.535% | 0.96465 | 6.794% | [5 empty] | Non-TXV | 3.535%
Manteca | CA | 95337-6881 |  | 2013-08-26 | 2013-08-26 09:14 | 2013-08-26 09:34 | BDP - 563CN036-B | 113 | 4 | Yes | Yes | 24 | 19 | 5 | 294E01AC189142F39E454BCC40BAFBB2 |  | R22 | Non-TXV |  | 3.54% | 0.9646 | 6.803% | [5 empty] | Non-TXV | 3.54%
Fowler | CA | 93625-2424 |  | 2013-08-20 | 2013-08-20 12:06 | 2013-08-20 12:06 | GOODMAN - PGJ048075-1 | 83 | 0 | Yes | Yes | 16.4 | 19.4 | -3 | 25B808AF2F1B4D9389FD865873E7EE0E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-4210 |  | 2013-09-27 | 2013-09-27 13:27 | 2013-09-27 14:00 | PAYNE - PH10JA024-C | 70 | -6.6 | Yes | Yes | 20 | 19.3 | 0.7 | A92A1B76BA314ECB89248B50EE93797C |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Los Banos | CA | 93635-8509 |  | 2013-07-30 | 2013-07-30 10:30 | 2013-07-30 10:44 | GOODMAN - GSC130361GA | 77 | 9.9 | Yes | Yes | 15.4 | 18.4 | -3 | 8AFB91D56A9441AF906360122D2C512E |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Stockton | CA | 95212-3212 |  | 2013-07-22 | 2013-07-22 14:01 | 2013-07-22 14:01 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 20.7 | 20.8 | -0.1 | 9A2D5F9C8B484836BE5C1529A148F5F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arbuckle | CA | 95912-9806 |  | 2013-08-08 | 2013-08-08 10:56 | 2013-08-08 10:56 | GOODMAN - GSC13060 | 169 | 0 | Yes | Yes | 24 | 19.3 | 4.7 | 0050509783204DF39D13EF4A153F6753 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-7444 |  | 2013-08-13 | 2013-08-13 09:03 | 2013-08-13 09:24 | CARRIER - 48SX-048100341AA | 88 | 15.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | 58617BD675454B3DBA5F7097E06C545D |  | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Los Banos | CA | 93635-6502 |  | 2013-07-29 | 2013-07-29 14:16 | 2013-07-29 14:21 | YORK - JS3BC-030KA | 68 | 3.4 | Yes | Yes | 18.9 | 18.5 | 0.4 | 941D44C594D141458E269F4717404489 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95215-4823 |  | 2013-08-13 | 2013-08-13 13:17 | 2013-08-13 13:34 | COLEMAN - BRCQ481BB | 87 | 5.1 | Yes | Yes | 29.6 | 24.2 | 5.4 | 79661006C6F94F3EA9149B158AE4C931 |  | R22 | Non-TXV |  | 5.862% | 0.94138 | 11.27% | [5 empty] | Non-TXV | 5.862%
Meadow Vista | CA | 95722-9400 |  | 2013-08-14 | 2013-08-14 09:24 | 2013-08-14 09:54 | BRYANT - 574ANW048090NA | 193 | 8.9 | Yes | Yes | 16 | 18.7 | -2.7 | B231C4AE0F4D48F6BA285D46B023803E |  | R22 | TXV |  | 4.611% | 0.95389 | 8.862% | [5 empty] | TXV | 4.611%
Merced | CA | 95348-3409 |  | 2013-07-24 | 2013-07-24 11:00 | 2013-07-24 11:02 | AMERICAN STANDARD - YCC024F1LOBE | 64 | 9.3 | Yes | Yes | 19.4 | 18.7 | 0.7 | 0C5A664D75BA4CD8A5CDEFEFDFD3EEC1 |  | R22 | Non-TXV |  | 14.53% | 0.85469 | 27.93% | [5 empty] | Non-TXV | 14.53%
Fresno | CA | 93705-1107 |  | 2013-08-12 | 2013-08-12 14:54 | 2013-08-12 14:56 | YORK - D1GH036N06406A | 112 | 5.1 | Yes | Yes | 23.5 | 20.6 | 2.9 | 2120817A89764392AC7265B3F0213940 |  | R22 | Non-TXV |  | 4.554% | 0.95446 | 8.751% | [5 empty] | Non-TXV | 4.554%
Lincoln | CA | 95648-2903 |  | 2013-08-17 | 2013-08-17 11:37 | 2013-08-17 11:58 | YORK - H3RA060S06A | 106 | 10.8 | Yes | Yes | 23.7 | 21 | 2.8 | 7FFA2F031DC14EBA81FDF2C9D499EAAC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.19% | 0.89811 | 19.58% | [5 empty] | Non-TXV | 10.19%
Stockton | CA | 95204-3321 |  | 2013-08-09 | 2013-08-09 15:40 | 2013-08-09 15:59 | RHEEM - RRNA-B036JK06X | 84 | 4.7 | Yes | Yes | 23.7 | 19.6 | 4.1 | 09198BB4E14A4F21A43476BD794C746F |  | R22 | Non-TXV |  | 5.595% | 0.94405 | 10.75% | [5 empty] | Non-TXV | 5.595%
Chico | CA | 95928-6451 |  | 2013-08-06 | 2013-08-06 12:16 | 2013-08-06 12:51 | TRANE - 2TTB00030A1000AA | 64 | 9.8 | Yes | Yes | 20.3 | 22.1 | -1.8 | CF026EB405E2432BBAA99E4FAA0D4230 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.31% | 0.84688 | 29.43% | [5 empty] | Non-TXV | 15.31%
Marysville | CA | 95901-8254 |  | 2013-08-08 | 2013-08-08 15:31 | 2013-08-08 15:55 | UNK - UNK | 85 | 17.2 | Yes | Yes | 17 | 19.3 | -2.3 | 3D9A2FE45556465D9A94B892809CCAA0 |  |  |  |  | 20.24% | 0.79765 | 38.89% | [5 empty] | 0 | 20.24%
Stockton | CA | 95219-5408 |  | 2013-07-26 | 2013-07-26 09:38 | 2013-07-26 09:56 | CARRIER - 38EN018310 | 55 | 2 | Yes | Yes | 19.2 | 18.9 | 0.3 | 7463449B50594366A9B214D645D42062 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Manteca | CA | 95337-8584 |  | 2013-07-30 | 2013-07-30 15:23 | 2013-07-30 15:40 | BRYANT - 563CN036-D | 101 | 5.8 | Yes | Yes | 17.3 | 19.5 | -2.2 | F614E0B4BCC949C4A019960DD9D20A1B |  | R22 | TXV |  | 5.743% | 0.94257 | 11.04% | [5 empty] | TXV | 5.743%
Merced | CA | 95348-9369 |  | 2013-07-24 | 2013-07-24 09:53 | 2013-07-24 09:54 | OTHER - 80WE30G1NA | 86 | 10.6 | Yes | Yes | 20.7 | 19.4 | 1.3 | A78EF2B14C2740F2A53CE8D751EE1609 |  | R22 | Non-TXV |  | 12.33% | 0.87674 | 23.69% | [5 empty] | Non-TXV | 12.33%
Riverbank | CA | 95367-9652 |  | 2013-07-22 | 2013-07-22 16:30 | 2013-07-22 17:00 | RUUD - UAKA-030JAZ | 65 | 2 | Yes | Yes | 20 | 18.9 | 1.1 | 9E1AA5E9AAEC42C98E564FE712B55836 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Riverbank | CA | 95367-2789 |  | 2013-07-22 | 2013-07-22 15:14 | 2013-07-22 15:41 | TRANE - TTR030C100A1 | 74 | 4.9 | Yes | Yes | 19.8 | 19.7 | 0.1 | 106D8F623ECF4129912707583A30CE2E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.622% | 0.93378 | 12.73% | [5 empty] | Non-TXV | 6.622%
Murphys | CA | 95247-0000 |  | 2013-08-22 | 2013-08-22 12:11 | 2013-08-22 12:34 | AMERICAN STANDARD - 247A10600A1000AA | 85 | 2.8 | Yes | Yes | 22.3 | 16.4 | 5.9 | 42BE7BCB1A2341229A8607B9EB406460 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Atascadero | CA | 93422-4070 |  | 2013-08-09 | 2013-08-09 08:20 | 2013-08-09 08:37 | ICP - CA5536VKD2 | 82 | -5.8 | Yes | Yes | 25.1 | 19.1 | 6 | B2F53B39890149B2944E28B3C593CAA0 |  | R22 | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Auburn | CA | 95603-3615 |  | 2013-08-13 | 2013-08-13 14:56 | 2013-08-13 15:25 | OTHER - AC024GA | 73 | 6.9 | Yes | Yes | 21.1 | 21 | 0.1 | 45BDD5217C0847D08EE63DE7A01AC692 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 9.452% | 0.90548 | 18.16% | [5 empty] | TXV | 9.452%
Auburn | CA | 95603-3615 |  | 2013-08-13 | 2013-08-13 15:35 | 2013-08-13 15:56 | PAYNE - PH10JA018-E | 66 | 5 | Yes | Yes | 22.1 | 22.5 | -0.4 | ABAFDAEB98304723ACE0DFF4A506F0AD |  | R22 | TXV |  | 7.576% | 0.92424 | 14.56% | [5 empty] | TXV | 7.576%
Lincoln | CA | 95648-3011 |  | 2013-08-17 | 2013-08-17 10:45 | 2013-08-17 10:45 | GOODMAN - CK30-1D | 70 | 0 | Yes | Yes | 16.9 | 18.6 | -1.7 | C9299A43E41D4D55BD35BE5CCEEF7CA3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3844 |  | 2013-08-21 | 2013-08-21 09:21 | 2013-08-21 09:40 | OTHER - 3A-100-CH-1-2 | 81 | 2.8 | Yes | Yes | 21 | 20.4 | 0.6 | B935130F31F44193A72CBA49C87BD510 |  | R22 | Non-TXV |  | 3.457% | 0.96543 | 6.643% | [5 empty] | Non-TXV | 3.457%
Stockton | CA | 95206-5903 |  | 2013-07-25 | 2013-07-25 10:40 | 2013-07-25 10:40 | YORK - H2RA036S06E | 63 | 0 | Yes | Yes | 19.4 | 19.9 | -0.5 | 5CE66586C6B64899ACB41DBC4D0A78B9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5398 |  | 2013-08-05 | 2013-08-05 13:40 | 2013-08-05 13:41 | LENNOX - PGE10A30D0751PA | 64 | 11.7 | Yes | Yes | 22.5 | 21.3 | 1.2 | DD31B422EFB0401BB269708F6BC58D47 |  | R22 | Non-TXV |  | 18.28% | 0.81719 | 35.13% | [5 empty] | Non-TXV | 18.28%
Stockton | CA | 95209-4261 |  | 2013-07-18 | 2013-07-18 14:36 | 2013-07-18 14:54 | YORK - H2RC036S06HG | 83 | 7.5 | Yes | Yes | 21.2 | 20.3 | 1 | FCD2198E200241F78EE1CA50FF233A83 |  | R22 | Non-TXV |  | 9.036% | 0.90964 | 17.37% | [5 empty] | Non-TXV | 9.036%
San Miguel | CA | 93451-0000 |  | 2013-08-16 | 2013-08-16 13:19 | 2013-08-17 21:48 | DUCANE - AC10B36-B | 96 | 8.8 | Yes | Yes | 19.2 | 19.2 | 0 | 85FA0A5B0E6B429DBFFD05CDDB3928ED |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Nevada City | CA | 95959-9009 |  | 2013-08-07 | 2013-08-07 12:11 | 2013-08-07 12:11 | COLEMAN - UNK | 78 | 0 | Yes | Yes | 21.8 | 18 | 3.8 | 09ACF3DBF12B4E5F9659C4714110FD45 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4516 |  | 2013-07-26 | 2013-07-26 16:03 | 2013-07-26 16:39 | UNITARY PRODUCTS GROUP - H2RD024S06B | 88 | 11.8 | Yes | Yes | 23.3 | 18.3 | 5 | 4333EF24E0CD434F954938C5301CDA16 |  | R22 | Non-TXV |  | 13.41% | 0.86591 | 25.77% | [5 empty] | Non-TXV | 13.41%
Chico | CA | 95928-5753 |  | 2013-08-06 | 2013-08-06 09:25 | 2013-08-06 10:01 | LENNOX - 10GCS024X-50-5PA | 52 | 4.1 | Yes | Yes | 18.3 | 20.2 | -1.9 | 903E7F9D6C42431493177CDF69F72A6F |  | R22 | Non-TXV |  | 7.885% | 0.92115 | 15.15% | [5 empty] | Non-TXV | 7.885%
Stockton | CA | 95212-3049 |  | 2013-07-22 | 2013-07-22 09:24 | 2013-07-22 09:50 | YORK - H2RC048S06HG | 119 | 5 | Yes | Yes | 17.3 | 19.7 | -2.4 | 2CE948BA918A46E1A2ED848FE76020D8 |  | R22 | Non-TXV |  | 4.202% | 0.95798 | 8.075% | [5 empty] | Non-TXV | 4.202%
Stockton | CA | 95209-2166 |  | 2013-07-22 | 2013-07-22 08:29 | 2013-07-22 08:47 | BDP - 569BJ036 | 93 | -5.5 | Yes | Yes | 23.6 | 18.1 | 5.5 | F7B4CF0FD0BD4782A375C27A7F90FD36 |  | R22 | Non-TXV |  | -5.914% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.914%
Fowler | CA | 93625-2639 |  | 2013-10-03 | 2013-10-03 12:59 | 2013-10-03 14:11 | CARRIER - 48NLT030300 | 69 | 3.5 | Yes | Yes | 24.5 | 20.7 | 3.8 | 3462D154049F4FD49A3E4D7E590CCC4C |  | R22 | Non-TXV |  | 5.072% | 0.94928 | 9.748% | [5 empty] | Non-TXV | 5.072%
Fresno | CA | 93705-2226 |  | 2013-07-19 | 2013-07-19 10:24 | 2013-07-19 10:26 | GOODMAN - PGB042075-1 | 68 | 2.8 | Yes | Yes | 19.4 | 21.3 | -1.9 | 828384B680594032AFD9AF77F0EE9D3D |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Magalia | CA | 95954-9422 |  | 2013-08-30 | 2013-08-30 09:42 | 2013-08-30 10:11 | INTERTHERM - CN42179A6C 0 | 70 | 4.9 | Yes | Yes | 22.5 | 20 | 2.6 | 4EBAB62114A4435C85BD2196969FB831 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Manteca | CA | 95336-4934 |  | 2013-07-18 | 2013-07-18 16:45 | 2013-07-18 17:10 | CARRIER - CBD | 64 | 15.1 | Yes | Yes | 17.1 | 19.6 | -2.5 | ED91F596FFBE4851AAF6D5F1BA400803 |  | R22 | Non-TXV |  | 23.59% | 0.76406 | 45.34% | [5 empty] | Non-TXV | 23.59%
Oroville | CA | 95966-3943 |  | 2013-08-28 | 2013-08-28 14:21 | 2013-08-28 20:57 | YORK - E2RC048S06A | 217 | 6.5 | Yes | Yes | 16.6 | 18.5 | -1.9 | 346A7000EDF24A2D9CFDFB994096830E |  | R22 | Non-TXV |  | 2.995% | 0.97005 | 5.756% | [5 empty] | Non-TXV | 2.995%
Stockton | CA | 95219-5408 |  | 2013-07-26 | 2013-07-26 09:08 | 2013-07-26 09:26 | CARRIER - 38EN018310 | 55 | 10 | Yes | Yes | 17.9 | 19.9 | -2 | 05C5C6AE6F7D4861B858D4228755E8FC |  | R22 | Non-TXV |  | 18.18% | 0.81818 | 34.94% | [5 empty] | Non-TXV | 18.18%
Fresno | CA | 93705-1105 |  | 2013-08-29 | 2013-08-29 12:30 | 2013-08-29 12:31 | OTHER - URMAA030JK0E | 80 | 13 | Yes | Yes | 21.8 | 19.8 | 2 | D4835FEE47604899A8EE0B4BD64EF1AE |  | R22 | Non-TXV |  | 16.25% | 0.8375 | 31.23% | [5 empty] | Non-TXV | 16.25%
Stockton | CA | 95210-3642 |  | 2013-08-28 | 2013-08-28 09:06 | 2013-08-28 09:24 | RHEEM - RACC030JAS | 58 | -5.5 | Yes | Yes | 20.5 | 18.2 | 2.3 | B08482F5ABE64BA19667834BDA6606BF |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Grass Valley | CA | 95949-8153 |  | 2013-09-30 | 2013-09-30 13:47 | 2013-09-30 14:06 | LENNOX - HS18-411-6P | 94 | 23.3 | Yes | Yes | 21.5 | 19.1 | 2.4 | E8BCCFA24E6044DFB9F1A0789D350761 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 24.79% | 0.75213 | 47.64% | [5 empty] | Non-TXV | 24.79%
Paso Robles | CA | 93446-5016 |  | 2013-08-08 | 2013-08-08 10:55 | 2013-08-08 11:16 | CARRIER - 38EN024310SM | 56 | 4.5 | Yes | Yes | 18.5 | 19 | -0.5 | C0C4D9FCF7144596B077C21E11899175 |  | R22 | Non-TXV |  | 8.036% | 0.91964 | 15.44% | [5 empty] | Non-TXV | 8.036%
Fresno | CA | 93704-1530 |  | 2013-08-12 | 2013-08-12 15:36 | 2013-08-12 15:37 | AMANA - PGD30C0702E | 74 | 12.3 | Yes | Yes | 27.8 | 23.6 | 4.2 | CBD84BED2EA74A04B8A90ECF15051F2B |  | R22 | Non-TXV |  | 16.62% | 0.83378 | 31.94% | [5 empty] | Non-TXV | 16.62%
Plumas Lake | CA | 95961-9101 |  | 2013-10-16 | 2013-10-16 11:45 | 2013-10-16 12:01 | CARRIER - UNK | 53 | 7.5 | Yes | Yes | 21 | 18.7 | 2.3 | 5829A8F68499420695961B892C653740 |  | R22 | Non-TXV |  | 14.15% | 0.85849 | 27.2% | [5 empty] | Non-TXV | 14.15%
Paso Robles | CA | 93446-5016 |  | 2013-08-08 | 2013-08-08 11:49 | 2013-08-08 12:12 | CARRIER - 38EN024310SM | 56 | 6.6 | Yes | Yes | 19.4 | 21.1 | -1.7 | 632F1EB8A19A4885B780E0B8FDBB8F62 |  | R22 | Non-TXV |  | 11.79% | 0.88214 | 22.65% | [5 empty] | Non-TXV | 11.79%
Fresno | CA | 93705-1331 |  | 2013-08-12 | 2013-08-12 14:24 | 2013-08-12 14:26 | LENNOX - 12GCS048-100-5PB | 167 | 5.3 | Yes | Yes | 24.7 | 20.7 | 4 | 3A48D83A91014620BBCB1E349CE5F43A |  | R22 | Non-TXV |  | 3.174% | 0.96826 | 6.099% | [5 empty] | Non-TXV | 3.174%
Atwater | CA | 95301-4818 |  | 2013-07-19 | 2013-07-19 17:34 | 2013-07-19 17:35 | WEATHER KING - 13AJA36A01 | 108 | 14.4 | Yes | Yes | 22.1 | 21.4 | 0.7 | 189118D307AD4648B043188A26CBEFBA |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Fresno | CA | 93722-6340 |  | 2013-07-17 | 2013-07-17 12:59 | 2013-07-17 13:01 | CARRIER - 591ANX042000ADAA | 87 | 14.4 | Yes | Yes | 22.5 | 23.7 | -1.2 | 2E299015BE724E7CB9F3168752C788FB |  | R22 | Non-TXV |  | 16.55% | 0.83448 | 31.81% | [5 empty] | Non-TXV | 16.55%
Fresno | CA | 93722-2584 |  | 2013-10-26 | 2013-10-26 14:54 | 2013-10-26 15:25 | LENNOX - 13ACC-048-230-01 | 158 | 15.2 | Yes | Yes | 20.5 | 20.4 | 0.1 | C027B1AD15EA4926AB4408F8C4584782 |  | R22 | Non-TXV |  | 9.62% | 0.9038 | 18.49% | [5 empty] | Non-TXV | 9.62%
Paso Robles | CA | 93446-5011 |  | 2013-08-06 | 2013-08-06 13:15 | 2013-08-06 13:33 | CARRIER - 38EN042310SM | 56 | 1.8 | Yes | Yes | 22.8 | 19.9 | 2.9 | 25696C4BD56F4BD1A4163EA4B5ABB9FF |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Chico | CA | 95973-1246 |  | 2013-08-07 | 2013-08-07 11:07 | 2013-08-07 11:54 | LENNOX - 12GCS036-75-3PA | 110 | 3.4 | Yes | Yes | 17.9 | 19.4 | -1.5 | F4ECEB808B354963A09618206B913F0C |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Fresno | CA | 93723-9280 |  | 2013-08-08 | 2013-08-08 14:15 | 2013-08-08 14:23 | ICP - GPFM48K080E | 100 | 4.1 | Yes | Yes | 22.5 | 20.4 | 2.1 | 646261E99C2B4DB28B0B429EA960EBE5 |  | R22 | Non-TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | Non-TXV | 4.1%
Fresno | CA | 93705-2339 |  | 2013-08-12 | 2013-08-12 11:59 | 2013-08-12 12:01 | YORK - DAYP-F030N070A | 73 | 2.6 | Yes | Yes | 20.9 | 19.9 | 1 | AAB9968D9AE64E16BB28A684AB24C4E8 |  | R22 | Non-TXV |  | 3.562% | 0.96438 | 6.845% | [5 empty] | Non-TXV | 3.562%
Chico | CA | 95928-7544 |  | 2013-08-06 | 2013-08-06 10:03 | 2013-08-06 10:19 | GOODMAN - CJK24-18 | 98 | 6.2 | Yes | Yes | 18.1 | 20.2 | -2.1 | E96ACD9352374E16AB15BBD79F4237CE |  | R22 | Non-TXV |  | 6.327% | 0.93673 | 12.16% | [5 empty] | Non-TXV | 6.327%
Marysville | CA | 95901-9414 |  | 2013-08-30 | 2013-08-30 12:49 | 2013-08-30 13:10 | TRANE - 4YCY4036B1075AA | 118 | 4.9 | Yes | Yes | 20.9 | 18.5 | 2.4 | 624E742EF4CA483DB0042A74923636C0 |  | R410A | Non-TXV |  | 4.153% | 0.95847 | 7.98% | [5 empty] | Non-TXV | 4.153%
Marysville | CA | 95901-9414 |  | 2013-08-30 | 2013-08-30 13:11 | 2013-08-30 13:26 | TRANE - 4YCY4036B1075AA | 118 | 5.6 | Yes | Yes | 19.3 | 19.9 | -0.6 | A0513B4A10CF48B088DACC356820DD76 |  | R410A | TXV |  | 4.746% | 0.95254 | 9.12% | [5 empty] | TXV | 4.746%
Plumas Lake | CA | 95961-9007 |  | 2013-08-19 | 2013-08-19 09:47 | 2013-08-19 10:05 | YORK - H2RA036S06E | 63 | 4.9 | Yes | Yes | 17 | 16.6 | 0.4 | 4174B7E74B5B4AF2B9B1CAD33D7DF6B4 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Atascadero | CA | 93422-0000 |  | 2013-08-07 | 2013-08-07 15:25 | 2013-08-07 15:42 | NORDYNE - NS4BD-036KB | 68 | -4 | Yes | Yes | 23.3 | 19 | 4.3 | ABAEF60B92724D9CA16990349EF144B6 |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95212-3051 |  | 2013-07-22 | 2013-07-22 15:05 | 2013-07-22 15:32 | YORK - H2RD048S06B | 134 | -9.5 | Yes | Yes | 20.1 | 19.1 | 1.1 | 370FA3EB377548C59A9CF9DCB3422880 |  | R22 | Non-TXV |  | -7.09% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.09%
Grass Valley | CA | 95949-6906 |  | 2013-08-05 | 2013-08-05 15:11 | 2013-08-05 15:33 | CARRIER - 38TXA048330 | 159 | 18.5 | Yes | Yes | 23.5 | 21.1 | 2.5 | 4BE5871D21B04A979EBF365CE2667815 |  | R410A | TXV |  | 11.64% | 0.88365 | 22.36% | [5 empty] | TXV | 11.64%
Atwater | CA | 95301-4842 |  | 2013-08-13 | 2013-08-13 14:06 | 2013-08-13 14:29 | BRYANT - 561CJ030-C | 72 | 13.9 | Yes | Yes | 16.2 | 17.6 | -1.4 | 2E51EA5CBBF2473E9B34D5AB1134C836 |  | R22 | Non-TXV |  | 19.31% | 0.80694 | 37.1% | [5 empty] | Non-TXV | 19.31%
Stockton | CA | 95206-3416 |  | 2013-08-10 | 2013-08-10 09:11 | 2013-08-10 09:27 | GOODMAN - PGB024075-1REVA | 54 | 2.4 | Yes | Yes | 18.4 | 18.2 | 0.2 | 14015D26BA4D479798C6E0D40ADA9310 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Stockton | CA | 95207-1630 |  | 2013-08-06 | 2013-08-06 11:18 | 2013-08-06 11:37 | GOODMAN - GB0360 | 70 | 4.4 | Yes | Yes | 24.7 | 18.8 | 5.9 | 7BE14006FF034BBDB6F3490051388D58 |  | R22 | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Paso Robles | CA | 93446-2828 |  | 2013-08-14 | 2013-08-14 11:17 | 2013-08-14 11:42 | GOODMAN - CKL36-10 | 75 | 2.3 | Yes | Yes | 18.2 | 17.7 | 0.5 | B42292D214674CC7B52176DCA6D4FA8C |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Ione | CA | 95640-5417 |  | 2013-08-02 | 2013-08-02 13:00 | 2013-08-02 13:25 | OTHER - PA12NA042-A | 100 | 13.2 | Yes | Yes | 19 | 21.3 | -2.3 | 47315A9BA98743C6B133F371B55FEF2E |  | R22 | TXV |  | 13.2% | 0.868 | 25.37% | [5 empty] | TXV | 13.2%
Chico | CA | 95973-0888 |  | 2013-08-07 | 2013-08-07 10:02 | 2013-08-07 11:05 | GIBSON - JT5BD-018K | 93 | 8.1 | Yes | Yes | 16.5 | 19 | -2.5 | 48120E902CD64B7BACFBCF2D58E11C43 |  | R22 | Non-TXV |  | 8.71% | 0.9129 | 16.74% | [5 empty] | Non-TXV | 8.71%
Stockton | CA | 95215-5206 |  | 2013-09-05 | 2013-09-05 14:28 | 2013-09-05 14:46 | RHEEM - UNK | 88 | 18.2 | Yes | Yes | 24.5 | 19.3 | 5.3 | D02B3C51B465400CA3837AA36B9BD366 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.68% | 0.79318 | 39.75% | [5 empty] | Non-TXV | 20.68%
Valley Springs | CA | 95252-9240 |  | 2013-09-12 | 2013-09-12 14:18 | 2013-09-12 14:51 | RUUD - UNK | 130 | 5 | Yes | Yes | 22 | 19.3 | 2.7 | 7F00CF68084945E68F4D380B01385334 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Stockton | CA | 95210-4417 |  | 2013-07-30 | 2013-07-30 13:44 | 2013-07-30 14:03 | PAYNE - PA10JA060000ACAA | 117 | 3.6 | Yes | Yes | 24 | 18 | 6 | 29CD050CCAD04E89A6734EF98F598B36 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Paso Robles | CA | 93446-5930 |  | 2013-08-15 | 2013-08-15 13:14 | 2013-08-15 13:35 | HEIL - UNK | 112 | -6.6 | Yes | Yes | 21.4 | 16.5 | 4.9 | C2564F34AC244A1F9499B99277311D8D |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Corning | CA | 96021-9231 |  | 2013-07-23 | 2013-07-23 18:29 | 2013-07-23 18:48 | COLEMAN - 9632E60 | 114 | 7.5 | Yes | Yes | 19.7 | 20.9 | -1.2 | 25DA73BAF9BE4C048B4A0F84223DEA4C |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Manteca | CA | 95336-8243 |  | 2013-07-18 | 2013-07-18 14:07 | 2013-07-18 14:32 | CARRIER - 38EN042300 | 114 | 4.4 | Yes | Yes | 19.9 | 19 | 0.9 | 0618A38A501C406DB742C5664805808C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.86% | 0.9614 | 7.417% | [5 empty] | Non-TXV | 3.86%
Los Banos | CA | 93635-6502 |  | 2013-08-20 | 2013-08-20 10:38 | 2013-08-20 10:41 | GIBSON - 7777UNK | 100 | 4.8 | Yes | Yes | 22.1 | 22.3 | -0.2 | 8EAB0DE352C34D38A2BCC30AF36B9DA8 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Paso Robles | CA | 93446-5031 |  | 2013-08-08 | 2013-08-08 12:22 | 2013-08-08 12:43 | CARRIER - 38EN024310SM | 56 | 1.8 | Yes | Yes | 21.7 | 16.1 | 5.6 | 63036843CFB747C29025547D8AA8D370 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Paso Robles | CA | 93446-2003 |  | 2013-08-16 | 2013-08-16 11:33 | 2013-08-16 11:57 | PAYNE - PA10048-C | 96 | 4.9 | Yes | Yes | 17.7 | 16.1 | 1.6 | 9FD3914BF7A44CAD8282A91D0770DC93 |  | R22 | Non-TXV |  | 5.104% | 0.94896 | 9.809% | [5 empty] | Non-TXV | 5.104%
Clovis | CA | 93611-7242 |  | 2013-08-06 | 2013-08-06 11:58 | 2013-08-06 12:00 | OTHER - EADB048JAS | 113 | 22 | Yes | Yes | 21.5 | 19.9 | 1.6 | FF52830B13FF4EDB86D617020C49F0E3 |  | R22 | Non-TXV |  | 19.47% | 0.80531 | 37.42% | [5 empty] | Non-TXV | 19.47%
Cameron Park | CA | 95682-9693 |  | 2013-08-15 | 2013-08-15 14:53 | 2013-08-15 14:53 | TRANE - YCC060F1M08G | 179 | 0 | Yes | Yes | 26.9 | 21.7 | 5.2 | CDB52E4ABE0D464DAE8E387E2852C477 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4240 |  | 2013-08-23 | 2013-08-23 10:27 | 2013-08-23 10:29 | RUUD - UNK | 68 | 6.7 | Yes | Yes | 25 | 20.2 | 4.8 | 00DE48FA15044A48802DFBCBE917738F |  | R22 | Non-TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | Non-TXV | 9.853%
Oroville | CA | 95966-5507 |  | 2013-08-06 | 2013-08-06 16:02 | 2013-08-06 16:28 | DAY & NIGHT - NA | 59 | 10.1 | Yes | Yes | 22.5 | 20.7 | 1.8 | B4EFAAD974BA4311ABFDE3623D0844B1 |  | R22 | Non-TXV |  | 17.12% | 0.82881 | 32.9% | [5 empty] | Non-TXV | 17.12%
Red Bluff | CA | 96080-2344 |  | 2013-07-20 | 2013-07-20 10:12 | 2013-07-20 13:04 | PAYNE - PA13NA024-B | 63 | 2.7 | Yes | Yes | 19.8 | 20.4 | -0.6 | 314AE26815A14D0D944F5B94EDD2CBD5 |  | R410A | TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | TXV | 4.286%
Valley Springs | CA | 95252-8682 |  | 2013-09-04 | 2013-09-04 15:57 | 2013-09-04 16:25 | BDP - 585HJ036060 | 102 | 5.9 | Yes | Yes | 26.8 | 20.9 | 6 | 4D8D3F9CBF9F44BC977DE7920E8DED4C |  | R22 | Non-TXV |  | 5.784% | 0.94216 | 11.12% | [5 empty] | Non-TXV | 5.784%
Magalia | CA | 95954-9442 |  | 2013-08-03 | 2013-08-03 13:42 | 2013-08-03 14:12 | BRYANT - 604ANX03600AA | 169 | 5.5 | Yes | Yes | 19 | 22 | -3 | F3ED838C651B4A9682F6DAC5871F03C0 |  | R22 | Non-TXV |  | 3.254% | 0.96746 | 6.254% | [5 empty] | Non-TXV | 3.254%
Stockton | CA | 95210-2448 |  | 2013-08-01 | 2013-08-01 10:52 | 2013-08-01 11:11 | GOODMAN - GSC130241 | 76 | -6.3 | Yes | Yes | 16.9 | 18.2 | -1.3 | 04E5A59D7DBA4B28BCE7B0417A824B2C |  | R22 | Non-TXV |  | -8.289% | 1.0829 | 2.321% |  |  |  |  | Non-TXV |  |  | -8.289%
Tracy | CA | 95376-9681 |  | 2013-08-01 | 2013-08-01 11:35 | 2013-08-01 11:54 | UNITARY PRODUCTS GROUP - DRCS0481BE | 103 | 12.4 | Yes | Yes | 18.2 | 20.3 | -2.1 | 1B7FF3E4FCE64921BC80BD16D6C792CB |  | R22 | Non-TXV |  | 12.04% | 0.87961 | 23.14% | [5 empty] | Non-TXV | 12.04%
Corning | CA | 96021-2701 |  | 2013-07-23 | 2013-07-23 12:23 | 2013-07-23 12:23 | GOODMAN - CKJ30-1B | 85 | 3.6 | Yes | Yes | 17.1 | 19.1 | -2 | 86438D01C04241399524323C4A26F7E8 | Add refrigerant: 3.6 oz | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Stockton | CA | 95210-2447 |  | 2013-08-01 | 2013-08-01 10:30 | 2013-08-01 10:48 | RHEEM - UNK | 50 | 3 | Yes | Yes | 20.4 | 18.8 | 1.6 | DC23F47F9E324718852617DEFE752790 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Colfax | CA | 95713-9732 |  | 2013-07-26 | 2013-07-26 11:30 | 2013-07-26 11:54 | RHEEM - RAMA-048JAZ | 172 | 10.9 | Yes | Yes | 20 | 19.8 | 0.2 | F3FB0557094A41C29400148D941B25A5 |  | R22 | TXV |  | 6.337% | 0.93663 | 12.18% | [5 empty] | TXV | 6.337%
Stockton | CA | 95209-4038 |  | 2013-08-02 | 2013-08-02 09:20 | 2013-08-02 09:38 | RHEEM - RRKA-A024JK06X | 50 | 1.5 | Yes | Yes | 15.8 | 18.2 | -2.4 | 7899D1C768C143EA80937F3069DFDC52 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-3951 |  | 2013-08-05 | 2013-08-05 12:24 | 2013-08-05 12:41 | RHEEM - HC-80-24-21C | 49 | 3.4 | Yes | Yes | 18.6 | 18.8 | -0.2 | 52384D950E864D6FA043D62D9902CACF |  | R22 | Non-TXV |  | 6.939% | 0.93061 | 13.33% | [5 empty] | Non-TXV | 6.939%
Yuba City | CA | 95991-5469 |  | 2013-07-17 | 2013-07-17 14:30 | 2013-07-17 14:54 | BRYANT - 561CJ024-D | 60 | 11.5 | Yes | Yes | 16 | 17.7 | -1.7 | 563C8DC6619C40C9B0F9800E0630ADBE |  | R22 | TXV |  | 19.17% | 0.80833 | 36.83% | [5 empty] | TXV | 19.17%
Fresno | CA | 93722-4117 |  | 2013-07-17 | 2013-07-17 13:54 | 2013-07-17 13:55 | RHEEM - UNK | 64 | 8.7 | Yes | Yes | 22.4 | 20.4 | 2 | 711A92D55B794129BBABB52AC73AFAF8 |  | R22 | Non-TXV |  | 13.59% | 0.86406 | 26.12% | [5 empty] | Non-TXV | 13.59%
Fresno | CA | 93703-1259 |  | 2013-08-08 | 2013-08-08 08:22 | 2013-08-08 08:24 | CARRIER - 38BA004300 | 176 | 7.1 | Yes | Yes | 18.8 | 18.2 | 0.6 | 307B878BC3E643CA91F5CE06BFD81288 |  | R22 | Non-TXV |  | 4.034% | 0.95966 | 7.753% | [5 empty] | Non-TXV | 4.034%
Fresno | CA | 93725-1849 |  | 2013-08-06 | 2013-08-06 14:43 | 2013-08-06 14:48 | COLEMAN - 7777UNK | 100 | 3 | Yes | Yes | 25.3 | 19.3 | 6 | 3FBD0D87C3F14923AC982A883771FB96 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Marysville | CA | 95901-8050 |  | 2013-08-08 | 2013-08-08 17:45 | 2013-08-08 18:13 | FRIGIDAIRE - FS3BA--030KA | 68 | 2.3 | Yes | Yes | 25 | 21.3 | 3.7 | 5D7ED26CF7494BF785E681305668DCB4 |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Ione | CA | 95640-9642 |  | 2013-08-02 | 2013-08-02 11:46 | 2013-08-02 12:08 | CARRIER - 38QB030300 | 112 | 16.6 | Yes | Yes | 18 | 20.4 | -2.4 | 23C6581AB7A6496B9A3E67E7A16C8912 |  | R22 | Non-TXV |  | 14.82% | 0.85179 | 28.48% | [5 empty] | Non-TXV | 14.82%
Sanger | CA | 93657-2258 |  | 2013-09-17 | 2013-09-17 10:14 | 2013-09-17 11:04 | ICP - GPCM036K060D | 68 | 3.9 | Yes | Yes | 17 | 19.9 | -2.9 | 29FC6452EB014D13B5D9F07DDEECF15B |  | R22 | Non-TXV |  | 5.735% | 0.94265 | 11.02% | [5 empty] | Non-TXV | 5.735%
Meadow Vista | CA | 95722-9499 |  | 2013-10-10 | 2013-10-10 12:14 | 2013-10-10 12:32 | BRYANT - 582ANW060115NAAG | 115 | 4.5 | Yes | Yes | 25 | 20.9 | 4.1 | 6AA196DA6EF04B1FAA0A3B67DBE58470 |  | R22 | TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | TXV | 3.913%
Stockton | CA | 95207-1462 |  | 2013-08-06 | 2013-08-06 10:37 | 2013-08-06 10:56 | TRANE - TTD730B100A | 80 | 15.2 | Yes | Yes | 23.2 | 19.1 | 4.1 | DADA821EDC2448568EAEA55E4EA242D5 |  | R22 | Non-TXV |  | 19% | 0.81 | 36.51% | [5 empty] | Non-TXV | 19%
Merced | CA | 95340-4210 |  | 2013-08-08 | 2013-08-08 08:46 | 2013-08-08 09:24 | AMERICAN STANDARD - TTR042C100A0 | 110 | 4.3 | Yes | Yes | 21.1 | 19.9 | 1.2 | EDD1B00E3A9743C39BCE2B8D8E87F1B3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.909% | 0.96091 | 7.512% | [5 empty] | Non-TXV | 3.909%
Atwater | CA | 95301-4838 |  | 2013-08-15 | 2013-08-15 11:55 | 2013-08-15 12:18 | GOODMAN - GSX130361DA | 76 | 4.2 | Yes | Yes | 22.5 | 19.5 | 3 | C2CEE8BB8DBE4ABEA6551AFDBE305990 |  | R410A | TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | TXV | 5.526%
Paso Robles | CA | 93446-1412 |  | 2013-09-04 | 2013-09-04 18:29 | 2013-09-04 18:46 | CARRIER - 48DL002 | 43 | -2.5 | Yes | Yes | 21 | 20.3 | 0.8 | 76B26ECB67414739BD8F32DD602297CF |  | R22 | Non-TXV |  | -5.814% | 1.0581 | 1.628% |  |  |  |  | Non-TXV |  |  | -5.814%
Stockton | CA | 95215-5206 |  | 2013-08-13 | 2013-08-13 16:21 | 2013-08-13 16:21 | BRYANT - 561CJ036-F | 70 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | 6E31070018284F60B4225FB0A4D03BA2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-1412 |  | 2013-08-05 | 2013-08-05 15:11 | 2013-08-05 15:35 | CARRIER - 48DL002 | 42 | 1.4 | Yes | Yes | 22 | 24.2 | -2.2 | 08851A41AB764F74900833AA1B14BEE9 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93722-7339 |  | 2013-08-09 | 2013-08-09 12:26 | 2013-08-09 12:29 | CARRIER - 38CK030310 | 68 | 2.9 | Yes | Yes | 21.8 | 20.4 | 1.4 | 19331423C45E451BBE8CA1761C3C052E |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Stockton | CA | 95205-3448 |  | 2013-08-26 | 2013-08-26 15:03 | 2013-08-26 15:06 | GOODMAN - PGB036075-1A-REV A | 68 | 6.4 | Yes | Yes | 25.4 | 20.1 | 5.3 | D7AACAF04E81433AA0B0A614AC5892F7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Ione | CA | 95640-4501 |  | 2013-08-02 | 2013-08-02 09:33 | 2013-08-02 09:57 | YORK - H2RD030S068 | 93 | 4.7 | Yes | Yes | 20 | 19.5 | 0.5 | C789AEF2FADA46929CB4D8B5956796C7 |  | R22 | TXV |  | 5.054% | 0.94946 | 9.712% | [5 empty] | TXV | 5.054%
Paso Robles | CA | 93446-4309 |  | 2013-08-06 | 2013-08-06 15:17 | 2013-08-06 15:33 | OTHER - UNK | 50 | -3.5 | Yes | Yes | 26.5 | 21 | 5.6 | 6A776C1FED6549F3A9A808B60B75C827 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Stockton | CA | 95212-3483 |  | 2013-08-09 | 2013-08-09 08:27 | 2013-08-09 08:27 | YORK - AC036X1222A | 83 | 0 | Yes | Yes | 24.6 | 18.7 | 5.9 | F5185F9156F44801A76723AB8F6182FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0450 |  | 2013-08-07 | 2013-08-07 17:13 | 2013-08-07 17:34 | BRYANT - 582ANW030060NAAD | 55 | 4.5 | Yes | Yes | 17 | 19.4 | -2.4 | D1D2D919AAB9482CA5E5C23F08ED8E66 |  | R22 | Non-TXV |  | 8.182% | 0.91818 | 15.72% | [5 empty] | Non-TXV | 8.182%
Lincoln | CA | 95648-8607 |  | 2013-08-23 | 2013-08-23 09:52 | 2013-08-23 10:19 | YORK - H1RC060S06D | 147 | 7.7 | Yes | Yes | 18 | 20.4 | -2.4 | B91DE810629B49358F17A5ED6BE96735 |  | R22 | TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | TXV | 5.238%
Chico | CA | 95973-8318 |  | 2013-08-16 | 2013-08-16 10:54 | 2013-08-16 11:23 | GOODMAN - C1T30-1B | 107 | 5.1 | Yes | Yes | 18.1 | 20.1 | -2 | 33EFB8F2D1C044A8B89334C789E22763 |  | R22 | Non-TXV |  | 4.766% | 0.95234 | 9.16% | [5 empty] | Non-TXV | 4.766%
San Miguel | CA | 93451-9121 |  | 2013-08-13 | 2013-08-13 09:57 | 2013-08-13 10:25 | BRYANT - 563CN030-C | 100 | 3.2 | Yes | Yes | 21.8 | 20.4 | 1.4 | 0523D85474CB4296981BE0EC52B9AB04 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fowler | CA | 93625-9440 |  | 2013-08-20 | 2013-08-20 11:15 | 2013-08-20 11:34 | LENNOX - 13ACC-060- | 168 | 14.8 | Yes | Yes | 17 | 19.8 | -2.8 | CA7BD45E78944205BAD68896CC76607E |  | R22 | Non-TXV |  | 8.81% | 0.9119 | 16.93% | [5 empty] | Non-TXV | 8.81%
Paso Robles | CA | 93446-3260 |  | 2013-08-05 | 2013-08-05 12:51 | 2013-08-05 13:26 | TEMPSTAR - CA5542VKD1 | 98 | -9.2 | Yes | Yes | 23.7 | 20.4 | 3.3 | 5E9D331869884F75935FD3E73604B7C9 |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Stockton | CA | 95215-5205 |  | 2013-08-13 | 2013-08-13 13:50 | 2013-08-13 14:33 | ICP - PGC024K040E | 54 | 7 | Yes | Yes | 24.4 | 25.1 | -0.6 | BA434A6BBCB94A4C86EA64AD24562016 |  | R22 | Non-TXV |  | 12.96% | 0.87037 | 24.91% | [5 empty] | Non-TXV | 12.96%
San Miguel | CA | 93451-9121 |  | 2013-08-13 | 2013-08-13 10:29 | 2013-08-13 10:55 | BRYANT - UNK | 105 | -14.2 | Yes | Yes | 19.3 | 16.9 | 2.4 | FC703945AD644C64A5A4CD4B5B63B4F4 |  | R22 | Non-TXV |  | -13.52% | 1.1352 | 3.787% |  |  |  |  | Non-TXV |  |  | -13.52%
Foresthill | CA | 95631-9715 |  | 2013-10-14 | 2013-10-14 16:16 | 2013-10-14 16:16 | TRANE - 2TTR2048A1000AA | 120 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | DF5EA6C199234A98B4A957AA2BD62641 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rescue | CA | 95672-9446 |  | 2013-08-10 | 2013-08-10 15:07 | 2013-08-10 15:07 | UNITARY PRODUCTS GROUP - BRCQ0301BD | 48 | 0 | Yes | Yes | 18.4 | 20.1 | -1.7 | AC4CDDC28C964907A2097B10D6589D2F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2959 |  | 2013-08-06 | 2013-08-06 14:21 | 2013-08-06 14:48 | BDP - 585HJW030040ABAF | 68 | 8 | Yes | Yes | 20 | 20.5 | -0.5 | 2921DB7A561B48DF8733CE4C47644521 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Stockton | CA | 95212-3816 |  | 2013-08-08 | 2013-08-08 09:34 | 2013-08-08 09:54 | GOODMAN - CKL42-1L | 115 | 4.8 | Yes | Yes | 15.7 | 18.5 | -2.8 | B452FC5D7C694C7EB46DB33B973B1878 |  | R22 | Non-TXV |  | 4.174% | 0.95826 | 8.021% | [5 empty] | Non-TXV | 4.174%
Winton | CA | 95388-9428 |  | 2013-08-15 | 2013-08-15 12:48 | 2013-08-15 13:14 | CARRIER - 48GS-030040301 | 55 | 2.7 | Yes | Yes | 24 | 20.4 | 3.7 | 3533F876B5BE48A5B665DE84DAD66FFF |  | R22 | Non-TXV |  | 4.909% | 0.95091 | 9.434% | [5 empty] | Non-TXV | 4.909%
San Miguel | CA | 93451-0000 |  | 2013-08-13 | 2013-08-13 12:53 | 2013-08-13 13:24 | CARRIER - CA5530UKA1 | 85 | 4.1 | Yes | Yes | 24 | 22.1 | 2 | B4CB9E1BD85F4C4891F3C614A39A79B2 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Paso Robles | CA | 93446-5930 |  | 2013-08-12 | 2013-08-12 13:59 | 2013-08-12 14:22 | OTHER - 36DNR10BC | 93 | 6.5 | Yes | Yes | 24.4 | 20 | 4.5 | 90081C5C00B641FEBCC4C6FBD006C620 |  | R22 | Non-TXV |  | 6.989% | 0.93011 | 13.43% | [5 empty] | Non-TXV | 6.989%
Stockton | CA | 95207-2356 |  | 2013-09-13 | 2013-09-13 12:03 | 2013-09-13 12:24 | DAY & NIGHT - UNK | 67 | 11.8 | Yes | Yes | 21.5 | 17.5 | 4 | F40A70B03594442C8769FBF48154C2BC |  | R22 | Non-TXV |  | 17.61% | 0.82388 | 33.85% | [5 empty] | Non-TXV | 17.61%
Sanger | CA | 93657-2969 |  | 2013-08-10 | 2013-08-10 09:58 | 2013-08-10 10:23 | RHEEM - RRNA-B036JK08X | 86 | 3.8 | Yes | Yes | 17.5 | 20.3 | -2.8 | 8B3726D01F294A72940FCCA76514381B |  | R22 | Non-TXV |  | 4.419% | 0.95581 | 8.492% | [5 empty] | Non-TXV | 4.419%
Chico | CA | 95973-0520 |  | 2013-09-25 | 2013-09-25 13:29 | 2013-09-25 14:02 | GIBSON - JS3BA-034KA | 64 | 7.1 | Yes | Yes | 18 | 20.9 | -2.9 | 8750E9A620614AFDA6D63F9B99AD4F3C |  | R22 | Non-TXV |  | 11.09% | 0.88906 | 21.32% | [5 empty] | Non-TXV | 11.09%
Atascadero | CA | 93422-5825 |  | 2013-08-08 | 2013-08-08 11:07 | 2013-08-08 11:25 | OTHER - TZGE-324JL060AX | 77 | -4.5 | Yes | Yes | 27 | 21.1 | 5.9 | F4C6F228D54F416C855C286384851851 |  | R410A | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Paso Robles | CA | 93446-5930 |  | 2013-08-14 | 2013-08-14 14:42 | 2013-08-14 15:07 | PAYNE - PA10JA042000AHAA | 90 | 5 | Yes | Yes | 24.5 | 19.9 | 4.6 | E185CED9CE7A4E32BCC78458433D0A03 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Sanger | CA | 93657-3711 |  | 2013-09-10 | 2013-09-10 15:40 | 2013-09-10 16:54 | RHEEM - RRPL-B048JK10X | 161 | 5.9 | Yes | Yes | 23.5 | 17.9 | 5.6 | AABBDF9BAEC6497F84086097F4C544EB |  | R410A | TXV |  | 3.665% | 0.96335 | 7.043% | [5 empty] | TXV | 3.665%
Rescue | CA | 95672-9306 |  | 2013-09-04 | 2013-09-04 09:57 | 2013-09-04 10:32 | GOODMAN - CPKJ42-1B | 160 | -15.1 | Yes | Yes | 19 | 19.9 | -0.9 | AD9F7FBD13BD493E8DBB89E91995A55B |  | R22 | Non-TXV |  | -9.438% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.438%
Stockton | CA | 95209-2184 |  | 2013-08-27 | 2013-08-27 10:13 | 2013-08-27 10:32 | BRYANT - 582ANW030060NAAD | 55 | 3.1 | Yes | Yes | 20.4 | 17.9 | 2.6 | 3114548E694C4D72BF9549C5990FE77F |  | R22 | Non-TXV |  | 5.636% | 0.94364 | 10.83% | [5 empty] | Non-TXV | 5.636%
Templeton | CA | 93465-4019 |  | 2013-08-15 | 2013-08-15 13:51 | 2013-08-15 14:29 | DAY & NIGHT - 561CJX048000AAAA | 109 | 7.6 | Yes | Yes | 24.2 | 19.3 | 4.9 | E877236D7F6B42AD9B1FC474967F937E |  | R22 | Non-TXV |  | 6.972% | 0.93028 | 13.4% | [5 empty] | Non-TXV | 6.972%
Merced | CA | 95340-4009 |  | 2013-07-22 | 2013-07-22 15:26 | 2013-07-22 15:26 | AMERICAN STANDARD - YCC030F1M0BH | 72 | 0 | Yes | Yes | 20.7 | 19.8 | 0.9 | 8403C08534154B82A4355425C5ACEDA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-9751 |  | 2013-09-09 | 2013-09-09 16:03 | 2013-09-09 17:11 | ICP - TCA048AKA5 | 123 | 3.9 | Yes | Yes | 21 | 20.4 | 0.6 | CCA26A09EE154CA18C9474D909536E23 |  | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Chico | CA | 95928-4124 |  | 2013-08-28 | 2013-08-28 08:26 | 2013-08-28 08:43 | GOODMAN - CLJ48-1 | 117 | -6.9 | Yes | Yes | 21.5 | 18.8 | 2.7 | 70F014ED6DF44194A2F33AAD39655DD8 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Colfax | CA | 95713-9527 |  | 2013-09-03 | 2013-09-03 08:55 | 2013-09-03 09:27 | CARRIER - 48GS-06009031 | 116 | 6.4 | Yes | Yes | 22 | 20.6 | 1.4 | 7675C3AC85454620ABEB88B725472D3F |  | R22 | TXV |  | 5.517% | 0.94483 | 10.6% | [5 empty] | TXV | 5.517%
Sanger | CA | 93657-2954 |  | 2013-08-07 | 2013-08-07 11:41 | 2013-08-07 12:39 | BDP - 585HJ036060ABAF | 102 | 3.1 | Yes | Yes | 20.1 | 22.7 | -2.6 | 91CB58AC74B14C309152C2E0BE141D9E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Yuba City | CA | 95993-1309 |  | 2013-07-17 | 2013-07-17 16:43 | 2013-07-17 17:03 | BRYANT - 561CJ036-E | 70 | -2.6 | Yes | Yes | 19 | 21 | -2 | FDEAA15BBAD849E5B4B2B7DF4AB71525 |  | R22 | TXV |  | -3.714% | 1.0371 | 1.04% |  |  |  |  | TXV |  |  | -3.714%
Chico | CA | 95973-9103 |  | 2013-08-09 | 2013-08-09 12:42 | 2013-08-09 13:00 | GOODMAN - GPG1336070M41AC | 85 | -8 | Yes | Yes | 21 | 19.2 | 1.8 | E783CCB79CAF42EA9692E3BA35135976 | OK: Verified Refrigerant Charge Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | TXV |  |  | -9.412%
San Miguel | CA | 93451-9110 |  | 2013-08-13 | 2013-08-13 11:36 | 2013-08-13 12:02 | DUCANE - AC10B6-B | 96 | 6.1 | Yes | Yes | 20.2 | 18.1 | 2.1 | E00AEBB2A05A463C85A3B2E66A89412C |  | R22 | Non-TXV |  | 6.354% | 0.93646 | 12.21% | [5 empty] | Non-TXV | 6.354%
Madera | CA | 93637-4817 |  | 2013-08-06 | 2013-08-06 10:08 | 2013-08-06 11:49 | CARRIER - UNK | 76 | 5.1 | Yes | Yes | 19.3 | 20.4 | -1.1 | 7B3D073543CA4F9ABA37C11DD089D0CB |  | R22 | Non-TXV |  | 6.711% | 0.93289 | 12.9% | [5 empty] | Non-TXV | 6.711%
Fresno | CA | 93722-7106 |  | 2013-08-09 | 2013-08-09 13:42 | 2013-08-09 13:45 | RHEEM - RRNA-B042JK0AX | 104 | 5.8 | Yes | Yes | 24.5 | 20.9 | 3.6 | 1A9E34E481BA4F9685D4BC40787502D5 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Merced | CA | 95340-2622 |  | 2013-08-09 | 2013-08-09 09:02 | 2013-08-09 09:27 | GOODMAN - GSC130301AE | 117 | 3.5 | Yes | Yes | 23.4 | 19.1 | 4.3 | C8A6ABAE15FD4B4190830722B6482F91 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Merced | CA | 95348-9528 |  | 2013-08-19 | 2013-08-19 10:46 | 2013-08-19 10:48 | GOODMAN - GSC130361GB | 77 | 4.4 | Yes | Yes | 18.1 | 21 | -2.9 | 0E58842B2B6D48ACAA0236B927D37F39 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Merced | CA | 95348-3128 |  | 2013-09-20 | 2013-09-20 14:30 | 2013-09-20 14:31 | GE - BWB918A10000 | 77 | 10.2 | Yes | Yes | 21.3 | 16.4 | 4.9 | 0F6B5C7B9DAD4E918B433C417CD9B317 |  | R22 | Non-TXV |  | 13.25% | 0.86753 | 25.46% | [5 empty] | Non-TXV | 13.25%
Merced | CA | 95348-2730 |  | 2013-08-23 | 2013-08-23 15:47 | 2013-08-23 15:49 | OTHER - WCA3242GKR1 | 65 | 4.9 | Yes | Yes | 16.2 | 18.5 | -2.3 | 68A835836B8C4B5F90209EC6C9BA85E4 |  | R22 | Non-TXV |  | 7.538% | 0.92462 | 14.49% | [5 empty] | Non-TXV | 7.538%
Chico | CA | 95973-8786 |  | 2013-08-26 | 2013-08-26 14:42 | 2013-08-26 15:01 | AMANA - RCC36C2A | 110 | 3.8 | Yes | Yes | 21.3 | 21 | 0.3 | 63C3147C55C740B494556E034AD65870 |  | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Corning | CA | 96021-3539 |  | 2013-08-13 | 2013-08-13 10:59 | 2013-08-13 12:34 | COLEMAN - NA | 55 | 6.8 | Yes | Yes | 21.6 | 21.7 | -0.1 | D1330C937E6D440796647803E1130395 |  | R22 | Non-TXV |  | 12.36% | 0.87636 | 23.76% | [5 empty] | Non-TXV | 12.36%
Selma | CA | 93662-2112 |  | 2013-08-20 | 2013-08-20 17:44 | 2013-08-20 18:44 | OTHER - 80AW36106 | 118 | 7.3 | Yes | Yes | 12.5 | 18.6 | -6.1 | 7F9D67E7B90548CDB6FDCEDF1DA7B314 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.186% | 0.93814 | 11.89% | [5 empty] | Non-TXV | 6.186%
Rescue | CA | 95672-9352 |  | 2013-08-10 | 2013-08-10 13:31 | 2013-08-10 13:48 | GOODMAN - CPKJ42-1B | 160 | 16.7 | Yes | Yes | 18.1 | 20.4 | -2.3 | C7921BD1B8224EFF9F27F846944098BC |  | R22 | Non-TXV |  | 10.44% | 0.89563 | 20.06% | [5 empty] | Non-TXV | 10.44%
Fresno | CA | 93722-5561 |  | 2013-08-09 | 2013-08-09 13:14 | 2013-08-09 13:17 | CARRIER - 7777UNK | 116 | 4.8 | Yes | Yes | 21.8 | 20.4 | 1.4 | 08223ACCD5BB456BB3434C4A8DC70620 |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Stockton | CA | 95207-4040 |  | 2013-08-06 | 2013-08-06 14:55 | 2013-08-06 14:55 | GUARDIAN - GCGD24S41S3A | 61 | 0 | Yes | Yes | 21.1 | 17 | 4.1 | AF7D1338C01D4E6D8ED457AF0A03AEC0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-9664 |  | 2013-08-20 | 2013-08-20 15:32 | 2013-08-20 15:58 | ARMSTRONG - SCU10G36A-1 | 80 | 2.4 | Yes | Yes | 21.6 | 18.1 | 3.5 | A5EC8C38698C4F8896709498A970D35C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95205-7144 |  | 2013-08-02 | 2013-08-02 09:13 | 2013-08-02 09:36 | WESTINGHOUSE - B1036CDW | 50 | 4.4 | Yes | Yes | 24.6 | 20 | 4.6 | 38E291A682FF4D259CB0E68358AFCE43 |  | R22 | Non-TXV |  | 8.8% | 0.912 | 16.91% | [5 empty] | Non-TXV | 8.8%
Oroville | CA | 95965-9654 |  | 2013-08-06 | 2013-08-06 10:56 | 2013-08-06 11:57 | TRANE - 2WCX3060A1000AA | 155 | 4.9 | Yes | Yes | 22.5 | 19.9 | 2.6 | 7BB6F75F2BB74FE88314747F34CB02DA |  | R22 | Non-TXV |  | 3.161% | 0.96839 | 6.075% | [5 empty] | Non-TXV | 3.161%
Colfax | CA | 95713-9722 |  | 2013-08-16 | 2013-08-16 15:26 | 2013-08-16 15:26 | PAYNE - | 85 | 0 | Yes | Yes | 8 | 20.4 | -12.4 | E43643C7FAEC492788C3EDC84A7C73F8 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Colfax | CA | 95713-9722 |  | 2013-08-16 | 2013-08-16 11:09 | 2013-08-16 11:41 | PAYNE - 5420024HP | 101 | 4.1 | Yes | Yes | 22 | 23.3 | -1.3 | 47D7AB8F0BAB454F8DA8C721FF5775B8 |  | R22 | Non-TXV |  | 4.059% | 0.95941 | 7.801% | [5 empty] | Non-TXV | 4.059%
Stockton | CA | 95209-2259 |  | 2013-08-01 | 2013-08-01 14:57 | 2013-08-01 15:13 | AMERICAN STANDARD - YCP036F1M0AA | 109 | -6.4 | Yes | Yes | 21.7 | 19.9 | 1.8 | 1411780979704D20893D566638280E4D |  | R22 | Non-TXV |  | -5.872% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.872%
Fresno | CA | 93722-5501 |  | 2013-08-08 | 2013-08-08 11:50 | 2013-08-08 11:51 | RHEEM - RRKA-A030JK06X | 54 | 2.2 | Yes | Yes | 20.1 | 18.8 | 1.3 | DA0702ADFAE045DFA2D9E56086772E69 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Stockton | CA | 95207-2356 |  | 2013-08-06 | 2013-08-06 10:01 | 2013-08-06 10:18 | AMANA - PGD30C0702G | 74 | -4.4 | Yes | Yes | 20.2 | 18.8 | 1.4 | 3B2CBF13A0A0408A9F5A22413EBA7E5D |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Fowler | CA | 93625-2459 |  | 2013-08-20 | 2013-08-20 10:26 | 2013-08-20 11:10 | RHEEM - RRGG-05N25JKR | 39 | 2.6 | Yes | Yes | 17.5 | 20.4 | -2.9 | B55DBF9543844D479568E1F6F54A3FE6 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Olivehurst | CA | 95961-9039 |  | 2013-08-30 | 2013-08-30 12:23 | 2013-08-30 12:40 | CARRIER - 38BRC048370 | 136 | 8 | Yes | Yes | 24.3 | 19.6 | 4.7 | BE3515685D154322942486787E052C93 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Stockton | CA | 95210-2008 |  | 2013-08-01 | 2013-08-01 09:52 | 2013-08-01 10:13 | RUUD - UAMB-030JBZ | 77 | -5.4 | Yes | Yes | 21 | 18.5 | 2.5 | 44A0B98B525A44A98A5DA24074A53C73 |  | R22 | Non-TXV |  | -7.013% | 1.0701 | 1.964% |  |  |  |  | Non-TXV |  |  | -7.013%
Grass Valley | CA | 95945-6870 |  | 2013-09-04 | 2013-09-04 12:47 | 2013-09-04 13:10 | TRANE - TTB718A100A1 | 50 | -2.6 | Yes | Yes | 20 | 18.8 | 1.2 | 636F7CA23F4C40179928EA43BA4C8D94 |  | R22 | TXV |  | -5.2% | 1.052 | 1.456% |  |  |  |  | TXV |  |  | -5.2%
Stockton | CA | 95215-5205 |  | 2013-09-04 | 2013-09-04 09:51 | 2013-09-04 10:32 | ICP - NAC042AKC3 | 112 | 3.4 | Yes | Yes | 17.4 | 17.7 | -0.3 | 1E751C284890454C8899DA79A863A21A |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Pine Grove | CA | 95665-4010 |  | 2013-09-03 | 2013-09-03 10:00 | 2013-09-03 10:28 | GOODMAN - PGB030050-1 | 56 | -4.6 | Yes | Yes | 20.7 | 19.1 | 1.7 | E76B1EC9B7454E5299B7729B87730D3C |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Riverbank | CA | 95367-9662 |  | 2013-08-20 | 2013-08-20 16:43 | 2013-08-20 17:02 | UNITARY PRODUCTS GROUP - AC024M1021CG | 52 | 1.6 | Yes | Yes | 19.5 | 20.9 | -1.4 | E6B0D46268884471A233AABB85B30FEB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
El Dorado Hills | CA | 95762-5523 |  | 2013-09-04 | 2013-09-04 15:34 | 2013-09-04 15:34 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 18.3 | 20.2 | -1.9 | 3475D83BC3FE4F4AA30E481CAC0BB47B | OK: Verified Refrigerant Charge Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-8244 |  | 2013-08-02 | 2013-08-02 12:19 | 2013-08-02 18:49 | COLEMAN - BRCQO551BD | 89 | 2.7 | Yes | Yes | 27.9 | 22.8 | 5.1 | 1167FC9F4BEE426C806B2D418973B667 |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Merced | CA | 95341-5496 |  | 2013-10-02 | 2013-10-02 14:56 | 2013-10-02 14:58 | RHEEM - UNK | 104 | 11.7 | Yes | Yes | 27.1 | 22 | 5.1 | 7779308F3FF24100B3438EC67052A7B0 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Marysville | CA | 95901-8233 |  | 2013-08-30 | 2013-08-30 14:39 | 2013-08-30 15:04 | YORK - H1RA048S06D | 117 | 7.5 | Yes | Yes | 21.1 | 20.4 | 0.7 | DB1584FCD62544DEBEE2766ECE80C1FB |  | R22 | Non-TXV |  | 6.41% | 0.9359 | 12.32% | [5 empty] | Non-TXV | 6.41%
Parlier | CA | 93648-2338 |  | 2013-09-27 | 2013-09-27 18:25 | 2013-09-27 18:44 | CONCORD - CCU10A18A-1 | 60 | 2.2 | Yes | Yes | 16.5 | 19.3 | -2.8 | BB8B3FA277534BD2AE48DC3D7F78C40F |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Riverbank | CA | 95367-2664 |  | 2013-08-19 | 2013-08-19 15:21 | 2013-08-19 15:47 | RUUD - UAMC-036JAZ | 93 | 2.9 | Yes | Yes | 20.9 | 21.2 | -0.3 | 9BAB0A45FEFE4AD495EABF7E3F8E51BF |  | R22 | Non-TXV |  | 3.118% | 0.96882 | 5.993% | [5 empty] | Non-TXV | 3.118%
El Dorado Hills | CA | 95762-7800 |  | 2013-09-04 | 2013-09-04 17:26 | 2013-09-04 17:48 | NORDYNE - UNK | 132 | 21.8 | Yes | Yes | 20.7 | 23.1 | -2.4 | 6305173ADF2B4E9AA9AB984808484852 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.52% | 0.83485 | 31.74% | [5 empty] | Non-TXV | 16.52%
El Dorado Hills | CA | 95762-7800 |  | 2013-09-04 | 2013-09-04 18:13 | 2013-09-04 18:39 | NORDYNE - UNK | 138 | 31.9 | Yes | Yes | 20.7 | 21 | -0.3 | 34B01F7754D64C37A9A981172995767D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 23.12% | 0.76884 | 44.42% | [5 empty] | Non-TXV | 23.12%
Stockton | CA | 95204-3958 |  | 2013-08-02 | 2013-08-02 15:24 | 2013-08-02 15:42 | UNITARY PRODUCTS GROUP - TCGD18S21S2HA | 48 | 3.9 | Yes | Yes | 20.2 | 23.1 | -2.9 | 49C52522E5CE4BB19F7330A05EACEEC7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Los Banos | CA | 93635-2963 |  | 2013-08-05 | 2013-08-05 10:29 | 2013-08-05 10:31 | RUUD - 7777UNK | 104 | 3.3 | Yes | Yes | 19.1 | 19.3 | -0.2 | 352B81A14D5D4B27B36B05445BBAA35D |  | R22 | Non-TXV |  | 3.173% | 0.96827 | 6.098% | [5 empty] | Non-TXV | 3.173%
Paradise | CA | 95969-3303 |  | 2013-08-08 | 2013-08-08 09:44 | 2013-08-08 10:28 | OTHER - 480L002 | 50 | 8.4 | Yes | Yes | 17.4 | 20.3 | -2.9 | 552C91BFBBBC46EFB1B0832E03B1FD50 |  | R22 | Non-TXV |  | 16.8% | 0.832 | 32.29% | [5 empty] | Non-TXV | 16.8%
Fresno | CA | 93704-1615 |  | 2013-08-13 | 2013-08-13 14:45 | 2013-08-13 14:46 | AIRE-FLO - CA5542VKD1 | 98 | 12 | Yes | Yes | 24.3 | 23 | 1.3 | 5BF2FB5E77554A90B9BAEA9354DEE3F9 |  | R22 | Non-TXV |  | 12.24% | 0.87755 | 23.53% | [5 empty] | Non-TXV | 12.24%
Plymouth | CA | 95669-0000 |  | 2013-09-06 | 2013-09-06 10:42 | 2013-09-06 10:42 | PAYNE - 561AJX036000ABAA | 80 | 0 | Yes | Yes | 18.7 | 18.5 | 0.2 | FDFE50E9DE8F42E0A5CD10F8E854261A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-9708 |  | 2013-10-17 | 2013-10-17 10:34 | 2013-10-17 10:50 | GOODMAN - GSC13030CA | 106 | 3.9 | Yes | Yes | 25 | 20.4 | 4.6 | 285DF917E1524B4EA45BC6BA4774386D |  | R22 | TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | TXV | 3.679%
Grass Valley | CA | 95945-9704 |  | 2013-08-07 | 2013-08-07 14:25 | 2013-08-07 14:25 | OTHER - UNK | 86 | 0 | Yes | Yes | 21.2 | 21 | 0.2 | 0EFF1539798E4BAABA67D5433ED14A32 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Colfax | CA | 95713-9010 |  | 2013-08-16 | 2013-08-16 13:39 | 2013-08-16 13:55 | YORK - SHP48-6A | 95 | 3.7 | Yes | Yes | 19 | 21.9 | -2.9 | 497B51F5DDB941529AA3C48D13AB7E9B |  | R22 | Non-TXV |  | 3.895% | 0.96105 | 7.485% | [5 empty] | Non-TXV | 3.895%
Merced | CA | 95348-2845 |  | 2013-08-19 | 2013-08-19 13:27 | 2013-08-19 13:31 | PAYNE - PY1PN030040AAAA | 55 | -5.2 | Yes | Yes | 22 | 16.1 | 5.9 | 3212DF9E57574B33B3391C33E1446F9A |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Stockton | CA | 95204-3958 |  | 2013-08-05 | 2013-08-05 12:58 | 2013-08-05 13:18 | CARRIER - UNK | 64 | 2.4 | Yes | Yes | 22.4 | 18.8 | 3.6 | 25AE2A38155A402BAD492ADABDFC13AD |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Madera | CA | 93638-1781 |  | 2013-08-06 | 2013-08-06 18:11 | 2013-08-06 21:41 | BRYANT - 574BN40WO30040NB | 129 | 5.3 | Yes | Yes | 21.5 | 22.9 | -1.4 | FF389DA7C1D2457984283E50FD398FF6 |  | R22 | Non-TXV |  | 4.109% | 0.95891 | 7.896% | [5 empty] | Non-TXV | 4.109%
Marysville | CA | 95901-8201 |  | 2013-08-21 | 2013-08-21 16:56 | 2013-08-21 17:13 | HEIL - N2A336AKB200 | 85 | 3.9 | Yes | Yes | 16 | 18.8 | -2.8 | 56A09B5E000C404C97BE77ED65B43033 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Red Bluff | CA | 96080-4208 |  | 2013-08-27 | 2013-08-27 15:36 | 2013-08-27 18:18 | TRANE - 2YCC3036A1075AA | 82 | 3.4 | Yes | Yes | 18.1 | 20.4 | -2.3 | 551DF2E89D034659B3A1AF1E6FB79272 |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Riverbank | CA | 95361-7873 |  | 2013-08-19 | 2013-08-19 14:30 | 2013-08-19 14:57 | YORK - D1NA042N03606C | 76 | 2.3 | Yes | Yes | 22.2 | 16.6 | 5.6 | 65C6C365887D4723AC669FBF1FC2B43D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95209-4035 |  | 2013-08-01 | 2013-08-01 15:17 | 2013-08-01 15:39 | BDP - 585B024075YACR | 52 | 3.5 | Yes | Yes | 16.4 | 18.3 | -1.9 | E127EF9E0F2145FDBEAE790B213B0684 |  | R22 | Non-TXV |  | 6.731% | 0.93269 | 12.94% | [5 empty] | Non-TXV | 6.731%
Parlier | CA | 93648-2338 |  | 2013-09-30 | 2013-09-30 17:30 | 2013-09-30 18:00 | CONCORD - CCU10A24A-1 | 50 | 4.9 | Yes | Yes | 18.5 | 20.4 | -1.9 | FAFEC746004F49D790580BB6FD9C0139 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | Non-TXV | 9.8%
West Point | CA | 95255-9776 |  | 2013-09-05 | 2013-09-05 10:16 | 2013-09-05 10:38 | GIBSON - GR4GA024KO45X | 70 | 4 | Yes | Yes | 18.7 | 19.6 | -0.9 | 1662504DEDFD479494026DAC52193B54 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Fresno | CA | 93702-2510 |  | 2013-08-12 | 2013-08-12 10:12 | 2013-08-12 15:54 | AMERICAN STANDARD - YCY048G1HOAD | 187 | 8.7 | Yes | Yes | 19.5 | 19.5 | 0 | 36390365A12C49D3B469A35BE1B80E85 |  | R22 | Non-TXV |  | 4.652% | 0.95348 | 8.941% | [5 empty] | Non-TXV | 4.652%
Merced | CA | 95348-3123 |  | 2013-09-04 | 2013-09-04 11:32 | 2013-09-04 11:34 | GOODMAN - CPKE241AB | 106 | 8.8 | Yes | Yes | 14.6 | 17.2 | -2.6 | 29B46A7559AF4149AEBB175A26E50384 |  | R22 | Non-TXV |  | 8.302% | 0.91698 | 15.95% | [5 empty] | Non-TXV | 8.302%
Sanger | CA | 93657-8627 |  | 2013-10-01 | 2013-10-01 12:22 | 2013-10-01 12:47 | GOODMAN - CRT36-1A | 140 | 11.5 | Yes | Yes | 18 | 19.6 | -1.6 | 0E14BD7867C74C8797BF2A9A57929D36 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.214% | 0.91786 | 15.79% | [5 empty] | Non-TXV | 8.214%
Oakdale | CA | 95361-4161 |  | 2013-08-28 | 2013-08-28 15:05 | 2013-08-28 15:29 | DAY & NIGHT - CBD | 64 | 2.1 | Yes | Yes | 20.2 | 19.3 | 0.9 | 8CCD4276BC114EBE82F7876840637942 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Stockton | CA | 95212-3050 |  | 2013-08-07 | 2013-08-07 12:19 | 2013-08-07 12:41 | YORK - H1RD048S06H | 227 | 8 | Yes | Yes | 17.4 | 20.1 | -2.7 | 8693D2A152054B0AB04918240F080CCF |  | R22 | Non-TXV |  | 3.524% | 0.96476 | 6.773% | [5 empty] | Non-TXV | 3.524%
Fresno | CA | 93706-1302 |  | 2013-08-27 | 2013-08-27 10:22 | 2013-08-27 10:24 | GOODMAN - GPG1336045M41AB | 85 | 2.7 | Yes | Yes | 21.6 | 18 | 3.6 | 2C38BF02A40F4EC39381DA6A6C6D004A |  | R410A | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Selma | CA | 93662-2447 |  | 2013-08-05 | 2013-08-05 10:02 | 2013-08-05 10:31 | RUUD - N/A | 90 | 11.8 | Yes | Yes | 20 | 20.4 | -0.4 | F179E3249FF74AA8B2AC932AC2802AE9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.11% | 0.86889 | 25.2% | [5 empty] | Non-TXV | 13.11%
Fresno | CA | 93722-2418 |  | 2013-08-07 | 2013-08-07 12:15 | 2013-08-07 12:18 | LENNOX - 12ACB36-5P | 103 | 3.1 | Yes | Yes | 18.7 | 18.1 | 0.6 | DCB8D35347CE4AC785F57F28D1E54262 |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Parlier | CA | 93648-2338 |  | 2013-08-28 | 2013-08-28 09:41 | 2013-08-28 10:12 | CONCORD - CCU1018A-2 | 60 | 3 | Yes | Yes | 20 | 20.4 | -0.4 | CAF3435AFF8F4973A8B1DF5AF24A2773 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Winton | CA | 95388-9537 |  | 2013-08-15 | 2013-08-15 13:28 | 2013-08-15 13:50 | BRYANT - 582ANW036060AAF | 56 | 2.4 | Yes | Yes | 20.3 | 19.7 | 0.6 | DB604FE0043245D9BAAD353EF88CC513 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Paradise | CA | 95969-5218 |  | 2013-08-08 | 2013-08-08 10:30 | 2013-08-08 11:29 | CARRIER - 480L003 | 54 | 3.4 | Yes | Yes | 26 | 21.4 | 4.6 | C9BC30AB20894DA4B467C5805F5A809C |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Atwater | CA | 95301-3733 |  | 2013-08-13 | 2013-08-13 12:36 | 2013-08-13 13:07 | YORK - D2NY036N05606A | 120 | 6.1 | Yes | Yes | 19.1 | 21.7 | -2.6 | 680A63C406D845B4BAA55567A2D45149 |  | R410A | Non-TXV |  | 5.083% | 0.94917 | 9.769% | [5 empty] | Non-TXV | 5.083%
Madera | CA | 93638-2253 |  | 2013-09-05 | 2013-09-05 13:12 | 2013-09-05 13:13 | WEATHER KING - 12AJA03601 | 117 | 15.7 | Yes | Yes | 22.4 | 20.4 | 2 | 7732EEC66992440F94B727A782A4779C |  | R22 | Non-TXV |  | 13.42% | 0.86581 | 25.79% | [5 empty] | Non-TXV | 13.42%
Merced | CA | 95340-3037 |  | 2013-08-06 | 2013-08-06 16:02 | 2013-08-06 16:30 | PAYNE - PY3PNA036090NB | 114 | 3.5 | Yes | Yes | 22.5 | 20.4 | 2.1 | 31FB531AA96F4B0F812EECD2310C72AC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
Loomis | CA | 95650-9711 |  | 2013-08-14 | 2013-08-14 15:51 | 2013-08-14 16:14 | CARRIER - 38TH042310 | 112 | 5.1 | Yes | Yes | 23 | 20.9 | 2.1 | B270C3DFBBFE402A9051A9B6128FD0E1 |  | R22 | TXV |  | 4.554% | 0.95446 | 8.751% | [5 empty] | TXV | 4.554%
Cameron Park | CA | 95682-9220 |  | 2013-08-30 | 2013-08-30 11:24 | 2013-08-30 11:41 | DAY & NIGHT - 543EJ024 | 100 | 3 | Yes | Yes | 22 | 21 | 1 | 98C95680D8964F91BFCA21B9B79AAF85 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Sanger | CA | 93657-2223 |  | 2013-08-07 | 2013-08-07 12:43 | 2013-08-07 13:18 | DAY & NIGHT - 30/80YAC 106T | 85 | 6.8 | Yes | Yes | 17.6 | 18.3 | -0.7 | 09F775E56547466A80976FE05D3843DF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Manteca | CA | 95336-5908 |  | 2013-08-12 | 2013-08-12 15:38 | 2013-08-12 15:58 | RHEEM - RRMA-A042JK08X | 114 | 3.6 | Yes | Yes | 20.1 | 20.4 | -0.3 | 228757879E8A40559B4476AEC30EDDE4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Sanger | CA | 93657-9213 |  | 2013-08-03 | 2013-08-03 14:55 | 2013-08-03 18:03 | AMERICAN STANDARD - YCP048F1H0AB | 166 | 5.3 | Yes | Yes | 18.8 | 19 | -0.2 | C8E8E70EB7704AE7B99243A1C1208C8B |  | R22 | Non-TXV |  | 3.193% | 0.96807 | 6.136% | [5 empty] | Non-TXV | 3.193%
Fresno | CA | 93723-9205 |  | 2013-08-16 | 2013-08-16 14:47 | 2013-08-16 14:52 | OTHER - UNK | 77 | 8.5 | Yes | Yes | 24.3 | 23.5 | 0.8 | 65CB2F5573104049B477CB968BCF0740 |  | R22 | Non-TXV |  | 11.04% | 0.88961 | 21.21% | [5 empty] | Non-TXV | 11.04%
Chico | CA | 95928-3832 |  | 2013-08-08 | 2013-08-08 09:27 | 2013-08-08 09:50 | LENNOX - 13ACC-036-230-01 | 115 | 12.6 | Yes | Yes | 23.4 | 21 | 2.4 | AFD633ED743F445380508C2E72E9D90E |  | R22 | TXV |  | 10.96% | 0.89043 | 21.06% | [5 empty] | TXV | 10.96%
Madera | CA | 93638-2294 |  | 2013-08-07 | 2013-08-07 15:43 | 2013-08-07 15:43 | GOODMAN - CLJ42-B | 84 | 0 | Yes | Yes | 19.3 | 19.7 | -0.4 | 11E48E4D610542CC9031ABFC1FED4369 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mariposa | CA | 95338-9775 |  | 2013-09-11 | 2013-09-11 15:00 | 2013-09-11 15:01 | ALLEGIANCE - 2A7A3048A1000AA | 142 | 15.7 | Yes | Yes | 27.6 | 22.6 | 5 | 4F9BBBA815CF418B97C20C8E45EF6ED1 |  | R22 | Non-TXV |  | 11.06% | 0.88944 | 21.25% | [5 empty] | Non-TXV | 11.06%
Madera | CA | 93638-4200 |  | 2013-09-04 | 2013-09-04 15:49 | 2013-09-04 15:51 | OTHER - TCG36S21S1H1 | 65 | 2.9 | Yes | Yes | 22.7 | 20.6 | 2.1 | A4F269A5405E4690995FEAF7BA82990E |  | R22 | Non-TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | Non-TXV | 4.462%
Sanger | CA | 93657-2738 |  | 2013-08-05 | 2013-08-05 17:16 | 2013-08-05 18:10 | UNITARY PRODUCTS GROUP - N2A336AKA200 | 88 | 4.6 | Yes | Yes | 20.5 | 19.7 | 0.8 | A754C62179BD41C595A3FB00E5100D5F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Chowchilla | CA | 93610-9798 |  | 2013-08-14 | 2013-08-14 13:57 | 2013-08-14 13:58 | GOODMAN - PGJ0300501B | 70 | 6.3 | Yes | Yes | 24.7 | 21.3 | 3.4 | 5F81D98BD2874C1C90B4FB42CE9A2295 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Fresno | CA | 93722-6112 |  | 2013-08-09 | 2013-08-09 14:12 | 2013-08-09 14:14 | YORK - D1NP048N09006A | 132 | 3.9 | Yes | Yes | 21.4 | 18.8 | 2.6 | 571E5CB33A0948C5A27EA3003850AF4F |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Lincoln | CA | 95648-3227 |  | 2013-08-06 | 2013-08-06 17:58 | 2013-08-06 18:23 | CARRIER - 38ETG048300 | 152 | -11.3 | Yes | Yes | 16.4 | 19.2 | -2.8 | 4013B97B9B6D4EE686727575F41F77F8 |  | R410A | TXV |  | -7.434% | 1.0743 | 2.082% |  |  |  |  | TXV |  |  | -7.434%
Fresno | CA | 93722-4130 |  | 2013-08-09 | 2013-08-09 11:49 | 2013-08-09 11:49 | DAY & NIGHT - 7777UNK | 100 | 0 | Yes | Yes | 20.4 | 18.8 | 1.6 | 48074962AC474445A1CF3F23AE9A4639 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-3220 |  | 2013-08-14 | 2013-08-14 17:13 | 2013-08-14 20:40 | CARRIER - 591ANX030000ABAA | 67 | 2.1 | Yes | Yes | 21.5 | 20.7 | 0.9 | 7366347A883E4FBF8426EFDD6B127AB8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Merced | CA | 95340-4217 |  | 2013-08-07 | 2013-08-07 12:46 | 2013-08-07 13:20 | OTHER - 60WE24G1 | 55 | 2.9 | Yes | Yes | 22 | 20.8 | 1.2 | CB8B384F96E04427A8A0F5D7F795A6CD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.273% | 0.94727 | 10.13% | [5 empty] | Non-TXV | 5.273%
Fresno | CA | 93710-4625 |  | 2013-08-10 | 2013-08-10 10:52 | 2013-08-10 11:15 | BDP - 48RCD108 | 103 | 3.8 | Yes | Yes | 17 | 19.2 | -2.2 | A919CFCE818149DAAC582E54E87677A5 |  | R22 | Non-TXV |  | 3.689% | 0.96311 | 7.09% | [5 empty] | Non-TXV | 3.689%
Fresno | CA | 93727-6487 |  | 2013-08-12 | 2013-08-12 15:02 | 2013-08-12 15:24 | LENNOX - 12ACB42-5P | 125 | 4.1 | Yes | Yes | 20.5 | 18.4 | 2.1 | 515B4E6746554A43AAEF41351111425C |  | R22 | Non-TXV |  | 3.28% | 0.9672 | 6.303% | [5 empty] | Non-TXV | 3.28%
Los Banos | CA | 93635-5444 |  | 2013-08-01 | 2013-08-01 16:01 | 2013-08-01 16:05 | CARRIER - 38HD048300 | 45 | 1.8 | Yes | Yes | 21.4 | 19.8 | 1.6 | 0F8F4F5471054529AAF0C2F1FB2210F0 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Clovis | CA | 93611-5928 |  | 2013-08-06 | 2013-08-06 10:34 | 2013-08-06 10:36 | BDP - 585HJW036060ABAF | 102 | 13.4 | Yes | Yes | 22.9 | 21.5 | 1.4 | BCA09F5E101C42BFBF4998457545060D |  | R22 | Non-TXV |  | 13.14% | 0.86863 | 25.25% | [5 empty] | Non-TXV | 13.14%
Clovis | CA | 93612-4912 |  | 2013-08-16 | 2013-08-16 13:35 | 2013-08-16 15:06 | TRANE - 4CC03030B1075AAY | 98 | 4.7 | Yes | Yes | 22 | 17.7 | 4.3 | B215F4CC90394B50B40AF30EC0A96024 |  | R410A | TXV |  | 4.796% | 0.95204 | 9.217% | [5 empty] | TXV | 4.796%
Atwater | CA | 95301-4819 |  | 2013-09-10 | 2013-09-10 13:52 | 2013-09-10 14:11 | OTHER - TZAA-330-2A | 98 | 6.9 | Yes | Yes | 20.5 | 20.9 | -0.4 | 30E3CA27AF4E4D07BCD15FF12CCB4407 |  | R22 | Non-TXV |  | 7.041% | 0.92959 | 13.53% | [5 empty] | Non-TXV | 7.041%
Paso Robles | CA | 93446-4751 |  | 2013-08-06 | 2013-08-06 11:08 | 2013-08-06 11:36 | BRYANT - 561CJ030-C | 76 | 2.3 | Yes | Yes | 19.9 | 19.3 | 0.6 | FBCE0B248C914D79A9F3AA71C561347F |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Oroville | CA | 95965-4203 |  | 2013-08-28 | 2013-08-28 10:31 | 2013-08-28 11:24 | AMANA - PGD30C0702E | 74 | 3.7 | Yes | Yes | 22.1 | 17.2 | 4.9 | 5FB89C66A863463F9DDF2AE3643E8C90 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Marysville | CA | 95901-8308 |  | 2013-08-21 | 2013-08-21 12:30 | 2013-08-21 12:46 | LENNOX - 13ACD-048-230 | 152 | 5.7 | Yes | Yes | 24 | 19.5 | 4.5 | ECD831F11E764141B99DBFD3EC98B050 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Stockton | CA | 95212-3218 |  | 2013-08-08 | 2013-08-08 12:23 | 2013-08-08 12:45 | CARRIER - 38CKC042340 | 80 | 9.1 | Yes | Yes | 19.5 | 17.7 | 1.8 | 313163BDEC3849968E6F4E90CA08F34F |  | R22 | TXV |  | 11.38% | 0.88625 | 21.86% | [5 empty] | TXV | 11.38%
Stockton | CA | 95209-1919 |  | 2013-08-02 | 2013-08-02 10:20 | 2013-08-02 10:39 | OTHER - UNK | 50 | 1.6 | Yes | Yes | 21.9 | 18.2 | 3.7 | C5F8ADE3849B4FF78038DBBFC01FDCF2 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Merced | CA | 95348-1602 |  | 2013-08-23 | 2013-08-23 13:03 | 2013-08-23 13:05 | GOODMAN - GPG13240701BB | 77 | 3.4 | Yes | Yes | 20.2 | 20.4 | -0.2 | 617A030C72744DB0B580F10CBC5C7CAC |  | R22 | Non-TXV |  | 4.416% | 0.95584 | 8.486% | [5 empty] | Non-TXV | 4.416%
Merced | CA | 95340-4226 |  | 2013-08-07 | 2013-08-07 14:45 | 2013-08-07 15:07 | - PGB24C0702D | 64 | 1.9 | Yes | Yes | 28.6 | 22.8 | 5.8 | 643C80076AE74D6A8A15AF7FC7E2A017 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Stockton | CA | 95207-4165 |  | 2013-08-09 | 2013-08-09 10:53 | 2013-08-09 11:13 | BDP - 585CJ036075 | 84 | 8.5 | Yes | Yes | 19.6 | 18.6 | 1.1 | CAF1D12F9F344C5B86F5502FE067BBF4 |  | R22 | Non-TXV |  | 10.12% | 0.89881 | 19.45% | [5 empty] | Non-TXV | 10.12%
Chico | CA | 95973-0591 |  | 2013-10-11 | 2013-10-11 11:39 | 2013-10-11 12:01 | GIBSON - JS3BA-018KA | 63 | 7 | Yes | Yes | 25.2 | 20.3 | 4.9 | 3E24C5231D9A496EAC566A3E7C51FE81 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Riverbank | CA | 95367-3149 |  | 2013-08-29 | 2013-08-29 11:31 | 2013-08-29 11:54 | DAY & NIGHT - 587AWZ024040AAAE | 64 | 2 | Yes | Yes | 20 | 21.9 | -1.9 | 6E04CE94BC784BFDAAAD65201CE7960A |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93726-6306 |  | 2013-08-13 | 2013-08-13 09:41 | 2013-08-13 09:58 | PAYNE - PY2PNB042060BAA | 118 | 3.5 | Yes | Yes | 22.5 | 19.9 | 2.6 | B32E25B044BD4D869DE3986B4AC6F6C2 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Mariposa | CA | 95338-9709 |  | 2013-08-02 | 2013-08-02 14:05 | 2013-08-02 14:07 | ICP - PGF348080K01A1 | 208 | 6.9 | Yes | Yes | 25.8 | 22.6 | 3.2 | 744F41E13D43462CA0B4C47D6840B277 |  | R22 | Non-TXV |  | 3.317% | 0.96683 | 6.375% | [5 empty] | Non-TXV | 3.317%
Fresno | CA | 93727-7372 |  | 2013-08-27 | 2013-08-27 17:54 | 2013-08-27 20:27 | RHEEM - RRKA-A036JK06E | 62 | 4.7 | Yes | Yes | 24.5 | 20.1 | 4.5 | D08544ED3A1448779B11659BA3F2C4BA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.581% | 0.92419 | 14.57% | [5 empty] | Non-TXV | 7.581%
Merced | CA | 95348-8716 |  | 2013-08-09 | 2013-08-09 13:38 | 2013-08-09 14:02 | GOODMAN - CKL60-1L | 115 | 7.9 | Yes | Yes | 22.2 | 19.8 | 2.4 | E4C3C8F075124117A304F68EF5113367 |  | R22 | Non-TXV |  | 6.87% | 0.9313 | 13.2% | [5 empty] | Non-TXV | 6.87%
Sanger | CA | 93657-2256 |  | 2013-08-06 | 2013-08-06 18:18 | 2013-08-06 18:58 | RHEEM - RRPL-B036JK06X | 92 | 3.9 | Yes | Yes | 21 | 19.5 | 1.5 | CA4CE9B11D8E4C8F93770CCFBDD8A571 |  | R410A | TXV |  | 4.239% | 0.95761 | 8.147% | [5 empty] | TXV | 4.239%
Riverbank | CA | 95367-3034 |  | 2013-08-20 | 2013-08-20 12:57 | 2013-08-20 13:20 | RUUD - UAFD-031JAS | 64 | 2.1 | Yes | Yes | 22.4 | 19.1 | 3.3 | E0A66631250D4DFBA6468F6276B9CD96 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Merced | CA | 95348-2545 |  | 2013-08-20 | 2013-08-20 13:50 | 2013-08-20 13:52 | GOODMAN - PGJ03625504 | 81 | 2.4 | Yes | Yes | 20.6 | 19.1 | 1.6 | E5CF1D400C3B456487BAFED5DD58CBB0 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Chico | CA | 95973-0000 |  | 2013-08-02 | 2013-08-02 12:28 | 2013-08-02 12:46 | LENNOX - 13ACD-036-230-02 | 111 | 4.9 | Yes | Yes | 22.8 | 19.9 | 2.9 | E34932E720704FF697BD1D9C4D88151E |  | R22 | Non-TXV |  | 4.414% | 0.95586 | 8.484% | [5 empty] | Non-TXV | 4.414%
Fresno | CA | 93726-3525 |  | 2013-08-20 | 2013-08-20 13:57 | 2013-08-20 14:14 | WESTINGHOUSE - UNK | 55 | 4.2 | Yes | Yes | 20.7 | 18.5 | 2.2 | 30694AF3AE5D46B29C97BBC5EBA71902 |  | R22 | Non-TXV |  | 7.636% | 0.92364 | 14.68% | [5 empty] | Non-TXV | 7.636%
Chico | CA | 95973-0591 |  | 2013-09-04 | 2013-09-04 13:54 | 2013-09-04 17:31 | PAYNE - 565BJ018 | 55 | 7.1 | Yes | Yes | 15.9 | 17.9 | -2 | 7D5EAC2D626A4FD9A7BC63B11ED0CC31 |  | R22 | Non-TXV |  | 12.91% | 0.87091 | 24.81% | [5 empty] | Non-TXV | 12.91%
Oroville | CA | 95965-3552 |  | 2013-08-06 | 2013-08-06 10:03 | 2013-08-06 10:54 | RUUD - RRNA-B042JK10E | 104 | 6.1 | Yes | Yes | 16.5 | 18.5 | -2 | 16E3879B1BA24ED6B6D6A85CBAEA167D |  | R22 | Non-TXV |  | 5.865% | 0.94135 | 11.27% | [5 empty] | Non-TXV | 5.865%
Marysville | CA | 95901-6222 |  | 2013-08-08 | 2013-08-08 16:17 | 2013-08-08 16:17 | BRYANT - 574DNW024060NA | 105 | 0 | Yes | Yes | 22 | 20.6 | 1.4 | A6092495863448ABAE1E6F3FBD1305AF |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5578 |  | 2013-08-08 | 2013-08-08 12:18 | 2013-08-08 12:20 | OTHER - 7777UNK | 100 | 3 | Yes | Yes | 19.3 | 20.4 | -1.1 | 16FFB90D03D541FB86DCD97126F5179E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95207-4008 |  | 2013-08-09 | 2013-08-09 12:44 | 2013-08-09 13:05 | BRYANT - UNK | 64 | 3.8 | Yes | Yes | 15.6 | 18.1 | -2.5 | 7A9FAC0C83B44AA09E98B3E7D8AA48D6 |  | R22 | Non-TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | Non-TXV | 5.938%
Atascadero | CA | 93422-7845 |  | 2013-08-07 | 2013-08-07 17:42 | 2013-08-07 18:01 | INTERTHERM - CNS368 | 40 | -2.8 | Yes | Yes | 24 | 20.9 | 3.1 | E67ADCBE706B4687AA8F6FD5AD1626BE |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93705-0813 |  | 2013-08-13 | 2013-08-13 10:22 | 2013-08-13 10:23 | GOODMAN - PGB030056 | 56 | 8.4 | Yes | Yes | 22.9 | 17.1 | 5.8 | C4FBC1F0E58E4E409F675A5BFBF4C953 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Red Bluff | CA | 96080-3025 |  | 2013-08-09 | 2013-08-09 11:15 | 2013-08-09 12:30 | DAY & NIGHT - N2A336AKB300 | 85 | -15.5 | Yes | Yes | 17.6 | 19.8 | -2.2 | 58D97C5367CE47BA8AC8CD2D4B6B8407 |  | R22 | TXV |  | -18.24% | 1.1824 | 5.107% |  |  |  |  | TXV |  |  | -18.24%
Parlier | CA | 93648-2337 |  | 2013-09-30 | 2013-09-30 18:02 | 2013-09-30 19:39 | CONCORD - CCU10A24A-1 | 50 | 9.8 | Yes | Yes | 17 | 19.8 | -2.8 | 795E878E6AB84314B0BD371FFFF47803 |  | R22 | Non-TXV |  | 19.6% | 0.804 | 37.67% | [5 empty] | Non-TXV | 19.6%
Stockton | CA | 95205-6506 |  | 2013-08-02 | 2013-08-02 16:04 | 2013-08-02 16:32 | TRANE - TZAA-330-2A | 98 | 9.6 | Yes | Yes | 24.9 | 20.8 | 4.1 | C003223325DF4F8CAF1A9BD41D05455C |  | R22 | TXV |  | 9.796% | 0.90204 | 18.83% | [5 empty] | TXV | 9.796%
Atwater | CA | 95301-4285 |  | 2013-08-27 | 2013-08-27 09:52 | 2013-08-27 10:37 | GOODMAN - CKL42-1B | 115 | 3.5 | Yes | Yes | 17.8 | 18.2 | -0.4 | EE5B29CE80F544B4825F5419F8AE3595 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Manteca | CA | 95336-7038 |  | 2013-08-02 | 2013-08-02 13:54 | 2013-08-02 14:14 | BRYANT - 563CN042-C | 104 | 3.1 | Yes | Yes | 20.1 | 20.9 | -0.8 | F73205CBDCD34AE7AD1EF7BF9D018C3F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Parlier | CA | 93648-2338 |  | 2013-09-09 | 2013-09-09 17:12 | 2013-09-09 18:08 | CONCORD - CCU10A30A-1 | 60 | 4.4 | Yes | Yes | 18 | 20.1 | -2.1 | 55570EE1EF1B4346B7E402BC12FC9D43 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Fresno | CA | 93722-4231 |  | 2013-11-20 | 2013-11-20 09:46 | 2013-11-20 09:46 | DAY & NIGHT - UNK | 110 | 0 | Yes | Yes | 27 | 19.7 | 7.4 | 813C54900229472DAA81682B04882671 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3630 |  | 2013-08-06 | 2013-08-06 13:31 | 2013-08-06 13:33 | YORK - 04CG048N06206A | 102 | 3.2 | Yes | Yes | 20.3 | 20.8 | -0.5 | 1DD37ECC406043D798C04DCCAF36567E |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Fresno | CA | 93711-1712 |  | 2013-08-10 | 2013-08-10 10:26 | 2013-08-10 10:29 | PAYNE - PY3GNAA30040NA | 98 | 3.2 | Yes | Yes | 22.7 | 19.4 | 3.3 | 4E4A710D32A24191862158F9BC44DA5F |  | R410A | Non-TXV |  | 3.265% | 0.96735 | 6.275% | [5 empty] | Non-TXV | 3.265%
Fresno | CA | 93711-1712 |  | 2013-08-10 | 2013-08-10 10:40 | 2013-08-10 10:43 | GOODMAN - GPG1360090M41AC | 185 | 5.6 | Yes | Yes | 24.8 | 18.8 | 6 | 9C01830753CE4AB08DEA21BEC874F6F7 |  | R410A | Non-TXV |  | 3.027% | 0.96973 | 5.817% | [5 empty] | Non-TXV | 3.027%
Fresno | CA | 93704-4547 |  | 2013-08-09 | 2013-08-09 12:35 | 2013-08-09 12:37 | YORK - D1NH036N05606C | 108 | 10.8 | Yes | Yes | 26.1 | 20.2 | 5.9 | 618FAB9200FC4C6E920A536739269868 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Chico | CA | 95973-9106 |  | 2013-08-20 | 2013-08-20 12:59 | 2013-08-20 19:29 | RHEEM - NA | 66 | 4.4 | Yes | Yes | 16.5 | 19.1 | -2.6 | 1EA6148140184D22AEC3A7C390460339 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Manteca | CA | 95336-2954 |  | 2013-08-02 | 2013-08-02 12:44 | 2013-08-02 13:22 | AMANA - RCE42C2A | 230 | 7 | Yes | Yes | 19.8 | 20.1 | -0.3 | 8DBFB16473F04C17906B9F454C87023B |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Sanger | CA | 93657-4245 |  | 2013-08-05 | 2013-08-05 15:08 | 2013-08-05 16:07 | GOODMAN - CK60-1C | 122 | 6.1 | Yes | Yes | 18.6 | 20.2 | -1.6 | 0F83F3507A81477595077D6E00A1742A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Merced | CA | 95348-3716 |  | 2013-08-09 | 2013-08-09 17:27 | 2013-08-09 17:52 | RHEEM - RRNA-B036JK06X | 83 | 2.7 | Yes | Yes | 21 | 18.6 | 2.4 | C08E9CC0F4C84BF4AAF7B9D7A52BD26B |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Atascadero | CA | 93422-5819 |  | 2013-08-08 | 2013-08-08 10:35 | 2013-08-08 10:52 | COLEMAN - 9541-90 | 56 | -3.3 | Yes | Yes | 23.2 | 18.2 | 5 | A7AE434BA14546F782351F0E129CA064 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Stockton | CA | 95206-6411 |  | 2013-08-19 | 2013-08-19 08:49 | 2013-08-19 09:11 | GOODMAN - CKL42-1A | 95 | 13.7 | Yes | Yes | 17.7 | 19.9 | -2.2 | 9D7E86AA607545C2AA26217345F2C1C6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.42% | 0.85579 | 27.71% | [5 empty] | Non-TXV | 14.42%
Olivehurst | CA | 95961-9039 |  | 2013-08-30 | 2013-08-30 12:53 | 2013-08-30 13:13 | CARRIER - 38BRC036340 | 101 | 3 | Yes | Yes | 23.1 | 18.8 | 4.3 | 8261AA20647F476895B0F9C0D3BEFD57 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Sanger | CA | 93657-4243 |  | 2013-08-10 | 2013-08-10 12:43 | 2013-08-10 13:04 | GOODMAN - GCS140481AE | 189 | 5.6 | Yes | Yes | 19 | 20.3 | -1.3 | C9AE29285CAE4CD09BEFAE4E4302C114 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Hamilton City | CA | 95951-0000 |  | 2013-09-23 | 2013-09-23 10:32 | 2013-09-23 11:09 | DAY & NIGHT - NA | 70 | 11 | Yes | Yes | 14.2 | 17.2 | -3 | 6F9E22AEF31D4DBCB61C330CC3BF3E1A |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Stockton | CA | 95219-5488 |  | 2013-08-07 | 2013-08-07 09:08 | 2013-08-07 09:32 | CARRIER - 38EN018310SM | 55 | 6.7 | Yes | Yes | 20 | 18.2 | 1.8 | 209F3AD814AB4B18B20B725DC0E94D10 |  | R22 | Non-TXV |  | 12.18% | 0.87818 | 23.41% | [5 empty] | Non-TXV | 12.18%
Chico | CA | 95973-0590 |  | 2013-09-19 | 2013-09-19 13:18 | 2013-09-19 13:35 | PAYNE - NA | 56 | 4 | Yes | Yes | 22.7 | 20.6 | 2.1 | 54FFDEFB06FC4348864AF149EADF2CC4 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Merced | CA | 95340-0971 |  | 2013-08-05 | 2013-08-05 14:04 | 2013-08-05 14:33 | GOODMAN - GPG1324045M41AA | 80 | 12.2 | Yes | Yes | 22.8 | 19.9 | 2.9 | C2CBE8A3EA384EDCAEB41EA1767F0108 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 15.25% | 0.8475 | 29.31% | [5 empty] | Non-TXV | 15.25%
Atascadero | CA | 93422-5853 |  | 2013-08-07 | 2013-08-07 13:31 | 2013-08-07 13:48 | COLEMAN - 9530F901 | 54 | -3.2 | Yes | Yes | 18.3 | 18.8 | -0.5 | 68C3B618F2A14FD9B322F5C61438687F |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Sanger | CA | 93657-0000 |  | 2013-08-06 | 2013-08-06 13:15 | 2013-08-06 14:18 | UNITARY PRODUCTS GROUP - TCGD42S21S2HA | 66 | 2.8 | Yes | Yes | 26 | 20.3 | 5.7 | D5EB2B8CE6F64B4F82C56F45BECB78D1 |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Oakdale | CA | 95361-3214 |  | 2013-09-11 | 2013-09-11 13:14 | 2013-09-11 13:46 | YORK - SA30G080-6G | 44 | 1.4 | Yes | Yes | 22.4 | 20.4 | 2 | 3B12554C9CC244CD9AC39F7A895F520B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Merced | CA | 95340-9378 |  | 2013-08-09 | 2013-08-09 08:38 | 2013-08-09 09:01 | RUUD - URGG05E37JKR | 77 | 2.4 | Yes | Yes | 21.6 | 19.1 | 2.5 | 77354ACA87D44266991B0E5744EB1890 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Stockton | CA | 95209-2184 |  | 2013-08-21 | 2013-08-21 09:48 | 2013-08-21 10:05 | HEIL - PGC024K060D | 58 | 1.8 | Yes | Yes | 19.8 | 17.9 | 1.9 | F6F30519747446B6A54033A5A5529ECC |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Stockton | CA | 95209-2184 |  | 2013-08-21 | 2013-08-21 10:07 | 2013-08-21 10:26 | HEIL - PGC024K060E | 54 | 4.5 | Yes | Yes | 16.6 | 15.8 | 0.8 | F900BBD5D722462BA5DA3513761D9237 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Fresno | CA | 93704-4338 |  | 2013-08-09 | 2013-08-09 11:58 | 2013-08-09 12:13 | RHEEM - RRKAA036JK06X | 62 | 9.2 | Yes | Yes | 22.1 | 20.4 | 1.7 | 4B88A29147194981A1DC5A6A169DE80C |  | R22 | Non-TXV |  | 14.84% | 0.85161 | 28.52% | [5 empty] | Non-TXV | 14.84%
Cool | CA | 95614-2132 |  | 2013-08-13 | 2013-08-13 10:52 | 2013-08-13 11:10 | PAYNE - 591ANX042000ABAA | 112 | 18.8 | Yes | Yes | 24.6 | 20.9 | 3.7 | DB211CA3BB7E43D4AFC76E12A3F56E0E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.79% | 0.83214 | 32.26% | [5 empty] | Non-TXV | 16.79%
Valley Springs | CA | 95252-9558 |  | 2013-08-20 | 2013-08-20 12:38 | 2013-08-20 12:55 | CARRIER - 38CKC036350 | 70 | 4.1 | Yes | Yes | 25.7 | 21 | 4.7 | 46B32B6DB0054513AB0824789B379F85 |  | R22 | Non-TXV |  | 5.857% | 0.94143 | 11.26% | [5 empty] | Non-TXV | 5.857%
Atwater | CA | 95301-9724 |  | 2013-08-15 | 2013-08-15 09:13 | 2013-08-15 09:31 | COLEMAN - DAYP-F030N070A | 73 | 2.3 | Yes | Yes | 20.9 | 18.7 | 2.2 | C21FAD48C7994B4BA7ED5D0B12FE695C |  | R22 | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Stockton | CA | 95212-0000 |  | 2013-08-08 | 2013-08-08 10:09 | 2013-08-08 10:30 | CARRIER - 38CKC042350 | 93 | 5.3 | Yes | Yes | 17.2 | 18.2 | -1 | E96412D3649948138FD79C59F6CECDA4 |  | R22 | Non-TXV |  | 5.699% | 0.94301 | 10.95% | [5 empty] | Non-TXV | 5.699%
Riverdale | CA | 93656-9798 |  | 2013-10-03 | 2013-10-03 17:32 | 2013-10-03 18:09 | GOODMAN - GPG1342701AB | 105 | 3.6 | Yes | Yes | 20.5 | 20.1 | 0.4 | 1C78196E8D774AD69C1518C47DBAB530 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Stockton | CA | 95204-4406 |  | 2013-08-09 | 2013-08-09 14:21 | 2013-08-09 14:42 | CARRIER - UNK | 64 | 7 | Yes | Yes | 22.2 | 19.5 | 2.7 | D2C2641F40864400BA65E10B896B6736 |  | R22 | Non-TXV |  | 10.94% | 0.89062 | 21.02% | [5 empty] | Non-TXV | 10.94%
Yuba City | CA | 95993-6002 |  | 2013-08-28 | 2013-08-28 14:25 | 2013-08-28 14:49 | CARRIER - 48GS-024060301 | 55 | 4.3 | Yes | Yes | 20 | 21.9 | -1.9 | 4568254E058D47DC8878485D4E948A66 |  | R22 | TXV |  | 7.818% | 0.92182 | 15.02% | [5 empty] | TXV | 7.818%
Atwater | CA | 95301-9724 |  | 2013-08-14 | 2013-08-14 15:38 | 2013-08-14 15:57 | AMANA - RCC36A2D | 114 | -10.7 | Yes | Yes | 24.9 | 20.4 | 4.5 | BE2CAE79E83343A29E408559DA6DD6A3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.386% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.386%
Auburn | CA | 95603-3741 |  | 2013-09-03 | 2013-09-03 12:35 | 2013-09-03 12:53 | OTHER - 7B0023B100A1 | 54 | 10.7 | Yes | Yes | 17 | 19.8 | -2.8 | B1C5AF328E34406DAC26FF633A605100 |  | R22 | TXV |  | 19.81% | 0.80185 | 38.08% | [5 empty] | TXV | 19.81%
Chico | CA | 95973-0590 |  | 2013-08-21 | 2013-08-21 13:35 | 2013-08-21 20:59 | PAYNE - 565BJ018 | 48 | 4 | Yes | Yes | 14.8 | 12.2 | 2.7 | 7F9C1CBD4AA8491393236AC1AB942FAF |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Fresno | CA | 93727-3260 |  | 2013-08-16 | 2013-08-16 11:44 | 2013-08-16 11:44 | AMERICAN STANDARD - YCC030F1M0BF | 69 | 0 | Yes | Yes | 24.1 | 21.2 | 2.9 | 51CC944195DB46869A8CFCBD38AB0BC6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3260 |  | 2013-08-17 | 2013-08-17 00:41 | 2013-08-17 01:04 | AMERICAN STANDARD - YCC024F1L0BG | 64 | 2.4 | Yes | Yes | 18.9 | 20.1 | -1.2 | A887BF0DF9AE4BED9170BB41D3D785CF |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95209-2124 |  | 2013-08-02 | 2013-08-02 10:52 | 2013-08-02 11:17 | OTHER - 80WR30E1NA | 55 | -3.2 | Yes | Yes | 18.4 | 18.1 | 0.3 | 4E1AED9FE9E44CD6903265BB8A5B6441 |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Fresno | CA | 93703-1007 |  | 2013-08-07 | 2013-08-07 13:25 | 2013-08-07 13:27 | CARRIER - 48GS036060301 | 56 | 7 | Yes | Yes | 20.1 | 18.2 | 1.9 | DD91A2E32D1A4ABC871D535D5AA6AC60 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Clovis | CA | 93611-5956 |  | 2013-08-06 | 2013-08-06 12:54 | 2013-08-06 12:56 | ALLEGIANCE - 2A7A4060B1000BA | 211 | 32.7 | Yes | Yes | 24 | 20.9 | 3.1 | 5C651735015D40B58CB41596C294B038 |  | R22 | Non-TXV |  | 15.5% | 0.84502 | 29.78% | [5 empty] | Non-TXV | 15.5%
Fresno | CA | 93722-7539 |  | 2013-08-13 | 2013-08-13 11:03 | 2013-08-13 11:04 | LENNOX - 12GCS0481005PB | 167 | 21.8 | Yes | Yes | 22.5 | 19.3 | 3.2 | 322E57F807DF4E36A19AACFA4AE4F871 |  | R22 | Non-TXV |  | 13.05% | 0.86946 | 25.09% | [5 empty] | Non-TXV | 13.05%
Penn Valley | CA | 95946-9380 |  | 2013-09-05 | 2013-09-05 09:44 | 2013-09-05 10:03 | RHEEM - RAKA-060JAZ | 112 | 3.4 | Yes | Yes | 24 | 19.9 | 4.1 | 0605C97C9A41483DBCCB441810C948B5 |  | R22 | TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | TXV | 3.036%
Fresno | CA | 93727-7012 |  | 2013-09-27 | 2013-09-27 12:18 | 2013-09-27 12:19 | OTHER - UNK | 54 | 6.1 | Yes | Yes | 19.4 | 19.8 | -0.4 | 95E37A667A434300AB1275A1D9AB3CA7 |  | R22 | Non-TXV |  | 11.3% | 0.88704 | 21.71% | [5 empty] | Non-TXV | 11.3%
Madera | CA | 93638-9614 |  | 2013-08-23 | 2013-08-23 15:47 | 2013-08-26 02:19 | - 48 NE T036. 321 -/- | 101 | 3 | Yes | Yes | 19.5 | 20.1 | -0.6 | B931391681E047DEA46F72FAE84C13FE |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Durham | CA | 95938-9417 |  | 2013-10-22 | 2013-10-22 14:04 | 2013-10-22 15:00 | RHEEM - RAKA-030JAZ | 102 | 3.2 | Yes | Yes | 19 | 19.7 | -0.7 | FF75DDA3DB064815BFA05CE71AD525B1 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Rocklin | CA | 95677-2751 |  | 2013-08-06 | 2013-08-06 13:14 | 2013-08-06 13:44 | ICP - NAC024AKB2 | 60 | 11.1 | Yes | Yes | 16.2 | 18.8 | -2.6 | 56046724D2D84B4F9748F80E1B6BCC4A |  | R22 | Non-TXV |  | 18.5% | 0.815 | 35.55% | [5 empty] | Non-TXV | 18.5%
Fresno | CA | 93704-2930 |  | 2013-08-09 | 2013-08-09 11:30 | 2013-08-09 11:37 | AIRE-FLO - RRNAA036JK08X | 114 | 11.9 | Yes | Yes | 20.3 | 18.8 | 1.5 | 7F5D96067B8746E3838554CE1403D31B |  | R22 | Non-TXV |  | 10.44% | 0.89561 | 20.06% | [5 empty] | Non-TXV | 10.44%
Parlier | CA | 93648-0000 |  | 2013-08-21 | 2013-08-21 12:37 | 2013-08-21 13:09 | ICP - PGF060K100B | 136 | 6.4 | Yes | Yes | 18 | 19.8 | -1.8 | CFAF7DAE10B44E4999ADD2387460EC0E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Merced | CA | 95340-0969 |  | 2013-08-05 | 2013-08-05 13:19 | 2013-08-05 13:44 | AMERICAN STANDARD - YCC024F1L0BG | 96 | 4.6 | Yes | Yes | 20.4 | 20.4 | 0 | 045F2661D2EC48B898E071C8B9B5CD07 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Madera | CA | 93637-4902 |  | 2013-09-11 | 2013-09-11 15:26 | 2013-09-11 15:28 | CARRIER - 38EH048320 | 141 | 6.4 | Yes | Yes | 19.1 | 19.7 | -0.6 | 7423EBA419DF418289B657C8883F861B |  | R22 | Non-TXV |  | 4.539% | 0.95461 | 8.723% | [5 empty] | Non-TXV | 4.539%
Stockton | CA | 95210-1725 |  | 2013-08-12 | 2013-08-12 08:11 | 2013-08-12 08:28 | PAYNE - PY3GNAA36060NA | 96 | -5.6 | Yes | Yes | 22.4 | 18.2 | 4.2 | 166A92E4D6F0459793A57311B7F3DFDC |  | R410A | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Clovis | CA | 93611-6927 |  | 2013-08-06 | 2013-08-06 13:22 | 2013-08-06 13:24 | BDP - 598AN036B | 182 | 24.4 | Yes | Yes | 18.8 | 19.7 | -0.9 | C43A1C928D5848A7AA7B34CE4B4734C1 |  | R22 | Non-TXV |  | 13.41% | 0.86593 | 25.76% | [5 empty] | Non-TXV | 13.41%
Stockton | CA | 95219-7120 |  | 2013-08-06 | 2013-08-06 13:36 | 2013-08-06 13:56 | YORK - H3RA060S06B | 98 | 6.9 | Yes | Yes | 21.3 | 19.3 | 2 | E655416B3D1545E890569787760EC778 |  | R22 | Non-TXV |  | 7.041% | 0.92959 | 13.53% | [5 empty] | Non-TXV | 7.041%
Sanger | CA | 93657-2600 |  | 2013-08-05 | 2013-08-05 18:59 | 2013-08-05 21:03 | RHEEM - N/A | 90 | 9.8 | Yes | Yes | 17.6 | 18.6 | -0.9 | D8DCF8C35B09403A8621BC32B6E9A22D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.89% | 0.89111 | 20.93% | [5 empty] | Non-TXV | 10.89%
Merced | CA | 95340-0974 |  | 2013-08-05 | 2013-08-05 15:36 | 2013-08-05 16:26 | GOODMAN - GPG13240451CB | 74 | 2.2 | Yes | Yes | 24.6 | 20.2 | 4.4 | 18B1A54B068C480D97BF71C69A7E475E |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Chico | CA | 95973-0574 |  | 2013-08-08 | 2013-08-08 14:50 | 2013-08-08 15:19 | PAYNE - 565BJ018 | 50 | 5 | Yes | Yes | 15.4 | 18.3 | -2.9 | 17E85139EA9D49BB9E224E89B94CB02D |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95212-3050 |  | 2013-08-08 | 2013-08-08 13:04 | 2013-08-08 13:26 | YORK - H2RD048S06B | 134 | 6.4 | Yes | Yes | 15.5 | 18.5 | -3 | B51D77C0722244B88FB74D65C6DA1356 |  | R22 | Non-TXV |  | 4.776% | 0.95224 | 9.179% | [5 empty] | Non-TXV | 4.776%
Sanger | CA | 93657-9465 |  | 2013-08-03 | 2013-08-03 12:30 | 2013-08-03 13:15 | CARRIER - N/A | 60 | 3.2 | Yes | Yes | 17.7 | 19 | -1.3 | 76DABFA48C344140A519156079057BF4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Merced | CA | 95348-3422 |  | 2013-09-16 | 2013-09-16 20:47 | 2013-09-16 20:50 | OTHER - 7777UNK | 68 | 3 | Yes | Yes | 24.6 | 20.9 | 3.7 | C584A30EADE14F9B86B2EC679A99C267 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Fresno | CA | 93722-9181 |  | 2013-08-23 | 2013-08-23 11:08 | 2013-08-23 11:09 | BDP - 585HJW024040ABAE | 68 | 10.1 | Yes | Yes | 19.3 | 17.2 | 2.2 | 78FF9FE202D64158BD57EC39D71FCC2E |  | R22 | Non-TXV |  | 14.85% | 0.85147 | 28.54% | [5 empty] | Non-TXV | 14.85%
Parlier | CA | 93648-2339 |  | 2013-09-27 | 2013-09-27 17:50 | 2013-09-27 18:22 | CONCORD - CCU10A24A-1 | 50 | 11.2 | Yes | Yes | 17 | 19.9 | -2.9 | F362E05850F842C2B2331A98EDAFE72E |  | R22 | Non-TXV |  | 22.4% | 0.776 | 43.05% | [5 empty] | Non-TXV | 22.4%
Parlier | CA | 93648-2446 |  | 2013-08-07 | 2013-08-07 16:06 | 2013-08-07 16:30 | CARRIER - N/A | 90 | 2.8 | Yes | Yes | 19.1 | 18.9 | 0.2 | 0595CA90826D4ADF99745E874830C45A |  | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Stockton | CA | 95209-1339 |  | 2013-08-02 | 2013-08-02 09:58 | 2013-08-02 10:16 | GOODMAN - GSX130481BA | 125 | -7.4 | Yes | Yes | 24.8 | 18.8 | 6 | 093F952109CC4D17A79458F69E813AA3 |  | R410A | Non-TXV |  | -5.92% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.92%
Stockton | CA | 95207-4454 |  | 2013-08-05 | 2013-08-05 15:51 | 2013-08-05 16:15 | BDP - 42RC0108K | 87 | 2.7 | Yes | Yes | 17.6 | 20.2 | -2.6 | 2501471975694F9A9586FF029A145614 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Atwater | CA | 95301-9724 |  | 2013-08-14 | 2013-08-14 15:05 | 2013-08-14 15:28 | AMANA - PGD24C0702E | 85 | 6.3 | Yes | Yes | 25.6 | 20.4 | 5.2 | BE1E53415AF945349718A565D992B6F6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.412% | 0.92588 | 14.24% | [5 empty] | Non-TXV | 7.412%
Stockton | CA | 95215-2223 |  | 2013-08-14 | 2013-08-14 09:30 | 2013-08-14 09:35 | YORK - BRCS0481BD | 117 | 5.3 | Yes | Yes | 21.8 | 18.6 | 3.2 | 4F069D2CF2CD4F4395267416AC208661 |  | R22 | Non-TXV |  | 4.53% | 0.9547 | 8.705% | [5 empty] | Non-TXV | 4.53%
Olivehurst | CA | 95961-6635 |  | 2013-08-30 | 2013-08-30 13:46 | 2013-08-30 14:04 | ARMSTRONG - SCU12G36A-1 | 99 | 10.2 | Yes | Yes | 24.2 | 20.1 | 4.2 | 884BCE26BD674B71818D4971848D28FE |  | R22 | Non-TXV |  | 10.3% | 0.89697 | 19.8% | [5 empty] | Non-TXV | 10.3%
Madera | CA | 93638-5104 |  | 2013-08-26 | 2013-08-26 11:27 | 2013-08-26 13:15 | YORK - DAYP-F030N70A | 73 | 5.1 | Yes | Yes | 18.1 | 19.8 | -1.7 | FCFB59E0D4764B0CAFD4D90C5D3BEC7C |  | R22 | Non-TXV |  | 6.986% | 0.93014 | 13.43% | [5 empty] | Non-TXV | 6.986%
Sanger | CA | 93657-2926 |  | 2013-08-07 | 2013-08-07 10:27 | 2013-08-07 11:13 | RHEEM - RRMA-A048JK10X | 117 | 5.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | C2F1510C77354100A941134AB9126F9A |  | R22 | Non-TXV |  | 4.786% | 0.95214 | 9.198% | [5 empty] | Non-TXV | 4.786%
Merced | CA | 95348-2244 |  | 2013-08-15 | 2013-08-15 14:41 | 2013-08-15 14:43 | CARRIER - 565BJ018 | 50 | 5.6 | Yes | Yes | 18.8 | 21 | -2.2 | 7F31A9823886458486BBF76F3A79B999 |  | R22 | Non-TXV |  | 11.2% | 0.888 | 21.52% | [5 empty] | Non-TXV | 11.2%
Stockton | CA | 95210-1789 |  | 2013-08-12 | 2013-08-12 08:38 | 2013-08-12 08:56 | YORK - BRCS0241BD | 59 | 2 | Yes | Yes | 15.8 | 17.7 | -1.9 | F826ED962ADC40BF8AE9CADA0266B389 |  | R22 | Non-TXV |  | 3.39% | 0.9661 | 6.515% | [5 empty] | Non-TXV | 3.39%
Grass Valley | CA | 95949-7302 |  | 2013-08-23 | 2013-08-23 17:37 | 2013-08-23 17:56 | RHEEM - UNK | 87 | 19.8 | Yes | Yes | 27.6 | 22 | 5.6 | 3E29F76BB13A4A079880577BF2A2B456 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.76% | 0.77241 | 43.74% | [5 empty] | Non-TXV | 22.76%
Merced | CA | 95340-4508 |  | 2013-08-20 | 2013-08-20 15:32 | 2013-08-20 15:33 | RUUD - URKAA042JK08E | 69 | 6.8 | Yes | Yes | 24.7 | 22.4 | 2.3 | B97BAA81EC2F46B1BD72FD906940E65F |  | R22 | Non-TXV |  | 9.855% | 0.90145 | 18.94% | [5 empty] | Non-TXV | 9.855%
Lincoln | CA | 95648-8351 |  | 2013-08-17 | 2013-08-17 15:33 | 2013-08-17 15:33 | YORK - H2RC036S06A | 83 | 0 | Yes | Yes | 19.3 | 21 | -1.7 | 3BB685D23EA645F4B063786B0C999A03 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-8419 |  | 2013-08-19 | 2013-08-19 16:28 | 2013-08-19 16:33 | RUUD - UAKA037JAZ | 79 | 6.2 | Yes | Yes | 21.3 | 22.1 | -0.8 | 6C9F29F8986542269409C7734E995273 |  | R22 | Non-TXV |  | 7.848% | 0.92152 | 15.08% | [5 empty] | Non-TXV | 7.848%
Chowchilla | CA | 93610-8419 |  | 2013-08-19 | 2013-08-19 16:42 | 2013-08-19 17:00 | RUUD - UAKA037JAZ | 79 | 10.2 | Yes | Yes | 17.3 | 19.8 | -2.5 | D34027EC7136406A8EC157B501F603DD |  | R22 | Non-TXV |  | 12.91% | 0.87089 | 24.81% | [5 empty] | Non-TXV | 12.91%
Fresno | CA | 93703-1571 |  | 2013-08-07 | 2013-08-07 14:34 | 2013-08-07 14:36 | CARRIER - 48KL024300BE | 50 | 7.6 | Yes | Yes | 18.1 | 16.6 | 1.5 | EF54C1EF2633497C8F9AACE3CA806140 |  | R22 | Non-TXV |  | 15.2% | 0.848 | 29.21% | [5 empty] | Non-TXV | 15.2%
Stockton | CA | 95204-4833 |  | 2013-08-05 | 2013-08-05 15:11 | 2013-08-05 15:28 | DAY & NIGHT - UNK | 85 | 3.2 | Yes | Yes | 16.9 | 18.7 | -1.8 | D39BF49C5B67473780F8951AAA67655F |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Stockton | CA | 95206-6264 |  | 2013-08-12 | 2013-08-12 09:35 | 2013-08-12 09:56 | CARRIER - 38CKC048300 | 102 | 3.6 | Yes | Yes | 22.3 | 19.9 | 2.4 | 55043933FA4848BD921A51806B91FAF4 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Roseville | CA | 95661-5903 |  | 2013-08-23 | 2013-08-23 14:31 | 2013-08-23 14:56 | OTHER - UNK | 70 | 19.1 | Yes | Yes | 26 | 21 | 5 | 44E1A493C02446AB956946E08D29230F |  | R22 | Non-TXV |  | 27.29% | 0.72714 | 52.44% | [5 empty] | Non-TXV | 27.29%
Stockton | CA | 95206-3880 |  | 2013-08-22 | 2013-08-22 09:13 | 2013-08-22 09:34 | RUUD - 13AJN36A01 | 90 | 2.6 | Yes | Yes | 23.5 | 19.4 | 4.1 | 314F288099A249A58B7D028EEDE33FE6 |  | R410A | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Fresno | CA | 93703-1567 |  | 2013-08-09 | 2013-08-09 10:21 | 2013-08-09 10:21 | CARRIER - 48KL024300BE | 50 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | D2CE8973DDD2407995B083709BD8FBBD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1570 |  | 2013-08-07 | 2013-08-07 15:02 | 2013-08-07 15:04 | CARRIER - 48KL024301BE | 50 | 7.4 | Yes | Yes | 20 | 18.7 | 1.3 | 0991B8CEB22847439235EFA374BE537B |  | R22 | Non-TXV |  | 14.8% | 0.852 | 28.44% | [5 empty] | Non-TXV | 14.8%
Stockton | CA | 95210-3595 |  | 2013-08-14 | 2013-08-14 11:56 | 2013-08-14 12:15 | PAYNE - PY3GNAA24060NA | 91 | 7.8 | Yes | Yes | 20.3 | 18.4 | 1.9 | 7356B84669E649B890965084313A69A4 |  | R410A | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Merced | CA | 95348-8416 |  | 2013-08-13 | 2013-08-13 15:57 | 2013-08-13 16:00 | GOODMAN - GSC130481AA | 110 | 5.9 | Yes | Yes | 16.4 | 19.4 | -3 | 6B5CEE97DDAB464BA180D94A4B8908C2 |  | R22 | Non-TXV |  | 5.364% | 0.94636 | 10.31% | [5 empty] | Non-TXV | 5.364%
Riverbank | CA | 95367-2219 |  | 2013-08-29 | 2013-08-29 13:33 | 2013-08-29 13:55 | LENNOX - 12GCS042X-100-6PB | 133 | 4 | Yes | Yes | 24.7 | 19.3 | 5.4 | 0512BCFE552944DB9247F4B489802038 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Chico | CA | 95973-0933 |  | 2013-08-07 | 2013-08-07 14:19 | 2013-08-07 14:38 | GOODMAN - SSX160601AB | 200 | 12.7 | Yes | Yes | 25.5 | 19.5 | 6 | 581BAC18A81649099D5E6CB6A6F2047D |  | R410A | TXV |  | 6.35% | 0.9365 | 12.2% | [5 empty] | TXV | 6.35%
Fresno | CA | 93703-1571 |  | 2013-08-12 | 2013-08-12 12:47 | 2013-08-12 12:48 | CARRIER - 48KL024301BE | 50 | 7.7 | Yes | Yes | 25.5 | 20.4 | 5.1 | ABD6947A59B241A7BA61D26FC5322F32 |  | R22 | Non-TXV |  | 15.4% | 0.846 | 29.6% | [5 empty] | Non-TXV | 15.4%
Fresno | CA | 93703-1568 |  | 2013-08-13 | 2013-08-13 15:31 | 2013-08-13 15:33 | CARRIER - 48KL024300BE | 50 | 7.9 | Yes | Yes | 22.4 | 19.6 | 2.8 | 7355672D679D4FF19F0C4622CC310883 |  | R22 | Non-TXV |  | 15.8% | 0.842 | 30.36% | [5 empty] | Non-TXV | 15.8%
Yuba City | CA | 95991-4319 |  | 2013-09-09 | 2013-09-09 14:18 | 2013-09-09 14:40 | OTHER - PGAA30C1K4 | 79 | 3.6 | Yes | Yes | 22.9 | 21 | 1.9 | 5A2F270060FA4316B0D6E2D450640266 |  | R22 | Non-TXV |  | 4.557% | 0.95443 | 8.757% | [5 empty] | Non-TXV | 4.557%
Madera | CA | 93636-1321 |  | 2013-08-05 | 2013-08-05 13:05 | 2013-08-05 13:10 | ICP - N2A330AKA200 | 82 | 8.9 | Yes | Yes | 22.1 | 22.4 | -0.3 | 83CE9D071DA94B88BD6D4BC16E439DAD |  | R22 | TXV |  | 10.85% | 0.89146 | 20.86% | [5 empty] | TXV | 10.85%
Manteca | CA | 95336-4401 |  | 2013-08-02 | 2013-08-02 14:29 | 2013-08-02 14:51 | GOODMAN - CKL30-1D | 70 | 11.9 | Yes | Yes | 19 | 19.3 | -0.3 | 8601D7CC0CC44D4C9D1DA21E0DEC2A54 |  | R22 | Non-TXV |  | 17% | 0.83 | 32.67% | [5 empty] | Non-TXV | 17%
Tracy | CA | 95377-8282 |  | 2013-08-12 | 2013-08-12 15:31 | 2013-08-12 15:50 | YORK - H2RC048S06A | 120 | 13.1 | Yes | Yes | 21 | 20.5 | 0.5 | C9A3AE7A5EC442F18B22089768DE89A5 |  | R22 | Non-TXV |  | 10.92% | 0.89083 | 20.98% | [5 empty] | Non-TXV | 10.92%
Chico | CA | 95973-0520 |  | 2013-08-21 | 2013-08-21 12:26 | 2013-08-21 12:55 | PAYNE - PA10JA024-A | 67 | 8 | Yes | Yes | 21.7 | 20.8 | 0.9 | 6B2EAC18BFAC44B3991A0BECE46570CD |  | R22 | TXV |  | 11.94% | 0.8806 | 22.95% | [5 empty] | TXV | 11.94%
Merced | CA | 95340-3220 |  | 2013-08-20 | 2013-08-20 12:09 | 2013-08-20 12:12 | AIRE-FLO - UNK | 85 | 10.7 | Yes | Yes | 24.5 | 22.5 | 2.1 | CD68440C836B40A0872314D565A3F130 |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
French Camp | CA | 95231-9667 |  | 2013-08-29 | 2013-08-29 15:30 | 2013-08-29 15:48 | PAYNE - PY1PNB030060AAAA | 55 | 2.6 | Yes | Yes | 20.4 | 19.8 | 0.6 | 51AE8E53CE724A179224B3A9FEA89CE4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.727% | 0.95273 | 9.085% | [5 empty] | Non-TXV | 4.727%
Yuba City | CA | 95991-1808 |  | 2013-08-21 | 2013-08-21 10:11 | 2013-08-21 10:27 | GE - UNK | 36 | 12.1 | Yes | Yes | 16 | 18.5 | -2.5 | 702D3BA990744248AE816326F054C040 |  | R22 | Non-TXV |  | 33.61% | 0.66389 | 64.59% | [5 empty] | Non-TXV | 33.61%
Fresno | CA | 93722-4379 |  | 2013-08-08 | 2013-08-08 10:40 | 2013-08-08 10:42 | DAY & NIGHT - 588ANW030080ABAD | 53 | 2.2 | Yes | Yes | 24.1 | 18.6 | 5.5 | 987871867AFC48BAA5466584F71922F0 |  | R22 | Non-TXV |  | 4.151% | 0.95849 | 7.977% | [5 empty] | Non-TXV | 4.151%
Los Banos | CA | 93635-4553 |  | 2013-08-14 | 2013-08-14 11:22 | 2013-08-14 11:26 | BRYANT - 561CJ042-A | 80 | 2.4 | Yes | Yes | 18.9 | 18.9 | 0 | 9A7CF6A5CB1146938DD29C76366E705B |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95205-7781 |  | 2013-08-02 | 2013-08-02 09:48 | 2013-08-02 10:06 | BRYANT - 581CJ024-E | 54 | 9 | Yes | Yes | 16.6 | 19.3 | -2.7 | DA82F46050FD41179F2A2824418EF960 |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Cameron Park | CA | 95682-7722 |  | 2013-08-28 | 2013-08-28 09:44 | 2013-08-28 10:12 | AMERICAN STANDARD - 4A6H6048B1000BA | 145 | 5 | Yes | Yes | 16.8 | 19.6 | -2.8 | E1CC0BFEA3E540E1B5BE9D9D125CB146 |  | R410A | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Fresno | CA | 93706-4756 |  | 2013-08-17 | 2013-08-17 11:57 | 2013-08-17 12:25 | GOODMAN - GPG13300451BB | 77 | 5.5 | Yes | Yes | 17.5 | 20.2 | -2.7 | A899A7B1AE394ACA8B413BB6AC5BD607 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Fresno | CA | 93705-0318 |  | 2013-08-02 | 2013-08-02 12:25 | 2013-08-02 14:13 | LENNOX - 10GCS024-50-3PA | 52 | 5.6 | Yes | Yes | 20.3 | 20.3 | 0 | 90A124BC648647D8813B2807F2998342 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | Non-TXV | 10.77%
Gustine | CA | 95322-1744 |  | 2013-09-05 | 2013-09-05 18:18 | 2013-09-05 18:20 | BRYANT - 561CJ030-C | 76 | 2.9 | Yes | Yes | 20.8 | 19.8 | 1 | C183DEB43ECD401DA53E421DBC4BB865 |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Fresno | CA | 93704-2633 |  | 2013-08-12 | 2013-08-12 14:00 | 2013-08-12 14:02 | LENNOX - UNK | 104 | 12 | Yes | Yes | 19.3 | 18.6 | 0.7 | 8EE8CF7AE77142708BF6B0E594BFECA8 |  | R22 | Non-TXV |  | 11.54% | 0.88462 | 22.17% | [5 empty] | Non-TXV | 11.54%
Fresno | CA | 93705-5150 |  | 2013-08-06 | 2013-08-06 12:24 | 2013-08-06 12:40 | CARRIER - 48GS-030060301 | 55 | 6.7 | Yes | Yes | 18.2 | 21.2 | -3 | 220E5BB8C93F4933B57E7EB293682944 |  | R22 | Non-TXV |  | 12.18% | 0.87818 | 23.41% | [5 empty] | Non-TXV | 12.18%
Fresno | CA | 93722-5508 |  | 2013-10-26 | 2013-10-26 16:56 | 2013-10-26 17:21 | UNITARY PRODUCTS GROUP - PA13NR036-E | 98 | 7 | Yes | Yes | 20.5 | 20.4 | 0.1 | 184E955F26BB483887AE053AEE5984CC |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Paso Robles | CA | 93446-1704 |  | 2013-10-08 | 2013-10-08 16:29 | 2013-10-08 16:47 | BRYANT - 582ANW018040NAAD | 43 | -2.5 | Yes | Yes | 18.1 | 19.5 | -1.4 | EE2BD056219244A3AB9F8FD9E3090C5B |  | R22 | Non-TXV |  | -5.814% | 1.0581 | 1.628% |  |  |  |  | Non-TXV |  |  | -5.814%
Fresno | CA | 93728-1703 |  | 2013-08-16 | 2013-08-16 13:40 | 2013-08-16 13:44 | CARRIER - UNK | 60 | 9.7 | Yes | Yes | 23 | 21 | 2 | 53EBDFE5D36A431C9F30914F7B6EFBB3 |  | R22 | Non-TXV |  | 16.17% | 0.83833 | 31.07% | [5 empty] | Non-TXV | 16.17%
Sanger | CA | 93657-1915 |  | 2013-08-06 | 2013-08-06 12:28 | 2013-08-06 12:28 | GOODMAN - ASX140481CA | 147 | 0 | Yes | Yes | 18 | 19.5 | -1.5 | 0922D3721A104C15BEDD89B2BD08232B |  | R410A | TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1523 |  | 2013-08-06 | 2013-08-06 15:14 | 2013-08-06 21:36 | YORK - D2NP030N05606NX | 36 | 6 | Yes | Yes | 16.5 | 19.2 | -2.7 | 2EDDA66AC4714F72B98BCEECF5E7836C |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Sanger | CA | 93657-2615 |  | 2013-08-06 | 2013-08-06 16:45 | 2013-08-06 17:34 | LENNOX - 12GCS036X-75-3PA | 110 | 4.8 | Yes | Yes | 24.6 | 21 | 3.6 | 2A0DC6E0BF924B4B99657EF937ECE76D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.364% | 0.95636 | 8.386% | [5 empty] | Non-TXV | 4.364%
Los Banos | CA | 93635-3716 |  | 2013-08-14 | 2013-08-14 10:03 | 2013-08-14 10:06 | RUUD - 7777UNK | 100 | 4 | Yes | Yes | 20.3 | 19.1 | 1.2 | F4E62245161A453AB145F0E3DDF55043 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Sanger | CA | 93657-2049 |  | 2013-08-06 | 2013-08-06 11:35 | 2013-08-06 11:52 | LENNOX - 10ACC-042-230-03 | 81 | 2.5 | Yes | Yes | 19.8 | 19.7 | 0.1 | 874077F475924B539147C5823997FA57 |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Sanger | CA | 93657-2052 |  | 2013-08-10 | 2013-08-10 11:02 | 2013-08-10 11:20 | LENNOX - 10ACC-042-230-03 | 81 | 4.2 | Yes | Yes | 17 | 19.9 | -2.9 | 5991890CBDE24EC38620548AD6BC942B |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Fresno | CA | 93705-0354 |  | 2013-08-02 | 2013-08-02 16:27 | 2013-08-02 17:03 | BRYANT - 582ANW036060AAAF | 56 | 2.3 | Yes | Yes | 20 | 19.2 | 0.9 | 03CAC4359F524C85B0FBDEC7C0FB06EE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Clovis | CA | 93612-2201 |  | 2013-08-07 | 2013-08-07 09:31 | 2013-08-07 09:33 | BRYANT - 574ANW036060NB | 130 | 8 | Yes | Yes | 22.9 | 18.2 | 4.7 | B3BF1AA693094ACD858730BB54DCFCAA |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Sanger | CA | 93657-9441 |  | 2013-08-06 | 2013-08-06 10:30 | 2013-08-06 11:31 | UNITARY PRODUCTS GROUP - TCGD48S21S2A | 69 | 11.1 | Yes | Yes | 26 | 20.7 | 5.3 | 64874C05060140B7BF3ADF8986E66E5D |  | R22 | Non-TXV |  | 16.09% | 0.83913 | 30.92% | [5 empty] | Non-TXV | 16.09%
Madera | CA | 93638-9499 |  | 2013-09-01 | 2013-09-01 00:59 | 2013-09-01 23:48 | YORK - UNK | 148 | 5.5 | Yes | Yes | 19.6 | 18.3 | 1.3 | 89AF7AA2602F40218F8493BAD598D46A |  | R22 | Non-TXV |  | 3.716% | 0.96284 | 7.142% | [5 empty] | Non-TXV | 3.716%
Mariposa | CA | 95338-9668 |  | 2013-08-02 | 2013-08-02 11:06 | 2013-08-02 11:06 | RUUD - 7777UNK | 110 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | A3343ACC2B164FA8A7D8911253149727 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-5315 |  | 2013-08-08 | 2013-08-08 13:25 | 2013-08-08 14:23 | CARRIER - 38CKC042---301 | 80 | 2.6 | Yes | Yes | 18 | 20.9 | -2.9 | 0AC263F0554F45BDA26C237D5A2B1A18 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Grass Valley | CA | 95949-6686 |  | 2013-08-07 | 2013-08-07 16:59 | 2013-08-07 16:59 | COLEMAN - BRC604818B I THINK | 119 | 0 | Yes | Yes | 24.6 | 20.8 | 3.8 | 854189D166164F5980FEF646A4411A3F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8813 |  | 2013-08-16 | 2013-08-16 09:50 | 2013-08-16 10:08 | LENNOX - 10ACC-042-230-02 | 81 | 5.7 | Yes | Yes | 22.3 | 21 | 1.3 | 38DE4CC39207442AAACE198E1523F622 |  | R22 | Non-TXV |  | 7.037% | 0.92963 | 13.52% | [5 empty] | Non-TXV | 7.037%
Magalia | CA | 95954-9551 |  | 2013-08-03 | 2013-08-03 12:25 | 2013-08-03 13:39 | PAYNE - PY3GNAA42090NA | 106 | 5.2 | Yes | Yes | 21.5 | 19.8 | 1.7 | 205F4D32C43047BB848F8A120840806C |  | R410A | Non-TXV |  | 4.906% | 0.95094 | 9.428% | [5 empty] | Non-TXV | 4.906%
Los Banos | CA | 93635-6501 |  | 2013-08-05 | 2013-08-05 12:10 | 2013-08-05 12:19 | GIBSON - JS3BA-060KB | 114 | 4.5 | Yes | Yes | 24.1 | 20.1 | 4 | 0693AC399DAB4128820797A35C07E559 |  | R22 | Non-TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | Non-TXV | 3.947%
Los Banos | CA | 93635-5306 |  | 2013-08-01 | 2013-08-01 16:41 | 2013-08-01 17:01 | RUUD - UAHE-P48JAS | 114 | 17.3 | Yes | Yes | 19.2 | 22.1 | -2.9 | 6CFDC27A61CE4B19BA07841D051AC7BB |  | R22 | Non-TXV |  | 15.18% | 0.84825 | 29.16% | [5 empty] | Non-TXV | 15.18%
Fresno | CA | 93722-3082 |  | 2013-08-07 | 2013-08-07 13:36 | 2013-08-07 13:43 | RHEEM - RAKA-048JAZ | 103 | 4.4 | Yes | Yes | 19.8 | 19 | 0.8 | 1867AE6050CB482FA447C16A8E5A113E |  | R22 | Non-TXV |  | 4.272% | 0.95728 | 8.21% | [5 empty] | Non-TXV | 4.272%
Newcastle | CA | 95658-9318 |  | 2013-08-08 | 2013-08-08 18:25 | 2013-08-08 18:25 | TRANE - YCY042G1M0AD | 148 | 0 | Yes | Yes | 24.6 | 21.3 | 3.4 | 9D331E4AECBF42F1BD12FBE837F4BCD1 |  | R22 | TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2453 |  | 2013-08-14 | 2013-08-14 12:52 | 2013-08-14 12:53 | YORK - D1NH042N09006C | 94 | 12.2 | Yes | Yes | 22.7 | 19.7 | 3 | B92F8EC5525F465C8D812D00B965E9F2 |  | R22 | Non-TXV |  | 12.98% | 0.87021 | 24.94% | [5 empty] | Non-TXV | 12.98%
Merced | CA | 95340-0972 |  | 2013-08-05 | 2013-08-05 16:50 | 2013-08-05 17:06 | AMERICAN STANDARD - YCC024F1L0BJ | 66 | 2.3 | Yes | Yes | 24 | 20.2 | 3.8 | CAF37BE1B9BD411E91E490B8278080E5 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Grass Valley | CA | 95945-7558 |  | 2013-08-22 | 2013-08-22 17:06 | 2013-08-22 17:25 | OTHER - UNK | 48 | 6.6 | Yes | Yes | 19.1 | 19.9 | -0.8 | D4923B7D167C4F769DEAE696532C0885 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Lincoln | CA | 95648-7618 |  | 2013-08-23 | 2013-08-23 12:47 | 2013-08-23 13:03 | CARRIER - 38BRC060360 | 197 | 7.9 | Yes | Yes | 20 | 19.8 | 0.2 | 2B766444319A4BCCB7A58BA40E364CFD |  | R22 | TXV |  | 4.01% | 0.9599 | 7.707% | [5 empty] | TXV | 4.01%
Ripon | CA | 95366-2816 |  | 2013-09-04 | 2013-09-04 15:01 | 2013-09-04 15:31 | BRYANT - 556AN042-F | 85 | 3.2 | Yes | Yes | 21.5 | 20.2 | 1.3 | 86636AAF85AF4F59A30C1F14E7545A0C |  | R410A | TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | TXV | 3.765%
Oroville | CA | 95966-6839 |  | 2013-08-12 | 2013-08-12 13:30 | 2013-08-12 19:48 | TEMPSTAR - PGD348090K001C1 | 100 | 6.2 | Yes | Yes | 17.5 | 18.9 | -1.4 | 1C8FBB65FFA94BC9B8818B9B7774279A |  | R410A | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Clovis | CA | 93611-6622 |  | 2013-08-06 | 2013-08-06 11:16 | 2013-08-06 11:17 | LENNOX - GCS29036752PA | 58 | 6.1 | Yes | Yes | 26.6 | 22.5 | 4.1 | CE5F12556A194ED9A91F6D642348CFD2 |  | R22 | Non-TXV |  | 10.52% | 0.89483 | 20.21% | [5 empty] | Non-TXV | 10.52%
Chowchilla | CA | 93610-2010 |  | 2013-08-14 | 2013-08-14 09:07 | 2013-08-14 09:10 | PAYNE - PY3PNA036090NA | 167 | 9.5 | Yes | Yes | 23.5 | 17.7 | 5.8 | 7516F7CA23AB47B8A85ED8512069AA6F |  | R22 | Non-TXV |  | 5.689% | 0.94311 | 10.93% | [5 empty] | Non-TXV | 5.689%
Jamestown | CA | 95327-9756 |  | 2013-10-21 | 2013-10-21 12:22 | 2013-10-21 12:41 | COLEMAN - H2RD042S06A | 141 | 4.2 | Yes | Yes | 24.4 | 22 | 2.4 | FD0103A3EF7148BA929474772AE49933 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.979% | 0.97021 | 5.724% | [5 empty] | Non-TXV | 2.979%
Rocklin | CA | 95677-3467 |  | 2013-08-06 | 2013-08-06 12:06 | 2013-08-06 12:49 | TRANE - 2TTZ9036C1000AA | 208 | -18.1 | Yes | Yes | 23.5 | 19.9 | 3.6 | D6B23D98861E424D9F374E1D278D9E0A |  | R22 | TXV |  | -8.702% | 1.087 | 2.437% |  |  |  |  | TXV |  |  | -8.702%
Tracy | CA | 95376-2133 |  | 2013-08-15 | 2013-08-15 12:01 | 2013-08-15 12:28 | CARRIER - 38CKC04250 | 93 | 4.2 | Yes | Yes | 21.8 | 21.9 | -0.1 | 33386E7ED45045F4B3C56E9F67A29FEA |  | R22 | Non-TXV |  | 4.516% | 0.95484 | 8.679% | [5 empty] | Non-TXV | 4.516%
Merced | CA | 95348-2239 |  | 2013-08-13 | 2013-08-13 16:54 | 2013-08-13 16:57 | GOODMAN - 7777UNK | 64 | 3.8 | Yes | Yes | 25.2 | 21.4 | 3.8 | 4EDE974AFB1E41ECB8BE79D86ABBECBE |  | R22 | Non-TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | Non-TXV | 5.938%
Chowchilla | CA | 93610-2010 |  | 2013-08-21 | 2013-08-21 11:06 | 2013-08-21 12:31 | AMERICAN STANDARD - YCY048G1HOAC | 114 | 5.8 | Yes | Yes | 18.5 | 20.2 | -1.7 | 4CF5837424E04686B9A981D4A3860B9B |  | R22 | Non-TXV |  | 5.088% | 0.94912 | 9.777% | [5 empty] | Non-TXV | 5.088%
Yuba City | CA | 95993-5185 |  | 2013-08-06 | 2013-08-06 13:29 | 2013-08-06 14:02 | BRYANT - 563CN042-D | 105 | 3.8 | Yes | Yes | 14 | 17 | -3 | 4727F12842C441D48ADC462D4318EDB9 |  | R22 | TXV |  | 3.619% | 0.96381 | 6.955% | [5 empty] | TXV | 3.619%
Fresno | CA | 93705-4437 |  | 2013-10-01 | 2013-10-01 10:34 | 2013-10-01 10:36 | COLEMAN - GCGD42S41S3A | 69 | 2.8 | Yes | Yes | 20.1 | 18.3 | 1.8 | A82E334ABD874B16B054CADCD1EA6920 |  | R410A | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Los Banos | CA | 93635-2609 |  | 2013-08-01 | 2013-08-01 15:35 | 2013-08-01 15:39 | BRYANT - 561CJ042-B | 90 | 2.7 | Yes | Yes | 21.4 | 21.3 | 0.1 | B3A7505AF6C54746BCA3392B842B5892 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95207-4418 |  | 2013-08-06 | 2013-08-06 16:39 | 2013-08-06 17:11 | ICP - TCA036AKC4 | 96 | 4.8 | Yes | Yes | 19.2 | 19.6 | -0.3 | A8BA815D51AF4E5681F466D5C803498D |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93703-1571 |  | 2013-08-07 | 2013-08-07 14:08 | 2013-08-07 14:09 | YORK - DCYPF02445A | 100 | 11.2 | Yes | Yes | 18.1 | 17.9 | 0.2 | EDAA3379A5614571B05D9C2AA3D7B4E7 |  | R22 | Non-TXV |  | 11.2% | 0.888 | 21.52% | [5 empty] | Non-TXV | 11.2%
Red Bluff | CA | 96080-9027 |  | 2013-08-09 | 2013-08-09 19:56 | 2013-08-09 20:15 | YORK - CMAO4811A | 116 | 5.3 | Yes | Yes | 18.3 | 20.7 | -2.4 | 67BE95CC41BB4497BEE3D7BA0615106D |  | R22 | Non-TXV |  | 4.569% | 0.95431 | 8.781% | [5 empty] | Non-TXV | 4.569%
Selma | CA | 93662-3820 |  | 2013-08-01 | 2013-08-01 09:53 | 2013-08-01 11:56 | ICP - NAC036AKC3 | 94 | 11.7 | Yes | Yes | 24 | 19.6 | 4.4 | 604E66A45BF444F2A43F4B40D6C94059 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.45% | 0.87553 | 23.92% | [5 empty] | Non-TXV | 12.45%
Chowchilla | CA | 93610-3427 |  | 2013-08-14 | 2013-08-14 11:56 | 2013-08-14 11:58 | RUUD - URKAA030JK06E | 54 | 6.4 | Yes | Yes | 22 | 17.8 | 4.3 | 8ADA38FD88FA4F20AA2DE4842BA02D40 |  | R22 | Non-TXV |  | 11.85% | 0.88148 | 22.78% | [5 empty] | Non-TXV | 11.85%
Riverbank | CA | 95367-2966 |  | 2013-08-20 | 2013-08-20 11:36 | 2013-08-20 12:05 | GOODMAN - CBD | 64 | 8.6 | Yes | Yes | 19 | 21 | -2 | F43F3AC4CADE408B9C37CE8D08DC6346 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
Merced | CA | 95348-2248 |  | 2013-08-15 | 2013-08-15 15:18 | 2013-08-15 15:19 | CARRIER - 585BJ018 | 55 | 6.3 | Yes | Yes | 18.7 | 18.7 | 0 | 5D956DE52101436A8B41F0AF555675ED |  | R22 | Non-TXV |  | 11.45% | 0.88545 | 22.01% | [5 empty] | Non-TXV | 11.45%
Chowchilla | CA | 93610-2444 |  | 2013-09-04 | 2013-09-04 16:37 | 2013-09-04 16:39 | YORK - D1NA036N05606A | 63 | 2.1 | Yes | Yes | 19.1 | 19.6 | -0.5 | 810786EE877D43F8910041823EBB28D6 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Red Bluff | CA | 96080-3719 |  | 2013-09-20 | 2013-09-20 13:37 | 2013-09-20 14:04 | OTHER - 597CN036-F | 98 | 5.5 | Yes | Yes | 23.5 | 22.6 | 0.9 | 631C9C1CF36E4159BC45650BF334F053 |  | R22 | TXV |  | 5.612% | 0.94388 | 10.79% | [5 empty] | TXV | 5.612%
Chico | CA | 95973-1144 |  | 2013-08-07 | 2013-08-07 08:36 | 2013-08-07 09:14 | RHEEM - RAJC-042JAS | 99 | 3.1 | Yes | Yes | 21.5 | 21.5 | 0 | C6428D27CED14A0E920F5CE3C6E01DE2 |  | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Merced | CA | 95348-9617 |  | 2013-08-26 | 2013-08-26 08:29 | 2013-08-26 08:31 | NORDYNE - JS3BA036KA | 69 | 6.1 | Yes | Yes | 20.6 | 17.7 | 2.9 | D566CFD6EA5F4651B53777723A3875AD |  | R22 | Non-TXV |  | 8.841% | 0.91159 | 16.99% | [5 empty] | Non-TXV | 8.841%
Fresno | CA | 93722-5126 |  | 2013-08-07 | 2013-08-07 14:28 | 2013-08-07 14:29 | CARRIER - 48ESNA360603TP | 100 | 4.4 | Yes | Yes | 24.8 | 20.4 | 4.4 | E076010313D94A4C84DF6F43A1420116 |  | R410A | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Fresno | CA | 93725-1828 |  | 2013-08-06 | 2013-08-06 14:12 | 2013-08-06 14:16 | OTHER - HABD-F036SG | 145 | 4.9 | Yes | Yes | 25.9 | 19.9 | 6 | 22CABA4385824C278D5BACCDAD6565ED |  | R22 | Non-TXV |  | 3.379% | 0.96621 | 6.494% | [5 empty] | Non-TXV | 3.379%
Clovis | CA | 93619-0000 |  | 2013-08-15 | 2013-08-15 09:06 | 2013-08-15 09:43 | RHEEM - N/A | 120 | 13.1 | Yes | Yes | 17.8 | 20.4 | -2.6 | CA2C93C4E69545F1ADDA5A53DEE680EF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.92% | 0.89083 | 20.98% | [5 empty] | Non-TXV | 10.92%
Clovis | CA | 93619-0000 |  | 2013-08-15 | 2013-08-15 09:46 | 2013-08-15 10:04 | RHEEM - N/A | 120 | 6.5 | Yes | Yes | 20.5 | 20.4 | 0.1 | 3C9CB3D44BEA41A894A3AD1133311055 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Merced | CA | 95348-2021 |  | 2013-08-15 | 2013-08-15 15:03 | 2013-08-15 15:05 | YORK - D1NP036N05606A | 108 | 4.6 | Yes | Yes | 20.1 | 19.2 | 0.9 | CAE1A16BAC0D4C59A18698D6B1B25D3C |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Placerville | CA | 95667-8974 |  | 2013-08-26 | 2013-08-26 15:28 | 2013-08-26 15:51 | CARRIER - 25HBS348A300 | 180 | 6.6 | Yes | Yes | 19 | 21.5 | -2.5 | 7866B6F2F2DE4CAE9FBA5DB5F65702CB |  | R22 | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Atwater | CA | 95301-9731 |  | 2013-08-14 | 2013-08-14 16:18 | 2013-08-14 16:40 | YORK - TCGD30S41S1HA | 62 | 6.6 | Yes | Yes | 22.3 | 21 | 1.3 | C8FFB3303952483A8366095F06B4ADC5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 10.65% | 0.89355 | 20.46% | [5 empty] | Non-TXV | 10.65%
Lincoln | CA | 95648-0000 |  | 2013-08-06 | 2013-08-06 15:51 | 2013-08-06 16:10 | YORK - H2RC030S06A | 88 | 5.4 | Yes | Yes | 17.4 | 19.7 | -2.3 | 8CA75DFDF8E840759AFC8ED9B296CD52 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.136% | 0.93864 | 11.79% | [5 empty] | Non-TXV | 6.136%
Red Bluff | CA | 96080-4138 |  | 2013-09-25 | 2013-09-25 14:28 | 2013-09-25 14:56 | DAY & NIGHT - 585T024055YACR | 79 | 5.2 | Yes | Yes | 17 | 19.3 | -2.3 | 9AAC4B52D5AF4AE2967AD8D34AB1D660 |  | R22 | Non-TXV |  | 6.582% | 0.93418 | 12.65% | [5 empty] | Non-TXV | 6.582%
Stockton | CA | 95210-1214 |  | 2013-08-01 | 2013-08-01 14:14 | 2013-08-01 14:37 | RHEEM - RAND042JAZ | 134 | 13.9 | Yes | Yes | 23.1 | 19.7 | 3.4 | 7BCE2CC612EA471F8938E3DFBFCDFECC |  | R22 | Non-TXV |  | 10.37% | 0.89627 | 19.93% | [5 empty] | Non-TXV | 10.37%
Red Bluff | CA | 96080-2806 |  | 2013-08-13 | 2013-08-13 13:33 | 2013-08-13 13:33 | WESTINGHOUSE - 55025CAV | 101 | 0 | Yes | Yes | 15.9 | 18.7 | -2.8 | 7B796101202E44C9AD3120C3F0C17532 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atascadero | CA | 93422-4526 |  | 2013-08-08 | 2013-08-08 14:27 | 2013-08-08 14:49 | ICP - GPCM24K040F | 58 | 1.8 | Yes | Yes | 19.8 | 21.9 | -2.1 | 54D10B6A005A4C43AF20200FB99146FC |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Chico | CA | 95928-7656 |  | 2013-08-27 | 2013-08-27 13:57 | 2013-08-27 14:16 | BRYANT - 563CN030-B | 100 | -5.9 | Yes | Yes | 21.6 | 18.3 | 3.3 | E450ACCED3DC4C55813AABF84A6AE22D |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Merced | CA | 95340-0904 |  | 2013-08-15 | 2013-08-15 16:00 | 2013-08-15 16:02 | GOODMAN - PGB024050 | 54 | 8.2 | Yes | Yes | 9.3 | 10.8 | -1.5 | D73F3FEDD4E2459A8B7316A2116A4F7B |  | R22 | Non-TXV |  | 15.19% | 0.84815 | 29.18% | [5 empty] | Non-TXV | 15.19%
Grass Valley | CA | 95945-4330 |  | 2013-08-05 | 2013-08-05 09:17 | 2013-08-05 09:17 | COLEMAN - DRCS0361BEG | 83 | 0 | Yes | Yes | 21.7 | 19.5 | 2.2 | C814E45039E24E26B45F09A616DE9CDA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-7004 |  | 2013-08-06 | 2013-08-06 14:22 | 2013-08-06 14:22 | LENNOX - 14ACX-060-230-10 | 192 | 0 | Yes | Yes | 20.6 | 19.9 | 0.7 | D7F862BB4577450FB0D85E14F27BDD25 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-8332 |  | 2013-08-14 | 2013-08-14 10:59 | 2013-08-14 11:18 | BRYANT - 563CN042-D | 107 | 6.1 | Yes | Yes | 19.1 | 18.5 | 0.6 | 8EE30543197E4CCCA9CD4325B52718C7 |  | R22 | Non-TXV |  | 5.701% | 0.94299 | 10.96% | [5 empty] | Non-TXV | 5.701%
Valley Springs | CA | 95252-0000 |  | 2013-08-14 | 2013-08-14 14:32 | 2013-08-14 15:11 | NORDYNE - S5QD-048K- | 147 | 9.7 | Yes | Yes | 24.3 | 20.9 | 3.4 | 5AD8A6817DF349E09A74F30AA7E45672 |  | R22 | Non-TXV |  | 6.599% | 0.93401 | 12.68% | [5 empty] | Non-TXV | 6.599%
Madera | CA | 93638-2295 |  | 2013-09-10 | 2013-09-10 15:13 | 2013-09-10 15:14 | YORK - BRCS0481BD | 117 | 12.2 | Yes | Yes | 27.7 | 23.7 | 4 | 32B7418FC3DE4C7F81BF068ED97A9B86 |  | R22 | Non-TXV |  | 10.43% | 0.89573 | 20.04% | [5 empty] | Non-TXV | 10.43%
Madera | CA | 93638-2295 |  | 2013-08-06 | 2013-08-06 18:47 | 2013-08-06 18:47 | CARRIER - 38EN048320 | 117 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | C5F34931302547A7A8BD19BCDE90D32F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1228 |  | 2013-08-15 | 2013-08-15 10:10 | 2013-08-15 10:12 | BRYANT - 588ANW030060ADAD | 53 | 2.3 | Yes | Yes | 18.1 | 18.5 | -0.3 | 50EBFFAAE36C4BA6B7A18008D779AE5D |  | R22 | Non-TXV |  | 4.34% | 0.9566 | 8.34% | [5 empty] | Non-TXV | 4.34%
Fresno | CA | 93710-6106 |  | 2013-08-11 | 2013-08-11 00:59 | 2013-08-11 01:25 | OTHER - UNK | 53 | 2.7 | Yes | Yes | 20.8 | 19.5 | 1.3 | FC2B2C7E0BE24E4AB99A1CE7FE5263DA |  | R22 | Non-TXV |  | 5.094% | 0.94906 | 9.79% | [5 empty] | Non-TXV | 5.094%
Merced | CA | 95340-0904 |  | 2013-08-15 | 2013-08-15 16:24 | 2013-08-15 16:26 | TRANE - YCC024F1LOBJ | 66 | 5.7 | Yes | Yes | 22.3 | 19.9 | 2.4 | DCDD5321904A4A968211DA5A8861A3D1 |  | R22 | Non-TXV |  | 8.636% | 0.91364 | 16.6% | [5 empty] | Non-TXV | 8.636%
Sonora | CA | 95370-5759 |  | 2013-09-05 | 2013-09-05 11:54 | 2013-09-05 12:16 | TRANE - 4TTB3036E1000AA | 92 | 6.1 | Yes | Yes | 18 | 20.4 | -2.4 | DF08EB2AC2504883B397BF07E2E9446B |  | R410A | Non-TXV |  | 6.63% | 0.9337 | 12.74% | [5 empty] | Non-TXV | 6.63%
Red Bluff | CA | 96080-7759 |  | 2013-08-09 | 2013-08-09 13:02 | 2013-08-09 13:44 | PAYNE - PA10JA042-B | 85 | 3.1 | Yes | Yes | 22 | 20.4 | 1.6 | 48F354F697B14316B005FC1BD14BC3D8 |  | R22 | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Clovis | CA | 93612-2336 |  | 2013-08-09 | 2013-08-09 08:32 | 2013-08-09 08:36 | YORK - AC024X1322B | 88 | 6.9 | Yes | Yes | 16.7 | 16.2 | 0.5 | FFD7274B481C411B85C7430DA66BA8A5 |  | R22 | Non-TXV |  | 7.841% | 0.92159 | 15.07% | [5 empty] | Non-TXV | 7.841%
Dos Palos | CA | 93620-0000 |  | 2013-08-05 | 2013-08-05 15:53 | 2013-08-05 16:01 | OTHER - TZAA-342-2A757 | 110 | 4.5 | Yes | Yes | 24.2 | 21.4 | 2.8 | 91FA854C824A44BA917D0EA4BC05D642 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Grass Valley | CA | 95949-6652 |  | 2013-08-23 | 2013-08-23 09:56 | 2013-08-23 09:56 | RHEEM - UNK | 76 | 0 | Yes | Yes | 24.4 | 19.7 | 4.7 | 7160D119A0104716855175BE09C29DBD | OK: Verified Refrigerant Charge Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Chico | CA | 95973-9523 |  | 2013-08-07 | 2013-08-07 15:04 | 2013-08-07 17:58 | TRANE - 2TTR1024A1000AA | 62 | 6.1 | Yes | Yes | 21.9 | 20.3 | 1.6 | B2E839DB58A849039D1A5DDEDC787100 |  | R22 | Non-TXV |  | 9.839% | 0.90161 | 18.91% | [5 empty] | Non-TXV | 9.839%
Chico | CA | 95973-7232 |  | 2013-08-08 | 2013-08-08 15:21 | 2013-08-08 15:36 | TRANE - TTN048D100A0 | 129 | 12.4 | Yes | Yes | 18.3 | 18.8 | -0.5 | 286D9FADBD054ECDB56E88551AAB2D3E |  | R22 | TXV |  | 9.612% | 0.90388 | 18.47% | [5 empty] | TXV | 9.612%
Atwater | CA | 95301-3726 |  | 2013-09-03 | 2013-09-03 09:14 | 2013-09-03 09:41 | PAYNE - CBD | 64 | 1.9 | Yes | Yes | 20.2 | 18.7 | 1.5 | 6E9C24BE29CA4928A3AA7147B72DDE08 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Dos Palos | CA | 93620-2733 |  | 2013-08-14 | 2013-08-14 14:58 | 2013-08-14 15:00 | BRYANT - 601ANX02400AAAD | 82 | 5.4 | Yes | Yes | 17.3 | 18.9 | -1.6 | 9EF5DBBD95A44CA08ADB726B0A9259F9 |  | R22 | Non-TXV |  | 6.585% | 0.93415 | 12.66% | [5 empty] | Non-TXV | 6.585%
Sonora | CA | 95370-5315 |  | 2013-10-14 | 2013-10-14 12:23 | 2013-10-14 12:53 | BDP - 561AJ048-B | 102 | -7.2 | Yes | Yes | 23.4 | 18.2 | 5.2 | B08D67D753214EBDBD04C0F2C5C3A7AE |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Valley Springs | CA | 95252-9538 |  | 2013-09-12 | 2013-09-12 13:57 | 2013-09-12 14:16 | PAYNE - PY3GNAA30060NA | 105 | 3.6 | Yes | Yes | 22.7 | 20.7 | 2 | 8BF0DA64DD9C42C6A28B85F08F820A45 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Plumas Lake | CA | 95961-9085 |  | 2013-08-19 | 2013-08-19 17:04 | 2013-08-19 17:22 | CARRIER - 38CKC030340 | 65 | 7.6 | Yes | Yes | 16 | 18.7 | -2.7 | 78556374B84D474EA68397855ECA2997 |  | R22 | Non-TXV |  | 11.69% | 0.88308 | 22.47% | [5 empty] | Non-TXV | 11.69%
Atwater | CA | 95301-4722 |  | 2013-08-14 | 2013-08-14 08:50 | 2013-08-14 09:20 | PAYNE - PA13NR042-H | 112 | 3.9 | Yes | Yes | 22.1 | 20.4 | 1.7 | 9584E4379C0F44E7AE38F84056AC5496 |  | R22 | Non-TXV |  | 3.482% | 0.96518 | 6.692% | [5 empty] | Non-TXV | 3.482%
Chico | CA | 95926-2607 |  | 2013-08-06 | 2013-08-06 15:21 | 2013-08-06 15:46 | DAY & NIGHT - N4A330AKC200 | 74 | 3.7 | Yes | Yes | 16.9 | 18.4 | -1.5 | D5BC50B4B4F046C098025F173E6C0160 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93726-3527 |  | 2013-09-20 | 2013-09-20 16:40 | 2013-09-20 16:58 | RHEEM - RRNL-B024JK06X | 77 | 3.4 | Yes | Yes | 17.6 | 20.4 | -2.8 | 19A3B06B1D6D40C1960C559AB621FD99 |  | R410A | TXV |  | 4.416% | 0.95584 | 8.486% | [5 empty] | TXV | 4.416%
Fresno | CA | 93711-2659 |  | 2013-08-28 | 2013-08-28 08:14 | 2013-08-28 08:17 | GOODMAN - GSC13D241DB | 82 | 4 | Yes | Yes | 19.6 | 22.1 | -2.5 | 17A79E6A952C4C2D8DFE075638D048C7 |  | R22 | Non-TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | Non-TXV | 4.878%
Merced | CA | 95340-3024 |  | 2013-08-06 | 2013-08-06 15:21 | 2013-08-06 15:44 | YORK - D1NH060N09006C | 140 | 4.6 | Yes | Yes | 28.5 | 22.8 | 5.7 | 4798F05AF3054C8A804CBC113D75FB74 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Paso Robles | CA | 93446-2768 |  | 2013-08-07 | 2013-08-07 11:57 | 2013-08-07 12:19 | PAYNE - PY3GNAA3060NA | 100 | -7.1 | Yes | Yes | 21.8 | 16.2 | 5.7 | 59F2DE1BA0E4496B89C031C13EDC36DB |  | R410A | Non-TXV |  | -7.1% | 1.071 | 1.988% |  |  |  |  | Non-TXV |  |  | -7.1%
Fresno | CA | 93704-1548 |  | 2013-08-09 | 2013-08-09 10:51 | 2013-08-09 10:52 | PAYNE - PA10JA36G | 72 | 4.6 | Yes | Yes | 17.4 | 17.7 | -0.3 | 17704B4F4DB3415598C406CF50D04F42 |  | R22 | TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | TXV | 6.389%
Paso Robles | CA | 93446-4054 |  | 2013-08-07 | 2013-08-07 12:24 | 2013-08-07 12:44 | HEIL - UNK | 102 | 3.1 | Yes | Yes | 19.5 | 18.3 | 1.2 | 61C007DB00FF490284D7B04389269184 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Chowchilla | CA | 93610-3234 |  | 2013-08-22 | 2013-08-22 23:57 | 2013-08-26 02:22 | RHEEM - RRKA-A030JK06X | 81 | 2.5 | Yes | Yes | 25.5 | 20.9 | 4.6 | B7FDE2FBFFB94BCE85521F61F34730B4 |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Colfax | CA | 95713-0000 |  | 2013-08-27 | 2013-08-27 09:13 | 2013-08-27 09:35 | RHEEM - UNK | 80 | 5.1 | Yes | Yes | 26 | 21.5 | 4.5 | 9512AFA528AE400180D28FE90729C298 |  | R22 | TXV |  | 6.375% | 0.93625 | 12.25% | [5 empty] | TXV | 6.375%
Rough & Ready | CA | 95975-9731 |  | 2013-08-26 | 2013-08-26 17:22 | 2013-08-26 17:22 | AMERICAN STANDARD - 4YCY4048A1120AB | 131 | 0 | Yes | Yes | 24.7 | 22.4 | 2.4 | 9ABD0EE5E1214AE786861BFCCE9C9ACE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-6090 |  | 2013-08-07 | 2013-08-07 16:36 | 2013-08-07 16:55 | LENNOX - 10ACC-036-230-02 | 74 | 2.9 | Yes | Yes | 18 | 20.4 | -2.4 | 4F8C0D9CB8734DE580987D26A6D9532B |  | R22 | TXV |  | 3.919% | 0.96081 | 7.531% | [5 empty] | TXV | 3.919%
Red Bluff | CA | 96080-3943 |  | 2013-08-13 | 2013-08-13 15:27 | 2013-08-13 18:37 | BRYANT - PA13NR024J | 72 | 3.5 | Yes | Yes | 18.5 | 21.2 | -2.7 | E66E13FE6C554BB1A12324021274B19E |  | R22 | TXV |  | 4.861% | 0.95139 | 9.342% | [5 empty] | TXV | 4.861%
Chowchilla | CA | 93610-2116 |  | 2013-08-14 | 2013-08-14 10:43 | 2013-08-14 10:45 | CARRIER - 48KLA136300BE | 95 | 12.8 | Yes | Yes | 22.5 | 19.9 | 2.6 | 0D2208E839B449C4BFF992DBCCDB87E0 |  | R22 | Non-TXV |  | 13.47% | 0.86526 | 25.89% | [5 empty] | Non-TXV | 13.47%
Stockton | CA | 95215-5905 |  | 2013-08-13 | 2013-08-13 15:29 | 2013-08-13 15:50 | GE - BGTA830R1C | 82 | 8.6 | Yes | Yes | 23.6 | 20.4 | 3.2 | E778E5540DF847DE9AD36B9D0D1BDAF9 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 10.49% | 0.89512 | 20.16% | [5 empty] | TXV | 10.49%
Valley Springs | CA | 95252-9382 |  | 2013-09-05 | 2013-09-05 15:20 | 2013-09-05 15:40 | YORK - D1NP048N06506A | 132 | 3.9 | Yes | Yes | 21.7 | 20.4 | 1.3 | F6A8057B06124974A390625F61127EE4 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Atwater | CA | 95301-2081 |  | 2013-08-21 | 2013-08-21 08:57 | 2013-08-21 09:22 | RHEEM - CBD | 64 | 3.5 | Yes | Yes | 23.4 | 21 | 2.4 | 2305F8CBFDB24638833318632B69CFE5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.469% | 0.94531 | 10.51% | [5 empty] | Non-TXV | 5.469%
Dos Palos | CA | 93620-9429 |  | 2013-08-16 | 2013-08-16 10:36 | 2013-08-16 10:39 | BRYANT - 563CN048-D | 167 | 5.3 | Yes | Yes | 21.7 | 17.4 | 4.3 | 6E0EEAF0F8EB410CB41BBFE593FCA43B |  | R22 | Non-TXV |  | 3.174% | 0.96826 | 6.099% | [5 empty] | Non-TXV | 3.174%
Stockton | CA | 95205-7738 |  | 2013-08-02 | 2013-08-02 16:48 | 2013-08-02 18:46 | BDP - 588ANW048080AAAG | 101 | 3.1 | Yes | Yes | 22.4 | 24.4 | -2 | 80CEABCB9A94487A8DDE8F5E726C8097 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Newcastle | CA | 95658-9415 |  | 2013-09-03 | 2013-09-03 15:46 | 2013-09-03 16:05 | TRANE - TTY060B100A0 | 170 | 12.6 | Yes | Yes | 20 | 20.6 | -0.6 | 514F68BE40984E829A680A94E594600D |  | R22 | TXV |  | 7.412% | 0.92588 | 14.24% | [5 empty] | TXV | 7.412%
Yuba City | CA | 95991-8415 |  | 2013-08-29 | 2013-08-29 16:02 | 2013-08-29 16:36 | OTHER - CJ30-1FB | 110 | 6.3 | Yes | Yes | 20 | 21.2 | -1.2 | 36496566DEC243F5AD2F4E63F157BAB4 |  | R22 | Non-TXV |  | 5.727% | 0.94273 | 11.01% | [5 empty] | Non-TXV | 5.727%
Rough & Ready | CA | 95975-0000 |  | 2013-08-26 | 2013-08-26 15:04 | 2013-08-26 15:21 | DAY & NIGHT - 589ANW048120ADG | 93 | 10.2 | Yes | Yes | 23.6 | 21 | 2.6 | 960103064E9A49BF89E5414A389BC0FB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.97% | 0.89032 | 21.08% | [5 empty] | Non-TXV | 10.97%
Dos Palos | CA | 93620-2406 |  | 2013-08-17 | 2013-08-17 10:33 | 2013-08-17 10:36 | TRANE - BTD724A10002 | 68 | 5.4 | Yes | Yes | 19.6 | 19.1 | 0.5 | 7D7AA1EBA1124423B00BE7168E93287E |  | R22 | Non-TXV |  | 7.941% | 0.92059 | 15.26% | [5 empty] | Non-TXV | 7.941%
Rocklin | CA | 95765-5425 |  | 2013-08-29 | 2013-08-29 08:51 | 2013-08-29 09:10 | UNITARY PRODUCTS GROUP - H1RC060S06D | 147 | 9.6 | Yes | Yes | 20.9 | 17.6 | 3.3 | 43E3AF7A501D4B55A880311A5432E444 |  | R22 | Non-TXV |  | 6.531% | 0.93469 | 12.55% | [5 empty] | Non-TXV | 6.531%
Clovis | CA | 93611-2002 |  | 2013-08-16 | 2013-08-16 09:50 | 2013-08-16 10:36 | LENNOX - 12GCS042X-75-3PA | 133 | 4.9 | Yes | Yes | 23.5 | 20.9 | 2.6 | F2811410511045D495E7A0C27C4A3C7C |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Fresno | CA | 93720-0272 |  | 2013-08-29 | 2013-08-29 20:52 | 2013-08-29 20:58 | OTHER - WC3422GKR2 | 112 | 3.4 | Yes | Yes | 17.9 | 18.8 | -0.9 | ED98449FC18645B18558EA13BF99D9E0 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Stockton | CA | 95209-1116 |  | 2013-08-02 | 2013-08-02 12:55 | 2013-08-02 13:19 | BDP - 567C036RCU4379C31046 | 67 | -3.9 | Yes | Yes | 18.4 | 19.7 | -1.3 | 947019290B7948F5804B5D74A9221779 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Lodi | CA | 95240-9714 |  | 2013-09-06 | 2013-09-06 15:44 | 2013-09-06 15:44 | CARRIER - 38EC048EDC310 | 115 | 0 | Yes | Yes | 18.9 | 18.5 | 0.4 | 2299023B76B34A2A89ABE5C26DBADF21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4433 |  | 2013-08-13 | 2013-08-13 17:49 | 2013-08-13 18:06 | LENNOX - 10GCS036X-75-3PA | 58 | 5 | Yes | Yes | 22.8 | 21.4 | 1.4 | 870454D84D754BB6A551F21A48279C20 |  | R22 | Non-TXV |  | 8.621% | 0.91379 | 16.57% | [5 empty] | Non-TXV | 8.621%
Stockton | CA | 95204-3928 |  | 2013-08-02 | 2013-08-02 14:58 | 2013-08-02 14:58 | GOODMAN - CRY18-1 | 94 | 0 | Yes | Yes | 16.7 | 19.7 | -3 | 1AA5E1456CD54DA79FDDE7A762AFA6DE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-8028 |  | 2013-08-05 | 2013-08-05 17:20 | 2013-08-05 17:20 | ICP - HAC060AKA1 | 131 | 0 | Yes | Yes | 24.6 | 21.5 | 3.1 | 40B9ECE6954E4CD0B6F9CAB66CFEDCE0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-9564 |  | 2013-08-09 | 2013-08-09 12:08 | 2013-08-09 12:32 | PAYNE - PY2PNB036060AAAA | 85 | 3.1 | Yes | Yes | 16 | 17.7 | -1.7 | A266990277BE4B19A2AFBA4588EEB4D4 |  | R22 | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Fresno | CA | 93727-3016 |  | 2013-08-14 | 2013-08-14 16:19 | 2013-08-14 16:37 | CARRIER - UNK | 64 | 3.2 | Yes | Yes | 19.3 | 20.6 | -1.3 | 974375EE164A464290DE5F630BBD61B0 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95205-2573 |  | 2013-08-02 | 2013-08-02 11:47 | 2013-08-02 12:11 | RUUD - UNK | 85 | 7.9 | Yes | Yes | 25.5 | 21.9 | 3.6 | D8F2676ABFD24EE38CE7705406CCABDC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | Non-TXV | 9.294%
Oakhurst | CA | 93644-8579 |  | 2013-08-14 | 2013-08-14 11:32 | 2013-08-14 12:31 | OTHER - 867.815015 | 53 | -5 | Yes | Yes | 18.1 | 20.3 | -2.2 | E4D24A5A71B84EF9B93E65E6C3955287 |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Stockton | CA | 95206-6011 |  | 2013-08-12 | 2013-08-12 14:40 | 2013-08-12 15:03 | GOODMAN - CE30-1HB | 72 | 21.1 | Yes | Yes | 17.9 | 19.9 | -2 | C5EF468605FC4E8D8552A75917EFB186 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 29.31% | 0.70694 | 56.32% | [5 empty] | Non-TXV | 29.31%
Sanger | CA | 93657-8771 |  | 2013-08-03 | 2013-08-03 17:06 | 2013-08-03 17:37 | LENNOX - 13GCSXA-36-068-230-1A | 125 | 9.7 | Yes | Yes | 17 | 18.5 | -1.5 | 3CE5B8A04E374CBDB1FD7599904A713F |  | R410A | TXV |  | 7.76% | 0.9224 | 14.91% | [5 empty] | TXV | 7.76%
Marysville | CA | 95901-6541 |  | 2013-08-20 | 2013-08-20 14:59 | 2013-08-20 15:16 | OTHER - 561CJ042-A | 80 | -10.6 | Yes | Yes | 19 | 19.2 | -0.2 | 0FEA57C898C14F59B1EE060D781CB7ED |  | R22 | TXV |  | -13.25% | 1.1325 | 3.711% |  |  |  |  | TXV |  |  | -13.25%
Paso Robles | CA | 93446-3616 |  | 2013-08-08 | 2013-08-08 13:15 | 2013-08-08 13:33 | GOODMAN - CKL24-1K | 76 | 5.5 | Yes | Yes | 19.9 | 19 | 0.9 | E3C3D3AC7BF048608FB90A5AFE8A047F |  | R22 | Non-TXV |  | 7.237% | 0.92763 | 13.91% | [5 empty] | Non-TXV | 7.237%
Oroville | CA | 95965-8111 |  | 2013-09-24 | 2013-09-24 12:27 | 2013-09-24 12:45 | CARRIER - 585H2W042ACAF | 85 | 2.6 | Yes | Yes | 26.1 | 20.4 | 5.7 | 5D2AAF3EE3614A1CAA6F3F76A32BDF35 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Chico | CA | 95928-5639 |  | 2013-08-28 | 2013-08-28 10:53 | 2013-08-28 13:39 | LENNOX - HS18-261-8P | 42 | -2.5 | Yes | Yes | 25.3 | 19.3 | 6 | D73099FA6CFE45118B51FEF24E66C6CF |  | R22 | Non-TXV |  | -5.952% | 1.0595 | 1.667% |  |  |  |  | Non-TXV |  |  | -5.952%
Oroville | CA | 95966-5761 |  | 2013-08-12 | 2013-08-12 13:40 | 2013-08-12 14:23 | COLEMAN - TCG036S21S1A | 65 | 3.6 | Yes | Yes | 21.5 | 21.2 | 0.3 | 6DCDFCB826CA4666B3FD932BA2062AA9 |  | R22 | Non-TXV |  | 5.538% | 0.94462 | 10.64% | [5 empty] | Non-TXV | 5.538%
Stockton | CA | 95210-3663 |  | 2013-08-01 | 2013-08-01 12:15 | 2013-08-01 12:41 | PAYNE - 2789E10866 | 85 | -5 | Yes | Yes | 27.9 | 22 | 5.9 | 29A20F539E2E4F6FAD87FBB14776EADB |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Sanger | CA | 93657-9309 |  | 2013-08-03 | 2013-08-03 15:58 | 2013-08-03 19:41 | ICP - AG048GB2 | 134 | 4.3 | Yes | Yes | 19.5 | 18.8 | 0.7 | 2B7E35A72AC240668918ACBA31B6910F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.209% | 0.96791 | 6.167% | [5 empty] | Non-TXV | 3.209%
Parlier | CA | 93648-2338 |  | 2013-09-04 | 2013-09-04 18:03 | 2013-09-04 19:37 | CONCORD - CCU10A18A-2 | 60 | 3.4 | Yes | Yes | 17.5 | 20.1 | -2.6 | 37A4A5DDF4E8456AA87698D78C848B8A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Fresno | CA | 93710-6106 |  | 2013-08-11 | 2013-08-11 01:35 | 2013-08-11 01:35 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 19.5 | 19 | 0.5 | D2C6FEF8A17941A3A975E90465E3054D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3220 |  | 2013-08-20 | 2013-08-20 11:35 | 2013-08-20 11:39 | YORK - D3GA036N07006A | 84 | 12.2 | Yes | Yes | 20.9 | 20.1 | 0.8 | 59709E7264474F5C96DED321F86627A6 |  | R22 | Non-TXV |  | 14.52% | 0.85476 | 27.91% | [5 empty] | Non-TXV | 14.52%
Stockton | CA | 95207-4715 |  | 2013-08-05 | 2013-08-05 16:36 | 2013-08-05 16:36 | GUARDIAN - GCGD4821SA | 75 | 0 | Yes | Yes | 26.8 | 21 | 5.8 | 1EFEF7AC96E84881AB6603C70A363685 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4149 |  | 2013-08-09 | 2013-08-09 13:20 | 2013-08-09 13:20 | CARRIER - 38TXA036330 | 104 | 0 | Yes | Yes | 25.1 | 19.2 | 5.9 | 088305D68AF647EC9675EF72A625A503 |  | R410A | TXV |  | 0% | 1 | 0%
El Dorado | CA | 95623-4965 |  | 2013-08-30 | 2013-08-30 09:51 | 2013-08-30 10:08 | CARRIER - 38CKC042350 | 93 | -8.8 | Yes | Yes | 19 | 20.9 | -1.9 | B0FFE4C0D3764E0E9772360A0D675925 |  | R22 | Non-TXV |  | -9.462% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.462%
Penn Valley | CA | 95946-9611 |  | 2013-08-15 | 2013-08-15 17:12 | 2013-08-15 17:34 | COLEMAN - ERCS0481BBA | 134 | 5.3 | Yes | Yes | 28 | 23.5 | 4.5 | 8AAE518A2659464DBD23D4EC002B0C09 |  | R22 | Non-TXV |  | 3.955% | 0.96045 | 7.601% | [5 empty] | Non-TXV | 3.955%
Stockton | CA | 95205-5646 |  | 2013-08-15 | 2013-08-15 11:43 | 2013-08-15 11:47 | CARRIER - 38CKC036350 | 72 | 11 | Yes | Yes | 17.4 | 16.2 | 1.2 | 128C7E985CA247E2A9B8085DF245CEED | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.28% | 0.84722 | 29.36% | [5 empty] | Non-TXV | 15.28%
Chico | CA | 95973-0590 |  | 2013-10-21 | 2013-10-21 11:29 | 2013-10-21 12:03 | PAYNE - 565BJ018 | 50 | 4.5 | Yes | Yes | 17 | 19.8 | -2.8 | CFC622CB5F844CA6953F46BE9250B054 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Lincoln | CA | 95648-2733 |  | 2013-08-23 | 2013-08-23 11:52 | 2013-08-23 12:12 | YORK - AC036X1222A | 83 | -7.8 | Yes | Yes | 16 | 18.8 | -2.8 | 9CAC165F4DDB4C099075FEEA04EE2425 |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Tracy | CA | 95376-0764 |  | 2013-08-15 | 2013-08-15 13:36 | 2013-08-15 13:56 | TRANE - 2TTR1036A1000AA | 73 | 17.2 | Yes | Yes | 18.7 | 21.2 | -2.5 | 896131E29031444FB6B0FCAA9D2D45FC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 23.56% | 0.76438 | 45.28% | [5 empty] | Non-TXV | 23.56%
Tracy | CA | 95376-0764 |  | 2013-08-15 | 2013-08-15 13:58 | 2013-08-15 14:18 | TRANE - 2TTR1036A1000AA | 73 | 9.1 | Yes | Yes | 17.7 | 20.4 | -2.7 | E2DA63B2F631458896BEDDDD76EA6C81 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.47% | 0.87534 | 23.96% | [5 empty] | Non-TXV | 12.47%
Chico | CA | 95973-0585 |  | 2013-08-28 | 2013-08-28 15:30 | 2013-08-28 15:48 | NORDYNE - JS3BA-024KA | 54 | -3.2 | Yes | Yes | 24.4 | 20.1 | 4.3 | C97E42726E684D26A66361E587D0452E |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Olivehurst | CA | 95961-0000 |  | 2013-10-22 | 2013-10-22 14:23 | 2013-10-22 14:23 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 20 | 22.5 | -2.5 | 99D3E4AB517D424CB09A9A46ED07DFF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3033 |  | 2013-08-07 | 2013-08-07 13:14 | 2013-08-07 13:33 | YORK - H2RC036S06HG | 83 | -7.8 | Yes | Yes | 16.6 | 19.6 | -3 | B6FC18E642B64366B3F55FA2CAC7D7AC |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Lathrop | CA | 95330-9340 |  | 2013-08-02 | 2013-08-02 09:35 | 2013-08-02 10:08 | RHEEM - RAMA-036JAS | 96 | 4.6 | Yes | Yes | 17.9 | 19.8 | -1.9 | 11BDD7E6F0794381BACC08EEFDB8F6BB |  | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Oroville | CA | 95966-5759 |  | 2013-09-24 | 2013-09-24 14:00 | 2013-09-24 14:21 | COLEMAN - BRCQ0481BDG | 103 | 3.8 | Yes | Yes | 26.2 | 20.9 | 5.3 | 8C5D9D4189834691856595F0C50488BA |  | R22 | Non-TXV |  | 3.689% | 0.96311 | 7.09% | [5 empty] | Non-TXV | 3.689%
Lathrop | CA | 95330-9328 |  | 2013-08-02 | 2013-08-02 10:38 | 2013-08-02 11:07 | RHEEM - RAMA-036JAS | 96 | 3.6 | Yes | Yes | 22.3 | 20.4 | 1.9 | C88DD9CF7FDB4119A5ACBE8A9256A2FA |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Clovis | CA | 93612-5018 |  | 2013-08-07 | 2013-08-07 10:43 | 2013-08-07 10:45 | GOODMAN - PGB036075 | 68 | 3.8 | Yes | Yes | 21.3 | 18.2 | 3.1 | D7BA3D72B925447DAD374EB835C8CD23 |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Manteca | CA | 95336-3636 |  | 2013-08-12 | 2013-08-12 08:54 | 2013-08-12 09:19 | TRANE - TTN030C100C2 | 95 | 3.1 | Yes | Yes | 22.2 | 18.7 | 3.5 | 31ED09E7CBCC4FBCAD56525649921E40 |  | R22 | Non-TXV |  | 3.263% | 0.96737 | 6.271% | [5 empty] | Non-TXV | 3.263%
Rescue | CA | 95672-9649 |  | 2013-08-10 | 2013-08-10 19:05 | 2013-08-10 19:25 | AMANA - ZRCF36U01D | 107.1 | -13.2 | Yes | Yes | 26.2 | 20.4 | 5.8 | 331E01570701447B9668431BD775AB8C |  | R22 | TXV |  | -12.32% | 1.1232 | 3.452% |  |  |  |  | TXV |  |  | -12.32%
Fresno | CA | 93704-3502 |  | 2013-08-13 | 2013-08-13 14:12 | 2013-08-13 14:13 | NORDYNE - VR8GD036K072X | 59 | 4.4 | Yes | Yes | 24.3 | 22.3 | 2.1 | 2A127C3E0FED4C66A3FF536442C65BBC |  | R410A | Non-TXV |  | 7.458% | 0.92542 | 14.33% | [5 empty] | Non-TXV | 7.458%
Red Bluff | CA | 96080-3939 |  | 2013-08-09 | 2013-08-09 13:47 | 2013-08-09 20:16 | PAYNE - 567C024RCO | 60 | 1.9 | Yes | Yes | 18.7 | 19.5 | -0.8 | B083C7AC8F8C4834BAEA29A697F7BB16 |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Stockton | CA | 95205-7705 |  | 2013-08-13 | 2013-08-13 14:30 | 2013-08-13 14:33 | RHEEM - RRNA-B036JK08X | 83 | 9.3 | Yes | Yes | 24.8 | 19.3 | 5.5 | 2431378ED76F45E8B9C8A3166E3AECCD |  | R22 | Non-TXV |  | 11.2% | 0.88795 | 21.53% | [5 empty] | Non-TXV | 11.2%
Tracy | CA | 95376-3453 |  | 2013-08-01 | 2013-08-01 16:59 | 2013-08-02 10:11 | GOODMAN - CBD | 85 | 8.5 | Yes | Yes | 17.5 | 19.5 | -2 | 1A1D59AFD0D5400884CB367E3E7C817C |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Valley Springs | CA | 95252-9505 |  | 2013-08-14 | 2013-08-14 13:14 | 2013-08-14 13:42 | ICP - NAC024AKB1 | 67 | 7.2 | Yes | Yes | 22 | 20.7 | 1.3 | E9223046808C44AAB460BD8AE9D3EAB0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.75% | 0.89254 | 20.65% | [5 empty] | Non-TXV | 10.75%
Gustine | CA | 95322-9593 |  | 2013-09-17 | 2013-09-17 12:06 | 2013-09-17 12:08 | YORK - H2RA030S06D | 62 | 2.2 | Yes | Yes | 17.8 | 17 | 0.8 | B60B205040164AF480F7D373BFA99202 |  | R22 | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Stockton | CA | 95206-6403 |  | 2013-08-26 | 2013-08-26 12:14 | 2013-08-26 12:31 | GOODMAN - CLJ60-1 | 141 | 11.4 | Yes | Yes | 20.3 | 19.5 | 0.8 | D84F42D459A54DA8B4150231FB277BBF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.085% | 0.91915 | 15.54% | [5 empty] | Non-TXV | 8.085%
Tracy | CA | 95377-7201 |  | 2013-08-22 | 2013-08-22 12:55 | 2013-08-22 13:19 | CARRIER - 38CKC042300 | 80 | 9 | Yes | Yes | 17.3 | 16.8 | 0.5 | D8641608E96C4BED95CCE43743DBE7E3 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Madera | CA | 93637-6116 |  | 2013-09-05 | 2013-09-05 12:07 | 2013-09-05 12:08 | YORK - D1NA024N05606C | 54 | 6.3 | Yes | Yes | 21.4 | 19.3 | 2.1 | DAD2051F1A074B3FB2EF44F9089FFADA |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Grass Valley | CA | 95945-5529 |  | 2013-09-12 | 2013-09-12 13:40 | 2013-09-12 13:40 | CARRIER - 38TH030310 | 68 | 0 | Yes | Yes | 25.2 | 21.3 | 3.9 | E3769E4482A843EF9232C0068C4CC0B2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-2338 |  | 2013-08-28 | 2013-08-28 16:41 | 2013-08-28 16:41 | CONCORD - CCU10A18A-1 | 60 | 0 | Yes | Yes | 21 | 20.2 | 0.9 | 081AB85AA3AE4B56BFC966359371A0C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93636-9213 |  | 2013-08-23 | 2013-08-23 18:11 | 2013-08-25 15:35 | RHEEM - RQMNA-AO36JK 000 | 89 | 5.7 | Yes | Yes | 17.7 | 18.8 | -1.1 | C1C311F77F9F4830BAA31AB7A712DAE3 |  | R22 | Non-TXV |  | 6.404% | 0.93596 | 12.31% | [5 empty] | Non-TXV | 6.404%
Valley Springs | CA | 95225-0000 |  | 2013-08-14 | 2013-08-14 10:42 | 2013-08-14 11:02 | YORK - H5DB048S06A | 96 | 16.1 | Yes | Yes | 19.1 | 22.1 | -3 | 789C44550516452682943FE03443D423 |  | R22 | Non-TXV |  | 16.77% | 0.83229 | 32.23% | [5 empty] | Non-TXV | 16.77%
Jackson | CA | 95642-9659 |  | 2013-08-20 | 2013-08-20 12:41 | 2013-08-20 13:48 | PAYNE - 582ANW036090AAAF | 85 | 7.6 | Yes | Yes | 19.1 | 21.7 | -2.6 | 6F63AB5EBA904140AC710C0D13C6FC64 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Cameron Park | CA | 95682-8650 |  | 2013-08-15 | 2013-08-15 13:36 | 2013-08-15 13:58 | TRANE - YCC048F1H0BA | 128 | 8.6 | Yes | Yes | 17.3 | 19.3 | -2 | F7397825F88F4A229A35AE6E8B2314D5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.719% | 0.93281 | 12.91% | [5 empty] | Non-TXV | 6.719%
Lincoln | CA | 95648-8353 |  | 2013-08-22 | 2013-08-22 09:08 | 2013-08-22 09:27 | YORK - H2RC030S06A | 88 | 2.8 | Yes | Yes | 18 | 19.3 | -1.3 | DC5615A2C4684784A7C59018734EB43C |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Paso Robles | CA | 93446-4070 |  | 2013-08-15 | 2013-08-15 09:59 | 2013-08-15 11:10 | HEIL - UNK | 100 | 8.1 | Yes | Yes | 21.5 | 18.2 | 3.3 | DBD0ECF063A041C983AA570D1B3E1019 |  | R22 | Non-TXV |  | 8.1% | 0.919 | 15.57% | [5 empty] | Non-TXV | 8.1%
Red Bluff | CA | 96080-3939 |  | 2013-08-27 | 2013-08-27 15:24 | 2013-08-27 18:18 | PAYNE - 567C024RCU | 63 | 4.1 | Yes | Yes | 15.8 | 18.8 | -3 | AFF1FB60C281479F9A57084D1C67D950 |  | R22 | Non-TXV |  | 6.508% | 0.93492 | 12.51% | [5 empty] | Non-TXV | 6.508%
Cameron Park | CA | 95682-8648 |  | 2013-09-04 | 2013-09-04 14:48 | 2013-09-04 14:48 | AMERICAN STANDARD - 7A0042A100A1 | 86 | 0 | Yes | Yes | 22.3 | 21 | 1.3 | 5AA9171FBBE14350AB1F52F056F9EF0D |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5125 |  | 2013-08-13 | 2013-08-13 13:10 | 2013-08-13 13:13 | TRANE - TTD736B10000 | 80 | 3.2 | Yes | Yes | 23.1 | 19.8 | 3.3 | 3CF38FE4816840D988901E9A49737BB8 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95207-4425 |  | 2013-08-19 | 2013-08-19 11:37 | 2013-08-19 12:00 | OTHER - PGC036K080E | 68 | 2.6 | Yes | Yes | 17.7 | 19.5 | -1.8 | 24D22480FBC3480CA38B056695B57363 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Los Banos | CA | 93635-5125 |  | 2013-08-13 | 2013-08-13 12:48 | 2013-08-13 12:56 | TRANE - 1TD730B100A1 | 69 | 4.6 | Yes | Yes | 23.9 | 20.4 | 3.5 | FA9F82C16E62493FA60FABFFAC2F01CA |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Manteca | CA | 95336-4557 |  | 2013-08-12 | 2013-08-12 13:35 | 2013-08-12 13:55 | GOODMAN - GSH130241A A | 106 | 3.9 | Yes | Yes | 22.5 | 20.9 | 1.6 | 194C35C784B2481882C346BF3603F84A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | Non-TXV | 3.679%
Penn Valley | CA | 95946-9479 |  | 2013-09-16 | 2013-09-16 11:44 | 2013-09-16 11:44 | TRANE - TTP048C100A4 | 156 | 0 | Yes | Yes | 22 | 19.9 | 2.1 | 26CD19AFBB5C46F3BAA218C2C5DEE7AE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-3974 |  | 2013-08-27 | 2013-08-27 13:18 | 2013-08-27 15:22 | BRYANT - PA13R02400GAJAA | 72 | 3 | Yes | Yes | 23.6 | 21.3 | 2.3 | 62375B8D16B24E9D82BA5C0528AFA102 |  | R22 | TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | TXV | 4.167%
Rough & Ready | CA | 95975-9709 |  | 2013-08-26 | 2013-08-26 16:21 | 2013-08-26 16:21 | DAY & NIGHT - 588ANW036100ADAF | 69 | 0 | Yes | Yes | 26.9 | 22.3 | 4.7 | 022715576B304863874CF9E0D6C0183A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6403 |  | 2013-08-12 | 2013-08-12 16:34 | 2013-08-12 17:25 | GOODMAN - CLJ48-1A | 130 | -35.9 | Yes | Yes | 24 | 19.3 | 4.7 | 1A19A87D5FFE49738D910DF5CB824DBC | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -27.62% | 1.2762 | 7.734% |  |  |  |  | TXV |  |  | -27.62%
Stockton | CA | 95207-4723 |  | 2013-08-19 | 2013-08-19 12:17 | 2013-08-19 12:41 | BRYANT - 582ANW030060AAAD | 55 | 4.9 | Yes | Yes | 15 | 15.4 | -0.4 | 1E319DC1A79044BF853EFA3E04FAD29C |  | R22 | Non-TXV |  | 8.909% | 0.91091 | 17.12% | [5 empty] | Non-TXV | 8.909%
Chico | CA | 95973-1222 |  | 2013-08-20 | 2013-08-20 14:21 | 2013-08-20 14:21 | PAYNE - 597BNX030-A | 109 | 0 | Yes | Yes | 25 | 21 | 4 | A50F928BCDDD4A0DBBE96B1CB4C886B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3880 |  | 2013-08-20 | 2013-08-20 14:14 | 2013-08-20 14:15 | LENNOX - UNK | 56 | 7.2 | Yes | Yes | 21.9 | 22.4 | -0.5 | 48DFF194AF39469BA4EAF4EB98CE57F3 |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Chowchilla | CA | 93610-2229 |  | 2013-08-22 | 2013-08-22 18:15 | 2013-08-22 18:56 | AMANA - P6B30C0702E | 37 | 5.8 | Yes | Yes | 17.2 | 19.4 | -2.2 | 259B1450A5FB42D18E682C22BB07A191 |  | R22 | Non-TXV |  | 15.68% | 0.84324 | 30.13% | [5 empty] | Non-TXV | 15.68%
Sonora | CA | 95370-5273 |  | 2013-09-05 | 2013-09-05 10:12 | 2013-09-05 10:47 | CARRIER - 38TH042310 | 76 | 16.7 | Yes | Yes | 20.2 | 21.7 | -1.5 | 70B7A17C2276452EAC8499A8C13F0BE2 |  | R22 | Non-TXV |  | 21.97% | 0.78026 | 42.23% | [5 empty] | Non-TXV | 21.97%
Oakhurst | CA | 93644-8579 |  | 2013-08-14 | 2013-08-14 12:29 | 2013-08-14 13:00 | OTHER - NRGF24DDB04 | 53 | 1.6 | Yes | Yes | 21.2 | 18.8 | 2.5 | 85E454ED8B1045B78C523AA24142438B |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Escalon | CA | 95320-2029 |  | 2013-10-11 | 2013-10-11 12:37 | 2013-10-11 13:09 | RUUD - URMA-A042JK08E | 114 | 10.9 | Yes | Yes | 23.8 | 19.9 | 3.9 | 68323BA5A4834D72B8FCE6F8B7544ABC |  | R22 | Non-TXV |  | 9.561% | 0.90439 | 18.37% | [5 empty] | Non-TXV | 9.561%
Chowchilla | CA | 93610-9533 |  | 2013-08-19 | 2013-08-19 12:11 | 2013-08-19 12:13 | ICP - CA5548VKA1 | 139 | 31.9 | Yes | Yes | 21.5 | 20.6 | 0.9 | 672393A347784777837790E3E2AB8DAD |  | R22 | Non-TXV |  | 22.95% | 0.7705 | 44.1% | [5 empty] | Non-TXV | 22.95%
Cameron Park | CA | 95682-9205 |  | 2013-08-15 | 2013-08-15 18:05 | 2013-08-15 19:07 | PAYNE - 591ANX042000ABAA | 112 | 7.7 | Yes | Yes | 24.5 | 23 | 1.5 | 20FE188F7F3D42F1AB9FC743FBD264B6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Grass Valley | CA | 95945-9681 |  | 2013-08-22 | 2013-08-22 13:13 | 2013-08-22 13:13 | YORK - D4NZ048N09006NX | 68 | 0 | Yes | Yes | 20.1 | 21.3 | -1.2 | D90203954BB74E899999FD50F8CA6ACB |  | R410A | TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-8752 |  | 2013-08-14 | 2013-08-14 09:58 | 2013-08-14 10:26 | BDP - 588ANW036060ADAF | 67 | 4.6 | Yes | Yes | 22.8 | 20.1 | 2.7 | B82626371E5C4B5D957E5754B590339A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.866% | 0.93134 | 13.19% | [5 empty] | Non-TXV | 6.866%
Paso Robles | CA | 93446-4068 |  | 2013-08-07 | 2013-08-07 16:08 | 2013-08-07 16:27 | HEIL - UNK | 59 | -3.5 | Yes | Yes | 17.8 | 16.8 | 1 | 695A518BFD6F461697B670D30D5752C9 |  | R22 | Non-TXV |  | -5.932% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.932%
Merced | CA | 95348-2172 |  | 2013-09-06 | 2013-09-06 13:46 | 2013-09-06 13:51 | BDP - 567GJ018 | 64 | 10.2 | Yes | Yes | 17.5 | 18.1 | -0.6 | CDC953EFC96F4A04986623A73CEE5C65 |  | R22 | Non-TXV |  | 15.94% | 0.84062 | 30.63% | [5 empty] | Non-TXV | 15.94%
Gerber | CA | 96035-2039 |  | 2013-08-19 | 2013-08-19 08:43 | 2013-08-19 10:14 | RUUD - 12AJB36A01 | 85 | 3.2 | Yes | Yes | 21.9 | 19.6 | 2.3 | 40FBAF8E58B549E6A93968CACE5651DB |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Penn Valley | CA | 95946-8602 |  | 2013-09-05 | 2013-09-05 15:09 | 2013-09-05 15:29 | RHEEM - RRMA-A042JK08X | 114 | 7.5 | Yes | Yes | 22 | 21 | 1 | 6762487D690C42A8BFB7CD461149C973 |  | R22 | TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | TXV | 6.579%
Granite Bay | CA | 95746-9492 |  | 2013-09-27 | 2013-09-27 17:38 | 2013-09-27 17:38 | AMERICAN STANDARD - WCC048F100BG | 208 | 0 | Yes | Yes | 26.2 | 20.6 | 5.6 | DFF2F8F7736041648716A8A0CD8CC64B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6124 |  | 2013-08-22 | 2013-08-22 13:30 | 2013-08-22 13:51 | GOODMAN - CKJ30-1A | 90 | 10.1 | Yes | Yes | 18.6 | 16.6 | 2 | 473F30B84D9B40CE8503457FCB0FA28B |  | R22 | Non-TXV |  | 11.22% | 0.88778 | 21.57% | [5 empty] | Non-TXV | 11.22%
Penn Valley | CA | 95946-9418 |  | 2013-08-15 | 2013-08-15 11:33 | 2013-08-15 11:57 | TRANE - TTR036D100AD | 79 | 8.7 | Yes | Yes | 26 | 20.8 | 5.2 | C5AA934A8D86470DA4C2D17D314658CB |  | R22 | TXV |  | 11.01% | 0.88987 | 21.16% | [5 empty] | TXV | 11.01%
Stockton | CA | 95206-6163 |  | 2013-08-12 | 2013-08-12 11:21 | 2013-08-12 11:41 | CARRIER - 38CKC060370 | 131 | 10.7 | Yes | Yes | 22.7 | 18.8 | 3.9 | 4400628BE08D475AB006F4DB40EDA990 |  | R22 | Non-TXV |  | 8.168% | 0.91832 | 15.7% | [5 empty] | Non-TXV | 8.168%
Chico | CA | 95973-8102 |  | 2013-08-07 | 2013-08-07 16:00 | 2013-08-07 16:28 | BDP - 563CN036-A | 122 | 31.2 | Yes | Yes | 19.8 | 22.1 | -2.3 | 407DC9D3E9074BAAA979F5133196F6D1 |  | R22 | Non-TXV |  | 25.57% | 0.74426 | 49.15% | [5 empty] | Non-TXV | 25.57%
Chico | CA | 95928-4180 |  | 2013-08-27 | 2013-08-27 08:40 | 2013-08-27 09:02 | RUUD - UAND-018JAZ | 68 | -4 | Yes | Yes | 21.5 | 19.9 | 1.6 | 0E82B517706946DBA247215D8B990E14 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Tracy | CA | 95376-1879 |  | 2013-08-15 | 2013-08-15 10:15 | 2013-08-15 10:31 | BDP - 565BJ024 | 70 | -6.6 | Yes | Yes | 25.8 | 20.1 | 5.7 | DA1FD531C9B747BB986009C2744D3504 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Merced | CA | 95340-2220 |  | 2013-08-07 | 2013-08-07 09:28 | 2013-08-07 09:51 | GOODMAN - SSX140481BA | 147 | -16.4 | Yes | Yes | 18.4 | 17.7 | 0.7 | 30CBEC9488FB4CF2AC195CFE3D1331F8 |  | R410A | Non-TXV |  | -11.16% | 1.1116 | 3.124% |  |  |  |  | Non-TXV |  |  | -11.16%
Chowchilla | CA | 93610-9562 |  | 2013-08-19 | 2013-08-19 11:22 | 2013-08-19 11:24 | RUUD - UAKA042JAS | 79 | 7.2 | Yes | Yes | 19.5 | 19.7 | -0.2 | 29139C4AC07540829D289040622F7EAC |  | R22 | Non-TXV |  | 9.114% | 0.90886 | 17.51% | [5 empty] | Non-TXV | 9.114%
Los Banos | CA | 93635-5371 |  | 2013-08-13 | 2013-08-13 12:01 | 2013-08-13 12:09 | BRYANT - 561CJ036E | 70 | 5.6 | Yes | Yes | 22.1 | 22 | 0.1 | 16AA1AE8DFC54C0AB43D96F1A904DD02 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Los Banos | CA | 93635-5371 |  | 2013-08-13 | 2013-08-13 12:13 | 2013-08-13 12:16 | BRYANT - 561CJ042B | 86 | 4.5 | Yes | Yes | 19.2 | 22 | -2.8 | 32C1F184C96E4113A9B6957D5FE27CE0 |  | R22 | Non-TXV |  | 5.233% | 0.94767 | 10.06% | [5 empty] | Non-TXV | 5.233%
Chico | CA | 95926-4373 |  | 2013-08-23 | 2013-08-23 11:17 | 2013-08-23 13:31 | PAYNE - 585JW030050ABAF | 58 | 7.1 | Yes | Yes | 16 | 18.9 | -2.8 | 960CFA2C6083432BBE01B9CCC0FFD9E7 |  | R22 | Non-TXV |  | 12.24% | 0.87759 | 23.53% | [5 empty] | Non-TXV | 12.24%
Stockton | CA | 95212-3009 |  | 2013-08-08 | 2013-08-08 16:22 | 2013-08-08 16:43 | GOODMAN - CKJ48-1AB | 118 | 7.8 | Yes | Yes | 26.1 | 20.1 | 6 | DF52EE32D05041B3842CA5E6EE8CCD93 |  | R22 | Non-TXV |  | 6.61% | 0.9339 | 12.7% | [5 empty] | Non-TXV | 6.61%
Chowchilla | CA | 93610-2032 |  | 2013-08-14 | 2013-08-14 09:49 | 2013-08-14 09:50 | AMERICAN STANDARD - TTD748A100AO | 118 | 16.4 | Yes | Yes | 15.9 | 14.4 | 1.5 | DD08F970AE1D49479886609B7F2CAF0B |  | R22 | Non-TXV |  | 13.9% | 0.86102 | 26.71% | [5 empty] | Non-TXV | 13.9%
Merced | CA | 95340-4237 |  | 2013-08-07 | 2013-08-07 13:26 | 2013-08-07 13:52 | PAYNE - PY1PNB036060AAAA | 56 | 2.4 | Yes | Yes | 22.5 | 18.5 | 4 | F03E7431255647E1875F4E079C259A0D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Chowchilla | CA | 93610-2017 |  | 2013-08-27 | 2013-08-27 09:49 | 2013-08-27 09:49 | ICP - PGF324040K01A--0 | 120 | 0 | Yes | Yes | 18.3 | 20.1 | -1.8 | 2500F8E816864740A016A54CE1C04FC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3427 |  | 2013-08-19 | 2013-08-19 14:27 | 2013-08-19 14:27 | COLEMAN - TCJD36S43HA | 73 | 0 | Yes | Yes | 23.3 | 20.1 | 3.2 | A5E1BBFC9F7347859C709A26E36E15C2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2322 |  | 2013-08-12 | 2013-08-12 12:53 | 2013-08-12 13:13 | PAYNE - UNK | 50 | 2 | Yes | Yes | 19.2 | 18.3 | 0.9 | FA744647C14B4FE3BF96118EB88A4AE8 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95210-2275 |  | 2013-08-12 | 2013-08-12 12:17 | 2013-08-12 12:34 | DAY & NIGHT - 585HJ036060 | 102 | -6 | Yes | Yes | 22 | 20.1 | 1.9 | 590FE121AAEB4B1381C6EE9880605746 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Chowchilla | CA | 93610-9464 |  | 2013-08-19 | 2013-08-19 13:04 | 2013-08-19 13:06 | YORK - H1RA048S06G | 117 | 10.6 | Yes | Yes | 19.3 | 18.1 | 1.2 | 5ADC976D134C4FA289AD058DBD98B4BB |  | R22 | Non-TXV |  | 9.06% | 0.9094 | 17.41% | [5 empty] | Non-TXV | 9.06%
Grass Valley | CA | 95945-5058 |  | 2013-08-20 | 2013-08-20 11:43 | 2013-08-20 11:43 | YORK - UNK | 43 | 0 | Yes | Yes | 20.9 | 21.3 | -0.3 | 0FF199D1610043AD9FE1891252F619F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Marysville | CA | 95901-4118 |  | 2013-08-20 | 2013-08-20 10:37 | 2013-08-20 11:08 | TRANE - 2TTB3034A1000AA | 82 | 6.3 | Yes | Yes | 17 | 17.2 | -0.2 | 69C44C995FCC4FE48635F147DFD9B6AC |  | R22 | TXV |  | 7.683% | 0.92317 | 14.76% | [5 empty] | TXV | 7.683%
Winton | CA | 95388-9261 |  | 2013-08-15 | 2013-08-15 14:40 | 2013-08-15 15:00 | GOODMAN - PGB030050-1 | 64 | 2 | Yes | Yes | 22.2 | 19 | 3.2 | 1BD38A92E94849A59F3843AE8512051C |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Tracy | CA | 95377-7053 |  | 2013-09-10 | 2013-09-10 15:36 | 2013-09-10 15:58 | YORK - AC048X1021A | 117 | 7.2 | Yes | Yes | 27.2 | 21.5 | 5.7 | D4ECC6D868264A418F8CC57F7B2A2A4B |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Tracy | CA | 95377-7053 |  | 2013-09-10 | 2013-09-10 16:08 | 2013-09-10 16:30 | YORK - AC036X1021A | 63 | 5.4 | Yes | Yes | 22.1 | 21.8 | 0.4 | 093A5C083C684DF2BE8F8A8D4EDF203C |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Tracy | CA | 95377-8342 |  | 2013-08-12 | 2013-08-12 14:54 | 2013-08-12 15:04 | BRYANT - 561CJ048-G | 100 | 9.9 | Yes | Yes | 20.4 | 19.5 | 0.9 | 5C3174F9D1E24E50B74AFE1BFC98030E |  | R22 | TXV |  | 9.9% | 0.901 | 19.03% | [5 empty] | TXV | 9.9%
Atwater | CA | 95301-4870 |  | 2013-08-13 | 2013-08-13 15:27 | 2013-08-13 16:03 | RUUD - UAFD-030JAS | 69 | 4.6 | Yes | Yes | 27.2 | 21.3 | 5.9 | 044B0AF1D87149F2AB333306BE3E9654 | OK: Verified Refrigerant Charge Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | TXV | 6.667%
Stockton | CA | 95212-3467 |  | 2013-08-08 | 2013-08-08 10:57 | 2013-08-08 11:25 | CARRIER - 38CKC042350 | 93 | 25.1 | Yes | Yes | 9.9 | 19.9 | -10 | C03F571076C4433EA5C9A7DDF4BC5108 | Add refrigerant: 18.8 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 26.99% | 0.73011 | 51.87% | [5 empty] | Non-TXV | 26.99%
Lathrop | CA | 95330-9649 |  | 2013-08-16 | 2013-08-16 10:22 | 2013-08-16 10:57 | GOODMAN - GSX130361DA | 77 | 2.4 | Yes | Yes | 14.8 | 16.9 | -2.1 | 3013324E928441A399A79FE4057A265D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Tracy | CA | 95376-7763 |  | 2013-08-23 | 2013-08-23 11:30 | 2013-08-23 11:53 | CARRIER - 591ANX030000ABAA | 67 | 2.2 | Yes | Yes | 25.5 | 20.8 | 4.7 | F622FE4C2BD342D9AA3BA6DE59207C41 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Atwater | CA | 95301-4534 |  | 2013-08-15 | 2013-08-15 11:14 | 2013-08-15 11:35 | COLEMAN - DRCS0481BB | 129 | 5.6 | Yes | Yes | 22.6 | 19.2 | 3.4 | F3E8B28A2DC5499D938A65238860F194 |  | R22 | TXV |  | 4.341% | 0.95659 | 8.343% | [5 empty] | TXV | 4.341%
Paradise | CA | 95969-3030 |  | 2013-08-08 | 2013-08-08 11:30 | 2013-08-08 12:09 | OTHER - 2APTB-1 | 64 | 10.5 | Yes | Yes | 18.4 | 21.3 | -2.9 | CCC93E2B1AA3461E936BBB32C76E6E8B |  | R22 | Non-TXV |  | 16.41% | 0.83594 | 31.53% | [5 empty] | Non-TXV | 16.41%
Foresthill | CA | 95631-9670 |  | 2013-10-14 | 2013-10-14 17:02 | 2013-10-14 17:02 | BARD - PH36-1 | 69 | 0 | Yes | Yes | 23.4 | 20.9 | 2.5 | 1319F12E0B034B09B90B45D909642E4F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-4302 |  | 2013-08-16 | 2013-08-16 12:58 | 2013-08-16 13:20 | BRYANT - 24ABA336A30010 | 82 | 6.3 | Yes | Yes | 19 | 18.8 | 0.2 | 360F484FD11D4B6C8778E053A9973506 |  | R410A | TXV |  | 7.683% | 0.92317 | 14.76% | [5 empty] | TXV | 7.683%
Atwater | CA | 95301-4869 |  | 2013-08-13 | 2013-08-13 15:42 | 2013-08-13 16:05 | UNITARY PRODUCTS GROUP - GSGD30S21S2A | 55 | 4.9 | Yes | Yes | 17.4 | 18.6 | -1.2 | 2C480D4DB35042C4B7B4EC2538C6C88D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.909% | 0.91091 | 17.12% | [5 empty] | Non-TXV | 8.909%
Nevada City | CA | 95959-9771 |  | 2013-08-27 | 2013-08-27 20:47 | 2013-08-27 20:47 | LENNOX - HS29-048-2P | 91 | 0 | Yes | Yes | 23.6 | 20.5 | 3.1 | 7EF75EBB984942D5A1DB2BF7FBAFEEFB |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-1647 |  | 2013-08-29 | 2013-08-29 13:24 | 2013-08-29 13:26 | CARRIER - 48GP-048090301 | 149 | 4.6 | Yes | Yes | 22.9 | 20.4 | 2.5 | 28042B497FAE473098024AA5B1F41980 |  | R410A | Non-TXV |  | 3.087% | 0.96913 | 5.933% | [5 empty] | Non-TXV | 3.087%
Stockton | CA | 95206-6286 |  | 2013-08-12 | 2013-08-12 10:21 | 2013-08-12 10:42 | GOODMAN - CKJ30-1A | 92 | 13.6 | Yes | Yes | 24.5 | 19.5 | 5 | 8BCD8CF4EEFB40A6A8AF228BA7D78D5F |  | R22 | Non-TXV |  | 14.78% | 0.85217 | 28.41% | [5 empty] | Non-TXV | 14.78%
Merced | CA | 95340-3829 |  | 2013-08-07 | 2013-08-07 11:31 | 2013-08-07 11:52 | ICP - HAC030AKC4 | 73 | 2.4 | Yes | Yes | 19.3 | 18.2 | 1.1 | 6CDE252DB1EC4555B4275DF373BA633E |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Tracy | CA | 95376-0716 |  | 2013-08-15 | 2013-08-15 08:34 | 2013-08-15 08:50 | YORK - UNK | 85 | -24.1 | Yes | Yes | 25 | 19.3 | 5.7 | 66AC8B21C1EE4332AF625C9484C23761 |  | R22 | Non-TXV |  | -28.35% | 1.2835 | 7.94% |  |  |  |  | Non-TXV |  |  | -28.35%
Atwater | CA | 95301-4884 |  | 2013-08-14 | 2013-08-14 13:27 | 2013-08-14 13:44 | CARRIER - 38CE003300 | 71 | 2.2 | Yes | Yes | 18.4 | 19.7 | -1.3 | 1B361C5881504B95950AF95320BE50C1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.099% | 0.96901 | 5.955% | [5 empty] | Non-TXV | 3.099%
Sonora | CA | 95370-6988 |  | 2013-09-06 | 2013-09-06 14:05 | 2013-09-06 14:05 | RUUD - UNK | 85 | 0 | Yes | Yes | 18.8 | 21.5 | -2.7 | 059484AB0D264EA4B6AD54EAA1396B2E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-3255 |  | 2013-09-06 | 2013-09-06 13:57 | 2013-09-06 14:13 | LENNOX - 13ACC-030-230-01 | 97 | 8.6 | Yes | Yes | 26.4 | 21.3 | 5.1 | D67894FABC6F449586CC6DC11132FA66 |  | R22 | Non-TXV |  | 8.866% | 0.91134 | 17.04% | [5 empty] | Non-TXV | 8.866%
Mariposa | CA | 95338-9623 |  | 2013-08-21 | 2013-08-21 13:05 | 2013-08-21 13:06 | HEIL - NRG63300C802 | 47 | 6.2 | Yes | Yes | 27.2 | 23.1 | 4.1 | 5E930B492F6C4F058E96CD73F5CA91C3 |  | R22 | Non-TXV |  | 13.19% | 0.86809 | 25.35% | [5 empty] | Non-TXV | 13.19%
Merced | CA | 95348-3175 |  | 2013-09-03 | 2013-09-03 16:23 | 2013-09-03 16:24 | GE - BGTA830R1E01 | 76 | 8.9 | Yes | Yes | 24.8 | 20.4 | 4.4 | 78058D76F85B4A37B3C3CAA0608F1609 |  | R22 | Non-TXV |  | 11.71% | 0.88289 | 22.51% | [5 empty] | Non-TXV | 11.71%
Wheatland | CA | 95692-9279 |  | 2013-10-25 | 2013-10-25 10:19 | 2013-10-25 10:36 | GOODMAN - UNK | 66 | 2 | Yes | Yes | 19 | 20.7 | -1.7 | 6366CDC3D5714BE0B178D8B813FFC189 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Red Bluff | CA | 96080-3944 |  | 2013-09-25 | 2013-09-25 15:58 | 2013-09-25 16:15 | PAYNE - 567C024RCU | 60 | 3.8 | Yes | Yes | 17.1 | 19 | -1.9 | 326817EF27C1452AAF4F05E381C39873 |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Merced | CA | 95348-1622 |  | 2013-08-14 | 2013-08-14 17:09 | 2013-08-14 17:10 | GOODMAN - GPG1324051BA | 77 | 5.1 | Yes | Yes | 21.1 | 20.1 | 1 | 247EF6619D9C47E1BC7CD6C957FF22C0 |  | R22 | Non-TXV |  | 6.623% | 0.93377 | 12.73% | [5 empty] | Non-TXV | 6.623%
Grass Valley | CA | 95949-9114 |  | 2013-08-07 | 2013-08-07 15:38 | 2013-08-07 15:38 | CARRIER - UNK | 48 | 0 | Yes | Yes | 24.5 | 21 | 3.5 | 1AFD61879E414EEB8B5CFD2B84720F1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Burson | CA | 95225-0000 |  | 2013-09-16 | 2013-09-16 13:35 | 2013-09-17 07:13 | GIBSON - JS3BC048KA | 131 | 4.4 | Yes | Yes | 22 | 18.5 | 3.5 | DAEB1B3F40094F938D24540EB2C54165 |  | R22 | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
Oroville | CA | 95966-5424 |  | 2013-08-17 | 2013-08-17 10:54 | 2013-08-17 12:06 | CARRIER - NA | 74 | 11.6 | Yes | Yes | 16.7 | 18.7 | -2 | D99B9B85F2D54E6C8DA932BC7FEE741F |  | R22 | Non-TXV |  | 15.68% | 0.84324 | 30.13% | [5 empty] | Non-TXV | 15.68%
Paradise | CA | 95969-5613 |  | 2013-09-26 | 2013-09-26 15:24 | 2013-09-26 15:42 | CARRIER - 480L029-BB | 41 | 1.2 | Yes | Yes | 24.5 | 20.2 | 4.4 | D4DA397142484DC79868F055BEAC1F52 |  | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Lincoln | CA | 95648-2933 |  | 2013-08-12 | 2013-08-12 10:35 | 2013-08-12 10:56 | CARRIER - 38CKC036350 | 70 | 2.1 | Yes | Yes | 18 | 19.7 | -1.7 | AD8D7D0819EB4EE0BA03CDC7F7384217 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Marysville | CA | 95901-3839 |  | 2013-08-08 | 2013-08-08 16:59 | 2013-08-08 16:59 | DAY & NIGHT - UNK | 100 | 0 | Yes | Yes | 25 | 21.9 | 3.1 | A9CC1F9D21AE4733ACD777FA1B20EDB4 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-5293 |  | 2013-09-11 | 2013-09-11 15:31 | 2013-09-11 15:31 | DAY & NIGHT - 563CN024-A | 86 | 0 | Yes | Yes | 26.2 | 20.5 | 5.8 | C26160D6C9AF496CB3E5E7C4C20C277F |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-5293 |  | 2013-09-11 | 2013-09-11 15:43 | 2013-09-11 16:32 | RUUD - UAPC-024JAZ | 114 | 6.5 | Yes | Yes | 22.8 | 19 | 3.8 | 7D8103EF76D14A3A89A0F238C9B04DBA |  | R22 | Non-TXV |  | 5.702% | 0.94298 | 10.96% | [5 empty] | Non-TXV | 5.702%
Magalia | CA | 95954-9611 |  | 2013-08-29 | 2013-08-29 16:46 | 2013-08-29 20:02 | PAYNE - PY1PNB036090AAAA | 56 | 4.1 | Yes | Yes | 22.1 | 22 | 0.1 | E52287263158478D915D8402CF165212 |  | R22 | Non-TXV |  | 7.321% | 0.92679 | 14.07% | [5 empty] | Non-TXV | 7.321%
Wallace | CA | 95254-0000 |  | 2013-08-23 | 2013-08-23 14:49 | 2013-08-23 15:08 | PAYNE - UNK | 85 | 18 | Yes | Yes | 17.8 | 20.5 | -2.7 | 68CE539580F04DA3AE8245DFC9A6C264 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.18% | 0.78824 | 40.7% | [5 empty] | Non-TXV | 21.18%
Stockton | CA | 95206-3886 |  | 2013-08-10 | 2013-08-10 10:24 | 2013-08-10 10:42 | GOODMAN - GSX130361BA | 89 | 2.8 | Yes | Yes | 21.7 | 19.3 | 2.4 | C5417851165C4DCB9C7578E2B665040D |  | R410A | Non-TXV |  | 3.146% | 0.96854 | 6.046% | [5 empty] | Non-TXV | 3.146%
Rocklin | CA | 95677-1703 |  | 2013-08-10 | 2013-08-10 10:23 | 2013-08-10 10:47 | RHEEM - HC-100-36-210 | 49 | 2.8 | Yes | Yes | 15.5 | 18.5 | -3 | 92A5C4B67B4340CB9F2792E8CC65C0CD |  | R22 | TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | TXV | 5.714%
Tracy | CA | 95376-1905 |  | 2013-08-15 | 2013-08-15 15:06 | 2013-08-15 15:27 | GE - BTN736A1000A0 | 144 | 23.9 | Yes | Yes | 25.2 | 21 | 4.2 | 5A308B9468CD4FB5B3E3B634A9A4AF6B |  | R22 | Non-TXV |  | 16.6% | 0.83403 | 31.9% | [5 empty] | Non-TXV | 16.6%
Atascadero | CA | 93422-3329 |  | 2013-08-15 | 2013-08-15 15:26 | 2013-08-15 15:53 | DUCANE - AC10B48 | 132 | 5.4 | Yes | Yes | 23.7 | 22.4 | 1.3 | 9DE142B6E04E4E1DA0B867E4E46A2D28 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Jackson | CA | 95642-9454 |  | 2013-08-20 | 2013-08-20 09:04 | 2013-08-20 09:27 | COLEMAN - 2448-901 | 69 | 8.4 | Yes | Yes | 25.8 | 20.6 | 5.2 | 8EDDB7E952C04787AF4BA3EC466A31DF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.17% | 0.87826 | 23.4% | [5 empty] | Non-TXV | 12.17%
Placerville | CA | 95667-4315 |  | 2013-08-16 | 2013-08-16 16:01 | 2013-08-16 16:01 | TRANE - 4YCY4048B1096AA | 128 | 0 | Yes | Yes | 24.2 | 19.7 | 4.5 | 35C650E76A45472CB69B29E708C71B57 |  | R410A | TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-4641 |  | 2013-08-16 | 2013-08-16 11:51 | 2013-08-16 11:51 | YORK - UNK FADED | 68 | 0 | Yes | Yes | 22.7 | 20.4 | 2.3 | DA1F9228EE2F4A8A93619155FBE3ABB5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6649 |  | 2013-08-08 | 2013-08-08 13:25 | 2013-08-08 13:55 | YORK - H2RC036S06G | 83 | 10 | Yes | Yes | 19.3 | 21.5 | -2.2 | 0BFC3EF4EC2042E298C7B88FFCA01E16 |  | R22 | Non-TXV |  | 12.05% | 0.87952 | 23.15% | [5 empty] | Non-TXV | 12.05%
Merced | CA | 95340-2374 |  | 2013-08-19 | 2013-08-19 15:20 | 2013-08-19 15:23 | RUUD - UAKA-024JAZ | 50 | 1.6 | Yes | Yes | 18.1 | 16.6 | 1.5 | 408200B340814B12ACBFC7DDA4C9C5F1 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95205-7876 |  | 2013-08-13 | 2013-08-13 14:57 | 2013-08-13 15:18 | HEIL - UNK | 112 | 14.4 | Yes | Yes | 21.9 | 20.8 | 1.1 | 8A87B213576047AAB1C0F2B05C634A55 |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Penn Valley | CA | 95946-9579 |  | 2013-08-15 | 2013-08-15 15:24 | 2013-08-15 16:00 | OTHER - BRC00361BD | 52 | 2.2 | Yes | Yes | 24 | 21 | 3 | 7A5ED7A92A3A41F6B53B671AA05AB9CA |  | R22 | Non-TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | Non-TXV | 4.231%
Paradise | CA | 95969-7108 |  | 2013-08-08 | 2013-08-08 13:57 | 2013-08-08 14:55 | YORK - H1RA042S06G | 84 | 15.5 | Yes | Yes | 18.4 | 21.3 | -2.9 | 37B55FC933BC44008B22B0F575BE3608 |  | R22 | Non-TXV |  | 18.45% | 0.81548 | 35.46% | [5 empty] | Non-TXV | 18.45%
Tracy | CA | 95376-7041 |  | 2013-08-23 | 2013-08-23 09:58 | 2013-08-23 10:19 | BRYANT - 561CJ060-A | 153 | 4.7 | Yes | Yes | 20.7 | 18.8 | 1.9 | 60427A8917AB4838BE3A3C606F2143FE |  | R22 | Non-TXV |  | 3.072% | 0.96928 | 5.904% | [5 empty] | Non-TXV | 3.072%
Chico | CA | 95973-0249 |  | 2013-09-19 | 2013-09-19 15:23 | 2013-09-19 16:17 | INTERTHERM - CN4813T765P27 | 55 | 13 | Yes | Yes | 17 | 19.9 | -2.9 | B0D18DB009434511B666A5501414CD89 |  | R22 | Non-TXV |  | 23.64% | 0.76364 | 45.42% | [5 empty] | Non-TXV | 23.64%
Penn Valley | CA | 95946-9206 |  | 2013-09-05 | 2013-09-05 12:01 | 2013-09-05 12:01 | CARRIER - 50EZ-A42-30 | 160 | 0 | Yes | Yes | 25 | 21 | 4 | 2F2C933EF34540DF8CF65355F3E50080 |  | R410A | TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2203 |  | 2013-08-21 | 2013-08-21 09:52 | 2013-08-21 10:19 | CARRIER - 48GS-036090301 | 56 | 1.9 | Yes | Yes | 19.8 | 19.7 | 0.2 | 4009EAD56D654BF2BB28ED6BBE19D18A |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Chowchilla | CA | 93610-9461 |  | 2013-09-12 | 2013-09-12 15:41 | 2013-09-12 15:42 | YORK - H2RH036S06G | 63 | 3 | Yes | Yes | 22.5 | 20.9 | 1.6 | E0E05CAA768C423F8250C5BA2F680A61 |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Oroville | CA | 95966-3971 |  | 2013-08-12 | 2013-08-12 15:24 | 2013-08-12 19:49 | CARRIER - 48SS-042100321 | 82 | 4.8 | Yes | Yes | 20 | 18 | 2 | F7150EE4C9C64D93AC22A65EF7DA7779 |  | R22 | Non-TXV |  | 5.854% | 0.94146 | 11.25% | [5 empty] | Non-TXV | 5.854%
Valley Springs | CA | 95252-9394 |  | 2013-09-05 | 2013-09-05 14:47 | 2013-09-05 15:04 | GOODMAN - CKJ36-1D | 90 | 4 | Yes | Yes | 25.1 | 20.4 | 4.7 | F055BF655D5840B6808669414A900D8A |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Penn Valley | CA | 95946-9561 |  | 2013-08-15 | 2013-08-15 14:49 | 2013-08-15 15:14 | BRYANT - 561CJ030-E | 70 | 4 | Yes | Yes | 18 | 18.7 | -0.7 | 6F765803C85D43B19F8FF5AABB9AC07C |  | R22 | TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | TXV | 5.714%
Stockton | CA | 95210-2322 |  | 2013-08-12 | 2013-08-12 13:26 | 2013-08-12 13:47 | RUUD - RRNA-B024JK06X | 70 | 2.4 | Yes | Yes | 18.1 | 17.5 | 0.7 | 2E03CA3B756B471F942067A7C1EA1B08 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Fresno | CA | 93722-6342 |  | 2013-10-26 | 2013-10-26 15:57 | 2013-10-26 16:25 | CARRIER - N/A | 90 | 17.9 | Yes | Yes | 17.4 | 20.4 | -3 | 6D8B1152257540C8995C534F235DA6FF |  | R22 | Non-TXV |  | 19.89% | 0.80111 | 38.22% | [5 empty] | Non-TXV | 19.89%
Stockton | CA | 95210-2322 |  | 2013-08-14 | 2013-08-14 15:41 | 2013-08-14 16:24 | BRYANT - 574DNWA30040NA-- | 98 | 9 | Yes | Yes | 22.5 | 20.8 | 1.7 | 7E95005D1A73483D9EB66A315DBDE648 |  | R410A | TXV |  | 9.184% | 0.90816 | 17.65% | [5 empty] | TXV | 9.184%
Chico | CA | 95926-1656 |  | 2013-08-16 | 2013-08-16 11:25 | 2013-08-16 17:58 | PAYNE - 5858030075YACR | 50 | 3.8 | Yes | Yes | 17.7 | 19.7 | -2 | F4F5655CAD6D48009152D62465452447 |  | R22 | Non-TXV |  | 7.6% | 0.924 | 14.61% | [5 empty] | Non-TXV | 7.6%
Manteca | CA | 95336-3819 |  | 2013-08-12 | 2013-08-12 10:54 | 2013-08-12 11:18 | ICP - HA5036AKC4 | 96 | 9.3 | Yes | Yes | 25.9 | 20.4 | 5.5 | 74483DF488AC418E93A5739E6C4B125F |  | R22 | Non-TXV |  | 9.688% | 0.90312 | 18.62% | [5 empty] | Non-TXV | 9.688%
Stockton | CA | 95219-7269 |  | 2013-08-27 | 2013-08-27 12:57 | 2013-08-27 13:17 | BRYANT - 113ANA048-B | 127 | 12.8 | Yes | Yes | 15.3 | 18.2 | -2.9 | 51856ED843F94C80B2AC80D84FC5AA50 |  | R410A | TXV |  | 10.08% | 0.89921 | 19.37% | [5 empty] | TXV | 10.08%
Tracy | CA | 95376-4302 |  | 2013-09-10 | 2013-09-10 13:08 | 2013-09-10 13:08 | CARRIER - 38ETG036300 | 133 | 0 | Yes | Yes | 19.9 | 20.1 | -0.2 | 9129C6B5FE12497498C5AE3DD0584B61 |  | R410A | TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3044 |  | 2013-08-19 | 2013-08-19 09:21 | 2013-08-19 09:48 | ICP - PGAA30C1K6 | 79 | 2.5 | Yes | Yes | 17.9 | 18.2 | -0.3 | 4C915502A8BF46D293B43A1EE6A9CB49 |  | R22 | Non-TXV |  | 3.165% | 0.96835 | 6.082% | [5 empty] | Non-TXV | 3.165%
Oakdale | CA | 95361-3044 |  | 2013-09-11 | 2013-09-11 16:13 | 2013-09-11 16:32 | RUUD - URGG-05E25JKR | 39 | 2.7 | Yes | Yes | 20.7 | 19.1 | 1.7 | 3BCB4F0E759C40E2B1297E6DF9F81417 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.923% | 0.93077 | 13.3% | [5 empty] | Non-TXV | 6.923%
Stockton | CA | 95210-1710 |  | 2013-08-14 | 2013-08-14 13:40 | 2013-08-14 13:58 | HEIL - PGC036K060B | 71 | 5.7 | Yes | Yes | 24.3 | 20.7 | 3.6 | B1F2AB1757FD4DFAAF5E2766725714D4 |  | R22 | Non-TXV |  | 8.028% | 0.91972 | 15.43% | [5 empty] | Non-TXV | 8.028%
Madera | CA | 93638-2836 |  | 2013-08-25 | 2013-08-25 15:36 | 2013-08-26 00:20 | CARRIER - UNK | 74 | -6.1 | Yes | Yes | 17.6 | 18 | -0.4 | A916008DC02845EF93DF54CDF16B09EE |  | R22 | Non-TXV |  | -8.243% | 1.0824 | 2.308% |  |  |  |  | Non-TXV |  |  | -8.243%
Los Banos | CA | 93635-9227 |  | 2013-09-10 | 2013-09-10 10:42 | 2013-09-10 10:44 | GIBSON - JS5BD-030KA | 99 | 3.7 | Yes | Yes | 24.9 | 20.4 | 4.5 | 7C4DB154A947471F924E4EB42508F2C2 |  | R22 | Non-TXV |  | 3.737% | 0.96263 | 7.182% | [5 empty] | Non-TXV | 3.737%
Los Banos | CA | 93635-9227 |  | 2013-09-10 | 2013-09-10 10:45 | 2013-09-10 10:47 | GIBSON - JS5BD-030KA | 99 | 5 | Yes | Yes | 22.6 | 20.6 | 2.1 | D277C2F8077348CFBC6423D9C6F8565E |  | R22 | Non-TXV |  | 5.051% | 0.94949 | 9.706% | [5 empty] | Non-TXV | 5.051%
Oakdale | CA | 95361-9701 |  | 2013-10-18 | 2013-10-18 11:53 | 2013-10-18 12:09 | COLEMAN - BRCQ0361BDG | 53 | 4.1 | Yes | Yes | 21.1 | 19.3 | 1.8 | F729485A67CD497C9FEB0945753E11D4 |  | R22 | Non-TXV |  | 7.736% | 0.92264 | 14.87% | [5 empty] | Non-TXV | 7.736%
Clovis | CA | 93611-3052 |  | 2013-08-16 | 2013-08-16 10:38 | 2013-08-16 11:51 | RHEEM - N/A | 120 | 5.2 | Yes | Yes | 18.5 | 20.4 | -1.9 | 216D7A0077544533B015F091AE4B5DB3 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Red Bluff | CA | 96080-4226 |  | 2013-09-03 | 2013-09-03 15:22 | 2013-09-03 14:39 | ALLEGIANCE - 2A7A3030A1000AA | 88 | 3.1 | Yes | Yes | 18.8 | 17.5 | 1.3 | 072D3041907947F4B2ADD06BE5703F36 |  | R22 | Non-TXV |  | 3.523% | 0.96477 | 6.77% | [5 empty] | Non-TXV | 3.523%
Merced | CA | 95340-2376 |  | 2013-08-15 | 2013-08-15 13:54 | 2013-08-15 14:17 | OTHER - GCGD30S21S2A | 55 | 14.2 | Yes | Yes | 20.2 | 19.3 | 0.9 | 0C117A6BD0F94DF4B5E925D9E33FED3D |  | R22 | Non-TXV |  | 25.82% | 0.74182 | 49.62% | [5 empty] | Non-TXV | 25.82%
Sutter Creek | CA | 95685-4319 |  | 2013-09-06 | 2013-09-06 13:37 | 2013-09-06 14:09 | GIBSON - GS3BA036 | 80 | 3.8 | Yes | Yes | 19.5 | 18 | 1.6 | 2DDA69A1E7294F0FA25305DE1BEF030F |  | R22 | Non-TXV |  | 4.75% | 0.9525 | 9.128% | [5 empty] | Non-TXV | 4.75%
Nevada City | CA | 95959-9235 |  | 2013-09-10 | 2013-09-10 10:41 | 2013-09-10 10:41 | CARRIER - 48SS-030060321-- | 56 | 0 | Yes | Yes | 24.3 | 20.6 | 3.7 | AC6EFE5C268141EE9BC94AAED9200F98 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-9235 |  | 2013-09-10 | 2013-09-10 11:06 | 2013-09-10 11:06 | CARRIER - 38CKB024310 | 61 | 0 | Yes | Yes | 21.8 | 21.7 | 0.1 | 447A2278E1124CA09BC5183FCEB99BCD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newcastle | CA | 95658-9209 |  | 2013-09-03 | 2013-09-03 14:39 | 2013-09-03 15:00 | PAYNE - 588ANW060100AEAG | 112 | 6.7 | Yes | Yes | 22 | 20.1 | 1.9 | 9BEDB78E4A9F461A8E353038AFA6AD9E |  | R22 | Non-TXV |  | 5.982% | 0.94018 | 11.5% | [5 empty] | Non-TXV | 5.982%
Oroville | CA | 95966-3670 |  | 2013-08-12 | 2013-08-12 08:56 | 2013-08-12 19:22 | CARRIER - 428GS-030060301 | 55 | 1.7 | Yes | Yes | 24 | 22.1 | 1.9 | 1CD87FF62ED04E41B22AB5EC424F8266 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Red Bluff | CA | 96080-2538 |  | 2013-08-09 | 2013-08-09 12:59 | 2013-08-09 13:46 | HEIL - PGD342060K001C1 | 106 | 6.1 | Yes | Yes | 21.4 | 21.3 | 0.1 | 231312309C1444E6A34C2965A51E3629 |  | R410A | Non-TXV |  | 5.755% | 0.94245 | 11.06% | [5 empty] | Non-TXV | 5.755%
Stockton | CA | 95219-3110 |  | 2013-08-27 | 2013-08-27 16:23 | 2013-08-27 17:31 | PAYNE - PA12NA036-A | 100 | 5.7 | Yes | Yes | 26 | 21.2 | 4.8 | A9CCEF3360D94909A32AAB579078BBC9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.7% | 0.943 | 10.95% | [5 empty] | Non-TXV | 5.7%
Winton | CA | 95388-9262 |  | 2013-08-15 | 2013-08-15 14:05 | 2013-08-15 14:22 | GOODMAN - PGB036075-1A | 60 | 2.2 | Yes | Yes | 20.9 | 17.1 | 3.8 | B22A03FC973D4540A693AB179165A28E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Paradise | CA | 95969-5109 |  | 2013-09-04 | 2013-09-04 10:34 | 2013-09-04 15:42 | YORK - H2DB036506A | 73 | 3.3 | Yes | Yes | 15.3 | 18.3 | -3 | 8C43013337F24837B0E2E8A91D9BF97E |  | R22 | Non-TXV |  | 4.521% | 0.95479 | 8.687% | [5 empty] | Non-TXV | 4.521%
Tracy | CA | 95377-8276 |  | 2013-08-12 | 2013-08-12 14:24 | 2013-08-12 14:24 | YORK - HRA048S06D | 117 | 0 | Yes | Yes | 19.3 | 20.3 | -1 | 1584D0DE8BE048F3BF1920B00CE078E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2823 |  | 2013-09-16 | 2013-09-16 11:42 | 2013-09-16 11:44 | AMERICAN STANDARD - YCY030G1LOAC | 120 | 12.9 | Yes | Yes | 24.6 | 21.5 | 3.1 | 526DF7B689754E73A530E4796D0298DD |  | R22 | Non-TXV |  | 10.75% | 0.8925 | 20.66% | [5 empty] | Non-TXV | 10.75%
Pilot Hill | CA | 95664-9698 |  | 2013-09-20 | 2013-09-20 09:40 | 2013-09-20 09:40 | UNITARY PRODUCTS GROUP - AC030M1021A | 57 | 0 | Yes | Yes | 18.4 | 19.9 | -1.5 | 05B730FDD5E541039FDD2B668339C0B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-9326 |  | 2013-08-09 | 2013-08-09 11:17 | 2013-08-09 11:53 | AMANA - PGB36C0702E | 64 | 4.1 | Yes | Yes | 26.2 | 20.7 | 5.6 | 705E7CDEAAAF4AE5B906E77E5A0068C9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.406% | 0.93594 | 12.31% | [5 empty] | Non-TXV | 6.406%
Stockton | CA | 95215-5903 |  | 2013-08-13 | 2013-08-13 17:37 | 2013-08-13 17:37 | COLEMAN - UNK | 85 | 0 | Yes | Yes | 15.3 | 17.7 | -2.4 | E077C1EEBDDE43F69B395795BCDD65E0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-3103 |  | 2013-08-22 | 2013-08-22 11:10 | 2013-08-22 11:29 | - BRCF36U0IA | 118 | 9.2 | Yes | Yes | 23.6 | 19.7 | 3.9 | 9A15656D211D4ACA9E2F2D38101B67A0 |  | R22 | TXV |  | 7.797% | 0.92203 | 14.98% | [5 empty] | TXV | 7.797%
Oroville | CA | 95966-3716 |  | 2013-08-12 | 2013-08-12 14:43 | 2013-08-12 18:56 | LENNOX - HS26-030-3P | 78 | 18.8 | Yes | Yes | 17.8 | 20.4 | -2.6 | C38BAF528CBA45C0A2861ECBE96937BD |  | R22 | Non-TXV |  | 24.1% | 0.75897 | 46.32% | [5 empty] | Non-TXV | 24.1%
Madera | CA | 93638-0369 |  | 2013-08-26 | 2013-08-26 00:52 | 2013-08-26 01:25 | YORK - D1NAP0360906A | 80 | 3.5 | Yes | Yes | 20 | 20.7 | -0.7 | 3600DC22BE0D4BE485FADA066AF0CBD7 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Madera | CA | 93636-8510 |  | 2013-09-03 | 2013-09-03 13:56 | 2013-09-03 13:59 | CARRIER - 38CK048330 | 112 | 17 | Yes | Yes | 20.1 | 20.9 | -0.8 | F52A8BC9D18247C4A227924263ADB2F7 |  | R22 | TXV |  | 15.18% | 0.84821 | 29.17% | [5 empty] | TXV | 15.18%
Stockton | CA | 95212-3113 |  | 2013-08-08 | 2013-08-08 15:34 | 2013-08-08 16:01 | YORK - H2RC048S06G | 119 | 16.2 | Yes | Yes | 20.6 | 20.1 | 0.5 | 17FCD4F04FB8487FA19E78ED8C98DBDF |  | R22 | Non-TXV |  | 13.61% | 0.86387 | 26.16% | [5 empty] | Non-TXV | 13.61%
Stockton | CA | 95205-2591 |  | 2013-08-15 | 2013-08-15 13:50 | 2013-08-15 14:14 | GOODMAN - GSC130601BA | 178 | 9.6 | Yes | Yes | 20.2 | 19.8 | 0.4 | F8E71F7683A944F59694F49A21C92639 |  | R22 | Non-TXV |  | 5.393% | 0.94607 | 10.36% | [5 empty] | Non-TXV | 5.393%
Merced | CA | 95340-2380 |  | 2013-08-15 | 2013-08-15 12:43 | 2013-08-15 12:44 | WEATHER KING - 10AJA3601 | 80 | 7.3 | Yes | Yes | 22 | 20.1 | 1.9 | 000860A01D64489DA51FB96C4A0687B5 |  | R22 | Non-TXV |  | 9.125% | 0.90875 | 17.54% | [5 empty] | Non-TXV | 9.125%
Stockton | CA | 95206-5134 |  | 2013-08-12 | 2013-08-12 08:42 | 2013-08-12 09:00 | CARRIER - 38CKC042350 | 81 | 5.1 | Yes | Yes | 16.8 | 19.3 | -2.5 | 62D9CB1876734688AAAB346A2B781D1B |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Rocklin | CA | 95765-5178 |  | 2013-08-12 | 2013-08-12 09:22 | 2013-08-12 09:40 | YORK - H2RA036S06D | 63 | 6.4 | Yes | Yes | 19 | 20.4 | -1.4 | 4EAC39959B7C49D2B376C03B7CD66240 |  | R22 | Non-TXV |  | 10.16% | 0.89841 | 19.52% | [5 empty] | Non-TXV | 10.16%
Stockton | CA | 95210-2119 |  | 2013-08-12 | 2013-08-12 10:34 | 2013-08-12 10:51 | GOODMAN - GSC130301AE | 117 | -6.9 | Yes | Yes | 23.1 | 18.7 | 4.4 | 6559D6716BD149C8B8595E8DFF6ABDBC |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Madera | CA | 93637-6210 |  | 2013-09-01 | 2013-09-01 00:33 | 2013-09-01 00:56 | CARRIER - 48GS-030040301-- | 57 | 3.5 | Yes | Yes | 16.4 | 19 | -2.6 | 83113781C9734807A07073AE3E502871 |  | R22 | Non-TXV |  | 6.14% | 0.9386 | 11.8% | [5 empty] | Non-TXV | 6.14%
Chico | CA | 95926-2820 |  | 2013-08-22 | 2013-08-22 13:29 | 2013-08-22 13:47 | LENNOX - HS18-411-5P | 82 | 5.3 | Yes | Yes | 21.2 | 20.7 | 0.5 | 0B6F11DD9EB14378AB315452EAE99E5B |  | R22 | Non-TXV |  | 6.463% | 0.93537 | 12.42% | [5 empty] | Non-TXV | 6.463%
Merced | CA | 95340-0659 |  | 2013-08-13 | 2013-08-13 15:23 | 2013-08-13 15:34 | OTHER - 7777UNK | 96 | 2.9 | Yes | Yes | 16.2 | 18.6 | -2.4 | E06EF1FD58C844798FAD8A0177E09236 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Stockton | CA | 95203-2516 |  | 2013-08-15 | 2013-08-15 08:38 | 2013-08-15 09:10 | DAY & NIGHT - 565BJ048 | 125 | 5.4 | Yes | Yes | 18.7 | 18.2 | 0.5 | 86300868A6E94604ACAC9D07689E315C |  | R22 | Non-TXV |  | 4.32% | 0.9568 | 8.302% | [5 empty] | Non-TXV | 4.32%
Stockton | CA | 95206-5707 |  | 2013-08-12 | 2013-08-12 12:56 | 2013-08-12 13:16 | BDP - AA1CJ036-C | 71 | 14.5 | Yes | Yes | 21.7 | 20.2 | 1.5 | 8F748503F0594C8AA92066F2E16E5F79 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.42% | 0.79577 | 39.25% | [5 empty] | Non-TXV | 20.42%
Chico | CA | 95973-9299 |  | 2013-08-08 | 2013-08-08 13:35 | 2013-08-08 13:54 | LENNOX - 13ACD-042-230-02 | 111 | 5.3 | Yes | Yes | 22.5 | 19.5 | 3 | 5B5BB7AAB7D0429383D4D982811205D4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.775% | 0.95225 | 9.176% | [5 empty] | Non-TXV | 4.775%
Stockton | CA | 95207-4429 |  | 2013-09-04 | 2013-09-04 09:45 | 2013-09-04 09:45 | RHEEM - HC-100-36-21C | 49 | 0 | Yes | Yes | 21.9 | 18 | 3.9 | B06B4C7BBCCB4826B8CE673B07F4A118 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-2308 |  | 2013-08-21 | 2013-08-21 08:29 | 2013-08-21 08:29 | RHEEM - UNK | 67 | 0 | Yes | Yes | 17 | 18.6 | -1.6 | AC0E8AE98579413BB087AD47BF5C9FFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1611 |  | 2013-09-05 | 2013-09-05 09:56 | 2013-09-05 10:24 | BDP - 588ANW03006ADAD | 53 | 7 | Yes | Yes | 20.6 | 19.9 | 0.7 | 2C651311E0A34BCE98B51E312D94B1F6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.21% | 0.86792 | 25.38% | [5 empty] | Non-TXV | 13.21%
Nevada City | CA | 95959-9293 |  | 2013-09-04 | 2013-09-04 09:21 | 2013-09-04 09:52 | CARRIER - 38TXA060350 | 180 | 6.6 | Yes | Yes | 17 | 19.5 | -2.5 | E370CBCAC0A6475794E2AB7C9EEDB939 |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Placerville | CA | 95667-3471 |  | 2013-08-16 | 2013-08-16 10:53 | 2013-08-16 10:53 | CARRIER - 38CK036300 | 80 | 0 | Yes | Yes | 22.7 | 22.4 | 0.3 | B2369DF8F1494CF0AE22401007C0E5A5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-8219 |  | 2013-08-12 | 2013-08-12 16:29 | 2013-08-12 16:48 | BRYANT - 561C036-E | 85 | 3.5 | Yes | Yes | 19.2 | 20.9 | -1.7 | 2EAFD6031CEA43D9AD709D6DCC322E23 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Merced | CA | 95340-2220 |  | 2013-08-15 | 2013-08-15 13:14 | 2013-08-15 13:16 | YORK - DAYPF030N070A | 73 | 7.3 | Yes | Yes | 23.3 | 22.6 | 0.7 | 24BEC57F96FF4DFAB2284AA86999B052 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Newman | CA | 95360-1496 |  | 2013-08-22 | 2013-08-22 12:07 | 2013-08-22 12:36 | DAY & NIGHT - 591AN0360000AAAA | 84 | 6.4 | Yes | Yes | 20 | 19.3 | 0.7 | A99687FDB8DF46E7A36184B6D137AD37 |  | R22 | Non-TXV |  | 7.619% | 0.92381 | 14.64% | [5 empty] | Non-TXV | 7.619%
Stockton | CA | 95209-1322 |  | 2013-08-21 | 2013-08-21 09:10 | 2013-08-21 09:10 | PAYNE - PY3PNA030060NB | 96 | 0 | Yes | Yes | 21.8 | 18.2 | 3.6 | 8357C521BA7C499DB9F5668181F68414 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Escalon | CA | 95320-1750 |  | 2013-08-29 | 2013-08-29 09:52 | 2013-08-29 10:11 | RUUD - UAPB-24JAZ | 114 | 3.5 | Yes | Yes | 21.4 | 20.4 | 1 | 24B1638BA5E64385A35BF35D7BF72B9F |  | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
Manteca | CA | 95336-6939 |  | 2013-08-30 | 2013-08-30 16:16 | 2013-08-30 17:02 | YORK - D1NH036N05606C | 108 | 5.3 | Yes | Yes | 12.3 | 14.4 | -2.1 | DEE35713E57C4BC5B1EAEB54EEA74CD5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.907% | 0.95093 | 9.431% | [5 empty] | Non-TXV | 4.907%
Stockton | CA | 95207-1113 |  | 2013-08-20 | 2013-08-20 10:00 | 2013-08-20 10:21 | CARRIER - 48KLA124--321BE | 68 | -6.4 | Yes | Yes | 16.8 | 17.9 | -1.1 | 7FC33BBB40DF43E99A38F25DB9CB4E6F |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Placerville | CA | 95667-4211 |  | 2013-08-29 | 2013-08-29 15:00 | 2013-08-29 15:00 | GOODMAN - SSZ140421AD | 213 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | 18646D9041DE4C37BD6008B5073DCF55 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4836 |  | 2013-09-04 | 2013-09-04 08:47 | 2013-09-04 09:06 | DAY & NIGHT - 565BJ036-A | 80 | 12.8 | Yes | Yes | 15.9 | 16.2 | -0.3 | 72C7E07B128A493B9D3D1378608348FC |  | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Stockton | CA | 95207-4836 |  | 2013-09-04 | 2013-09-04 09:16 | 2013-09-04 09:30 | DAY & NIGHT - UNK | 96 | 10 | Yes | Yes | 20.2 | 17.3 | 2.9 | 6D6BF36421774FF1A6684F6D99F9B848 |  | R22 | Non-TXV |  | 10.42% | 0.89583 | 20.02% | [5 empty] | Non-TXV | 10.42%
Los Banos | CA | 93635-2640 |  | 2013-08-16 | 2013-08-16 13:12 | 2013-08-16 13:15 | GOODMAN - CK30-1A | 76 | 2.6 | Yes | Yes | 24.1 | 19.6 | 4.5 | 735BE06D350B4428B334857409AF2320 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Oroville | CA | 95965-4021 |  | 2013-08-12 | 2013-08-12 11:03 | 2013-08-12 11:51 | COLEMAN - TC07JD48S41S3HA | 85 | 4 | Yes | Yes | 22.5 | 22.3 | 0.2 | 90E4E8A7FE584659B47AB789E376A3C2 |  | R410A | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fresno | CA | 93727-3656 |  | 2013-08-27 | 2013-08-27 13:06 | 2013-08-27 13:07 | LENNOX - 10GCS036X-75-1PA | 58 | 4.6 | Yes | Yes | 26 | 21.2 | 4.8 | 113B70DFB3E3455E994EF90A238DC66B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.931% | 0.92069 | 15.24% | [5 empty] | Non-TXV | 7.931%
Stockton | CA | 95209-1561 |  | 2013-08-21 | 2013-08-21 13:58 | 2013-08-21 14:16 | GOODMAN - GSC130481AG | 147 | 7.4 | Yes | Yes | 22.2 | 18.8 | 3.5 | 822BFCD92C1548D9A06E9EC64D97952A |  | R22 | Non-TXV |  | 5.034% | 0.94966 | 9.674% | [5 empty] | Non-TXV | 5.034%
Tracy | CA | 95376-2653 |  | 2013-08-22 | 2013-08-22 08:50 | 2013-08-22 09:10 | GOODMAN - CKL24-1F | 72 | 11.6 | Yes | Yes | 16.4 | 18.6 | -2.2 | 0C157D6B68E74171BB1EF14636DE36F1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Stockton | CA | 95207-2904 |  | 2013-08-09 | 2013-08-09 09:57 | 2013-08-09 10:23 | AMANA - PGD36C0902E | 110 | 7.2 | Yes | Yes | 23.6 | 17.7 | 5.9 | F0CDE21587CB431B88C63620B9B79CDD |  | R22 | Non-TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | Non-TXV | 6.545%
Stockton | CA | 95206-5825 |  | 2013-08-28 | 2013-08-28 10:14 | 2013-08-28 10:38 | RHEEM - RAFD-031JAS | 64 | 4.6 | Yes | Yes | 19.7 | 18.2 | 1.5 | 31ED451ADAC8459F9A64266421A75F4F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Stockton | CA | 95207-3340 |  | 2013-08-19 | 2013-08-19 09:28 | 2013-08-19 09:46 | YORK - D1NP030N05606A | 73 | 3.5 | Yes | Yes | 17 | 17.2 | -0.2 | 3E80A139E4DB43E4AD1407C67B023FD1 |  | R22 | Non-TXV |  | 4.795% | 0.95205 | 9.214% | [5 empty] | Non-TXV | 4.795%
Winton | CA | 95388-9358 |  | 2013-09-03 | 2013-09-03 12:00 | 2013-09-03 12:29 | DAY & NIGHT - CBD | 64 | 7.3 | Yes | Yes | 19.6 | 18.3 | 1.3 | EDBF6B00ECE74E579E4736837E44FA34 |  | R22 | Non-TXV |  | 11.41% | 0.88594 | 21.92% | [5 empty] | Non-TXV | 11.41%
Fresno | CA | 93727-3207 |  | 2013-08-27 | 2013-08-27 09:32 | 2013-08-27 09:32 | OTHER - N/A | 90 | 0 | Yes | Yes | 23.5 | 20.4 | 3.1 | 832BBB5088F74D0AA25ED5863E376205 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-2264 |  | 2013-09-03 | 2013-09-03 11:58 | 2013-09-03 13:19 | RUUD - UAFO-025JAS | 51 | 2.5 | Yes | Yes | 16.7 | 19.5 | -2.8 | 1E6D52CE504B468D9F2B0E82EDD86106 |  | R22 | Non-TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | Non-TXV | 4.902%
Riverbank | CA | 95367-2722 |  | 2013-08-20 | 2013-08-20 09:45 | 2013-08-20 10:08 | YORK - D1NH030N05606C | 73 | 2.1 | Yes | Yes | 22.7 | 19.3 | 3.4 | 6359EAA5B03A448B9D8CAF99157724AB |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Stockton | CA | 95210-1449 |  | 2013-08-12 | 2013-08-12 14:21 | 2013-08-12 14:42 | AMANA - PGD36C0902E | 110 | -6.5 | Yes | Yes | 18.3 | 19.7 | -1.4 | 30405E28924A4D34BD4F3179BE482E4E |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Red Bluff | CA | 96080-3131 |  | 2013-09-03 | 2013-09-03 15:41 | 2013-09-03 16:05 | PAYNE - 585A0306100YAC | 81 | 2.5 | Yes | Yes | 22.8 | 20.6 | 2.3 | 844D6A887A104310B05C71C45A644DAF |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Chowchilla | CA | 93610-2359 |  | 2013-08-14 | 2013-08-14 11:18 | 2013-08-14 11:20 | RHEEM - 13AJM36A01 | 96 | 5.6 | Yes | Yes | 25.7 | 20.4 | 5.3 | 61222928A7E4449D86C354000AFBFB12 |  | R410A | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Stockton | CA | 95209-1322 |  | 2013-08-23 | 2013-08-23 13:52 | 2013-08-23 14:10 | BDP - 585A024055YAC | 51 | 3 | Yes | Yes | 20 | 18.5 | 1.5 | 47AA0E5DCF5C4C469A7940FAB505BE77 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Stockton | CA | 95203-2718 |  | 2013-08-15 | 2013-08-15 09:37 | 2013-08-15 09:56 | LENNOX - HS29411-P | 74 | 11.3 | Yes | Yes | 17.2 | 16.6 | 0.6 | A09E8778C129408B94F012C9BF436541 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.27% | 0.8473 | 29.35% | [5 empty] | Non-TXV | 15.27%
Stockton | CA | 95204-2016 |  | 2013-08-22 | 2013-08-22 08:21 | 2013-08-22 08:47 | ICP - PGF336060K01 | 65 | -5.4 | Yes | Yes | 22.3 | 19.7 | 2.6 | 031F2BBF94154132B373AF71FD6CEAB4 |  | R22 | Non-TXV |  | -8.308% | 1.0831 | 2.327% |  |  |  |  | Non-TXV |  |  | -8.308%
Stockton | CA | 95203-2718 |  | 2013-08-15 | 2013-08-15 10:26 | 2013-08-15 10:45 | AMANA - APG133007OM41AD | 80 | 4.1 | Yes | Yes | 16.2 | 18.4 | -2.2 | D47B9665C4EF4BC4B7451E49A056CC80 |  | R410A | Non-TXV |  | 5.125% | 0.94875 | 9.849% | [5 empty] | Non-TXV | 5.125%
Los Banos | CA | 93635-3558 |  | 2013-08-13 | 2013-08-13 13:35 | 2013-08-13 13:37 | BRYANT - 661CJ048-A | 148 | 6.6 | Yes | Yes | 16.9 | 19.9 | -3 | 5E0ABDF77E604197AE3C4F932311E494 |  | R22 | Non-TXV |  | 4.459% | 0.95541 | 8.57% | [5 empty] | Non-TXV | 4.459%
Merced | CA | 95348-3792 |  | 2013-08-09 | 2013-08-09 16:51 | 2013-08-09 17:10 | CARRIER - 591ANX036000AAAA | 84 | 2.9 | Yes | Yes | 21.7 | 21 | 0.7 | 9AB544A1F9684A3FADC461A234FBB638 |  | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Willows | CA | 95988-0000 |  | 2013-09-12 | 2013-09-12 11:02 | 2013-09-12 11:31 | GMC - CK36-1A | 73 | 7.2 | Yes | Yes | 15.9 | 16.2 | -0.3 | 4D2604DE24954CF5B53C892718576FB4 |  | R22 | Non-TXV |  | 9.863% | 0.90137 | 18.95% | [5 empty] | Non-TXV | 9.863%
Yuba City | CA | 95993-5907 |  | 2013-09-06 | 2013-09-06 08:48 | 2013-09-06 09:14 | BRYANT - 563CN048-H | 133 | 4.1 | Yes | Yes | 21 | 20.3 | 0.7 | 06789CB81C2E452391D2415179234181 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.924% | [5 empty] | Non-TXV | 3.083%
Fresno | CA | 93728-1742 |  | 2013-08-16 | 2013-08-16 13:03 | 2013-08-16 13:08 | NORDYNE - JS5BD030KA | 99 | 18.3 | Yes | Yes | 26.2 | 21.2 | 5 | E131688279D34BCCACEFE2133FFE46F8 |  | R22 | Non-TXV |  | 18.48% | 0.81515 | 35.52% | [5 empty] | Non-TXV | 18.48%
Stockton | CA | 95203-2109 |  | 2013-08-28 | 2013-08-28 12:23 | 2013-08-28 12:42 | TRANE - TTP036D100A0 | 133 | 8.4 | Yes | Yes | 21.1 | 18.5 | 2.6 | 8AEDFE3E462A4057A559FE2A03891642 |  | R22 | Non-TXV |  | 6.316% | 0.93684 | 12.14% | [5 empty] | Non-TXV | 6.316%
Paradise | CA | 95969-3124 |  | 2013-08-26 | 2013-08-26 09:05 | 2013-08-26 09:05 | PAYNE - 591ANX042000ABAA | 112 | 0 | Yes | Yes | 24.7 | 18.8 | 5.9 | 8918451C84F0428BA4C10F6443D6A97F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1109 |  | 2013-08-19 | 2013-08-19 08:11 | 2013-08-19 08:28 | RHEEM - RRGG-05E24JKR | 42 | 7.8 | Yes | Yes | 18.8 | 20.4 | -1.6 | 9E0F005592B440A9A875706C36F6EEE3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Paradise | CA | 95969-3453 |  | 2013-09-04 | 2013-09-04 09:19 | 2013-09-04 10:24 | OTHER - NA | 72 | 8.8 | Yes | Yes | 23.7 | 19.1 | 4.7 | 846516AC61E6480C92A815F6E6FD989F |  | R22 | Non-TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | Non-TXV | 12.22%
Chico | CA | 95926-4213 |  | 2013-08-16 | 2013-08-16 15:01 | 2013-08-16 15:19 | PAYNE - PH10JA030-C | 86 | 7.8 | Yes | Yes | 22.6 | 17.9 | 4.7 | D1AFE1968F094D4FAA0294B9A5668122 |  | R22 | Non-TXV |  | 9.07% | 0.9093 | 17.43% | [5 empty] | Non-TXV | 9.07%
Gerber | CA | 96035-9505 |  | 2013-09-13 | 2013-09-13 11:37 | 2013-09-13 11:58 | GOODMAN - CLJ60-1 | 141 | 6.7 | Yes | Yes | 19.2 | 19.9 | -0.7 | 28A194072BD0442298FC46A29D3D6976 |  | R22 | Non-TXV |  | 4.752% | 0.95248 | 9.132% | [5 empty] | Non-TXV | 4.752%
Stockton | CA | 95207-1109 |  | 2013-08-15 | 2013-08-15 15:18 | 2013-08-15 15:30 | PAYNE - PY3PNA024040NB | 89 | 7.8 | Yes | Yes | 18.4 | 19.2 | -0.8 | C9776910D18649AAA42D472F526C197E |  | R22 | Non-TXV |  | 8.764% | 0.91236 | 16.84% | [5 empty] | Non-TXV | 8.764%
Paradise | CA | 95969-6364 |  | 2013-09-04 | 2013-09-04 10:25 | 2013-09-04 15:43 | CARRIER - 48SD-048090301 | 193 | 5.9 | Yes | Yes | 19.5 | 19.4 | 0.1 | F531EDA00D5B4B8CB1B0B5E99DE09D1E |  | R22 | Non-TXV |  | 3.057% | 0.96943 | 5.875% | [5 empty] | Non-TXV | 3.057%
Jamestown | CA | 95327-9670 |  | 2013-09-06 | 2013-09-06 09:06 | 2013-09-06 09:29 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 5.7 | Yes | Yes | 21.9 | 19.9 | 2 | 2748918FC6FC45EA833323DBAD40F918 |  | R22 | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Yuba City | CA | 95993-8333 |  | 2013-08-29 | 2013-08-29 11:08 | 2013-08-29 11:29 | BRYANT - 563CN042-D | 100 | 3.6 | Yes | Yes | 18 | 20.7 | -2.7 | 94ECF0334B0849AD9D066316E1371BAC |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Sonora | CA | 95370-5064 |  | 2013-09-05 | 2013-09-05 11:01 | 2013-09-05 11:24 | CARRIER - 48SS-030060331 | 53 | 8.5 | Yes | Yes | 24.1 | 20.3 | 3.8 | A493763AB7C94869A24B987255B5E728 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.04% | 0.83962 | 30.82% | [5 empty] | Non-TXV | 16.04%
Paradise | CA | 95969-3707 |  | 2013-10-01 | 2013-10-01 13:59 | 2013-10-01 14:51 | YORK - H2RC042506G | 61 | 3 | Yes | Yes | 17.7 | 20.7 | -3 | 972F8686DBEA410AB1EAA164312795CE |  | R22 | Non-TXV |  | 4.918% | 0.95082 | 9.451% | [5 empty] | Non-TXV | 4.918%
Paradise | CA | 95969-3707 |  | 2013-10-01 | 2013-10-01 13:53 | 2013-10-01 15:13 | YORK - D1NH024N05606C | 70 | 4 | Yes | Yes | 17.6 | 17.2 | 0.4 | 30D0CD77CD6F4E13A1B0FCAF9C4F5372 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Stockton | CA | 95207-1109 |  | 2013-08-30 | 2013-08-30 09:58 | 2013-08-30 10:16 | PAYNE - PY3PNA024060NB | 89 | -10.5 | Yes | Yes | 12.2 | 14.4 | -2.2 | 85B1E3E3645341BEA015B9E13D6FC52D |  | R22 | Non-TXV |  | -11.8% | 1.118 | 3.304% |  |  |  |  | Non-TXV |  |  | -11.8%
Jamestown | CA | 95327-9670 |  | 2013-09-06 | 2013-09-06 09:50 | 2013-09-06 10:17 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 3.1 | Yes | Yes | 23.5 | 21 | 2.5 | B99F0DDBD32046C89F2601C9FC765ECF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.69% | 0.9631 | 7.092% | [5 empty] | Non-TXV | 3.69%
Stockton | CA | 95207-6502 |  | 2013-08-20 | 2013-08-20 11:15 | 2013-08-20 11:41 | PAYNE - 563CN048-A | 166 | 8.8 | Yes | Yes | 24.5 | 19.2 | 5.3 | AB9E5E9253984F60BE0C12313E4C4852 |  | R22 | Non-TXV |  | 5.301% | 0.94699 | 10.19% | [5 empty] | Non-TXV | 5.301%
Chowchilla | CA | 93610-8997 |  | 2013-08-21 | 2013-08-21 15:17 | 2013-08-21 20:14 | - 1RA0245606G | 60 | -5.6 | Yes | Yes | 17.8 | 16.9 | 0.9 | C63684359A674F67A8FDD6CF7B64079C |  | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Chowchilla | CA | 93610-2227 |  | 2013-11-06 | 2013-11-06 15:08 | 2013-11-06 15:10 | YORK - D1NP030N05606A | 73 | 2.8 | Yes | Yes | 18 | 19.3 | -1.3 | 8368ED191F9F4F2C8EA10AF995AA5515 |  | R22 | Non-TXV |  | 3.836% | 0.96164 | 7.371% | [5 empty] | Non-TXV | 3.836%
Chowchilla | CA | 93610-8998 |  | 2013-08-22 | 2013-08-22 10:17 | 2013-08-22 10:17 | RUUD - UNK | 61 | 0 | Yes | Yes | 26.8 | 21.3 | 5.6 | E50D50B9B6624307A397379FD835E91D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-8990 |  | 2013-08-26 | 2013-08-26 00:27 | 2013-08-26 00:45 | YORK - D2YSO24N04506A | 62 | 5.9 | Yes | Yes | 20.7 | 21.3 | -0.5 | A2F687462A024E3EA132365402D89523 |  | R22 | Non-TXV |  | 9.516% | 0.90484 | 18.29% | [5 empty] | Non-TXV | 9.516%
Merced | CA | 95340-3809 |  | 2013-08-20 | 2013-08-20 13:25 | 2013-08-20 13:26 | - CK421C | 86 | 12.1 | Yes | Yes | 22.5 | 22 | 0.5 | 92E284CD772440B6A4A2832AA0F234EC |  | R22 | Non-TXV |  | 14.07% | 0.8593 | 27.04% | [5 empty] | Non-TXV | 14.07%
Merced | CA | 95340-3902 |  | 2013-08-28 | 2013-08-28 15:04 | 2013-08-28 15:06 | PAYNE - 7777UNK | 66 | 2.3 | Yes | Yes | 25.8 | 19.9 | 5.9 | A004C56CD6864ECAB7D01E0382F41DB0 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Jamestown | CA | 95327-9670 |  | 2013-09-12 | 2013-09-12 14:18 | 2013-09-12 14:36 | UNITARY PRODUCTS GROUP - BRCS0481BD | 117 | 27.7 | Yes | Yes | 18.8 | 21.5 | -2.7 | DF346B932E1D4E5F992206E1CDA39719 |  | R22 | Non-TXV |  | 23.68% | 0.76325 | 45.5% | [5 empty] | Non-TXV | 23.68%
Jamestown | CA | 95327-9670 |  | 2013-09-06 | 2013-09-06 11:43 | 2013-09-06 11:46 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 12.3 | Yes | Yes | 24.6 | 20.3 | 4.3 | 342A2418A7854D8790103EDF9C8DB801 |  | R22 | Non-TXV |  | 14.64% | 0.85357 | 28.14% | [5 empty] | Non-TXV | 14.64%
Red Bluff | CA | 96080-8993 |  | 2013-08-09 | 2013-08-09 13:51 | 2013-08-09 13:51 | AMANA - GPG13360701AK | 112 | 0 | Yes | Yes | 18.8 | 21.5 | -2.7 | CA2768AFE4BA4F639E8F0779AF608043 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Jamestown | CA | 95327-9670 |  | 2013-09-24 | 2013-09-24 13:35 | 2013-09-24 13:56 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 4.6 | Yes | Yes | 20.2 | 19.9 | 0.3 | F0E570F9B15048A59CC5A08A0762E1DA |  | R22 | Non-TXV |  | 5.476% | 0.94524 | 10.52% | [5 empty] | Non-TXV | 5.476%
Corning | CA | 96021-9246 |  | 2013-08-13 | 2013-08-13 10:02 | 2013-08-13 10:31 | RUUD - 13AJA30A01 | 98 | 3.1 | Yes | Yes | 21 | 23.7 | -2.7 | 7FD65AE0D18442698EF7A04A39B91CE6 |  | R22 | Non-TXV |  | 3.163% | 0.96837 | 6.079% | [5 empty] | Non-TXV | 3.163%
Chico | CA | 95926-2921 |  | 2013-08-22 | 2013-08-22 16:17 | 2013-08-22 20:36 | PAYNE - 113RNA24-C | 70 | 3.8 | Yes | Yes | 18.7 | 17.7 | 1 | 2C8A4A1CF2A54ADD8595675696FC4A9F |  | R22 | TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | TXV | 5.429%
Manteca | CA | 95336-3637 |  | 2013-08-16 | 2013-08-16 15:51 | 2013-08-16 16:17 | GOODMAN - PGB024050-1 | 54 | 1.8 | Yes | Yes | 17.6 | 19.5 | -1.9 | 690B4DFBA70041C48240F99493510E5A |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Thornton | CA | 95686-0000 |  | 2013-09-25 | 2013-09-25 11:50 | 2013-09-25 12:16 | BRYANT - 561CJ048-A | 102 | 5.9 | Yes | Yes | 24.1 | 18.2 | 5.9 | 6B232CB67CF846D9ABD9998DF7BCA149 |  | R22 | Non-TXV |  | 5.784% | 0.94216 | 11.12% | [5 empty] | Non-TXV | 5.784%
Atwater | CA | 95301-2218 |  | 2013-08-21 | 2013-08-21 10:44 | 2013-08-21 11:20 | YORK - D1NY048N0906A | 152 | 5.2 | Yes | Yes | 18.3 | 19.2 | -0.9 | 3EE8A6431FAC4A37B138A7E8E708059C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Red Bluff | CA | 96080-9303 |  | 2013-08-09 | 2013-08-09 17:45 | 2013-08-09 17:45 | PAYNE - PA13NA036 | 70 | 0 | Yes | Yes | 18.6 | 20.7 | -2.1 | 82C9A90DDE2C4042B65F81F43288315A |  | R410A | TXV |  | 0% | 1 | 0%
Pine Grove | CA | 95665-9613 |  | 2013-09-23 | 2013-09-23 12:53 | 2013-09-23 13:13 | BDP - 588ANW030060ADAD | 56 | 17.1 | Yes | Yes | 25.8 | 20 | 5.8 | 644786A2D7E74EE2964C177662B02D7A |  | R22 | Non-TXV |  | 30.54% | 0.69464 | 58.68% | [5 empty] | Non-TXV | 30.54%
Dos Palos | CA | 93620-2653 |  | 2013-08-16 | 2013-08-16 11:12 | 2013-08-16 11:15 | YORK - H1BD036S06A | 72 | 2.4 | Yes | Yes | 21 | 19.1 | 1.9 | EABAF3D6FE734366A58BD4E63874237D |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Mariposa | CA | 95338-0000 |  | 2013-09-11 | 2013-09-11 10:00 | 2013-09-11 10:01 | BRYANT - 561CJ048F | 109 | 8.5 | Yes | Yes | 23.4 | 18.2 | 5.2 | C3B175C11CDD4028901F6DABD89C4DED |  | R22 | TXV |  | 7.798% | 0.92202 | 14.99% | [5 empty] | TXV | 7.798%
Merced | CA | 95341-6689 |  | 2013-08-15 | 2013-08-15 16:59 | 2013-08-15 17:03 | OTHER - 7777UNK | 80 | 3.4 | Yes | Yes | 22.8 | 16.8 | 6 | 1733E11A209D4F40B9920C3E6C934F74 |  | R22 | Non-TXV |  | 4.25% | 0.9575 | 8.168% | [5 empty] | Non-TXV | 4.25%
Chowchilla | CA | 93610-2059 |  | 2013-08-19 | 2013-08-19 15:23 | 2013-08-19 15:25 | NORDYNE - JS3BD048K | 143 | 17.7 | Yes | Yes | 20.8 | 20.8 | 0 | 55FC0DF092B147A0B7CDC988DE2AD034 |  | R22 | Non-TXV |  | 12.38% | 0.87622 | 23.79% | [5 empty] | Non-TXV | 12.38%
Dos Palos | CA | 93620-2737 |  | 2013-08-17 | 2013-08-17 10:06 | 2013-08-17 10:09 | RHEEM - ATT48B1 0 | 126 | 4.3 | Yes | Yes | 20.7 | 21.4 | -0.7 | 6B14931D03634FEA9ED9194526E4FC0B |  | R22 | Non-TXV |  | 3.413% | 0.96587 | 6.558% | [5 empty] | Non-TXV | 3.413%
Cameron Park | CA | 95682-9267 |  | 2013-09-18 | 2013-09-18 14:41 | 2013-09-18 14:41 | GE - UNK | 125 | 0 | Yes | Yes | 17.5 | 18.2 | -0.7 | B7A6FF01D4F444DC92B6ED6A3A99168F |  | R22 | TXV |  | 0% | 1 | 0%
Corning | CA | 96021-3440 |  | 2013-09-18 | 2013-09-18 14:14 | 2013-09-18 15:02 | RUUD - RRKA-042JK08E | 69 | 8.4 | Yes | Yes | 16.5 | 19.3 | -2.8 | C8BD50FD1ECB49F2B447DDD641115D77 |  | R22 | Non-TXV |  | 12.17% | 0.87826 | 23.4% | [5 empty] | Non-TXV | 12.17%
Merced | CA | 95348-1656 |  | 2013-08-15 | 2013-08-15 15:47 | 2013-08-15 15:49 | GOODMAN - PGB03605-1 | 60 | 1.8 | Yes | Yes | 22.7 | 21.2 | 1.5 | 29BCDA57A4214252BB32AC68224DA907 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Manteca | CA | 95336-3512 |  | 2013-10-03 | 2013-10-03 13:27 | 2013-10-03 13:50 | GE - BGTA730B1A01 | 53 | 1.8 | Yes | Yes | 22.2 | 19.3 | 2.9 | CCB339261B2D40C29717750A396BF321 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Chowchilla | CA | 93610-2079 |  | 2013-09-06 | 2013-09-06 10:11 | 2013-09-06 10:12 | CARRIER - 38CK048370 | 100 | 5.2 | Yes | Yes | 26.7 | 20.9 | 5.8 | 97FB0CE265B744DC9B30280731C49117 |  | R22 | TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | TXV | 5.2%
Manteca | CA | 95336-4812 |  | 2013-08-16 | 2013-08-16 16:30 | 2013-08-16 16:50 | RHEEM - 13AJN30A01 | 75 | 4.9 | Yes | Yes | 20.4 | 21 | -0.6 | 83F3CBDCFFF74A02AFB04C8E894A1EA7 |  | R410A | TXV |  | 6.533% | 0.93467 | 12.56% | [5 empty] | TXV | 6.533%
Wallace | CA | 95254-0000 |  | 2013-08-23 | 2013-08-23 13:11 | 2013-08-23 13:37 | RUUD - URKA-A030JK06E | 54 | 3.4 | Yes | Yes | 24.2 | 21 | 3.2 | E50E44079D584BA5A027ABEE420DE0DB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Atwater | CA | 95301-4512 |  | 2013-08-15 | 2013-08-15 09:54 | 2013-08-15 10:25 | TRANE - BTD730A100B0 | 74 | 2.2 | Yes | Yes | 21.2 | 18.8 | 2.5 | 9D1F8EFD3B19481A98307CAD715F7350 |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Orosi | CA | 93647-1922 |  | 2013-08-21 | 2013-08-21 15:39 | 2013-08-21 15:57 | DUCANE - AC12B30-A | 48 | 3.9 | Yes | Yes | 19 | 20.5 | -1.5 | 0A211ACC935E4DEAB9253A5DC8FC8375 |  | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Stockton | CA | 95207-1117 |  | 2013-08-15 | 2013-08-15 15:42 | 2013-08-15 16:00 | RHEEM - URKA-A036JK06E | 62 | 10.7 | Yes | Yes | 20.5 | 21.2 | -0.7 | AC68B73AA72C4B9EB0E299F513029DA2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.26% | 0.82742 | 33.17% | [5 empty] | Non-TXV | 17.26%
Paradise | CA | 95969-2921 |  | 2013-08-30 | 2013-08-30 14:28 | 2013-08-30 15:02 | GOODMAN - GPG153009041AA | 102 | 4.6 | Yes | Yes | 22.5 | 23.5 | -0.9 | DA4EF7C4A85842C1B2EF522A8B4C7B93 |  | R410A | Non-TXV |  | 4.51% | 0.9549 | 8.667% | [5 empty] | Non-TXV | 4.51%
Pioneer | CA | 95666-9650 |  | 2013-09-10 | 2013-09-10 10:48 | 2013-09-10 11:19 | PAYNE - PY2PNB024060AAAA | 52 | 9 | Yes | Yes | 19.4 | 21 | -1.6 | C417F29BF2EF461CBAD611B751F6C1C6 |  | R22 | Non-TXV |  | 17.31% | 0.82692 | 33.26% | [5 empty] | Non-TXV | 17.31%
Stockton | CA | 95207-2112 |  | 2013-08-19 | 2013-08-19 08:57 | 2013-08-19 08:57 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 18 | 17.6 | 0.4 | 3A1947BDF72045869A661C4958FE53E7 |  | R410A | TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-8456 |  | 2013-08-28 | 2013-08-28 17:01 | 2013-08-28 17:40 | TRANE - 4TTX3036A1000AA | 78 | 9.2 | Yes | Yes | 18.9 | 21 | -2.1 | DD0EBF4E0AEE416289AAC2F128CE85AF |  | R410A | TXV |  | 11.79% | 0.88205 | 22.67% | [5 empty] | TXV | 11.79%
Sonora | CA | 95370-6959 |  | 2013-09-06 | 2013-09-06 14:48 | 2013-09-06 15:46 | CARRIER - 38TH042330 | 87 | 8.7 | Yes | Yes | 26.8 | 23.1 | 3.7 | 4E0CC332B9114CE3AA8BD3C3BBADA667 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Maxwell | CA | 95955-0000 |  | 2013-09-09 | 2013-09-09 09:59 | 2013-09-09 09:59 | RHEEM - RRNA-B024JK06X | 70 | 0 | Yes | Yes | 0 | 17.7 | -17.7 | 986200A5F29E440F92553BCF9204A9AB |  | R22 | TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-8245 |  | 2013-08-28 | 2013-08-28 12:22 | 2013-08-28 12:22 | RHEEM - RQKA-A042JK | 139 | 0 | Yes | Yes | 21.8 | 19.3 | 2.5 | 1DF4F70CC0DE4B18816EFEF88977CDA9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3855 |  | 2013-08-27 | 2013-08-27 11:46 | 2013-08-27 11:49 | YORK - 7777UNK | 80 | 4.7 | Yes | Yes | 26.7 | 21.2 | 5.5 | 8B7EAEAF89214C0D9A7B2B2D3F0AE79D |  | R22 | Non-TXV |  | 5.875% | 0.94125 | 11.29% | [5 empty] | Non-TXV | 5.875%
Sonora | CA | 95370-8046 |  | 2013-10-03 | 2013-10-03 11:31 | 2013-10-03 11:50 | BRYANT - 582AJW048115AAAG | 81 | -7.6 | Yes | Yes | 17.5 | 19.1 | -1.6 | 9B4E7EDFC154465F89474F992B14D1F9 |  | R22 | Non-TXV |  | -9.383% | 1.0938 | 2.628% |  |  |  |  | Non-TXV |  |  | -9.383%
Meadow Vista | CA | 95722-9471 |  | 2013-08-30 | 2013-08-30 16:36 | 2013-08-30 16:36 | LENNOX - HS18-651-2P | 139 | 0 | Yes | Yes | 20.7 | 19.3 | 1.4 | C2BA5A1CBC4B453985D7C7EFC1EAB178 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Meadow Vista | CA | 95722-9471 |  | 2013-08-30 | 2013-08-30 16:50 | 2013-08-30 16:50 | LENNOX - HS18-261-8P | 42 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 51CCDD4F919C4ED0B47FF4C52AA4D893 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3240 |  | 2013-08-15 | 2013-08-15 08:38 | 2013-08-15 08:40 | RHEEM - RAKA037JAZ | 79 | 6.3 | Yes | Yes | 22 | 16.5 | 5.5 | 7D15D717FA2949A8AF7C7833EFA38B30 |  | R22 | Non-TXV |  | 7.975% | 0.92025 | 15.33% | [5 empty] | Non-TXV | 7.975%
Grass Valley | CA | 95945-9706 |  | 2013-08-30 | 2013-08-30 13:07 | 2013-08-30 13:07 | CARRIER - 38BR042300 | 134 | 0 | Yes | Yes | 23.6 | 23.4 | 0.2 | B35C00C09C5649E08C95F090AAE2DF5D |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3125 |  | 2013-09-11 | 2013-09-11 15:50 | 2013-09-11 22:10 | YORK - H3RC060S06HA | 144 | 10 | Yes | Yes | 20.8 | 18.7 | 2.1 | 43B0763B8A2A43CCB5038B12CA00ED6D |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Jamestown | CA | 95327-9670 |  | 2013-09-06 | 2013-09-06 10:58 | 2013-09-06 11:11 | BRYANT - 113RNA036-D | 84 | -11.3 | Yes | Yes | 25.7 | 19.8 | 5.9 | 855B3C1B217742078B0C08ECF2BA46B4 |  | R22 | TXV |  | -13.45% | 1.1345 | 3.767% |  |  |  |  | TXV |  |  | -13.45%
Magalia | CA | 95954-9567 |  | 2013-10-01 | 2013-10-01 12:02 | 2013-10-01 12:20 | LENNOX - 10GCS036X-75-3PB | 58 | 3.3 | Yes | Yes | 19.8 | 20.5 | -0.7 | 761645D5FAED4C48A1D833885A0FF0FC |  | R22 | Non-TXV |  | 5.69% | 0.9431 | 10.93% | [5 empty] | Non-TXV | 5.69%
Stockton | CA | 95206-6135 |  | 2013-08-19 | 2013-08-19 11:59 | 2013-08-19 12:38 | YORK - H2RA030S06A | 62 | 6.2 | Yes | Yes | 21.5 | 19 | 2.5 | DCD1C4DCCC4F4567A141E92B3CCA3395 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Penn Valley | CA | 95946-9206 |  | 2013-08-15 | 2013-08-15 10:45 | 2013-08-15 11:04 | RHEEM - RRNA-B036JK08X | 84 | 8.7 | Yes | Yes | 20 | 19.7 | 0.3 | 96EB4BA8F9BF4978A1C46C7892622B92 |  | R22 | TXV |  | 10.36% | 0.89643 | 19.9% | [5 empty] | TXV | 10.36%
Tracy | CA | 95376-7005 |  | 2013-08-22 | 2013-08-22 14:33 | 2013-08-22 14:54 | BRYANT - 561CJ060-H | 85 | 7.9 | Yes | Yes | 19.9 | 19.5 | 0.4 | 4F0FCF1BFC24441C8715ED79A52E741C |  | R22 | Non-TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | Non-TXV | 9.294%
Atwater | CA | 95301-2040 |  | 2013-09-09 | 2013-09-09 10:27 | 2013-09-09 10:48 | LUXAIRE - 36ECW080GB | 129 | 8.2 | Yes | Yes | 18.3 | 20.2 | -1.9 | FA52731266744A21A31636B4A262F482 |  | R22 | Non-TXV |  | 6.357% | 0.93643 | 12.22% | [5 empty] | Non-TXV | 6.357%
Fresno | CA | 93727-3071 |  | 2013-08-21 | 2013-08-21 13:24 | 2013-08-21 13:47 | RHEEM - RRPL036JKO6X | 92 | 3.3 | Yes | Yes | 18.2 | 17.6 | 0.7 | 3F98E202C7D744A0995880B494C168C6 |  | R410A | Non-TXV |  | 3.587% | 0.96413 | 6.893% | [5 empty] | Non-TXV | 3.587%
Stockton | CA | 95215-5209 |  | 2013-09-12 | 2013-09-12 14:42 | 2013-09-12 14:45 | CARRIER - 50YH024300 | 70 | 7.5 | Yes | Yes | 19.9 | 18.7 | 1.2 | D40A18B8E34E47BDA21BFD3E02D417A1 |  | R22 | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Merced | CA | 95348-9520 |  | 2013-08-23 | 2013-08-23 13:34 | 2013-08-23 13:36 | OTHER - CKL42-1B | 115 | 4 | Yes | Yes | 22.4 | 20.8 | 1.6 | 2EC5CD98BE7147A8A20F5AEC31714134 |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Chico | CA | 95973-0156 |  | 2013-08-21 | 2013-08-21 14:04 | 2013-08-21 21:23 | PAYNE - 585G1018040 | 55 | 8.4 | Yes | Yes | 15.8 | 18.8 | -3 | 85708E6D20EE45E8A9AF59CE3FC04C44 |  | R22 | Non-TXV |  | 15.27% | 0.84727 | 29.35% | [5 empty] | Non-TXV | 15.27%
Magalia | CA | 95954-9412 |  | 2013-08-29 | 2013-08-29 11:57 | 2013-08-29 12:32 | DAY & NIGHT - NA | 70 | 2.2 | Yes | Yes | 21 | 20.6 | 0.4 | DFD528F484814DE694EE5B83DC9D4C8C |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Merced | CA | 95341-5617 |  | 2013-08-20 | 2013-08-20 08:08 | 2013-08-20 08:10 | OTHER - GPG13360701AA | 112 | 4.4 | Yes | Yes | 24.3 | 20.8 | 3.5 | B9B7BDB846F04D85BEE1D20166726E7B |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Stockton | CA | 95209-2661 |  | 2013-08-20 | 2013-08-20 17:08 | 2013-08-20 17:25 | GOODMAN - CRT36-1A | 140 | 13 | Yes | Yes | 21.7 | 22.7 | -0.9 | 450FC6971E0C46518747BED0C03DB403 |  | R22 | Non-TXV |  | 9.286% | 0.90714 | 17.85% | [5 empty] | Non-TXV | 9.286%
Stockton | CA | 95207-3609 |  | 2013-08-19 | 2013-08-19 10:00 | 2013-08-19 10:17 | YORK - D1NA036N03606C | 67 | 5.3 | Yes | Yes | 18.4 | 17.7 | 0.8 | 6659C0F177DB4839A637840F3A74302D |  | R22 | Non-TXV |  | 7.91% | 0.9209 | 15.2% | [5 empty] | Non-TXV | 7.91%
Sonora | CA | 95370-9080 |  | 2013-10-03 | 2013-10-03 14:12 | 2013-10-03 14:43 | PAYNE - PA10JA048-C | 96 | -9 | Yes | Yes | 14.9 | 17.7 | -2.8 | ADB880DB6C5C4C0CA8D7B224161F76A3 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Stockton | CA | 95209-2447 |  | 2013-08-20 | 2013-08-20 14:53 | 2013-08-20 15:07 | HEIL - HAC042AKA5 | 98 | 15.3 | Yes | Yes | 18 | 19.2 | -1.2 | 1B8B051FBE0D4588889022B50B615FEE |  | R22 | Non-TXV |  | 15.61% | 0.84388 | 30% | [5 empty] | Non-TXV | 15.61%
Stockton | CA | 95204-2752 |  | 2013-08-23 | 2013-08-23 12:32 | 2013-08-23 12:50 | SEARS - 76981604 | 64 | 16.9 | Yes | Yes | 18.6 | 19.3 | -0.7 | F8748BCD648941458E820B211BA72729 |  | R22 | Non-TXV |  | 26.41% | 0.73594 | 50.75% | [5 empty] | Non-TXV | 26.41%
Red Bluff | CA | 96080-4907 |  | 2013-09-24 | 2013-09-24 16:25 | 2013-09-24 16:44 | GOODMAN - CK36-1A | 73 | 3.5 | Yes | Yes | 25.5 | 23.4 | 2.1 | 543F60DF35EA4A9284B997FED3363485 |  | R22 | Non-TXV |  | 4.795% | 0.95205 | 9.214% | [5 empty] | Non-TXV | 4.795%
Stockton | CA | 95210-3714 |  | 2013-08-16 | 2013-08-16 11:05 | 2013-08-16 11:05 | RHEEM - RRNL-B030JK06X | 76 | 0 | Yes | Yes | 15.1 | 16.9 | -1.8 | 6C6379CCFED44C2BBD89DEC9A698BBED |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-1820 |  | 2013-08-21 | 2013-08-21 15:59 | 2013-08-21 16:45 | RHEEM - UNK | 80 | -5.6 | Yes | Yes | 15.4 | 18.3 | -2.9 | 738DBDED06D24A8FA52E08DAC4C63A05 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Oroville | CA | 95966-3976 |  | 2013-08-29 | 2013-08-29 15:02 | 2013-08-29 15:25 | CARRIER - 50YQ048300 | 115 | 3.4 | Yes | Yes | 26 | 21.5 | 4.5 | 15986D9C6C364C89B94F19AD97638C74 |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Merced | CA | 95341-5300 |  | 2013-08-20 | 2013-08-20 15:50 | 2013-08-20 15:52 | GOODMAN - CKL24-1E | 69 | 3.2 | Yes | Yes | 22 | 20.4 | 1.6 | 2033A96AEE5D435EB5639851384F4C7B |  | R22 | Non-TXV |  | 4.638% | 0.95362 | 8.913% | [5 empty] | Non-TXV | 4.638%
Stockton | CA | 95207-6579 |  | 2013-08-19 | 2013-08-19 15:15 | 2013-08-19 15:15 | RHEEM - UNK | 96 | 0 | Yes | Yes | 16 | 17.4 | -1.4 | 44A6191104DA4AD693BAF90093035673 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1544 |  | 2013-08-21 | 2013-08-21 15:24 | 2013-08-21 15:35 | BRYANT - UNK | 96 | 6.6 | Yes | Yes | 18.8 | 19.7 | -0.9 | 9F53609B35F744BFAD16B873F721BC11 |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Corning | CA | 96021-3239 |  | 2013-09-16 | 2013-09-16 12:43 | 2013-09-16 13:43 | AMANA - PGD42CO902E | 120 | 8.3 | Yes | Yes | 19.3 | 19.1 | 0.2 | 8504AED471B04627BD5BC8B7BDA81070 |  | R22 | Non-TXV |  | 6.917% | 0.93083 | 13.29% | [5 empty] | Non-TXV | 6.917%
Chowchilla | CA | 93610-9396 |  | 2013-09-06 | 2013-09-06 10:48 | 2013-09-06 10:49 | LENNOX - 10ACB48-10P | 102 | 3.5 | Yes | Yes | 20.1 | 19.8 | 0.3 | 27CBA540864947BBA997B3A53DAB5CCF |  | R22 | Non-TXV |  | 3.431% | 0.96569 | 6.594% | [5 empty] | Non-TXV | 3.431%
Tracy | CA | 95376-5313 |  | 2013-09-16 | 2013-09-16 12:09 | 2013-09-16 12:30 | GOODMAN - CL42-18B | 101 | 3.2 | Yes | Yes | 22.2 | 19.2 | 3 | D99C09CBC8B04C978C10E972D6400408 |  | R22 | Non-TXV |  | 3.168% | 0.96832 | 6.089% | [5 empty] | Non-TXV | 3.168%
Chico | CA | 95926-3812 |  | 2013-08-16 | 2013-08-16 14:35 | 2013-08-16 15:59 | LENNOX - 12GCS030-75-3PH | 85 | 7.2 | Yes | Yes | 25.6 | 20 | 5.7 | 82427DCF22544B248FDD9A2AEC230846 |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Stockton | CA | 95207-1109 |  | 2013-08-15 | 2013-08-15 14:47 | 2013-08-15 15:04 | RHEEM - RRKA-A030JK06E | 54 | 2.5 | Yes | Yes | 18.1 | 17.5 | 0.6 | 657B1617F79041CFB50B9C1FFEE2C656 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Oakdale | CA | 95361-3412 |  | 2013-08-28 | 2013-08-28 09:31 | 2013-08-28 10:01 | ICP - HAC236AKC3 | 114 | 3.4 | Yes | Yes | 20.3 | 18.2 | 2.1 | 37F7F629EC854FF781F9ECC31D0C8EF3 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Copperopolis | CA | 95228-9464 |  | 2013-09-24 | 2013-09-24 16:06 | 2013-09-24 17:19 | BDP - 563CN024-C | 103 | -8.5 | Yes | Yes | 25.5 | 19.9 | 5.6 | ACAC8DAFFD1B428989E0B8A118D1BB25 |  | R22 | Non-TXV |  | -8.252% | 1.0825 | 2.311% |  |  |  |  | Non-TXV |  |  | -8.252%
Chico | CA | 95973-0843 |  | 2013-08-28 | 2013-08-28 14:55 | 2013-08-28 15:26 | GIBSON - JS5BD-024K | 104 | 3.1 | Yes | Yes | 16.4 | 19.2 | -2.8 | 4BDA83A06EA64B5B942AD919677595D3 |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Oakdale | CA | 95361-8727 |  | 2013-08-19 | 2013-08-19 12:54 | 2013-08-19 13:28 | ICP - T4A436GKA100 | 165 | -21 | Yes | Yes | 22.7 | 20.2 | 2.5 | 09142581040541F0832C3BA700FCAC7D |  | R410A | TXV |  | -12.73% | 1.1273 | 3.564% |  |  |  |  | TXV |  |  | -12.73%
Red Bluff | CA | 96080-3851 |  | 2013-08-29 | 2013-08-29 08:23 | 2013-08-29 10:27 | GOODMAN - CKL 49-1L | 112 | 9 | Yes | Yes | 14 | 17 | -3 | 4D71269C9DA540979A8229ECCAECEDE0 |  | R22 | Non-TXV |  | 8.036% | 0.91964 | 15.44% | [5 empty] | Non-TXV | 8.036%
Tracy | CA | 95376-0747 |  | 2013-08-15 | 2013-08-15 09:23 | 2013-08-15 09:33 | RUUD - UARL-048JEZ | 150 | -11.5 | Yes | Yes | 21.7 | 17.9 | 3.8 | 51CEA786B96F4643A0B8531D7696BA18 |  | R410A | TXV |  | -7.667% | 1.0767 | 2.147% |  |  |  |  | TXV |  |  | -7.667%
Nevada City | CA | 95959-9643 |  | 2013-08-27 | 2013-08-27 16:29 | 2013-08-27 16:48 | YORK - H1DA030S06A | 83 | 8 | Yes | Yes | 25.8 | 20.9 | 4.9 | 8BDE9B2229F8490DA4D0A9405C227BF0 |  | R22 | Non-TXV |  | 9.639% | 0.90361 | 18.52% | [5 empty] | Non-TXV | 9.639%
Madera | CA | 93637-2985 |  | 2013-09-11 | 2013-09-11 18:33 | 2013-09-11 18:36 | YORK - AC048X1021A | 117 | 4.1 | Yes | Yes | 20.5 | 19 | 1.5 | E1FB7162D88F4BD58F53F667E8EE9BA3 |  | R22 | Non-TXV |  | 3.504% | 0.96496 | 6.734% | [5 empty] | Non-TXV | 3.504%
Chico | CA | 95973-0139 |  | 2013-08-22 | 2013-08-22 12:31 | 2013-08-22 13:28 | AMANA - PGD42C0902E | 120 | 13.6 | Yes | Yes | 22.8 | 19.3 | 3.5 | 152881CCB3B04E8F9710B82F60AE54B3 |  | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Stockton | CA | 95215-9507 |  | 2013-08-29 | 2013-08-29 17:41 | 2013-08-29 18:00 | YORK - H2RD042S06B | 141 | 4.3 | Yes | Yes | 24.3 | 18.5 | 5.8 | FB633BC1196A4A3B8BFDA214BCD4BD9B |  | R22 | Non-TXV |  | 3.05% | 0.9695 | 5.861% | [5 empty] | Non-TXV | 3.05%
Red Bluff | CA | 96080-2846 |  | 2013-08-26 | 2013-08-26 15:05 | 2013-08-26 19:33 | RHEEM - BAJA24A01757 | 51 | 2.7 | Yes | Yes | 15.9 | 18.8 | -2.9 | BC42E3276068458491C321FAB6F72D8C |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Tracy | CA | 95377-8958 |  | 2013-08-22 | 2013-08-22 16:03 | 2013-08-22 16:13 | TRANE - TTD730B100A1 | 85 | 5.9 | Yes | Yes | 20.1 | 19.7 | 0.4 | D59841B507C34D1590110E7D49E66EC1 |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
Tracy | CA | 95377-8958 |  | 2013-08-22 | 2013-08-22 16:19 | 2013-08-22 16:38 | TRANE - TTD748B100A0 | 116 | 4.2 | Yes | Yes | 23 | 20.9 | 2.1 | 80E56A67EA844588B9E2D63B421D0A30 |  | R22 | Non-TXV |  | 3.621% | 0.96379 | 6.958% | [5 empty] | Non-TXV | 3.621%
Fresno | CA | 93726-4014 |  | 2013-08-20 | 2013-08-20 16:48 | 2013-08-20 17:19 | PAYNE - UNK | 52 | 4.3 | Yes | Yes | 29.9 | 24.2 | 5.7 | 998700657CB8436F8D31A8C2799D8803 |  | R22 | Non-TXV |  | 8.269% | 0.91731 | 15.89% | [5 empty] | Non-TXV | 8.269%
Garden Valley | CA | 95633-9505 |  | 2013-10-03 | 2013-10-03 14:57 | 2013-10-03 14:57 | AMERICAN STANDARD - YCC036F1M0BC | 85 | 0 | Yes | Yes | 25.1 | 20.9 | 4.2 | 8BB610B38DD8432484D4427504D5C18E |  | R22 | TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5706 |  | 2013-08-23 | 2013-08-23 19:28 | 2013-08-23 19:46 | YORK - CKL30-10 | 70 | 5.3 | Yes | Yes | 17.1 | 18.8 | -1.7 | 44654819FBB2475DABDE8BE61EB3CBB9 |  | R22 | Non-TXV |  | 7.571% | 0.92429 | 14.55% | [5 empty] | Non-TXV | 7.571%
Sanger | CA | 93657-2056 |  | 2013-08-23 | 2013-08-23 13:25 | 2013-08-23 13:46 | LENNOX - 10ACC-042-230-03 | 81 | 7.5 | Yes | Yes | 18.5 | 21 | -2.5 | 31487F700631470991829B0F81C53484 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.259% | 0.90741 | 17.79% | [5 empty] | Non-TXV | 9.259%
Fresno | CA | 93705-2307 |  | 2013-08-27 | 2013-08-27 08:22 | 2013-08-27 08:23 | AMERICAN STANDARD - 4YCY4048A1096AA | 131 | 4.3 | Yes | Yes | 22.5 | 18.3 | 4.2 | BAF3E01761174D7294486B2725AA32B2 |  | R410A | Non-TXV |  | 3.282% | 0.96718 | 6.308% | [5 empty] | Non-TXV | 3.282%
Kerman | CA | 93630-9366 |  | 2013-08-21 | 2013-08-21 11:17 | 2013-08-21 11:19 | LENNOX - 13ACC-048-230-01 | 158 | 5.3 | Yes | Yes | 23.2 | 19.7 | 3.5 | 4C49538BA39F412CAF61A9AD82903D3D |  | R22 | Non-TXV |  | 3.354% | 0.96646 | 6.446% | [5 empty] | Non-TXV | 3.354%
Madera | CA | 93637-6146 |  | 2013-08-28 | 2013-08-28 10:51 | 2013-08-28 12:12 | GOODMAN - GPG13240451CB | 74 | 2.8 | Yes | Yes | 21.5 | 21.6 | 0 | 413F09F791C04904825447A25780BFD7 |  | R22 | Non-TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | Non-TXV | 3.784%
Sanger | CA | 93657-2272 |  | 2013-09-25 | 2013-09-25 18:00 | 2013-09-25 18:26 | CARRIER - N/A | 60 | 6.8 | Yes | Yes | 23 | 20.4 | 2.6 | 63FD1E738E274393BE8A9CA8C2B9C8FC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Sanger | CA | 93657-2972 |  | 2013-08-23 | 2013-08-23 16:51 | 2013-08-23 18:36 | PAYNE - 580AN036060 | 96 | 5.7 | Yes | Yes | 18 | 18.9 | -0.9 | C775B4907B684326806E9DB3FC653483 |  | R22 | Non-TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | Non-TXV | 5.938%
Red Bluff | CA | 96080-4145 |  | 2013-09-24 | 2013-09-24 17:27 | 2013-09-24 17:43 | GOODMAN - GSC130241DA | 83 | 2.7 | Yes | Yes | 18.3 | 20.4 | -2.1 | 6BF2F635EF3241BA8EBED4D47A3BDAAC |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Jackson | CA | 95642-9536 |  | 2013-09-04 | 2013-09-04 10:50 | 2013-09-04 11:16 | NORDYNE - JS3BD-036K | 114 | 4.9 | Yes | Yes | 22.8 | 19.1 | 3.7 | C30208CA0D2743EA8FD67272AB87FDFF |  | R22 | Non-TXV |  | 4.298% | 0.95702 | 8.26% | [5 empty] | Non-TXV | 4.298%
Tracy | CA | 95376-2335 |  | 2013-10-09 | 2013-10-09 14:16 | 2013-10-09 14:38 | TEMPSTAR - N4A336AKB200 | 83 | 6.6 | Yes | Yes | 25.9 | 19.9 | 6 | 652C376D99664F388B7CF32EA6FCC6F3 |  | R410A | TXV |  | 7.952% | 0.92048 | 15.28% | [5 empty] | TXV | 7.952%
Lathrop | CA | 95330-9592 |  | 2013-09-13 | 2013-09-13 10:43 | 2013-09-13 11:14 | OTHER - 24E0W060GA | 84 | 12.3 | Yes | Yes | 16.9 | 18.8 | -1.9 | 0EFEE101B33B4C79BD99788E92A64168 |  | R22 | Non-TXV |  | 14.64% | 0.85357 | 28.14% | [5 empty] | Non-TXV | 14.64%
Oroville | CA | 95966-6543 |  | 2013-08-17 | 2013-08-17 09:38 | 2013-08-17 10:17 | TRANE - 2TTB03042A1000AA | 109 | 6.9 | Yes | Yes | 21.9 | 20.4 | 1.5 | E01C4EECEB954BB9AA606FD93AC1BA48 |  | R22 | Non-TXV |  | 6.33% | 0.9367 | 12.17% | [5 empty] | Non-TXV | 6.33%
Merced | CA | 95340-4003 |  | 2013-08-19 | 2013-08-19 11:32 | 2013-08-19 11:33 | TRANE - TTX742B100A0 | 170 | 5.1 | Yes | Yes | 19 | 17.7 | 1.3 | 6750F27A35634E0E88EF92D58781C389 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95340-4003 |  | 2013-08-19 | 2013-08-19 11:58 | 2013-08-19 11:59 | PAYNE - 7777UNK | 114 | 3.7 | Yes | Yes | 15.1 | 17.6 | -2.5 | 66E8A7FC60FC4FDBA4A6B10379B4B749 |  | R22 | Non-TXV |  | 3.246% | 0.96754 | 6.237% | [5 empty] | Non-TXV | 3.246%
Manteca | CA | 95336-3431 |  | 2013-08-30 | 2013-08-30 14:29 | 2013-08-30 15:00 | GE - BGTA730B1B01 | 53 | 1.6 | Yes | Yes | 20.6 | 16 | 4.6 | 76C9CB13F7A84E6BB30338FC3B89B156 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Lincoln | CA | 95648-2327 |  | 2013-08-22 | 2013-08-22 09:56 | 2013-08-22 10:34 | OTHER - ERCS0421CAG | 152 | 6.3 | Yes | Yes | 18 | 21 | -3 | BB5FFD44F5FA4FC6A905DBB7D1735A7D |  | R22 | Non-TXV |  | 4.145% | 0.95855 | 7.965% | [5 empty] | Non-TXV | 4.145%
Mariposa | CA | 95338-0000 |  | 2013-09-25 | 2013-09-25 12:19 | 2013-09-25 12:21 | YORK - E1FH030S06A | 100 | 5.8 | Yes | Yes | 21.8 | 19.7 | 2.1 | DEBB96F2CA6F4C879727D60DD65C006C |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Mariposa | CA | 95338-0000 |  | 2013-09-25 | 2013-09-25 12:22 | 2013-09-25 12:23 | YORK - E1FH030S06A | 100 | 4.5 | Yes | Yes | 19.6 | 19.1 | 0.5 | BBB9E4A6A64D4225A7F0E7F784F37696 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Gustine | CA | 95322-1612 |  | 2013-09-05 | 2013-09-05 10:59 | 2013-09-05 11:00 | CARRIER - 7777UNK | 84 | 4.2 | Yes | Yes | 19.3 | 18.5 | 0.8 | C4118832412644729E12280B52060115 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95212-3456 |  | 2013-09-16 | 2013-09-16 09:44 | 2013-09-16 10:21 | BRYANT - 561CJ060-H | 131 | -12.3 | Yes | Yes | 19 | 18.3 | 0.7 | ED448207B93A4F8CBB1056BA88B02283 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.389% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.389%
Fresno | CA | 93703-5300 |  | 2013-08-27 | 2013-08-27 13:04 | 2013-08-27 13:05 | GOODMAN - PGB0240501A | 54 | 10.8 | Yes | Yes | 24 | 19.9 | 4.1 | 231DD423998D4720B0D0DE81957DFCC7 |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Manteca | CA | 95336-6902 |  | 2013-08-26 | 2013-08-26 11:31 | 2013-08-26 11:54 | DAY & NIGHT - 585EJW030050ABAF | 58 | 1.8 | Yes | Yes | 18.2 | 19.2 | -1 | AE55830C8B6F47FDB3E7BAFA2F1A54E5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Stockton | CA | 95204-2523 |  | 2013-08-21 | 2013-08-21 12:58 | 2013-08-21 13:14 | PAYNE - PY1PNB036060AAAA | 56 | 5.4 | Yes | Yes | 21.4 | 18.6 | 2.9 | 3E1BB301B8D0459491F57F3315B59068 |  | R22 | Non-TXV |  | 9.643% | 0.90357 | 18.53% | [5 empty] | Non-TXV | 9.643%
Lodi | CA | 95242-9565 |  | 2013-08-20 | 2013-08-20 16:15 | 2013-08-20 16:35 | COLEMAN - 0RCS0481BC | 129 | 16 | Yes | Yes | 21.8 | 20.4 | 1.4 | BF558A2405F74D73BFECB26C54B03D8C |  | R22 | Non-TXV |  | 12.4% | 0.87597 | 23.84% | [5 empty] | Non-TXV | 12.4%
Cameron Park | CA | 95682-9147 |  | 2013-09-04 | 2013-09-04 13:58 | 2013-09-04 13:58 | GOODMAN - CPKE48-1B | 128 | 0 | Yes | Yes | 17.8 | 19.9 | -2.1 | 4611B23B2FC34B99849EA4CD5B060F57 | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Penn Valley | CA | 95946-9544 |  | 2013-08-16 | 2013-08-16 08:47 | 2013-08-16 09:20 | RUUD - URMA-A042JK08E | 114 | 3.6 | Yes | Yes | 21 | 19.9 | 1.1 | AB7F61D813884A17AF437A2DB61046C2 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Manteca | CA | 95336-3479 |  | 2013-08-16 | 2013-08-16 13:44 | 2013-08-16 14:08 | BRYANT - 562CJ060-A | 160 | 10.3 | Yes | Yes | 20 | 19.7 | 0.3 | 83E638DF76164D57B2A46CD354BD1008 |  | R22 | Non-TXV |  | 6.438% | 0.93563 | 12.37% | [5 empty] | Non-TXV | 6.438%
Stockton | CA | 95209-2269 |  | 2013-08-20 | 2013-08-20 15:58 | 2013-08-20 15:58 | GOODMAN - GSX130361BA | 89 | 0 | Yes | Yes | 19 | 21.7 | -2.7 | B68470FCC6F545E59024613DE299B65F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-9783 |  | 2013-08-22 | 2013-08-22 12:13 | 2013-08-22 12:32 | PAYNE - 596ANX018000AAAA | 85 | 12 | Yes | Yes | 19 | 20.1 | -1.1 | E4354DD6199E407FBB1826623EEDD605 |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Lincoln | CA | 95648-9783 |  | 2013-08-22 | 2013-08-22 12:34 | 2013-08-22 12:58 | LENNOX - 12GCS060-100-4PB | 159 | 8.6 | Yes | Yes | 24 | 22.1 | 1.9 | E758DABD38EA468ABD7C8A1DC7D075BC |  | R22 | TXV |  | 5.409% | 0.94591 | 10.39% | [5 empty] | TXV | 5.409%
Merced | CA | 95340-9317 |  | 2013-08-20 | 2013-08-20 15:16 | 2013-08-20 15:18 | RUUD - 7777UNK | 100 | 4.4 | Yes | Yes | 15.9 | 18.1 | -2.2 | 8261FBBF4FA54F8EBFDA76229E275B1B |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Fresno | CA | 93702-2602 |  | 2013-08-17 | 2013-08-17 15:29 | 2013-08-17 15:48 | BDP - 588ANW042100ADAAG | 82 | 16.5 | Yes | Yes | 17.4 | 20.4 | -3 | FF6C92B36D214FF08378D84CB0F9BD95 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.12% | 0.79878 | 38.67% | [5 empty] | Non-TXV | 20.12%
Stockton | CA | 95207-6013 |  | 2013-08-19 | 2013-08-19 10:50 | 2013-08-19 11:07 | PAYNE - 567C048RCU | 66 | 7.8 | Yes | Yes | 22 | 18.9 | 3.1 | B40886B9FD3D47C2849D9E619EA7A4C8 |  | R22 | Non-TXV |  | 11.82% | 0.88182 | 22.71% | [5 empty] | Non-TXV | 11.82%
Lincoln | CA | 95648-9427 |  | 2013-08-29 | 2013-08-29 09:46 | 2013-08-29 10:06 | AMANA - RCE60C2C | 197 | 10.2 | Yes | Yes | 18.7 | 18.3 | 0.4 | E78411740FE04C2D8EE3B97D3B6C9299 |  | R22 | Non-TXV |  | 5.178% | 0.94822 | 9.95% | [5 empty] | Non-TXV | 5.178%
Chico | CA | 95973-0843 |  | 2013-08-21 | 2013-08-21 15:26 | 2013-08-21 21:43 | GIBSON - JS5BD-029K | 104 | 5.3 | Yes | Yes | 17.2 | 19.1 | -1.9 | BCFC3554BEA14DF2A074A4E8192BDA3E |  | R22 | Non-TXV |  | 5.096% | 0.94904 | 9.794% | [5 empty] | Non-TXV | 5.096%
Stockton | CA | 95207-7426 |  | 2013-08-19 | 2013-08-19 13:49 | 2013-08-19 14:12 | OTHER - AR6-36-1 | 108 | 7.3 | Yes | Yes | 14 | 15.4 | -1.4 | C7C6C2C77F1248CE89446E536FE1D54E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.759% | 0.93241 | 12.99% | [5 empty] | Non-TXV | 6.759%
Valley Springs | CA | 95252-9539 |  | 2013-09-05 | 2013-09-05 14:09 | 2013-09-05 14:28 | CARRIER - 561CJ036-C | 71 | 7.8 | Yes | Yes | 23.3 | 17.5 | 5.8 | 7710E62DBD304806B0834848A0BB2B69 |  | R22 | TXV |  | 10.99% | 0.89014 | 21.11% | [5 empty] | TXV | 10.99%
Fresno | CA | 93722-4676 |  | 2013-08-26 | 2013-08-26 14:53 | 2013-08-26 14:55 | CARRIER - 7777UNK | 110 | 3.3 | Yes | Yes | 19.6 | 19.9 | -0.3 | EFF4EC4546B44C82BCF10B8A6E591317 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Penn Valley | CA | 95946-9403 |  | 2013-08-15 | 2013-08-15 12:23 | 2013-08-15 12:42 | OTHER - BRHS0361BB | 100 | 4.6 | Yes | Yes | 19 | 21.7 | -2.7 | 47D1147AE2FC43EE912BB1A57B634166 |  | R22 | TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | TXV | 4.6%
Stockton | CA | 95203-2013 |  | 2013-09-04 | 2013-09-04 14:28 | 2013-09-04 15:03 | ARCOAIRE - PGC036K060B | 71 | 5.6 | Yes | Yes | 24.5 | 19.9 | 4.6 | 4AED44C6828E4DF9B6736BF2F520ABBD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.887% | 0.92113 | 15.16% | [5 empty] | Non-TXV | 7.887%
Lincoln | CA | 95648-2922 |  | 2013-08-17 | 2013-08-17 12:26 | 2013-08-17 12:49 | YORK - H2RC030S06A | 88 | 4 | Yes | Yes | 16.5 | 18.7 | -2.2 | 10BFFDC048EF43FB94C278DEFCC442DD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Madera | CA | 93637-4867 |  | 2013-08-26 | 2013-08-26 17:28 | 2013-08-26 20:02 | OTHER - 13ACC-042-230-01 | 115 | 3.5 | Yes | Yes | 17.6 | 20.4 | -2.8 | BE498198FD1A46BE8BF43BE21FEE27E7 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Tracy | CA | 95376-2169 |  | 2013-08-16 | 2013-08-16 14:45 | 2013-08-16 15:11 | AIRE-FLO - RHE42C2B | 145 | -8.4 | Yes | Yes | 16.6 | 19.3 | -2.7 | 346DA52ECC464216B69E3EBD5660EED3 |  | R22 | TXV |  | -5.793% | 1.0579 | 1.622% |  |  |  |  | TXV |  |  | -5.793%
Sanger | CA | 93657-8633 |  | 2013-08-23 | 2013-08-23 18:38 | 2013-08-23 19:10 | GOODMAN - CLT36-1C | 140 | 4.2 | Yes | Yes | 20.5 | 20.2 | 0.4 | 42F97866275645F9AF2ECB4CC43766D4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Sanger | CA | 93657-1927 |  | 2013-09-12 | 2013-09-12 15:30 | 2013-09-12 15:49 | LENNOX - 13ACD-042-230-02 | 111 | 8.7 | Yes | Yes | 17.6 | 20.2 | -2.6 | 3308F56791DF447888CED91EEB913D29 |  | R22 | Non-TXV |  | 7.838% | 0.92162 | 15.06% | [5 empty] | Non-TXV | 7.838%
Fresno | CA | 93704-4144 |  | 2013-10-21 | 2013-10-21 10:52 | 2013-10-21 12:18 | RUUD - N/A | 90 | 9 | Yes | Yes | 25.7 | 20.9 | 4.9 | BF8758557026460DA30551054A88C74F |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Sanger | CA | 93657-8838 |  | 2013-08-26 | 2013-08-26 15:35 | 2013-08-26 16:19 | LENNOX - 10ACB48-10P | 102 | 15.5 | Yes | Yes | 21.5 | 20.5 | 1 | 51A7B498D2F545DCB4AEBB9E1A9CB948 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.2% | 0.84804 | 29.2% | [5 empty] | Non-TXV | 15.2%
Ione | CA | 95640-9504 |  | 2013-08-23 | 2013-08-23 11:07 | 2013-08-23 11:29 | BRYANT - 582ANW036060AAAF | 56 | 4.3 | Yes | Yes | 16.8 | 19.1 | -2.3 | 73F3661E19164A22945B3F43FA0CEE2C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.679% | 0.92321 | 14.76% | [5 empty] | Non-TXV | 7.679%
Sonora | CA | 95370-9080 |  | 2013-10-03 | 2013-10-03 13:47 | 2013-10-03 14:10 | PAYNE - PA10JA042-C | 90 | -7.4 | Yes | Yes | 16.3 | 18.7 | -2.4 | 7443B23989214D839D5CAA0EAA5FBC2B |  | R22 | Non-TXV |  | -8.222% | 1.0822 | 2.303% |  |  |  |  | Non-TXV |  |  | -8.222%
Arnold | CA | 95223-0000 |  | 2013-09-04 | 2013-09-04 12:54 | 2013-09-04 13:35 | AMANA - ARCF42UOID | 88 | 2.7 | Yes | Yes | 21.4 | 18.8 | 2.6 | F586BA2D1F9F40A28F045F0FCBE5CF01 |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Lodi | CA | 95242-9564 |  | 2013-08-20 | 2013-08-20 16:56 | 2013-08-20 17:44 | UNITARY PRODUCTS GROUP - DRCS0481BD | 122 | 6.8 | Yes | Yes | 27.8 | 21 | 6.8 | B726077A2A03464B82B0C6015ED46E50 |  | R22 | Non-TXV |  | 5.574% | 0.94426 | 10.71% | [5 empty] | Non-TXV | 5.574%
Sonora | CA | 95370-9033 |  | 2013-09-05 | 2013-09-05 12:32 | 2013-09-05 12:55 | AMERICAN STANDARD - YCP036F1H0AD | 109 | 21.1 | Yes | Yes | 17.6 | 20.4 | -2.8 | 77B96CFA1C6444679C7AB682241C2B02 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.36% | 0.80642 | 37.2% | [5 empty] | Non-TXV | 19.36%
Chowchilla | CA | 93610-9315 |  | 2013-10-11 | 2013-10-11 14:24 | 2013-10-11 14:26 | YORK - D1NH048N09006C | 124 | 17.1 | Yes | Yes | 20 | 18.8 | 1.2 | AF1AA0B17EA4425C8094C3A03CA90169 |  | R22 | Non-TXV |  | 13.79% | 0.8621 | 26.5% | [5 empty] | Non-TXV | 13.79%
Chico | CA | 95973-9272 |  | 2013-08-20 | 2013-08-20 09:12 | 2013-08-20 09:12 | DAY & NIGHT - 591ANX0480000ABAA | 114 | 0 | Yes | Yes | 17.7 | 17.7 | 0 | 37F6CFA4538142B5A09BF3056B5F055B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-7844 |  | 2013-08-28 | 2013-08-28 14:17 | 2013-08-28 14:34 | RHEEM - UNK | 96 | 7.7 | Yes | Yes | 25.3 | 20.7 | 4.6 | 40F32CCDAF0245AB9E7401E56C4094FB |  | R22 | Non-TXV |  | 8.021% | 0.91979 | 15.41% | [5 empty] | Non-TXV | 8.021%
Stockton | CA | 95219-2042 |  | 2013-08-27 | 2013-08-27 10:13 | 2013-08-27 10:34 | GOODMAN - CLJ36-1A | 109 | 9.7 | Yes | Yes | 18.4 | 17.6 | 0.8 | 0E0FC8D978A1448AA19E5983ECD912D8 |  | R22 | Non-TXV |  | 8.899% | 0.91101 | 17.1% | [5 empty] | Non-TXV | 8.899%
Fresno | CA | 93722-3757 |  | 2013-09-13 | 2013-09-13 11:13 | 2013-09-13 12:28 | LENNOX - 12GCS036X-75-3PA | 110 | 4.6 | Yes | Yes | 18.5 | 20.9 | -2.4 | ECE19460DDAE471BA75AA109997EC083 |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
Placerville | CA | 95667-8539 |  | 2013-09-06 | 2013-09-06 15:44 | 2013-09-06 16:06 | GOODMAN - GPG154211541AB | 162 | 16.2 | Yes | Yes | 29.5 | 23.7 | 5.8 | 4790C09D15EE44108C54C5B60EC27238 |  | R410A | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Oroville | CA | 95965-4380 |  | 2013-08-28 | 2013-08-28 13:06 | 2013-08-28 19:44 | TRANE - 2TTB2042A1000AA | 97 | 5.3 | Yes | Yes | 19.1 | 21.4 | -2.3 | FCC80817D9D14D7BAC66D28B25FDAAE5 |  | R22 | Non-TXV |  | 5.464% | 0.94536 | 10.5% | [5 empty] | Non-TXV | 5.464%
Red Bluff | CA | 96080-4055 |  | 2013-09-05 | 2013-09-05 08:23 | 2013-09-05 09:48 | AMANA - PGD30C0702E | 74 | 7.6 | Yes | Yes | 24 | 21.8 | 2.3 | CEA9E99C37EC46E49EBD55238504A3AD |  | R22 | Non-TXV |  | 10.27% | 0.8973 | 19.74% | [5 empty] | Non-TXV | 10.27%
Stockton | CA | 95206-6374 |  | 2013-09-04 | 2013-09-04 09:36 | 2013-09-04 09:54 | CARRIER - 38CKC042340 | 80 | 8.6 | Yes | Yes | 16.3 | 19.2 | -2.9 | 00967E19272F404FA4BB77B30E90DBAF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.75% | 0.8925 | 20.66% | [5 empty] | Non-TXV | 10.75%
Chico | CA | 95926-4350 |  | 2013-09-26 | 2013-09-26 10:46 | 2013-09-26 11:02 | GOODMAN - GSC130301AE | 117 | 5.2 | Yes | Yes | 19 | 20.1 | -1.1 | 071B42012FE84124998A008E413D8FF6 |  | R22 | TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | TXV | 4.444%
Oakdale | CA | 95361-9678 |  | 2013-08-19 | 2013-08-19 13:30 | 2013-08-19 13:51 | YORK - H2RD030S06B | 93 | 6.7 | Yes | Yes | 21.6 | 19.9 | 1.7 | 1507DE4B35CF4AB18AA29B86791A48FB |  | R22 | TXV |  | 7.204% | 0.92796 | 13.85% | [5 empty] | TXV | 7.204%
Grass Valley | CA | 95949-9269 |  | 2013-08-30 | 2013-08-30 10:40 | 2013-08-30 10:40 | COLEMAN - DAYY-F048N080A | 152 | 0 | Yes | Yes | 24.3 | 20.2 | 4.1 | B8AFF34437604802A6E6792425CE13F8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5729 |  | 2013-08-28 | 2013-08-28 11:14 | 2013-08-28 11:34 | CARRIER - 38CKC048-301 | 104 | -9.8 | Yes | Yes | 18 | 19 | -1 | 977C932933D7495C9D4D565F5D4F85D4 |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Grass Valley | CA | 95945-8440 |  | 2013-08-22 | 2013-08-22 11:25 | 2013-08-22 11:25 | LENNOX - HS18-511-4P | 114 | 0 | Yes | Yes | 25 | 20.9 | 4.1 | 5DB294C2139C4E09908FC74760A74A8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-5922 |  | 2013-08-19 | 2013-08-19 13:14 | 2013-08-19 13:31 | BRYANT - 563CNO36A | 122 | 12.6 | Yes | Yes | 16.8 | 16.9 | -0.1 | CFCCEBFD9BCF46DBAE7E4B6DC6BBBBB1 |  | R22 | Non-TXV |  | 10.33% | 0.89672 | 19.85% | [5 empty] | Non-TXV | 10.33%
Madera | CA | 93636-8465 |  | 2013-08-23 | 2013-08-23 10:48 | 2013-08-25 15:36 | AIRE-FLO - GCGD48S1SA | 69 | 7 | Yes | Yes | 15.9 | 18.8 | -2.9 | 63932CE2E16B4865AD36C794C7A6CBD8 |  | R22 | Non-TXV |  | 10.14% | 0.89855 | 19.5% | [5 empty] | Non-TXV | 10.14%
Red Bluff | CA | 96080-4218 |  | 2013-08-27 | 2013-08-27 16:06 | 2013-08-27 18:14 | WEATHER KING - 13AJA36A01 | 108 | 5.1 | Yes | Yes | 22.4 | 23.4 | -1 | 5AC304765E944646B395CBEBC2C84094 |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Fresno | CA | 93722-1141 |  | 2013-08-22 | 2013-08-22 11:12 | 2013-08-22 11:15 | YORK - H1DB030S06B | 70 | 2.4 | Yes | Yes | 27.1 | 21.7 | 5.4 | 4D8C8F76B55944FCB76C11EE4D76894A |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Stockton | CA | 95206-6163 |  | 2013-08-19 | 2013-08-19 11:00 | 2013-08-19 11:21 | BRYANT - 38CKC048360 | 97 | 18.1 | Yes | Yes | 16.6 | 17.7 | -1.1 | 0716C416793C484485423A99B7360316 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.66% | 0.8134 | 35.86% | [5 empty] | Non-TXV | 18.66%
Manteca | CA | 95336-6432 |  | 2013-08-26 | 2013-08-26 12:11 | 2013-08-26 12:36 | DAY & NIGHT - 585EJW024050ABAE | 54 | 1.9 | Yes | Yes | 18.7 | 21.3 | -2.6 | 39E27D4722FE419CAEF444239FC192E6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Placerville | CA | 95667-4848 |  | 2013-08-29 | 2013-08-29 11:25 | 2013-08-29 11:25 | CARRIER - 38BRC036320 | 104 | 0 | Yes | Yes | 20.9 | 19.5 | 1.4 | 623DDE428BEE441C96475C95CE6D9CA6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-4205 |  | 2013-08-22 | 2013-08-22 15:42 | 2013-08-22 15:43 | CARRIER - 38TDA036300 | 184 | 24.8 | Yes | Yes | 21.9 | 19.6 | 2.3 | 0D0B3F2066EF4A028FA9A50CDD48BB02 |  | R22 | Non-TXV |  | 13.48% | 0.86522 | 25.9% | [5 empty] | Non-TXV | 13.48%
Madera | CA | 93636-8225 |  | 2013-08-26 | 2013-08-26 10:18 | 2013-08-26 13:40 | ARCOAIRE - PHAD36N1K6 | 132 | 4.3 | Yes | Yes | 17.2 | 19.4 | -2.2 | B7EE9E320C024F8F93DAA7EB84A93F34 |  | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.26% | [5 empty] | Non-TXV | 3.258%
Fresno | CA | 93722-3757 |  | 2013-08-17 | 2013-08-17 13:19 | 2013-08-17 14:00 | LENNOX - 12GCS036X-75-3PA | 110 | 4.4 | Yes | Yes | 18 | 19.7 | -1.7 | 96D87582F0B74E6DB02D55408D1861F1 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95207-3011 |  | 2013-08-20 | 2013-08-20 09:04 | 2013-08-20 09:23 | OTHER - 2SCU13LB136P-1 | 111 | -11.1 | Yes | Yes | 16.7 | 18 | -1.3 | AD02A5F0A46C4FD592DE37DECD624767 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Lathrop | CA | 95330-9387 |  | 2013-09-13 | 2013-09-13 14:54 | 2013-09-13 15:10 | BRYANT - 113RNA036-C | 90 | -5.3 | Yes | Yes | 22.8 | 19 | 3.8 | 764DB75683F64E56878C11340261578F |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Clovis | CA | 93612-4851 |  | 2013-08-16 | 2013-08-16 17:05 | 2013-08-16 18:19 | ICP - PGF036KO60E | 68 | 2.4 | Yes | Yes | 18.5 | 20.5 | -2 | 2F8E452FA24C420FA955D6FE52FCABE7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93705-2306 |  | 2013-08-26 | 2013-08-26 17:27 | 2013-08-26 17:30 | CARRIER - 7777UNK | 96 | 3.4 | Yes | Yes | 17.2 | 19.3 | -2.1 | 89818577184C43FCB9508BBB8D37B41B |  | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Merced | CA | 95340-2619 |  | 2013-08-19 | 2013-08-19 10:14 | 2013-08-19 10:17 | RHEEM - 13AJN36A01 | 90 | 2.9 | Yes | Yes | 19.6 | 17.4 | 2.2 | D1BA47A00BE3468BAD7286DF298B37D7 |  | R410A | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Livingston | CA | 95334-9728 |  | 2013-08-22 | 2013-08-22 15:39 | 2013-08-22 16:08 | GOODMAN - CKL30-1L | 74 | 2.3 | Yes | Yes | 19.1 | 18.3 | 0.8 | 70704EDB6A32428D8F080F4328B023EC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.108% | 0.96892 | 5.973% | [5 empty] | Non-TXV | 3.108%
Los Banos | CA | 93635-9204 |  | 2013-08-16 | 2013-08-16 12:44 | 2013-08-16 12:45 | OTHER - JS3BC-042KA | 102 | 3 | Yes | Yes | 19.5 | 18.8 | 0.7 | ED6612F2CEC64EE1BEB2E31D54DACFB6 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Clovis | CA | 93612-0442 |  | 2013-09-03 | 2013-09-03 09:11 | 2013-09-03 09:12 | CARRIER - 48KLA136300BE | 102 | 9.1 | Yes | Yes | 27 | 21.7 | 5.3 | 85A6200B1F8641E29A23AEA083F50547 |  | R22 | Non-TXV |  | 8.922% | 0.91078 | 17.15% | [5 empty] | Non-TXV | 8.922%
Sanger | CA | 93657-2272 |  | 2013-10-01 | 2013-10-01 15:13 | 2013-10-01 16:01 | YORK - 1NA030N05606C | 76 | 4.1 | Yes | Yes | 18 | 20.4 | -2.4 | 6618665F0B374CE090E9972E1A886875 |  | R22 | Non-TXV |  | 5.395% | 0.94605 | 10.37% | [5 empty] | Non-TXV | 5.395%
Fresno | CA | 93722-4379 |  | 2013-09-10 | 2013-09-10 10:39 | 2013-09-10 10:46 | YORK - DAYPF036N070A | 108 | 16 | Yes | Yes | 24.5 | 19 | 5.5 | 2AFAD63E16324229AA23BCBDCA0C6074 |  | R22 | Non-TXV |  | 14.81% | 0.85185 | 28.47% | [5 empty] | Non-TXV | 14.81%
Stockton | CA | 95215-9725 |  | 2013-08-29 | 2013-08-29 14:05 | 2013-08-29 14:05 | AMANA - VCA36B2E | 79 | 0 | Yes | Yes | 23.8 | 18.6 | 5.2 | 9536C0AFD1C24AA2A7555A4DE1D84405 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6059 |  | 2013-08-19 | 2013-08-19 12:41 | 2013-08-19 16:15 | GOODMAN - CKJ48-1A | 118 | 7 | Yes | Yes | 19.4 | 19.9 | -0.5 | 1E2F4863C7374887B6074C0FE358190D |  | R22 | Non-TXV |  | 5.932% | 0.94068 | 11.4% | [5 empty] | Non-TXV | 5.932%
Fresno | CA | 93722-7143 |  | 2013-08-29 | 2013-08-29 10:02 | 2013-08-29 10:08 | YORK - H1RA036S06A | 69 | 3.9 | Yes | Yes | 20 | 18.9 | 1.2 | A3B86B7055664E98892189C172C1EDD2 |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Chowchilla | CA | 93610-1810 |  | 2013-08-28 | 2013-08-28 20:21 | 2013-08-28 20:21 | AIRE-FLO - 591AN024000AAAAA | 85 | 0 | Yes | Yes | 20.3 | 19.8 | 0.5 | 6F1B1A4E7B8846E292C913E119408C49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-2539 |  | 2013-08-20 | 2013-08-20 08:12 | 2013-08-20 08:15 | OTHER - 13AJM30A01 | 86 | 2.6 | Yes | Yes | 15.7 | 16.6 | -0.9 | 70774B79BDA747AD974646961CCD45B1 |  | R410A | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Sanger | CA | 93657-2584 |  | 2013-08-23 | 2013-08-23 14:56 | 2013-08-23 14:56 | LENNOX - 10GCS036-75-3PA | 58 | 0 | Yes | Yes | 22.5 | 20.8 | 1.7 | 5DCD988C34A0413EACB6E5B838FA0DB4 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3106 |  | 2013-09-24 | 2013-09-24 11:35 | 2013-09-24 11:37 | BDP - 585A036080YACR | 60 | 9 | Yes | Yes | 18.5 | 18.8 | -0.3 | AB49981AFA324417A3EF6E203A6D8478 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Fresno | CA | 93704-5916 |  | 2013-08-22 | 2013-08-22 13:20 | 2013-08-22 13:21 | YORK - DCYZF042N080A | 78 | 4.6 | Yes | Yes | 24 | 18.8 | 5.2 | AE4F9AED28DB407EA8CF66CCE74C244D |  | R410A | Non-TXV |  | 5.897% | 0.94103 | 11.33% | [5 empty] | Non-TXV | 5.897%
Fresno | CA | 93705-5042 |  | 2013-08-30 | 2013-08-30 13:11 | 2013-08-30 13:13 | YORK - DAYP-F036N070A | 108 | 5.2 | Yes | Yes | 20.3 | 19.1 | 1.3 | 5DE65DDB20CA4EDEB6D90ABC125CF9A2 |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Fresno | CA | 93706-4262 |  | 2013-08-17 | 2013-08-17 16:32 | 2013-08-17 17:13 | GOODMAN - CPLJ30-1B | 123 | 7.5 | Yes | Yes | 21 | 18.8 | 2.2 | 9DA5B67430C44A6DB644383595EB5DEE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | Non-TXV | 6.098%
Chico | CA | 95973-0941 |  | 2013-08-20 | 2013-08-20 16:38 | 2013-08-20 19:56 | TEMPSTAR - EO72309746 | 213 | 7.8 | Yes | Yes | 19.7 | 19.3 | 0.4 | 1359F10B9FBC45AB87706BC046818972 |  | R410A | TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | TXV | 3.662%
Ripon | CA | 95366-2031 |  | 2013-10-10 | 2013-10-10 11:25 | 2013-10-10 12:09 | UNITARY PRODUCTS GROUP - H2DR3048S06B | 134 | 3.9 | Yes | Yes | 22.9 | 20.1 | 2.8 | 8980DFE9169241AC8CA10B57FE16F6E5 |  | R22 | Non-TXV |  | 2.91% | 0.9709 | 5.593% | [5 empty] | Non-TXV | 2.91%
Fresno | CA | 93722-9102 |  | 2013-08-22 | 2013-08-22 15:10 | 2013-08-22 15:14 | DAY & NIGHT - 585EJ036075 | 82 | 4 | Yes | Yes | 23.3 | 20.4 | 2.9 | 4CE2A232D00142B1809E2278DF55E92A |  | R22 | Non-TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | Non-TXV | 4.878%
Sanger | CA | 93657-2198 |  | 2013-09-17 | 2013-09-17 11:06 | 2013-09-17 11:51 | UNITARY PRODUCTS GROUP - H4RC060S06HG | 143 | 7.5 | Yes | Yes | 19 | 22 | -3 | 0C722F1DFE0F475BAFA212F7D2272425 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.245% | 0.94755 | 10.08% | [5 empty] | Non-TXV | 5.245%
Tracy | CA | 95376-4360 |  | 2013-08-22 | 2013-08-22 13:38 | 2013-08-22 13:57 | CARRIER - 38EH036300 | 117 | 13.9 | Yes | Yes | 23.9 | 18.7 | 5.2 | E47FB0A31456477282992CD0F46D18D8 |  | R22 | Non-TXV |  | 11.88% | 0.8812 | 22.83% | [5 empty] | Non-TXV | 11.88%
Stockton | CA | 95203-3211 |  | 2013-08-28 | 2013-08-28 11:31 | 2013-08-28 11:31 | BRYANT - 582ANW030040NAAD | 55 | 0 | Yes | Yes | 21.9 | 19.8 | 2.1 | 2A60CC047C424D9DA3ABA03BA339F137 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4538 |  | 2013-08-20 | 2013-08-20 12:05 | 2013-08-20 12:24 | YORK - H4DB024S06A | 58 | 22 | Yes | Yes | 19 | 19.5 | -0.5 | 0A32EA44FB0147EFBF866946C38B68D0 |  | R22 | Non-TXV |  | 37.93% | 0.62069 | 72.9% | [5 empty] | Non-TXV | 37.93%
Fresno | CA | 93726-1538 |  | 2013-08-20 | 2013-08-20 14:57 | 2013-08-20 15:21 | BRYANT - 583ANW036060NAFF | 82 | 8.3 | Yes | Yes | 21.2 | 19.8 | 1.4 | 166A171C8D1E40DC8135034B81AB1847 |  | R22 | Non-TXV |  | 10.12% | 0.89878 | 19.45% | [5 empty] | Non-TXV | 10.12%
Colfax | CA | 95713-0000 |  | 2013-09-05 | 2013-09-05 18:20 | 2013-09-05 18:37 | LENNOX - HS29-036-5P | 70 | 7.2 | Yes | Yes | 25.4 | 22.6 | 2.8 | BC5CAB39770D41B08843FA4850C6903F |  | R22 | TXV |  | 10.29% | 0.89714 | 19.77% | [5 empty] | TXV | 10.29%
Atwater | CA | 95301-4530 |  | 2013-08-27 | 2013-08-27 10:39 | 2013-08-27 11:08 | TRANE - 2TTR2048A1000AA | 120 | 3.7 | Yes | Yes | 20.1 | 18.7 | 1.4 | 5DAD60B7FBEB43C88E071AC78BFC69B2 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Stockton | CA | 95209-1419 |  | 2013-08-28 | 2013-08-28 13:23 | 2013-08-28 13:42 | PAYNE - 567C08RCU | 76 | 3.7 | Yes | Yes | 25.3 | 19.8 | 5.5 | D42C4239C4014C1482EBD57A14C97644 |  | R22 | Non-TXV |  | 4.868% | 0.95132 | 9.356% | [5 empty] | Non-TXV | 4.868%
Los Banos | CA | 93635-2817 |  | 2013-09-09 | 2013-09-09 10:58 | 2013-09-09 10:59 | GOODMAN - CK24-1B | 71 | 3.3 | Yes | Yes | 18.8 | 19.3 | -0.5 | A5127B9033D7446691DFAD58014184D9 |  | R22 | Non-TXV |  | 4.648% | 0.95352 | 8.932% | [5 empty] | Non-TXV | 4.648%
Tuolumne | CA | 95379-9628 |  | 2013-09-12 | 2013-09-12 13:01 | 2013-09-12 13:37 | DAY & NIGHT - 36DNR-108 | 84 | 2.9 | Yes | Yes | 24.8 | 22.1 | 2.7 | CF03C66D5C4648F0877A297105AD9950 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Placerville | CA | 95667-9641 |  | 2013-08-26 | 2013-08-26 11:11 | 2013-08-26 11:49 | RHEEM - PPND-042J 000 | 128 | 5.2 | Yes | Yes | 18 | 18.7 | -0.7 | ED53068E8F0E47EEB3B57065F7048E8D |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Sanger | CA | 93657-3615 |  | 2013-08-23 | 2013-08-23 17:35 | 2013-08-23 18:35 | ARCOAIRE - N/A | 90 | 16.5 | Yes | Yes | 18.5 | 19.2 | -0.7 | 36DDD8A984C64F9C88DCC19785DC10F1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.33% | 0.81667 | 35.23% | [5 empty] | Non-TXV | 18.33%
Chico | CA | 95926-4106 |  | 2013-10-02 | 2013-10-02 11:57 | 2013-10-02 12:27 | BRYANT - 582ANW024040NAAD | 70 | 5.4 | Yes | Yes | 18.1 | 20.4 | -2.3 | AEB1DEA3DF384924A1C92F84AEC9D412 |  | R22 | Non-TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | Non-TXV | 7.714%
Stockton | CA | 95205-5614 |  | 2013-08-26 | 2013-08-26 15:27 | 2013-08-26 15:44 | RUUD - UNK | 64 | 4.9 | Yes | Yes | 24.3 | 18.8 | 5.5 | 7B7219792E954CFD970D57244F65096A |  | R22 | Non-TXV |  | 7.656% | 0.92344 | 14.71% | [5 empty] | Non-TXV | 7.656%
Fresno | CA | 93725-1634 |  | 2013-09-06 | 2013-09-06 11:07 | 2013-09-06 12:08 | CARRIER - 48XP-036090301 | 66 | 7.8 | Yes | Yes | 18.5 | 20.4 | -1.9 | C94CFF557CB74AEF9A30CDFCCDD5DBF4 |  | R410A | TXV |  | 11.82% | 0.88182 | 22.71% | [5 empty] | TXV | 11.82%
Pollock Pines | CA | 95726-9426 |  | 2013-09-03 | 2013-09-03 11:54 | 2013-09-03 12:16 | AMANA - VRCF60U018 | 168.8 | 5.8 | Yes | Yes | 24.7 | 19.9 | 4.8 | 23A76B8A54274E18BEB02737D515DCF5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.436% | 0.96564 | 6.603% | [5 empty] | Non-TXV | 3.436%
Paso Robles | CA | 93446-5000 |  | 2013-08-16 | 2013-08-16 10:54 | 2013-08-16 11:11 | CARRIER - 38EN024310M | 56 | -4 | Yes | Yes | 21.9 | 16.6 | 5.3 | 192C4B5C4C7D4E038F95518E1CA820ED |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Wallace | CA | 95254-0000 |  | 2013-10-01 | 2013-10-01 13:15 | 2013-10-01 13:40 | LENNOX - GCS26X-048-125-1PA | 164 | 4.9 | Yes | Yes | 15.8 | 17.2 | -1.4 | 747133CFA9594F6C9DBFBCA77F80B5FF |  | R22 | Non-TXV |  | 2.988% | 0.97012 | 5.742% | [5 empty] | Non-TXV | 2.988%
Merced | CA | 95340-1557 |  | 2013-09-16 | 2013-09-16 17:02 | 2013-09-16 17:03 | AMERICAN STANDARD - YCC048F1M0BC | 100 | 5.8 | Yes | Yes | 26 | 21.7 | 4.3 | 757C69F6EC6A4864B1E2A65A6D2778FD |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Paso Robles | CA | 93446-3668 |  | 2013-09-06 | 2013-09-06 09:24 | 2013-09-06 09:41 | YORK - AC036X1021A | 63 | -4.4 | Yes | Yes | 23.6 | 18.7 | 4.9 | E02292D3B30D465BB9A09DC002DFDA22 |  | R22 | Non-TXV |  | -6.984% | 1.0698 | 1.956% |  |  |  |  | Non-TXV |  |  | -6.984%
Fresno | CA | 93722-1156 |  | 2013-08-23 | 2013-08-23 08:43 | 2013-08-23 08:44 | RHEEM - RAKA030JAZ | 66 | 5 | Yes | Yes | 20 | 18.1 | 1.9 | 75148BF07209426898670EC143991B4B |  | R22 | Non-TXV |  | 7.576% | 0.92424 | 14.56% | [5 empty] | Non-TXV | 7.576%
Fresno | CA | 93722-1156 |  | 2013-08-23 | 2013-08-23 09:05 | 2013-08-23 09:21 | RHEEM - RAKA030JAZ | 66 | 6.2 | Yes | Yes | 21 | 18.8 | 2.2 | 8CB624A15FCF454697574B17D72ED266 |  | R22 | Non-TXV |  | 9.394% | 0.90606 | 18.05% | [5 empty] | Non-TXV | 9.394%
Stockton | CA | 95212-3425 |  | 2013-08-23 | 2013-08-23 16:06 | 2013-08-23 16:21 | CARRIER - 38CKC048360 | 109 | 3.6 | Yes | Yes | 24.6 | 20.4 | 4.2 | 4F5A98C6C15549B0B388FFFD2F647F1D |  | R22 | Non-TXV |  | 3.303% | 0.96697 | 6.347% | [5 empty] | Non-TXV | 3.303%
Merced | CA | 95348-1552 |  | 2013-08-20 | 2013-08-20 14:18 | 2013-08-20 14:20 | RHEEM - 7777UNK | 60 | 2.4 | Yes | Yes | 27 | 21.5 | 5.6 | C4CDD28AC43A44909AE453B3543AF104 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Los Banos | CA | 93635-5440 |  | 2013-09-09 | 2013-09-09 13:29 | 2013-09-09 13:31 | OTHER - 561AJ036-C | 74 | 2.4 | Yes | Yes | 23.2 | 20.7 | 2.5 | 863BC9E31FCF4448B0BC40BA238785D4 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Fresno | CA | 93727-7220 |  | 2013-08-30 | 2013-08-30 11:09 | 2013-08-30 11:11 | LENNOX - GCS26X-036-75-2PA | 110 | 4.1 | Yes | Yes | 22.7 | 19.5 | 3.2 | E752993042C442799C4F68085A783411 |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.163% | [5 empty] | Non-TXV | 3.727%
Stockton | CA | 95206-6411 |  | 2013-08-28 | 2013-08-28 12:12 | 2013-08-28 12:58 | GOODMAN - CKL30-1F | 72 | 5.4 | Yes | Yes | 18.4 | 19.5 | -1.1 | F86D5B19E9E84636B8A6CF9EE90F4AD8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Fresno | CA | 93722-1156 |  | 2013-08-28 | 2013-08-28 12:24 | 2013-08-28 12:25 | RHEEM - RAKA037JAZ | 79 | 10.3 | Yes | Yes | 19.4 | 20.9 | -1.5 | A604D8E9347048B2B9BFE31E5885CDC3 |  | R22 | Non-TXV |  | 13.04% | 0.86962 | 25.06% | [5 empty] | Non-TXV | 13.04%
Red Bluff | CA | 96080-4140 |  | 2013-08-27 | 2013-08-27 15:27 | 2013-08-27 18:17 | BRYANT - 561CJ024-D | 54 | 5.8 | Yes | Yes | 23.9 | 21.5 | 2.4 | 888C53C65C6C4F0B82A174936E6ADC01 |  | R22 | TXV |  | 10.74% | 0.89259 | 20.64% | [5 empty] | TXV | 10.74%
Stockton | CA | 95204-5420 |  | 2013-09-09 | 2013-09-09 09:10 | 2013-09-09 09:32 | PAYNE - PA10JA042-C | 82 | -5.8 | Yes | Yes | 18.1 | 18.2 | -0.1 | 49BFED6776DA47CB8A52CD1317B7057D |  | R22 | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Chowchilla | CA | 93610-9386 |  | 2013-09-04 | 2013-09-04 08:02 | 2013-09-04 08:03 | CARRIER - 7777UNK | 104 | 3.1 | Yes | Yes | 19.6 | 19.5 | 0.1 | FAE155ED5202445A8538E0FB0C3B10FE |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Copperopolis | CA | 95228-9504 |  | 2013-08-22 | 2013-08-22 15:52 | 2013-08-22 16:10 | TRANE - UNK | 75 | 4.7 | Yes | Yes | 23.5 | 23.2 | 0.4 | 0A6B44BBD1D54528BD890662E20E9694 |  | R22 | Non-TXV |  | 6.267% | 0.93733 | 12.04% | [5 empty] | Non-TXV | 6.267%
Stockton | CA | 95203-2145 |  | 2013-09-13 | 2013-09-13 10:27 | 2013-09-13 10:59 | COLEMAN - BRCS048B | 104 | 10 | Yes | Yes | 24.5 | 18.7 | 5.8 | D8B0FF4478204E02BD473832AA7BC1C4 |  | R22 | Non-TXV |  | 9.615% | 0.90385 | 18.48% | [5 empty] | Non-TXV | 9.615%
Stockton | CA | 95205-2588 |  | 2013-08-26 | 2013-08-26 11:29 | 2013-08-26 11:46 | GUARDIAN - GCGD48S21S2B | 128 | 8.3 | Yes | Yes | 22.4 | 19.2 | 3.3 | 1C258B769427423EB29B45E771472649 |  | R22 | Non-TXV |  | 6.484% | 0.93516 | 12.46% | [5 empty] | Non-TXV | 6.484%
Chico | CA | 95926-3790 |  | 2013-08-16 | 2013-08-16 12:51 | 2013-08-16 19:33 | DAY & NIGHT - 585HW030040ABA | 68 | 13.8 | Yes | Yes | 26 | 22.8 | 3.2 | 7996A6908BE54729917EFA2B854DC340 |  | R22 | Non-TXV |  | 20.29% | 0.79706 | 39% | [5 empty] | Non-TXV | 20.29%
Magalia | CA | 95954-9680 |  | 2013-08-30 | 2013-08-30 10:20 | 2013-08-30 16:06 | CARRIER - 24ABS342A300 | 104 | 4.4 | Yes | Yes | 25.6 | 22.3 | 3.3 | 5A2A5CD9FF764F7CB305F2D288A5BE63 |  | R22 | TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | TXV | 4.231%
Red Bluff | CA | 96080-3909 |  | 2013-08-27 | 2013-08-27 15:31 | 2013-08-27 18:16 | AMERICAN STANDARD - YC1030F1MBE | 69 | 5.5 | Yes | Yes | 17.8 | 20.2 | -2.4 | 1EB7F537B8E54536A307C433B44027E8 |  | R22 | Non-TXV |  | 7.971% | 0.92029 | 15.32% | [5 empty] | Non-TXV | 7.971%
Stockton | CA | 95212-3050 |  | 2013-09-05 | 2013-09-05 13:29 | 2013-09-05 13:46 | GUARDIAN - GCGD60S4S3A | 86 | 5.8 | Yes | Yes | 20.5 | 20.2 | 0.4 | 0AA416F8D6684F21A2CF6D9415A1FF9D |  | R410A | TXV |  | 6.744% | 0.93256 | 12.96% | [5 empty] | TXV | 6.744%
Gerber | CA | 96035-9612 |  | 2013-08-19 | 2013-08-19 11:38 | 2013-08-19 13:29 | RUUD - UAPM-048JEZ | 203 | 7.5 | Yes | Yes | 18.9 | 19.3 | -0.4 | 21E0C4802E5F406D85CF57EB1B55FE2B |  | R410A | Non-TXV |  | 3.695% | 0.96305 | 7.1% | [5 empty] | Non-TXV | 3.695%
Fresno | CA | 93722-4751 |  | 2013-10-24 | 2013-10-24 16:48 | 2013-10-24 17:09 | HEIL - NRGF30DDB03 | 53 | 12.1 | Yes | Yes | 18.5 | 20.1 | -1.6 | 14B9410C27D34EB1AB34ED5C6D2ADE1A |  | R22 | Non-TXV |  | 22.83% | 0.7717 | 43.87% | [5 empty] | Non-TXV | 22.83%
Sonora | CA | 95370-8757 |  | 2013-09-05 | 2013-09-05 08:42 | 2013-09-05 08:42 | BRYANT - 563CN060-D | 200 | 0 | Yes | Yes | 26.6 | 21.5 | 5.1 | 97EEA8E9E0DF429D84D89D84CAE2E24A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sonora | CA | 95370-8757 |  | 2013-09-05 | 2013-09-05 09:20 | 2013-09-05 09:39 | BRYANT - 563CN060-D | 200 | 32.2 | Yes | Yes | 25.9 | 20.4 | 5.5 | 60FDAA36DAD942AB8E8F3D59ED4C47C0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.1% | 0.839 | 30.94% | [5 empty] | Non-TXV | 16.1%
Corning | CA | 96021-2114 |  | 2013-09-16 | 2013-09-16 14:14 | 2013-09-16 14:32 | BRYANT - 563CN048-F | 160 | 7.2 | Yes | Yes | 15.2 | 18.2 | -3 | C6DFF0624D1C4EC7A42A3B8116A66535 |  | R22 | TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | TXV | 4.5%
Tracy | CA | 95304-5861 |  | 2013-08-23 | 2013-08-23 09:19 | 2013-08-23 09:37 | YORK - H1RA048S06D | 117 | 3.7 | Yes | Yes | 22 | 19.3 | 2.7 | F6846B40ADB442299C1E59988A8B8427 |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Chico | CA | 95926-7109 |  | 2013-08-16 | 2013-08-16 15:20 | 2013-08-16 13:57 | WESTINGHOUSE - FS3BC-036KA | 82 | 10.9 | Yes | Yes | 21 | 21 | 0 | F717CD1B6113402C990ADFF79043D534 |  | R22 | Non-TXV |  | 13.29% | 0.86707 | 25.55% | [5 empty] | Non-TXV | 13.29%
Oroville | CA | 95966-3930 |  | 2013-09-17 | 2013-09-17 08:45 | 2013-09-17 09:14 | CARRIER - 38YRA048300 | 185 | 5.4 | Yes | Yes | 17 | 19.3 | -2.3 | D9BAF56B9D744177875B5771E25FB59D |  | R22 | Non-TXV |  | 2.919% | 0.97081 | 5.61% | [5 empty] | Non-TXV | 2.919%
Stockton | CA | 95204-1939 |  | 2013-08-22 | 2013-08-22 09:04 | 2013-08-22 09:32 | ICP - CA5536VKD2 | 82 | 9.3 | Yes | Yes | 22.8 | 18.7 | 4.1 | 8841EE6EC03B4DA39CEC6A23D19535C5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.34% | 0.88659 | 21.8% | [5 empty] | Non-TXV | 11.34%
Magalia | CA | 95954-9611 |  | 2013-10-23 | 2013-10-23 10:02 | 2013-10-23 10:23 | RHEEM - RPFB-036JAS | 94 | 9 | Yes | Yes | 18.5 | 20.2 | -1.7 | 5A36F74287EB4770B19A8316B2678B2A |  | R22 | Non-TXV |  | 9.574% | 0.90426 | 18.4% | [5 empty] | Non-TXV | 9.574%
Oroville | CA | 95965-3493 |  | 2013-08-17 | 2013-08-17 10:52 | 2013-08-17 12:06 | DAY & NIGHT - 561AJX024-E | 55 | 2.7 | Yes | Yes | 15.8 | 18.5 | -2.7 | 93D0397745D04BAAB21D2C21C4EEE04B |  | R22 | TXV |  | 4.909% | 0.95091 | 9.434% | [5 empty] | TXV | 4.909%
Winton | CA | 95388-9391 |  | 2013-10-18 | 2013-10-18 10:28 | 2013-10-18 10:30 | TRANE - YCC030F1MOBE | 68 | 2.5 | Yes | Yes | 20 | 18.8 | 1.2 | 55FB235DB37C43179E224A1B834CE4DB |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Fresno | CA | 93727-5137 |  | 2013-08-27 | 2013-08-27 14:31 | 2013-08-27 14:52 | LENNOX - PA10JA042-D | 90 | 2.9 | Yes | Yes | 20 | 17.6 | 2.5 | DA033ECE2EEF4C0EABB358C924D68A22 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Stockton | CA | 95209-2100 |  | 2013-08-27 | 2013-08-27 09:23 | 2013-08-27 09:46 | LUXAIRE - 60WE24G1 | 55 | 3.6 | Yes | Yes | 18.2 | 18 | 0.2 | 434CD7AD8B5C4DCEA3E40C2B9BBE528C |  | R22 | Non-TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | Non-TXV | 6.545%
Auburn | CA | 95603-4819 |  | 2013-09-19 | 2013-09-19 13:07 | 2013-09-19 13:07 | OTHER - 561CJ024-C | 70 | 0 | Yes | Yes | 25 | 20.1 | 4.9 | 50F4264F78CA4887AF4477B9EAFE9AD4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-9179 |  | 2013-08-20 | 2013-08-20 16:16 | 2013-08-20 16:18 | RUUD - 7777UNK | 100 | 3.1 | Yes | Yes | 20.5 | 18.5 | 2 | C5049359686844279DCFB599F3141BD8 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Merced | CA | 95340-1326 |  | 2013-08-21 | 2013-08-21 15:33 | 2013-08-21 15:34 | GOODMAN - CK241B | 71 | 7.9 | Yes | Yes | 19.7 | 19.7 | 0 | EB975043262E4EB08F0614BF18E8C408 |  | R22 | Non-TXV |  | 11.13% | 0.88873 | 21.38% | [5 empty] | Non-TXV | 11.13%
Stockton | CA | 95205-2727 |  | 2013-08-26 | 2013-08-26 12:27 | 2013-08-26 12:44 | YORK - H2RA030S06D | 62 | 3.4 | Yes | Yes | 18 | 17.2 | 0.8 | 5523EE8CDB1C41149BF618E024AC99FA |  | R22 | Non-TXV |  | 5.484% | 0.94516 | 10.54% | [5 empty] | Non-TXV | 5.484%
San Andreas | CA | 95249-9683 |  | 2013-09-05 | 2013-09-05 10:59 | 2013-09-05 11:19 | CARRIER - 38YCH036-301 | 99 | 4.5 | Yes | Yes | 20.3 | 19.3 | 1 | E93D0990E4064FBE89FB2FA3F0E0581D |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93726-5902 |  | 2013-09-09 | 2013-09-09 12:47 | 2013-09-09 12:47 | YORK - D1NQ048N09006NXA | 70 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 1E8C7C7AAE244B35843E55A98048A8BE |  | R410A | TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-2801 |  | 2013-09-04 | 2013-09-04 10:27 | 2013-09-04 10:53 | GOODMAN - GSC130361FA | 83 | 3 | Yes | Yes | 19 | 16.5 | 2.5 | 083235073AB94AE0AC8EB8067E0F12FA |  | R22 | TXV |  | 3.614% | 0.96386 | 6.946% | [5 empty] | TXV | 3.614%
Winton | CA | 95388-9392 |  | 2013-08-27 | 2013-08-27 12:06 | 2013-08-27 12:27 | GOODMAN - CKL30-1F | 72 | 2.6 | Yes | Yes | 19.2 | 20.2 | -1 | 94B5154AFA244423A42013058668088E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Fresno | CA | 93728-1639 |  | 2013-08-26 | 2013-08-26 13:10 | 2013-08-26 13:13 | TRANE - YCC042F1M0AA | 104 | 5.1 | Yes | Yes | 23 | 20 | 3.1 | CE2E6BF959634D76B7869C2FD2A87F3C |  | R22 | Non-TXV |  | 4.904% | 0.95096 | 9.424% | [5 empty] | Non-TXV | 4.904%
Nevada City | CA | 95959-9451 |  | 2013-09-10 | 2013-09-10 15:32 | 2013-09-10 15:32 | CARRIER - 38BRC042300 | 134 | 0 | Yes | Yes | 20.3 | 19.8 | 0.5 | 7BEB71D6AB784152A03C8C59CB04FD6E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-4912 |  | 2013-08-23 | 2013-08-23 14:21 | 2013-08-23 14:24 | GOODMAN - CKL36-1D | 72 | 3.7 | Yes | Yes | 26 | 20.4 | 5.6 | 699B42FE914843E79E311C64A8925EA6 |  | R22 | Non-TXV |  | 5.139% | 0.94861 | 9.876% | [5 empty] | Non-TXV | 5.139%
Chico | CA | 95928-4138 |  | 2013-08-28 | 2013-08-28 11:37 | 2013-08-28 11:55 | AMANA - PGD36C0702E | 110 | -7.8 | Yes | Yes | 25 | 19 | 6 | FA0C010A30B849F982130B2573E9D3DA |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Red Bluff | CA | 96080-2642 |  | 2013-08-26 | 2013-08-26 17:15 | 2013-08-26 16:32 | YORK - D1NA030N05606C | 76 | 8.8 | Yes | Yes | 17.7 | 20.7 | -3 | 1B491AE6BDED4FF3B212BEC020925066 |  | R22 | Non-TXV |  | 11.58% | 0.88421 | 22.25% | [5 empty] | Non-TXV | 11.58%
Stockton | CA | 95206-4885 |  | 2013-08-22 | 2013-08-22 16:08 | 2013-08-22 16:33 | CARRIER - 38TH030310 | 64 | 7.8 | Yes | Yes | 26.4 | 20.4 | 6 | 7ABCED4D51CA47208EB2CB8EE8B93CE4 |  | R22 | Non-TXV |  | 12.19% | 0.87813 | 23.42% | [5 empty] | Non-TXV | 12.19%
Fresno | CA | 93706-4262 |  | 2013-10-09 | 2013-10-09 12:47 | 2013-10-09 14:06 | GOODMAN - CPLJ30-1B | 123 | 16.6 | Yes | Yes | 17.9 | 20.8 | -2.9 | 502832959847432D84990D277325680B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.5% | 0.86504 | 25.94% | [5 empty] | Non-TXV | 13.5%
Stockton | CA | 95210-5206 |  | 2013-08-16 | 2013-08-16 13:58 | 2013-08-16 14:14 | DAY & NIGHT - UNK | 96 | 9.7 | Yes | Yes | 20.8 | 20.7 | 0.1 | A5568C6AC24E4BC491AC0CE181F4FDE4 |  | R22 | Non-TXV |  | 10.1% | 0.89896 | 19.42% | [5 empty] | Non-TXV | 10.1%
Madera | CA | 93638-0446 |  | 2013-09-05 | 2013-09-05 09:07 | 2013-09-05 09:08 | BDP - 589ANW048080ADBG | 88 | 7.2 | Yes | Yes | 23.9 | 19.3 | 4.6 | 8EEFE72C27354C548AB2048798B5BF00 |  | R22 | Non-TXV |  | 8.182% | 0.91818 | 15.72% | [5 empty] | Non-TXV | 8.182%
Stockton | CA | 95206-6365 |  | 2013-09-11 | 2013-09-11 11:50 | 2013-09-11 12:10 | CARRIER - 38CKC060370 | 131 | 12.4 | Yes | Yes | 18.5 | 20.4 | -1.9 | 417CC3D7690646A99E4D2653B8E78D7F |  | R22 | Non-TXV |  | 9.466% | 0.90534 | 18.19% | [5 empty] | Non-TXV | 9.466%
Stockton | CA | 95210-4421 |  | 2013-08-28 | 2013-08-28 11:30 | 2013-08-28 11:30 | PAYNE - 567GJ030-B | 80 | 0 | Yes | Yes | 24.5 | 19.5 | 5.1 | 1E25106A50224B00968B6C83593FA269 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-3105 |  | 2013-09-04 | 2013-09-04 12:01 | 2013-09-04 12:23 | LENNOX - HS26-48-3P | 114 | 20.9 | Yes | Yes | 18.8 | 19.2 | -0.4 | 3AB1482F7201483EBA50CB1BAD03CDA6 |  | R22 | Non-TXV |  | 18.33% | 0.81667 | 35.23% | [5 empty] | Non-TXV | 18.33%
Caruthers | CA | 93609-9635 |  | 2013-09-05 | 2013-09-05 10:49 | 2013-09-05 11:42 | BDP - 585B042100YACR | 89 | 15.1 | Yes | Yes | 17.5 | 20.4 | -2.9 | 07B977D988A046F9ADAE8A1703D03D38 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.97% | 0.83034 | 32.61% | [5 empty] | Non-TXV | 16.97%
Placerville | CA | 95667-9170 |  | 2013-09-03 | 2013-09-03 17:25 | 2013-09-03 17:25 | CARRIER - 50MQ037300 | 115 | 0 | Yes | Yes | 20.1 | 22.1 | -2 | D604CECFE3BF4F0B8290D766BE03EB30 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-8257 |  | 2013-08-27 | 2013-08-27 17:20 | 2013-08-27 17:38 | GOODMAN - GPG1324045M41AC | 80 | 2.5 | Yes | Yes | 17.8 | 18.5 | -0.7 | 9DDC98A8675247129D0DBB07C1568715 |  | R410A | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Tranquillity | CA | 93668-0000 |  | 2013-09-12 | 2013-09-12 10:34 | 2013-09-12 10:36 | GOODMAN - GPG13420701A | 107 | 7.3 | Yes | Yes | 23.8 | 18.3 | 5.5 | D394BCC92BF34E5FB32D1A8D91460FB5 |  | R22 | Non-TXV |  | 6.822% | 0.93178 | 13.11% | [5 empty] | Non-TXV | 6.822%
Rail Road Flat | CA | 95248-0000 |  | 2013-09-30 | 2013-09-30 11:41 | 2013-09-30 12:11 | YORK - UNK | 85 | 2.7 | Yes | Yes | 21.1 | 17.2 | 3.9 | 29BB986B30784555B1A1F40C07A18F81 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Stockton | CA | 95205-7792 |  | 2013-09-10 | 2013-09-10 10:58 | 2013-09-10 11:17 | CARRIER - 38TH024300 | 56 | 2.7 | Yes | Yes | 19.3 | 19.1 | 0.2 | B03D5359FD454B2380DF07975F5780B2 |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Stockton | CA | 95212-3114 |  | 2013-09-05 | 2013-09-05 12:45 | 2013-09-05 13:02 | YORK - H2RD048S06B | 134 | 9.8 | Yes | Yes | 22.6 | 21.7 | 1 | 0B4A8272EB0844F0AF67DC73058F93C8 |  | R22 | TXV |  | 7.313% | 0.92687 | 14.05% | [5 empty] | TXV | 7.313%
Stockton | CA | 95206-6305 |  | 2013-08-22 | 2013-08-22 14:13 | 2013-08-22 14:30 | GOODMAN - CKJ30-1O | 85 | 3 | Yes | Yes | 24.8 | 19.8 | 5.1 | 5F317423D430488C88A5479AFD3A9B5F |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Stockton | CA | 95204-3443 |  | 2013-08-22 | 2013-08-22 10:13 | 2013-08-22 12:39 | ICP - PGF330060K01A2 | 89 | 5.6 | Yes | Yes | 20 | 17.2 | 2.8 | AE0B1C4B86DE4E808F71D9097434F9F6 |  | R22 | Non-TXV |  | 6.292% | 0.93708 | 12.09% | [5 empty] | Non-TXV | 6.292%
Stockton | CA | 95209-1420 |  | 2013-08-27 | 2013-08-27 08:37 | 2013-08-27 09:00 | BDP - 585A06080YACR | 59 | 6.2 | Yes | Yes | 25.7 | 19.8 | 5.9 | 4AFC4C7DEB8C408CACF9931CBA16DF56 |  | R22 | Non-TXV |  | 10.51% | 0.89492 | 20.19% | [5 empty] | Non-TXV | 10.51%
Fresno | CA | 93706-0000 |  | 2013-10-10 | 2013-10-10 14:23 | 2013-10-10 14:52 | OTHER - 55AW24106 | 69 | 4 | Yes | Yes | 17.2 | 20.2 | -3 | EF2DFDF474AA4937AE24122B7589D167 |  | R22 | Non-TXV |  | 5.797% | 0.94203 | 11.14% | [5 empty] | Non-TXV | 5.797%
Tracy | CA | 95376-4302 |  | 2013-08-23 | 2013-08-23 10:44 | 2013-08-23 11:09 | ICP - NAC224AKA1 | 79 | 7.5 | Yes | Yes | 15.9 | 18 | -2.1 | D3F51DD90EF646E58CBF53465E56207B |  | R22 | Non-TXV |  | 9.494% | 0.90506 | 18.24% | [5 empty] | Non-TXV | 9.494%
Coalinga | CA | 93210-2203 |  | 2013-10-11 | 2013-10-11 12:15 | 2013-10-11 12:54 | UNITARY PRODUCTS GROUP - TCGD36S21S1A | 65 | 7 | Yes | Yes | 25.3 | 20.9 | 4.4 | 8640C0A831B9415B81A3A861AA2A1E2B |  | R22 | Non-TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | Non-TXV | 10.77%
Oroville | CA | 95966-6606 |  | 2013-09-17 | 2013-09-17 10:21 | 2013-09-17 11:00 | LENNOX - 13HPD-036-230-01 | 138 | 5.4 | Yes | Yes | 19 | 18.8 | 0.2 | DD86526D01C64ABEA905C35BF282235B |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Tracy | CA | 95376-2793 |  | 2013-08-22 | 2013-08-22 09:43 | 2013-08-22 10:04 | - H2RD042S6B | 141 | 7.5 | Yes | Yes | 21.4 | 18.8 | 2.6 | 5F0195A8D58F45529B4464253B980B18 |  | R22 | TXV |  | 5.319% | 0.94681 | 10.22% | [5 empty] | TXV | 5.319%
Atwater | CA | 95301-4528 |  | 2013-09-03 | 2013-09-03 10:47 | 2013-09-03 11:14 | COLEMAN - FRCS041CEG2 | 224 | 6.6 | Yes | Yes | 23.2 | 21 | 2.2 | 3CE98F42F50F453899D550A901189425 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.662% | [5 empty] | Non-TXV | 2.946%
Fresno | CA | 93722-4732 |  | 2013-08-22 | 2013-08-22 13:58 | 2013-08-22 13:59 | CARRIER - 585HJ030040 | 68 | 3 | Yes | Yes | 17.2 | 18.9 | -1.7 | C5C5CCCE99CC4A40A9A34AFB8B91F2C3 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Stockton | CA | 95206-6374 |  | 2013-08-26 | 2013-08-26 11:19 | 2013-08-26 11:37 | CARRIER - 38CKC060370 | 131 | 8.5 | Yes | Yes | 16.3 | 19.2 | -2.9 | 953A0DB39049420E94A635E509787CD4 |  | R22 | Non-TXV |  | 6.489% | 0.93511 | 12.47% | [5 empty] | Non-TXV | 6.489%
Red Bluff | CA | 96080-3756 |  | 2013-08-27 | 2013-08-27 10:31 | 2013-08-27 11:18 | GOODMAN - PGB030050-1A | 56 | 5.4 | Yes | Yes | 20.6 | 19.3 | 1.3 | 43F7622B2BD0460CAE08657A1F0FF599 |  | R22 | Non-TXV |  | 9.643% | 0.90357 | 18.53% | [5 empty] | Non-TXV | 9.643%
Tracy | CA | 95376-3218 |  | 2013-08-22 | 2013-08-22 11:55 | 2013-08-22 12:14 | CARRIER - 48ESN036060301 | 146 | 8.6 | Yes | Yes | 22.6 | 19.3 | 3.3 | 63C6C9C80AF84D8993576DB50097C2A8 |  | R410A | TXV |  | 5.89% | 0.9411 | 11.32% | [5 empty] | TXV | 5.89%
Magalia | CA | 95954-9415 |  | 2013-08-29 | 2013-08-29 13:22 | 2013-08-29 13:22 | - GSC-140421AE | 64 | 0 | Yes | Yes | 18.1 | 21 | -2.9 | DB317F040A304D38A0F694BD028C0DF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1429 |  | 2013-08-27 | 2013-08-27 10:05 | 2013-08-27 10:06 | BDP - 585HJW048080ABAF | 118 | 10.7 | Yes | Yes | 19.9 | 19.2 | 0.7 | 42062F75FFD44DC6B9069CAED860806E |  | R22 | Non-TXV |  | 9.068% | 0.90932 | 17.43% | [5 empty] | Non-TXV | 9.068%
Fresno | CA | 93722-3604 |  | 2013-10-14 | 2013-10-14 13:46 | 2013-10-14 14:25 | CARRIER - N/A | 90 | 20.8 | Yes | Yes | 22.3 | 21.4 | 0.9 | 54FC1D21DA65404787DDED9C8D0DD48A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 23.11% | 0.76889 | 44.41% | [5 empty] | Non-TXV | 23.11%
Fresno | CA | 93722-4051 |  | 2013-08-29 | 2013-08-29 08:59 | 2013-08-29 09:01 | COLEMAN - DAYAF024N045C | 54 | 3.5 | Yes | Yes | 18.4 | 14.4 | 4 | 74647E4F06984705A7882CE022D9045E |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Coalinga | CA | 93210-2231 |  | 2013-09-11 | 2013-09-11 10:44 | 2013-09-11 16:02 | DAY & NIGHT - N/A | 90 | 12.8 | Yes | Yes | 17 | 19.9 | -2.9 | 61B545BFC61F4AB8886054F74B5E5208 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.22% | 0.85778 | 27.33% | [5 empty] | Non-TXV | 14.22%
Fresno | CA | 93727-6516 |  | 2013-09-16 | 2013-09-16 12:28 | 2013-09-16 12:38 | GOODMAN - PGB036075-1 | 60 | 2.8 | Yes | Yes | 16.5 | 19.2 | -2.7 | CADEBC0A060C414A8FAF8C003536D1D8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Fresno | CA | 93727-6516 |  | 2013-09-16 | 2013-09-16 12:41 | 2013-09-16 13:00 | YORK - DCYZ-F036N070A | 64 | 3.7 | Yes | Yes | 17.3 | 19.5 | -2.2 | E7EFD38E2ABE4EADAEF9CF1946E6F56A |  | R410A | TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | TXV | 5.781%
Tracy | CA | 95376-2793 |  | 2013-08-22 | 2013-08-22 10:27 | 2013-08-22 10:46 | YORK - H2RD042S06B | 141 | 10.3 | Yes | Yes | 20.8 | 17.8 | 3 | 212563AD0FD54174819ACDB2D9E5B270 |  | R22 | TXV |  | 7.305% | 0.92695 | 14.04% | [5 empty] | TXV | 7.305%
Stockton | CA | 95212-3465 |  | 2013-08-23 | 2013-08-23 16:51 | 2013-08-23 17:53 | CARRIER - 38CKC030340 | 66 | 9.3 | Yes | Yes | 16.1 | 18.5 | -2.4 | 9EFC72E5AA3B4BC2AC8F355810C9FB2A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.09% | 0.85909 | 27.08% | [5 empty] | Non-TXV | 14.09%
Magalia | CA | 95954-9460 |  | 2013-08-29 | 2013-08-29 14:56 | 2013-08-29 14:56 | DAY & NIGHT - NAB4BAKB200 | 112 | 0 | Yes | Yes | 20.5 | 20.1 | 0.4 | F760980DFFA8437A84E7264F4C251A45 |  | R410A | TXV |  | 0% | 1 | 0%
Chico | CA | 95973-9190 |  | 2013-08-20 | 2013-08-20 11:02 | 2013-08-20 20:21 | GOODMAN - PGB030050-1 | 56 | 2.6 | Yes | Yes | 15.9 | 18.7 | -2.8 | C21A7A75B9DB45F49915B8305E608C00 |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Stockton | CA | 95206-6161 |  | 2013-09-11 | 2013-09-11 13:04 | 2013-09-11 18:18 | CARRIER - 38CKC030340 | 68 | -6.7 | Yes | Yes | 18.8 | 18.3 | 0.5 | 96115EE0E33F4EB8872747EEA563C99D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.853% | 1.0985 | 2.759% |  |  |  |  | Non-TXV |  |  | -9.853%
Arnold | CA | 95223-0000 |  | 2013-09-12 | 2013-09-12 11:43 | 2013-09-12 12:19 | TRANE - TTX736AT00A | 128 | -9 | Yes | Yes | 22.1 | 21.5 | 0.6 | 7048A8BB719642B8B71A7A7E4208E2E9 |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Placerville | CA | 95667-3315 |  | 2013-09-06 | 2013-09-06 13:20 | 2013-09-06 13:20 | CARRIER - 48SX-042080321AA | 91 | 0 | Yes | Yes | 24.5 | 20 | 4.5 | A45F4EC8159A47CFAD654430EFB6F42F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-5001 |  | 2013-08-28 | 2013-08-28 16:06 | 2013-08-28 16:06 | TRANE - YCC036F1M0BC | 85 | 0 | Yes | Yes | 22.9 | 21.4 | 1.5 | DF0E58BB647F48748BEB196EF522E667 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1043 |  | 2013-09-18 | 2013-09-18 12:14 | 2013-09-18 12:47 | YORK - D2NP024N05606A | 100 | 5.6 | Yes | Yes | 22 | 20.4 | 1.6 | 1F75D980DEAD4631987BC03459EF0461 |  | R22 | Non-TXV |  | 5.6% | 0.944 | 10.76% | [5 empty] | Non-TXV | 5.6%
Red Bluff | CA | 96080-3756 |  | 2013-08-27 | 2013-08-27 11:21 | 2013-08-27 11:39 | DAY & NIGHT - J88ANW0240ADAD | 42 | 6.8 | Yes | Yes | 20.5 | 22.9 | -2.4 | B1C512EF67B9437B863DC56F0808C938 |  | R22 | Non-TXV |  | 16.19% | 0.8381 | 31.11% | [5 empty] | Non-TXV | 16.19%
Manteca | CA | 95336-4003 |  | 2013-08-26 | 2013-08-26 13:19 | 2013-08-26 13:41 | GE - BGTA842R1D | 111 | 3.4 | Yes | Yes | 22.3 | 19.2 | 3.1 | EAE248ECE0234A9BA3E449CFC030A9D2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.063% | 0.96937 | 5.887% | [5 empty] | Non-TXV | 3.063%
Manteca | CA | 95336-4003 |  | 2013-08-26 | 2013-08-26 13:36 | 2013-08-26 14:12 | ICP - NAC018AKB1 | 73 | 2.3 | Yes | Yes | 21.9 | 21.6 | 0.3 | D72C38B1E0D84515971B9CE239034AE2 |  | R22 | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Rocklin | CA | 95677-2952 |  | 2013-09-10 | 2013-09-10 21:32 | 2013-09-10 21:32 | BRYANT - 577DNNA6009GNATP | 160 | 0 | Yes | Yes | 19.3 | 21 | -1.7 | BF39DBBFF81F4B9FBA44DFF1BDD90DCE |  | R410A | TXV |  | 0% | 1 | 0%
Chico | CA | 95926-3067 |  | 2013-08-22 | 2013-08-22 15:30 | 2013-08-22 16:44 | PAYNE - | 72 | 3.6 | Yes | Yes | 24.4 | 19.3 | 5.1 | 4EF914043668468781DA7DFAC2ADC8D9 |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Winton | CA | 95388-9336 |  | 2013-10-18 | 2013-10-18 11:35 | 2013-10-18 11:36 | TRANE - TTB724A100A1 | 54 | 2.8 | Yes | Yes | 17.9 | 18.8 | -0.9 | A2F2DEFF2E244099836CA530051297B2 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Red Bluff | CA | 96080-3459 |  | 2013-09-18 | 2013-09-18 16:17 | 2013-09-18 17:00 | BRYANT - 4399E04678 | 48 | 5.4 | Yes | Yes | 17.5 | 20.4 | -2.9 | 2542E4E6AA0F455CB98450B73924DD39 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Tracy | CA | 95377-7951 |  | 2013-09-11 | 2013-09-11 14:41 | 2013-09-11 14:41 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 24.7 | 18.8 | 5.9 | 9B37264C03FC45659CA1F63A63719C6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-7951 |  | 2013-09-11 | 2013-09-11 14:50 | 2013-09-11 15:12 | CARRIER - 38CKC03640 | 70 | 3.5 | Yes | Yes | 25 | 19 | 6 | F5712A1F6DB84CDBBDF6552021667331 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93727-5110 |  | 2013-09-04 | 2013-09-04 13:59 | 2013-09-04 14:01 | ICP - GPM60K100F | 133 | 4 | Yes | Yes | 17.5 | 19.3 | -1.8 | ED24FE50B7F148309DB44A53528BA004 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Fresno | CA | 93727-7925 |  | 2013-08-27 | 2013-08-27 16:57 | 2013-08-27 16:57 | GOODMAN - GPG1330045M41CA | 78 | 0 | Yes | Yes | 26 | 20.4 | 5.7 | 563609270F004FF88F12EA1E450ED61A |  | R410A | TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-9060 |  | 2013-08-26 | 2013-08-26 13:39 | 2013-08-26 13:57 | LENNOX - HP27-036-2P | 192 | 7 | Yes | Yes | 24 | 21.3 | 2.7 | 0D232A7E96114AC9BDD35459682357A7 |  | R22 | TXV |  | 3.646% | 0.96354 | 7.006% | [5 empty] | TXV | 3.646%
Stockton | CA | 95205-2728 |  | 2013-08-26 | 2013-08-26 13:08 | 2013-08-26 13:26 | GOODMAN - GSC130361GA | 77 | 6.3 | Yes | Yes | 24.1 | 18.9 | 5.3 | D7EA661CC2C842D8865E671C9E91DBEE |  | R22 | Non-TXV |  | 8.182% | 0.91818 | 15.72% | [5 empty] | Non-TXV | 8.182%
Tracy | CA | 95377-7094 |  | 2013-08-29 | 2013-08-29 13:57 | 2013-08-29 14:20 | BRYANT - 561CJ042-A | 80 | 3.5 | Yes | Yes | 21.5 | 21.9 | -0.4 | 02AE5CF292334530B3092D4009774A37 |  | R22 | TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | TXV | 4.375%
Tracy | CA | 95377-7094 |  | 2013-08-29 | 2013-08-29 13:52 | 2013-08-29 14:19 | BRYANT - 561CJ036-E | 73 | 6.1 | Yes | Yes | 23.4 | 22.2 | 1.3 | DA076D1ED311448897CEA1B8EDAB4C65 |  | R22 | TXV |  | 8.356% | 0.91644 | 16.06% | [5 empty] | TXV | 8.356%
Stockton | CA | 95209-1614 |  | 2013-09-13 | 2013-09-13 16:08 | 2013-09-13 16:26 | YORK - TCGD36S21S2HA | 85 | 4.9 | Yes | Yes | 21.3 | 18.5 | 2.8 | E78A21505D614FF580CBCDAB8050B98D |  | R22 | TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | TXV | 5.765%
Clovis | CA | 93619-9706 |  | 2013-08-26 | 2013-08-26 12:46 | 2013-08-26 12:47 | BDP - 588ANW036080ABAF | 67 | 2.3 | Yes | Yes | 17.6 | 20.4 | -2.8 | E701D6EBF6D6413D8E3702043F7DD572 |  | R22 | Non-TXV |  | 3.433% | 0.96567 | 6.597% | [5 empty] | Non-TXV | 3.433%
Clovis | CA | 93619-9706 |  | 2013-08-26 | 2013-08-26 12:49 | 2013-08-26 13:07 | AMANA - PGD30C0702E | 74 | 8.1 | Yes | Yes | 25.5 | 20.4 | 5.1 | 2191224DFF434CE4B9E86DEA8B1DB2A6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.95% | 0.89054 | 21.04% | [5 empty] | Non-TXV | 10.95%
Paradise | CA | 95969-3426 |  | 2013-08-30 | 2013-08-30 12:04 | 2013-08-30 12:58 | TEMPSTAR - PGAA30C1K4 | 85 | 5.8 | Yes | Yes | 18.4 | 21.2 | -2.8 | B2575A0AE1374343A36B75FFFD4D20EE |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Placerville | CA | 95667-8830 |  | 2013-08-29 | 2013-08-29 13:46 | 2013-08-29 14:09 | ICP - TCA442AKA5 | 272 | 16.3 | Yes | Yes | 20.1 | 22.6 | -2.5 | 5F33B132B5344316A174560756550287 |  | R22 | TXV |  | 5.993% | 0.94007 | 11.52% | [5 empty] | TXV | 5.993%
Stockton | CA | 95209-2322 |  | 2013-08-27 | 2013-08-27 12:25 | 2013-08-27 12:42 | PAYNE - PA10JA048-C | 96 | 4.9 | Yes | Yes | 19 | 16.6 | 2.4 | 53EEECBF1A3F45EAB6CC4B80C0417D9E |  | R22 | Non-TXV |  | 5.104% | 0.94896 | 9.809% | [5 empty] | Non-TXV | 5.104%
Fresno | CA | 93722-4728 |  | 2013-08-23 | 2013-08-23 12:14 | 2013-08-23 12:15 | AIRE-FLO - 585HJW036060ABAF | 102 | 19 | Yes | Yes | 22.6 | 20.2 | 2.4 | A724FD5918C9427DAADA00D524E43078 |  | R22 | Non-TXV |  | 18.63% | 0.81373 | 35.8% | [5 empty] | Non-TXV | 18.63%
Stockton | CA | 95206-2150 |  | 2013-08-22 | 2013-08-22 16:51 | 2013-08-22 17:11 | YORK - D3NZ030N05606NXA | 64 | 2.9 | Yes | Yes | 22.2 | 20.1 | 2.1 | D54AC2AA0ED341E0B00DCD1D07EFED4A |  | R410A | Non-TXV |  | 4.531% | 0.95469 | 8.708% | [5 empty] | Non-TXV | 4.531%
Stockton | CA | 95207-4732 |  | 2013-08-23 | 2013-08-23 11:09 | 2013-08-23 11:09 | TRANE - YCC030F1MOBJ | 72 | 0 | Yes | Yes | 19.6 | 19.2 | 0.4 | B49F71A89A9B450898695368C49A95F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3524 |  | 2013-08-29 | 2013-08-29 13:11 | 2013-08-29 13:12 | OTHER - GPCM36K060F | 85 | 14.3 | Yes | Yes | 23.9 | 21 | 2.9 | 2166E157A1574115B75ABE28B13D48EC |  | R22 | Non-TXV |  | 16.82% | 0.83176 | 32.33% | [5 empty] | Non-TXV | 16.82%
Merced | CA | 95348-2187 |  | 2013-08-30 | 2013-08-30 12:24 | 2013-08-30 12:26 | AIRE-FLO - 113ANA018E | 53 | 5.3 | Yes | Yes | 19 | 19.7 | -0.7 | F6CBAF2AA1CD4DAF9A55BF4FA1FF9163 |  | R410A | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Tracy | CA | 95377-9580 |  | 2013-08-22 | 2013-08-22 15:22 | 2013-08-22 15:22 | YORK - H1CB042S06A | 94 | 0 | Yes | Yes | 20.3 | 20.8 | -0.5 | FCB02FDC9DC640EBBA9FAD79C531629D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-4341 |  | 2013-08-27 | 2013-08-27 09:29 | 2013-08-27 10:03 | YORK - H2RD060S06B | 162 | 49.7 | Yes | Yes | 17.1 | 19.8 | -2.7 | D6AD5CD1284E4DD2840D49978C45CE07 |  | R22 | Non-TXV |  | 30.68% | 0.69321 | 58.96% | [5 empty] | Non-TXV | 30.68%
Corning | CA | 96021-9536 |  | 2013-09-03 | 2013-09-03 13:24 | 2013-09-03 14:18 | GOODMAN - GSC130481AA | 158 | 4.8 | Yes | Yes | 22.7 | 19.9 | 2.8 | 8B9585EF522347AE9683549B1FBA86CF |  | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Placerville | CA | 95667-8128 |  | 2013-08-26 | 2013-08-26 12:13 | 2013-08-26 12:13 | LENNOX - 12HPB42-10P | 136 | 0 | Yes | Yes | 21 | 20.9 | 0.1 | 1D27A4CC5F7A4AFBB6CF18A0C587E15A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-9491 |  | 2013-09-09 | 2013-09-09 15:12 | 2013-09-09 15:13 | BRYANT - 563CN048-H | 140 | 4.4 | Yes | Yes | 25.7 | 20.4 | 5.3 | 7E837A7D83654099980F664D469836E5 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Fresno | CA | 93722-4548 |  | 2013-08-22 | 2013-08-22 12:55 | 2013-08-22 12:57 | GOODMAN - CK36-1B | 79 | 3.5 | Yes | Yes | 21.9 | 20.1 | 1.9 | C590BB131C1D465B841E6DFAC062F5E4 |  | R22 | Non-TXV |  | 4.43% | 0.9557 | 8.514% | [5 empty] | Non-TXV | 4.43%
Madera | CA | 93636-7974 |  | 2013-09-18 | 2013-09-18 12:35 | 2013-09-18 12:36 | AIRE-FLO - 585HJW036060D | 70 | 6.4 | Yes | Yes | 26.9 | 21 | 5.9 | 21E1936987924CC8A8AF9A139ABEF559 |  | R22 | Non-TXV |  | 9.143% | 0.90857 | 17.57% | [5 empty] | Non-TXV | 9.143%
Fresno | CA | 93728-2732 |  | 2013-08-26 | 2013-08-26 13:36 | 2013-08-26 13:39 | OTHER - 7777UNK | 104 | 3.8 | Yes | Yes | 17.2 | 18.6 | -1.4 | F03A435C7FE64D01B11D1B53FE328E29 |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Stockton | CA | 95204-2610 |  | 2013-08-22 | 2013-08-22 16:30 | 2013-08-22 17:12 | YORK - D1NA030N05606 | 72 | 6.6 | Yes | Yes | 21 | 19.1 | 1.9 | 95D9F0C4B6CB4F37A0B27BB1E69695DF |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Manteca | CA | 95336-7038 |  | 2013-08-26 | 2013-08-26 10:38 | 2013-08-26 11:15 | BRYANT - 563CN060-D | 201 | 20.9 | Yes | Yes | 25.6 | 19.8 | 5.8 | 600EC2E522E24AFABB9CA4FB99C22302 |  | R22 | Non-TXV |  | 10.4% | 0.89602 | 19.98% | [5 empty] | Non-TXV | 10.4%
Stockton | CA | 95215-4843 |  | 2013-09-09 | 2013-09-09 14:43 | 2013-09-09 15:01 | GOODMAN - UNK | 71 | 6.2 | Yes | Yes | 22.7 | 22.1 | 0.6 | 5180B7396BE44F0CBD5ECA89A457F4AF |  | R22 | Non-TXV |  | 8.732% | 0.91268 | 16.78% | [5 empty] | Non-TXV | 8.732%
Fresno | CA | 93723-9207 |  | 2013-09-04 | 2013-09-04 10:51 | 2013-09-04 10:53 | OTHER - DEYZ-F048N0800A | 72 | 2.9 | Yes | Yes | 24.8 | 19.3 | 5.5 | 7176F9488A5049E4B9C2C32591600D09 |  | R410A | Non-TXV |  | 4.028% | 0.95972 | 7.741% | [5 empty] | Non-TXV | 4.028%
Stockton | CA | 95205-2639 |  | 2013-08-26 | 2013-08-26 10:48 | 2013-08-26 11:05 | OTHER - N2A330AKC200 | 67 | -3.9 | Yes | Yes | 19.7 | 18.8 | 0.9 | 8C7A8D7020D04B44A50F701284E466FA |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Stockton | CA | 95215-8213 |  | 2013-08-29 | 2013-08-29 15:14 | 2013-08-29 15:31 | AMERICAN STANDARD - YCX030F1M0BC | 102 | 3.1 | Yes | Yes | 24.9 | 21.4 | 3.5 | 463DA79FA8C640EB80806091EBFD78B7 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Paso Robles | CA | 93446-3512 |  | 2013-09-05 | 2013-09-05 09:14 | 2013-09-05 09:31 | ARCOAIRE - NAC036AKA4 | 87 | -5.1 | Yes | Yes | 16 | 18.8 | -2.8 | 7EAAF0B012544D7DAD041C26C1EFDA35 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Fresno | CA | 93703-5300 |  | 2013-09-27 | 2013-09-27 10:18 | 2013-09-27 10:20 | GOODMAN - GSX130241DA | 76 | 2.9 | Yes | Yes | 20.5 | 19.5 | 1 | 5D4FE02EA2C14EAB881B36647F430EE8 |  | R410A | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Stockton | CA | 95205-4613 |  | 2013-08-26 | 2013-08-26 16:41 | 2013-08-26 17:00 | PAYNE - PY3GNAA30060NA | 98 | 6.1 | Yes | Yes | 21.5 | 19.6 | 1.9 | C3ECEB43E8F742E88B093359E03BB5BC |  | R410A | TXV |  | 6.224% | 0.93776 | 11.96% | [5 empty] | TXV | 6.224%
Red Bluff | CA | 96080-4469 |  | 2013-09-20 | 2013-09-20 15:11 | 2013-09-20 15:28 | BRYANT - 661CJ030-C | 95 | 6.5 | Yes | Yes | 17 | 19.3 | -2.3 | 7FEED6DBA60544BF80678654B03454BF |  | R22 | TXV |  | 6.842% | 0.93158 | 13.15% | [5 empty] | TXV | 6.842%
Fresno | CA | 93722-2355 |  | 2013-08-22 | 2013-08-22 21:53 | 2013-08-22 22:02 | CARRIER - 48SX-030040321 | 69 | 2.2 | Yes | Yes | 17.7 | 20.5 | -2.8 | 01292BE3347B44609C3569EF6D61D03F |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Rocklin | CA | 95677-3461 |  | 2013-08-22 | 2013-08-22 14:06 | 2013-08-22 14:28 | COPELAND - VSX130241DA | 76 | -3.7 | Yes | Yes | 21 | 20.4 | 0.6 | 0C381E25B2CB4B5FA37FA510513DF698 |  | R410A | TXV |  | -4.868% | 1.0487 | 1.363% |  |  |  |  | TXV |  |  | -4.868%
Manteca | CA | 95336-6212 |  | 2013-08-26 | 2013-08-26 15:43 | 2013-08-26 16:01 | BDP - 561CJ036-C | 72 | 2.4 | Yes | Yes | 18.6 | 20.8 | -2.2 | C581772D6CD54C45B02F0FDEA7E3DB26 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Grass Valley | CA | 95949-6756 |  | 2013-09-05 | 2013-09-05 10:27 | 2013-09-05 10:46 | BRYANT - 577DNW042090 | 221 | 19.2 | Yes | Yes | 22.9 | 19.7 | 3.2 | 2EEEE8119AF74953AF9B8828C0FC9C2A |  | R410A | TXV |  | 8.688% | 0.91312 | 16.7% | [5 empty] | TXV | 8.688%
Fresno | CA | 93722-7158 |  | 2013-08-26 | 2013-08-26 14:30 | 2013-08-26 14:32 | YORK - H1RA048S06A | 117 | 3.7 | Yes | Yes | 17.1 | 19.5 | -2.4 | 270D15AEDAA340C4908833BF3D1F6256 |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Oroville | CA | 95966-8023 |  | 2013-08-29 | 2013-08-29 17:18 | 2013-08-29 17:36 | DAY & NIGHT - N2A336AKB200 | 86 | -5.1 | Yes | Yes | 25.3 | 19.5 | 5.9 | EF5B12C0181149D5904C3D52A85009AB |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Winton | CA | 95388-0000 |  | 2013-08-21 | 2013-08-21 12:40 | 2013-08-21 13:08 | DAY & NIGHT - UNK | 64 | 10.2 | Yes | Yes | 18.2 | 20.7 | -2.5 | BFD9FF1231DD4F5E83ABEBEB9B6E13B3 |  | R22 | Non-TXV |  | 15.94% | 0.84062 | 30.63% | [5 empty] | Non-TXV | 15.94%
Chico | CA | 95973-7661 |  | 2013-08-28 | 2013-08-28 12:16 | 2013-08-28 12:36 | DAY & NIGHT - 593BJ036-A | 86 | 6.3 | Yes | Yes | 15.9 | 18.1 | -2.2 | 4043B0DEF4424C558B3BAB818F97F770 |  | R22 | Non-TXV |  | 7.326% | 0.92674 | 14.08% | [5 empty] | Non-TXV | 7.326%
Stockton | CA | 95215-5222 |  | 2013-10-15 | 2013-10-15 15:23 | 2013-10-15 15:41 | GOODMAN - CLK60-1 | 115 | 7 | Yes | Yes | 18.8 | 18.7 | 0.1 | 9C494CD9041E4EC28996DDD158BF9F5C |  | R22 | Non-TXV |  | 6.087% | 0.93913 | 11.7% | [5 empty] | Non-TXV | 6.087%
Clovis | CA | 93619-5008 |  | 2013-08-23 | 2013-08-23 12:17 | 2013-08-23 12:17 | LENNOX - XC13-048-230-01 | 146 | 0 | Yes | Yes | 17 | 19.5 | -2.5 | E377F27180DF47F1838443C1975C6EB7 | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2150 |  | 2013-09-23 | 2013-09-23 12:58 | 2013-09-23 13:00 | OTHER - 7777UNK | 90 | 3.4 | Yes | Yes | 22.9 | 20.4 | 2.5 | E9540DF5DDA14834BF852FA965886767 |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Fresno | CA | 93722-4394 |  | 2013-08-29 | 2013-08-29 09:32 | 2013-08-29 09:39 | GOODMAN - GSC130481AG | 147 | 13.9 | Yes | Yes | 26.2 | 20.6 | 5.6 | 8C42B4C107614D02950625C2D5969173 |  | R22 | Non-TXV |  | 9.456% | 0.90544 | 18.17% | [5 empty] | Non-TXV | 9.456%
Huron | CA | 93234-0000 |  | 2013-10-11 | 2013-10-11 13:25 | 2013-10-11 14:18 | CARRIER - 48SDN036060311 | 130 | 4 | Yes | Yes | 26.1 | 20.4 | 5.7 | 2EEFF9FDB337469CB363018B03D4167A |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Paradise | CA | 95969-4212 |  | 2013-08-30 | 2013-08-30 13:03 | 2013-08-30 13:48 | RUUD - RRNA-BO36JK08E | 83 | 5.4 | Yes | Yes | 23.8 | 22.2 | 1.6 | 7806E46ADFDC4D21BA1679AE8469D03A |  | R22 | Non-TXV |  | 6.506% | 0.93494 | 12.5% | [5 empty] | Non-TXV | 6.506%
Sanger | CA | 93657-2808 |  | 2013-08-23 | 2013-08-23 15:36 | 2013-08-23 16:07 | CARRIER - 48SDN036060301 | 167 | 6.2 | Yes | Yes | 18.5 | 21.2 | -2.7 | 5301DE87C57D49348BA37E7877E1FCB8 |  | R22 | Non-TXV |  | 3.713% | 0.96287 | 7.135% | [5 empty] | Non-TXV | 3.713%
Fresno | CA | 93727-7969 |  | 2013-09-04 | 2013-09-04 09:58 | 2013-09-04 10:38 | ICP - PGAD30D1K5 | 78 | 6.4 | Yes | Yes | 23.5 | 20.4 | 3.1 | 148D6CD04F434D65877F8BD1F4B5D0EE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.205% | 0.91795 | 15.77% | [5 empty] | Non-TXV | 8.205%
Stockton | CA | 95207-7547 |  | 2013-08-30 | 2013-08-30 13:42 | 2013-08-30 14:00 | DAY & NIGHT - 567C042RCU | 74 | 8.8 | Yes | Yes | 17.7 | 17.9 | -0.2 | 908448E3C0184422BF919C8D9B0F93F3 |  | R22 | Non-TXV |  | 11.89% | 0.88108 | 22.85% | [5 empty] | Non-TXV | 11.89%
Red Bluff | CA | 96080-2521 |  | 2013-08-26 | 2013-08-26 15:58 | 2013-08-26 15:58 | RHEEM - RRN-603608E | 92 | 0 | Yes | Yes | 17.2 | 20.2 | -3 | 4FA13EB101E64780B3C7420CA8627F64 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3561 |  | 2013-08-26 | 2013-08-26 09:29 | 2013-08-26 09:51 | DUCANE - AC10B24 | 60 | 2 | Yes | Yes | 17 | 19.9 | -2.9 | 30B7DAD76D574B7B90FC8B6B4CB46408 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95215-6742 |  | 2013-08-29 | 2013-08-29 17:03 | 2013-08-29 17:20 | DAY & NIGHT - 588ANW03606ACAF | 67 | 3.3 | Yes | Yes | 23.4 | 21 | 2.4 | C9F557381D9544E4A9705A317059C8B4 |  | R22 | Non-TXV |  | 4.925% | 0.95075 | 9.465% | [5 empty] | Non-TXV | 4.925%
Stockton | CA | 95215-7960 |  | 2013-09-26 | 2013-09-26 13:24 | 2013-09-26 13:40 | DAY & NIGHT - 30/80YAC-106T | 65 | 2.6 | Yes | Yes | 24.1 | 19.1 | 5 | 056B9ED76C544A3F826844DD380865FF |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93727-7962 |  | 2013-09-12 | 2013-09-12 11:50 | 2013-09-12 12:55 | YORK - D2NP036N05606A | 108 | 5 | Yes | Yes | 20 | 20.1 | -0.1 | 9A4482EB087C4D82B0839ADE4D0CD428 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Fresno | CA | 93702-3642 |  | 2013-08-23 | 2013-08-23 15:37 | 2013-08-23 15:39 | ICP - PGAD36D1K6 | 102 | 13.9 | Yes | Yes | 23 | 22.1 | 0.9 | B5B16EA226E2409A87686DC3EA0B6457 |  | R22 | Non-TXV |  | 13.63% | 0.86373 | 26.19% | [5 empty] | Non-TXV | 13.63%
Winton | CA | 95388-9523 |  | 2013-08-27 | 2013-08-27 14:01 | 2013-08-27 14:31 | AMERICAN STANDARD - YCP042FM0AC | 128 | 3.8 | Yes | Yes | 24.3 | 20.9 | 3.4 | DA38780D948644268E99DEA46444C5BB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Lathrop | CA | 95330-9375 |  | 2013-08-30 | 2013-08-30 10:43 | 2013-08-30 11:04 | CARRIER - 38CKC060370 | 131 | 17.6 | Yes | Yes | 19 | 19.9 | -0.9 | C2133590083B4EBCA863354A7F19C6A1 |  | R22 | Non-TXV |  | 13.44% | 0.86565 | 25.82% | [5 empty] | Non-TXV | 13.44%
Tracy | CA | 95376-8741 |  | 2013-09-10 | 2013-09-10 14:45 | 2013-09-10 15:13 | PAYNE - PA10JA036-A | 83 | 4.8 | Yes | Yes | 27.3 | 21.7 | 5.6 | A9C51F59F961496F80A2FA90AC72A264 |  | R22 | Non-TXV |  | 5.783% | 0.94217 | 11.11% | [5 empty] | Non-TXV | 5.783%
Stockton | CA | 95210-5129 |  | 2013-08-27 | 2013-08-27 13:59 | 2013-08-27 14:21 | CARRIER - 38CKC048370 | 99 | 6.3 | Yes | Yes | 19.4 | 17.9 | 1.5 | 0601950DF6D14B5D88EF5585DD4B6726 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Fresno | CA | 93722-1143 |  | 2013-08-23 | 2013-08-23 09:40 | 2013-08-23 09:41 | NORDYNE - JS5BD042KA | 122 | 10.3 | Yes | Yes | 18.6 | 18.7 | -0.1 | 62551B140FF6493C8BB50308109FC783 |  | R22 | Non-TXV |  | 8.443% | 0.91557 | 16.22% | [5 empty] | Non-TXV | 8.443%
Chico | CA | 95973-5833 |  | 2013-08-30 | 2013-08-30 09:43 | 2013-08-30 10:04 | CARRIER - 38BRC030310 | 100 | -5.9 | Yes | Yes | 22.2 | 19.7 | 2.5 | 73779BCB6CC64CB2892C60B7D33B1C38 |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Stockton | CA | 95204-3701 |  | 2013-08-23 | 2013-08-23 08:39 | 2013-08-23 08:56 | ARCOAIRE - GPFM24K040A | 58 | 4.1 | Yes | Yes | 23.2 | 18.2 | 5 | C09A61923496481CBD205E4FD3E6B601 |  | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Fresno | CA | 93702-3807 |  | 2013-08-26 | 2013-08-26 11:15 | 2013-08-26 11:18 | CARRIER - 7777UNK | 100 | 3.1 | Yes | Yes | 22.3 | 18 | 4.3 | E0E4673972CE40D9981345222929EA26 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Tracy | CA | 95377-9569 |  | 2013-08-29 | 2013-08-29 12:18 | 2013-08-29 12:40 | YORK - UNK | 85 | 9.8 | Yes | Yes | 17.2 | 19.6 | -2.4 | 536861AF89D84B6F801D6FA3AFEC09C7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.53% | 0.88471 | 22.16% | [5 empty] | Non-TXV | 11.53%
Artois | CA | 95913-0000 |  | 2013-09-11 | 2013-09-11 10:52 | 2013-09-11 11:11 | CARRIER - 50Y00365300 | 76 | 5.7 | Yes | Yes | 16.6 | 19.5 | -2.9 | 0D11C9FC42574692AAD0C7604F6FAC0D |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95206-6120 |  | 2013-08-26 | 2013-08-26 08:52 | 2013-08-26 09:13 | RUUD - UAMA-048JBZ | 172 | 9.3 | Yes | Yes | 19.7 | 19.1 | 0.6 | 71E5CC81CF064528BBE8123B896A2246 |  | R22 | Non-TXV |  | 5.407% | 0.94593 | 10.39% | [5 empty] | Non-TXV | 5.407%
Fresno | CA | 93705-2817 |  | 2013-08-29 | 2013-08-29 13:31 | 2013-08-29 13:32 | AMANA - PGD36C0702E | 110 | 13.4 | Yes | Yes | 30.1 | 24.8 | 5.3 | F3583E058FE841A4B5475D42F867A0E8 |  | R22 | Non-TXV |  | 12.18% | 0.87818 | 23.41% | [5 empty] | Non-TXV | 12.18%
Fresno | CA | 93702-3144 |  | 2013-08-23 | 2013-08-23 13:49 | 2013-08-23 13:51 | CARRIER - 48GX048115301AD | 114 | 26 | Yes | Yes | 21 | 20.1 | 0.9 | E8D0E51F0F7940438EE0BEA5D3A6EA51 |  | R22 | Non-TXV |  | 22.81% | 0.77193 | 43.83% | [5 empty] | Non-TXV | 22.81%
Fresno | CA | 93728-3064 |  | 2013-09-23 | 2013-09-23 15:59 | 2013-09-23 16:34 | ICP - PGF330060K01A1 | 152 | 4.6 | Yes | Yes | 23 | 20.4 | 2.6 | ACA1131D09B0456299EC6284D8557AF7 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Valley Springs | CA | 95252-9452 |  | 2013-09-05 | 2013-09-05 17:02 | 2013-09-05 17:19 | YORK - ERCS0481BBB | 134 | 10.7 | Yes | Yes | 28.6 | 22.6 | 6 | ED6A10BC422C4AD4877CCD373A412595 |  | R22 | Non-TXV |  | 7.985% | 0.92015 | 15.35% | [5 empty] | Non-TXV | 7.985%
Stockton | CA | 95210-1252 |  | 2013-09-09 | 2013-09-09 13:23 | 2013-09-09 13:43 | CARRIER - 38BA003300 | 144 | -8.5 | Yes | Yes | 18.6 | 19.5 | -0.9 | 06FE5C835FC64DB1AE081A44D177718C |  | R22 | Non-TXV |  | -5.903% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.903%
Manteca | CA | 95336-3358 |  | 2013-08-26 | 2013-08-26 14:34 | 2013-08-26 14:54 | GE - BGTA724B1B | 46 | 1.9 | Yes | Yes | 20 | 20.7 | -0.7 | C47E9AC6335F4FA3833714EE0993FB23 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.13% | 0.9587 | 7.938% | [5 empty] | Non-TXV | 4.13%
Magalia | CA | 95954-9124 |  | 2013-09-26 | 2013-09-26 11:36 | 2013-09-26 12:24 | COLEMAN - NA | 65 | 6.4 | Yes | Yes | 21.6 | 24.4 | -2.8 | E0737FECA3C14440B0FA10DA9C4BF1CC |  | R22 | Non-TXV |  | 9.846% | 0.90154 | 18.92% | [5 empty] | Non-TXV | 9.846%
Red Bluff | CA | 96080-4469 |  | 2013-09-10 | 2013-09-10 16:43 | 2013-09-10 17:02 | BRYANT - 213RNA030-A | 117 | 4.4 | Yes | Yes | 16.4 | 19.3 | -2.9 | B428D128C9AB4CC980929DB0C9F0481C |  | R22 | TXV |  | 3.761% | 0.96239 | 7.227% | [5 empty] | TXV | 3.761%
Fresno | CA | 93722-7164 |  | 2013-08-22 | 2013-08-22 14:43 | 2013-08-22 14:46 | GIBSON - JS3BC-048KA | 110 | 4.1 | Yes | Yes | 20.4 | 19.3 | 1.1 | 4CB9A99814754AB0A3C59B400EB2BB72 |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.163% | [5 empty] | Non-TXV | 3.727%
Chico | CA | 95926-4369 |  | 2013-09-26 | 2013-09-26 12:29 | 2013-09-26 12:50 | PAYNE - 585GJ024040 | 54 | 1.6 | Yes | Yes | 24 | 20.4 | 3.6 | 2E4640E941DA4C018832B3ADECFC1D86 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95215-9309 |  | 2013-09-12 | 2013-09-12 15:43 | 2013-09-12 16:01 | GOODMAN - GSH130361CB | 188 | 12.2 | Yes | Yes | 20.7 | 18.2 | 2.6 | 5CB29AB79EB34EBDB3D367F94578B31B |  | R22 | Non-TXV |  | 6.489% | 0.93511 | 12.47% | [5 empty] | Non-TXV | 6.489%
Magalia | CA | 95954-9457 |  | 2013-09-19 | 2013-09-19 09:41 | 2013-09-19 19:09 | BRYANT - 582ANW042090AAAG | 97 | 5.9 | Yes | Yes | 22.7 | 20.4 | 2.4 | C63E8F9ECBFA4AFC9B65969446E33651 |  | R22 | Non-TXV |  | 6.082% | 0.93918 | 11.69% | [5 empty] | Non-TXV | 6.082%
Fresno | CA | 93727-5682 |  | 2013-08-27 | 2013-08-27 15:49 | 2013-08-27 16:17 | LENNOX - 13ACD-042-230-02 | 111 | 4.1 | Yes | Yes | 20.5 | 18.8 | 1.7 | A5B70E7AEA9A46D6BA02EF4B7CD7DA4E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.694% | 0.96306 | 7.098% | [5 empty] | Non-TXV | 3.694%
Fresno | CA | 93702-2439 |  | 2013-09-18 | 2013-09-18 17:02 | 2013-09-18 17:21 | OTHER - NRGF36DDB04 | 90 | 6.6 | Yes | Yes | 17 | 18.6 | -1.6 | F6E40B08F53745D498680E78B000B5D5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Fresno | CA | 93702-3630 |  | 2013-08-30 | 2013-08-30 14:49 | 2013-08-30 14:52 | RHEEM - RRNL-B036JK06X | 93 | 4.5 | Yes | Yes | 17.5 | 19.7 | -2.2 | 67758CCDFE2C4D1C9B9799724096DA44 |  | R22 | Non-TXV |  | 4.839% | 0.95161 | 9.299% | [5 empty] | Non-TXV | 4.839%
Fresno | CA | 93703-4103 |  | 2013-08-27 | 2013-08-27 12:15 | 2013-08-27 12:16 | ICP - PGMD36G0602 | 81 | 8 | Yes | Yes | 22.3 | 20.9 | 1.4 | E722BDD684514DBDB5B73A4AD2667843 |  | R22 | Non-TXV |  | 9.877% | 0.90123 | 18.98% | [5 empty] | Non-TXV | 9.877%
Stockton | CA | 95209-1222 |  | 2013-08-23 | 2013-08-23 14:22 | 2013-08-23 14:40 | RHEEM - UNK | 68 | 14.5 | Yes | Yes | 24.6 | 19 | 5.6 | E05B963CE435479DB321FB0028932DE8 |  | R22 | Non-TXV |  | 21.32% | 0.78676 | 40.98% | [5 empty] | Non-TXV | 21.32%
Stockton | CA | 95205-6448 |  | 2013-08-26 | 2013-08-26 16:00 | 2013-08-26 16:19 | YORK - D3NZ036N05606NXA | 64 | 3.7 | Yes | Yes | 21.9 | 17.5 | 4.5 | C2251D9D1B6D468D8194F804BD1056AD |  | R410A | TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | TXV | 5.781%
Lathrop | CA | 95330-9728 |  | 2013-08-30 | 2013-08-30 11:35 | 2013-08-30 11:57 | PAYNE - PY3PNA030060NA | 130 | 3.9 | Yes | Yes | 22.7 | 21.3 | 1.4 | BBA8A02195864C3EB28E7567BDF8147B |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95926-7760 |  | 2013-08-30 | 2013-08-30 12:03 | 2013-08-30 12:28 | COLEMAN - BRCS042C | 90 | -6.4 | Yes | Yes | 23.5 | 18.5 | 5 | F076D25135F3425DAFF102B9791A6907 |  | R22 | Non-TXV |  | -7.111% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.111%
Merced | CA | 95341-6627 |  | 2013-08-29 | 2013-08-29 15:01 | 2013-08-29 15:03 | RHEEM - UNK | 56 | 8.7 | Yes | Yes | 25.1 | 21.3 | 3.8 | 023D2D69DC8A4A8696850877876E1073 |  | R22 | Non-TXV |  | 15.54% | 0.84464 | 29.86% | [5 empty] | Non-TXV | 15.54%
Fresno | CA | 93706-9205 |  | 2013-09-12 | 2013-09-12 14:12 | 2013-09-12 14:13 | GOODMAN - GPG13300451BB | 77 | 11.5 | Yes | Yes | 23.1 | 21 | 2.1 | 5745522B26574BD08229156D4842042E |  | R22 | Non-TXV |  | 14.94% | 0.85065 | 28.7% | [5 empty] | Non-TXV | 14.94%
Manteca | CA | 95336-6454 |  | 2013-11-14 | 2013-11-14 12:52 | 2013-11-14 13:09 | BRYANT - 563CN048-H | 136 | 8.6 | Yes | Yes | 23.4 | 20.1 | 3.3 | 159E4772B4434490925B3FD6F5B7FF11 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 6.324% | 0.93676 | 12.15% | [5 empty] | TXV | 6.324%
Tracy | CA | 95377-8422 |  | 2013-08-23 | 2013-08-23 14:50 | 2013-08-23 15:19 | CARRIER - 38EZG036310 | 99 | 6.8 | Yes | Yes | 18 | 20.8 | -2.8 | 755A8C1F80E54EFF80445F5CE5E19AA8 |  | R410A | Non-TXV |  | 6.869% | 0.93131 | 13.2% | [5 empty] | Non-TXV | 6.869%
Stockton | CA | 95210-1153 |  | 2013-09-05 | 2013-09-05 11:37 | 2013-09-05 11:57 | NORDYNE - NAC024AKB2 | 60 | 10.3 | Yes | Yes | 20.2 | 18.2 | 2 | 65DE303D71F7410EB8C818327265EFAE |  | R22 | Non-TXV |  | 17.17% | 0.82833 | 32.99% | [5 empty] | Non-TXV | 17.17%
Fowler | CA | 93625-9662 |  | 2013-09-19 | 2013-09-19 16:11 | 2013-09-19 16:31 | BDP - 585HJW036060ABAF | 101 | 15.2 | Yes | Yes | 18.1 | 18.4 | -0.3 | E30FB442F18E466780C809794DE15BD0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.05% | 0.8495 | 28.92% | [5 empty] | Non-TXV | 15.05%
Reedley | CA | 93654-2536 |  | 2013-09-03 | 2013-09-03 15:10 | 2013-09-03 16:00 | RUUD - URGG005E30JKR | 85 | 3.2 | Yes | Yes | 21.1 | 21.5 | -0.4 | 990FF4F5D7524E26888A0C46928B70F9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Stockton | CA | 95206-2148 |  | 2013-09-16 | 2013-09-16 13:54 | 2013-09-16 14:24 | HEIL - UNK | 85 | 5.6 | Yes | Yes | 16.6 | 19.5 | -2.9 | 183A177D6F0844069671F095B9C80BBF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Fresno | CA | 93720-2421 |  | 2013-08-22 | 2013-08-22 15:01 | 2013-08-22 15:02 | LENNOX - GCS20H311751P | 48 | 5.3 | Yes | Yes | 25.3 | 22.8 | 2.5 | 8F04B1BC79554DE0A977B370972BE75A |  | R22 | Non-TXV |  | 11.04% | 0.88958 | 21.22% | [5 empty] | Non-TXV | 11.04%
Huron | CA | 93234-0000 |  | 2013-10-11 | 2013-10-11 14:22 | 2013-10-11 15:02 | LENNOX - 12GCS-42X-75-6PB | 133 | 4.3 | Yes | Yes | 26 | 20.4 | 5.6 | 63DAC3A5438E415FAD6B746DC89ADDE5 |  | R22 | Non-TXV |  | 3.233% | 0.96767 | 6.213% | [5 empty] | Non-TXV | 3.233%
Fresno | CA | 93727-2297 |  | 2013-09-04 | 2013-09-04 08:51 | 2013-09-04 09:55 | BDP - 598AN036-B | 182 | 12.7 | Yes | Yes | 21.5 | 20.8 | 0.7 | 76A640837FBE4C0BB52CB04519A38D62 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.978% | 0.93022 | 13.41% | [5 empty] | Non-TXV | 6.978%
Fresno | CA | 93727-3018 |  | 2013-08-27 | 2013-08-27 09:01 | 2013-08-27 09:46 | GOODMAN - GPG13300701AB | 77 | 5.8 | Yes | Yes | 22 | 20.4 | 1.6 | 3ABD71A9D94A4CF7A8ACCB24119B8076 |  | R22 | Non-TXV |  | 7.532% | 0.92468 | 14.48% | [5 empty] | Non-TXV | 7.532%
Reedley | CA | 93654-2356 |  | 2013-10-07 | 2013-10-07 15:43 | 2013-10-07 16:28 | RHEEM - N/A | 60 | 5.3 | Yes | Yes | 25 | 20.3 | 4.7 | 2668317E73D4469C83C1266520FD828E |  | R22 | Non-TXV |  | 8.833% | 0.91167 | 16.98% | [5 empty] | Non-TXV | 8.833%
Chowchilla | CA | 93610-9581 |  | 2013-09-02 | 2013-09-02 01:19 | 2013-09-02 01:40 | YORK - UNK | 85 | 3 | Yes | Yes | 20.5 | 20.4 | 0.1 | 3F20DE925F8148A8B399B5AFE9BF0308 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93710-5431 |  | 2013-08-23 | 2013-08-23 16:21 | 2013-08-23 16:28 | OTHER - GCGD36S21S2A | 63 | 21.1 | Yes | Yes | 20.4 | 21.4 | -1 | BF90297F756C4EF688DB596C65B235F0 |  | R22 | Non-TXV |  | 33.49% | 0.66508 | 64.36% | [5 empty] | Non-TXV | 33.49%
Reedley | CA | 93654-2355 |  | 2013-09-03 | 2013-09-03 16:53 | 2013-09-03 17:20 | ICP - PGF324040K01A2 | 64 | 4.6 | Yes | Yes | 17.1 | 18.7 | -1.6 | D3C09709F61C40B791B5A4728B1F8ACB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Fresno | CA | 93702-4702 |  | 2013-08-22 | 2013-08-22 09:58 | 2013-08-22 10:00 | YORK - CHE366A | 95 | 15.6 | Yes | Yes | 19.7 | 15.7 | 4 | BB92443622394488B48F0596650A7EA5 |  | R22 | Non-TXV |  | 16.42% | 0.83579 | 31.56% | [5 empty] | Non-TXV | 16.42%
Reedley | CA | 93654-2356 |  | 2013-09-03 | 2013-09-03 16:02 | 2013-09-03 16:50 | RUUD - N/A | 60 | 4.6 | Yes | Yes | 19 | 20.7 | -1.7 | 653DD431DA3C48539534616589A62DC5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.667% | 0.92333 | 14.73% | [5 empty] | Non-TXV | 7.667%
Fresno | CA | 93726-2503 |  | 2013-09-13 | 2013-09-13 18:01 | 2013-09-13 19:35 | LENNOX - 13ACD-036-230-15 | 92 | 7 | Yes | Yes | 14.8 | 14.9 | -0.1 | 349CC158B09A4FE484785959A8750BC7 |  | R22 | Non-TXV |  | 7.609% | 0.92391 | 14.62% | [5 empty] | Non-TXV | 7.609%
Reedley | CA | 93654-2358 |  | 2013-09-03 | 2013-09-03 17:41 | 2013-09-03 19:30 | RUUD - N/A | 60 | 2.1 | Yes | Yes | 17 | 19.8 | -2.8 | 78D13A54C21B4DCEB87EFDB63B27CF78 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Stockton | CA | 95210-1843 |  | 2013-08-27 | 2013-08-27 13:06 | 2013-08-27 13:24 | OTHER - CA5542VKD2 | 98 | 10.1 | Yes | Yes | 20.6 | 17.3 | 3.3 | 4A02CF4787F44D7FB163E79E78A3995A |  | R22 | Non-TXV |  | 10.31% | 0.89694 | 19.81% | [5 empty] | Non-TXV | 10.31%
Atwater | CA | 95301-3836 |  | 2013-09-03 | 2013-09-03 09:48 | 2013-09-03 10:09 | GOODMAN - PGJ042075-1 | 90 | 3.3 | Yes | Yes | 15.9 | 18.2 | -2.3 | 07DFFBF334FF4B989B72B10E3895E42C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Sanger | CA | 93657-3330 |  | 2013-09-10 | 2013-09-10 13:55 | 2013-09-10 14:13 | ICP - N/A | 113 | 3.9 | Yes | Yes | 17.5 | 20.1 | -2.6 | 043AEBA72FC345179B13F2B740BAA77C |  | R22 | Non-TXV |  | 3.451% | 0.96549 | 6.633% | [5 empty] | Non-TXV | 3.451%
Murphys | CA | 95247-9520 |  | 2013-09-04 | 2013-09-04 14:37 | 2013-09-04 15:40 | GUARDIAN - CK481B | 140 | 4.3 | Yes | Yes | 19.6 | 18.6 | 1 | 5B881F8CD2B64BA7A5E94D851E4526FC |  | R22 | Non-TXV |  | 3.071% | 0.96929 | 5.903% | [5 empty] | Non-TXV | 3.071%
Placerville | CA | 95667-3461 |  | 2013-09-06 | 2013-09-06 12:36 | 2013-09-06 12:36 | TRANE - TWD736B100A0 | 92 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | 88484BDDA48B40A5B4AB656BC2646E6D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-0000 |  | 2013-09-09 | 2013-09-09 12:02 | 2013-09-09 12:23 | RHEEM - RRMA-A048JK10X | 115 | 3.4 | Yes | Yes | 20.1 | 20.2 | -0.1 | FDB201EBF06347B480AB8C3E6A2F56DE |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Murphys | CA | 95247-9520 |  | 2013-09-04 | 2013-09-04 14:16 | 2013-09-04 14:34 | TRANE - TTX060C100A1 | 192 | 5.7 | Yes | Yes | 22.2 | 20.7 | 1.5 | E426692D732344B1AE06A32819AF6F43 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93727-2479 |  | 2013-08-27 | 2013-08-27 10:24 | 2013-08-27 10:43 | YORK - N/A | 60 | 1.9 | Yes | Yes | 16 | 19 | -3 | 3438D147B54D412186DC1DDB5E867BD0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Grass Valley | CA | 95949-6739 |  | 2013-08-23 | 2013-08-23 15:32 | 2013-08-23 15:32 | BRYANT - 583BNW0481115AAAF | 152 | 0 | Yes | Yes | 26.7 | 21.3 | 5.4 | 8B462A9A35694471801F925327F791A9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3001 |  | 2013-08-26 | 2013-08-26 13:59 | 2013-08-26 14:01 | PAYNE - 7777UNK | 64 | 2 | Yes | Yes | 20.2 | 18.1 | 2.1 | 39E89B1F204B4B20A67FC1B182F73537 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Stockton | CA | 95205-7206 |  | 2013-10-11 | 2013-10-11 14:00 | 2013-10-11 14:17 | AMANA - APG13420901AA | 107 | 17.6 | Yes | Yes | 24.2 | 19.7 | 4.5 | 99DD5A5EC9B748AB8379ACB4A1A3735C |  | R22 | Non-TXV |  | 16.45% | 0.83551 | 31.61% | [5 empty] | Non-TXV | 16.45%
Clovis | CA | 93612-5113 |  | 2013-09-20 | 2013-09-20 11:26 | 2013-09-20 11:28 | LENNOX - 10GCS036X-75-6PB | 58 | 3 | Yes | Yes | 23.2 | 20.2 | 3 | C5344F2055914A8B88F50F87966D4B97 |  | R22 | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Fresno | CA | 93720-4047 |  | 2013-08-29 | 2013-08-29 12:08 | 2013-08-29 12:10 | CARRIER - 7777UNK | 96 | 3.6 | Yes | Yes | 22.1 | 20.2 | 1.9 | 4FD1CCC8BDF042D491F79A2EC49276DD |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Fresno | CA | 93711-4055 |  | 2013-09-23 | 2013-09-23 13:16 | 2013-09-23 14:13 | LENNOX - 24ABR330A003010 | 82 | 2.7 | Yes | Yes | 17.3 | 20.1 | -2.8 | 85EAEDA486D043809118395E1E3BEB74 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Stockton | CA | 95215-9535 |  | 2013-09-04 | 2013-09-04 11:50 | 2013-09-04 12:16 | GOODMAN - GPG1348090M41AB | 125 | 3.8 | Yes | Yes | 23.9 | 18.2 | 5.7 | 3F61DA44CC6247CAAC161E7662478067 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.04% | 0.9696 | 5.842% | [5 empty] | Non-TXV | 3.04%
Fresno | CA | 93726-7509 |  | 2013-08-30 | 2013-08-30 10:25 | 2013-08-30 10:26 | DAY & NIGHT - 585GJ024040 | 54 | 1.8 | Yes | Yes | 22.1 | 19.7 | 2.4 | CDCA38B022384A5E8F9740E2092B8ADC |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93702-1655 |  | 2013-09-18 | 2013-09-18 12:49 | 2013-09-18 13:15 | RHEEM - N/A | 60 | 6.4 | Yes | Yes | 18.7 | 20.2 | -1.5 | E52AB0270F5F4960B83A04C1FC0CD1A0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Selma | CA | 93662-2470 |  | 2013-10-04 | 2013-10-04 12:24 | 2013-10-04 13:00 | LENNOX - 13ACC-036-230-01 | 115 | 6.7 | Yes | Yes | 24 | 20.5 | 3.5 | 6ADE05151817453F9849ED44C7D9E29A |  | R22 | Non-TXV |  | 5.826% | 0.94174 | 11.2% | [5 empty] | Non-TXV | 5.826%
Lathrop | CA | 95330-8899 |  | 2013-08-30 | 2013-08-30 09:55 | 2013-08-30 10:15 | CARRIER - 38CKC060370 | 131 | 15.2 | Yes | Yes | 21 | 19.9 | 1.1 | 2F2EF3F1D4A24AB9BAD220AE4678C3DB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.6% | 0.88397 | 22.3% | [5 empty] | Non-TXV | 11.6%
Paso Robles | CA | 93446-5065 |  | 2013-10-08 | 2013-10-08 12:19 | 2013-10-08 12:38 | OTHER - 2AC13B24P-2B | 89 | -5.2 | Yes | Yes | 18.5 | 19.1 | -0.6 | 4DF8047CBD4C48DD81C0917C07F4D3CB |  | R22 | Non-TXV |  | -5.843% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.843%
Red Bluff | CA | 96080-2835 |  | 2013-08-26 | 2013-08-26 16:11 | 2013-08-26 19:33 | AMANA - PGD36C0702F | 110 | 3.4 | Yes | Yes | 26.4 | 20.4 | 6 | C455B0D883ED4EA8AC1EA7F6E1FFEAFE |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Tracy | CA | 95376-2303 |  | 2013-10-16 | 2013-10-16 10:20 | 2013-10-16 10:39 | PAYNE - PY1PNB036060ABAA | 68 | 2.8 | Yes | Yes | 26.1 | 20.1 | 6 | 636B05BA70984730AAE41F3359CB92FF |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Los Banos | CA | 93635-3111 |  | 2013-09-09 | 2013-09-09 12:58 | 2013-09-09 13:00 | DAY & NIGHT - 7777UNK | 92 | 4.9 | Yes | Yes | 19.4 | 20.2 | -0.8 | 3FD23FD66B284CD1B1DF10200AE1AB30 |  | R22 | Non-TXV |  | 5.326% | 0.94674 | 10.24% | [5 empty] | Non-TXV | 5.326%
Stockton | CA | 95206-6095 |  | 2013-08-26 | 2013-08-26 10:28 | 2013-08-26 10:50 | GOODMAN - CLJ48-1A | 130 | 4.7 | Yes | Yes | 22.8 | 18.1 | 4.7 | 51217E230380455AB26A609BE395B4A9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | Non-TXV | 3.615%
Clovis | CA | 93612-2392 |  | 2013-08-22 | 2013-08-22 14:11 | 2013-08-22 15:41 | CARRIER - 591ANX036000AAAA | 83 | 7.5 | Yes | Yes | 19.5 | 19.8 | -0.3 | A87F34440319484C81CD59C66048CEA6 |  | R22 | Non-TXV |  | 9.036% | 0.90964 | 17.37% | [5 empty] | Non-TXV | 9.036%
Clovis | CA | 93611-2054 |  | 2013-08-22 | 2013-08-22 11:04 | 2013-08-22 11:21 | CARRIER - N/A | 90 | 3 | Yes | Yes | 20 | 21.8 | -1.8 | 9D87A33A5CC042DF978C6419A0C8ECCE |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95215-9305 |  | 2013-08-29 | 2013-08-29 16:29 | 2013-08-29 16:49 | ICP - PGC036K060B | 71 | 5.4 | Yes | Yes | 22.5 | 19.5 | 3 | B5308E20D06541768DF1D5B449BA42F2 |  | R22 | Non-TXV |  | 7.606% | 0.92394 | 14.62% | [5 empty] | Non-TXV | 7.606%
Fresno | CA | 93722-4603 |  | 2013-09-10 | 2013-09-10 14:05 | 2013-09-10 14:06 | GOODMAN - PGB024050 | 54 | 8.2 | Yes | Yes | 20.3 | 20.4 | -0.1 | 44D951E35B41417591D7F8D85CBAFE2E |  | R22 | Non-TXV |  | 15.19% | 0.84815 | 29.18% | [5 empty] | Non-TXV | 15.19%
Mariposa | CA | 95338-9347 |  | 2013-09-11 | 2013-09-11 11:25 | 2013-09-11 11:26 | CARRIER - 50YQ060300 | 134 | 12 | Yes | Yes | 26.6 | 20.9 | 5.7 | 0FD46BCE571C402B900CCEA7A120CD41 |  | R22 | Non-TXV |  | 8.955% | 0.91045 | 17.21% | [5 empty] | Non-TXV | 8.955%
Fresno | CA | 93702-4717 |  | 2013-08-22 | 2013-08-22 12:07 | 2013-08-22 12:10 | BDP - 588ANW036080ABAF | 67 | 8.1 | Yes | Yes | 19.3 | 18.5 | 0.8 | 7D6364B29AC94E0993F9D791371BC9C6 |  | R22 | Non-TXV |  | 12.09% | 0.8791 | 23.23% | [5 empty] | Non-TXV | 12.09%
Fresno | CA | 93727-2327 |  | 2013-08-27 | 2013-08-27 11:17 | 2013-08-27 11:51 | PAYNE - PY2PNB048090ABAA | 131 | 16.8 | Yes | Yes | 16.4 | 19.2 | -2.8 | 6E9C6C8290E447C494BBEF740259641F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.82% | 0.87176 | 24.65% | [5 empty] | Non-TXV | 12.82%
Corning | CA | 96021-2159 |  | 2013-09-03 | 2013-09-03 13:21 | 2013-09-03 18:18 | RUUD - UAMC-036JAZ | 93 | 2.7 | Yes | Yes | 21.4 | 16.3 | 5.1 | AF52B3B169884A99A611BAD46DE1920E |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Merced | CA | 95348-1561 |  | 2013-08-23 | 2013-08-23 12:35 | 2013-08-23 12:37 | GOODMAN - GPG13240451CB | 74 | 3.2 | Yes | Yes | 23.6 | 19.9 | 3.7 | 7E43EE225DEB4BFEAC86A34253B1185C |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
Kerman | CA | 93630-1261 |  | 2013-08-28 | 2013-08-28 11:57 | 2013-08-28 11:58 | CARRIER - 7777UNK | 100 | 4.8 | Yes | Yes | 19.8 | 19.3 | 0.5 | D235EA68DC10429D979C931258ED0752 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Stockton | CA | 95215-9703 |  | 2013-08-29 | 2013-08-29 15:51 | 2013-08-29 16:13 | AMERICAN STANDARD - 4YCY4030A1075AB | 97 | 4 | Yes | Yes | 19.8 | 19.2 | 0.6 | 927A546F4280462184DFDC1EDB3F2FAF |  | R410A | Non-TXV |  | 4.124% | 0.95876 | 7.925% | [5 empty] | Non-TXV | 4.124%
Fresno | CA | 93722-7712 |  | 2013-10-02 | 2013-10-02 12:41 | 2013-10-02 12:43 | BRYANT - 561CJ03036E | 70 | 9.4 | Yes | Yes | 20.5 | 18.1 | 2.4 | F2A919503FFD40D4B6AEE0088424A53B |  | R22 | TXV |  | 13.43% | 0.86571 | 25.81% | [5 empty] | TXV | 13.43%
Winton | CA | 95388-0000 |  | 2013-09-03 | 2013-09-03 12:55 | 2013-09-03 14:18 | AMERICAN STANDARD - YCP036F1M0AC | 109 | 9 | Yes | Yes | 24.6 | 21.4 | 3.2 | 6073BA13DD04493E8617624C6FC70459 |  | R22 | Non-TXV |  | 8.257% | 0.91743 | 15.87% | [5 empty] | Non-TXV | 8.257%
Winton | CA | 95388-0000 |  | 2013-09-03 | 2013-09-03 13:56 | 2013-09-03 14:13 | AMERICAN STANDARD - YCP036F1M0AC | 109 | 3.3 | Yes | Yes | 22.4 | 20.4 | 2 | A2258F1FC2AB447882E2A4A34580FF5E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.028% | 0.96972 | 5.818% | [5 empty] | Non-TXV | 3.028%
Winton | CA | 95388-0000 |  | 2013-11-20 | 2013-11-20 10:11 | 2013-11-20 10:11 | AMERICAN STANDARD - YCP036F1M0AC | 109 | 0 | Yes | Yes | 29.9 | 20.4 | 9.5 | F3789E11E3BF4F6DB129CF21426AB047 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6027 |  | 2013-08-26 | 2013-08-26 13:27 | 2013-08-26 13:48 | ICP - R2A336GKR2 | 83 | 9.4 | Yes | Yes | 24.9 | 19 | 5.9 | 632EBC9EC6FE4AD1AD32AE4C6E225BD4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.33% | 0.88675 | 21.76% | [5 empty] | Non-TXV | 11.33%
Stockton | CA | 95206-6303 |  | 2013-08-26 | 2013-08-26 09:41 | 2013-08-26 09:59 | GOODMAN - CJK30-1D | 85 | 24.8 | Yes | Yes | 24 | 18.2 | 5.8 | F96865984B824ED3BC560113A65665FC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 29.18% | 0.70824 | 56.07% | [5 empty] | Non-TXV | 29.18%
Oakdale | CA | 95361-2716 |  | 2013-08-28 | 2013-08-28 10:37 | 2013-08-28 11:03 | YORK - H1RE036S06H | 150 | 4.5 | Yes | Yes | 19.7 | 18.2 | 1.5 | 19CFB50C8877458B84A6DDE55CD06A75 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-5528 |  | 2013-08-23 | 2013-08-23 11:43 | 2013-08-23 11:45 | AIRE-FLO - UNK | 64 | 9.3 | Yes | Yes | 27.1 | 21.8 | 5.3 | A119A443406347BCB47F5F4C68E77262 |  | R22 | Non-TXV |  | 14.53% | 0.85469 | 27.93% | [5 empty] | Non-TXV | 14.53%
Winton | CA | 95388-9543 |  | 2013-08-27 | 2013-08-27 13:05 | 2013-08-27 13:40 | TRANE - TTR736A100A0 | 116 | 3.5 | Yes | Yes | 20.1 | 19.3 | 0.8 | 40F36B006D55425F8B8A08939C2ED3AA |  | R22 | Non-TXV |  | 3.017% | 0.96983 | 5.798% | [5 empty] | Non-TXV | 3.017%
Winton | CA | 95388-9543 |  | 2013-08-27 | 2013-08-27 13:25 | 2013-08-27 13:53 | TRANE - TTR724B100A0 | 73 | 2.2 | Yes | Yes | 18.7 | 20.2 | -1.5 | DF8934B22FD9468A9B83C7E2C8A6C7F1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Penn Valley | CA | 95946-8824 |  | 2013-09-05 | 2013-09-05 13:12 | 2013-09-05 13:47 | CARRIER - 48SX-036080321AA | 85 | 4 | Yes | Yes | 21 | 18.8 | 2.2 | 8607C7E4B512459B9277A6DAF90FDC46 |  | R22 | TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | TXV | 4.706%
Marysville | CA | 95901-3431 |  | 2013-08-30 | 2013-08-30 11:32 | 2013-08-30 11:50 | CARRIER - N2A336AKB300 | 84 | 3.9 | Yes | Yes | 19.3 | 18.6 | 0.7 | C0C20CA6FB074612AC38E0D4D20A47C8 |  | R22 | TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | TXV | 4.643%
Stockton | CA | 95205-2528 |  | 2013-08-26 | 2013-08-26 09:48 | 2013-08-26 10:01 | TRANE - YCC036F1MOBF | 83 | 4.6 | Yes | Yes | 19.7 | 18.3 | 1.4 | D9ABF3EC0C0A4C7DB598741BBBABAAA6 |  | R22 | Non-TXV |  | 5.542% | 0.94458 | 10.65% | [5 empty] | Non-TXV | 5.542%
Stockton | CA | 95205-2528 |  | 2013-08-26 | 2013-08-26 10:03 | 2013-08-26 10:20 | HEIL - NRGC24MAK02 | 55 | 7.8 | Yes | Yes | 19.6 | 17 | 2.6 | 4DBA69645F5040E7B1EB87549DE6A2B2 |  | R22 | Non-TXV |  | 14.18% | 0.85818 | 27.25% | [5 empty] | Non-TXV | 14.18%
Thornton | CA | 95686-0000 |  | 2013-10-21 | 2013-10-21 14:11 | 2013-10-21 14:54 | AMANA - RCC36A2B | 114 | -4 | Yes | Yes | 18.6 | 19.9 | -1.3 | AB95C6E6CF944E3FAB6F2C1A4C947FDD |  | R22 | TXV |  | -3.509% | 1.0351 | 0.9826% |  |  |  |  | TXV |  |  | -3.509%
Stockton | CA | 95207-6501 |  | 2013-09-13 | 2013-09-13 08:30 | 2013-09-13 08:53 | PAYNE - 567C036RCU | 67 | 3.7 | Yes | Yes | 19 | 17.7 | 1.3 | 88955D85C8684C4CADF077B257C213DF |  | R22 | Non-TXV |  | 5.522% | 0.94478 | 10.61% | [5 empty] | Non-TXV | 5.522%
Stockton | CA | 95209-3000 |  | 2013-08-27 | 2013-08-27 11:27 | 2013-08-27 11:45 | HEIL - GPCM42KO80B | 87 | 5.6 | Yes | Yes | 20.9 | 18.9 | 2 | 8718513DD8044AA29C796E5D8B96E7E1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.437% | 0.93563 | 12.37% | [5 empty] | Non-TXV | 6.437%
Red Bluff | CA | 96080-4141 |  | 2013-08-27 | 2013-08-27 15:33 | 2013-08-27 18:19 | RUUD - UAKB-030JAZ | 66 | 3 | Yes | Yes | 18.9 | 19.4 | -0.5 | 4E292DCF7F324D468BACE2999B4EACB4 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Stockton | CA | 95205-2576 |  | 2013-08-26 | 2013-08-26 09:15 | 2013-08-26 09:15 | CARRIER - 38EZG036--311-- | 99 | 0 | Yes | Yes | 20.7 | 18.6 | 2.1 | ECCB115F383E48F08EC1D1D422E45F5B |  | R410A | TXV |  | 0% | 1 | 0%
Live Oak | CA | 95953-2278 |  | 2013-09-10 | 2013-09-10 13:46 | 2013-09-10 14:26 | DAY & NIGHT - N4A348AKB200 | 112 | 4.3 | Yes | Yes | 20.5 | 19.6 | 0.9 | F64E9D6A29CB47C5AD1D221B93817D44 |  | R410A | TXV |  | 3.839% | 0.96161 | 7.378% | [5 empty] | TXV | 3.839%
Atascadero | CA | 93422-3509 |  | 2013-09-06 | 2013-09-06 11:26 | 2013-09-06 11:45 | PAYNE - 591ANX036000AAAA | 85 | -5 | Yes | Yes | 22.6 | 20.4 | 2.2 | 28C92B29CE4343FDB29331FD24AB1BC8 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Dinuba | CA | 93618-4014 |  | 2013-09-05 | 2013-09-05 17:54 | 2013-09-05 19:02 | RHEEM - N/A | 90 | 4.8 | Yes | Yes | 20 | 18 | 2 | 89563D4BFABD4DA2B93C5F922C905E26 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Penn Valley | CA | 95946-9570 |  | 2013-09-05 | 2013-09-05 11:17 | 2013-09-05 11:46 | HEIL - NRGF48EDB02 | 112 | 3.6 | Yes | Yes | 25 | 20.6 | 4.4 | A8349980513D4FA08036E77C5A5E4022 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Clovis | CA | 93612-5113 |  | 2013-08-26 | 2013-08-26 14:27 | 2013-08-26 16:49 | LENNOX - 10GCS030X-75-3PA | 51 | 4.1 | Yes | Yes | 15.5 | 18 | -2.5 | E7929BC113A843469536CC08F1D97108 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.039% | 0.91961 | 15.45% | [5 empty] | Non-TXV | 8.039%
Stockton | CA | 95202-2509 |  | 2013-08-30 | 2013-08-30 09:09 | 2013-08-30 09:09 | RHEEM - RAKA-030JAZ | 66 | 0 | Yes | Yes | 17.3 | 18.6 | -1.3 | F6483D1B4B6740E59C3866F695F1ECBD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-1355 |  | 2013-08-30 | 2013-08-30 14:31 | 2013-08-30 15:01 | BDP - 585CJ02450 | 72 | 3.3 | Yes | Yes | 24.7 | 21 | 3.7 | B1EB788C15A84C95BE3BFC1A7DC68E08 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Merced | CA | 95340-3157 |  | 2013-08-28 | 2013-08-28 15:34 | 2013-08-28 15:37 | CARRIER - 48SS024040321 | 38 | 2.8 | Yes | Yes | 14.2 | 16.4 | -2.2 | 8C5C9B2140AB4F3CAA547C92F84364E6 |  | R22 | Non-TXV |  | 7.368% | 0.92632 | 14.16% | [5 empty] | Non-TXV | 7.368%
Merced | CA | 95340-3212 |  | 2013-10-07 | 2013-10-07 14:55 | 2013-10-07 14:56 | ICP - PGC036K030B | 71 | 11.1 | Yes | Yes | 19.6 | 17.5 | 2.1 | D55DFF41C3BE49218355D595E5A1CC27 |  | R22 | Non-TXV |  | 15.63% | 0.84366 | 30.04% | [5 empty] | Non-TXV | 15.63%
Stockton | CA | 95205-6337 |  | 2013-08-28 | 2013-08-28 14:54 | 2013-08-28 15:12 | RHEEM - RAHE-036JAS | 91 | -6.4 | Yes | Yes | 19.1 | 19.6 | -0.5 | F5230EF77FD34D11AA3012D45FD35618 |  | R22 | Non-TXV |  | -7.033% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.033%
Oakdale | CA | 95361-8752 |  | 2013-08-28 | 2013-08-28 15:31 | 2013-08-28 15:53 | DAY & NIGHT - 561CJ036-D | 83 | 2.7 | Yes | Yes | 26.1 | 21.3 | 4.8 | 3FA5415EA3C84AEA9AD58CE8E9488665 |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Merced | CA | 95341-5614 |  | 2013-08-29 | 2013-08-29 17:07 | 2013-08-29 17:10 | GOODMAN - GPG1330045M41AC | 80 | 2.7 | Yes | Yes | 24.4 | 19.3 | 5.1 | 3CD8F175C55B435D807CACA90E2CD41C |  | R410A | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Angels Camp | CA | 95222-0000 |  | 2013-09-04 | 2013-09-04 16:35 | 2013-09-04 17:50 | RHEEM - RRKAA030JK06X | 54 | 1.7 | Yes | Yes | 22.9 | 20.4 | 2.5 | B60B165D65604162BBDCC044633C65FA |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Grass Valley | CA | 95945-0000 |  | 2013-08-23 | 2013-08-23 11:09 | 2013-08-23 11:09 | BRYANT - 577DNW030060 | 181 | 0 | Yes | Yes | 22.9 | 20.1 | 2.8 | F1151E1F982442A4B9CB470E51ABBC09 |  | R410A | TXV |  | 0% | 1 | 0%
Atascadero | CA | 93422-1128 |  | 2013-09-06 | 2013-09-06 12:16 | 2013-09-06 12:39 | YORK - H2CB048S06C | 162 | 6.3 | Yes | Yes | 25.7 | 19.9 | 5.8 | 741E3AABB3B947878133CBC6E214CEA7 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Fresno | CA | 93722-5184 |  | 2013-08-28 | 2013-08-28 14:12 | 2013-08-28 14:14 | AIRE-FLO - 48KLA136300BE | 102 | 17.1 | Yes | Yes | 25 | 20.6 | 4.4 | BAEC431719B940479188E1ABEFC53DC3 |  | R22 | Non-TXV |  | 16.76% | 0.83235 | 32.22% | [5 empty] | Non-TXV | 16.76%
Merced | CA | 95340-2754 |  | 2013-08-26 | 2013-08-26 10:11 | 2013-08-26 10:13 | TRANE - 2TWR1048A1000AB | 134 | 6.7 | Yes | Yes | 24 | 18.8 | 5.2 | 3A95C26D8FE3434B87A3EE97AB57C300 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95207-7409 |  | 2013-08-30 | 2013-08-30 12:59 | 2013-08-30 13:17 | OTHER - CE42 | 96 | 5.8 | Yes | Yes | 17.8 | 19.2 | -1.4 | 1A0EC5489398480B9AC3FD36F3B8B040 |  | R22 | Non-TXV |  | 6.042% | 0.93958 | 11.61% | [5 empty] | Non-TXV | 6.042%
Coarsegold | CA | 93614-9749 |  | 2013-09-16 | 2013-09-16 13:36 | 2013-09-16 13:38 | RUUD - 7777UNK | 80 | 4.8 | Yes | Yes | 25.5 | 21.2 | 4.3 | 8BF0EF43C02B43B7950D0AA20520FA45 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Dinuba | CA | 93618-3388 |  | 2013-09-05 | 2013-09-05 17:11 | 2013-09-05 17:53 | LENNOX - 13ACD-042-230-02 | 111 | 8.1 | Yes | Yes | 19 | 20.9 | -1.9 | 2532889DDF994B9985082058D44C9BAD |  | R22 | Non-TXV |  | 7.297% | 0.92703 | 14.02% | [5 empty] | Non-TXV | 7.297%
Tracy | CA | 95376-1956 |  | 2013-09-10 | 2013-09-10 10:38 | 2013-09-10 11:11 | PAYNE - PA10JA036000AAA | 83 | 6 | Yes | Yes | 19 | 18.2 | 0.8 | D8256F01A1F2483E85DD499ABB0F4315 |  | R22 | Non-TXV |  | 7.229% | 0.92771 | 13.89% | [5 empty] | Non-TXV | 7.229%
Fresno | CA | 93726-4308 |  | 2013-09-09 | 2013-09-09 10:47 | 2013-09-09 11:38 | TRANE - TTB036C10A1 | 90 | 2.9 | Yes | Yes | 17.3 | 20.2 | -2.9 | 69664052FC264112BF003A46D2015020 |  | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Merced | CA | 95340-3905 |  | 2013-08-28 | 2013-08-28 16:03 | 2013-08-28 16:07 | TRANE - YCY048G1HOAD | 183 | 36.8 | Yes | Yes | 27.3 | 21.5 | 5.8 | F33E9C11ABF84BC3B211153FAC15DB44 |  | R22 | Non-TXV |  | 20.11% | 0.79891 | 38.65% | [5 empty] | Non-TXV | 20.11%
Coarsegold | CA | 93614-9168 |  | 2013-09-12 | 2013-09-12 13:09 | 2013-09-12 13:11 | BRYANT - 583ANW0300600AAAD | 70 | 3.2 | Yes | Yes | 24.8 | 20.4 | 4.4 | 4329F8C5A4F042B6B862F3CDE38D03F5 |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Atascadero | CA | 93422-2346 |  | 2013-09-03 | 2013-09-03 12:25 | 2013-09-03 12:43 | ARCOAIRE - PGC048K080A | 102 | -6 | Yes | Yes | 16.2 | 16.4 | -0.2 | CAD435E50E1C40E3AA90DD7586B4BE83 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Arbuckle | CA | 95912-0000 |  | 2013-09-17 | 2013-09-17 14:12 | 2013-09-17 14:53 | RUUD - UAKB-042JAZ | 79 | 5.3 | Yes | Yes | 18 | 21 | -3 | 8187FDA2259646DFA45E6C4C4D69CA19 |  | R22 | Non-TXV |  | 6.709% | 0.93291 | 12.89% | [5 empty] | Non-TXV | 6.709%
Stockton | CA | 95210-3127 |  | 2013-08-28 | 2013-08-28 10:14 | 2013-08-28 10:20 | RHEEM - HC-80-24-21C | 49 | 16 | Yes | Yes | 20.1 | 17.4 | 2.7 | 65FA8052547F4E88A6538F4686EA3636 |  | R22 | Non-TXV |  | 32.65% | 0.67347 | 62.75% | [5 empty] | Non-TXV | 32.65%
Oroville | CA | 95966-7032 |  | 2013-08-29 | 2013-08-29 16:18 | 2013-08-29 16:40 | TRANE - YCC018F1LOBH | 60 | -3.5 | Yes | Yes | 23.5 | 21 | 2.5 | B3574916EFD1418A8B43F58887FFFBA3 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93720-1965 |  | 2013-09-06 | 2013-09-06 09:56 | 2013-09-06 10:33 | WEATHER KING - 10AJA4801 | 90 | 10.9 | Yes | Yes | 18.3 | 21.2 | -2.9 | 3EA0975C273646C6BC288A339AF1BC3A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.11% | 0.87889 | 23.27% | [5 empty] | Non-TXV | 12.11%
Tracy | CA | 95377-9266 |  | 2013-08-23 | 2013-08-23 14:02 | 2013-08-23 14:28 | DAY & NIGHT - 591ANX042000ABAA | 112 | 10.5 | Yes | Yes | 18.8 | 19.4 | -0.6 | 8272761E7FEC4CEFB5B55AD3088F6623 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Fresno | CA | 93722-5562 |  | 2013-08-29 | 2013-08-29 10:21 | 2013-08-29 10:23 | CARRIER - 48KLA130321BE | 68 | 7.3 | Yes | Yes | 22.3 | 17.5 | 4.8 | 908C031FDB9946C7867D355C7829DFB4 |  | R22 | Non-TXV |  | 10.74% | 0.89265 | 20.63% | [5 empty] | Non-TXV | 10.74%
Atascadero | CA | 93422-2330 |  | 2013-09-03 | 2013-09-03 13:01 | 2013-09-03 13:19 | PAYNE - PA13NR024-C | 112 | 3.4 | Yes | Yes | 17.6 | 18.6 | -1 | E351C3C512694AEBA9FEB10A237704EB |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Tracy | CA | 95377-8802 |  | 2013-08-23 | 2013-08-23 12:40 | 2013-08-23 13:03 | UNITARY PRODUCTS GROUP - H2RC060S06A | 133 | 11.5 | Yes | Yes | 21.2 | 20.4 | 0.8 | ADF88941577148EE9FD84795924EDEF2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.647% | 0.91353 | 16.62% | [5 empty] | Non-TXV | 8.647%
Fresno | CA | 93722-4691 |  | 2013-08-28 | 2013-08-28 11:54 | 2013-08-28 11:55 | OTHER - GSC130481BB | 102 | 11.2 | Yes | Yes | 23.6 | 23.7 | -0.1 | 5D3BB10EEDF74A1E83339979AAAB959A |  | R22 | Non-TXV |  | 10.98% | 0.8902 | 21.1% | [5 empty] | Non-TXV | 10.98%
Merced | CA | 95340-1621 |  | 2013-08-23 | 2013-08-23 11:58 | 2013-08-23 11:59 | YORK - D1NH042N06506C | 94 | 5.9 | Yes | Yes | 23.9 | 20.1 | 3.8 | 1ECA6A119F664C6899CBED5CF22C094A |  | R22 | Non-TXV |  | 6.277% | 0.93723 | 12.06% | [5 empty] | Non-TXV | 6.277%
Stockton | CA | 95210-3538 |  | 2013-09-05 | 2013-09-05 11:12 | 2013-09-05 11:12 | GOODMAN - GPG13240451AA | 77 | 0 | Yes | Yes | 24 | 18.1 | 5.9 | 465C10E9233B4A94A8267146C9D38D3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-9768 |  | 2013-09-10 | 2013-09-10 09:18 | 2013-09-10 09:18 | AMERICAN STANDARD - YCX042F1M0CA | 123 | 0 | Yes | Yes | 23.6 | 20.1 | 3.5 | F6E3B9C373E34B769EFAF39F140F6C12 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2645 |  | 2013-08-27 | 2013-08-27 13:49 | 2013-08-27 13:51 | CARRIER - 48KLA124-321BE | 68 | 2.9 | Yes | Yes | 17.8 | 19.3 | -1.5 | 90AD51D092B342B6A509A436F33A6706 |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Merced | CA | 95348-2822 |  | 2013-08-30 | 2013-08-30 11:07 | 2013-08-30 11:08 | AIRE-FLO - YCX036F1MOAB | 116 | 13.3 | Yes | Yes | 22.1 | 19.2 | 2.9 | 5B845F154997400483C76383EAAE90C4 |  | R22 | Non-TXV |  | 11.47% | 0.88534 | 22.03% | [5 empty] | Non-TXV | 11.47%
Fresno | CA | 93711-6655 |  | 2013-10-07 | 2013-10-07 15:52 | 2013-10-07 16:14 | CARRIER - 48SDN024040311 | 89 | 2.7 | Yes | Yes | 19.8 | 19.1 | 0.7 | 6010229AC0C042C5AD7A32B73851D14C |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Fresno | CA | 93702-2156 |  | 2013-09-20 | 2013-09-20 15:48 | 2013-09-20 16:12 | YORK - DAYP-F048N080A | 132 | 4.7 | Yes | Yes | 16.7 | 19 | -2.3 | 7E813BA1BA65481683A8BE988CA86D08 |  | R22 | Non-TXV |  | 3.561% | 0.96439 | 6.843% | [5 empty] | Non-TXV | 3.561%
Sanger | CA | 93657-9220 |  | 2013-09-12 | 2013-09-12 16:33 | 2013-09-12 18:06 | RHEEM - RRMA-A036JKO8X | 99 | 5.6 | Yes | Yes | 18.1 | 17.6 | 0.5 | B253C2B7F5E84175A47323A96E89ABF4 |  | R22 | Non-TXV |  | 5.657% | 0.94343 | 10.87% | [5 empty] | Non-TXV | 5.657%
Fresno | CA | 93722-5432 |  | 2013-09-04 | 2013-09-04 14:45 | 2013-09-04 14:47 | OTHER - 7777UNK | 110 | 3.5 | Yes | Yes | 21.9 | 20.4 | 1.5 | F45E91E7DFD1407884C6BA60CDC46908 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Lincoln | CA | 95648-2827 |  | 2013-10-08 | 2013-10-08 15:02 | 2013-10-08 15:21 | YORK - H1RC060S06D | 147 | 5.4 | Yes | Yes | 27 | 21.7 | 5.3 | 620BE21DF6B2491FA7CF0D0CFF995CCD |  | R22 | TXV |  | 3.673% | 0.96327 | 7.06% | [5 empty] | TXV | 3.673%
Tracy | CA | 95376-2125 |  | 2013-08-29 | 2013-08-29 09:15 | 2013-08-29 09:33 | GUARDIAN - TCGD42S41S1HA | 69 | 5.6 | Yes | Yes | 18.2 | 17.3 | 1 | F6165CD55F35426F939EA7EE19C1DEE1 |  | R410A | TXV |  | 8.116% | 0.91884 | 15.6% | [5 empty] | TXV | 8.116%
Fresno | CA | 93711-6654 |  | 2013-08-27 | 2013-08-27 23:07 | 2013-08-27 23:11 | AIRE-FLO - 48KLA118 | 61 | 2.4 | Yes | Yes | 23.2 | 20.1 | 3.1 | CCFB17E9712A46ADB492CA4F71B64F4D |  | R22 | Non-TXV |  | 3.934% | 0.96066 | 7.561% | [5 empty] | Non-TXV | 3.934%
Atascadero | CA | 93422-4273 |  | 2013-09-03 | 2013-09-03 16:00 | 2013-09-03 16:19 | YORK - D1NA024N03606C | 54 | 1.8 | Yes | Yes | 26.4 | 20.4 | 6 | DD3192B2BDE04A03A637889C4BF5093C |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Huron | CA | 93234-0000 |  | 2013-10-11 | 2013-10-11 15:05 | 2013-10-11 15:28 | GOODMAN - GPG1336070M41AC | 85 | 3.3 | Yes | Yes | 26.2 | 20.4 | 5.8 | 0EF83EE37E204CA6AF8A066B25898EEC |  | R410A | TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | TXV | 3.882%
Fresno | CA | 93722-5524 |  | 2013-08-28 | 2013-08-28 13:25 | 2013-08-28 13:28 | AIRE-FLO - RCE48C2A | 156 | 20.2 | Yes | Yes | 23.5 | 18.7 | 4.8 | 1DE001D8586948DC89CB90905824E44A |  | R22 | Non-TXV |  | 12.95% | 0.87051 | 24.88% | [5 empty] | Non-TXV | 12.95%
Red Bluff | CA | 96080-5201 |  | 2013-09-11 | 2013-09-11 17:21 | 2013-09-11 17:38 | DAY & NIGHT - NA | 72 | 7.2 | Yes | Yes | 15.8 | 18.2 | -2.4 | DBB902FBC5D34DD18497CEF43A80142D |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Merced | CA | 95348-0000 |  | 2013-09-06 | 2013-09-06 14:31 | 2013-09-06 14:32 | CARRIER - 38ETG030300 | 133 | 10.8 | Yes | Yes | 21.2 | 20.6 | 0.6 | 61DD9D37C5B04C7FBC83C71866D24DD1 |  | R410A | Non-TXV |  | 8.12% | 0.9188 | 15.61% | [5 empty] | Non-TXV | 8.12%
Stockton | CA | 95205-3414 |  | 2013-08-26 | 2013-08-26 14:16 | 2013-08-26 14:21 | TRANE - SFHA251--LB | 51 | 17.8 | Yes | Yes | 25.9 | 22.4 | 3.5 | 1FBB014787DC4DFE8B8DD98E62E453ED |  | R22 | Non-TXV |  | 34.9% | 0.65098 | 67.07% | [5 empty] | Non-TXV | 34.9%
Atascadero | CA | 93422-0000 |  | 2013-09-03 | 2013-09-03 15:12 | 2013-09-03 15:30 | NORDYNE - NS4BD-030KB | 56 | 2.1 | Yes | Yes | 22.4 | 17.5 | 4.9 | EA528E7392564FB1AE951C558751404B |  | R410A | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95207-4837 |  | 2013-09-12 | 2013-09-12 16:36 | 2013-09-12 16:59 | TRANE - 2YCX3030A1064AA | 88 | 5.8 | Yes | Yes | 21.2 | 17.9 | 3.4 | FBC49F13FACA491BA9BB874153A1B706 |  | R22 | Non-TXV |  | 6.591% | 0.93409 | 12.67% | [5 empty] | Non-TXV | 6.591%
Madera | CA | 93638-1620 |  | 2013-09-09 | 2013-09-09 13:09 | 2013-09-09 13:11 | AMANA - PGA36B0702C | 112 | 23.5 | Yes | Yes | 22.1 | 19 | 3.1 | 7C318058E3154C9E8C650C26625E002B |  | R22 | Non-TXV |  | 20.98% | 0.79018 | 40.32% | [5 empty] | Non-TXV | 20.98%
Paso Robles | CA | 93446-2873 |  | 2013-09-05 | 2013-09-05 12:49 | 2013-09-05 13:08 | CARRIER - 38EA018300 | 48 | 2.3 | Yes | Yes | 15.9 | 18.6 | -2.7 | CDA23DFA581141A1A0C59529CF97551C |  | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Paso Robles | CA | 93446-3489 |  | 2013-09-04 | 2013-09-04 16:03 | 2013-09-04 16:22 | LENNOX - 13ACD-036-230-02 | 111 | 3.6 | Yes | Yes | 18.8 | 18.9 | 0 | 2945F65EB7064DBA8305B7803F0F9F0E |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Paso Robles | CA | 93446-3405 |  | 2013-09-05 | 2013-09-05 10:50 | 2013-09-05 11:06 | TRANE - 4TTB3060D1000AA | 128 | -7.5 | Yes | Yes | 21 | 18.8 | 2.2 | FD277F4386DF41BFA13A2EF1F06074B1 |  | R410A | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Stockton | CA | 95206-6452 |  | 2013-09-04 | 2013-09-04 08:39 | 2013-09-04 08:58 | GOODMAN - CKL42-1B | 115 | 16.5 | Yes | Yes | 16.5 | 19.1 | -2.6 | 3E5C330DC2F442F6A64F30F7E2D7A052 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.35% | 0.85652 | 27.57% | [5 empty] | Non-TXV | 14.35%
Fresno | CA | 93702-3520 |  | 2013-09-19 | 2013-09-19 14:01 | 2013-09-19 14:02 | GOODMAN - PGB0300501 | 56 | 7 | Yes | Yes | 28.6 | 22.6 | 6 | D0B25D8AF11246FC95B9F52C517F9CEC |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Lathrop | CA | 95330-8882 |  | 2013-10-11 | 2013-10-11 12:21 | 2013-10-11 12:28 | CARRIER - 38ETG048300 | 152 | 10.6 | Yes | Yes | 21.1 | 18.8 | 2.3 | F0034E859A62452FB1AB1CAC96B68ACF |  | R22 | Non-TXV |  | 6.974% | 0.93026 | 13.4% | [5 empty] | Non-TXV | 6.974%
Paso Robles | CA | 93446-4829 |  | 2013-09-04 | 2013-09-04 16:33 | 2013-09-04 16:51 | BDP - 561AJ036-D | 74 | -4.4 | Yes | Yes | 24.3 | 19.5 | 4.8 | 55D2326E6F1C4CBEAE4C2A6E44671721 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Paso Robles | CA | 93446-3211 |  | 2013-09-04 | 2013-09-04 17:05 | 2013-09-04 17:23 | RHEEM - RRNA-B036JK06X | 83 | -5.9 | Yes | Yes | 24.6 | 18.6 | 6 | 5F8DAF332646433E85D3F22914AAB25A |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Stockton | CA | 95204-4260 |  | 2013-09-09 | 2013-09-09 08:31 | 2013-09-09 08:49 | ICP - PGC036K060E | 71 | -5 | Yes | Yes | 24 | 18.2 | 5.8 | 3BF3371DD219441BB8B4AFD47D506712 |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Manteca | CA | 95336-2956 |  | 2013-10-07 | 2013-10-07 10:23 | 2013-10-07 10:46 | WESTINGHOUSE - FS3BD-030K | 114 | 3.5 | Yes | Yes | 21.2 | 19.3 | 1.9 | C77A89C012BD4C11B731733B8146F9CA |  | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
Rocklin | CA | 95765-5841 |  | 2013-08-27 | 2013-08-27 15:33 | 2013-08-27 16:00 | GOODMAN - CKJ36-1AB | 97 | 8.2 | Yes | Yes | 17 | 19.9 | -2.9 | 86831FBEA4174E60A7A4D1ABD924057B |  | R22 | TXV |  | 8.454% | 0.91546 | 16.25% | [5 empty] | TXV | 8.454%
Rocklin | CA | 95765-5841 |  | 2013-08-27 | 2013-08-27 15:49 | 2013-08-27 16:04 | GOODMAN - CKJ36-1AB | 97 | 3.7 | Yes | Yes | 18 | 21 | -3 | 47B97B1BD59B474AAB77D7A472AD4DCF |  | R22 | TXV |  | 3.814% | 0.96186 | 7.331% | [5 empty] | TXV | 3.814%
Los Banos | CA | 93635-9490 |  | 2013-09-10 | 2013-09-10 12:12 | 2013-09-10 12:14 | BRYANT - 561CJ048-G | 100 | 4.5 | Yes | Yes | 19.9 | 21 | -1.1 | 94F854C969544FA18FE6CE725328A00B |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Stockton | CA | 95206-4669 |  | 2013-11-01 | 2013-11-01 11:19 | 2013-11-01 11:38 | BDP - 561AJ042-D | 80 | -4.7 | Yes | Yes | 20.3 | 18.2 | 2.1 | 5A6D911F7F7E42568A6913C93BBCA458 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Oroville | CA | 95965-4112 |  | 2013-08-28 | 2013-08-28 10:23 | 2013-08-28 11:24 | AMANA - PGB36C0702E | 64 | 5.5 | Yes | Yes | 17.1 | 19.9 | -2.8 | 3D09BEEE4D50444F83305E2C46B67152 |  | R22 | Non-TXV |  | 8.594% | 0.91406 | 16.52% | [5 empty] | Non-TXV | 8.594%
Fresno | CA | 93722-4694 |  | 2013-08-28 | 2013-08-28 13:00 | 2013-08-28 13:01 | YORK - H2RC048S06HA | 119 | 22.3 | Yes | Yes | 23.6 | 22.8 | 0.8 | 720B078CC5DF458A80E075F06A087EC7 |  | R22 | Non-TXV |  | 18.74% | 0.81261 | 36.01% | [5 empty] | Non-TXV | 18.74%
Stockton | CA | 95209-2316 |  | 2013-09-25 | 2013-09-25 11:06 | 2013-09-25 11:28 | LENNOX - HS29-036-1P | 73 | -4.3 | Yes | Yes | 22.7 | 18.7 | 4 | C332DFBB4E0C4DE6A34DD602784BA46C |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Stockton | CA | 95204-4615 |  | 2013-08-28 | 2013-08-28 16:07 | 2013-08-28 16:18 | YORK - D1NP048N09006A | 132 | 15.5 | Yes | Yes | 27.5 | 22.1 | 5.5 | 76D89760A6DA4688B763E7063DC45C84 |  | R22 | Non-TXV |  | 11.74% | 0.88258 | 22.57% | [5 empty] | Non-TXV | 11.74%
Merced | CA | 95348-3609 |  | 2013-08-29 | 2013-08-29 15:40 | 2013-08-29 15:41 | GOODMAN - CK301T | 76 | 10.1 | Yes | Yes | 28.9 | 23.7 | 5.2 | 71A7FB0C646644D78C0CD80C0128DBF7 |  | R22 | Non-TXV |  | 13.29% | 0.86711 | 25.54% | [5 empty] | Non-TXV | 13.29%
Fresno | CA | 93728-2035 |  | 2013-10-02 | 2013-10-02 10:41 | 2013-10-02 10:42 | GOODMAN - GPG10300701A | 50 | 3.4 | Yes | Yes | 24.5 | 19.1 | 5.4 | 7A39CE0D2C1D41BF82253D872D9FB304 |  | R22 | Non-TXV |  | 6.8% | 0.932 | 13.07% | [5 empty] | Non-TXV | 6.8%
Stockton | CA | 95207-3119 |  | 2013-08-30 | 2013-08-30 10:54 | 2013-08-30 11:13 | BRYANT - 165ANA030-B | 176 | 10.1 | Yes | Yes | 19.5 | 20 | -0.4 | 9A710E0C3BA04FB89955503DB1316C9F |  | R410A | TXV |  | 5.739% | 0.94261 | 11.03% | [5 empty] | TXV | 5.739%
Fresno | CA | 93727-3572 |  | 2013-09-11 | 2013-09-11 10:11 | 2013-09-11 10:13 | PAYNE - 585HJ036060 | 102 | 3.5 | Yes | Yes | 17.7 | 17.1 | 0.6 | 10C027225521423898DC10F32D719564 |  | R22 | Non-TXV |  | 3.431% | 0.96569 | 6.594% | [5 empty] | Non-TXV | 3.431%
Penn Valley | CA | 95946-8948 |  | 2013-09-18 | 2013-09-18 13:04 | 2013-09-18 13:23 | TRANE - TTB036C100A1 | 90 | 8.6 | Yes | Yes | 20.6 | 20.6 | 0 | 7CD155E4F28F4E63A237E6C96A7B0E94 |  | R22 | Non-TXV |  | 9.556% | 0.90444 | 18.36% | [5 empty] | Non-TXV | 9.556%
Stockton | CA | 95210-1139 |  | 2013-08-28 | 2013-08-28 10:42 | 2013-08-28 10:42 | OTHER - TZAL-336-2C | 90 | 0 | Yes | Yes | 18.7 | 18.5 | 0.2 | F72F8E8AED534B5FBC2F8B66868C4BBE |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1913 |  | 2013-08-29 | 2013-08-29 11:42 | 2013-08-29 11:43 | CARRIER - 38GS018340 | 58 | 11.1 | Yes | Yes | 26.4 | 21.7 | 4.7 | 35D1B01229944DAA98B3EACC62BA0609 |  | R22 | Non-TXV |  | 19.14% | 0.80862 | 36.78% | [5 empty] | Non-TXV | 19.14%
Stockton | CA | 95210-5334 |  | 2013-09-05 | 2013-09-05 08:59 | 2013-09-05 09:03 | PAYNE - PA13NR024-J | 65 | 6.1 | Yes | Yes | 18.6 | 18.6 | 0 | 5107EA0558D54DCFB09B4E6524F2B78B |  | R22 | Non-TXV |  | 9.385% | 0.90615 | 18.04% | [5 empty] | Non-TXV | 9.385%
Paso Robles | CA | 93446-4634 |  | 2013-09-04 | 2013-09-04 14:41 | 2013-09-04 15:01 | RHEEM - RAHE-036JAS | 91 | 11.8 | Yes | Yes | 18.1 | 19.2 | -1.1 | ADD49255379140E9943B4506246A9F80 |  | R22 | Non-TXV |  | 12.97% | 0.87033 | 24.92% | [5 empty] | Non-TXV | 12.97%
Stockton | CA | 95210-5218 |  | 2013-08-28 | 2013-08-28 08:21 | 2013-08-28 08:41 | PAYNE - PA13NR018-E | 68 | -4.4 | Yes | Yes | 21.6 | 18.7 | 2.9 | 24330223CC674F2B83A62547F242DBA5 |  | R22 | TXV |  | -6.471% | 1.0647 | 1.812% |  |  |  |  | TXV |  |  | -6.471%
Grass Valley | CA | 95945-8512 |  | 2013-09-17 | 2013-09-17 06:18 | 2013-09-17 06:39 | RHEEM - UNK | 89 | 10.5 | Yes | Yes | 21 | 23.1 | -2.1 | 103C88DE15534DB59DB01B6A9F0FF500 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.8% | 0.88202 | 22.67% | [5 empty] | Non-TXV | 11.8%
Lathrop | CA | 95330-8882 |  | 2013-09-27 | 2013-09-27 12:17 | 2013-09-27 14:17 | CARRIER - 38ETG048300 | 149 | 4.5 | Yes | Yes | 25.5 | 22 | 3.5 | D1D35903C4754B5D8C2BFA2EA493782F |  | R410A | Non-TXV |  | 3.02% | 0.9698 | 5.804% | [5 empty] | Non-TXV | 3.02%
Paso Robles | CA | 93446-3014 |  | 2013-09-05 | 2013-09-05 10:13 | 2013-09-05 10:33 | YORK - H4DB036S06A | 73 | -4.3 | Yes | Yes | 17 | 18.2 | -1.2 | 6F2CBF370AE24776AC3C201045E291C2 |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Stockton | CA | 95205-7850 |  | 2013-09-09 | 2013-09-09 09:49 | 2013-09-09 10:17 | AMERICAN STANDARD - 4YCY4036A1075AA | 108 | 7 | Yes | Yes | 17.2 | 19.4 | -2.2 | ECB6DDF52D8D414FA32FBF16D34A0610 |  | R410A | TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | TXV | 6.481%
Stockton | CA | 95205-7062 |  | 2013-09-10 | 2013-09-10 09:34 | 2013-09-10 09:54 | GUARDIAN - PGB030050-1A | 56 | 2.3 | Yes | Yes | 16.2 | 18.2 | -2 | 1DD74F67DC6B47E4A43D7225F26F1A25 |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
French Camp | CA | 95231-9794 |  | 2013-09-13 | 2013-09-13 08:37 | 2013-09-13 08:52 | AMANA - PGD36C0902E | 110 | -10.4 | Yes | Yes | 24.5 | 18.7 | 5.8 | 2B172669A1794245AB1D1AEDB08D638A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Winton | CA | 95388-9250 |  | 2013-09-09 | 2013-09-09 12:42 | 2013-09-09 13:05 | GOODMAN - PGB030050-1 | 56 | 2.2 | Yes | Yes | 22.5 | 22.7 | -0.2 | 67D62DE873AE47E3941363F1E1CA8829 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Farmington | CA | 95230-0000 |  | 2013-10-02 | 2013-10-02 17:52 | 2013-10-02 18:32 | NORDYNE - R6GF-X48K120X | 240 | 19.2 | Yes | Yes | 23.6 | 20.3 | 3.3 | 64F63953CB6F4824BDF86A4FDAD19F8F |  | R410A | TXV |  | 8% | 0.92 | 15.37% | [5 empty] | TXV | 8%
Tracy | CA | 95377-8225 |  | 2013-09-10 | 2013-09-10 14:01 | 2013-09-10 14:01 | DAY & NIGHT - 598WN036-A | 184 | 0 | Yes | Yes | 26.4 | 20.4 | 6 | 3AFAEC8916AC411F9EFC63F0968508EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5025 |  | 2013-08-29 | 2013-08-29 15:21 | 2013-08-29 16:45 | YORK - D1NP030N05606A | 73 | 4.2 | Yes | Yes | 19 | 21.2 | -2.2 | 9AE4B5F1C3E94DAC8EDD1AFF6647A396 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.753% | 0.94247 | 11.06% | [5 empty] | Non-TXV | 5.753%
Fresno | CA | 93711-2839 |  | 2013-08-28 | 2013-08-28 11:01 | 2013-08-28 11:02 | OTHER - AC100OH2 | 67 | 7.5 | Yes | Yes | 23.3 | 20.4 | 2.9 | 036A675CFE9F4C6BBB5DB7F1CAEAD205 |  | R22 | Non-TXV |  | 11.19% | 0.88806 | 21.51% | [5 empty] | Non-TXV | 11.19%
Kingsburg | CA | 93631-2809 |  | 2013-09-11 | 2013-09-11 17:37 | 2013-09-11 18:11 | LENNOX - 12ACB60-4P | 173 | 12.2 | Yes | Yes | 19.3 | 15.9 | 3.5 | 8A35A97A810B46F1A12177AD170A63EF |  | R22 | Non-TXV |  | 7.052% | 0.92948 | 13.55% | [5 empty] | Non-TXV | 7.052%
Pinedale | CA | 93650-1061 |  | 2013-09-03 | 2013-09-03 11:55 | 2013-09-03 11:57 | RHEEM - RRNLB024JK06X | 77 | 3.2 | Yes | Yes | 22.4 | 19.7 | 2.7 | EC87FEC423C841D59C6E1413342B5650 |  | R410A | Non-TXV |  | 4.156% | 0.95844 | 7.987% | [5 empty] | Non-TXV | 4.156%
Stockton | CA | 95215-6706 |  | 2013-08-29 | 2013-08-29 18:20 | 2013-08-29 18:42 | YORK - D1NA030N03606C | 76 | 3.9 | Yes | Yes | 23.4 | 19.6 | 3.8 | 54AA93AD933E47C99208D191C09B4CD3 |  | R22 | Non-TXV |  | 5.132% | 0.94868 | 9.862% | [5 empty] | Non-TXV | 5.132%
Fresno | CA | 93723-9286 |  | 2013-09-04 | 2013-09-04 11:29 | 2013-09-04 11:31 | LENNOX - HS22-411U-3P | 129 | 4 | Yes | Yes | 22.2 | 20.6 | 1.6 | 66FAB85E5F904A55BDBF583CF7E682FB |  | R22 | Non-TXV |  | 3.101% | 0.96899 | 5.959% | [5 empty] | Non-TXV | 3.101%
Stockton | CA | 95205-2738 |  | 2013-09-10 | 2013-09-10 08:14 | 2013-09-10 08:34 | WEATHER KING - 13AJA48A01 | 123 | -7.2 | Yes | Yes | 24.8 | 18.8 | 6 | 6EA97B047B5A48A6AA0B6B201851EEFD |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Merced | CA | 95341-5716 |  | 2013-08-28 | 2013-08-28 16:37 | 2013-08-28 16:39 | GOODMAN - PGB0420751A | 68 | 15.8 | Yes | Yes | 20.7 | 19.3 | 1.4 | D8A97505DE7F4770BDAE9414CFAF0F9E |  | R22 | Non-TXV |  | 23.24% | 0.76765 | 44.65% | [5 empty] | Non-TXV | 23.24%
Fresno | CA | 93705-1858 |  | 2013-10-07 | 2013-10-07 15:19 | 2013-10-07 15:39 | YORK - D1NAA036NO5606C | 77 | 3.4 | Yes | Yes | 20 | 19.1 | 0.9 | 11012EB25530482B8E03F5CD7E18EB72 |  | R22 | Non-TXV |  | 4.416% | 0.95584 | 8.486% | [5 empty] | Non-TXV | 4.416%
Paso Robles | CA | 93446-3416 |  | 2013-09-05 | 2013-09-05 08:33 | 2013-09-05 08:55 | PAYNE - 42RAC-158K | 91 | -5.4 | Yes | Yes | 21.4 | 19.4 | 2 | 59966126FEEA411890CA6814B84C0DC1 |  | R22 | Non-TXV |  | -5.934% | 1.0593 | 1.662% |  |  |  |  | Non-TXV |  |  | -5.934%
Templeton | CA | 93465-5127 |  | 2013-09-05 | 2013-09-05 16:52 | 2013-09-05 17:11 | NORDYNE - R4GA-030K045X | 65 | 2.1 | Yes | Yes | 23.6 | 21 | 2.6 | 791AA3474D034810875E7F89135E0E72 |  | R22 | Non-TXV |  | 3.231% | 0.96769 | 6.209% | [5 empty] | Non-TXV | 3.231%
Corning | CA | 96021-0000 |  | 2013-10-25 | 2013-10-25 14:29 | 2013-10-25 15:07 | INTERTHERM - NA | 95 | 4.1 | Yes | Yes | 21.4 | 19.4 | 2 | 909FE064EBFD48C8B33B5EFD7E064080 |  | R22 | Non-TXV |  | 4.316% | 0.95684 | 8.294% | [5 empty] | Non-TXV | 4.316%
Oakdale | CA | 95361-2530 |  | 2013-09-11 | 2013-09-11 10:19 | 2013-09-11 10:47 | TRANE - YCY036G1H0AD | 130 | 3.9 | Yes | Yes | 17.2 | 17.7 | -0.5 | 90180141238543B7AB04291CDA85E4FE |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Atwater | CA | 95301-3058 |  | 2013-09-10 | 2013-09-10 12:01 | 2013-09-10 12:32 | KENMORE - PGC030K060ALLLLLLLLLLLLLLLLLLL010S 20085 | 52 | 2.9 | Yes | Yes | 22.8 | 20.4 | 2.4 | F9E17D6138FE4D75950F26CA09867437 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Manteca | CA | 95337-8586 |  | 2013-09-04 | 2013-09-04 13:28 | 2013-09-04 13:55 | BRYANT - 563CN30-C | 99 | 3 | Yes | Yes | 18.6 | 19.5 | -0.9 | 29AF9612D06F4CD8A4F2A854F4036759 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Oroville | CA | 95966-9651 |  | 2013-08-29 | 2013-08-29 14:00 | 2013-08-29 14:33 | TEMPSTAR - T2A342GKA100 | 133 | 4.9 | Yes | Yes | 23.1 | 20.6 | 2.5 | 4D4DB02F192547E38348C558116973BF |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Grass Valley | CA | 95949-7353 |  | 2013-09-05 | 2013-09-05 17:42 | 2013-09-05 18:15 | BRYANT - 574BNW042090NB-- | 171 | -6.4 | Yes | Yes | 21.1 | 20.2 | 0.9 | 7BAC50C481C449BAA55323B1EE4310A8 |  | R410A | TXV |  | -3.743% | 1.0374 | 1.048% |  |  |  |  | TXV |  |  | -3.743%
Loomis | CA | 95650-8793 |  | 2013-10-10 | 2013-10-10 14:07 | 2013-10-10 14:24 | PAYNE - PA12NA036-B | 97 | 4.5 | Yes | Yes | 23 | 20.6 | 2.4 | C45DE718CFCD4F488DF8B0AB3E5827FE |  | R22 | Non-TXV |  | 4.639% | 0.95361 | 8.915% | [5 empty] | Non-TXV | 4.639%
Oroville | CA | 95966-6607 |  | 2013-08-28 | 2013-08-28 16:32 | 2013-08-28 22:00 | TRANE - YCYO3061M0AA | 120 | 7.1 | Yes | Yes | 26.5 | 22.3 | 4.2 | C2D94803CEBA44CBA3251C109911F591 |  | R22 | Non-TXV |  | 5.917% | 0.94083 | 11.37% | [5 empty] | Non-TXV | 5.917%
Manteca | CA | 95336-2614 |  | 2013-08-30 | 2013-08-30 16:02 | 2013-08-30 16:19 | AMERICAN STANDARD - 7A2060A100A2 | 85 | 3.2 | Yes | Yes | 18.5 | 19.3 | -0.8 | DC3472F1E06F40A48FEB68C7C69D5BCC | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | TXV | 3.765%
Lathrop | CA | 95330-9702 |  | 2013-09-19 | 2013-09-19 11:26 | 2013-09-19 11:45 | OTHER - BRCQO48B | 81 | 8 | Yes | Yes | 24.3 | 20.2 | 4.2 | 61A677D9E95740BD99DA23DD16A552DF |  | R22 | Non-TXV |  | 9.877% | 0.90123 | 18.98% | [5 empty] | Non-TXV | 9.877%
Tracy | CA | 95304-5865 |  | 2013-09-10 | 2013-09-10 09:55 | 2013-09-10 10:15 | YORK - H4DE030S06A | 122 | 5.5 | Yes | Yes | 20 | 18.7 | 1.3 | EB58D59CE0A64C2EBF435C3C43B290DC |  | R22 | Non-TXV |  | 4.508% | 0.95492 | 8.664% | [5 empty] | Non-TXV | 4.508%
Paso Robles | CA | 93446-1633 |  | 2013-10-08 | 2013-10-08 15:59 | 2013-10-08 16:19 | CARRIER - 38EA018300 | 32 | 10.5 | Yes | Yes | 22.6 | 19.3 | 3.3 | 54FB619916764C5F871C1060B78DF9A8 |  | R22 | Non-TXV |  | 32.81% | 0.67188 | 63.06% | [5 empty] | Non-TXV | 32.81%
Los Banos | CA | 93635-6373 |  | 2013-09-11 | 2013-09-11 07:34 | 2013-09-11 07:36 | LENNOX - 10GCS042-75 | 73 | 2.7 | Yes | Yes | 24.7 | 19.5 | 5.2 | 03090D288FB243BD858AAFABE06B997E |  | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Fresno | CA | 93722-2519 |  | 2013-10-02 | 2013-10-02 07:52 | 2013-10-02 07:53 | BRYANT - 561EJ030-A | 76 | 2.4 | Yes | Yes | 25.5 | 19.6 | 5.9 | 14BDEF992C4C4262BE146E31A91BDA0A |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Tracy | CA | 95376-3122 |  | 2013-09-10 | 2013-09-10 12:26 | 2013-09-10 12:46 | YORK - TCGD48S21S2HA | 69 | 2.4 | Yes | Yes | 21.9 | 21 | 1 | 1AE02243C56F477FB61F78BA2991FDD3 |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Lathrop | CA | 95330-9632 |  | 2013-09-13 | 2013-09-13 10:18 | 2013-09-13 10:41 | RUUD - UAFD-0361JAS | 80 | 2.9 | Yes | Yes | 18.5 | 17 | 1.5 | 73B3873F85F84EDCA035B017E4C38792 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Madera | CA | 93638-2115 |  | 2013-09-09 | 2013-09-09 09:43 | 2013-09-09 09:44 | GOODMAN - GPG1336070M41BA | 70 | 3.5 | Yes | Yes | 21 | 17.7 | 3.3 | 104E64F04B1844E4B78F23B2E54F1144 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95207-3604 |  | 2013-09-06 | 2013-09-06 10:34 | 2013-09-06 10:34 | GE - BTN930A100A0 | 150 | 0 | Yes | Yes | 19.6 | 18.3 | 1.4 | 7340C3E9732949EB9B5C50BF500B371C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95965-0000 |  | 2013-08-28 | 2013-08-28 11:26 | 2013-08-28 12:21 | TRANE - 2TTB03036A1000AA | 101 | 8.2 | Yes | Yes | 20.8 | 18.9 | 1.9 | 7D9F6C1D1CD7419F96D9BC09942A8688 |  | R22 | Non-TXV |  | 8.119% | 0.91881 | 15.6% | [5 empty] | Non-TXV | 8.119%
Lathrop | CA | 95330-9692 |  | 2013-09-13 | 2013-09-13 09:39 | 2013-09-13 10:00 | DAY & NIGHT - 591ANX030000ABAA | 85 | 12.6 | Yes | Yes | 20 | 19.3 | 0.7 | 9C1E23B449954EDEBC8AA954102FBD97 |  | R22 | Non-TXV |  | 14.82% | 0.85176 | 28.49% | [5 empty] | Non-TXV | 14.82%
Los Banos | CA | 93635-8557 |  | 2013-09-23 | 2013-09-23 09:30 | 2013-09-23 09:42 | AMERICAN STANDARD - 2A7B3048A1000AA | 142 | 17.4 | Yes | Yes | 21.7 | 17.2 | 4.5 | 64B75B1EC3204EA0A459374D30AAC21C |  | R22 | Non-TXV |  | 12.25% | 0.87746 | 23.55% | [5 empty] | Non-TXV | 12.25%
Los Banos | CA | 93635-3076 |  | 2013-09-09 | 2013-09-09 11:53 | 2013-09-09 11:56 | BRYANT - 563CN024-D | 84 | 2.8 | Yes | Yes | 17.7 | 20.6 | -2.9 | 093ECA3044544AC49B5B1D4272584F99 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93710-6348 |  | 2013-09-06 | 2013-09-06 14:59 | 2013-09-06 15:47 | GOODMAN - GPG133600701AC | 112 | 6.1 | Yes | Yes | 17.6 | 20.3 | -2.7 | 4247C42C70694FDB82BB855062F164C8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.446% | 0.94554 | 10.47% | [5 empty] | Non-TXV | 5.446%
Fresno | CA | 93722-5296 |  | 2013-09-11 | 2013-09-11 10:47 | 2013-09-11 10:50 | RHEEM - RRPL-B030JK06X | 77 | 2.6 | Yes | Yes | 17.7 | 19.2 | -1.5 | 34EBDCBF6698441E9503F72192131795 |  | R410A | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Menlo Park | CA | 94025-5921 |  | 2013-10-21 | 2013-10-21 13:56 | 2013-10-21 14:24 | BRYANT - 561CJX024D | 55 | 2.1 | Yes | Yes | 16.8 | 17.7 | -0.9 | 764641592CED4F6FBC8A1DBBE590C8F1 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Stockton | CA | 95207-3519 |  | 2013-09-06 | 2013-09-06 11:14 | 2013-09-06 11:14 | DAY & NIGHT - N4A336AKB200 | 84 | 0 | Yes | Yes | 21.7 | 18.4 | 3.3 | 28571DABA3204A33A56C908EFE971A51 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1237 |  | 2013-09-12 | 2013-09-12 10:26 | 2013-09-12 10:43 | DAY & NIGHT - UNK | 53 | 1.6 | Yes | Yes | 20.1 | 18.1 | 2 | 81AA1287ACD94DE8A28AB6C08123EF1A |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Los Banos | CA | 93635-3022 |  | 2013-09-10 | 2013-09-10 08:07 | 2013-09-10 08:10 | YORK - H1DA036S06A | 92 | 2.9 | Yes | Yes | 26.2 | 21.3 | 4.9 | 3A8957AF05E74B5FA6D521CD22FE3031 |  | R22 | Non-TXV |  | 3.152% | 0.96848 | 6.058% | [5 empty] | Non-TXV | 3.152%
Kingsburg | CA | 93631-2634 |  | 2013-09-11 | 2013-09-11 15:16 | 2013-09-11 15:36 | RUUD - URKA0A030JK06E | 54 | 5.5 | Yes | Yes | 19 | 18.9 | 0.1 | C7F712767EC94FBCB231B16DEADE2D20 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.19% | 0.89815 | 19.57% | [5 empty] | Non-TXV | 10.19%
Nevada City | CA | 95959-8544 |  | 2013-09-24 | 2013-09-24 10:58 | 2013-09-24 10:58 | ICP - PGD336060K001C1 | 102 | 0 | Yes | Yes | 25.1 | 19.9 | 5.2 | 9F1BCB8E0B464E9E9C26C442B69C7EAC |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2639 |  | 2013-09-09 | 2013-09-09 09:47 | 2013-09-09 10:45 | GOODMAN - GPG13240451BA | 77 | 2.9 | Yes | Yes | 22 | 20.6 | 1.5 | F01CABDD10F245FCBBE153270559953B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.766% | 0.96234 | 7.238% | [5 empty] | Non-TXV | 3.766%
Arnold | CA | 95223-0000 |  | 2013-09-12 | 2013-09-12 11:20 | 2013-09-12 11:39 | GOODMAN - CK4918 | 97 | -6.8 | Yes | Yes | 21.5 | 19.1 | 2.5 | 2939F1953C074573917F6ADADEFEF86F |  | R22 | Non-TXV |  | -7.01% | 1.0701 | 1.963% |  |  |  |  | Non-TXV |  |  | -7.01%
Los Banos | CA | 93635-3022 |  | 2013-09-10 | 2013-09-10 08:02 | 2013-09-10 08:05 | RHEEM - RAKA-048JAZ | 103 | 3.5 | Yes | Yes | 22.6 | 18.5 | 4.1 | 6337E45F6FEF4BAF844F1CBDB6985C2D |  | R22 | Non-TXV |  | 3.398% | 0.96602 | 6.53% | [5 empty] | Non-TXV | 3.398%
Fresno | CA | 93722-3530 |  | 2013-09-10 | 2013-09-10 13:18 | 2013-09-10 13:19 | YORK - H1CB042S06A | 94 | 10.6 | Yes | Yes | 21.1 | 21.5 | -0.4 | 0BD7926D30C24172A8FDFCD72102505A |  | R22 | Non-TXV |  | 11.28% | 0.88723 | 21.67% | [5 empty] | Non-TXV | 11.28%
Stockton | CA | 95206-3040 |  | 2013-09-11 | 2013-09-11 09:28 | 2013-09-11 09:48 | RHEEM - UNK | 85 | 3.9 | Yes | Yes | 16.4 | 17.7 | -1.3 | 8932A30180ED4F85A6F3427E8DB2662C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Clovis | CA | 93612-4737 |  | 2013-10-09 | 2013-10-09 16:19 | 2013-10-09 16:39 | ARCOAIRE - PGF024K040A | 58 | 3.2 | Yes | Yes | 20.6 | 17.7 | 2.9 | 8EAA433E7A554FE3B1979AD417B92594 |  | R22 | Non-TXV |  | 5.517% | 0.94483 | 10.6% | [5 empty] | Non-TXV | 5.517%
Pinedale | CA | 93650-1061 |  | 2013-09-03 | 2013-09-03 12:01 | 2013-09-03 12:02 | GOODMAN - GPG13300701AC | 77 | 9.9 | Yes | Yes | 22.7 | 19.8 | 2.9 | 7227B882DC154EDF9F71300DF8CE9DC6 |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Sanger | CA | 93657-2252 |  | 2013-09-10 | 2013-09-10 12:51 | 2013-09-10 13:18 | CARRIER - 48SX-036080311AA | 84 | 4.5 | Yes | Yes | 17.5 | 20.2 | -2.7 | 02CCB8A81E684D7FB08220FAAE821B80 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Magalia | CA | 95954-9107 |  | 2013-08-29 | 2013-08-29 11:03 | 2013-08-29 11:03 | CARRIER - 38RQ046300 | 164 | 0 | Yes | Yes | 18.6 | 19.9 | -1.3 | 6800A6433FCB403BBE8C5C2DC6D33293 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-2793 |  | 2013-09-10 | 2013-09-10 16:57 | 2013-09-10 17:31 | YORK - H2RD042S06B | 141 | 4.1 | Yes | Yes | 24.1 | 21.2 | 2.9 | 0B9D20385B8A4646B2B70A5B76B36577 |  | R22 | Non-TXV |  | 2.908% | 0.97092 | 5.588% | [5 empty] | Non-TXV | 2.908%
Fresno | CA | 93722-6044 |  | 2013-10-08 | 2013-10-08 10:39 | 2013-10-08 11:02 | GOODMAN - PGB024050-1 | 54 | 12.1 | Yes | Yes | 17.4 | 20.4 | -3 | F56F911EA35B4D3ABC2974C134801654 |  | R22 | Non-TXV |  | 22.41% | 0.77593 | 43.06% | [5 empty] | Non-TXV | 22.41%
Sanger | CA | 93657-2253 |  | 2013-09-12 | 2013-09-12 14:30 | 2013-09-12 14:54 | TAPPAN - N/A | 90 | 5.1 | Yes | Yes | 19.3 | 19.1 | 0.2 | 7F828C2C1F514FB19CF66F0FD26D75CE |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Yuba City | CA | 95991-8241 |  | 2013-08-29 | 2013-08-29 16:55 | 2013-08-29 17:21 | OTHER - 56CJ042-A | 80 | -3 | Yes | Yes | 20 | 21 | -1 | E24A81DF82B944AF97D44D7EB59DF1AB |  | R22 | TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | TXV |  |  | -3.75%
Fresno | CA | 93722-5741 |  | 2013-09-11 | 2013-09-11 11:21 | 2013-09-11 11:23 | BRYANT - 563CN048-H | 140 | 4.6 | Yes | Yes | 23 | 19.7 | 3.3 | B068DD45805C43B69A52B6F6BF48C9DC |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Fresno | CA | 93722-5741 |  | 2013-09-11 | 2013-09-11 11:32 | 2013-09-11 11:34 | PAYNE - PY2PNB048115ABAA | 132 | 5.3 | Yes | Yes | 22.8 | 19.8 | 3 | BDE70CB258914045A781B2A1D255CA2B |  | R22 | Non-TXV |  | 4.015% | 0.95985 | 7.716% | [5 empty] | Non-TXV | 4.015%
Madera | CA | 93637-4617 |  | 2013-09-06 | 2013-09-06 14:00 | 2013-09-06 14:01 | OTHER - DCYZ-F036N070B | 64 | 2.3 | Yes | Yes | 24.3 | 20.1 | 4.2 | 87DF132798DF44FC96843AD7A31651F0 |  | R410A | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Fresno | CA | 93722-4144 |  | 2013-09-10 | 2013-09-10 12:41 | 2013-09-10 12:43 | CARRIER - 3680YAC | 66 | 9.5 | Yes | Yes | 21.1 | 21.3 | -0.2 | 353D5FA445A04D38ADEB89B7C0F6CCFD |  | R22 | Non-TXV |  | 14.39% | 0.85606 | 27.66% | [5 empty] | Non-TXV | 14.39%
Fresno | CA | 93722-5712 |  | 2013-09-11 | 2013-09-11 12:20 | 2013-09-11 12:20 | RHEEM - 13AJN36A01 | 90 | 0 | Yes | Yes | 18.9 | 19.5 | -0.6 | 6277F3080FE647CE9F89C4FEDC4E1A96 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-7130 |  | 2013-09-13 | 2013-09-13 12:55 | 2013-09-13 13:15 | CARRIER - 38CCKC060370 | 131 | 19.6 | Yes | Yes | 17.1 | 17.5 | -0.4 | 5C6DFD00DAA04625A9FDC8EB4B1B1E4E |  | R22 | Non-TXV |  | 14.96% | 0.85038 | 28.75% | [5 empty] | Non-TXV | 14.96%
Templeton | CA | 93465-8552 |  | 2013-09-05 | 2013-09-05 16:11 | 2013-09-05 16:30 | PAYNE - PA10JA036-C | 78 | 10.1 | Yes | Yes | 18 | 19.5 | -1.5 | 717F56F0A5694E3CA56CA9895518ED4D |  | R22 | Non-TXV |  | 12.95% | 0.87051 | 24.88% | [5 empty] | Non-TXV | 12.95%
Fresno | CA | 93722-2812 |  | 2013-09-13 | 2013-09-13 12:29 | 2013-09-13 13:23 | OTHER - N/A | 90 | 2.5 | Yes | Yes | 17.3 | 19.1 | -1.8 | 9760711850DC40DAAC15EBC5B6B6A8B1 |  | R22 | Non-TXV |  | 2.778% | 0.97222 | 5.338% | [5 empty] | Non-TXV | 2.778%
Fresno | CA | 93725-1217 |  | 2013-09-12 | 2013-09-12 12:58 | 2013-09-12 14:47 | INTERTHERM - N/A | 85 | 3 | Yes | Yes | 18 | 18.9 | -0.9 | 284805F005954216AB659CD97C50B2B3 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
San Miguel | CA | 93451-9577 |  | 2013-10-09 | 2013-10-09 11:45 | 2013-10-09 12:01 | HEIL - CA5542VKD1 | 98 | -5.8 | Yes | Yes | 24.5 | 19.5 | 5 | 1C1CCA7F32814400BF008972C4C72664 |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Coalinga | CA | 93210-2532 |  | 2013-10-11 | 2013-10-11 11:28 | 2013-10-11 12:11 | TRANE - 4TTM3024AA1000BA | 75 | 3.1 | Yes | Yes | 18.7 | 20.7 | -2 | B5A3C641FA2B4CC490FD74B9183A78BB |  | R410A | TXV |  | 4.133% | 0.95867 | 7.943% | [5 empty] | TXV | 4.133%
Fresno | CA | 93722-4382 |  | 2013-09-13 | 2013-09-13 13:26 | 2013-09-13 13:52 | BDP - 585GJW024040ABAE | 54 | 6.2 | Yes | Yes | 21.7 | 19.7 | 2 | D1FB1D9AE1794A32AF4C247C484B855D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.48% | 0.88519 | 22.06% | [5 empty] | Non-TXV | 11.48%
Winton | CA | 95388-9249 |  | 2013-09-10 | 2013-09-10 14:59 | 2013-09-10 15:16 | RHEEM - RRNL-B036JK06X | 93 | 2.8 | Yes | Yes | 27 | 23.1 | 3.9 | 1B958672822349C7B12D0238C1F0BDD1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Manteca | CA | 95337-6695 |  | 2013-09-16 | 2013-09-16 10:35 | 2013-09-16 11:25 | RHEEM - RAMC-036JBZ | 85 | 2.8 | Yes | Yes | 19.7 | 18 | 1.8 | 14760DCF696246C99E7ED34AAA846BAE |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Penn Valley | CA | 95946-9675 |  | 2013-09-18 | 2013-09-18 11:27 | 2013-09-18 11:27 | AMERICAN STANDARD - YCC036F1M0BJ | 85 | 0 | Yes | Yes | 18.7 | 20.6 | -1.9 | 0F2128B8D8F04FD9B83A66DACF82B023 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Penn Valley | CA | 95946-9675 |  | 2013-09-18 | 2013-09-18 11:53 | 2013-09-18 11:53 | AMERICAN STANDARD - YCC030F1M0BH | 72 | 0 | Yes | Yes | 22.3 | 20.9 | 1.4 | 3EA48FCF95884D79A4098433D35C1E92 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-6362 |  | 2013-09-11 | 2013-09-11 07:31 | 2013-09-11 07:32 | BRYANT - 561CJ048-A | 105 | 5 | Yes | Yes | 21 | 20.4 | 0.6 | 4667C8BF9FE7443B8202499BEB4C4113 |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Stockton | CA | 95205-3413 |  | 2013-09-10 | 2013-09-10 10:12 | 2013-09-10 10:29 | RUUD - URMA-A036JK08X | 99 | -5.8 | Yes | Yes | 18.8 | 18.1 | 0.7 | 253568E0EE1942AB931B96653C89B815 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Stockton | CA | 95219-3561 |  | 2013-09-16 | 2013-09-16 11:49 | 2013-09-16 11:49 | RHEEM - RRNL-B030JK06X | 76 | 0 | Yes | Yes | 17.4 | 18.7 | -1.3 | E6C2238DA9A2493BA6676FC9767EC74F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6655 |  | 2013-09-12 | 2013-09-12 10:26 | 2013-09-12 10:46 | BRYANT - 563CN036-C | 101 | 3.1 | Yes | Yes | 20 | 19.3 | 0.7 | 8485A127363644DFB7022FDA9474E600 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Manteca | CA | 95337-6655 |  | 2013-09-12 | 2013-09-12 10:48 | 2013-09-12 11:04 | BRYANT - 563CN036-C | 101 | 4 | Yes | Yes | 21.1 | 19.8 | 1.3 | C83C6346D9C54CF88A8EBC5CAC8B524C |  | R22 | Non-TXV |  | 3.96% | 0.9604 | 7.611% | [5 empty] | Non-TXV | 3.96%
Fresno | CA | 93728-2942 |  | 2013-09-23 | 2013-09-23 16:36 | 2013-09-23 17:34 | LENNOX - 12GCS042X-100-3PA | 133 | 5.2 | Yes | Yes | 20 | 19.8 | 0.2 | BBCC2C470165419C9C7D97CDD98095E2 |  | R22 | Non-TXV |  | 3.91% | 0.9609 | 7.514% | [5 empty] | Non-TXV | 3.91%
Gustine | CA | 95322-1357 |  | 2013-10-09 | 2013-10-09 12:30 | 2013-10-09 12:31 | GOODMAN - CK361A | 73 | 5.8 | Yes | Yes | 22.6 | 19.5 | 3.1 | 6599166813A145738B0A4A2E06489C6D |  | R22 | Non-TXV |  | 7.945% | 0.92055 | 15.27% | [5 empty] | Non-TXV | 7.945%
Fresno | CA | 93706-2647 |  | 2013-09-26 | 2013-09-26 13:20 | 2013-09-26 13:22 | YORK - DAYPF042N080A | 150 | 14.5 | Yes | Yes | 22.6 | 19.9 | 2.7 | 6ACE689FB4C74FFBA3AE451F4783F196 |  | R22 | Non-TXV |  | 9.667% | 0.90333 | 18.58% | [5 empty] | Non-TXV | 9.667%
Merced | CA | 95341-6932 |  | 2013-09-16 | 2013-09-16 14:19 | 2013-09-16 14:20 | AMANA - APG13204701CB | 74 | 11.6 | Yes | Yes | 30.2 | 24.4 | 5.8 | 8C3AA690CC714AFF8A63C642336CFA04 |  | R22 | Non-TXV |  | 15.68% | 0.84324 | 30.13% | [5 empty] | Non-TXV | 15.68%
Chico | CA | 95926-7799 |  | 2013-09-13 | 2013-09-13 09:45 | 2013-09-13 10:06 | GIBSON - JSDC-036KA | 82 | 3.8 | Yes | Yes | 12 | 15 | -3 | E7F7D4F1357B420397F8843F02F0D3FC |  | R22 | Non-TXV |  | 4.634% | 0.95366 | 8.906% | [5 empty] | Non-TXV | 4.634%
Paradise | CA | 95969-2241 |  | 2013-09-26 | 2013-09-26 12:39 | 2013-09-26 12:48 | YORK - H1RAO42S06G | 84 | 2.6 | Yes | Yes | 26 | 21.8 | 4.2 | A14D23EEC7E3492281595DAAFBE1F0E6 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Sanger | CA | 93657-2767 |  | 2013-09-10 | 2013-09-10 14:53 | 2013-09-10 15:37 | AMERICAN STANDARD - YCC0360F1M0BK | 83 | 3.7 | Yes | Yes | 20.5 | 20.2 | 0.3 | A4F9668F4D1740869F1AA8501E8E946E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.458% | 0.95542 | 8.567% | [5 empty] | Non-TXV | 4.458%
Gustine | CA | 95322-1358 |  | 2013-09-17 | 2013-09-17 10:52 | 2013-09-17 10:54 | GOODMAN - CK60-1C | 115 | 5 | Yes | Yes | 25.6 | 19.8 | 5.8 | 30BFFF68956E4697B4CE823C6BD0AF47 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Oakdale | CA | 95361-4203 |  | 2013-09-11 | 2013-09-11 12:41 | 2013-09-11 13:00 | CARRIER - 24ABC630A300 | 104 | 4 | Yes | Yes | 19.4 | 18.5 | 0.9 | C4FBA8E7C7664B63A103B8D3C1792736 |  | R410A | TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | TXV | 3.846%
Stockton | CA | 95210-2050 |  | 2013-09-25 | 2013-09-25 14:54 | 2013-09-25 15:14 | BDP - 585A030050YAC | 50 | 2.5 | Yes | Yes | 21.9 | 18.7 | 3.2 | 70019392F61C405A8B9160C62C85D3DF |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95215-9514 |  | 2013-09-11 | 2013-09-11 15:21 | 2013-09-11 15:42 | RHEEM - RRNL-B042JK08X | 112 | 10 | Yes | Yes | 20.5 | 19.3 | 1.3 | B2940BDB565A4ECB9FF02EAE1D1CDE35 |  | R410A | TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | TXV | 8.929%
Grass Valley | CA | 95945-7034 |  | 2013-08-30 | 2013-08-30 14:12 | 2013-08-30 14:12 | BRYANT - 113ANA036-E | 85 | 0 | Yes | Yes | 17.8 | 20.6 | -2.8 | 433373B5E0314DC4A2E32AF7DF015443 |  | R410A | TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-8722 |  | 2013-09-06 | 2013-09-06 09:50 | 2013-09-06 10:19 | BRYANT - 114ANA048-A | 176 | 5.6 | Yes | Yes | 20.9 | 18.8 | 2.1 | 7373AFE799B243B3AAF1CDE1D576205A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Reedley | CA | 93654-2375 |  | 2013-10-02 | 2013-10-02 14:37 | 2013-10-02 14:37 | RHEEM - RRNL-B024JK06X | 77 | 0 | Yes | Yes | 17.5 | 20.3 | -2.8 | 595460C5B83246A9AA4051DA8E78307B |  | R410A | TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-4500 |  | 2013-09-13 | 2013-09-13 14:56 | 2013-09-13 15:26 | PAYNE - PA13NR060-A | 181 | 6 | Yes | Yes | 20.9 | 20.6 | 0.3 | D53CC86C6D1A4178ADDFE075C5A93DED |  | R22 | Non-TXV |  | 3.315% | 0.96685 | 6.371% | [5 empty] | Non-TXV | 3.315%
Paso Robles | CA | 93446-3623 |  | 2013-09-06 | 2013-09-06 08:36 | 2013-09-06 08:56 | OTHER - EEC024FAA | 38 | -5 | Yes | Yes | 24.7 | 18.9 | 5.8 | 76ECC8112D934DA4BFA58FF9BB52B485 |  | R22 | Non-TXV |  | -13.16% | 1.1316 | 3.685% |  |  |  |  | Non-TXV |  |  | -13.16%
El Dorado Hills | CA | 95762-5517 |  | 2013-09-13 | 2013-09-13 13:39 | 2013-09-13 13:57 | GOODMAN - CKL42-1A | 95 | 2.8 | Yes | Yes | 22.1 | 20.8 | 1.3 | 5995F436A73040D6A8B1EE4B389B6674 |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Winton | CA | 95388-9246 |  | 2013-09-10 | 2013-09-10 15:32 | 2013-09-10 16:00 | GOODMAN - PGB0300??-1 | 56 | 2.8 | Yes | Yes | 18.6 | 20.4 | -1.8 | 8222525ABCE74287B30E6CE0E4232CC9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93720-2498 |  | 2013-09-20 | 2013-09-20 11:40 | 2013-09-20 12:19 | BDP - 585GJWO24O40ABAE | 54 | 4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 40E28378060C4521A31F715855124F4A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
El Dorado Hills | CA | 95762-5514 |  | 2013-09-13 | 2013-09-13 14:09 | 2013-09-13 14:26 | INTERTHERM - UNK | 85 | 4.4 | Yes | Yes | 22.1 | 20.6 | 1.5 | 8C9083506A124EC894BDF8B6784FA10B |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Grass Valley | CA | 95949-6502 |  | 2013-09-05 | 2013-09-05 13:06 | 2013-09-05 13:06 | ICP - UNK | 83 | 0 | Yes | Yes | 25.1 | 19.9 | 5.2 | 30D80682E9BD43D4918333B1F90AF4E2 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2277 |  | 2013-09-25 | 2013-09-25 16:36 | 2013-09-25 16:54 | RUUD - UAKA-030JAZ | 66 | -3.9 | Yes | Yes | 25.5 | 22.3 | 3.2 | 2E6565D773CE4A6BA14A993C65845F8B |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Chico | CA | 95973-0115 |  | 2013-11-01 | 2013-11-01 16:38 | 2013-11-01 17:00 | PAYNE - 585GJW018040ABAC | 53 | 4.6 | Yes | Yes | 17.9 | 18.3 | -0.4 | F39D0FC103BE41979491EBC31557FDA6 |  | R22 | Non-TXV |  | 8.679% | 0.91321 | 16.68% | [5 empty] | Non-TXV | 8.679%
Manteca | CA | 95337-6866 |  | 2013-10-03 | 2013-10-03 10:17 | 2013-10-03 10:47 | TRANE - TTN048C100A0 | 151 | 5.5 | Yes | Yes | 25.9 | 20.6 | 5.3 | 12F1E713C0174A93BF41A6DDE0D7B9F2 |  | R22 | TXV |  | 3.642% | 0.96358 | 7% | [5 empty] | TXV | 3.642%
Fresno | CA | 93726-0702 |  | 2013-09-06 | 2013-09-06 15:51 | 2013-09-06 16:41 | BRYANT - 582ANW036060AAAF | 56 | 1.8 | Yes | Yes | 20 | 20.9 | -0.9 | F2E59CE9079441E88F331E48E7A2DDD9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Lincoln | CA | 95648-2338 |  | 2013-08-29 | 2013-08-29 10:47 | 2013-08-29 11:19 | YORK - H2RA030S06D | 62 | -5.8 | Yes | Yes | 17.4 | 18.5 | -1.1 | A5A6FAF74A474C9D9CD33D6A3551080B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.355% | 1.0935 | 2.62% |  |  |  |  | Non-TXV |  |  | -9.355%
Dos Palos | CA | 93620-2144 |  | 2013-09-23 | 2013-09-23 12:28 | 2013-09-23 12:30 | TRANE - TTR036C100A1 | 92 | 13 | Yes | Yes | 20.5 | 17.5 | 3 | FB99F09AD698456B8DEE36233E1D3971 |  | R22 | Non-TXV |  | 14.13% | 0.8587 | 27.16% | [5 empty] | Non-TXV | 14.13%
Shingle Springs | CA | 95682-8031 |  | 2013-09-18 | 2013-09-18 13:06 | 2013-09-18 13:25 | TRANE - YCY030G1M0AC | 120 | 4.4 | Yes | Yes | 22 | 21 | 1 | 190A986BD4824B9A861557AE8E3DD5F5 |  | R22 | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Shingle Springs | CA | 95682-8031 |  | 2013-09-18 | 2013-09-18 13:10 | 2013-09-18 13:44 | TRANE - YCY048G1H0AC | 183 | 6.7 | Yes | Yes | 20.5 | 21 | -0.5 | AF04A90E91834F5F95567D80A9648A26 |  | R22 | TXV |  | 3.661% | 0.96339 | 7.036% | [5 empty] | TXV | 3.661%
Reedley | CA | 93654-2358 |  | 2013-09-26 | 2013-09-26 17:20 | 2013-09-26 18:01 | - | 85 | 3 | Yes | Yes | 25.8 | 20.4 | 5.4 | 1830022EC5E7465281FC0AC05FB9E73A |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Clovis | CA | 93611-5377 |  | 2013-09-27 | 2013-09-27 11:06 | 2013-09-27 11:42 | BDP - 565BJ042 | 62 | 4 | Yes | Yes | 18 | 19.9 | -1.9 | CBDF8152657D45899E97B15E6A212D1A |  | R22 | Non-TXV |  | 6.452% | 0.93548 | 12.4% | [5 empty] | Non-TXV | 6.452%
Manteca | CA | 95337-5316 |  | 2013-09-06 | 2013-09-06 14:11 | 2013-09-06 14:38 | RUUD - UAKB-036JAZ | 79 | 2.6 | Yes | Yes | 20.9 | 19.9 | 1.1 | 6CEE661328A24BDDAE74CCCA7E7BD17A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Fresno | CA | 93702-2429 |  | 2013-10-02 | 2013-10-02 11:58 | 2013-10-02 11:59 | CARRIER - 48DL004 | 81 | 2.7 | Yes | Yes | 21.8 | 20.4 | 1.4 | 9B2D2FE72A3C4B1BB63DE2CCAC673B59 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Clovis | CA | 93611-3124 |  | 2013-09-19 | 2013-09-19 10:07 | 2013-09-19 10:08 | YORK - D1NA042N05606C | 76 | 10.2 | Yes | Yes | 23.4 | 19.9 | 3.5 | 12ED246BA6634F94B9F28B008E3C9914 |  | R22 | Non-TXV |  | 13.42% | 0.86579 | 25.79% | [5 empty] | Non-TXV | 13.42%
Reedley | CA | 93654-2371 |  | 2013-10-07 | 2013-10-07 16:31 | 2013-10-07 16:51 | YORK - DCYP-F024N045B | 100 | 2.9 | Yes | Yes | 24 | 21.3 | 2.8 | 6ADD3F7E6D3D473DA4020BF138CA7CF6 |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Reedley | CA | 93654-2372 |  | 2013-09-26 | 2013-09-26 18:04 | 2013-09-26 18:39 | RHEEM - N/A | 60 | 5.5 | Yes | Yes | 24.5 | 20.2 | 4.4 | CE1A8E443DE24E47BF8F769FC6093B5B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Clovis | CA | 93612-2678 |  | 2013-09-10 | 2013-09-10 09:07 | 2013-09-10 09:08 | ICP - NAC042AKA4 | 105 | 9.3 | Yes | Yes | 24.5 | 21 | 3.5 | 7D736913DF0A44C28787BF8A8C7E35EC |  | R22 | Non-TXV |  | 8.857% | 0.91143 | 17.02% | [5 empty] | Non-TXV | 8.857%
Stockton | CA | 95206-1504 |  | 2013-09-06 | 2013-09-06 10:45 | 2013-09-06 11:11 | - VSX130301AB | 69 | 2.8 | Yes | Yes | 24.5 | 18.7 | 5.8 | D524E4DE64B64D92A8B235FA5B2F195B |  | R410A | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Reedley | CA | 93654-2373 |  | 2013-10-09 | 2013-10-09 15:53 | 2013-10-09 16:29 | GOODMAN - PGBPGB024075 | 54 | 6.4 | Yes | Yes | 26.5 | 21.5 | 5 | C57964A805264EBEA54B53CF9001EEC3 |  | R22 | Non-TXV |  | 11.85% | 0.88148 | 22.78% | [5 empty] | Non-TXV | 11.85%
Manteca | CA | 95336-6413 |  | 2013-09-12 | 2013-09-12 12:53 | 2013-09-12 13:16 | PAYNE - P1YPNB036060ABAA | 69 | 2.2 | Yes | Yes | 20.4 | 16.9 | 3.5 | D35CA44A8DAA4A30858FF75BA4BDFC48 |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Los Banos | CA | 93635-9451 |  | 2013-09-19 | 2013-09-19 11:17 | 2013-09-19 11:18 | BRYANT - 5561CJ048-A | 105 | 4.2 | Yes | Yes | 21.2 | 21 | 0.2 | 0C822A77580B46D5A1D046712F12CC07 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93722-8020 |  | 2013-09-13 | 2013-09-13 14:21 | 2013-09-13 15:47 | UNITARY PRODUCTS GROUP - H2RC048S06G | 119 | 12.2 | Yes | Yes | 17.9 | 20.1 | -2.2 | 9DA26EB134404609A90E80C4980A0AA5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.25% | 0.89748 | 19.7% | [5 empty] | Non-TXV | 10.25%
Fresno | CA | 93711-4037 |  | 2013-09-06 | 2013-09-06 13:00 | 2013-09-06 14:02 | CARRIER - 24ABS330A0030010 | 73 | 3 | Yes | Yes | 18 | 20.7 | -2.7 | 685DB12D483A4D3E9CDE153E34E04179 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.11% | 0.9589 | 7.898% | [5 empty] | Non-TXV | 4.11%
Fresno | CA | 93726-5409 |  | 2013-09-20 | 2013-09-20 18:13 | 2013-09-20 18:59 | RHEEM - RRNA-B024JK06X | 70 | 8.2 | Yes | Yes | 18.5 | 20.7 | -2.2 | 0CE15359335A4E1B98FE9665F7845C08 |  | R22 | Non-TXV |  | 11.71% | 0.88286 | 22.51% | [5 empty] | Non-TXV | 11.71%
Manteca | CA | 95337-6030 |  | 2013-09-06 | 2013-09-06 13:19 | 2013-09-06 13:42 | OTHER - CBD | 85 | 2.7 | Yes | Yes | 21.2 | 21.3 | -0.1 | 1504637042054590A2BDD6098043DEE8 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Manteca | CA | 95336-8427 |  | 2013-09-12 | 2013-09-12 11:22 | 2013-09-12 11:48 | PAYNE - PY1PJB048115AAAA | 81 | 2.4 | Yes | Yes | 17.4 | 18.2 | -0.8 | C042DE56CA2B448AB9908F9BC0DA69F2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95209-1638 |  | 2013-09-13 | 2013-09-13 16:41 | 2013-09-13 16:49 | GOODMAN - GPG133007OM41AA | 80 | 8.6 | Yes | Yes | 23 | 19.3 | 3.7 | CD1A53C967E64C538CA0F74047A89AA0 |  | R410A | Non-TXV |  | 10.75% | 0.8925 | 20.66% | [5 empty] | Non-TXV | 10.75%
Winton | CA | 95388-9388 |  | 2013-09-09 | 2013-09-09 13:30 | 2013-09-09 13:58 | RHEEM - RAND-042JAZ | 136 | 4.1 | Yes | Yes | 20.9 | 20.2 | 0.7 | 2D08CF42708A4A02A5689438D2E95FAA |  | R22 | Non-TXV |  | 3.015% | 0.96985 | 5.794% | [5 empty] | Non-TXV | 3.015%
Kingsburg | CA | 93631-2014 |  | 2013-10-01 | 2013-10-01 17:20 | 2013-10-01 17:39 | ICP - PGAD47D1K6 | 215 | 6.4 | Yes | Yes | 18.5 | 20.7 | -2.2 | EBF5FA3384144F16A5D28DDE40CC55D4 |  | R22 | Non-TXV |  | 2.977% | 0.97023 | 5.721% | [5 empty] | Non-TXV | 2.977%
Fresno | CA | 93722-8011 |  | 2013-09-13 | 2013-09-13 16:13 | 2013-09-13 16:15 | TRANE - 2TTB360A1000A | 139 | 7.8 | Yes | Yes | 18.9 | 16.8 | 2.1 | 3ABD5E6B436D4CCF9BC436317FB4E4FF |  | R22 | Non-TXV |  | 5.612% | 0.94388 | 10.78% | [5 empty] | Non-TXV | 5.612%
Stockton | CA | 95204-2220 |  | 2013-09-09 | 2013-09-09 10:10 | 2013-09-09 10:30 | GOODMAN - GSX130361DA | 77 | -4.5 | Yes | Yes | 24.8 | 19.1 | 5.7 | F8C993DFFEA0465BBCA57E0A46131208 |  | R410A | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Oakdale | CA | 95361-0000 |  | 2013-09-11 | 2013-09-11 08:57 | 2013-09-11 09:15 | RUUD - CBD | 79 | 2.6 | Yes | Yes | 18.6 | 18.2 | 0.4 | 8F1A413B903C45969DA7B2BA8EB692A2 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Reedley | CA | 93654-2357 |  | 2013-09-26 | 2013-09-26 16:42 | 2013-09-26 17:17 | RHEEM - N/A | 60 | 5.9 | Yes | Yes | 24.5 | 20.4 | 4.1 | 4DCE17E685C7478A891E19371DD0A50B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.833% | 0.90167 | 18.9% | [5 empty] | Non-TXV | 9.833%
Stockton | CA | 95209-1343 |  | 2013-09-12 | 2013-09-12 14:00 | 2013-09-12 14:18 | LENNOX - HS29-036-1P | 73 | 2.8 | Yes | Yes | 22.8 | 18.3 | 4.5 | A29E8F11025E4F5F9BB973E8AF0C26E4 |  | R22 | Non-TXV |  | 3.836% | 0.96164 | 7.371% | [5 empty] | Non-TXV | 3.836%
Reedley | CA | 93654-2359 |  | 2013-09-30 | 2013-09-30 13:40 | 2013-09-30 14:21 | RHEEM - N/A | 60 | 4.3 | Yes | Yes | 20.1 | 20.4 | -0.3 | F31219AF6D5D4A848F4136BBF0ABD458 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | Non-TXV | 7.167%
Reedley | CA | 93654-2373 |  | 2013-10-02 | 2013-10-02 13:51 | 2013-10-02 15:01 | RHEEM - RRKA-A024JK06E | 50 | 4.8 | Yes | Yes | 23.4 | 20.6 | 2.9 | EA34DED87CE746E4933BEF24B69FF81C |  | R22 | Non-TXV |  | 9.6% | 0.904 | 18.45% | [5 empty] | Non-TXV | 9.6%
Fresno | CA | 93704-5905 |  | 2013-09-19 | 2013-09-19 09:15 | 2013-09-19 11:46 | AMERICAN STANDARD - YCC042F1M0BE | 101 | 6.4 | Yes | Yes | 25.5 | 20.4 | 5.1 | 7CF6E728F02A478F97E75FA8C910A31B |  | R22 | Non-TXV |  | 6.337% | 0.93663 | 12.18% | [5 empty] | Non-TXV | 6.337%
Fresno | CA | 93703-2435 |  | 2013-09-23 | 2013-09-23 13:29 | 2013-09-23 13:31 | TRANE - YCX036F1M0BC | 116 | 5.7 | Yes | Yes | 22.5 | 19.9 | 2.6 | E2E0B9A764E34F3F936399B524007841 |  | R22 | Non-TXV |  | 4.914% | 0.95086 | 9.443% | [5 empty] | Non-TXV | 4.914%
Yuba City | CA | 95991-7323 |  | 2013-09-06 | 2013-09-06 15:43 | 2013-09-06 15:43 | OTHER - 563CN060-A | 195 | 0 | Yes | Yes | 17 | 19.8 | -2.8 | E7BA905E1B0A4259A92A8DC1272B85A1 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-2010 |  | 2013-09-20 | 2013-09-20 11:40 | 2013-09-20 11:58 | AMANA - PCE60A2D | 200 | 20.6 | Yes | Yes | 21.8 | 18.2 | 3.6 | B7369E6649564E3B8020E86053EA5C99 |  | R22 | Non-TXV |  | 10.3% | 0.897 | 19.79% | [5 empty] | Non-TXV | 10.3%
Stockton | CA | 95212-2010 |  | 2013-09-20 | 2013-09-20 12:16 | 2013-09-20 12:51 | AMANA - RCE48A2D | 180 | 6 | Yes | Yes | 20.5 | 18 | 2.6 | 938AB3382DF3459EB25E04FE6F401CAD |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Mariposa | CA | 95338-9628 |  | 2013-09-11 | 2013-09-11 13:33 | 2013-09-11 13:35 | OTHER - BWC0480100B1 | 206 | 19.3 | Yes | Yes | 20 | 18 | 2 | CB46DDB4E61D4476868CD45020CBF447 |  | R22 | Non-TXV |  | 9.369% | 0.90631 | 18.01% | [5 empty] | Non-TXV | 9.369%
Madera | CA | 93638-0435 |  | 2013-09-09 | 2013-09-09 10:17 | 2013-09-09 10:21 | CARRIER - UNK | 68 | 11.4 | Yes | Yes | 22.2 | 20.4 | 1.8 | B79B6B8185C94D0D95DA0E65154CCD17 |  | R22 | Non-TXV |  | 16.76% | 0.83235 | 32.22% | [5 empty] | Non-TXV | 16.76%
Fresno | CA | 93705-3517 |  | 2013-09-16 | 2013-09-16 10:14 | 2013-09-16 10:16 | YORK - D1NA036N05606A | 63 | 7.2 | Yes | Yes | 22.6 | 19.9 | 2.7 | C226ED23F6854B48AC3C57D698B4587F |  | R22 | Non-TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | Non-TXV | 11.43%
Magalia | CA | 95954-9505 |  | 2013-10-01 | 2013-10-01 10:02 | 2013-10-01 10:26 | BARD - PH11361 | 80 | 4.4 | Yes | Yes | 17.3 | 19.9 | -2.6 | 44A6BA1AFF1E4D6E8F95F2655C5D4822 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Chico | CA | 95928-7575 |  | 2013-09-13 | 2013-09-13 10:09 | 2013-09-13 10:27 | PAYNE - 585HJO24040 | 66 | 11.1 | Yes | Yes | 13.7 | 16.7 | -3 | E7456ED10731466BB3124A310B0F8242 |  | R22 | Non-TXV |  | 16.82% | 0.83182 | 32.32% | [5 empty] | Non-TXV | 16.82%
Fresno | CA | 93704-5533 |  | 2013-10-08 | 2013-10-08 14:06 | 2013-10-08 14:33 | CARRIER - 036 | 104 | 4.4 | Yes | Yes | 20.6 | 19.4 | 1.2 | 0F3F413288E04BE3966927C32268D6F7 |  | R22 | Non-TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | Non-TXV | 4.231%
Stockton | CA | 95207-3109 |  | 2013-09-06 | 2013-09-06 09:38 | 2013-09-06 09:38 | PAYNE - 38CKC024340 | 55 | 0 | Yes | Yes | 18.9 | 18.2 | 0.7 | FB28F6C5432B4688931E2C177BF56CAE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6888 |  | 2013-10-09 | 2013-10-09 11:30 | 2013-10-09 18:14 | CARRIER - 38CKC036---351 | 70 | 4.7 | Yes | Yes | 24.5 | 20.4 | 4.1 | 04D3246F664949F79394E7D21B33306B |  | R22 | Non-TXV |  | 6.714% | 0.93286 | 12.9% | [5 empty] | Non-TXV | 6.714%
Penn Valley | CA | 95946-9320 |  | 2013-09-18 | 2013-09-18 09:32 | 2013-09-18 09:32 | PAYNE - PY1PNB030060AAAA | 59 | 0 | Yes | Yes | 18.5 | 20.9 | -2.4 | 2E9937458E764ED0BC4970002B078826 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2172 |  | 2013-09-25 | 2013-09-25 14:43 | 2013-09-25 14:43 | AMERICAN STANDARD - 7A2024A100A2 | 92 | 0 | Yes | Yes | 22.2 | 21.4 | 0.8 | EBE44D1AC5664CDB868EB03559CE6D2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2337 |  | 2013-09-10 | 2013-09-10 12:42 | 2013-09-10 13:07 | YORK - HR1A024S060 | 59 | 1.9 | Yes | Yes | 19.1 | 18.8 | 0.3 | 6889DEDF8B63447F97E4850A108CDD2C |  | R22 | Non-TXV |  | 3.22% | 0.9678 | 6.189% | [5 empty] | Non-TXV | 3.22%
Fresno | CA | 93720-3922 |  | 2013-09-20 | 2013-09-20 14:23 | 2013-09-20 14:49 | LENNOX - HS14-411-9P | 164 | 22 | Yes | Yes | 17 | 19.7 | -2.7 | E9447982C9274B06BCD68B4281F4A067 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.41% | 0.86585 | 25.78% | [5 empty] | Non-TXV | 13.41%
Escalon | CA | 95320-2174 |  | 2013-09-26 | 2013-09-26 13:33 | 2013-09-26 13:48 | TRANE - `TTD730B100A0 | 69 | 2.1 | Yes | Yes | 23.9 | 21.5 | 2.4 | CF379CF5C20D421CB268993C13AE3ADC |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Clovis | CA | 93611-4034 |  | 2013-09-30 | 2013-09-30 13:27 | 2013-09-30 13:28 | ICP - PGC036K060B | 71 | 2.9 | Yes | Yes | 23.4 | 21 | 2.4 | C21107B1EBF448AE86AB33F72002ED15 |  | R22 | Non-TXV |  | 4.085% | 0.95915 | 7.85% | [5 empty] | Non-TXV | 4.085%
Stockton | CA | 95206-6155 |  | 2013-09-09 | 2013-09-09 11:02 | 2013-09-09 11:21 | CARRIER - 38CKC042340 | 80 | 4.4 | Yes | Yes | 15.8 | 18.7 | -2.9 | 57607681703B461DB572B50E20C9D8F5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Lincoln | CA | 95648-1714 |  | 2013-09-17 | 2013-09-17 10:37 | 2013-09-17 11:16 | TRANE - TTB024C100A2 | 54 | 4.4 | Yes | Yes | 18.2 | 19.8 | -1.6 | 663A5A182FFD4A16A596E02D5B8438DF |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Sanger | CA | 93657-2329 |  | 2013-09-10 | 2013-09-10 19:42 | 2013-09-10 19:42 | CARRIER - 38GF005310 | 120 | 0 | Yes | Yes | 23.8 | 17.9 | 6 | 27E5FA2ACFF1481590D8809F3B431A0F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7829 |  | 2013-09-26 | 2013-09-26 12:28 | 2013-09-26 12:51 | COLEMAN - 6285B901 | 96 | 3 | Yes | Yes | 19.5 | 19.8 | -0.3 | 172E82FE1C574B8EA0F6C5863D37736B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Stockton | CA | 95206-6366 |  | 2013-09-12 | 2013-09-12 17:32 | 2013-09-12 18:01 | CARRIER - 38CKC060370 | 130 | 4.7 | Yes | Yes | 19.6 | 19.2 | 0.5 | 7985DB438D9C4F10952F3082C642D0CA |  | R22 | TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | TXV | 3.615%
Menlo Park | CA | 94025-6023 |  | 2013-10-21 | 2013-10-21 14:26 | 2013-10-21 17:50 | CARRIER - 38EN036300 | 95 | 3.7 | Yes | Yes | 18.5 | 17.7 | 0.8 | 2B651E6609C9493485647FC31A216614 |  | R22 | Non-TXV |  | 3.895% | 0.96105 | 7.485% | [5 empty] | Non-TXV | 3.895%
Los Banos | CA | 93635-9452 |  | 2013-09-10 | 2013-09-10 11:46 | 2013-09-10 11:47 | BRYANT - 561CJ060-A | 157 | 5.4 | Yes | Yes | 22.4 | 20.8 | 1.6 | B20C56D934DE4849BDA2192359E81D03 |  | R22 | Non-TXV |  | 3.439% | 0.96561 | 6.61% | [5 empty] | Non-TXV | 3.439%
Fresno | CA | 93727-7830 |  | 2013-09-12 | 2013-09-12 09:59 | 2013-09-12 10:20 | UNITARY PRODUCTS GROUP - DRCS0481BD | 122 | 4.9 | Yes | Yes | 20.3 | 20.7 | -0.4 | 80E5E04A4A2D426DB6DF9B596CECBD3A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.016% | 0.95984 | 7.719% | [5 empty] | Non-TXV | 4.016%
Mariposa | CA | 95338-9381 |  | 2013-09-11 | 2013-09-11 14:25 | 2013-09-11 14:27 | RUUD - UNK | 56 | 7.6 | Yes | Yes | 28.4 | 23.1 | 5.3 | 10AE389A1C2243C29180F50C0A428024 |  | R22 | Non-TXV |  | 13.57% | 0.86429 | 26.08% | [5 empty] | Non-TXV | 13.57%
Fresno | CA | 93726-6756 |  | 2013-10-09 | 2013-10-09 10:22 | 2013-10-09 10:56 | CARRIER - N/A | 90 | 4.2 | Yes | Yes | 24.1 | 20.9 | 3.2 | 426A6C03D9FF41578385A25A223EBE7E |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Paso Robles | CA | 93446-3987 |  | 2013-10-09 | 2013-10-09 12:52 | 2013-10-09 13:10 | COLEMAN - UNK | 80 | -4.7 | Yes | Yes | 25.8 | 19.8 | 6 | 0D1DE0F7D644495F8A3029EA56306D8B |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Oroville | CA | 95965-4002 |  | 2013-09-16 | 2013-09-16 10:16 | 2013-09-16 10:39 | RHEEM - UNK | 100 | 3 | Yes | Yes | 25 | 19.9 | 5.1 | 3E8233D74C8348AB90268EE6AAB245CB |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Yuba City | CA | 95991-3702 |  | 2013-09-11 | 2013-09-11 12:27 | 2013-09-11 12:49 | OTHER - 13ACD-024-230-13 | 67 | 4.1 | Yes | Yes | 15 | 17.6 | -2.6 | 17501DC66E4A41ABA68B0B5AD3449412 |  | R22 | Non-TXV |  | 6.119% | 0.93881 | 11.76% | [5 empty] | Non-TXV | 6.119%
Magalia | CA | 95954-9453 |  | 2013-09-19 | 2013-09-19 10:22 | 2013-09-19 10:50 | CARRIER - 38EB030300 | 83 | 2.5 | Yes | Yes | 18.1 | 21 | -2.9 | 1F0C57CF01C84AB8994A1208308078F2 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Lathrop | CA | 95330-9178 |  | 2013-09-13 | 2013-09-13 15:46 | 2013-09-13 16:02 | CARRIER - 38CMC048 | 134 | 4.7 | Yes | Yes | 21.4 | 19.9 | 1.5 | CC7690612C94496287410F11C7FA9AF7 |  | R22 | Non-TXV |  | 3.507% | 0.96493 | 6.741% | [5 empty] | Non-TXV | 3.507%
Fresno | CA | 93706-3828 |  | 2013-09-12 | 2013-09-12 14:47 | 2013-09-12 14:49 | LENNOX - 10GCS036X753PA | 58 | 7.6 | Yes | Yes | 24.7 | 24.2 | 0.5 | 264023914A5D437C8AA97C2FED61C88D |  | R22 | Non-TXV |  | 13.1% | 0.86897 | 25.18% | [5 empty] | Non-TXV | 13.1%
Stockton | CA | 95205-3527 |  | 2013-09-10 | 2013-09-10 08:54 | 2013-09-10 09:14 | ICP - NAC030AKC3 | 75 | -4.4 | Yes | Yes | 17.7 | 18.3 | -0.6 | 871144F480AA4D1EB5EDDC5C56192C92 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Los Banos | CA | 93635-4524 |  | 2013-09-20 | 2013-09-20 12:35 | 2013-09-20 12:37 | OTHER - UNK | 68 | 7.8 | Yes | Yes | 24 | 19.8 | 4.2 | 9F970D30FFAA496F90ACDEB7AAECA04D |  | R22 | Non-TXV |  | 11.47% | 0.88529 | 22.04% | [5 empty] | Non-TXV | 11.47%
Atwater | CA | 95301-2087 |  | 2013-09-10 | 2013-09-10 10:25 | 2013-09-10 10:45 | COLEMAN - DAYP-F036N070A | 108 | 3.2 | Yes | Yes | 19.8 | 18.1 | 1.7 | D225313B2CF14F0CA55FBFFFD3BADF07 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Lathrop | CA | 95330-8877 |  | 2013-09-13 | 2013-09-13 14:22 | 2013-09-13 15:29 | CARRIER - 24ABA348A300 | 128 | 5.6 | Yes | Yes | 22.5 | 22.1 | 0.4 | E2E5D0467C3849E7B05796560F1BADB8 |  | R410A | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Stockton | CA | 95207-5424 |  | 2013-09-06 | 2013-09-06 11:44 | 2013-09-06 12:04 | DAY & NIGHT - 48RCU108 | 103 | 17.5 | Yes | Yes | 23.5 | 19.2 | 4.3 | 298C7500E9E04B938768C1A69F2C5731 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.99% | 0.8301 | 32.65% | [5 empty] | Non-TXV | 16.99%
Orange Cove | CA | 93646-2054 |  | 2013-09-17 | 2013-09-17 15:18 | 2013-09-17 16:20 | ICP - GPCM036K060F | 68 | 14 | Yes | Yes | 18.8 | 17.7 | 1.1 | 959D1C235EF84355BF7D9306ECB1BD15 |  | R22 | Non-TXV |  | 20.59% | 0.79412 | 39.57% | [5 empty] | Non-TXV | 20.59%
Chowchilla | CA | 93610-9228 |  | 2013-09-09 | 2013-09-09 14:05 | 2013-09-09 14:07 | AMANA - UNK | 76 | 6.3 | Yes | Yes | 23.6 | 21.7 | 1.9 | 5C1F70EC71CD48309129764AC440CAAB |  | R22 | Non-TXV |  | 8.289% | 0.91711 | 15.93% | [5 empty] | Non-TXV | 8.289%
Merced | CA | 95341-7005 |  | 2013-09-19 | 2013-09-19 15:38 | 2013-09-19 15:39 | BRYANT - 582ANW042060NAAG | 100 | 4.8 | Yes | Yes | 19.5 | 22.4 | -2.9 | 1EBBFDDC1BB840B5810E672AC9AFABFB |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Firebaugh | CA | 93622-0000 |  | 2013-09-18 | 2013-09-18 09:20 | 2013-09-18 09:21 | CARRIER - 48SS048080311 | 101 | 7.5 | Yes | Yes | 23.9 | 18.2 | 5.7 | 2F47595C82384012B0C111FDB14EC8A6 |  | R22 | Non-TXV |  | 7.426% | 0.92574 | 14.27% | [5 empty] | Non-TXV | 7.426%
Stockton | CA | 95206-6164 |  | 2013-09-16 | 2013-09-16 12:38 | 2013-09-16 13:05 | CARRIER - 38CKC060370 | 131 | 5.5 | Yes | Yes | 18 | 18.5 | -0.5 | F11E3878573D46C7AA4AE56F25C046AF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.198% | 0.95802 | 8.069% | [5 empty] | Non-TXV | 4.198%
Fresno | CA | 93704-1548 |  | 2013-09-19 | 2013-09-19 11:34 | 2013-09-19 12:20 | TRANE - TTB042C100A0 | 103 | 3.1 | Yes | Yes | 19 | 20.4 | -1.4 | D62DEF5801CE40F99106BBD6B1996DF1 |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Dos Palos | CA | 93620-0000 |  | 2013-09-23 | 2013-09-23 11:04 | 2013-09-23 11:06 | YORK - H2RD048S06B | 134 | 12.3 | Yes | Yes | 22.2 | 19.3 | 2.9 | 494C68B6C7B44607847475FE234F60FE |  | R22 | Non-TXV |  | 9.179% | 0.90821 | 17.64% | [5 empty] | Non-TXV | 9.179%
Merced | CA | 95348-1825 |  | 2013-09-06 | 2013-09-06 15:28 | 2013-09-06 15:29 | BRYANT - 583ANW048115AAHF | 114 | 17.3 | Yes | Yes | 30.1 | 24.2 | 5.9 | 1DCCCE4219AB462B802FB1281C030BBC |  | R22 | Non-TXV |  | 15.18% | 0.84825 | 29.16% | [5 empty] | Non-TXV | 15.18%
Olivehurst | CA | 95961-4810 |  | 2013-10-02 | 2013-10-02 15:17 | 2013-10-02 15:40 | CARRIER - 38BRC060360 | 195 | 24.9 | Yes | Yes | 23 | 19.9 | 3.1 | 06EEFFAB2DCA434E89FB6D90C360B62E |  | R22 | Non-TXV |  | 12.77% | 0.87231 | 24.54% | [5 empty] | Non-TXV | 12.77%
Orland | CA | 95963-1801 |  | 2013-09-10 | 2013-09-10 15:16 | 2013-09-10 15:39 | LENNOX - HS16-411V-3P | 105 | 3.4 | Yes | Yes | 16.3 | 19.2 | -2.9 | 8A11B63E2C4545438197F76E2A28DE28 |  | R22 | Non-TXV |  | 3.238% | 0.96762 | 6.223% | [5 empty] | Non-TXV | 3.238%
Willows | CA | 95988-2035 |  | 2013-09-09 | 2013-09-09 15:07 | 2013-09-09 19:23 | YORK - H1CH024S06A | 89 | 3.7 | Yes | Yes | 19 | 16.9 | 2.1 | 0E629631CC234B339F23DF02724DE518 |  | R22 | Non-TXV |  | 4.157% | 0.95843 | 7.989% | [5 empty] | Non-TXV | 4.157%
Stockton | CA | 95215-7904 |  | 2013-09-11 | 2013-09-11 14:32 | 2013-09-11 14:51 | COLEMAN - ERCQ0361BBA | 83 | 4.5 | Yes | Yes | 21.4 | 17.9 | 3.5 | B84DFAA751A546C4B3282A63CD9B8098 |  | R22 | Non-TXV |  | 5.422% | 0.94578 | 10.42% | [5 empty] | Non-TXV | 5.422%
Lincoln | CA | 95648-2963 |  | 2013-09-19 | 2013-09-19 09:11 | 2013-09-19 09:32 | CARRIER - 38CKC042350 | 90 | 6.7 | Yes | Yes | 20 | 21.5 | -1.5 | 37C02DDB4F4F4F86ABE7A7B4350D7172 |  | R22 | Non-TXV |  | 7.444% | 0.92556 | 14.31% | [5 empty] | Non-TXV | 7.444%
Fresno | CA | 93722-6803 |  | 2013-09-11 | 2013-09-11 12:53 | 2013-09-11 12:56 | CARRIER - 7777UNK | 85 | 2.6 | Yes | Yes | 22.1 | 19.9 | 2.2 | 04684EDA1ACC4880B3840E027B7C9D13 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Paradise | CA | 95969-6216 |  | 2013-09-26 | 2013-09-26 13:03 | 2013-09-26 13:31 | DAY & NIGHT - 588ANW036080ACBF | 67 | 5.4 | Yes | Yes | 19.4 | 20.9 | -1.5 | 40E6AC6EB5BD40C3890E1F882B106404 |  | R22 | Non-TXV |  | 8.06% | 0.9194 | 15.49% | [5 empty] | Non-TXV | 8.06%
Oroville | CA | 95965-8055 |  | 2013-09-16 | 2013-09-16 11:55 | 2013-09-16 12:32 | BARD - PH36-2 | 91 | 9.1 | Yes | Yes | 23 | 18.8 | 4.2 | 5A74881AD19241F3ACB9233BF61FDE34 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Chico | CA | 95973-7710 |  | 2013-09-06 | 2013-09-06 12:33 | 2013-09-06 12:50 | LENNOX - 13ACD-048-230-04 | 120 | 5.8 | Yes | Yes | 18 | 19.7 | -1.7 | 7FDE826A9C9040338ABC86049D9FCAA7 |  | R22 | Non-TXV |  | 4.833% | 0.95167 | 9.289% | [5 empty] | Non-TXV | 4.833%
Stockton | CA | 95207-2109 |  | 2013-09-06 | 2013-09-06 10:09 | 2013-09-06 10:09 | GOODMAN - CE42-1GC | 107 | 0 | Yes | Yes | 21.8 | 18.7 | 3.1 | 47628FC4099440F28CEE7E9F97A2B7B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6848 |  | 2013-09-06 | 2013-09-06 11:46 | 2013-09-06 12:17 | AMERICAN STANDARD - TTL048C100A0 | 160 | 7.2 | Yes | Yes | 22.9 | 19.3 | 3.6 | 356300C2E9DF41B6B27CE25631CA120C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Lathrop | CA | 95330-8699 |  | 2013-09-18 | 2013-09-18 14:06 | 2013-09-18 14:39 | CARRIER - 24ABA342A00310210 | 105 | 3.6 | Yes | Yes | 19.7 | 19.9 | -0.2 | 8BEA944AF83340C5A6F141ADB244C2D2 |  | R410A | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Stockton | CA | 95206-1654 |  | 2013-09-06 | 2013-09-06 09:42 | 2013-09-06 09:59 | CARRIER - 48XP-048115301 | 179 | 5.4 | Yes | Yes | 19 | 18.5 | 0.5 | A399CF84211549518BD77BD9AF415418 |  | R410A | Non-TXV |  | 3.017% | 0.96983 | 5.798% | [5 empty] | Non-TXV | 3.017%
Tracy | CA | 95376-1912 |  | 2013-09-19 | 2013-09-19 12:16 | 2013-09-19 12:33 | GOODMAN - CRT361A | 140 | 5.1 | Yes | Yes | 17.5 | 19.9 | -2.4 | BC6B9BDBA2DA417D9DB3EAD1456E524B |  | R22 | Non-TXV |  | 3.643% | 0.96357 | 7.001% | [5 empty] | Non-TXV | 3.643%
Fresno | CA | 93722-9114 |  | 2013-09-13 | 2013-09-13 17:35 | 2013-09-13 17:37 | BDP - N/A | 90 | 5 | Yes | Yes | 15.6 | 14.4 | 1.2 | 40981E77779E499F8BA0C3675810C0EF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Lincoln | CA | 95648-2074 |  | 2013-09-10 | 2013-09-10 10:51 | 2013-09-10 11:09 | RHEEM - RGKAA036JKO8X | 63 | 3.4 | Yes | Yes | 19.2 | 19.9 | -0.7 | DEFC3430498D40AB95748CA14BC32E19 |  | R22 | Non-TXV |  | 5.397% | 0.94603 | 10.37% | [5 empty] | Non-TXV | 5.397%
Atwater | CA | 95301-4501 |  | 2013-09-09 | 2013-09-09 11:07 | 2013-09-09 11:24 | HEIL - CA3036VKA1 | 94 | 3 | Yes | Yes | 21.2 | 20.2 | 1 | 373A6825F5574E38A7104146D13AA933 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.191% | 0.96809 | 6.133% | [5 empty] | Non-TXV | 3.191%
Gustine | CA | 95322-1923 |  | 2013-09-17 | 2013-09-17 11:30 | 2013-09-17 11:32 | ARCOAIRE - PGAD42D1KE | 180 | 6.8 | Yes | Yes | 26.2 | 20.2 | 6 | 339D82A05569425EAD87CCD680A767CE |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Fresno | CA | 93726-1119 |  | 2013-09-06 | 2013-09-06 16:46 | 2013-09-06 16:52 | OTHER - 24ECW060GA | 84 | 2.5 | Yes | Yes | 24 | 18.8 | 5.2 | 30316225D70F4119843F04329DF9E26D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Fresno | CA | 93726-1119 |  | 2013-09-06 | 2013-09-06 17:13 | 2013-09-06 17:48 | OTHER - 24ECW060GA | 84 | 18.2 | Yes | Yes | 17.5 | 20.2 | -2.7 | 139131F3A2D346C0A0EF19B30288BEF8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.67% | 0.78333 | 41.64% | [5 empty] | Non-TXV | 21.67%
Fresno | CA | 93726-1119 |  | 2013-09-06 | 2013-09-06 17:51 | 2013-09-06 19:50 | OTHER - 24ECW060GA | 84 | 4.3 | Yes | Yes | 20 | 20.5 | -0.5 | EC691F20BF7C4D54A398314292E60BC1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.119% | 0.94881 | 9.838% | [5 empty] | Non-TXV | 5.119%
Grass Valley | CA | 95949-7112 |  | 2013-09-09 | 2013-09-09 13:31 | 2013-09-09 13:31 | DAY & NIGHT - 561AJ030-A | 67 | 0 | Yes | Yes | 19.5 | 21.8 | -2.3 | 98463A9504DF4C36A1FA48FD4E94A9D3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-8843 |  | 2013-09-16 | 2013-09-16 11:47 | 2013-09-16 12:04 | CARRIER - 38CKC048370 | 100 | -5.4 | Yes | Yes | 19.6 | 18.3 | 1.3 | 0AC1535D8FF14B53949CF5350417CD50 |  | R22 | TXV |  | -5.4% | 1.054 | 1.512% |  |  |  |  | TXV |  |  | -5.4%
Orland | CA | 95963-9690 |  | 2013-09-10 | 2013-09-10 13:48 | 2013-09-10 14:14 | LENNOX - CHP26-042-1PA | 108 | 9 | Yes | Yes | 16.9 | 19.9 | -3 | 95769ADCB6CE4CA7B2F2FEBACA3C676B |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Madera | CA | 93638-7317 |  | 2013-10-07 | 2013-10-07 11:00 | 2013-10-07 11:01 | CARRIER - 48GS048090301 | 81 | 9.4 | Yes | Yes | 22.1 | 18.7 | 3.4 | 91D258D5433F4933B3A72DCDF24B400C |  | R22 | Non-TXV |  | 11.6% | 0.88395 | 22.3% | [5 empty] | Non-TXV | 11.6%
Oroville | CA | 95965-4421 |  | 2013-10-07 | 2013-10-07 10:59 | 2013-10-07 11:30 | TRANE - 2TTB3036A1000AA | 101 | 3.5 | Yes | Yes | 17.4 | 20.2 | -2.8 | 5C889D8016C743ECA2185EFB9B648E94 |  | R22 | Non-TXV |  | 3.465% | 0.96535 | 6.66% | [5 empty] | Non-TXV | 3.465%
Paso Robles | CA | 93446-3666 |  | 2013-10-08 | 2013-10-08 15:10 | 2013-10-08 15:32 | YORK - AC036X1021A | 63 | 9.2 | Yes | Yes | 22.4 | 21.3 | 1.1 | 644810B75AE8437BBE720A9BD5659A8D |  | R22 | Non-TXV |  | 14.6% | 0.85397 | 28.06% | [5 empty] | Non-TXV | 14.6%
Kingsburg | CA | 93631-1520 |  | 2013-09-11 | 2013-09-11 16:32 | 2013-09-11 17:31 | RUUD - N/A | 85 | 3.8 | Yes | Yes | 20.8 | 21.5 | -0.7 | F5CE4E2E1FC2419A9C0118170943CE03 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Willows | CA | 95988-3307 |  | 2013-09-17 | 2013-09-17 13:49 | 2013-09-17 14:09 | YORK - H3RA060S06B | 98 | 7 | Yes | Yes | 14.2 | 17.2 | -3 | EB2007B947914164A076AC0D8F188D4E |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Tracy | CA | 95377-8501 |  | 2013-09-23 | 2013-09-23 09:57 | 2013-09-23 10:23 | CARRIER - 38CKC036-351 | 70 | 3.9 | Yes | Yes | 18.6 | 17.7 | 0.9 | 20C3CC05A0D54D4C834A34DCC5DAB1C1 |  | R22 | Non-TXV |  | 5.571% | 0.94429 | 10.71% | [5 empty] | Non-TXV | 5.571%
Lincoln | CA | 95648-0000 |  | 2013-09-10 | 2013-09-10 13:15 | 2013-09-10 13:15 | YORK - H2RD036SO6B | 100 | 0 | Yes | Yes | 18.5 | 18.2 | 0.3 | C343C9D56CEE4E568283B761D80E4610 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4413 |  | 2013-09-09 | 2013-09-09 12:37 | 2013-09-09 12:55 | OTHER - TZAA-342-2A757 | 144 | 5.1 | Yes | Yes | 26.4 | 20.4 | 6 | EEB643412C5749D3863590DFBCE242F6 |  | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Manteca | CA | 95336-3147 |  | 2013-09-12 | 2013-09-12 14:49 | 2013-09-12 15:16 | AMANA - CBD | 64 | 1.9 | Yes | Yes | 21.1 | 21.1 | 0 | A4AF44B10D1D4BF7AECB4CAD1A4B7D32 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93722-7101 |  | 2013-09-20 | 2013-09-20 12:46 | 2013-09-20 12:46 | BRYANT - 577CNWA36060NA | 149 | 0 | Yes | Yes | 18.3 | 20.7 | -2.4 | 31C7D6A7F54E401CBDAC6FB31457564F |  | R410A | TXV |  | 0% | 1 | 0%
Copperopolis | CA | 95228-9625 |  | 2013-09-24 | 2013-09-24 15:17 | 2013-09-24 15:46 | GOODMAN - CK42-1A | 86 | 3.2 | Yes | Yes | 25.4 | 20.4 | 5 | EC30AD6FE5F74C29A0BB75DEB249C23E |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Atwater | CA | 95301-9672 |  | 2013-09-10 | 2013-09-10 11:02 | 2013-09-10 11:35 | GOODMAN - PGB060100-1 | 82 | 7.1 | Yes | Yes | 24.8 | 20.9 | 3.9 | 6553B81BF07B4505BCF8B84C938DB510 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.659% | 0.91341 | 16.64% | [5 empty] | Non-TXV | 8.659%
Lincoln | CA | 95648-2025 |  | 2013-09-10 | 2013-09-10 12:10 | 2013-09-10 12:10 | TRANE - 4A78A03DDAA | 82 | 0 | Yes | Yes | 19.7 | 17.8 | 2 | F7D3FC5828714D2D8A4A5E461499CC0A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3053 |  | 2013-11-20 | 2013-11-20 09:54 | 2013-11-20 09:54 | DAY & NIGHT - 7777UNK | 92 | 0 | Yes | Yes | 22.3 | 20.4 | 1.9 | A5D514A7DBF6417C8AE99381BEA9C937 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Orland | CA | 95963-1500 |  | 2013-09-10 | 2013-09-10 12:08 | 2013-09-10 12:30 | BRYANT - 577DNW036060 | 67 | 2.2 | Yes | Yes | 18.4 | 20.4 | -2 | 51785887E9AC4BC59B86E62D851862A7 |  | R410A | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Fresno | CA | 93726-5409 |  | 2013-09-09 | 2013-09-09 11:40 | 2013-09-09 12:42 | ICP - GPC030K080E | 51 | 4.7 | Yes | Yes | 17.2 | 20.1 | -2.9 | 83D8259B3EAA44C083EED2CB294D03E6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.216% | 0.90784 | 17.71% | [5 empty] | Non-TXV | 9.216%
Chico | CA | 95926-4741 |  | 2013-09-06 | 2013-09-06 14:53 | 2013-09-06 15:14 | PAYNE - 585HJWO24040ABAE | 68 | 9.1 | Yes | Yes | 16.9 | 18.7 | -1.8 | B44A98969EC64AAE900A1BF6E672EE29 |  | R22 | Non-TXV |  | 13.38% | 0.86618 | 25.72% | [5 empty] | Non-TXV | 13.38%
Stockton | CA | 95205-4358 |  | 2013-09-16 | 2013-09-16 10:27 | 2013-09-16 10:46 | OTHER - UNK | 69 | 2.2 | Yes | Yes | 17.4 | 17.2 | 0.2 | D09150793BAF4C758CD3C97EF00E7F8A |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Atwater | CA | 95301-2121 |  | 2013-09-09 | 2013-09-09 09:35 | 2013-09-09 10:00 | AMANA - RCE36C2A | 230 | 6.9 | Yes | Yes | 19.2 | 20.9 | -1.7 | 36238EC940DD479FABE0081A49F00849 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-5241 |  | 2013-10-02 | 2013-10-02 12:07 | 2013-10-02 12:09 | BDP - 585HJW36060ABAF | 102 | 10.2 | Yes | Yes | 23.7 | 18.2 | 5.5 | A8E63C6A68FF469E884BC156ED9D045A |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Willows | CA | 95988-2423 |  | 2013-09-09 | 2013-09-09 09:15 | 2013-09-09 09:15 | LENNOX - 13GCSXA-30-068X-230-1A | 106 | 0 | Yes | Yes | 19.7 | 21 | -1.3 | 9C0A207AD8524C75BD0A392AB313CF07 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1980 |  | 2013-09-30 | 2013-09-30 14:03 | 2013-09-30 14:04 | WEATHER KING - WRKA-030JK06E | 54 | 1.7 | Yes | Yes | 25.9 | 20.6 | 5.3 | 24FE091C6D3B42C6B4F786D139E1E8AC |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Lincoln | CA | 95648-1971 |  | 2013-09-25 | 2013-09-25 16:21 | 2013-09-25 16:21 | OTHER - CA5530VKD1 | 74 | 0 | Yes | Yes | 20.9 | 22 | -1.1 | A347E4FC0D4B4AD7A99DD7C809AB61A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-9643 |  | 2013-09-10 | 2013-09-10 11:37 | 2013-09-10 11:54 | RHEEM - RAKA036JAZ | 79 | 3.4 | Yes | Yes | 18.5 | 16.6 | 1.9 | D6AD29DFC1814F5DAD9B95EA64FEA574 |  | R22 | Non-TXV |  | 4.304% | 0.95696 | 8.271% | [5 empty] | Non-TXV | 4.304%
Copperopolis | CA | 95228-9766 |  | 2013-09-06 | 2013-09-06 16:11 | 2013-09-06 16:31 | PAYNE - UNK | 85 | 6 | Yes | Yes | 20.6 | 21.8 | -1.1 | ED4F8C20C402492FA57DCD4F9312ED81 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Merced | CA | 95340-2325 |  | 2013-09-16 | 2013-09-16 15:00 | 2013-09-16 15:01 | GOODMAN - PGB024050 | 54 | 7.1 | Yes | Yes | 26.6 | 21 | 5.6 | EC721CA68CB941279470DCADB613555B |  | R22 | Non-TXV |  | 13.15% | 0.86852 | 25.27% | [5 empty] | Non-TXV | 13.15%
Stockton | CA | 95205-7024 |  | 2013-09-16 | 2013-09-16 15:41 | 2013-09-16 16:00 | GOODMAN - GPG10480901A | 98 | 3.1 | Yes | Yes | 25.9 | 20.4 | 5.6 | AD55677A048847E4A665A75EB41791BC |  | R22 | Non-TXV |  | 3.163% | 0.96837 | 6.079% | [5 empty] | Non-TXV | 3.163%
Merced | CA | 95348-2248 |  | 2013-09-20 | 2013-09-20 18:54 | 2013-09-20 18:56 | BDP - 565BJ018 | 64 | 2.4 | Yes | Yes | 20.3 | 19.9 | 0.4 | 439111A7B0824454BE6B4FCEBDC68BBB |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95209-5049 |  | 2013-09-12 | 2013-09-12 13:09 | 2013-09-12 13:35 | PAYNE - 562GJ042 | 94 | 14.7 | Yes | Yes | 24.7 | 18.8 | 5.9 | A994E0BCF7724555880F128B085EA649 |  | R22 | Non-TXV |  | 15.64% | 0.84362 | 30.05% | [5 empty] | Non-TXV | 15.64%
Los Banos | CA | 93635-3089 |  | 2013-09-09 | 2013-09-09 12:24 | 2013-09-09 12:26 | GIBSON - 7I77UNK | 84 | 6 | Yes | Yes | 21 | 21.4 | -0.4 | 107456A44AED4CED888E4F882B3CB6FF |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Clovis | CA | 93612-4827 |  | 2013-09-27 | 2013-09-27 09:43 | 2013-09-27 09:46 | RHEEM - RRMAA030JK06X | 80 | 5 | Yes | Yes | 23.6 | 18.7 | 4.9 | 3572BBB8BA3B43C9AA2D9581927DEED3 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Stockton | CA | 95209-2718 |  | 2013-09-06 | 2013-09-06 13:17 | 2013-09-06 13:35 | BRYANT - 582ANW042090NAAG | 100 | 8.6 | Yes | Yes | 23.9 | 20.4 | 3.5 | 8AA986A9E5F14056AF810194ECBCA02E |  | R22 | Non-TXV |  | 8.6% | 0.914 | 16.53% | [5 empty] | Non-TXV | 8.6%
Manteca | CA | 95336-9177 |  | 2013-09-12 | 2013-09-12 12:10 | 2013-09-12 12:33 | GOODMAN - CKT60-1AB | 130 | 7.1 | Yes | Yes | 18.6 | 18.7 | -0.1 | 05CA1772735A4FF6A171059FF6107EA5 |  | R22 | Non-TXV |  | 5.462% | 0.94538 | 10.5% | [5 empty] | Non-TXV | 5.462%
Fresno | CA | 93722-4328 |  | 2013-09-10 | 2013-09-10 12:01 | 2013-09-10 12:02 | LENNOX - 10GCS024501PA | 52 | 8.2 | Yes | Yes | 22.9 | 20.2 | 2.7 | B9705405D1D84FBA91ACBC87FC2BD7A3 |  | R22 | Non-TXV |  | 15.77% | 0.84231 | 30.3% | [5 empty] | Non-TXV | 15.77%
Chico | CA | 95973-8205 |  | 2013-09-19 | 2013-09-19 14:38 | 2013-09-19 15:02 | PAYNE - 591ANX024000AAAF | 53 | 3.5 | Yes | Yes | 17.6 | 18.8 | -1.2 | F913C76126D946C686A2E8794B1B3DD6 |  | R22 | Non-TXV |  | 6.604% | 0.93396 | 12.69% | [5 empty] | Non-TXV | 6.604%
Fresno | CA | 93727-3536 |  | 2013-09-27 | 2013-09-27 10:20 | 2013-09-27 10:21 | RHEEM - RRMAA042JK08X | 114 | 8.7 | Yes | Yes | 22.7 | 18.7 | 4 | FE463D9B1BBE44C9BAA7989018ED2DA4 |  | R22 | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
Fresno | CA | 93722-1132 |  | 2013-09-10 | 2013-09-10 11:18 | 2013-09-10 11:20 | LENNOX - 12ACB424P | 128 | 17.3 | Yes | Yes | 25 | 22 | 3 | 9736EB87E62045239E23E63882CC75CA |  | R22 | Non-TXV |  | 13.52% | 0.86484 | 25.97% | [5 empty] | Non-TXV | 13.52%
Paso Robles | CA | 93446-4033 |  | 2013-09-06 | 2013-09-06 09:58 | 2013-09-06 10:17 | PAYNE - PA10JA042-C | 82 | -4.8 | Yes | Yes | 25.3 | 20.4 | 4.9 | 8BBBA2B96BE54663B525EA3E7303E8EA |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Stockton | CA | 95210-6772 |  | 2013-09-09 | 2013-09-09 14:04 | 2013-09-09 14:24 | YORK - H2RA060S06D | 118 | -6.9 | Yes | Yes | 14.4 | 14.4 | 0 | 0C06B4DA1D284EE8A15419952A1725D6 |  | R22 | Non-TXV |  | -5.847% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.847%
Tracy | CA | 95377-0208 |  | 2013-09-11 | 2013-09-11 13:46 | 2013-09-11 14:05 | BRYANT - 561CJ036-D | 82 | 2.6 | Yes | Yes | 24.5 | 18.5 | 6 | 17F7E3BA94D84357B33590BA8D3DC6E4 |  | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Orland | CA | 95963-1606 |  | 2013-09-12 | 2013-09-12 14:01 | 2013-09-12 14:20 | LENNOX - GCSZOR-411-100-3P | 70 | 2.4 | Yes | Yes | 17 | 18 | -1 | ACBF85885A914BE4B84D17A54BF3D651 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Fresno | CA | 93728-3213 |  | 2013-09-23 | 2013-09-23 10:48 | 2013-09-23 10:50 | YORK - D1NP048N09006A | 132 | 4.1 | Yes | Yes | 17.5 | 17.7 | -0.2 | F288261E0B60495384462CFC7E9F9095 |  | R22 | Non-TXV |  | 3.106% | 0.96894 | 5.969% | [5 empty] | Non-TXV | 3.106%
Chico | CA | 95926-4200 |  | 2013-09-06 | 2013-09-06 13:45 | 2013-09-06 13:45 | DAY & NIGHT - 770B018300 | 83 | 0 | Yes | Yes | 17.2 | 20.1 | -2.9 | C808E97A7D8D407FA4C752BAFBA4788C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-3326 |  | 2013-09-09 | 2013-09-09 14:02 | 2013-09-09 15:24 | AMERICAN STANDARD - 7A2036A100AZ | 101 | 3.9 | Yes | Yes | 17.1 | 19.9 | -2.8 | FB4A13AB4FDB4B24BAE991E2152929A9 |  | R22 | Non-TXV |  | 3.861% | 0.96139 | 7.421% | [5 empty] | Non-TXV | 3.861%
Stockton | CA | 95206-6226 |  | 2013-09-17 | 2013-09-17 11:52 | 2013-09-17 12:10 | CARRIER - 561CJ042-A | 80 | 3 | Yes | Yes | 19.9 | 18.2 | 1.7 | C2399CA16E86407DA2B48899E65B9C86 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Riverdale | CA | 93656-9483 |  | 2013-11-02 | 2013-11-02 15:22 | 2013-11-02 15:40 | RUUD - UAKA-030JAZ | 66 | 2.6 | Yes | Yes | 21 | 20.4 | 0.6 | 871C4D6CED0E4DB39E8DD323776EE54D |  | R22 | Non-TXV |  | 3.939% | 0.96061 | 7.571% | [5 empty] | Non-TXV | 3.939%
Stockton | CA | 95209-2329 |  | 2013-09-19 | 2013-09-19 10:49 | 2013-09-19 11:15 | AMERICAN STANDARD - 7A2048A100A0 | 156 | -9.2 | Yes | Yes | 23 | 18.7 | 4.3 | 26F32CD2C3514B20B8CFA81E99C74D5A |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Stockton | CA | 95210-2048 |  | 2013-09-09 | 2013-09-09 12:04 | 2013-09-09 12:21 | PAYNE - PY3PNA042060NA | 173 | 5.9 | Yes | Yes | 21.5 | 19.5 | 2 | 8AFA73CE205A441F9B897C90271960C1 |  | R22 | Non-TXV |  | 3.41% | 0.9659 | 6.554% | [5 empty] | Non-TXV | 3.41%
Paradise | CA | 95969-5679 |  | 2013-10-08 | 2013-10-08 13:00 | 2013-10-08 13:30 | TEMPSTAR - TYA330GKD300 | 70 | 2.7 | Yes | Yes | 17.2 | 20.2 | -3 | C50EE7B72C0042328663564B5010FF1D |  | R410A | TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | TXV | 3.857%
Jackson | CA | 95642-2453 |  | 2013-09-10 | 2013-09-10 14:30 | 2013-09-10 14:30 | HEIL - UNK | 85 | 0 | Yes | Yes | 25.5 | 20.2 | 5.3 | 81B43E7B5624434D9C26753E603E18D6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-7010 |  | 2013-09-12 | 2013-09-12 16:42 | 2013-09-12 16:42 | DAY & NIGHT - 565BJ036 | 84 | 0 | Yes | Yes | 19.6 | 19.9 | -0.3 | E087DAD6D730442EBB4F885FB234957A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95965-4036 |  | 2013-09-16 | 2013-09-16 09:49 | 2013-09-16 10:12 | DAY & NIGHT - PGD336060K001C1 | 106 | 3.9 | Yes | Yes | 22 | 18.8 | 3.2 | 0E723CE0E37540BF870B192D68D1B416 |  | R410A | TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | TXV | 3.679%
Atwater | CA | 95301-4247 |  | 2013-09-10 | 2013-09-10 13:15 | 2013-09-10 13:50 | AMERICAN STANDARD - TTR030C100A0 | 74 | 9.9 | Yes | Yes | 21.6 | 21.7 | 0 | 132C3EFA25A245EF81C2EA46358B5DE4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.38% | 0.86622 | 25.71% | [5 empty] | Non-TXV | 13.38%
Corning | CA | 96021-2102 |  | 2013-09-17 | 2013-09-17 15:13 | 2013-09-17 15:36 | RUUD - UAMC-036JAZ | 93 | 13.4 | Yes | Yes | 14.8 | 17.7 | -2.9 | 0FDD1F7788F440CAA5B09CD3F8C99612 |  | R22 | Non-TXV |  | 14.41% | 0.85591 | 27.69% | [5 empty] | Non-TXV | 14.41%
Madera | CA | 93637-6222 |  | 2013-09-18 | 2013-09-18 13:47 | 2013-09-18 13:49 | AIRE-FLO - 10GCS042X756PB | 73 | 7.7 | Yes | Yes | 25.2 | 19.8 | 5.4 | 5094C87476CF4F5EB35233BCF5F82F27 |  | R22 | Non-TXV |  | 10.55% | 0.89452 | 20.27% | [5 empty] | Non-TXV | 10.55%
Madera | CA | 93638-2836 |  | 2013-09-24 | 2013-09-24 13:19 | 2013-09-24 13:21 | YORK - B1HP036A06A | 132 | 6.4 | Yes | Yes | 24.7 | 20.2 | 4.5 | 9CDF754CFC4C429C9842D2DF50A869A6 |  | R22 | Non-TXV |  | 4.848% | 0.95152 | 9.318% | [5 empty] | Non-TXV | 4.848%
Stockton | CA | 95206-3889 |  | 2013-09-25 | 2013-09-25 12:10 | 2013-09-25 12:36 | OTHER - 4AC13L48P | 124 | 3.7 | Yes | Yes | 16.6 | 16.4 | 0.2 | D56FA1F76EEC43DCA61C67C8179B4840 |  | R410A | Non-TXV |  | 2.984% | 0.97016 | 5.734% | [5 empty] | Non-TXV | 2.984%
Chico | CA | 95926-3234 |  | 2013-10-02 | 2013-10-02 11:50 | 2013-10-02 12:31 | BRYANT - 561CJ036-E | 70 | 3.3 | Yes | Yes | 17.5 | 20.4 | -2.9 | 0C4596EBD2BF491FBAA213A936AB8071 |  | R22 | TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | TXV | 4.714%
Fresno | CA | 93722-8631 |  | 2013-10-03 | 2013-10-03 14:50 | 2013-10-03 14:52 | LENNOX - HS290365P | 70 | 8.7 | Yes | Yes | 24.3 | 19.3 | 5 | 974EA600FBBE4B3A8EEB05C4F3B70D76 |  | R22 | Non-TXV |  | 12.43% | 0.87571 | 23.88% | [5 empty] | Non-TXV | 12.43%
Fresno | CA | 93722-8631 |  | 2013-10-03 | 2013-10-03 15:08 | 2013-10-03 15:14 | LENNOX - HS290365P | 70 | 7.6 | Yes | Yes | 22.1 | 17.2 | 4.9 | D12BF6C521834FFDBE047805CF6A50BB |  | R22 | Non-TXV |  | 10.86% | 0.89143 | 20.87% | [5 empty] | Non-TXV | 10.86%
Stockton | CA | 95207-1305 |  | 2013-09-13 | 2013-09-13 09:52 | 2013-09-13 10:11 | HEIL - HAC036AKA1 | 80 | -7.5 | Yes | Yes | 21.7 | 18.3 | 3.4 | 585BFBE9DC444399B9ACD69E1A153673 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Marysville | CA | 95901-5442 |  | 2013-09-10 | 2013-09-10 15:26 | 2013-09-10 16:07 | GOODMAN - GSC13030AE | 117 | 4.3 | Yes | Yes | 19 | 19.5 | -0.5 | 5AF5F65C2A134351B3947332580B2AB5 |  | R22 | TXV |  | 3.675% | 0.96325 | 7.063% | [5 empty] | TXV | 3.675%
Stockton | CA | 95205-7743 |  | 2013-09-16 | 2013-09-16 10:59 | 2013-09-16 11:16 | RHEEM - RRMA-A036JK06X | 99 | -5.8 | Yes | Yes | 21.3 | 18.2 | 3.1 | 9BBCC2E7E8DB45F8A15B39F7E912FE92 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Stockton | CA | 95215-6019 |  | 2013-09-12 | 2013-09-12 09:50 | 2013-09-12 10:09 | BRYANT - 582ANW036060AAAF | 56 | 2 | Yes | Yes | 17 | 17.2 | -0.1 | 4BDE3F2BD12D4E11BA8DD2910F20B61D |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Stockton | CA | 95207-4456 |  | 2013-09-17 | 2013-09-17 09:44 | 2013-09-17 10:04 | RHEEM - AB36B10 | 98 | -9.2 | Yes | Yes | 18.7 | 18.8 | -0.1 | 8C1EE53AE55B4E39B1C33E4ED2084BA0 |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Fresno | CA | 93722-7117 |  | 2013-09-20 | 2013-09-20 10:44 | 2013-09-20 10:46 | CARRIER - N/A | 90 | 8 | Yes | Yes | 17 | 19.8 | -2.8 | F3CD1A91C1834E9C952CF5B8F90615AE |  | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Stockton | CA | 95215-6062 |  | 2013-09-12 | 2013-09-12 09:07 | 2013-09-12 09:24 | GUARDIAN - GCGD36S41S3A | 73 | 9.1 | Yes | Yes | 21.9 | 16.4 | 5.5 | 034FC7ADEF59466F97BC3DA87C201B40 |  | R22 | TXV |  | 12.47% | 0.87534 | 23.96% | [5 empty] | TXV | 12.47%
Placerville | CA | 95667-4420 |  | 2013-09-18 | 2013-09-18 09:03 | 2013-09-18 09:03 | PAYNE - PA10JA30-G | 70 | 0 | Yes | Yes | 35 | 21.4 | 13.6 | A75B15D094B04060A71E8EDA46D0D554 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-3312 |  | 2013-09-09 | 2013-09-09 13:18 | 2013-09-09 13:41 | YORK - D1NP036N07206A | 98 | 4.2 | Yes | Yes | 17.1 | 17.5 | -0.4 | EC00B11001214C54AF51292DBD53637F |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Burson | CA | 95225-0000 |  | 2013-09-16 | 2013-09-16 12:36 | 2013-09-16 13:15 | RUUD - URKAA042JK08E | 69 | 2.5 | Yes | Yes | 21.4 | 20.4 | 1 | 78BB98868DB145D3911AA9CA2ECB3302 |  | R22 | Non-TXV |  | 3.623% | 0.96377 | 6.963% | [5 empty] | Non-TXV | 3.623%
Coarsegold | CA | 93614-9649 |  | 2013-09-12 | 2013-09-12 13:36 | 2013-09-12 13:38 | GOODMAN - FGB036073-1A | 60 | 3.7 | Yes | Yes | 17.6 | 18.2 | -0.6 | 91EAD49A6BCE4B39BDC61D2E5C862564 |  | R22 | Non-TXV |  | 6.167% | 0.93833 | 11.85% | [5 empty] | Non-TXV | 6.167%
Paradise | CA | 95969-5303 |  | 2013-09-26 | 2013-09-26 13:47 | 2013-09-26 13:47 | PAYNE - PY2PNB0360AAA | 48 | 0 | Yes | Yes | 24.5 | 18.6 | 5.9 | 622B8776D8014B28B4F932FDD720A496 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-6080 |  | 2013-09-26 | 2013-09-26 14:00 | 2013-09-26 14:17 | KENMORE - PGF036K060A | 71 | -4.2 | Yes | Yes | 21.1 | 18.7 | 2.4 | 9B0026D128604142BE5CFC58F5AC9E13 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Stockton | CA | 95215-5405 |  | 2013-09-26 | 2013-09-26 12:01 | 2013-09-26 12:21 | RHEEM - UNK | 73 | -4.3 | Yes | Yes | 23 | 19.1 | 3.9 | F66A19A3EFC4409A92A41CB1285DAFD5 |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Tracy | CA | 95376-1819 |  | 2013-09-11 | 2013-09-11 10:49 | 2013-09-11 11:17 | RUUD - UAKA-042JAZ | 79 | 8.3 | Yes | Yes | 24.3 | 19.5 | 4.8 | 61914C454D01456BAA50F24F8766FABD |  | R22 | Non-TXV |  | 10.51% | 0.89494 | 20.19% | [5 empty] | Non-TXV | 10.51%
Manteca | CA | 95337-8654 |  | 2013-09-16 | 2013-09-16 09:48 | 2013-09-16 10:10 | ICP - GPCM036K060P | 86 | 2.9 | Yes | Yes | 15.1 | 17.7 | -2.6 | 71EB43BAFE924E74B870236531221C54 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.372% | 0.96628 | 6.48% | [5 empty] | Non-TXV | 3.372%
Fresno | CA | 93722-2531 |  | 2013-09-10 | 2013-09-10 09:58 | 2013-09-10 10:00 | LENNOX - GCS26X042751PA | 133 | 16.6 | Yes | Yes | 26.4 | 20.7 | 5.7 | EAF8D29A4C90494987739BB0A279A4ED |  | R22 | Non-TXV |  | 12.48% | 0.87519 | 23.99% | [5 empty] | Non-TXV | 12.48%
Manteca | CA | 95337-5145 |  | 2013-09-12 | 2013-09-12 13:36 | 2013-09-12 14:06 | YORK - D2NP030N03606NXA | 73 | 2.7 | Yes | Yes | 16.6 | 17.6 | -1 | 3A76324B3CEF4B81905975F1C9043CE6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Tracy | CA | 95376-5235 |  | 2013-09-11 | 2013-09-11 13:12 | 2013-09-11 13:29 | RUUD - UAHE-042JAS | 101 | 3.1 | Yes | Yes | 24.4 | 19.3 | 5.1 | A7F04B86E2B24D5CBE16AB35FB9A9258 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Stockton | CA | 95210-2145 |  | 2013-09-16 | 2013-09-16 12:43 | 2013-09-16 13:03 | GOODMAN - CK36-1A | 73 | 2.4 | Yes | Yes | 21.9 | 18.8 | 3.1 | AD1F92A1E21F44CDAFCD0540406AA15C |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Chico | CA | 95926-5303 |  | 2013-09-27 | 2013-09-27 12:05 | 2013-09-27 12:28 | DAY & NIGHT - 591ANX024000AAAA | 55 | 1.6 | Yes | Yes | 22 | 20.4 | 1.6 | 23403259CD3F41C5A9EE425AFD8FC657 |  | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Riverbank | CA | 95367-2920 |  | 2013-09-12 | 2013-09-12 16:10 | 2013-09-12 16:37 | RUUD - URKA-A036JK08X | 62 | 4.9 | Yes | Yes | 20.3 | 20.2 | 0.1 | 27A4A25167E14415AC9EFBBE2BEB37D2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.903% | 0.92097 | 15.19% | [5 empty] | Non-TXV | 7.903%
Stockton | CA | 95204-2746 |  | 2013-09-16 | 2013-09-16 14:49 | 2013-09-16 15:07 | BDP - 567018RCU | 37 | 12.4 | Yes | Yes | 20.4 | 18.5 | 1.9 | 0A3A9A4ED82C49ABA77A56D1CE51B439 |  | R22 | Non-TXV |  | 33.51% | 0.66486 | 64.41% | [5 empty] | Non-TXV | 33.51%
Tracy | CA | 95376-7038 |  | 2013-09-23 | 2013-09-23 11:08 | 2013-09-23 11:51 | BRYANT - 561CJ042-A | 80 | -4.7 | Yes | Yes | 21.3 | 18.1 | 3.2 | 42DA414C80434FC8B19C5009D6AE2934 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Oakhurst | CA | 93644-9523 |  | 2013-09-12 | 2013-09-12 12:16 | 2013-09-12 12:17 | BRYANT - 583ANW060115AAAAG | 129 | 7.2 | Yes | Yes | 20.3 | 18.9 | 1.4 | 6409A60DE5C44A97A077127E5C33B894 |  | R22 | Non-TXV |  | 5.581% | 0.94419 | 10.73% | [5 empty] | Non-TXV | 5.581%
Oakdale | CA | 95361-8003 |  | 2013-09-11 | 2013-09-11 13:54 | 2013-09-11 14:17 | RUUD - CBD | 64 | 4.9 | Yes | Yes | 22.6 | 18.3 | 4.3 | C886BA676AC4435481BEAB52564D82B3 |  | R22 | Non-TXV |  | 7.656% | 0.92344 | 14.71% | [5 empty] | Non-TXV | 7.656%
Orange Cove | CA | 93646-2482 |  | 2013-10-02 | 2013-10-02 11:44 | 2013-10-02 12:23 | UNITARY PRODUCTS GROUP - HP030X1221A | 105 | 5 | Yes | Yes | 19.6 | 20.7 | -1.1 | 0AB4BD444EA44317A808A424CE469D6D |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Tracy | CA | 95376-2023 |  | 2013-09-11 | 2013-09-11 10:10 | 2013-09-11 10:27 | PAYNE - PA10JA042-C | 81 | 2.7 | Yes | Yes | 24.1 | 20.2 | 3.9 | BF9D3816AB9D454681E449E9270A2D72 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93711-6005 |  | 2013-09-06 | 2013-09-06 14:04 | 2013-09-06 14:56 | AMERICAN STANDARD - YCY036G1H0AD | 130 | 4.9 | Yes | Yes | 21.5 | 20 | 1.6 | 0A198FC086A1446DB674D9161354BF38 |  | R22 | Non-TXV |  | 3.769% | 0.96231 | 7.244% | [5 empty] | Non-TXV | 3.769%
Fresno | CA | 93706-3817 |  | 2013-09-26 | 2013-09-26 10:27 | 2013-09-26 10:28 | ICP - PGAD36D1K | 100 | 6 | Yes | Yes | 23.3 | 19.5 | 3.8 | 371F741AFBF446328644F59BDAF77D4C |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Valley Springs | CA | 95252-9340 |  | 2013-09-11 | 2013-09-11 13:19 | 2013-09-11 14:42 | RHEEM - UNK | 160 | 6.9 | Yes | Yes | 21.5 | 19.2 | 2.3 | 930C9DF556F344348EA7A65BEA215B1A |  | R22 | Non-TXV |  | 4.312% | 0.95688 | 8.288% | [5 empty] | Non-TXV | 4.312%
Lincoln | CA | 95648-2071 |  | 2013-09-17 | 2013-09-17 11:53 | 2013-09-17 11:53 | AMANA - PGD42C0902E | 120 | 0 | Yes | Yes | 24.7 | 19.5 | 5.2 | 3EF77EADDAE94DB3AA2C6190E6D216BE |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-4889 |  | 2013-09-13 | 2013-09-13 13:48 | 2013-09-13 14:16 | CARRIER - 38THO30310 | 69 | -6.5 | Yes | Yes | 19.3 | 17 | 2.3 | 7D4DA612CC66441AA2FB03B2E53E6ECE |  | R22 | Non-TXV |  | -9.42% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.42%
Oroville | CA | 95966-6032 |  | 2013-09-16 | 2013-09-16 13:32 | 2013-09-16 13:53 | RUUD - RRNL-B030JK06E | 76 | 3.6 | Yes | Yes | 18 | 18.8 | -0.8 | 8C4D27DCE5C54394AFD41455EE5F616F |  | R410A | TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | TXV | 4.737%
Orange Cove | CA | 93646-2482 |  | 2013-10-02 | 2013-10-02 12:25 | 2013-10-02 12:48 | UNITARY PRODUCTS GROUP - HP030X1221A | 105 | 3.6 | Yes | Yes | 20.5 | 20.8 | -0.3 | 73C7D013A13B48738AEC5EB7F39132DF |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Willows | CA | 95988-3310 |  | 2013-09-12 | 2013-09-12 09:12 | 2013-09-12 09:48 | DAY & NIGHT - 587ANZ036080AAAF | 70 | 6.7 | Yes | Yes | 18.3 | 20.1 | -1.8 | A23AEB9D64264515AF24F9BF82040062 |  | R22 | Non-TXV |  | 9.571% | 0.90429 | 18.39% | [5 empty] | Non-TXV | 9.571%
Madera | CA | 93637-5917 |  | 2013-09-18 | 2013-09-18 14:17 | 2013-09-18 14:19 | CARRIER - 38BRB048300 | 164 | 18.5 | Yes | Yes | 23.9 | 19.9 | 4 | FEF4C824128947DA8A3E22758762B950 |  | R22 | TXV |  | 11.28% | 0.8872 | 21.68% | [5 empty] | TXV | 11.28%
Stockton | CA | 95205-7869 |  | 2013-09-12 | 2013-09-12 12:16 | 2013-09-12 12:34 | OTHER - UNK | 96 | 3.7 | Yes | Yes | 20.1 | 17.5 | 2.7 | C43CDC8EE6E2474CAE28932C3813C106 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.854% | 0.96146 | 7.407% | [5 empty] | Non-TXV | 3.854%
Lathrop | CA | 95330-8826 |  | 2013-09-16 | 2013-09-16 12:30 | 2013-09-16 12:48 | GOODMAN - UNK | 128 | -12 | Yes | Yes | 18.2 | 17.5 | 0.7 | C0964598496B4979AA10BA98FEF86DAB |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Oakdale | CA | 95361-3444 |  | 2013-09-11 | 2013-09-11 14:59 | 2013-09-11 15:21 | RHEEM - RAMA-036JAZ | 96 | 3.5 | Yes | Yes | 22.8 | 19.7 | 3.1 | 496099974ED743009343A64486DDB5B3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.646% | 0.96354 | 7.006% | [5 empty] | Non-TXV | 3.646%
Cool | CA | 95614-9501 |  | 2013-10-03 | 2013-10-03 10:16 | 2013-10-03 10:16 | RHEEM - 13PJL30A01 | 101 | 0 | Yes | Yes | 25.1 | 20.4 | 4.7 | A87CAF2EAA924565AA3C880655D710C2 |  | R410A | TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-9691 |  | 2013-09-13 | 2013-09-13 11:43 | 2013-09-13 12:10 | DAY & NIGHT - 591AN036-A | 84 | 8.7 | Yes | Yes | 17.8 | 19.7 | -1.9 | 5457664D7CDA421D9ABF51F614478913 |  | R22 | Non-TXV |  | 10.36% | 0.89643 | 19.9% | [5 empty] | Non-TXV | 10.36%
Lathrop | CA | 95330-9691 |  | 2013-09-13 | 2013-09-13 12:03 | 2013-09-13 12:26 | DAY & NIGHT - 591ANX024000AAA | 84 | 5 | Yes | Yes | 19.3 | 20.6 | -1.3 | 71DA366659564DC29CEAA746976AD29A |  | R22 | Non-TXV |  | 5.952% | 0.94048 | 11.44% | [5 empty] | Non-TXV | 5.952%
Nevada City | CA | 95959-2802 |  | 2013-09-11 | 2013-09-11 10:51 | 2013-09-11 10:51 | LENNOX - HS29-036-1P | 73 | 0 | Yes | Yes | 25.1 | 19.9 | 5.2 | 1E6ABCDB531F4624ADE7664902D03107 |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5232 |  | 2013-09-13 | 2013-09-13 11:34 | 2013-09-13 11:35 | BRYANT - 561CJ042-A | 80 | 2.6 | Yes | Yes | 18.9 | 18 | 0.9 | 928329890B1E4BFCA9D41DD308084659 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Manteca | CA | 95336-3428 |  | 2013-09-20 | 2013-09-20 10:22 | 2013-09-20 10:46 | AMANA - PGD36C0702E | 110 | 4.9 | Yes | Yes | 22.9 | 19.6 | 3.3 | 4D64B9AF64EB4DB189BE463B164AECBD |  | R22 | Non-TXV |  | 4.455% | 0.95545 | 8.561% | [5 empty] | Non-TXV | 4.455%
Stockton | CA | 95210-6751 |  | 2013-09-23 | 2013-09-23 12:16 | 2013-09-23 12:35 | BDP - 561AJ042-D | 80 | -4.7 | Yes | Yes | 14.6 | 17.5 | -2.9 | AE0CB16E041E4654A30FC1262083D9D3 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Los Banos | CA | 93635-6412 |  | 2013-09-13 | 2013-09-13 12:59 | 2013-09-13 13:00 | BRYANT - 563CN060-G | 206 | 6.3 | Yes | Yes | 22.5 | 19 | 3.5 | F3B792305230467287FFCFC52BD49523 |  | R22 | Non-TXV |  | 3.058% | 0.96942 | 5.877% | [5 empty] | Non-TXV | 3.058%
Red Bluff | CA | 96080-4903 |  | 2013-09-11 | 2013-09-11 16:18 | 2013-09-11 16:39 | RUUD - UAKA-030JA2 | 62 | 9.1 | Yes | Yes | 15.6 | 18 | -2.4 | CDF0604D3B844BE9BA0F57E313477AA5 |  | R22 | Non-TXV |  | 14.68% | 0.85323 | 28.21% | [5 empty] | Non-TXV | 14.68%
Stockton | CA | 95219-7173 |  | 2013-09-16 | 2013-09-16 10:45 | 2013-09-16 11:04 | RHEEM - RAMB-036JBZ | 93 | 4.1 | Yes | Yes | 19.5 | 20.4 | -0.9 | 90C39DAA3B76474D8E4048C9AE92FD24 |  | R22 | Non-TXV |  | 4.409% | 0.95591 | 8.472% | [5 empty] | Non-TXV | 4.409%
Stockton | CA | 95219-7173 |  | 2013-09-16 | 2013-09-16 11:06 | 2013-09-16 11:30 | RHEEM - RAMB-036JBZ | 93 | 7.5 | Yes | Yes | 20.8 | 19.9 | 0.9 | E22F4F482BC04F7CBB0F8AC7870005EC |  | R22 | Non-TXV |  | 8.065% | 0.91935 | 15.5% | [5 empty] | Non-TXV | 8.065%
Los Banos | CA | 93635-5305 |  | 2013-09-13 | 2013-09-13 12:12 | 2013-09-13 12:13 | RUUD - UAKA-060JAS | 112 | 3.8 | Yes | Yes | 21.3 | 19.5 | 1.8 | 2C5E420B1D2F40E1BB840A0D2CCEB1FE |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Fresno | CA | 93705-0209 |  | 2013-09-16 | 2013-09-16 09:39 | 2013-09-16 09:41 | BDP - 588ANW036080ACAF | 67 | 7.1 | Yes | Yes | 21.2 | 19.4 | 1.8 | 8A369B9604BF44AE9CD52C9D1047AEBF |  | R22 | Non-TXV |  | 10.6% | 0.89403 | 20.37% | [5 empty] | Non-TXV | 10.6%
Los Banos | CA | 93635-5359 |  | 2013-09-20 | 2013-09-20 09:46 | 2013-09-20 09:48 | BRYANT - 561CJ030 | 71 | 8.2 | Yes | Yes | 22.1 | 19.3 | 2.8 | 4DD00C25CB3A484A99876B96244FB34D |  | R22 | TXV |  | 11.55% | 0.88451 | 22.2% | [5 empty] | TXV | 11.55%
Nevada City | CA | 95959-9481 |  | 2013-09-11 | 2013-09-11 14:28 | 2013-09-11 14:28 | LENNOX - HS29-060-3P | 128 | 0 | Yes | Yes | 17.7 | 19.7 | -2 | B22E0BE4380D4376B458C9F0F9F14596 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-5923 |  | 2013-09-12 | 2013-09-12 13:52 | 2013-09-12 14:09 | BRYANT - 582ANW036060NBAF | 68 | -6.4 | Yes | Yes | 22 | 17.7 | 4.3 | 464E5E257AEE4887AAB394AD629BDBCC |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Diamond Springs | CA | 95619-9704 |  | 2013-09-06 | 2013-09-06 11:41 | 2013-09-06 11:41 | GOODMAN - GSC130601BC | 169 | 0 | Yes | Yes | 26.7 | 20.9 | 5.8 | 5B7E3A8179FD4DD3AFCCF282991E2352 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-4833 |  | 2013-09-16 | 2013-09-16 14:36 | 2013-09-16 15:06 | RUUD - URKA-A030JK06X | 79 | 2.6 | Yes | Yes | 19.1 | 19.9 | -0.8 | 9C78E200F4D54A9188B89F367F65DBC2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Lincoln | CA | 95648-1859 |  | 2013-09-25 | 2013-09-25 15:34 | 2013-09-25 15:34 | BRYANT - 582ANW030060AAAD | 59 | 0 | Yes | Yes | 25.6 | 20.9 | 4.7 | 1877E356CE61407A9AE8A20C75AFC9CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5529 |  | 2013-10-08 | 2013-10-08 15:28 | 2013-10-08 16:12 | BDP - 561CJ060-A | 152 | 10.4 | Yes | Yes | 26.4 | 21.9 | 4.5 | 1CDCDC465C4B44BF9B922F096BE92CDF |  | R22 | TXV |  | 6.842% | 0.93158 | 13.15% | [5 empty] | TXV | 6.842%
Los Banos | CA | 93635-5388 |  | 2013-09-23 | 2013-09-23 08:41 | 2013-09-23 08:44 | BRYANT - 561CJ060A | 152 | 6.1 | Yes | Yes | 23.3 | 17.7 | 5.6 | E406F21B14F94F4AAC0F87C0FB118CDF |  | R22 | TXV |  | 4.013% | 0.95987 | 7.712% | [5 empty] | TXV | 4.013%
Redwood City | CA | 94061-2231 |  | 2013-10-14 | 2013-10-14 16:02 | 2013-10-14 16:18 | CARRIER - 24APA536A300 | 161 | 5.9 | Yes | Yes | 23 | 19.3 | 3.7 | 082C644825D444D98544CAC2A3822F5A |  | R410A | TXV |  | 3.665% | 0.96335 | 7.043% | [5 empty] | TXV | 3.665%
Stockton | CA | 95207-3613 |  | 2013-09-13 | 2013-09-13 12:50 | 2013-09-13 13:25 | DAY & NIGHT - UNK | 85 | 17.2 | Yes | Yes | 21.5 | 18.8 | 2.7 | BAFBB18E5ADA4BFAB1DE745FE42F51F4 |  | R22 | Non-TXV |  | 20.24% | 0.79765 | 38.89% | [5 empty] | Non-TXV | 20.24%
Los Banos | CA | 93635-3151 |  | 2013-09-20 | 2013-09-20 12:06 | 2013-09-20 12:07 | GOODMAN - CK361B | 76 | 10.5 | Yes | Yes | 22.5 | 20.4 | 2.1 | 7A72F97543C2479A9335932A478D4AD1 |  | R22 | Non-TXV |  | 13.82% | 0.86184 | 26.55% | [5 empty] | Non-TXV | 13.82%
Cool | CA | 95614-2138 |  | 2013-09-20 | 2013-09-20 11:45 | 2013-09-20 11:45 | TRANE - TTX048C100A0 | 160 | 0 | Yes | Yes | 25.4 | 21.9 | 3.6 | E3199D52D5F345B989D79E46933844FE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2946 |  | 2013-09-26 | 2013-09-26 13:44 | 2013-09-26 13:46 | OTHER - UNK | 76 | 6.2 | Yes | Yes | 26.9 | 20.9 | 6 | 8F8853E70FBE41E3A44EAD77A77DA5D2 |  | R22 | Non-TXV |  | 8.158% | 0.91842 | 15.68% | [5 empty] | Non-TXV | 8.158%
Madera | CA | 93637-2959 |  | 2013-09-18 | 2013-09-18 11:40 | 2013-09-18 11:42 | RUUD - URGG05N36JKR | 75 | 8.3 | Yes | Yes | 23.1 | 19.9 | 3.2 | 1935870197D9487A9E167B6F0E4A88E9 |  | R22 | Non-TXV |  | 11.07% | 0.88933 | 21.27% | [5 empty] | Non-TXV | 11.07%
Chico | CA | 95928-8501 |  | 2013-09-25 | 2013-09-25 14:47 | 2013-09-25 14:47 | OTHER - R2A324GKR200 | 65 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | AFE8FB1BBEC6410F8A898BDA71DE2372 |  | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3636 |  | 2013-09-23 | 2013-09-23 10:09 | 2013-09-23 10:29 | BRYANT - 582ANW036060AAAF | 56 | 1.9 | Yes | Yes | 21.1 | 18.7 | 2.4 | E77DEDE8C75F4ED7BC459D876DBD9594 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Clovis | CA | 93619-9007 |  | 2013-10-04 | 2013-10-04 12:02 | 2013-10-04 12:04 | GOODMAN - GPG1360090M41AD | 185 | 5.5 | Yes | Yes | 25.9 | 19.9 | 6 | 818B116A0C9840948FCD8126C871BE1A |  | R410A | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Riverdale | CA | 93656-9344 |  | 2013-10-03 | 2013-10-03 16:45 | 2013-10-03 17:29 | RHEEM - RRKA-A042JKO8E | 69 | 3 | Yes | Yes | 24 | 20.6 | 3.4 | 0B4337B09750401BABC5F5D8B44BBC6D | Add refrigerant: 2.1 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Tracy | CA | 95376-4605 |  | 2013-09-11 | 2013-09-11 11:40 | 2013-09-11 12:03 | AMANA - RCB60B2A | 123 | 3.7 | Yes | Yes | 23.3 | 19.5 | 3.8 | 7D69430DDF9D4F0CBB8941778F5626E5 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.781% | [5 empty] | Non-TXV | 3.008%
Los Banos | CA | 93635-5216 |  | 2013-09-30 | 2013-09-30 12:39 | 2013-09-30 12:40 | YORK - H4DB036S06A | 73 | 10.4 | Yes | Yes | 20.5 | 18.2 | 2.3 | FF88477841094566A396B2DFB7FCC13A |  | R22 | Non-TXV |  | 14.25% | 0.85753 | 27.38% | [5 empty] | Non-TXV | 14.25%
Madera | CA | 93637-6246 |  | 2013-09-18 | 2013-09-18 13:17 | 2013-09-18 13:19 | AIRE-FLO - 38ETG030300 | 133 | 9.5 | Yes | Yes | 23.1 | 19.3 | 3.8 | BBCEB88C40FE43AAAC74041A27ED9FB9 |  | R410A | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Los Banos | CA | 93635-3069 |  | 2013-09-20 | 2013-09-20 09:14 | 2013-09-20 09:18 | NORDYNE - UNK | 76 | 5.4 | Yes | Yes | 19.4 | 18.2 | 1.2 | 7CFE30FB3CAA4E9EA553ADA903504B92 |  | R22 | Non-TXV |  | 7.105% | 0.92895 | 13.65% | [5 empty] | Non-TXV | 7.105%
Nevada City | CA | 95959-9335 |  | 2013-09-12 | 2013-09-12 10:47 | 2013-09-12 10:47 | PAYNE - 565BJ036-A | 80 | 0 | Yes | Yes | 23.7 | 20.1 | 3.6 | 7702B2EDA5C842C2ADBDD240AE368A44 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-4449 |  | 2013-09-11 | 2013-09-11 16:56 | 2013-09-11 17:23 | CARRIER - 568EJX048000ACAA | 178 | 7.2 | Yes | Yes | 26.2 | 20.3 | 6 | B78A15029BA3404682E5EACC33BBE280 |  | R22 | Non-TXV |  | 4.045% | 0.95955 | 7.773% | [5 empty] | Non-TXV | 4.045%
Willows | CA | 95988-2104 |  | 2013-09-09 | 2013-09-09 10:42 | 2013-09-09 11:38 | DAY & NIGHT - C4A436GKA200 | 163 | 6.1 | Yes | Yes | 17.3 | 20.2 | -2.9 | B5836F218C71495FA73D255E6E8197D0 |  | R410A | TXV |  | 3.742% | 0.96258 | 7.192% | [5 empty] | TXV | 3.742%
Chico | CA | 95926-4494 |  | 2013-09-24 | 2013-09-24 13:30 | 2013-09-24 13:52 | DAY & NIGHT - 5856J024050 | 54 | 1.7 | Yes | Yes | 23 | 18.6 | 4.4 | 3965F0D0CD87474CBD3D4164E8AE7EFE |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Lathrop | CA | 95330-8818 |  | 2013-09-19 | 2013-09-19 10:45 | 2013-09-19 11:02 | CARRIER - 38BRC048370 | 128 | 3.8 | Yes | Yes | 25.7 | 20.4 | 5.3 | 8282CA6A597C48AA92D2653B1ABF56A2 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Los Banos | CA | 93635-5217 |  | 2013-09-13 | 2013-09-13 10:40 | 2013-09-13 10:41 | BRYANT - 561CJ036-E | 72 | 3.3 | Yes | Yes | 19.5 | 20.2 | -0.7 | 582DCE7EF669497E930D8898F9F0E5F6 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Los Banos | CA | 93635-5217 |  | 2013-09-13 | 2013-09-13 10:42 | 2013-09-13 10:44 | BRYANT - 561CJ036-E | 72 | 4 | Yes | Yes | 18.2 | 20.9 | -2.7 | E542186275E44BC5A203C0B94905A64F |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Fresno | CA | 93726-5528 |  | 2013-09-20 | 2013-09-20 17:25 | 2013-09-20 18:10 | RHEEM - RRNA-B036JK06X | 83 | 4.1 | Yes | Yes | 17.4 | 20.4 | -3 | F2F04795B6F84B26A63BB3AB5A8A81E8 |  | R22 | Non-TXV |  | 4.94% | 0.9506 | 9.493% | [5 empty] | Non-TXV | 4.94%
Merced | CA | 95340-2425 |  | 2013-09-16 | 2013-09-16 16:11 | 2013-09-16 16:13 | RHEEM - UNK | 67 | 8.2 | Yes | Yes | 30.4 | 24.8 | 5.6 | 3BDCF14B23AE4A3EA2C76CB2F780D7F4 |  | R22 | Non-TXV |  | 12.24% | 0.87761 | 23.52% | [5 empty] | Non-TXV | 12.24%
Stockton | CA | 95209-1204 |  | 2013-09-13 | 2013-09-13 15:00 | 2013-09-13 15:17 | HEIL - HAC036AKA1 | 80 | 6.7 | Yes | Yes | 24.6 | 19.1 | 5.5 | 2F242F237E1840209A95E123C322A27C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.375% | 0.91625 | 16.09% | [5 empty] | Non-TXV | 8.375%
Stockton | CA | 95209-2329 |  | 2013-09-12 | 2013-09-12 12:35 | 2013-09-12 12:35 | RUUD - UNK | 103 | 0 | Yes | Yes | 19.3 | 17.7 | 1.6 | 9EF04B8FFF2B445A81ABFDD1169D1333 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-6219 |  | 2013-09-16 | 2013-09-16 11:46 | 2013-09-16 12:04 | BDP - 568DJ024 | 104 | 3.1 | Yes | Yes | 18.8 | 18.2 | 0.6 | D7D304AD544C423B8ED651F7F6C82774 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Madera | CA | 93638-9320 |  | 2013-09-24 | 2013-09-24 12:43 | 2013-09-24 12:44 | CARRIER - 24ABA348A300 | 126 | 3.9 | Yes | Yes | 16.2 | 18.5 | -2.3 | BC71237C5A04485E9E33B6976538C67B |  | R410A | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Stockton | CA | 95209-4259 |  | 2013-09-13 | 2013-09-13 18:08 | 2013-09-13 18:32 | YORK - H2RC036S0606HG | 83 | 17.3 | Yes | Yes | 21.8 | 19.8 | 2 | 578C474E7FA946509ED535F098CC8BA1 |  | R22 | Non-TXV |  | 20.84% | 0.79157 | 40.06% | [5 empty] | Non-TXV | 20.84%
Merced | CA | 95340-2622 |  | 2013-09-17 | 2013-09-17 13:46 | 2013-09-17 13:48 | TRANE - YCY030G1MOAC | 116 | 7.1 | Yes | Yes | 24.4 | 22.1 | 2.3 | 1ACB10F9A7E04F9BB354670D5C1E1B8F |  | R22 | Non-TXV |  | 6.121% | 0.93879 | 11.76% | [5 empty] | Non-TXV | 6.121%
Tracy | CA | 95376-5143 |  | 2013-09-11 | 2013-09-11 12:32 | 2013-09-11 12:52 | PAYNE - PA10JA036-C | 72 | 3.2 | Yes | Yes | 24 | 19.3 | 4.7 | C02410645C0440629660BA11058A0211 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Los Banos | CA | 93635-3012 |  | 2013-09-19 | 2013-09-19 12:14 | 2013-09-19 12:16 | LENNOX - 14ACX-030-230-10 | 107 | 3.3 | Yes | Yes | 18.9 | 21.4 | -2.5 | C08FE34BD30E49258574B2D37530FD1C |  | R410A | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Fresno | CA | 93701-1441 |  | 2013-09-18 | 2013-09-18 11:24 | 2013-09-18 12:11 | YORK - DBYP-F048N080A | 100 | 3.2 | Yes | Yes | 24.3 | 20.4 | 3.9 | 0A1664238C1B4F98AC9FA8D432281020 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Lathrop | CA | 95330-8614 |  | 2013-09-16 | 2013-09-16 11:08 | 2013-09-16 11:26 | CARRIER - N2A360AKB200 | 146 | 7.2 | Yes | Yes | 23.1 | 17.2 | 5.9 | E5BD87D0629D44349388CB3EA436B9DA |  | R22 | Non-TXV |  | 4.932% | 0.95068 | 9.477% | [5 empty] | Non-TXV | 4.932%
Merced | CA | 95341-8992 |  | 2013-09-17 | 2013-09-17 23:07 | 2013-09-17 23:11 | YORK - D1NH048N09006C | 124 | 5 | Yes | Yes | 26.8 | 20.9 | 5.9 | ACC9EC14E96B4AEF937A58D95A915C32 |  | R22 | Non-TXV |  | 4.032% | 0.95968 | 7.749% | [5 empty] | Non-TXV | 4.032%
Galt | CA | 95632-8268 |  | 2013-10-21 | 2013-10-21 13:09 | 2013-10-21 13:26 | BRYANT - 561CJ036-F | 70 | 2.8 | Yes | Yes | 20.3 | 18.7 | 1.6 | 4AE67061896F48D5BE634EC0ED2BC597 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93711-2131 |  | 2013-09-20 | 2013-09-20 14:31 | 2013-09-20 14:32 | BRYANT - 561CJ036-F | 74 | 2.8 | Yes | Yes | 20.4 | 21.4 | -0.9 | 5CBE7245303D45549F82F7F51BC22567 |  | R22 | Non-TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | Non-TXV | 3.784%
Clovis | CA | 93612-4246 |  | 2013-09-26 | 2013-09-26 10:13 | 2013-09-26 10:15 | WEATHER KING - WRKAA036JK06E | 62 | 5.7 | Yes | Yes | 25.7 | 20.4 | 5.3 | D9BA1333A197462885823F0D3B381F69 |  | R22 | Non-TXV |  | 9.194% | 0.90806 | 17.67% | [5 empty] | Non-TXV | 9.194%
Fresno | CA | 93705-4650 |  | 2013-09-16 | 2013-09-16 10:38 | 2013-09-16 10:39 | OTHER - UNK | 70 | 7.6 | Yes | Yes | 21.3 | 18.6 | 2.7 | C853A54F025E4AA5919EFE367CC69033 |  | R22 | Non-TXV |  | 10.86% | 0.89143 | 20.87% | [5 empty] | Non-TXV | 10.86%
Fresno | CA | 93704-5575 |  | 2013-09-18 | 2013-09-18 18:03 | 2013-09-18 19:29 | BDP - 585B030075YACR | 50 | 13.6 | Yes | Yes | 16.1 | 19 | -2.9 | 4A6372D6E11844519C17EB2CBDFBEE29 |  | R22 | Non-TXV |  | 27.2% | 0.728 | 52.27% | [5 empty] | Non-TXV | 27.2%
Stockton | CA | 95210-3670 |  | 2013-09-12 | 2013-09-12 11:17 | 2013-09-12 11:48 | CARRIER - 59ANX042000ABAA | 114 | 4 | Yes | Yes | 21.8 | 17.7 | 4.1 | 519C5EEF85C3417D8E51C3362235DB50 |  | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Stockton | CA | 95210-2068 |  | 2013-09-23 | 2013-09-23 12:57 | 2013-09-23 13:16 | ICP - HAC042AKA4 | 98 | -5.8 | Yes | Yes | 23.4 | 17.6 | 5.8 | 6E0D2DF00ABB4EACB9FCF169C5260540 |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Fresno | CA | 93722-4335 |  | 2013-10-04 | 2013-10-04 10:48 | 2013-10-04 10:49 | ICP - WPG3364060LKC1 | 100 | 3.4 | Yes | Yes | 21.8 | 17.1 | 4.7 | DE208D4DECF541DD8349C22079301847 |  | R410A | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Merced | CA | 95348-3812 |  | 2013-09-26 | 2013-09-26 08:09 | 2013-09-26 08:11 | TRANE - HB030C100A1 | 70 | 3.6 | Yes | Yes | 19.8 | 20.3 | -0.5 | E3550FEC45E8405788931821A66265E7 |  | R22 | Non-TXV |  | 5.143% | 0.94857 | 9.883% | [5 empty] | Non-TXV | 5.143%
Stockton | CA | 95203-2429 |  | 2013-09-16 | 2013-09-16 14:07 | 2013-09-16 14:07 | RUUD - UANC-036JAS | 183 | 0 | Yes | Yes | 21.1 | 17.6 | 3.6 | DD79FE37DF6342D99717BAFE0D91C433 |  | R22 | TXV |  | 0% | 1 | 0%
Willows | CA | 95988-0000 |  | 2013-09-12 | 2013-09-12 09:51 | 2013-09-12 10:07 | YORK - H1RCO36S06D | 62 | 11.5 | Yes | Yes | 15 | 18 | -3 | DD1B587EBCCC4C048C96FF599F66BDDE |  | R22 | Non-TXV |  | 18.55% | 0.81452 | 35.65% | [5 empty] | Non-TXV | 18.55%
Stockton | CA | 95207-3341 |  | 2013-10-02 | 2013-10-02 12:10 | 2013-10-02 12:28 | LENNOX - GSS10-411-501P | 82 | 5.1 | Yes | Yes | 22.2 | 17.7 | 4.5 | 47B9A6EC82C240ACBA1958DB53D1CAA0 |  | R22 | TXV |  | 6.22% | 0.9378 | 11.95% | [5 empty] | TXV | 6.22%
Red Bluff | CA | 96080-4250 |  | 2013-09-11 | 2013-09-11 15:32 | 2013-09-11 16:16 | PAYNE - 585CJWO30075ABAE | 62 | 7.6 | Yes | Yes | 16.9 | 19.9 | -3 | 3DD59D45FF2742D388C8E5B218A7EBD2 |  | R22 | Non-TXV |  | 12.26% | 0.87742 | 23.56% | [5 empty] | Non-TXV | 12.26%
Rocklin | CA | 95677-2563 |  | 2013-10-09 | 2013-10-09 10:49 | 2013-10-09 10:49 | AMERICAN STANDARD - TTD724B100A0 | 67 | 0 | Yes | Yes | 26.3 | 20.7 | 5.6 | B5EFF07201594CCBA39F926185137A8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4254 |  | 2013-09-12 | 2013-09-12 09:33 | 2013-09-12 10:07 | CARRIER - 38TH036300 | 83 | 5.4 | Yes | Yes | 21.4 | 17.7 | 3.7 | 4BFF5F3828C446389D558C330A384E2F |  | R22 | Non-TXV |  | 6.506% | 0.93494 | 12.5% | [5 empty] | Non-TXV | 6.506%
Willows | CA | 95988-2606 |  | 2013-09-12 | 2013-09-12 11:41 | 2013-09-12 11:55 | COLEMAN - NA | 75 | 9.8 | Yes | Yes | 16.5 | 18.5 | -2 | 3E47F22C2F1B434E9EC04419CDD4F514 |  | R22 | Non-TXV |  | 13.07% | 0.86933 | 25.11% | [5 empty] | Non-TXV | 13.07%
Williams | CA | 95987-0000 |  | 2013-09-12 | 2013-09-12 11:24 | 2013-09-12 11:40 | RUUD - URGG-05E24JKR | 42 | 1.4 | Yes | Yes | 17 | 17.9 | -0.9 | B4AF4415DD984005BC08BE07453994C4 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Los Banos | CA | 93635-4538 |  | 2013-09-13 | 2013-09-13 11:07 | 2013-09-13 11:09 | WESTINGHOUSE - 7777UNK | 84 | 2.6 | Yes | Yes | 20 | 18.3 | 1.7 | AA33C41B402E4DF392E7DD4CC8F26947 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Los Banos | CA | 93635-6416 |  | 2013-10-11 | 2013-10-11 11:11 | 2013-10-11 11:12 | BRYANT - 563CN042-D | 124 | 4.1 | Yes | Yes | 21.1 | 21 | 0.1 | 11C862DE8BE042F19602A3B0917F0A83 |  | R22 | Non-TXV |  | 3.306% | 0.96694 | 6.354% | [5 empty] | Non-TXV | 3.306%
Stockton | CA | 95206-2366 |  | 2013-09-18 | 2013-09-18 12:31 | 2013-09-18 12:53 | RUUD - UAHE-025JAS | 63 | 8.5 | Yes | Yes | 27.2 | 21.3 | 6 | C05547A8C8AF4C0191A1F4C388BD8483 |  | R22 | Non-TXV |  | 13.49% | 0.86508 | 25.93% | [5 empty] | Non-TXV | 13.49%
Fresno | CA | 93722-5530 |  | 2013-10-02 | 2013-10-02 11:38 | 2013-10-02 11:40 | RUUD - UNK | 68 | 9.5 | Yes | Yes | 23.1 | 19.7 | 3.4 | 8FAB90EA4511445E96065CF1E1770A0C |  | R22 | Non-TXV |  | 13.97% | 0.86029 | 26.85% | [5 empty] | Non-TXV | 13.97%
Chico | CA | 95973-8206 |  | 2013-09-19 | 2013-09-19 15:41 | 2013-09-19 16:00 | PAYNE - 585JW036075ABAF | 68 | 10.2 | Yes | Yes | 19.4 | 21.5 | -2.1 | 6F053B8AE9334641972DB740DB5805BF |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Atwater | CA | 95301-4221 |  | 2013-09-26 | 2013-09-26 16:06 | 2013-09-26 16:08 | TRANE - BTD730A100B0 | 74 | 6.3 | Yes | Yes | 22 | 17.6 | 4.4 | 82F09EC68B354DD69C5074A441E220AF |  | R22 | Non-TXV |  | 8.514% | 0.91486 | 16.36% | [5 empty] | Non-TXV | 8.514%
Oroville | CA | 95966-7713 |  | 2013-09-16 | 2013-09-16 15:26 | 2013-09-16 15:46 | PAYNE - PA13NR018-E | 65 | 3.7 | Yes | Yes | 20 | 21.3 | -1.3 | AFDA0DF56AD64BE1AF2A7DAFD917D254 |  | R22 | TXV |  | 5.692% | 0.94308 | 10.94% | [5 empty] | TXV | 5.692%
Stockton | CA | 95206-6018 |  | 2013-09-17 | 2013-09-17 13:38 | 2013-09-17 13:57 | GOODMAN - CKJ42-1B | 98 | 4.1 | Yes | Yes | 19.4 | 19.9 | -0.5 | 41ADAEA815104EDA885BEA5269ACA359 |  | R22 | Non-TXV |  | 4.184% | 0.95816 | 8.04% | [5 empty] | Non-TXV | 4.184%
Los Banos | CA | 93635-9490 |  | 2013-09-13 | 2013-09-13 14:15 | 2013-09-13 14:17 | BRYANT - 561CJ042-F | 85 | 2.6 | Yes | Yes | 21.2 | 19.3 | 1.9 | 444DA714373F439D8157E0D9500B079B |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Orland | CA | 95963-9687 |  | 2013-09-12 | 2013-09-12 15:19 | 2013-09-12 15:37 | TEMPSTAR - CA042VK02 | 81 | 4 | Yes | Yes | 18.6 | 19.1 | -0.5 | 521DA76350AC4DCC82B47934FCFB70E2 |  | R22 | Non-TXV |  | 4.938% | 0.95062 | 9.49% | [5 empty] | Non-TXV | 4.938%
Stockton | CA | 95206-3024 |  | 2013-09-16 | 2013-09-16 13:20 | 2013-09-16 13:36 | ICP - N2A330AKA200 | 82 | 4.7 | Yes | Yes | 20.4 | 21 | -0.6 | F27D827EBDA64431827FC9FFC801A233 |  | R22 | Non-TXV |  | 5.732% | 0.94268 | 11.02% | [5 empty] | Non-TXV | 5.732%
Stockton | CA | 95206-3811 |  | 2013-09-25 | 2013-09-25 13:51 | 2013-09-25 14:18 | GOODMAN - GSC120301AE | 109 | 4.5 | Yes | Yes | 21.5 | 18.8 | 2.7 | 4D6D350A7AC54997A68260630FA76D5F |  | R22 | Non-TXV |  | 4.128% | 0.95872 | 7.934% | [5 empty] | Non-TXV | 4.128%
Tracy | CA | 95376-6705 |  | 2013-09-13 | 2013-09-13 11:43 | 2013-09-13 12:44 | AMERICAN STANDARD - 2A75048A1000AA | 182 | -12.8 | Yes | Yes | 21.3 | 20.4 | 0.9 | C525E404672E49C98E96F89E20AA590B |  | R22 | Non-TXV |  | -7.033% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.033%
Grass Valley | CA | 95949-7814 |  | 2013-09-12 | 2013-09-12 15:11 | 2013-09-12 15:31 | RUUD - 13AJA60A01 | 191 | -39.8 | Yes | Yes | 21.4 | 21.4 | 0 | 936EFDC3E5764607AA698EFD0B2407C0 |  | R22 | TXV |  | -20.84% | 1.2084 | 5.836% |  |  |  |  | TXV |  |  | -20.84%
Atwater | CA | 95301-2072 |  | 2013-09-17 | 2013-09-17 14:13 | 2013-09-17 14:14 | CARRIER - 48VNLA3606030 | 149 | 5.3 | Yes | Yes | 26.6 | 21.4 | 5.2 | A14B80DD4E3945FF82802274223FCCCB |  | R410A | Non-TXV |  | 3.557% | 0.96443 | 6.836% | [5 empty] | Non-TXV | 3.557%
Manteca | CA | 95336-5926 |  | 2013-09-16 | 2013-09-16 13:37 | 2013-09-16 15:07 | RHEEM - RAKA-042JAZ | 79 | 2.8 | Yes | Yes | 19.2 | 19 | 0.2 | 7878FA29D5E84C0F9CFB8EFF9D9B1DB7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.544% | 0.96456 | 6.811% | [5 empty] | Non-TXV | 3.544%
Fresno | CA | 93702-2343 |  | 2013-09-20 | 2013-09-20 13:36 | 2013-09-20 13:37 | OTHER - NAC048AKA1 | 108 | 3.9 | Yes | Yes | 20.5 | 20.1 | 0.5 | 038A015515684485816754DE2CF07CCF |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Fresno | CA | 93727-6466 |  | 2013-10-03 | 2013-10-03 10:16 | 2013-10-03 10:40 | LENNOX - 12ACB48-4P | 171 | 20.3 | Yes | Yes | 19 | 20.8 | -1.8 | DB2F1A10EE4148FBB7D7BD83E8A14D28 |  | R22 | Non-TXV |  | 11.87% | 0.88129 | 22.81% | [5 empty] | Non-TXV | 11.87%
Stockton | CA | 95210-3642 |  | 2013-10-02 | 2013-10-02 14:52 | 2013-10-02 15:18 | RUUD - UNK | 64 | 6.5 | Yes | Yes | 21.3 | 21 | 0.3 | E10DC30E17CD4C43B77142C7C5F9A1F2 |  | R22 | Non-TXV |  | 10.16% | 0.89844 | 19.52% | [5 empty] | Non-TXV | 10.16%
Redwood City | CA | 94063-4118 |  | 2013-10-15 | 2013-10-15 11:55 | 2013-10-15 12:21 | OTHER - BRC0301BD | 62 | 14.8 | Yes | Yes | 21 | 22.9 | -1.9 | D4C534BAAAFC4F9DAE58183066F5C0D3 |  | R22 | Non-TXV |  | 23.87% | 0.76129 | 45.87% | [5 empty] | Non-TXV | 23.87%
Placerville | CA | 95667-4516 |  | 2013-09-18 | 2013-09-18 11:24 | 2013-09-18 11:24 | PAYNE - PA10JA036-C | 72 | 0 | Yes | Yes | 22 | 17.7 | 4.3 | 00CBB089A96F4B49955055D2B9D17BE2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Orland | CA | 95963-2400 |  | 2013-09-16 | 2013-09-16 11:11 | 2013-09-16 11:33 | RHEEM - RAHE-025-JAS | 63 | 6.3 | Yes | Yes | 14.9 | 17.9 | -3 | FD813F70065D4E12854581CB5C65F1BA |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Manteca | CA | 95336-3223 |  | 2013-09-16 | 2013-09-16 13:54 | 2013-09-16 14:23 | TRANE - BTD736A100A0 | 88 | 2.8 | Yes | Yes | 21.8 | 19.9 | 1.9 | 7B69F8580E194E8AB7C4B8CF9144D196 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Stockton | CA | 95204-1634 |  | 2013-09-16 | 2013-09-16 15:01 | 2013-09-17 07:33 | AMANA - PGD30C07020 | 74 | 6.4 | Yes | Yes | 18.3 | 18.4 | -0.1 | 80BF1BE725E047F3A191BF5199F78D08 |  | R22 | Non-TXV |  | 8.649% | 0.91351 | 16.62% | [5 empty] | Non-TXV | 8.649%
Fresno | CA | 93722-7305 |  | 2013-10-14 | 2013-10-14 17:43 | 2013-10-14 19:24 | CARRIER - 38CK036340 | 71 | 2.5 | Yes | Yes | 22.6 | 19.6 | 3.1 | DE59AC92BC9646CCB1AE9C7AE94BF864 |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Stockton | CA | 95206-6030 |  | 2013-09-19 | 2013-09-19 10:32 | 2013-09-19 10:59 | TRANE - TZAA-336-2A757 | 87 | 15.4 | Yes | Yes | 19 | 20.1 | -1.1 | CCD077A1EA414097A59F633553328E03 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.7% | 0.82299 | 34.02% | [5 empty] | Non-TXV | 17.7%
Stockton | CA | 95210-3136 |  | 2013-09-18 | 2013-09-18 14:07 | 2013-09-18 14:27 | OTHER - PGAD24B1K1 | 73 | 3.3 | Yes | Yes | 24.3 | 20.1 | 4.2 | 1920C13402CB4AD4BC0FC08DDB6E494D |  | R22 | Non-TXV |  | 4.521% | 0.95479 | 8.687% | [5 empty] | Non-TXV | 4.521%
Cameron Park | CA | 95682-7690 |  | 2013-09-13 | 2013-09-13 12:24 | 2013-09-13 12:44 | CARRIER - 24ABA360A320 | 131 | 3.9 | Yes | Yes | 22.8 | 18.9 | 3.9 | D35F9C67D5B44790853FE8219AFACA8F |  | R410A | Non-TXV |  | 2.977% | 0.97023 | 5.721% | [5 empty] | Non-TXV | 2.977%
Gridley | CA | 95948-9534 |  | 2013-09-30 | 2013-09-30 10:01 | 2013-09-30 10:18 | RUUD - AC46HB1Q | 96 | 2.8 | Yes | Yes | 17.5 | 13.1 | 4.4 | 14F56034E4784DE39A528DA560D2F922 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Oroville | CA | 95966-3961 |  | 2013-09-16 | 2013-09-16 14:18 | 2013-09-16 14:50 | COLEMAN - UNK | 90 | 2.7 | Yes | Yes | 20 | 22 | -2 | 66FE6027069347B5895BCD7D394FF8F5 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Paso Robles | CA | 93446-5007 |  | 2013-10-07 | 2013-10-07 13:40 | 2013-10-07 13:56 | CARRIER - 38EN024310 | 61 | 3.4 | Yes | Yes | 20.3 | 20 | 0.3 | A8DC8615F1FD4653AD9D3C65F09F5EA9 |  | R22 | Non-TXV |  | 5.574% | 0.94426 | 10.71% | [5 empty] | Non-TXV | 5.574%
Fresno | CA | 93722-4761 |  | 2013-09-25 | 2013-09-25 13:37 | 2013-09-25 13:38 | CARRIER - UNK | 68 | 7.6 | Yes | Yes | 23.9 | 18.7 | 5.2 | 7A4D7BDEE2C04EFE9496565AF5F337FA |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Stockton | CA | 95212-2121 |  | 2013-09-20 | 2013-09-20 15:27 | 2013-09-20 15:45 | ICP - R2A330GKC1 | 65 | 3.4 | Yes | Yes | 18.3 | 18.7 | -0.4 | 8C4DC8F4AC9A448EBBC017FACA1F125E |  | R22 | TXV |  | 5.231% | 0.94769 | 10.05% | [5 empty] | TXV | 5.231%
Willows | CA | 95988-3238 |  | 2013-09-17 | 2013-09-17 12:09 | 2013-09-17 13:01 | LENNOX - 12GCS036X-75PB | 110 | 6.9 | Yes | Yes | 17.2 | 18.2 | -1 | 6C5127E030564E938D2E294CEC550477 |  | R22 | Non-TXV |  | 6.273% | 0.93727 | 12.05% | [5 empty] | Non-TXV | 6.273%
Grass Valley | CA | 95945-5225 |  | 2013-09-12 | 2013-09-12 12:59 | 2013-09-12 12:59 | CARRIER - 38CKC024340 | 58 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | 4EF951B7D7504EF0A9E3EEB27934841D |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2935 |  | 2013-09-16 | 2013-09-16 13:02 | 2013-09-16 13:03 | RHEEM - RRPLB036JK08X | 92 | 5.9 | Yes | Yes | 23.1 | 19.4 | 3.7 | B2591FBE33AF4C05877EB6E52DFF29F6 |  | R410A | Non-TXV |  | 6.413% | 0.93587 | 12.32% | [5 empty] | Non-TXV | 6.413%
Fresno | CA | 93722-9195 |  | 2013-10-07 | 2013-10-07 16:23 | 2013-10-07 16:48 | COLEMAN - DAYPFO36N070A | 108 | 8.2 | Yes | Yes | 19.3 | 18.5 | 0.8 | 64BC166DDB6E4863AC3FE58FBDD31B8E |  | R22 | Non-TXV |  | 7.593% | 0.92407 | 14.59% | [5 empty] | Non-TXV | 7.593%
Paso Robles | CA | 93446-5437 |  | 2013-10-07 | 2013-10-07 12:13 | 2013-10-07 12:31 | CARRIER - 38EZG024300 | 80 | -4.7 | Yes | Yes | 26.8 | 21 | 5.8 | C40AC85FADC44FFDB87EF9CC3EA1B315 |  | R410A | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Lincoln | CA | 95648-1539 |  | 2013-09-13 | 2013-09-13 16:21 | 2013-09-13 16:21 | RHEEM - RAKB-048JAZ | 103 | 0 | Yes | Yes | 20 | 18.3 | 1.7 | 5DB6ED2D8F88466E88527ABC111FA6B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Redwood City | CA | 94061-1203 |  | 2013-10-14 | 2013-10-14 15:05 | 2013-10-14 15:05 | RHEEM - UNK | 90 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | F7F29CF8E1B0461D979F99D917DF82A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-4571 |  | 2013-09-25 | 2013-09-25 11:41 | 2013-09-25 12:08 | YORK - H2RC048S06G | 119 | 4 | Yes | Yes | 21.5 | 20.4 | 1.1 | D2FD8FD302974948B662D81CAF1F0A9F |  | R22 | Non-TXV |  | 3.361% | 0.96639 | 6.46% | [5 empty] | Non-TXV | 3.361%
Los Banos | CA | 93635-2986 |  | 2013-09-19 | 2013-09-19 13:35 | 2013-09-19 13:43 | PAYNE - PA13NR048000AHAA | 142 | 15.4 | Yes | Yes | 17.4 | 20.4 | -3 | 295F84FFE60642F3A401A93244A2DDBE |  | R22 | Non-TXV |  | 10.85% | 0.89155 | 20.84% | [5 empty] | Non-TXV | 10.85%
Stockton | CA | 95209-3025 |  | 2013-09-13 | 2013-09-13 17:19 | 2013-09-13 17:40 | TRANE - TTB024C100A0 | 58 | 9.6 | Yes | Yes | 27.3 | 21.5 | 5.8 | FCBEF0B7E14841A0A7F68CD0AC527DA1 |  | R22 | Non-TXV |  | 16.55% | 0.83448 | 31.81% | [5 empty] | Non-TXV | 16.55%
Stockton | CA | 95205-3020 |  | 2013-09-16 | 2013-09-16 09:05 | 2013-09-16 09:23 | AMANA - PGB30C0702E | 64 | -3.8 | Yes | Yes | 22.3 | 18.2 | 4.1 | 97DF2366D6E7435C9EDF7E60502C811B |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Tracy | CA | 95377-5605 |  | 2013-09-13 | 2013-09-13 13:20 | 2013-09-13 13:38 | GOODMAN - CKJ601-C | 149 | 4.6 | Yes | Yes | 21.7 | 20.4 | 1.3 | EF948981737C4CAFBCC95BBA1B9A6BD4 |  | R22 | Non-TXV |  | 3.087% | 0.96913 | 5.933% | [5 empty] | Non-TXV | 3.087%
Stockton | CA | 95206-3057 |  | 2013-10-11 | 2013-10-11 17:30 | 2013-10-11 18:30 | BDP - 585GJ018040 | 55 | 4.9 | Yes | Yes | 20.5 | 20.4 | 0.1 | 0B2703285D3A4DD3BBB6AF1C628D07C1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.909% | 0.91091 | 17.12% | [5 empty] | Non-TXV | 8.909%
Los Banos | CA | 93635-2631 |  | 2013-09-19 | 2013-09-19 22:46 | 2013-09-19 22:48 | GOODMAN - CKJ48-1AB | 106 | 3.9 | Yes | Yes | 20 | 20.4 | -0.4 | 0570A9B7320C4A23AB00565BF22DADD8 |  | R22 | Non-TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | Non-TXV | 3.679%
Sanger | CA | 93657-2004 |  | 2013-09-17 | 2013-09-17 11:53 | 2013-09-17 12:52 | TAPPAN - N/A | 120 | 3.7 | Yes | Yes | 22.2 | 20.2 | 2.1 | BB4A6A1988904F7AAB36E360A7C00F78 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Stockton | CA | 95209-2905 |  | 2013-09-13 | 2013-09-13 14:11 | 2013-09-13 14:30 | PAYNE - 597CN030-B | 88 | 5.4 | Yes | Yes | 24.3 | 19 | 5.3 | 10492FD566574275A11082380766BA92 |  | R22 | TXV |  | 6.136% | 0.93864 | 11.79% | [5 empty] | TXV | 6.136%
Lathrop | CA | 95330-9171 |  | 2013-09-18 | 2013-09-18 09:58 | 2013-09-18 10:15 | CARRIER - 38CMC060300 | 160 | 4.9 | Yes | Yes | 19.3 | 18.2 | 1.1 | 178A79688B9A4BEE991E8005F6D0EB09 |  | R22 | Non-TXV |  | 3.062% | 0.96937 | 5.885% | [5 empty] | Non-TXV | 3.062%
Nevada City | CA | 95959-9214 |  | 2013-09-11 | 2013-09-11 11:55 | 2013-09-11 11:55 | TRANE - 4TTR2048A100BAA | 126 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | 04E5EF102A0847168EC06A23372B7D13 |  | R410A | TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-8659 |  | 2013-09-16 | 2013-09-16 10:22 | 2013-09-16 10:34 | CARRIER - 24ABA336A300 | 85 | 4.6 | Yes | Yes | 17.8 | 17.4 | 0.4 | D08B964DC4C74D1CB9EBF1F24A7AB36F |  | R410A | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Nevada City | CA | 95959-9447 |  | 2013-09-11 | 2013-09-11 09:32 | 2013-09-11 09:32 | PAYNE - PY1PNB036090AAAA | 61 | 0 | Yes | Yes | 23.3 | 19.7 | 3.6 | D33D2BA7524140D09EB86CF4A8CCF330 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-9447 |  | 2013-09-11 | 2013-09-11 09:59 | 2013-09-11 09:59 | BRYANT - 113RNA036-E | 86 | 0 | Yes | Yes | 22.7 | 19.5 | 3.2 | 4DC9CA4F0C624AE9BCCB261863422836 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lodi | CA | 95242-9478 |  | 2013-10-01 | 2013-10-01 11:16 | 2013-10-01 11:45 | GOODMAN - GPG12420701A | 105 | -9.9 | Yes | Yes | 25.3 | 19.9 | 5.4 | DDD9DFE8664245898BE0FC2B6AF5990C |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Stockton | CA | 95210-2015 |  | 2013-09-16 | 2013-09-16 13:13 | 2013-09-16 13:33 | GOODMAN - GSC130481BB | 102 | -6 | Yes | Yes | 20.7 | 18.6 | 2.2 | DDA6A40B1F28498DAB9CA4BC5C24D286 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95207-1905 |  | 2013-10-02 | 2013-10-02 09:33 | 2013-10-02 09:56 | PAYNE - 30RAC | 88 | 16.6 | Yes | Yes | 15.5 | 17.7 | -2.2 | 96E8AEA9C8CE46CC81B29CFF72637CD5 |  | R22 | Non-TXV |  | 18.86% | 0.81136 | 36.25% | [5 empty] | Non-TXV | 18.86%
Fresno | CA | 93722-5199 |  | 2013-10-04 | 2013-10-04 11:16 | 2013-10-04 11:17 | YORK - D1NH042N09006C | 94 | 9.8 | Yes | Yes | 22.6 | 18.2 | 4.4 | 109E4C4AB1BD4A06AA5688C639223DE7 |  | R22 | Non-TXV |  | 10.43% | 0.89574 | 20.04% | [5 empty] | Non-TXV | 10.43%
Paradise | CA | 95969-2420 |  | 2013-09-19 | 2013-09-19 12:16 | 2013-09-19 12:36 | CARRIER - 24AR34YBA300 | 146 | 6.4 | Yes | Yes | 20 | 20.4 | -0.4 | 8A7577A0E11546F191C1347E33D99B07 |  | R22 | Non-TXV |  | 4.384% | 0.95616 | 8.424% | [5 empty] | Non-TXV | 4.384%
Willows | CA | 95988-2660 |  | 2013-09-12 | 2013-09-12 12:10 | 2013-09-12 12:38 | WESTINGHOUSE - FSBC042KA | 102 | 13.2 | Yes | Yes | 17.5 | 19.3 | -1.8 | 19BC5F4F52C84FC3BF0F274365A8AE7E |  | R22 | Non-TXV |  | 12.94% | 0.87059 | 24.87% | [5 empty] | Non-TXV | 12.94%
Lathrop | CA | 95330-9476 |  | 2013-09-13 | 2013-09-13 13:06 | 2013-09-13 13:47 | UNITARY PRODUCTS GROUP - GCGD36S21S2B | 85 | 4.3 | Yes | Yes | 17.5 | 17.9 | -0.4 | A208F69C95614E17AE76F121E977AD71 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Orland | CA | 95963-2027 |  | 2013-09-12 | 2013-09-12 14:22 | 2013-09-12 14:37 | YORK - H2RD04206B | 141 | 8.4 | Yes | Yes | 16.2 | 19.1 | -2.9 | C6CDA9C6EE3045598F6C2B948154F47D |  | R22 | Non-TXV |  | 5.957% | 0.94043 | 11.45% | [5 empty] | Non-TXV | 5.957%
Lincoln | CA | 95648-8356 |  | 2013-09-19 | 2013-09-19 10:11 | 2013-09-19 10:31 | YORK - H2RC030S06A | 88 | 4.7 | Yes | Yes | 21 | 19.9 | 1.1 | ED0C46711AAB4EA89AA9F3A76D66195C |  | R22 | TXV |  | 5.341% | 0.94659 | 10.26% | [5 empty] | TXV | 5.341%
Tracy | CA | 95376-2780 |  | 2013-09-16 | 2013-09-16 11:13 | 2013-09-16 11:40 | GOODMAN - GPG10240451A | 50 | 2 | Yes | Yes | 17.8 | 18.8 | -1 | C1B37994D0D244A7A99164C1EF8E917A |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Tracy | CA | 95376-2780 |  | 2013-09-16 | 2013-09-16 11:41 | 2013-09-16 12:07 | GOODMAN - GPG10240451A | 50 | 1.6 | Yes | Yes | 16.9 | 17.7 | -0.8 | 7EDFED66A8644E9B8FD264183C7AD7C0 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93722-6870 |  | 2013-10-08 | 2013-10-08 13:05 | 2013-10-08 13:34 | CARRIER - N/A | 90 | 5.2 | Yes | Yes | 18.8 | 20.4 | -1.6 | 90195811C2F34F5FAE6F4E68FEEB5963 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.778% | 0.94222 | 11.1% | [5 empty] | Non-TXV | 5.778%
Oakdale | CA | 95361-2832 |  | 2013-09-17 | 2013-09-17 13:11 | 2013-09-17 13:29 | AMERICAN STANDARD - YCY048G1H0AA | 183 | 6.2 | Yes | Yes | 22 | 20.4 | 1.6 | 116B96B32F68400CB8C1E3FD73FE0940 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.388% | 0.96612 | 6.511% | [5 empty] | Non-TXV | 3.388%
Lathrop | CA | 95330-9316 |  | 2013-09-16 | 2013-09-16 09:02 | 2013-09-16 09:21 | DAY & NIGHT - 565BJ030-B | 76 | 14.1 | Yes | Yes | 18.2 | 18.3 | -0.1 | 812EA1C8B7C14692B1607DBC1B2E61EE |  | R22 | Non-TXV |  | 18.55% | 0.81447 | 35.65% | [5 empty] | Non-TXV | 18.55%
Merced | CA | 95348-9101 |  | 2013-09-18 | 2013-09-18 12:17 | 2013-09-18 12:27 | YORK - H2RD042S06B | 141 | 6.6 | Yes | Yes | 21.8 | 20.7 | 1.1 | D65ED7BEB7A94E44AFF044E2A6430B02 |  | R22 | Non-TXV |  | 4.681% | 0.95319 | 8.996% | [5 empty] | Non-TXV | 4.681%
Paradise | CA | 95969-3807 |  | 2013-09-19 | 2013-09-19 11:13 | 2013-09-19 11:13 | DAY & NIGHT - PGD42040K001C1 | 97 | 0 | Yes | Yes | 18.2 | 21.2 | -3 | 7FA93626B9024EEFA30D9CA15A6A1CE2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5415 |  | 2013-09-18 | 2013-09-18 11:41 | 2013-09-18 11:59 | GOODMAN - CH42-1GB | 104 | 9.2 | Yes | Yes | 25.6 | 20.9 | 4.7 | 2361AA648D314B369BCC1975DB5D08A4 |  | R22 | Non-TXV |  | 8.846% | 0.91154 | 17% | [5 empty] | Non-TXV | 8.846%
Cameron Park | CA | 95682-9029 |  | 2013-09-13 | 2013-09-13 13:07 | 2013-09-13 13:27 | GIBSON - JS3BA-036KA | 70 | 2.2 | Yes | Yes | 20.4 | 19.8 | 0.6 | 2D6F8E74086F4B19853AADA17DBC9C98 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Grass Valley | CA | 95945-9710 |  | 2013-09-11 | 2013-09-11 15:55 | 2013-09-11 15:55 | CARRIER - BRB024300 | 91 | 0 | Yes | Yes | 21.6 | 20.2 | 1.5 | 565D5267AFE540A3BFF0686D883C0F47 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1139 |  | 2013-09-18 | 2013-09-18 12:53 | 2013-09-18 12:53 | FRESCHI - 30J0-105 | 52 | 0 | Yes | Yes | 23.2 | 17.7 | 5.5 | 30ECFBEE0CA240A4993CDE524BA6A58D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-2962 |  | 2013-09-23 | 2013-09-23 10:10 | 2013-09-23 10:13 | RHEEM - RRGG05N36JKR | 75 | 8.3 | Yes | Yes | 22.1 | 17.2 | 4.9 | 374508A44DBD43BBB6627121AEE33270 |  | R22 | Non-TXV |  | 11.07% | 0.88933 | 21.27% | [5 empty] | Non-TXV | 11.07%
Willows | CA | 95988-9600 |  | 2013-09-18 | 2013-09-18 11:24 | 2013-09-18 12:08 | YORK - D1NA024N05606C | 54 | 4.5 | Yes | Yes | 17 | 19.9 | -2.9 | D6C81C9D84B34E6ABCCAFBF3743BDE78 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Lathrop | CA | 95330-9678 |  | 2013-10-02 | 2013-10-02 11:18 | 2013-10-02 11:56 | TEMPSTAR - 7ZAA3362A57 | 115 | 5.5 | Yes | Yes | 20.9 | 17.5 | 3.5 | 1E654EB399524A549349D9CCC8A571FC |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Stockton | CA | 95210-4410 |  | 2013-09-16 | 2013-09-16 12:11 | 2013-09-16 12:28 | PAYNE - 591ANX060000AAAA | 170 | -10 | Yes | Yes | 24.5 | 18.5 | 6 | 4988C10675D74A0CBD3018DF3FA57B66 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93726-3528 |  | 2013-10-03 | 2013-10-03 12:34 | 2013-10-03 12:35 | RHEEM - RRNA0B024JK06X | 70 | 3.8 | Yes | Yes | 20.5 | 19.9 | 0.6 | 764FAEBE955041C4BA68D0C350CDB4B7 |  | R22 | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Tracy | CA | 95376-8725 |  | 2013-09-16 | 2013-09-16 13:36 | 2013-09-16 13:53 | GOODMAN - GSC13042-1BB | 95 | 5.3 | Yes | Yes | 25.7 | 19.7 | 6 | A9F79BF8D22246659C44F6D182F76999 |  | R22 | Non-TXV |  | 5.579% | 0.94421 | 10.72% | [5 empty] | Non-TXV | 5.579%
Paradise | CA | 95969-2253 |  | 2013-10-18 | 2013-10-18 11:14 | 2013-10-18 11:48 | COLEMAN - 8736-801 | 67 | 10 | Yes | Yes | 24.8 | 21.8 | 3 | 3BE39C026ADA49C3B776375D92134FD4 |  | R22 | Non-TXV |  | 14.93% | 0.85075 | 28.68% | [5 empty] | Non-TXV | 14.93%
Redwood City | CA | 94065-1916 |  | 2013-10-15 | 2013-10-15 12:55 | 2013-10-15 13:20 | CARRIER - 38HDL024311 | 70 | 2.1 | Yes | Yes | 17 | 19.3 | -2.3 | 10D9FA082C1E4BACA0E04E3FBEFB8981 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Valley Springs | CA | 95252-9537 |  | 2013-09-26 | 2013-09-26 15:16 | 2013-09-26 15:41 | RUUD - UNK | 80 | 5.4 | Yes | Yes | 18.7 | 18.7 | 0 | C72B3F88A6B7436F9D791A71DF2A0F00 |  | R22 | Non-TXV |  | 6.75% | 0.9325 | 12.97% | [5 empty] | Non-TXV | 6.75%
Chico | CA | 95973-0391 |  | 2013-09-25 | 2013-09-25 12:30 | 2013-09-25 12:52 | AMANA - PGB30C0702E | 64 | 2.6 | Yes | Yes | 25 | 20.6 | 4.4 | A7C9B447C3524975AEE08AAB15508672 |  | R22 | TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | TXV | 4.062%
Winton | CA | 95388-0000 |  | 2013-09-17 | 2013-09-17 13:39 | 2013-09-17 13:41 | COLEMAN - UNK | 56 | 6.4 | Yes | Yes | 19.8 | 18.8 | 1 | 8BB11646EEC24BD4A0811B3783187F7A |  | R22 | Non-TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | Non-TXV | 11.43%
Chico | CA | 95973-5860 |  | 2013-11-01 | 2013-11-01 10:28 | 2013-11-01 11:32 | TRANE - 2TTB2048A10000AA | 120 | 3.7 | Yes | Yes | 25.3 | 19.7 | 5.6 | 66955227F17E43D284F7ABBA90AA86D1 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Willows | CA | 95988-2660 |  | 2013-09-12 | 2013-09-12 12:41 | 2013-09-12 12:58 | WESTINGHOUSE - FS3BC-048KA | 110 | 12.6 | Yes | Yes | 21.1 | 18.4 | 2.7 | 60B581278FCD4D96854EA2527F067CF9 |  | R22 | Non-TXV |  | 11.45% | 0.88545 | 22.01% | [5 empty] | Non-TXV | 11.45%
Cameron Park | CA | 95682-8525 |  | 2013-09-18 | 2013-09-18 15:33 | 2013-09-18 15:33 | GOODMAN - CKL18-1 | 53 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 56C4E112F54A4802B7400C40620C001C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Diamond Springs | CA | 95619-9379 |  | 2013-09-18 | 2013-09-18 11:26 | 2013-09-18 11:26 | RHEEM - RRNA-B030JK06X | 72 | 0 | Yes | Yes | 24.4 | 20.3 | 4.1 | E731FBFA20ED46118060E7DE69966B39 |  | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-8428 |  | 2013-10-03 | 2013-10-03 14:57 | 2013-10-03 15:28 | OTHER - CFC024D3B | 50 | 2.4 | Yes | Yes | 20 | 19.1 | 0.9 | EE6369DB5AB14EDA8C75D2096EF7EF15 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Cameron Park | CA | 95682-8525 |  | 2013-10-11 | 2013-10-11 12:45 | 2013-10-11 12:45 | GE - BTB818A100A | 36 | 0 | Yes | Yes | 24.4 | 20.1 | 4.3 | 40F42EBD52C847828327459ECFA7D676 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1798 |  | 2013-09-25 | 2013-09-25 15:34 | 2013-09-25 15:35 | BRYANT - 574BNW030040NB | 128 | 5.7 | Yes | Yes | 20.8 | 19.9 | 0.9 | 6475D9A172ED4C98A158EFEF2E7E4AC6 |  | R410A | Non-TXV |  | 4.453% | 0.95547 | 8.558% | [5 empty] | Non-TXV | 4.453%
Valley Springs | CA | 95252-9427 |  | 2013-09-16 | 2013-09-16 10:59 | 2013-09-16 11:15 | RHEEM - URKAA024JKO6E | 55 | 1.7 | Yes | Yes | 21.6 | 19.2 | 2.4 | 56C19C24B22840CDAAAC3826998ECF69 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Clovis | CA | 93611-6085 |  | 2013-09-23 | 2013-09-23 10:27 | 2013-09-23 10:47 | UNITARY PRODUCTS GROUP - ERCS0481BBB | 134 | 4.9 | Yes | Yes | 17.9 | 20.4 | -2.5 | 96F3838ED69F4A3EB2716682FBD76A27 |  | R22 | Non-TXV |  | 3.657% | 0.96343 | 7.027% | [5 empty] | Non-TXV | 3.657%
Fresno | CA | 93720-4128 |  | 2013-09-26 | 2013-09-26 11:48 | 2013-09-26 11:53 | CARRIER - UNK | 68 | 6 | Yes | Yes | 22.7 | 17.2 | 5.5 | A541D3C02477497B81D5A56727CC43E2 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Fresno | CA | 93704-4900 |  | 2013-09-26 | 2013-09-26 12:49 | 2013-09-26 12:51 | ICP - PGF024K040E | 54 | 5 | Yes | Yes | 18.9 | 15.7 | 3.2 | 068A05E709904838A264F02AC88FA4E4 |  | R22 | Non-TXV |  | 9.259% | 0.90741 | 17.79% | [5 empty] | Non-TXV | 9.259%
Fresno | CA | 93702-3234 |  | 2013-10-02 | 2013-10-02 21:37 | 2013-10-02 21:37 | OTHER - 7777UNK | 80 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | FA364AE94AE04F2580C9570FF374CDA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-0950 |  | 2013-09-23 | 2013-09-23 14:02 | 2013-09-23 14:03 | CARRIER - 48DL003 | 54 | 5.7 | Yes | Yes | 21.5 | 17.2 | 4.3 | 02373F114F1943299D0C9E67C03294B9 |  | R22 | Non-TXV |  | 10.56% | 0.89444 | 20.29% | [5 empty] | Non-TXV | 10.56%
Reedley | CA | 93654-3660 |  | 2013-10-02 | 2013-10-02 15:47 | 2013-10-02 16:40 | UNITARY PRODUCTS GROUP - CCJF48S41S1A | 73 | 5 | Yes | Yes | 25 | 20.4 | 4.6 | 7B30BA99091E401CB4B444114AE28566 |  | R410A | TXV |  | 6.849% | 0.93151 | 13.16% | [5 empty] | TXV | 6.849%
Merced | CA | 95340-2438 |  | 2013-09-18 | 2013-09-18 13:12 | 2013-09-18 13:14 | PAYNE - PY1PNB036060ABAA | 68 | 4.7 | Yes | Yes | 20.1 | 18.5 | 1.6 | 93CFD75ED3864F169849F538698CA556 |  | R22 | Non-TXV |  | 6.912% | 0.93088 | 13.28% | [5 empty] | Non-TXV | 6.912%
Chico | CA | 95973-1151 |  | 2013-09-25 | 2013-09-25 10:16 | 2013-09-25 10:16 | BRYANT - 561CJ048-G | 99 | 0 | Yes | Yes | 25 | 19.9 | 5.1 | 26FCCCCED9C245228F219CDE03AC1E09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-2884 |  | 2013-10-11 | 2013-10-11 15:47 | 2013-10-11 16:12 | CARRIER - 38EH048320 | 137 | 5.8 | Yes | Yes | 21.1 | 21 | 0.1 | 5E1E3F22B0AE42DEBC4B89549451FE69 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.234% | 0.95766 | 8.136% | [5 empty] | Non-TXV | 4.234%
Clovis | CA | 93619-4623 |  | 2013-09-20 | 2013-09-20 10:54 | 2013-09-20 10:55 | BRYANT - 563CN042-C | 108 | 4.9 | Yes | Yes | 19 | 20.7 | -1.7 | 2187AA3EC8FD4418810DFF3E86D5CC3C |  | R22 | Non-TXV |  | 4.537% | 0.95463 | 8.719% | [5 empty] | Non-TXV | 4.537%
Chico | CA | 95973-0450 |  | 2013-09-25 | 2013-09-25 16:36 | 2013-09-25 16:59 | BRYANT - 582ANW024060NAAD | 50 | -2.9 | Yes | Yes | 22 | 20.7 | 1.3 | ACE3E825A7C743A280D8754AF177541D |  | R22 | TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | TXV |  |  | -5.8%
Stockton | CA | 95210-3272 |  | 2013-09-19 | 2013-09-19 10:47 | 2013-09-19 11:04 | RHEEM - UNK | 78 | -6.4 | Yes | Yes | 19.2 | 18.1 | 1.1 | EC055C5522874B018C769F4374C2EB8F |  | R22 | Non-TXV |  | -8.205% | 1.0821 | 2.298% |  |  |  |  | Non-TXV |  |  | -8.205%
Stockton | CA | 95207-2261 |  | 2013-09-20 | 2013-09-20 12:05 | 2013-09-20 12:24 | OTHER - 10AJB24A01 | 65 | 3.6 | Yes | Yes | 19.5 | 19.5 | 0 | 2CC0AA5AECE24607BBE669766A9E6E53 |  | R22 | Non-TXV |  | 5.538% | 0.94462 | 10.64% | [5 empty] | Non-TXV | 5.538%
Riverbank | CA | 95367-3847 |  | 2013-10-01 | 2013-10-01 10:50 | 2013-10-01 11:20 | CARRIER - 38BRC030310 | 99 | 2.9 | Yes | Yes | 20.8 | 18.7 | 2.1 | BE85C730D669484D9BDB0621822B3E2E |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Stockton | CA | 95210-6769 |  | 2013-10-07 | 2013-10-07 15:51 | 2013-10-07 16:31 | YORK - H2RA036S06A | 63 | 11.1 | Yes | Yes | 27.7 | 24.8 | 2.9 | 4B7B7E56A6C94B3FA27FDA3ADF028605 |  | R22 | Non-TXV |  | 17.62% | 0.82381 | 33.86% | [5 empty] | Non-TXV | 17.62%
Reedley | CA | 93654-3661 |  | 2013-09-30 | 2013-09-30 15:54 | 2013-09-30 16:45 | UNITARY PRODUCTS GROUP - GCGD21S1A48S1 | 75 | 13.8 | Yes | Yes | 19.9 | 20.4 | -0.5 | FF7346D457814B09A13B3BFF969F91F9 |  | R22 | Non-TXV |  | 18.4% | 0.816 | 35.36% | [5 empty] | Non-TXV | 18.4%
Fresno | CA | 93722-9180 |  | 2013-10-21 | 2013-10-21 09:46 | 2013-10-21 10:49 | YORK - D2NP024N03606A | 100 | 12.7 | Yes | Yes | 21.2 | 20.7 | 0.5 | ABF0D12541FB4581B22064CFBABA9D57 |  | R22 | Non-TXV |  | 12.7% | 0.873 | 24.41% | [5 empty] | Non-TXV | 12.7%
Clovis | CA | 93611-5464 |  | 2013-09-19 | 2013-09-19 10:40 | 2013-09-19 10:42 | RHEEM - RRPLB036JK08X | 92 | 3.2 | Yes | Yes | 20 | 17.6 | 2.4 | 24C13883F15B412692D6A3EA72E0565A |  | R410A | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Rocklin | CA | 95765-4647 |  | 2013-09-27 | 2013-09-27 16:18 | 2013-09-27 16:18 | YORK - H3RA060S06B | 98 | 0 | Yes | Yes | 24.9 | 23.7 | 1.2 | 6A0AFA2A8A9C4D2D91B0D3F5634055A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1513 |  | 2013-09-16 | 2013-09-16 11:16 | 2013-09-16 11:18 | BDP - 56AN036A | 122 | 14.6 | Yes | Yes | 29.2 | 23.7 | 5.5 | 2FF1CB6BFDB7447D846ABA026C40CEB8 |  | R22 | TXV |  | 11.97% | 0.88033 | 23% | [5 empty] | TXV | 11.97%
Fresno | CA | 93702-1767 |  | 2013-09-18 | 2013-09-18 16:12 | 2013-09-18 16:33 | BDP - 585CJ024050 | 72 | 10.5 | Yes | Yes | 22.5 | 19.7 | 2.8 | 1409A71BA2A745A8BDD72D6D42466654 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.58% | 0.85417 | 28.03% | [5 empty] | Non-TXV | 14.58%
Fresno | CA | 93704-1708 |  | 2013-09-19 | 2013-09-19 12:23 | 2013-09-19 13:18 | DAY & NIGHT - N/A | 55 | 4 | Yes | Yes | 19 | 21 | -2 | C3BCB7380B394B7182FA4069FA5AF985 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Fresno | CA | 93725-1841 |  | 2013-09-23 | 2013-09-23 17:39 | 2013-09-23 18:11 | UNITARY PRODUCTS GROUP - AC048X1021G | 117 | 4.7 | Yes | Yes | 21 | 20.2 | 0.8 | B8879EF3F3DE4E5A9F3010480E8FF569 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.017% | 0.95983 | 7.72% | [5 empty] | Non-TXV | 4.017%
Reedley | CA | 93654-3661 |  | 2013-09-30 | 2013-09-30 11:47 | 2013-09-30 12:33 | RHEEM - RAND--42JBZ | 136 | 7.2 | Yes | Yes | 22.3 | 19.6 | 2.7 | 4DD9ACF9AC434D54A1563C4AAE96ED01 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Tracy | CA | 95376-2319 |  | 2013-09-16 | 2013-09-16 12:55 | 2013-09-16 13:16 | PAYNE - PA13NR036-H | 83 | 3.2 | Yes | Yes | 18.9 | 17 | 1.9 | 8DB23F36D6F04EF9AB4E8B6BD02FADAB |  | R22 | TXV |  | 3.855% | 0.96145 | 7.409% | [5 empty] | TXV | 3.855%
Los Banos | CA | 93635-6342 |  | 2013-09-19 | 2013-09-19 12:52 | 2013-09-19 12:53 | PAYNE - PY1PNB042090AAAA | 100 | 5.3 | Yes | Yes | 26.5 | 20.9 | 5.6 | 42B19B41EFA34408BB038E4323427EC9 |  | R22 | Non-TXV |  | 5.3% | 0.947 | 10.19% | [5 empty] | Non-TXV | 5.3%
Orland | CA | 95963-2053 |  | 2013-09-16 | 2013-09-16 08:49 | 2013-09-16 08:49 | DAY & NIGHT - N2A342AKA200 | 113 | 0 | Yes | Yes | 20.3 | 19.1 | 1.3 | 52BC13F274D54E0F9EBF66A984F274F3 |  | R410A | TXV |  | 0% | 1 | 0%
Madera | CA | 93637-4860 |  | 2013-10-11 | 2013-10-11 12:03 | 2013-10-11 12:04 | CARRIER - 48GX036060301 | 82 | 7.1 | Yes | Yes | 22 | 19.3 | 2.7 | FF59A2F6FF5E4C1282DD7D9E255F5D0B |  | R22 | Non-TXV |  | 8.659% | 0.91341 | 16.64% | [5 empty] | Non-TXV | 8.659%
Los Banos | CA | 93635-6438 |  | 2013-09-13 | 2013-09-13 13:21 | 2013-09-13 13:23 | BRYANT - 563CN042-E | 108 | 3.2 | Yes | Yes | 18.8 | 18.8 | 0 | 6511D6F2116F416099BEA89B767361EC |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Paso Robles | CA | 93446-1803 |  | 2013-10-07 | 2013-10-07 14:36 | 2013-10-07 14:53 | NORDYNE - VR8GD-X60K096X | 64 | -3.8 | Yes | Yes | 26.5 | 20.9 | 5.6 | DFE5DD1B2F284F948CEEE1AA4706D6D2 |  | R410A | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Stockton | CA | 95203-1337 |  | 2013-09-30 | 2013-09-30 09:59 | 2013-09-30 10:25 | OTHER - UNK | 85 | 6.8 | Yes | Yes | 18.6 | 21.5 | -2.9 | 45F73A9A6B0540EE8245AE8A49BA625F |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Stockton | CA | 95209-4813 |  | 2013-09-25 | 2013-09-25 10:32 | 2013-09-25 10:50 | PAYNE - 591ANX036000AAAA | 85 | -5 | Yes | Yes | 24.8 | 18.8 | 6 | 8F596D8C978146E3B2CEE016FD0907D5 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93722-3711 |  | 2013-09-26 | 2013-09-26 14:25 | 2013-09-26 14:26 | CARRIER - 38CK036330 | 70 | 11 | Yes | Yes | 21.1 | 17.6 | 3.5 | 895EF2C995AE4B52B99E5320337F60C8 |  | R22 | TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | TXV | 15.71%
Los Banos | CA | 93635-6326 |  | 2013-10-08 | 2013-10-08 22:11 | 2013-10-08 22:14 | OTHER - 561CJ048-A | 105 | 4.4 | Yes | Yes | 23.5 | 22 | 1.5 | 6E3425611A6946CA83FEB25E3C2D9D12 |  | R22 | Non-TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | Non-TXV | 4.19%
Fresno | CA | 93702-4604 |  | 2013-09-18 | 2013-09-18 15:26 | 2013-09-18 15:43 | YORK - D1NA03605606B | 63 | 2.4 | Yes | Yes | 17.6 | 19.5 | -1.9 | 7502171492E34E64B4E3E183D381F192 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Chico | CA | 95926-3055 |  | 2013-09-24 | 2013-09-24 12:30 | 2013-09-24 12:55 | OTHER - CA5530VK02 | 74 | 4.6 | Yes | Yes | 24 | 19.3 | 4.7 | 95EEA379ED8C42A3BB6C3684C2B3B114 |  | R22 | Non-TXV |  | 6.216% | 0.93784 | 11.95% | [5 empty] | Non-TXV | 6.216%
Clovis | CA | 93612-0403 |  | 2013-09-30 | 2013-09-30 14:29 | 2013-09-30 14:30 | CARRIER - 48GS-036060311 | 68 | 3.8 | Yes | Yes | 23.8 | 20.4 | 3.4 | 25A9E4D1A1354760A2C8A1F3EDFD8112 |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Riverdale | CA | 93656-9253 |  | 2013-10-03 | 2013-10-03 14:57 | 2013-10-03 15:45 | WEATHER KING - 12AJB48A01 | 245 | 7.8 | Yes | Yes | 21.8 | 20.2 | 1.7 | 324A38A99E214D469464066228C4282C |  | R22 | Non-TXV |  | 3.184% | 0.96816 | 6.118% | [5 empty] | Non-TXV | 3.184%
Fresno | CA | 93722-9180 |  | 2013-10-07 | 2013-10-07 13:00 | 2013-10-07 13:59 | DAY & NIGHT - 5H5J024040 | 68 | 2.2 | Yes | Yes | 23.7 | 20.4 | 3.3 | 3D2492667F3F414F99A5A6A8F6BE643C |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Orland | CA | 95963-1970 |  | 2013-09-16 | 2013-09-16 08:37 | 2013-09-16 08:56 | TRANE - TTNO24C100AO | 107 | 8.8 | Yes | Yes | 19.2 | 17.2 | 2 | B7F6586166D844468E46A038142B4BBE |  | R22 | Non-TXV |  | 8.224% | 0.91776 | 15.81% | [5 empty] | Non-TXV | 8.224%
Fresno | CA | 93727-7220 |  | 2013-09-16 | 2013-09-16 16:07 | 2013-09-16 16:43 | AMANA - PGD36C0702X | 110 | 10.5 | Yes | Yes | 21.9 | 19.5 | 2.4 | F3597DFFBE7B467389D08C0782DF2B1C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Auburn | CA | 95603-3124 |  | 2013-09-13 | 2013-09-13 15:16 | 2013-09-13 15:37 | PAYNE - 589ANW030080ACBD | 65 | 1.9 | Yes | Yes | 16 | 16.4 | -0.4 | 9490C9A0DA9441C38F946E15D0DCF372 |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Loomis | CA | 95650-8514 |  | 2013-09-13 | 2013-09-13 10:45 | 2013-09-13 10:45 | TRANE - WCY042G100BB | 142 | 0 | Yes | Yes | 22.1 | 18.8 | 3.3 | 6DF7797DDBE244BF9082309FF61AE30E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93723-9369 |  | 2013-10-14 | 2013-10-14 12:40 | 2013-10-14 13:12 | CARRIER - 48SX-036080311AA | 84 | 14.5 | Yes | Yes | 23.7 | 21.7 | 2 | 64739646639340B18548B7D9C6219DFB |  | R22 | Non-TXV |  | 17.26% | 0.82738 | 33.17% | [5 empty] | Non-TXV | 17.26%
Clovis | CA | 93612-3326 |  | 2013-09-19 | 2013-09-19 09:01 | 2013-09-19 09:03 | COLEMAN - DAYPF036N090A | 108 | 9.9 | Yes | Yes | 19 | 18.3 | 0.7 | 1C9C158BD1424AACAB4A32FD3CE98454 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Fresno | CA | 93727-1949 |  | 2013-09-17 | 2013-09-17 10:07 | 2013-09-17 10:19 | RUUD - 13AJA24A01757 | 56 | 4.4 | Yes | Yes | 17.6 | 18.2 | -0.6 | 49F405A353F74FF79E204D2299D8FEC2 |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Auburn | CA | 95602-8088 |  | 2013-09-13 | 2013-09-13 12:33 | 2013-09-13 12:55 | WHIRLPOOL - UNK | 70 | 6.8 | Yes | Yes | 17 | 17.4 | -0.4 | 754769D1957347FDA24B32C391D86E54 |  | R22 | Non-TXV |  | 9.714% | 0.90286 | 18.67% | [5 empty] | Non-TXV | 9.714%
Merced | CA | 95341-5592 |  | 2013-09-17 | 2013-09-17 15:16 | 2013-09-17 15:18 | PAYNE - 591ANX036000AAAA | 85 | 2.6 | Yes | Yes | 24.8 | 20.1 | 4.7 | A063408B8F7A4116AF15CD992CEA2F75 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Clovis | CA | 93612-3326 |  | 2013-09-19 | 2013-09-19 09:28 | 2013-09-19 09:29 | DAY & NIGHT - UNK | 56 | 6.5 | Yes | Yes | 20.4 | 17.2 | 3.2 | 0EE4EECD5AB74A8F9C0A2CD45410F294 |  | R22 | Non-TXV |  | 11.61% | 0.88393 | 22.31% | [5 empty] | Non-TXV | 11.61%
Willows | CA | 95988-2028 |  | 2013-09-17 | 2013-09-17 13:18 | 2013-09-17 13:38 | PAYNE - NA | 70 | 4.4 | Yes | Yes | 16.2 | 17.7 | -1.5 | 575933BE42A44BD8AA3945D8B2553D0B |  | R22 | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Fresno | CA | 93703-2804 |  | 2013-09-23 | 2013-09-23 14:27 | 2013-09-23 14:27 | OTHER - GCGD36S21S2B | 80 | 0 | Yes | Yes | 18.5 | 20.8 | -2.3 | AC6A67493A424961AA0BE321F27D3FF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3741 |  | 2013-09-25 | 2013-09-25 13:59 | 2013-09-25 14:35 | CARRIER - 38TDA036300 | 184 | 11.1 | Yes | Yes | 18 | 20.7 | -2.7 | CBE4BE20BB8F46DF8C58A2C5F1AFD970 |  | R22 | Non-TXV |  | 6.033% | 0.93967 | 11.59% | [5 empty] | Non-TXV | 6.033%
Orange Cove | CA | 93646-2479 |  | 2013-10-09 | 2013-10-09 17:43 | 2013-10-09 18:13 | UNITARY PRODUCTS GROUP - HP030X1221A | 105 | 4.4 | Yes | Yes | 19.1 | 21.3 | -2.2 | 5A473A96F46045C78C87F8A7438E1DD6 |  | R22 | Non-TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | Non-TXV | 4.19%
Orange Cove | CA | 93646-2476 |  | 2013-10-09 | 2013-10-09 16:56 | 2013-10-09 17:41 | UNITARY PRODUCTS GROUP - HP030X1221A | 105 | 5.8 | Yes | Yes | 18.5 | 20.7 | -2.2 | 98B708A31B734D8DA38EFECCBACE72FB |  | R22 | Non-TXV |  | 5.524% | 0.94476 | 10.62% | [5 empty] | Non-TXV | 5.524%
Placerville | CA | 95667-3409 |  | 2013-09-19 | 2013-09-19 15:27 | 2013-09-19 15:27 | NORDYNE - S3BA-036KA | 69 | 0 | Yes | Yes | 26.6 | 22.4 | 4.2 | 2A02CACCB9704F43AFCBC990387C925C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5057 |  | 2013-09-19 | 2013-09-19 11:30 | 2013-09-19 11:31 | GOODMAN - PGB0360501 | 60 | 7.8 | Yes | Yes | 20 | 18.3 | 1.7 | BA1FA7764BA145328C8B4A1AE962BED0 |  | R22 | Non-TXV |  | 13% | 0.87 | 24.98% | [5 empty] | Non-TXV | 13%
Clovis | CA | 93612-5047 |  | 2013-09-17 | 2013-09-17 09:34 | 2013-09-17 09:36 | BDP - 588ANW036080ACAF | 67 | 5.7 | Yes | Yes | 20.7 | 18.2 | 2.5 | 3D6DF69E70194BF790E94DC4F1839646 |  | R22 | Non-TXV |  | 8.507% | 0.91493 | 16.35% | [5 empty] | Non-TXV | 8.507%
Madera | CA | 93637-4117 |  | 2013-10-17 | 2013-10-17 11:56 | 2013-10-17 11:57 | AIRE-FLO - 110AW42105 | 54 | 6.7 | Yes | Yes | 27.8 | 22.2 | 5.6 | 380A46F9EC5B40C5AF6A0510962CCA71 |  | R22 | Non-TXV |  | 12.41% | 0.87593 | 23.84% | [5 empty] | Non-TXV | 12.41%
Fresno | CA | 93720-1246 |  | 2013-09-20 | 2013-09-20 21:23 | 2013-09-20 21:25 | RHEEM - 7777UNK | 92 | 4.2 | Yes | Yes | 21.1 | 20.4 | 0.7 | 550AE7DAD9E94E2296E6B292FC7CD048 |  | R22 | Non-TXV |  | 4.565% | 0.95435 | 8.773% | [5 empty] | Non-TXV | 4.565%
Fresno | CA | 93720-1246 |  | 2013-09-20 | 2013-09-20 21:26 | 2013-09-20 21:29 | RHEEM - 7777UNK | 92 | 4.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | 9FA922BD41CC40B8B8BDDADDCA2C52CD |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Sanger | CA | 93657-3570 |  | 2013-09-25 | 2013-09-25 17:17 | 2013-09-25 17:57 | UNITARY PRODUCTS GROUP - H2RC036S06G | 83 | 3.2 | Yes | Yes | 17.5 | 20.4 | -2.9 | 3D38F03455454BEE9D49950BD07FA41C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.855% | 0.96145 | 7.409% | [5 empty] | Non-TXV | 3.855%
Stockton | CA | 95207-2027 |  | 2013-09-13 | 2013-09-13 10:43 | 2013-09-13 11:00 | OTHER - GAS4TF-1 | 133 | 21.6 | Yes | Yes | 16 | 17.9 | -1.8 | 6E277D7172A344DE9E34C3B8746AEC31 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.24% | 0.83759 | 31.21% | [5 empty] | Non-TXV | 16.24%
Durham | CA | 95938-9662 |  | 2013-10-25 | 2013-10-25 10:48 | 2013-10-25 11:10 | NORDYNE - NA | 75 | 3.5 | Yes | Yes | 25 | 24 | 1.1 | 5BF5582A87534B1D8584AC560753A80A |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Orange Cove | CA | 93646-2475 |  | 2013-09-17 | 2013-09-17 17:13 | 2013-09-17 17:34 | UNITARY PRODUCTS GROUP - HP036X1221A | 105 | 3.3 | Yes | Yes | 21.5 | 22.2 | -0.7 | 16B6E1290D264BA69F7FF7B7017796F1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Chico | CA | 95926-7323 |  | 2013-09-26 | 2013-09-26 16:42 | 2013-09-26 17:06 | LENNOX - GCS20R-411-75-4P | 70 | -6.9 | Yes | Yes | 21 | 19.9 | 1.1 | 8C8E1CE903EC493096B51CA8C19F6B73 |  | R22 | TXV |  | -9.857% | 1.0986 | 2.76% |  |  |  |  | TXV |  |  | -9.857%
Los Banos | CA | 93635-3402 |  | 2013-09-30 | 2013-09-30 15:56 | 2013-09-30 15:56 | CARRIER - 48DC003 | 56 | 0 | Yes | Yes | 0 | 25.3 | -25.3 | E27BD648F0B54409903616BE85E36659 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1623 |  | 2013-09-25 | 2013-09-25 15:46 | 2013-09-25 15:47 | OTHER - PA13NR030-B | 88 | 4.6 | Yes | Yes | 22.1 | 20 | 2.2 | 32A6202B6F65412D82946AAE5C447F8F |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Ripon | CA | 95366-2631 |  | 2013-10-09 | 2013-10-09 12:23 | 2013-10-09 12:39 | TRANE - TT7D42A100A0 | 106 | 14.6 | Yes | Yes | 21.4 | 19.9 | 1.5 | 6A371483BEDC4AF499EF0C5C99A95EFB | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 13.77% | 0.86226 | 26.47% | [5 empty] | Non-TXV | 13.77%
Stockton | CA | 95210-5639 |  | 2013-09-23 | 2013-09-23 10:11 | 2013-09-23 10:31 | PAYNE - 591ANX048000ABAA | 116 | -8.2 | Yes | Yes | 15.9 | 17.7 | -1.8 | 8AE6D5BBD8F84A3CA03DA014AA3195C5 |  | R22 | Non-TXV |  | -7.069% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.069%
Fresno | CA | 93727-6420 |  | 2013-09-16 | 2013-09-16 15:06 | 2013-09-16 16:03 | CARRIER - 38BR-036---301 | 122 | 4.1 | Yes | Yes | 19 | 20.4 | -1.4 | 6396399AB9384792893DE3507C5BACB3 |  | R22 | Non-TXV |  | 3.361% | 0.96639 | 6.458% | [5 empty] | Non-TXV | 3.361%
Stockton | CA | 95206-2495 |  | 2013-09-25 | 2013-09-25 11:47 | 2013-09-25 12:06 | GOODMAN - UNK | 101 | 3.1 | Yes | Yes | 17.5 | 18 | -0.5 | 86BF25C79C4C4731B04D8ECC318C1BCB |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Fresno | CA | 93727-1419 |  | 2013-09-23 | 2013-09-23 11:37 | 2013-09-23 12:30 | LENNOX - 13ACD-036-230-01 | 111 | 3.9 | Yes | Yes | 17.7 | 20.4 | -2.7 | 6E363506967246C3BE024CDF34901ABC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Woodbridge | CA | 95258-9323 |  | 2013-10-03 | 2013-10-03 11:54 | 2013-10-03 12:12 | BDP - 565BJ042 | 94 | 4.3 | Yes | Yes | 25.4 | 20.1 | 5.3 | B64EAB7CF5F04D83A08276B54B2350D4 |  | R22 | Non-TXV |  | 4.574% | 0.95426 | 8.791% | [5 empty] | Non-TXV | 4.574%
Grass Valley | CA | 95949-6518 |  | 2013-09-30 | 2013-09-30 10:35 | 2013-09-30 10:54 | TRANE - TTD736A100A0 | 100 | 5.4 | Yes | Yes | 24.4 | 20.1 | 4.3 | C4B5B759846C4D42BF6C5F9B78BAE208 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Chico | CA | 95973-0179 |  | 2013-10-16 | 2013-10-16 15:35 | 2013-10-16 16:31 | PAYNE - PA13NR048-H | 136 | 5.6 | Yes | Yes | 16.2 | 19.1 | -2.9 | 6887A960AF494B6CBD1683B60BF381A7 |  | R22 | TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | TXV | 4.118%
Stockton | CA | 95212-3458 |  | 2013-09-24 | 2013-09-24 09:34 | 2013-09-24 09:55 | CARRIER - 561CJ030-E | 66 | 2.1 | Yes | Yes | 18.5 | 18.2 | 0.3 | C71D2860FE784B3389706519FE56414C |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Chico | CA | 95973-1151 |  | 2013-09-25 | 2013-09-25 10:44 | 2013-09-25 11:05 | CARRIER - UNK | 50 | 1.5 | Yes | Yes | 26 | 20.6 | 5.4 | E236206EB12D401FB61AF6704CC9DDAF |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95209-3501 |  | 2013-09-23 | 2013-09-23 10:30 | 2013-09-23 10:50 | YORK - H2RA036S06E | 63 | 2.9 | Yes | Yes | 19.3 | 17.4 | 1.9 | 5636BAD1FBA244248884C687D86943F5 |  | R22 | Non-TXV |  | 4.603% | 0.95397 | 8.846% | [5 empty] | Non-TXV | 4.603%
Nevada City | CA | 95959-8984 |  | 2013-09-24 | 2013-09-24 12:02 | 2013-09-24 12:02 | CARRIER - 48XP-060115301-- | 211 | 0 | Yes | Yes | 26.1 | 20.7 | 5.4 | D3FEF260D1E94BF4A9ADFC4BDAFC508E |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6347 |  | 2013-09-19 | 2013-09-19 13:42 | 2013-09-19 14:09 | YORK - H2RC036S06A | 83 | 13.8 | Yes | Yes | 18.6 | 20.7 | -2.1 | EA29085400DD4CCAB617A82D609469CE |  | R22 | Non-TXV |  | 16.63% | 0.83373 | 31.95% | [5 empty] | Non-TXV | 16.63%
Willows | CA | 95988-2008 |  | 2013-09-17 | 2013-09-17 10:27 | 2013-09-17 11:25 | YORK - D1NH036N07206A | 104 | 5.7 | Yes | Yes | 15.7 | 18.7 | -3 | 7096079E74FA49FCA9FD2D72F97BA74B |  | R22 | Non-TXV |  | 5.481% | 0.94519 | 10.53% | [5 empty] | Non-TXV | 5.481%
Stockton | CA | 95215-6706 |  | 2013-10-16 | 2013-10-16 15:12 | 2013-10-16 15:44 | YORK - H2RA036S06G | 63 | 16.8 | Yes | Yes | 22.2 | 21.8 | 0.5 | 7CC673E183CC4F0884730D3DF9A296B0 |  | R22 | Non-TXV |  | 26.67% | 0.73333 | 51.25% | [5 empty] | Non-TXV | 26.67%
Auburn | CA | 95602-9191 |  | 2013-09-13 | 2013-09-13 13:59 | 2013-09-13 14:27 | CARRIER - 38CKC060300 | 150 | 10.1 | Yes | Yes | 17 | 19.3 | -2.3 | E846FBC67F124C31B34630A113F2E346 |  | R22 | TXV |  | 6.733% | 0.93267 | 12.94% | [5 empty] | TXV | 6.733%
Stockton | CA | 95207-4126 |  | 2013-10-04 | 2013-10-04 12:59 | 2013-10-04 13:17 | YORK - D1NA036N03606C | 67 | 3.5 | Yes | Yes | 24.5 | 18.5 | 6 | EB938E53244D484B85A439048733AB31 |  | R22 | Non-TXV |  | 5.224% | 0.94776 | 10.04% | [5 empty] | Non-TXV | 5.224%
Fresno | CA | 93727-1914 |  | 2013-09-26 | 2013-09-26 10:12 | 2013-09-26 10:45 | BDP - N/A | 85 | 24.7 | Yes | Yes | 21 | 20.4 | 0.6 | 5D26C89D653A44EFBC968C9778FDD316 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 29.06% | 0.70941 | 55.84% | [5 empty] | Non-TXV | 29.06%
Mariposa | CA | 95338-9128 |  | 2013-09-25 | 2013-09-25 13:28 | 2013-09-25 13:30 | RUUD - 7777UNK | 80 | 6.5 | Yes | Yes | 21.6 | 19.5 | 2.1 | 56BDFCCBC6454D9E817418084F0A08E5 |  | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Kingsburg | CA | 93631-1741 |  | 2013-10-07 | 2013-10-07 12:56 | 2013-10-07 13:36 | TEMPSTAR - CA3048UKA1 | 138 | 19.1 | Yes | Yes | 24 | 19.8 | 4.2 | 3B032F70CFF04EA5997B6E123687907A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.84% | 0.86159 | 26.6% | [5 empty] | Non-TXV | 13.84%
Reedley | CA | 93654-2620 |  | 2013-09-30 | 2013-09-30 14:23 | 2013-09-30 15:51 | ICP - HAC048KA1 | 123 | 3.7 | Yes | Yes | 23.8 | 20.4 | 3.4 | 1E5E5F0920134CDCB92633CE0A2DD7B8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.781% | [5 empty] | Non-TXV | 3.008%
Los Banos | CA | 93635-3906 |  | 2013-09-20 | 2013-09-20 10:26 | 2013-09-20 10:28 | WESTINGHOUSE - UNK | 76 | 8.9 | Yes | Yes | 19.8 | 17.2 | 2.6 | F96E959248EA4A9D8C8A36D7E9A6572A |  | R22 | Non-TXV |  | 11.71% | 0.88289 | 22.51% | [5 empty] | Non-TXV | 11.71%
Paso Robles | CA | 93446-2914 |  | 2013-10-09 | 2013-10-09 13:20 | 2013-10-09 13:39 | PAYNE - PY3GNAA36090NA | 102 | -6 | Yes | Yes | 21.9 | 19.1 | 2.8 | BE51BD5A78A0491BB91F69B546CA8756 |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Paso Robles | CA | 93446-2914 |  | 2013-10-09 | 2013-10-09 13:42 | 2013-10-09 14:05 | RHEEM - HC-80-30-21C | 48 | -2.8 | Yes | Yes | 22.2 | 19.5 | 2.7 | 71E5E3CBCD604D3A981C3D7938C6F98E |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95206-6386 |  | 2013-09-19 | 2013-09-19 12:37 | 2013-09-19 13:00 | GOODMAN - CLJ48-1 | 117 | 9.1 | Yes | Yes | 21.7 | 21.5 | 0.2 | CC17983F38D745189FD2CA67C95EF288 |  | R22 | TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | TXV | 7.778%
Chico | CA | 95926-4653 |  | 2013-10-21 | 2013-10-21 16:37 | 2013-10-21 16:05 | PAYNE - 541DJ024 | 118 | 3.7 | Yes | Yes | 16.1 | 18.2 | -2.1 | D4240FCDB9A44AAE843F1807B8AD2AC8 |  | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Atwater | CA | 95301-2072 |  | 2013-09-26 | 2013-09-26 16:38 | 2013-09-26 16:41 | CARRIER - 48GX036090301AD | 82 | 8.4 | Yes | Yes | 23.3 | 18.7 | 4.6 | 5576DEA9725F4527A3DAA501C7F5665D |  | R22 | Non-TXV |  | 10.24% | 0.89756 | 19.69% | [5 empty] | Non-TXV | 10.24%
Lincoln | CA | 95648-9568 |  | 2013-09-19 | 2013-09-19 16:46 | 2013-09-19 17:33 | OTHER - UNK | 95 | 3.7 | Yes | Yes | 18 | 20.1 | -2.1 | 7CD2C0F67BEF4526BB4C68F4653AC78F |  | R22 | Non-TXV |  | 3.895% | 0.96105 | 7.485% | [5 empty] | Non-TXV | 3.895%
Stockton | CA | 95209-0000 |  | 2013-09-30 | 2013-09-30 10:44 | 2013-09-30 11:02 | CARRIER - 24ABA348A300 | 121 | -4.8 | Yes | Yes | 20.8 | 16.8 | 4 | 8524D6EAD63D47B697A99065927E0512 |  | R410A | TXV |  | -3.967% | 1.0397 | 1.111% |  |  |  |  | TXV |  |  | -3.967%
Yuba City | CA | 95993-7687 |  | 2013-10-22 | 2013-10-22 10:57 | 2013-10-22 11:16 | DAY & NIGHT - AA1CJ-042-A | 80 | 4 | Yes | Yes | 18 | 19.5 | -1.5 | F5FFE3A5211C4904BC9AFAED894EB9D2 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Lathrop | CA | 95330-9359 |  | 2013-09-18 | 2013-09-18 10:34 | 2013-09-18 10:53 | CARRIER - UNK | 140 | 4.9 | Yes | Yes | 17.5 | 17.2 | 0.3 | 5B202086F2E04DDBB1647841F140F12E |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Merced | CA | 95348-2236 |  | 2013-09-18 | 2013-09-18 14:37 | 2013-09-18 14:39 | OTHER - 3TZAA3182A | 67 | 2.8 | Yes | Yes | 23.6 | 20.2 | 3.4 | A3B57B2AF16043AE9E7C45D9272F682F |  | R22 | Non-TXV |  | 4.179% | 0.95821 | 8.031% | [5 empty] | Non-TXV | 4.179%
Fresno | CA | 93722-4222 |  | 2013-10-02 | 2013-10-02 10:36 | 2013-10-02 10:37 | WESTINGHOUSE - ID036BAA | 118 | 11.4 | Yes | Yes | 15.6 | 17.1 | -1.5 | 8651FAFF047F4D0AA8B3D29762BC9962 |  | R22 | Non-TXV |  | 9.661% | 0.90339 | 18.57% | [5 empty] | Non-TXV | 9.661%
Willows | CA | 95988-2914 |  | 2013-10-10 | 2013-10-10 13:00 | 2013-10-10 13:39 | YORK - D1NH042N09006C | 94 | 6.2 | Yes | Yes | 23.2 | 20.8 | 2.4 | 9DF046299FAA41F68D979FCB814950F8 |  | R22 | Non-TXV |  | 6.596% | 0.93404 | 12.68% | [5 empty] | Non-TXV | 6.596%
Stockton | CA | 95206-6357 |  | 2013-10-11 | 2013-10-11 16:32 | 2013-10-11 17:12 | GOODMAN - CLJ42-1 | 99 | 10 | Yes | Yes | 18.3 | 19.8 | -1.5 | 35BE00B9FD544009B0B84A272898D6AF |  | R22 | TXV |  | 10.1% | 0.89899 | 19.41% | [5 empty] | TXV | 10.1%
South Dos Palos | CA | 93665-0000 |  | 2013-09-30 | 2013-09-30 17:02 | 2013-09-30 17:03 | AMANA - VCA30B2D | 68 | 7.6 | Yes | Yes | 20.4 | 19.3 | 1.1 | 026B7E7657D24C60A2E4F79822216AE4 |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Fresno | CA | 93727-2315 |  | 2013-09-16 | 2013-09-16 10:43 | 2013-09-16 11:39 | PAYNE - 48RAC-1S8C | 103 | 19.4 | Yes | Yes | 16.1 | 18.7 | -2.6 | CF4089DADCE34DCCAAC4659BCDE44353 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.83% | 0.81165 | 36.2% | [5 empty] | Non-TXV | 18.83%
Stockton | CA | 95207-4212 |  | 2013-09-20 | 2013-09-20 12:56 | 2013-09-20 13:19 | PAYNE - PY3PNA030060NA-- | 130 | 11.1 | Yes | Yes | 20.7 | 17.3 | 3.5 | AFB57CD2BDEB4FBAA22C49E8BE607A72 |  | R22 | Non-TXV |  | 8.538% | 0.91462 | 16.41% | [5 empty] | Non-TXV | 8.538%
Merced | CA | 95340-3229 |  | 2013-09-23 | 2013-09-23 14:56 | 2013-09-23 14:57 | JANITROL - UNK | 76 | 9.1 | Yes | Yes | 24.2 | 19.2 | 5 | C69C5CE4A6E640828A18823F748E3240 |  | R22 | Non-TXV |  | 11.97% | 0.88026 | 23.01% | [5 empty] | Non-TXV | 11.97%
Atwater | CA | 95301-9495 |  | 2013-09-24 | 2013-09-24 13:26 | 2013-09-24 13:28 | GOODMAN - CK421C | 92 | 13.6 | Yes | Yes | 21.2 | 19.8 | 1.4 | E0D7F3E983AF402A901B44249A94F20B |  | R22 | Non-TXV |  | 14.78% | 0.85217 | 28.41% | [5 empty] | Non-TXV | 14.78%
Merced | CA | 95348-1122 |  | 2013-09-20 | 2013-09-20 15:01 | 2013-09-20 15:03 | GOODMAN - PGB0360751 | 60 | 0 | Yes | Yes | 6.1 | 21.3 | -15.2 | C874715C762B4BF38BB120F0CD77A7CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Escalon | CA | 95320-9545 |  | 2013-09-30 | 2013-09-30 12:42 | 2013-09-30 13:03 | COLEMAN - CBD | 64 | 1.9 | Yes | Yes | 20.1 | 17.7 | 2.4 | C812AE2BA9D449AFB245F61275662394 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Los Banos | CA | 93635-5115 |  | 2013-10-21 | 2013-10-21 21:42 | 2013-10-21 21:44 | BRYANT - 563CN036-A | 115 | 3.8 | Yes | Yes | 21 | 19.9 | 1.1 | AEDAAA2A31D74B44A445B334ADFDD601 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.35% | [5 empty] | Non-TXV | 3.304%
Los Banos | CA | 93635-5115 |  | 2013-10-21 | 2013-10-21 21:46 | 2013-10-21 21:47 | BRYANT - 563CN036-A | 115 | 3.9 | Yes | Yes | 23.2 | 21 | 2.2 | BB4002EF37104E79814497F94CEF2E05 |  | R22 | Non-TXV |  | 3.391% | 0.96609 | 6.517% | [5 empty] | Non-TXV | 3.391%
Willows | CA | 95988-0186 |  | 2013-09-17 | 2013-09-17 10:37 | 2013-09-17 11:24 | LENNOX - GCS20R-411-100-1P | 70 | 2.4 | Yes | Yes | 19 | 19.6 | -0.6 | 40DFFD87543E4A8F94A777E3FDE32128 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Chowchilla | CA | 93610-2423 |  | 2013-09-20 | 2013-09-20 17:14 | 2013-09-20 17:15 | WEATHER KING - 10AJA3001 | 70 | 3 | Yes | Yes | 19.2 | 20.8 | -1.6 | E05E225E28574DC599746362F5F5BAA9 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Merced | CA | 95341-5572 |  | 2013-09-17 | 2013-09-17 14:36 | 2013-09-17 14:43 | GOODMAN - CK30-1A | 76 | 5 | Yes | Yes | 24.3 | 22.3 | 2 | 5805B87FA5E54DE4B95AD61C214B1EAC |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Stockton | CA | 95212-1123 |  | 2013-09-23 | 2013-09-23 09:51 | 2013-09-23 10:08 | GOODMAN - GSC130361GA | 80 | 5.1 | Yes | Yes | 21.7 | 17.2 | 4.5 | 2F623CE7A081438F81E56451E1DD9D8B |  | R22 | Non-TXV |  | 6.375% | 0.93625 | 12.25% | [5 empty] | Non-TXV | 6.375%
Fresno | CA | 93727-3689 |  | 2013-09-16 | 2013-09-16 13:42 | 2013-09-16 15:04 | LENNOX - 12GCS-42-75-6PB | 133 | 4.4 | Yes | Yes | 17.5 | 20.4 | -2.9 | 3B2B32559AC44E89A8654E67F30D7606 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.308% | 0.96692 | 6.358% | [5 empty] | Non-TXV | 3.308%
Stockton | CA | 95207-5419 |  | 2013-09-20 | 2013-09-20 15:41 | 2013-09-20 16:06 | GOODMAN - CKL42-1B | 115 | -10.8 | Yes | Yes | 20.4 | 18.8 | 1.6 | 12FCECECEC5848AA93E35C2C516554CE |  | R22 | Non-TXV |  | -9.391% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.391%
Los Banos | CA | 93635-5102 |  | 2013-10-21 | 2013-10-21 14:04 | 2013-10-21 14:05 | DAY & NIGHT - 777UNK | 85 | 2.9 | Yes | Yes | 22.5 | 21.5 | 1 | D52DA15145484B70A8619A14614AFC7D |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Stockton | CA | 95209-1643 |  | 2013-10-02 | 2013-10-02 09:59 | 2013-10-02 10:20 | YORK - H1RD036S06C | 145 | 10.6 | Yes | Yes | 21 | 18.7 | 2.3 | 16530149D63B48F8B0C557312C7533A7 |  | R22 | Non-TXV |  | 7.31% | 0.9269 | 14.05% | [5 empty] | Non-TXV | 7.31%
Orland | CA | 95963-8143 |  | 2013-09-16 | 2013-09-16 09:52 | 2013-09-16 10:08 | DAY & NIGHT - N4A336KB200 | 83 | 3.9 | Yes | Yes | 16.2 | 18.5 | -2.3 | 05C0B36D29464E25A7FE504B57950782 |  | R410A | TXV |  | 4.699% | 0.95301 | 9.03% | [5 empty] | TXV | 4.699%
Penn Valley | CA | 95946-9646 |  | 2013-09-30 | 2013-09-30 16:56 | 2013-09-30 16:56 | AMANA - ARCF36U01B | 126.1 | 0 | Yes | Yes | 24.9 | 19.3 | 5.6 | 85EFAA28CAC14BC8B42F0CC4349BB642 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1732 |  | 2013-09-27 | 2013-09-27 11:57 | 2013-09-27 12:20 | DAY & NIGHT - 589ANW0442080ACAF | 87 | 5.4 | Yes | Yes | 22 | 21.4 | 0.6 | 5C8029F0D364430D83ADFA47B32CE3DD | Add refrigerant: 2.6 oz | R22 | Non-TXV |  | 6.207% | 0.93793 | 11.93% | [5 empty] | Non-TXV | 6.207%
Oroville | CA | 95966-6033 |  | 2013-09-24 | 2013-09-24 11:06 | 2013-09-24 11:24 | YORK - BRCS0361BD | 49 | 3.1 | Yes | Yes | 17.2 | 20.2 | -3 | 4FBF87088A83479398908BC8563542D1 |  | R22 | Non-TXV |  | 6.327% | 0.93673 | 12.16% | [5 empty] | Non-TXV | 6.327%
Linden | CA | 95236-9626 |  | 2013-10-02 | 2013-10-02 15:36 | 2013-10-02 16:02 | HEIL - PGC024K060A | 58 | 6.2 | Yes | Yes | 24.9 | 20.9 | 4 | 1B1D96823A38458189BBFD4F4DA4815D |  | R22 | Non-TXV |  | 10.69% | 0.8931 | 20.54% | [5 empty] | Non-TXV | 10.69%
Stockton | CA | 95209-4275 |  | 2013-10-25 | 2013-10-25 15:50 | 2013-10-25 16:30 | CARRIER - 24ABA360A300 | 135 | -23.7 | Yes | Yes | 21.5 | 20.3 | 1.2 | 4346C922004D44D8ABE959B446B1F9ED |  | R410A | TXV |  | -17.56% | 1.1756 | 4.916% |  |  |  |  | TXV |  |  | -17.56%
Lathrop | CA | 95330-9672 |  | 2013-10-02 | 2013-10-02 12:29 | 2013-10-02 12:48 | BRYANT - 574DNWA48090NA | 105 | 7 | Yes | Yes | 19.5 | 17.5 | 2.1 | 0F04A16762C74EBAA965B5430785C4CF |  | R410A | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Reedley | CA | 93654-3656 |  | 2013-09-26 | 2013-09-26 18:42 | 2013-09-26 19:02 | UNITARY PRODUCTS GROUP - BRCS0361BD | 63 | 13.5 | Yes | Yes | 22.5 | 20.8 | 1.7 | 8A45AE69103F448FA34C753BE3D01B7C |  | R22 | Non-TXV |  | 21.43% | 0.78571 | 41.18% | [5 empty] | Non-TXV | 21.43%
Willows | CA | 95988-3338 |  | 2013-09-18 | 2013-09-18 10:27 | 2013-09-18 11:06 | LENNOX - 13ACD0036-230-01 | 111 | 7 | Yes | Yes | 18.7 | 20.9 | -2.2 | 63F90113767C46B5A5077DB23C65CDD5 |  | R22 | Non-TXV |  | 6.306% | 0.93694 | 12.12% | [5 empty] | Non-TXV | 6.306%
Fresno | CA | 93722-4225 |  | 2013-09-25 | 2013-09-25 14:22 | 2013-09-25 14:23 | CARRIER - 48XP036060301 | 149 | 5.3 | Yes | Yes | 27.7 | 22.1 | 5.6 | 8A474876736843ECA343477AD8CE451D |  | R410A | Non-TXV |  | 3.557% | 0.96443 | 6.836% | [5 empty] | Non-TXV | 3.557%
Stockton | CA | 95205-3037 |  | 2013-09-26 | 2013-09-26 08:54 | 2013-09-26 09:14 | OTHER - UNK | 96 | 11.2 | Yes | Yes | 19.3 | 17.7 | 1.6 | 0B5B3E85D5DB4308BA9F0AC65936AF51 |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Orange Cove | CA | 93646-9413 |  | 2013-10-04 | 2013-10-04 16:35 | 2013-10-04 16:55 | RHEEM - RRGG-07N43JKR | 109 | 7.5 | Yes | Yes | 25.5 | 20.7 | 4.9 | 5ACC349B11984412AD1973A1CDC08FE5 |  | R22 | Non-TXV |  | 6.881% | 0.93119 | 13.22% | [5 empty] | Non-TXV | 6.881%
Willows | CA | 95988-2931 |  | 2013-09-17 | 2013-09-17 09:47 | 2013-09-17 10:26 | YORK - D1NH036N05606A | 104 | 4.8 | Yes | Yes | 21.3 | 18.2 | 3.1 | 872B2C5A514D4AA5A476D566D1C4058F |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Fresno | CA | 93704-1406 |  | 2013-09-19 | 2013-09-19 12:35 | 2013-09-19 12:37 | CARRIER - 38TR036300 | 132 | 17.1 | Yes | Yes | 25 | 22.1 | 2.9 | E4A9889957824D0CA96AFBC17DB303E4 |  | R22 | Non-TXV |  | 12.95% | 0.87045 | 24.9% | [5 empty] | Non-TXV | 12.95%
Atwater | CA | 95301-4833 |  | 2013-09-24 | 2013-09-24 14:44 | 2013-09-24 14:46 | BDP - 561CJ024C | 69 | 10.5 | Yes | Yes | 25.9 | 23.6 | 2.3 | CC5A6CB5BCF54A2BBACD21FE781FAD4B |  | R22 | TXV |  | 15.22% | 0.84783 | 29.24% | [5 empty] | TXV | 15.22%
Merced | CA | 95348-1122 |  | 2013-10-02 | 2013-10-02 14:14 | 2013-10-02 14:16 | AMERICAN STANDARD - 2YCX3030A1064AA | 88 | 8.1 | Yes | Yes | 19.2 | 18.2 | 1 | 4D83967ABBF7413285724FA7A598672A |  | R22 | Non-TXV |  | 9.205% | 0.90795 | 17.69% | [5 empty] | Non-TXV | 9.205%
Stockton | CA | 95206-5622 |  | 2013-09-26 | 2013-09-26 11:21 | 2013-09-26 11:42 | AMANA - GSC130361DF | 120 | 5.2 | Yes | Yes | 20.3 | 17.7 | 2.6 | 827CA919FA6D437F9B1F4330763F3117 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Stockton | CA | 95206-1865 |  | 2013-09-20 | 2013-09-20 14:39 | 2013-09-22 13:11 | PAYNE - UNK | 120 | 3.9 | Yes | Yes | 19.7 | 20.4 | -0.7 | 6D2C69FF76E744249752EC8F67F73AE0 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Willows | CA | 95988-2708 |  | 2013-09-18 | 2013-09-18 10:53 | 2013-09-18 13:17 | AMERICAN STANDARD - YCY036G1M0AC | 129 | 4.3 | Yes | Yes | 16.5 | 18.9 | -2.4 | 18C5E5263251408E952AF3999F875A4B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Reedley | CA | 93654-3658 |  | 2013-09-30 | 2013-09-30 12:36 | 2013-09-30 13:05 | ICP - NAC048AKA4 | 108 | 3.2 | Yes | Yes | 18.5 | 20.3 | -1.8 | 3F068B3C4EB84EAAAEA7F1C501F04273 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Oroville | CA | 95965-4220 |  | 2013-09-24 | 2013-09-24 10:23 | 2013-09-24 11:03 | LENNOX - GR4017734GA-030K072X | 65 | 5.4 | Yes | Yes | 18.7 | 21.5 | -2.8 | ED4B2BD98636408E93A7D21883FFA7CF |  | R22 | Non-TXV |  | 8.308% | 0.91692 | 15.97% | [5 empty] | Non-TXV | 8.308%
Manteca | CA | 95336-4400 |  | 2013-09-23 | 2013-09-23 14:56 | 2013-09-23 15:18 | UNITARY PRODUCTS GROUP - AC048X1221A | 121 | 6.5 | Yes | Yes | 24.9 | 22.3 | 2.6 | 9E495AEE9D844AF9AD222B36874B6175 |  | R22 | TXV |  | 5.372% | 0.94628 | 10.32% | [5 empty] | TXV | 5.372%
Sanger | CA | 93657-9757 |  | 2013-10-01 | 2013-10-01 16:04 | 2013-10-01 16:49 | CARRIER - 38YK036300 | 147 | 9.4 | Yes | Yes | 24.5 | 20.2 | 4.4 | 2E394A3430ED4F69AA1D501369DA9DC1 |  | R22 | Non-TXV |  | 6.395% | 0.93605 | 12.29% | [5 empty] | Non-TXV | 6.395%
Oroville | CA | 95966-3829 |  | 2013-10-02 | 2013-10-02 10:43 | 2013-10-02 11:07 | OTHER - DRHS04818E | 217 | 6.5 | Yes | Yes | 23.5 | 19.1 | 4.4 | DCB2A2449B794AD7B22B077C95648FAA |  | R22 | Non-TXV |  | 2.995% | 0.97005 | 5.756% | [5 empty] | Non-TXV | 2.995%
Fresno | CA | 93727-3664 |  | 2013-09-25 | 2013-09-25 11:35 | 2013-09-25 12:13 | LENNOX - 10GCS036X-75-3PA | 58 | 7.4 | Yes | Yes | 23 | 20.3 | 2.7 | 597DE7BEB53249F6A2F8267C8D17FBB8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.76% | 0.87241 | 24.52% | [5 empty] | Non-TXV | 12.76%
Atwater | CA | 95301-4810 |  | 2013-09-24 | 2013-09-24 14:12 | 2013-09-24 14:13 | BDP - 598AN036 | 194 | 33.3 | Yes | Yes | 18 | 17.6 | 0.4 | 83E477B973D84B568723B07FD0EDD75B |  | R22 | Non-TXV |  | 17.16% | 0.82835 | 32.99% | [5 empty] | Non-TXV | 17.16%
Fresno | CA | 93727-3750 |  | 2013-09-27 | 2013-09-27 14:08 | 2013-09-27 14:30 | BRYANT - 574ANW036060NB | 130 | 5.9 | Yes | Yes | 26 | 20.4 | 5.6 | A1577191F6C8467AAF7F9BE82425B54F |  | R22 | Non-TXV |  | 4.538% | 0.95462 | 8.722% | [5 empty] | Non-TXV | 4.538%
Fresno | CA | 93705-1921 |  | 2013-10-04 | 2013-10-04 11:59 | 2013-10-04 12:01 | RHEEM - UNK | 56 | 7.3 | Yes | Yes | 26.8 | 20.9 | 5.9 | CD203EC311854752AE9DAA1793D64EE5 |  | R22 | Non-TXV |  | 13.04% | 0.86964 | 25.05% | [5 empty] | Non-TXV | 13.04%
Manteca | CA | 95336-5818 |  | 2013-09-27 | 2013-09-27 13:42 | 2013-09-27 14:15 | GE - BTD724A100A0 | 68 | 2 | Yes | Yes | 19.5 | 20.4 | -0.9 | FF990E883FD740BF81555612882FE31D |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95210-1202 |  | 2013-09-20 | 2013-09-20 10:07 | 2013-09-20 10:24 | BRYANT - 582ANW036060NBAF | 70 | -4.1 | Yes | Yes | 17.8 | 18.7 | -0.9 | 512C0FF851474BEB98FAA284914B6936 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Willows | CA | 95988-3018 |  | 2013-09-18 | 2013-09-18 09:44 | 2013-09-18 10:01 | LENNOX - 15GCSXAV-36-090X230-1A | 140 | 9.3 | Yes | Yes | 23.4 | 19.6 | 3.9 | 0A7185EC247949D8BBD7654A2F8BF3CD |  | R410A | Non-TXV |  | 6.643% | 0.93357 | 12.77% | [5 empty] | Non-TXV | 6.643%
Chico | CA | 95973-9138 |  | 2013-09-19 | 2013-09-19 16:44 | 2013-09-19 17:00 | RHEEM - RAMA-042JH2 | 95 | 3.8 | Yes | Yes | 20.5 | 21.5 | -1 | 19FAB4D0BE2746CE9308B5A21218AF95 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Orland | CA | 95963-9793 |  | 2013-09-23 | 2013-09-23 12:11 | 2013-09-23 12:56 | YORK - H2DB06S06A | 128 | 3.9 | Yes | Yes | 17.3 | 20.2 | -2.9 | 7AB8918EC9994C3F8C93D9FDF839D1C4 |  | R22 | Non-TXV |  | 3.047% | 0.96953 | 5.855% | [5 empty] | Non-TXV | 3.047%
Valley Springs | CA | 95252-0000 |  | 2013-09-26 | 2013-09-26 14:33 | 2013-09-26 14:49 | RHEEM - RRNA-B030JK08X | 65 | 3.6 | Yes | Yes | 23.8 | 20.3 | 3.5 | BD9D06D314964ECFB7B6F38DDF40C48F |  | R22 | Non-TXV |  | 5.538% | 0.94462 | 10.64% | [5 empty] | Non-TXV | 5.538%
Reedley | CA | 93654-2112 |  | 2013-09-26 | 2013-09-26 15:26 | 2013-09-26 15:46 | CARRIER - 48OL002-9 | 41 | 3.6 | Yes | Yes | 21.1 | 20.4 | 0.7 | 48A9748FCB594213A408E1D67BCAB2FE |  | R22 | Non-TXV |  | 8.78% | 0.9122 | 16.87% | [5 empty] | Non-TXV | 8.78%
Reedley | CA | 93654-2112 |  | 2013-09-26 | 2013-09-26 15:50 | 2013-09-26 16:37 | CARRIER - 38EZG042300 | 99 | 3.8 | Yes | Yes | 17.5 | 20.4 | -2.9 | 1832B761728A43DC974DB44457F322BE |  | R410A | TXV |  | 3.838% | 0.96162 | 7.377% | [5 empty] | TXV | 3.838%
Dos Palos | CA | 93620-9564 |  | 2013-09-23 | 2013-09-23 11:42 | 2013-09-23 11:44 | YORK - H2RD036S06B | 96 | 13.9 | Yes | Yes | 19.2 | 21 | -1.8 | 76744D5BEFDD4360BDB12DB7683CD32C |  | R22 | Non-TXV |  | 14.48% | 0.85521 | 27.83% | [5 empty] | Non-TXV | 14.48%
Manteca | CA | 95337-6887 |  | 2013-09-29 | 2013-09-29 12:39 | 2013-09-29 12:59 | TRANE - TTN036C100B3 | 117 | 6.1 | Yes | Yes | 24.3 | 20.4 | 3.9 | D8A816A5F4C644EB8B0F5993D07F6CC5 | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 5.214% | 0.94786 | 10.02% | [5 empty] | TXV | 5.214%
Stockton | CA | 95209-2505 |  | 2013-09-27 | 2013-09-27 15:10 | 2013-09-27 15:28 | GOODMAN - GSC130421AC | 137 | 4.3 | Yes | Yes | 18.5 | 20.6 | -2.1 | AA99F43D515D4897B901D334801858F9 |  | R22 | Non-TXV |  | 3.139% | 0.96861 | 6.032% | [5 empty] | Non-TXV | 3.139%
Tracy | CA | 95377-7923 |  | 2013-10-08 | 2013-10-08 09:40 | 2013-10-08 10:05 | YORK - H1RA042S06D | 84 | -7.9 | Yes | Yes | 21.6 | 20.2 | 1.5 | AC786D0A32F4423496AC8DF5F5C35D7E |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Chico | CA | 95926-4814 |  | 2013-09-26 | 2013-09-26 18:00 | 2013-09-26 18:15 | CARRIER - 38EN024300 | 55 | 5.5 | Yes | Yes | 19 | 21.8 | -2.8 | 2F597AFDB30B46338A01A8C6621332E3 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Dos Palos | CA | 93620-2715 |  | 2013-09-30 | 2013-09-30 16:37 | 2013-09-30 16:38 | OTHER - 80WE3001 | 85 | 9.6 | Yes | Yes | 25.3 | 20.4 | 4.9 | 652547C404E94F25AF15673C79B2536C |  | R22 | Non-TXV |  | 11.29% | 0.88706 | 21.7% | [5 empty] | Non-TXV | 11.29%
Merced | CA | 95341-5584 |  | 2013-10-09 | 2013-10-09 14:26 | 2013-10-09 14:28 | RUUD - 7777UNK | 80 | 2.5 | Yes | Yes | 23.7 | 19.9 | 3.8 | C88B946B9F9042109640C84C3E749322 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Reedley | CA | 93654-2070 |  | 2013-09-26 | 2013-09-26 14:15 | 2013-09-26 14:33 | RUUD - UACC-024JAS | 49 | 3.3 | Yes | Yes | 16.7 | 19.7 | -3 | D4C247DCD52B46268031E8E32D34E475 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.735% | 0.93265 | 12.94% | [5 empty] | Non-TXV | 6.735%
Willows | CA | 95988-3033 |  | 2013-09-27 | 2013-09-27 10:30 | 2013-09-27 10:49 | ICP - PGF330060K01 | 89 | 4.9 | Yes | Yes | 26.1 | 22.6 | 3.5 | 966037B3369B48BD8BDE5A569D83ED14 |  | R22 | Non-TXV |  | 5.506% | 0.94494 | 10.58% | [5 empty] | Non-TXV | 5.506%
Stockton | CA | 95210-2018 |  | 2013-10-09 | 2013-10-09 11:41 | 2013-10-09 12:04 | GE - BGT1A856R1D | 80 | 4.8 | Yes | Yes | 19.9 | 18.2 | 1.7 | C088157D0EAE4104B5B26F8089D62A38 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Los Banos | CA | 93635-9204 |  | 2013-09-20 | 2013-09-20 11:33 | 2013-09-20 11:34 | NORDYNE - JS3BC036KA | 82 | 7.9 | Yes | Yes | 20.4 | 19.3 | 1.1 | 4574ADEC9F1B4315870735B2529DCAC7 |  | R22 | Non-TXV |  | 9.634% | 0.90366 | 18.51% | [5 empty] | Non-TXV | 9.634%
Grass Valley | CA | 95945-5258 |  | 2013-09-24 | 2013-09-24 14:46 | 2013-09-24 14:46 | BRYANT - 574DNWA24060NA-- | 77 | 0 | Yes | Yes | 26.1 | 20.6 | 5.5 | CF649A05B9504E00A9976C4612763BF8 |  | R410A | TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-1634 |  | 2013-09-26 | 2013-09-26 12:25 | 2013-09-26 12:25 | ICP - PGC030K080E----- | 53 | 0 | Yes | Yes | 18.6 | 20.6 | -2 | 5A42A61E03574231B90324AB8D968869 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4315 |  | 2013-09-25 | 2013-09-25 13:01 | 2013-09-25 13:03 | YORK - D1GH036N06406B | 112 | 9.8 | Yes | Yes | 26.9 | 20.9 | 6 | 00B8FB61106844468F66203419A9A589 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Chico | CA | 95973-2023 |  | 2013-09-26 | 2013-09-26 11:30 | 2013-09-26 11:56 | AMERICAN STANDARD - YCZ050F1H0AE | 189 | 6.9 | Yes | Yes | 26.8 | 20.9 | 5.9 | 6029D6C9C3254A9FA0EE1B5DFE6CAA93 |  | R22 | TXV |  | 3.651% | 0.96349 | 7.016% | [5 empty] | TXV | 3.651%
Auburn | CA | 95602-8422 |  | 2013-09-19 | 2013-09-19 11:58 | 2013-09-19 12:16 | CARRIER - 38CKC042300 | 80 | 5.5 | Yes | Yes | 15 | 17.1 | -2.1 | E3DD2F7CB9954F6491364E7EDE627EDF |  | R22 | TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | TXV | 6.875%
Manteca | CA | 95336-9604 |  | 2013-10-03 | 2013-10-03 11:05 | 2013-10-03 11:25 | UNITARY PRODUCTS GROUP - BRCS0361BDG | 63 | 10.6 | Yes | Yes | 24.4 | 19.1 | 5.3 | 5355B20478144FC5811467386DD26F6D |  | R22 | Non-TXV |  | 16.83% | 0.83175 | 32.33% | [5 empty] | Non-TXV | 16.83%
Fresno | CA | 93727-3663 |  | 2013-09-25 | 2013-09-25 12:15 | 2013-09-25 12:33 | LENNOX - 12GSC042X-100-3PA | 133 | 44.6 | Yes | Yes | 18.7 | 21.5 | -2.8 | C7E32C9A164D4DAB9BC872D4BDDECA84 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 33.53% | 0.66466 | 64.44% | [5 empty] | Non-TXV | 33.53%
Fresno | CA | 93703-4388 |  | 2013-09-27 | 2013-09-27 12:02 | 2013-09-27 12:03 | BDP - 585EJ0240505 | 54 | 3.8 | Yes | Yes | 20.2 | 20.6 | -0.4 | 2A9D73B4B851426AB3DC8F8AAD39CAB3 |  | R22 | Non-TXV |  | 7.037% | 0.92963 | 13.52% | [5 empty] | Non-TXV | 7.037%
Stockton | CA | 95204-3616 |  | 2013-10-01 | 2013-10-01 12:34 | 2013-10-01 12:50 | AMERICAN STANDARD - YCX036F1MOAB | 120 | 11.2 | Yes | Yes | 23 | 18.3 | 4.7 | 291D7A61761C49E296ECF9863B7A1EE6 |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Atascadero | CA | 93422-5822 |  | 2013-10-08 | 2013-10-08 14:28 | 2013-10-08 14:45 | COLEMAN - BRCQ0361BB | 71 | -4.2 | Yes | Yes | 26 | 20.1 | 5.9 | F43D7388012240B8A3B7CFB86EC4F182 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Stockton | CA | 95210-1476 |  | 2013-09-19 | 2013-09-19 15:56 | 2013-09-19 16:05 | BRYANT - 574ANW0360909B-- | 114 | -9.4 | Yes | Yes | 23 | 18 | 5.1 | C2BE3F7FA18E44A7B2F50DC45CF42BE2 |  | R22 | Non-TXV |  | -8.246% | 1.0825 | 2.309% |  |  |  |  | Non-TXV |  |  | -8.246%
Madera | CA | 93637-8826 |  | 2013-10-08 | 2013-10-08 12:08 | 2013-10-08 12:10 | CARRIER - 48GX036060301 | 82 | 10.6 | Yes | Yes | 25.8 | 19.9 | 5.9 | E5C6409C2A9B4AD587D0E499475F460C |  | R22 | Non-TXV |  | 12.93% | 0.87073 | 24.84% | [5 empty] | Non-TXV | 12.93%
Auburn | CA | 95602-9387 |  | 2013-10-08 | 2013-10-08 13:52 | 2013-10-08 14:09 | OTHER - FS5BD-030KA | 99 | 3 | Yes | Yes | 22.9 | 20.7 | 2.2 | 94E2760B8FE349609495678D7EFA46D1 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Riverbank | CA | 95367-3088 |  | 2013-10-24 | 2013-10-24 15:51 | 2013-10-24 16:21 | CARRIER - 591ANX030000ABAA | 67 | 11.9 | Yes | Yes | 16.6 | 18.8 | -2.2 | BBE8FDDE91724246BC81DF94DE5E9593 |  | R22 | Non-TXV |  | 17.76% | 0.82239 | 34.13% | [5 empty] | Non-TXV | 17.76%
Stockton | CA | 95210-2607 |  | 2013-09-19 | 2013-09-19 14:22 | 2013-09-19 14:40 | OTHER - CA5530VKA1 | 77 | 7.6 | Yes | Yes | 17.5 | 17.8 | -0.3 | EE7213B3CAEF429585492A0176C89D95 |  | R22 | Non-TXV |  | 9.87% | 0.9013 | 18.97% | [5 empty] | Non-TXV | 9.87%
Oroville | CA | 95966-3925 |  | 2013-09-24 | 2013-09-24 13:47 | 2013-09-24 13:59 | ALLEGIANCE - TWNO36C100B4 | 135 | 4 | Yes | Yes | 15.2 | 17.5 | -2.3 | ACBC795179304F80B19FE8F0391464FB |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Tracy | CA | 95376-1404 |  | 2013-09-27 | 2013-09-27 11:48 | 2013-09-27 12:04 | RHEEM - RAFD042JBS | 79 | 2.6 | Yes | Yes | 20.4 | 17.5 | 3 | E847B710F6E8443E802B43A436ADE23E |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Templeton | CA | 93465-9094 |  | 2013-10-08 | 2013-10-08 11:37 | 2013-10-08 11:54 | BRYANT - 561CJ018-D | 54 | -3.2 | Yes | Yes | 18.3 | 19.5 | -1.2 | 3B2D25672FB148E59B72C6534253BA73 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Fresno | CA | 93722-3770 |  | 2013-10-14 | 2013-10-14 16:49 | 2013-10-14 17:41 | RHEEM - RRNA-B042JK08X | 104 | 5.1 | Yes | Yes | 26.3 | 20.6 | 5.7 | 1616E73380DE4762B46DE608CE7CC7F0 |  | R22 | Non-TXV |  | 4.904% | 0.95096 | 9.424% | [5 empty] | Non-TXV | 4.904%
Stockton | CA | 95210-1846 |  | 2013-10-16 | 2013-10-16 12:47 | 2013-10-16 13:05 | RUUD - UAKA-030JAZ | 66 | 2.6 | Yes | Yes | 21.2 | 18.7 | 2.5 | 6FC2BB0C1C1A4F0B9CF894F1A0BF815E |  | R22 | Non-TXV |  | 3.939% | 0.96061 | 7.571% | [5 empty] | Non-TXV | 3.939%
Fresno | CA | 93727-8116 |  | 2013-09-27 | 2013-09-27 13:17 | 2013-09-27 13:18 | CARRIER - UNK | 56 | 5.1 | Yes | Yes | 23.3 | 19.6 | 3.7 | 378D18A5AC5742C896FF8C98E6B1FA6A |  | R22 | Non-TXV |  | 9.107% | 0.90893 | 17.5% | [5 empty] | Non-TXV | 9.107%
Fresno | CA | 93727-3669 |  | 2013-09-25 | 2013-09-25 15:01 | 2013-09-25 16:15 | LENNOX - 10GCS042X-75-3PA | 73 | 4.4 | Yes | Yes | 25.5 | 20.2 | 5.4 | 8329CCD22EF24D4FA745004E5FA6E8A4 |  | R22 | Non-TXV |  | 6.027% | 0.93973 | 11.58% | [5 empty] | Non-TXV | 6.027%
Fresno | CA | 93726-3741 |  | 2013-10-03 | 2013-10-03 13:14 | 2013-10-03 13:15 | YORK - D1NA024N03606C | 54 | 2.8 | Yes | Yes | 23.1 | 20.4 | 2.7 | 508792BD24564E588C66655052D1C899 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Stockton | CA | 95210-1243 |  | 2013-09-20 | 2013-09-20 11:55 | 2013-09-20 12:14 | RUUD - UAKA-037JAZ | 79 | 2.6 | Yes | Yes | 20.2 | 18.2 | 2 | 8D9E80D16D2F45AB85DF4C71A410F7FE |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Stockton | CA | 95209-1532 |  | 2013-09-30 | 2013-09-30 12:04 | 2013-09-30 12:22 | OTHER - RCB36C2C | 80 | 6.7 | Yes | Yes | 18.4 | 19.1 | -0.7 | 8973F9FAC35E4B5E90CED0A3C7936273 |  | R22 | Non-TXV |  | 8.375% | 0.91625 | 16.09% | [5 empty] | Non-TXV | 8.375%
Chico | CA | 95973-0310 |  | 2013-09-25 | 2013-09-25 15:58 | 2013-09-25 16:19 | TEMPSTAR - PGF33060K01 | 89 | 3.2 | Yes | Yes | 21 | 21.3 | -0.3 | EC85B8E6A4144FD094AA467F14ED8EAA |  | R22 | TXV |  | 3.596% | 0.96404 | 6.91% | [5 empty] | TXV | 3.596%
Red Bluff | CA | 96080-2031 |  | 2013-09-20 | 2013-09-20 10:44 | 2013-09-20 11:09 | AMANA - SRCF42001F | 156 | 5.5 | Yes | Yes | 20.7 | 23.5 | -2.8 | 4391A77067CC44D098774EFE8F5B9BA1 |  | R22 | Non-TXV |  | 3.526% | 0.96474 | 6.776% | [5 empty] | Non-TXV | 3.526%
Orland | CA | 95963-2314 |  | 2013-09-23 | 2013-09-23 14:15 | 2013-09-23 14:56 | YORK - H4DH036S06A | 81 | 4.4 | Yes | Yes | 20 | 22.8 | -2.8 | 528D0766B64142DD8C3E864E4D4BA632 |  | R22 | Non-TXV |  | 5.432% | 0.94568 | 10.44% | [5 empty] | Non-TXV | 5.432%
Stockton | CA | 95210-4454 |  | 2013-09-30 | 2013-09-30 16:01 | 2013-09-30 16:32 | PAYNE - 591ANX030000ABAA | 66 | -6.2 | Yes | Yes | 24 | 18 | 6 | BDA18203DE674865A3AFF437E47CFEAF |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
Foresthill | CA | 95631-9745 |  | 2013-10-17 | 2013-10-17 12:47 | 2013-10-17 13:04 | RHEEM - RAKA-042JAZ | 79 | 2.4 | Yes | Yes | 18 | 20.9 | -2.9 | 9DBC3319F316466BB01A30F3F1CB666B |  | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Clovis | CA | 93612-1671 |  | 2013-09-24 | 2013-09-24 10:47 | 2013-09-24 11:14 | COLEMAN - 6283B901 | 74 | 18.6 | Yes | Yes | 19 | 20.7 | -1.7 | D306A4F97C38439B848AF8EFE75C5A02 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 25.14% | 0.74865 | 48.3% | [5 empty] | Non-TXV | 25.14%
Auburn | CA | 95602-8165 |  | 2013-09-20 | 2013-09-20 13:34 | 2013-09-20 13:34 | BARD - 36HP03 | 84 | 0 | Yes | Yes | 18.7 | 20.6 | -1.8 | 07D654563A154EC3B32CE66C0416C8BE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-4653 |  | 2013-09-24 | 2013-09-24 10:58 | 2013-09-24 11:28 | DAY & NIGHT - 5410J024 | 118 | 3.6 | Yes | Yes | 17 | 19.3 | -2.3 | 6005F8BD90984A5DA8E81797011A709E |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Fresno | CA | 93722-6129 |  | 2013-10-08 | 2013-10-08 21:32 | 2013-10-08 21:32 | HEIL - CA3036VKA1 | 94 | 15.6 | Yes | Yes | 19.6 | 21.1 | -1.5 | 84BBA4E9D52B4655AC89A5CB01F0C0ED | Add refrigerant: 15.6 oz | R22 | Non-TXV |  | 16.6% | 0.83404 | 31.89% | [5 empty] | Non-TXV | 16.6%
Merced | CA | 95340-1627 |  | 2013-10-09 | 2013-10-09 15:23 | 2013-10-09 15:24 | TRANE - 4YCY4048B112 | 128 | 4 | Yes | Yes | 24.7 | 19.9 | 4.8 | B68783FADFBA475C9C2C18FF552F86E4 |  | R410A | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93725-4017 |  | 2013-10-10 | 2013-10-10 11:12 | 2013-10-10 12:03 | CARRIER - 24ABA336A300 | 82 | 5 | Yes | Yes | 21.4 | 20.7 | 0.7 | CFBC56CE8A6642C19B449E36350F1DC9 |  | R410A | TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | TXV | 6.098%
Stockton | CA | 95209-1455 |  | 2013-09-23 | 2013-09-23 11:20 | 2013-09-23 11:38 | RHEEM - RACB-036JAS | 48 | 5 | Yes | Yes | 21.5 | 18.6 | 2.9 | A8AC2167475C41AC81F031CEBDB5B439 |  | R22 | Non-TXV |  | 10.42% | 0.89583 | 20.02% | [5 empty] | Non-TXV | 10.42%
Merced | CA | 95340-1411 |  | 2013-10-01 | 2013-10-01 09:09 | 2013-10-01 09:32 | GOODMAN - SSX160481BA | 138 | 4.3 | Yes | Yes | 21.4 | 18.8 | 2.6 | 9D9B9D1178C9466799DF0EED4D9D6555 |  | R410A | Non-TXV |  | 3.116% | 0.96884 | 5.988% | [5 empty] | Non-TXV | 3.116%
Fresno | CA | 93704-4074 |  | 2013-09-19 | 2013-09-19 13:22 | 2013-09-19 13:22 | YORK - F024N070C | 54 | 0 | Yes | Yes | 22 | 20.1 | 2 | E1CF1AB1B901496BB6322458C63BAF95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atascadero | CA | 93422-8866 |  | 2013-10-08 | 2013-10-08 10:10 | 2013-10-08 10:30 | PAYNE - PA10JA024-C | 64 | -3.8 | Yes | Yes | 22.1 | 19.9 | 2.2 | 1DBD27A817554631B8F6DA1FEB28F812 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Fresno | CA | 93722-3699 |  | 2013-09-25 | 2013-09-25 11:49 | 2013-09-25 11:50 | CARRIER - UNK | 64 | 7.7 | Yes | Yes | 21.3 | 15.9 | 5.4 | E3BBD56C322546B985A3CC55AAF9D3F7 |  | R22 | Non-TXV |  | 12.03% | 0.87969 | 23.12% | [5 empty] | Non-TXV | 12.03%
Rough & Ready | CA | 95975-9700 |  | 2013-10-02 | 2013-10-02 10:54 | 2013-10-02 10:54 | UNITARY PRODUCTS GROUP - DRCQ0361BE | 64 | 0 | Yes | Yes | 16.1 | 19.1 | -3 | 1B262499B53046ECB1407EB5D3B73511 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4464 |  | 2013-09-27 | 2013-09-27 13:31 | 2013-09-27 13:52 | BDP - 591ANX036000AAAA | 81 | 3.2 | Yes | Yes | 23.3 | 20.4 | 3 | D1ACD2CFD82D447CA96FC10BEE31D012 |  | R22 | Non-TXV |  | 3.951% | 0.96049 | 7.592% | [5 empty] | Non-TXV | 3.951%
Orland | CA | 95963-2130 |  | 2013-09-25 | 2013-09-25 10:52 | 2013-09-25 11:35 | TEMPSTAR - ACS030A2C1 | 75 | 3.8 | Yes | Yes | 17.9 | 20.8 | -2.9 | 69817081DC294ABC90B87D7740F1A2AB |  | R22 | Non-TXV |  | 5.067% | 0.94933 | 9.737% | [5 empty] | Non-TXV | 5.067%
Stockton | CA | 95206-6319 |  | 2013-09-26 | 2013-09-26 15:53 | 2013-09-26 16:10 | YORK - H2RA036104-A | 65 | 5.1 | Yes | Yes | 21.5 | 18.8 | 2.7 | 0923D4AE62234FB9846B19FF0D3E1A7D |  | R22 | Non-TXV |  | 7.846% | 0.92154 | 15.08% | [5 empty] | Non-TXV | 7.846%
Fresno | CA | 93705-5032 |  | 2013-09-25 | 2013-09-25 12:28 | 2013-09-25 12:30 | PAYNE - UNK | 64 | 6.6 | Yes | Yes | 19.9 | 17.6 | 2.3 | E0F561AC211D4F1E9D4D793B4626C763 |  | R22 | Non-TXV |  | 10.31% | 0.89687 | 19.82% | [5 empty] | Non-TXV | 10.31%
Fresno | CA | 93722-6112 |  | 2013-10-08 | 2013-10-08 14:03 | 2013-10-08 14:43 | BDP - 585EJW036075ABAF | 82 | 5.5 | Yes | Yes | 26 | 20.7 | 5.4 | DCDE98D09BF74C12959442CBAF2F8ED6 |  | R22 | Non-TXV |  | 6.707% | 0.93293 | 12.89% | [5 empty] | Non-TXV | 6.707%
Grass Valley | CA | 95949-9607 |  | 2013-09-24 | 2013-09-24 15:44 | 2013-09-24 15:44 | PAYNE - PA10JA048-A | 102 | 0 | Yes | Yes | 22.5 | 19.5 | 3 | F235BEF24E3247259DB23E91DDF784EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2473 |  | 2013-09-20 | 2013-09-20 14:11 | 2013-09-20 14:37 | DAY & NIGHT - UNK | 95 | 6.3 | Yes | Yes | 18.8 | 19.9 | -1.1 | 15DEE93921FF4BD58FDE92572B3D659C |  | R22 | Non-TXV |  | 6.632% | 0.93368 | 12.74% | [5 empty] | Non-TXV | 6.632%
Orland | CA | 95963-1844 |  | 2013-09-23 | 2013-09-23 16:08 | 2013-09-23 16:25 | DAY & NIGHT - N4A360AKC200 | 55 | 2 | Yes | Yes | 20.1 | 20.4 | -0.3 | 8890B05999274C2E8AA6FD9ACAE265A9 |  | R410A | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Orland | CA | 95963-1844 |  | 2013-09-23 | 2013-09-23 16:29 | 2013-09-23 16:47 | LENNOX - 10ACB24-9P | 64 | 6.2 | Yes | Yes | 20.2 | 21.8 | -1.6 | 25C82181BEEB4841844B7B1502B8D1B9 |  | R22 | Non-TXV |  | 9.688% | 0.90312 | 18.62% | [5 empty] | Non-TXV | 9.688%
Madera | CA | 93637-8821 |  | 2013-10-18 | 2013-10-18 12:56 | 2013-10-18 12:58 | CARRIER - 48GX036060301 | 82 | 8.2 | Yes | Yes | 20.2 | 19.9 | 0.3 | FE9227BD941344418E20609BF025D341 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93704-4502 |  | 2013-09-19 | 2013-09-19 10:14 | 2013-09-19 11:31 | CARRIER - 48SX-048100311AA | 88 | 17.8 | Yes | Yes | 18.7 | 20.4 | -1.7 | 41D4B06BB9AB45BF82455A2A83779058 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 20.23% | 0.79773 | 38.87% | [5 empty] | Non-TXV | 20.23%
Fowler | CA | 93625-2703 |  | 2013-09-19 | 2013-09-19 18:23 | 2013-09-19 18:28 | PAYNE - N/A | 90 | 12 | Yes | Yes | 16.8 | 18.8 | -2 | 1B5504C5A3304F9F9520A589FE3AFB06 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Fowler | CA | 93625-2703 |  | 2013-09-19 | 2013-09-19 18:45 | 2013-09-19 19:10 | CARRIER - 48GS-030060301 | 55 | 1.8 | Yes | Yes | 15.9 | 18.9 | -3 | E3487A673F0B4354BCDFC151EA19EB2A |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Stockton | CA | 95205-6638 |  | 2013-09-26 | 2013-09-26 10:33 | 2013-09-26 11:00 | OTHER - SCU10B30A | 65 | 4.8 | Yes | Yes | 24 | 18 | 6 | B904AD33B6C34927B48C1BDF8E5C7E6A |  | R22 | Non-TXV |  | 7.385% | 0.92615 | 14.19% | [5 empty] | Non-TXV | 7.385%
Orland | CA | 95963-9162 |  | 2013-09-25 | 2013-09-25 10:19 | 2013-09-25 10:47 | COLEMAN - 9636-661 | 83 | 7.4 | Yes | Yes | 25.7 | 19.9 | 5.8 | 164F810422874584AF8401D9DDA05C7D |  | R22 | Non-TXV |  | 8.916% | 0.91084 | 17.13% | [5 empty] | Non-TXV | 8.916%
Auburn | CA | 95602-8066 |  | 2013-10-07 | 2013-10-07 15:24 | 2013-10-07 16:38 | CARRIER - 38TH036330 | 85 | 2.5 | Yes | Yes | 20 | 20.9 | -0.9 | 662FC7526B56448CBF82BEA002AAB477 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Orland | CA | 95963-8120 |  | 2013-09-25 | 2013-09-25 11:36 | 2013-09-25 11:58 | DAY & NIGHT - NA | 76 | 6.6 | Yes | Yes | 24.9 | 22.2 | 2.7 | 30A7A7FCB7054130B7C79FA92BCF4247 |  | R22 | Non-TXV |  | 8.684% | 0.91316 | 16.69% | [5 empty] | Non-TXV | 8.684%
Fresno | CA | 93726-4607 |  | 2013-10-03 | 2013-10-03 11:26 | 2013-10-03 11:27 | RHEEM - RRKA-A036JK06X | 62 | 2.9 | Yes | Yes | 23.7 | 19.5 | 4.2 | 44CB5BDF76AD41EE82FEA45C0DAA55CC |  | R22 | Non-TXV |  | 4.677% | 0.95323 | 8.989% | [5 empty] | Non-TXV | 4.677%
Stockton | CA | 95210-2268 |  | 2013-10-01 | 2013-10-01 16:20 | 2013-10-01 16:44 | CARRIER - 38EN024300 | 56 | 7 | Yes | Yes | 27.1 | 21.2 | 6 | 2FF05280BABE43D891C7CE0B1838A560 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Orange Cove | CA | 93646-2264 |  | 2013-10-09 | 2013-10-09 18:17 | 2013-10-09 18:34 | BDP - 588ANW036080ACAF | 67 | 4.1 | Yes | Yes | 25 | 20.7 | 4.3 | E022958CFEBB4BEC94B4F865CFE85970 |  | R22 | Non-TXV |  | 6.119% | 0.93881 | 11.76% | [5 empty] | Non-TXV | 6.119%
Stockton | CA | 95204-2626 |  | 2013-09-24 | 2013-09-24 09:51 | 2013-09-24 10:08 | TRANE - TTR730A100A0 | 92 | 6.3 | Yes | Yes | 15 | 17.1 | -2.1 | 43505583623E4892B7EB8B9E63415296 |  | R22 | Non-TXV |  | 6.848% | 0.93152 | 13.16% | [5 empty] | Non-TXV | 6.848%
Fresno | CA | 93727-4117 |  | 2013-10-08 | 2013-10-08 18:04 | 2013-10-08 20:20 | YORK - D1NH048N09006C | 128 | 4.4 | Yes | Yes | 24.3 | 21.3 | 3 | 7827DEDC4C6A4AA488394DEA38E7042F |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Los Banos | CA | 93635-3851 |  | 2013-09-20 | 2013-09-20 11:01 | 2013-09-20 11:04 | TRANE - BWC036C100AO | 139 | 15.8 | Yes | Yes | 20.3 | 18.2 | 2.1 | 3529531128114479B27E381C40F337CA |  | R22 | Non-TXV |  | 11.37% | 0.88633 | 21.84% | [5 empty] | Non-TXV | 11.37%
Fresno | CA | 93703-1735 |  | 2013-09-24 | 2013-09-24 08:23 | 2013-09-24 08:25 | OTHER - UNK | 56 | 4.1 | Yes | Yes | 21.8 | 17.7 | 4.1 | CC8C68FD10F54BA88C89D786EE800482 |  | R22 | Non-TXV |  | 7.321% | 0.92679 | 14.07% | [5 empty] | Non-TXV | 7.321%
Lathrop | CA | 95330-8517 |  | 2013-10-02 | 2013-10-02 12:09 | 2013-10-02 12:26 | CARRIER - UNK | 111 | 4 | Yes | Yes | 20.7 | 18.8 | 1.9 | 581114ECDE3E40FBAD531727BB8EF163 |  | R410A | Non-TXV |  | 3.604% | 0.96396 | 6.925% | [5 empty] | Non-TXV | 3.604%
Willows | CA | 95988-3439 |  | 2013-09-27 | 2013-09-27 10:52 | 2013-09-27 11:00 | TRANE - YCX036F1M0AA | 66 | 7.6 | Yes | Yes | 23.9 | 22.2 | 1.7 | BA54F49EEDA94932A444AF04AA6D4767 |  | R22 | Non-TXV |  | 11.52% | 0.88485 | 22.13% | [5 empty] | Non-TXV | 11.52%
Kingsburg | CA | 93631-1108 |  | 2013-10-01 | 2013-10-01 18:10 | 2013-10-01 18:27 | AMERICAN STANDARD - YCC048F1H0BC | 128 | 8.4 | Yes | Yes | 21 | 20.4 | 0.6 | 14DE08C40C494C1BABBBEA5EED43EA8C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.562% | 0.93437 | 12.61% | [5 empty] | Non-TXV | 6.562%
Stockton | CA | 95204-2525 |  | 2013-09-27 | 2013-09-27 13:09 | 2013-09-27 13:43 | AMANA - PGD30C0702E | 74 | 11.8 | Yes | Yes | 25.7 | 20.3 | 5.5 | C725612A92B94B17A998534462589986 |  | R22 | TXV |  | 15.95% | 0.84054 | 30.64% | [5 empty] | TXV | 15.95%
Manteca | CA | 95337-6701 |  | 2013-09-19 | 2013-09-19 11:08 | 2013-09-19 11:33 | RUUD - UAPC-030JAZ | 120 | 3.5 | Yes | Yes | 22.1 | 19.1 | 3.1 | ACBA4BCA4EF54DF18A0841E0522FEB44 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Fresno | CA | 93722-6112 |  | 2013-10-31 | 2013-10-31 15:01 | 2013-10-31 15:02 | TRANE - 4YCY4036A1075AA | 108 | 3.3 | Yes | Yes | 22.9 | 20.3 | 2.6 | 1B5853567CD54F53B9D3570CE43D94D5 |  | R410A | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Willows | CA | 95988-2329 |  | 2013-10-10 | 2013-10-10 11:30 | 2013-10-10 12:00 | LENNOX - H529-060-1P | 131 | 6.6 | Yes | Yes | 27.3 | 21.4 | 6 | 9D4AE7B217134B73A9B37F3727613B07 |  | R22 | TXV |  | 5.038% | 0.94962 | 9.682% | [5 empty] | TXV | 5.038%
Stockton | CA | 95209-1544 |  | 2013-09-30 | 2013-09-30 10:33 | 2013-09-30 10:57 | RUUD - UAPC-048JAS | 288 | 35.9 | Yes | Yes | 19.3 | 18 | 1.3 | 38FC185744F84B419372E8BB8FB9424B |  | R22 | TXV |  | 12.47% | 0.87535 | 23.96% | [5 empty] | TXV | 12.47%
Stockton | CA | 95204-4156 |  | 2013-10-01 | 2013-10-01 13:26 | 2013-10-01 13:51 | AMANA - PGD30C0702G | 80 | 9.1 | Yes | Yes | 19 | 17.1 | 1.9 | 700DDCD59C3E4618BAA23D54AB9193A8 |  | R22 | TXV |  | 11.38% | 0.88625 | 21.86% | [5 empty] | TXV | 11.38%
Fresno | CA | 93727-8702 |  | 2013-09-27 | 2013-09-27 13:43 | 2013-09-27 13:45 | YORK - D1NA036N03606C | 67 | 5.3 | Yes | Yes | 24.3 | 19.3 | 5 | 14830BD1060847CA8DFB95B1CB8E6924 |  | R22 | Non-TXV |  | 7.91% | 0.9209 | 15.2% | [5 empty] | Non-TXV | 7.91%
Parlier | CA | 93648-2037 |  | 2013-09-30 | 2013-09-30 10:04 | 2013-09-30 10:47 | LENNOX - N/A | 120 | 5.7 | Yes | Yes | 17.9 | 20.7 | -2.8 | 4E6505421D9E4ADB920E9D018C4D02FA |  | R22 | Non-TXV |  | 4.75% | 0.9525 | 9.128% | [5 empty] | Non-TXV | 4.75%
Fresno | CA | 93722-7348 |  | 2013-10-03 | 2013-10-03 15:35 | 2013-10-03 15:36 | LENNOX - 12GCS030753PA | 85 | 11 | Yes | Yes | 23.9 | 19.3 | 4.6 | D14EF4F9BF7642B5BCA9948A6C0EECB0 |  | R22 | Non-TXV |  | 12.94% | 0.87059 | 24.87% | [5 empty] | Non-TXV | 12.94%
Fresno | CA | 93722-5629 |  | 2013-10-10 | 2013-10-10 18:08 | 2013-10-10 18:10 | GOODMAN - GP13480701AC | 145 | 5.3 | Yes | Yes | 24.5 | 20.4 | 4.1 | E5BDC4899F1647E4B3761E8925975777 |  | R22 | Non-TXV |  | 3.655% | 0.96345 | 7.024% | [5 empty] | Non-TXV | 3.655%
Fresno | CA | 93722-6012 |  | 2013-10-04 | 2013-10-04 10:01 | 2013-10-04 10:02 | OTHER - CA3042VKA1 | 99 | 4.2 | Yes | Yes | 23.1 | 18.2 | 4.9 | 4522E6080BDA42E7A1FAAEFB0092B5C4 |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Manteca | CA | 95337-6774 |  | 2013-10-08 | 2013-10-08 12:34 | 2013-10-08 12:40 | BRYANT - 563CN030-B | 99 | 8.3 | Yes | Yes | 24.2 | 20.4 | 3.8 | 38CEDB5184654614B2D1C9DD191BC9DC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.384% | 0.91616 | 16.11% | [5 empty] | Non-TXV | 8.384%
Manteca | CA | 95337-6774 |  | 2013-10-08 | 2013-10-08 12:58 | 2013-10-08 13:30 | BDP - 585HJ018040 | 61 | 1.9 | Yes | Yes | 23.4 | 20.6 | 2.9 | 90EFD35E9C204D87BE249EDA909118AC |  | R22 | Non-TXV |  | 3.115% | 0.96885 | 5.986% | [5 empty] | Non-TXV | 3.115%
Stockton | CA | 95212-1123 |  | 2013-09-20 | 2013-09-20 10:44 | 2013-09-20 11:04 | RUUD - UAKA-037JAZ | 79 | 7.1 | Yes | Yes | 24.4 | 19.3 | 5.1 | 3833BD9BE7D844A79EB162ADD5DAAA88 |  | R22 | Non-TXV |  | 8.987% | 0.91013 | 17.27% | [5 empty] | Non-TXV | 8.987%
Stockton | CA | 95210-3656 |  | 2013-09-20 | 2013-09-20 09:31 | 2013-09-20 09:47 | RHEEM - UNK | 80 | -4.7 | Yes | Yes | 15.5 | 18.5 | -3 | F6F90ACA25D6486AACD21EA4A9B68A2F |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Stockton | CA | 95210-6701 |  | 2013-09-25 | 2013-09-25 13:47 | 2013-09-25 14:05 | RUUD - UNK | 80 | 4 | Yes | Yes | 17.9 | 19.4 | -1.5 | 7AA9697863984205BB76F8C04FC9C628 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95212-2769 |  | 2013-09-20 | 2013-09-20 14:31 | 2013-09-20 14:51 | CARRIER - 24BA360A0030010 | 135 | 4.9 | Yes | Yes | 23.7 | 20.2 | 3.5 | 7079236A86BD4D21888BA6E19D588261 |  | R410A | TXV |  | 3.63% | 0.9637 | 6.975% | [5 empty] | TXV | 3.63%
Stockton | CA | 95210-3322 |  | 2013-09-20 | 2013-09-20 14:19 | 2013-09-20 14:37 | COLEMAN - BRCS0361BDG | 63 | -3.7 | Yes | Yes | 18.1 | 19.2 | -1.1 | FE15E10833FA424FA7DF4676B1A08F68 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Ione | CA | 95640-9608 |  | 2013-09-17 | 2013-09-17 12:36 | 2013-09-17 12:54 | DAY & NIGHT - 588ANW048100AEAG | 101 | 9 | Yes | Yes | 22.4 | 18.3 | 4.1 | 240FFB598C1F4859975DCFC4AD5FFAF5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.911% | 0.91089 | 17.12% | [5 empty] | Non-TXV | 8.911%
Stockton | CA | 95209-1865 |  | 2013-09-18 | 2013-09-18 13:13 | 2013-09-18 13:32 | LENNOX - UNK | 144 | 4.9 | Yes | Yes | 26.1 | 20.4 | 5.7 | 4B7F670293E243BE82A27FF7DC986883 |  | R22 | Non-TXV |  | 3.403% | 0.96597 | 6.539% | [5 empty] | Non-TXV | 3.403%
Stockton | CA | 95212-3407 |  | 2013-09-24 | 2013-09-24 10:14 | 2013-09-24 10:38 | YORK - H2RC036S06A | 83 | 3.5 | Yes | Yes | 19.5 | 17.5 | 2 | 3FF989C5887E430C903AD0B82217A30F |  | R22 | Non-TXV |  | 4.217% | 0.95783 | 8.104% | [5 empty] | Non-TXV | 4.217%
Tracy | CA | 95376-5331 |  | 2013-09-20 | 2013-09-20 15:25 | 2013-09-20 15:46 | BDP - 56CN036-A | 122 | -32.9 | Yes | Yes | 18.5 | 20.6 | -2.1 | 2CE212F3463A49FEA5F4C0413B058CA4 |  | R22 | Non-TXV |  | -26.97% | 1.2697 | 7.552% |  |  |  |  | Non-TXV |  |  | -26.97%
Manteca | CA | 95337-5461 |  | 2013-10-07 | 2013-10-07 11:40 | 2013-10-07 12:06 | AMANA - PGD48C0902E | 139 | 4.2 | Yes | Yes | 25.5 | 20.2 | 5.3 | 702E9C11167548959817E00EBB8841AD |  | R22 | Non-TXV |  | 3.022% | 0.96978 | 5.807% | [5 empty] | Non-TXV | 3.022%
Stockton | CA | 95206-1896 |  | 2013-09-26 | 2013-09-26 11:46 | 2013-09-26 12:10 | PAYNE - PA10JA36-A | 95 | 3.7 | Yes | Yes | 19.3 | 18.3 | 1 | 50ABEA9B116340BC99BCC5A9885D3CBB |  | R22 | Non-TXV |  | 3.895% | 0.96105 | 7.485% | [5 empty] | Non-TXV | 3.895%
Manteca | CA | 95336-5025 |  | 2013-09-24 | 2013-09-24 13:12 | 2013-09-24 13:58 | COLEMAN - GCGD48S41S3A | 73 | 4.1 | Yes | Yes | 21.7 | 19.3 | 2.4 | B2B1CA37FC794AB3A748C904D9389838 |  | R410A | TXV |  | 5.616% | 0.94384 | 10.79% | [5 empty] | TXV | 5.616%
Stockton | CA | 95203-1206 |  | 2013-09-25 | 2013-09-25 10:12 | 2013-09-25 10:32 | PAYNE - 585HJ036060 | 102 | -8.4 | Yes | Yes | 24.9 | 20.4 | 4.5 | 0C9ED94D7590434A8D17ED16783AB697 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Stockton | CA | 95219-2314 |  | 2013-09-23 | 2013-09-23 14:14 | 2013-09-23 14:19 | LENNOX - HS22-461V-3P | 85 | -5.5 | Yes | Yes | 25.2 | 20.6 | 4.6 | FB696F1262DF47BC82B2FC73FB319FBC |  | R22 | TXV |  | -6.471% | 1.0647 | 1.812% |  |  |  |  | TXV |  |  | -6.471%
Ione | CA | 95640-9611 |  | 2013-09-17 | 2013-09-17 13:21 | 2013-09-17 14:03 | PAYNE - PA13NA042-C | 103 | 8.5 | Yes | Yes | 24.6 | 19.6 | 5.1 | A9F0B073A15F41E08BA30C15C14BCDF2 |  | R410A | Non-TXV |  | 8.252% | 0.91748 | 15.86% | [5 empty] | Non-TXV | 8.252%
Stockton | CA | 95210-1638 |  | 2013-10-03 | 2013-10-03 14:00 | 2013-10-03 14:21 | DAY & NIGHT - UNK | 96 | 5.2 | Yes | Yes | 24.5 | 18.5 | 6 | 37F2AAA2D19C439F9EB76C88FFA6B382 |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Oakdale | CA | 95361-2697 |  | 2013-10-04 | 2013-10-04 11:12 | 2013-10-04 11:42 | BRYANT - 552AN036-E | 84 | 2.5 | Yes | Yes | 24.4 | 19.9 | 4.5 | 0184F1FAE3784A78A177E5B63ECB144D |  | R410A | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Stockton | CA | 95210-5131 |  | 2013-10-01 | 2013-10-01 15:41 | 2013-10-01 15:59 | RHEEM - RRFG-05E24JKR | 42 | 2.5 | Yes | Yes | 25.3 | 20.4 | 4.9 | 89FA61F2B591433C9B4A97D6532C035E |  | R22 | Non-TXV |  | 5.952% | 0.94048 | 11.44% | [5 empty] | Non-TXV | 5.952%
Tracy | CA | 95376-3104 |  | 2013-09-19 | 2013-09-19 10:26 | 2013-09-19 10:42 | WESTINGHOUSE - JE030AAA0N | 95 | 5.1 | Yes | Yes | 17.8 | 18.2 | -0.4 | 11991A1BB14746EC8A5AD5CAFAD04D3B |  | R22 | Non-TXV |  | 5.368% | 0.94632 | 10.32% | [5 empty] | Non-TXV | 5.368%
Escalon | CA | 95320-2047 |  | 2013-09-30 | 2013-09-30 10:07 | 2013-09-30 10:07 | HEIL - GPCM024K040D | 54 | 0 | Yes | Yes | 22.2 | 18.2 | 4 | BFEC9BCEE0424D8F8511B1175F10359E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3219 |  | 2013-09-25 | 2013-09-25 13:14 | 2013-09-25 13:37 | GE - UNK | 72 | -5.1 | Yes | Yes | 23.4 | 20.2 | 3.3 | D46DBF5733274702B6853B1BAFE58308 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Lathrop | CA | 95330-9340 |  | 2013-09-19 | 2013-09-19 09:40 | 2013-09-19 10:18 | RHEEM - RAMA-036JAS | 96 | 2.9 | Yes | Yes | 20 | 19.3 | 0.7 | D0A04253E6954D0BA6A56F1D48781657 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Stockton | CA | 95210-5687 |  | 2013-10-11 | 2013-10-11 15:41 | 2013-10-11 16:30 | PAYNE - 591ANX048000ACAA | 128 | 7.9 | Yes | Yes | 23.4 | 19.1 | 4.3 | 15EE586CA45F42A1AB4F3C1D18213BA3 |  | R22 | Non-TXV |  | 6.172% | 0.93828 | 11.86% | [5 empty] | Non-TXV | 6.172%
Stockton | CA | 95209-2002 |  | 2013-09-18 | 2013-09-18 12:30 | 2013-09-18 12:47 | GOODMAN - CLJ60-1C | 141 | 5.1 | Yes | Yes | 25.3 | 19.9 | 5.4 | A8F76928C61A4FEB9EBEEF7397C53CF2 |  | R22 | Non-TXV |  | 3.617% | 0.96383 | 6.951% | [5 empty] | Non-TXV | 3.617%
Stockton | CA | 95204-1412 |  | 2013-09-25 | 2013-09-25 12:22 | 2013-09-25 17:27 | BDP - 559B030PAC | 50 | 5.7 | Yes | Yes | 23.1 | 20 | 3.1 | BA2FDEFC95B24490A490EA092019D9C7 |  | R22 | Non-TXV |  | 11.4% | 0.886 | 21.91% | [5 empty] | Non-TXV | 11.4%
Manteca | CA | 95337-6806 |  | 2013-09-25 | 2013-09-25 13:40 | 2013-09-25 14:04 | TRANE - BTD724A1000C0 | 68 | 4.3 | Yes | Yes | 17.9 | 18.2 | -0.3 | E3A14636EF5D4718896C3CDEF2584ECA |  | R22 | Non-TXV |  | 6.324% | 0.93676 | 12.15% | [5 empty] | Non-TXV | 6.324%
Stockton | CA | 95207-5407 |  | 2013-09-26 | 2013-09-26 12:13 | 2013-09-26 12:30 | PAYNE - N2A348AKA300 | 118 | 11.4 | Yes | Yes | 20.5 | 18.2 | 2.3 | C28543456B75460E8A011FEBFA4BD619 |  | R22 | TXV |  | 9.661% | 0.90339 | 18.57% | [5 empty] | TXV | 9.661%
Riverbank | CA | 95367-3142 |  | 2013-10-01 | 2013-10-01 13:00 | 2013-10-01 13:23 | ICP - ACS024A2C1 | 62 | 1.9 | Yes | Yes | 23.5 | 20.2 | 3.3 | 8217D766B371434F856DBF57B7AD6DB6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Stockton | CA | 95210-6731 |  | 2013-09-25 | 2013-09-25 13:03 | 2013-09-25 13:25 | YORK - H1DE030506A | 80 | 5.5 | Yes | Yes | 21.5 | 20.8 | 0.7 | FFE24880120A43FE995D6A1B0EC1D19E |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Riverbank | CA | 95367-2888 |  | 2013-10-02 | 2013-10-02 12:31 | 2013-10-02 13:02 | CARRIER - 383H048320 | 137 | 27.2 | Yes | Yes | 17.8 | 17.7 | 0.1 | F7F4008A4A374E319150284CD632D134 |  | R22 | Non-TXV |  | 19.85% | 0.80146 | 38.16% | [5 empty] | Non-TXV | 19.85%
Stockton | CA | 95210-1953 |  | 2013-10-02 | 2013-10-02 11:08 | 2013-10-02 11:32 | YORK - H1DA030S06A | 83 | 2.6 | Yes | Yes | 17.2 | 18.9 | -1.7 | 8B39B50B45C241EFA07DEA5728246519 |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Stockton | CA | 95206-6244 |  | 2013-09-26 | 2013-09-26 14:31 | 2013-09-26 15:01 | GOODMAN - CJJ48-1AB | 115 | 11.3 | Yes | Yes | 21.5 | 18.5 | 3 | 06BBBC76370C4C55BFF5DE84C31E9BCC |  | R22 | Non-TXV |  | 9.826% | 0.90174 | 18.88% | [5 empty] | Non-TXV | 9.826%
Stockton | CA | 95204-3330 |  | 2013-09-30 | 2013-09-30 14:28 | 2013-09-30 14:49 | CARRIER - 48DL029-BB | 45 | 14.2 | Yes | Yes | 16.6 | 18.5 | -1.9 | D7D148635D5E46F78F398AC5790F909A |  | R22 | Non-TXV |  | 31.56% | 0.68444 | 60.64% | [5 empty] | Non-TXV | 31.56%
Tracy | CA | 95376-6700 |  | 2013-09-24 | 2013-09-24 10:51 | 2013-09-24 11:20 | RHEEM - UAMA048JAZ | 172 | 5.2 | Yes | Yes | 17.2 | 16.8 | 0.5 | 2D65818443DE4899BB963F492E53CD5B |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Lathrop | CA | 95330-8955 |  | 2013-09-19 | 2013-09-19 13:00 | 2013-09-19 13:28 | YORK - H1RA042S06G | 69 | 12.7 | Yes | Yes | 24.2 | 19 | 5.2 | CF5E6B027B6247E69F89D4D053F2DDBA |  | R22 | Non-TXV |  | 18.41% | 0.81594 | 35.37% | [5 empty] | Non-TXV | 18.41%
Lathrop | CA | 95330-8955 |  | 2013-09-19 | 2013-09-19 13:45 | 2013-09-19 14:12 | YORK - H1RA042S06G | 84 | 5.2 | Yes | Yes | 22.5 | 21.5 | 1 | 679EE0A193EE485F8937C2BAB9D1BBAA |  | R22 | Non-TXV |  | 6.19% | 0.9381 | 11.9% | [5 empty] | Non-TXV | 6.19%
Stockton | CA | 95206-5216 |  | 2013-09-25 | 2013-09-25 12:40 | 2013-09-25 13:04 | BRYANT - 56CN042-A | 135 | 4.1 | Yes | Yes | 20.4 | 15.3 | 5.1 | 79D1A8172A0240C4B19F108B8ACD9273 |  | R22 | Non-TXV |  | 3.037% | 0.96963 | 5.837% | [5 empty] | Non-TXV | 3.037%
Stockton | CA | 95204-3003 |  | 2013-09-23 | 2013-09-23 14:15 | 2013-09-23 14:36 | RHEEM - RAPA-061JAS | 262 | -8 | Yes | Yes | 25.1 | 19.3 | 5.8 | 323B84CC5B7445569E7CFF1F23699394 |  | R22 | Non-TXV |  | -3.053% | 1.0305 | 0.8551% |  |  |  |  | Non-TXV |  |  | -3.053%
Stockton | CA | 95209-1603 |  | 2013-11-14 | 2013-11-14 14:49 | 2013-11-14 14:49 | DAY & NIGHT - 567C042RCU | 74 | 0 | Yes | Yes | 22.1 | 18.3 | 3.8 | 03092914B2DC416E9303AEE86BB869BB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-8306 |  | 2013-09-23 | 2013-09-23 12:25 | 2013-09-23 12:43 | RUUD - RAHE048JAS | 114 | 3.7 | Yes | Yes | 20.3 | 19.1 | 1.3 | A6656B55CE03492FB8AF5DC67D9CA899 |  | R22 | Non-TXV |  | 3.246% | 0.96754 | 6.237% | [5 empty] | Non-TXV | 3.246%
Linden | CA | 95236-9585 |  | 2013-10-02 | 2013-10-02 16:05 | 2013-10-02 16:39 | GE - BGT4836R1D | 80 | 5.2 | Yes | Yes | 21 | 20.1 | 0.9 | 182A20D0BF5140E1B266765F1FBF1018 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Valley Springs | CA | 95252-9547 |  | 2013-09-26 | 2013-09-26 15:45 | 2013-09-26 16:09 | CARRIER - UNK | 80 | 3.2 | Yes | Yes | 27.2 | 21.3 | 5.9 | E21AAD113D7949A7BD36E38256CBE728 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Manteca | CA | 95336-3357 |  | 2013-09-20 | 2013-09-20 12:55 | 2013-09-20 13:19 | LENNOX - 13ACX-036-230-15 | 89 | 3.6 | Yes | Yes | 21.9 | 20.4 | 1.5 | BB977F9806E2402F85B5D4E9B43DD42D |  | R410A | Non-TXV |  | 4.045% | 0.95955 | 7.773% | [5 empty] | Non-TXV | 4.045%
Tracy | CA | 95376-2470 |  | 2013-10-11 | 2013-10-11 11:09 | 2013-10-11 11:41 | GOODMAN - CK24-1B | 71 | 8.6 | Yes | Yes | 17.4 | 20.2 | -2.8 | 9B49BE705596431FB187EB2A0B7748F4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.11% | 0.87887 | 23.28% | [5 empty] | Non-TXV | 12.11%
Stockton | CA | 95210-1250 |  | 2013-09-20 | 2013-09-20 12:15 | 2013-09-20 12:35 | AMANA - PGD36C0702E | 110 | -6.5 | Yes | Yes | 22.2 | 20.4 | 1.8 | 07CE33E923314F059E6B6537C5DFFA01 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Pioneer | CA | 95666-9617 |  | 2013-09-23 | 2013-09-23 11:32 | 2013-09-23 11:32 | TRANE - TWR030C100A5 | 81 | 0 | Yes | Yes | 21.1 | 20.1 | 1 | 63D7800EC1A047478735103DCD7BFC9D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3435 |  | 2013-09-23 | 2013-09-23 12:09 | 2013-09-23 12:32 | YORK - AC060X1222A | 136 | 8 | Yes | Yes | 24 | 18 | 6 | 68AE755687F545A486F551F97C0BA18D |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Manteca | CA | 95337-8968 |  | 2013-09-18 | 2013-09-18 10:53 | 2013-09-18 11:13 | BRYANT - 563CN060-F | 201 | 5.9 | Yes | Yes | 22.1 | 19.1 | 3.1 | 7660A933FD7D4215858049EA5827DFFF |  | R22 | Non-TXV |  | 2.935% | 0.97065 | 5.641% | [5 empty] | Non-TXV | 2.935%
Pine Grove | CA | 95665-9404 |  | 2013-09-23 | 2013-09-23 14:14 | 2013-09-23 14:14 | RHEEM - RAKA-048JAZ | 110 | 0 | Yes | Yes | 26.1 | 20.3 | 5.8 | FB29770533CF4E5995A81AF499D8FDCD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-6723 |  | 2013-09-25 | 2013-09-25 14:18 | 2013-09-25 14:42 | BRYANT - 562CJ036-C | 96 | 5.3 | Yes | Yes | 24.9 | 20.1 | 4.8 | DE5F50FCC7E5472597F839C66465625F |  | R22 | Non-TXV |  | 5.521% | 0.94479 | 10.61% | [5 empty] | Non-TXV | 5.521%
Tracy | CA | 95376-2703 |  | 2013-09-24 | 2013-09-24 14:01 | 2013-09-24 14:21 | PAYNE - PY1PJB04809ABAA | 81 | 2.5 | Yes | Yes | 21.5 | 19.1 | 2.4 | DF4AFA87D7A440FC8B6682169EB79230 |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Stockton | CA | 95210-3271 |  | 2013-09-23 | 2013-09-23 08:59 | 2013-09-23 09:18 | PAYNE - PA13NR030-J | 66 | -3.9 | Yes | Yes | 15.1 | 17.2 | -2.1 | B4A2A39E28624FB08F7F5B3E3A11E397 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Lodi | CA | 95240-9428 |  | 2013-10-11 | 2013-10-11 10:39 | 2013-10-11 10:58 | DAY & NIGHT - 561AJ060-C | 144 | 12.5 | Yes | Yes | 25.8 | 20.6 | 5.2 | 34BF34B2443546B6949EA0E18D88168E |  | R22 | Non-TXV |  | 8.681% | 0.91319 | 16.68% | [5 empty] | Non-TXV | 8.681%
Tracy | CA | 95376-2061 |  | 2013-09-19 | 2013-09-19 14:05 | 2013-09-19 14:21 | BRYANT - 2398E221233 | 110 | 4.7 | Yes | Yes | 19.2 | 19.6 | -0.4 | D3BB053496514180A5445569963D63F4 |  | R22 | Non-TXV |  | 4.273% | 0.95727 | 8.211% | [5 empty] | Non-TXV | 4.273%
Stockton | CA | 95204-2825 |  | 2013-09-24 | 2013-09-24 09:06 | 2013-09-24 09:06 | PAYNE - PA12NA04 | 136 | 0 | Yes | Yes | 23.4 | 18.2 | 5.2 | 58CB6D693DB842D3BB3502A16A633E7D |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1570 |  | 2013-09-18 | 2013-09-18 11:20 | 2013-09-18 11:37 | YORK - D1NP036N05606A | 108 | 4 | Yes | Yes | 21.8 | 18.8 | 3 | 1FFB9E2123084F3DAF6D615C811157AD |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Stockton | CA | 95207-3224 |  | 2013-09-18 | 2013-09-18 10:29 | 2013-09-18 10:52 | DAY & NIGHT - 569BJ024 | 72 | 11.6 | Yes | Yes | 18.9 | 18.3 | 0.6 | DA67EDBA99BE4FFF90904AE811B8F262 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Riverbank | CA | 95367-2737 |  | 2013-10-14 | 2013-10-14 14:34 | 2013-10-14 14:56 | YORK - AYA-F042N070C | 76 | 2.3 | Yes | Yes | 20.2 | 18.3 | 1.9 | 236296FBB90245EB96A77421A257FB4D |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95204-6206 |  | 2013-10-01 | 2013-10-01 11:45 | 2013-10-01 12:01 | LENNOX - GCS10-411-50-1P | 82 | 9.6 | Yes | Yes | 21 | 18.5 | 2.5 | DA1921D582B741E1A129E66EABDF2E7D |  | R22 | TXV |  | 11.71% | 0.88293 | 22.5% | [5 empty] | TXV | 11.71%
Tracy | CA | 95376-5292 |  | 2013-09-20 | 2013-09-20 10:17 | 2013-09-20 10:34 | BDP - 563CN024-A | 86 | 8.3 | Yes | Yes | 23.8 | 20.4 | 3.4 | F44B5059DCE648399197E4194E300478 |  | R22 | Non-TXV |  | 9.651% | 0.90349 | 18.55% | [5 empty] | Non-TXV | 9.651%
Manteca | CA | 95336-3344 |  | 2013-09-24 | 2013-09-24 11:43 | 2013-09-24 12:10 | YORK - H1DE036S06A | 84 | 10.6 | Yes | Yes | 21.8 | 19.9 | 1.9 | 998F8B6F184546658FDB050EE14FCECA |  | R22 | Non-TXV |  | 12.62% | 0.87381 | 24.25% | [5 empty] | Non-TXV | 12.62%
Valley Springs | CA | 95252-9075 |  | 2013-09-26 | 2013-09-26 10:55 | 2013-09-26 11:12 | CARRIER - 38CKC042356 | 81 | 5.6 | Yes | Yes | 23.5 | 20.4 | 3.1 | 9ABAC63D8DAE483A9FD13CBF76A57C28 |  | R22 | TXV |  | 6.914% | 0.93086 | 13.29% | [5 empty] | TXV | 6.914%
Valley Springs | CA | 95252-9529 |  | 2013-10-10 | 2013-10-10 10:03 | 2013-10-10 10:22 | OTHER - UNK | 64 | 5 | Yes | Yes | 26.4 | 20.4 | 6 | 47D6527ECC194CCFB6A184058768B07E |  | R22 | Non-TXV |  | 7.812% | 0.92188 | 15.01% | [5 empty] | Non-TXV | 7.812%
Tracy | CA | 95376-2605 |  | 2013-09-19 | 2013-09-19 13:38 | 2013-09-19 13:57 | YORK - D1NA048N06506C | 91 | 4.3 | Yes | Yes | 17.5 | 18.1 | -0.6 | B47F88E6C4A643B19612AD4DC08920AC |  | R22 | Non-TXV |  | 4.725% | 0.95275 | 9.081% | [5 empty] | Non-TXV | 4.725%
Stockton | CA | 95210-4601 |  | 2013-09-23 | 2013-09-23 13:46 | 2013-09-23 14:05 | CARRIER - 38EB024300 | 53 | 1.8 | Yes | Yes | 17.1 | 17.9 | -0.8 | 798807CE5FF548A5BA2E7A73EB3711B2 |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Stockton | CA | 95210-4495 |  | 2013-09-19 | 2013-09-19 12:51 | 2013-09-19 12:51 | PAYNE - 561AJ030-1A | 78 | 0 | Yes | Yes | 25.4 | 19.9 | 5.5 | 42A5060F18504FFE81A8170208CD844D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4498 |  | 2013-09-27 | 2013-09-27 12:58 | 2013-09-27 13:14 | CARRIER - 563AN030-A | 102 | 5.9 | Yes | Yes | 23.9 | 19.9 | 4 | 34B84161B88B44D69148AFAF967823B3 |  | R22 | TXV |  | 5.784% | 0.94216 | 11.12% | [5 empty] | TXV | 5.784%
Stockton | CA | 95207-7123 |  | 2013-09-20 | 2013-09-20 11:04 | 2013-09-20 11:24 | YORK - AC042X1221A | 85 | 3.2 | Yes | Yes | 22.7 | 19.6 | 3.1 | 60AF992C882B4D638FE7854516FEF948 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Valley Springs | CA | 95252-9572 |  | 2013-10-10 | 2013-10-10 12:29 | 2013-10-10 12:47 | DAY & NIGHT - UNK | 64 | 6 | Yes | Yes | 23.5 | 20 | 3.5 | FA4E180830764320AA20E5A739876010 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Stockton | CA | 95205-8413 |  | 2013-09-26 | 2013-09-26 09:53 | 2013-09-26 10:12 | DAY & NIGHT - GCGD02482182XB | 64 | -14.4 | Yes | Yes | 22.1 | 18.3 | 3.8 | D9E2C790AF284B73A51B52D73A5C201D |  | R22 | TXV |  | -22.5% | 1.225 | 6.301% |  |  |  |  | TXV |  |  | -22.5%
Stockton | CA | 95207-7535 |  | 2013-10-02 | 2013-10-02 11:18 | 2013-10-02 11:34 | YORK - H2RA036S06E | 63 | 6.7 | Yes | Yes | 20.4 | 17.6 | 2.8 | BA2B2D51B8394B1B98EF7D14020D2B0F |  | R22 | Non-TXV |  | 10.63% | 0.89365 | 20.44% | [5 empty] | Non-TXV | 10.63%
Manteca | CA | 95336-5025 |  | 2013-09-23 | 2013-09-23 16:57 | 2013-09-23 17:26 | AMANA - 9204281504 | 107 | 3.3 | Yes | Yes | 17.1 | 17.4 | -0.3 | CD523308A3E846659A22120E109395D1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Manteca | CA | 95336-5034 |  | 2013-10-03 | 2013-10-03 11:50 | 2013-10-03 12:13 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 3.8 | Yes | Yes | 28.3 | 22.8 | 5.5 | 124CE375D06349F4AA37E9BC3A48E908 |  | R22 | Non-TXV |  | 4.524% | 0.95476 | 8.694% | [5 empty] | Non-TXV | 4.524%
Oakdale | CA | 95361-9659 |  | 2013-09-17 | 2013-09-17 10:04 | 2013-09-17 10:30 | ICP - HAC248AC4 | 85 | 2.5 | Yes | Yes | 21.8 | 19.9 | 1.9 | 41E44A5E9AE24DB8ABF7D77556AED446 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95204-6209 |  | 2013-09-25 | 2013-09-25 11:45 | 2013-09-25 12:03 | BRYANT - 583BNW036060ABVS | 105 | 4.3 | Yes | Yes | 18.8 | 19.4 | -0.6 | 249B687349F644FFAFD6FB26A5B0EBFB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 4.095% | 0.95905 | 7.87% | [5 empty] | Non-TXV | 4.095%
Manteca | CA | 95337-8615 |  | 2013-09-18 | 2013-09-18 12:40 | 2013-09-18 13:09 | BRYANT - 113RNA042-A | 114 | 3.8 | Yes | Yes | 21.3 | 18.8 | 2.5 | 8C6DE2E0E7ED4AABB8058CD07D657133 |  | R22 | TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | TXV | 3.333%
Stockton | CA | 95206-6033 |  | 2013-09-17 | 2013-09-17 12:41 | 2013-09-17 13:21 | YORK - AC036X1021A | 63 | -5.9 | Yes | Yes | 23.5 | 20.5 | 3 | 154CCA31B892477EA61FD789D155C07E |  | R22 | Non-TXV |  | -9.365% | 1.0937 | 2.623% |  |  |  |  | Non-TXV |  |  | -9.365%
Stockton | CA | 95210-6746 |  | 2013-09-30 | 2013-09-30 14:56 | 2013-09-30 15:25 | BDP - 561CJ030-A | 65 | -6.1 | Yes | Yes | 19.8 | 17.7 | 2.1 | 89BC579F62634C57B5A87C2E3B885155 |  | R22 | Non-TXV |  | -9.385% | 1.0938 | 2.628% |  |  |  |  | Non-TXV |  |  | -9.385%
Stockton | CA | 95206-6129 |  | 2013-09-25 | 2013-09-25 15:29 | 2013-09-25 20:20 | YORK - YCJF3641S20 | 52 | 4.9 | Yes | Yes | 23.5 | 20.4 | 3.1 | ADDEAB07E1EF4B72843E84A4D179F340 |  | R22 | Non-TXV |  | 9.423% | 0.90577 | 18.11% | [5 empty] | Non-TXV | 9.423%
Stockton | CA | 95210-2108 |  | 2013-09-19 | 2013-09-19 09:20 | 2013-09-19 09:46 | OTHER - CA9636VKA3 | 156 | -12.8 | Yes | Yes | 18.6 | 18 | 0.6 | 8E2BC84798FD41C2BFEB394B3C6ED389 |  | R22 | Non-TXV |  | -8.205% | 1.0821 | 2.298% |  |  |  |  | Non-TXV |  |  | -8.205%
Stockton | CA | 95209-2530 |  | 2013-09-30 | 2013-09-30 09:39 | 2013-09-30 09:39 | AMANA - PGB36C0702E | 64 | 0 | Yes | Yes | 23.7 | 18.3 | 5.4 | 24AE6C4440BA4BEAB2EA88D9DA18B08E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-4638 |  | 2013-10-11 | 2013-10-11 14:51 | 2013-10-11 15:11 | PAYNE - PY1PNB036060ABAA | 68 | 4 | Yes | Yes | 19.4 | 20.3 | -0.9 | 2012026EDB364F30B5BE8C9C06F822F5 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Manteca | CA | 95336-9100 |  | 2013-09-19 | 2013-09-19 16:12 | 2013-09-19 16:30 | - TTD742A100A0 | 106 | 8 | Yes | Yes | 18.7 | 20.1 | -1.4 | A0BC984931544FF8BF5CFAF71809D95A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.547% | 0.92453 | 14.5% | [5 empty] | Non-TXV | 7.547%
Stockton | CA | 95206-3304 |  | 2013-09-30 | 2013-09-30 11:34 | 2013-09-30 11:56 | YORK - D1NA030N05606C | 76 | -5.4 | Yes | Yes | 19 | 18.3 | 0.7 | A946BAD7A26E418AAFD7DE6EAB51AE9C |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Manteca | CA | 95337-8713 |  | 2013-09-19 | 2013-09-19 12:07 | 2013-09-19 12:28 | BRYANT - 563CN048-F | 165 | 6 | Yes | Yes | 22.9 | 20.4 | 2.5 | 92DE068C408D4765AE7E04142A2DF07C |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Stockton | CA | 95204-2846 |  | 2013-09-30 | 2013-09-30 13:05 | 2013-09-30 13:21 | GE - BGTA836R1D | 80 | 17.8 | Yes | Yes | 20.6 | 19.8 | 0.8 | 030AA924C9534416BCCDF93A98861236 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.25% | 0.7775 | 42.76% | [5 empty] | Non-TXV | 22.25%
Tracy | CA | 95376-3034 |  | 2013-10-04 | 2013-10-04 10:24 | 2013-10-04 10:43 | YORK - H3RA060S06B | 98 | 3.5 | Yes | Yes | 19.4 | 20.1 | -0.7 | AEDBF8651A764892AEA2D73FBD22C254 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Stockton | CA | 95207-7554 |  | 2013-10-17 | 2013-10-17 16:42 | 2013-10-17 16:59 | YORK - BRCS0361CB | 72 | 10.2 | Yes | Yes | 21.5 | 18.5 | 3 | B9535BF8CE35430A8D3FBCAA2B001D5E |  | R22 | Non-TXV |  | 14.17% | 0.85833 | 27.23% | [5 empty] | Non-TXV | 14.17%
Manteca | CA | 95337-5224 |  | 2013-09-23 | 2013-09-23 14:16 | 2013-09-23 14:37 | UNITARY PRODUCTS GROUP - GCGD36S41S1A | 73 | 2.1 | Yes | Yes | 22.7 | 20.2 | 2.6 | 6BDC47178269400DAF047551C6D2B535 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Escalon | CA | 95320-2023 |  | 2013-10-11 | 2013-10-11 14:07 | 2013-10-11 14:27 | OTHER - 30JQ-105 | 56 | 3.8 | Yes | Yes | 22.6 | 19.3 | 3.3 | F81115241A5B4E8993028580D4FF5607 |  | R22 | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Stockton | CA | 95206-5116 |  | 2013-10-08 | 2013-10-08 16:14 | 2013-10-08 16:25 | RUUD - UAFD-0036JAS | 80 | 9 | Yes | Yes | 26.7 | 20.9 | 5.8 | F75356881CDC47FE8A3B9ECA468D922E |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Stockton | CA | 95206-5116 |  | 2013-10-08 | 2013-10-08 16:33 | 2013-10-08 16:55 | RUUD - UAFD-0031JAS | 64 | 9.7 | Yes | Yes | 22 | 21.5 | 0.5 | 1D344667713149959A5193153448B352 |  | R22 | Non-TXV |  | 15.16% | 0.84844 | 29.13% | [5 empty] | Non-TXV | 15.16%
Manteca | CA | 95336-5023 |  | 2013-09-23 | 2013-09-23 12:30 | 2013-09-23 13:01 | GE - CBD | 64 | -6 | Yes | Yes | 18.8 | 18.7 | 0.1 | 3ECC93188A0141A78AF4881753E5CAC4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Lathrop | CA | 95330-9167 |  | 2013-09-19 | 2013-09-19 14:28 | 2013-09-19 14:57 | GOODMAN - CKJ30-1A | 92 | 9.1 | Yes | Yes | 25.4 | 21.5 | 3.9 | 946EFA49691446989637CB60277AB3F2 |  | R22 | Non-TXV |  | 9.891% | 0.90109 | 19.01% | [5 empty] | Non-TXV | 9.891%
Stockton | CA | 95215-1119 |  | 2013-10-02 | 2013-10-02 13:45 | 2013-10-02 14:13 | YORK - CZB03611B | 100 | 10.5 | Yes | Yes | 19.1 | 19.8 | -0.7 | 98421ED81E494121B3167FCB29E4F842 |  | R410A | TXV |  | 10.5% | 0.895 | 20.18% | [5 empty] | TXV | 10.5%
Stockton | CA | 95210-1446 |  | 2013-10-02 | 2013-10-02 12:07 | 2013-10-02 12:29 | AMERICAN STANDARD - YCY030G1M0AD | 120 | 4 | Yes | Yes | 23.5 | 20.1 | 3.4 | EBFA2A86101D46458357B33ADA5BB9B9 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Manteca | CA | 95337-8230 |  | 2013-09-18 | 2013-09-18 11:40 | 2013-09-18 12:01 | BRYANT - 563CN036-D | 101 | 3.1 | Yes | Yes | 20.5 | 19.3 | 1.2 | BC2FF32F73AE4E698DE2893F121D2CD3 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Manteca | CA | 95337-8230 |  | 2013-09-18 | 2013-09-18 12:06 | 2013-09-18 12:11 | BRYANT - 563CN036-D | 101 | 3.1 | Yes | Yes | 21.7 | 19.1 | 2.7 | 7DA0D79E377948CC9E67DCDD3038FFBF |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Tracy | CA | 95376-5247 |  | 2013-09-19 | 2013-09-19 15:24 | 2013-09-20 08:36 | CARRIER - 38CKC060 | 140 | 5.6 | Yes | Yes | 19.3 | 18.5 | 0.8 | 16043D3C632D487DA2F70F7FD40A8F7F |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95205-6200 |  | 2013-09-26 | 2013-09-26 11:12 | 2013-09-26 11:31 | RHEEM - UNK | 96 | 9.5 | Yes | Yes | 23 | 18.5 | 4.5 | BF05ED2D77054953830F901C1DBC18B9 |  | R22 | Non-TXV |  | 9.896% | 0.90104 | 19.02% | [5 empty] | Non-TXV | 9.896%
Manteca | CA | 95337-8405 |  | 2013-10-22 | 2013-10-22 10:43 | 2013-10-22 11:03 | YORK - H4DE036S06A | 82 | 2.9 | Yes | Yes | 22.7 | 20.6 | 2.1 | 2EC3331867E14BC9988374A1939629B1 |  | R22 | Non-TXV |  | 3.537% | 0.96463 | 6.797% | [5 empty] | Non-TXV | 3.537%
Stockton | CA | 95215-8226 |  | 2013-09-26 | 2013-09-26 15:17 | 2013-09-26 15:34 | CARRIER - 38GC042310 | 86 | 2.5 | Yes | Yes | 23.9 | 19.9 | 4 | E24069936A534107824269AC332A1C9A |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Stockton | CA | 95206-6418 |  | 2013-09-19 | 2013-09-19 11:37 | 2013-09-19 11:56 | GOODMAN - CKL-49-1L | 112 | 19.5 | Yes | Yes | 24.4 | 21.2 | 3.3 | 506F23B0ACF24D8AA7A91CE168E1189E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.41% | 0.82589 | 33.46% | [5 empty] | Non-TXV | 17.41%
Stockton | CA | 95206-5426 |  | 2013-09-18 | 2013-09-18 10:55 | 2013-09-18 11:18 | OTHER - AA1AJ030-B | 66 | 7.3 | Yes | Yes | 25 | 19.7 | 5.3 | FC67338727D2488EA3A5809A97B45BDC |  | R22 | Non-TXV |  | 11.06% | 0.88939 | 21.26% | [5 empty] | Non-TXV | 11.06%
Manteca | CA | 95337-8402 |  | 2013-09-19 | 2013-09-19 09:23 | 2013-09-19 09:42 | YORK - H4DE03606A | 82 | 2.5 | Yes | Yes | 20.8 | 19.1 | 1.8 | 200BEB0277854C549E46580D8A9D89C6 |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Stockton | CA | 95206-5627 |  | 2013-09-17 | 2013-09-17 16:27 | 2013-09-17 16:58 | GOODMAN - CA5524VKD3 | 73 | 5 | Yes | Yes | 26 | 20.1 | 6 | C351CD60DBB94225A964636842A376E6 |  | R22 | Non-TXV |  | 6.849% | 0.93151 | 13.16% | [5 empty] | Non-TXV | 6.849%
Stockton | CA | 95219-1847 |  | 2013-09-23 | 2013-09-23 10:42 | 2013-09-23 10:49 | BDP - 561AJ036-A | 80 | -7.5 | Yes | Yes | 18 | 19 | -0.9 | 27A47854321943158C4C9EFEB0237689 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Stockton | CA | 95219-1847 |  | 2013-09-23 | 2013-09-23 11:17 | 2013-09-23 11:39 | GUARDIAN - GCGD30S21S2C | 80 | 12.6 | Yes | Yes | 15.5 | 18.2 | -2.7 | CB3E3213449C4E5DAB7AB25B2FD11DFE |  | R22 | Non-TXV |  | 15.75% | 0.8425 | 30.27% | [5 empty] | Non-TXV | 15.75%
Stockton | CA | 95212-2897 |  | 2013-09-23 | 2013-09-23 11:10 | 2013-09-23 11:29 | PAYNE - PA13NR060-H | 165 | 8 | Yes | Yes | 22.5 | 17.7 | 4.8 | 8E0558B0BF084CB6B526B86684FF79C0 |  | R22 | Non-TXV |  | 4.848% | 0.95152 | 9.318% | [5 empty] | Non-TXV | 4.848%
Lathrop | CA | 95330-9368 |  | 2013-10-02 | 2013-10-02 12:51 | 2013-10-02 13:14 | CARRIER - 38CKC048-371 | 108 | 5.1 | Yes | Yes | 19.5 | 18 | 1.5 | 25F7130C8AE94E0199867C7A9B7E7ACB |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Manteca | CA | 95337-8983 |  | 2013-09-25 | 2013-09-25 14:33 | 2013-09-25 14:54 | BRYANT - 563CNX036-D | 101 | 3.7 | Yes | Yes | 21.7 | 21 | 0.7 | 0B083BAFAD7847FC91D4531AEEF75974 |  | R22 | Non-TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | Non-TXV | 3.663%
Manteca | CA | 95337-8983 |  | 2013-09-25 | 2013-09-25 14:46 | 2013-09-25 15:02 | BRYANT - 563CNX036-D | 101 | 3.1 | Yes | Yes | 22 | 20.4 | 1.6 | B10A73B4162149F1ADF8BD16AC294D65 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Stockton | CA | 95204-2539 |  | 2013-10-01 | 2013-10-01 10:24 | 2013-10-01 10:24 | BRYANT - 574BNW036090NA-- | 149 | 0 | Yes | Yes | 20.5 | 17.1 | 3.4 | F33554E8FCB94F78984A5B50EE1DBFD3 |  | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-7917 |  | 2013-09-18 | 2013-09-18 14:01 | 2013-09-18 14:26 | UNITARY PRODUCTS GROUP - H2RC030S06A | 88 | 2.6 | Yes | Yes | 21.4 | 20.2 | 1.3 | 9D9F7B02752A4A3FA75BBB16FB6FBB0A |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Ripon | CA | 95366-2805 |  | 2013-09-25 | 2013-09-25 17:16 | 2013-09-25 18:00 | TRANE - TTR036D100A0 | 79 | 9.9 | Yes | Yes | 21.8 | 21.3 | 0.5 | 824656E21A3E40ADAA4D723C7DD633DB |  | R22 | Non-TXV |  | 12.53% | 0.87468 | 24.08% | [5 empty] | Non-TXV | 12.53%
Ripon | CA | 95366-2925 |  | 2013-10-23 | 2013-10-23 13:51 | 2013-10-23 14:09 | PAYNE - 591ANX042000ABAA | 112 | 3.3 | Yes | Yes | 23.3 | 18.7 | 4.6 | AC41AE28AE9D435EA8A970FBE72BD64D |  | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.662% | [5 empty] | Non-TXV | 2.946%
Stockton | CA | 95212-3511 |  | 2013-09-23 | 2013-09-23 15:57 | 2013-09-23 16:25 | YORK - AC048X1222A | 119 | 13.4 | Yes | Yes | 23.4 | 19.2 | 4.2 | A8109871463549CBA34CF6A9E92D1F1F |  | R22 | Non-TXV |  | 11.26% | 0.88739 | 21.64% | [5 empty] | Non-TXV | 11.26%
Manteca | CA | 95336-6230 |  | 2013-09-27 | 2013-09-27 15:27 | 2013-09-27 15:51 | - 585GJ036060 | 82 | 4.1 | Yes | Yes | 22.8 | 21 | 1.8 | 35FDE181AAAE4C6184FB3111C24A6FFA |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Pioneer | CA | 95666-9588 |  | 2013-09-23 | 2013-09-23 12:01 | 2013-09-23 12:01 | BRYANT - 582ANW036060AAAAF | 62 | 0 | Yes | Yes | 23.5 | 20.8 | 2.7 | AD20374B0D444C28AB16AB8AF1DF6AE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-5255 |  | 2013-09-20 | 2013-09-20 12:36 | 2013-09-20 12:54 | CONCORD - CCU10A36A-1 | 78 | 5.7 | Yes | Yes | 21.3 | 18.5 | 2.8 | 386013B26430435B822FC3812F1BBBF3 |  | R22 | Non-TXV |  | 7.308% | 0.92692 | 14.04% | [5 empty] | Non-TXV | 7.308%
Stockton | CA | 95215-1113 |  | 2013-09-27 | 2013-09-27 10:13 | 2013-09-27 10:31 | RHEEM - RAKA-030JAZ | 66 | -3.9 | Yes | Yes | 22 | 18.7 | 3.3 | 77F6C79C129F417EB252A91AA93CA846 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Stockton | CA | 95204-4838 |  | 2013-09-23 | 2013-09-23 12:22 | 2013-09-23 12:40 | BRYANT - 561CJ036-F | 71 | 5.6 | Yes | Yes | 17.8 | 18.1 | -0.3 | 559F7E00662941158900F7128339BBEB |  | R22 | Non-TXV |  | 7.887% | 0.92113 | 15.16% | [5 empty] | Non-TXV | 7.887%
Linden | CA | 95236-9702 |  | 2013-10-02 | 2013-10-02 16:40 | 2013-10-02 17:14 | DAY & NIGHT - UNK | 85 | 6.2 | Yes | Yes | 18.7 | 19.9 | -1.2 | 5A8DAAB7B67F4350AF3066CE788D6FE0 |  | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Manteca | CA | 95336-8226 |  | 2013-09-27 | 2013-09-27 14:17 | 2013-09-27 14:44 | YORK - D1NA060N11006A | 85 | 6.6 | Yes | Yes | 18.6 | 19.7 | -1.1 | 768AA1D7432844469010EED64AF0E6FA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | Non-TXV | 7.765%
Stockton | CA | 95207-2731 |  | 2013-09-18 | 2013-09-18 10:08 | 2013-09-18 10:12 | RHEEM - RACA-036ABQ | 35 | -8.5 | Yes | Yes | 17.1 | 17.9 | -0.8 | 4B2E13F91FDD471292BABB3B2AA80317 |  | R22 | Non-TXV |  | -24.29% | 1.2429 | 6.801% |  |  |  |  | Non-TXV |  |  | -24.29%
Stockton | CA | 95207-7773 |  | 2013-09-18 | 2013-09-18 08:23 | 2013-09-18 08:40 | PAYNE - 38CKB018320 | 69 | 6.9 | Yes | Yes | 20.4 | 18.7 | 1.7 | 274D36C3B9634B799132E0AF92DE4B44 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95210-3325 |  | 2013-09-20 | 2013-09-20 13:54 | 2013-09-20 14:14 | COLEMAN - UNK | 96 | 3.4 | Yes | Yes | 24.7 | 20.4 | 4.4 | 71E425267C2E4794AC18FD60C91049F1 |  | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Acampo | CA | 95220-9574 |  | 2013-10-01 | 2013-10-01 10:16 | 2013-10-01 10:42 | RHEEM - UNK | 85 | 9.8 | Yes | Yes | 18.8 | 19.9 | -1.1 | D2BD204DCC524DAFA5AE374EA855F732 |  | R22 | Non-TXV |  | 11.53% | 0.88471 | 22.16% | [5 empty] | Non-TXV | 11.53%
Stockton | CA | 95210-3663 |  | 2013-09-19 | 2013-09-19 12:05 | 2013-09-19 12:27 | TRANE - TTX048D100A0 | 139 | 6.2 | Yes | Yes | 23.8 | 18.2 | 5.6 | 845B8511BFED4EF3867DB862C12E9DDF |  | R22 | Non-TXV |  | 4.46% | 0.9554 | 8.572% | [5 empty] | Non-TXV | 4.46%
Acampo | CA | 95220-9205 |  | 2013-10-03 | 2013-10-03 10:07 | 2013-10-03 10:24 | BRYANT - 574ANW030060NB | 96 | 4.6 | Yes | Yes | 20.2 | 20.1 | 0.1 | 0A07B6AB55FB400AA7BBAFA0BAD6F878 |  | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Ripon | CA | 95366-3107 |  | 2013-09-26 | 2013-09-26 16:20 | 2013-09-26 16:43 | RUUD - CBD | 64 | 5.5 | Yes | Yes | 19.2 | 20.3 | -1.1 | 5C062D6803B64F58B81C45E136C30C64 |  | R22 | Non-TXV |  | 8.594% | 0.91406 | 16.52% | [5 empty] | Non-TXV | 8.594%
Stockton | CA | 95215-1123 |  | 2013-09-27 | 2013-09-27 09:33 | 2013-09-27 09:56 | AMERICAN STANDARD - YCG042A1LNA | 72 | -4.2 | Yes | Yes | 21.1 | 18 | 3.2 | 4377F9249B5F4C9B85DF579575FF7DC0 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95206-5622 |  | 2013-09-18 | 2013-09-18 10:01 | 2013-09-18 10:19 | GOODMAN - GSC130481BA | 102 | -6 | Yes | Yes | 19.3 | 19.3 | 0 | 61D4362531754B8689C64D9B70C34EAB |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95207-3101 |  | 2013-10-02 | 2013-10-02 10:20 | 2013-10-02 10:20 | GOODMAN - CKL36-1K | 84 | 0 | Yes | Yes | 21.2 | 18.2 | 3 | C688D72596324BE99306E063AA00E13C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ripon | CA | 95366-3110 |  | 2013-10-10 | 2013-10-10 10:19 | 2013-10-10 10:42 | BDP - 563AN030-A | 98 | 3.2 | Yes | Yes | 22.8 | 20.7 | 2.2 | 83DE5B13BFBB4BBFB47EA25BD0C90C3F |  | R22 | Non-TXV |  | 3.265% | 0.96735 | 6.275% | [5 empty] | Non-TXV | 3.265%
Stockton | CA | 95207-7532 |  | 2013-09-17 | 2013-09-17 11:09 | 2013-09-17 11:09 | RHEEM - A1-30B10 | 37 | 0 | Yes | Yes | 19.2 | 17.6 | 1.7 | 31B5C1481BF04AFBB667AB23BFDE356E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-8528 |  | 2013-09-19 | 2013-09-19 16:24 | 2013-09-19 16:43 | TRANE - TTN042C100A2 | 126 | 9.9 | Yes | Yes | 19.4 | 21 | -1.6 | EEBC8D7ECA414D6395AC6D7E22084B37 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Stockton | CA | 95207-4541 |  | 2013-09-17 | 2013-09-17 09:14 | 2013-09-17 09:18 | HEIL - HAC242AKA4 | 125 | -6.6 | Yes | Yes | 21.9 | 18.8 | 3.1 | D8D56D39FAA54B5295E64132BB04824A |  | R22 | TXV |  | -5.28% | 1.0528 | 1.479% |  |  |  |  | TXV |  |  | -5.28%
Ripon | CA | 95366-3201 |  | 2013-09-30 | 2013-09-30 14:40 | 2013-09-30 15:26 | DAY & NIGHT - 585GJ030040 | 58 | 4.9 | Yes | Yes | 18.6 | 17.5 | 1.1 | 3B203A5A5A83483193CD82FB45609B11 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.448% | 0.91552 | 16.24% | [5 empty] | Non-TXV | 8.448%
Stockton | CA | 95215-2045 |  | 2013-09-27 | 2013-09-27 11:30 | 2013-09-27 11:48 | GOODMAN - CL048-1B | 225 | -13.2 | Yes | Yes | 25.2 | 21.4 | 3.8 | 835B67FC2CAB4B328B823A565AB4678E |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Manteca | CA | 95337-5301 |  | 2013-09-25 | 2013-09-25 15:46 | 2013-09-25 16:15 | ICP - NAC036AKA1 | 87 | 7 | Yes | Yes | 22.2 | 19.8 | 2.4 | 546DBF46D3DF4F8E8C3E011D9A5CB387 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.046% | 0.91954 | 15.46% | [5 empty] | Non-TXV | 8.046%
Stockton | CA | 95212-2221 |  | 2013-09-24 | 2013-09-24 14:40 | 2013-09-24 15:00 | ICP - CA5548VKD2 | 134 | 16 | Yes | Yes | 23.9 | 20.1 | 3.9 | 8EA982347DC443E9BA281466F07CB5C6 |  | R22 | Non-TXV |  | 11.94% | 0.8806 | 22.95% | [5 empty] | Non-TXV | 11.94%
Stockton | CA | 95212-2752 |  | 2013-09-20 | 2013-09-20 16:32 | 2013-09-20 16:32 | CARRIER - UNK | 115 | 0 | Yes | Yes | 25.3 | 19.7 | 5.6 | A1DFAF494A9347088FF7B40CA80D81F7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-2769 |  | 2013-09-24 | 2013-09-24 13:57 | 2013-09-24 14:16 | CARRIER - 24BA3604300 | 135 | 4.9 | Yes | Yes | 24.9 | 19.4 | 5.5 | 1709E3A08FB041E2AAF08E8351AC78EC |  | R410A | TXV |  | 3.63% | 0.9637 | 6.975% | [5 empty] | TXV | 3.63%
Stockton | CA | 95215-7445 |  | 2013-09-26 | 2013-09-26 16:28 | 2013-09-26 16:44 | RHEEM - RRKA-A036JK06X | 62 | 1.9 | Yes | Yes | 23 | 19.7 | 3.4 | 4F685415087B400B92B392BA48A7284F |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Stockton | CA | 95204-2823 |  | 2013-09-23 | 2013-09-23 13:07 | 2013-09-23 13:30 | YORK - D1NA036N05606C | 67 | 7.3 | Yes | Yes | 16.3 | 17.9 | -1.6 | 5C994680D0584F38906B55B66C52DD3F |  | R22 | Non-TXV |  | 10.9% | 0.89104 | 20.94% | [5 empty] | Non-TXV | 10.9%
Lockeford | CA | 95237-9620 |  | 2013-09-17 | 2013-09-17 14:57 | 2013-09-17 15:29 | BDP - 561CCJ036-C | 71 | 10.1 | Yes | Yes | 20.3 | 19.9 | 0.4 | 8C0FA2EFAA64415DA4F9BC4F0020A8F2 |  | R22 | Non-TXV |  | 14.23% | 0.85775 | 27.34% | [5 empty] | Non-TXV | 14.23%
Ripon | CA | 95366-3358 |  | 2013-10-03 | 2013-10-03 16:34 | 2013-10-03 16:54 | TRANE - TTR048C100A2 | 114 | 26.1 | Yes | Yes | 28 | 22.4 | 5.6 | 17164437D8454A8CB1B1E989C7694E49 |  | R22 | Non-TXV |  | 22.89% | 0.77105 | 44% | [5 empty] | Non-TXV | 22.89%
Stockton | CA | 95210-6772 |  | 2013-09-25 | 2013-09-25 14:22 | 2013-09-25 14:40 | YORK - H1RA042S06D | 84 | -4.9 | Yes | Yes | 26.7 | 20.8 | 5.9 | 3C765C16007A4507AB8FE87FEE01B9DD |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95210-1942 |  | 2013-09-19 | 2013-09-19 10:05 | 2013-09-19 10:23 | HEIL - UNK | 96 | 6.9 | Yes | Yes | 21.6 | 18.8 | 2.8 | F42570EE33DF4B589B091CE1DB1E1946 |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Valley Springs | CA | 95252-9057 |  | 2013-10-10 | 2013-10-10 10:46 | 2013-10-10 11:05 | RUUD - URGG-05E30JKR | 46 | 2.7 | Yes | Yes | 26.4 | 20.4 | 6 | 860867522C154947918F1A3DDE4F8386 |  | R22 | Non-TXV |  | 5.87% | 0.9413 | 11.28% | [5 empty] | Non-TXV | 5.87%
Stockton | CA | 95212-3819 |  | 2013-09-24 | 2013-09-24 10:58 | 2013-09-24 11:24 | CARRIER - 38CKC036350 | 70 | 2.6 | Yes | Yes | 17.6 | 18.8 | -1.2 | 5D5320FE4E4C41A38C494C6AED089DE2 |  | R22 | TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | TXV | 3.714%
Lathrop | CA | 95330-8818 |  | 2013-09-18 | 2013-09-18 13:47 | 2013-09-18 14:03 | CARRIER - 38BRC048-371 | 142 | 5.2 | Yes | Yes | 21.2 | 20.4 | 0.8 | 3F389F3105AB446BA78869F419707CF4 |  | R22 | Non-TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | Non-TXV | 3.662%
Jackson | CA | 95642-9705 |  | 2013-09-17 | 2013-09-17 08:38 | 2013-09-17 08:38 | UNITARY PRODUCTS GROUP - BRCS0361BD | 63 | 0 | Yes | Yes | 21 | 20.6 | 0.4 | 27A60A7706C448AC861FFB53CADAA7FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sonora | CA | 95370-9150 |  | 2013-10-03 | 2013-10-03 12:36 | 2013-10-03 13:08 | YORK - UNK | 85 | 8 | Yes | Yes | 19.8 | 17.7 | 2.1 | 2DB88040436B4CFDA925BBF33CEE3E91 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Stockton | CA | 95207-5241 |  | 2013-09-20 | 2013-09-20 14:56 | 2013-09-20 15:14 | YORK - H2RD048S06B | 134 | 7.1 | Yes | Yes | 25 | 19.8 | 5.2 | A1D334D6F6B94770ADDA59301CBC64A8 |  | R22 | Non-TXV |  | 5.299% | 0.94701 | 10.18% | [5 empty] | Non-TXV | 5.299%
Lockeford | CA | 95237-9653 |  | 2013-09-17 | 2013-09-17 15:24 | 2013-09-17 16:10 | RHEEM - RAFD-036JAS | 80 | 6.8 | Yes | Yes | 26 | 20.2 | 5.9 | 811D4A4813634587AEC810667E5AB858 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Copperopolis | CA | 95228-0000 |  | 2013-10-03 | 2013-10-03 16:55 | 2013-10-03 17:44 | COLEMAN - ERCQ0361BBA | 83 | 4.5 | Yes | Yes | 19.7 | 21.4 | -1.7 | AA453267EF4D4CE7885EEC7CCFFCDCC7 |  | R22 | TXV |  | 5.422% | 0.94578 | 10.42% | [5 empty] | TXV | 5.422%
Stockton | CA | 95205-2634 |  | 2013-09-24 | 2013-09-24 12:34 | 2013-09-24 12:45 | TRANE - 2TTB0036A1000A | 76 | 3.7 | Yes | Yes | 21.7 | 20 | 1.8 | 74EA6A2EF8774EE192D6F819C5A508C7 |  | R22 | TXV |  | 4.868% | 0.95132 | 9.356% | [5 empty] | TXV | 4.868%
Manteca | CA | 95337-6834 |  | 2013-09-18 | 2013-09-18 15:02 | 2013-09-18 15:25 | TRANE - TTD730B100A0 | 69 | 6.7 | Yes | Yes | 25.2 | 22.1 | 3.1 | AA3865BBDE7B48AA9C4C840412A5B384 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.71% | 0.9029 | 18.66% | [5 empty] | Non-TXV | 9.71%
Stockton | CA | 95205-2698 |  | 2013-09-27 | 2013-09-27 10:19 | 2013-09-27 10:36 | TRANE - 4TTB3036A1000AA | 103 | 5.5 | Yes | Yes | 24 | 18.6 | 5.5 | 02A2119164824DDE87B644D6FFA34E38 |  | R410A | Non-TXV |  | 5.34% | 0.9466 | 10.26% | [5 empty] | Non-TXV | 5.34%
Tracy | CA | 95376-2135 |  | 2013-09-19 | 2013-09-19 09:54 | 2013-09-19 10:11 | YORK - HR1E030S06Q | 158 | 5.2 | Yes | Yes | 19.4 | 18.2 | 1.2 | D7CB49D5F0294B80A8E4467FD04A5315 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Ripon | CA | 95366-3220 |  | 2013-09-30 | 2013-09-30 14:12 | 2013-09-30 14:39 | DAY & NIGHT - 585GJ024040 | 54 | 1.6 | Yes | Yes | 20.4 | 19.2 | 1.2 | 6C95307440CE4106B89B998DF79CF681 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95205-3514 |  | 2013-09-24 | 2013-09-24 14:42 | 2013-09-24 15:01 | HEIL - NAC036AKC3 | 94 | 4.1 | Yes | Yes | 25.5 | 20.1 | 5.4 | 5CDF233CE8784613B9770CD1504D2591 |  | R22 | Non-TXV |  | 4.362% | 0.95638 | 8.382% | [5 empty] | Non-TXV | 4.362%
Lockeford | CA | 95237-9705 |  | 2013-10-11 | 2013-10-11 10:00 | 2013-10-11 10:19 | PAYNE - PA10JA048-C | 96 | 5.2 | Yes | Yes | 24.6 | 19.5 | 5.1 | EC10DB4BCBA0456AA0D7785872897DF4 |  | R22 | TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | TXV | 5.417%
Oakdale | CA | 95361-3247 |  | 2013-09-17 | 2013-09-17 15:49 | 2013-09-17 16:08 | RHEEM - RRPL-BO30JK06X | 77 | 3.8 | Yes | Yes | 23.2 | 20.9 | 2.3 | 7D30B21A898D4ED7BC0C572D710A0605 |  | R410A | Non-TXV |  | 4.935% | 0.95065 | 9.484% | [5 empty] | Non-TXV | 4.935%
Stockton | CA | 95219-7137 |  | 2013-11-02 | 2013-11-02 13:17 | 2013-11-02 13:17 | PAYNE - 38CKC048360 | 109 | 0 | Yes | Yes | 18.3 | 20 | -1.7 | 5D70E6C260D54F4BA04049EC83192069 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-2135 |  | 2013-09-20 | 2013-09-20 10:57 | 2013-09-20 10:57 | YORK - H1DE030S06B | 80 | 0 | Yes | Yes | 22.4 | 19.9 | 2.5 | 66E64A94895E4E8D9D0C75ADB18171A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-7913 |  | 2013-09-23 | 2013-09-23 11:54 | 2013-09-23 12:13 | BRYANT - 561CJ036-A | 90 | 3.3 | Yes | Yes | 19.2 | 18.8 | 0.4 | 20ECFC91CD114BE89D5EC7A9FCE7A341 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Tracy | CA | 95376-5438 |  | 2013-10-04 | 2013-10-04 11:04 | 2013-10-04 11:25 | RHEEM - RAFD-036JAS | 80 | 3.4 | Yes | Yes | 25.1 | 20.6 | 4.5 | DE95D6F0BB09412997D2D322E744227D |  | R22 | Non-TXV |  | 4.25% | 0.9575 | 8.168% | [5 empty] | Non-TXV | 4.25%
Stockton | CA | 95206-6439 |  | 2013-09-18 | 2013-09-18 08:27 | 2013-09-18 08:45 | GOODMAN - UNK | 84 | 12.1 | Yes | Yes | 17.2 | 19.9 | -2.7 | B8EBC57F15F649AFA04E1B5787D7DE2F |  | R22 | Non-TXV |  | 14.4% | 0.85595 | 27.68% | [5 empty] | Non-TXV | 14.4%
Manteca | CA | 95336-9134 |  | 2013-09-19 | 2013-09-19 14:58 | 2013-09-19 15:17 | BDP - 561CJ042-A | 80 | 2.7 | Yes | Yes | 19.9 | 20.9 | -1 | 8FDFDCEB2BE14CE1906B5C7DAAA2DD4D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Manteca | CA | 95337-8310 |  | 2013-09-18 | 2013-09-18 15:48 | 2013-09-18 16:08 | BDP - 563CN036-A | 113 | 19.5 | Yes | Yes | 21.1 | 21 | 0.1 | 1D8668F8703349A688BFE01855B9298B |  | R22 | Non-TXV |  | 17.26% | 0.82743 | 33.16% | [5 empty] | Non-TXV | 17.26%
Sonora | CA | 95370-8999 |  | 2013-10-14 | 2013-10-14 14:01 | 2013-10-14 14:09 | GE - TA936H1F | 101 | 23.1 | Yes | Yes | 25.7 | 20.9 | 4.8 | AA81C2B3CE2D47EA91FAD0A492190FCE |  | R22 | Non-TXV |  | 22.87% | 0.77129 | 43.95% | [5 empty] | Non-TXV | 22.87%
Valley Springs | CA | 95252-9138 |  | 2013-09-26 | 2013-09-26 11:29 | 2013-09-26 11:45 | GOODMAN - PGB030075-1 | 56 | 2.5 | Yes | Yes | 26.6 | 20.6 | 6 | 1015CCF83BE643049FA6381DEB89FF34 |  | R22 | Non-TXV |  | 4.464% | 0.95536 | 8.579% | [5 empty] | Non-TXV | 4.464%
Tracy | CA | 95376-2737 |  | 2013-09-24 | 2013-09-24 15:47 | 2013-09-24 19:37 | GOODMAN - UNK | 110 | 3.7 | Yes | Yes | 16.4 | 19.1 | -2.7 | D17ACCA4AAB948CFA57C4032EA840C49 |  | R22 | Non-TXV |  | 3.364% | 0.96636 | 6.464% | [5 empty] | Non-TXV | 3.364%
Riverbank | CA | 95367-3150 |  | 2013-10-01 | 2013-10-01 13:28 | 2013-10-01 13:47 | BDP - 561CJ030-B | 69 | 10 | Yes | Yes | 21.5 | 19.9 | 1.6 | BEA9614C23A04F089043357E23FACD83 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.49% | 0.85507 | 27.85% | [5 empty] | Non-TXV | 14.49%
Stockton | CA | 95209-4220 |  | 2013-09-25 | 2013-09-25 12:11 | 2013-09-25 12:35 | YORK - AC060X1223A | 147 | -8.6 | Yes | Yes | 21 | 19.9 | 1.1 | D586587B6AA84E22AA4D5787003E38AB |  | R22 | Non-TXV |  | -5.85% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.85%
Stockton | CA | 95206-5908 |  | 2013-09-17 | 2013-09-17 14:35 | 2013-09-17 14:52 | GOODMAN - CLJ42-1A | 99 | 3 | Yes | Yes | 19.6 | 19.5 | 0.1 | 8F1C48170CDE4BE9913F19C33A6641DE |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Stockton | CA | 95205-5742 |  | 2013-09-25 | 2013-09-25 11:20 | 2013-09-25 11:20 | LENNOX - HS22-311V-3P | 85 | 0 | Yes | Yes | 15.5 | 17.6 | -2.1 | E25F183652604956873A6CE81AB2253F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3350 |  | 2013-09-17 | 2013-09-17 11:48 | 2013-09-17 12:19 | DAY & NIGHT - 585HJ024040 | 68 | 8.2 | Yes | Yes | 23 | 19.9 | 3.1 | DABF813EE96A45B2A73D1AEA8D5011F8 |  | R22 | Non-TXV |  | 12.06% | 0.87941 | 23.17% | [5 empty] | Non-TXV | 12.06%
Oakdale | CA | 95361-2773 |  | 2013-10-18 | 2013-10-18 13:15 | 2013-10-18 13:34 | GOODMAN - CKL60-1 | 115 | 8.4 | Yes | Yes | 22.8 | 20.4 | 2.4 | 1A045735234E428D9B2F7A8C0DA6371A |  | R22 | TXV |  | 7.304% | 0.92696 | 14.04% | [5 empty] | TXV | 7.304%
Tracy | CA | 95377-7242 |  | 2013-09-23 | 2013-09-23 09:08 | 2013-09-23 09:26 | AMANA - ZRCF36UOID | 107 | 3.8 | Yes | Yes | 19.3 | 18.8 | 0.5 | B023AF10946240C79BB328D246C6570B |  | R22 | Non-TXV |  | 3.551% | 0.96449 | 6.825% | [5 empty] | Non-TXV | 3.551%
Stockton | CA | 95205-3807 |  | 2013-09-27 | 2013-09-27 15:09 | 2013-09-27 15:20 | KENMORE - PGAD30D1K5 | 78 | 7.1 | Yes | Yes | 24.9 | 20.1 | 4.8 | A69DC778DCA64937B38E37B05D747A88 |  | R22 | Non-TXV |  | 9.103% | 0.90897 | 17.49% | [5 empty] | Non-TXV | 9.103%
Tracy | CA | 95376-0717 |  | 2013-09-20 | 2013-09-20 09:58 | 2013-09-20 10:15 | WHIRLPOOL - HICF060SOG6 | 213 | 6.5 | Yes | Yes | 17 | 16.8 | 0.3 | 31F980866C67411F9ECE88813D8F90E7 |  | R22 | Non-TXV |  | 3.052% | 0.96948 | 5.865% | [5 empty] | Non-TXV | 3.052%
Stockton | CA | 95210-5696 |  | 2013-09-25 | 2013-09-25 15:22 | 2013-09-25 15:56 | BDP - 598AN036-B | 194 | 10 | Yes | Yes | 24.6 | 19.3 | 5.3 | 8CA8AE3DC4224A3CA6A94135C9A8EAA4 |  | R22 | Non-TXV |  | 5.155% | 0.94845 | 9.906% | [5 empty] | Non-TXV | 5.155%
Stockton | CA | 95206-4972 |  | 2013-09-19 | 2013-09-19 16:12 | 2013-09-19 17:18 | GOODMAN - CKL49-1L | 112 | 9.3 | Yes | Yes | 22.2 | 20.2 | 2 | 230F989BA9C54C3F96E030A27608AE6A |  | R22 | Non-TXV |  | 8.304% | 0.91696 | 15.96% | [5 empty] | Non-TXV | 8.304%
Stockton | CA | 95207-4172 |  | 2013-09-20 | 2013-09-20 09:40 | 2013-09-20 09:40 | OTHER - UNK | 51 | 0 | Yes | Yes | 17.1 | 17.9 | -0.8 | 0D12CE2B47434888AAF02E162BE3E56A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Jamestown | CA | 95327-9654 |  | 2013-09-24 | 2013-09-24 12:49 | 2013-09-24 13:12 | CARRIER - 38EN048310 | 145 | 43 | Yes | Yes | 16.7 | 19.6 | -2.9 | 270E62DB69AE40ECB61E3EE6E5B720B4 |  | R22 | Non-TXV |  | 29.66% | 0.70345 | 56.99% | [5 empty] | Non-TXV | 29.66%
Stockton | CA | 95207-3358 |  | 2013-09-17 | 2013-09-17 10:29 | 2013-09-17 11:07 | GOODMAN - CLJ48-1C | 130 | -12.2 | Yes | Yes | 18.4 | 16.7 | 1.7 | 0135757FAEBF494088519ECD4615A309 |  | R22 | Non-TXV |  | -9.385% | 1.0938 | 2.628% |  |  |  |  | Non-TXV |  |  | -9.385%
Tracy | CA | 95376-8183 |  | 2013-09-27 | 2013-09-27 10:48 | 2013-09-27 11:05 | AMERICAN STANDARD - YCY048F1H0AA | 184 | 6.7 | Yes | Yes | 21.3 | 18 | 3.3 | 2515D3D1E8D241238EE095997CDC0255 |  | R22 | Non-TXV |  | 3.641% | 0.96359 | 6.998% | [5 empty] | Non-TXV | 3.641%
Tracy | CA | 95376-6720 |  | 2013-09-24 | 2013-09-24 11:22 | 2013-09-24 11:48 | YORK - H1RA048S06D | 120 | 4.1 | Yes | Yes | 18.7 | 17.2 | 1.5 | 40C95EE5B5D24BAAAC2CACE3653788BB |  | R22 | Non-TXV |  | 3.417% | 0.96583 | 6.566% | [5 empty] | Non-TXV | 3.417%
Oakdale | CA | 95361-2224 |  | 2013-09-17 | 2013-09-17 16:30 | 2013-09-17 17:07 | HEIL - CA3042VKA1 | 99 | 3 | Yes | Yes | 20.3 | 19.8 | 0.5 | 8534727BC5C7421B98F259515A25767E |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Oakdale | CA | 95361-9672 |  | 2013-09-17 | 2013-09-17 09:17 | 2013-09-17 09:45 | GOODMAN - CK42-1C | 86 | 2.8 | Yes | Yes | 21.8 | 19.9 | 1.9 | 08B5A532276242BE8A5FB4418E104989 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
Stockton | CA | 95209-4548 |  | 2013-09-19 | 2013-09-19 10:17 | 2013-09-19 10:33 | CARRIER - 38CKC042350 | 83 | -4.9 | Yes | Yes | 18 | 20.7 | -2.7 | A296946D9C3D4D88A1D86D4298E8A584 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Lathrop | CA | 95330-8919 |  | 2013-09-19 | 2013-09-19 12:15 | 2013-09-19 12:40 | GOODMAN - CKJ48-1A | 118 | 5.3 | Yes | Yes | 24 | 19.3 | 4.7 | D4368AB90F6147ABBF873C08876B1429 |  | R22 | Non-TXV |  | 4.492% | 0.95508 | 8.632% | [5 empty] | Non-TXV | 4.492%
Manteca | CA | 95337-6690 |  | 2013-09-20 | 2013-09-20 09:11 | 2013-09-20 09:31 | BRYANT - 563CN048-F | 165 | 6.2 | Yes | Yes | 21.1 | 18.2 | 2.9 | 5802D7695C7B4245948F9CFFEB5FD2B6 |  | R22 | TXV |  | 3.758% | 0.96242 | 7.221% | [5 empty] | TXV | 3.758%
Oakdale | CA | 95361-3704 |  | 2013-10-04 | 2013-10-04 13:14 | 2013-10-04 13:37 | YORK - D2N0024N03606A | 116 | 10.2 | Yes | Yes | 19.8 | 21.2 | -1.4 | ED5B40540FFE4D64902495C64ABEF48D |  | R410A | TXV |  | 8.793% | 0.91207 | 16.9% | [5 empty] | TXV | 8.793%
Manteca | CA | 95336-5015 |  | 2013-09-23 | 2013-09-23 17:01 | 2013-09-23 17:27 | - GCGD36S41S3A | 73 | 3.6 | Yes | Yes | 22.7 | 19.9 | 2.8 | 1E72A30459A94EC5BD89B6E20A7C1716 |  | R410A | Non-TXV |  | 4.932% | 0.95068 | 9.477% | [5 empty] | Non-TXV | 4.932%
Stockton | CA | 95207-4553 |  | 2013-09-20 | 2013-09-20 13:52 | 2013-09-20 14:01 | PAYNE - 565AJ024 | 70 | 4.2 | Yes | Yes | 18.8 | 18.5 | 0.3 | 051A98C09F88409FAF30ADE3BFDA0484 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Stockton | CA | 95207-4553 |  | 2013-09-20 | 2013-09-20 14:09 | 2013-09-20 14:34 | OTHER - AC030M1021A | 57 | 2.5 | Yes | Yes | 17.8 | 19.2 | -1.4 | 6E64EC4BB4C740D6B66C842133D691AD |  | R22 | Non-TXV |  | 4.386% | 0.95614 | 8.429% | [5 empty] | Non-TXV | 4.386%
Stockton | CA | 95207-4553 |  | 2013-09-20 | 2013-09-20 14:20 | 2013-09-20 14:36 | YORK - H2RA036S06E | 63 | -3.7 | Yes | Yes | 21.2 | 18.7 | 2.5 | 5F95A1ED7E9E4159AC1ED0F2225F0A01 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Stockton | CA | 95206-6140 |  | 2013-09-17 | 2013-09-17 15:01 | 2013-09-17 15:19 | GOODMAN - CKJ48-1AB | 118 | 3.5 | Yes | Yes | 24.1 | 19.6 | 4.5 | 71AC507DF9684955A7AFB891BA45418C |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Stockton | CA | 95209-3921 |  | 2013-09-23 | 2013-09-23 09:44 | 2013-09-23 10:02 | CARRIER - 38CKC042350 | 93 | 7.9 | Yes | Yes | 23 | 18 | 5 | B60900C7072F4AE99C717DEA6ADBCC3A |  | R22 | TXV |  | 8.495% | 0.91505 | 16.32% | [5 empty] | TXV | 8.495%
Stockton | CA | 95206-4661 |  | 2013-09-30 | 2013-09-30 17:09 | 2013-09-30 17:30 | RHEEM - RAMA-048JA | 172 | 23.1 | Yes | Yes | 16.9 | 18.7 | -1.7 | 1890D10FFB4D426BA19D2A3A3D1DAD5B |  | R22 | Non-TXV |  | 13.43% | 0.8657 | 25.81% | [5 empty] | Non-TXV | 13.43%
Jamestown | CA | 95327-9426 |  | 2013-10-21 | 2013-10-21 11:06 | 2013-10-21 11:30 | WESTINGHOUSE - UNK | 96 | 7.1 | Yes | Yes | 25.5 | 20.7 | 4.8 | FA5AED6DD0D94806A4249344AD6F1A3E |  | R22 | Non-TXV |  | 7.396% | 0.92604 | 14.21% | [5 empty] | Non-TXV | 7.396%
Manteca | CA | 95337-6522 |  | 2013-09-25 | 2013-09-25 12:32 | 2013-09-25 12:55 | YORK - H2CB024S06A | 65 | 2.8 | Yes | Yes | 19.6 | 18.8 | 0.8 | B1AA350BBEB149FBBCA0084130663F74 |  | R22 | Non-TXV |  | 4.308% | 0.95692 | 8.278% | [5 empty] | Non-TXV | 4.308%
Tracy | CA | 95304-7219 |  | 2013-09-18 | 2013-09-18 11:13 | 2013-09-18 11:34 | COLEMAN - BRCQ0361BD | 52 | 1.9 | Yes | Yes | 22 | 21.3 | 0.7 | B3B53102497A44958E705FD42EAC0FFE |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Stockton | CA | 95203-1715 |  | 2013-09-27 | 2013-09-27 11:18 | 2013-09-27 11:35 | AMANA - PGE36C0702E | 64 | 7.9 | Yes | Yes | 29.2 | 23.7 | 5.5 | 3E8E36BD1BCF45DC9B9D3A717A1FF01D |  | R22 | Non-TXV |  | 12.34% | 0.87656 | 23.72% | [5 empty] | Non-TXV | 12.34%
Stockton | CA | 95205-0000 |  | 2013-10-03 | 2013-10-03 13:35 | 2013-10-03 13:55 | AMERICAN STANDARD - YCY042G1M0AC | 147 | 8.9 | Yes | Yes | 26.5 | 20.6 | 5.9 | 2A84B9F456F34B0CB74FCBE59F5F16D5 |  | R22 | Non-TXV |  | 6.054% | 0.93946 | 11.64% | [5 empty] | Non-TXV | 6.054%
Oakdale | CA | 95361-8909 |  | 2013-09-17 | 2013-09-17 10:53 | 2013-09-17 11:23 | BDP - 561AJ042-C | 89 | 16.9 | Yes | Yes | 17.1 | 19 | -1.9 | F1C44097AEF0432D97A6141D75051A1C |  | R22 | Non-TXV |  | 18.99% | 0.81011 | 36.49% | [5 empty] | Non-TXV | 18.99%
Valley Springs | CA | 95252-9409 |  | 2013-09-26 | 2013-09-26 13:50 | 2013-09-26 14:09 | CARRIER - 24APA548A310 | 180 | 6.8 | Yes | Yes | 25.2 | 20.6 | 4.6 | AB72C2BCE4FB4D449FDB4B6925A1E60E |  | R410A | TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | TXV | 3.778%
Stockton | CA | 95206-6062 |  | 2013-09-25 | 2013-09-25 13:20 | 2013-09-25 13:38 | GOODMAN - CKJ60-1 | 150 | 5.3 | Yes | Yes | 21.3 | 17.3 | 4.1 | 694E83D620F84F7086DEFF0E41943E8C |  | R22 | Non-TXV |  | 3.533% | 0.96467 | 6.79% | [5 empty] | Non-TXV | 3.533%
Tracy | CA | 95376-1404 |  | 2013-09-20 | 2013-09-20 09:35 | 2013-09-20 09:57 | RHEEM - RAFD-042JBS | 79 | -5.6 | Yes | Yes | 19.5 | 20.8 | -1.3 | E4E88E02959143A58B844732BBC9F959 |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Stockton | CA | 95205-3341 |  | 2013-09-24 | 2013-09-24 13:58 | 2013-09-24 14:16 | PAYNE - 598WNX036000AAAA | 187 | 34.8 | Yes | Yes | 19.6 | 19.5 | 0.1 | 699D3A8CF9504BA993E89EDD6F7C1722 |  | R22 | Non-TXV |  | 18.61% | 0.8139 | 35.76% | [5 empty] | Non-TXV | 18.61%
Manteca | CA | 95336-8539 |  | 2013-09-25 | 2013-09-25 11:54 | 2013-09-25 12:12 | GOODMAN - GSC130601BC | 169 | 5.1 | Yes | Yes | 21.1 | 18.7 | 2.4 | 014704BBFFF442A3A4EE894E44800B9B |  | R22 | Non-TXV |  | 3.018% | 0.96982 | 5.799% | [5 empty] | Non-TXV | 3.018%
Riverbank | CA | 95367-2667 |  | 2013-10-02 | 2013-10-02 11:50 | 2013-10-02 12:29 | OTHER - AA1AJ036-B | 73 | 2.2 | Yes | Yes | 17.5 | 18.7 | -1.2 | 77EDAA8A767D4C489CD73473FC0C8FF0 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Oakdale | CA | 95361-8227 |  | 2013-09-17 | 2013-09-17 17:22 | 2013-09-17 17:42 | DAY & NIGHT - 591AN060-A | 161 | 4.9 | Yes | Yes | 21.1 | 19.3 | 1.8 | 04CF9C57B2F7441F9CFFDCB46BC64D3E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Tracy | CA | 95376-1830 |  | 2013-09-23 | 2013-09-23 13:26 | 2013-09-23 13:57 | RHEEM - RRNLB036JKO6X | 96 | 3 | Yes | Yes | 19.2 | 19.9 | -0.7 | B3ED50FD1A874132A35528DA6EA89F51 |  | R410A | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Tracy | CA | 95376-1889 |  | 2013-09-23 | 2013-09-23 14:57 | 2013-09-23 22:26 | CARRIER - 38CKC048-371 | 110 | 3.6 | Yes | Yes | 18.6 | 19.9 | -1.3 | 78F553EEE60A4E19B62C0E40FF00823E |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Valley Springs | CA | 95252-9240 |  | 2013-09-26 | 2013-09-26 13:04 | 2013-09-26 13:21 | RHEEM - UNK | 64 | 9 | Yes | Yes | 25.8 | 19.9 | 5.9 | C1A364EC795D4163A389F0248E1858E4 |  | R22 | Non-TXV |  | 14.06% | 0.85938 | 27.03% | [5 empty] | Non-TXV | 14.06%
Oakdale | CA | 95361-3243 |  | 2013-10-24 | 2013-10-24 12:18 | 2013-10-24 12:40 | RHEEM - RRNA-A036JK08X | 114 | 4.6 | Yes | Yes | 19.7 | 19.1 | 0.6 | F34EC65C6BE44C36823F955106604FC4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.035% | 0.95965 | 7.755% | [5 empty] | Non-TXV | 4.035%
Riverbank | CA | 95367-2642 |  | 2013-10-14 | 2013-10-14 15:38 | 2013-10-14 16:02 | RHEEM - RAFD-030JAS | 69 | 12.4 | Yes | Yes | 19.7 | 20.8 | -1.1 | BC6291CB075C4160AA729099E4AA4C66 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.97% | 0.82029 | 34.54% | [5 empty] | Non-TXV | 17.97%
Tracy | CA | 95376-8727 |  | 2013-10-04 | 2013-10-04 12:47 | 2013-10-04 13:16 | ICP - CA5542VKD2 | 98 | 11.3 | Yes | Yes | 26.3 | 21.2 | 5.1 | 7B6840B05F344DECB11478624A328D1B |  | R22 | Non-TXV |  | 11.53% | 0.88469 | 22.16% | [5 empty] | Non-TXV | 11.53%
Tracy | CA | 95377-6723 |  | 2013-09-20 | 2013-09-20 10:28 | 2013-09-20 10:53 | GOODMAN - CKL421A | 95 | 5.9 | Yes | Yes | 19.5 | 15.9 | 3.6 | 89D009CA05454B99B1F6B52F193C736C |  | R22 | Non-TXV |  | 6.211% | 0.93789 | 11.94% | [5 empty] | Non-TXV | 6.211%
Stockton | CA | 95205-2593 |  | 2013-09-25 | 2013-09-25 16:06 | 2013-09-25 16:24 | CARRIER - 38EZG048300 | 125 | 15.7 | Yes | Yes | 21.3 | 19.8 | 1.5 | 47F94C607AD94DFFB50693480E1F5E25 |  | R410A | TXV |  | 12.56% | 0.8744 | 24.14% | [5 empty] | TXV | 12.56%
Oakdale | CA | 95361-9457 |  | 2013-10-24 | 2013-10-24 12:59 | 2013-10-24 13:25 | UNITARY PRODUCTS GROUP - BRCQ0481BD | 103 | 3.1 | Yes | Yes | 20.1 | 17.7 | 2.4 | BFD005E8AF8B4D428606251FE3458E67 |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Stockton | CA | 95206-1855 |  | 2013-09-30 | 2013-09-30 13:44 | 2013-09-30 14:01 | BDP - 585HJW030040 | 68 | 3.7 | Yes | Yes | 21.9 | 19.1 | 2.9 | 80D8C4C4FCA247E3B6D49B6336164251 |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Stockton | CA | 95206-6291 |  | 2013-10-04 | 2013-10-04 14:50 | 2013-10-04 15:12 | CARRIER - 38CKC048370 | 98 | 5.1 | Yes | Yes | 17.9 | 20.9 | -3 | 566C1470701D4AB29E881F7E9B65C9A8 |  | R22 | TXV |  | 5.204% | 0.94796 | 10% | [5 empty] | TXV | 5.204%
Stockton | CA | 95206-2030 |  | 2013-09-25 | 2013-09-25 11:16 | 2013-09-25 11:42 | ICP - ACSO48GB2 | 102 | 3.1 | Yes | Yes | 19.2 | 17.5 | 1.8 | 610129CBA7C54F77B85CC46DAF695B27 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Stockton | CA | 95215-5111 |  | 2013-09-26 | 2013-09-26 14:30 | 2013-09-26 14:47 | YORK - D1NA048N09006C | 92 | -6.5 | Yes | Yes | 26.1 | 20.1 | 6 | A39E2CE27F4340BCB81F9B7543B0475E |  | R22 | Non-TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.065%
Stockton | CA | 95205-7214 |  | 2013-09-25 | 2013-09-25 13:25 | 2013-09-25 13:42 | DAY & NIGHT - 591AN024-A | 53 | 8.9 | Yes | Yes | 20.4 | 19.4 | 1.1 | EE9EC161111D4B74B81501A77304CD33 |  | R22 | Non-TXV |  | 16.79% | 0.83208 | 32.27% | [5 empty] | Non-TXV | 16.79%
Riverbank | CA | 95367-2322 |  | 2013-10-02 | 2013-10-02 16:13 | 2013-10-02 20:09 | LENNOX - GCS20R-411-75-2P | 70 | 5.2 | Yes | Yes | 21.7 | 21.3 | 0.4 | F752BC93574740C181F08695149B486F |  | R22 | TXV |  | 7.429% | 0.92571 | 14.28% | [5 empty] | TXV | 7.429%
Riverbank | CA | 95367-3826 |  | 2013-10-01 | 2013-10-01 16:10 | 2013-10-01 18:21 | RHEEM - RAFD-036JAS | 85 | 2.6 | Yes | Yes | 24.9 | 20.4 | 4.5 | 7A84E1C18CED412FB0283025396025AE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Stockton | CA | 95206-4684 |  | 2013-09-19 | 2013-09-19 15:14 | 2013-09-19 16:23 | BDP - 563CN030-A | 102 | 6.4 | Yes | Yes | 24.4 | 22 | 2.4 | F557DBACDEDC412D87AB5CD3281D66E7 |  | R22 | Non-TXV |  | 6.275% | 0.93725 | 12.06% | [5 empty] | Non-TXV | 6.275%
Ripon | CA | 95366-2435 |  | 2013-10-09 | 2013-10-09 12:59 | 2013-10-09 13:27 | YORK - H10H030S06B | 122 | 10.5 | Yes | Yes | 21.8 | 18.7 | 3.1 | 90642732A73C488DBA2E9D90E0762CDF |  | R22 | TXV |  | 8.607% | 0.91393 | 16.54% | [5 empty] | TXV | 8.607%
Stockton | CA | 95206-0000 |  | 2013-10-04 | 2013-10-04 17:36 | 2013-10-04 18:06 | BRYANT - 563CN042-C | 103 | 4.4 | Yes | Yes | 22.5 | 21.6 | 0.9 | 00A2AC99D8EA42498C5877DE1911EF6F |  | R22 | TXV |  | 4.272% | 0.95728 | 8.21% | [5 empty] | TXV | 4.272%
Stockton | CA | 95210-1312 |  | 2013-09-20 | 2013-09-20 12:52 | 2013-09-20 13:11 | TRANE - TTB036C100A1 | 90 | 3.7 | Yes | Yes | 16 | 15.6 | 0.4 | BDECD12DF2E34EF98E2ED5516F41AB9E |  | R22 | Non-TXV |  | 4.111% | 0.95889 | 7.901% | [5 empty] | Non-TXV | 4.111%
Stockton | CA | 95206-5900 |  | 2013-09-17 | 2013-09-17 15:35 | 2013-09-17 15:53 | YORK - H1RA048S06D | 117 | 3.6 | Yes | Yes | 19.4 | 19.3 | 0.1 | 24151DCFD5B14E33B6A1DAD751372475 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Lathrop | CA | 95330-9631 |  | 2013-09-18 | 2013-09-18 12:56 | 2013-09-18 13:16 | RUUD - UAFD024JAS | 67 | 3.5 | Yes | Yes | 20.1 | 17.5 | 2.6 | 952D3DE48C5F4DDFAAF7BB2CCA0E7E81 |  | R22 | Non-TXV |  | 5.224% | 0.94776 | 10.04% | [5 empty] | Non-TXV | 5.224%
Stockton | CA | 95210-5695 |  | 2013-09-30 | 2013-09-30 13:18 | 2013-09-30 13:36 | PAYNE - PA13NR036-J | 83 | 4 | Yes | Yes | 22.1 | 16.4 | 5.7 | 202C4546368B48C3A41A58FC1CDE1F18 |  | R22 | TXV |  | 4.819% | 0.95181 | 9.262% | [5 empty] | TXV | 4.819%
Stockton | CA | 95206-5905 |  | 2013-10-10 | 2013-10-10 11:53 | 2013-10-10 12:11 | UNITARY PRODUCTS GROUP - H1RA048S06D | 117 | 5.8 | Yes | Yes | 21.6 | 20.2 | 1.4 | 99ACDC1B29FD44D9BE7513F1CC3F761F |  | R22 | Non-TXV |  | 4.957% | 0.95043 | 9.527% | [5 empty] | Non-TXV | 4.957%
Stockton | CA | 95219-5467 |  | 2013-10-02 | 2013-10-02 12:18 | 2013-10-02 12:38 | BDP - 565BJ030 | 105 | -7.4 | Yes | Yes | 22.3 | 19.8 | 2.5 | 2451D335E4164F008CF0AC483D312C51 |  | R22 | Non-TXV |  | -7.048% | 1.0705 | 1.974% |  |  |  |  | Non-TXV |  |  | -7.048%
Escalon | CA | 95320-8525 |  | 2013-09-26 | 2013-09-26 14:15 | 2013-09-26 14:39 | OTHER - 13CD=036-230-14 | 92 | 4.1 | Yes | Yes | 19.4 | 21.4 | -2 | 159F86C010A04E3DB150F51471CFB16A |  | R22 | Non-TXV |  | 4.457% | 0.95543 | 8.564% | [5 empty] | Non-TXV | 4.457%
Tracy | CA | 95376-3344 |  | 2013-09-20 | 2013-09-20 11:20 | 2013-09-20 11:44 | DAY & NIGHT - UNK | 110 | -7.8 | Yes | Yes | 20.7 | 20.4 | 0.3 | 887EBA919C214AFD862E2387BF23A56C |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Stockton | CA | 95210-1798 |  | 2013-09-25 | 2013-09-25 16:09 | 2013-09-25 16:26 | BDP - 585A030060YACR | 50 | 2.2 | Yes | Yes | 22.2 | 19.9 | 2.3 | 7B83FC871CF94305954EA5165328A6B6 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Ripon | CA | 95366-3225 |  | 2013-10-09 | 2013-10-09 13:58 | 2013-10-09 14:29 | TRANE - YCY030G1M0AD | 124 | 3.7 | Yes | Yes | 21.5 | 19.1 | 2.4 | BD1827E31C8C4A1CB34554EA88AF58C3 |  | R22 | Non-TXV |  | 2.984% | 0.97016 | 5.734% | [5 empty] | Non-TXV | 2.984%
Stockton | CA | 95205-0000 |  | 2013-10-18 | 2013-10-18 10:28 | 2013-10-18 10:46 | GOODMAN - CRT48-1 | 115 | 4.9 | Yes | Yes | 18 | 18.2 | -0.2 | BEBA93BDB40B4AF6B7E95635E0CAF912 |  | R22 | TXV |  | 4.261% | 0.95739 | 8.188% | [5 empty] | TXV | 4.261%
Manteca | CA | 95336-3533 |  | 2013-09-24 | 2013-09-24 09:40 | 2013-09-24 10:07 | BRYANT - 583BNW036060AB | 105 | 3.1 | Yes | Yes | 20.8 | 18.2 | 2.6 | BCD79FA14C204ADD87E638096AF4EE3B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 2.952% | 0.97048 | 5.674% | [5 empty] | Non-TXV | 2.952%
Stockton | CA | 95205-2580 |  | 2013-09-25 | 2013-09-25 14:53 | 2013-09-25 15:11 | CARRIER - 38EZG036310 | 99 | 11.6 | Yes | Yes | 17.5 | 18.2 | -0.7 | 1067B1874FD54E6CAE7247E2A3C5005C |  | R410A | Non-TXV |  | 11.72% | 0.88283 | 22.52% | [5 empty] | Non-TXV | 11.72%
Stockton | CA | 95205-2909 |  | 2013-10-10 | 2013-10-10 14:00 | 2013-10-10 14:17 | COMFORT AIRE - NAC036AKC3 | 94 | 14.2 | Yes | Yes | 21.7 | 18.6 | 3.1 | 19D2EE683CC44DD3A553F9C80AF27BF2 |  | R22 | Non-TXV |  | 15.11% | 0.84894 | 29.03% | [5 empty] | Non-TXV | 15.11%
Stockton | CA | 95205-2571 |  | 2013-09-24 | 2013-09-24 12:00 | 2013-09-24 12:18 | CARRIER - 24ABA348A300 | 122 | 14.2 | Yes | Yes | 20.5 | 19 | 1.5 | 4225DBEC71CE4A2DBABC101DA22A89F0 |  | R410A | TXV |  | 11.64% | 0.88361 | 22.37% | [5 empty] | TXV | 11.64%
Stockton | CA | 95207-7512 |  | 2013-11-08 | 2013-11-08 09:16 | 2013-11-08 09:16 | RHEEM - UAPA-049JAS | 240 | 0 | Yes | Yes | 26.1 | 20.9 | 5.2 | 537AF7F653BC442FAC362F36AB90562B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-4801 |  | 2013-09-19 | 2013-09-19 08:42 | 2013-09-19 09:22 | GOODMAN - VSX130301AA | 78 | -7.3 | Yes | Yes | 22.6 | 19.1 | 3.5 | 67DEB963CE85432CB61E5320A0967C08 |  | R410A | Non-TXV |  | -9.359% | 1.0936 | 2.621% |  |  |  |  | Non-TXV |  |  | -9.359%
Riverbank | CA | 95367-2821 |  | 2013-10-02 | 2013-10-02 13:13 | 2013-10-02 13:36 | RHEEM - RRKA-A048JK10X | 75 | 3.2 | Yes | Yes | 20.1 | 19.9 | 0.2 | 8062B538133C4148B8D52A975A1B0BEB |  | R22 | Non-TXV |  | 4.267% | 0.95733 | 8.2% | [5 empty] | Non-TXV | 4.267%
Oakdale | CA | 95361-0000 |  | 2013-10-04 | 2013-10-04 11:44 | 2013-10-04 12:07 | COLEMAN - BRCQ0301BEG | 41 | 1.8 | Yes | Yes | 23.7 | 19.1 | 4.6 | F0B7B27B8EFA4BDE8DB052760C112976 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.39% | 0.9561 | 8.437% | [5 empty] | Non-TXV | 4.39%
Tracy | CA | 95377-8653 |  | 2013-09-24 | 2013-09-24 14:56 | 2013-09-24 15:13 | BRYANT - 5633N0042-C | 109 | -6.4 | Yes | Yes | 20.6 | 15.1 | 5.5 | 8AE653610AAB4633B7229D56F95DA07B |  | R22 | Non-TXV |  | -5.872% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.872%
Tracy | CA | 95377-8950 |  | 2013-10-07 | 2013-10-07 10:43 | 2013-10-07 11:09 | TRANE - TTD760B100A | 129 | 12.4 | Yes | Yes | 25.7 | 20.1 | 5.6 | 9979DE04D6B44156ABAF8E29350FC7EB |  | R22 | TXV |  | 9.612% | 0.90388 | 18.47% | [5 empty] | TXV | 9.612%
Oakdale | CA | 95361-7773 |  | 2013-10-24 | 2013-10-24 10:10 | 2013-10-24 10:30 | AMANA - PGD36C0702E | 110 | 3.9 | Yes | Yes | 25.7 | 20.1 | 5.6 | 376996984BD7409090F8DD0EA5A88C9C |  | R22 | Non-TXV |  | 3.545% | 0.96455 | 6.814% | [5 empty] | Non-TXV | 3.545%
Valley Springs | CA | 95252-9008 |  | 2013-09-26 | 2013-09-26 10:04 | 2013-09-26 10:36 | TRANE - 2TTR2048A1000AA | 120 | -7.1 | Yes | Yes | 24.3 | 19.5 | 4.8 | 7B045FACAE08433DA35550E030CE28FC |  | R22 | Non-TXV |  | -5.917% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.917%
Stockton | CA | 95212-3053 |  | 2013-09-23 | 2013-09-23 13:32 | 2013-09-23 13:51 | YORK - H2RC048S06G | 119 | 4.1 | Yes | Yes | 16.8 | 18.7 | -1.9 | 51936F076C204CA2A2E46585B8C629DF |  | R22 | Non-TXV |  | 3.445% | 0.96555 | 6.621% | [5 empty] | Non-TXV | 3.445%
Stockton | CA | 95206-4766 |  | 2013-09-30 | 2013-09-30 14:52 | 2013-09-30 15:19 | RHEEM - RAKA-030JAS | 68 | 18.2 | Yes | Yes | 23.3 | 19.5 | 3.8 | 9F23DE4CBBD74FD1B896616A7D8C0971 |  | R22 | Non-TXV |  | 26.76% | 0.73235 | 51.44% | [5 empty] | Non-TXV | 26.76%
Stockton | CA | 95215-8107 |  | 2013-09-27 | 2013-09-27 14:05 | 2013-09-27 14:24 | BRYANT - 561CJ060-A | 154 | -9.1 | Yes | Yes | 23.7 | 20.4 | 3.3 | F400A5F543A44FCEA691079DE7E43191 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Burson | CA | 95225-0000 |  | 2013-10-10 | 2013-10-10 13:19 | 2013-10-10 13:36 | YORK - BRCQ0481BD | 103 | 3.5 | Yes | Yes | 24.8 | 20.8 | 4 | 80A67F78CEE143BD88526FEF10B976E7 |  | R22 | Non-TXV |  | 3.398% | 0.96602 | 6.53% | [5 empty] | Non-TXV | 3.398%
Stockton | CA | 95206-6291 |  | 2013-09-17 | 2013-09-17 10:50 | 2013-09-17 11:29 | CARRIER - 38CKC042350 | 81 | 8.3 | Yes | Yes | 23.2 | 18.3 | 4.9 | BE0EE0B852154F69A6642EFEEE894291 |  | R22 | Non-TXV |  | 10.25% | 0.89753 | 19.69% | [5 empty] | Non-TXV | 10.25%
San Andreas | CA | 95249-9503 |  | 2013-09-26 | 2013-09-26 13:32 | 2013-09-26 13:50 | UNITARY PRODUCTS GROUP - AC036X1021A | 63 | 7.4 | Yes | Yes | 25.5 | 19.5 | 6 | 1F1D9792B6BD4E5C901BD78C01C629A4 |  | R22 | Non-TXV |  | 11.75% | 0.88254 | 22.57% | [5 empty] | Non-TXV | 11.75%
Wallace | CA | 95254-0000 |  | 2013-10-01 | 2013-10-01 12:36 | 2013-10-01 12:56 | AMANA - RCE60C2C | 235 | 10.4 | Yes | Yes | 24.6 | 19.3 | 5.3 | 6D10ECEA9E294DD3963A2BC24D61A2AC |  | R22 | Non-TXV |  | 4.426% | 0.95574 | 8.505% | [5 empty] | Non-TXV | 4.426%
Tracy | CA | 95377-7905 |  | 2013-09-24 | 2013-09-24 13:27 | 2013-09-24 13:58 | YORK - H1RA048S060 | 90 | 2.6 | Yes | Yes | 19.2 | 17.7 | 1.5 | B17E35888A6C42AFB8BD24FCD858F465 |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Tracy | CA | 95377-8651 |  | 2013-10-08 | 2013-10-08 12:16 | 2013-10-08 12:40 | YORK - H1DE048S06B | 112 | 4.6 | Yes | Yes | 18.9 | 21.7 | -2.8 | 30820DFAF84845CB9537C5991360796B |  | R22 | TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | TXV | 4.107%
San Andreas | CA | 95249-9729 |  | 2013-09-26 | 2013-09-26 14:06 | 2013-09-26 14:27 | UNITARY PRODUCTS GROUP - H1RA042S06D | 84 | 4.7 | Yes | Yes | 18.5 | 21.5 | -3 | B6DE3F1DAD6D4FA4BB196B365A153C8C |  | R22 | Non-TXV |  | 5.595% | 0.94405 | 10.75% | [5 empty] | Non-TXV | 5.595%
Tracy | CA | 95376-3218 |  | 2013-09-19 | 2013-09-19 11:37 | 2013-09-19 11:54 | GOODMAN - GPG10360701A | 75 | 2.8 | Yes | Yes | 21 | 19.1 | 1.9 | A2740472473E43A3A28FAE0F54805524 |  | R22 | Non-TXV |  | 3.733% | 0.96267 | 7.175% | [5 empty] | Non-TXV | 3.733%
Stockton | CA | 95206-2406 |  | 2013-09-20 | 2013-09-20 13:52 | 2013-09-20 14:09 | RHEEM - UNK | 100 | 6.1 | Yes | Yes | 19.2 | 19.7 | -0.4 | 5C41F3ABEA7F437999BBD6761C2BBEC1 |  | R22 | Non-TXV |  | 6.1% | 0.939 | 11.72% | [5 empty] | Non-TXV | 6.1%
Stockton | CA | 95206-4645 |  | 2013-09-25 | 2013-09-25 14:20 | 2013-09-25 14:45 | RHEEM - UNK | 135 | 5.1 | Yes | Yes | 21.2 | 18.2 | 3 | FD584608FE764171A74435D483186D03 |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Tracy | CA | 95304-9207 |  | 2013-09-18 | 2013-09-18 09:48 | 2013-09-18 10:07 | TRANE - TT3730A100A0 | 115 | 2.5 | Yes | Yes | 18.4 | 19.5 | -1.1 | 50F1E55A85C94F7DAF6051AD32C1633D |  | R22 | Non-TXV |  | 2.174% | 0.97826 | 4.178% | [5 empty] | Non-TXV | 2.174%
Tracy | CA | 95304-9207 |  | 2013-09-18 | 2013-09-18 10:09 | 2013-09-18 10:41 | TRANE - TTB72AA100A1 | 54 | 2.3 | Yes | Yes | 17.7 | 20.4 | -2.7 | E3D73B232AC24FDCAA74E1B7E79F3700 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Stockton | CA | 95210-3323 |  | 2013-09-25 | 2013-09-25 17:14 | 2013-09-25 17:32 | GOODMAN - GSC130361FA | 83 | 19.1 | Yes | Yes | 25.9 | 21 | 4.9 | E49D24C6B81F42C19354F852EA39BBE9 |  | R22 | Non-TXV |  | 23.01% | 0.76988 | 44.22% | [5 empty] | Non-TXV | 23.01%
Acampo | CA | 95220-9531 |  | 2013-10-03 | 2013-10-03 10:52 | 2013-10-03 11:10 | RHEEM - RRMA-A030JK06X | 80 | 5.6 | Yes | Yes | 24.6 | 19.9 | 4.7 | 47829C57EBD44ACEB8ACD8136BC8CB6A |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Stockton | CA | 95207-7118 |  | 2013-10-08 | 2013-10-08 10:08 | 2013-10-08 10:08 | TRANE - YCY048G1HOAB | 85 | 0 | Yes | Yes | 22.9 | 18.6 | 4.4 | AAF80D23D4064C96A6E5BDD07236ADF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-5159 |  | 2013-10-01 | 2013-10-01 16:48 | 2013-10-01 17:13 | CARRIER - 48KHA024-300BF | 65 | 6.8 | Yes | Yes | 20.8 | 19.1 | 1.7 | 9B02EAC5FD2743028B50BF033CE3F687 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.46% | 0.89538 | 20.1% | [5 empty] | Non-TXV | 10.46%
Stockton | CA | 95210-2043 |  | 2013-09-20 | 2013-09-20 14:49 | 2013-09-20 15:06 | PAYNE - 585A036080YAC | 60 | -3.5 | Yes | Yes | 24.5 | 19.7 | 4.8 | ACA4742E46E143A69436E0D526425471 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95210-1227 |  | 2013-09-30 | 2013-09-30 13:57 | 2013-09-30 14:21 | RUUD - UAND-036JAZ | 116 | 3.5 | Yes | Yes | 21.3 | 15.3 | 6 | EB06BD6D9D114EBFAFF32DE5DB7F9FF1 |  | R22 | Non-TXV |  | 3.017% | 0.96983 | 5.798% | [5 empty] | Non-TXV | 3.017%
Tracy | CA | 95376-3822 |  | 2013-10-04 | 2013-10-04 12:05 | 2013-10-04 12:27 | RHEEM - RRNA-B030JK06X | 72 | 5.2 | Yes | Yes | 28.6 | 25.3 | 3.3 | A488F09C5EE34D6B9840C15E6A790F12 |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Stockton | CA | 95206-2414 |  | 2013-09-20 | 2013-09-20 13:31 | 2013-09-20 13:31 | GE - UNK | 60 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 3CE4DAAB171445F18892F4947500CC2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-6705 |  | 2013-10-01 | 2013-10-01 17:10 | 2013-10-01 17:57 | YORK - H1DE030B06B | 80 | 5.6 | Yes | Yes | 24.2 | 21.5 | 2.7 | 86CE43705E9C42B1908DD73701593938 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Manteca | CA | 95336-6242 |  | 2013-10-03 | 2013-10-03 14:08 | 2013-10-03 14:38 | TRANE - BTD736A100B0 | 88 | 12.9 | Yes | Yes | 21.6 | 20.1 | 1.5 | 516010C968D04E4D94240CBFFCA1B3F4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.66% | 0.85341 | 28.17% | [5 empty] | Non-TXV | 14.66%
Stockton | CA | 95209-1796 |  | 2013-09-18 | 2013-09-18 09:03 | 2013-09-18 09:21 | RHEEM - 13AJM42A01 | 126 | -7.4 | Yes | Yes | 22.6 | 19.1 | 3.5 | 21DF4D6E106F4C778878AFE6E243390D |  | R410A | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Manteca | CA | 95336-7073 |  | 2013-09-24 | 2013-09-24 14:57 | 2013-09-24 15:20 | YORK - H2RC036S06D | 98 | 2.9 | Yes | Yes | 17.6 | 18.3 | -0.7 | 007D2D61D97F4679B9060627832CEDA2 |  | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.687% | [5 empty] | Non-TXV | 2.959%
Riverbank | CA | 95367-3109 |  | 2013-10-22 | 2013-10-22 15:47 | 2013-10-22 16:22 | BDP - 561AJ042-A | 89 | 7.7 | Yes | Yes | 20.3 | 18.2 | 2.1 | 8230772BCE68479D8F6E3498B0DAB342 |  | R22 | Non-TXV |  | 8.652% | 0.91348 | 16.63% | [5 empty] | Non-TXV | 8.652%
Riverbank | CA | 95367-3825 |  | 2013-10-01 | 2013-10-01 11:23 | 2013-10-01 11:50 | PAYNE - PY1PNB036060ABAA | 68 | 2 | Yes | Yes | 23.9 | 19.1 | 4.8 | 1C4F4E5A31454646B9B0320587DDBA1A |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Manteca | CA | 95336-2849 |  | 2013-09-20 | 2013-09-20 13:55 | 2013-09-20 14:18 | TRANE - TTR030C10A4 | 66 | 2 | Yes | Yes | 19.5 | 19.7 | -0.2 | 551359C63C024DD482122233F71FE426 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Tracy | CA | 95377-8972 |  | 2013-10-04 | 2013-10-04 13:43 | 2013-10-04 14:03 | YORK - H2RA060S06D | 118 | 3.9 | Yes | Yes | 28.9 | 22.9 | 6 | 0D0FBD7EBD9D4244A3CADFD121A7825B |  | R22 | Non-TXV |  | 3.305% | 0.96695 | 6.352% | [5 empty] | Non-TXV | 3.305%
Stockton | CA | 95206-3837 |  | 2013-09-30 | 2013-09-30 12:54 | 2013-09-30 13:29 | DAY & NIGHT - UNK | 85 | -8 | Yes | Yes | 21.9 | 20.8 | 1.1 | E082DE0B747E48B8AC58AAF8C2D1D2B4 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95212-9466 |  | 2013-10-01 | 2013-10-01 13:45 | 2013-10-01 14:10 | DAY & NIGHT - 591ANX036000AAAAA | 83 | 24.5 | Yes | Yes | 19.4 | 19.3 | 0.1 | FA473595E0D041E1B7CA60BC57FDCBDB |  | R22 | Non-TXV |  | 29.52% | 0.70482 | 56.73% | [5 empty] | Non-TXV | 29.52%
Stockton | CA | 95212-9466 |  | 2013-10-01 | 2013-10-01 14:13 | 2013-10-01 14:39 | ICP - CA5536VKAD | 82 | 3.5 | Yes | Yes | 22.9 | 20.4 | 2.5 | 967C859E3A9046C19A6A3CCAB39D503F |  | R22 | Non-TXV |  | 4.268% | 0.95732 | 8.203% | [5 empty] | Non-TXV | 4.268%
Escalon | CA | 95320-9678 |  | 2013-10-18 | 2013-10-18 14:42 | 2013-10-18 15:18 | TRANE - TT3736B100C0 | 80 | 3.2 | Yes | Yes | 20.4 | 19.9 | 0.5 | F0E5BF5846894921874536AF5E6C9852 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Burson | CA | 95225-0000 |  | 2013-10-10 | 2013-10-10 14:18 | 2013-10-10 14:39 | BDP - CA5542VKD2 | 98 | 19.4 | Yes | Yes | 22.7 | 19.9 | 2.8 | B84FC5FD484E4AC5B499CF9329336333 |  | R22 | Non-TXV |  | 19.8% | 0.80204 | 38.04% | [5 empty] | Non-TXV | 19.8%
Stockton | CA | 95207-6508 |  | 2013-09-20 | 2013-09-20 16:34 | 2013-09-20 16:52 | PAYNE - 561CJ060-A | 154 | 8.9 | Yes | Yes | 21.8 | 20.1 | 1.7 | EB91D1C865A54C47AD718130D0E6EBC9 |  | R22 | Non-TXV |  | 5.779% | 0.94221 | 11.11% | [5 empty] | Non-TXV | 5.779%
Escalon | CA | 95320-8614 |  | 2013-09-30 | 2013-09-30 10:54 | 2013-09-30 11:07 | BDP - 597CN036-B | 102 | 4.2 | Yes | Yes | 20.8 | 18.5 | 2.4 | 3274140BCB1441FABB507153C3902192 |  | R22 | TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | TXV | 4.118%
Escalon | CA | 95320-8614 |  | 2013-09-30 | 2013-09-30 11:24 | 2013-09-30 11:49 | BRYANT - 597CN024-F | 83 | 9.3 | Yes | Yes | 21.6 | 18.7 | 2.9 | 42D8569C4AAD4AFE8EB1490E1FBB14A7 |  | R22 | Non-TXV |  | 11.2% | 0.88795 | 21.53% | [5 empty] | Non-TXV | 11.2%
Valley Springs | CA | 95252-9105 |  | 2013-09-26 | 2013-09-26 12:08 | 2013-09-26 12:08 | YORK - D1NA042N03606C | 76 | 0 | Yes | Yes | 25.5 | 20.1 | 5.4 | 8CA11A7854434DE388676368EA097A61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-9105 |  | 2013-09-26 | 2013-09-26 12:26 | 2013-09-26 12:48 | OTHER - AD024GD | 50 | 7.3 | Yes | Yes | 20.8 | 20.1 | 0.7 | 50362499D31E40908AFE747A87B4E90E |  | R22 | Non-TXV |  | 14.6% | 0.854 | 28.06% | [5 empty] | Non-TXV | 14.6%
Stockton | CA | 95210-1418 |  | 2013-10-02 | 2013-10-02 10:34 | 2013-10-02 10:51 | AMERICAN STANDARD - YCY036G1M0AD | 130 | 11.9 | Yes | Yes | 25.5 | 19.5 | 6 | CAA6A8BDA64B4738AB5452B69D1F1E7B |  | R22 | Non-TXV |  | 9.154% | 0.90846 | 17.59% | [5 empty] | Non-TXV | 9.154%
Angels Camp | CA | 95222-0000 |  | 2013-10-15 | 2013-10-15 10:54 | 2013-10-15 11:21 | PAYNE - PY1PNB024060AAAA | 53 | 2.2 | Yes | Yes | 23.1 | 20.6 | 2.5 | 3DBEC0811E4A43DEA6D65151BC54946B |  | R22 | Non-TXV |  | 4.151% | 0.95849 | 7.977% | [5 empty] | Non-TXV | 4.151%
Stockton | CA | 95215-8102 |  | 2013-10-01 | 2013-10-01 17:33 | 2013-10-01 17:38 | FRIGIDAIRE - UNK | 85 | -7 | Yes | Yes | 20.2 | 21 | -0.8 | 86BEB158E22645E8B06BDF2B4B308B1D |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Stockton | CA | 95215-8102 |  | 2013-10-01 | 2013-10-01 17:39 | 2013-10-01 18:07 | FRIGIDAIRE - UNK | 85 | 9 | Yes | Yes | 21.6 | 20.4 | 1.2 | E38CA670AD5D4653B678412E509F43F2 |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Tracy | CA | 95376-4426 |  | 2013-10-09 | 2013-10-09 13:31 | 2013-10-09 13:51 | BRYANT - 561CJ060-A | 152 | 8.8 | Yes | Yes | 26.2 | 20.4 | 5.8 | 862BF59FE608480F882E665EC4AC56F4 |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Valley Springs | CA | 95252-8856 |  | 2013-09-17 | 2013-09-17 12:09 | 2013-09-17 12:32 | YORK - CMA04211A | 120 | 4.9 | Yes | Yes | 18.9 | 18.8 | 0.1 | 53670387EA784F869280B60BB88670D2 |  | R22 | Non-TXV |  | 4.083% | 0.95917 | 7.847% | [5 empty] | Non-TXV | 4.083%
Escalon | CA | 95320-9553 |  | 2013-09-30 | 2013-09-30 13:19 | 2013-09-30 13:55 | PAYNE - PA1ENA048-D | 136 | 4.1 | Yes | Yes | 19.2 | 18.6 | 0.7 | 3D096089B2444166BB9C4169CC76CB8B |  | R22 | Non-TXV |  | 3.015% | 0.96985 | 5.794% | [5 empty] | Non-TXV | 3.015%
Wallace | CA | 95254-0000 |  | 2013-10-01 | 2013-10-01 13:56 | 2013-10-01 14:13 | BDP - 588ANW036060ADAF | 67 | 3.7 | Yes | Yes | 23.7 | 21 | 2.7 | 468D77AC87874BEDB6598351AB927574 |  | R22 | Non-TXV |  | 5.522% | 0.94478 | 10.61% | [5 empty] | Non-TXV | 5.522%
Manteca | CA | 95336-2983 |  | 2013-09-20 | 2013-09-20 14:32 | 2013-09-20 15:00 | LENNOX - GCS26X-024-59-1PA | 76 | 2.3 | Yes | Yes | 23 | 20.4 | 2.6 | 7764D655D6F7483DACADFB877AB34B1C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95210-3272 |  | 2013-09-19 | 2013-09-19 11:20 | 2013-09-19 11:38 | GE - BTB936A100C2 | 83 | -4.9 | Yes | Yes | 21.4 | 17.7 | 3.8 | 5C9CDB35D3F74B5CBCC2C1E499F9243A |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Manteca | CA | 95337-4415 |  | 2013-09-20 | 2013-09-20 09:42 | 2013-09-20 10:10 | GOODMAN - GPG1348090M41AD | 125 | 4.2 | Yes | Yes | 24.5 | 19.1 | 5.4 | 8FEA95D3DF0B4907BB10AB60AB820A39 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.36% | 0.9664 | 6.457% | [5 empty] | Non-TXV | 3.36%
Stockton | CA | 95215-8101 |  | 2013-10-15 | 2013-10-15 16:10 | 2013-10-15 16:12 | PAYNE - PY1PNB036060ABAA | 68 | 7.2 | Yes | Yes | 23.8 | 20.9 | 2.9 | B7D33677321641218E0B9D9B9D0356CE |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Stockton | CA | 95215-5947 |  | 2013-10-15 | 2013-10-15 14:42 | 2013-10-15 15:01 | AMERICAN STANDARD - YCYY036G1MOAD | 130 | 8.9 | Yes | Yes | 24.6 | 20.9 | 3.7 | 5E3240AEFB3B4E8EBBED2FEF37ABC2EB |  | R22 | TXV |  | 6.846% | 0.93154 | 13.16% | [5 empty] | TXV | 6.846%
Stockton | CA | 95205-2554 |  | 2013-09-24 | 2013-09-24 11:08 | 2013-09-24 11:08 | GOODMAN - CKL49-1L | 112 | 0 | Yes | Yes | 16.6 | 17.2 | -0.6 | 0520019F892A49B79EB98EEAB4C117C7 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-7312 |  | 2013-10-01 | 2013-10-01 16:12 | 2013-10-01 16:47 | RUUD - UNK | 85 | -6 | Yes | Yes | 26.7 | 21.5 | 5.2 | 5DABA90B6AD840E09BE4B5A81810C76E |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Valley Springs | CA | 95252-8757 |  | 2013-09-17 | 2013-09-17 11:39 | 2013-09-17 12:04 | BRYANT - 574DNWA30060NA | 110 | 3.2 | Yes | Yes | 21.4 | 21 | 0.4 | 1B0F7E1DC6C94805A4DF69523AB658B6 |  | R410A | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Stockton | CA | 95205-4425 |  | 2013-09-27 | 2013-09-27 16:10 | 2013-09-27 16:39 | GOODMAN - GLJ36-1C | 109 | 6.3 | Yes | Yes | 19.7 | 18.7 | 1 | E5D2CDD0B48C426EAAA32E26990A1963 |  | R22 | TXV |  | 5.78% | 0.9422 | 11.11% | [5 empty] | TXV | 5.78%
Manteca | CA | 95337-5224 |  | 2013-09-19 | 2013-09-19 13:26 | 2013-09-19 13:49 | YORK - H1DE042S06B | 95 | 2.9 | Yes | Yes | 23.1 | 19.8 | 3.3 | 3DE41CFB162F45A383671415004DEF89 |  | R22 | Non-TXV |  | 3.053% | 0.96947 | 5.866% | [5 empty] | Non-TXV | 3.053%
Stockton | CA | 95210-1650 |  | 2013-09-18 | 2013-09-18 13:21 | 2013-09-18 13:40 | RUUD - UAFD-060JBS | 118 | 15.5 | Yes | Yes | 25 | 20.4 | 4.6 | 169A1D7C70EF45818788A5B1AE5365A3 |  | R22 | Non-TXV |  | 13.14% | 0.86864 | 25.24% | [5 empty] | Non-TXV | 13.14%
Oakdale | CA | 95361-2511 |  | 2013-09-17 | 2013-09-17 15:07 | 2013-09-17 15:25 | NORDYNE - R6GF-X48K120X | 85 | 22.3 | Yes | Yes | 17.4 | 19.9 | -2.5 | 5A008568D20E4EB4AED0D0A8489EE10A |  | R410A | Non-TXV |  | 26.24% | 0.73765 | 50.42% | [5 empty] | Non-TXV | 26.24%
Stockton | CA | 95210-1723 |  | 2013-09-18 | 2013-09-18 14:58 | 2013-09-18 15:04 | WESTINGHOUSE - IE024AAAON | 54 | 5.1 | Yes | Yes | 23.6 | 20.9 | 2.7 | 37FFBA14211546A9B60247FB13AE3114 |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Stockton | CA | 95209-2444 |  | 2013-09-18 | 2013-09-18 11:51 | 2013-09-18 12:12 | RUUD - UNK | 73 | -4.3 | Yes | Yes | 25.7 | 19.8 | 5.9 | DBE10536273742D08992D04D2E0EABD4 |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Stockton | CA | 95210-3657 |  | 2013-09-25 | 2013-09-25 15:36 | 2013-09-25 15:55 | RHEEM - UNK | 96 | 3 | Yes | Yes | 18.3 | 20.3 | -2 | 294A7E01164F4FB696403CA2CE1F7805 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Escalon | CA | 95320-9578 |  | 2013-09-26 | 2013-09-26 11:59 | 2013-09-26 12:26 | PAYNE - 591ANX03600AAAA | 81 | 3.3 | Yes | Yes | 20.9 | 20.1 | 0.8 | 8636DFBC69C8493FBA60E7A4F392B37D |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Stockton | CA | 95210-5654 |  | 2013-09-23 | 2013-09-23 10:46 | 2013-09-23 11:03 | GOODMAN - CK36-1A | 73 | -5.2 | Yes | Yes | 23.1 | 17.1 | 6 | 5BA87DD49D4D4A6389B64B49258A166E |  | R22 | Non-TXV |  | -7.123% | 1.0712 | 1.995% |  |  |  |  | Non-TXV |  |  | -7.123%
Stockton | CA | 95212-3437 |  | 2013-09-23 | 2013-09-23 12:53 | 2013-09-23 13:16 | YORK - AC036X1222A | 83 | 5.6 | Yes | Yes | 23.4 | 20.4 | 3 | 843BEB22D77444A0A8E529FF66A493AF |  | R22 | Non-TXV |  | 6.747% | 0.93253 | 12.97% | [5 empty] | Non-TXV | 6.747%
Stockton | CA | 95203-1056 |  | 2013-10-02 | 2013-10-02 11:27 | 2013-10-02 11:51 | RUUD - UAKA-024JAZ | 50 | -2.9 | Yes | Yes | 22.3 | 21 | 1.3 | E95D63D9E2264E6ABD031867800DD023 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Manteca | CA | 95337-9613 |  | 2013-09-25 | 2013-09-25 16:35 | 2013-09-25 16:58 | UNITARY PRODUCTS GROUP - TCGD36S21S1HA | 65 | 2.7 | Yes | Yes | 17.6 | 20.2 | -2.6 | BB721C671905465B8359C0C24797A881 |  | R22 | Non-TXV |  | 4.154% | 0.95846 | 7.983% | [5 empty] | Non-TXV | 4.154%
Stockton | CA | 95206-4672 |  | 2013-10-02 | 2013-10-02 10:09 | 2013-10-02 10:35 | GOODMAN - GSC140421AA | 143 | 31.4 | Yes | Yes | 21.7 | 19.9 | 1.8 | E5C07A52743044B8AFBD051D4A937AA6 |  | R22 | Non-TXV |  | 21.96% | 0.78042 | 42.2% | [5 empty] | Non-TXV | 21.96%
Manteca | CA | 95336-6333 |  | 2013-10-16 | 2013-10-16 14:55 | 2013-10-16 15:23 | BDP - 585GJW030040ABAF | 58 | 3.9 | Yes | Yes | 26.1 | 22.9 | 3.2 | F482D09DB685463CABD852B50D28E363 |  | R22 | Non-TXV |  | 6.724% | 0.93276 | 12.92% | [5 empty] | Non-TXV | 6.724%
Tracy | CA | 95376-2045 |  | 2013-09-19 | 2013-09-19 12:46 | 2013-09-19 12:46 | NORDYNE - JS38C042KA | 105 | 28.8 | Yes | Yes | 35 | 20.4 | 14.6 | 11BF7C251A1345AD9AC8E808904D605E | Add refrigerant: 28.8 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 27.43% | 0.72571 | 52.71% | [5 empty] | Non-TXV | 27.43%
Stockton | CA | 95206-5711 |  | 2013-09-26 | 2013-09-26 12:29 | 2013-09-26 13:05 | YORK - H24A036S06E | 63 | 4.4 | Yes | Yes | 18.4 | 18.5 | -0.1 | 5F709BEBDE9D494197AA361EB9762E62 |  | R22 | Non-TXV |  | 6.984% | 0.93016 | 13.42% | [5 empty] | Non-TXV | 6.984%
Stockton | CA | 95215-9655 |  | 2013-09-27 | 2013-09-27 13:37 | 2013-09-27 13:55 | YORK - D1NP048N06506A | 132 | 4.3 | Yes | Yes | 22 | 19.1 | 2.9 | 5DCBDEE8214D4798AE312FC60D41BA43 |  | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.26% | [5 empty] | Non-TXV | 3.258%
Stockton | CA | 95205-5740 |  | 2013-09-25 | 2013-09-25 11:54 | 2013-09-25 12:13 | OTHER - UNK | 70 | 2.5 | Yes | Yes | 17 | 17.1 | -0.1 | FBDE6FE116324E38A500A2C30DE9840C |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Stockton | CA | 95209-1942 |  | 2013-09-18 | 2013-09-18 14:09 | 2013-09-18 14:31 | ICP - HAC048AKA4 | 123 | 13.5 | Yes | Yes | 18.5 | 20.7 | -2.2 | E6473EC24D5F4107BB85BC73769C078E |  | R22 | Non-TXV |  | 10.98% | 0.89024 | 21.09% | [5 empty] | Non-TXV | 10.98%
Tracy | CA | 95377-7015 |  | 2013-10-08 | 2013-10-08 14:25 | 2013-10-08 14:42 | BRYANT - 561CJ042-B | 83 | 16.3 | Yes | Yes | 27.8 | 22.2 | 5.6 | 0867C7D471934146A503A8CD8E4A0C02 |  | R22 | Non-TXV |  | 19.64% | 0.80361 | 37.74% | [5 empty] | Non-TXV | 19.64%
Tracy | CA | 95377-6609 |  | 2013-09-20 | 2013-09-20 10:55 | 2013-09-20 11:13 | YORK - H1RA042SO6D | 85 | 3.4 | Yes | Yes | 21 | 20.7 | 0.3 | D59B6F71888A4E30BD7584D9EAC66280 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Manteca | CA | 95336-3450 |  | 2013-09-23 | 2013-09-23 09:36 | 2013-09-23 10:02 | OTHER - DRC0301BB | 85 | 3.1 | Yes | Yes | 21.5 | 18.2 | 3.3 | DEE13320B50E4DA4ACA6CDFAB783E66C |  | R22 | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Stockton | CA | 95205-3139 |  | 2013-09-24 | 2013-09-24 13:19 | 2013-09-24 13:37 | CARRIER - 48GX-036090301AD | 82 | 4 | Yes | Yes | 21.9 | 19.7 | 2.2 | 325931DF88874231AC4EC2BAAADDD594 |  | R22 | Non-TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | Non-TXV | 4.878%
Manteca | CA | 95336-3449 |  | 2013-10-08 | 2013-10-08 11:30 | 2013-10-08 12:08 | BRYANT - 563CN030-B | 100 | 3.1 | Yes | Yes | 24.6 | 20.9 | 3.7 | 66F78795B94546B58C2BD2FE1C299A41 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Ione | CA | 95640-9629 |  | 2013-09-17 | 2013-09-17 11:51 | 2013-09-17 12:16 | KENMORE - TCA036AKA5 | 80 | 7 | Yes | Yes | 20.9 | 19.3 | 1.6 | 0DE21C38E5B741F8B110DB14CF5404FA |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Stockton | CA | 95209-5194 |  | 2013-09-18 | 2013-09-18 10:54 | 2013-09-18 11:15 | PAYNE - 585BJ036-A | 80 | -5.6 | Yes | Yes | 25.4 | 19.9 | 5.5 | E9D2D0ACD487402EA7EE5F4C96A9E76A |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Manteca | CA | 95336-2844 |  | 2013-09-20 | 2013-09-20 11:41 | 2013-09-20 12:25 | GOODMAN - CKL24-1M | 72 | 2.2 | Yes | Yes | 21.2 | 19.6 | 1.6 | 9C4BD3103A364688B8C8BAD7DDA1AEC7 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Pioneer | CA | 95666-9624 |  | 2013-09-23 | 2013-09-23 10:44 | 2013-09-23 11:06 | BARD - UNK | 82 | 10.1 | Yes | Yes | 22 | 20.6 | 1.4 | 79DBAF78A08A47FF9A5D33AB6841B86B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.32% | 0.87683 | 23.67% | [5 empty] | Non-TXV | 12.32%
Stockton | CA | 95205-7891 |  | 2013-09-25 | 2013-09-25 12:40 | 2013-09-25 12:49 | BRYANT - 561CJ042-F | 93 | -14.9 | Yes | Yes | 22.9 | 18.3 | 4.6 | 6FFE1831BE054914A236A3E2B3E01C9E |  | R22 | TXV |  | -16.02% | 1.1602 | 4.487% |  |  |  |  | TXV |  |  | -16.02%
Stockton | CA | 95212-2872 |  | 2013-09-23 | 2013-09-23 10:34 | 2013-09-23 10:53 | CARRIER - 38CKC060360 | 131 | 4.8 | Yes | Yes | 22.2 | 18 | 4.3 | 431CD3F0E2104560833D3BCD90EB64F6 |  | R22 | TXV |  | 3.664% | 0.96336 | 7.042% | [5 empty] | TXV | 3.664%
Stockton | CA | 95212-3541 |  | 2013-09-23 | 2013-09-23 14:27 | 2013-09-23 14:52 | GOODMAN - CLJ42-1A | 135 | 21 | Yes | Yes | 21.5 | 18.6 | 2.9 | 12BFB73C263540F0BA1DBE3F2B38D6A7 |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Lathrop | CA | 95330-9204 |  | 2013-09-18 | 2013-09-18 13:21 | 2013-09-18 13:43 | CARRIER - 38CMC060 | 160 | 8 | Yes | Yes | 18.5 | 19.3 | -0.8 | DBA4DA211484435DAE13EB170A523914 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Sonora | CA | 95370-7504 |  | 2013-10-14 | 2013-10-14 16:55 | 2013-10-14 16:55 | PAYNE - PA13NR060-E | 184 | 0 | Yes | Yes | 25.4 | 19.9 | 5.5 | 0280B140389F4557A7E7B465BABC92E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6318 |  | 2013-09-17 | 2013-09-17 09:42 | 2013-09-17 10:18 | YORK - H2RC048S06A | 120 | 4 | Yes | Yes | 25.2 | 19.3 | 5.9 | 44F5C18BC00F407BB0D6D2E4A1B61556 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Manteca | CA | 95336-3126 |  | 2013-09-24 | 2013-09-24 10:40 | 2013-09-24 11:09 | YORK - D5YS024N03206A | 70 | 3.3 | Yes | Yes | 23.3 | 18.2 | 5.1 | DC1A296C5F114952AE3C75031098D579 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | Non-TXV | 4.714%
Manteca | CA | 95336-2839 |  | 2013-09-20 | 2013-09-20 11:09 | 2013-09-20 11:39 | GOODMAN - CKL24-1K | 76 | 2.4 | Yes | Yes | 19.2 | 18.2 | 1 | 1C2C459DBFC64F7D93FF85262B53764A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Manteca | CA | 95337-6023 |  | 2013-09-19 | 2013-09-19 12:47 | 2013-09-19 13:07 | GE - BT936A100A0 | 48 | 9.2 | Yes | Yes | 17.9 | 18.5 | -0.6 | 70F46153B2EE4FDF961398092800BA06 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.17% | 0.80833 | 36.83% | [5 empty] | Non-TXV | 19.17%
Stockton | CA | 95210-1484 |  | 2013-09-18 | 2013-09-18 15:26 | 2013-09-18 15:50 | LENNOX - UNK | 96 | 5.1 | Yes | Yes | 19.2 | 19 | 0.2 | 82F97B58E4104C02BA1F43ED720B4948 |  | R22 | TXV |  | 5.312% | 0.94688 | 10.21% | [5 empty] | TXV | 5.312%
Colfax | CA | 95713-8806 |  | 2013-09-25 | 2013-09-25 12:55 | 2013-09-25 13:19 | RUUD - URKA-A030JK08X | 54 | 14.3 | Yes | Yes | 24.7 | 20.6 | 4.1 | 2901B49B2C074C0DACFEBCD89F900178 |  | R22 | Non-TXV |  | 26.48% | 0.73519 | 50.89% | [5 empty] | Non-TXV | 26.48%
Tracy | CA | 95376-7772 |  | 2013-10-01 | 2013-10-01 10:55 | 2013-10-01 11:20 | RHEEM - UNK | 150 | 4.9 | Yes | Yes | 20.3 | 17.7 | 2.6 | 06155ABD04294AFF97D695A1968131C7 |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.278% | [5 empty] | Non-TXV | 3.267%
Stockton | CA | 95204-4916 |  | 2013-10-01 | 2013-10-01 14:22 | 2013-10-01 14:39 | YORK - D1NP030N05606A | 73 | 5.2 | Yes | Yes | 21.3 | 17.1 | 4.2 | 9528B39CF02D403F879211DD730FA312 |  | R22 | Non-TXV |  | 7.123% | 0.92877 | 13.69% | [5 empty] | Non-TXV | 7.123%
Stockton | CA | 95204-5207 |  | 2013-10-04 | 2013-10-04 14:10 | 2013-10-04 14:30 | GE - BTD736100B0 | 88 | 14.3 | Yes | Yes | 24.9 | 20.1 | 4.8 | D9A0B76C456D4F2F82972D82CF3FEA3D |  | R22 | Non-TXV |  | 16.25% | 0.8375 | 31.23% | [5 empty] | Non-TXV | 16.25%
Parlier | CA | 93648-2019 |  | 2013-09-25 | 2013-09-25 18:51 | 2013-09-25 21:27 | LENNOX - 12GCS042X-75-3PA | 133 | 8.3 | Yes | Yes | 16.5 | 19.3 | -2.8 | 8A1EBB6DE801495EBFA7604896ED3E62 |  | R22 | Non-TXV |  | 6.241% | 0.93759 | 11.99% | [5 empty] | Non-TXV | 6.241%
Fresno | CA | 93727-7940 |  | 2013-09-30 | 2013-09-30 15:28 | 2013-09-30 15:29 | BDP - 588ANW036060ADAF | 69 | 3.5 | Yes | Yes | 24.5 | 20.9 | 3.6 | F1191A0A5C7C400680334ED016C635EE |  | R22 | Non-TXV |  | 5.072% | 0.94928 | 9.748% | [5 empty] | Non-TXV | 5.072%
Ripon | CA | 95366-3301 |  | 2013-09-30 | 2013-09-30 15:52 | 2013-09-30 16:45 | OTHER - TZAA-348-2A757 | 85 | 2.6 | Yes | Yes | 20.3 | 19.3 | 1.1 | DC7FD4428B864C798962E752F24CAAA1 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93703-4353 |  | 2013-09-27 | 2013-09-27 12:30 | 2013-09-27 12:34 | DAY & NIGHT - 7777UNK | 54 | 3.7 | Yes | Yes | 16.8 | 19.1 | -2.3 | FEACD3D2D92147128C32A882211B87FC |  | R22 | Non-TXV |  | 6.852% | 0.93148 | 13.17% | [5 empty] | Non-TXV | 6.852%
Willows | CA | 95988-3022 |  | 2013-10-10 | 2013-10-10 12:23 | 2013-10-10 13:00 | DUCANE - SG12B48100 | 116 | 6.1 | Yes | Yes | 22.9 | 21.2 | 1.7 | 20E30642A2D044EB87C15694CB4B13A4 |  | R22 | Non-TXV |  | 5.259% | 0.94741 | 10.11% | [5 empty] | Non-TXV | 5.259%
Fresno | CA | 93727-7631 |  | 2013-09-30 | 2013-09-30 11:25 | 2013-09-30 11:29 | OTHER - DAYP-F036N070A | 108 | 4.6 | Yes | Yes | 16.9 | 18.8 | -1.9 | 4B9B763A1CF54165A398B635C9641419 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Lathrop | CA | 95330-9461 |  | 2013-09-27 | 2013-09-27 12:49 | 2013-09-27 13:10 | RUUD - UAFD-030JAS | 69 | 6.3 | Yes | Yes | 23.1 | 20.2 | 3 | F8AD84E008204FDFBB94624FB4B814CA |  | R22 | Non-TXV |  | 9.13% | 0.9087 | 17.55% | [5 empty] | Non-TXV | 9.13%
Parlier | CA | 93648-2338 |  | 2013-09-27 | 2013-09-27 17:01 | 2013-09-27 17:21 | CONCORD - CCU10A24A-1 | 50 | 6.1 | Yes | Yes | 17.7 | 19.9 | -2.2 | EB7CB45499BE4D49ABA5AB460EA33BB3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.2% | 0.878 | 23.45% | [5 empty] | Non-TXV | 12.2%
Tracy | CA | 95376-4701 |  | 2013-10-01 | 2013-10-01 11:21 | 2013-10-01 11:41 | RUUD - UAKA048JAZ | 105 | 4.8 | Yes | Yes | 19.4 | 17.7 | 1.7 | 174C0B7B282243C7B7C5CFAD56089272 |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Fresno | CA | 93720-2778 |  | 2013-10-04 | 2013-10-04 13:06 | 2013-10-04 13:07 | DAY & NIGHT - 7777UNK | 90 | 3.7 | Yes | Yes | 21.8 | 19.7 | 2.1 | C604818448DA450B9F3733199D56EAF2 |  | R22 | Non-TXV |  | 4.111% | 0.95889 | 7.901% | [5 empty] | Non-TXV | 4.111%
Chico | CA | 95926-4679 |  | 2013-09-27 | 2013-09-27 11:12 | 2013-09-27 11:28 | BRYANT - 574DNW0240400NA | 100 | 3.6 | Yes | Yes | 22 | 20.1 | 1.9 | 8E77A945A3944E8DBE0363C5550098AA |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Fresno | CA | 93704-6227 |  | 2013-10-21 | 2013-10-21 13:15 | 2013-10-21 13:47 | CARRIER - 48GS-24060301 | 53 | 3.3 | Yes | Yes | 19 | 21.8 | -2.8 | 95388717C6464182898AAC25F5B8D728 |  | R22 | Non-TXV |  | 6.226% | 0.93774 | 11.97% | [5 empty] | Non-TXV | 6.226%
Stockton | CA | 95204-3939 |  | 2013-10-10 | 2013-10-10 14:42 | 2013-10-10 15:00 | DAY & NIGHT - 585HJ024040 | 68 | 2.2 | Yes | Yes | 23.8 | 19.7 | 4.2 | 6A28117A8291473FA80BD68A4275FC08 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Stockton | CA | 95215-1502 |  | 2013-09-27 | 2013-09-27 10:48 | 2013-09-27 11:05 | TRANE - 2YCC3036A1075AA | 82 | -4.8 | Yes | Yes | 20.2 | 18.2 | 2 | BF5EA02C43204CFDB6A8B6C66E3F9D28 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Stockton | CA | 95206-2894 |  | 2013-09-26 | 2013-09-26 13:08 | 2013-09-26 13:34 | UNK - UNK | 85 | 6 | Yes | Yes | 18.6 | 17.1 | 1.5 | 2EA8BFAE3F08488684CC8A15CFABD6AA |  |  |  |  | 7.059% | 0.92941 | 13.57% | [5 empty] | 0 | 7.059%
Coarsegold | CA | 93614-9002 |  | 2013-10-18 | 2013-10-18 10:27 | 2013-10-18 10:31 | CARRIER - 48SS048080311 | 101 | 9.4 | Yes | Yes | 23.6 | 18.5 | 5.2 | 4D8303696A9D4181B98EE2291E7857EC |  | R22 | Non-TXV |  | 9.307% | 0.90693 | 17.89% | [5 empty] | Non-TXV | 9.307%
Stockton | CA | 95210-3136 |  | 2013-10-15 | 2013-10-15 11:23 | 2013-10-15 11:43 | PAYNE - P719030060AAAA | 55 | 3 | Yes | Yes | 20.5 | 17.2 | 3.3 | A3E7B4F198944F48B06E8AE812A9B455 |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Los Banos | CA | 93635-3148 |  | 2013-09-30 | 2013-09-30 10:48 | 2013-09-30 10:49 | CARRIER - 591ANX048000ACAA | 128 | 12.3 | Yes | Yes | 21.2 | 17.2 | 4 | 2E397661F1A8415880691F7D390D4F0A |  | R22 | Non-TXV |  | 9.609% | 0.90391 | 18.47% | [5 empty] | Non-TXV | 9.609%
Tracy | CA | 95376-3345 |  | 2013-10-04 | 2013-10-04 09:49 | 2013-10-04 10:07 | PAYNE - PA12NA036-A | 98 | 4.4 | Yes | Yes | 26.9 | 20.9 | 6 | 930014B08F934A5289FFF72F3C084C74 |  | R22 | TXV |  | 4.49% | 0.9551 | 8.628% | [5 empty] | TXV | 4.49%
Tracy | CA | 95376-1324 |  | 2013-09-27 | 2013-09-27 12:06 | 2013-09-27 12:35 | DAY & NIGHT - 591ANX036 | 95 | 3.1 | Yes | Yes | 22 | 17.7 | 4.3 | CD91710B36864CA1ACD80651F3592370 |  | R22 | Non-TXV |  | 3.263% | 0.96737 | 6.271% | [5 empty] | Non-TXV | 3.263%
Stockton | CA | 95205-2586 |  | 2013-09-27 | 2013-09-27 09:42 | 2013-09-27 09:47 | GOODMAN - UNK | 160 | 18.1 | Yes | Yes | 22.4 | 18.6 | 3.9 | 862B6CA31097443DA4913230915F627B |  | R22 | TXV |  | 11.31% | 0.88687 | 21.74% | [5 empty] | TXV | 11.31%
Fresno | CA | 93722-6351 |  | 2013-10-03 | 2013-10-03 14:14 | 2013-10-03 14:16 | DAY & NIGHT - 7777UNK | 80 | 4 | Yes | Yes | 21.4 | 20.1 | 1.3 | 4C97A55BC8DD480AB39A05D3BAEA3856 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93727-3660 |  | 2013-09-24 | 2013-09-24 11:00 | 2013-09-24 11:01 | LENNOX - 12GCS042X753PA | 133 | 10.2 | Yes | Yes | 26.2 | 20.4 | 5.8 | 54668D1735E549BF9E516B4B9B84AB85 |  | R22 | Non-TXV |  | 7.669% | 0.92331 | 14.74% | [5 empty] | Non-TXV | 7.669%
Stockton | CA | 95204-3409 |  | 2013-09-30 | 2013-09-30 13:47 | 2013-09-30 14:01 | TRANE - YCC036F1MOBF | 83 | 5.1 | Yes | Yes | 20.9 | 18.9 | 2 | 82A95CAB5FDD46C586D07DE36A603B22 |  | R22 | Non-TXV |  | 6.145% | 0.93855 | 11.81% | [5 empty] | Non-TXV | 6.145%
Chico | CA | 95926-3143 |  | 2013-09-26 | 2013-09-26 17:24 | 2013-09-26 17:41 | LENNOX - 12GCS030X-75-3PA | 85 | 3.8 | Yes | Yes | 24 | 18.7 | 5.3 | 9AA7D4D6E8DE44B4A9C817FF3E1AF1DA |  | R22 | TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | TXV | 4.471%
Tracy | CA | 95376-6703 |  | 2013-09-27 | 2013-09-27 14:53 | 2013-09-30 09:02 | RHEEM - UAMA036JBZ | 100 | 6.7 | Yes | Yes | 20.5 | 18.2 | 2.3 | 1CD425C42055461EA50AC4148498275A |  | R22 | Non-TXV |  | 6.7% | 0.933 | 12.88% | [5 empty] | Non-TXV | 6.7%
Chico | CA | 95973-7249 |  | 2013-09-25 | 2013-09-25 11:54 | 2013-09-25 12:20 | LENNOX - HS22-461U-2P | 133 | 8.6 | Yes | Yes | 25 | 19.9 | 5.1 | A11D9BA02A2F4DB18D580459A9802FD6 |  | R22 | TXV |  | 6.466% | 0.93534 | 12.43% | [5 empty] | TXV | 6.466%
Stockton | CA | 95205-2725 |  | 2013-09-27 | 2013-09-27 11:55 | 2013-09-27 12:12 | OTHER - HC36D1VAR | 135 | 15.8 | Yes | Yes | 16.4 | 17.3 | -0.9 | 68FF8162DD2140DBBE35AB33B9F220F9 |  | R22 | Non-TXV |  | 11.7% | 0.88296 | 22.49% | [5 empty] | Non-TXV | 11.7%
Fresno | CA | 93722-2566 |  | 2013-09-20 | 2013-09-20 21:39 | 2013-09-20 21:42 | YORK - H4DE048S06A | 112 | 3.7 | Yes | Yes | 18.2 | 18.1 | 0.1 | A849E16D60F7472FBD4F5FF39D498FEA |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Fresno | CA | 93727-3659 |  | 2013-09-24 | 2013-09-24 10:35 | 2013-09-24 10:37 | LENNOX - 10GCS036X753PA | 58 | 5.9 | Yes | Yes | 22.5 | 19.9 | 2.6 | 6CA6DC92C3534C87A29276AAD0A3E87D |  | R22 | Non-TXV |  | 10.17% | 0.89828 | 19.55% | [5 empty] | Non-TXV | 10.17%
Stockton | CA | 95204-4823 |  | 2013-10-01 | 2013-10-01 15:01 | 2013-10-01 15:28 | OTHER - NAC024AKB2 | 60 | 5.6 | Yes | Yes | 24.1 | 19.8 | 4.3 | A82B8CA620FE454FAD72D16FB41683BE |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Fresno | CA | 93722-8015 |  | 2013-10-03 | 2013-10-03 14:20 | 2013-10-03 14:22 | YORK - H2RC042S06HG | 109 | 9.9 | Yes | Yes | 20.4 | 17.6 | 2.8 | A40222859E764BAB8708FD05DDA12245 |  | R22 | Non-TXV |  | 9.083% | 0.90917 | 17.45% | [5 empty] | Non-TXV | 9.083%
Fresno | CA | 93722-3602 |  | 2013-10-01 | 2013-10-01 13:07 | 2013-10-01 13:09 | CARRIER - 7777UNK | 96 | 3.2 | Yes | Yes | 21.3 | 19.6 | 1.7 | E610088F1AD946FABCD3BB777C744E48 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93705-3728 |  | 2013-10-04 | 2013-10-04 12:54 | 2013-10-04 12:56 | BARD - 585JW018040ABAC | 55 | 7.6 | Yes | Yes | 28 | 22.8 | 5.2 | B277D4E548E54F7A9603B6B443A9FC92 |  | R22 | Non-TXV |  | 13.82% | 0.86182 | 26.56% | [5 empty] | Non-TXV | 13.82%
Fresno | CA | 93705-3728 |  | 2013-10-04 | 2013-10-04 12:57 | 2013-10-04 13:02 | BARD - 585JW018040ABAC | 55 | 7.9 | Yes | Yes | 27.6 | 21.8 | 5.8 | D26A74CEB967461D817D16B70031AD63 |  | R22 | Non-TXV |  | 14.36% | 0.85636 | 27.6% | [5 empty] | Non-TXV | 14.36%
Stockton | CA | 95207-5427 |  | 2013-09-26 | 2013-09-26 12:41 | 2013-09-26 12:59 | HEIL - CA5536VKC1 | 74 | 9.6 | Yes | Yes | 24.4 | 18.8 | 5.6 | D612B3963CCD423B8C1B7036A5A78EF4 |  | R22 | Non-TXV |  | 12.97% | 0.87027 | 24.93% | [5 empty] | Non-TXV | 12.97%
Stockton | CA | 95210-2609 |  | 2013-09-19 | 2013-09-19 13:44 | 2013-09-19 14:00 | YORK - TCGD36S21S2HA | 63 | -15.5 | Yes | Yes | 18.3 | 18.4 | -0.1 | AB03E3A3EE904651AC4BBFF1302B8BD7 |  | R22 | TXV |  | -24.6% | 1.246 | 6.89% |  |  |  |  | TXV |  |  | -24.6%
Woodbridge | CA | 95258-9146 |  | 2013-10-11 | 2013-10-11 11:25 | 2013-10-11 11:52 | RUUD - UAFD-030JAS | 69 | 2.2 | Yes | Yes | 17.5 | 18.7 | -1.2 | A8AC15A699964C728330CEADC507AE0D |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Fresno | CA | 93727-3653 |  | 2013-09-27 | 2013-09-27 10:47 | 2013-09-27 10:49 | LENNOX - 10GCS036X753PA | 58 | 4.1 | Yes | Yes | 23.7 | 18.3 | 5.4 | 54A86C361B63408C9C3E81833E5201DD |  | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Rocklin | CA | 95765-5280 |  | 2013-09-20 | 2013-09-20 15:25 | 2013-09-20 15:25 | BRYANT - 563CN048-D | 167 | 0 | Yes | Yes | 19.2 | 21.4 | -2.2 | E360965ED490454093032519DB6AC414 |  | R22 | TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-3033 |  | 2013-10-01 | 2013-10-01 14:47 | 2013-10-01 15:48 | OTHER - 60R24A1NA | 48 | 3.2 | Yes | Yes | 17.2 | 19.9 | -2.7 | E1901C51D2AA41488725B8AE47737E0A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93727-0000 |  | 2013-10-01 | 2013-10-01 11:48 | 2013-10-01 11:50 | RHEEM - RRMA0A048JK10X | 115 | 6.4 | Yes | Yes | 23.4 | 20.4 | 3 | 96F160B33B214725A162A42E07FD4AA1 |  | R22 | Non-TXV |  | 5.565% | 0.94435 | 10.7% | [5 empty] | Non-TXV | 5.565%
Clovis | CA | 93611-6933 |  | 2013-09-24 | 2013-09-24 13:49 | 2013-09-24 14:51 | DAY & NIGHT - 598ANO36-B | 194 | 27.7 | Yes | Yes | 18 | 20.1 | -2.1 | 5AE8D44B340F4F0294A9EC993A5F2BBE |  | R22 | Non-TXV |  | 14.28% | 0.85722 | 27.44% | [5 empty] | Non-TXV | 14.28%
Ripon | CA | 95366-2034 |  | 2013-09-26 | 2013-09-26 15:32 | 2013-09-26 15:49 | PAYNE - PA12NA060-G | 181 | 5.4 | Yes | Yes | 23.4 | 20.9 | 2.5 | 9185D17CCC5C40BC9AF6E1A2B224F401 |  | R22 | Non-TXV |  | 2.983% | 0.97017 | 5.733% | [5 empty] | Non-TXV | 2.983%
Fresno | CA | 93720-2781 |  | 2013-10-08 | 2013-10-08 15:29 | 2013-10-08 15:59 | DAY & NIGHT - N/A | 85 | 16.5 | Yes | Yes | 18.5 | 20.7 | -2.2 | 6FED3065C5DE4376A965184FE212D687 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 19.41% | 0.80588 | 37.31% | [5 empty] | Non-TXV | 19.41%
Fresno | CA | 93720-2781 |  | 2013-10-08 | 2013-10-08 16:01 | 2013-10-08 16:55 | DAY & NIGHT - N/A | 85 | 3.6 | Yes | Yes | 22 | 20.4 | 1.6 | 146A93A1C80F4272B8ADD6D1D5AB3EDD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Fresno | CA | 93710-6809 |  | 2013-09-27 | 2013-09-27 09:59 | 2013-09-27 10:19 | YORK - D2NP048N09006NXA | 132 | 19.9 | Yes | Yes | 26 | 21.1 | 4.9 | 2831C04ACD864B1E927B1AB42A7A4060 | Add refrigerant: 15.9 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 15.08% | 0.84924 | 28.97% | [5 empty] | Non-TXV | 15.08%
Atwater | CA | 95301-3859 |  | 2013-10-10 | 2013-10-10 10:15 | 2013-10-10 10:18 | OTHER - RRMAA030JK08X | 80 | 6.2 | Yes | Yes | 23.7 | 18.2 | 5.5 | 2D6F1A0E5FBA44A2ACEDAB458E596412 |  | R22 | Non-TXV |  | 7.75% | 0.9225 | 14.89% | [5 empty] | Non-TXV | 7.75%
Lathrop | CA | 95330-9163 |  | 2013-10-16 | 2013-10-16 11:02 | 2013-10-16 11:20 | GOODMAN - CKJ42-1AB | 105 | 4.4 | Yes | Yes | 18.5 | 17.7 | 0.8 | 6CCB3CBC9A274664B39FEE58366B7F47 |  | R22 | Non-TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | Non-TXV | 4.19%
Stockton | CA | 95206-6373 |  | 2013-10-04 | 2013-10-04 16:33 | 2013-10-04 16:58 | CARRIER - 38CKC042340 | 80 | 15.4 | Yes | Yes | 24.3 | 22.8 | 1.5 | BC2FB493A92D4A3A85A9F5053E35B9D5 |  | R22 | Non-TXV |  | 19.25% | 0.8075 | 36.99% | [5 empty] | Non-TXV | 19.25%
Fresno | CA | 93727-2438 |  | 2013-09-25 | 2013-09-25 10:43 | 2013-09-25 11:07 | RHEEM - RRMA-A042JK08X | 114 | 9 | Yes | Yes | 21.5 | 19.9 | 1.6 | 44E928D3F91B48EEB730FAE97105E77F |  | R22 | Non-TXV |  | 7.895% | 0.92105 | 15.17% | [5 empty] | Non-TXV | 7.895%
Fresno | CA | 93720-0235 |  | 2013-09-24 | 2013-09-24 14:55 | 2013-09-24 15:26 | YORK - H1DH0360S06A | 127 | 8.9 | Yes | Yes | 17.5 | 20.4 | -2.9 | 977D90403C2246B4B3AB60995C1C579B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.008% | 0.92992 | 13.47% | [5 empty] | Non-TXV | 7.008%
Fowler | CA | 93625-9646 |  | 2013-09-19 | 2013-09-19 14:33 | 2013-09-19 16:07 | PAYNE - N/A | 120 | 6.8 | Yes | Yes | 19.4 | 20.4 | -1 | CAE24AF5E8A2446DB30361B3664F98C7 |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Fresno | CA | 93710-3606 |  | 2013-09-23 | 2013-09-23 14:16 | 2013-09-23 14:36 | YORK - DCYZ-F036N070A | 64 | 3.8 | Yes | Yes | 19 | 21 | -2 | 1A41C6047AE54C3B8B16B8FC44F278EB |  | R410A | TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | TXV | 5.938%
Fresno | CA | 93703-2207 |  | 2013-10-21 | 2013-10-21 17:52 | 2013-10-21 17:52 | YORK - DDYZ-F048N080C | 68 | 0 | Yes | Yes | 26 | 20.4 | 5.6 | 9DE14CAAF5D64E9AA0D8D6CE8E87A7D0 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5148 |  | 2013-09-30 | 2013-09-30 16:17 | 2013-09-30 16:36 | DAY & NIGHT - 591ANX048000ACAA | 128 | 5.2 | Yes | Yes | 23 | 19.3 | 3.7 | DBE1FC24401C4834BD8BB1EAAA1C547F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Clovis | CA | 93612-4623 |  | 2013-09-24 | 2013-09-24 09:38 | 2013-09-24 10:45 | BRYANT - 582ANW030060AAAD | 55 | 4.7 | Yes | Yes | 21 | 20.3 | 0.7 | 2F0760F8BF6043BE988361487627A744 |  | R22 | Non-TXV |  | 8.545% | 0.91455 | 16.42% | [5 empty] | Non-TXV | 8.545%
Stockton | CA | 95204-4130 |  | 2013-10-01 | 2013-10-01 11:03 | 2013-10-01 11:25 | PAYNE - 585CJO42100 | 104 | 9.7 | Yes | Yes | 23.3 | 18 | 5.3 | C9DACABC755B42B28821C761C4CB74BD |  | R22 | Non-TXV |  | 9.327% | 0.90673 | 17.92% | [5 empty] | Non-TXV | 9.327%
Placerville | CA | 95667-8333 |  | 2013-10-01 | 2013-10-01 11:13 | 2013-10-01 11:13 | CARRIER - 48SS-04808031-- | 104 | 0 | Yes | Yes | 25.4 | 20.4 | 5 | CEA24EDC86DD41A1A3963BC0BF34528B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-2145 |  | 2013-09-27 | 2013-09-27 12:47 | 2013-09-27 13:04 | GOODMAN - CE301HB | 72 | 3.8 | Yes | Yes | 21.3 | 18.6 | 2.8 | 9F1298168DBB45A79B325D0E0C367154 |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Selma | CA | 93662-4906 |  | 2013-10-04 | 2013-10-04 14:52 | 2013-10-04 15:13 | LENNOX - 13ACC-042-230-2PA | 123 | 3.8 | Yes | Yes | 19 | 20.6 | -1.6 | 22E766635D83407AAB8DAB8C40ECEBCC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.089% | 0.96911 | 5.937% | [5 empty] | Non-TXV | 3.089%
Fresno | CA | 93710-6118 |  | 2013-09-20 | 2013-09-20 15:07 | 2013-09-20 15:09 | TRANE - YCC036F1M0AA | 89 | 3 | Yes | Yes | 18.6 | 20.4 | -1.8 | FD7EBCD859A0437E93BF45025AFD1470 |  | R22 | Non-TXV |  | 3.371% | 0.96629 | 6.478% | [5 empty] | Non-TXV | 3.371%
Fresno | CA | 93704-5908 |  | 2013-09-19 | 2013-09-19 15:00 | 2013-09-19 15:02 | YORK - DAYHF042N080C | 94 | 17.5 | Yes | Yes | 27 | 21.4 | 5.6 | 8B697E5F60954AD8B30046E7704AAFEA |  | R22 | Non-TXV |  | 18.62% | 0.81383 | 35.78% | [5 empty] | Non-TXV | 18.62%
Penn Valley | CA | 95946-9418 |  | 2013-09-25 | 2013-09-25 10:44 | 2013-09-25 11:48 | PAYNE - 588ANW048120AEAG | 104 | 11.7 | Yes | Yes | 25.3 | 20.6 | 4.7 | 5E9D1F6881154E09B2F8586540179895 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Yuba City | CA | 95993-0000 |  | 2013-10-23 | 2013-10-23 12:23 | 2013-10-23 12:23 | LENNOX - 13ACD-060-230-02 | 214 | 0 | Yes | Yes | 25 | 23.1 | 1.9 | 9546CB6F6FAA46EAA57923480AD07D29 |  | R22 | TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3124 |  | 2013-10-04 | 2013-10-04 14:21 | 2013-10-04 14:23 | GOODMAN - CK301A | 76 | 7.2 | Yes | Yes | 25.3 | 20.4 | 4.9 | 3A8C72B1D40347A19140C6AE16DBE34D |  | R22 | Non-TXV |  | 9.474% | 0.90526 | 18.21% | [5 empty] | Non-TXV | 9.474%
Fresno | CA | 93727-8713 |  | 2013-10-01 | 2013-10-01 10:45 | 2013-10-01 11:10 | YORK - D1NA030N03606C | 76 | 3.8 | Yes | Yes | 19.3 | 20.7 | -1.4 | 272EC26F845D4C76BEBB354219976C36 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93728-1038 |  | 2013-10-02 | 2013-10-02 11:20 | 2013-10-02 11:22 | DAY & NIGHT - 585EJO30050 | 58 | 3 | Yes | Yes | 22.2 | 19.8 | 2.4 | DF19BB37B068420883E732F98B13D021 |  | R22 | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Fresno | CA | 93722-2567 |  | 2013-10-02 | 2013-10-02 09:27 | 2013-10-02 09:28 | LENNOX - 12ACB424P | 125 | 7.3 | Yes | Yes | 20.9 | 16.5 | 4.4 | FC89AA1534CB493AAF8FCBA3893B4C10 |  | R22 | Non-TXV |  | 5.84% | 0.9416 | 11.22% | [5 empty] | Non-TXV | 5.84%
Merced | CA | 95340-9484 |  | 2013-09-25 | 2013-09-25 07:21 | 2013-09-25 07:22 | RHEEM - 7777UNK | 80 | 3.6 | Yes | Yes | 20.5 | 19.9 | 0.6 | 7DE0BF864BF84919A986B5439F4067E2 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Fresno | CA | 93703-4350 |  | 2013-10-10 | 2013-10-10 09:54 | 2013-10-10 10:30 | GOODMAN - N/A | 54 | 6.1 | Yes | Yes | 26 | 21.2 | 4.8 | 40FBBD38D25140769F0A7492132D3D78 |  | R22 | Non-TXV |  | 11.3% | 0.88704 | 21.71% | [5 empty] | Non-TXV | 11.3%
Stockton | CA | 95205-2660 |  | 2013-09-27 | 2013-09-27 11:14 | 2013-09-27 11:27 | CARRIER - 38EZG048300 | 125 | 7.4 | Yes | Yes | 20.3 | 17.7 | 2.6 | 557B9E11A369435A83B7140CFF4CE16B |  | R410A | TXV |  | 5.92% | 0.9408 | 11.38% | [5 empty] | TXV | 5.92%
Tracy | CA | 95376-5616 |  | 2013-09-27 | 2013-09-27 14:14 | 2013-09-27 14:30 | BRYANT - 563CN030=A | 105 | 3.1 | Yes | Yes | 18 | 15.9 | 2.1 | 1425CC280ED647E287A8D7826C0AB55B |  | R22 | Non-TXV |  | 2.952% | 0.97048 | 5.674% | [5 empty] | Non-TXV | 2.952%
Orange Cove | CA | 93646-2122 |  | 2013-10-02 | 2013-10-02 11:03 | 2013-10-02 11:04 | YORK - D1NH036N03606C | 108 | 6.4 | Yes | Yes | 25.1 | 21.1 | 4 | 95301770813B4D8B83CD8CB77ED0BD62 |  | R22 | Non-TXV |  | 5.926% | 0.94074 | 11.39% | [5 empty] | Non-TXV | 5.926%
Los Banos | CA | 93635-3283 |  | 2013-09-30 | 2013-09-30 14:44 | 2013-09-30 14:46 | CARRIER - 584BNW024040AABE | 58 | 7.9 | Yes | Yes | 23.1 | 22 | 1.1 | 6FEF72633EAA4B1999EDCA88B4279A94 |  | R22 | Non-TXV |  | 13.62% | 0.86379 | 26.18% | [5 empty] | Non-TXV | 13.62%
Stockton | CA | 95205-2725 |  | 2013-09-30 | 2013-09-30 11:13 | 2013-09-30 11:40 | OTHER - HC36D1VAR | 134 | 4 | Yes | Yes | 19.5 | 17.9 | 1.6 | 283F26DC33234F1D9ACD558B8D9637D8 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Merced | CA | 95341-8205 |  | 2013-09-25 | 2013-09-25 07:18 | 2013-09-25 07:19 | ARCOAIRE - HAC036AKA5 | 80 | 2.7 | Yes | Yes | 18.8 | 19.3 | -0.5 | 021D8278B84B43B98756693EDD47A8AE |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Stockton | CA | 95206-2481 |  | 2013-09-30 | 2013-09-30 12:14 | 2013-09-30 12:41 | BRYANT - 561CJ024-E | 54 | 20.2 | Yes | Yes | 23 | 19.5 | 3.5 | E7ACCCDDD165478B97EEA03135119372 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 37.41% | 0.62593 | 71.89% | [5 empty] | Non-TXV | 37.41%
Magalia | CA | 95954-9603 |  | 2013-10-01 | 2013-10-01 11:34 | 2013-10-01 11:58 | WEATHER KING - 43AJA36A01 | 108 | 3.9 | Yes | Yes | 16.1 | 18.3 | -2.2 | B32D40D13C474B8EAC06145B89A38E15 |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Merced | CA | 95340-0937 |  | 2013-09-20 | 2013-09-20 13:57 | 2013-09-20 13:58 | RHEEM - RRKAA042JK08X | 69 | 8.6 | Yes | Yes | 29.5 | 23.7 | 5.8 | 6DC5AF9BE9A24F4A955B21C09361DFD5 |  | R22 | Non-TXV |  | 12.46% | 0.87536 | 23.95% | [5 empty] | Non-TXV | 12.46%
Oroville | CA | 95965-3420 |  | 2013-10-02 | 2013-10-02 12:04 | 2013-10-02 12:34 | YORK - H2RA036S06G | 63 | 2.3 | Yes | Yes | 18 | 19.9 | -1.9 | 2E762AFAB4454CEDA6A71748B7809DA0 |  | R22 | TXV |  | 3.651% | 0.96349 | 7.016% | [5 empty] | TXV | 3.651%
Fresno | CA | 93727-3382 |  | 2013-09-24 | 2013-09-24 17:35 | 2013-09-24 19:07 | RHEEM - RRGE-05E24JKR | 50 | 3.8 | Yes | Yes | 23.3 | 20.4 | 2.9 | D3249017B60C42A8AC4AE38730120DFC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.6% | 0.924 | 14.61% | [5 empty] | Non-TXV | 7.6%
Stockton | CA | 95205-2944 |  | 2013-09-27 | 2013-09-27 13:58 | 2013-09-27 14:17 | RHEEM - RRMA-A048JK08X | 115 | 15.2 | Yes | Yes | 23.6 | 18 | 5.6 | 40C454598E5A40EC855488E8B1A52C5B |  | R22 | Non-TXV |  | 13.22% | 0.86783 | 25.4% | [5 empty] | Non-TXV | 13.22%
Stockton | CA | 95205-2944 |  | 2013-09-27 | 2013-09-27 14:24 | 2013-09-27 14:44 | RUUD - URGG-05024 | 54 | 9.3 | Yes | Yes | 18.7 | 17.4 | 1.4 | F26B850CB50C46A5930A97BFD3B75436 |  | R22 | Non-TXV |  | 17.22% | 0.82778 | 33.1% | [5 empty] | Non-TXV | 17.22%
Placerville | CA | 95667-9212 |  | 2013-09-19 | 2013-09-19 13:25 | 2013-09-19 13:47 | LENNOX - UNK | 84 | 14.6 | Yes | Yes | 21.1 | 20.4 | 0.7 | B440A305B27F4245A6ABA0029B3A53F5 |  | R22 | Non-TXV |  | 17.38% | 0.82619 | 33.4% | [5 empty] | Non-TXV | 17.38%
Fresno | CA | 93727-4011 |  | 2013-09-27 | 2013-09-27 11:34 | 2013-09-27 11:35 | GOODMAN - PGB024050 | 54 | 5 | Yes | Yes | 22.5 | 18.3 | 4.2 | D943B28A04F448DB9D87747B7A0F46A7 |  | R22 | Non-TXV |  | 9.259% | 0.90741 | 17.79% | [5 empty] | Non-TXV | 9.259%
Chico | CA | 95973-8205 |  | 2013-10-02 | 2013-10-02 10:29 | 2013-10-02 10:55 | YORK - 82CC024A6A | 50 | 8.1 | Yes | Yes | 20 | 21.7 | -1.7 | 031E5527369649519F8DE65308954B87 |  | R22 | Non-TXV |  | 16.2% | 0.838 | 31.13% | [5 empty] | Non-TXV | 16.2%
Placerville | CA | 95667-3418 |  | 2013-09-19 | 2013-09-19 15:01 | 2013-09-19 15:18 | WESTINGHOUSE - HP036DBW | 157 | 22.6 | Yes | Yes | 20.3 | 22.9 | -2.6 | 3D614B3BBA154E6D91DCA506ED0CE165 |  | R22 | Non-TXV |  | 14.39% | 0.85605 | 27.66% | [5 empty] | Non-TXV | 14.39%
Fresno | CA | 93722-2546 |  | 2013-10-01 | 2013-10-01 14:39 | 2013-10-01 14:41 | LENNOX - GCS26X-042-75-2PA | 133 | 4.7 | Yes | Yes | 18.3 | 20.9 | -2.6 | B881E2CBB8E94328B12D9989109E0BB4 |  | R22 | Non-TXV |  | 3.534% | 0.96466 | 6.791% | [5 empty] | Non-TXV | 3.534%
Loomis | CA | 95650-9092 |  | 2013-10-10 | 2013-10-10 12:51 | 2013-10-10 13:13 | GOODMAN - GPG13300701AB | 77 | 2.3 | Yes | Yes | 24 | 20.9 | 3.1 | B594B9AF753A44CD89D947E7F75FB16C |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Paradise | CA | 95969-6169 |  | 2013-09-26 | 2013-09-26 14:33 | 2013-09-26 15:08 | CARRIER - NA | 85 | 2.8 | Yes | Yes | 24.1 | 18.6 | 5.5 | A8FBA33E14214192B2DF120DFAC372B5 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fresno | CA | 93725-1668 |  | 2013-10-07 | 2013-10-07 14:02 | 2013-10-07 14:24 | CARRIER - 24ABA336A1131010 | 85 | -6 | Yes | Yes | 20.4 | 21 | -0.6 | 4180987A923C4B80A0669F15E5D9993A |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Paso Robles | CA | 93446-4039 |  | 2013-10-07 | 2013-10-07 15:01 | 2013-10-07 15:18 | CARRIER - 38EN030300 | 90 | 3.3 | Yes | Yes | 23.9 | 22.3 | 1.6 | 65D9A621438B4F20BDFA12EE19A83820 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Paradise | CA | 95969-2708 |  | 2013-10-18 | 2013-10-18 13:52 | 2013-10-18 14:11 | CARRIER - 38BR6048310 | 136 | 5 | Yes | Yes | 21.1 | 23.1 | -2 | 4376A49D6EC54435B75464A5C3CBC6E5 |  | R22 | TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | TXV | 3.676%
Merced | CA | 95341-9518 |  | 2013-10-01 | 2013-10-01 13:16 | 2013-10-01 13:18 | AIRE-FLO - YCC048F1HOBB | 128 | 14.2 | Yes | Yes | 23.8 | 21 | 2.8 | BEFCC18181C443678A216E32D3D557DA |  | R22 | Non-TXV |  | 11.09% | 0.88906 | 21.32% | [5 empty] | Non-TXV | 11.09%
Stockton | CA | 95212-2866 |  | 2013-09-27 | 2013-09-27 11:10 | 2013-09-27 11:10 | CARRIER - 38CKC060370 | 131 | 0 | Yes | Yes | 25.1 | 19.1 | 6 | EF11CE816C7846E7B7CEC217C0186C1F |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-1323 |  | 2013-10-03 | 2013-10-03 11:56 | 2013-10-03 12:16 | PAYNE - PA13NR042-H | 113 | 10.1 | Yes | Yes | 22.8 | 17.9 | 4.9 | 806C2F0CB3AC475BB804822E97D3E92D |  | R22 | Non-TXV |  | 8.938% | 0.91062 | 17.18% | [5 empty] | Non-TXV | 8.938%
Corning | CA | 96021-3633 |  | 2013-09-25 | 2013-09-25 13:07 | 2013-09-25 13:24 | GOODMAN - CKL36-1H | 71 | 6.6 | Yes | Yes | 18.5 | 21.5 | -3 | 35E306F74EEA479088FDD3AD7CE4858A |  | R22 | Non-TXV |  | 9.296% | 0.90704 | 17.86% | [5 empty] | Non-TXV | 9.296%
Paso Robles | CA | 93446-4443 |  | 2013-10-07 | 2013-10-07 13:07 | 2013-10-07 13:24 | RUUD - UACB-018JAZ | 28 | 3.2 | Yes | Yes | 18.4 | 20.1 | -1.7 | 5A22A0DA85524EDA8619776568BEB5E4 |  | R22 | Non-TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | Non-TXV | 11.43%
Escalon | CA | 95320-9648 |  | 2013-10-22 | 2013-10-22 12:42 | 2013-10-22 13:03 | HEIL - CA3024VKA2 | 66 | 2.3 | Yes | Yes | 17.6 | 19.1 | -1.5 | 8DC58D84FB82420CA9C9D9C3F7B9C16E |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Fresno | CA | 93726-6507 |  | 2013-09-23 | 2013-09-23 14:58 | 2013-09-23 14:58 | GOODMAN - GPG1336045M41CA | 108 | 0 | Yes | Yes | 25.5 | 20.4 | 5.1 | 1A99EB901475463195660EC8D31EAB76 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1339 |  | 2013-10-01 | 2013-10-01 15:52 | 2013-10-01 18:04 | COLEMAN - DRCS02416B | 80 | 5.6 | Yes | Yes | 21.1 | 19.7 | 1.4 | 9F6B353DE87B44D6953D4DDADC32AC50 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Merced | CA | 95348-3644 |  | 2013-10-01 | 2013-10-01 11:23 | 2013-10-01 11:25 | GOODMAN - PGB024050 | 54 | 5.3 | Yes | Yes | 22.6 | 19.4 | 3.2 | 40D829BF3A294080A9B8C4246D9C8E99 |  | R22 | Non-TXV |  | 9.815% | 0.90185 | 18.86% | [5 empty] | Non-TXV | 9.815%
Stockton | CA | 95203-3008 |  | 2013-09-30 | 2013-09-30 09:21 | 2013-09-30 09:41 | YORK - H2RA030S06G | 62 | 7.9 | Yes | Yes | 17.2 | 19.1 | -1.9 | DE570E443B4943F6A585BCC5F4EA5C85 |  | R22 | Non-TXV |  | 12.74% | 0.87258 | 24.49% | [5 empty] | Non-TXV | 12.74%
Clovis | CA | 93612-5897 |  | 2013-09-24 | 2013-09-24 12:09 | 2013-09-24 12:26 | CARRIER - 38BR042300 | 131 | 29 | Yes | Yes | 17.5 | 20.4 | -2.9 | 6BC3DFD13F9147A5BA7E80D5DFF389F6 |  | R22 | Non-TXV |  | 22.14% | 0.77863 | 42.54% | [5 empty] | Non-TXV | 22.14%
Stockton | CA | 95204-1507 |  | 2013-10-07 | 2013-10-07 13:10 | 2013-10-07 13:27 | DAY & NIGHT - UNK | 96 | 5 | Yes | Yes | 24.6 | 18.8 | 5.8 | 086B5CA680CC439E964EDF2BF3BB4E61 |  | R22 | Non-TXV |  | 5.208% | 0.94792 | 10.01% | [5 empty] | Non-TXV | 5.208%
San Mateo | CA | 94403-2920 |  | 2013-10-14 | 2013-10-14 12:44 | 2013-10-14 13:12 | GMC - CK36-1T | 76 | 3.5 | Yes | Yes | 22 | 20.4 | 1.6 | C1376F0B36CC44DCB79FA43CAF4CF8CC |  | R22 | Non-TXV |  | 4.605% | 0.95395 | 8.85% | [5 empty] | Non-TXV | 4.605%
Stockton | CA | 95206-6102 |  | 2013-10-02 | 2013-10-02 09:17 | 2013-10-02 09:36 | YORK - H1DB036S06B | 72 | 10.5 | Yes | Yes | 18.8 | 19.3 | -0.5 | DC75EBD2144B45F0B222416F87D4FA11 |  | R22 | Non-TXV |  | 14.58% | 0.85417 | 28.03% | [5 empty] | Non-TXV | 14.58%
Chico | CA | 95973-9189 |  | 2013-09-27 | 2013-09-27 14:46 | 2013-09-27 15:02 | BRYANT - 550AN042-F | 135 | 4.9 | Yes | Yes | 26 | 21.4 | 4.6 | 9D48495D2A2B42F3B1B67AEC3D04801B |  | R410A | TXV |  | 3.63% | 0.9637 | 6.975% | [5 empty] | TXV | 3.63%
Fresno | CA | 93725-1648 |  | 2013-10-09 | 2013-10-09 11:49 | 2013-10-09 12:33 | CARRIER - 24ABA342A310 | 105 | -9.9 | Yes | Yes | 21.1 | 17.7 | 3.4 | 0EF4C4E9CA9F49F881220369AF4E6F9E |  | R410A | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Fresno | CA | 93727-3039 |  | 2013-09-27 | 2013-09-27 13:02 | 2013-09-27 14:05 | GOODMAN - GPG10420701A | 88 | 16.5 | Yes | Yes | 19.5 | 20.7 | -1.2 | C81DF75D6DA74A17BD5A629C0EFD8E64 |  | R22 | Non-TXV |  | 18.75% | 0.8125 | 36.03% | [5 empty] | Non-TXV | 18.75%
Stockton | CA | 95206-6148 |  | 2013-10-04 | 2013-10-04 15:44 | 2013-10-04 16:11 | GOODMAN - CLJ36-1A | 109 | 27.2 | Yes | Yes | 26.7 | 20.9 | 5.8 | 00B78869AC9F4B139156E359F71DAF78 |  | R22 | Non-TXV |  | 24.95% | 0.75046 | 47.96% | [5 empty] | Non-TXV | 24.95%
Fresno | CA | 93705-2765 |  | 2013-10-04 | 2013-10-04 19:50 | 2013-10-04 19:54 | OTHER - AC024X1321A | 88 | 3.3 | Yes | Yes | 16.9 | 19.7 | -2.8 | 88DF815725A646CBAAE6EBC3D5A58C20 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95205-3603 |  | 2013-09-27 | 2013-09-27 12:34 | 2013-09-27 12:34 | GE - BTN930A100A0 | 54 | 0 | Yes | Yes | 18.1 | 19.1 | -1 | 2B98F5AFE37C48BAA3A065EAB97BE3C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-2751 |  | 2013-10-14 | 2013-10-14 14:06 | 2013-10-14 14:32 | RHEEM - RRKA-A030JK06X | 54 | 1.6 | Yes | Yes | 28 | 23.2 | 4.8 | 3DD4241D59E8496B8FF818C67A132D68 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95209-1533 |  | 2013-09-30 | 2013-09-30 11:17 | 2013-09-30 11:46 | WESTINGHOUSE - IE2024PAAON | 53 | 2.4 | Yes | Yes | 16.8 | 18.4 | -1.6 | 5A08E7286446429888DE2F1CA0085965 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.528% | 0.95472 | 8.702% | [5 empty] | Non-TXV | 4.528%
Merced | CA | 95341-7036 |  | 2013-10-01 | 2013-10-01 10:38 | 2013-10-01 10:39 | LENNOX - 13ACD03023001 | 85 | 10.7 | Yes | Yes | 24.9 | 19.7 | 5.2 | C11CBCBC36C04FB7A9BF387912DE6E6A |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Stockton | CA | 95205-4702 |  | 2013-10-09 | 2013-10-09 15:12 | 2013-10-09 15:29 | RHEEM - RRKA-A048JK10X | 78 | 8.9 | Yes | Yes | 23.3 | 19.9 | 3.4 | AD26E18B0E0C4412B2E40F3ABB227893 |  | R22 | Non-TXV |  | 11.41% | 0.8859 | 21.93% | [5 empty] | Non-TXV | 11.41%
Fresno | CA | 93722-5243 |  | 2013-10-09 | 2013-10-09 15:35 | 2013-10-09 16:08 | YORK - DINH036NO5606E | 108 | 3.5 | Yes | Yes | 20.6 | 17.2 | 3.4 | DB2640F428F94E80A916149B369ABDB3 |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Fresno | CA | 93725-0000 |  | 2013-10-08 | 2013-10-08 11:10 | 2013-10-08 11:30 | CARRIER - 24ABA442A300 | 170 | 8 | Yes | Yes | 19.7 | 18.3 | 1.4 | 1193B55D1DF44E1B8E74E2239A1D0093 |  | R410A | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Stockton | CA | 95210-3412 |  | 2013-09-30 | 2013-09-30 11:31 | 2013-09-30 11:52 | RHEEM - BRCS0241BD | 59 | 5.8 | Yes | Yes | 14.8 | 16.5 | -1.7 | CF85DD10E380428FAB1E2F62F954CDC0 |  | R22 | Non-TXV |  | 9.831% | 0.90169 | 18.89% | [5 empty] | Non-TXV | 9.831%
Los Banos | CA | 93635-2817 |  | 2013-10-10 | 2013-10-10 11:15 | 2013-10-10 11:16 | GOODMAN - CK24-1B | 71 | 3.8 | Yes | Yes | 21.4 | 19.8 | 1.6 | EE8547E846EF48D799EE8A4B9295C93B |  | R22 | TXV |  | 5.352% | 0.94648 | 10.29% | [5 empty] | TXV | 5.352%
San Mateo | CA | 94403-1044 |  | 2013-10-14 | 2013-10-14 13:28 | 2013-10-14 13:50 | DAY & NIGHT - 561CJ036-D | 81 | 2.4 | Yes | Yes | 17 | 19.3 | -2.3 | 8061462B4D9E4F809B34C5692F61EA06 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93706-9601 |  | 2013-09-27 | 2013-09-27 06:57 | 2013-09-27 06:59 | BRYANT - 550AN048-E | 165 | 4.9 | Yes | Yes | 22.2 | 19.8 | 2.4 | E5C10A14F82746FCB6F70357D399328D |  | R410A | Non-TXV |  | 2.97% | 0.9703 | 5.707% | [5 empty] | Non-TXV | 2.97%
Fresno | CA | 93706-9601 |  | 2013-09-27 | 2013-09-27 07:02 | 2013-09-27 07:04 | BRYANT - 550AN030-E | 96 | 3.2 | Yes | Yes | 18.1 | 20.3 | -2.2 | 5CE22BFEA17746999675A3257A73A3B9 |  | R410A | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93703-2917 |  | 2013-09-27 | 2013-09-27 11:14 | 2013-09-27 11:16 | OTHER - GR6GD-X48K096X | 224 | 6.7 | Yes | Yes | 25.6 | 19.9 | 5.7 | 4ACB3F1CF70C44C9BE3C7E5D2A5CFDB4 |  | R410A | Non-TXV |  | 2.991% | 0.97009 | 5.748% | [5 empty] | Non-TXV | 2.991%
Fresno | CA | 93702-2639 |  | 2013-10-02 | 2013-10-02 12:32 | 2013-10-02 12:33 | GOODMAN - GPG13480701AB | 146 | 6 | Yes | Yes | 26.1 | 20.4 | 5.7 | D462C0AA423A4D1D846926E4D253C350 |  | R22 | Non-TXV |  | 4.11% | 0.9589 | 7.898% | [5 empty] | Non-TXV | 4.11%
Stockton | CA | 95210-5666 |  | 2013-09-27 | 2013-09-27 12:00 | 2013-09-27 12:30 | GOODMAN - GSC130301DA | 87 | 5.3 | Yes | Yes | 21.5 | 21.5 | 0 | 44E97F86AF384726B71A769A622670C2 |  | R22 | Non-TXV |  | 6.092% | 0.93908 | 11.71% | [5 empty] | Non-TXV | 6.092%
Stockton | CA | 95205-2725 |  | 2013-09-30 | 2013-09-30 10:45 | 2013-09-30 11:03 | OTHER - HC36D1VAR | 134 | 8.4 | Yes | Yes | 16.7 | 18.3 | -1.6 | F5CA923722734CADA300E05BC842645E |  | R22 | Non-TXV |  | 6.269% | 0.93731 | 12.05% | [5 empty] | Non-TXV | 6.269%
Lincoln | CA | 95648-1949 |  | 2013-10-21 | 2013-10-21 10:47 | 2013-10-21 11:10 | OTHER - 561AJO36-B | 70 | 2.2 | Yes | Yes | 19 | 21.4 | -2.4 | B45CA03C77E84B7F925F250548BE36F8 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Los Banos | CA | 93635-5460 |  | 2013-10-08 | 2013-10-08 12:58 | 2013-10-08 12:59 | OTHER - EADB-025JAS | 61 | 2.6 | Yes | Yes | 17.9 | 20.2 | -2.3 | 1864929E3A9B450195B0266D0E997490 |  | R22 | Non-TXV |  | 4.262% | 0.95738 | 8.191% | [5 empty] | Non-TXV | 4.262%
Stockton | CA | 95207-4202 |  | 2013-09-26 | 2013-09-26 13:44 | 2013-09-26 13:46 | COLEMAN - BRCS0361CB | 58 | 7.1 | Yes | Yes | 24.1 | 19.8 | 4.3 | 4346460BFA2C40B69A027D9E5925D056 |  | R22 | Non-TXV |  | 12.24% | 0.87759 | 23.53% | [5 empty] | Non-TXV | 12.24%
Sanger | CA | 93657-2398 |  | 2013-10-17 | 2013-10-17 17:55 | 2013-10-17 18:21 | RHEEM - RAND-024JAZ | 76 | 2.3 | Yes | Yes | 20.1 | 20.4 | -0.3 | C5229E6AA8FC4D28BCA447D55214545B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Fresno | CA | 93725-1653 |  | 2013-10-09 | 2013-10-09 11:30 | 2013-10-09 11:46 | CARRIER - 24ABA348A300 | 125 | -10.3 | Yes | Yes | 22.4 | 17.2 | 5.2 | 06F7533AD3F34592BAFE3577EE85C8F9 |  | R410A | Non-TXV |  | -8.24% | 1.0824 | 2.308% |  |  |  |  | Non-TXV |  |  | -8.24%
Madera | CA | 93637-4530 |  | 2013-10-07 | 2013-10-07 13:18 | 2013-10-07 13:19 | CARRIER - 4496E05084 | 82 | 13 | Yes | Yes | 28.7 | 23.1 | 5.6 | BC33440D4D9F4916936C6B9648FCD0E0 |  | R22 | TXV |  | 15.85% | 0.84146 | 30.47% | [5 empty] | TXV | 15.85%
Lincoln | CA | 95648-2313 |  | 2013-09-26 | 2013-09-26 15:08 | 2013-09-26 15:08 | RUUD - UNK | 89 | 0 | Yes | Yes | 18.9 | 20.9 | -2 | 1EB5E5CB706A44839BCEA55CA127FB86 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-6617 |  | 2013-09-27 | 2013-09-27 13:09 | 2013-09-27 13:29 | OTHER - RAUC-30-2B | 67 | 10.1 | Yes | Yes | 23.8 | 18 | 5.9 | FD63087D97314F4196EA140CB454A301 |  | R22 | Non-TXV |  | 15.07% | 0.84925 | 28.97% | [5 empty] | Non-TXV | 15.07%
Fresno | CA | 93727-2262 |  | 2013-09-30 | 2013-09-30 11:57 | 2013-09-30 12:00 | ICP - PGF024K040D | 58 | 3 | Yes | Yes | 17.7 | 19.9 | -2.2 | C661908629F3408692FF68E9ADE7043F |  | R22 | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Fresno | CA | 93703-4350 |  | 2013-10-08 | 2013-10-08 17:15 | 2013-10-08 18:02 | YORK - D1NA024N03606C | 54 | 2.8 | Yes | Yes | 24.1 | 21 | 3.1 | 01238D8A62E84C3699BEC4B7ABE0A3BC |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Magalia | CA | 95954-9393 |  | 2013-09-26 | 2013-09-26 11:01 | 2013-09-26 11:01 | COLEMAN - 6284B901 | 70 | 0 | Yes | Yes | 22.9 | 20.8 | 2.1 | F48CA40514E6491981FBBC786CC42E52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2434 |  | 2013-10-03 | 2013-10-03 10:50 | 2013-10-03 10:52 | RUUD - 7777UNK | 80 | 3.2 | Yes | Yes | 23.7 | 19.7 | 4 | EF47BE62299043E3BBD47C091ED419D4 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Paradise | CA | 95969-2272 |  | 2013-09-26 | 2013-09-26 11:45 | 2013-09-26 12:00 | OTHER - AC024X1222A | 71 | 3 | Yes | Yes | 16.3 | 18.7 | -2.4 | 4C27D8C3279A4D318525B62F9D078BF3 |  | R22 | Non-TXV |  | 4.225% | 0.95775 | 8.12% | [5 empty] | Non-TXV | 4.225%
Stockton | CA | 95204-5441 |  | 2013-10-24 | 2013-10-24 12:01 | 2013-10-24 12:01 | GOODMAN - GSC130241AA | 99 | 0 | Yes | Yes | 18.8 | 19.4 | -0.6 | C81CADDD07FD4D28BC6D53CBD59516E3 |  | R22 | TXV |  | 0% | 1 | 0%
Twain Harte | CA | 95383-9788 |  | 2013-10-14 | 2013-10-14 11:24 | 2013-10-14 12:05 | DAY & NIGHT - 584AN030060AC | 67 | 5 | Yes | Yes | 26.2 | 20.7 | 5.5 | DEFE7AB402424F18921C0231C1595677 |  | R22 | Non-TXV |  | 7.463% | 0.92537 | 14.34% | [5 empty] | Non-TXV | 7.463%
Chowchilla | CA | 93610-2017 |  | 2013-10-11 | 2013-10-11 13:54 | 2013-10-11 13:56 | RHEEM - RRNLB042JK08X | 112 | 4.8 | Yes | Yes | 29.4 | 24.6 | 4.8 | 646487B41E75410FBBEE121C3CDC0515 |  | R410A | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Fresno | CA | 93704-4074 |  | 2013-10-14 | 2013-10-14 11:10 | 2013-10-14 12:37 | BDP - 585EJW18050ABAC | 55 | 2.3 | Yes | Yes | 24.3 | 20.7 | 3.6 | 04619F345F3A4E57831D895144A8ACDE |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
San Andreas | CA | 95249-9462 |  | 2013-09-26 | 2013-09-26 16:27 | 2013-09-26 16:44 | BRYANT - 561CJ036-F | 70 | 8.8 | Yes | Yes | 25.8 | 20.4 | 5.4 | BBFAD74F4D404ED398B020FE0617657D |  | R22 | Non-TXV |  | 12.57% | 0.87429 | 24.16% | [5 empty] | Non-TXV | 12.57%
Fresno | CA | 93722-2545 |  | 2013-10-01 | 2013-10-01 14:43 | 2013-10-01 14:45 | LENNOX - GCS26X-042-75-2PA | 133 | 4.8 | Yes | Yes | 25.6 | 19.7 | 5.9 | AD4492A6F1034462A3CF242DB76E7DF0 |  | R22 | Non-TXV |  | 3.609% | 0.96391 | 6.936% | [5 empty] | Non-TXV | 3.609%
Tracy | CA | 95377-8804 |  | 2013-10-07 | 2013-10-07 09:59 | 2013-10-07 10:19 | YORK - H1RA042S06D | 84 | 5.8 | Yes | Yes | 30.2 | 20.4 | 9.8 | 63002F2232AD4C05913AE64CC6B256D7 |  | R22 | Non-TXV |  | 6.905% | 0.93095 | 13.27% | [5 empty] | Non-TXV | 6.905%
Los Banos | CA | 93635-0000 |  | 2013-10-08 | 2013-10-08 10:38 | 2013-10-08 10:40 | GIBSON - JS3BBA-030KA | 68 | 4 | Yes | Yes | 21.6 | 20.1 | 1.5 | 6F330617B25A4D4888735C51895016CF |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Manteca | CA | 95336-3636 |  | 2013-10-08 | 2013-10-08 10:47 | 2013-10-08 11:12 | BRYANT - 583BNW036060AB | 73 | 2.8 | Yes | Yes | 24.6 | 21.1 | 3.5 | 4B71D0DCFDEA4DD0887954BFE1F6C771 |  | R410A | Non-TXV |  | 3.836% | 0.96164 | 7.371% | [5 empty] | Non-TXV | 3.836%
Fresno | CA | 93722-2545 |  | 2013-10-02 | 2013-10-02 10:04 | 2013-10-02 10:07 | LENNOX - GCS26X030752PA | 85 | 6.6 | Yes | Yes | 23.2 | 18.2 | 5 | CFBA83AF2FFD4BDB88F7EF5FC8259D02 |  | R22 | Non-TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | Non-TXV | 7.765%
Clovis | CA | 93611-5521 |  | 2013-10-04 | 2013-10-04 11:29 | 2013-10-04 11:30 | CARRIER - 38BRB036300 | 118 | 5.5 | Yes | Yes | 20.6 | 19.1 | 1.5 | 803657F2A862475488C26DE3CA5100B1 |  | R22 | Non-TXV |  | 4.661% | 0.95339 | 8.957% | [5 empty] | Non-TXV | 4.661%
Stockton | CA | 95206-6506 |  | 2013-10-16 | 2013-10-16 12:50 | 2013-10-16 13:09 | YORK - H2RA030SO6D | 61 | 3 | Yes | Yes | 19.9 | 17.7 | 2.2 | 1FC5AD50A2D047EFBE6A8E260F7A2CCE |  | R22 | Non-TXV |  | 4.918% | 0.95082 | 9.451% | [5 empty] | Non-TXV | 4.918%
Stockton | CA | 95205-8410 |  | 2013-10-02 | 2013-10-02 13:56 | 2013-10-02 14:18 | CARRIER - 38TH024300 | 53 | 2.2 | Yes | Yes | 21 | 21.5 | -0.5 | 1EFEA1E6E087466D85F6E54501D48040 |  | R22 | Non-TXV |  | 4.151% | 0.95849 | 7.977% | [5 empty] | Non-TXV | 4.151%
Valley Springs | CA | 95252-9193 |  | 2013-10-10 | 2013-10-10 11:29 | 2013-10-10 11:47 | DAY & NIGHT - UNK | 64 | 2.3 | Yes | Yes | 25.3 | 19.9 | 5.4 | D7EE8215A5AD4E74BF2841F82B971D57 |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Stockton | CA | 95206-5723 |  | 2013-09-30 | 2013-09-30 15:37 | 2013-09-30 16:00 | BRYANT - 561CJ048-A | 102 | 8 | Yes | Yes | 24.2 | 18.7 | 5.5 | DDB17F9769BC4D4599C121CFACFD57BA |  | R22 | Non-TXV |  | 7.843% | 0.92157 | 15.07% | [5 empty] | Non-TXV | 7.843%
Lincoln | CA | 95648-3251 |  | 2013-09-27 | 2013-09-27 11:04 | 2013-09-27 11:04 | GOODMAN - GSC140361AB | 155 | 0 | Yes | Yes | 21.3 | 20.7 | 0.6 | DC350A1B01DD4E4CAACDC6980744B6DD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6811 |  | 2013-10-03 | 2013-10-03 11:30 | 2013-10-03 11:32 | CARRIER - UNK | 68 | 3.1 | Yes | Yes | 22.2 | 17.2 | 5 | B98CABBA80A8401FAEF5A1AA38F7D72D |  | R22 | Non-TXV |  | 4.559% | 0.95441 | 8.761% | [5 empty] | Non-TXV | 4.559%
Stockton | CA | 95210-5674 |  | 2013-10-03 | 2013-10-03 13:14 | 2013-10-03 13:35 | PAYNE - 598AN036-B | 195 | 17.8 | Yes | Yes | 17.6 | 17.5 | 0.1 | 2E0D5CD99994453699CE76FC03C9A429 |  | R22 | Non-TXV |  | 9.128% | 0.90872 | 17.54% | [5 empty] | Non-TXV | 9.128%
Burson | CA | 95225-0000 |  | 2013-10-01 | 2013-10-01 11:43 | 2013-10-01 11:43 | RUUD - UAFD-060JBS | 118 | 0 | Yes | Yes | 21.4 | 19.1 | 2.3 | F69D954BA9A34DFEBDDCE9162599E250 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-2489 |  | 2013-09-27 | 2013-09-27 12:11 | 2013-09-27 12:11 | GOODMAN - CK18-1B | 59 | 0 | Yes | Yes | 17.9 | 20.9 | -3 | 944B6A85A3134B1CB2F97E7813933467 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2542 |  | 2013-10-08 | 2013-10-08 12:21 | 2013-10-08 12:45 | LENNOX - 12GCS030X-75-1PA | 80 | 3.2 | Yes | Yes | 18.1 | 18.5 | -0.4 | 5C1CE47A49F84550A2017A60A79394C7 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93703-3207 |  | 2013-09-27 | 2013-09-27 10:43 | 2013-09-27 10:44 | TEMPSTAR - PGF330060K01A2 | 85 | 4.9 | Yes | Yes | 23.3 | 19.5 | 3.8 | A73E9C75FD66448F825D8ED0D52A250E |  | R22 | Non-TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | Non-TXV | 5.765%
Chico | CA | 95928-6049 |  | 2013-10-08 | 2013-10-08 14:40 | 2013-10-08 20:01 | LENNOX - 13GEP24050ALP-1A | 82 | 4 | Yes | Yes | 28.9 | 23.4 | 5.5 | F84FF0338D2845028D448D0F0CF042BE |  | R410A | Non-TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | Non-TXV | 4.878%
Stockton | CA | 95206-3884 |  | 2013-10-10 | 2013-10-10 15:33 | 2013-10-10 16:00 | CARRIER - 38EZG042300 | 99 | 8.4 | Yes | Yes | 26 | 20.2 | 5.9 | 340C7426201E44AB809F8E43D3501065 |  | R410A | Non-TXV |  | 8.485% | 0.91515 | 16.31% | [5 empty] | Non-TXV | 8.485%
Los Banos | CA | 93635-5459 |  | 2013-10-08 | 2013-10-08 12:34 | 2013-10-08 12:35 | OTHER - EADB-025JAS | 61 | 2.8 | Yes | Yes | 18.8 | 20.4 | -1.6 | 47180B11852F4DA7822F24DE8ACF8891 |  | R22 | Non-TXV |  | 4.59% | 0.9541 | 8.821% | [5 empty] | Non-TXV | 4.59%
Fresno | CA | 93725-1253 |  | 2013-10-10 | 2013-10-10 12:06 | 2013-10-10 12:36 | BDP - 585CJ030075 | 78 | 4.2 | Yes | Yes | 24 | 20.9 | 3.1 | 5B9D64E43F454836831881A0B44D8BF9 |  | R22 | Non-TXV |  | 5.385% | 0.94615 | 10.35% | [5 empty] | Non-TXV | 5.385%
Fresno | CA | 93722-7707 |  | 2013-10-03 | 2013-10-03 12:09 | 2013-10-03 12:13 | OTHER - EADB048JAS | 113 | 11.8 | Yes | Yes | 21.1 | 18.3 | 2.8 | 605F3AC5C7844B37BA305DE4147E6D03 |  | R22 | Non-TXV |  | 10.44% | 0.89558 | 20.07% | [5 empty] | Non-TXV | 10.44%
Stockton | CA | 95204-1713 |  | 2013-10-03 | 2013-10-03 10:09 | 2013-10-03 10:30 | AMANA - RCE42C2A | 220 | 28 | Yes | Yes | 15.7 | 17.9 | -2.2 | A26F83111A794365939BC7F1FF104248 |  | R22 | TXV |  | 12.73% | 0.87273 | 24.46% | [5 empty] | TXV | 12.73%
Lincoln | CA | 95648-1556 |  | 2013-09-26 | 2013-09-26 10:09 | 2013-09-26 10:09 | TRANE - 4TTX4042A1000AA | 103 | 0 | Yes | Yes | 24.9 | 20.1 | 4.8 | A03D6C982A484695848EB0B9B8855809 |  | R410A | TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2823 |  | 2013-10-08 | 2013-10-08 16:22 | 2013-10-08 16:22 | YORK - H1RC060S06D | 147 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | D7809BA8545D40BF91E299FD7C05EA52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6837 |  | 2013-09-27 | 2013-09-27 14:33 | 2013-09-27 14:35 | LENNOX - GCS26X752PA | 110 | 19.2 | Yes | Yes | 23.6 | 19.3 | 4.3 | 2229FA04038A469EAAE4F1B12057A8F2 |  | R22 | Non-TXV |  | 17.45% | 0.82545 | 33.54% | [5 empty] | Non-TXV | 17.45%
Stockton | CA | 95215-7321 |  | 2013-10-02 | 2013-10-02 14:30 | 2013-10-02 15:09 | CARRIER - 24ABR330A310 | 84 | 7.7 | Yes | Yes | 17.7 | 20.4 | -2.7 | 9979064914A1491D9514C65D6403FA5F |  | R22 | TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | TXV | 9.167%
Riverbank | CA | 95367-3080 |  | 2013-10-01 | 2013-10-01 14:02 | 2013-10-01 14:21 | RHEEM - RRNA-B030JK06X | 72 | 4.1 | Yes | Yes | 16.5 | 18.7 | -2.2 | 9F2784F446144F7EB447F57AB6DAFD81 |  | R22 | Non-TXV |  | 5.694% | 0.94306 | 10.94% | [5 empty] | Non-TXV | 5.694%
Stockton | CA | 95207-2308 |  | 2013-10-04 | 2013-10-04 11:43 | 2013-10-04 12:12 | PAYNE - UNK | 52 | -4.9 | Yes | Yes | 16.8 | 18.1 | -1.3 | 046D04C4AD68454CBE4F9C90A7676AAA |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Atwater | CA | 95301-3178 |  | 2013-10-18 | 2013-10-18 23:59 | 2013-10-19 00:01 | RHEEM - RPKA025JAZ | 54 | 2.5 | Yes | Yes | 24.1 | 21.5 | 2.6 | 8049ACDE36D54E7CADEE18F22A97AFB1 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Stockton | CA | 95207-1539 |  | 2013-10-02 | 2013-10-02 12:48 | 2013-10-02 13:12 | DAY & NIGHT - 561CJ48-A | 103 | 22.5 | Yes | Yes | 20.4 | 20.4 | 0 | CB91186F696443C49E51CA6E24E4D2DF |  | R22 | Non-TXV |  | 21.84% | 0.78155 | 41.98% | [5 empty] | Non-TXV | 21.84%
Stockton | CA | 95206-6224 |  | 2013-09-26 | 2013-09-26 15:04 | 2013-09-26 15:27 | BDP - 561CJ036-C | 85 | 4.1 | Yes | Yes | 19.4 | 19.7 | -0.3 | EE86BEFC26A84F63945FB15CFE53A893 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Redwood City | CA | 94061-2524 |  | 2013-10-14 | 2013-10-14 16:46 | 2013-10-14 17:01 | TRANE - 2TTR048A1000AA | 120 | 4.4 | Yes | Yes | 21 | 20.6 | 0.4 | 5F1847D927D04771BD3724B19C731068 |  | R22 | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Stockton | CA | 95215-7321 |  | 2013-10-01 | 2013-10-01 15:31 | 2013-10-01 15:58 | CARRIER - 24ABR330A310 | 84 | 8.1 | Yes | Yes | 21.2 | 21.8 | -0.6 | 708A28244A6C4645B6AA2F260648DF36 |  | R22 | TXV |  | 9.643% | 0.90357 | 18.53% | [5 empty] | TXV | 9.643%
Fresno | CA | 93706-4801 |  | 2013-09-26 | 2013-09-26 11:15 | 2013-09-26 11:17 | ICP - PGC030K060A | 52 | 2.3 | Yes | Yes | 20.2 | 19.9 | 0.3 | 6A581B7484CE41B5B37F6B445170EE5E |  | R22 | Non-TXV |  | 4.423% | 0.95577 | 8.5% | [5 empty] | Non-TXV | 4.423%
Stockton | CA | 95212-3819 |  | 2013-09-27 | 2013-09-27 10:17 | 2013-09-27 10:34 | CARRIER - 38CKC036350 | 70 | 5.8 | Yes | Yes | 16.9 | 19.1 | -2.2 | 51C5D19700BF46A9B4B40EFE05BEAF89 |  | R22 | TXV |  | 8.286% | 0.91714 | 15.92% | [5 empty] | TXV | 8.286%
Sanger | CA | 93657-3839 |  | 2013-10-09 | 2013-10-09 14:08 | 2013-10-09 14:38 | LENNOX - 13ACC-048-230-01 | 157 | 41.7 | Yes | Yes | 30.8 | 21.1 | 9.7 | B132563F4F6B420187A19CF8570EBCCC | Add refrigerant: 46.5 oz Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 26.56% | 0.73439 | 51.04% | [5 empty] | Non-TXV | 26.56%
Stockton | CA | 95210-4452 |  | 2013-10-11 | 2013-10-11 10:55 | 2013-10-11 11:17 | PAYNE - UNK | 96 | 19.3 | Yes | Yes | 24.4 | 18.7 | 5.7 | 8906CECC0E474C209DDAE1BF5CD1D337 |  | R22 | Non-TXV |  | 20.1% | 0.79896 | 38.64% | [5 empty] | Non-TXV | 20.1%
Stockton | CA | 95207-4614 |  | 2013-09-26 | 2013-09-26 14:13 | 2013-09-26 14:16 | DAY & NIGHT - 5858048125YACR | 93 | 8.2 | Yes | Yes | 24 | 18.2 | 5.8 | E2B9172593C14480A50EC7A7794D30D4 |  | R22 | Non-TXV |  | 8.817% | 0.91183 | 16.94% | [5 empty] | Non-TXV | 8.817%
Fresno | CA | 93722-7767 |  | 2013-10-03 | 2013-10-03 12:48 | 2013-10-03 12:50 | YORK - H2RC042S06HG | 109 | 10.5 | Yes | Yes | 23 | 20.4 | 2.6 | C5A27B6540D343A68C2AC115132C7BD3 |  | R22 | Non-TXV |  | 9.633% | 0.90367 | 18.51% | [5 empty] | Non-TXV | 9.633%
Lincoln | CA | 95648-8028 |  | 2013-09-27 | 2013-09-27 10:20 | 2013-09-27 10:20 | YORK - H1RA042S06D | 84 | 0 | Yes | Yes | 18.7 | 20.3 | -1.6 | AC037949A1CA4D77A821A12962DA428E |  | R22 | TXV |  | 0% | 1 | 0%
Chico | CA | 95926-3058 |  | 2013-09-26 | 2013-09-26 14:23 | 2013-09-26 14:40 | DAY & NIGHT - 591ANX030000AAAA | 70 | -8 | Yes | Yes | 26 | 20.4 | 5.6 | 6E3247529A6747FC90F1CB6F772B08AC |  | R22 | Non-TXV |  | -11.43% | 1.1143 | 3.201% |  |  |  |  | Non-TXV |  |  | -11.43%
Stockton | CA | 95204-2123 |  | 2013-10-07 | 2013-10-07 09:30 | 2013-10-07 09:47 | HEIL - CA9030VKD2 | 91 | 3.3 | Yes | Yes | 23.6 | 18.2 | 5.4 | 3C535B3FDB7C439B81F1D859FD33DD48 |  | R22 | Non-TXV |  | 3.626% | 0.96374 | 6.969% | [5 empty] | Non-TXV | 3.626%
Redwood City | CA | 94062-3352 |  | 2013-10-15 | 2013-10-15 11:18 | 2013-10-15 11:42 | FRIGIDAIRE - FS3BA060KA | 122 | 3.7 | Yes | Yes | 27 | 22.2 | 4.8 | E6EA8D3E986142CB9BCAB71E86130BD9 |  | R22 | Non-TXV |  | 3.033% | 0.96967 | 5.828% | [5 empty] | Non-TXV | 3.033%
Fresno | CA | 93722-2508 |  | 2013-10-02 | 2013-10-02 07:55 | 2013-10-02 07:56 | BRYANT - 561EJ042-A | 80 | 2.7 | Yes | Yes | 20.1 | 20.6 | -0.5 | C88B18782CDF4FF18533B9C7DB41291E |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Stockton | CA | 95204-1424 |  | 2013-09-30 | 2013-09-30 15:32 | 2013-09-30 15:32 | RHEEM - RRGG-07N36JKR | 75 | 0 | Yes | Yes | 20.8 | 18.5 | 2.3 | 8CF996F3EF8648DE9EA2240FF9F309D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2538 |  | 2013-10-01 | 2013-10-01 14:26 | 2013-10-01 14:27 | GOODMAN - CK301B | 76 | 12 | Yes | Yes | 25.1 | 20.9 | 4.2 | 92573E9E28FB4DFCA8CE8FC2928BD759 |  | R22 | Non-TXV |  | 15.79% | 0.84211 | 30.34% | [5 empty] | Non-TXV | 15.79%
Stockton | CA | 95204-4037 |  | 2013-10-03 | 2013-10-03 10:51 | 2013-10-03 11:11 | RHEEM - RRNL-B036JK06X | 98 | 10.6 | Yes | Yes | 23.2 | 17.2 | 6 | 90DE5066EC8D402483DE2D941DD6312E |  | R410A | Non-TXV |  | 10.82% | 0.89184 | 20.79% | [5 empty] | Non-TXV | 10.82%
Gridley | CA | 95948-9505 |  | 2013-09-30 | 2013-09-30 10:37 | 2013-09-30 11:14 | OTHER - 0A5530UKA10 | 77 | -4.7 | Yes | Yes | 21 | 21.2 | -0.2 | EFE5C83E058045C290514BFC1F3E4529 |  | R22 | Non-TXV |  | -6.104% | 1.061 | 1.709% |  |  |  |  | Non-TXV |  |  | -6.104%
Stockton | CA | 95206-6063 |  | 2013-09-26 | 2013-09-26 14:05 | 2013-09-26 14:23 | GOODMAN - CKJO60-1 | 142 | 5.7 | Yes | Yes | 20.5 | 17.7 | 2.8 | CF9C3A13D04044BCB5CEA09FC8F4BB33 |  | R22 | Non-TXV |  | 4.014% | 0.95986 | 7.714% | [5 empty] | Non-TXV | 4.014%
Stockton | CA | 95209-1968 |  | 2013-10-10 | 2013-10-10 10:53 | 2013-10-10 11:13 | RUUD - UACB-036JAS | 48 | 3.6 | Yes | Yes | 21.3 | 19.6 | 1.8 | F735229DF3054B0CA46F54879B5F72D8 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Riverdale | CA | 93656-9471 |  | 2013-10-03 | 2013-10-03 15:49 | 2013-10-03 16:10 | ICP - N2A324AKA200 | 70 | 5.3 | Yes | Yes | 26 | 20.4 | 5.6 | 42DE5C665A7A4AEC887AC6F87CA9E737 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.571% | 0.92429 | 14.55% | [5 empty] | Non-TXV | 7.571%
Riverdale | CA | 93656-9468 |  | 2013-11-02 | 2013-11-02 14:21 | 2013-11-02 15:19 | ICP - N2A324AKA200 | 70 | 7.7 | Yes | Yes | 17.9 | 20.8 | -2.8 | 9BF88A7E4A16408BB1ABFB321F8797D0 |  | R22 | Non-TXV |  | 11% | 0.89 | 21.14% | [5 empty] | Non-TXV | 11%
Stockton | CA | 95204-3717 |  | 2013-10-17 | 2013-10-17 11:49 | 2013-10-17 12:14 | GOODMAN - GSC130301AE | 117 | -6.9 | Yes | Yes | 20.1 | 19.1 | 1 | A78A79D77D464BEDA60F4F6C928EE7A7 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Los Banos | CA | 93635-5347 |  | 2013-09-30 | 2013-09-30 12:00 | 2013-09-30 12:02 | GOODMAN - CKJ301B | 92 | 6.5 | Yes | Yes | 21 | 18.2 | 2.8 | D339DBE2E7C14C79BC557133FED1D72D |  | R22 | Non-TXV |  | 7.065% | 0.92935 | 13.58% | [5 empty] | Non-TXV | 7.065%
Fresno | CA | 93727-6835 |  | 2013-09-30 | 2013-09-30 10:54 | 2013-09-30 10:55 | RUUD - URKA-A036JK06E | 62 | 3.6 | Yes | Yes | 22.1 | 19.8 | 2.3 | 5448222B844149E5A4F7D4225640724A |  | R22 | Non-TXV |  | 5.806% | 0.94194 | 11.16% | [5 empty] | Non-TXV | 5.806%
Lincoln | CA | 95648-1710 |  | 2013-09-26 | 2013-09-26 11:14 | 2013-09-26 11:14 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 19.8 | 20.2 | -0.4 | DBA824338E6B4016AC7C92CBB9F7F803 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5387 |  | 2013-09-30 | 2013-09-30 13:20 | 2013-09-30 13:34 | BRYANT - 561CJ060A | 152 | 20.2 | Yes | Yes | 21.4 | 19.9 | 1.6 | B9CD25FF2C0A493A86663787A8662C2D |  | R22 | TXV |  | 13.29% | 0.86711 | 25.54% | [5 empty] | TXV | 13.29%
Stockton | CA | 95205-7842 |  | 2013-10-09 | 2013-10-09 13:38 | 2013-10-09 14:00 | GUARDIAN - GCGD36S41S3A | 73 | 8.2 | Yes | Yes | 21.1 | 18.6 | 2.6 | B67962D4262E4EBD9F27BEE1F822695B |  | R410A | TXV |  | 11.23% | 0.88767 | 21.59% | [5 empty] | TXV | 11.23%
Clovis | CA | 93612-2684 |  | 2013-09-26 | 2013-09-26 09:41 | 2013-09-26 09:44 | AMERICAN STANDARD - YCC036F1MOBF | 83 | 8.2 | Yes | Yes | 24.3 | 19.5 | 4.8 | 6B0AE2C4E7EB454BBA9A47984DF70A90 |  | R22 | Non-TXV |  | 9.88% | 0.9012 | 18.99% | [5 empty] | Non-TXV | 9.88%
Fresno | CA | 93725-9437 |  | 2013-10-14 | 2013-10-14 15:42 | 2013-10-14 16:01 | BDP - 588ANW042100ADAG | 82 | 3.1 | Yes | Yes | 25.6 | 20.3 | 5.3 | D454E43DE34849B180AA3EA35FE2398B |  | R22 | Non-TXV |  | 3.78% | 0.9622 | 7.265% | [5 empty] | Non-TXV | 3.78%
Los Banos | CA | 93635-3133 |  | 2013-10-08 | 2013-10-08 13:34 | 2013-10-08 13:35 | YORK - 7777UNK | 80 | 3.7 | Yes | Yes | 20.3 | 20.8 | -0.5 | 631F5857FBEC4858AFDFDCB30580C57B |  | R22 | Non-TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | Non-TXV | 4.625%
Clovis | CA | 93612-2633 |  | 2013-10-09 | 2013-10-09 16:40 | 2013-10-09 16:40 | BRYANT - 561CJ036-F | 75 | 0 | Yes | Yes | 20.5 | 16.5 | 4 | CF5E9B8B7A644201BFB56BA281F62163 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6826 |  | 2013-09-27 | 2013-09-27 14:10 | 2013-09-27 14:12 | RUUD - URKAA036JK06E | 62 | 6.7 | Yes | Yes | 20.7 | 17.6 | 3.1 | 6CDDF0C1F3DA44E59652BDE4598C2797 |  | R22 | Non-TXV |  | 10.81% | 0.89194 | 20.77% | [5 empty] | Non-TXV | 10.81%
Fresno | CA | 93703-3439 |  | 2013-10-04 | 2013-10-04 13:41 | 2013-10-04 13:43 | ICP - GPCM36K060F | 88 | 5.3 | Yes | Yes | 19.6 | 20.4 | -0.8 | 9CF838217EF44580801BE8A12364EFA5 |  | R22 | Non-TXV |  | 6.023% | 0.93977 | 11.57% | [5 empty] | Non-TXV | 6.023%
Stockton | CA | 95204-4133 |  | 2013-10-22 | 2013-10-22 10:11 | 2013-10-22 10:29 | COMFORT AIRE - PGC024K04A | 58 | 4.2 | Yes | Yes | 22 | 19.5 | 2.5 | 9D7691CAE905459E9CBC9464AFFC1D4A |  | R22 | Non-TXV |  | 7.241% | 0.92759 | 13.92% | [5 empty] | Non-TXV | 7.241%
Stockton | CA | 95206-6115 |  | 2013-10-10 | 2013-10-10 13:26 | 2013-10-10 13:46 | GOODMAN - GSC130361DE | 119 | 4.3 | Yes | Yes | 25.1 | 21 | 4.1 | 5E682761CF6A4A5CA2DE459E0BBEB56F |  | R22 | Non-TXV |  | 3.613% | 0.96387 | 6.944% | [5 empty] | Non-TXV | 3.613%
Atwater | CA | 95301-3178 |  | 2013-10-01 | 2013-10-01 14:00 | 2013-10-01 14:01 | GE - BWB924A100C1 | 81 | 5 | Yes | Yes | 25.6 | 20.3 | 5.3 | 37161B05AEA94CDEA14F4E4FB14CD9FA |  | R22 | Non-TXV |  | 6.173% | 0.93827 | 11.86% | [5 empty] | Non-TXV | 6.173%
Escalon | CA | 95320-1656 |  | 2013-10-11 | 2013-10-11 11:57 | 2013-10-11 12:21 | UNITARY PRODUCTS GROUP - ERSH0241BAB | 102 | 3.7 | Yes | Yes | 24.2 | 20.7 | 3.5 | 94549728F976445D8770E04170B42874 |  | R22 | Non-TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | Non-TXV | 3.627%
Oroville | CA | 95966-3949 |  | 2013-10-02 | 2013-10-02 11:09 | 2013-10-02 11:51 | LENNOX - HP22-461-2P | 200 | 7.3 | Yes | Yes | 18 | 21 | -3 | AA237E1447344628A7EB03B0EA107AA7 |  | R22 | TXV |  | 3.65% | 0.9635 | 7.014% | [5 empty] | TXV | 3.65%
Merced | CA | 95348-9616 |  | 2013-10-18 | 2013-10-18 08:57 | 2013-10-18 08:59 | YORK - H2RA030S06G | 62 | 2.6 | Yes | Yes | 20.2 | 20.4 | -0.2 | E1C5CC44EE154D8085ECAD5986F6FF74 |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Chico | CA | 95928-9443 |  | 2013-10-18 | 2013-10-18 15:18 | 2013-10-18 15:34 | BRYANT - 550AN060-H | 177 | 14.8 | Yes | Yes | 19 | 21.9 | -2.9 | 302B40370D2144A88EA5A6FBE8639A0F |  | R410A | TXV |  | 8.362% | 0.91638 | 16.07% | [5 empty] | TXV | 8.362%
Fresno | CA | 93722-2529 |  | 2013-10-08 | 2013-10-08 12:50 | 2013-10-08 13:07 | LENNOX - GCS26X036752PA | 110 | 5.3 | Yes | Yes | 19.2 | 19.7 | -0.4 | 92CCC38905204D84ADF105B04C07B836 |  | R22 | Non-TXV |  | 4.818% | 0.95182 | 9.259% | [5 empty] | Non-TXV | 4.818%
Stockton | CA | 95210-5686 |  | 2013-10-07 | 2013-10-07 11:01 | 2013-10-07 11:19 | CARRIER - 591ANX048000ACAA | 128 | 4.1 | Yes | Yes | 24 | 19.4 | 4.6 | 3951E66153CD48378344F89D6F0B83B1 |  | R22 | Non-TXV |  | 3.203% | 0.96797 | 6.156% | [5 empty] | Non-TXV | 3.203%
Merced | CA | 95340-9484 |  | 2013-10-09 | 2013-10-09 10:53 | 2013-10-09 10:55 | RHEEM - RRMA-A036JK08X | 99 | 3 | Yes | Yes | 25.3 | 20.1 | 5.2 | F4FB9227802442D2A195E5ED01B87672 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Stockton | CA | 95204-3319 |  | 2013-10-11 | 2013-10-11 12:22 | 2013-10-11 12:38 | PAYNE - PY3PNA042060NB | 125 | -7.4 | Yes | Yes | 22.8 | 18.7 | 4.1 | 2FEB937D6D8D40B69827A8EA987A483C |  | R22 | Non-TXV |  | -5.92% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.92%
Chico | CA | 95928-4104 |  | 2013-10-08 | 2013-10-08 14:02 | 2013-10-08 14:35 | COLEMAN - NA | 70 | 4.3 | Yes | Yes | 25.5 | 21.7 | 3.8 | 0A48655E2BD7495ABFDB0838F336E8B4 |  | R22 | Non-TXV |  | 6.143% | 0.93857 | 11.81% | [5 empty] | Non-TXV | 6.143%
Fresno | CA | 93705-1248 |  | 2013-10-04 | 2013-10-04 12:23 | 2013-10-04 12:25 | CARRIER - 48GS042090301 | 100 | 10.8 | Yes | Yes | 26.6 | 20.7 | 5.9 | D8C74877DE74443BB2054564CDE8F948 |  | R22 | Non-TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | Non-TXV | 10.8%
Chico | CA | 95973-0477 |  | 2013-09-26 | 2013-09-26 15:35 | 2013-09-26 15:52 | TRANE - YCX030F1M0BC | 100 | 3.6 | Yes | Yes | 18 | 20.1 | -2.1 | 19F715913D92442989B9C7AEAF77B772 |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Lathrop | CA | 95330-9425 |  | 2013-10-11 | 2013-10-11 14:42 | 2013-10-11 15:07 | GOODMAN - PGB060100-1 | 82 | 6.3 | Yes | Yes | 22.4 | 20.2 | 2.3 | 3DEDDE76FD134A99867C83E6C772D0AE |  | R22 | Non-TXV |  | 7.683% | 0.92317 | 14.76% | [5 empty] | Non-TXV | 7.683%
Stockton | CA | 95210-2508 |  | 2013-10-07 | 2013-10-07 11:45 | 2013-10-07 11:59 | GE - UNK | 64 | 2.7 | Yes | Yes | 25.6 | 19.9 | 5.7 | BD08E69BC9E64E9695164CE65E053324 |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Fresno | CA | 93722-5162 |  | 2013-10-02 | 2013-10-02 11:12 | 2013-10-02 11:13 | CARRIER - 48KLA130300BE | 68 | 7.3 | Yes | Yes | 26.2 | 20.2 | 6 | F58E40C884F44F2D8737243305A10C31 |  | R22 | Non-TXV |  | 10.74% | 0.89265 | 20.63% | [5 empty] | Non-TXV | 10.74%
Lincoln | CA | 95648-8729 |  | 2013-10-18 | 2013-10-18 12:16 | 2013-10-18 12:16 | UNITARY PRODUCTS GROUP - H2RC048S068 | 120 | 0 | Yes | Yes | 24.1 | 22 | 2.1 | 60A255C0C8484F5EAC865866D3DCFABD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-7121 |  | 2013-10-02 | 2013-10-02 13:51 | 2013-10-02 14:19 | LENNOX - GCS10-411-75-1P | 71 | -6 | Yes | Yes | 24 | 20.9 | 3.1 | 1BDD3C39EB9A4A5BBF87C2841C375BC1 |  | R22 | TXV |  | -8.451% | 1.0845 | 2.367% |  |  |  |  | TXV |  |  | -8.451%
Lincoln | CA | 95648-2126 |  | 2013-09-26 | 2013-09-26 09:31 | 2013-09-26 09:31 | RHEEM - UNK | 68 | 0 | Yes | Yes | 25.4 | 20.8 | 4.6 | CE4FA949D6934277BEEC96F3688B2EE7 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3647 |  | 2013-10-08 | 2013-10-08 15:09 | 2013-10-08 15:27 | WHIRLPOOL - `CBD | 64 | 1.9 | Yes | Yes | 24.5 | 21.5 | 3 | 3641BA5FC7EF48B68A56D07641F3A047 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Oroville | CA | 95966-9225 |  | 2013-10-07 | 2013-10-07 12:51 | 2013-10-07 13:47 | BRYANT - 57DW3606NA | 100 | 4.5 | Yes | Yes | 17.3 | 20.2 | -2.9 | 4C477C2E7EF2444BAF541ADDB47040BB |  | R410A | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Penn Valley | CA | 95946-9664 |  | 2013-09-30 | 2013-09-30 17:51 | 2013-09-30 17:51 | CARRIER - 38BRC036320 | 104 | 0 | Yes | Yes | 18.7 | 21.1 | -2.4 | 3D935F136FBF4267A40684B0A9B061DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93636-8218 |  | 2013-10-07 | 2013-10-07 11:56 | 2013-10-07 11:58 | RUUD - URKAA036JK08E | 62 | 5 | Yes | Yes | 24.5 | 19.4 | 5.1 | 3C4D984828BB4CE1A6DE85202437406F |  | R22 | Non-TXV |  | 8.065% | 0.91935 | 15.5% | [5 empty] | Non-TXV | 8.065%
Tracy | CA | 95377-8959 |  | 2013-10-08 | 2013-10-08 11:19 | 2013-10-08 11:44 | AMERICAN STANDARD - TTD760B100A2 | 129 | 8.8 | Yes | Yes | 26.3 | 20.4 | 5.9 | EE772FED16584043976DA6B2C2D843EA |  | R22 | Non-TXV |  | 6.822% | 0.93178 | 13.11% | [5 empty] | Non-TXV | 6.822%
Gridley | CA | 95948-9760 |  | 2013-10-22 | 2013-10-22 09:45 | 2013-10-22 10:13 | RUUD - UAMC-048JAZ | 162 | 5.9 | Yes | Yes | 26 | 21.1 | 4.9 | 7BB0A3CC2A874AC786385B69DE6EA64E |  | R22 | TXV |  | 3.642% | 0.96358 | 6.999% | [5 empty] | TXV | 3.642%
Stockton | CA | 95209-4364 |  | 2013-10-10 | 2013-10-10 12:23 | 2013-10-10 12:30 | BRYANT - 561CJ042-F | 93 | 5.9 | Yes | Yes | 21.4 | 18.5 | 3 | 02B9D2A620784C12B6617D8A27E1A7B9 |  | R22 | Non-TXV |  | 6.344% | 0.93656 | 12.19% | [5 empty] | Non-TXV | 6.344%
Stockton | CA | 95209-4364 |  | 2013-10-10 | 2013-10-10 12:40 | 2013-10-10 13:00 | BRYANT - 561CJ036-F | 73 | 7.6 | Yes | Yes | 25.1 | 19.3 | 5.8 | 23A3FBD93394481094DED9E1FB2BAC2D |  | R22 | TXV |  | 10.41% | 0.89589 | 20.01% | [5 empty] | TXV | 10.41%
Oakdale | CA | 95361-2746 |  | 2013-10-18 | 2013-10-18 10:57 | 2013-10-18 11:15 | RHEEM - RRKA-A024JK06X | 50 | 2.6 | Yes | Yes | 24.1 | 19.5 | 4.6 | CD4E282A301444FC85760BF9E889FE56 |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Fresno | CA | 93725-0000 |  | 2013-10-04 | 2013-10-04 11:17 | 2013-10-04 11:55 | CARRIER - 24ABA336A31010 | 85 | 3.5 | Yes | Yes | 19.5 | 21.3 | -1.8 | 3B7EE72EA5BF4DBAB4830975D6D60DEC |  | R410A | TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | TXV | 4.118%
Los Banos | CA | 93635-3086 |  | 2013-10-10 | 2013-10-10 11:49 | 2013-10-10 11:50 | GIBSON - JS3BC-030KA | 68 | 2.7 | Yes | Yes | 18.1 | 19.1 | -1 | 65F098AC697C4D33B4C929B37A00431B |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Madera | CA | 93638-0320 |  | 2013-10-08 | 2013-10-08 13:04 | 2013-10-08 13:05 | CARRIER - UNK | 76 | 8.2 | Yes | Yes | 27.3 | 21.8 | 5.5 | 66C3833BF114456DB081ED0225AD076E |  | R22 | Non-TXV |  | 10.79% | 0.89211 | 20.73% | [5 empty] | Non-TXV | 10.79%
Stockton | CA | 95203-2532 |  | 2013-10-22 | 2013-10-22 12:40 | 2013-10-22 12:57 | RHEEM - HC-100-36-21C | 49 | 5.5 | Yes | Yes | 24.1 | 19.1 | 5.1 | 29FE46F4CBD94AD59E7AF4FCA8E1A564 |  | R22 | Non-TXV |  | 11.22% | 0.88776 | 21.57% | [5 empty] | Non-TXV | 11.22%
Livingston | CA | 95334-9735 |  | 2013-10-23 | 2013-10-23 15:53 | 2013-10-24 09:54 | TRANE - TTD730B10 | 85 | 5 | Yes | Yes | 18 | 17.2 | 0.8 | 1F941B2D5CA34A82AE9F8A3BD70E9301 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Grass Valley | CA | 95949-6653 |  | 2013-10-02 | 2013-10-02 14:56 | 2013-10-02 15:14 | LENNOX - HS22-311U-2P | 129 | 9 | Yes | Yes | 16.8 | 19.1 | -2.3 | 40A812B3B7724F699CEA95AC6B2769CC | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 6.977% | 0.93023 | 13.41% | [5 empty] | TXV | 6.977%
Paradise | CA | 95969-4939 |  | 2013-10-08 | 2013-10-08 11:11 | 2013-10-08 11:36 | CARRIER - 38CKCO42-301 | 80 | 3.6 | Yes | Yes | 16.8 | 19.7 | -2.9 | A7487299C93C4F1D8D60BA9F3E83B0C6 |  | R22 | TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | TXV | 4.5%
Los Banos | CA | 93635-3108 |  | 2013-10-08 | 2013-10-08 11:54 | 2013-10-08 11:55 | DAY & NIGHT - 7777UNK | 80 | 3.5 | Yes | Yes | 17 | 18.8 | -1.8 | 6D558C044B05434DA2FEB9682103B3DE |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Stockton | CA | 95206-6148 |  | 2013-10-09 | 2013-10-09 16:10 | 2013-10-09 16:50 | GOODMAN - CLJ48-1 | 117 | 10.1 | Yes | Yes | 27.9 | 22.4 | 5.5 | B1E232CF70B5484FB0C3FC420DBE1DCE |  | R22 | Non-TXV |  | 8.632% | 0.91368 | 16.59% | [5 empty] | Non-TXV | 8.632%
Fresno | CA | 93727-6828 |  | 2013-10-03 | 2013-10-03 11:13 | 2013-10-03 11:52 | RUUD - URMA-A036JK08E | 99 | 4.1 | Yes | Yes | 19.1 | 21 | -1.9 | 469847B326D542AE90E5CDD0DCFAA0B7 |  | R22 | Non-TXV |  | 4.141% | 0.95859 | 7.959% | [5 empty] | Non-TXV | 4.141%
Madera | CA | 93638-2761 |  | 2013-10-07 | 2013-10-07 10:32 | 2013-10-07 10:34 | CARRIER - 48GS036060311 | 68 | 5.2 | Yes | Yes | 24.4 | 19.5 | 4.9 | 16188EA725F24FC28B245981501E32BB |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Escalon | CA | 95320-9406 |  | 2013-10-18 | 2013-10-18 14:07 | 2013-10-18 14:25 | TRANE - 2TTX4024A1000AA | 105 | 4.4 | Yes | Yes | 24.5 | 19.9 | 4.6 | 325F5A7BBD2F4B20A66E8B1FCD17D333 |  | R22 | TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | TXV | 4.19%
Fresno | CA | 93727-6824 |  | 2013-09-27 | 2013-09-27 15:09 | 2013-09-27 15:10 | LENNOX - GCS26036751PA | 110 | 13.1 | Yes | Yes | 22.7 | 18.8 | 3.9 | C56C85A09B8344ADA4D5C856FAE81A14 |  | R22 | Non-TXV |  | 11.91% | 0.88091 | 22.89% | [5 empty] | Non-TXV | 11.91%
Clovis | CA | 93611-6272 |  | 2013-10-09 | 2013-10-09 17:16 | 2013-10-15 10:11 | CARRIER - 38BR048300 | 165 | 6.3 | Yes | Yes | 20.4 | 16.9 | 3.6 | B10613A2B58E4A8E9D9BEAD6F006E4E3 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Manteca | CA | 95337-8999 |  | 2013-10-16 | 2013-10-16 12:12 | 2013-10-16 12:42 | RHEEM - RAKA-048JAZ | 103 | 5 | Yes | Yes | 24.8 | 20.3 | 4.5 | B95F62CE63864CEE88066EF995D2231D |  | R22 | Non-TXV |  | 4.854% | 0.95146 | 9.329% | [5 empty] | Non-TXV | 4.854%
Manteca | CA | 95337-8999 |  | 2013-10-16 | 2013-10-16 12:27 | 2013-10-16 12:43 | RHEEM - RAKA-037JAZ | 79 | 3.1 | Yes | Yes | 18.7 | 19.6 | -0.8 | D9A95B224DFF460BAE08F7D29DF11997 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.924% | 0.96076 | 7.541% | [5 empty] | Non-TXV | 3.924%
Fresno | CA | 93726-5623 |  | 2013-10-07 | 2013-10-07 10:08 | 2013-10-07 10:35 | RHEEM - N/A | 90 | 7.6 | Yes | Yes | 27 | 21.4 | 5.7 | B999ED8B20DB4D9A973BD52B0E1493E3 |  | R22 | Non-TXV |  | 8.444% | 0.91556 | 16.23% | [5 empty] | Non-TXV | 8.444%
Fresno | CA | 93727-3635 |  | 2013-10-03 | 2013-10-03 11:54 | 2013-10-03 12:26 | LENNOX - 10GCS042X075-2PA | 73 | 21.3 | Yes | Yes | 21 | 21.8 | -0.8 | E3B6595B35244FACAFC966EB558E0320 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 29.18% | 0.70822 | 56.07% | [5 empty] | Non-TXV | 29.18%
Stockton | CA | 95205-3833 |  | 2013-10-15 | 2013-10-15 15:35 | 2013-10-15 15:51 | GIBSON - UNK | 110 | 6.5 | Yes | Yes | 18 | 16.9 | 1.2 | D96BFDA3B68C4531B72D4365045B9BBC |  | R22 | Non-TXV |  | 5.909% | 0.94091 | 11.36% | [5 empty] | Non-TXV | 5.909%
Stockton | CA | 95205-3561 |  | 2013-10-09 | 2013-10-09 16:19 | 2013-10-09 16:24 | GUARDIAN - TCGD42S21S2HA | 66 | 9.9 | Yes | Yes | 18.2 | 18.4 | -0.1 | 85AAED646207440EBB01C249E14626C7 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Stockton | CA | 95210-3613 |  | 2013-10-11 | 2013-10-11 09:21 | 2013-10-11 09:39 | COLEMAN - BRCS030B | 76 | 7.2 | Yes | Yes | 20.1 | 19.1 | 1 | AEF0414B7F5344CD8F2D425349A16C76 |  | R22 | Non-TXV |  | 9.474% | 0.90526 | 18.21% | [5 empty] | Non-TXV | 9.474%
Kerman | CA | 93630-1231 |  | 2013-10-03 | 2013-10-03 09:50 | 2013-10-03 10:10 | ALLEGIANCE - 7A0036A100A1 | 88 | 0 | Yes | Yes | 25.5 | 19.9 | 5.6 | ECACD2A87BDB47539CFC10090AFE2EC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-2844 |  | 2013-10-08 | 2013-10-08 14:13 | 2013-10-08 14:39 | GOODMAN - CK24-1D | 65 | 2.3 | Yes | Yes | 20.3 | 20.2 | 0.1 | EEF1E2D3FF534FC390CF0015CCAC4E76 |  | R22 | Non-TXV |  | 3.538% | 0.96462 | 6.8% | [5 empty] | Non-TXV | 3.538%
Fresno | CA | 93727-3635 |  | 2013-10-10 | 2013-10-10 15:25 | 2013-10-10 16:17 | LENNOX - 10GCS042X-75-1PA | 73 | 4.6 | Yes | Yes | 24.4 | 21 | 3.4 | 00AB418E6A6841769965EF99373F1E84 |  | R22 | Non-TXV |  | 6.301% | 0.93699 | 12.11% | [5 empty] | Non-TXV | 6.301%
Fresno | CA | 93727-3039 |  | 2013-09-30 | 2013-09-30 12:41 | 2013-09-30 12:42 | GOODMAN - PGB036050-1REV A | 60 | 4.2 | Yes | Yes | 23.4 | 19.9 | 3.5 | 6A3FEA00069B44D38B80FA65D4A95C8D |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93727-9322 |  | 2013-09-27 | 2013-09-27 12:46 | 2013-09-27 12:48 | ICP - PGF042K080B | 67 | 9 | Yes | Yes | 24.9 | 19.9 | 5 | BDA4F760E8DF48BE85A6B68A58F2A942 |  | R22 | Non-TXV |  | 13.43% | 0.86567 | 25.81% | [5 empty] | Non-TXV | 13.43%
Fresno | CA | 93727-1960 |  | 2013-09-26 | 2013-09-26 11:15 | 2013-09-26 12:16 | PAYNE - PA13NR030-H | 75 | 6 | Yes | Yes | 18 | 20.7 | -2.7 | 39F6330A5E8F437098AA07CE13FF6840 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Stockton | CA | 95205-7791 |  | 2013-10-09 | 2013-10-09 14:30 | 2013-10-09 14:54 | BRYANT - 561C1036-F | 72 | 5.9 | Yes | Yes | 18.8 | 17.6 | 1.2 | A33046BA43724472A4935E57DE03AD19 |  | R22 | Non-TXV |  | 8.194% | 0.91806 | 15.75% | [5 empty] | Non-TXV | 8.194%
Fresno | CA | 93727-3630 |  | 2013-10-01 | 2013-10-01 09:57 | 2013-10-01 10:20 | LENNOX - 10GCS0360X-75-2PA | 58 | 4.6 | Yes | Yes | 21.1 | 20.9 | 0.3 | 8E459884708441B0BEFD6CDCB5E094F4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.931% | 0.92069 | 15.24% | [5 empty] | Non-TXV | 7.931%
Escalon | CA | 95320-1625 |  | 2013-10-11 | 2013-10-11 11:14 | 2013-10-11 11:35 | BRYANT - 113ANA36-E | 83 | 7.1 | Yes | Yes | 25.7 | 20.3 | 5.5 | 04D067EB14014EC18164376F730D0F52 |  | R410A | TXV |  | 8.554% | 0.91446 | 16.44% | [5 empty] | TXV | 8.554%
Selma | CA | 93662-4334 |  | 2013-10-07 | 2013-10-07 14:21 | 2013-10-07 15:41 | UNITARY PRODUCTS GROUP - H1RD036S06G | 155 | 4.8 | Yes | Yes | 18.5 | 21.3 | -2.8 | 4A6F45EC21FD4E37BC202B6533CB2F86 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.097% | 0.96903 | 5.951% | [5 empty] | Non-TXV | 3.097%
Sonora | CA | 95370-5741 |  | 2013-10-03 | 2013-10-03 10:49 | 2013-10-03 11:08 | GOODMAN - PCK036-1 | 73 | 7.4 | Yes | Yes | 16.4 | 18.7 | -2.3 | 9792CE7BB39849A5962721187ADD2C94 |  | R22 | Non-TXV |  | 10.14% | 0.89863 | 19.48% | [5 empty] | Non-TXV | 10.14%
Manteca | CA | 95336-4402 |  | 2013-10-07 | 2013-10-07 14:13 | 2013-10-07 15:18 | GOODMAN - CK30-1A | 69 | 2.2 | Yes | Yes | 22.4 | 20.2 | 2.3 | C708DC0D7F1040CB92695D66853A82DB |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Lathrop | CA | 95330-9473 |  | 2013-10-11 | 2013-10-11 13:25 | 2013-10-11 13:41 | RUUD - UAFO-030JAS | 69 | 11.7 | Yes | Yes | 21.8 | 18.8 | 3 | 46F6A6F0C8B34643AEDA3797490ED6B5 |  | R22 | Non-TXV |  | 16.96% | 0.83043 | 32.59% | [5 empty] | Non-TXV | 16.96%
Fresno | CA | 93727-3643 |  | 2013-10-07 | 2013-10-07 11:27 | 2013-10-07 12:53 | LENNOX - 10GCS042-75-3PA | 73 | 12.3 | Yes | Yes | 20 | 20.8 | -0.8 | 484F0447F27741DE9D09CCB6EA1D4FAC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16.85% | 0.83151 | 32.38% | [5 empty] | Non-TXV | 16.85%
Lincoln | CA | 95648-2901 |  | 2013-10-08 | 2013-10-08 15:42 | 2013-10-08 15:59 | YORK - H1RA042S06D | 84 | 3.1 | Yes | Yes | 27 | 23.1 | 3.9 | 764225F50C07409F868CC7376C77638A |  | R22 | TXV |  | 3.69% | 0.9631 | 7.092% | [5 empty] | TXV | 3.69%
Rocklin | CA | 95765-4129 |  | 2013-09-27 | 2013-09-27 15:02 | 2013-09-27 15:02 | CARRIER - 38EN030300 | 90 | 0 | Yes | Yes | 21.6 | 21.2 | 0.4 | D4593AF7F3454051A0C01E8F7FD8B542 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-8585 |  | 2013-10-16 | 2013-10-16 11:28 | 2013-10-16 12:09 | BRYANT - 563CN030-C | 99 | 3.6 | Yes | Yes | 24.9 | 19.4 | 5.5 | C80EE2C486134E22AC4CE5545748FD38 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Lincoln | CA | 95648-2720 |  | 2013-09-27 | 2013-09-27 11:49 | 2013-09-27 11:49 | YORK - AC036X1222A | 83 | 0 | Yes | Yes | 24.2 | 20.6 | 3.6 | 3D00BEC35F7E41C8AA36082603B7FD11 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4848 |  | 2013-10-07 | 2013-10-07 10:05 | 2013-10-07 10:26 | LENNOX - GCS26-030-752PA | 85 | 6.1 | Yes | Yes | 23.8 | 18 | 5.8 | 8C49A44996A14BF3A0C170DBFAF617C7 |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
El Dorado Hills | CA | 95762-5517 |  | 2013-10-10 | 2013-10-10 10:32 | 2013-10-10 10:58 | COLEMAN - UNK | 63 | 10.1 | Yes | Yes | 25.7 | 20.7 | 5 | 12496ABAC9FA4E0EB98C49D8F911F046 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16.03% | 0.83968 | 30.81% | [5 empty] | Non-TXV | 16.03%
Merced | CA | 95348-3171 |  | 2013-10-16 | 2013-10-16 10:58 | 2013-10-16 10:59 | GE - BTB924A100AO | 45 | 3.3 | Yes | Yes | 23.2 | 18.2 | 5 | 0354007F6FEA4BB49487E6808AA4D52A |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Stockton | CA | 95209-4836 |  | 2013-10-10 | 2013-10-10 10:18 | 2013-10-10 10:18 | PAYNE - 591ANX048000ABAA | 115 | 0 | Yes | Yes | 24.4 | 18.8 | 5.7 | 3982AE21C6834DFDB0590169AEFD50AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2517 |  | 2013-10-09 | 2013-10-09 15:21 | 2013-10-09 15:39 | BDP - 588ANW024060ADAD | 38 | 14.9 | Yes | Yes | 23.6 | 20.4 | 3.2 | 66E1D78689D4442EBF23C54E05D8F81E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 39.21% | 0.60789 | 75.35% | [5 empty] | Non-TXV | 39.21%
Merced | CA | 95348-2715 |  | 2013-10-10 | 2013-10-10 11:43 | 2013-10-10 11:44 | OTHER - BTB930A100AO | 53 | 2.9 | Yes | Yes | 24.1 | 18.7 | 5.4 | FA29C10878D44E06B1AD6178E4519EF2 |  | R22 | Non-TXV |  | 5.472% | 0.94528 | 10.52% | [5 empty] | Non-TXV | 5.472%
Stockton | CA | 95210-2145 |  | 2013-10-22 | 2013-10-22 13:26 | 2013-10-22 13:44 | AMANA - RCC36C2C | 110 | 7 | Yes | Yes | 20 | 18.8 | 1.2 | FBB0A9095BB1426E8D9AE635EB464135 |  | R22 | TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | TXV | 6.364%
Lincoln | CA | 95648-2801 |  | 2013-09-26 | 2013-09-26 13:01 | 2013-09-26 13:01 | YORK - H1RC036S06B | 98 | 0 | Yes | Yes | 25.3 | 20.1 | 5.2 | 49F88965349C4D53B169D724EDDAC457 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-8539 |  | 2013-10-07 | 2013-10-07 11:02 | 2013-10-07 11:24 | CARRIER - 38CK048370 | 99 | 3.8 | Yes | Yes | 22.1 | 19.7 | 2.4 | 7D500E1A9DB348F5B1455F2FBABFC8EA |  | R22 | TXV |  | 3.838% | 0.96162 | 7.377% | [5 empty] | TXV | 3.838%
Merced | CA | 95348-2730 |  | 2013-10-10 | 2013-10-10 13:09 | 2013-10-10 13:11 | GOODMAN - CK241B | 71 | 6.1 | Yes | Yes | 20 | 16.4 | 3.6 | AA1F81AF30974D3CBB7C833DF8C04759 |  | R22 | Non-TXV |  | 8.592% | 0.91408 | 16.51% | [5 empty] | Non-TXV | 8.592%
Merced | CA | 95348-1766 |  | 2013-10-09 | 2013-10-09 13:51 | 2013-10-09 13:52 | BDP - 588ANW048100AEAG | 101 | 3.3 | Yes | Yes | 24.5 | 19.5 | 5 | 48C64A57863A4F4EBE562CB35307D027 |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Stockton | CA | 95204-2027 |  | 2013-10-17 | 2013-10-17 09:37 | 2013-10-17 09:54 | HEIL - PGC030K060A | 52 | -3.1 | Yes | Yes | 17.2 | 18.7 | -1.5 | 57EF4ABA119C4E61AEA52AC26A21D368 |  | R22 | Non-TXV |  | -5.962% | 1.0596 | 1.67% |  |  |  |  | Non-TXV |  |  | -5.962%
Lincoln | CA | 95648-2150 |  | 2013-09-26 | 2013-09-26 14:21 | 2013-09-26 14:21 | GOODMAN - GPG13240451BA | 77 | 0 | Yes | Yes | 25.9 | 20.6 | 5.3 | D470B536067542D79E5721C4918A1A61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-2926 |  | 2013-10-16 | 2013-10-16 13:41 | 2013-10-16 14:08 | BRYANT - 582ANW036090AAAF | 56 | 5 | Yes | Yes | 17.6 | 20.3 | -2.7 | D42418F6DD624A4FB76674937E68C6E2 |  | R22 | Non-TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | Non-TXV | 8.929%
Stockton | CA | 95206-0000 |  | 2013-10-10 | 2013-10-10 12:35 | 2013-10-10 13:02 | GOODMAN - CKJ42-1AB | 106 | -10 | Yes | Yes | 24.9 | 19.4 | 5.5 | 45EB0C2EAF624DDCB8942DA99E3941B7 |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Stockton | CA | 95205-7791 |  | 2013-10-11 | 2013-10-11 15:40 | 2013-10-11 16:01 | BRYANT - 561CJ036-F | 70 | 3.5 | Yes | Yes | 26.2 | 20.4 | 5.8 | 33C607F519D54F47A1DEEFF4949ADD6D |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Merced | CA | 95348-2712 |  | 2013-10-10 | 2013-10-10 10:58 | 2013-10-10 11:00 | OTHER - RAKA024JAZ | 50 | 6.6 | Yes | Yes | 23.9 | 18.7 | 5.2 | 19082171F8BA42E7986BDEC3077E73A7 |  | R22 | Non-TXV |  | 13.2% | 0.868 | 25.37% | [5 empty] | Non-TXV | 13.2%
Coarsegold | CA | 93614-9728 |  | 2013-10-18 | 2013-10-18 11:11 | 2013-10-18 11:12 | OTHER - UNK | 76 | 8.2 | Yes | Yes | 22.7 | 17.7 | 5 | 681457804B2641F78F4D7A3EFF05BB24 |  | R22 | Non-TXV |  | 10.79% | 0.89211 | 20.73% | [5 empty] | Non-TXV | 10.79%
El Dorado Hills | CA | 95762-8060 |  | 2013-10-11 | 2013-10-11 15:57 | 2013-10-11 15:57 | TRANE - 2TTX5048A1000AA | 182 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 80C8A561343D4644991A8EECD2044B61 |  | R22 | TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-8060 |  | 2013-10-11 | 2013-10-11 16:22 | 2013-10-11 16:22 | TRANE - 2TWX5042A1000AA | 157 | 0 | Yes | Yes | 25.9 | 20.7 | 5.2 | 8F29F2F4F2174B619895D8F6584E6544 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-5010 |  | 2013-10-10 | 2013-10-10 11:33 | 2013-10-10 11:33 | WESTINGHOUSE - 1E024PAAD1 | 53 | 0 | Yes | Yes | 18.8 | 18.6 | 0.2 | F9C39946288D4AC3BBB2D77D0D202198 |  | R22 | Non-TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-6318 |  | 2013-10-11 | 2013-10-11 18:28 | 2013-10-11 18:48 | YORK - H1RA042S06D | 84 | 12.6 | Yes | Yes | 22.6 | 20.7 | 1.9 | A1821DB5F0F349F3A31EC0D9DBA70438 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Stockton | CA | 95204-3737 |  | 2013-10-07 | 2013-10-07 12:24 | 2013-10-07 12:43 | GOODMAN - CK18-1B | 59 | 6.4 | Yes | Yes | 22 | 18.2 | 3.8 | 458DE5DF490F4BF180508FE163E742E8 |  | R22 | TXV |  | 10.85% | 0.89153 | 20.85% | [5 empty] | TXV | 10.85%
Oroville | CA | 95966-6523 |  | 2013-10-17 | 2013-10-17 11:46 | 2013-10-17 12:00 | OTHER - JS3BA-036KA | 85 | 5 | Yes | Yes | 17.5 | 20.4 | -2.9 | F785C81509D442CAAA735FDBE5FB7E12 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Rocklin | CA | 95765-4800 |  | 2013-10-09 | 2013-10-09 15:29 | 2013-10-09 15:49 | AMERICAN STANDARD - TTR048C100A0 | 114 | 9.7 | Yes | Yes | 24.3 | 21.5 | 2.8 | 759A2DAD73734CE28277134703EA3710 |  | R22 | Non-TXV |  | 8.509% | 0.91491 | 16.35% | [5 empty] | Non-TXV | 8.509%
Chico | CA | 95926-4296 |  | 2013-10-21 | 2013-10-21 14:00 | 2013-10-21 14:30 | OTHER - CH5524VKD1 | 104 | 3.8 | Yes | Yes | 17.9 | 20.8 | -2.9 | 9B643F777C8F47248200B4ECF48481EC |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Lincoln | CA | 95648-7409 |  | 2013-10-18 | 2013-10-18 14:14 | 2013-10-18 14:14 | UNITARY PRODUCTS GROUP - H2RD036S06B | 96 | 0 | Yes | Yes | 20.5 | 20.3 | 0.2 | 9BC56A251799474EAF9840D535CCCE91 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-2926 |  | 2013-10-07 | 2013-10-07 13:13 | 2013-10-07 13:57 | CARRIER - 48SS-042080321AA | 82 | 5.8 | Yes | Yes | 17.6 | 18.9 | -1.3 | 2A3DCA0F7CB34BC89B64AA6B42ED01C1 |  | R22 | Non-TXV |  | 7.073% | 0.92927 | 13.59% | [5 empty] | Non-TXV | 7.073%
Rocklin | CA | 95765-5627 |  | 2013-10-07 | 2013-10-07 14:17 | 2013-10-07 14:17 | YORK - H1RA042S06G | 84 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | 06C2C4BE152D4D6498BCBCC3128DE631 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-2332 |  | 2013-10-07 | 2013-10-07 15:03 | 2013-10-07 16:37 | AMANA - RCE36A2D | 150 | 16.6 | Yes | Yes | 21.3 | 21 | 0.3 | 1B8187FDBDD549CCAACBBB3E1BABF87A |  | R22 | TXV |  | 11.07% | 0.88933 | 21.27% | [5 empty] | TXV | 11.07%
Stockton | CA | 95206-3840 |  | 2013-10-10 | 2013-10-10 14:32 | 2013-10-10 15:00 | RHEEM - UNK | 85 | 10.7 | Yes | Yes | 17.8 | 18.8 | -1 | B5482B825CFA4E459276F7144E11912E |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Lathrop | CA | 95330-8832 |  | 2013-10-24 | 2013-10-24 12:03 | 2013-10-24 12:19 | GUARDIAN - CLK36-1L | 88 | 3 | Yes | Yes | 18.5 | 17.7 | 0.8 | 39BC64CB3B084E249382CE2A239131B2 |  | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Lathrop | CA | 95330-9415 |  | 2013-10-11 | 2013-10-11 12:57 | 2013-10-11 12:57 | DAY & NIGHT - 585HJW024040ABAE | 85 | 0 | Yes | Yes | 15.5 | 18.1 | -2.6 | 5347774116AB4A538BFF0FB1FF9BFE7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-2023 |  | 2013-10-10 | 2013-10-10 15:31 | 2013-10-10 15:52 | RHEEM - 13AJA30A01757 | 74 | 3.5 | Yes | Yes | 18.1 | 19.9 | -1.8 | 91E5A56085204AD6A592DBE2BA8DC4C1 |  | R22 | Non-TXV |  | 4.73% | 0.9527 | 9.09% | [5 empty] | Non-TXV | 4.73%
Sonora | CA | 95370-9559 |  | 2013-10-14 | 2013-10-14 15:39 | 2013-10-14 16:15 | GOODMAN - CK42-1C | 92 | 9.7 | Yes | Yes | 25.3 | 19.5 | 5.8 | 1E8C2FA1219C43E6AC7AEBBEE9CECD4E |  | R22 | Non-TXV |  | 10.54% | 0.89457 | 20.26% | [5 empty] | Non-TXV | 10.54%
Stockton | CA | 95206-3840 |  | 2013-10-11 | 2013-10-11 13:56 | 2013-10-11 14:24 | GOODMAN - NUK | 85 | 4.8 | Yes | Yes | 19.2 | 19.5 | -0.3 | D249EBEAE35B49B2976B0DAE7164D70B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Manteca | CA | 95337-4256 |  | 2013-10-08 | 2013-10-08 12:10 | 2013-10-08 12:33 | RUUD - UAHE-023JAS | 64 | 1.9 | Yes | Yes | 24.3 | 20.7 | 3.6 | C6AFD45F17304087824C668F99101FFB |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Stockton | CA | 95209-5186 |  | 2013-10-10 | 2013-10-10 16:42 | 2013-10-10 17:04 | BDP - 585HJ036060 | 102 | 20 | Yes | Yes | 25.9 | 20.3 | 5.6 | 17AF724CBF434A3E8421B74059633850 |  | R22 | Non-TXV |  | 19.61% | 0.80392 | 37.68% | [5 empty] | Non-TXV | 19.61%
El Dorado Hills | CA | 95762-4312 |  | 2013-10-11 | 2013-10-11 17:23 | 2013-10-11 17:23 | DAY & NIGHT - 542D048HP | 163 | 0 | Yes | Yes | 21.6 | 20.1 | 1.5 | 74ED169FAD4A44C7B02724F858CF4A2A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-8949 |  | 2013-10-17 | 2013-10-17 10:52 | 2013-10-17 11:19 | YORK - H2RA036S06E | 63 | 3.6 | Yes | Yes | 15.9 | 17.2 | -1.3 | B7803992C24749B9996045034F42A931 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Lathrop | CA | 95330-9682 |  | 2013-10-24 | 2013-10-24 11:36 | 2013-10-24 12:00 | PAYNE - PA13NA042-C | 85 | 9.2 | Yes | Yes | 14.9 | 17.7 | -2.8 | 3B3578301C0E4BEA9C8FBD8986D97259 |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
Manteca | CA | 95337-4262 |  | 2013-10-07 | 2013-10-07 15:43 | 2013-10-07 16:03 | RUUD - UAHE-023JAS | 64 | 1.9 | Yes | Yes | 21.8 | 19.8 | 2 | 6B6A798DC4284A27860BEAF4145057A4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Madera | CA | 93638-1786 |  | 2013-10-08 | 2013-10-08 13:38 | 2013-10-08 13:40 | BRYANT - 574BNW036060NB | 149 | 12.7 | Yes | Yes | 25.9 | 20.8 | 5.1 | 3BC610A3F7994CB4BA16536DF3F37FCE |  | R410A | Non-TXV |  | 8.523% | 0.91477 | 16.38% | [5 empty] | Non-TXV | 8.523%
Lincoln | CA | 95648-9622 |  | 2013-10-09 | 2013-10-09 11:57 | 2013-10-09 12:19 | GOODMAN - GPG13360701AC | 112 | 4.1 | Yes | Yes | 26 | 20.4 | 5.6 | 3B83EF381C5E4D26A6697171D7D8F10B |  | R22 | TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | TXV | 3.661%
Lincoln | CA | 95648-9622 |  | 2013-10-09 | 2013-10-09 12:21 | 2013-10-09 12:21 | GOODMAN - GPG13360701AC | 112 | 0 | Yes | Yes | 10 | 20.8 | -10.8 | 3446D26034BC4704BBB36436384299BA |  | R22 | TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-0000 |  | 2013-10-11 | 2013-10-11 10:05 | 2013-10-11 10:05 | YORK - H2RD060S06B | 162 | 0 | Yes | Yes | 19.8 | 18.5 | 1.3 | B03E64D249BC4EAEBC080CC87C8FF4F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-7911 |  | 2013-10-16 | 2013-10-16 13:14 | 2013-10-16 13:42 | YORK - H2RA036S06E | 63 | 4.3 | Yes | Yes | 22.3 | 19.6 | 2.8 | 94AC02DCDC33470FBD880DD687C833FE |  | R22 | Non-TXV |  | 6.825% | 0.93175 | 13.12% | [5 empty] | Non-TXV | 6.825%
Tracy | CA | 95376-0711 |  | 2013-10-09 | 2013-10-09 12:52 | 2013-10-09 13:13 | CARRIER - 59ANX036000AAAA | 83 | -6.8 | Yes | Yes | 26.2 | 20.3 | 6 | BE53E2B6F42C43CD8F34D76802C9CDEF |  | R22 | Non-TXV |  | -8.193% | 1.0819 | 2.294% |  |  |  |  | Non-TXV |  |  | -8.193%
San Carlos | CA | 94070-4245 |  | 2013-10-14 | 2013-10-14 14:13 | 2013-10-14 14:30 | TRANE - 4TTR5060E1000AB | 136 | 5 | Yes | Yes | 20 | 19.8 | 0.2 | 617D72FCA8A94102BDC2A38C3B965B1A |  | R410A | TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | TXV | 3.676%
Stockton | CA | 95204-3737 |  | 2013-10-22 | 2013-10-22 10:59 | 2013-10-22 11:05 | PAYNE - 591AN030-B | 69 | 7.7 | Yes | Yes | 22.3 | 19.7 | 2.6 | 8DCBFE5BDF904522994C5D6E725CECD3 |  | R22 | Non-TXV |  | 11.16% | 0.88841 | 21.45% | [5 empty] | Non-TXV | 11.16%
Los Banos | CA | 93635-3832 |  | 2013-10-08 | 2013-10-08 11:31 | 2013-10-08 11:33 | BRYANT - 583ANW024060AAHD | 52 | 2.1 | Yes | Yes | 18.4 | 20.8 | -2.4 | 5752D30C6F8749C7A7DA5306FF500B68 |  | R22 | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
Lincoln | CA | 95648-2126 |  | 2013-10-21 | 2013-10-21 11:28 | 2013-10-21 11:48 | RHEEM - RACB-030JAS | 46 | 1.4 | Yes | Yes | 21 | 20.1 | 0.9 | C31EA9739AC04AE1BBAE12A20F9E51CC |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Stockton | CA | 95204-2004 |  | 2013-10-07 | 2013-10-07 11:49 | 2013-10-07 12:06 | BRYANT - 561CJX036-D | 85 | 7.2 | Yes | Yes | 21.7 | 17.6 | 4.1 | C964057EBC214E1DB5BEABC30172B394 |  | R22 | TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | TXV | 8.471%
Oroville | CA | 95966-5555 |  | 2013-10-17 | 2013-10-17 12:30 | 2013-10-17 13:06 | AMANA - APG12360701A | 85 | 5.5 | Yes | Yes | 16.7 | 19.3 | -2.6 | D912B72296564655A972F0BDFEA0CF9C |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Stockton | CA | 95210-2324 |  | 2013-10-07 | 2013-10-07 12:53 | 2013-10-07 13:15 | BRYANT - 582ANW024040NAAD | 53 | 3.1 | Yes | Yes | 28.1 | 23.1 | 5 | 9E23431CC7534A46B16DBEB07D878ADC |  | R22 | Non-TXV |  | 5.849% | 0.94151 | 11.24% | [5 empty] | Non-TXV | 5.849%
Stockton | CA | 95206-3832 |  | 2013-10-10 | 2013-10-10 09:20 | 2013-10-10 09:43 | DAY & NIGHT - UNK | 85 | -8 | Yes | Yes | 26.6 | 20.7 | 5.9 | 403ACF71DFEA46BEBD1E8B39DE546AD6 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Lincoln | CA | 95648-2324 |  | 2013-10-09 | 2013-10-09 14:14 | 2013-10-09 14:14 | AMERICAN STANDARD - 2A7B3030A1000AA | 88 | 0 | Yes | Yes | 18 | 20.3 | -2.3 | 8C50C3654E0143E4A4E9C041AA156681 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Jamestown | CA | 95327-9439 |  | 2013-10-21 | 2013-10-21 11:45 | 2013-10-21 12:20 | COLEMAN - BRCS0481BD | 117 | 3.5 | Yes | Yes | 25.3 | 20.1 | 5.2 | D446B229C1044329B5A2BD2B45031955 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Lathrop | CA | 95330-8697 |  | 2013-10-11 | 2013-10-11 11:40 | 2013-10-11 11:59 | CARRIER - 24ABA336A310 | 86 | 10 | Yes | Yes | 21.4 | 19 | 2.4 | 387B842F8A644D3580F180123850B3EE |  | R410A | TXV |  | 11.63% | 0.88372 | 22.35% | [5 empty] | TXV | 11.63%
Lathrop | CA | 95330-9458 |  | 2013-10-11 | 2013-10-11 13:59 | 2013-10-11 14:15 | KENMORE - TCA030AKA5 | 74 | 3.2 | Yes | Yes | 24.2 | 19.1 | 5.2 | 5F263C20A3E4402FA406ABA03EE3216F |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
Stockton | CA | 95209-3014 |  | 2013-10-15 | 2013-10-15 11:49 | 2013-10-15 12:10 | PAYNE - PGN342090K01AZ1 | 120 | 5.9 | Yes | Yes | 21.5 | 19.4 | 2.1 | 4CAA68D1AEF940EFA0EC4F0C2366F9AC |  | R22 | Non-TXV |  | 4.917% | 0.95083 | 9.449% | [5 empty] | Non-TXV | 4.917%
Manteca | CA | 95336-3459 |  | 2013-10-22 | 2013-10-22 11:32 | 2013-10-22 12:01 | YORK - MC30-10A | 56 | 2.7 | Yes | Yes | 23.1 | 19.9 | 3.2 | 40C8DEA6EAD04B8AAAB25E7157C74BF8 |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Chico | CA | 95926-3057 |  | 2013-10-08 | 2013-10-08 15:14 | 2013-10-08 15:35 | DAY & NIGHT - 591ANX03000AAAA | 76 | 7.5 | Yes | Yes | 19.2 | 19.7 | -0.5 | 33FC346F03BC492C811BC49044738FC8 |  | R22 | Non-TXV |  | 9.868% | 0.90132 | 18.96% | [5 empty] | Non-TXV | 9.868%
Stockton | CA | 95205-7822 |  | 2013-10-09 | 2013-10-09 12:55 | 2013-10-09 13:16 | YORK - D1NA036NO5606C | 67 | 3.7 | Yes | Yes | 24.4 | 18.8 | 5.6 | A87498FCC8A84B45954A08EFA063631A |  | R22 | Non-TXV |  | 5.522% | 0.94478 | 10.61% | [5 empty] | Non-TXV | 5.522%
Manteca | CA | 95337-4244 |  | 2013-10-17 | 2013-10-17 14:27 | 2013-10-17 14:48 | RUUD - UAHE-023JAS | 64 | 2.9 | Yes | Yes | 21.8 | 20.3 | 1.5 | A0F4123A07A2404AA95FED87897C1752 |  | R22 | Non-TXV |  | 4.531% | 0.95469 | 8.708% | [5 empty] | Non-TXV | 4.531%
Tracy | CA | 95376-5247 |  | 2013-10-07 | 2013-10-07 11:29 | 2013-10-07 11:49 | CARRIER - 38CKC048370 | 100 | 5.1 | Yes | Yes | 25.5 | 19.9 | 5.6 | 4B2EB96D0B064BCDB6EA814E0E280EB6 |  | R22 | Non-TXV |  | 5.1% | 0.949 | 9.801% | [5 empty] | Non-TXV | 5.1%
Madera | CA | 93637-4263 |  | 2013-10-11 | 2013-10-11 10:57 | 2013-10-11 10:59 | CARRIER - 38CK060310 | 131 | 10 | Yes | Yes | 21.2 | 16.5 | 4.7 | DAD2ACF566704404ACC5564089712538 |  | R22 | Non-TXV |  | 7.634% | 0.92366 | 14.67% | [5 empty] | Non-TXV | 7.634%
Auburn | CA | 95603-9759 |  | 2013-10-07 | 2013-10-07 14:22 | 2013-10-07 14:41 | OTHER - 361CJ036-D | 85 | 4 | Yes | Yes | 19 | 21.7 | -2.7 | 2017F14A34124A99A9472AACDBE778B6 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Madera | CA | 93637-4965 |  | 2013-10-11 | 2013-10-11 12:41 | 2013-10-11 12:42 | YORK - H1RA060S06A | 124 | 13.1 | Yes | Yes | 23.5 | 18.3 | 5.2 | 2E8E7B048C6F411AB68FAB8F0E0A67E8 |  | R22 | Non-TXV |  | 10.56% | 0.89435 | 20.3% | [5 empty] | Non-TXV | 10.56%
French Camp | CA | 95231-9611 |  | 2013-10-11 | 2013-10-11 12:29 | 2013-10-11 12:49 | YORK - D0NZ048N06506NXA | 85 | 8.7 | Yes | Yes | 17.4 | 19.5 | -2.1 | B40CCBD82B3945F8B6173A734C958B2A |  | R410A | TXV |  | 10.24% | 0.89765 | 19.67% | [5 empty] | TXV | 10.24%
Stockton | CA | 95203-1402 |  | 2013-10-09 | 2013-10-09 13:22 | 2013-10-09 13:40 | BDP - UNK | 39 | 10 | Yes | Yes | 23.5 | 19.7 | 3.8 | 81D51C2099924CE8B039B937B037C8FF |  | R22 | Non-TXV |  | 25.64% | 0.74359 | 49.28% | [5 empty] | Non-TXV | 25.64%
Stockton | CA | 95210-1842 |  | 2013-10-09 | 2013-10-09 10:52 | 2013-10-09 11:09 | OTHER - UNK | 96 | 4 | Yes | Yes | 21.1 | 18 | 3.2 | 1928A4FF461640458676A1466659D370 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Rocklin | CA | 95765-4541 |  | 2013-10-07 | 2013-10-07 16:48 | 2013-10-07 16:48 | GOODMAN - CKJ36-1A | 90 | 0 | Yes | Yes | 23.3 | 20.9 | 2.4 | 162692CF72804DF5BC61C13099F1D962 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95949-8790 |  | 2013-10-10 | 2013-10-10 10:14 | 2013-10-10 10:34 | COLEMAN - BRCQ0421BB | 64 | 2.4 | Yes | Yes | 23 | 20.6 | 2.4 | 0852E5389EC744D09392222CC76884D7 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Tracy | CA | 95376-1886 |  | 2013-10-09 | 2013-10-09 12:12 | 2013-10-09 12:36 | BDP - 565BJ036 | 84 | -7.9 | Yes | Yes | 25.4 | 20.3 | 5.2 | 14DA22C76B8D4F2688379D1A1E49DD13 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Stockton | CA | 95203-1339 |  | 2013-10-09 | 2013-10-09 12:51 | 2013-10-09 13:10 | AMANA - PGD36C0702E | 110 | 4.7 | Yes | Yes | 25.5 | 19.5 | 6 | 17711B7C117240FEA4252CDC05453416 |  | R22 | Non-TXV |  | 4.273% | 0.95727 | 8.211% | [5 empty] | Non-TXV | 4.273%
Rocklin | CA | 95677-2912 |  | 2013-10-08 | 2013-10-08 13:08 | 2013-10-08 13:08 | GE - BG1A736B1B | 70 | 0 | Yes | Yes | 21.8 | 20.6 | 1.2 | A690274AE93049EB803472497CE73B23 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2308 |  | 2013-10-15 | 2013-10-15 13:43 | 2013-10-15 15:19 | PAYNE - KEMCHO2471443 | 50 | 2.6 | Yes | Yes | 18.8 | 17.7 | 1.1 | 07357C32D7334E3EA471B589C89740DF |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Stockton | CA | 95205-2836 |  | 2013-10-11 | 2013-10-11 13:26 | 2013-10-11 13:44 | ARMSTRONG - PGE10B24D050LA-3A | 52 | 5 | Yes | Yes | 21.2 | 18.6 | 2.6 | EA0508E319FB4508B202638A24DDDA02 |  | R22 | Non-TXV |  | 9.615% | 0.90385 | 18.48% | [5 empty] | Non-TXV | 9.615%
Stockton | CA | 95209-3019 |  | 2013-10-15 | 2013-10-15 10:47 | 2013-10-15 11:15 | BRYANT - 583BNW036060AB | 106 | 3.5 | Yes | Yes | 20.6 | 16.2 | 4.4 | EBD10F1E97DA4DACA0DBA2BB9684FAF8 |  | R22 | Non-TXV |  | 3.302% | 0.96698 | 6.345% | [5 empty] | Non-TXV | 3.302%
Tracy | CA | 95376-3134 |  | 2013-10-07 | 2013-10-07 14:00 | 2013-10-07 14:41 | CARRIER - 38CKC060370 | 136 | 13.4 | Yes | Yes | 25.6 | 20.4 | 5.2 | 5A7E3F05A6364A53BE644E611402EE10 |  | R22 | TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | TXV | 9.853%
Redwood City | CA | 94063-4141 |  | 2013-10-21 | 2013-10-21 13:11 | 2013-10-21 13:28 | COLEMAN - BRCQ0241BE | 45 | 2.1 | Yes | Yes | 18.1 | 17.7 | 0.4 | E2A0B646606D4798B995E314EE624ACE |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Chico | CA | 95973-7640 |  | 2013-10-08 | 2013-10-08 16:17 | 2013-10-08 16:34 | CARRIER - 38TRAO48340 | 151 | 4.8 | Yes | Yes | 25.6 | 21.8 | 3.8 | 79199DF1321A47A3A8024F3E22742BCA |  | R22 | Non-TXV |  | 3.179% | 0.96821 | 6.109% | [5 empty] | Non-TXV | 3.179%
Rocklin | CA | 95677-2332 |  | 2013-10-10 | 2013-10-10 15:30 | 2013-10-10 15:46 | RHEEM - RRGF-07E42JKR | 100 | 3.4 | Yes | Yes | 23.5 | 19.5 | 4 | 2A5FB58F55654C20865A9A80FC146DD8 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Stockton | CA | 95206-2487 |  | 2013-10-21 | 2013-10-21 09:38 | 2013-10-21 09:54 | GOODMAN - CE25-1EB | 66 | 10.2 | Yes | Yes | 21.3 | 20.1 | 1.2 | B7AC3D6130154E75B12EB5C9A233FEE4 |  | R22 | Non-TXV |  | 15.45% | 0.84545 | 29.7% | [5 empty] | Non-TXV | 15.45%
Rocklin | CA | 95765-5253 |  | 2013-10-07 | 2013-10-07 13:06 | 2013-10-07 13:06 | OTHER - 563AN036-A | 114 | 0 | Yes | Yes | 26.9 | 21.1 | 5.8 | EEEF0B011B94475A86E157FD295173E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-8786 |  | 2013-10-24 | 2013-10-24 15:37 | 2013-10-24 16:24 | YORK - H2RC042S06G | 109 | 11.2 | Yes | Yes | 20.3 | 21.2 | -0.9 | 5BB53DCA2A434A13AA13A1C92296223F |  | R22 | Non-TXV |  | 10.28% | 0.89725 | 19.75% | [5 empty] | Non-TXV | 10.28%
Stockton | CA | 95206-3845 |  | 2013-10-10 | 2013-10-10 14:57 | 2013-10-10 15:17 | GOODMAN - PGB036075-1A | 60 | 4.3 | Yes | Yes | 25.9 | 20.8 | 5.2 | B8C49579CE5747319D31379ECDB83D10 |  | R22 | Non-TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | Non-TXV | 7.167%
Auburn | CA | 95603-3427 |  | 2013-10-08 | 2013-10-08 13:19 | 2013-10-08 13:38 | COLEMAN - DRC0481BD | 104 | 8.3 | Yes | Yes | 26 | 20.6 | 5.4 | D818C0AF23804395AB70969E48B2359A |  | R22 | Non-TXV |  | 7.981% | 0.92019 | 15.34% | [5 empty] | Non-TXV | 7.981%
Stockton | CA | 95210-6707 |  | 2013-10-07 | 2013-10-07 10:17 | 2013-10-07 10:40 | YORK - H2RD036S06B | 96 | 3.1 | Yes | Yes | 24 | 20.4 | 3.6 | 0CD04D134B9E4E52BBA90BBC0ACA7D14 |  | R22 | Non-TXV |  | 3.229% | 0.96771 | 6.206% | [5 empty] | Non-TXV | 3.229%
Manteca | CA | 95337-8406 |  | 2013-10-17 | 2013-10-17 10:19 | 2013-10-17 10:40 | YORK - H4DE042S06A | 93 | 2.8 | Yes | Yes | 24.7 | 20.1 | 4.6 | 58BACA422BD54A02BF76D6CCCBC615B6 |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
El Dorado Hills | CA | 95762-5929 |  | 2013-10-10 | 2013-10-10 12:39 | 2013-10-10 12:39 | PAYNE - 591ANX060-A | 170 | 0 | Yes | Yes | 22.7 | 20.7 | 2 | BDDCEFC102884A43B75778A8F02F397B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-4225 |  | 2013-10-10 | 2013-10-10 14:20 | 2013-10-10 14:20 | RUUD - UAHE-023JAS | 64 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 54D8A8DFDC1B49E49E29664679664ADF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-0000 |  | 2013-10-09 | 2013-10-09 11:06 | 2013-10-09 11:23 | YORK - H2RC042S06G | 109 | 3.2 | Yes | Yes | 27 | 21.7 | 5.3 | 2C034D4021D14BE1A276AC728A0EE789 |  | R22 | Non-TXV |  | 2.936% | 0.97064 | 5.642% | [5 empty] | Non-TXV | 2.936%
Rocklin | CA | 95677-4482 |  | 2013-10-07 | 2013-10-07 18:08 | 2013-10-07 18:08 | GOODMAN - CK60-1C | 122 | 0 | Yes | Yes | 21.3 | 21.8 | -0.5 | 5E42B4F8BCCF4ACDA4ABE97675288BDA |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-1889 |  | 2013-10-09 | 2013-10-09 11:45 | 2013-10-09 12:10 | HEIL - ACS030A2C1 | 71 | 7 | Yes | Yes | 23.6 | 20.1 | 3.5 | F24696CDF2C34A6581DB7291AB867C84 |  | R22 | Non-TXV |  | 9.859% | 0.90141 | 18.95% | [5 empty] | Non-TXV | 9.859%
Riverbank | CA | 95367-2969 |  | 2013-10-11 | 2013-10-11 14:55 | 2013-10-11 15:15 | RUUD - CBD | 64 | 2.1 | Yes | Yes | 21.7 | 20.7 | 1 | FC8B2CF6DA4A4407A7079672C12AEC30 |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Manteca | CA | 95337-4259 |  | 2013-10-08 | 2013-10-08 15:55 | 2013-10-08 16:23 | RUUD - UAHE-030JAS | 77 | 2.3 | Yes | Yes | 24.3 | 21 | 3.3 | 665CBF536FA442CF8DDE469FED8A88FA |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Escalon | CA | 95320-2156 |  | 2013-10-11 | 2013-10-11 14:06 | 2013-10-11 14:30 | TRANE - | 118 | 3.8 | Yes | Yes | 23.3 | 19.5 | 3.8 | 043ADBC6ECEB49F1BC6A85889BD50DF5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.22% | 0.9678 | 6.189% | [5 empty] | Non-TXV | 3.22%
Chico | CA | 95926-1627 |  | 2013-10-07 | 2013-10-07 15:52 | 2013-10-07 16:09 | YORK - H1CH048506B | 195 | 5.9 | Yes | Yes | 21.3 | 23.1 | -1.8 | 5329CF4AACF942CAA97FC877C12802B6 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.815% | [5 empty] | Non-TXV | 3.026%
Manteca | CA | 95336-4512 |  | 2013-10-16 | 2013-10-16 14:15 | 2013-10-16 14:34 | RUUD - CBD | 64 | 5.4 | Yes | Yes | 26.9 | 21.3 | 5.6 | 9652F70271634134A2F508F8CE299E8B |  | R22 | Non-TXV |  | 8.438% | 0.91563 | 16.22% | [5 empty] | Non-TXV | 8.438%
Orland | CA | 95963-1972 |  | 2013-10-10 | 2013-10-10 14:00 | 2013-10-10 14:29 | RUUD - 13AJA24A01 | 77 | 6 | Yes | Yes | 19 | 20.7 | -1.7 | B9C26594C33F47CBA5A871DD4B1D32A6 |  | R22 | Non-TXV |  | 7.792% | 0.92208 | 14.97% | [5 empty] | Non-TXV | 7.792%
Atascadero | CA | 93422-3730 |  | 2013-10-10 | 2013-10-10 12:54 | 2013-10-10 13:10 | NORDYNE - FS3BC-060KA | 165 | -9.7 | Yes | Yes | 22.1 | 19.1 | 3 | 02D1CC9297B2441185E71796DF5CB65E |  | R22 | Non-TXV |  | -5.879% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.879%
Stockton | CA | 95206-5812 |  | 2013-10-10 | 2013-10-10 17:07 | 2013-10-10 17:44 | YORK - D3NZ036N05606NXA | 64 | 5 | Yes | Yes | 21.6 | 20.7 | 1 | 76052144C5AF4CFB8E13A187D7FA29B1 |  | R410A | Non-TXV |  | 7.812% | 0.92188 | 15.01% | [5 empty] | Non-TXV | 7.812%
Stockton | CA | 95206-1274 |  | 2013-10-10 | 2013-10-10 16:22 | 2013-10-10 16:49 | ICP - GPCM042K080I | 84 | 6.2 | Yes | Yes | 25.7 | 20.3 | 5.4 | B5BDDB6F297B403982CC10BABBA01D0C |  | R22 | Non-TXV |  | 7.381% | 0.92619 | 14.18% | [5 empty] | Non-TXV | 7.381%
Madera | CA | 93637-2626 |  | 2013-10-07 | 2013-10-07 13:56 | 2013-10-07 13:58 | BRYANT - 574BNW048090NB | 178 | 6.1 | Yes | Yes | 21 | 18.8 | 2.2 | 0BFEC958434D4739BE59800FCB024655 |  | R410A | Non-TXV |  | 3.427% | 0.96573 | 6.586% | [5 empty] | Non-TXV | 3.427%
Merced | CA | 95341-6963 |  | 2013-10-07 | 2013-10-07 15:40 | 2013-10-07 15:41 | RHEEM - RRKAA024JK06X | 50 | 7 | Yes | Yes | 30.4 | 24.7 | 5.7 | F29CB62185C44646A76BEE3D771BD98C |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Stockton | CA | 95206-1273 |  | 2013-10-18 | 2013-10-18 11:10 | 2013-10-18 11:29 | BRYANT - 561CJ018 | 60 | 2.8 | Yes | Yes | 18 | 17.7 | 0.3 | 6981B08CEFB3498181290D6EC8AB2640 |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Madera | CA | 93637-0000 |  | 2013-10-08 | 2013-10-08 09:52 | 2013-10-08 09:53 | ICP - NAC036AKA1 | 87 | 4.5 | Yes | Yes | 22.3 | 17.2 | 5.1 | FF2FDB658C7F46D6A6F786692608CEB2 |  | R22 | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Madera | CA | 93637-4903 |  | 2013-10-08 | 2013-10-08 10:42 | 2013-10-08 10:45 | ICP - 48KLA160 | 160 | 8.4 | Yes | Yes | 24.6 | 18.7 | 5.9 | 6A6B80E1FE2D45B28F9A9F7F299E82BB |  | R22 | Non-TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | Non-TXV | 5.25%
Copperopolis | CA | 95228-9709 |  | 2013-10-16 | 2013-10-16 13:29 | 2013-10-16 13:47 | PAYNE - PY1PNB036090AAAA | 56 | 2.6 | Yes | Yes | 18.7 | 21.2 | -2.5 | BCBB094F04E1458694F5A017F2DD832E |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Angels Camp | CA | 95222-0000 |  | 2013-10-15 | 2013-10-15 09:57 | 2013-10-15 10:26 | RHEEM - RAHE-048JAS | 114 | 46.8 | Yes | Yes | 17.8 | 20.7 | -2.9 | 988B52C8FED943D7864216B310AE418E |  | R22 | Non-TXV |  | 41.05% | 0.58947 | 78.89% | [5 empty] | Non-TXV | 41.05%
Stockton | CA | 95210-2343 |  | 2013-10-07 | 2013-10-07 12:26 | 2013-10-07 12:44 | TRANE - TTX730A1036A | 121 | 4.1 | Yes | Yes | 24.5 | 19.9 | 4.6 | 493F4F9CCB0C4EB68E3712554F808A34 |  | R22 | Non-TXV |  | 3.388% | 0.96612 | 6.512% | [5 empty] | Non-TXV | 3.388%
Cameron Park | CA | 95682-9248 |  | 2013-10-11 | 2013-10-11 14:18 | 2013-10-11 14:42 | NORDYNE - JS5BD-048K | 147 | 13.4 | Yes | Yes | 26.3 | 20.4 | 5.9 | 9FFAB02F11574DD987411BCE470881CD |  | R22 | Non-TXV |  | 9.116% | 0.90884 | 17.52% | [5 empty] | Non-TXV | 9.116%
Grass Valley | CA | 95949-8881 |  | 2013-10-21 | 2013-10-21 14:28 | 2013-10-21 14:28 | LENNOX - GCS20RV-411-75-1P | 70 | 0 | Yes | Yes | 25.5 | 20.1 | 5.4 | 87B08CA16DF74DDB9215FA7FEED742A8 |  | R22 | TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-3619 |  | 2013-10-07 | 2013-10-07 12:04 | 2013-10-07 12:54 | GE - NA | 60 | 8.5 | Yes | Yes | 18 | 19.7 | -1.7 | F51E06A99A8548DE9F6C782FB6FDF565 |  | R22 | Non-TXV |  | 14.17% | 0.85833 | 27.23% | [5 empty] | Non-TXV | 14.17%
Merced | CA | 95341-6831 |  | 2013-10-07 | 2013-10-07 16:22 | 2013-10-07 16:23 | GOODMAN - GPG10360701A | 75 | 12.5 | Yes | Yes | 23.1 | 19 | 4.2 | 0606A29780F24B9097BDB1F42C28117B |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Merced | CA | 95340-2376 |  | 2013-10-04 | 2013-10-04 15:40 | 2013-10-04 15:41 | GOODMAN - CK361B | 76 | 7.1 | Yes | Yes | 25.1 | 20.4 | 4.7 | CE43A66FEFEA40898A0092D525D170D6 |  | R22 | Non-TXV |  | 9.342% | 0.90658 | 17.95% | [5 empty] | Non-TXV | 9.342%
Rocklin | CA | 95765-4167 |  | 2013-10-17 | 2013-10-17 14:51 | 2013-10-17 14:51 | OTHER - 4AC13L42P-6A | 102 | 0 | Yes | Yes | 27.4 | 22.5 | 4.9 | 4E58BBEF81604667AA2A62CE593D0BB2 |  | R410A | TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-2453 |  | 2013-10-08 | 2013-10-08 12:38 | 2013-10-08 12:55 | DAY & NIGHT - A | 70 | 6 | Yes | Yes | 18 | 20.9 | -2.9 | 7A505E84D5FD4EE8BF243BE6F9CDEBB1 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Lathrop | CA | 95330-9714 |  | 2013-10-11 | 2013-10-11 10:55 | 2013-10-11 11:12 | CARRIER - 38TH042310 | 112 | 6.1 | Yes | Yes | 22.8 | 18.8 | 4 | B6836D5705864CFA84E960A27C0009FD |  | R22 | Non-TXV |  | 5.446% | 0.94554 | 10.47% | [5 empty] | Non-TXV | 5.446%
Cameron Park | CA | 95682-9019 |  | 2013-10-18 | 2013-10-18 15:03 | 2013-10-18 15:25 | RHEEM - UNK | 154 | 5.6 | Yes | Yes | 21 | 20.6 | 0.4 | 124EDE605CA34388832F5B7A790803C5 |  | R410A | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Stockton | CA | 95206-4860 |  | 2013-10-11 | 2013-10-11 14:38 | 2013-10-11 15:00 | RHEEM - RAFD031JAS | 64 | 7.2 | Yes | Yes | 23 | 21 | 2 | 85FA4CE54F234BD89542A6E47C47C2C3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Lincoln | CA | 95648-2922 |  | 2013-10-09 | 2013-10-09 14:52 | 2013-10-09 15:10 | YORK - H2RC030S06A | 88 | 2.6 | Yes | Yes | 18 | 20.6 | -2.6 | CD81B62C302F44F2B65731CB0B3A4A31 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Madera | CA | 93637-8664 |  | 2013-10-08 | 2013-10-08 14:16 | 2013-10-08 14:17 | CARRIER - 38CKC042350 | 93 | 4 | Yes | Yes | 23.7 | 21 | 2.7 | B60058763D754130A8013065913EC98E |  | R22 | TXV |  | 4.301% | 0.95699 | 8.266% | [5 empty] | TXV | 4.301%
Chico | CA | 95926-4680 |  | 2013-10-21 | 2013-10-21 13:12 | 2013-10-21 13:32 | PAYNE - NA | 55 | 6.6 | Yes | Yes | 19.3 | 19.6 | -0.3 | 822437FB71DC4EB5AF74A04550CF589F |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Stockton | CA | 95205-6370 |  | 2013-10-31 | 2013-10-31 14:49 | 2013-10-31 15:06 | RHEEM - RRNA-B024JK06X | 70 | -4.1 | Yes | Yes | 27 | 21 | 6 | FA5830AE3BCC47F3868EF7A12ECBA505 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Grass Valley | CA | 95949-7606 |  | 2013-10-08 | 2013-10-08 11:20 | 2013-10-08 11:51 | TRANE - TTN048C100A3 | 135 | 4 | Yes | Yes | 25 | 21.4 | 3.6 | 4A06260FC73D4AF4AD87879F000E44F5 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Sonora | CA | 95370-5116 |  | 2013-10-14 | 2013-10-14 13:15 | 2013-10-14 13:33 | AMANA - APG13300701B | 77 | -6.5 | Yes | Yes | 22.3 | 19.7 | 2.6 | 4569F218218E4AACB17A8B38C8710EB5 |  | R22 | TXV |  | -8.442% | 1.0844 | 2.364% |  |  |  |  | TXV |  |  | -8.442%
Merced | CA | 95340-5642 |  | 2013-10-04 | 2013-10-04 14:56 | 2013-10-04 14:57 | ICP - PGC042K080B | 87 | 13.2 | Yes | Yes | 20.4 | 18.2 | 2.2 | 31043357BE9B4E90BACFA2B2A697ACB4 |  | R22 | Non-TXV |  | 15.17% | 0.84828 | 29.16% | [5 empty] | Non-TXV | 15.17%
Madera | CA | 93637-8646 |  | 2013-11-02 | 2013-11-02 12:21 | 2013-11-02 12:23 | CARRIER - 38CK0422356 | 93 | 4 | Yes | Yes | 22.2 | 19.7 | 2.5 | DD35A55C83384324A8E61D0952758417 |  | R22 | Non-TXV |  | 4.301% | 0.95699 | 8.266% | [5 empty] | Non-TXV | 4.301%
Stockton | CA | 95204-2241 |  | 2013-10-17 | 2013-10-17 11:10 | 2013-10-17 11:28 | DAY & NIGHT - 585EJW024050AAA8 | 54 | 3.9 | Yes | Yes | 23.2 | 19.3 | 3.9 | F4254B2496054FAF946F4F5B3D071ECF |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Fresno | CA | 93722-3636 |  | 2013-10-25 | 2013-10-25 14:58 | 2013-10-25 15:18 | CARRIER - N/A | 90 | 3.9 | Yes | Yes | 25 | 20.4 | 4.6 | 3757C4AA82F444B69D1792C8519417FE |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Gustine | CA | 95322-1957 |  | 2013-10-09 | 2013-10-09 13:50 | 2013-10-09 13:51 | CARRIER - 568EJX024000ABAA | 112 | 10.1 | Yes | Yes | 22.8 | 19.3 | 3.5 | FB0381DFD9204F14A8C72520784E0E03 |  | R22 | Non-TXV |  | 9.018% | 0.90982 | 17.33% | [5 empty] | Non-TXV | 9.018%
Gustine | CA | 95322-1956 |  | 2013-10-09 | 2013-10-09 13:14 | 2013-10-09 13:17 | CARRIER - 568EJX024000ABAA | 112 | 9.5 | Yes | Yes | 21.5 | 17.2 | 4.3 | E60ADF5A15AE47B78F4B76E90B37A416 |  | R22 | Non-TXV |  | 8.482% | 0.91518 | 16.3% | [5 empty] | Non-TXV | 8.482%
Gustine | CA | 95322-1959 |  | 2013-10-21 | 2013-10-21 11:38 | 2013-10-21 11:40 | OTHER - 58EJX024000ABAA | 112 | 12.5 | Yes | Yes | 22.2 | 21 | 1.2 | BBC985DF3E074831A633B6B81FFFA8A6 |  | R22 | Non-TXV |  | 11.16% | 0.88839 | 21.45% | [5 empty] | Non-TXV | 11.16%
Stockton | CA | 95212-1519 |  | 2013-10-09 | 2013-10-09 12:02 | 2013-10-09 12:20 | ICP - N2A360AKB400 | 146 | 5.7 | Yes | Yes | 19.8 | 20.2 | -0.4 | BEC80B5A37C54D6294105B8A5C46CC65 |  | R22 | TXV |  | 3.904% | 0.96096 | 7.503% | [5 empty] | TXV | 3.904%
Stockton | CA | 95210-2072 |  | 2013-10-07 | 2013-10-07 15:05 | 2013-10-07 15:24 | DAY & NIGHT - UNK | 64 | 6 | Yes | Yes | 25.8 | 19.9 | 5.9 | 6EBC19686087443DAA7AA03E289484D2 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Newman | CA | 95360-1868 |  | 2013-10-09 | 2013-10-09 11:54 | 2013-10-09 11:56 | CARRIER - 561AJ042 | 88 | 10.1 | Yes | Yes | 26.1 | 20.4 | 5.7 | EA51AF9809054AE984AE9BFD3DD361FB |  | R22 | TXV |  | 11.48% | 0.88523 | 22.06% | [5 empty] | TXV | 11.48%
Merced | CA | 95348-3123 |  | 2013-10-10 | 2013-10-10 07:25 | 2013-10-10 07:27 | GOODMAN - CFKE18-1A | 75 | 4.6 | Yes | Yes | 18.1 | 19.1 | -0.9 | 0442877D575C445380D25B0998B84A49 |  | R22 | Non-TXV |  | 6.133% | 0.93867 | 11.79% | [5 empty] | Non-TXV | 6.133%
Newman | CA | 95360-1411 |  | 2013-10-09 | 2013-10-09 11:10 | 2013-10-09 11:18 | AMANA - APG13360701AB | 112 | 9.9 | Yes | Yes | 24.3 | 19.1 | 5.2 | 3F9E21CB81834E18AB09BD83C4DFB525 |  | R22 | Non-TXV |  | 8.839% | 0.91161 | 16.99% | [5 empty] | Non-TXV | 8.839%
Stockton | CA | 95204-2111 |  | 2013-10-18 | 2013-10-18 09:51 | 2013-10-18 09:59 | GOODMAN - CKL36-1H | 71 | -5 | Yes | Yes | 22.7 | 18.6 | 4.2 | BDD285962BA846F9851A57FD13CAC898 |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Merced | CA | 95348-3179 |  | 2013-10-18 | 2013-10-18 17:19 | 2013-10-18 17:20 | RHEEM - RAHE023JAS | 64 | 7.5 | Yes | Yes | 21.2 | 18.8 | 2.4 | 884FC36434624F73AA359E380415894E |  | R22 | Non-TXV |  | 11.72% | 0.88281 | 22.52% | [5 empty] | Non-TXV | 11.72%
Merced | CA | 95348-3180 |  | 2013-10-10 | 2013-10-10 12:31 | 2013-10-10 12:32 | GOODMAN - CPKE181A | 75 | 6.5 | Yes | Yes | 19.9 | 16.5 | 3.4 | 36D1FA66C97249B5A66B994049C11700 |  | R22 | Non-TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | Non-TXV | 8.667%
Arnold | CA | 95223-0000 |  | 2013-10-16 | 2013-10-16 11:16 | 2013-10-16 11:34 | ICP - NAC042AJC3 | 112 | -6.6 | Yes | Yes | 25.9 | 20.7 | 5.2 | 36E784C4B4564B09A0354BD58DDD6B91 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Lathrop | CA | 95330-8897 |  | 2013-10-17 | 2013-10-17 11:48 | 2013-10-17 12:11 | CARRIER - UNK | 131 | 9.9 | Yes | Yes | 16.8 | 17.7 | -0.9 | 770DF92F93194A98B599409EB0E6377D |  | R22 | Non-TXV |  | 7.557% | 0.92443 | 14.52% | [5 empty] | Non-TXV | 7.557%
Merced | CA | 95348-2717 |  | 2013-10-10 | 2013-10-10 13:26 | 2013-10-10 13:27 | TRANE - TTD724B100BO | 60 | 6.7 | Yes | Yes | 20.7 | 17.7 | 3 | 376ED9EEC15E44B49C3CCBE443C00799 |  | R22 | Non-TXV |  | 11.17% | 0.88833 | 21.46% | [5 empty] | Non-TXV | 11.17%
Merced | CA | 95341-7030 |  | 2013-10-21 | 2013-10-21 15:41 | 2013-10-21 15:42 | BRYANT - 582ANW036060NBAF | 68 | 7.4 | Yes | Yes | 21.8 | 18.1 | 3.7 | 9210197E9FF441E6AF3770C77C9467BA |  | R22 | Non-TXV |  | 10.88% | 0.89118 | 20.91% | [5 empty] | Non-TXV | 10.88%
Foresthill | CA | 95631-0000 |  | 2013-10-25 | 2013-10-25 10:28 | 2013-10-25 10:28 | CARRIER - 24ABR324A310 | 74 | 0 | Yes | Yes | 25.2 | 20.9 | 4.3 | 8BDCD5EE54234B5ABC3972D08B8F6562 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-0000 |  | 2013-10-25 | 2013-10-25 11:04 | 2013-10-25 11:04 | CARRIER - 24ABR336A310 | 93 | 0 | Yes | Yes | 26.1 | 20.7 | 5.4 | BD710716E08E4E8B979AFF2DE36026AD |  | R22 | TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-0000 |  | 2013-10-25 | 2013-10-25 11:24 | 2013-10-25 11:24 | CARRIER - 24ABR336A310 | 93 | 0 | Yes | Yes | 25.2 | 20.9 | 4.3 | 170459C3E60B4D67BC6D2DDC6C8F5E23 |  | R22 | TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-8013 |  | 2013-10-08 | 2013-10-08 12:28 | 2013-10-08 12:48 | HEIL - UNK | 90 | 2.7 | Yes | Yes | 26 | 20.9 | 5.1 | 65BBE1BF6C874606AFDD070132665798 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-3731 |  | 2013-10-11 | 2013-10-11 11:49 | 2013-10-11 12:06 | RHEEM - ARGG-07N36JKR | 75 | -4.4 | Yes | Yes | 21.6 | 18.2 | 3.4 | D66B947D0E29421F9ECAC095CE5A7B29 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Merced | CA | 95341-6829 |  | 2013-10-09 | 2013-10-09 11:35 | 2013-10-09 11:37 | RHEEM - RAKB-036JAZ | 79 | 2.6 | Yes | Yes | 20.4 | 19.9 | 0.5 | 45402EC22F884245805CA3DA6CA6B332 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Merced | CA | 95348-3126 |  | 2013-10-16 | 2013-10-16 09:54 | 2013-10-16 09:55 | AIRE-FLO - BWB918A10000 | 77 | 5 | Yes | Yes | 22.6 | 17.7 | 4.9 | 35DB480840394F828CD3F5497F9BD5E2 |  | R22 | Non-TXV |  | 6.494% | 0.93506 | 12.48% | [5 empty] | Non-TXV | 6.494%
Oroville | CA | 95966-8201 |  | 2013-10-22 | 2013-10-22 13:02 | 2013-10-22 13:30 | TRANE - YCC048F1M0BH | 100 | 9.3 | Yes | Yes | 21.1 | 21.9 | -0.8 | 205DD6A36E274CFBB14F58980ED5D4F2 |  | R22 | Non-TXV |  | 9.3% | 0.907 | 17.87% | [5 empty] | Non-TXV | 9.3%
Magalia | CA | 95954-9716 |  | 2013-10-08 | 2013-10-08 10:05 | 2013-10-08 10:26 | RHEEM - RRGG-05N37JKR | 77 | 6.8 | Yes | Yes | 25.5 | 22 | 3.5 | 66610F272B12469D860CBAB00D62CD9B |  | R22 | Non-TXV |  | 8.831% | 0.91169 | 16.97% | [5 empty] | Non-TXV | 8.831%
Los Banos | CA | 93635-9490 |  | 2013-10-17 | 2013-10-17 09:09 | 2013-10-17 09:11 | BRYANT - 777UNK | 80 | 3.3 | Yes | Yes | 21.1 | 19.6 | 1.6 | 198B4701083A45BEBA6769B1AF880BD6 |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Merced | CA | 95348-3129 |  | 2013-10-16 | 2013-10-16 09:02 | 2013-10-16 09:05 | GOODMAN - GSC130181AE | 89 | 6.4 | Yes | Yes | 21.4 | 17.7 | 3.7 | 4F506E8404164D0F9D2361E6759E9913 |  | R22 | Non-TXV |  | 7.191% | 0.92809 | 13.82% | [5 empty] | Non-TXV | 7.191%
Dos Palos | CA | 93620-2032 |  | 2013-10-21 | 2013-10-21 11:29 | 2013-10-21 11:30 | GOODMAN - GPG13360701AC | 112 | 4.3 | Yes | Yes | 20.8 | 20.2 | 0.6 | 4BD2D9E7C31B404F8D9B2DE4461551BD |  | R22 | Non-TXV |  | 3.839% | 0.96161 | 7.378% | [5 empty] | Non-TXV | 3.839%
Ripon | CA | 95366-9673 |  | 2013-10-09 | 2013-10-09 11:24 | 2013-10-09 11:55 | DAY & NIGHT - CBD | 68 | 5.6 | Yes | Yes | 22.9 | 20.4 | 2.5 | C38B439C41674B3F994CBB233F85074E |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Stockton | CA | 95204-3901 |  | 2013-10-04 | 2013-10-04 16:20 | 2013-10-04 17:01 | RHEEM - RRKA-A036JK06X | 62 | 7.7 | Yes | Yes | 23.8 | 18.6 | 5.2 | 867467A2C40A4D629DA85585A21ED875 |  | R22 | Non-TXV |  | 12.42% | 0.87581 | 23.87% | [5 empty] | Non-TXV | 12.42%
Stockton | CA | 95206-4731 |  | 2013-10-18 | 2013-10-18 14:14 | 2013-10-18 14:32 | RHEEM - RAKS042JAS | 80 | 6.4 | Yes | Yes | 20.9 | 20.2 | 0.8 | 2D913B4660B048BD9B42B59871D46F18 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Oroville | CA | 95966-3606 |  | 2013-10-07 | 2013-10-07 13:54 | 2013-10-07 14:46 | PAYNE - PA13NR036-H | 83 | 3.2 | Yes | Yes | 25.4 | 19.9 | 5.5 | A43F48E8A20049E7A3BBFAF379604996 |  | R22 | TXV |  | 3.855% | 0.96145 | 7.409% | [5 empty] | TXV | 3.855%
Rocklin | CA | 95677-2542 |  | 2013-10-08 | 2013-10-08 17:46 | 2013-10-08 18:31 | PAYNE - 567C018R | 37 | 23.1 | Yes | Yes | 23.5 | 20.1 | 3.4 | D6DD74C5F7114B8BA544C9B023D9E4BE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 62.43% | 0.37568 | 120% | [5 empty] | Non-TXV | 62.43%
Stockton | CA | 95204-1341 |  | 2013-10-07 | 2013-10-07 11:08 | 2013-10-07 11:08 | MAYTAG - UNK | 80 | 0 | Yes | Yes | 20.5 | 18.2 | 2.3 | 020F8245268B40DA97B638C43B8CCEFF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3034 |  | 2013-10-08 | 2013-10-08 12:12 | 2013-10-08 12:12 | GOODMAN - GSC130241DA | 83 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 39D405E2694D4881A9F705A92B561342 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3419 |  | 2013-10-21 | 2013-10-21 16:05 | 2013-10-21 16:22 | PAYNE - PY1PNB030060AAA | 55 | 3.9 | Yes | Yes | 24 | 22.1 | 1.9 | 631495F51BED4986A626BA3C0A79A3D4 |  | R22 | TXV |  | 7.091% | 0.92909 | 13.63% | [5 empty] | TXV | 7.091%
Merced | CA | 95340-3187 |  | 2013-10-23 | 2013-10-23 14:26 | 2013-10-23 14:47 | YORK - UNKUNK | 70 | 2.1 | Yes | Yes | 21 | 17.7 | 3.3 | 1AE13E15DAAA4103AE6BDB5063BEF636 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95204-3742 |  | 2013-10-04 | 2013-10-04 15:44 | 2013-10-04 16:01 | BRYANT - 563CNO36-D | 102 | 5.9 | Yes | Yes | 18.9 | 19.8 | -0.9 | 2BF5DAD656C3463C9840532C8DD59D45 |  | R22 | TXV |  | 5.784% | 0.94216 | 11.12% | [5 empty] | TXV | 5.784%
Merced | CA | 95348-2712 |  | 2013-10-16 | 2013-10-16 11:32 | 2013-10-16 11:33 | GE - BTB818A100A | 36 | 11.6 | Yes | Yes | 20.8 | 19.9 | 0.9 | AB7FA44509974895945CB78C932B6616 |  | R22 | Non-TXV |  | 32.22% | 0.67778 | 61.92% | [5 empty] | Non-TXV | 32.22%
Stockton | CA | 95205-7027 |  | 2013-10-18 | 2013-10-18 13:50 | 2013-10-18 13:50 | BRYANT - 582ANW24060NAAD | 53 | 0 | Yes | Yes | 21.4 | 19.2 | 2.2 | CBE0199AC20F4474A47B920AE9423BB1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-1504 |  | 2013-10-08 | 2013-10-08 11:01 | 2013-10-08 11:01 | AMERICAN STANDARD - 2A7B3030A1000AA | 88 | 0 | Yes | Yes | 23.5 | 20.9 | 2.6 | 66E1AC1607D24D5BB844C282E759E0BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-1504 |  | 2013-10-08 | 2013-10-08 11:04 | 2013-10-08 11:04 | AMERICAN STANDARD - 2A7B3060A1000AA | 139 | 0 | Yes | Yes | 26.7 | 20.9 | 5.8 | A14F0857CA5841B1B409396D42E4AA06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-6990 |  | 2013-10-11 | 2013-10-11 13:29 | 2013-10-11 14:18 | CARRIER - 24ABA324A310 | 65 | 7.6 | Yes | Yes | 23.3 | 21.9 | 1.4 | 8C1313EAD33C4F2393DDFFBB49B360AF |  | R410A | TXV |  | 11.69% | 0.88308 | 22.47% | [5 empty] | TXV | 11.69%
Shingle Springs | CA | 95682-9349 |  | 2013-11-02 | 2013-11-02 14:55 | 2013-11-02 15:12 | COLEMAN - BRCQ0361BD | 52 | 2.7 | Yes | Yes | 27 | 22.9 | 4.1 | 39ABCDDCEA204C2E879E6FF56AADB040 |  | R22 | Non-TXV |  | 5.192% | 0.94808 | 9.978% | [5 empty] | Non-TXV | 5.192%
Stockton | CA | 95210-4454 |  | 2013-10-23 | 2013-10-23 13:37 | 2013-10-23 14:03 | RHEEM - RAPM-036JAZ | 146 | 14.9 | Yes | Yes | 25.2 | 20.2 | 5 | EC9A1257C4234186BA7F7C39E55301AB |  | R410A | TXV |  | 10.21% | 0.89795 | 19.61% | [5 empty] | TXV | 10.21%
Stockton | CA | 95203-1246 |  | 2013-10-18 | 2013-10-18 15:29 | 2013-10-18 15:56 | YORK - D2NP036N05606A | 108 | 12.9 | Yes | Yes | 19.7 | 20.6 | -0.9 | C18BDDD98A774DCCA8F02E53F089C570 |  | R22 | Non-TXV |  | 11.94% | 0.88056 | 22.95% | [5 empty] | Non-TXV | 11.94%
Corning | CA | 96021-9776 |  | 2013-10-10 | 2013-10-10 14:57 | 2013-10-10 15:13 | PAYNE - PY1PNB036060AAAA | 56 | 4.5 | Yes | Yes | 23.8 | 20.9 | 2.9 | 5D55AFF51C674ACCAB97578222ECFEAF |  | R22 | Non-TXV |  | 8.036% | 0.91964 | 15.44% | [5 empty] | Non-TXV | 8.036%
Chico | CA | 95973-0881 |  | 2013-10-16 | 2013-10-16 14:44 | 2013-10-16 15:19 | BRYANT - 588ANW030060ABAD | 52 | 7.5 | Yes | Yes | 19.4 | 20.8 | -1.4 | 002653F2B4E7436B8ED8AFCC2ADECE91 |  | R22 | Non-TXV |  | 14.42% | 0.85577 | 27.72% | [5 empty] | Non-TXV | 14.42%
Chico | CA | 95926-3056 |  | 2013-10-17 | 2013-10-17 15:40 | 2013-10-17 16:08 | DAY & NIGHT - 591ANX030000AAAD | 76 | 3.4 | Yes | Yes | 19.5 | 19.9 | -0.4 | F02151A02F284809B302601D2E3BD130 |  | R22 | Non-TXV |  | 4.474% | 0.95526 | 8.597% | [5 empty] | Non-TXV | 4.474%
Rocklin | CA | 95677-2663 |  | 2013-10-08 | 2013-10-08 15:21 | 2013-10-08 15:21 | GOODMAN - ASX140361AD | 85 | 0 | Yes | Yes | 24 | 20.4 | 3.6 | 71189F85621140A0A04645ED92116475 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-6064 |  | 2013-10-11 | 2013-10-11 12:32 | 2013-10-11 12:50 | YORK - D1NA036N05606C | 67 | 4.2 | Yes | Yes | 21.9 | 21.8 | 0.1 | E4A9A875C0484C2CA2D75A0A33DDDE3C |  | R22 | Non-TXV |  | 6.269% | 0.93731 | 12.05% | [5 empty] | Non-TXV | 6.269%
Chico | CA | 95973-7634 |  | 2013-10-21 | 2013-10-21 10:53 | 2013-10-21 11:24 | LENNOX - GCS26-060-100-2PA | 159 | 9.9 | Yes | Yes | 22.2 | 21.4 | 0.8 | 1EC92DDE0B4643928E7E4259D3FE633A |  | R22 | Non-TXV |  | 6.226% | 0.93774 | 11.97% | [5 empty] | Non-TXV | 6.226%
Chico | CA | 95926-1674 |  | 2013-10-17 | 2013-10-17 15:12 | 2013-10-17 15:38 | PAYNE - 585FW024050ABAF | 54 | 5.4 | Yes | Yes | 19.3 | 20.3 | -1 | 979693B833FA42A889EBE39EACD5C8E4 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Placerville | CA | 95667-4739 |  | 2013-10-18 | 2013-10-18 11:43 | 2013-10-18 12:24 | DAY & NIGHT - UNK | 90 | 2.7 | Yes | Yes | 22 | 20.9 | 1.1 | 57F0A59792A74A678992DA0EA5195658 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Oakdale | CA | 95361-9410 |  | 2013-10-21 | 2013-10-21 15:05 | 2013-10-21 15:39 | OTHER - TZAA-348-2A757 | 85 | 11.2 | Yes | Yes | 22.9 | 20.4 | 2.5 | 099CCF587C16437BBF7A433A6DEB1323 |  | R22 | Non-TXV |  | 13.18% | 0.86824 | 25.32% | [5 empty] | Non-TXV | 13.18%
Chico | CA | 95926-4814 |  | 2013-10-21 | 2013-10-21 15:34 | 2013-10-21 15:23 | PAYNE - 561AJ024B | 56 | 5.5 | Yes | Yes | 17.6 | 20.6 | -3 | 87996032817A4813AD79934B1ADA0E7C |  | R22 | Non-TXV |  | 9.821% | 0.90179 | 18.87% | [5 empty] | Non-TXV | 9.821%
Rocklin | CA | 95765-4982 |  | 2013-10-07 | 2013-10-07 10:28 | 2013-10-07 10:28 | GOODMAN - CKJ48-1B | 110 | 0 | Yes | Yes | 25.8 | 20.6 | 5.2 | 1D245162064C418EB7DA5C0971B529DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4951 |  | 2013-10-04 | 2013-10-04 10:27 | 2013-10-04 10:27 | CARRIER - 48GP-02404031 | 80 | 0 | Yes | Yes | 17.8 | 18 | -0.2 | 2682EBEAEF8E48E69F9C10A65DCE2815 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-5129 |  | 2013-10-09 | 2013-10-09 14:13 | 2013-10-09 14:13 | BRYANT - 563CN036-E | 104 | 0 | Yes | Yes | 25.4 | 20.4 | 5 | B42FD5CC0C0E4CAB9C09ACC8B60940B2 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2886 |  | 2013-10-16 | 2013-10-16 14:40 | 2013-10-17 09:25 | RHEEM - 13AJA36A01757 | 95 | 3.4 | Yes | Yes | 17.5 | 17.7 | -0.2 | 49E0D3C1C51A4A74B979A23471D3133C |  | R22 | Non-TXV |  | 3.579% | 0.96421 | 6.878% | [5 empty] | Non-TXV | 3.579%
Stockton | CA | 95204-4950 |  | 2013-10-10 | 2013-10-10 15:19 | 2013-10-10 15:46 | PAYNE - PY3PNA036060NA | 167 | 6.4 | Yes | Yes | 19.2 | 16.7 | 2.5 | 4E3D3F1812574816AB665EE719B577E5 |  | R22 | Non-TXV |  | 3.832% | 0.96168 | 7.365% | [5 empty] | Non-TXV | 3.832%
Stockton | CA | 95206-4698 |  | 2013-10-18 | 2013-10-18 12:10 | 2013-10-18 12:49 | GOODMAN - CLK30-1D | 75 | 3.6 | Yes | Yes | 20 | 18.8 | 1.2 | 078AF5CE0D8648518BC718397F5633D2 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Manteca | CA | 95337-4268 |  | 2013-10-25 | 2013-10-25 12:00 | 2013-10-25 12:22 | RUUD - UAKA-024JAS | 51 | 3 | Yes | Yes | 24.9 | 19.9 | 5 | 4471E3F670AE4A98A15A496DA865349A |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Placerville | CA | 95667-7924 |  | 2013-11-02 | 2013-11-02 12:20 | 2013-11-02 12:43 | RUUD - UAHE-042JAS | 101 | 3 | Yes | Yes | 23 | 20.9 | 2.1 | 59E24C2063A0404D955E878D8B0E89E6 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Parlier | CA | 93648-2850 |  | 2013-10-22 | 2013-10-22 15:33 | 2013-10-22 16:52 | LENNOX - 10GCS03036X-75-5PB | 58 | 3.6 | Yes | Yes | 26.9 | 21.2 | 5.7 | CF6550A82CAB4E70884564AE9AD62C53 |  | R22 | Non-TXV |  | 6.207% | 0.93793 | 11.93% | [5 empty] | Non-TXV | 6.207%
Kerman | CA | 93630-1314 |  | 2013-10-18 | 2013-10-18 10:53 | 2013-10-18 12:31 | DAY & NIGHT - N/A | 120 | 11.4 | Yes | Yes | 20.8 | 20.6 | 0.2 | D78E0E66FAD34C818ED969FBEA132FBA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.5% | 0.905 | 18.26% | [5 empty] | Non-TXV | 9.5%
Stockton | CA | 95205-3845 |  | 2013-10-17 | 2013-10-17 12:43 | 2013-10-17 12:59 | GE - BGTA730B1A01 | 53 | 8 | Yes | Yes | 22.8 | 17.9 | 4.9 | 7152260B43C84CD1BB049E5D0B995717 |  | R22 | Non-TXV |  | 15.09% | 0.84906 | 29.01% | [5 empty] | Non-TXV | 15.09%
El Dorado Hills | CA | 95762-7561 |  | 2013-10-10 | 2013-10-10 14:16 | 2013-10-10 14:16 | GOODMAN - VSC130601AA | 169 | 0 | Yes | Yes | 26.1 | 20.4 | 5.7 | B56129F68C374700B688288989518523 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
El Dorado Hills | CA | 95762-7561 |  | 2013-10-10 | 2013-10-10 14:45 | 2013-10-10 14:45 | LENNOX - 13ACC-048-230-02 | 158 | 0 | Yes | Yes | 24.5 | 20.5 | 4 | 2E1951A65402495F95717CF763F3EB7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93636-8529 |  | 2013-10-07 | 2013-10-07 12:33 | 2013-10-07 12:35 | YORK - B3HP048A06A | 192 | 18.1 | Yes | Yes | 22.8 | 19.4 | 3.4 | 16109569EBC240DE9B2A7C1FD6CAC49F |  | R22 | Non-TXV |  | 9.427% | 0.90573 | 18.12% | [5 empty] | Non-TXV | 9.427%
Rocklin | CA | 95765-4775 |  | 2013-10-09 | 2013-10-09 16:35 | 2013-10-09 16:54 | YORK - H1RA048S06D | 117 | 21 | Yes | Yes | 19.9 | 21.8 | -1.9 | 7705F321C7FE432F84A2CB137531F59A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 17.95% | 0.82051 | 34.49% | [5 empty] | Non-TXV | 17.95%
Stockton | CA | 95210-2004 |  | 2013-10-16 | 2013-10-16 10:04 | 2013-10-16 10:24 | DAY & NIGHT - 585HJ030040 | 68 | -4 | Yes | Yes | 25.1 | 19.1 | 6 | D4F41D7DB5B2462A90A0483FE328653A |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Rocklin | CA | 95765-4267 |  | 2013-10-07 | 2013-10-07 12:13 | 2013-10-07 12:35 | UNITARY PRODUCTS GROUP - AC024M1021A | 52 | 7.5 | Yes | Yes | 23.8 | 21.8 | 2 | 8E30515E022E484AA710F798AA8CE0CB |  | R22 | Non-TXV |  | 14.42% | 0.85577 | 27.72% | [5 empty] | Non-TXV | 14.42%
Tracy | CA | 95376-7910 |  | 2013-10-17 | 2013-10-17 10:03 | 2013-10-17 10:21 | BRYANT - 561CJ042-B | 81 | 6.2 | Yes | Yes | 26 | 20.3 | 5.8 | 16941A01855C463A80CB36E18F9CC938 |  | R22 | Non-TXV |  | 7.654% | 0.92346 | 14.71% | [5 empty] | Non-TXV | 7.654%
Rocklin | CA | 95677-2628 |  | 2013-10-08 | 2013-10-08 13:51 | 2013-10-08 13:51 | AMERICAN STANDARD - YCY048F1H0AA | 178 | 0 | Yes | Yes | 25.3 | 20.4 | 4.9 | 453961C7564F46A59AF8D779FEC4AA89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-3903 |  | 2013-10-17 | 2013-10-17 10:41 | 2013-10-17 11:00 | TRANE - 4WCY4048A1000AA | 129 | 7.9 | Yes | Yes | 21 | 20.4 | 0.6 | 6F779A0DF0224E65BBED987F66B77F34 |  | R410A | Non-TXV |  | 6.124% | 0.93876 | 11.77% | [5 empty] | Non-TXV | 6.124%
Rocklin | CA | 95677-3353 |  | 2013-10-24 | 2013-10-24 12:43 | 2013-10-24 13:00 | CARRIER - 380N036300 | 135 | 4 | Yes | Yes | 26 | 20.6 | 5.4 | 29F94951C2FC4257A293193FE0065EB4 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Madera | CA | 93637-5947 |  | 2013-10-08 | 2013-10-08 11:45 | 2013-10-08 11:47 | CARRIER - 48SS048080311 | 101 | 9.3 | Yes | Yes | 24.7 | 19.5 | 5.2 | 9474FB085B394BDB85F4A32F1BA09563 |  | R22 | Non-TXV |  | 9.208% | 0.90792 | 17.7% | [5 empty] | Non-TXV | 9.208%
Merced | CA | 95348-2168 |  | 2013-11-07 | 2013-11-07 16:53 | 2013-11-07 16:55 | DAY & NIGHT - 777UNK | 64 | 3.7 | Yes | Yes | 21.3 | 20.4 | 0.9 | 738F741FF78B457EA051968DCEAD88AF |  | R22 | Non-TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | Non-TXV | 5.781%
Rocklin | CA | 95765-4260 |  | 2013-10-07 | 2013-10-07 11:21 | 2013-10-07 11:43 | UNITARY PRODUCTS GROUP - AC024M1021A | 52 | 9.4 | Yes | Yes | 17 | 19.5 | -2.5 | E6D35EEF3F894764B54F81545E617E12 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.08% | 0.81923 | 34.74% | [5 empty] | Non-TXV | 18.08%
Chowchilla | CA | 93610-3316 |  | 2013-10-11 | 2013-10-11 13:27 | 2013-10-11 13:29 | ICP - GPCM036K060D | 68 | 6.7 | Yes | Yes | 30.6 | 24.7 | 5.9 | 41D44C2E004F404BAD29846F93827089 |  | R22 | Non-TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | Non-TXV | 9.853%
Rocklin | CA | 95677-3527 |  | 2013-10-09 | 2013-10-09 12:27 | 2013-10-09 12:51 | OTHER - AA1AJ018-B | 53 | 2.9 | Yes | Yes | 21.3 | 20.1 | 1.2 | 21C545484B2E4431B2E54DDEB295AD30 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.472% | 0.94528 | 10.52% | [5 empty] | Non-TXV | 5.472%
Red Bluff | CA | 96080-2451 |  | 2013-10-11 | 2013-10-11 16:17 | 2013-10-11 16:39 | RUUD - NA | 70 | 7.3 | Yes | Yes | 21 | 20.7 | 0.3 | 222BDBBC6EF3404FB469333E60792FD8 |  | R22 | Non-TXV |  | 10.43% | 0.89571 | 20.04% | [5 empty] | Non-TXV | 10.43%
Auburn | CA | 95603-2963 |  | 2013-10-07 | 2013-10-07 13:24 | 2013-10-07 13:43 | ALLEGIANCE - 7A0036A100AZ | 88 | 2.6 | Yes | Yes | 20 | 22.2 | -2.2 | 7E682320C5F544AD964D84B759407F88 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Rocklin | CA | 95765-4136 |  | 2013-10-07 | 2013-10-07 15:27 | 2013-10-07 15:54 | CARRIER - 38EN036300 | 118 | 14.9 | Yes | Yes | 27.3 | 24.2 | 3.1 | B4DEC83542464EB58F7F074F02080A29 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.63% | 0.87373 | 24.27% | [5 empty] | Non-TXV | 12.63%
Stockton | CA | 95210-4172 |  | 2013-10-16 | 2013-10-16 10:42 | 2013-10-16 11:00 | GOODMAN - CKL42-1A | 95 | -5.6 | Yes | Yes | 26.1 | 20.1 | 6 | 73E3818EBA064F44A5C618DA4C361302 |  | R22 | Non-TXV |  | -5.895% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Merced | CA | 95340-4223 |  | 2013-10-17 | 2013-10-17 11:53 | 2013-10-17 11:54 | GOODMAN - GPG1336070M41BA | 70 | 2.8 | Yes | Yes | 24.5 | 18.7 | 5.8 | B454829A2E4A46B0B7EF2F8BC71F0DE9 |  | R410A | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Merced | CA | 95340-4223 |  | 2013-10-17 | 2013-10-17 12:12 | 2013-10-17 12:14 | GOODMAN - GPH1324M41AC | 54 | 2.5 | Yes | Yes | 24.2 | 19.5 | 4.7 | 8055D02FFDF74BE4920D70FD230855F9 |  | R410A | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Stockton | CA | 95209-4297 |  | 2013-10-23 | 2013-10-23 09:49 | 2013-10-23 10:16 | CARRIER - 24ABA348A300 | 121 | -6 | Yes | Yes | 26.1 | 20.1 | 6 | 262DD7212A154AD9812E9AEDDC9B83FF |  | R410A | TXV |  | -4.959% | 1.0496 | 1.389% |  |  |  |  | TXV |  |  | -4.959%
Lincoln | CA | 95648-0000 |  | 2013-10-09 | 2013-10-09 13:17 | 2013-10-09 13:36 | CARRIER - 38CKC060370 | 131 | 5.9 | Yes | Yes | 20 | 20.1 | -0.1 | CB1341CAF1F844E2B86383AB8142D661 |  | R22 | Non-TXV |  | 4.504% | 0.95496 | 8.655% | [5 empty] | Non-TXV | 4.504%
Stockton | CA | 95206-5244 |  | 2013-10-21 | 2013-10-21 10:44 | 2013-10-21 11:15 | PAYNE - 563CN042-A | 135 | 10.6 | Yes | Yes | 19.2 | 19.8 | -0.6 | FBB78469B3FB4E06878C286EF3DFD0CF |  | R22 | Non-TXV |  | 7.852% | 0.92148 | 15.09% | [5 empty] | Non-TXV | 7.852%
Sanger | CA | 93657-8761 |  | 2013-10-22 | 2013-10-22 11:34 | 2013-10-22 11:51 | LENNOX - 10ACC-048-230-04 | 96 | 7.7 | Yes | Yes | 21 | 19.8 | 1.3 | 26477AECC82B4E7EAAA106AE11642274 |  | R22 | Non-TXV |  | 8.021% | 0.91979 | 15.41% | [5 empty] | Non-TXV | 8.021%
Stockton | CA | 95210-5232 |  | 2013-10-23 | 2013-10-23 15:55 | 2013-10-23 16:16 | RUUD - UNK | 85 | 24.1 | Yes | Yes | 25.3 | 20.4 | 4.9 | 099D772E04F743A58C65E072DDC2A83C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 28.35% | 0.71647 | 54.49% | [5 empty] | Non-TXV | 28.35%
Merced | CA | 95341-6410 |  | 2013-11-01 | 2013-11-01 16:51 | 2013-11-01 16:52 | RUUD - 777UNK | 80 | 3 | Yes | Yes | 21.9 | 20.4 | 1.5 | 9B875A5A64BB4153BEB8BBA80B2FB228 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95203-3263 |  | 2013-10-25 | 2013-10-25 13:23 | 2013-10-25 13:46 | RHEEM - UNK | 85 | 8.6 | Yes | Yes | 26.3 | 20.8 | 5.5 | 996AAFF099EC4379AB92EA401266EAE2 |  | R22 | Non-TXV |  | 10.12% | 0.89882 | 19.44% | [5 empty] | Non-TXV | 10.12%
Stockton | CA | 95210-4177 |  | 2013-10-16 | 2013-10-16 13:19 | 2013-10-16 13:45 | PAYNE - 593ANX048000AAAA | 172 | 7.1 | Yes | Yes | 26.7 | 20.8 | 6 | 86C0D8013AFB4306B60356B9DD011929 |  | R22 | Non-TXV |  | 4.128% | 0.95872 | 7.933% | [5 empty] | Non-TXV | 4.128%
Manteca | CA | 95336-3511 |  | 2013-10-17 | 2013-10-17 15:16 | 2013-10-17 15:45 | OTHER - | 64 | 1.9 | Yes | Yes | 18.7 | 19.3 | -0.6 | 8ED8C32604A342DCABE0114D94EF164B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Colfax | CA | 95713-0000 |  | 2013-10-24 | 2013-10-24 10:30 | 2013-10-24 10:49 | TRANE - TTR030C100A2 | 74 | 2.7 | Yes | Yes | 25.5 | 22.5 | 3 | 71979240547B4A5CAAB6D94B065F97DB |  | R22 | TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | TXV | 3.649%
Stockton | CA | 95206-1857 |  | 2013-10-16 | 2013-10-16 14:17 | 2013-10-16 14:37 | BDP - 585HJW030040ABAF | 75 | 6.2 | Yes | Yes | 19.2 | 20.4 | -1.2 | 2AA5B36EB8D54993A9FEABE4E4E3FD11 |  | R22 | Non-TXV |  | 8.267% | 0.91733 | 15.89% | [5 empty] | Non-TXV | 8.267%
Sanger | CA | 93657-8750 |  | 2013-10-22 | 2013-10-22 10:44 | 2013-10-22 11:31 | LENNOX - 10ACC-048-230-04 | 96 | 9 | Yes | Yes | 27.4 | 21.7 | 5.7 | A4B6EF41D3434D62A4EC38ED89D82E9C |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Chico | CA | 95926-3855 |  | 2013-10-17 | 2013-10-17 16:43 | 2013-10-17 17:06 | LENNOX - 10GC5030-75-6PA | 53 | 8.8 | Yes | Yes | 18.5 | 21.5 | -3 | FF742AB0C66A4E68BABA9F2FE505235D |  | R22 | Non-TXV |  | 16.6% | 0.83396 | 31.91% | [5 empty] | Non-TXV | 16.6%
Atwater | CA | 95301-3242 |  | 2013-10-21 | 2013-10-21 13:03 | 2013-10-21 13:04 | LENNOX - HS84119FFA | 82 | 11.3 | Yes | Yes | 20.2 | 19.3 | 0.9 | 0EEA519DF1994571803FD2E2DFED49E0 |  | R22 | Non-TXV |  | 13.78% | 0.8622 | 26.48% | [5 empty] | Non-TXV | 13.78%
Granite Bay | CA | 95746-5860 |  | 2013-10-21 | 2013-10-21 09:42 | 2013-10-21 10:03 | BDP - 588ANW048100AEAG | 101 | 8.5 | Yes | Yes | 22.7 | 20.7 | 2 | 8696AF073C994B7394F610551CB2A1A9 |  | R22 | Non-TXV |  | 8.416% | 0.91584 | 16.17% | [5 empty] | Non-TXV | 8.416%
Oroville | CA | 95966-6341 |  | 2013-10-22 | 2013-10-22 12:04 | 2013-10-22 12:25 | RHEEM - RHKA-042JAZ | 79 | 11.2 | Yes | Yes | 18.9 | 21.9 | -3 | 1D17174BC45646FBB5DF97680A977B09 |  | R22 | Non-TXV |  | 14.18% | 0.85823 | 27.25% | [5 empty] | Non-TXV | 14.18%
Los Banos | CA | 93635-9488 |  | 2013-10-21 | 2013-10-21 13:03 | 2013-10-21 13:04 | BRYANT - 561CJ048-G | 100 | 3.3 | Yes | Yes | 24 | 21 | 3 | 0A45E500C805468DBF028C64492246BD |  | R22 | Non-TXV |  | 3.3% | 0.967 | 6.342% | [5 empty] | Non-TXV | 3.3%
Lathrop | CA | 95330-8850 |  | 2013-10-16 | 2013-10-16 12:16 | 2013-10-16 12:45 | CARRIER - 336A003100 | 90 | -8.5 | Yes | Yes | 19.3 | 15.9 | 3.4 | BC621E14A163449282737BCEAAC00975 |  | R410A | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Chico | CA | 95928-6898 |  | 2013-10-23 | 2013-10-23 15:27 | 2013-10-23 15:44 | CARRIER - 24AB324A310 | 74 | 3 | Yes | Yes | 15.8 | 18.8 | -3 | 8A00804320E94CF9BF5134E5B49345C5 |  | R410A | TXV |  | 4.054% | 0.95946 | 7.791% | [5 empty] | TXV | 4.054%
Tracy | CA | 95376-2237 |  | 2013-10-16 | 2013-10-16 11:19 | 2013-10-16 11:43 | PAYNE - 563CN036-A | 113 | 6.6 | Yes | Yes | 26.4 | 20.4 | 6 | EF6666A05704441F9BE1543C38E2D664 |  | R22 | TXV |  | 5.841% | 0.94159 | 11.22% | [5 empty] | TXV | 5.841%
Stockton | CA | 95215-5209 |  | 2013-10-31 | 2013-10-31 11:21 | 2013-10-31 11:38 | PAYNE - PA13NR024-J | 67 | 8.1 | Yes | Yes | 20.6 | 19.9 | 0.7 | B176C8B79FA64BDD98D840562E41AE06 |  | R22 | Non-TXV |  | 12.09% | 0.8791 | 23.23% | [5 empty] | Non-TXV | 12.09%
Granite Bay | CA | 95746-8141 |  | 2013-10-24 | 2013-10-24 11:39 | 2013-10-24 12:46 | TRANE - 2TTB0048A1000AA | 109 | 4 | Yes | Yes | 26.4 | 20.4 | 6 | FD64F21393E24C91B1845997372CD5D5 |  | R22 | TXV |  | 3.67% | 0.9633 | 7.052% | [5 empty] | TXV | 3.67%
Chico | CA | 95926-3065 |  | 2013-10-22 | 2013-10-22 16:15 | 2013-10-22 16:30 | DAY & NIGHT - 591ANX03000AAAA | 76 | 5 | Yes | Yes | 26.5 | 20.7 | 5.9 | 5AB7C74F8C714043ADFB78730838C7A5 |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Grass Valley | CA | 95945-5053 |  | 2013-10-21 | 2013-10-21 13:21 | 2013-10-21 13:41 | RHEEM - RRKA-A036JK08E | 62 | 11.6 | Yes | Yes | 24.7 | 20.9 | 3.8 | BAE6973F8DFA492B8191CD985A30A949 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.71% | 0.8129 | 35.96% | [5 empty] | Non-TXV | 18.71%
Chico | CA | 95973-0318 |  | 2013-10-18 | 2013-10-18 16:02 | 2013-10-18 16:31 | LENNOX - GCS20R-411-75-2P | 70 | 6.4 | Yes | Yes | 18.5 | 21.2 | -2.7 | 3902F8476A894F318BB135562501C980 |  | R22 | Non-TXV |  | 9.143% | 0.90857 | 17.57% | [5 empty] | Non-TXV | 9.143%
Auburn | CA | 95603-9370 |  | 2013-10-16 | 2013-10-16 12:58 | 2013-10-16 12:58 | GOODMAN - ASX140601AD | 274 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | 577B74BEDA75452F866D4805C93796B0 |  | R410A | TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-9370 |  | 2013-10-16 | 2013-10-16 13:28 | 2013-10-16 13:28 | GOODMAN - ASX140421AA | 180 | 0 | Yes | Yes | 22.2 | 20.9 | 1.3 | 0767F42306FB44C8898118778947DBCE |  | R410A | TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9059 |  | 2013-10-18 | 2013-10-18 10:37 | 2013-10-18 10:49 | RHEEM - RAFD-025-JAG | 51 | 6.5 | Yes | Yes | 18.2 | 20.8 | -2.6 | 45D3ABC95A4648B79ABF850025C78858 |  | R22 | Non-TXV |  | 12.75% | 0.87255 | 24.49% | [5 empty] | Non-TXV | 12.75%
Foresthill | CA | 95631-9251 |  | 2013-10-17 | 2013-10-17 10:54 | 2013-10-17 11:30 | RHEEM - RAFD-036JAS | 80 | 2.4 | Yes | Yes | 22 | 22.5 | -0.5 | 569D742111CE4A7596FABA72918A059C |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95210-5235 |  | 2013-10-16 | 2013-10-16 14:40 | 2013-10-16 14:57 | DAY & NIGHT - 585HJ036060 | 96 | -5.6 | Yes | Yes | 23.5 | 20.4 | 3.1 | 555A74881B5C4F3693DB0D4C07B3DF41 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95203-1748 |  | 2013-11-08 | 2013-11-08 12:56 | 2013-11-08 13:20 | RHEEM - RAKA-037JAZ | 79 | -5.6 | Yes | Yes | 18.7 | 19.1 | -0.4 | 6A2210CB424F443EB09B91804FA8B3EE |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Stockton | CA | 95206-4652 |  | 2013-10-18 | 2013-10-18 11:42 | 2013-10-18 12:01 | GUARDIAN - GCGD36S21S2B | 110 | 5.3 | Yes | Yes | 21.1 | 19.7 | 1.5 | E7AF7D95982A4B39A83FB4FAABDC2053 |  | R22 | Non-TXV |  | 4.818% | 0.95182 | 9.259% | [5 empty] | Non-TXV | 4.818%
Rocklin | CA | 95677-4435 |  | 2013-10-25 | 2013-10-25 15:33 | 2013-10-25 15:33 | GOODMAN - GSX30481AB | 166 | 0 | Yes | Yes | 21 | 19.9 | 1.1 | CBC4C0A3D539415392FB5DF027270EB6 |  | R410A | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9287 |  | 2013-10-22 | 2013-10-22 11:49 | 2013-10-22 12:05 | LENNOX - 13ACC-048-230-01 | 158 | 5.8 | Yes | Yes | 23 | 20.7 | 2.3 | E5345DC5789242D88BCF7EE4626267F3 |  | R22 | TXV |  | 3.671% | 0.96329 | 7.055% | [5 empty] | TXV | 3.671%
Stockton | CA | 95206-6230 |  | 2013-10-21 | 2013-10-21 13:17 | 2013-10-21 13:36 | BRYANT - 561CJ060-A | 154 | 7.6 | Yes | Yes | 19.3 | 18.5 | 0.8 | 5F11ADC92550446FB89348630649BBE0 |  | R22 | TXV |  | 4.935% | 0.95065 | 9.484% | [5 empty] | TXV | 4.935%
Cameron Park | CA | 95682-8138 |  | 2013-10-18 | 2013-10-18 15:45 | 2013-10-18 16:06 | TRANE - TTD742B100AD | 97 | 2.9 | Yes | Yes | 21 | 23.7 | -2.7 | 7FCADD486AF14BD082EA16FE52D6110C |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Cameron Park | CA | 95682-8138 |  | 2013-10-18 | 2013-10-18 15:53 | 2013-10-18 16:19 | TRANE - 2TTB3024A1000AA | 82 | 3.2 | Yes | Yes | 23 | 22 | 1 | 57F23D66417F45CDBB7D9999F83B932A |  | R22 | Non-TXV |  | 3.902% | 0.96098 | 7.5% | [5 empty] | Non-TXV | 3.902%
Chico | CA | 95926-4739 |  | 2013-10-23 | 2013-10-23 11:41 | 2013-10-23 12:01 | PAYNE - 585GJW024040 | 54 | 5.1 | Yes | Yes | 15.1 | 18 | -2.9 | BB5635C4CA4347979B18EDB310BA16FE |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Stockton | CA | 95205-3623 |  | 2013-10-17 | 2013-10-17 11:59 | 2013-10-17 12:15 | OTHER - SCU10G36A-1 | 80 | 20.4 | Yes | Yes | 24 | 18.8 | 5.2 | D9233CB23779424CA5C6BFEB6BDAEC06 |  | R22 | Non-TXV |  | 25.5% | 0.745 | 49.01% | [5 empty] | Non-TXV | 25.5%
Nevada City | CA | 95959-9328 |  | 2013-10-23 | 2013-10-23 12:14 | 2013-10-23 12:14 | TRANE - 2TTX4024B1000AA | 105 | 0 | Yes | Yes | 23.2 | 20.4 | 2.8 | 07CBE8FB49FF4AAC8F7B89448BAA565E |  | R22 | TXV |  | 0% | 1 | 0%
Nevada City | CA | 95959-9273 |  | 2013-10-23 | 2013-10-23 15:05 | 2013-10-23 15:05 | AMERICAN STANDARD - YCP036F1H0AB | 109 | 0 | Yes | Yes | 26.7 | 22.5 | 4.2 | 65B3EA4222804FF3959FE5E16913F0B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2123 |  | 2013-10-18 | 2013-10-18 09:51 | 2013-10-18 10:10 | DAY & NIGHT - 567C030RCU | 63 | -3.7 | Yes | Yes | 20.7 | 19.1 | 1.6 | 516FBFE810FA425CB5536C990674835F |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Chico | CA | 95926-1032 |  | 2013-10-23 | 2013-10-23 13:04 | 2013-10-23 13:55 | TEMPSTAR - TCA024AKCA | 68 | 5.2 | Yes | Yes | 15.4 | 18.3 | -2.9 | DA9571CA0B7F444DA3FCC19BAB293531 |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Rocklin | CA | 95765-1737 |  | 2013-10-17 | 2013-10-17 16:38 | 2013-10-17 16:55 | TRANE - TTZ0906B1000AA | 235 | 8.6 | Yes | Yes | 24 | 21.2 | 2.8 | BA7DA651FE8548919F6EEB824A6CFB39 |  | R22 | TXV |  | 3.66% | 0.9634 | 7.033% | [5 empty] | TXV | 3.66%
Stockton | CA | 95204-3820 |  | 2013-10-17 | 2013-10-17 13:29 | 2013-10-17 13:47 | KENMORE - UNK | 96 | -5.6 | Yes | Yes | 20 | 19.5 | 0.5 | ACA37449ADC342FDA2DCDAF20D36C7CE |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Tracy | CA | 95376-5117 |  | 2013-10-17 | 2013-10-17 14:06 | 2013-10-17 14:29 | GOODMAN - VSC130361AA | 118 | 7.1 | Yes | Yes | 24.9 | 20.9 | 4 | FE90C496BEB243539474266CB4D541A2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.017% | 0.93983 | 11.56% | [5 empty] | Non-TXV | 6.017%
Stockton | CA | 95206-5605 |  | 2013-10-22 | 2013-10-22 11:11 | 2013-10-22 11:27 | BRYANT - 561CJ048A | 110 | 4.2 | Yes | Yes | 23.7 | 20.4 | 3.3 | 0B786A0427B9442E813EAFC3A2C155E9 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Stockton | CA | 95209-3725 |  | 2013-10-18 | 2013-10-18 13:22 | 2013-10-18 13:45 | ICP - NAC048AKA5 | 108 | 3.5 | Yes | Yes | 21.5 | 19.8 | 1.7 | 10FAA4F3BC6F405388049C634777F48F |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Stockton | CA | 95206-6320 |  | 2013-10-21 | 2013-10-21 12:39 | 2013-10-21 12:56 | YORK - H1RA048S06D | 117 | 16.4 | Yes | Yes | 21.2 | 18.8 | 2.4 | 35B04B62205F4E228A0666EA1D092BDD |  | R22 | Non-TXV |  | 14.02% | 0.85983 | 26.94% | [5 empty] | Non-TXV | 14.02%
Tracy | CA | 95376-8932 |  | 2013-10-25 | 2013-10-25 10:01 | 2013-10-25 10:23 | UNK - UNK | 85 | -6 | Yes | Yes | 21.8 | 18.7 | 3.1 | 10771DA72D464AB997FE44CC189905CE |  |  |  |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | 0 |  |  | -7.059%
Fresno | CA | 93722-3271 |  | 2013-10-18 | 2013-10-18 14:06 | 2013-10-18 14:28 | RHEEM - EADB-037JAS | 85 | 3.1 | Yes | Yes | 18.3 | 21.3 | -3 | B15A0694B2C8427E969B9BF2C698A7C9 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Tracy | CA | 95376-0712 |  | 2013-10-23 | 2013-10-23 13:34 | 2013-10-23 13:54 | RUUD - UAND-036JAZ | 116 | 15.6 | Yes | Yes | 22.9 | 18.5 | 4.4 | 4869A4DD7BF04559A1F95B028CCCA355 |  | R22 | Non-TXV |  | 13.45% | 0.86552 | 25.84% | [5 empty] | Non-TXV | 13.45%
Placerville | CA | 95667-4720 |  | 2013-10-18 | 2013-10-18 11:05 | 2013-10-18 11:27 | TRANE - WCH036C100BA | 112 | 4.1 | Yes | Yes | 24 | 20.9 | 3.1 | 339924F6FD9549F0AD74CE9233106D67 |  | R22 | TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | TXV | 3.661%
Stockton | CA | 95206-5120 |  | 2013-10-18 | 2013-10-18 12:54 | 2013-10-18 13:12 | RUUD - UAFD036JAS | 80 | 4.9 | Yes | Yes | 20.1 | 19.4 | 0.7 | 358939BBBDBD4342A33FB137BC064C13 |  | R22 | Non-TXV |  | 6.125% | 0.93875 | 11.77% | [5 empty] | Non-TXV | 6.125%
Stockton | CA | 95206-5120 |  | 2013-10-18 | 2013-10-18 13:14 | 2013-10-18 13:43 | RUUD - UAFD036JAS | 80 | 3.6 | Yes | Yes | 21.6 | 20.4 | 1.2 | FDDAA73F971A4A3B81B5CE33265BB652 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Stockton | CA | 95209-1799 |  | 2013-10-18 | 2013-10-18 14:04 | 2013-10-18 14:21 | YORK - HAMC-042SA | 103 | 3.2 | Yes | Yes | 21.2 | 18.7 | 2.5 | A5EA5FA32EE540D3A2D3ED17E55D6BDE |  | R22 | Non-TXV |  | 3.107% | 0.96893 | 5.971% | [5 empty] | Non-TXV | 3.107%
Stockton | CA | 95210-6618 |  | 2013-10-18 | 2013-10-18 12:35 | 2013-10-18 12:53 | YORK - D3YS024N03206B | 62 | 2.4 | Yes | Yes | 19 | 20.8 | -1.8 | CFC9B5CC2A44402799D7DFF535C9E06C |  | R22 | Non-TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | Non-TXV | 3.871%
Granite Bay | CA | 95746-9515 |  | 2013-10-24 | 2013-10-24 10:19 | 2013-10-24 10:37 | AIRE-FLO - 585JJ048125 | 118 | -8.3 | Yes | Yes | 26.7 | 20.9 | 5.8 | C1EDA2B8F00D4E648581A6328596CB10 |  | R22 | Non-TXV |  | -7.034% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.034%
Gustine | CA | 95322-1933 |  | 2013-10-21 | 2013-10-21 10:31 | 2013-10-21 10:32 | ICP - CA9042GA2 | 128 | 9.6 | Yes | Yes | 22.7 | 17.7 | 5 | ABF4B59A3AA145C4AA55B3E30715E7FE |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95210-2523 |  | 2013-10-18 | 2013-10-18 09:19 | 2013-10-18 09:36 | OTHER - UNK | 64 | -3.8 | Yes | Yes | 18 | 19.6 | -1.6 | 50D381D2A95547B6B4C0D776FD57378B |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Madera | CA | 93638-0156 |  | 2013-10-17 | 2013-10-17 11:25 | 2013-10-17 11:26 | GOODMAN - GPG13360451AC | 112 | 12.6 | Yes | Yes | 25.8 | 20.1 | 5.7 | 0B3094F0B4A743B6B2FAF497CC628225 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Wheatland | CA | 95692-9260 |  | 2013-10-25 | 2013-10-25 11:21 | 2013-10-25 11:49 | GOODMAN - CKL30-1F | 72 | 2.3 | Yes | Yes | 19 | 19.5 | -0.5 | C56A030E2E8D4DE6A7E5BBDD731888BD |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Stockton | CA | 95215-5914 |  | 2013-10-31 | 2013-10-31 12:18 | 2013-10-31 12:36 | RHEEM - RRKA-A036JK06X | 62 | 5.3 | Yes | Yes | 22.4 | 19.3 | 3.1 | EE1292993B9E4A3EBBA8BECA3992113D |  | R22 | Non-TXV |  | 8.548% | 0.91452 | 16.43% | [5 empty] | Non-TXV | 8.548%
Sanger | CA | 93657-9725 |  | 2013-10-31 | 2013-10-31 14:23 | 2013-10-31 14:26 | AMANA - PGA36B0702C | 112 | 7.3 | Yes | Yes | 21 | 20.6 | 0.4 | 121154B2BA934EBC9762CF55918E75CA |  | R22 | Non-TXV |  | 6.518% | 0.93482 | 12.53% | [5 empty] | Non-TXV | 6.518%
Sanger | CA | 93657-9725 |  | 2013-10-31 | 2013-10-31 14:59 | 2013-10-31 16:01 | GOODMAN - PGB042075-1A | 68 | 6.2 | Yes | Yes | 14.5 | 20.8 | -6.3 | 77591E23A1BF4EF2910458D6B43FA582 | Add refrigerant: 5.1 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 9.118% | 0.90882 | 17.52% | [5 empty] | Non-TXV | 9.118%
Stockton | CA | 95205-7916 |  | 2013-10-24 | 2013-10-24 10:01 | 2013-10-24 10:24 | PAYNE - PA13NR036-C | 128 | 7.2 | Yes | Yes | 17.4 | 18.5 | -1.1 | 4BB724FE087C413381A55013AA09DEC2 |  | R22 | TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | TXV | 5.625%
Merced | CA | 95348-1321 |  | 2013-10-18 | 2013-10-18 14:34 | 2013-10-18 14:35 | RUUD - UAKA030JAZ | 62 | 8.7 | Yes | Yes | 18.3 | 17 | 1.3 | 8F0DDA05B6404D05A46EFBB908D5F620 |  | R22 | Non-TXV |  | 14.03% | 0.85968 | 26.97% | [5 empty] | Non-TXV | 14.03%
Madera | CA | 93637-5403 |  | 2013-10-17 | 2013-10-17 09:48 | 2013-10-17 09:49 | AIRE-FLO - PGC036K060B | 71 | 6.5 | Yes | Yes | 22.3 | 17.2 | 5.1 | 11CDF8CBEB74424B9DAC3F24C23A4BDC |  | R22 | Non-TXV |  | 9.155% | 0.90845 | 17.59% | [5 empty] | Non-TXV | 9.155%
Stockton | CA | 95205-3819 |  | 2013-11-01 | 2013-11-01 15:16 | 2013-11-01 15:35 | TRANE - 2YCC3036A1075AA | 82 | -7.3 | Yes | Yes | 25.7 | 20.1 | 5.6 | E38C4F93836840DEA9DCD8422A93F1F7 |  | R22 | TXV |  | -8.902% | 1.089 | 2.493% |  |  |  |  | TXV |  |  | -8.902%
Tracy | CA | 95376-5336 |  | 2013-10-17 | 2013-10-17 12:38 | 2013-10-17 12:57 | CARRIER - 591ANX06000AAAA | 166 | 34.4 | Yes | Yes | 25.7 | 20.1 | 5.6 | 8D83B51D76414EB8A7977C3BE9347F43 |  | R22 | Non-TXV |  | 20.72% | 0.79277 | 39.82% | [5 empty] | Non-TXV | 20.72%
Merced | CA | 95340-3232 |  | 2013-10-16 | 2013-10-16 13:40 | 2013-10-16 13:42 | OTHER - 80RBR60 | 56 | 7 | Yes | Yes | 17.8 | 18.7 | -0.9 | 0CE0EBF08BA14F3C9C354375006039D3 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Lathrop | CA | 95330-0000 |  | 2013-10-17 | 2013-10-17 11:21 | 2013-10-17 11:37 | CARRIER - 24ABA348A310 | 127 | 4.4 | Yes | Yes | 18.6 | 16.2 | 2.4 | 7506471ABED74D7EB121E1A95BF19A71 |  | R22 | Non-TXV |  | 3.465% | 0.96535 | 6.658% | [5 empty] | Non-TXV | 3.465%
Stockton | CA | 95210-1914 |  | 2013-10-16 | 2013-10-16 12:15 | 2013-10-16 12:32 | GOODMAN - UNK | 79 | -4.6 | Yes | Yes | 23 | 19.3 | 3.7 | 08B81585A91741BEB2A0AA6ADB58CF44 |  | R22 | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Chico | CA | 95926-3062 |  | 2013-10-23 | 2013-10-23 17:00 | 2013-10-23 17:35 | DAY & NIGHT - 591ANX030000AAAA | 76 | 9 | Yes | Yes | 22.2 | 21.2 | 1 | 7F04A358DC8F4AE483131305B068137F |  | R22 | Non-TXV |  | 11.84% | 0.88158 | 22.76% | [5 empty] | Non-TXV | 11.84%
Tracy | CA | 95376-9486 |  | 2013-10-23 | 2013-10-23 12:12 | 2013-10-23 12:12 | TRANE - 2TTB0042A1000AA | 95 | 0 | Yes | Yes | 15.4 | 18.1 | -2.7 | FD18BFBB2A554C38922AE7F6B040D145 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-9360 |  | 2013-10-25 | 2013-10-25 13:26 | 2013-10-25 13:26 | GOODMAN - GSX10301DB | 76 | 0 | Yes | Yes | 25.4 | 20.9 | 4.5 | 523F2DD386324C0AACBA29254792DE2E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-5611 |  | 2013-10-18 | 2013-10-18 16:33 | 2013-10-18 16:33 | TRANE - TTP042C100A3 | 156 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | ACD85C249C344D3BA9440588F5A3B40E |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-8807 |  | 2013-10-21 | 2013-10-21 12:17 | 2013-10-21 12:18 | OTHER - 563CN048-H | 140 | 4.2 | Yes | Yes | 23.1 | 21.4 | 1.7 | EE92BBF60C174E47BC5EC5EAD54B2DE8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Colfax | CA | 95713-0000 |  | 2013-10-18 | 2013-10-18 12:35 | 2013-10-18 12:35 | TRANE - YCC030F1M0BG | 72 | 0 | Yes | Yes | 23.9 | 20.6 | 3.3 | D92ADD26A6E541798074A416B77640AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-2612 |  | 2013-10-17 | 2013-10-17 12:32 | 2013-10-17 12:50 | AMANA - PGD36C0902E | 110 | 4.1 | Yes | Yes | 23.7 | 19.1 | 4.6 | B77E6CC29F9F4C78A157FDC378B1A72D |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.163% | [5 empty] | Non-TXV | 3.727%
Stockton | CA | 95204-5219 |  | 2013-10-16 | 2013-10-16 10:05 | 2013-10-16 10:05 | RHEEM - RAKA-043JAZ | 79 | 0 | Yes | Yes | 23.4 | 18.2 | 5.2 | B3B729D253A04076A5603B92B593292D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3747 |  | 2013-10-17 | 2013-10-17 09:57 | 2013-10-17 10:15 | RHEEM - RRNA-A024JK06X | 80 | 7.2 | Yes | Yes | 22.8 | 18.8 | 4 | 4C2B744B239B46169501967C803756D6 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Fowler | CA | 93625-9690 |  | 2013-10-22 | 2013-10-22 13:15 | 2013-10-22 14:02 | LENNOX - 12ACB42-4P | 125 | 8.8 | Yes | Yes | 21.5 | 20.9 | 0.6 | 9290819A4B264830B08C66E1E6C012EC |  | R22 | Non-TXV |  | 7.04% | 0.9296 | 13.53% | [5 empty] | Non-TXV | 7.04%
Auburn | CA | 95602-8904 |  | 2013-10-16 | 2013-10-16 11:34 | 2013-10-16 11:34 | LENNOX - XC14-036-230-01 | 137 | 0 | Yes | Yes | 26.6 | 20.9 | 5.7 | 3F031409C50443F288E48FB4BC647356 |  | R410A | TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-2335 |  | 2013-10-16 | 2013-10-16 10:46 | 2013-10-16 11:03 | KENMORE - CA5036QKA1 | 93 | 7.8 | Yes | Yes | 24.5 | 20.4 | 4.1 | 1E7D18E9F3B64297835D1D0445DF5B71 |  | R22 | Non-TXV |  | 8.387% | 0.91613 | 16.12% | [5 empty] | Non-TXV | 8.387%
Granite Bay | CA | 95746-6423 |  | 2013-10-24 | 2013-10-24 09:29 | 2013-10-24 09:59 | ICP - AC1CN060-A | 200 | 12.4 | Yes | Yes | 25.3 | 20.1 | 5.2 | AC96653AFF4047128476D44E8344A002 |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Madera | CA | 93638-0846 |  | 2013-10-17 | 2013-10-17 10:13 | 2013-10-17 10:16 | AIRE-FLO - UNK | 68 | 7.9 | Yes | Yes | 23.8 | 18.8 | 5 | 41FD9DDD627D421EBEFF2B61A5696F91 |  | R22 | Non-TXV |  | 11.62% | 0.88382 | 22.33% | [5 empty] | Non-TXV | 11.62%
Oroville | CA | 95966-8216 |  | 2013-10-17 | 2013-10-17 13:34 | 2013-10-17 14:10 | DAY & NIGHT - NA | 95 | 6 | Yes | Yes | 20.2 | 22.6 | -2.4 | E43E891326444826B72B1AA85803DD02 |  | R22 | Non-TXV |  | 6.316% | 0.93684 | 12.14% | [5 empty] | Non-TXV | 6.316%
Ripon | CA | 95366-2063 |  | 2013-10-23 | 2013-10-23 14:40 | 2013-10-23 14:55 | RHEEM - RAKA-060JAZ | 112 | 3.4 | Yes | Yes | 20.2 | 19.3 | 0.9 | 0CE09705FF40415CBCD30F773605B210 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Fresno | CA | 93722-2914 |  | 2013-10-18 | 2013-10-18 15:12 | 2013-10-18 15:36 | CARRIER - N/A | 90 | 7.3 | Yes | Yes | 20.5 | 20.4 | 0.1 | 1D0642821D714FA8B902E9B56E303CB3 |  | R22 | Non-TXV |  | 8.111% | 0.91889 | 15.59% | [5 empty] | Non-TXV | 8.111%
Tracy | CA | 95376-5272 |  | 2013-10-16 | 2013-10-16 13:16 | 2013-10-16 13:35 | FRIGIDAIRE - UNK | 68 | 5 | Yes | Yes | 24.7 | 20.1 | 4.6 | 3557E89D3E5A4A8CBB3D95112A72E3E1 |  | R22 | Non-TXV |  | 7.353% | 0.92647 | 14.13% | [5 empty] | Non-TXV | 7.353%
Stockton | CA | 95210-3674 |  | 2013-10-25 | 2013-10-25 15:56 | 2013-10-25 16:13 | PAYNE - 591ANX042000ABAA | 112 | -6.6 | Yes | Yes | 18 | 18.5 | -0.5 | F1420BBDBA6C48649D266F0AA7F60FFB |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Stockton | CA | 95203-1332 |  | 2013-10-18 | 2013-10-18 15:12 | 2013-10-18 15:12 | GOODMAN - GPG133045M41BA | 85 | 0 | Yes | Yes | 25.7 | 20.2 | 5.5 | C7CF8CB5CD624ADEA931790F3C980084 |  | R410A | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-1604 |  | 2013-10-23 | 2013-10-23 13:06 | 2013-10-23 13:31 | OTHER - 563CN042-A | 130 | 3.9 | Yes | Yes | 22 | 19.1 | 2.9 | 0AB45ADA703D461789232D371EE1147E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95212-1019 |  | 2013-10-17 | 2013-10-17 09:43 | 2013-10-17 10:05 | GOODMAN - CK42-1C | 86 | 2.5 | Yes | Yes | 26.4 | 20.4 | 6 | 4553B642889B49B49E7B08CAD2B9A5D5 |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Chico | CA | 95926-1404 |  | 2013-10-21 | 2013-10-21 11:50 | 2013-10-21 12:15 | LENNOX - 563CNX036000ACAA | 101 | 5.7 | Yes | Yes | 22.1 | 22 | 0.1 | 006B384AC84C431C97E79768962F2853 |  | R22 | TXV |  | 5.644% | 0.94356 | 10.85% | [5 empty] | TXV | 5.644%
Paradise | CA | 95969-6201 |  | 2013-10-18 | 2013-10-18 13:38 | 2013-10-18 14:06 | BRYANT - 30-579A | 46 | 4.7 | Yes | Yes | 18 | 20.9 | -2.9 | E81BD9B474084CD7A284F121A0003436 |  | R22 | Non-TXV |  | 10.22% | 0.89783 | 19.64% | [5 empty] | Non-TXV | 10.22%
Merced | CA | 95341-7027 |  | 2013-10-21 | 2013-10-21 15:23 | 2013-10-21 15:24 | BRYANT - 582ANW036060NBAF | 68 | 2.9 | Yes | Yes | 24.3 | 20.9 | 3.4 | 84D22FAFE9A4418591C58A8E8F43C633 |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Chico | CA | 95973-0472 |  | 2013-10-24 | 2013-10-24 16:11 | 2013-10-24 16:29 | YORK - JSA050701003 | 54 | 4.4 | Yes | Yes | 17.5 | 20.4 | -2.9 | F6EEE803BE1A41A685CA4220DDD689FD |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Fresno | CA | 93702-2343 |  | 2013-10-23 | 2013-10-23 17:47 | 2013-10-23 18:51 | - | 85 | 5.8 | Yes | Yes | 26 | 20.2 | 5.9 | 146B85D6A14F4ACF8A64512E8F1EF449 |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Merced | CA | 95341-7015 |  | 2013-10-16 | 2013-10-16 12:14 | 2013-10-16 12:15 | BRYANT - 582ANW036060NBAF | 68 | 6.8 | Yes | Yes | 21.3 | 18.8 | 2.5 | 69829F319A3C433287A906D582C01BA4 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Rocklin | CA | 95677-2550 |  | 2013-10-17 | 2013-10-17 16:46 | 2013-10-17 16:46 | PAYNE - 567C018RCU | 37 | 0 | Yes | Yes | 26.2 | 20.4 | 5.8 | A73CADFEC7BB4584AA40DB0F70092E75 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-4604 |  | 2013-10-22 | 2013-10-22 10:48 | 2013-10-22 11:09 | BRYANT - PA10JA60-C | 120 | 7.9 | Yes | Yes | 18 | 17.7 | 0.3 | 0538809F2F10413391B1374E5F85E76C |  | R22 | Non-TXV |  | 6.583% | 0.93417 | 12.65% | [5 empty] | Non-TXV | 6.583%
Chico | CA | 95928-0000 |  | 2013-10-23 | 2013-10-23 16:00 | 2013-10-23 16:31 | CARRIER - 24AB324A310 | 74 | 7 | Yes | Yes | 19.1 | 21.5 | -2.4 | 4CD03D451611460BB865A8B2E781414A |  | R410A | TXV |  | 9.459% | 0.90541 | 18.18% | [5 empty] | TXV | 9.459%
Stockton | CA | 95205-3346 |  | 2013-10-18 | 2013-10-18 11:52 | 2013-10-18 11:52 | RHEEM - RRNA-B042JK08X | 85 | 0 | Yes | Yes | 19.3 | 19.4 | -0.1 | 5E1C6F5B2015444DB50B1F7D04515FB1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7919 |  | 2013-10-26 | 2013-10-26 17:54 | 2013-10-26 18:13 | LENNOX - 12ACB60-4P | 173 | 15.2 | Yes | Yes | 18.5 | 20.6 | -2.1 | F240F9E7A1E84B8EB7330F8933578EEC |  | R22 | Non-TXV |  | 8.786% | 0.91214 | 16.89% | [5 empty] | Non-TXV | 8.786%
Kerman | CA | 93630-9372 |  | 2013-10-31 | 2013-10-31 16:41 | 2013-10-31 16:42 | CARRIER - 38RBC060360 | 206 | 6.4 | Yes | Yes | 25.7 | 19.8 | 5.9 | 76F6F9471B514E5C858A82A3CD0FF751 |  | R22 | Non-TXV |  | 3.107% | 0.96893 | 5.971% | [5 empty] | Non-TXV | 3.107%
Madera | CA | 93638-1522 |  | 2013-10-17 | 2013-10-17 10:39 | 2013-10-17 10:40 | NORDYNE - GR6GDX30K045X | 96 | 3.6 | Yes | Yes | 23.9 | 18.7 | 5.2 | B4F0EEBE24CB401D844C84CDF92C9F11 |  | R410A | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Madera | CA | 93637-5917 |  | 2013-11-01 | 2013-11-01 14:03 | 2013-11-01 14:04 | CARRIER - 38BR042300 | 133 | 4.1 | Yes | Yes | 23 | 20.3 | 2.7 | A6A0D216E98E40F98280050125158764 |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.924% | [5 empty] | Non-TXV | 3.083%
Rocklin | CA | 95765-4772 |  | 2013-10-21 | 2013-10-21 14:26 | 2013-10-21 14:44 | OTHER - JS5BD-060K | 232 | 7 | Yes | Yes | 24 | 21 | 3 | 98F40E095D2D4676BC093EAF1B344DB4 |  | R22 | Non-TXV |  | 3.017% | 0.96983 | 5.798% | [5 empty] | Non-TXV | 3.017%
Magalia | CA | 95954-9120 |  | 2013-10-23 | 2013-10-23 10:26 | 2013-10-23 10:43 | YORK - H1RD04806G | 229 | 8.1 | Yes | Yes | 19.7 | 22.5 | -2.8 | 5B9B5577B6A245119BA0F93AC2D5791F |  | R22 | Non-TXV |  | 3.537% | 0.96463 | 6.798% | [5 empty] | Non-TXV | 3.537%
Stockton | CA | 95206-6148 |  | 2013-11-01 | 2013-11-01 14:30 | 2013-11-01 14:53 | GOODMAN - CLJ36-1A | 109 | 22 | Yes | Yes | 21.3 | 18.8 | 2.5 | 2177349A8D604C1BA296C24BEEE84898 |  | R22 | Non-TXV |  | 20.18% | 0.79817 | 38.79% | [5 empty] | Non-TXV | 20.18%
Stockton | CA | 95206-6385 |  | 2013-10-21 | 2013-10-21 12:01 | 2013-10-21 12:17 | GOODMAN - CLJ48-1 | 117 | 12.7 | Yes | Yes | 20 | 18.7 | 1.3 | 1FD27E8FAA24491FA6CF8AC40B203597 |  | R22 | TXV |  | 10.85% | 0.89145 | 20.86% | [5 empty] | TXV | 10.85%
Foresthill | CA | 95631-9741 |  | 2013-10-17 | 2013-10-17 11:53 | 2013-10-17 12:09 | YORK - H2RD030S06B | 93 | 2.8 | Yes | Yes | 24 | 20.6 | 3.4 | EBD6C92479224204A7E2338A891A4CA6 |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Fresno | CA | 93702-2838 |  | 2013-10-18 | 2013-10-18 17:35 | 2013-10-18 17:37 | BDP - 585HJ048080 | 118 | 6.2 | Yes | Yes | 26.5 | 20.7 | 5.8 | 21FE71BDBA184D4F9522FC763A52E0DF |  | R22 | Non-TXV |  | 5.254% | 0.94746 | 10.1% | [5 empty] | Non-TXV | 5.254%
Atwater | CA | 95301-4859 |  | 2013-10-21 | 2013-10-21 14:36 | 2013-10-21 14:37 | OTHER - RAC13J304S21A | 62 | 5 | Yes | Yes | 19.6 | 18.2 | 1.4 | 786CD0ABA347425A8A9B59EF394D8D17 |  | R410A | Non-TXV |  | 8.065% | 0.91935 | 15.5% | [5 empty] | Non-TXV | 8.065%
Fresno | CA | 93710-4614 |  | 2013-10-16 | 2013-10-16 15:23 | 2013-10-16 16:00 | PAYNE - N/A | 84 | 4.6 | Yes | Yes | 22.5 | 20.4 | 2.1 | 4ECAFB23D33E43B8A304F09003D0C44A |  | R22 | Non-TXV |  | 5.476% | 0.94524 | 10.52% | [5 empty] | Non-TXV | 5.476%
Chico | CA | 95926-2785 |  | 2013-10-22 | 2013-10-22 15:36 | 2013-10-22 16:00 | DAY & NIGHT - 565BJ018 | 50 | 2.9 | Yes | Yes | 17 | 18.3 | -1.3 | 9F3F769DCB1F4525861FB1F315F02833 |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Ripon | CA | 95366-9730 |  | 2013-10-23 | 2013-10-23 15:52 | 2013-10-23 16:11 | TRANE - 2TTR2048A1000AA | 120 | 7.9 | Yes | Yes | 20.6 | 19.3 | 1.3 | 3BB456FDF72C42D692CC762D356C6FED | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.583% | 0.93417 | 12.65% | [5 empty] | Non-TXV | 6.583%
Stockton | CA | 95210-1843 |  | 2013-10-22 | 2013-10-22 13:58 | 2013-10-22 14:15 | GOODMAN - GSC130421AC | 134 | 6.8 | Yes | Yes | 21.3 | 19.8 | 1.5 | FFAB99AF869E4615ADE6AAD8ABE8E50C |  | R22 | TXV |  | 5.075% | 0.94925 | 9.752% | [5 empty] | TXV | 5.075%
Auburn | CA | 95603-7923 |  | 2013-10-18 | 2013-10-18 15:42 | 2013-10-18 15:59 | RUUD - URAD-06E36JR | 83 | 6.8 | Yes | Yes | 22 | 20.7 | 1.3 | 136FB8B2188342228A9F85431981B56B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.193% | 0.91807 | 15.74% | [5 empty] | Non-TXV | 8.193%
Stockton | CA | 95204-1922 |  | 2013-10-17 | 2013-10-17 10:40 | 2013-10-17 10:40 | PAYNE - PY3GNAA3006NA | 102 | 0 | Yes | Yes | 25.2 | 19.5 | 5.7 | 8A83D7AE40B64F57BD6BA5C7FAF2252B |  | R410A | TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-2031 |  | 2013-10-25 | 2013-10-25 16:07 | 2013-10-25 16:23 | RUUD - 13JM42401 | 106 | 3.2 | Yes | Yes | 24 | 20.2 | 3.9 | 0E41BE3B4D9742538F9A01EA4B56564E |  | R410A | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Lincoln | CA | 95648-1689 |  | 2013-10-24 | 2013-10-24 10:55 | 2013-10-24 10:55 | ICP - TCA460AKA1 | 310 | 0 | Yes | Yes | 23 | 19.9 | 3.1 | E90E4FFD42084DEE81AB406A7C3F151A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1922 |  | 2013-10-17 | 2013-10-17 10:02 | 2013-10-17 10:19 | RHEEM - RRNL-B042JK08X | 112 | -7.9 | Yes | Yes | 21.5 | 19.1 | 2.4 | FE81B28AA6D8445A9E4CE349C6E016CD |  | R410A | Non-TXV |  | -7.054% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.054%
Tracy | CA | 95376-3530 |  | 2013-10-16 | 2013-10-16 12:38 | 2013-10-16 12:55 | ICP - PGC024K060A | 58 | 8 | Yes | Yes | 25.1 | 20.4 | 4.7 | 6F18834CDAF046B6A6D0593583C0FB89 |  | R22 | Non-TXV |  | 13.79% | 0.86207 | 26.51% | [5 empty] | Non-TXV | 13.79%
Sanger | CA | 93657-8779 |  | 2013-10-22 | 2013-10-22 09:53 | 2013-10-22 10:42 | UNITARY PRODUCTS GROUP - H2RD048S06B | 134 | 4.4 | Yes | Yes | 20.2 | 20.7 | -0.4 | 71D17CFC6EF847479A56CA81EFEEDDCB |  | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Oakdale | CA | 95361-3104 |  | 2013-10-21 | 2013-10-21 14:00 | 2013-10-21 14:33 | ICP - NAC042AKA1 | 105 | 15.8 | Yes | Yes | 23.1 | 20.3 | 2.8 | E03D6B60B7AB4F1D88DF589B84CCF037 |  | R22 | Non-TXV |  | 15.05% | 0.84952 | 28.92% | [5 empty] | Non-TXV | 15.05%
Manteca | CA | 95337-4254 |  | 2013-10-25 | 2013-10-25 11:33 | 2013-10-25 11:58 | RUUD - UAHE-023JAS | 64 | 6 | Yes | Yes | 26.6 | 20.6 | 6 | 8C496BDB24264BCC87712341F2A2BCD5 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Rocklin | CA | 95677-3535 |  | 2013-10-17 | 2013-10-17 18:01 | 2013-10-17 18:01 | GOODMAN - CK18-1B | 59 | 0 | Yes | Yes | 22.9 | 21.5 | 1.4 | 4DDDC5B0F1A54426A80CF99C912CDFC5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5963 |  | 2013-11-01 | 2013-11-01 13:22 | 2013-11-01 13:24 | CARRIER - 48GX-042060301 | 118 | 3.8 | Yes | Yes | 19.8 | 19.3 | 0.5 | E9563EB0B95E434E9F55897C669845A8 |  | R22 | Non-TXV |  | 3.22% | 0.9678 | 6.189% | [5 empty] | Non-TXV | 3.22%
Madera | CA | 93636-8875 |  | 2013-10-18 | 2013-10-18 11:57 | 2013-10-18 11:59 | OTHER - BBUZF036AA | 150 | 6.2 | Yes | Yes | 23.9 | 18.7 | 5.2 | AECA19804AE64ECA8A8C9AE1DAAE6B5F |  | R410A | Non-TXV |  | 4.133% | 0.95867 | 7.943% | [5 empty] | Non-TXV | 4.133%
Tracy | CA | 95376-3828 |  | 2013-10-17 | 2013-10-17 11:57 | 2013-10-17 12:15 | CARRIER - 24ABR342A300 | 113 | 7.6 | Yes | Yes | 21.5 | 20.4 | 1.1 | DE2D9CE172C54C94AA38A7F291C49652 |  | R22 | TXV |  | 6.726% | 0.93274 | 12.93% | [5 empty] | TXV | 6.726%
Oakdale | CA | 95361-4119 |  | 2013-10-24 | 2013-10-24 11:40 | 2013-10-24 12:03 | PAYNE - PY1PNB024060AAAA | 53 | 1.6 | Yes | Yes | 19.9 | 20 | -0.1 | D73B4F04B4B64D20B84DB335BED6EE40 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Stockton | CA | 95203-2960 |  | 2013-10-18 | 2013-10-18 14:18 | 2013-10-18 14:38 | YORK - D1NP030N05606A | 73 | 3.4 | Yes | Yes | 22.7 | 18.8 | 3.9 | 1746A1276B95468AB3A75044255B4C3D |  | R22 | Non-TXV |  | 4.658% | 0.95342 | 8.951% | [5 empty] | Non-TXV | 4.658%
Yuba City | CA | 95993-5901 |  | 2013-10-23 | 2013-10-23 12:05 | 2013-10-23 12:21 | LENNOX - 10ACC-042-230-04 | 81 | 3.2 | Yes | Yes | 20 | 21.7 | -1.7 | 47672D9949C84536860EF3011027C57A |  | R22 | Non-TXV |  | 3.951% | 0.96049 | 7.592% | [5 empty] | Non-TXV | 3.951%
Stockton | CA | 95210-3216 |  | 2013-10-16 | 2013-10-16 09:31 | 2013-10-16 09:48 | RHEEM - RAFD-042JBS | 79 | -5.6 | Yes | Yes | 16.5 | 19.5 | -3 | 32B4226F93D741F0A3CB26554B31E778 |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Chico | CA | 95926-5132 |  | 2013-11-01 | 2013-11-01 14:30 | 2013-11-01 15:00 | PAYNE - 597CN042-B | 131 | 4.9 | Yes | Yes | 20 | 22 | -2 | 0EA42AE3379C4F34A168DDA920FE26AD |  | R22 | TXV |  | 3.74% | 0.9626 | 7.188% | [5 empty] | TXV | 3.74%
Rocklin | CA | 95765-4154 |  | 2013-10-24 | 2013-10-24 17:13 | 2013-10-24 17:13 | OTHER - 597CN036-D | 100 | 0 | Yes | Yes | 24 | 20.9 | 3.1 | EA185E85535A43259A040F8CE606FBF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4312 |  | 2013-10-16 | 2013-10-16 14:22 | 2013-10-16 15:20 | YORK - D1NP036N05606A | 108 | 6.8 | Yes | Yes | 26.9 | 20.9 | 6 | 94206FDE61BD4B74BAD00562F75E779A |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Stockton | CA | 95202-1315 |  | 2013-10-22 | 2013-10-22 11:33 | 2013-10-22 11:49 | TRANE - 2TTB0030A1000AA | 64 | 3.6 | Yes | Yes | 19.3 | 19 | 0.3 | 2BDF5F6B41C548B883F651F91734B11F |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Oroville | CA | 95965-4847 |  | 2013-10-22 | 2013-10-22 10:42 | 2013-10-22 11:00 | TRANE - YCCO18F1LOBC | 56 | 7.8 | Yes | Yes | 21.1 | 20.1 | 1 | 2B6471E307644CCC8D2400128B0BC789 |  | R22 | Non-TXV |  | 13.93% | 0.86071 | 26.77% | [5 empty] | Non-TXV | 13.93%
Stockton | CA | 95219-3107 |  | 2013-10-21 | 2013-10-21 15:09 | 2013-10-21 15:30 | LENNOX - 13ACX-030-230-13 | 68 | 5.8 | Yes | Yes | 24.1 | 18.7 | 5.4 | 56F8D846820E44EFB27F90B70AD8B3AF |  | R410A | TXV |  | 8.529% | 0.91471 | 16.39% | [5 empty] | TXV | 8.529%
Oroville | CA | 95966-5066 |  | 2013-10-22 | 2013-10-22 11:00 | 2013-10-22 12:26 | YORK - D1NP036N05606A | 108 | 8.8 | Yes | Yes | 28.5 | 22.9 | 5.6 | A442C0F8464C41B6ADDBE99064F9D57C |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Tracy | CA | 95376-3210 |  | 2013-10-16 | 2013-10-16 11:59 | 2013-10-16 18:31 | GE - BGTA924H1K | 52 | 4.1 | Yes | Yes | 22 | 20.6 | 1.4 | 7786BA1362DF48FB98A3307F2A1273B5 |  | R22 | Non-TXV |  | 7.885% | 0.92115 | 15.15% | [5 empty] | Non-TXV | 7.885%
Fresno | CA | 93702-5612 |  | 2013-10-23 | 2013-10-23 14:05 | 2013-10-23 14:33 | RHEEM - RRGF-05E24JKR | 42 | 5.8 | Yes | Yes | 19.9 | 20.7 | -0.8 | 6787F185C2F8484BB67BD66F8413B7B6 |  | R22 | Non-TXV |  | 13.81% | 0.8619 | 26.54% | [5 empty] | Non-TXV | 13.81%
Stockton | CA | 95205-5528 |  | 2013-10-18 | 2013-10-18 11:19 | 2013-10-18 11:36 | OTHER - NAC030AKC3 | 75 | 7.7 | Yes | Yes | 17.3 | 18.2 | -0.9 | D265D7C6BF09424BA1F812154A776AFF |  | R22 | Non-TXV |  | 10.27% | 0.89733 | 19.73% | [5 empty] | Non-TXV | 10.27%
Lincoln | CA | 95648-3203 |  | 2013-11-01 | 2013-11-01 16:19 | 2013-11-01 16:19 | YORK - H2RC036S06HG | 83 | 0 | Yes | Yes | 17.2 | 19.1 | -1.9 | 0764703E548B448FBDD74E62657718BD |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-2266 |  | 2013-10-17 | 2013-10-17 10:59 | 2013-10-17 11:19 | GOODMAN - CK49-1B | 97 | 18.4 | Yes | Yes | 21.5 | 20.6 | 0.9 | 8356D16A0F9C4DF38E6286FF5874448E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.97% | 0.81031 | 36.45% | [5 empty] | Non-TXV | 18.97%
Auburn | CA | 95602-8543 |  | 2013-10-18 | 2013-10-18 14:50 | 2013-10-18 14:50 | DAY & NIGHT - UNK | 112 | 0 | Yes | Yes | 22.1 | 20.7 | 1.4 | C2524E81FAF244E090ABF1951BB05DA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-8713 |  | 2013-10-18 | 2013-10-18 12:13 | 2013-10-18 12:14 | BDP - 587ANZ30060AAAE | 67 | 3.3 | Yes | Yes | 17.9 | 20.4 | -2.5 | D9A18BB8433445CAA33B9EAB98FA77E9 |  | R22 | Non-TXV |  | 4.925% | 0.95075 | 9.465% | [5 empty] | Non-TXV | 4.925%
Tracy | CA | 95376-2315 |  | 2013-10-23 | 2013-10-23 14:47 | 2013-10-24 07:29 | BRYANT - 563CNO42-C | 104 | 7.1 | Yes | Yes | 21.3 | 18.8 | 2.5 | 9687915559524C12965C531729989943 |  | R22 | Non-TXV |  | 6.827% | 0.93173 | 13.12% | [5 empty] | Non-TXV | 6.827%
Placerville | CA | 95667-8407 |  | 2013-11-02 | 2013-11-02 13:55 | 2013-11-02 14:14 | TRANE - YCC042F1M0BC | 101 | 3.3 | Yes | Yes | 26 | 21.1 | 4.9 | 332A8F1A12A249DDBE50840F040C733D |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Stockton | CA | 95207-2107 |  | 2013-10-17 | 2013-10-17 13:49 | 2013-10-17 14:05 | BRYANT - 561CJ036-E | 87 | 10.2 | Yes | Yes | 20 | 18.5 | 1.5 | 02C9789B5E9C42FC8345A2BC465BC1CF |  | R22 | Non-TXV |  | 11.72% | 0.88276 | 22.53% | [5 empty] | Non-TXV | 11.72%
Chico | CA | 95973-8209 |  | 2013-10-25 | 2013-10-25 11:13 | 2013-10-25 11:30 | LENNOX - 13ACC-030-230-01 | 106 | 6.2 | Yes | Yes | 19.5 | 20.7 | -1.2 | 1F179C07D4FA4BB5B670BAD4A1006F53 |  | R22 | Non-TXV |  | 5.849% | 0.94151 | 11.24% | [5 empty] | Non-TXV | 5.849%
Auburn | CA | 95603-4509 |  | 2013-10-18 | 2013-10-18 13:53 | 2013-10-18 13:53 | TRANE - YCC03F1M0BE | 72 | 0 | Yes | Yes | 24.6 | 20.6 | 4 | 2CCA83317B1E44E6AD5E463342B422DF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-4238 |  | 2013-10-23 | 2013-10-23 11:26 | 2013-10-23 11:53 | RUUD - UAHE-023JAS | 64 | 2 | Yes | Yes | 23.3 | 18.2 | 5.1 | 98496CA28D5B40F9AC845ADE2B3BE80F |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Atwater | CA | 95301-3013 |  | 2013-10-21 | 2013-10-21 14:57 | 2013-10-21 14:59 | YORK - D1NP036N05606A | 108 | 11.4 | Yes | Yes | 21 | 18.7 | 2.3 | 5AAA0D3984FC4AA9983BC58DA89B02F5 |  | R22 | Non-TXV |  | 10.56% | 0.89444 | 20.29% | [5 empty] | Non-TXV | 10.56%
Winton | CA | 95388-0000 |  | 2013-10-18 | 2013-10-18 10:50 | 2013-10-18 10:51 | COLEMAN - BRCS042C | 89 | 3.3 | Yes | Yes | 23.9 | 19.9 | 4 | 5137B6FD4BD643719D72C0ACC88489D9 |  | R22 | Non-TXV |  | 3.708% | 0.96292 | 7.126% | [5 empty] | Non-TXV | 3.708%
Stockton | CA | 95206-6314 |  | 2013-11-12 | 2013-11-12 12:45 | 2013-11-12 13:02 | YORK - H1R048S06D | 117 | 4 | Yes | Yes | 18 | 18.3 | -0.3 | 6730CB5F62044372AD71E00378DB9DC0 |  | R22 | Non-TXV |  | 3.419% | 0.96581 | 6.57% | [5 empty] | Non-TXV | 3.419%
Manteca | CA | 95337-4238 |  | 2013-10-31 | 2013-10-31 12:27 | 2013-10-31 12:47 | RUUD - UAHE-023JAS | 64 | -13 | Yes | Yes | 20.2 | 19.1 | 1.1 | 45E02FC8792844698A3E67B6F9148CF8 |  | R22 | Non-TXV |  | -20.31% | 1.2031 | 5.688% |  |  |  |  | Non-TXV |  |  | -20.31%
Chowchilla | CA | 93610-8467 |  | 2013-10-17 | 2013-10-17 13:15 | 2013-10-17 13:16 | GOODMAN - CLJ601 | 141 | 16.2 | Yes | Yes | 22.7 | 17.2 | 5.5 | 809817A8957E490E829F7366C8F436C0 |  | R22 | Non-TXV |  | 11.49% | 0.88511 | 22.08% | [5 empty] | Non-TXV | 11.49%
Stockton | CA | 95206-4623 |  | 2013-10-25 | 2013-10-25 14:58 | 2013-10-25 15:14 | CARRIER - UNK | 104 | 4.1 | Yes | Yes | 23 | 18.5 | 4.5 | 8AEC54A5B312496DB371CB49D7EDC345 |  | R22 | Non-TXV |  | 3.942% | 0.96058 | 7.576% | [5 empty] | Non-TXV | 3.942%
Manteca | CA | 95336-4142 |  | 2013-10-17 | 2013-10-17 11:58 | 2013-10-17 12:17 | GE - BGTA736B1B | 70 | 4.6 | Yes | Yes | 18.9 | 18.7 | 0.2 | 0C2A455D711D4E67B449E796FA72C944 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 6.571% | 0.93429 | 12.63% | [5 empty] | Non-TXV | 6.571%
Manteca | CA | 95337-4237 |  | 2013-10-31 | 2013-10-31 13:15 | 2013-10-31 13:36 | RUUD - UAHE-023JAS | 64 | 11.9 | Yes | Yes | 26.2 | 20.4 | 5.8 | BCADC2F31AD44F08AAF42FD54039CEF7 |  | R22 | Non-TXV |  | 18.59% | 0.81406 | 35.73% | [5 empty] | Non-TXV | 18.59%
Fresno | CA | 93727-4605 |  | 2013-10-17 | 2013-10-17 15:34 | 2013-10-17 15:53 | OTHER - N/A | 60 | 4.4 | Yes | Yes | 23.7 | 20.1 | 3.6 | F128622CB0554650A18E3E912311C800 |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Manteca | CA | 95336-3917 |  | 2013-10-31 | 2013-10-31 14:39 | 2013-10-31 15:05 | OTHER - CBD | 64 | 2.1 | Yes | Yes | 19.3 | 19.4 | -0.1 | 0478687CD6944F7BB9EEECF7F3D31A7B |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Stockton | CA | 95210-1758 |  | 2013-10-18 | 2013-10-18 10:30 | 2013-10-18 10:51 | BDP - 585B030075YACR | 50 | -3.5 | Yes | Yes | 21.9 | 18.7 | 3.2 | 70A5CC774A4A425D8FA6033B454BF0CC |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
San Carlos | CA | 94070-4533 |  | 2013-10-21 | 2013-10-21 11:53 | 2013-10-21 12:36 | OTHER - HC4A336AKA100 | 140 | 8.9 | Yes | Yes | 17.3 | 17.7 | -0.4 | C6BBE95858D74CF98020758618B5B3FB |  | R410A | Non-TXV |  | 6.357% | 0.93643 | 12.22% | [5 empty] | Non-TXV | 6.357%
Stockton | CA | 95212-3031 |  | 2013-10-17 | 2013-10-17 10:59 | 2013-10-17 11:26 | GOODMAN - GSC130361GA | 77 | 3.4 | Yes | Yes | 22.7 | 21 | 1.7 | 179C5CC4BCBE49E0A5E3D54984E2550E |  | R22 | Non-TXV |  | 4.416% | 0.95584 | 8.486% | [5 empty] | Non-TXV | 4.416%
Rocklin | CA | 95677-4503 |  | 2013-10-21 | 2013-10-21 13:36 | 2013-10-21 13:53 | GOODMAN - CK49-1B | 90 | 3.3 | Yes | Yes | 23 | 21.5 | 1.5 | 483F29A7C121438782FEC3B4C7155F01 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Manteca | CA | 95337-6017 |  | 2013-10-17 | 2013-10-17 11:11 | 2013-10-17 11:39 | AMERICAN STANDARD - 7B0023B100A1 | 54 | 3.4 | Yes | Yes | 23.5 | 18.2 | 5.3 | B71D062DA8004DFC98249D24DCBEFE55 |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Kerman | CA | 93630-1515 |  | 2013-10-24 | 2013-10-24 11:14 | 2013-10-24 11:43 | DAY & NIGHT - N/A | 124 | 3.7 | Yes | Yes | 21.5 | 20.9 | 0.6 | 132BF5AAE9C44E0BB721DAF58AA5D7C8 |  | R22 | Non-TXV |  | 2.984% | 0.97016 | 5.734% | [5 empty] | Non-TXV | 2.984%
Kerman | CA | 93630-1515 |  | 2013-10-24 | 2013-10-24 11:46 | 2013-10-24 12:14 | DAY & NIGHT - N/A | 60 | 3.8 | Yes | Yes | 26.6 | 21.4 | 5.2 | 89391C82B4A147F494C92DA6711AF0F0 |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Auburn | CA | 95603-5502 |  | 2013-10-16 | 2013-10-16 14:43 | 2013-10-16 15:01 | RHEEM - HC-80-30-210 | 48 | 3.1 | Yes | Yes | 25.2 | 20.4 | 4.8 | CF15E1ABB61C40FDAE58301D2930C57F |  | R22 | Non-TXV |  | 6.458% | 0.93542 | 12.41% | [5 empty] | Non-TXV | 6.458%
Lincoln | CA | 95648-8261 |  | 2013-10-18 | 2013-10-18 13:03 | 2013-10-18 13:25 | CARRIER - 38CKC048-371 | 100 | 10.6 | Yes | Yes | 18.5 | 20.9 | -2.4 | ED7E4A247567446F89D0E37D2E526039 |  | R22 | Non-TXV |  | 10.6% | 0.894 | 20.37% | [5 empty] | Non-TXV | 10.6%
Pinedale | CA | 93650-1074 |  | 2013-10-25 | 2013-10-25 11:01 | 2013-10-25 12:04 | BDP - 585A048125YAC | 93 | 7.5 | Yes | Yes | 24 | 21.2 | 2.8 | 9F05A483377D47B190F164D9D906E473 |  | R22 | Non-TXV |  | 8.065% | 0.91935 | 15.5% | [5 empty] | Non-TXV | 8.065%
El Dorado Hills | CA | 95762-0000 |  | 2013-10-21 | 2013-10-21 11:44 | 2013-10-21 12:02 | LENNOX - 13ACD-048-230-01 | 204 | 22.3 | Yes | Yes | 23.9 | 20.6 | 3.3 | 720F5AC5B7E94B0BB4AE9D64A0AD62A2 |  | R22 | Non-TXV |  | 10.93% | 0.89069 | 21.01% | [5 empty] | Non-TXV | 10.93%
Stockton | CA | 95206-6056 |  | 2013-11-12 | 2013-11-12 14:16 | 2013-11-12 14:34 | GOODMAN - CLJ36-J | 80 | 4.3 | Yes | Yes | 17.5 | 17.7 | -0.2 | A13335D0437A4D29B67A6C8FF8C8C16B |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Manteca | CA | 95336-3987 |  | 2013-10-17 | 2013-10-17 13:11 | 2013-10-17 13:31 | BRYANT - 56CJ024-E | 55 | 3 | Yes | Yes | 20.1 | 18.8 | 1.3 | A08263B8296744BB86330F0740DD3FCD |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Fresno | CA | 93704-6136 |  | 2013-10-16 | 2013-10-16 13:30 | 2013-10-16 14:20 | AMERICAN STANDARD - YCY042G1M0AB | 147 | 19.6 | Yes | Yes | 17.7 | 20.4 | -2.7 | CBE284089374480FAB96A4A207F44D94 |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Manteca | CA | 95336-3986 |  | 2013-10-17 | 2013-10-17 12:37 | 2013-10-17 13:10 | BRYANT - 561CJ024-E | 55 | 2 | Yes | Yes | 20 | 18.2 | 1.8 | 1C89E660B5DB45148DB4159A93033229 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Wheatland | CA | 95692-9263 |  | 2013-10-16 | 2013-10-16 16:42 | 2013-10-16 16:58 | GOODMAN - GSC140601AE | 279 | 8.9 | Yes | Yes | 20 | 22.6 | -2.6 | 250B91D020524DCC860F517162948D8F |  | R22 | Non-TXV |  | 3.19% | 0.9681 | 6.13% | [5 empty] | Non-TXV | 3.19%
Stockton | CA | 95207-7714 |  | 2013-10-24 | 2013-10-24 13:02 | 2013-10-24 13:20 | GOODMAN - CK30-1T | 76 | -6.3 | Yes | Yes | 18.4 | 18.7 | -0.3 | 558C21F0664F4E12A233C68EEB959D36 |  | R22 | Non-TXV |  | -8.289% | 1.0829 | 2.321% |  |  |  |  | Non-TXV |  |  | -8.289%
Fresno | CA | 93705-5147 |  | 2013-10-25 | 2013-10-25 16:47 | 2013-10-25 16:48 | DAY & NIGHT - 777UNK | 80 | 2.9 | Yes | Yes | 24.6 | 19.3 | 5.3 | 0EF2F47A98F74D6DA132BB72E8A703F9 |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Madera | CA | 93638-1624 |  | 2013-11-01 | 2013-11-01 23:26 | 2013-11-01 23:28 | RHEEM - RRNL-B036JK06X | 93 | 2.9 | Yes | Yes | 22.2 | 19.3 | 2.9 | FD71086FFF5A42C1BCB832872FF694C8 |  | R410A | Non-TXV |  | 3.118% | 0.96882 | 5.993% | [5 empty] | Non-TXV | 3.118%
Stockton | CA | 95206-4811 |  | 2013-10-31 | 2013-10-31 15:12 | 2013-10-31 15:57 | GOODMAN - CE30-1HB | 72 | 6.2 | Yes | Yes | 25 | 19.9 | 5.1 | 6763A1CAB40D4F6AAF8609214A4DAED1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.611% | 0.91389 | 16.55% | [5 empty] | Non-TXV | 8.611%
Fresno | CA | 93705-1550 |  | 2013-10-17 | 2013-10-17 11:12 | 2013-10-17 16:04 | CARRIER - 38CKC048300 | 99 | 13 | Yes | Yes | 18.5 | 20.9 | -2.4 | 0807D023BB7340CB9C2BF5A93B38160C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.13% | 0.86869 | 25.24% | [5 empty] | Non-TXV | 13.13%
Fresno | CA | 93727-2029 |  | 2013-10-17 | 2013-10-17 13:48 | 2013-10-17 14:27 | CARRIER - 48DL004 | 81 | 4.4 | Yes | Yes | 25.5 | 20.9 | 4.6 | CDD60E56CA7440DDB189597CDD028AE8 |  | R22 | Non-TXV |  | 5.432% | 0.94568 | 10.44% | [5 empty] | Non-TXV | 5.432%
Madera | CA | 93638-1053 |  | 2013-11-01 | 2013-11-01 15:12 | 2013-11-01 15:13 | CARRIER - 48GS-036060301 | 82 | 3.6 | Yes | Yes | 23.6 | 19.8 | 3.8 | BE17D857590441F88DB3F655CB1C61A6 |  | R22 | Non-TXV |  | 4.39% | 0.9561 | 8.437% | [5 empty] | Non-TXV | 4.39%
Manteca | CA | 95336-4515 |  | 2013-10-25 | 2013-10-25 10:45 | 2013-10-25 11:10 | RHEEM - RRMA-A024JK06X | 70 | -6.3 | Yes | Yes | 23.5 | 20.4 | 3.1 | 2EA7C408D10F411EB1620EA5B6BF7C24 |  | R22 | TXV |  | -9% | 1.09 | 2.52% |  |  |  |  | TXV |  |  | -9%
Fresno | CA | 93722-5181 |  | 2013-10-18 | 2013-10-18 09:49 | 2013-10-18 10:26 | CARRIER - N/A | 90 | 9.2 | Yes | Yes | 21 | 20.8 | 0.2 | 6AAF4B41C6124255A1A280505110EC4B |  | R22 | Non-TXV |  | 10.22% | 0.89778 | 19.64% | [5 empty] | Non-TXV | 10.22%
Stockton | CA | 95206-3737 |  | 2013-10-25 | 2013-10-25 14:28 | 2013-10-25 14:46 | ICP - UNK | 98 | -5.8 | Yes | Yes | 25.6 | 19.6 | 6 | 54F3226C9A494F7E9EAFBFBE777504F9 |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Lincoln | CA | 95648-8004 |  | 2013-10-24 | 2013-10-24 13:51 | 2013-10-24 14:09 | CARRIER - 38CBC042350 | 83 | 5.2 | Yes | Yes | 24.6 | 21.2 | 3.4 | F12EBF4E817040FF9A4F493B6821B4B2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.265% | 0.93735 | 12.04% | [5 empty] | Non-TXV | 6.265%
Manteca | CA | 95337-5546 |  | 2013-10-31 | 2013-10-31 15:22 | 2013-10-31 17:26 | GOODMAN - CKL24-1L | 76 | 2.3 | Yes | Yes | 19 | 19.3 | -0.3 | 830D25DEE53449CDB08F951E2E0BB9A5 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Fresno | CA | 93706-5021 |  | 2013-10-25 | 2013-10-25 15:35 | 2013-10-25 15:37 | GOODMAN - GPG10360701A | 75 | 2.7 | Yes | Yes | 22.5 | 21 | 1.5 | 70653A24AE384CC6ADADEE22DC72BB15 |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Tracy | CA | 95376-3223 |  | 2013-10-23 | 2013-10-23 14:24 | 2013-10-23 14:24 | BRYANT - 561CJ046-C | 72 | 0 | Yes | Yes | 21.3 | 18.5 | 2.9 | 00187A7AB7704929B9523C1DCE977F5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3017 |  | 2013-10-17 | 2013-10-17 16:35 | 2013-10-17 17:15 | YORK - D1NP042N6506A | 150 | 6.3 | Yes | Yes | 25.9 | 21.5 | 4.4 | 597FFB31F7F349368B4B6EBB34AADFA9 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Rocklin | CA | 95765-5419 |  | 2013-10-24 | 2013-10-24 14:49 | 2013-10-24 15:06 | YORK - H1RA042S06A | 84 | 2.6 | Yes | Yes | 20 | 21.1 | -1.1 | D57A652AFB3F42D98C2C980BD68D1FD2 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Manteca | CA | 95336-5043 |  | 2013-10-25 | 2013-10-25 09:50 | 2013-10-25 10:24 | GOODMAN - GSC130481AF | 152 | -10.7 | Yes | Yes | 25.4 | 20.6 | 4.8 | 666D6E34CD2E46F98D0814C75CF01AE9 |  | R22 | Non-TXV |  | -7.039% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.039%
Tracy | CA | 95377-2287 |  | 2013-10-17 | 2013-10-17 14:51 | 2013-10-17 15:09 | BRYANT - 561CJ048-A | 102 | -9.6 | Yes | Yes | 22.5 | 20.6 | 1.9 | BC519CC7DF8F4112A15E0DF805E43F77 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Rocklin | CA | 95765-5834 |  | 2013-10-17 | 2013-10-17 15:34 | 2013-10-17 15:34 | GOODMAN - CLJ36-1A | 109 | 0 | Yes | Yes | 18.1 | 20.8 | -2.7 | 33BC0C6D56094A4892909C9017A09AA7 |  | R22 | TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-5834 |  | 2013-10-17 | 2013-10-17 15:51 | 2013-10-17 16:34 | GOODMAN - CLJ36-1A | 109 | 9.5 | Yes | Yes | 19.6 | 20.4 | -0.8 | F27D35D0CDB24D6DAB79BA0AF5CB718A |  | R22 | TXV |  | 8.716% | 0.91284 | 16.75% | [5 empty] | TXV | 8.716%
Tracy | CA | 95376-2724 |  | 2013-11-02 | 2013-11-02 13:42 | 2013-11-02 14:11 | BDP - 582ANW030060NAAD | 55 | 2.9 | Yes | Yes | 20.8 | 19.5 | 1.3 | A1C24BFD61924031B17562DB70628B95 |  | R22 | Non-TXV |  | 5.273% | 0.94727 | 10.13% | [5 empty] | Non-TXV | 5.273%
Rocklin | CA | 95765-4112 |  | 2013-10-24 | 2013-10-24 16:45 | 2013-10-24 17:01 | TRANE - 4TTX6048A1000AA | 120 | 4.4 | Yes | Yes | 19 | 21.4 | -2.4 | 3635AF85197442CB9C0CE4CAF9C03E8C |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Manteca | CA | 95336-5025 |  | 2013-10-25 | 2013-10-25 09:13 | 2013-10-25 09:35 | UNITARY PRODUCTS GROUP - BRCQ0421BD | 66 | 15.4 | Yes | Yes | 17.8 | 19.5 | -1.7 | 2C5DDC794D5542D9AB25B0AD2B44635E |  | R22 | Non-TXV |  | 23.33% | 0.76667 | 44.84% | [5 empty] | Non-TXV | 23.33%
Fresno | CA | 93722-2772 |  | 2013-10-16 | 2013-10-16 16:31 | 2013-10-16 16:50 | CARRIER - 48SS-030040321 | 53 | 5.3 | Yes | Yes | 26.7 | 20.9 | 5.8 | CA008DE148EB4297871F36962F335A01 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Kingsburg | CA | 93631-1212 |  | 2013-11-01 | 2013-11-01 15:32 | 2013-11-01 15:53 | CARRIER - N/A | 120 | 3.6 | Yes | Yes | 17 | 19.8 | -2.8 | 91280EF8942C42CB89627529496791B8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Manteca | CA | 95336-5037 |  | 2013-10-23 | 2013-10-23 12:42 | 2013-10-23 13:04 | COPELAND - BRC00361BD | 52 | 1.8 | Yes | Yes | 23.4 | 18.5 | 5 | 2BE9891FF826454E90CC573D97F3386B |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Chico | CA | 95928-3961 |  | 2013-10-23 | 2013-10-23 12:44 | 2013-10-23 13:01 | DAY & NIGHT - 593CJ042-A | 88 | 4.9 | Yes | Yes | 18.4 | 21.4 | -3 | DA5069002B8947138ED984CF968F1EC2 |  | R22 | TXV |  | 5.568% | 0.94432 | 10.7% | [5 empty] | TXV | 5.568%
Fresno | CA | 93722-2848 |  | 2013-10-18 | 2013-10-18 13:20 | 2013-10-18 13:39 | CARRIER - 8BR060300 | 200 | 8.4 | Yes | Yes | 18 | 20.7 | -2.7 | 65AB21CDDC3C488EB115FDAF552A47AA |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Stockton | CA | 95204-3113 |  | 2013-10-31 | 2013-10-31 12:20 | 2013-10-31 12:38 | RHEEM - RAKA-037JAZ | 79 | -5.6 | Yes | Yes | 20.3 | 18.2 | 2.1 | 353E0CD833A944FC9D7DE983348198BA |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Rocklin | CA | 95677-3522 |  | 2013-10-17 | 2013-10-17 17:36 | 2013-10-17 17:36 | CARRIER - 38CKC018330 | 53 | 0 | Yes | Yes | 17.7 | 20.6 | -2.9 | 97F07B97664D49B2A5D7DD4C52343729 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-1435 |  | 2013-10-21 | 2013-10-21 16:02 | 2013-10-21 16:03 | WEATHER KING - 12AJAA4801 | 85 | 8.2 | Yes | Yes | 18.8 | 21 | -2.2 | 3BC93529DDEA44ACA1A63D76A99FFE2E |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Paradise | CA | 95969-5980 |  | 2013-10-24 | 2013-10-24 11:50 | 2013-10-24 19:31 | DAY & NIGHT - PGD324060K00C1 | 72 | 5.2 | Yes | Yes | 21.5 | 24.4 | -2.9 | F7ED8B2473C448268D1770928CD3F2C1 |  | R410A | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Chico | CA | 95926-3198 |  | 2013-10-21 | 2013-10-21 09:45 | 2013-10-21 10:26 | YORK - H2CB036506A | 51 | 1.8 | Yes | Yes | 18.6 | 20.9 | -2.3 | BA2BF2B1512D443DA9869B3E00EB5F81 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Clovis | CA | 93611-5163 |  | 2013-10-21 | 2013-10-21 14:08 | 2013-10-21 15:09 | YORK - D1NH036N05606C | 108 | 8.5 | Yes | Yes | 24.2 | 22.3 | 1.9 | 6230BDBEFDA44AF7851995BA22529609 |  | R22 | Non-TXV |  | 7.87% | 0.9213 | 15.13% | [5 empty] | Non-TXV | 7.87%
Kerman | CA | 93630-0000 |  | 2013-10-23 | 2013-10-23 10:12 | 2013-10-23 11:54 | CARRIER - 24ABR336A330 | 84 | 2.7 | Yes | Yes | 19.4 | 21.4 | -2 | D1E4CE39833A4ADDBA5B8FD9B1C48B71 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Stockton | CA | 95209-3601 |  | 2013-10-23 | 2013-10-23 10:39 | 2013-10-23 10:58 | PAYNE - PA13NR060-H | 165 | -11.6 | Yes | Yes | 20.9 | 19.9 | 1 | 124E85F8452C408DACAAD389936258B2 |  | R22 | Non-TXV |  | -7.03% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.03%
Stockton | CA | 95205-2691 |  | 2013-10-24 | 2013-10-24 11:10 | 2013-10-24 11:13 | PAYNE - PA13NA024-B | 63 | 4.7 | Yes | Yes | 18.6 | 18.8 | -0.2 | F150F0927E7D4F608AFA3AA68217BF07 |  | R410A | TXV |  | 7.46% | 0.9254 | 14.34% | [5 empty] | TXV | 7.46%
Stockton | CA | 95203-3241 |  | 2013-10-24 | 2013-10-24 10:14 | 2013-10-24 10:32 | BRYANT - 561CJ030-D | 68 | -4 | Yes | Yes | 19.7 | 18.7 | 1 | 4B660473F22B4343A7EECDC59736110D |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Live Oak | CA | 95953-9439 |  | 2013-10-23 | 2013-10-23 11:29 | 2013-10-23 11:50 | CARRIER - 24ABA360A300 | 105 | 3.8 | Yes | Yes | 22 | 20.4 | 1.6 | 08C31FAF8F7E42B8912526BCE1403900 |  | R410A | TXV |  | 3.619% | 0.96381 | 6.955% | [5 empty] | TXV | 3.619%
Stockton | CA | 95206-4635 |  | 2013-10-31 | 2013-10-31 16:58 | 2013-10-31 17:23 | GOODMAN - CKJ60-1C | 142 | 10.3 | Yes | Yes | 17.4 | 19.8 | -2.4 | 1499C34F5D7F485EB4DFD7D3EE2651E7 |  | R22 | Non-TXV |  | 7.254% | 0.92746 | 13.94% | [5 empty] | Non-TXV | 7.254%
Stockton | CA | 95210-3427 |  | 2013-10-18 | 2013-10-18 11:09 | 2013-10-18 11:29 | CARRIER - 38EB030300 | 85 | -5 | Yes | Yes | 19.4 | 20.1 | -0.7 | F15FC4C0E7D149568D38EC817C13FC6B |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Auburn | CA | 95602-8261 |  | 2013-10-17 | 2013-10-17 12:55 | 2013-10-17 13:18 | CARRIER - 48SS-036080311-- | 69 | 8 | Yes | Yes | 22.9 | 20.4 | 2.5 | 59E3EDA71410429A9C9BC156D7285772 |  | R22 | TXV |  | 11.59% | 0.88406 | 22.28% | [5 empty] | TXV | 11.59%
Clovis | CA | 93611-3141 |  | 2013-10-23 | 2013-10-23 16:00 | 2013-10-23 16:54 | GOODMAN - PGB036075-1 | 60 | 4.1 | Yes | Yes | 22 | 20.4 | 1.6 | DD6FE4F808DB4B5DAC338360E4A03CE6 |  | R22 | Non-TXV |  | 6.833% | 0.93167 | 13.13% | [5 empty] | Non-TXV | 6.833%
Fresno | CA | 93722-5182 |  | 2013-10-17 | 2013-10-17 12:43 | 2013-10-17 16:05 | CARRIER - 48KLS124-300BE | 68 | 10.4 | Yes | Yes | 17.5 | 20.4 | -2.9 | E2DB33ACCBD74757836BF9487B640573 |  | R22 | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
Fresno | CA | 93711-0515 |  | 2013-10-16 | 2013-10-16 18:17 | 2013-10-16 18:34 | AMANA - PGA48B0802 | 140 | 13.1 | Yes | Yes | 17.5 | 20.4 | -2.9 | 55E5DA85B8D849A1A1A1FC4014104FF2 |  | R22 | Non-TXV |  | 9.357% | 0.90643 | 17.98% | [5 empty] | Non-TXV | 9.357%
Oakdale | CA | 95361-2739 |  | 2013-10-24 | 2013-10-24 10:59 | 2013-10-24 11:25 | DAY & NIGHT - CBD | 64 | 2.1 | Yes | Yes | 22.2 | 19.5 | 2.7 | 5A3065BCC27F42899EE91927AEA3AD2A |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Kerman | CA | 93630-2111 |  | 2013-10-24 | 2013-10-24 12:50 | 2013-10-24 13:33 | LENNOX - 10GCS030X-75-1PA | 51 | 1.6 | Yes | Yes | 24.5 | 21.1 | 3.5 | 38B5D3A5028E441A9E5BA411A62F9976 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Fresno | CA | 93722-6809 |  | 2013-10-24 | 2013-10-24 17:57 | 2013-10-24 19:27 | UNITARY PRODUCTS GROUP - DAYP-F036N070A | 108 | 5.5 | Yes | Yes | 23.8 | 21 | 2.8 | 6E1E6ED1161442FABA9E5D84C75EEF63 |  | R22 | Non-TXV |  | 5.093% | 0.94907 | 9.787% | [5 empty] | Non-TXV | 5.093%
Fresno | CA | 93703-1455 |  | 2013-10-16 | 2013-10-16 12:17 | 2013-10-16 12:33 | BDP - 588ANE042080 | 82 | 11.7 | Yes | Yes | 19.5 | 20 | -0.4 | 61EC6A422E664AE0831F01488E5864B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.27% | 0.85732 | 27.42% | [5 empty] | Non-TXV | 14.27%
Lincoln | CA | 95648-1649 |  | 2013-10-18 | 2013-10-18 10:07 | 2013-10-18 10:29 | HEIL - PGAA36D1K6 | 69 | 4 | Yes | Yes | 26.1 | 20.7 | 5.4 | 26B6591336D3497ABAB20B714D9EF844 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.797% | 0.94203 | 11.14% | [5 empty] | Non-TXV | 5.797%
Stockton | CA | 95205-2535 |  | 2013-10-24 | 2013-10-24 09:34 | 2013-10-24 09:34 | BRYANT - 561CJ036-F | 71 | 0 | Yes | Yes | 21.5 | 19.4 | 2.1 | D97C8152053D43768D8E9D25864333D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-0000 |  | 2013-10-18 | 2013-10-18 16:31 | 2013-10-18 16:32 | OTHER - ACC042BVAA | 81 | 12.1 | Yes | Yes | 20.4 | 19.3 | 1.1 | 7D04E3CB7E2B4964A4C405BC53A62D09 |  | R22 | Non-TXV |  | 14.94% | 0.85062 | 28.71% | [5 empty] | Non-TXV | 14.94%
Tracy | CA | 95377-2285 |  | 2013-10-25 | 2013-10-25 11:29 | 2013-10-25 11:55 | BRYANT - 561CJ042-A | 80 | 2.7 | Yes | Yes | 19.8 | 18.7 | 1.1 | B36B373B94F74FACB5426642E24320B6 |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Fresno | CA | 93722-3325 |  | 2013-10-25 | 2013-10-25 15:54 | 2013-10-25 16:34 | RHEEM - RRNL-B042JK08X | 112 | 5.3 | Yes | Yes | 22 | 20.4 | 1.6 | 11B20AB1D5624518A5C0ABB49B93EF59 |  | R410A | TXV |  | 4.732% | 0.95268 | 9.094% | [5 empty] | TXV | 4.732%
Selma | CA | 93662-2634 |  | 2013-10-22 | 2013-10-22 14:05 | 2013-10-22 14:30 | COLEMAN - N/A | 90 | 3 | Yes | Yes | 24.5 | 20.4 | 4.1 | 24B6AA661D7C4287AE492668C67F6512 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Tracy | CA | 95376-2066 |  | 2013-10-23 | 2013-10-23 10:43 | 2013-10-23 10:43 | BRYANT - 561CJ042-A | 80 | 0 | Yes | Yes | 20.2 | 18.3 | 2 | 3031FF9FAE66476CAC941C0F958BB89F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3143 |  | 2013-10-31 | 2013-10-31 13:39 | 2013-10-31 13:58 | YORK - CHE-024-6A | 82 | 36.9 | Yes | Yes | 24.9 | 20.6 | 4.3 | 32ADC58FB37F47E9A082FE708BD8B491 |  | R22 | Non-TXV |  | 45% | 0.55 | 86.48% | [5 empty] | Non-TXV | 45%
Stockton | CA | 95206-1800 |  | 2013-10-31 | 2013-10-31 11:30 | 2013-10-31 11:50 | DAY & NIGHT - 565BJ030 | 72 | 11.4 | Yes | Yes | 17 | 18.2 | -1.2 | 6537F998A14E4924BC8B63ECA11FB4BA |  | R22 | Non-TXV |  | 15.83% | 0.84167 | 30.43% | [5 empty] | Non-TXV | 15.83%
Atwater | CA | 95301-3866 |  | 2013-10-21 | 2013-10-21 13:52 | 2013-10-21 14:04 | CARRIER - 38CKC060371 | 131 | 13.6 | Yes | Yes | 21.3 | 18.1 | 3.2 | D2034F187C304F13BE695FD51D334849 |  | R22 | TXV |  | 10.38% | 0.89618 | 19.95% | [5 empty] | TXV | 10.38%
Stockton | CA | 95206-6113 |  | 2013-11-01 | 2013-11-01 13:20 | 2013-11-01 13:45 | RUUD - UAMA-030JBZ | 96 | -5.6 | Yes | Yes | 16.5 | 18.2 | -1.7 | A98DF58D40074C53941DBF82B07DD336 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93728-2233 |  | 2013-10-21 | 2013-10-21 13:10 | 2013-10-21 13:11 | OTHER - N/A | 60 | 4.4 | Yes | Yes | 20 | 21.4 | -1.4 | 4E271E5D690B44C5BF0C89D05D19948C |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Fresno | CA | 93727-3685 |  | 2013-10-23 | 2013-10-23 13:09 | 2013-10-23 14:02 | LENNOX - 10GCS042X-75-5PB | 73 | 8.5 | Yes | Yes | 26 | 21.3 | 4.7 | 2ECFC5B51ABA4A35B7B6342499B8DB19 |  | R22 | Non-TXV |  | 11.64% | 0.88356 | 22.38% | [5 empty] | Non-TXV | 11.64%
Stockton | CA | 95209-5118 |  | 2013-10-23 | 2013-10-23 11:22 | 2013-10-23 11:41 | BDP - 565BJ048 | 91 | 47.5 | Yes | Yes | 16.7 | 19.5 | -2.8 | E56AC0B7187E463DAEB1C6892EDB6F82 |  | R22 | Non-TXV |  | 52.2% | 0.47802 | 100.3% | [5 empty] | Non-TXV | 52.2%
Chico | CA | 95926-1039 |  | 2013-10-23 | 2013-10-23 15:07 | 2013-10-23 15:24 | BRYANT - 113RNA024-E | 69 | 4.2 | Yes | Yes | 22 | 21.4 | 0.6 | 1C2A91E3251245579144946D0BC844A8 |  | R22 | TXV |  | 6.087% | 0.93913 | 11.7% | [5 empty] | TXV | 6.087%
Rocklin | CA | 95765-5089 |  | 2013-10-24 | 2013-10-24 13:23 | 2013-10-24 13:41 | BRYANT - 563CN048-E | 149 | 4.4 | Yes | Yes | 21 | 20.6 | 0.4 | 796FE9EB08F34C7FBF52BEB20F586B1B |  | R22 | Non-TXV |  | 2.953% | 0.97047 | 5.675% | [5 empty] | Non-TXV | 2.953%
Clovis | CA | 93612-6013 |  | 2013-10-21 | 2013-10-21 16:06 | 2013-10-21 17:10 | BDP - 589ANW0030060ADBD | 69 | 4.3 | Yes | Yes | 22.5 | 20.7 | 1.8 | DBE9AE935A224894929FCFDF57587E9B |  | R22 | Non-TXV |  | 6.232% | 0.93768 | 11.98% | [5 empty] | Non-TXV | 6.232%
Stockton | CA | 95203-2017 |  | 2013-10-24 | 2013-10-24 11:02 | 2013-10-24 11:28 | GOODMAN - GSC130421AC | 137 | -9.7 | Yes | Yes | 24.2 | 18.7 | 5.5 | AE5288D140CB4FDEB9247EADFE968E78 |  | R22 | Non-TXV |  | -7.08% | 1.0708 | 1.983% |  |  |  |  | Non-TXV |  |  | -7.08%
Fresno | CA | 93722-3335 |  | 2013-10-16 | 2013-10-16 17:24 | 2013-10-16 17:49 | CARRIER - 48NLT036301L | 84 | 13.3 | Yes | Yes | 22.9 | 20.4 | 2.5 | 9389B08BC1E042A2B2E3093DF6B0DEDB |  | R22 | Non-TXV |  | 15.83% | 0.84167 | 30.43% | [5 empty] | Non-TXV | 15.83%
Fresno | CA | 93727-2320 |  | 2013-10-17 | 2013-10-17 14:30 | 2013-10-17 14:54 | TRANE - TTR042D100B0 | 81 | 2.8 | Yes | Yes | 18 | 20.9 | -2.9 | ABCBB39380BD4311BC8C5C05C9183F6D |  | R22 | Non-TXV |  | 3.457% | 0.96543 | 6.643% | [5 empty] | Non-TXV | 3.457%
Manteca | CA | 95336-3147 |  | 2013-10-23 | 2013-10-23 10:37 | 2013-10-23 11:01 | YORK - D3NZ030N3606NXC | 64 | 1.9 | Yes | Yes | 25.3 | 20.1 | 5.2 | 6E5F8F7426B2404CAA6EA2934FC99B37 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93722-2406 |  | 2013-10-25 | 2013-10-25 16:36 | 2013-10-25 17:06 | CARRIER - N/A | 90 | 6 | Yes | Yes | 18 | 20.7 | -2.7 | 4D6A087C698348E6A56E4B1B7DEC8DDF |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Colfax | CA | 95713-9601 |  | 2013-10-24 | 2013-10-24 11:11 | 2013-10-24 11:28 | AMERICAN STANDARD - YCP048F1H0AB | 166 | 6.2 | Yes | Yes | 26 | 20.9 | 5.1 | 7AA3DD1FE41A4ADC86EE555E6774C8F5 |  | R22 | TXV |  | 3.735% | 0.96265 | 7.178% | [5 empty] | TXV | 3.735%
Fresno | CA | 93722-6775 |  | 2013-10-25 | 2013-10-25 18:16 | 2013-10-25 18:17 | GOODMAN - CJ24-1AB | 101 | 5.5 | Yes | Yes | 18 | 20.4 | -2.4 | 5E77BA5D8C4348A8A920938AB994BAFF |  | R22 | Non-TXV |  | 5.446% | 0.94554 | 10.47% | [5 empty] | Non-TXV | 5.446%
Stockton | CA | 95206-6442 |  | 2013-10-31 | 2013-10-31 13:13 | 2013-10-31 13:37 | CARRIER - 38CKC030340 | 68 | -4 | Yes | Yes | 19.5 | 20.2 | -0.7 | B388E75B1F104880B6878C68C0CB7916 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93702-1934 |  | 2013-10-21 | 2013-10-21 17:12 | 2013-10-21 17:50 | RHEEM - RRNA-B030JKO6X | 65 | 8.2 | Yes | Yes | 23 | 20.7 | 2.3 | EFFBE47F45FB41A2950DA49A6AF82212 |  | R22 | Non-TXV |  | 12.62% | 0.87385 | 24.24% | [5 empty] | Non-TXV | 12.62%
Merced | CA | 95348-2179 |  | 2013-10-21 | 2013-10-21 21:51 | 2013-10-21 21:52 | BRYANT - 113ANA018-E | 54 | 2.2 | Yes | Yes | 19.7 | 21.2 | -1.5 | 170E65E0E06C4A558BA5A46E1F760E22 |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Stockton | CA | 95215-5416 |  | 2013-10-24 | 2013-10-24 15:55 | 2013-10-24 16:18 | YORK - D1NA036N05606C | 67 | 4.8 | Yes | Yes | 24.6 | 20.1 | 4.5 | 9DD69D8816804035897404E5B421ACF1 |  | R22 | Non-TXV |  | 7.164% | 0.92836 | 13.77% | [5 empty] | Non-TXV | 7.164%
Stockton | CA | 95210-4226 |  | 2013-10-23 | 2013-10-23 14:58 | 2013-10-23 15:16 | CARRIER - 38EN024300 | 56 | 2.4 | Yes | Yes | 20.3 | 19.3 | 1 | C287D0FB0CFD477391A859D74BA9C794 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95219-3509 |  | 2013-11-02 | 2013-11-02 13:58 | 2013-11-02 14:15 | PAYNE - PA13NR024-E | 85 | -7 | Yes | Yes | 17.7 | 18.7 | -1 | F6AA127629FD43B49440732C73101210 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Fresno | CA | 93710-6326 |  | 2013-10-23 | 2013-10-23 11:56 | 2013-10-23 12:05 | OTHER - N/A | 85 | 3 | Yes | Yes | 26.5 | 21.5 | 5 | 53FFE5439A47405D896C91616418BC71 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93710-6326 |  | 2013-10-23 | 2013-10-23 12:05 | 2013-10-23 14:02 | OTHER - N/A | 85 | 5.9 | Yes | Yes | 19.5 | 20.5 | -1 | D0521121D17F46CEB405DDD9CD12D9EE |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
Fresno | CA | 93710-7111 |  | 2013-10-23 | 2013-10-23 18:53 | 2013-10-23 20:21 | CARRIER - 24ACA436A0030010 | 117 | 4.5 | Yes | Yes | 18 | 20.6 | -2.6 | 775435D14FFB41639B161B54565BDE56 |  | R410A | TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | TXV | 3.846%
Lincoln | CA | 95648-8435 |  | 2013-10-18 | 2013-10-18 11:33 | 2013-10-18 11:52 | RUUD - 14AJA36AA01 | 144 | 9 | Yes | Yes | 26.3 | 20.7 | 5.6 | 17ED01C371734BAD8604974FB7C4D755 |  | R22 | TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | TXV | 6.25%
Fresno | CA | 93704-5933 |  | 2013-10-18 | 2013-10-18 18:17 | 2013-10-18 21:46 | BDP - 588CB060-E | 240 | 23.3 | Yes | Yes | 17.9 | 20.8 | -2.9 | 38E4C0124C3E46679A17D85F87E5E136 | Add refrigerant: 10.3 oz | R22 | Non-TXV |  | 9.708% | 0.90292 | 18.66% | [5 empty] | Non-TXV | 9.708%
Fresno | CA | 93711-1738 |  | 2013-10-18 | 2013-10-18 16:13 | 2013-10-18 16:46 | RHEEM - RKMA-A060JL10X | 184 | 5.7 | Yes | Yes | 26.5 | 20.7 | 5.8 | 94E06BB822ED4079A457F644633ADDE4 |  | R22 | Non-TXV |  | 3.098% | 0.96902 | 5.953% | [5 empty] | Non-TXV | 3.098%
Stockton | CA | 95212-1019 |  | 2013-10-25 | 2013-10-25 16:38 | 2013-10-25 16:45 | UNITARY PRODUCTS GROUP - DRCS0421BE | 107 | 18.5 | Yes | Yes | 20 | 18.7 | 1.3 | 23DD32BD71C14837A662E3D3F4CBAAB8 |  | R22 | Non-TXV |  | 17.29% | 0.8271 | 33.23% | [5 empty] | Non-TXV | 17.29%
Rocklin | CA | 95677-3049 |  | 2013-10-17 | 2013-10-17 13:36 | 2013-10-17 13:55 | OTHER - CPE24-1AB | 93 | 2.7 | Yes | Yes | 17 | 19.1 | -2.1 | A226A721C4ED4843917FD587600C1E5C |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Rocklin | CA | 95677-3050 |  | 2013-10-17 | 2013-10-17 13:57 | 2013-10-17 14:18 | PAYNE - PH10JA034-E | 66 | 12.5 | Yes | Yes | 20 | 20.6 | -0.6 | 2843EBCAF651489A83342EA162EFD461 |  | R22 | Non-TXV |  | 18.94% | 0.81061 | 36.4% | [5 empty] | Non-TXV | 18.94%
Merced | CA | 95348-3207 |  | 2013-10-23 | 2013-10-23 12:46 | 2013-10-23 13:08 | WESTINGHOUSE - 048 | 130 | 4.5 | Yes | Yes | 18 | 17.7 | 0.3 | 02DEBEE9390449048B19BD5D76B284EA |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Lathrop | CA | 95330-8997 |  | 2013-11-02 | 2013-11-02 14:36 | 2013-11-02 15:07 | CARRIER - 38CKC060370 | 131 | 15.6 | Yes | Yes | 23.2 | 20.4 | 2.8 | 52435E8E759E46B892F846EA9B469491 |  | R22 | TXV |  | 11.91% | 0.88092 | 22.89% | [5 empty] | TXV | 11.91%
Magalia | CA | 95954-9502 |  | 2013-11-01 | 2013-11-01 11:40 | 2013-11-01 11:37 | DAY & NIGHT - 542EJX03000AAAD | 106 | 3.3 | Yes | Yes | 23.1 | 20.2 | 2.9 | 32C3FEA5271F43F799B4C883C6D16B9E |  | R22 | Non-TXV |  | 3.113% | 0.96887 | 5.983% | [5 empty] | Non-TXV | 3.113%
Tracy | CA | 95376-4031 |  | 2013-11-14 | 2013-11-14 15:25 | 2013-11-14 16:10 | NORDYNE - FS3BA-048KA | 102 | 7.1 | Yes | Yes | 25.1 | 19.9 | 5.2 | 174083E4B9C74F12A53FFEA2AED128BA |  | R22 | TXV |  | 6.961% | 0.93039 | 13.38% | [5 empty] | TXV | 6.961%
Oroville | CA | 95966-3983 |  | 2013-10-25 | 2013-10-25 09:33 | 2013-10-25 10:00 | CARRIER - 38CKC048300 | 103 | 5.2 | Yes | Yes | 22.1 | 20.4 | 1.7 | 1893E170D3984245AFB8E7288C52797F |  | R22 | TXV |  | 5.049% | 0.94951 | 9.702% | [5 empty] | TXV | 5.049%
Lincoln | CA | 95648-1949 |  | 2013-10-24 | 2013-10-24 17:50 | 2013-10-24 17:50 | RHEEM - RRPL-B048JK08X | 161.2 | 0 | Yes | Yes | 25.7 | 20.1 | 5.6 | 5773A2C96C264B38B99C0A76B93447C9 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3337 |  | 2013-10-31 | 2013-10-31 14:17 | 2013-10-31 14:18 | BRYANT - 582ANW036090NABF | 68 | 3 | Yes | Yes | 22.7 | 19.8 | 2.9 | 52131D84C7BC4CB48B8988CA51EBDF61 |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Pinedale | CA | 93650-1072 |  | 2013-10-31 | 2013-10-31 15:38 | 2013-10-31 15:39 | RUUD - 777UNK | 64 | 2.9 | Yes | Yes | 22.9 | 21.3 | 1.7 | 51487F2CE32D430089D20C76E328BC15 |  | R22 | Non-TXV |  | 4.531% | 0.95469 | 8.708% | [5 empty] | Non-TXV | 4.531%
Escalon | CA | 95320-1809 |  | 2013-10-24 | 2013-10-24 14:20 | 2013-10-24 14:20 | RHEEM - RRMA-A036JK08X | 99 | 0 | Yes | Yes | 21.9 | 19.1 | 2.8 | 91C931B169FD4A3B9AB4424926F7F739 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Foresthill | CA | 95631-0000 |  | 2013-10-25 | 2013-10-25 14:13 | 2013-10-25 14:13 | NORDYNE - FS4BI-048K | 188 | 0 | Yes | Yes | 26.7 | 20.9 | 5.8 | 0A99515C0D464448B0119E44E9F32F5D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-5748 |  | 2013-10-24 | 2013-10-24 02:07 | 2013-10-24 14:30 | PAYNE - 585EJW018050ABAC | 55 | 7 | Yes | Yes | 24 | 20.7 | 3.3 | F6CD2F4BCD554432BF61A2BDA3F94FA0 |  | R22 | Non-TXV |  | 12.73% | 0.87273 | 24.46% | [5 empty] | Non-TXV | 12.73%
Paradise | CA | 95969-3234 |  | 2013-10-24 | 2013-10-24 15:09 | 2013-10-24 15:29 | CARRIER - NA | 50 | 3 | Yes | Yes | 19.5 | 19.3 | 0.2 | 2C93A31BFE94499C8F8F4AD165AEB772 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Paradise | CA | 95969-7119 |  | 2013-10-24 | 2013-10-24 11:24 | 2013-10-24 12:04 | RUUD - UAMA-048JAZ | 165 | 2.8 | Yes | Yes | 22.8 | 21.2 | 1.6 | A08042463CC04A93BDD5AD785265D0BD |  | R22 | Non-TXV |  | 1.697% | 0.98303 | 3.261% | [5 empty] | Non-TXV | 1.697%
Granite Bay | CA | 95746-6934 |  | 2013-10-24 | 2013-10-24 11:00 | 2013-10-24 11:23 | RHEEM - RRNL-B048JK08X | 161 | 7.2 | Yes | Yes | 26.2 | 20.6 | 5.6 | 716661F1B0284DB6B08FF124CD1A53CD |  | R410A | Non-TXV |  | 4.472% | 0.95528 | 8.594% | [5 empty] | Non-TXV | 4.472%
Merced | CA | 95348-2840 |  | 2013-10-23 | 2013-10-23 13:34 | 2013-10-23 13:51 | GIBSON - JS3BA030KA | 66 | 4.2 | Yes | Yes | 18.7 | 17.7 | 1 | 2F91DBA6DCCF4364A36A3C101814DE5B |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Stockton | CA | 95206-2534 |  | 2013-10-31 | 2013-10-31 16:12 | 2013-10-31 16:36 | BRYANT - 5574ANW030060NA | 130 | 7.6 | Yes | Yes | 20.8 | 19.5 | 1.3 | D24C713A20AC484DB2EE17D4F5CBB7F8 |  | R22 | Non-TXV |  | 5.846% | 0.94154 | 11.24% | [5 empty] | Non-TXV | 5.846%
Clovis | CA | 93612-3305 |  | 2013-10-31 | 2013-10-31 13:01 | 2013-10-31 14:21 | UNITARY PRODUCTS GROUP - DAYP-F036N070A | 53 | 6.8 | Yes | Yes | 25 | 20.8 | 4.3 | 7736BB444BBC4CBC99BF6E66E90EAD61 |  | R22 | Non-TXV |  | 12.83% | 0.8717 | 24.66% | [5 empty] | Non-TXV | 12.83%
Colfax | CA | 95713-9455 |  | 2013-10-24 | 2013-10-24 09:34 | 2013-10-24 10:03 | COLEMAN - TCGD36S31S2A | 63 | 1.9 | Yes | Yes | 25 | 20.6 | 4.4 | 3BB06CDD6C584DCF846B0A2CF45183BF |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Rocklin | CA | 95765-4260 |  | 2013-10-25 | 2013-10-25 13:58 | 2013-10-25 13:58 | OTHER - UNK | 65 | 0 | Yes | Yes | 18 | 19.5 | -1.5 | DFAB729D25ED4103849403F3E464B9F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-7947 |  | 2013-11-01 | 2013-11-01 13:27 | 2013-11-01 13:51 | BRYANT - 561CJ048-A | 102 | 26.8 | Yes | Yes | 17.9 | 19.1 | -1.2 | 0E0FBA9756A34573803A9AF13ED8ABE7 |  | R22 | Non-TXV |  | 26.27% | 0.73725 | 50.49% | [5 empty] | Non-TXV | 26.27%
Stockton | CA | 95210-3334 |  | 2013-10-25 | 2013-10-25 15:05 | 2013-10-25 15:33 | AMANA - RCE48A2D | 150 | 7.2 | Yes | Yes | 25 | 19.5 | 5.5 | E2CEDE54F4BF403EAE3B098DB683901A |  | R22 | TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | TXV | 4.8%
Fresno | CA | 93710-4546 |  | 2013-10-25 | 2013-10-25 12:07 | 2013-10-25 12:54 | BDP - 42RC0108K | 87 | 5.5 | Yes | Yes | 23 | 20.9 | 2.1 | 65D6C9B4AD04496198C3AE6DF9370FF1 |  | R22 | Non-TXV |  | 6.322% | 0.93678 | 12.15% | [5 empty] | Non-TXV | 6.322%
Lincoln | CA | 95648-3286 |  | 2013-10-25 | 2013-10-25 12:31 | 2013-10-25 12:48 | YORK - H4RC060S06G | 143 | 11.8 | Yes | Yes | 18 | 20.1 | -2.1 | A6C69E2269794E7CB477515A8E094C6E |  | R22 | Non-TXV |  | 8.252% | 0.91748 | 15.86% | [5 empty] | Non-TXV | 8.252%
Stockton | CA | 95219-7187 |  | 2013-10-24 | 2013-10-24 13:40 | 2013-10-24 14:00 | RHEEM - RAMBB-048JBZ | 162 | 8.8 | Yes | Yes | 23.6 | 19.7 | 3.9 | 5FA9E47AB8564711B840EA2977EC5274 |  | R22 | TXV |  | 5.432% | 0.94568 | 10.44% | [5 empty] | TXV | 5.432%
Tracy | CA | 95377-8824 |  | 2013-11-01 | 2013-11-01 17:36 | 2013-11-01 17:53 | CARRIER - UNK | 104 | 3.2 | Yes | Yes | 21.9 | 21 | 0.9 | 230195DC10BC4E41BD03B3B36C9FB079 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Tracy | CA | 95377-8824 |  | 2013-11-01 | 2013-11-01 17:39 | 2013-11-01 17:58 | CARRIER - 38CKC036350 | 70 | 2.1 | Yes | Yes | 22.7 | 20.4 | 2.3 | AE5629D79CBC4417A851A3605A8BD04A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-6780 |  | 2013-10-25 | 2013-10-25 18:20 | 2013-10-25 18:42 | GOODMAN - CJ24-1AB | 101 | 5.6 | Yes | Yes | 17.8 | 20.4 | -2.6 | 1F4E65457F554B7E82166D522EA01C84 |  | R22 | Non-TXV |  | 5.545% | 0.94455 | 10.66% | [5 empty] | Non-TXV | 5.545%
Merced | CA | 95340-0904 |  | 2013-10-23 | 2013-10-23 13:11 | 2013-10-23 13:27 | CARRIER - 38EN024 | 55 | 2.5 | Yes | Yes | 17.2 | 17.7 | -0.5 | A1AE0A58EEA942CBA854B292F2747C6B |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Tracy | CA | 95377-9214 |  | 2013-11-01 | 2013-11-01 15:08 | 2013-11-01 15:34 | RHEEM - RAFD-048JBS | 101 | 3.1 | Yes | Yes | 21.5 | 20.4 | 1.1 | 4A8E678A1062406FA6EAF6BAAF377252 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Stockton | CA | 95204-4125 |  | 2013-10-24 | 2013-10-24 12:47 | 2013-10-24 12:47 | HEIL - PGAD60E1K6 | 215 | 0 | Yes | Yes | 26.3 | 20.6 | 5.7 | C13CCEC0F4CA46DE826A05B2A3BA3FBD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Riverdale | CA | 93656-9255 |  | 2013-11-02 | 2013-11-02 13:44 | 2013-11-02 14:19 | RHEEM - RRMA-A042JK08X | 114 | 3.6 | Yes | Yes | 25.5 | 20.4 | 5.1 | CC3D6E67B8864459B97586F205FCFE0B |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Stockton | CA | 95219-7184 |  | 2013-10-24 | 2013-10-24 14:17 | 2013-10-24 14:35 | GOODMAN - CLJ48-1A | 130 | 7.6 | Yes | Yes | 21.4 | 19.1 | 2.3 | 922B0CEABD15476F89974EB2676549C7 |  | R22 | TXV |  | 5.846% | 0.94154 | 11.24% | [5 empty] | TXV | 5.846%
Magalia | CA | 95954-9436 |  | 2013-10-24 | 2013-10-24 10:37 | 2013-10-24 10:51 | BRYANT - 604BNX036000AB | 117 | 7.7 | Yes | Yes | 22.1 | 21.5 | 0.6 | 41056DFBBE2F44259C22BEBB83CAF42D |  | R410A | Non-TXV |  | 6.581% | 0.93419 | 12.65% | [5 empty] | Non-TXV | 6.581%
Stockton | CA | 95210-3319 |  | 2013-11-13 | 2013-11-13 13:18 | 2013-11-13 13:33 | CARRIER - 38EN042300 | 115 | 5.5 | Yes | Yes | 19.1 | 19.4 | -0.3 | 547CE48D731B49A7AD550827FE0FC0A6 |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Stockton | CA | 95215-5331 |  | 2013-10-31 | 2013-10-31 11:51 | 2013-10-31 12:01 | AMANA - PGD24C0452E | 74 | 9.2 | Yes | Yes | 24.9 | 20.1 | 4.8 | EBC7303E8D07466CBBCFF3436525AD73 |  | R22 | Non-TXV |  | 12.43% | 0.87568 | 23.89% | [5 empty] | Non-TXV | 12.43%
Madera | CA | 93636-8323 |  | 2013-11-02 | 2013-11-02 13:07 | 2013-11-02 13:08 | GOODMAN - GPG13300451BB | 77 | 3.1 | Yes | Yes | 20.6 | 19.3 | 1.3 | 6D52305CAFD64E2AA37B44B8E619743E |  | R22 | Non-TXV |  | 4.026% | 0.95974 | 7.737% | [5 empty] | Non-TXV | 4.026%
Stockton | CA | 95209-1503 |  | 2013-10-23 | 2013-10-23 12:11 | 2013-10-23 12:29 | BDP - 567C042RCU | 74 | 7.8 | Yes | Yes | 23.6 | 19.7 | 3.9 | 30633FBFB00C44C1802A1F4B054E59C1 |  | R22 | Non-TXV |  | 10.54% | 0.89459 | 20.26% | [5 empty] | Non-TXV | 10.54%
Caruthers | CA | 93609-9532 |  | 2013-11-02 | 2013-11-02 11:12 | 2013-11-02 11:30 | BDP - 597BN036-A | 144 | 7.4 | Yes | Yes | 18.6 | 21.3 | -2.7 | 240B4B9CE3E747E3957AD20DD3AB0DFE |  | R22 | Non-TXV |  | 5.139% | 0.94861 | 9.876% | [5 empty] | Non-TXV | 5.139%
Riverbank | CA | 95367-2868 |  | 2013-10-24 | 2013-10-24 15:09 | 2013-10-24 15:50 | DAY & NIGHT - 565BJ030 | 72 | 2.2 | Yes | Yes | 23.8 | 20.4 | 3.4 | 8FFAE47DA26E442A9849CEF07210B462 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Manteca | CA | 95337-8406 |  | 2013-11-14 | 2013-11-14 13:31 | 2013-11-14 13:54 | RUUD - 13AJA42A01 | 121 | 3.6 | Yes | Yes | 21.6 | 20.1 | 1.5 | 641417AF220F4EEA8197453A1B370477 |  | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.718% | [5 empty] | Non-TXV | 2.975%
Stockton | CA | 95206-3747 |  | 2013-11-06 | 2013-11-06 12:21 | 2013-11-06 12:35 | BRYANT - 561CJ030-D | 69 | 2.9 | Yes | Yes | 19.5 | 17.7 | 1.8 | D5385AF249AB4646AC3E9AE6413A1B34 |  | R22 | Non-TXV |  | 4.203% | 0.95797 | 8.077% | [5 empty] | Non-TXV | 4.203%
Kerman | CA | 93630-1655 |  | 2013-10-24 | 2013-10-24 13:35 | 2013-10-24 14:57 | CARRIER - 48GP-03006031105 | 85 | 3.4 | Yes | Yes | 22.5 | 20.9 | 1.6 | F837F65841D54AF796332F89D19A9E62 |  | R410A | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Lincoln | CA | 95648-2946 |  | 2013-10-24 | 2013-10-24 11:40 | 2013-10-24 12:09 | BDP - PA13N060-J | 168 | 12.6 | Yes | Yes | 26 | 20.4 | 5.6 | 76ED5301B7A14DEA9CA3B08E89E03A4B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95207-3049 |  | 2013-11-01 | 2013-11-01 14:22 | 2013-11-01 14:39 | CARRIER - 38TH03630 | 90 | 5.8 | Yes | Yes | 23.8 | 20.4 | 3.5 | 380A555BB5C3475A9414755802879FC6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.444% | 0.93556 | 12.38% | [5 empty] | Non-TXV | 6.444%
Manteca | CA | 95336-3436 |  | 2013-10-25 | 2013-10-25 12:36 | 2013-10-25 13:09 | LENNOX - HS299-030-1P | 84 | 4 | Yes | Yes | 22.7 | 19.7 | 3 | 41A08BF78DD94B3794C0955FEB58BCDE |  | R22 | TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | TXV | 4.762%
Rocklin | CA | 95765-5816 |  | 2013-10-24 | 2013-10-24 13:55 | 2013-10-24 14:29 | YORK - H1RA048S06D | 117 | 3.5 | Yes | Yes | 19 | 20.1 | -1.1 | 8E3602B21AF64A50A86278B0C34C1673 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Stockton | CA | 95204-4722 |  | 2013-11-01 | 2013-11-01 13:06 | 2013-11-01 13:23 | BDP - 595JJ030075 | 68 | 4.4 | Yes | Yes | 23.9 | 19.7 | 4.2 | 0199C6C036F9404AA5D5277BC1DFE0D4 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Stockton | CA | 95207-4814 |  | 2013-10-24 | 2013-10-24 12:25 | 2013-10-24 12:45 | NORDYNE - FS3BA-042KA | 87 | -5.1 | Yes | Yes | 19.4 | 18.7 | 0.7 | 167C6EE8539C4732A9B07E4590836B69 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Stockton | CA | 95219-7139 |  | 2013-11-02 | 2013-11-02 16:32 | 2013-11-02 17:11 | - | 85 | -7 | Yes | Yes | 25 | 19.9 | 5.1 | 9A86AAAA1E0447A5B110F662CB2570D2 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Stockton | CA | 95203-1023 |  | 2013-11-01 | 2013-11-01 12:12 | 2013-11-01 12:31 | UNITARY PRODUCTS GROUP - ACO18M1021A | 49 | -4.6 | Yes | Yes | 20.6 | 19.9 | 0.7 | BD3E5EA9264C4B4A894EA90130D8B346 |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Selma | CA | 93662-9756 |  | 2013-11-01 | 2013-11-01 14:34 | 2013-11-01 15:30 | GOODMAN - GPH1336M41AC | 135 | 5.4 | Yes | Yes | 26.6 | 20.6 | 6 | 3225616EB5F545C8B3F2A9656CB9412C |  | R410A | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Rocklin | CA | 95677-2731 |  | 2013-10-24 | 2013-10-24 16:04 | 2013-10-24 16:20 | AMANA - RCB36C2C | 80 | 3.1 | Yes | Yes | 22 | 21 | 1 | 7B65EEC408F744209546FDC6A30EEB93 |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Tracy | CA | 95376-8922 |  | 2013-10-25 | 2013-10-25 10:34 | 2013-10-25 10:54 | RUUD - UAKA-060JAS | 112 | -7.9 | Yes | Yes | 22.8 | 18.7 | 4.1 | C1431F16E39E422FABF6C0466666FBBF |  | R22 | Non-TXV |  | -7.054% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.054%
Madera | CA | 93638-2141 |  | 2013-11-02 | 2013-11-02 20:53 | 2013-11-02 20:56 | CARRIER - 489-036060301 | 82 | 4.3 | Yes | Yes | 21.5 | 19.5 | 2 | 9F89FB914E5B424B8C74FA6FEA8D7AE1 |  | R22 | Non-TXV |  | 5.244% | 0.94756 | 10.08% | [5 empty] | Non-TXV | 5.244%
Stockton | CA | 95209-2317 |  | 2013-10-23 | 2013-10-23 12:44 | 2013-10-23 13:05 | PAYNE - PA10JA060-C | 118 | 4.7 | Yes | Yes | 26.1 | 20.1 | 6 | 1BC96D5E87ED4648A72B28B0F9ECA932 |  | R22 | Non-TXV |  | 3.983% | 0.96017 | 7.655% | [5 empty] | Non-TXV | 3.983%
Selma | CA | 93662-2263 |  | 2013-10-31 | 2013-10-31 18:06 | 2013-10-31 18:32 | CARRIER - 38TK048310 | 166 | 5.5 | Yes | Yes | 26.5 | 20.8 | 5.7 | 09BE9F70D007443393AD3CFB1B191765 |  | R22 | Non-TXV |  | 3.313% | 0.96687 | 6.367% | [5 empty] | Non-TXV | 3.313%
Penryn | CA | 95663-9403 |  | 2013-11-01 | 2013-11-01 13:24 | 2013-11-01 13:24 | YORK - UN K | 90 | 0 | Yes | Yes | 34.5 | 20.4 | 14.1 | 724045CF98AF44BD949C4EDD64F03C57 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Penryn | CA | 95663-9403 |  | 2013-11-01 | 2013-11-01 13:26 | 2013-11-01 13:45 | CARRIER - 24ABB336A310 | 83 | 3 | Yes | Yes | 19 | 20.4 | -1.4 | AE066241F0824361AF5C41CC0D191F19 |  | R410A | TXV |  | 3.614% | 0.96386 | 6.946% | [5 empty] | TXV | 3.614%
Fresno | CA | 93727-9325 |  | 2013-10-24 | 2013-10-24 14:59 | 2013-10-24 15:28 | ICP - PGF042K080B | 87 | 2.9 | Yes | Yes | 21.5 | 20.4 | 1.1 | B96EB55F7C0142FCA13CE1AC341FB1EB |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Paradise | CA | 95969-6201 |  | 2013-10-24 | 2013-10-24 09:44 | 2013-10-24 10:22 | AMANA - PGB30C0702D | 64 | 9.7 | Yes | Yes | 20.7 | 22.4 | -1.7 | F7D16B371A6A47338E97F5427255DF53 |  | R22 | Non-TXV |  | 15.16% | 0.84844 | 29.13% | [5 empty] | Non-TXV | 15.16%
Stockton | CA | 95207-2356 |  | 2013-11-01 | 2013-11-01 11:35 | 2013-11-01 11:35 | YORK - D3NZ024N03606NXB | 58 | 0 | Yes | Yes | 25.2 | 19.8 | 5.4 | 603530000BF34CD09E86E80F58BD776C |  | R410A | TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2263 |  | 2013-10-31 | 2013-10-31 16:43 | 2013-10-31 17:03 | WHIRLPOOL - NCABA47AB02 | 74 | 4.3 | Yes | Yes | 17.5 | 20.4 | -2.9 | 4042ACF9EA1A484F9364D83EDB6F45C2 |  | R22 | Non-TXV |  | 5.811% | 0.94189 | 11.17% | [5 empty] | Non-TXV | 5.811%
Foresthill | CA | 95631-9742 |  | 2013-10-25 | 2013-10-25 16:46 | 2013-10-25 16:46 | COLEMAN - PGB042075-1 | 68 | 0 | Yes | Yes | 25.8 | 20.7 | 5.1 | 2CE06CA6558B4975AAC7735CB2BD8458 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-9346 |  | 2013-11-06 | 2013-11-06 14:34 | 2013-11-06 14:35 | YORK - D2YS024P04506A | 74 | 3.5 | Yes | Yes | 23.9 | 19.3 | 4.6 | BB32DF24249349439B4F7C7ED33C9BDE |  | R22 | Non-TXV |  | 4.73% | 0.9527 | 9.09% | [5 empty] | Non-TXV | 4.73%
Selma | CA | 93662-2263 |  | 2013-10-31 | 2013-10-31 17:07 | 2013-10-31 17:33 | GOODMAN - CK49-1B | 90 | 12.1 | Yes | Yes | 27 | 21.4 | 5.7 | A593544596024DC499609ECC49432939 |  | R22 | Non-TXV |  | 13.44% | 0.86556 | 25.84% | [5 empty] | Non-TXV | 13.44%
Caruthers | CA | 93609-9532 |  | 2013-11-02 | 2013-11-02 11:57 | 2013-11-02 12:34 | UNITARY PRODUCTS GROUP - DBYZ-F030N070A | 117 | 6.9 | Yes | Yes | 17.3 | 19.9 | -2.6 | 4177467A8B3F41E19759253AD2E1C8E7 |  | R410A | TXV |  | 5.897% | 0.94103 | 11.33% | [5 empty] | TXV | 5.897%
Chico | CA | 95926-3459 |  | 2013-11-01 | 2013-11-01 14:57 | 2013-11-01 15:36 | BRYANT - 561CJ036-D | 82 | 3.7 | Yes | Yes | 18.5 | 21 | -2.5 | A9313DF46E014037B211F6DCF0516145 |  | R22 | TXV |  | 4.512% | 0.95488 | 8.671% | [5 empty] | TXV | 4.512%
Chowchilla | CA | 93610-9426 |  | 2013-11-07 | 2013-11-07 13:01 | 2013-11-07 13:02 | CARRIER - 38BR042300 | 132 | 3.9 | Yes | Yes | 21.7 | 19.7 | 2 | C21B7925B26D4DC6BBA3BF31F794CC33 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Paradise | CA | 95969-3242 |  | 2013-11-01 | 2013-11-01 12:15 | 2013-11-01 12:30 | HEIL - NA | 105 | 4.9 | Yes | Yes | 22.4 | 19.7 | 2.8 | 901E008D53BE496DAD0863B4D259EE41 |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Fresno | CA | 93722-2535 |  | 2013-10-31 | 2013-10-31 12:00 | 2013-10-31 12:35 | RHEEM - RRPL-B036JK08X | 93 | 3.7 | Yes | Yes | 26.2 | 21.7 | 4.5 | B7E79B321D63456390708099D27C1ABC |  | R410A | TXV |  | 3.978% | 0.96022 | 7.646% | [5 empty] | TXV | 3.978%
Fresno | CA | 93727-9332 |  | 2013-10-24 | 2013-10-24 15:30 | 2013-10-24 17:13 | ICP - PGF042K080B | 87 | 7.5 | Yes | Yes | 18 | 20.4 | -2.4 | 133D5DF2A23549789899A9BB77DE9AD4 |  | R22 | Non-TXV |  | 8.621% | 0.91379 | 16.57% | [5 empty] | Non-TXV | 8.621%
Auburn | CA | 95603-2804 |  | 2013-11-01 | 2013-11-01 12:19 | 2013-11-01 12:38 | OTHER - UNK | 129 | 3.9 | Yes | Yes | 25 | 20.7 | 4.3 | 4887C078E6FD489CAE5A136F04569DCA |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Grass Valley | CA | 95949-8304 |  | 2013-10-23 | 2013-10-23 18:11 | 2013-10-23 18:11 | YORK - UNK | 73 | 0 | Yes | Yes | 19.6 | 21.3 | -1.7 | 6B968B8F492A4D448D03F663168C3A77 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-4200 |  | 2013-10-24 | 2013-10-24 12:34 | 2013-10-24 13:03 | OTHER - R2H324GKR4 | 70 | 7.4 | Yes | Yes | 20.5 | 20.4 | 0.1 | A1A27F1555524802994FFF85F1EEFAB3 |  | R22 | TXV |  | 10.57% | 0.89429 | 20.32% | [5 empty] | TXV | 10.57%
Stockton | CA | 95206-3747 |  | 2013-11-01 | 2013-11-01 13:57 | 2013-11-01 14:15 | BRYANT - 113RNA060-D | 162 | -9.5 | Yes | Yes | 20 | 18.8 | 1.2 | FCEDA8A2651F46A9B22868D63FF1AF30 |  | R22 | Non-TXV |  | -5.864% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.864%
Fresno | CA | 93703-1423 |  | 2013-10-25 | 2013-10-25 12:56 | 2013-10-25 14:56 | BDP - 588ANW048080AAAC | 101 | 3.5 | Yes | Yes | 25.2 | 20.4 | 4.8 | CDE61B21D8C642618346FA2BC0FDF211 |  | R22 | Non-TXV |  | 3.465% | 0.96535 | 6.66% | [5 empty] | Non-TXV | 3.465%
Tracy | CA | 95376-5143 |  | 2013-11-01 | 2013-11-01 15:57 | 2013-11-01 16:12 | BRYANT - 561CJ036-F | 64 | 1.9 | Yes | Yes | 22.8 | 19.9 | 2.9 | A14F8A86334147669CCDC9BBBCB8EF2B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93722-3330 |  | 2013-10-31 | 2013-10-31 13:34 | 2013-10-31 13:36 | CARRIER - 777UNK | 80 | 2.8 | Yes | Yes | 21.3 | 20.3 | 1 | 016ADF9B39394542A65BDD7EEFC18223 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Yuba City | CA | 95991-9451 |  | 2013-10-31 | 2013-10-31 13:45 | 2013-10-31 14:02 | LENNOX - 13ACD-036-230-01 | 111 | 4 | Yes | Yes | 19 | 18.7 | 0.3 | C5CF8665C38B4707B06553CAA0463EC4 |  | R22 | TXV |  | 3.604% | 0.96396 | 6.925% | [5 empty] | TXV | 3.604%
Fresno | CA | 93727-0000 |  | 2013-10-26 | 2013-10-26 13:23 | 2013-10-26 13:25 | LENNOX - 13ACC-024-230-02 | 81 | 7.8 | Yes | Yes | 18 | 20.8 | -2.8 | 0FBDBEB0874A4A83A1D5A6D7439C80F5 |  | R22 | Non-TXV |  | 9.63% | 0.9037 | 18.51% | [5 empty] | Non-TXV | 9.63%
Fresno | CA | 93727-0000 |  | 2013-10-26 | 2013-10-26 13:27 | 2013-10-26 13:52 | LENNOX - 13ACD-048-230-01 | 204 | 22.7 | Yes | Yes | 19.3 | 21.2 | -1.9 | 073B02A4D1F34FEF82BAEA4A254A89A5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.13% | 0.88873 | 21.38% | [5 empty] | Non-TXV | 11.13%
Tracy | CA | 95377-8242 |  | 2013-11-02 | 2013-11-02 12:14 | 2013-11-02 12:36 | BRYANT - 113RNA042-A | 113 | -24 | Yes | Yes | 25.7 | 20.3 | 5.5 | C759655A564D4EA6A5DF132E1EB24131 |  | R22 | TXV |  | -21.24% | 1.2124 | 5.948% |  |  |  |  | TXV |  |  | -21.24%
Chowchilla | CA | 93610-9452 |  | 2013-11-07 | 2013-11-07 12:16 | 2013-11-07 12:18 | YORK - D1NA036N03606C | 67 | 3.8 | Yes | Yes | 22 | 19.7 | 2.3 | 7D09999297944CD09C2E40DC5AD0502A |  | R22 | Non-TXV |  | 5.672% | 0.94328 | 10.9% | [5 empty] | Non-TXV | 5.672%
Stockton | CA | 95205-3455 |  | 2013-11-01 | 2013-11-01 14:28 | 2013-11-01 14:44 | RHEEM - RRNA-B036K06X | 83 | 9.7 | Yes | Yes | 20.6 | 19.9 | 0.7 | 6FC7A895DC3547B0BB85EB0E16F451B6 |  | R22 | TXV |  | 11.69% | 0.88313 | 22.46% | [5 empty] | TXV | 11.69%
Rocklin | CA | 95677-2320 |  | 2013-10-25 | 2013-10-25 14:47 | 2013-10-25 15:03 | TRANE - YCY030G1M0AC | 120 | 3.6 | Yes | Yes | 18 | 20.7 | -2.7 | 96EDD71DEDE24F7ABF1F9000E2B570A9 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Caruthers | CA | 93609-9463 |  | 2013-11-02 | 2013-11-02 12:37 | 2013-11-02 13:10 | UNITARY PRODUCTS GROUP - DAYH-F042N080C | 94 | 5 | Yes | Yes | 26 | 20.7 | 5.3 | 72A202DB74A84414A73FB7791C97AA1E |  | R22 | Non-TXV |  | 5.319% | 0.94681 | 10.22% | [5 empty] | Non-TXV | 5.319%
Fresno | CA | 93703-3144 |  | 2013-10-23 | 2013-10-23 17:45 | 2013-10-23 17:46 | OTHER - SA30G080-6G | 44 | 4.3 | Yes | Yes | 26 | 20.4 | 5.6 | 166B6B5AA4C948DCB0224CDDAC376E8F |  | R22 | Non-TXV |  | 9.773% | 0.90227 | 18.78% | [5 empty] | Non-TXV | 9.773%
Selma | CA | 93662-2267 |  | 2013-10-31 | 2013-10-31 16:04 | 2013-10-31 16:39 | TEMPSTAR - CA3048VKA1 | 138 | 4.5 | Yes | Yes | 27 | 21.4 | 5.7 | 3F477165BB614DB7937022AA9971DCF5 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Stockton | CA | 95215-5327 |  | 2013-10-31 | 2013-10-31 14:07 | 2013-10-31 14:07 | GOODMAN - CKL36-1H | 112 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | 69545DC29BF14E24918FACEE50A00965 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2355 |  | 2013-11-01 | 2013-11-01 11:36 | 2013-11-01 11:57 | RHEEM - RRMA-A036JK06X | 99 | 7.1 | Yes | Yes | 23.5 | 21 | 2.6 | E0F6E6F44C4B423C8AAE4A1E2CA2E6DA |  | R22 | Non-TXV |  | 7.172% | 0.92828 | 13.78% | [5 empty] | Non-TXV | 7.172%
Foresthill | CA | 95631-0000 |  | 2013-10-25 | 2013-10-25 14:52 | 2013-10-25 14:52 | BRYANT - 561CJ030-D | 68 | 0 | Yes | Yes | 24.5 | 23.8 | 0.8 | 7E6482AB08904722B6AD88F344096E24 |  | R22 | TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2086 |  | 2013-10-31 | 2013-10-31 12:28 | 2013-10-31 12:28 | TRANE - 2TTB2048A1000AA | 120 | 0 | Yes | Yes | 26 | 20.4 | 5.6 | BE649917E0A54D479DBB543CC3F61058 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-3259 |  | 2013-11-01 | 2013-11-01 12:40 | 2013-11-01 12:40 | LENNOX - 13ACD-060-230-01 | 214 | 0 | Yes | Yes | 17.8 | 20.1 | -2.3 | 4AA1A1DAC08D43449FE358D4861569DF |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4131 |  | 2013-10-23 | 2013-10-23 15:03 | 2013-10-23 15:58 | YORK - D3YS0360806C | 78 | 6 | Yes | Yes | 26 | 20.2 | 5.9 | DB57D9DD90E445449214152C9E4C8FCA |  | R22 | Non-TXV |  | 7.692% | 0.92308 | 14.78% | [5 empty] | Non-TXV | 7.692%
Lincoln | CA | 95648-2701 |  | 2013-11-01 | 2013-11-01 15:40 | 2013-11-01 15:40 | OTHER - CA5036VKB1 | 86 | 0 | Yes | Yes | 19.6 | 19.1 | 0.5 | EF461806AF53438EBDDA7E3C0ABA0E45 | Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2357 |  | 2013-11-01 | 2013-11-01 15:05 | 2013-11-01 15:05 | CARRIER - 38ETG030300 | 136 | 0 | Yes | Yes | 21.5 | 21.4 | 0.1 | 5D8B47875CF74696BAAB4EEA9140D0CB |  | R410A | TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-0000 |  | 2013-10-31 | 2013-10-31 13:49 | 2013-10-31 13:49 | CARRIER - 38ETG030300 | 136 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | 03B8BD01A7074B989EFE450AAC161E34 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lincoln | CA | 95648-2491 |  | 2013-11-01 | 2013-11-01 14:26 | 2013-11-01 14:26 | YORK - H2RAC030S06D | 62 | 0 | Yes | Yes | 21.2 | 21.7 | -0.5 | FFA3FB4FBF5D4C2F9BE42F0C134EDEE1 |  | R22 | TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2127 |  | 2013-11-08 | 2013-11-08 12:11 | 2013-11-08 12:12 | BDP - 585EJ030050 | 58 | 3.4 | Yes | Yes | 23.1 | 20.2 | 2.9 | A84D97830130424B94C8990ED56BFE59 |  | R22 | Non-TXV |  | 5.862% | 0.94138 | 11.27% | [5 empty] | Non-TXV | 5.862%
Selma | CA | 93662-2263 |  | 2013-10-31 | 2013-10-31 17:36 | 2013-10-31 18:03 | ICP - PGF030K060A | 52 | 5.8 | Yes | Yes | 26 | 20.2 | 5.9 | BE3CF3AE413748BEB9783204B7A4B0CB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.15% | 0.88846 | 21.44% | [5 empty] | Non-TXV | 11.15%
Tracy | CA | 95304-5835 |  | 2013-11-01 | 2013-11-01 14:10 | 2013-11-01 14:40 | GOODMAN - CK42-1C | 86 | 2.5 | Yes | Yes | 19.4 | 18.5 | 0.9 | 7CB1698FB4E145F1A13ED3B824D0A910 |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Chowchilla | CA | 93610-2124 |  | 2013-11-06 | 2013-11-06 13:52 | 2013-11-06 13:53 | RHEEM - RRNA-B030JK06X | 65 | 3.1 | Yes | Yes | 22.7 | 19.3 | 3.4 | 8C6A027271AA4C63811FF174CBFBE59E |  | R22 | Non-TXV |  | 4.769% | 0.95231 | 9.165% | [5 empty] | Non-TXV | 4.769%
Tracy | CA | 95376-8737 |  | 2013-11-02 | 2013-11-02 12:59 | 2013-11-02 13:19 | BDP - 587BN036-A | 144 | 11.2 | Yes | Yes | 21.1 | 19.1 | 2 | 0BC4585316A54A169B641DCE3E1CDD08 |  | R22 | TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | TXV | 7.778%
Manteca | CA | 95337-5617 |  | 2013-11-12 | 2013-11-12 14:02 | 2013-11-12 14:23 | BRYANT - 113RNA024-C | 71 | 2.1 | Yes | Yes | 24.8 | 19.9 | 4.9 | 8597CE4043BE4E3599AB3299AA5FE52A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Stockton | CA | 95209-2015 |  | 2013-11-01 | 2013-11-01 12:57 | 2013-11-01 13:15 | PAYNE - 569A042RCUE | 114 | 22.9 | Yes | Yes | 21.6 | 19.4 | 2.2 | DA41335525784687A9934BF0845DA933 |  | R22 | Non-TXV |  | 20.09% | 0.79912 | 38.6% | [5 empty] | Non-TXV | 20.09%
Manteca | CA | 95337-5617 |  | 2013-10-31 | 2013-10-31 17:24 | 2013-10-31 17:25 | BRYANT - 113RNA024-C | 71 | 3.9 | Yes | Yes | 21.5 | 19.3 | 2.2 | B7F75E8E7D584EDC985C3C47A32C5544 |  | R22 | TXV |  | 5.493% | 0.94507 | 10.56% | [5 empty] | TXV | 5.493%
Merced | CA | 95348-2240 |  | 2013-10-23 | 2013-10-23 13:53 | 2013-10-23 14:23 | CARRIER - 38EN024 | 56 | -4.6 | Yes | Yes | 17.1 | 17.7 | -0.6 | 05E4BFF433B545958E583B219F9B0147 |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Stockton | CA | 95219-3148 |  | 2013-11-02 | 2013-11-02 14:33 | 2013-11-02 14:52 | RHEEM - AT-30B1E | 58 | 7.4 | Yes | Yes | 19.3 | 19.6 | -0.3 | 630D8FE7449842169772371F1C4416B7 |  | R22 | Non-TXV |  | 12.76% | 0.87241 | 24.52% | [5 empty] | Non-TXV | 12.76%
Madera | CA | 93637-4907 |  | 2013-11-01 | 2013-11-01 14:35 | 2013-11-01 14:36 | CARRIER - 777UNK | 90 | 3.6 | Yes | Yes | 20.8 | 18.8 | 2 | F99191338DC64D0D875CA32FFFBE1AF9 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Merced | CA | 95341-7029 |  | 2013-11-01 | 2013-11-01 23:22 | 2013-11-01 23:23 | BRYANT - 582ANW042060NAAAG | 100 | 3.1 | Yes | Yes | 23.8 | 19.3 | 4.5 | 1C021C49833743099BBD196E25038061 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Lincoln | CA | 95648-8753 |  | 2013-10-24 | 2013-10-24 16:39 | 2013-10-24 17:16 | UNK - UNK | 85 | 5.4 | Yes | Yes | 21.8 | 20.1 | 1.7 | CFC62DE959724C2CAFF6D5FCED82A684 |  |  |  |  | 6.353% | 0.93647 | 12.21% | [5 empty] | 0 | 6.353%
Lincoln | CA | 95648-8753 |  | 2013-10-24 | 2013-10-24 17:18 | 2013-10-24 17:18 | YORK - E1RC018S06D | 93 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 6A26D959D58A4BAE91CCCBE96F15E7B1 |  | R22 | TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-3046 |  | 2013-11-01 | 2013-11-01 13:31 | 2013-11-01 14:00 | YORK - P3YS036N0806B | 78 | 4.6 | Yes | Yes | 25 | 21.8 | 3.2 | 4379DF1D99C84314899B53728419697A |  | R22 | Non-TXV |  | 5.897% | 0.94103 | 11.33% | [5 empty] | Non-TXV | 5.897%
Yuba City | CA | 95993-1177 |  | 2013-10-23 | 2013-10-23 14:06 | 2013-10-23 14:06 | HEIL - 48DC-000088ZR | 207 | 0 | Yes | Yes | 26 | 21 | 5 | 8AD15B7FC80D49D7AB612AB83A7A25DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-1113 |  | 2013-11-02 | 2013-11-02 12:44 | 2013-11-02 12:44 | DAY & NIGHT - 569BJ036 | 93 | 0 | Yes | Yes | 24.3 | 19.8 | 4.5 | B495DBCF6B0E41EC9B85CD53DEB0AC07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Roseville | CA | 95661-5908 |  | 2013-10-24 | 2013-10-24 18:12 | 2013-10-24 18:29 | GOODMAN - PGB 036075-1B | 50 | 2.5 | Yes | Yes | 25 | 20.1 | 4.9 | AB0CEB282D0945D6AAC15DB0B6331EB1 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Lincoln | CA | 95648-3246 |  | 2013-10-24 | 2013-10-24 14:42 | 2013-10-24 14:42 | CARRIER - 24ABA336A300 | 84 | 0 | Yes | Yes | 21.8 | 19.9 | 1.9 | BD4455C45D7F4788978D5BA93C73826B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-1804 |  | 2013-11-06 | 2013-11-06 13:28 | 2013-11-06 13:29 | OTHER - TCGD30621S2HA | 55 | 3.1 | Yes | Yes | 20.9 | 19.9 | 1 | 34BAA823661B4837B7A7732076DB41C6 |  | R22 | Non-TXV |  | 5.636% | 0.94364 | 10.83% | [5 empty] | Non-TXV | 5.636%
Stockton | CA | 95205-3224 |  | 2013-11-07 | 2013-11-07 11:17 | 2013-11-07 11:17 | ALLEGIANCE - 2A7A8036B1000AA | 224 | 0 | Yes | Yes | 19.6 | 20 | -0.4 | A7A51CE3C18F469A8FEC77CEE763BD7F |  | R22 | TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2116 |  | 2013-11-06 | 2013-11-06 12:46 | 2013-11-06 12:49 | YORK - D1NH060N11006C | 140 | 4.2 | Yes | Yes | 17.2 | 20.2 | -3 | 4386A2E4778245829CAE8509D8BC65FF |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Lathrop | CA | 95330-8734 |  | 2013-11-02 | 2013-11-02 15:25 | 2013-11-02 16:09 | ICP - PGAA36C1K2 | 81 | 6.5 | Yes | Yes | 16.9 | 19.5 | -2.6 | 906C53B6C855446284A1AC7527224E33 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.025% | 0.91975 | 15.42% | [5 empty] | Non-TXV | 8.025%
Manteca | CA | 95336-4416 |  | 2013-10-31 | 2013-10-31 14:06 | 2013-10-31 14:52 | RHEEM - RAKB-036JAZ | 79 | 2.6 | Yes | Yes | 25.3 | 20.6 | 4.7 | EE6CA17DE2B345A39D6A1C97C1125201 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Chowchilla | CA | 93610-2116 |  | 2013-11-07 | 2013-11-07 11:52 | 2013-11-07 11:54 | YORK - D2NY048N09006A | 152 | 4.5 | Yes | Yes | 20 | 19.5 | 0.5 | 5C16DC171E824F2EA630B95FC531AE0D |  | R410A | Non-TXV |  | 2.961% | 0.97039 | 5.689% | [5 empty] | Non-TXV | 2.961%
Lincoln | CA | 95648-3216 |  | 2013-11-01 | 2013-11-01 13:20 | 2013-11-01 13:37 | LENNOX - 13ACC-042-230-02 | 123 | 19.2 | Yes | Yes | 17.5 | 19.9 | -2.4 | A940DBAC8DDB4B2F9516D5BB83A4849A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.61% | 0.8439 | 30% | [5 empty] | Non-TXV | 15.61%
Tracy | CA | 95304-0000 |  | 2013-11-01 | 2013-11-01 12:16 | 2013-11-01 12:57 | BRYANT - 583BNW036060AAF | 105 | 16.1 | Yes | Yes | 18 | 19.9 | -1.9 | DDA3BC0CAC434750BBA73FDF0B5A6AF0 |  | R410A | Non-TXV |  | 15.33% | 0.84667 | 29.47% | [5 empty] | Non-TXV | 15.33%
Tracy | CA | 95376-3406 |  | 2013-11-14 | 2013-11-14 12:22 | 2013-11-14 12:36 | CARRIER - 591ANX036000AAAA | 90 | 7.1 | Yes | Yes | 25.4 | 19.9 | 5.5 | 9BD18FC0A3A046599E817A435FA07181 |  | R22 | TXV |  | 7.889% | 0.92111 | 15.16% | [5 empty] | TXV | 7.889%
Manteca | CA | 95336-5043 |  | 2013-11-12 | 2013-11-12 11:25 | 2013-11-12 11:56 | NORDYNE - S30A-030KA | 68 | 19.4 | Yes | Yes | 18.9 | 20.7 | -1.8 | 40BBD40A44C84FF0A7C9557EFC1CF0A9 |  | R22 | Non-TXV |  | 28.53% | 0.71471 | 54.83% | [5 empty] | Non-TXV | 28.53%
Manteca | CA | 95336-5924 |  | 2013-11-07 | 2013-11-07 14:25 | 2013-11-07 14:25 | GOODMAN - GAX130241BA | 76 | 0 | Yes | Yes | 23.5 | 20.7 | 2.9 | 1F791F48A5D041779561DC8687941F23 |  | R410A | TXV |  | 0% | 1 | 0%
Oakdale | CA | 95361-3569 |  | 2013-11-13 | 2013-11-13 12:51 | 2013-11-13 13:19 | ICP - ACS030A2C1 | 85 | 2.5 | Yes | Yes | 18.1 | 19.9 | -1.8 | 3555D08C23484F908A0D5F370592B9CB |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95207-7518 |  | 2013-11-07 | 2013-11-07 14:52 | 2013-11-07 15:08 | GOODMAN - GE36-1GB | 79 | 4.7 | Yes | Yes | 22.8 | 18.6 | 4.3 | BF9F5367F22D4926A5CB1175B915843C |  | R22 | Non-TXV |  | 5.949% | 0.94051 | 11.43% | [5 empty] | Non-TXV | 5.949%
Paradise | CA | 95969-5173 |  | 2013-11-01 | 2013-11-01 12:33 | 2013-11-01 13:00 | PAYNE - PY1PNB024040AAAA | 53 | -5 | Yes | Yes | 24.6 | 20.3 | 4.3 | 1CFFFC7C61DB43F19A53E8593298892D |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Manteca | CA | 95336-5910 |  | 2013-11-07 | 2013-11-07 14:00 | 2013-11-07 14:23 | GOODMAN - GPG10360701A | 75 | 5 | Yes | Yes | 21.2 | 18.9 | 2.3 | 00DE6527B0D6476DBF65B81390611A7A |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Manteca | CA | 95336-3908 |  | 2013-11-07 | 2013-11-07 15:00 | 2013-11-07 15:27 | OTHER - TZGE--330JL0060AX | 85 | 5.3 | Yes | Yes | 17 | 19.9 | -2.9 | 6533BBF8204C40908C0B2600DAB18830 |  | R410A | TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | TXV | 6.235%
Stockton | CA | 95206-6080 |  | 2013-11-12 | 2013-11-12 13:05 | 2013-11-12 14:09 | - 561CJ042-E | 85 | 6.3 | Yes | Yes | 21.3 | 20.4 | 0.9 | 3CCB9A41D1BB4920AAE717FD621CCB28 |  | R22 | Non-TXV |  | 7.412% | 0.92588 | 14.24% | [5 empty] | Non-TXV | 7.412%
Oakdale | CA | 95361-3233 |  | 2013-11-13 | 2013-11-13 13:37 | 2013-11-13 14:34 | BRYANT - 582ANW042060NAG | 100 | 3 | Yes | Yes | 19.1 | 20.6 | -1.5 | 9F242A36692045E2A3E002F458E61167 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Tracy | CA | 95304-5800 |  | 2013-11-12 | 2013-11-12 14:12 | 2013-11-12 14:31 | YORK - E060S06A | 122 | 17.2 | Yes | Yes | 25.6 | 19.8 | 5.8 | 69D4D46787F1466FA96A5CE4F1C8438A |  | R22 | Non-TXV |  | 14.1% | 0.85902 | 27.09% | [5 empty] | Non-TXV | 14.1%
Rocklin | CA | 95677-3047 |  | 2013-11-01 | 2013-11-01 16:07 | 2013-11-01 16:07 | TRANE - 2TWB3024A1000CA | 91 | 0 | Yes | Yes | 20 | 19.3 | 0.7 | A81B4F3F852E4B11A29B6B516E517281 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-7435 |  | 2013-11-06 | 2013-11-06 13:14 | 2013-11-06 13:30 | LENNOX - HS1-6-261U-7P | 86 | 11.3 | Yes | Yes | 20.6 | 19.8 | 0.8 | 0031CCCA215547798917EB886649DA31 |  | R22 | Non-TXV |  | 13.14% | 0.8686 | 25.25% | [5 empty] | Non-TXV | 13.14%
Stockton | CA | 95209-3781 |  | 2013-11-08 | 2013-11-08 11:44 | 2013-11-08 12:02 | CARRIER - 38ETG042---301 | 133 | 15.2 | Yes | Yes | 22.5 | 19.6 | 3 | A03780946B824063B87A38B3620987E8 |  | R410A | TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | TXV | 11.43%
Tracy | CA | 95377-7938 |  | 2013-11-13 | 2013-11-13 11:32 | 2013-11-13 11:50 | GOODMAN - CKT42-1AB | 132 | 12.6 | Yes | Yes | 18.6 | 19.1 | -0.4 | 44F55D3BA5EA4C06A2E184ADD4E9879C |  | R22 | TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | TXV | 9.545%
Yuba City | CA | 95991-7509 |  | 2013-10-31 | 2013-10-31 13:19 | 2013-10-31 13:41 | LENNOX - 10AC36-1P | 92 | 3.4 | Yes | Yes | 17 | 19.5 | -2.5 | ABDC479F73FC4F79A519BF3C87F9D942 |  | R22 | TXV |  | 3.696% | 0.96304 | 7.102% | [5 empty] | TXV | 3.696%
Stockton | CA | 95204-1415 |  | 2013-11-08 | 2013-11-08 12:24 | 2013-11-08 12:41 | ICP - HAC036AKA1 | 80 | -5.6 | Yes | Yes | 21.3 | 19.1 | 2.2 | 4489BB943E244992892A84CEB811F410 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Stockton | CA | 95207-2111 |  | 2013-11-06 | 2013-11-06 11:18 | 2013-11-06 11:34 | GOODMAN - VSX130361AA | 89 | 3.9 | Yes | Yes | 21.4 | 19.8 | 1.6 | FC126193C6824A08AB118E2E934611AB |  | R410A | TXV |  | 4.382% | 0.95618 | 8.421% | [5 empty] | TXV | 4.382%
Stockton | CA | 95209-5030 |  | 2013-11-08 | 2013-11-08 13:04 | 2013-11-08 13:21 | PAYNE - 591ANX036000AAAA | 84 | 6.8 | Yes | Yes | 19.3 | 17.7 | 1.6 | F1A46D91596E4301B3B8926DCCB79253 |  | R22 | Non-TXV |  | 8.095% | 0.91905 | 15.56% | [5 empty] | Non-TXV | 8.095%
Stockton | CA | 95209-3724 |  | 2013-11-08 | 2013-11-08 11:16 | 2013-11-08 11:16 | LENNOX - 13ACX-048-230-13 | 120 | 0 | Yes | Yes | 19.2 | 19.6 | -0.4 | DF454CCBB9FC41EB858C12BA5C9DD87E |  | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3602 |  | 2013-11-12 | 2013-11-12 12:56 | 2013-11-12 13:13 | TRANE - CBD | 64 | 1.9 | Yes | Yes | 23.4 | 19.5 | 3.9 | F547FBD0B4AE469FB5B4184CD241AA43 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Stockton | CA | 95212-0000 |  | 2013-11-06 | 2013-11-06 14:46 | 2013-11-06 15:13 | CARRIER - 38BRC042340 | 103 | 4.5 | Yes | Yes | 16.4 | 19.1 | -2.7 | E0A9FA7A0E5C41DCB40F407676D7D68C |  | R22 | Non-TXV |  | 4.369% | 0.95631 | 8.396% | [5 empty] | Non-TXV | 4.369%
Lincoln | CA | 95648-1516 |  | 2013-10-31 | 2013-10-31 13:09 | 2013-10-31 13:09 | CARRIER - 38BRC036330 | 104 | 0 | Yes | Yes | 23.4 | 20.4 | 3 | 879B3A5CFAAF448F9BBCB21C82CE29BA |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95304-9148 |  | 2013-11-13 | 2013-11-13 12:47 | 2013-11-13 13:08 | BRYANT - 561CJ060-A | 152 | 6.6 | Yes | Yes | 26.1 | 20.1 | 6 | D9BE9EE960644430BFD04B7D385B6C16 |  | R22 | Non-TXV |  | 4.342% | 0.95658 | 8.345% | [5 empty] | Non-TXV | 4.342%
Lathrop | CA | 95330-9192 |  | 2013-11-07 | 2013-11-07 10:18 | 2013-11-07 10:46 | GOODMAN - GSC130601BC | 169 | -15.9 | Yes | Yes | 26.5 | 20.9 | 5.6 | BAE7143BB0CA4EA0903F23E759BF27B7 |  | R22 | Non-TXV |  | -9.408% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.408%
Tracy | CA | 95377-5396 |  | 2013-11-14 | 2013-11-14 11:44 | 2013-11-14 12:01 | GOODMAN - CKJ60-1C | 149 | 10 | Yes | Yes | 25.7 | 20.1 | 5.6 | 364D630402B3498EA8B96B503801BD2E |  | R22 | Non-TXV |  | 6.711% | 0.93289 | 12.9% | [5 empty] | Non-TXV | 6.711%
Rocklin | CA | 95765-4280 |  | 2013-11-01 | 2013-11-01 15:41 | 2013-11-01 15:58 | OTHER - TZAA-3422A757 | 90 | 2.7 | Yes | Yes | 19 | 20.1 | -1.1 | 036928A56B3840B4A4A4150B99043433 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Lathrop | CA | 95330-9157 |  | 2013-11-06 | 2013-11-06 13:08 | 2013-11-06 13:28 | GOODMAN - CKJ30-1B | 92 | 4.6 | Yes | Yes | 21.6 | 19.5 | 2.1 | A6CDF76AE37D4F57ABD444A12D604DCB |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Lathrop | CA | 95330-8822 |  | 2013-11-06 | 2013-11-06 12:14 | 2013-11-06 12:33 | CARRIER - 38BRC048370 | 136 | -33.8 | Yes | Yes | 35 | 20.4 | 14.6 | 5501BE79B0654489BE9265E83CF1C3F1 |  | R22 | TXV |  | -24.85% | 1.2485 | 6.96% |  |  |  |  | TXV |  |  | -24.85%
Tracy | CA | 95304-5933 |  | 2013-11-13 | 2013-11-13 12:07 | 2013-11-13 12:25 | CARRIER - 38CKC042350 | 93 | 3.5 | Yes | Yes | 20.8 | 20.1 | 0.7 | 93C9BCCDA86A493EBE13884EFE59956A |  | R22 | Non-TXV |  | 3.763% | 0.96237 | 7.233% | [5 empty] | Non-TXV | 3.763%
Manteca | CA | 95337-7313 |  | 2013-11-07 | 2013-11-07 16:06 | 2013-11-07 16:48 | TRANE - 4TTB3024D1000AA | 85 | 7.2 | Yes | Yes | 21.7 | 19.5 | 2.2 | ACE76F99E42B413CA0EC792DDAFC869E |  | R410A | TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | TXV | 8.471%
Tracy | CA | 95304-1522 |  | 2013-11-13 | 2013-11-13 14:14 | 2013-11-13 14:28 | OTHER - 38TKB048350 | 112 | 7.4 | Yes | Yes | 20.6 | 18.8 | 1.8 | E1F1598DD8EB49FDBD621A451D2A2CE2 |  | R22 | Non-TXV |  | 6.607% | 0.93393 | 12.7% | [5 empty] | Non-TXV | 6.607%
Tracy | CA | 95304-1522 |  | 2013-11-13 | 2013-11-13 14:20 | 2013-11-13 14:36 | CARRIER - 38TKB048350 | 112 | 7.8 | Yes | Yes | 21.9 | 19.7 | 2.3 | 082C681F5FD6464C95DAFBD4400C5C07 |  | R22 | Non-TXV |  | 6.964% | 0.93036 | 13.38% | [5 empty] | Non-TXV | 6.964%
Stockton | CA | 95205-6518 |  | 2013-11-07 | 2013-11-07 14:01 | 2013-11-07 14:20 | AMANA - PGD36C0702E | 110 | 8 | Yes | Yes | 23.1 | 18.8 | 4.3 | EA4B38CAC690419CB37DC83B0D965993 |  | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Tracy | CA | 95377-8745 |  | 2013-11-14 | 2013-11-14 14:21 | 2013-11-14 14:44 | BDP - 563AN048-A | 168 | -13.8 | Yes | Yes | 19.2 | 19.5 | -0.3 | DD54FB074D384F3DA3FF229BBA3E3D40 |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Tracy | CA | 95304-5915 |  | 2013-11-13 | 2013-11-13 12:44 | 2013-11-13 13:01 | YORK - H3RC06S06HA | 147 | 6.7 | Yes | Yes | 18.5 | 19.6 | -1.1 | 42486245A5D14623BBB35F36C15D54DF |  | R22 | Non-TXV |  | 4.558% | 0.95442 | 8.759% | [5 empty] | Non-TXV | 4.558%
Oakdale | CA | 95361-8766 |  | 2013-11-08 | 2013-11-08 12:21 | 2013-11-08 12:42 | DAY & NIGHT - 561AJX024000ABAA | 60 | 4.8 | Yes | Yes | 18.3 | 20.1 | -1.8 | B6F63CFBD71F4E3A9B9DE69D90AFD042 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Stockton | CA | 95206-2235 |  | 2013-11-06 | 2013-11-06 12:52 | 2013-11-06 13:11 | GOODMAN - CLK361H | 71 | 5.3 | Yes | Yes | 20.4 | 20.4 | 0 | DD0577B99702448AA30B1AFD5C9D86CE |  | R22 | Non-TXV |  | 7.465% | 0.92535 | 14.35% | [5 empty] | Non-TXV | 7.465%
Stockton | CA | 95209-2716 |  | 2013-11-08 | 2013-11-08 10:35 | 2013-11-08 10:52 | DAY & NIGHT - N2A342AKA300 | 105 | 6.2 | Yes | Yes | 24.7 | 19.7 | 5 | 2DC2FF55206D4135B1D71E7AF9BDC73B |  | R22 | TXV |  | 5.905% | 0.94095 | 11.35% | [5 empty] | TXV | 5.905%
Tracy | CA | 95304-9413 |  | 2013-11-13 | 2013-11-13 13:42 | 2013-11-13 14:00 | RHEEM - RAPC-036JAZ | 160 | 11.9 | Yes | Yes | 27.2 | 21.3 | 5.9 | 609DCEED5B514B9D9F45C49FE624EDE1 |  | R22 | TXV |  | 7.438% | 0.92563 | 14.29% | [5 empty] | TXV | 7.438%
Tracy | CA | 95304-9413 |  | 2013-11-13 | 2013-11-13 14:06 | 2013-11-13 14:13 | RHEEM - RAPC-036JAZ | 160 | 23.4 | Yes | Yes | 24.8 | 21.4 | 3.5 | 8F6B6CC896B741EC9B31858288CC7C2B |  | R22 | TXV |  | 14.62% | 0.85375 | 28.11% | [5 empty] | TXV | 14.62%
Oakdale | CA | 95361-3940 |  | 2013-11-07 | 2013-11-07 16:17 | 2013-11-08 10:10 | HEIL - H2A324GKA100 | 90 | 8.3 | Yes | Yes | 20 | 19.1 | 0.9 | 795D30250DA14028BC85ADC703BD70B4 |  | R22 | Non-TXV |  | 9.222% | 0.90778 | 17.72% | [5 empty] | Non-TXV | 9.222%
Stockton | CA | 95215-9655 |  | 2013-11-14 | 2013-11-14 11:13 | 2013-11-14 11:29 | GE - BWC024E100A0 | 84 | 7.2 | Yes | Yes | 24.3 | 19.1 | 5.3 | 77437D73473F486B930632356FD7750A |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Stockton | CA | 95212-3219 |  | 2013-11-14 | 2013-11-14 12:17 | 2013-11-14 12:17 | GOODMAN - CL448-1A | 150 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | DB03CE85E8864CD89F5C8D82DDB5F190 |  | R22 | TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-6401 |  | 2013-11-08 | 2013-11-08 14:33 | 2013-11-27 16:15 | GE - UNK | 60 | 5.4 | Yes | Yes | 20.1 | 17.9 | 2.2 | 188FC1F0ACC34F559521FA12FE65CB2A |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Manteca | CA | 95337-4466 |  | 2013-11-07 | 2013-11-07 15:31 | 2013-11-07 15:50 | RUUD - UNK | 85 | 5.4 | Yes | Yes | 25.4 | 20.3 | 5.2 | EFA3731F083F44338273DCB96C08600F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Stockton | CA | 95215-9655 |  | 2013-11-14 | 2013-11-14 10:52 | 2013-11-14 10:52 | BRYANT - 583BNW036060AB | 105 | 0 | Yes | Yes | 22.4 | 19.2 | 3.2 | 588CD1178DC44A1D8A37C281E8EE4DCE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3205 |  | 2013-11-08 | 2013-11-08 13:48 | 2013-11-08 14:10 | GE - BTB930A100A | 53 | 6.4 | Yes | Yes | 21 | 18.8 | 2.2 | BD437DE100DA4FB59B603F0CE6582FBD |  | R22 | Non-TXV |  | 12.08% | 0.87925 | 23.21% | [5 empty] | Non-TXV | 12.08%
Stockton | CA | 95206-2802 |  | 2013-11-06 | 2013-11-06 14:04 | 2013-11-07 06:59 | CARRIER - 38CK042-35 | 90 | 3.8 | Yes | Yes | 20.6 | 20.4 | 0.2 | 0CB0D30D857D416ABAB6588122280E0A |  | R22 | Non-TXV |  | 4.222% | 0.95778 | 8.114% | [5 empty] | Non-TXV | 4.222%
Stockton | CA | 95212-3406 |  | 2013-11-06 | 2013-11-06 16:52 | 2013-11-06 17:12 | YORK - H2RC42S06A | 107 | -8.8 | Yes | Yes | 16.1 | 19.1 | -3 | BC84A257F50646CEAD7B8C6F555C17C6 |  | R22 | Non-TXV |  | -8.224% | 1.0822 | 2.303% |  |  |  |  | Non-TXV |  |  | -8.224%
Stockton | CA | 95205-4638 |  | 2013-11-07 | 2013-11-07 10:21 | 2013-11-07 10:43 | LENNOX - GCS20RV-411-75-1P | 70 | 5.4 | Yes | Yes | 23.4 | 20.4 | 3 | 60D3EE255EFA400FB53751F5981C58CB |  | R22 | Non-TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | Non-TXV | 7.714%
Stockton | CA | 95212-3042 |  | 2013-11-06 | 2013-11-06 15:28 | 2013-11-06 15:47 | CARRIER - 38CKC036350 | 70 | 5 | Yes | Yes | 17.8 | 19.9 | -2.1 | E6CFD26D90CE42379590FB7D66A83891 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Stockton | CA | 95205-7809 |  | 2013-11-07 | 2013-11-07 13:24 | 2013-11-07 13:41 | DAY & NIGHT - UNK | 96 | 25 | Yes | Yes | 22.4 | 19.1 | 3.3 | 49EA3FD362D6479FB10CBC600BB82D6C |  | R22 | Non-TXV |  | 26.04% | 0.73958 | 50.05% | [5 empty] | Non-TXV | 26.04%
Stockton | CA | 95215-8227 |  | 2013-11-14 | 2013-11-14 10:11 | 2013-11-14 10:11 | COLEMAN - TCGD48S21S2A | 69 | 0 | Yes | Yes | 19.3 | 20.1 | -0.8 | C17FE56E951E4E6EB1B3C1ADF551006F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-2032 |  | 2013-11-14 | 2013-11-14 12:56 | 2013-11-14 13:19 | RHEEM - UNK | 85 | -8 | Yes | Yes | 23.5 | 19.1 | 4.4 | EA3C8BEE0D4244278C752312CFA98484 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95205-5051 |  | 2013-11-07 | 2013-11-07 11:41 | 2013-11-07 11:59 | BRYANT - 582ANW030060AAAD | 55 | 5.1 | Yes | Yes | 21 | 19.8 | 1.2 | 7DDE4F9A89994EA38928B188C5033430 |  | R22 | Non-TXV |  | 9.273% | 0.90727 | 17.82% | [5 empty] | Non-TXV | 9.273%
Stockton | CA | 95207-4411 |  | 2013-11-14 | 2013-11-14 15:24 | 2013-11-14 15:24 | TRANE - TTP030C100BO | 151 | 0 | Yes | Yes | 22.1 | 19.3 | 2.8 | 84099E75330B4FD3AFD2E29AE37650DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1724 |  | 2013-11-08 | 2013-11-08 15:46 | 2013-11-08 16:14 | TRANE - YCY030G1MOAD | 124 | 10.5 | Yes | Yes | 20.6 | 18 | 2.7 | B458DAAEA99440E1B3AD4E45C0B81714 |  | R22 | Non-TXV |  | 8.468% | 0.91532 | 16.27% | [5 empty] | Non-TXV | 8.468%
Tracy | CA | 95304-1518 |  | 2013-11-12 | 2013-11-12 12:08 | 2013-11-12 12:45 | BRYANT - 561CJ042-3 | 93 | 5.7 | Yes | Yes | 25.5 | 20.1 | 5.4 | EF9FB9FD0FA946C28913F3F377DB0929 |  | R22 | Non-TXV |  | 6.129% | 0.93871 | 11.78% | [5 empty] | Non-TXV | 6.129%
Ripon | CA | 95366-2778 |  | 2013-11-13 | 2013-11-13 16:35 | 2013-11-13 17:10 | PAYNE - PA10JA018-C | 56 | 2.9 | Yes | Yes | 18.3 | 19.3 | -1 | CF362A5D4DF64E2A8BF1CE469425264D |  | R22 | TXV |  | 5.179% | 0.94821 | 9.952% | [5 empty] | TXV | 5.179%
Stockton | CA | 95207-1354 |  | 2013-11-06 | 2013-11-06 10:01 | 2013-11-06 10:17 | - HS29-411-2P | 80 | 4.4 | Yes | Yes | 21.3 | 19.7 | 1.6 | DEF0F9972B2C4F6386FDFEC9C0AEA850 |  | R22 | TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | TXV | 5.5%
Stockton | CA | 95210-4413 |  | 2013-11-08 | 2013-11-08 13:46 | 2013-11-08 14:03 | PAYNE - 591ANX042000ABAA | 112 | -6.6 | Yes | Yes | 24.6 | 18.7 | 5.9 | 91B589065E10488CA3B025D624E41744 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Merced | CA | 95348-2829 |  | 2013-11-07 | 2013-11-07 16:09 | 2013-11-07 16:11 | YORK - D1NA048N09006B | 88 | 4.7 | Yes | Yes | 23.1 | 19.7 | 3.4 | 327E93B2443C4B96BD534852B4C2CF60 |  | R22 | Non-TXV |  | 5.341% | 0.94659 | 10.26% | [5 empty] | Non-TXV | 5.341%
Manteca | CA | 95336-9191 |  | 2013-11-14 | 2013-11-14 11:37 | 2013-11-14 12:09 | GOODMAN - CBD | 96 | 2.9 | Yes | Yes | 24.6 | 20.1 | 4.5 | E9C8662803EC42FF8F7527802C26C9E7 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Merced | CA | 95348-2238 |  | 2013-11-08 | 2013-11-08 13:19 | 2013-11-08 13:20 | BRYANT - 113ANA018-E | 56 | 3 | Yes | Yes | 21.5 | 20.4 | 1.1 | 4D7131AEA4C1468ABD8BFC73DBBAE634 |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Ripon | CA | 95366-2778 |  | 2013-11-13 | 2013-11-13 15:56 | 2013-11-13 16:33 | PAYNE - PA10JA018-C | 56 | 27.9 | Yes | Yes | 18.2 | 19.5 | -1.3 | 2B5773C552F6403CACEE9AEB8AE55785 |  | R22 | TXV |  | 49.82% | 0.50179 | 95.75% | [5 empty] | TXV | 49.82%
Stockton | CA | 95207-4505 |  | 2013-11-06 | 2013-11-06 12:30 | 2013-11-06 12:42 | GOODMAN - CKL24-1H | 72 | 4.5 | Yes | Yes | 20.4 | 19.6 | 0.8 | 54333B88301E4E0BA3090C9E9BE0F45B |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Tracy | CA | 95304-8834 |  | 2013-11-12 | 2013-11-12 15:57 | 2013-11-12 16:15 | UNITARY PRODUCTS GROUP - BRCQQ0361BD | 52 | -4.9 | Yes | Yes | 22 | 19.7 | 2.3 | F9AF3405C503467CB5528A1C1CD7408A |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Merced | CA | 95341-5540 |  | 2013-11-07 | 2013-11-07 14:25 | 2013-11-07 14:27 | RHEEM - RRNL-B036JK06X | 93 | 2.9 | Yes | Yes | 22.8 | 19.1 | 3.7 | EAD5C12FC1784F69B96BF237BFDB6E45 |  | R410A | Non-TXV |  | 3.118% | 0.96882 | 5.993% | [5 empty] | Non-TXV | 3.118%
Stockton | CA | 95209-2722 |  | 2013-11-06 | 2013-11-06 14:26 | 2013-11-06 19:23 | GE - BGTA736B1A01 | 94 | 4.1 | Yes | Yes | 22.2 | 19.7 | 2.6 | 142E259F98C047BAB9080F21139E7F83 |  | R22 | Non-TXV |  | 4.362% | 0.95638 | 8.382% | [5 empty] | Non-TXV | 4.362%
Merced | CA | 95348-3128 |  | 2013-11-08 | 2013-11-08 14:59 | 2013-11-08 15:01 | GE - 777UNK | 74 | 3.5 | Yes | Yes | 20.3 | 20.1 | 0.2 | 072EAB74D49F45109B34EDDF5832C9ED |  | R22 | Non-TXV |  | 4.73% | 0.9527 | 9.09% | [5 empty] | Non-TXV | 4.73%
Tracy | CA | 95377-6645 |  | 2013-11-14 | 2013-11-14 13:41 | 2013-11-14 14:04 | YORK - H1RA048S6D | 117 | 4.5 | Yes | Yes | 18.9 | 20.4 | -1.5 | 1B081B2BE9FF48C2BD9B702058045AAA |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Merced | CA | 95348-3118 |  | 2013-11-08 | 2013-11-08 15:17 | 2013-11-08 15:18 | GE - BTB924A100A0 | 45 | 1.6 | Yes | Yes | 21 | 19.9 | 1.1 | 59BB2B20E55F4634BD35AF35F18EA72B |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Merced | CA | 95348-2249 |  | 2013-11-08 | 2013-11-08 14:20 | 2013-11-08 14:21 | DAY & NIGHT - 777UNK | 54 | 3 | Yes | Yes | 22.8 | 20.3 | 2.5 | 1AD134F1A4F64A3697B347037DB3B455 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Merced | CA | 95340-3577 |  | 2013-11-07 | 2013-11-07 15:03 | 2013-11-07 15:05 | AMANA - PGD30C702E | 74 | 4.1 | Yes | Yes | 23.2 | 20.2 | 3 | B3631DB4C929432E934432CD7766CA5B |  | R22 | Non-TXV |  | 5.541% | 0.94459 | 10.65% | [5 empty] | Non-TXV | 5.541%
Stockton | CA | 95210-3742 |  | 2013-11-08 | 2013-11-08 14:54 | 2013-11-08 15:12 | YORK - TCGD36S21S2HA | 63 | -3.7 | Yes | Yes | 15.7 | 18.7 | -3 | FBC0D3C621764B6BA4AD1DC93B1FB7FE |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Stockton | CA | 95209-2728 |  | 2013-11-08 | 2013-11-08 09:56 | 2013-11-08 10:09 | GE - BGTA736B1B | 70 | -6.6 | Yes | Yes | 22.7 | 19.8 | 2.9 | 1C12EFE2D55F43B2ABE187EEAD1A3B26 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Stockton | CA | 95206-2802 |  | 2013-11-13 | 2013-11-13 12:03 | 2013-11-13 12:23 | CARRIER - 38CKC030-J | 70 | 2.8 | Yes | Yes | 22 | 20.4 | 1.6 | E17FBD970A71452EA97540A795EAA2A7 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Manteca | CA | 95336-3222 |  | 2013-11-12 | 2013-11-12 14:41 | 2013-11-12 14:56 | TRANE - BTD736A100B0 | 88 | 2.7 | Yes | Yes | 24.5 | 19.7 | 4.8 | 8B8120DDD2B644349243D8252A011732 |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Stockton | CA | 95209-2721 |  | 2013-11-08 | 2013-11-08 12:25 | 2013-11-08 12:43 | RHEEM - RRNA-B060JK10X | 145 | 16.2 | Yes | Yes | 23.8 | 19.8 | 4.1 | 36D019AF52074C14BB9703DF38D68766 |  | R22 | TXV |  | 11.17% | 0.88828 | 21.47% | [5 empty] | TXV | 11.17%
Stockton | CA | 95209-2117 |  | 2013-11-06 | 2013-11-06 13:54 | 2013-11-06 14:13 | WESTINGHOUSE - 1E024AAA0 | 53 | 5.7 | Yes | Yes | 20.8 | 20.1 | 0.7 | 32F3687784B44CD6B1E13048B471A5C0 |  | R22 | Non-TXV |  | 10.75% | 0.89245 | 20.67% | [5 empty] | Non-TXV | 10.75%
Stockton | CA | 95212-2211 |  | 2013-11-13 | 2013-11-13 14:06 | 2013-11-14 10:49 | CARRIER - 38CK042 | 90 | 5.3 | Yes | Yes | 19.5 | 20.4 | -0.9 | 6429EAC0AD2B496AB11A01D445265007 |  | R22 | Non-TXV |  | 5.889% | 0.94111 | 11.32% | [5 empty] | Non-TXV | 5.889%
Stockton | CA | 95207-4509 |  | 2013-11-07 | 2013-11-07 15:35 | 2013-11-07 15:59 | PAYNE - 561CJ024-C | 72 | 6.8 | Yes | Yes | 23.2 | 19.4 | 3.8 | 422226432EC048BAA81B427F1896F006 |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Tracy | CA | 95304-8824 |  | 2013-11-12 | 2013-11-12 15:06 | 2013-11-12 15:30 | BRYANT - 574BNW036060NA | 149 | -44.2 | Yes | Yes | 19.8 | 19.9 | -0.1 | 3384E95134874F6384AD5481804D41F4 |  | R410A | TXV |  | -29.66% | 1.2966 | 8.307% |  |  |  |  | TXV |  |  | -29.66%
Manteca | CA | 95336-3327 |  | 2013-11-07 | 2013-11-07 11:18 | 2013-11-07 11:36 | OTHER - UNK | 53 | 8 | Yes | Yes | 25.6 | 20.4 | 5.2 | FBF3B105B5A34D26B450008B0729310D |  | R22 | Non-TXV |  | 15.09% | 0.84906 | 29.01% | [5 empty] | Non-TXV | 15.09%
Stockton | CA | 95205-5638 |  | 2013-11-07 | 2013-11-07 12:16 | 2013-11-07 12:32 | BRYANT - 563ANX030000AAAA | 103 | 10.1 | Yes | Yes | 18 | 19.8 | -1.8 | 592E3752F95048429473DFC53B2B7954 |  | R22 | Non-TXV |  | 9.806% | 0.90194 | 18.84% | [5 empty] | Non-TXV | 9.806%
Stockton | CA | 95210-2618 |  | 2013-11-08 | 2013-11-08 15:24 | 2013-11-08 15:41 | GOODMAN - GPG13300701AB | 77 | 2.4 | Yes | Yes | 23 | 18.2 | 4.8 | 9A35EB34414343EB94A782CC0865CDD9 |  | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Stockton | CA | 95205-6144 |  | 2013-11-07 | 2013-11-07 12:51 | 2013-11-07 13:05 | RHEEM - RRNL-B036JK06X | 92 | 10.8 | Yes | Yes | 22.3 | 19.1 | 3.3 | D7DE57800E224F7E84BBF2C7D2408DC6 |  | R410A | TXV |  | 11.74% | 0.88261 | 22.56% | [5 empty] | TXV | 11.74%
Manteca | CA | 95336-2823 |  | 2013-11-07 | 2013-11-07 12:40 | 2013-11-07 12:58 | YORK - H1DA036S06A | 92 | 5.8 | Yes | Yes | 23.7 | 20.1 | 3.6 | 9CFDE878A5304D03987FA62555A66468 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.304% | 0.93696 | 12.12% | [5 empty] | Non-TXV | 6.304%
Stockton | CA | 95212-3803 |  | 2013-11-06 | 2013-11-06 16:04 | 2013-11-06 16:22 | BRYANT - 388CK048370 | 98 | 15.4 | Yes | Yes | 19.2 | 19.5 | -0.3 | D6F67F11D56A4862867C4CDEF7376B57 |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Tracy | CA | 95304-0000 |  | 2013-11-12 | 2013-11-12 13:00 | 2013-11-12 13:29 | GOODMAN - PGB030075-1A | 56 | -5.3 | Yes | Yes | 19.1 | 20.1 | -1 | 7B8FA3450E67403FBDE82EC2CD5E6779 |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
Stockton | CA | 95206-3662 |  | 2013-11-06 | 2013-11-06 11:46 | 2013-11-06 12:19 | GOODMAN - GPG10240451A | 50 | 2.4 | Yes | Yes | 18.7 | 17.7 | 1 | 6FC6AA7904B542EE84F254D97A5A3E24 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Manteca | CA | 95336-3834 |  | 2013-11-07 | 2013-11-07 11:54 | 2013-11-07 12:21 | GE - BTR942A100A1 | 142 | 5.2 | Yes | Yes | 26 | 20.4 | 5.6 | D357CAD6496A4A8EB545C499D494E802 |  | R22 | Non-TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | Non-TXV | 3.662%
Lathrop | CA | 95330-8791 |  | 2013-11-14 | 2013-11-14 11:40 | 2013-11-14 12:01 | CARRIER - 38CK060 | 140 | 10 | Yes | Yes | 20.8 | 20.2 | 0.6 | 0F0DAAAE8CA24870A137B5F6AE208467 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Ripon | CA | 95366-2449 |  | 2013-11-13 | 2013-11-13 15:00 | 2013-11-13 15:26 | ICP - PGD330060K001C1 | 98 | 46.7 | Yes | Yes | 22.5 | 19.9 | 2.6 | C340F00F81D14BBEB23A991703CA1874 |  | R410A | TXV |  | 47.65% | 0.52347 | 91.58% | [5 empty] | TXV | 47.65%
Stockton | CA | 95207-3132 |  | 2013-11-06 | 2013-11-06 11:56 | 2013-11-06 11:56 | RHEEM - 13AJM30A01 | 86 | 0 | Yes | Yes | 20 | 19.8 | 0.3 | 31942B8ED013464294C23A5A969A0350 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2467 |  | 2013-11-06 | 2013-11-06 13:22 | 2013-11-06 13:52 | DAY & NIGHT - N2A324AKB200 | 70 | 5.1 | Yes | Yes | 23.1 | 19.9 | 3.2 | 85CD3453840649AA9EC37F96B50BF2F4 |  | R22 | Non-TXV |  | 7.286% | 0.92714 | 14% | [5 empty] | Non-TXV | 7.286%
Manteca | CA | 95337-8962 |  | 2013-11-12 | 2013-11-12 15:42 | 2013-11-12 16:22 | BRYANT - 563CN042-D | 104 | 3.9 | Yes | Yes | 21.8 | 19.1 | 2.7 | BC9C8639287E4F5EB20E9D35A659D9AA |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Merced | CA | 95348-2250 |  | 2013-11-08 | 2013-11-08 14:05 | 2013-11-08 14:06 | BRYANT - 777UNK | 54 | 2.6 | Yes | Yes | 19.6 | 19.9 | -0.3 | E180D5F3428841D0810702031882A12E |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Merced | CA | 95348-2240 |  | 2013-11-08 | 2013-11-08 13:44 | 2013-11-08 13:45 | BRYANT - 113ANA018-E | 56 | 2.6 | Yes | Yes | 19.8 | 20.2 | -0.4 | E55C01A9A6544B6DA2810775FC5C2503 |  | R410A | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Manteca | CA | 95336-3021 |  | 2013-11-14 | 2013-11-14 15:49 | 2013-11-14 16:32 | GE - BTB942A100A0 | 101 | 29.2 | Yes | Yes | 18.1 | 19.5 | -1.4 | 443E8EBEDF7A40DBB02558F6C41311B5 |  | R22 | Non-TXV |  | 28.91% | 0.71089 | 55.56% | [5 empty] | Non-TXV | 28.91%
Manteca | CA | 95336-3830 |  | 2013-11-14 | 2013-11-14 16:48 | 2013-11-14 18:11 | GE - BTR930C100A1 | 108 | 3.2 | Yes | Yes | 21.1 | 19.9 | 1.2 | A45C9B6E86C548B3B11DC6A9073D7E68 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95209-4275 |  | 2014-05-14 | 2014-05-14 11:47 | 2014-05-14 12:11 | CARRIER - 24ABA36BA300 | 135 | 7.5 | Yes | Yes | 20.3 | 20.1 | 0.2 | D02243C9E91D43A78D408A3EDC63879C |  | R410A | TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | TXV | 5.556%
Riverbank | CA | 95367-9662 |  | 2014-05-20 | 2014-05-20 12:06 | 2014-05-20 12:31 | COLEMAN - BRCQ0361BB | 91 | 13.8 | Yes | Yes | 21.9 | 20.4 | 1.5 | 5737A7535BDE4BFF8A9E23021BB8C8D6 |  | R22 | Non-TXV |  | 15.16% | 0.84835 | 29.14% | [5 empty] | Non-TXV | 15.16%
Stockton | CA | 95207-3306 |  | 2014-06-04 | 2014-06-04 11:30 | 2014-06-04 11:46 | RUUD - URKA-A036JK08X | 62 | 2.6 | Yes | Yes | 26.6 | 20.7 | 6 | 8D95AE1582CD4B76A21884749E92145E |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Oakdale | CA | 95361-7533 |  | 2014-06-04 | 2014-06-04 12:28 | 2014-06-04 12:50 | YORK - H2RC036S06HA | 83 | 8.4 | Yes | Yes | 21.2 | 19.4 | 1.8 | 532CCB40A4B3465ABB96E881E73333A0 |  | R22 | Non-TXV |  | 10.12% | 0.8988 | 19.45% | [5 empty] | Non-TXV | 10.12%
Oakdale | CA | 95361-7533 |  | 2014-06-04 | 2014-06-04 12:52 | 2014-06-04 13:13 | YORK - H2RC036S06HG | 83 | 7.1 | Yes | Yes | 20 | 19.9 | 0.1 | 6203C2DFA1FA474EA3EB2B0D51CB52BC |  | R22 | Non-TXV |  | 8.554% | 0.91446 | 16.44% | [5 empty] | Non-TXV | 8.554%
Fresno | CA | 93727-3081 |  | 2014-06-12 | 2014-06-12 16:20 | 2014-06-12 16:49 | RHEEM - N/A | 60 | 5.1 | Yes | Yes | 23.7 | 23.7 | 0 | 19F8B589500743CD82DCC71B64A276E1 |  | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Fresno | CA | 93705-2821 |  | 2014-05-28 | 2014-05-28 08:39 | 2014-05-28 08:42 | GOODMAN - GSX130301BA | 78 | 4.7 | Yes | Yes | 23.5 | 21.4 | 2.1 | 9D8752F45EA241D0B4B54B854E322975 |  | R410A | TXV |  | 6.026% | 0.93974 | 11.58% | [5 empty] | TXV | 6.026%
Stockton | CA | 95207-2302 |  | 2014-06-11 | 2014-06-11 08:46 | 2014-06-11 09:04 | ICP - GPCM030K060F | 53 | 6.9 | Yes | Yes | 19.4 | 20.2 | -0.8 | 50A94BF0A7264751807D1FF8A5530AF7 |  | R22 | Non-TXV |  | 13.02% | 0.86981 | 25.02% | [5 empty] | Non-TXV | 13.02%
Fresno | CA | 93727-5404 |  | 2014-07-16 | 2014-07-16 12:36 | 2014-07-16 12:38 | OTHER - 7777UNK | 70 | 3.5 | Yes | Yes | 16.7 | 19.3 | -2.6 | B69B47F924AB479E9F9585C8118CEB46 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93705-4520 |  | 2014-07-15 | 2014-07-15 10:22 | 2014-07-15 10:43 | DAY & NIGHT - UNK | 80 | -5.6 | Yes | Yes | 18.9 | 15.5 | 3.4 | 952B90FF3F3245B9BCEED197891599B1 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Gustine | CA | 95322-1608 |  | 2014-06-20 | 2014-06-20 09:24 | 2014-06-20 09:43 | RHEEM - RSMA-30A | 85 | 2.9 | Yes | Yes | 20.8 | 20.4 | 0.4 | 27FA5130274B47A0B1B7CCA1C382FBB8 |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Clovis | CA | 93611-6240 |  | 2014-06-24 | 2014-06-24 13:05 | 2014-06-24 13:53 | CARRIER - 48NLT042100 | 105 | 4.7 | Yes | Yes | 21.7 | 21.3 | 0.5 | 0148CE17F2A445938D9C5A5487C312EA |  | R22 | Non-TXV |  | 4.476% | 0.95524 | 8.602% | [5 empty] | Non-TXV | 4.476%
Fresno | CA | 93720-5318 |  | 2014-06-19 | 2014-06-19 13:57 | 2014-06-19 14:14 | LENNOX - 13ACC-048-230-01 | 158 | 15.7 | Yes | Yes | 21.4 | 21.8 | -0.4 | EF7B94A339464975BEEB737822ACAE4A |  | R22 | Non-TXV |  | 9.937% | 0.90063 | 19.1% | [5 empty] | Non-TXV | 9.937%
Fresno | CA | 93720-5318 |  | 2014-06-19 | 2014-06-19 14:16 | 2014-06-19 14:46 | LENNOX - 13ACC-048-230-01 | 158 | 7.7 | Yes | Yes | 22 | 21.4 | 0.6 | B7CC0811AF404753871A42D6B672D14F |  | R22 | Non-TXV |  | 4.873% | 0.95127 | 9.366% | [5 empty] | Non-TXV | 4.873%
Tracy | CA | 95376-3023 |  | 2014-05-29 | 2014-05-29 10:33 | 2014-05-29 10:59 | GOODMAN - ASX130601AA | 85 | -4.9 | Yes | Yes | 19.2 | 20.8 | -1.6 | 5356B35D01994A958E9E675AD8F7696C |  | R410A | TXV |  | -5.765% | 1.0576 | 1.614% |  |  |  |  | TXV |  |  | -5.765%
Fresno | CA | 93703-1652 |  | 2014-05-15 | 2014-05-15 13:34 | 2014-05-15 13:48 | YORK - DBYP-F036N070A | 108 | 3.4 | Yes | Yes | 22 | 19.3 | 2.7 | 343DB09F33D3437E9A6B8A49EEE29DF0 |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Fowler | CA | 93625-2029 |  | 2014-08-06 | 2014-08-06 11:03 | 2014-08-06 11:22 | GOODMAN - PGB030075-1 | 45 | 3.9 | Yes | Yes | 18.4 | 19.8 | -1.4 | 0AF6587387574BAAA8BD649A3772E2A5 |  | R22 | Non-TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | Non-TXV | 8.667%
Stockton | CA | 95210-1533 |  | 2014-05-16 | 2014-05-16 11:11 | 2014-05-16 11:28 | RHEEM - RRKA-A024JK06X | 50 | 3.5 | Yes | Yes | 23.8 | 21.4 | 2.4 | 46DC0864EC82404C8F5FA91E192800F6 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Stockton | CA | 95206-5838 |  | 2014-06-09 | 2014-06-09 12:38 | 2014-06-09 12:38 | PAYNE - 561CJ036 | 72 | 0 | Yes | Yes | 19.5 | 20.1 | -0.6 | 4454CAC5998B4574B95C6A2BCC829197 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-9294 |  | 2014-05-27 | 2014-05-27 13:43 | 2014-05-27 14:11 | PAYNE - PA12NA48-B | 150 | 7.8 | Yes | Yes | 24.5 | 19.9 | 4.6 | 0FA183F2BFDF497F805F384A01D89A3A |  | R22 | TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | TXV | 5.2%
Chico | CA | 95973-9294 |  | 2014-05-27 | 2014-05-27 14:45 | 2014-05-27 15:11 | PAYNE - PA12NA048-B | 155 | 6.7 | Yes | Yes | 18 | 21 | -3 | C0CC98DFFEE848E982B8A3A9D3BD32C1 |  | R22 | Non-TXV |  | 4.323% | 0.95677 | 8.307% | [5 empty] | Non-TXV | 4.323%
Chico | CA | 95973-9294 |  | 2014-05-27 | 2014-05-27 15:00 | 2014-05-27 15:49 | PAYNE - PA12NA024-B | 86 | 5.3 | Yes | Yes | 20.1 | 21.2 | -1.1 | C96BA5C7FF2446E29AF2787764212FC1 |  | R22 | TXV |  | 6.163% | 0.93837 | 11.84% | [5 empty] | TXV | 6.163%
Yuba City | CA | 95991-6753 |  | 2014-05-30 | 2014-05-30 14:29 | 2014-05-30 14:50 | GOODMAN - CK36-1A | 73 | 2.1 | Yes | Yes | 23 | 23.7 | -0.7 | 469D3CBD049844B5A22955D9EC179188 |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Atwater | CA | 95301-4878 |  | 2014-07-01 | 2014-07-01 09:59 | 2014-07-01 10:25 | GOODMAN - CK30-1B | 85 | 4.4 | Yes | Yes | 19.7 | 20.4 | -0.7 | C20A7A3B4F224201883249A61445DF11 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Stockton | CA | 95210-3716 |  | 2014-06-07 | 2014-06-07 09:56 | 2014-06-07 10:13 | PAYNE - PA10JA036-A | 85 | -5 | Yes | Yes | 25.4 | 19.8 | 5.6 | 9580C4515D434F51BD8419FEFDB09B6C |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93727-7373 |  | 2014-06-06 | 2014-06-06 15:11 | 2014-06-06 15:34 | OTHER - 80AW36-1006 | 112 | 3.4 | Yes | Yes | 22.8 | 22.8 | 0 | 06904C44686C4B6DB285F80A34458952 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Stockton | CA | 95203-1318 |  | 2014-08-19 | 2014-08-19 10:23 | 2014-08-19 10:59 | UNITARY PRODUCTS GROUP - TCJD36S41S3A | 73 | -3.5 | Yes | Yes | 24.3 | 21 | 3.3 | EE9B70A77AF44C75825D7CF3E88A58B5 |  | R410A | TXV |  | -4.795% | 1.0479 | 1.343% |  |  |  |  | TXV |  |  | -4.795%
Ripon | CA | 95366-3401 |  | 2014-05-19 | 2014-05-19 15:28 | 2014-05-19 16:02 | YORK - AC048X1021A | 117 | -11 | Yes | Yes | 20.3 | 22.1 | -1.8 | C34E34A851DF424CAA6A84E67392450F |  | R22 | Non-TXV |  | -9.402% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.402%
Stockton | CA | 95210-4459 |  | 2014-06-14 | 2014-06-14 13:57 | 2014-06-14 14:15 | PAYNE - 591ANX036000AAAA | 87 | -5.1 | Yes | Yes | 27.4 | 22.3 | 5.1 | EBA3EC9F98D14B2FA99CFCF76DF35CDB |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Yuba City | CA | 95991-8857 |  | 2014-05-21 | 2014-05-21 16:13 | 2014-05-21 16:29 | COLEMAN - BRCQ048B | 93 | 2.7 | Yes | Yes | 20 | 21.3 | -1.3 | F392220271F444FCB016C10ACE1C9D4C |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Clovis | CA | 93619-3756 |  | 2014-06-13 | 2014-06-13 08:55 | 2014-06-13 08:57 | BRYANT - 561CJ036-F | 75 | 3.4 | Yes | Yes | 22.7 | 21.7 | 1.1 | 156724E0127F46528A5C6CD6E897A433 |  | R22 | Non-TXV |  | 4.533% | 0.95467 | 8.712% | [5 empty] | Non-TXV | 4.533%
Sanger | CA | 93657-8770 |  | 2014-06-20 | 2014-06-20 15:29 | 2014-06-20 15:49 | LENNOX - 13ACD-060-230-02 | 214 | 6.8 | Yes | Yes | 20.8 | 21.4 | -0.6 | C4F398A4FF4B4E30911C35FAA736A309 |  | R22 | Non-TXV |  | 3.178% | 0.96822 | 6.107% | [5 empty] | Non-TXV | 3.178%
Stockton | CA | 95209-2156 |  | 2014-05-14 | 2014-05-14 14:17 | 2014-05-14 14:37 | OTHER - UNK | 55 | 5.8 | Yes | Yes | 18.6 | 19.8 | -1.2 | B49DB1B4FF6746CFB7B91D48CD1A4A5A |  | R22 | Non-TXV |  | 10.55% | 0.89455 | 20.27% | [5 empty] | Non-TXV | 10.55%
Merced | CA | 95340-4116 |  | 2014-05-15 | 2014-05-15 12:33 | 2014-05-15 12:36 | BDP - 585HJW030040ABAF | 68 | 19.6 | Yes | Yes | 26.3 | 24 | 2.4 | D13C28BFDA164E45AFA0F2F9EDC1204E |  | R22 | Non-TXV |  | 28.82% | 0.71176 | 55.39% | [5 empty] | Non-TXV | 28.82%
Lodi | CA | 95240-7258 |  | 2014-06-16 | 2014-06-16 08:18 | 2014-06-16 08:39 | PAYNE - PA13NA048-E | 50 | -2.9 | Yes | Yes | 20.1 | 19.5 | 0.6 | 33503CE01C43459BAF1C2B593F8D2460 |  | R410A | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Colusa | CA | 95932-3129 |  | 2014-07-03 | 2014-07-03 08:50 | 2014-07-03 09:14 | OTHER - NA | 65 | 13.9 | Yes | Yes | 19 | 18.3 | 0.8 | ABA539ADA5B2414A83E842FE8AA77138 |  | R22 | Non-TXV |  | 21.38% | 0.78615 | 41.1% | [5 empty] | Non-TXV | 21.38%
Clovis | CA | 93611-2005 |  | 2014-06-03 | 2014-06-03 15:31 | 2014-06-03 15:33 | PAYNE - 7777UNK | 110 | 3.6 | Yes | Yes | 17.3 | 19.9 | -2.6 | 6FEE1A43DC824B21B56CB0F6471D4AE1 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Stockton | CA | 95206-3829 |  | 2014-08-19 | 2014-08-19 16:14 | 2014-08-19 16:37 | BRYANT - 582ANW042090AAAG | 100 | 5.4 | Yes | Yes | 24 | 20.4 | 3.6 | A1721EC0C3A24C9AAF80158D01BBE59B |  | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Fresno | CA | 93722-8012 |  | 2014-05-23 | 2014-05-23 14:34 | 2014-05-23 14:35 | YORK - H2RC042S06HG | 109 | 4.2 | Yes | Yes | 18.7 | 19.9 | -1.2 | 6334E3AFC9ED47068BEA61D244FFC08C |  | R22 | Non-TXV |  | 3.853% | 0.96147 | 7.405% | [5 empty] | Non-TXV | 3.853%
Valley Springs | CA | 95252-9385 |  | 2014-06-19 | 2014-06-19 10:43 | 2014-06-19 11:01 | DAY & NIGHT - 588ANW060100ACAG | 112 | -6.6 | Yes | Yes | 28 | 22 | 6 | BCDFA9818C7743B68BF9F0FC20771A2C |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Valley Springs | CA | 95252-9205 |  | 2014-09-24 | 2014-09-24 14:41 | 2014-09-25 00:33 | ICP - NAC036AKA5 | 87 | 12 | Yes | Yes | 23.8 | 19.5 | 4.3 | CAAF9BF799EE4F92B63A068854E06040 |  | R22 | Non-TXV |  | 13.79% | 0.86207 | 26.51% | [5 empty] | Non-TXV | 13.79%
Fresno | CA | 93720-2308 |  | 2014-06-04 | 2014-06-04 10:44 | 2014-06-04 11:15 | CARRIER - 585HJW036060ACAA | 102 | 15.8 | Yes | Yes | 25 | 19.3 | 5.7 | 89C3F612BD0E4271BC2E361A021B4594 |  | R22 | Non-TXV |  | 15.49% | 0.8451 | 29.77% | [5 empty] | Non-TXV | 15.49%
Fresno | CA | 93720-2308 |  | 2014-06-04 | 2014-06-04 11:17 | 2014-06-04 11:32 | CARRIER - 585HJW036060ACAA | 102 | 13.3 | Yes | Yes | 25.9 | 20.4 | 5.5 | 1CA961314E7D488EB1E8903CB5EE133A |  | R22 | Non-TXV |  | 13.04% | 0.86961 | 25.06% | [5 empty] | Non-TXV | 13.04%
Fresno | CA | 93705-1831 |  | 2014-05-22 | 2014-05-22 13:56 | 2014-05-22 14:17 | GOODMAN - GPG030 | 56 | 8.6 | Yes | Yes | 19.6 | 19.8 | -0.2 | 157872F30AC94756AD2F8E73E722273F |  | R22 | Non-TXV |  | 15.36% | 0.84643 | 29.51% | [5 empty] | Non-TXV | 15.36%
Fresno | CA | 93710-4744 |  | 2014-06-25 | 2014-06-25 14:32 | 2014-06-25 14:33 | PAYNE - 36RAC1S8C | 84 | 12.7 | Yes | Yes | 21 | 21 | 0 | 4D6760B39D7A4256BAD17163DA9B0C49 |  | R22 | Non-TXV |  | 15.12% | 0.84881 | 29.06% | [5 empty] | Non-TXV | 15.12%
Clovis | CA | 93612-1511 |  | 2014-06-05 | 2014-06-05 10:50 | 2014-06-05 11:07 | YORK - D1NA024N03606C | 54 | 7.3 | Yes | Yes | 22.1 | 16.3 | 5.8 | 6A691B96BED34831BAC02271FB453585 |  | R22 | Non-TXV |  | 13.52% | 0.86481 | 25.98% | [5 empty] | Non-TXV | 13.52%
Fresno | CA | 93725-1850 |  | 2014-06-17 | 2014-06-17 09:52 | 2014-06-17 09:57 | CARRIER - 38TRA048360 | 151 | 12.6 | Yes | Yes | 23 | 20.4 | 2.6 | 0A3C106F261F4470A3972F877C27B3A1 |  | R22 | TXV |  | 8.344% | 0.91656 | 16.04% | [5 empty] | TXV | 8.344%
Madera | CA | 93638-1914 |  | 2014-06-02 | 2014-06-02 14:26 | 2014-06-02 14:48 | OTHER - 100WR42A1NA | 55 | 9.4 | Yes | Yes | 14.4 | 16.6 | -2.2 | FEAD872986644D5AA2651C0A5159668B |  | R22 | Non-TXV |  | 17.09% | 0.82909 | 32.84% | [5 empty] | Non-TXV | 17.09%
Fresno | CA | 93726-3927 |  | 2014-08-15 | 2014-08-15 08:13 | 2014-08-15 08:30 | OTHER - UNK | 85 | 2.5 | Yes | Yes | 23 | 20.2 | 2.8 | 1793E347935F4F8F951316A440680E63 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Selma | CA | 93662-2947 |  | 2014-06-16 | 2014-06-16 09:27 | 2014-06-16 09:45 | GOODMAN - N/A | 90 | 6.2 | Yes | Yes | 24.9 | 19.9 | 5 | 147B983E2EAC4D29A95CBD6B5EE21659 |  | R22 | Non-TXV |  | 6.889% | 0.93111 | 13.24% | [5 empty] | Non-TXV | 6.889%
Fresno | CA | 93722-4673 |  | 2014-05-21 | 2014-05-21 20:23 | 2014-05-21 20:25 | OTHER - 7777UNK | 87 | 3.2 | Yes | Yes | 18.5 | 20.4 | -1.9 | CC353FA21C9547C2AB72B2364B67475C |  | R22 | Non-TXV |  | 3.678% | 0.96322 | 7.069% | [5 empty] | Non-TXV | 3.678%
Clovis | CA | 93612-5013 |  | 2014-06-05 | 2014-06-05 13:13 | 2014-06-05 13:30 | RHEEM - RRNAB030JK06X | 72 | 11.6 | Yes | Yes | 22.1 | 18.5 | 3.6 | 9DF18476E8DF461FABB0BF117297770B |  | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Fresno | CA | 93726-5522 |  | 2014-06-20 | 2014-06-20 11:21 | 2014-06-20 11:23 | YORK - D2NP036N05606A | 108 | 20.1 | Yes | Yes | 25.4 | 22.1 | 3.3 | 467A31ABC1EE451F9E1D6E3C5C40CD29 |  | R22 | Non-TXV |  | 18.61% | 0.81389 | 35.77% | [5 empty] | Non-TXV | 18.61%
Fresno | CA | 93711-0957 |  | 2014-05-26 | 2014-05-26 09:52 | 2014-05-26 10:18 | LENNOX - HS253111P | 129 | 22.8 | Yes | Yes | 20.4 | 18.8 | 1.6 | 33F73DE0D31F4DC0BE61DAEFADA6CDEA |  | R22 | Non-TXV |  | 17.67% | 0.82326 | 33.97% | [5 empty] | Non-TXV | 17.67%
Fresno | CA | 93711-1547 |  | 2014-05-26 | 2014-05-26 10:56 | 2014-05-26 11:12 | PAYNE - PY1PNB030060AAAA | 55 | 7.1 | Yes | Yes | 27.1 | 21.5 | 5.6 | B191A6AE131745A2B9FB6CD8D02228D5 |  | R22 | Non-TXV |  | 12.91% | 0.87091 | 24.81% | [5 empty] | Non-TXV | 12.91%
Fresno | CA | 93725-0907 |  | 2014-06-17 | 2014-06-17 08:48 | 2014-06-17 09:08 | BDP - 563CN030 | 102 | 13.7 | Yes | Yes | 26.3 | 20.7 | 5.7 | EDD7FB80547F4CF1BA6F257553DFEA1D |  | R22 | TXV |  | 13.43% | 0.86569 | 25.81% | [5 empty] | TXV | 13.43%
Fresno | CA | 93722-4394 |  | 2014-06-14 | 2014-06-14 12:17 | 2014-06-14 12:37 | RHEEM - RAKA0042JAZ | 79 | 19.2 | Yes | Yes | 21.3 | 21.3 | 0 | 82D09B1629094A1AA769B65CA1B79775 |  | R22 | Non-TXV |  | 24.3% | 0.75696 | 46.71% | [5 empty] | Non-TXV | 24.3%
Clovis | CA | 93619-9247 |  | 2014-06-26 | 2014-06-26 13:54 | 2014-06-26 14:18 | LENNOX - 13AC-060-230-02 | 214 | 10.7 | Yes | Yes | 19.9 | 21.5 | -1.6 | B350ADC108BC4091BC9C3CB821C0E6DA |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Kerman | CA | 93630-2008 |  | 2014-06-18 | 2014-06-18 13:47 | 2014-06-18 14:05 | LENNOX - 12ACB364P | 103 | 16.6 | Yes | Yes | 23.3 | 23.1 | 0.2 | B13654F32D9A47E3852304C58E022370 |  | R22 | Non-TXV |  | 16.12% | 0.83883 | 30.97% | [5 empty] | Non-TXV | 16.12%
Fresno | CA | 93726-0403 |  | 2014-05-27 | 2014-05-27 14:24 | 2014-05-27 14:51 | ICP - PGAA36C1K3 | 81 | 4 | Yes | Yes | 25.9 | 23 | 2.9 | F9C7789B670A4111A9A45BEFEC344A5A |  | R22 | Non-TXV |  | 4.938% | 0.95062 | 9.49% | [5 empty] | Non-TXV | 4.938%
Fresno | CA | 93725-1873 |  | 2014-06-17 | 2014-06-17 11:33 | 2014-06-17 11:58 | LENNOX - HS253111P | 129 | 18.4 | Yes | Yes | 20.9 | 20.1 | 0.8 | 760A7273392340DA9FE5226CB696EA22 |  | R22 | Non-TXV |  | 14.26% | 0.85736 | 27.41% | [5 empty] | Non-TXV | 14.26%
Stockton | CA | 95206-6332 |  | 2014-06-07 | 2014-06-07 10:49 | 2014-06-07 11:22 | YORK - H1RA042S06D | 84 | 2.9 | Yes | Yes | 21.3 | 20.8 | 0.5 | 2AC28F14CD0A4F1BB6665C40E161067F |  | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Manteca | CA | 95336-4152 |  | 2014-05-14 | 2014-05-14 12:39 | 2014-05-14 13:05 | BRYANT - 561CJ036-D | 105 | 7.4 | Yes | Yes | 19 | 20.4 | -1.4 | 6A075A6EA0C449A0824311D05B0C7952 |  | R22 | TXV |  | 7.048% | 0.92952 | 13.54% | [5 empty] | TXV | 7.048%
Stockton | CA | 95204-2521 |  | 2014-06-03 | 2014-06-03 08:51 | 2014-06-03 09:09 | RUUD - URMA-A048JK10E | 117 | -8.3 | Yes | Yes | 24 | 18.7 | 5.3 | 5F9C9BBAC18C4FEDA52AEE2964008062 |  | R22 | Non-TXV |  | -7.094% | 1.0709 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.094%
Tracy | CA | 95376-1304 |  | 2014-05-29 | 2014-05-29 09:59 | 2014-05-29 10:24 | PAYNE - PA12NA042-H | 101 | -5.8 | Yes | Yes | 21 | 20.9 | 0.1 | 1F4A21AAF96743E18F75F864FA037201 |  | R22 | TXV |  | -5.743% | 1.0574 | 1.608% |  |  |  |  | TXV |  |  | -5.743%
Tracy | CA | 95376-8113 |  | 2014-05-29 | 2014-05-29 12:09 | 2014-05-29 12:38 | GOODMAN - GPH1336M41AB | 85 | 3.6 | Yes | Yes | 21.7 | 22 | -0.3 | 864813DB5B854336A3792CB9F5E76003 |  | R410A | TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | TXV | 4.235%
Manteca | CA | 95336-6921 |  | 2014-06-03 | 2014-06-03 15:30 | 2014-06-03 15:54 | DAY & NIGHT - 585GJ030040 | 58 | 5.6 | Yes | Yes | 24.8 | 19.9 | 4.9 | EBC05C59187148F28EE247512AD1AB34 |  | R22 | Non-TXV |  | 9.655% | 0.90345 | 18.56% | [5 empty] | Non-TXV | 9.655%
Manteca | CA | 95336-6922 |  | 2014-05-15 | 2014-05-15 08:49 | 2014-05-15 09:10 | CARRIER - 48GXN048090311 | 131 | 6.5 | Yes | Yes | 23 | 20.9 | 2.1 | E9C8593AFBF54B97AAA3275CACDB9ADB |  | R22 | Non-TXV |  | 4.962% | 0.95038 | 9.536% | [5 empty] | Non-TXV | 4.962%
Stockton | CA | 95210-1115 |  | 2014-05-15 | 2014-05-15 11:56 | 2014-05-15 12:19 | YORK - H2RD036S06B | 96 | 17.2 | Yes | Yes | 26.6 | 20.9 | 5.7 | 248768464D374247BC4A3DE5D04BB727 |  | R22 | Non-TXV |  | 17.92% | 0.82083 | 34.43% | [5 empty] | Non-TXV | 17.92%
Tracy | CA | 95376-2317 |  | 2014-06-02 | 2014-06-02 14:19 | 2014-06-02 14:41 | RHEEM - AT-30B10 | 85 | 16.1 | Yes | Yes | 22.2 | 21.4 | 0.8 | 8414518E658C47F584D15FDE621A6646 |  | R22 | Non-TXV |  | 18.94% | 0.81059 | 36.4% | [5 empty] | Non-TXV | 18.94%
Manteca | CA | 95336-3306 |  | 2014-05-27 | 2014-05-27 08:16 | 2014-05-27 08:36 | TRANE - TTY030A100A2 | 85 | -6 | Yes | Yes | 20.9 | 19.8 | 1.1 | CA3924C08FBF49C69861FB08CEFC5A79 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Manteca | CA | 95336-9236 |  | 2014-05-16 | 2014-05-16 13:55 | 2014-05-16 14:28 | GOODMAN - CKT60-1A | 85 | -4.9 | Yes | Yes | 21.5 | 22.6 | -1.1 | 3D826BAAD3114391B3C2D405F37BE6D6 |  | R22 | Non-TXV |  | -5.765% | 1.0576 | 1.614% |  |  |  |  | Non-TXV |  |  | -5.765%
Tracy | CA | 95376-1468 |  | 2014-05-21 | 2014-05-21 10:07 | 2014-05-21 10:34 | HEIL - ACS048A2B2 | 85 | 11.7 | Yes | Yes | 18.4 | 19.9 | -1.5 | 0FF025D12B47490BBE260CAAECA20222 |  | R22 | Non-TXV |  | 13.76% | 0.86235 | 26.45% | [5 empty] | Non-TXV | 13.76%
Stockton | CA | 95209-1735 |  | 2014-05-13 | 2014-05-13 10:15 | 2014-05-13 10:15 | HEIL - N4A330AKC200 | 74 | 0 | Yes | Yes | 19.4 | 19.8 | -0.4 | A7EA298EF61147FB9B80E40FD6CFB1EC |  | R410A | TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-8772 |  | 2014-05-27 | 2014-05-27 10:56 | 2014-05-27 11:25 | CARRIER - 24ABA336A310 | 85 | 4.4 | Yes | Yes | 22.9 | 21 | 1.9 | 2DFF89A32B6247D6A92EC18CCEC1D54A |  | R410A | TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | TXV | 5.176%
Stockton | CA | 95204-5209 |  | 2014-06-06 | 2014-06-06 09:23 | 2014-06-06 09:48 | GOODMAN - CKL36-1K | 84 | -5.9 | Yes | Yes | 22.4 | 19.9 | 2.5 | B7974D2C9F6440E0800E2504F60E3DF9 |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Stockton | CA | 95206-6155 |  | 2014-06-07 | 2014-06-07 10:17 | 2014-06-07 10:38 | CARRIER - 38CKC030340 | 89 | -6.6 | Yes | Yes | 22.7 | 20.6 | 2.1 | F87A2344F96040889D357BC6F3EDBDA5 |  | R22 | TXV |  | -7.416% | 1.0742 | 2.077% |  |  |  |  | TXV |  |  | -7.416%
Stockton | CA | 95209-2344 |  | 2014-05-14 | 2014-05-14 13:18 | 2014-05-14 13:23 | GUARDIAN - GCGD24S41S3A | 61 | 3.4 | Yes | Yes | 15.9 | 18.3 | -2.4 | 205AE5EEF3ED43D59EFD2F6202DF584C |  | R410A | TXV |  | 5.574% | 0.94426 | 10.71% | [5 empty] | TXV | 5.574%
Stockton | CA | 95205-2607 |  | 2014-06-12 | 2014-06-12 12:12 | 2014-06-12 12:29 | HEIL - PGC036K080B | 71 | -4.2 | Yes | Yes | 18.6 | 18.2 | 0.4 | 1D4F3236F52A4E03B8986798EEEFBA83 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Stockton | CA | 95210-1221 |  | 2014-05-15 | 2014-05-15 12:47 | 2014-05-15 13:10 | OTHER - UNK | 64 | 15 | Yes | Yes | 21.1 | 23.3 | -2.2 | 79F813CE56F44AE6B870F533F1A29F84 |  | R22 | Non-TXV |  | 23.44% | 0.76562 | 45.04% | [5 empty] | Non-TXV | 23.44%
Stockton | CA | 95210-1710 |  | 2014-05-16 | 2014-05-16 12:46 | 2014-05-16 12:46 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 26 | 20.1 | 5.9 | 5C17B91D61B242A6A977189497255BC1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1443 |  | 2014-05-20 | 2014-05-20 15:10 | 2014-05-20 15:36 | DAY & NIGHT - PGD336090K001C1 | 100 | 4.8 | Yes | Yes | 21 | 19.1 | 1.9 | 1A4D26217E2D4F7DAB0D61B7E5333345 |  | R410A | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Stockton | CA | 95204-2129 |  | 2014-06-12 | 2014-06-12 12:43 | 2014-06-12 12:59 | DAY & NIGHT - 36100YAC108T | 70 | -4.1 | Yes | Yes | 25.2 | 19.5 | 5.7 | 3438212044AA47FBAAD69D81E7953878 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Manteca | CA | 95336-3641 |  | 2014-06-27 | 2014-06-27 12:44 | 2014-06-27 13:04 | AMANA - PGD36C0702E | 85 | 9.6 | Yes | Yes | 23 | 20.8 | 2.2 | CF2FE2D3F14344119D652963E62DC54C |  | R22 | Non-TXV |  | 11.29% | 0.88706 | 21.7% | [5 empty] | Non-TXV | 11.29%
Fresno | CA | 93726-6734 |  | 2014-06-24 | 2014-06-24 08:20 | 2014-06-24 08:22 | BDP - 588ANW036060ADAF | 72 | 3.5 | Yes | Yes | 19 | 21.5 | -2.5 | 08513691108247EC9E82002EAD8F626C |  | R22 | Non-TXV |  | 4.861% | 0.95139 | 9.342% | [5 empty] | Non-TXV | 4.861%
Oroville | CA | 95965-3583 |  | 2014-05-27 | 2014-05-27 08:02 | 2014-05-27 08:38 | YORK - H1RA048S06G | 117 | 3.6 | Yes | Yes | 24.5 | 20.4 | 4.1 | FFED27E77BCB46589349BB9FE7572851 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95206-6046 |  | 2014-06-05 | 2014-06-05 08:14 | 2014-06-05 08:37 | YORK - AC036X1221A | 98 | -9.2 | Yes | Yes | 18.1 | 20.4 | -2.3 | 549E786997F24A759BF3AEBB400E6ECC |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Paradise | CA | 95969-2380 |  | 2014-06-11 | 2014-06-11 16:14 | 2014-06-11 16:31 | YORK - CMB06011A | 243 | 7.7 | Yes | Yes | 23.7 | 20.2 | 3.5 | A48F55D46B1246B4830997D1935A243A |  | R22 | Non-TXV |  | 3.169% | 0.96831 | 6.09% | [5 empty] | Non-TXV | 3.169%
Chico | CA | 95926-3479 |  | 2014-05-20 | 2014-05-20 08:50 | 2014-05-20 09:01 | LENNOX - GCS20RV-411-100-1P | 68 | 3.4 | Yes | Yes | 21 | 21.2 | -0.2 | E078DC30682C42A6B5E333CB13B3C879 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Gridley | CA | 95948-9519 |  | 2014-05-30 | 2014-05-30 09:22 | 2014-05-30 09:39 | TRANE - 2TTX4036B1000AA | 118 | 3.6 | Yes | Yes | 23 | 19.5 | 3.5 | 93CBF6E5B309475090E073F47248E474 |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Manteca | CA | 95336-3641 |  | 2014-06-27 | 2014-06-27 12:12 | 2014-06-27 12:37 | PAYNE - PY3GNAA30060NA | 98 | 11 | Yes | Yes | 22.4 | 20.1 | 2.3 | 65F38820E1D94F1187CF34FAAB4EFA06 |  | R410A | TXV |  | 11.22% | 0.88776 | 21.57% | [5 empty] | TXV | 11.22%
Manteca | CA | 95336-2556 |  | 2014-05-14 | 2014-05-14 10:10 | 2014-05-14 10:38 | TRANE - BTD736A100A0 | 88 | 6.1 | Yes | Yes | 19.3 | 20.7 | -1.4 | 29C756B5889A4CD485CAD50E609B36B5 |  | R22 | Non-TXV |  | 6.932% | 0.93068 | 13.32% | [5 empty] | Non-TXV | 6.932%
Stockton | CA | 95204-4102 |  | 2014-06-03 | 2014-06-03 11:54 | 2014-06-03 12:11 | PAYNE - PY3GNAA30060NA | 99 | 4.1 | Yes | Yes | 16.7 | 18.8 | -2.1 | FE4859180AB3473AB60DDF7CB5FA4F52 |  | R410A | Non-TXV |  | 4.141% | 0.95859 | 7.959% | [5 empty] | Non-TXV | 4.141%
Stockton | CA | 95206-6148 |  | 2014-06-05 | 2014-06-05 11:46 | 2014-06-05 12:13 | GOODMAN - CLJ48-1 | 85 | 2.9 | Yes | Yes | 22.4 | 20.7 | 1.7 | 7344F675BF544AE6BCAAFA50315B285F |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Stockton | CA | 95209-3922 |  | 2014-06-03 | 2014-06-03 11:58 | 2014-06-03 11:58 | BRYANT - PA13NR42-J | 85 | 0 | Yes | Yes | 29.2 | 23.7 | 5.5 | CCC175646EC143C4B1F365284435751B |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-3125 |  | 2014-06-06 | 2014-06-06 11:32 | 2014-06-06 11:51 | GOODMAN - CKL-36 | 102 | 13 | Yes | Yes | 22.5 | 19.9 | 2.6 | 74474FA101B34251B013C2B74D835D8A |  | R22 | Non-TXV |  | 12.75% | 0.87255 | 24.49% | [5 empty] | Non-TXV | 12.75%
Stockton | CA | 95209-2654 |  | 2014-05-14 | 2014-05-14 15:34 | 2014-05-14 15:51 | HEIL - HAC236AKC4 | 114 | 11.7 | Yes | Yes | 25.1 | 20.4 | 4.7 | E43256D0033948E9AF96134607745AF6 |  | R22 | TXV |  | 10.26% | 0.89737 | 19.72% | [5 empty] | TXV | 10.26%
Stockton | CA | 95207-2202 |  | 2014-06-03 | 2014-06-03 10:12 | 2014-06-03 10:29 | PAYNE - 561CJ036-D | 84 | 2.6 | Yes | Yes | 17.5 | 19.1 | -1.6 | 7378B3CBE5B2495C9524170604749CDB |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Stockton | CA | 95212-3513 |  | 2014-06-19 | 2014-06-19 16:09 | 2014-06-19 16:28 | CARRIER - UNK | 70 | 9.7 | Yes | Yes | 24.5 | 24.8 | -0.3 | B5B307689E0D408A98F40B11C53798B4 |  | R22 | Non-TXV |  | 13.86% | 0.86143 | 26.63% | [5 empty] | Non-TXV | 13.86%
Stockton | CA | 95206-6022 |  | 2014-06-07 | 2014-06-07 09:36 | 2014-06-07 10:03 | BRYANT - 561CJ024-C | 114 | 7.9 | Yes | Yes | 22.2 | 21 | 1.2 | C6A1DF3D8F1C4917A5018D8C81EFCB5D |  | R22 | TXV |  | 6.93% | 0.9307 | 13.32% | [5 empty] | TXV | 6.93%
Stockton | CA | 95204-2023 |  | 2014-06-02 | 2014-06-02 12:37 | 2014-06-02 12:58 | YORK - D2NP036N05606A | 108 | 3.8 | Yes | Yes | 25.4 | 21.4 | 4 | 26161656F6864F7FA96FB763B8BCF227 |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Stockton | CA | 95210-1504 |  | 2014-05-16 | 2014-05-16 09:06 | 2014-05-16 09:23 | AMERICAN STANDARD - YCC030F1M0BH | 69 | 8.3 | Yes | Yes | 20.4 | 20.4 | 0 | 676A3EC145614CDEBC745676ED6B29C4 |  | R22 | Non-TXV |  | 12.03% | 0.87971 | 23.12% | [5 empty] | Non-TXV | 12.03%
Fresno | CA | 93722-8309 |  | 2014-05-22 | 2014-05-22 12:11 | 2014-05-22 12:13 | YORK - H1RA048S06D | 117 | 5.5 | Yes | Yes | 21 | 21.5 | -0.5 | 0DFFE44E9CC74EA2A34396606647BAA4 |  | R22 | Non-TXV |  | 4.701% | 0.95299 | 9.034% | [5 empty] | Non-TXV | 4.701%
Fresno | CA | 93727-5408 |  | 2014-07-16 | 2014-07-16 13:37 | 2014-07-16 13:39 | YORK - H2RD02406B | 88 | 5 | Yes | Yes | 19.1 | 20.8 | -1.7 | 9397A240C4D448D9906F39CEBED48481 |  | R22 | Non-TXV |  | 5.682% | 0.94318 | 10.92% | [5 empty] | Non-TXV | 5.682%
Fresno | CA | 93704-1440 |  | 2014-06-13 | 2014-06-13 10:19 | 2014-06-13 10:36 | OTHER - PY3GNAA24060NA | 72 | 9.3 | Yes | Yes | 23.5 | 21 | 2.5 | 222FFCC55E7F42E2995C2BC606D709BA |  | R410A | Non-TXV |  | 12.92% | 0.87083 | 24.82% | [5 empty] | Non-TXV | 12.92%
Fresno | CA | 93726-1105 |  | 2014-05-23 | 2014-05-23 13:42 | 2014-05-23 14:01 | PAYNE - 36/80 YAC 108-C | 66 | 2.1 | Yes | Yes | 24.8 | 18.9 | 6 | B50FE25EA1BF429BA524F92AF54AACE9 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Fresno | CA | 93702-1539 |  | 2014-05-20 | 2014-05-20 10:46 | 2014-05-20 11:05 | NORDYNE - N/A | 120 | 3.6 | Yes | Yes | 19.3 | 20.9 | -1.6 | 794D7A8DF343419CA390882BF7E69713 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-5159 |  | 2014-08-16 | 2014-08-16 10:03 | 2014-08-16 10:04 | CARRIER - 48KLA36300BE | 102 | 11.5 | Yes | Yes | 19.7 | 15.9 | 3.8 | BBD261CDAC72437BB7E23FC92344DE62 |  | R22 | Non-TXV |  | 11.27% | 0.88725 | 21.67% | [5 empty] | Non-TXV | 11.27%
Yuba City | CA | 95991-8857 |  | 2014-05-16 | 2014-05-16 08:48 | 2014-05-16 09:04 | CARRIER - 38TXA048330 | 148 | 10.3 | Yes | Yes | 26 | 21.2 | 4.8 | 7848BB25496B4A04BB6FC8199D92C57E |  | R410A | TXV |  | 6.959% | 0.93041 | 13.37% | [5 empty] | TXV | 6.959%
Chico | CA | 95926-2048 |  | 2014-05-15 | 2014-05-15 10:34 | 2014-05-15 11:06 | DAY & NIGHT - NA | 60 | 3.8 | Yes | Yes | 20.8 | 19.3 | 1.5 | 84F7F3EE7EC448029D7BF9DD28C2AFB4 |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Atwater | CA | 95301-2653 |  | 2014-05-15 | 2014-05-15 13:52 | 2014-05-15 13:54 | GOODMAN - CPLE18-1C | 88 | 5.5 | Yes | Yes | 16.3 | 18.2 | -1.9 | CA536977ACEF4AC58C6658EA76CDBC5A |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fresno | CA | 93702-2335 |  | 2014-05-21 | 2014-05-21 10:16 | 2014-05-21 10:43 | YORK - DBYP-F024N045A | 100 | 4.4 | Yes | Yes | 22 | 19.9 | 2.1 | D44BFB83F1E94144950C4FF8EF53BAC2 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Ripon | CA | 95366-2413 |  | 2014-07-17 | 2014-07-17 13:27 | 2014-07-17 13:47 | OTHER - UNK | 85 | 3.2 | Yes | Yes | 24.5 | 19.3 | 5.2 | 5DDC8CD757F54AEF9615F536D0452337 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Fresno | CA | 93727-5518 |  | 2014-06-05 | 2014-06-05 13:21 | 2014-06-05 13:52 | YORK - D2NP042N06506NXA | 150 | 22.9 | Yes | Yes | 15.6 | 16.3 | -0.7 | B533F35480E04735A637DD9EAE982884 |  | R22 | Non-TXV |  | 15.27% | 0.84733 | 29.34% | [5 empty] | Non-TXV | 15.27%
Fresno | CA | 93727-4867 |  | 2014-06-25 | 2014-06-25 07:54 | 2014-06-25 07:55 | BDP - 585HJ024040 | 68 | 2.6 | Yes | Yes | 22.2 | 22.1 | 0.1 | DAD1417D1E8E482380A74B823E1BD7F7 |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Riverbank | CA | 95367-3129 |  | 2014-05-20 | 2014-05-20 11:18 | 2014-05-20 11:47 | HEIL - N2A36AKB300 | 120 | 6.6 | Yes | Yes | 19.8 | 21.9 | -2.1 | C4EFD4B8A9D646D3B299B648CA682092 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Paradise | CA | 95969-6211 |  | 2014-05-22 | 2014-05-22 13:53 | 2014-05-22 15:18 | GOODMAN - GPG153709041AC | 112 | 7.6 | Yes | Yes | 22 | 20.4 | 1.6 | 7E748B2F027C4F2F8D0FB96A0CF59E1D |  | R410A | TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | TXV | 6.786%
Fresno | CA | 93720-2792 |  | 2014-06-04 | 2014-06-04 13:09 | 2014-06-04 13:33 | HEIL - NRGF36DDB04 | 90 | 18.2 | Yes | Yes | 20.8 | 20.2 | 0.6 | 6C257BDD6038409587BAE4C5C7ED0829 |  | R22 | Non-TXV |  | 20.22% | 0.79778 | 38.86% | [5 empty] | Non-TXV | 20.22%
Yuba City | CA | 95991-6730 |  | 2014-06-24 | 2014-06-24 12:31 | 2014-06-24 12:51 | TRANE - 2TTB3048A1000AA | 142 | 4.5 | Yes | Yes | 27 | 22 | 5 | ADD2DC4E3DED403AB5FC4D5B13CFB599 |  | R22 | Non-TXV |  | 3.169% | 0.96831 | 6.09% | [5 empty] | Non-TXV | 3.169%
Sanger | CA | 93657-2033 |  | 2014-07-23 | 2014-07-23 09:40 | 2014-07-23 10:08 | CARRIER - 48GX-042090301AD | 118 | 6.1 | Yes | Yes | 19.4 | 21 | -1.6 | A69EF3E92EFF4D1BA0FE94AE6948D138 |  | R22 | Non-TXV |  | 5.169% | 0.94831 | 9.935% | [5 empty] | Non-TXV | 5.169%
Fresno | CA | 93727-3634 |  | 2014-07-08 | 2014-07-08 12:01 | 2014-07-08 12:22 | LENNOX - 10GCS036-75-2PA | 58 | 4.9 | Yes | Yes | 22.3 | 21 | 1.3 | 90AD2B702FF84A45948F6B434715F250 |  | R22 | Non-TXV |  | 8.448% | 0.91552 | 16.24% | [5 empty] | Non-TXV | 8.448%
Dinuba | CA | 93618-4013 |  | 2014-07-29 | 2014-07-29 13:26 | 2014-07-29 13:46 | PAYNE - PY3GNAA24040 | 72 | 2.9 | Yes | Yes | 19.2 | 21.3 | -2.1 | 81289F4C815747A2BB7E1E4080253FA0 |  | R410A | TXV |  | 4.028% | 0.95972 | 7.741% | [5 empty] | TXV | 4.028%
Sanger | CA | 93657-8779 |  | 2014-08-19 | 2014-08-19 12:45 | 2014-08-19 13:12 | UNITARY PRODUCTS GROUP - H2RD043S06B | 141 | 4.5 | Yes | Yes | 19.1 | 21.5 | -2.4 | 31725C5C33B947B3BD625D072059EF82 |  | R22 | Non-TXV |  | 3.191% | 0.96809 | 6.133% | [5 empty] | Non-TXV | 3.191%
Fresno | CA | 93703-1143 |  | 2014-05-23 | 2014-05-23 16:13 | 2014-05-23 17:30 | CARRIER - 593ANX042000ABAA | 102 | 10.1 | Yes | Yes | 19 | 20.2 | -1.2 | EA757822ADD04B038ADFC9AD4E49A733 |  | R22 | Non-TXV |  | 9.902% | 0.90098 | 19.03% | [5 empty] | Non-TXV | 9.902%
Sanger | CA | 93657-8769 |  | 2014-06-21 | 2014-06-21 13:19 | 2014-06-21 13:44 | LENNOX - 13GCSXA-42-083X-230-1A | 181 | 5.8 | Yes | Yes | 22 | 21.4 | 0.6 | 5C7000ED00294589B299A7A2FBD60C8D |  | R410A | Non-TXV |  | 3.204% | 0.96796 | 6.158% | [5 empty] | Non-TXV | 3.204%
Fresno | CA | 93727-3344 |  | 2014-06-03 | 2014-06-03 14:49 | 2014-06-03 15:10 | TRANE - N/A | 90 | 4.5 | Yes | Yes | 22.4 | 20.1 | 2.3 | 99B390B1F17E4CEA8F3524FD6469F077 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Clovis | CA | 93619-8636 |  | 2014-06-14 | 2014-06-14 15:36 | 2014-06-14 15:54 | ICP - PGF036K060A | 71 | 18.1 | Yes | Yes | 20.6 | 20.8 | -0.2 | DB16323A22A54DAB87868DE6AD716042 |  | R22 | Non-TXV |  | 25.49% | 0.74507 | 48.99% | [5 empty] | Non-TXV | 25.49%
Clovis | CA | 93619-8636 |  | 2014-06-14 | 2014-06-14 21:31 | 2014-06-14 22:35 | ICP - PGF036K060A | 71 | 16.4 | Yes | Yes | 22.7 | 23.1 | -0.4 | 822DB5CD82E940B687D7D0BAA75B3B17 |  | R22 | Non-TXV |  | 23.1% | 0.76901 | 44.39% | [5 empty] | Non-TXV | 23.1%
Fresno | CA | 93727-3633 |  | 2014-06-04 | 2014-06-04 12:05 | 2014-06-04 12:36 | LENNOX - 10GCS042-75-2PA | 73 | 7.6 | Yes | Yes | 23.7 | 23.6 | 0.1 | 05D312AB854D48B6AFA9950A88DE2977 |  | R22 | Non-TXV |  | 10.41% | 0.89589 | 20.01% | [5 empty] | Non-TXV | 10.41%
Atascadero | CA | 93422-6807 |  | 2014-08-14 | 2014-08-14 09:10 | 2014-08-14 09:31 | PAYNE - PA10JA024-A | 70 | 2.3 | Yes | Yes | 16.5 | 18.2 | -1.7 | 2ECAF8E938654D998E3647D8AD85E67A |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Sanger | CA | 93657-8768 |  | 2014-06-18 | 2014-06-18 12:18 | 2014-06-18 12:46 | LENNOX - 13GCSXA-42-083X-230-1A | 181 | 9.4 | Yes | Yes | 21.3 | 21.4 | -0.1 | B66763F2DB794470B07C81640A4136A6 |  | R410A | TXV |  | 5.193% | 0.94807 | 9.981% | [5 empty] | TXV | 5.193%
Fresno | CA | 93703-4074 |  | 2014-05-20 | 2014-05-20 12:24 | 2014-05-20 12:53 | RUUD - URKA-A030JK06E | 54 | 12.1 | Yes | Yes | 18.3 | 20.1 | -1.8 | E04537B970704C1CABAD55B7ED3DFCC1 |  | R22 | Non-TXV |  | 22.41% | 0.77593 | 43.06% | [5 empty] | Non-TXV | 22.41%
Fresno | CA | 93726-5035 |  | 2014-05-29 | 2014-05-29 12:22 | 2014-05-29 13:07 | CARRIER - N/A | 60 | 6 | Yes | Yes | 23.6 | 21.9 | 1.7 | 41211282E0EA48BA998AA8252899B011 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Sanger | CA | 93657-8771 |  | 2014-06-18 | 2014-06-18 13:37 | 2014-06-18 14:02 | LENNOX - 13GCSA-42-230-1A | 122 | 9.6 | Yes | Yes | 20.9 | 22.1 | -1.2 | 67D927F5684F4E1CB0614B353482A511 |  | R22 | Non-TXV |  | 7.869% | 0.92131 | 15.12% | [5 empty] | Non-TXV | 7.869%
Fresno | CA | 93727-7974 |  | 2014-06-07 | 2014-06-07 16:55 | 2014-06-07 17:29 | GOODMAN - PGB036075-1A | 60 | 6 | Yes | Yes | 19.5 | 21 | -1.5 | C70097A3145049E78AF207D4CB6430A2 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Manteca | CA | 95337-8740 |  | 2014-05-16 | 2014-05-16 08:30 | 2014-05-16 08:46 | YORK - H2RD060S06B | 162 | 8.6 | Yes | Yes | 19.5 | 20.2 | -0.7 | 066043DA272D4844B9ACC58585546F70 |  | R22 | TXV |  | 5.309% | 0.94691 | 10.2% | [5 empty] | TXV | 5.309%
Fresno | CA | 93728-3800 |  | 2014-07-30 | 2014-07-30 07:44 | 2014-07-30 08:03 | UNITARY PRODUCTS GROUP - DCYZ-F024N045A | 58 | 2.1 | Yes | Yes | 18.9 | 20.4 | -1.5 | 468442DD48F146EABB063EBC30425D0E |  | R410A | TXV |  | 3.621% | 0.96379 | 6.958% | [5 empty] | TXV | 3.621%
Fresno | CA | 93727-6838 |  | 2014-06-06 | 2014-06-06 12:44 | 2014-06-06 13:07 | RHEEM - URKA-A036JK06E | 62 | 7.5 | Yes | Yes | 22.7 | 22.4 | 0.3 | 74008A5B31BC40848508A36665ECEF44 |  | R22 | Non-TXV |  | 12.1% | 0.87903 | 23.25% | [5 empty] | Non-TXV | 12.1%
Manteca | CA | 95336-3459 |  | 2014-05-14 | 2014-05-14 09:32 | 2014-05-14 09:53 | GOODMAN - PGB036100-1A REV A | 85 | 6.8 | Yes | Yes | 17.2 | 18.8 | -1.6 | AB357168D2924B8991BF5BA9764B8B2E |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Fresno | CA | 93725-1868 |  | 2014-07-25 | 2014-07-25 11:42 | 2014-07-25 11:43 | LENNOX - HS253111P | 129 | 12.1 | Yes | Yes | 18.9 | 19 | -0.1 | 802643110A714026B5E36ACBE82EBE2C |  | R22 | Non-TXV |  | 9.38% | 0.9062 | 18.03% | [5 empty] | Non-TXV | 9.38%
Fresno | CA | 93726-5036 |  | 2014-06-24 | 2014-06-24 10:09 | 2014-06-24 10:10 | DAY & NIGHT - UNK | 56 | 11.9 | Yes | Yes | 23.5 | 20.4 | 3.1 | D6A0776D0F02416CA15ACD24DE5AAE56 |  | R22 | Non-TXV |  | 21.25% | 0.7875 | 40.84% | [5 empty] | Non-TXV | 21.25%
Rescue | CA | 95672-9474 |  | 2014-09-20 | 2014-09-20 09:01 | 2014-09-20 09:29 | BRYANT - 583BNW042090NC | 144 | 4.6 | Yes | Yes | 20 | 18.2 | 1.8 | 113CE72D3CA94E41A7B5DAC2FB8468F7 |  | R410A | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Cameron Park | CA | 95682-8558 |  | 2014-06-03 | 2014-06-03 15:32 | 2014-06-03 15:53 | GE - UNK | 75 | 2.3 | Yes | Yes | 24 | 21 | 3 | 60D865B6B8134853A0FA99C584CB2831 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Cameron Park | CA | 95682-9263 |  | 2014-08-01 | 2014-08-01 15:16 | 2014-08-01 15:43 | LENNOX - HS26-036-3P | 90 | 3.3 | Yes | Yes | 18 | 21 | -3 | 9587B63DA4954559B40113C0EAAABB56 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Placerville | CA | 95667-4716 |  | 2014-06-03 | 2014-06-03 09:11 | 2014-06-03 09:28 | LENNOX - 12GCS030X | 85 | 3 | Yes | Yes | 24.7 | 21.7 | 3 | 9025BF8232244030A321BC5D9E4C2326 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Placerville | CA | 95667-4716 |  | 2014-06-03 | 2014-06-03 09:29 | 2014-06-03 09:45 | LENNOX - 12GCS030X-75-3PA | 85 | 2.5 | Yes | Yes | 25 | 20.4 | 4.6 | 315116F4A036483B8B06D018DD6B6749 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Placerville | CA | 95667-8198 |  | 2014-07-11 | 2014-07-11 13:09 | 2014-07-11 13:31 | FRIGIDAIRE - FS3BC-042K | 125 | 4.2 | Yes | Yes | 27 | 21.5 | 5.5 | 77539DFA4E58421AA09448560B192699 |  | R22 | Non-TXV |  | 3.36% | 0.9664 | 6.457% | [5 empty] | Non-TXV | 3.36%
Fresno | CA | 93710-7124 |  | 2014-09-20 | 2014-09-20 10:20 | 2014-09-20 10:22 | CARRIER - 38BRB036310 | 122 | 5.7 | Yes | Yes | 18.7 | 17.6 | 1.1 | 212394DB2A954012BE941167BDA66D81 |  | R22 | Non-TXV |  | 4.672% | 0.95328 | 8.979% | [5 empty] | Non-TXV | 4.672%
Fresno | CA | 93704-4061 |  | 2014-06-13 | 2014-06-13 15:00 | 2014-06-13 15:17 | OTHER - UNK | 56 | 10.4 | Yes | Yes | 16.7 | 18.5 | -1.8 | 6CF1BF2CBD2F44819F7E91FB1239564D |  | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Fresno | CA | 93727-4859 |  | 2014-06-24 | 2014-06-24 13:17 | 2014-06-24 13:19 | BDP - 585HJ024040 | 68 | 2.5 | Yes | Yes | 25.5 | 19.5 | 6 | 3CCC0115C9854062B3E7F8B6C1FFFAA0 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Fresno | CA | 93727-4865 |  | 2014-06-25 | 2014-06-25 10:03 | 2014-06-25 10:05 | BDP - 585HJ024040 | 68 | 2.6 | Yes | Yes | 21.5 | 19.9 | 1.6 | 6C651B0407E64898BB6EAF7AE70873D6 |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Fresno | CA | 93727-4868 |  | 2014-06-24 | 2014-06-24 13:14 | 2014-06-24 13:16 | BDP - 585HJ024040 | 68 | 2 | Yes | Yes | 19.8 | 19.3 | 0.5 | 8FAF5AE012534A28A7366BC250AF5F62 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93727-3032 |  | 2014-06-03 | 2014-06-03 13:47 | 2014-06-03 14:26 | GOODMAN - PGB042075-1 | 68 | 2.6 | Yes | Yes | 22.1 | 22.1 | 0 | AA7D5A6A508F4385933BE2135CF516CE |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Fresno | CA | 93702-3837 |  | 2014-07-09 | 2014-07-09 14:04 | 2014-07-09 14:23 | ARCOAIRE - PGF348080K01A1 | 94 | 3.6 | Yes | Yes | 22.7 | 22.1 | 0.6 | 39E36855B03C4C1BA801BB6058762080 |  | R22 | Non-TXV |  | 3.83% | 0.9617 | 7.36% | [5 empty] | Non-TXV | 3.83%
Clovis | CA | 93611-2015 |  | 2014-05-30 | 2014-05-30 12:12 | 2014-05-30 12:14 | CARRIER - 7777UNK | 94 | 5.1 | Yes | Yes | 22.5 | 22.5 | 0 | EC183DB264A443CCABC13E78B7EB7441 |  | R22 | Non-TXV |  | 5.426% | 0.94574 | 10.43% | [5 empty] | Non-TXV | 5.426%
Fresno | CA | 93727-7932 |  | 2014-07-10 | 2014-07-10 12:28 | 2014-07-10 12:29 | PAYNE - PY3PNA030040NA | 130 | 27.8 | Yes | Yes | 30 | 25.1 | 5 | B047A471305F40A9B61A265ABFC65746 |  | R22 | Non-TXV |  | 21.38% | 0.78615 | 41.1% | [5 empty] | Non-TXV | 21.38%
Fresno | CA | 93727-3536 |  | 2014-06-27 | 2014-06-27 09:15 | 2014-06-27 09:35 | LENNOX - 10GCS042-100-3PA | 73 | 4.4 | Yes | Yes | 25.9 | 21.5 | 4.4 | BB10C39EAD464F69A8060D4CA683BE1F |  | R22 | Non-TXV |  | 6.027% | 0.93973 | 11.58% | [5 empty] | Non-TXV | 6.027%
Clovis | CA | 93619-0000 |  | 2014-06-26 | 2014-06-26 09:35 | 2014-06-26 09:57 | BRYANT - 114ANA042-A | 164 | 11.8 | Yes | Yes | 19.3 | 20.9 | -1.6 | 3CA0B6D279364F8C9DF564ABC2AF40D4 |  | R410A | TXV |  | 7.195% | 0.92805 | 13.83% | [5 empty] | TXV | 7.195%
Fresno | CA | 93710-3901 |  | 2014-06-23 | 2014-06-23 10:00 | 2014-06-23 10:25 | CARRIER - 48SX-042080321AA | 87 | 6.5 | Yes | Yes | 24.1 | 21.5 | 2.6 | E4F9F056C39943128D2812C3C277CDBF |  | R22 | Non-TXV |  | 7.471% | 0.92529 | 14.36% | [5 empty] | Non-TXV | 7.471%
Fresno | CA | 93726-7023 |  | 2014-05-29 | 2014-05-29 15:21 | 2014-05-29 15:42 | ICP - PGC048K080A | 102 | 7.4 | Yes | Yes | 21.1 | 22 | -0.9 | 6E13868118134C3494DF1D4BBB8B052B |  | R22 | Non-TXV |  | 7.255% | 0.92745 | 13.94% | [5 empty] | Non-TXV | 7.255%
Stockton | CA | 95209-1648 |  | 2014-05-20 | 2014-05-20 11:23 | 2014-05-20 11:41 | OTHER - UNK | 64 | 10 | Yes | Yes | 25.6 | 20.4 | 5.2 | 553727367872429B87E19802BB05D5D1 |  | R22 | Non-TXV |  | 15.62% | 0.84375 | 30.03% | [5 empty] | Non-TXV | 15.62%
Thornton | CA | 95686-0000 |  | 2014-08-26 | 2014-08-26 11:19 | 2014-08-26 11:48 | DAY & NIGHT - 568B024RCUHL | 77 | 14.4 | Yes | Yes | 19.2 | 19.9 | -0.7 | 562CD6C8275744999DE774502CEE2C13 |  | R22 | Non-TXV |  | 18.7% | 0.81299 | 35.94% | [5 empty] | Non-TXV | 18.7%
Fresno | CA | 93726-5037 |  | 2014-05-29 | 2014-05-29 13:09 | 2014-05-29 13:31 | CARRIER - N/A | 60 | 5.4 | Yes | Yes | 23 | 20.4 | 2.6 | CEF737E39BF64F5F816019B1C640A2DB |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Madera | CA | 93636-0000 |  | 2014-06-19 | 2014-06-19 08:50 | 2014-06-19 09:09 | RHEEM - RRNAC048JK10X | 97 | 18.4 | Yes | Yes | 19.6 | 19.2 | 0.4 | 5F264CF48BFF4374B26457D6ADE7947D |  | R22 | Non-TXV |  | 18.97% | 0.81031 | 36.45% | [5 empty] | Non-TXV | 18.97%
Madera | CA | 93636-0000 |  | 2014-06-19 | 2014-06-19 09:11 | 2014-06-19 09:14 | RHEEM - RRNAC048JK10X | 97 | 14.7 | Yes | Yes | 19.3 | 20.6 | -1.2 | 937BE6127BEB46A6B88B4D77BAD53571 |  | R22 | Non-TXV |  | 15.15% | 0.84845 | 29.12% | [5 empty] | Non-TXV | 15.15%
Fresno | CA | 93722-6142 |  | 2014-05-22 | 2014-05-22 21:53 | 2014-05-22 21:54 | CARRIER - 585CJ030050 | 78 | 2.4 | Yes | Yes | 20.7 | 19.9 | 0.8 | 9F0B51CF3B634BE29F864687471C563F |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Atwater | CA | 95301-2653 |  | 2014-05-15 | 2014-05-15 12:38 | 2014-05-15 12:43 | GUARDIAN - CPLE18-1 | 72 | 6.6 | Yes | Yes | 22.5 | 21 | 1.5 | 805CC93224F547F19754BD1C814E60E1 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Atwater | CA | 95301-2652 |  | 2014-05-19 | 2014-05-19 13:25 | 2014-05-19 13:27 | GOODMAN - G8H1B01811AB | 127 | 3.7 | Yes | Yes | 16.3 | 19.2 | -2.9 | E016EB9EE68A419093E25A7B4C9E682A |  | R22 | Non-TXV |  | 2.913% | 0.97087 | 5.599% | [5 empty] | Non-TXV | 2.913%
Los Banos | CA | 93635-4553 |  | 2014-06-07 | 2014-06-07 09:48 | 2014-06-07 09:51 | BRYANT - 561CJ030-E | 100 | 2.9 | Yes | Yes | 20.7 | 22.8 | -2.1 | 8099DC4CDD1D453F90DA90FEA1541519 |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Los Banos | CA | 93635-4553 |  | 2014-06-07 | 2014-06-07 09:52 | 2014-06-07 09:54 | BRYANT - 561CJ030-E | 100 | 3 | Yes | Yes | 21.2 | 22.1 | -0.9 | 624066C1861F4150AF6B1DDE2885B299 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Atwater | CA | 95301-2653 |  | 2014-06-30 | 2014-06-30 08:13 | 2014-06-30 08:35 | OTHER - GHGD18S21S1A | 115 | 9 | Yes | Yes | 20.9 | 19.1 | 1.9 | 2464EA99BA7E4C49AACBF09527FAFD20 |  | R22 | Non-TXV |  | 7.826% | 0.92174 | 15.04% | [5 empty] | Non-TXV | 7.826%
Dos Palos | CA | 93620-0000 |  | 2014-07-08 | 2014-07-08 12:49 | 2014-07-08 12:51 | BRYANT - 561CJ036-F | 75 | 3.4 | Yes | Yes | 21.6 | 20.4 | 1.2 | 7489421C080547C1BFFA8C3B566F0E9C |  | R22 | Non-TXV |  | 4.533% | 0.95467 | 8.712% | [5 empty] | Non-TXV | 4.533%
Dos Palos | CA | 93620-0000 |  | 2014-07-08 | 2014-07-08 12:46 | 2014-07-08 12:48 | BDP - 589ANW024040ABAD | 57 | 2.3 | Yes | Yes | 22 | 21 | 1 | 55D40EC30CF14277B04CCECAEDF9DB08 |  | R22 | Non-TXV |  | 4.035% | 0.95965 | 7.755% | [5 empty] | Non-TXV | 4.035%
Friant | CA | 93626-9703 |  | 2014-09-30 | 2014-09-30 08:00 | 2014-09-30 08:56 | BRYANT - 577DNW048090 | 85 | 8.9 | Yes | Yes | 17.8 | 18.7 | -0.9 | 53561C9F4B4E4F38AED4F01DB2947578 |  | R410A | TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | TXV | 10.47%
Magalia | CA | 95954-9637 |  | 2014-06-11 | 2014-06-11 08:48 | 2014-06-11 09:05 | LENNOX - GCS20RV-411-100-P | 80 | 3.6 | Yes | Yes | 25.5 | 20.4 | 5.1 | B29D76A5E12C4462AC11A76D58182067 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Chico | CA | 95926-4285 |  | 2014-05-15 | 2014-05-15 13:55 | 2014-05-15 13:26 | DAY & NIGHT - 58CJ030050 | 78 | 6.6 | Yes | Yes | 20.3 | 19.6 | 0.7 | 5D6BA485481F43C9AB6D79527E6C31FC |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Chico | CA | 95926-4372 |  | 2014-05-19 | 2014-05-19 09:47 | 2014-05-19 09:05 | UNK - UNK | 85 | 5.9 | Yes | Yes | 19.4 | 19.9 | -0.5 | 4094FCB913B34CA79F5ED1884B5C986C |  |  |  |  | 6.941% | 0.93059 | 13.34% | [5 empty] | 0 | 6.941%
Chico | CA | 95973-0370 |  | 2014-06-20 | 2014-06-20 15:34 | 2014-06-20 15:34 | RUUD - UAKB-030JAZ | 66 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | C5CEAFD38E444B79B6CA96376907B94E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-4709 |  | 2014-05-16 | 2014-05-16 13:20 | 2014-05-16 14:10 | PAYNE - PY1PNB036090AAAA | 56 | 6 | Yes | Yes | 17.2 | 19.4 | -2.2 | 911DECDD966441C396B684C794F954D9 |  | R22 | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Chico | CA | 95926-4709 |  | 2014-05-16 | 2014-05-16 15:13 | 2014-05-16 15:13 | CARRIER - 48ESNA2406030 | 72 | 0 | Yes | Yes | 18.4 | 21.2 | -2.8 | F2EBC842FD504273BC82D5C969BE62D2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-1403 |  | 2014-06-06 | 2014-06-06 11:16 | 2014-06-06 11:39 | LENNOX - AC13048-230-03 | 146 | 4.9 | Yes | Yes | 22 | 19.9 | 2.1 | 71276567730146429763BFE468D71B52 |  | R22 | Non-TXV |  | 3.356% | 0.96644 | 6.45% | [5 empty] | Non-TXV | 3.356%
Paradise | CA | 95969-5553 |  | 2014-05-23 | 2014-05-23 13:48 | 2014-05-23 14:13 | CARRIER - 50YQ048300 | 70 | 2.1 | Yes | Yes | 20.5 | 19.1 | 1.5 | DE97F9C776EF4DC3826CDB806B9ACDE8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95973-7665 |  | 2014-05-29 | 2014-05-29 19:26 | 2014-05-29 19:42 | TRANE - 2TTB3036A1000AA | 101 | 12 | Yes | Yes | 20 | 21.8 | -1.8 | 2A4FA70459B542F4B8C68948E2237FB0 |  | R22 | Non-TXV |  | 11.88% | 0.88119 | 22.83% | [5 empty] | Non-TXV | 11.88%
Paradise | CA | 95969-4419 |  | 2014-06-05 | 2014-06-05 12:40 | 2014-06-05 12:58 | YORK - DAYA-F036N070C | 67 | 4.8 | Yes | Yes | 19.5 | 19 | 0.5 | B31F352A32EA462D91D3030B67D1926B |  | R22 | Non-TXV |  | 7.164% | 0.92836 | 13.77% | [5 empty] | Non-TXV | 7.164%
Gridley | CA | 95948-9320 |  | 2014-05-30 | 2014-05-30 08:42 | 2014-05-30 08:58 | AMERICAN STANDARD - YCC036F1M0BF | 83 | 3.7 | Yes | Yes | 26 | 20.9 | 5.1 | 51FCE84E2C754ADEB75C51671BCC3B8E |  | R22 | Non-TXV |  | 4.458% | 0.95542 | 8.567% | [5 empty] | Non-TXV | 4.458%
Oroville | CA | 95966-6819 |  | 2014-05-29 | 2014-05-29 11:48 | 2014-05-29 12:10 | CARRIER - 48SS-30060321 | 53 | 8.6 | Yes | Yes | 21 | 21.2 | -0.2 | 37073308CC264F6084EF2251E76E772E |  | R22 | Non-TXV |  | 16.23% | 0.83774 | 31.18% | [5 empty] | Non-TXV | 16.23%
Chico | CA | 95926-2010 |  | 2014-05-29 | 2014-05-29 15:47 | 2014-05-29 16:26 | YORK - H2RA030S06A | 50 | 6.1 | Yes | Yes | 23.5 | 21.8 | 1.7 | C5B176D24AB548C09F49402FF7FBFD1A |  | R22 | Non-TXV |  | 12.2% | 0.878 | 23.45% | [5 empty] | Non-TXV | 12.2%
Orange Cove | CA | 93646-2277 |  | 2014-09-22 | 2014-09-22 10:06 | 2014-09-22 10:38 | ICP - PGF324040K01A2 | 64 | 4.7 | Yes | Yes | 21.5 | 21 | 0.5 | 9BD85C47A07543358437D5361077513C |  | R22 | Non-TXV |  | 7.344% | 0.92656 | 14.11% | [5 empty] | Non-TXV | 7.344%
Parlier | CA | 93648-2441 |  | 2014-06-16 | 2014-06-16 14:58 | 2014-06-16 15:56 | TEMPSTAR - NRGF300DB04 | 53 | 4.6 | Yes | Yes | 21.6 | 21.5 | 0.1 | 7C106B75E4294CEEB4B7E01D1D23D806 |  | R22 | Non-TXV |  | 8.679% | 0.91321 | 16.68% | [5 empty] | Non-TXV | 8.679%
Stockton | CA | 95209-2455 |  | 2014-05-19 | 2014-05-19 16:13 | 2014-05-19 17:14 | HEIL - CA5036VKB1 | 86 | -5.1 | Yes | Yes | 26 | 20.3 | 5.7 | 91A10E1889E34FFF80827B7394A1B004 |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Fresno | CA | 93727-3323 |  | 2014-06-10 | 2014-06-10 14:17 | 2014-06-10 14:46 | HEIL - NRGF36DDB04 | 90 | 3 | Yes | Yes | 25.9 | 20.7 | 5.2 | 4AF1BB8048BB4AD8B8AB6CBF6B1DE757 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93726-5039 |  | 2014-06-24 | 2014-06-24 12:53 | 2014-06-24 12:56 | PAYNE - UNK | 56 | 13.5 | Yes | Yes | 21.3 | 20.2 | 1.1 | D214E6B4E811423A8215D62FD31F31D3 |  | R22 | Non-TXV |  | 24.11% | 0.75893 | 46.33% | [5 empty] | Non-TXV | 24.11%
Coarsegold | CA | 93614-9453 |  | 2014-07-11 | 2014-07-11 15:01 | 2014-07-11 15:03 | RUUD - URKAA036JK08E | 62 | 10.8 | Yes | Yes | 31 | 25.3 | 5.7 | 350FADAB8BFE438E9721F7E77E4D3075 |  | R22 | Non-TXV |  | 17.42% | 0.82581 | 33.48% | [5 empty] | Non-TXV | 17.42%
Fresno | CA | 93704-5637 |  | 2014-06-16 | 2014-06-16 12:18 | 2014-06-16 12:19 | OTHER - 7777UNK | 54 | 1.8 | Yes | Yes | 18.9 | 21.7 | -2.8 | 44961A7D3D444BF48ED0EEAC85C0DC96 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93727-2483 |  | 2014-06-03 | 2014-06-03 11:14 | 2014-06-03 11:44 | RUUD - N/A | 60 | 9.6 | Yes | Yes | 20.9 | 22 | -1.1 | F13C3529599B4E2C86BB591E468A797F |  | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Kerman | CA | 93630-9316 |  | 2014-06-18 | 2014-06-18 14:17 | 2014-06-18 14:26 | OTHER - UNK | 76 | 20.1 | Yes | Yes | 22.1 | 18.6 | 3.5 | 7D7995611E574687A62D30B8221612A7 |  | R22 | Non-TXV |  | 26.45% | 0.73553 | 50.83% | [5 empty] | Non-TXV | 26.45%
Oakdale | CA | 95361-3435 |  | 2014-05-19 | 2014-05-19 11:20 | 2014-05-19 11:46 | RHEEM - RRPL-B024JK06X | 85 | 4.1 | Yes | Yes | 22.1 | 20.8 | 1.3 | F5B0871DC291481B966E748AFFDC63F1 |  | R410A | TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | TXV | 4.824%
Atwater | CA | 95301-2652 |  | 2014-06-06 | 2014-06-06 15:27 | 2014-06-06 15:43 | GOODMAN - GSH130181AB | 127 | 23.2 | Yes | Yes | 23 | 22.1 | 0.9 | 7E3505B26B5E493E8196985CD30F1739 |  | R22 | Non-TXV |  | 18.27% | 0.81732 | 35.11% | [5 empty] | Non-TXV | 18.27%
Oroville | CA | 95966-5752 |  | 2014-06-04 | 2014-06-04 12:12 | 2014-06-04 12:29 | TRANE - 4TTB3048D1000BA | 109 | 4.5 | Yes | Yes | 26.5 | 21.3 | 5.2 | 27B85B8B6C514F17B7AEDD1D255B295A |  | R410A | Non-TXV |  | 4.128% | 0.95872 | 7.934% | [5 empty] | Non-TXV | 4.128%
Clovis | CA | 93611-9018 |  | 2014-06-25 | 2014-06-25 13:30 | 2014-06-25 13:54 | ALLEGIANCE - 7A2048A100A2 | 142 | 9.3 | Yes | Yes | 19.7 | 22.1 | -2.4 | 841587B824DE4FC8B0DFF14681352604 |  | R22 | Non-TXV |  | 6.549% | 0.93451 | 12.59% | [5 empty] | Non-TXV | 6.549%
Fresno | CA | 93705-3813 |  | 2014-05-21 | 2014-05-21 10:34 | 2014-05-21 10:54 | UNITARY PRODUCTS GROUP - C3000 | 39 | 7.2 | Yes | Yes | 20 | 19.3 | 0.7 | C7762CD49B6545ACA5F42BE6CA459CC8 |  | R22 | Non-TXV |  | 18.46% | 0.81538 | 35.48% | [5 empty] | Non-TXV | 18.46%
Durham | CA | 95938-9744 |  | 2014-06-03 | 2014-06-03 11:50 | 2014-06-03 12:12 | DAY & NIGHT - 588ANW0480BOADBG | 101 | 15.2 | Yes | Yes | 20 | 19.7 | 0.3 | 45F2FC3441FD4BEDA7706B8EEDE0BE1E |  | R22 | Non-TXV |  | 15.05% | 0.8495 | 28.92% | [5 empty] | Non-TXV | 15.05%
Stockton | CA | 95203-1651 |  | 2014-06-10 | 2014-06-10 11:02 | 2014-06-10 11:29 | KENMORE - HAC042AKA1 | 85 | 9.2 | Yes | Yes | 23.4 | 20.1 | 3.4 | DEC54E522D0342458F996FE9D86B6103 |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
Fresno | CA | 93726-7428 |  | 2014-06-23 | 2014-06-23 10:46 | 2014-06-23 10:47 | BRYANT - 561CJ036-E | 70 | 2.9 | Yes | Yes | 26.3 | 20.6 | 5.8 | 0736EEADA1064A988ECA140B7C2826D0 |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Fresno | CA | 93727-5527 |  | 2014-06-09 | 2014-06-09 10:19 | 2014-06-09 10:49 | RHEEM - RRPL-B048JK10X | 161 | 8.7 | Yes | Yes | 17.6 | 20.4 | -2.8 | 0320284D23F44D4CB6E766D5CAAEA709 |  | R410A | TXV |  | 5.404% | 0.94596 | 10.38% | [5 empty] | TXV | 5.404%
Yuba City | CA | 95993-2304 |  | 2014-05-16 | 2014-05-16 14:11 | 2014-05-16 14:11 | PAYNE - PA13NR030000AEAA | 90 | 0 | Yes | Yes | 22 | 19.6 | 2.4 | AD2FA8311B0741FF99156E415C10DA1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakhurst | CA | 93644-9348 |  | 2014-08-06 | 2014-08-06 08:59 | 2014-08-06 09:00 | CARRIER - 38BRC060340 | 200 | 20.2 | Yes | Yes | 19.7 | 18.7 | 1 | 35FA1DCCD14D46F184B585C12845F446 |  | R22 | TXV |  | 10.1% | 0.899 | 19.41% | [5 empty] | TXV | 10.1%
Yuba City | CA | 95993-8222 |  | 2014-05-16 | 2014-05-16 12:19 | 2014-05-16 12:38 | JANITROL - CE48-1FB | 111 | 3.3 | Yes | Yes | 20 | 22.6 | -2.6 | 295E4839CC3A4428AFB9BCA86DF2778A |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Manteca | CA | 95336-3053 |  | 2014-06-07 | 2014-06-07 13:37 | 2014-06-07 14:07 | BRYANT - 561CJ024-C | 114 | 6.7 | Yes | Yes | 20.5 | 21.5 | -1 | 4D0DFEB3FAAA48EC8888AF264CA26AD4 |  | R22 | TXV |  | 5.877% | 0.94123 | 11.29% | [5 empty] | TXV | 5.877%
Stockton | CA | 95209-1455 |  | 2014-05-20 | 2014-05-20 10:11 | 2014-05-20 10:30 | RHEEM - RACB-036JAS | 48 | 6 | Yes | Yes | 25.6 | 19.7 | 5.9 | C10B6F60A5DF4A19BC69C959E0A20F63 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Fresno | CA | 93722-2101 |  | 2014-05-20 | 2014-05-20 10:21 | 2014-05-20 10:23 | LENNOX - 12ACB42-4P | 128 | 4.7 | Yes | Yes | 22.7 | 19.1 | 3.6 | A31BC9CD75514195B41619F10A1D4FEC |  | R22 | Non-TXV |  | 3.672% | 0.96328 | 7.057% | [5 empty] | Non-TXV | 3.672%
Fresno | CA | 93726-1122 |  | 2014-05-23 | 2014-05-23 12:34 | 2014-05-23 13:03 | RHEEM - RAMC-048JBZ | 162 | 6.8 | Yes | Yes | 20 | 20.4 | -0.4 | 079502D166C4444EBB2A509D2EE8653F |  | R22 | Non-TXV |  | 4.198% | 0.95802 | 8.067% | [5 empty] | Non-TXV | 4.198%
Stockton | CA | 95209-4218 |  | 2014-06-03 | 2014-06-03 16:32 | 2014-06-03 16:36 | YORK - AC060X1223A | 147 | 12.5 | Yes | Yes | 22.4 | 21.5 | 0.9 | 88BEF5A1B5494A28A90C778342800B2C |  | R22 | TXV |  | 8.503% | 0.91497 | 16.34% | [5 empty] | TXV | 8.503%
Stockton | CA | 95210-1542 |  | 2014-05-23 | 2014-05-23 09:01 | 2014-05-23 09:18 | RHEEM - RRKA-A024JK06X | 50 | 3.7 | Yes | Yes | 26.6 | 20.6 | 6 | 3BB6904C6F9F4363879195C3076050CD |  | R22 | Non-TXV |  | 7.4% | 0.926 | 14.22% | [5 empty] | Non-TXV | 7.4%
Chico | CA | 95928-9449 |  | 2014-05-29 | 2014-05-29 14:28 | 2014-05-29 14:43 | ARMSTRONG - SCU12G48A-1 | 130 | 4.2 | Yes | Yes | 23 | 18.8 | 4.2 | 6B69C21AA87D40FB90CD8E5DBCC0D608 |  | R22 | Non-TXV |  | 3.231% | 0.96769 | 6.209% | [5 empty] | Non-TXV | 3.231%
Fresno | CA | 93722-4717 |  | 2014-05-21 | 2014-05-21 20:27 | 2014-05-21 20:30 | CARRIER - 7777UNK | 84 | 3.3 | Yes | Yes | 20.5 | 20.4 | 0.1 | D9F1ECBC49474FAC973EF50C4353735A |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Fresno | CA | 93703-4246 |  | 2014-05-19 | 2014-05-19 15:53 | 2014-05-19 16:42 | YORK - DCYZ-F036N70A | 64 | 3.8 | Yes | Yes | 24.9 | 20.7 | 4.2 | AEDD1C05DAFC46C6A66E1BA3D846185B |  | R410A | TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | TXV | 5.938%
Merced | CA | 95340-3326 |  | 2014-05-15 | 2014-05-15 11:05 | 2014-05-15 11:07 | TRANE - YCC030F1MOBA | 69 | 6.9 | Yes | Yes | 22 | 20.1 | 1.9 | D6CA1A0A0F314BABAD2F5E9AE1DE7945 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Atwater | CA | 95301-2654 |  | 2014-05-15 | 2014-05-15 17:41 | 2014-05-15 17:43 | GUARDIAN - GSH13024188 | 122 | 3.8 | Yes | Yes | 24.6 | 23.1 | 1.5 | D6DDCE22305645708B17D956FA730617 |  | R22 | Non-TXV |  | 3.115% | 0.96885 | 5.986% | [5 empty] | Non-TXV | 3.115%
Oroville | CA | 95965-3509 |  | 2014-05-29 | 2014-05-29 09:40 | 2014-05-29 10:18 | TRANE - 2TTB3042A1000AA | 109 | 7 | Yes | Yes | 28 | 22.6 | 5.4 | C3B0669FF39240548A211FDE14E04484 |  | R22 | Non-TXV |  | 6.422% | 0.93578 | 12.34% | [5 empty] | Non-TXV | 6.422%
Fresno | CA | 93703-1035 |  | 2014-05-20 | 2014-05-20 11:34 | 2014-05-20 11:55 | CARRIER - 38BRC042320 | 103 | 3.4 | Yes | Yes | 26.5 | 20.9 | 5.6 | 01A508DC8C9F4539BDED7DD6925528A8 |  | R22 | Non-TXV |  | 3.301% | 0.96699 | 6.344% | [5 empty] | Non-TXV | 3.301%
Oakdale | CA | 95361-3800 |  | 2014-05-20 | 2014-05-20 13:39 | 2014-05-20 13:59 | RHEEM - RRKA-A036JK08X | 85 | 5.6 | Yes | Yes | 19.4 | 20.9 | -1.5 | 92BA254DDF1E4243872A31C1E745F6EF |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Oakdale | CA | 95361-3950 |  | 2014-05-19 | 2014-05-19 12:48 | 2014-05-19 13:12 | YORK - UNK | 85 | 8 | Yes | Yes | 18.8 | 20.4 | -1.6 | 09AD4CC82E244EEC8CF1FB6488320FD7 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Fresno | CA | 93727-2504 |  | 2014-06-03 | 2014-06-03 11:48 | 2014-06-03 12:07 | BDP - 589ANW036060ADBF | 84 | 4.9 | Yes | Yes | 28.6 | 22.6 | 6 | 5C764887E9C0429F8366026AF4041E77 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Fresno | CA | 93703-4134 |  | 2014-05-20 | 2014-05-20 14:03 | 2014-05-20 14:22 | GOODMAN - GPG10360701A | 75 | 2.4 | Yes | Yes | 23.1 | 22.6 | 0.5 | 312AFAA76F49474AB78A10F319CDD03C |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95205-5727 |  | 2014-06-03 | 2014-06-03 10:17 | 2014-06-03 10:43 | NORDYNE - S3BA-036K | 90 | 4.8 | Yes | Yes | 21.7 | 18.8 | 2.9 | 6D94F4486601475C8DBD315891CBA641 |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Fresno | CA | 93705-1739 |  | 2014-05-22 | 2014-05-22 13:27 | 2014-05-22 13:44 | DAY & NIGHT - 3680YAC107C | 67 | 13 | Yes | Yes | 20.7 | 16.6 | 4.1 | C3A93190C5D94702BBE456B67CC71036 |  | R22 | Non-TXV |  | 19.4% | 0.80597 | 37.29% | [5 empty] | Non-TXV | 19.4%
Fresno | CA | 93727-7267 |  | 2014-06-26 | 2014-06-26 16:01 | 2014-06-26 16:02 | BRYANT - 38BRC042340 | 108 | 3.6 | Yes | Yes | 20.1 | 20.4 | -0.3 | 44B3AA43537A4E9E92C552858BE0B50F |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Tracy | CA | 95376-1903 |  | 2014-05-23 | 2014-05-23 14:53 | 2014-05-23 15:17 | OTHER - TZAL--2348-2C | 85 | 7.6 | Yes | Yes | 20.8 | 19.5 | 1.3 | AC293D981A6041F492AFAB2D916279B2 |  | R410A | TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | TXV | 8.941%
Stockton | CA | 95215-2016 |  | 2014-07-02 | 2014-07-02 10:35 | 2014-07-02 11:00 | CARRIER - 38TH0363002590E49509 | 86 | -5.1 | Yes | Yes | 20 | 18.8 | 1.2 | DF785C81CF0446C1B8C4410159939915 |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Fresno | CA | 93704-6129 |  | 2014-06-17 | 2014-06-17 09:16 | 2014-06-17 09:18 | YORK - H1RA048S069 | 117 | 5.4 | Yes | Yes | 21.7 | 20.9 | 0.8 | 57C5ECD156E0449C99FBBCD379C7E14A |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Stockton | CA | 95206-3859 |  | 2014-06-09 | 2014-06-09 14:51 | 2014-06-09 14:51 | PAYNE - PY3PNA036 | 167 | 0 | Yes | Yes | 24.9 | 22.8 | 2.1 | C7E8A04DADFB4112981ED60AFD5BBFC0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-1913 |  | 2014-06-16 | 2014-06-16 13:28 | 2014-06-16 13:52 | YORK - H1RA048S06D | 117 | 4.7 | Yes | Yes | 21.6 | 20.9 | 0.7 | 7F3520E49B8D449DA205E72990C6E5C9 |  | R22 | Non-TXV |  | 4.017% | 0.95983 | 7.72% | [5 empty] | Non-TXV | 4.017%
Stockton | CA | 95206-1913 |  | 2014-06-16 | 2014-06-16 13:54 | 2014-06-16 14:11 | HEIL - N2A330AKA200 | 105 | 8.3 | Yes | Yes | 21 | 20.4 | 0.6 | A09D417355C24E94953FB06E7727A452 |  | R22 | TXV |  | 7.905% | 0.92095 | 15.19% | [5 empty] | TXV | 7.905%
Stockton | CA | 95209-4228 |  | 2014-05-14 | 2014-05-14 10:51 | 2014-05-14 11:36 | YORK - H2R030S06A | 88 | 4.7 | Yes | Yes | 20.1 | 23.1 | -3 | 9FB43A2374B94EA19118A489638FB09A |  | R22 | Non-TXV |  | 5.341% | 0.94659 | 10.26% | [5 empty] | Non-TXV | 5.341%
Placerville | CA | 95667-6056 |  | 2014-06-03 | 2014-06-03 11:25 | 2014-06-03 12:04 | AMERICAN STANDARD - 6H0036A100A4 | 103 | 18.9 | Yes | Yes | 22.8 | 20.9 | 1.9 | A0C3D11B22CE4F9598F9D5147D5CF4A2 |  | R22 | Non-TXV |  | 18.35% | 0.8165 | 35.26% | [5 empty] | Non-TXV | 18.35%
Stockton | CA | 95209-5003 |  | 2014-06-03 | 2014-06-03 10:59 | 2014-06-03 11:18 | AMANA - PGB24C0702E | 64 | 8.3 | Yes | Yes | 24.3 | 19.5 | 4.8 | 3B756C53E69E491DA985D4E2AC85F85B |  | R22 | Non-TXV |  | 12.97% | 0.87031 | 24.92% | [5 empty] | Non-TXV | 12.97%
Tracy | CA | 95376-2258 |  | 2014-05-21 | 2014-05-21 13:39 | 2014-05-21 14:00 | YORK - H4DB036S06A | 73 | 6.7 | Yes | Yes | 21.3 | 20.4 | 0.9 | 217B11EF15FA4F1AB9C65674C51CF0B4 |  | R22 | Non-TXV |  | 9.178% | 0.90822 | 17.64% | [5 empty] | Non-TXV | 9.178%
Stockton | CA | 95207-1137 |  | 2014-05-20 | 2014-05-20 12:09 | 2014-05-20 12:33 | OTHER - UNK | 48 | 2 | Yes | Yes | 20.8 | 19.5 | 1.3 | 43310C2F972043EC93D6281FBEE960E8 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Fresno | CA | 93722-2524 |  | 2014-07-09 | 2014-07-09 12:57 | 2014-07-09 13:36 | LENNOX - GCS26X-036-75-2PA | 110 | 3.9 | Yes | Yes | 23.1 | 21.5 | 1.6 | A82E79C3F69448CE87BC7CB401570996 |  | R22 | Non-TXV |  | 3.545% | 0.96455 | 6.814% | [5 empty] | Non-TXV | 3.545%
Fresno | CA | 93720-2528 |  | 2014-06-19 | 2014-06-19 11:31 | 2014-06-19 11:49 | TRANE - YCY036F1M0A | 90 | 5.1 | Yes | Yes | 28.2 | 22.4 | 5.8 | E0CE862D69DD4A7383035762DEB84AB5 |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Clovis | CA | 93611-8586 |  | 2014-07-02 | 2014-07-02 08:48 | 2014-07-02 09:27 | LENNOX - 13ACC-060-230-01 | 168 | 8.5 | Yes | Yes | 18.8 | 20.9 | -2.1 | 4C13ABCECBEE4AEAB9D7F04AC4F8F876 |  | R22 | Non-TXV |  | 5.06% | 0.9494 | 9.723% | [5 empty] | Non-TXV | 5.06%
Rocklin | CA | 95677-2049 |  | 2014-05-22 | 2014-05-22 12:38 | 2014-05-22 13:02 | OTHER - CA5536VKD2 | 82 | 6.5 | Yes | Yes | 19 | 18.8 | 0.2 | FDE2712591B74CFCB1618BF5C3284C7F |  | R22 | Non-TXV |  | 7.927% | 0.92073 | 15.23% | [5 empty] | Non-TXV | 7.927%
Chico | CA | 95926-2090 |  | 2014-05-21 | 2014-05-21 16:03 | 2014-05-21 17:36 | DAY & NIGHT - 58GJ018040 | 62 | 2.5 | Yes | Yes | 21.5 | 23 | -1.5 | 04BE95EDADFD4C45A7E8828DB077D4F4 |  | R22 | Non-TXV |  | 4.032% | 0.95968 | 7.749% | [5 empty] | Non-TXV | 4.032%
Marysville | CA | 95901-6881 |  | 2014-05-21 | 2014-05-21 10:16 | 2014-05-21 11:01 | GIBSON - GS3BA-036KA | 69 | 2.2 | Yes | Yes | 26 | 21 | 5 | 99DC8617FFF94500ADA16F3FC9936A81 |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Marysville | CA | 95901-7314 |  | 2014-06-12 | 2014-06-12 09:35 | 2014-06-12 09:55 | BRYANT - 574DNW024060NA | 105 | 3.8 | Yes | Yes | 22 | 19.3 | 2.7 | BD0B64831BCE49EDBB3D2C7CA4EE3862 |  | R410A | TXV |  | 3.619% | 0.96381 | 6.955% | [5 empty] | TXV | 3.619%
Yuba City | CA | 95991-8421 |  | 2014-05-15 | 2014-05-15 12:01 | 2014-05-15 12:25 | DAY & NIGHT - N2A348AKA300 | 115 | 17 | Yes | Yes | 22 | 20.7 | 1.3 | 8F337682E22844229F25F650E555D1EB |  | R22 | Non-TXV |  | 14.78% | 0.85217 | 28.41% | [5 empty] | Non-TXV | 14.78%
Stockton | CA | 95204-5436 |  | 2014-06-04 | 2014-06-04 09:37 | 2014-06-04 09:54 | RHEEM - RRKA-A024JK06X | 50 | 2 | Yes | Yes | 19.3 | 19.1 | 0.2 | 9D64C731EBBF484898EEC31FB2C180B2 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Chico | CA | 95928-6802 |  | 2014-05-19 | 2014-05-19 14:17 | 2014-05-19 14:42 | UNK - UNK | 85 | 5.8 | Yes | Yes | 24.5 | 20.9 | 3.6 | 9E3C0376D448407E8BFB386BDFEFDFBE |  |  |  |  | 6.824% | 0.93176 | 13.11% | [5 empty] | 0 | 6.824%
Stockton | CA | 95204-5436 |  | 2014-06-12 | 2014-06-12 08:15 | 2014-06-12 08:33 | DAY & NIGHT - UNK | 44 | -3.1 | Yes | Yes | 24.1 | 19.5 | 4.6 | 45ADEC4C98664E44B3592361304D9E46 |  | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Fresno | CA | 93703-4212 |  | 2014-05-30 | 2014-05-30 14:04 | 2014-05-30 14:22 | AMERICAN STANDARD - YCC048F1MBH | 100 | 3.2 | Yes | Yes | 21.5 | 22.1 | -0.6 | 1033298D753043779E27C1A7BAE61C33 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93727-2034 |  | 2014-06-11 | 2014-06-11 09:37 | 2014-06-11 10:01 | CARRIER - 585HJW0360100 | 84 | 4.3 | Yes | Yes | 19.3 | 20.4 | -1.1 | A6C474F3352141E5834A6D1D41A7848D |  | R22 | Non-TXV |  | 5.119% | 0.94881 | 9.838% | [5 empty] | Non-TXV | 5.119%
Stockton | CA | 95209-2601 |  | 2014-05-13 | 2014-05-13 11:35 | 2014-05-13 11:35 | RHEEM - UNK | 80 | 0 | Yes | Yes | 20.5 | 20 | 0.5 | B62CF67119324E2383E3EC17D7E93EA8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1080 |  | 2014-06-17 | 2014-06-17 14:52 | 2014-06-17 14:54 | YORK - D3NZ030N05606NXB | 64 | 6.7 | Yes | Yes | 26 | 20.6 | 5.4 | 86B8507E935142518CDE6A7D89A4FD70 |  | R410A | Non-TXV |  | 10.47% | 0.89531 | 20.12% | [5 empty] | Non-TXV | 10.47%
Clovis | CA | 93611-4594 |  | 2014-06-02 | 2014-06-02 10:51 | 2014-06-02 10:53 | BDP - 585HJ036060 | 102 | 4.1 | Yes | Yes | 26 | 20.2 | 5.9 | 19B3F256E5E74842978C5609BABAB24C |  | R22 | Non-TXV |  | 4.02% | 0.9598 | 7.725% | [5 empty] | Non-TXV | 4.02%
Oroville | CA | 95966-6903 |  | 2014-05-29 | 2014-05-29 13:52 | 2014-05-29 13:52 | TRANE - UNK | 94 | 0 | Yes | Yes | 22 | 19.1 | 2.9 | A3A5270AAD6744B8ABA3B3971CBC2507 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-9623 |  | 2014-06-13 | 2014-06-13 14:41 | 2014-06-13 15:10 | UNITARY PRODUCTS GROUP - TCGD42S21S1HA | 72 | 5 | Yes | Yes | 27.7 | 22.1 | 5.6 | F86B06A4514D464289D7B175E4A228C9 |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Kerman | CA | 93630-1266 |  | 2014-06-18 | 2014-06-18 10:45 | 2014-06-18 10:55 | CARRIER - 591ANX036000AAAA | 83 | 11.5 | Yes | Yes | 23.2 | 19.9 | 3.3 | E7D649A589A64FA1A72E4D9644DEC676 |  | R22 | Non-TXV |  | 13.86% | 0.86145 | 26.63% | [5 empty] | Non-TXV | 13.86%
Tracy | CA | 95376-4522 |  | 2014-05-22 | 2014-05-22 10:38 | 2014-05-22 11:00 | TRANE - YCC024F1L0BH | 65 | 3.7 | Yes | Yes | 21.6 | 20.9 | 0.7 | A5F6541FA6AC4773970B67774FF31EB3 |  | R22 | Non-TXV |  | 5.692% | 0.94308 | 10.94% | [5 empty] | Non-TXV | 5.692%
Fresno | CA | 93721-2419 |  | 2014-05-22 | 2014-05-22 14:50 | 2014-05-22 14:51 | YORK - D1NP048N09006A | 132 | 4.6 | Yes | Yes | 23.8 | 20.9 | 2.9 | 28DB58DCFC4446B997459FFEEDC709F0 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Fresno | CA | 93727-4712 |  | 2014-06-25 | 2014-06-25 11:24 | 2014-06-25 11:25 | OTHER - AC024M1021CG | 52 | 2.1 | Yes | Yes | 23.4 | 22.5 | 0.9 | E7BA5EEC5B5744ADB297864121C36A2A |  | R22 | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
Stockton | CA | 95209-4256 |  | 2014-05-14 | 2014-05-14 10:13 | 2014-05-14 10:36 | CARRIER - 38CKC042350 | 93 | 8.6 | Yes | Yes | 22.4 | 21 | 1.4 | 2951A82B01E44014BC2AEC675BE6277D |  | R22 | Non-TXV |  | 9.247% | 0.90753 | 17.77% | [5 empty] | Non-TXV | 9.247%
Magalia | CA | 95954-9630 |  | 2014-06-04 | 2014-06-04 12:16 | 2014-06-04 12:45 | RHEEM - RRNA-BO48JK40E | 105 | 4.3 | Yes | Yes | 18.6 | 21.1 | -2.5 | DFCE0E1C0BEA445A952ED0725239B208 |  | R22 | Non-TXV |  | 4.095% | 0.95905 | 7.87% | [5 empty] | Non-TXV | 4.095%
Clovis | CA | 93611-7236 |  | 2014-06-03 | 2014-06-03 08:51 | 2014-06-03 08:53 | RHEEM - 7777UNK | 86 | 3.5 | Yes | Yes | 19.6 | 19.9 | -0.3 | BCD90CCFAE474598A10BAA5271EC3DDD |  | R22 | Non-TXV |  | 4.07% | 0.9593 | 7.821% | [5 empty] | Non-TXV | 4.07%
Chico | CA | 95926-1722 |  | 2014-07-01 | 2014-07-01 14:38 | 2014-07-01 14:44 | GOODMAN - GS140307AE | 134 | 4.7 | Yes | Yes | 19 | 18.8 | 0.3 | E1902418648D4F6A83E3D5A4D5432B71 |  | R22 | Non-TXV |  | 3.507% | 0.96493 | 6.741% | [5 empty] | Non-TXV | 3.507%
Stockton | CA | 95206-6112 |  | 2014-06-06 | 2014-06-06 08:36 | 2014-06-06 08:57 | BRYANT - 562CJ042-B | 171 | -11.1 | Yes | Yes | 20.3 | 19.9 | 0.4 | F1E553EE94DE40879E19A5237ACE8900 |  | R22 | TXV |  | -6.491% | 1.0649 | 1.818% |  |  |  |  | TXV |  |  | -6.491%
Paradise | CA | 95969-3046 |  | 2014-07-31 | 2014-07-31 14:48 | 2014-07-31 15:08 | YORK - D3YS03608006B | 55 | 2 | Yes | Yes | 18.5 | 20.4 | -1.9 | 4679AC551F6B447089DDE2CB3CC453BF |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Oroville | CA | 95965-4230 |  | 2014-06-19 | 2014-06-19 10:40 | 2014-06-19 11:19 | DAY & NIGHT - 585H036100YACR | 80 | 4.6 | Yes | Yes | 22.5 | 21.4 | 1.1 | 31CC4203239446EAABEE0BFA2519D189 |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Chico | CA | 95973-9239 |  | 2014-05-27 | 2014-05-27 09:41 | 2014-05-27 09:20 | YORK - H1RE030S06D | 158 | 5.7 | Yes | Yes | 19 | 21 | -2 | E346FD9E8B6846668DDE8D5C979FA444 |  | R22 | Non-TXV |  | 3.608% | 0.96392 | 6.933% | [5 empty] | Non-TXV | 3.608%
Chico | CA | 95926-2413 |  | 2014-06-19 | 2014-06-19 08:30 | 2014-06-19 08:46 | LENNOX - HP21-511-3P | 248 | 9 | Yes | Yes | 18.5 | 21.3 | -2.8 | ABC520F7A91E4B709D0740A840EF5944 |  | R22 | TXV |  | 3.629% | 0.96371 | 6.974% | [5 empty] | TXV | 3.629%
Chico | CA | 95973-7257 |  | 2014-05-21 | 2014-05-21 15:00 | 2014-05-21 15:37 | COLEMAN - NA | 61 | 3.1 | Yes | Yes | 22.8 | 24.8 | -2 | D8EDEF39803345BF9B0704D8C36345D7 |  | R22 | Non-TXV |  | 5.082% | 0.94918 | 9.766% | [5 empty] | Non-TXV | 5.082%
Fresno | CA | 93727-4707 |  | 2014-06-25 | 2014-06-25 11:29 | 2014-06-25 11:31 | RHEEM - RAHE-023JAS | 64 | 3 | Yes | Yes | 18.7 | 19.2 | -0.5 | 4421307A56A04B3C9D8DD4ECB4D15806 |  | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Oroville | CA | 95965-4425 |  | 2014-05-27 | 2014-05-27 09:01 | 2014-05-27 09:19 | AMERICAN STANDARD - 2A7A4030A1000AA | 105 | 3.7 | Yes | Yes | 17 | 15.2 | 1.8 | 0C6ED141FD3B4140955C9D0355BC87A2 |  | R22 | Non-TXV |  | 3.524% | 0.96476 | 6.772% | [5 empty] | Non-TXV | 3.524%
Stockton | CA | 95210-1401 |  | 2014-05-15 | 2014-05-15 14:19 | 2014-05-15 14:38 | BRYANT - 582ANW024040NAAD | 53 | 3.5 | Yes | Yes | 27.8 | 22.4 | 5.4 | 1A697E228DFE46D8AAA8A5E40FF43B04 |  | R22 | Non-TXV |  | 6.604% | 0.93396 | 12.69% | [5 empty] | Non-TXV | 6.604%
Paradise | CA | 95969-5656 |  | 2014-05-22 | 2014-05-22 14:11 | 2014-05-22 12:39 | GOODMAN - GPG154911541AC | 167 | 6.1 | Yes | Yes | 25.8 | 19.9 | 5.9 | 6EF3B1C479F5426CA3F632C20262C3C8 |  | R410A | TXV |  | 3.653% | 0.96347 | 7.02% | [5 empty] | TXV | 3.653%
Fresno | CA | 93726-5922 |  | 2014-06-02 | 2014-06-02 09:57 | 2014-06-02 10:14 | RHEEM - RRNA-B036JK06X | 83 | 5.6 | Yes | Yes | 19.5 | 20.2 | -0.7 | CE54AB2B1C98404398FF99F728475A42 |  | R22 | Non-TXV |  | 6.747% | 0.93253 | 12.97% | [5 empty] | Non-TXV | 6.747%
Stockton | CA | 95205-8423 |  | 2014-06-05 | 2014-06-05 15:00 | 2014-06-05 15:21 | GE - TA042H1B | 87 | 14.4 | Yes | Yes | 20.1 | 20.2 | -0.1 | C4AD0B726B1E469A9382FAA0E9B6619C |  | R22 | Non-TXV |  | 16.55% | 0.83448 | 31.81% | [5 empty] | Non-TXV | 16.55%
Manteca | CA | 95336-5804 |  | 2014-05-16 | 2014-05-16 12:23 | 2014-05-16 12:49 | CARRIER - PGD348090K001C1 | 100 | 5.2 | Yes | Yes | 21.8 | 21.9 | -0.1 | 78A3C5EE38E949CA809A78AE5349C93F |  | R22 | TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | TXV | 5.2%
Camino | CA | 95709-0000 |  | 2014-06-10 | 2014-06-10 13:25 | 2014-06-10 13:54 | LENNOX - HS25-411-1P | 129 | 3.8 | Yes | Yes | 29 | 23.7 | 5.3 | 722262E427324BB7AFADFE9E08F4E22B |  | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.661% | [5 empty] | Non-TXV | 2.946%
Fresno | CA | 93703-1932 |  | 2014-05-22 | 2014-05-22 14:41 | 2014-05-22 15:26 | PAYNE - N/A | 90 | 5.5 | Yes | Yes | 21.9 | 21.8 | 0.1 | 09883017B90C430B960228F7DBD2C8BE |  | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Fresno | CA | 93727-3703 |  | 2014-06-04 | 2014-06-04 14:28 | 2014-06-04 14:57 | OTHER - 60WR24G1NA | 52 | 1.8 | Yes | Yes | 19.4 | 20.6 | -1.2 | 61B6963B84754CAAB7AADE28B6C653F1 |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Clovis | CA | 93612-4431 |  | 2014-06-03 | 2014-06-03 13:18 | 2014-06-03 13:19 | RHEEM - 7777UNK | 80 | 2.6 | Yes | Yes | 24.2 | 22.6 | 1.6 | D35B450A75C04104B7A9A04338395801 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Fresno | CA | 93726-1638 |  | 2014-05-28 | 2014-05-28 12:03 | 2014-05-28 12:23 | HEIL - C30036UKB1 | 79 | 3.1 | Yes | Yes | 19.1 | 21.5 | -2.4 | EB1FF038E0624738AB865DFFC1ACEE63 |  | R22 | Non-TXV |  | 3.924% | 0.96076 | 7.541% | [5 empty] | Non-TXV | 3.924%
Fresno | CA | 93722-8600 |  | 2014-05-28 | 2014-05-28 14:22 | 2014-05-28 14:45 | LENNOX - 12GCS036X753PA | 110 | 24.2 | Yes | Yes | 26.2 | 21 | 5.2 | 495BAB83CBA44ACBBAEDFBDDB0F13A16 |  | R22 | Non-TXV |  | 22% | 0.78 | 42.28% | [5 empty] | Non-TXV | 22%
Fresno | CA | 93727-6847 |  | 2014-06-06 | 2014-06-06 12:17 | 2014-06-06 12:42 | WEATHER KING - 14AJA42A01 | 237 | 7 | Yes | Yes | 21.7 | 20.8 | 0.9 | B083845321184ADBAC790795D5D17BDE |  | R22 | Non-TXV |  | 2.954% | 0.97046 | 5.676% | [5 empty] | Non-TXV | 2.954%
Stockton | CA | 95215-1214 |  | 2014-06-04 | 2014-06-04 13:29 | 2014-06-04 13:47 | AMANA - GSC140361AA | 155 | -10.9 | Yes | Yes | 24.6 | 20.2 | 4.4 | 0E5C2494615A4D258E0B9F3A9CC4928A |  | R22 | Non-TXV |  | -7.032% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.032%
Clovis | CA | 93611-4126 |  | 2014-06-10 | 2014-06-10 09:51 | 2014-06-10 10:08 | OTHER - 140WE60G1 | 92 | 15.7 | Yes | Yes | 24.9 | 19.8 | 5.1 | 5FF734C140714B109FCDDC4E2F14E948 |  | R22 | Non-TXV |  | 17.07% | 0.82935 | 32.8% | [5 empty] | Non-TXV | 17.07%
Stockton | CA | 95210-4148 |  | 2014-05-27 | 2014-05-27 13:23 | 2014-05-27 13:46 | RUUD - UNK | 60 | 10 | Yes | Yes | 26.2 | 20.7 | 5.5 | 5CBC0C1E21DC4B7F833C63781115CDF0 |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Stockton | CA | 95206-2231 |  | 2014-06-09 | 2014-06-09 09:20 | 2014-06-09 09:20 | TRANE - RAUB-302-F | 63 | 0 | Yes | Yes | 16.1 | 18.1 | -2 | 660EFF8C671348EEBBEB210EA8D3E018 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4433 |  | 2014-06-11 | 2014-06-11 11:22 | 2014-06-11 11:39 | GOODMAN - GPGB0300751 | 56 | 7.8 | Yes | Yes | 18.7 | 15.9 | 2.8 | C24541F83BEE436EBD845833EE46B381 |  | R22 | Non-TXV |  | 13.93% | 0.86071 | 26.77% | [5 empty] | Non-TXV | 13.93%
Fresno | CA | 93703-3241 |  | 2014-05-19 | 2014-05-19 09:20 | 2014-05-19 09:20 | BRYANT - 574DNWA36060NA | 100 | 0 | Yes | Yes | 25.4 | 20.6 | 4.8 | 0F834F3C02764E1CA4EF29961E927910 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4461 |  | 2014-06-17 | 2014-06-17 12:59 | 2014-06-17 13:17 | PAYNE - 591ANX042000ABAA | 112 | -6.6 | Yes | Yes | 24.6 | 21.4 | 3.2 | 474EE47FE3E24016B4D2DA8329019C35 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Oakdale | CA | 95361-3955 |  | 2014-06-04 | 2014-06-04 09:16 | 2014-06-04 09:37 | PAYNE - PA10JA018-A | 136 | 7.8 | Yes | Yes | 19.2 | 16.9 | 2.3 | 58D1B3AECB4D48498A63F753017BAE85 |  | R22 | TXV |  | 5.735% | 0.94265 | 11.02% | [5 empty] | TXV | 5.735%
Oroville | CA | 95966-3621 |  | 2014-06-23 | 2014-06-23 10:36 | 2014-06-23 10:53 | AMERICAN STANDARD - YCY036G1MOAB | 129 | 4.8 | Yes | Yes | 19.5 | 19.9 | -0.4 | 4D187780DA9F4C0B88C35DD9A5DAC63E |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Fresno | CA | 93727-4703 |  | 2014-06-27 | 2014-06-27 16:45 | 2014-06-27 17:13 | BDP - 565BJ030 | 72 | 2.5 | Yes | Yes | 20.1 | 21.4 | -1.3 | F4F65646CD214D0F891773D007F24DC2 |  | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Fresno | CA | 93726-5036 |  | 2014-06-24 | 2014-06-24 09:46 | 2014-06-24 09:49 | DAY & NIGHT - UNK | 56 | 6.7 | Yes | Yes | 19.2 | 19 | 0.2 | CAE16FFA6EBB42BA89D9D56355ACB50B |  | R22 | Non-TXV |  | 11.96% | 0.88036 | 22.99% | [5 empty] | Non-TXV | 11.96%
Magalia | CA | 95954-9690 |  | 2014-07-15 | 2014-07-15 15:11 | 2014-07-16 15:54 | GOODMAN - CK24-18 | 55 | 5.3 | Yes | Yes | 21.5 | 21 | 0.5 | 299DDEC97E4B4F91AD7794BC2535B648 |  | R22 | Non-TXV |  | 9.636% | 0.90364 | 18.52% | [5 empty] | Non-TXV | 9.636%
Magalia | CA | 95954-9690 |  | 2014-07-15 | 2014-07-15 15:33 | 2014-07-16 15:55 | RUUD - UAMB-060JAZ | 192 | 8.9 | Yes | Yes | 22.5 | 20.9 | 1.6 | D4620D2A841643C7B015C132ACF1F322 |  | R22 | Non-TXV |  | 4.635% | 0.95365 | 8.908% | [5 empty] | Non-TXV | 4.635%
Fresno | CA | 93727-3559 |  | 2014-06-04 | 2014-06-04 11:12 | 2014-06-04 11:36 | BDP - 585GJWO36060 | 82 | 4.7 | Yes | Yes | 23.1 | 20.7 | 2.5 | 1266F083FC66417BBEBFC417CC81C6F1 |  | R22 | Non-TXV |  | 5.732% | 0.94268 | 11.02% | [5 empty] | Non-TXV | 5.732%
Merced | CA | 95340-5126 |  | 2014-05-19 | 2014-05-19 09:41 | 2014-05-19 10:21 | UNK - UNK | 85 | 11.3 | Yes | Yes | 26.1 | 20.4 | 5.7 | 7E08390D836B4B3F95CB5A4A4C4572E5 |  |  |  |  | 13.29% | 0.86706 | 25.55% | [5 empty] | 0 | 13.29%
Chico | CA | 95926-1606 |  | 2014-05-15 | 2014-05-15 09:21 | 2014-05-15 09:52 | LENNOX - HS29-048-5P | 88 | 2.8 | Yes | Yes | 20.3 | 20.6 | -0.3 | 090ED204F8FF4B32A0D5559F73321439 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Fresno | CA | 93725-1117 |  | 2014-06-16 | 2014-06-16 12:45 | 2014-06-16 12:47 | OTHER - UNK | 76 | 13.7 | Yes | Yes | 28.1 | 23.1 | 5 | 341AD47E066740F1BD7B4E02C68ED601 |  | R22 | Non-TXV |  | 18.03% | 0.81974 | 34.64% | [5 empty] | Non-TXV | 18.03%
Stockton | CA | 95206-6277 |  | 2014-06-12 | 2014-06-12 09:27 | 2014-06-12 09:45 | GOODMAN - CKJ30-1A | 85 | 8.4 | Yes | Yes | 23.4 | 20.4 | 3 | 8F2F0C39556A4304BA5C034E160C2BA6 |  | R22 | Non-TXV |  | 9.882% | 0.90118 | 18.99% | [5 empty] | Non-TXV | 9.882%
Fresno | CA | 93722-3289 |  | 2014-05-20 | 2014-05-20 12:47 | 2014-05-20 12:48 | OTHER - EADC0036JAS | 80 | 3.7 | Yes | Yes | 25 | 21.5 | 3.5 | 632CA19FF34C45CDB985278810BBD260 |  | R22 | Non-TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | Non-TXV | 4.625%
Lathrop | CA | 95330-9731 |  | 2014-05-28 | 2014-05-28 14:50 | 2014-05-28 15:13 | YORK - H2DH036S06B | 124 | 10.6 | Yes | Yes | 22.6 | 24.1 | -1.5 | 7DE9A0317D9E43E9A528984197EF4B52 |  | R22 | Non-TXV |  | 8.548% | 0.91452 | 16.43% | [5 empty] | Non-TXV | 8.548%
Fresno | CA | 93727-5524 |  | 2014-06-06 | 2014-06-06 09:30 | 2014-06-06 09:55 | LENNOX - 12GCS0480-100-5PB | 167 | 5.3 | Yes | Yes | 24.7 | 21.5 | 3.2 | B5D18FC4B28246FDA21D411B9740FBE2 |  | R22 | Non-TXV |  | 3.174% | 0.96826 | 6.099% | [5 empty] | Non-TXV | 3.174%
Stockton | CA | 95207-8122 |  | 2014-06-17 | 2014-06-17 10:05 | 2014-06-17 10:23 | RHEEM - RRNL-B024JK06X | 77 | 5.6 | Yes | Yes | 24.2 | 19.7 | 4.5 | 74135658BCB64DE6ACD3006CBAE376FB |  | R410A | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Manteca | CA | 95336-3830 |  | 2014-05-15 | 2014-05-15 09:47 | 2014-05-15 10:18 | GE - BTR930C100A1 | 108 | 7.1 | Yes | Yes | 21.5 | 20.2 | 1.3 | D55C22F486764B80A14DD7D991957D57 |  | R22 | Non-TXV |  | 6.574% | 0.93426 | 12.63% | [5 empty] | Non-TXV | 6.574%
Fresno | CA | 93728-3117 |  | 2014-06-13 | 2014-06-13 11:49 | 2014-06-13 11:51 | CARRIER - 7777UNK | 68 | 2.4 | Yes | Yes | 21.1 | 21.5 | -0.4 | 178D6EA27536470097BF506B9E7E4E6F |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Placerville | CA | 95667-9671 |  | 2014-07-15 | 2014-07-15 12:44 | 2014-07-15 13:11 | COLEMAN - BRCQ0421BB | 80 | 2.7 | Yes | Yes | 27.5 | 22 | 5.5 | 62F686B20FC144D4A7C765459DA2DE97 |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Selma | CA | 93662-0000 |  | 2014-06-13 | 2014-06-13 16:36 | 2014-06-13 16:53 | GOODMAN - GPG13360701AC | 112 | 3.7 | Yes | Yes | 23.2 | 23.2 | 0 | 2618C92080874BA5B8FC072BB4676265 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Oroville | CA | 95965-3484 |  | 2014-06-12 | 2014-06-12 08:30 | 2014-06-12 08:48 | OTHER - NXAG42GKA100 | 129 | 13.4 | Yes | Yes | 21.6 | 21 | 0.6 | 6BA2D4248121485FA0F1CE0F81DE0243 |  | R410A | Non-TXV |  | 10.39% | 0.89612 | 19.96% | [5 empty] | Non-TXV | 10.39%
Tracy | CA | 95377-8821 |  | 2014-06-17 | 2014-06-17 10:14 | 2014-06-17 10:35 | CARRIER - 38CKC060370 | 159 | -9.4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 82AD73F0867542E98BD678049FD79721 |  | R22 | TXV |  | -5.912% | 1.0591 | 1.656% |  |  |  |  | TXV |  |  | -5.912%
Chowchilla | CA | 93610-8444 |  | 2014-06-05 | 2014-06-05 23:09 | 2014-06-05 23:12 | OTHER - 10ACB60-10 | 136 | 5.9 | Yes | Yes | 19.1 | 19.9 | -0.8 | 385609AAF9E84773A7AC4A9F2B0D3776 |  | R22 | Non-TXV |  | 4.338% | 0.95662 | 8.337% | [5 empty] | Non-TXV | 4.338%
Chico | CA | 95926-3782 |  | 2014-06-06 | 2014-06-06 13:36 | 2014-06-06 14:03 | LENNOX - GCSB3B | 64 | 4.6 | Yes | Yes | 16.4 | 19.3 | -2.9 | 33428BA86F514DCE935C2FA4DD2CF5EA |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Fresno | CA | 93722-7164 |  | 2014-05-23 | 2014-05-23 12:54 | 2014-05-23 12:55 | GOODMAN - 7777UNK | 130 | 5.4 | Yes | Yes | 19.1 | 20.6 | -1.5 | 350E2B01A6824D9BA3220FAE9EA53DD1 |  | R22 | Non-TXV |  | 4.154% | 0.95846 | 7.983% | [5 empty] | Non-TXV | 4.154%
Stockton | CA | 95209-4263 |  | 2014-06-03 | 2014-06-03 14:07 | 2014-06-03 14:26 | CARRIER - 24ABA360A300 | 136 | 15.5 | Yes | Yes | 22 | 22.4 | -0.4 | D7EE10D5474E414E960076C5A37B6A5E |  | R410A | TXV |  | 11.4% | 0.88603 | 21.9% | [5 empty] | TXV | 11.4%
Marysville | CA | 95901-4821 |  | 2014-05-21 | 2014-05-21 08:17 | 2014-05-21 09:04 | CARRIER - 46NHT042300 | 100 | 2.9 | Yes | Yes | 25 | 20.8 | 4.2 | 2BE369E824CA45108D8903223EFB1391 |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Fresno | CA | 93727-3703 |  | 2014-06-04 | 2014-06-04 15:00 | 2014-06-04 15:29 | OTHER - 60WR24G1NA | 52 | 1.6 | Yes | Yes | 19 | 21.9 | -2.9 | 2C2076959D1C4DA092FA9B392FF053C1 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Chico | CA | 95926-3767 |  | 2014-06-18 | 2014-06-18 09:37 | 2014-06-18 09:55 | OTHER - JS3BA-024KA | 40 | 7.8 | Yes | Yes | 17.8 | 20.7 | -2.9 | 8971D873BD974AEAAEBE2BA49836C35F |  | R22 | Non-TXV |  | 19.5% | 0.805 | 37.47% | [5 empty] | Non-TXV | 19.5%
Selma | CA | 93662-3842 |  | 2014-06-16 | 2014-06-16 11:25 | 2014-06-16 11:45 | YORK - D2GA036N04806C | 84 | 5.7 | Yes | Yes | 23.6 | 22.9 | 0.7 | B0034841D0D943EEAAADBF3C9E932F60 |  | R22 | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Oroville | CA | 95966-8249 |  | 2014-06-04 | 2014-06-04 15:43 | 2014-06-04 16:06 | TRANE - 2TTR2030A1000AA | 68 | 11.9 | Yes | Yes | 24 | 23.6 | 0.4 | 2FD235DC24BD438C9BFC5FC1C9186263 |  | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Gridley | CA | 95948-9512 |  | 2014-05-30 | 2014-05-30 09:48 | 2014-05-30 10:21 | OTHER - UNK | 86 | 3.2 | Yes | Yes | 18 | 19.9 | -1.9 | CC6706AAC627446F96D4E280FB3C0ACA |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Fresno | CA | 93705-3345 |  | 2014-07-14 | 2014-07-14 14:51 | 2014-07-14 15:09 | OTHER - ACP5-24-75-1 | 72 | -5.1 | Yes | Yes | 17 | 18.5 | -1.5 | 6678B89C7C87414FA9CF477A46D63037 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Manteca | CA | 95336-3444 |  | 2014-05-15 | 2014-05-15 11:59 | 2014-05-15 12:27 | FRIGIDAIRE - FS3BC-024K | 85 | -6 | Yes | Yes | 20 | 19.7 | 0.3 | 9BB96D69665A48C99C57735D51045C65 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Sanger | CA | 93657-3715 |  | 2014-07-07 | 2014-07-07 13:52 | 2014-07-07 14:14 | YORK - H2RA036S06G | 63 | 6.8 | Yes | Yes | 19.9 | 21.4 | -1.5 | 57B2C267C20E4A858DB4A8DECB57BC23 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.79% | 0.89206 | 20.74% | [5 empty] | Non-TXV | 10.79%
Fresno | CA | 93710-4743 |  | 2014-06-23 | 2014-06-23 11:31 | 2014-06-23 11:57 | CARRIER - 38TXA048320 | 173 | 6.9 | Yes | Yes | 19.1 | 21 | -1.9 | 58A4CAAF89B5409BADA5ABB4F165A566 |  | R410A | TXV |  | 3.988% | 0.96012 | 7.665% | [5 empty] | TXV | 3.988%
Stockton | CA | 95206-2308 |  | 2014-06-06 | 2014-06-06 09:59 | 2014-06-06 10:18 | RUUD - URMA-A030JK060 | 80 | 8.6 | Yes | Yes | 22.2 | 20.1 | 2.1 | 00393F757B8644B6BFEC36EADF2FE755 |  | R22 | Non-TXV |  | 10.75% | 0.8925 | 20.66% | [5 empty] | Non-TXV | 10.75%
Chico | CA | 95973-7216 |  | 2014-06-20 | 2014-06-20 16:15 | 2014-06-20 16:35 | RHEEM - RAKA-024JAZ | 50 | -2.9 | Yes | Yes | 20 | 21.3 | -1.3 | 78913090612F4ED8B25B6435C1F46213 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Clovis | CA | 93611-0629 |  | 2014-06-14 | 2014-06-14 14:32 | 2014-06-14 15:07 | DAY & NIGHT - N/A | 90 | 3.9 | Yes | Yes | 22.2 | 20.9 | 1.3 | 31CC9C42F44E4E979CE5DA76382A442D |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Stockton | CA | 95210-6700 |  | 2014-05-28 | 2014-05-28 11:21 | 2014-05-28 11:47 | RUUD - UNK | 64 | 4.4 | Yes | Yes | 23.9 | 22.6 | 1.3 | 4CDED9B938704EC1848F4C1AACAB2E50 |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Fresno | CA | 93703-1033 |  | 2014-05-15 | 2014-05-15 09:33 | 2014-05-15 10:45 | YORK - DAY-PF030N070A | 73 | 5.6 | Yes | Yes | 18 | 21 | -3 | ABF978F2561C45379B67B582BC2EA755 |  | R22 | Non-TXV |  | 7.671% | 0.92329 | 14.74% | [5 empty] | Non-TXV | 7.671%
Fresno | CA | 93726-2612 |  | 2014-05-26 | 2014-05-26 12:32 | 2014-05-26 12:57 | GOODMAN - GPG10480901A | 116 | 10.4 | Yes | Yes | 28.3 | 22.9 | 5.4 | 4E6995D9D0C449B6AC046D8582E7CBFE |  | R22 | Non-TXV |  | 8.966% | 0.91034 | 17.23% | [5 empty] | Non-TXV | 8.966%
Oroville | CA | 95966-3954 |  | 2014-06-12 | 2014-06-12 08:53 | 2014-06-12 09:11 | COLEMAN - 3236-901 | 102 | 3.8 | Yes | Yes | 17.3 | 19.9 | -2.6 | 18E2ED92E04E461AB880C2249F47391D |  | R22 | Non-TXV |  | 3.725% | 0.96275 | 7.16% | [5 empty] | Non-TXV | 3.725%
Manteca | CA | 95336-9193 |  | 2014-05-16 | 2014-05-16 09:08 | 2014-05-16 09:28 | TRANE - 2TTR1036A1000AA | 73 | 6 | Yes | Yes | 19.8 | 21.3 | -1.5 | 2E3EC229C68741E2A1454E71A0FA865D |  | R22 | Non-TXV |  | 8.219% | 0.91781 | 15.8% | [5 empty] | Non-TXV | 8.219%
Stockton | CA | 95205-2593 |  | 2014-06-05 | 2014-06-05 09:24 | 2014-06-05 09:45 | CARRIER - 38EZGO36310 | 102 | 10.9 | Yes | Yes | 20 | 20.2 | -0.1 | 4586AA3A54574BF9A069096A22C6EBD6 |  | R410A | Non-TXV |  | 10.69% | 0.89314 | 20.54% | [5 empty] | Non-TXV | 10.69%
Clovis | CA | 93612-4435 |  | 2014-06-03 | 2014-06-03 13:56 | 2014-06-03 13:57 | GOODMAN - CKL36-1K | 84 | 4.5 | Yes | Yes | 24.9 | 21.1 | 3.9 | 0E8FDB817C6449F793EA902B69E9F477 |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Clovis | CA | 93611-0649 |  | 2014-05-30 | 2014-05-30 11:32 | 2014-05-30 11:33 | AMERICAN STANDARD - YCP024F1MOBA | 118 | 6.4 | Yes | Yes | 24.2 | 22.2 | 2 | AAB618AA7C694C19B423502C3002CC23 |  | R22 | Non-TXV |  | 5.424% | 0.94576 | 10.42% | [5 empty] | Non-TXV | 5.424%
Clovis | CA | 93611-0649 |  | 2014-05-30 | 2014-05-30 11:40 | 2014-05-30 11:41 | CARRIER - 48KL036300BE | 76 | 3.5 | Yes | Yes | 25.2 | 21.9 | 3.3 | 421C567F19834F40A8ABA678548E5500 |  | R22 | Non-TXV |  | 4.605% | 0.95395 | 8.85% | [5 empty] | Non-TXV | 4.605%
Fresno | CA | 93702-2352 |  | 2014-07-09 | 2014-07-09 10:08 | 2014-07-09 10:28 | GOODMAN - GPG13300451AB | 77 | 2.5 | Yes | Yes | 17.5 | 18.8 | -1.3 | ADD11DB4A1014916B2A3BD17FA67E811 |  | R22 | Non-TXV |  | 3.247% | 0.96753 | 6.24% | [5 empty] | Non-TXV | 3.247%
Fresno | CA | 93722-4728 |  | 2014-05-23 | 2014-05-23 12:21 | 2014-05-23 12:23 | CARRIER - 7777UNK | 102 | 3.4 | Yes | Yes | 23.3 | 21 | 2.3 | AA40E74E7F984D48B9AC4E9C6426FFF0 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Kerman | CA | 93630-9754 |  | 2014-06-18 | 2014-06-18 12:21 | 2014-06-18 12:32 | CARRIER - UNK | 76 | 18.3 | Yes | Yes | 21.5 | 19.2 | 2.3 | 04FAF556A9D445F5AB5D401E0766A221 |  | R22 | Non-TXV |  | 24.08% | 0.75921 | 46.27% | [5 empty] | Non-TXV | 24.08%
Kerman | CA | 93630-9754 |  | 2014-06-18 | 2014-06-18 12:33 | 2014-06-18 12:45 | CARRIER - UNK | 76 | 12.2 | Yes | Yes | 22.7 | 19.3 | 3.4 | 0C28D922BA5C4F67AB9B665D533BDB17 |  | R22 | Non-TXV |  | 16.05% | 0.83947 | 30.85% | [5 empty] | Non-TXV | 16.05%
Fresno | CA | 93722-7309 |  | 2014-05-27 | 2014-05-27 10:22 | 2014-05-27 10:39 | CARRIER - 48SS036060301 | 67 | 7.6 | Yes | Yes | 21.3 | 18.8 | 2.5 | 93A216CA75B14E5CAFAD5724CA33380E |  | R22 | Non-TXV |  | 11.34% | 0.88657 | 21.8% | [5 empty] | Non-TXV | 11.34%
Stockton | CA | 95210-1865 |  | 2014-05-26 | 2014-05-26 10:11 | 2014-05-26 10:27 | YORK - D3NZ030N05606NXA | 64 | 2.8 | Yes | Yes | 22.9 | 19.7 | 3.3 | BBB11F63760048C8A6791CC28B6F8F90 |  | R410A | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Oroville | CA | 95965-9114 |  | 2014-05-29 | 2014-05-29 11:02 | 2014-05-29 11:21 | AMERICAN STANDARD - YCZ036F1M0BD | 160 | 4.9 | Yes | Yes | 23 | 22.8 | 0.2 | E18280C1D0464ADF92A180E797BC2264 |  | R22 | Non-TXV |  | 3.062% | 0.96937 | 5.885% | [5 empty] | Non-TXV | 3.062%
Durham | CA | 95938-9615 |  | 2014-06-03 | 2014-06-03 08:26 | 2014-06-03 21:05 | OTHER - NA | 65 | 7 | Yes | Yes | 17.5 | 18.8 | -1.3 | 6334BC75EB0B4A82A213BFDF84A845E0 |  | R22 | Non-TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | Non-TXV | 10.77%
Paradise | CA | 95969-4314 |  | 2014-06-05 | 2014-06-05 15:23 | 2014-06-05 15:56 | BRYANT - 58A6110AAHFNW03 | 65 | 4.1 | Yes | Yes | 23 | 20.4 | 2.6 | 7A6E2B5656EE4D6D9CAF5A94D0A2254C |  | R22 | Non-TXV |  | 6.308% | 0.93692 | 12.12% | [5 empty] | Non-TXV | 6.308%
Stockton | CA | 95215-8229 |  | 2014-06-10 | 2014-06-10 11:48 | 2014-06-10 12:11 | DAY & NIGHT - 591ANX030000ABAA | 65 | -3.8 | Yes | Yes | 21.5 | 20.9 | 0.6 | A9FD1D3597F145ADB032C60B17ECFC36 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Stockton | CA | 95207-8120 |  | 2014-05-29 | 2014-05-29 10:47 | 2014-05-29 10:47 | DAY & NIGHT - 585EJW024050ABAF | 54 | 0 | Yes | Yes | 20.9 | 18.8 | 2.1 | DF513247F93D4E8FADADB825D85F65C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-8120 |  | 2014-05-23 | 2014-05-23 13:06 | 2014-05-23 23:46 | TRANE - 2TTB03060A100AA | 135 | 7.1 | Yes | Yes | 23.5 | 20.4 | 3.1 | EAB739FAB5F542F68A7BD5AE863F65B3 |  | R22 | Non-TXV |  | 5.259% | 0.94741 | 10.11% | [5 empty] | Non-TXV | 5.259%
Paradise | CA | 95969-8120 |  | 2014-05-23 | 2014-05-23 23:48 | 2014-05-23 12:09 | TRANE - 2TTB03024A100AA | 82 | 5.1 | Yes | Yes | 22 | 20.4 | 1.6 | CF091807A5694EDF992C4F9A8BA4D39C |  | R22 | Non-TXV |  | 6.22% | 0.9378 | 11.95% | [5 empty] | Non-TXV | 6.22%
Magalia | CA | 95954-9014 |  | 2014-06-04 | 2014-06-04 09:17 | 2014-06-04 09:33 | BDP - 542EJX03600AAAE | 72 | 4.6 | Yes | Yes | 27 | 23.4 | 3.6 | B1392F377BCC4E0B8A8AEC9D173E0266 |  | R22 | Non-TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | Non-TXV | 6.389%
Oakdale | CA | 95361-3381 |  | 2014-05-19 | 2014-05-19 12:04 | 2014-05-19 12:27 | RHEEM - UNK | 85 | 10.9 | Yes | Yes | 18.5 | 19.9 | -1.4 | 40DA9333B2F54CA8A76634F59DA41AA3 |  | R22 | Non-TXV |  | 12.82% | 0.87176 | 24.64% | [5 empty] | Non-TXV | 12.82%
Oakdale | CA | 95361-7703 |  | 2014-05-19 | 2014-05-19 14:10 | 2014-05-19 14:52 | YORK - H4DH036S06 | 95 | 4.8 | Yes | Yes | 18.5 | 20.8 | -2.3 | 5D3B12B99F174AAD87FFACF6FE54CF4E |  | R22 | Non-TXV |  | 5.053% | 0.94947 | 9.71% | [5 empty] | Non-TXV | 5.053%
Manteca | CA | 95336-3149 |  | 2014-05-15 | 2014-05-15 15:18 | 2014-05-15 15:43 | BRYANT - 574DNWA36060NA | 136 | -5.1 | Yes | Yes | 23.3 | 19.5 | 3.8 | 55F3BF58C5864EB7A25A8C5D2C3C2038 |  | R22 | Non-TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | Non-TXV |  |  | -3.75%
Fresno | CA | 93727-5532 |  | 2014-07-09 | 2014-07-09 10:44 | 2014-07-09 11:08 | GOODMAN - PGBO60100-1 | 91 | 3.3 | Yes | Yes | 19.3 | 18.6 | 0.7 | 925C1C5AA32046AE895D951D7D68F8C4 |  | R22 | Non-TXV |  | 3.626% | 0.96374 | 6.969% | [5 empty] | Non-TXV | 3.626%
Paso Robles | CA | 93446-5094 |  | 2014-06-24 | 2014-06-24 11:10 | 2014-06-24 11:27 | CARRIER - 38EN024310 | 61 | 15.1 | Yes | Yes | 21.1 | 19.8 | 1.3 | C81FC157983F4E60A7497FD0DA5DDB86 |  | R22 | Non-TXV |  | 24.75% | 0.75246 | 47.57% | [5 empty] | Non-TXV | 24.75%
Fresno | CA | 93722-3508 |  | 2014-05-20 | 2014-05-20 21:02 | 2014-05-20 21:05 | OTHER - 7777UNK | 80 | 2.6 | Yes | Yes | 17.5 | 20.1 | -2.6 | 242431BF6E5D4DF2A40750B4432D5CDA |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Clovis | CA | 93612-2545 |  | 2014-06-23 | 2014-06-23 15:34 | 2014-06-23 15:56 | OTHER - M R51-36PI | 99 | 3 | Yes | Yes | 21.1 | 22.1 | -1 | 054A56E817284431A440FA95E02239C6 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Yuba City | CA | 95993-5622 |  | 2014-05-21 | 2014-05-21 17:20 | 2014-05-21 17:20 | LENNOX - HS26-036-3P | 90 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 128E1CA380D84D539C5CFC4A7FF6BB14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-5622 |  | 2014-05-21 | 2014-05-21 17:22 | 2014-05-21 17:22 | LENNOX - HS26-060-3P | 165 | 0 | Yes | Yes | 26 | 24.2 | 1.8 | 9E523D389466403DAE2153CB607FA1C9 |  | R22 | TXV |  | 0% | 1 | 0%
Fowler | CA | 93625-2521 |  | 2014-07-31 | 2014-07-31 12:04 | 2014-07-31 12:24 | RUUD - URKA-A030JK06E | 54 | 5.2 | Yes | Yes | 21.5 | 20.4 | 1.1 | 30DB288BFE024A9A93107A6193ADFF19 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.63% | 0.9037 | 18.51% | [5 empty] | Non-TXV | 9.63%
Chico | CA | 95926-7362 |  | 2014-05-19 | 2014-05-19 10:08 | 2014-05-19 10:29 | UNK - UNK | 85 | 2.4 | Yes | Yes | 23.2 | 22.2 | 1 | EA97E06AE13C4B6DBA71A4D154AF8668 |  |  |  |  | 2.824% | 0.97176 | 5.426% | [5 empty] | 0 | 2.824%
Fresno | CA | 93722-9084 |  | 2014-05-29 | 2014-05-29 14:10 | 2014-05-29 14:25 | LENNOX - 12GCS036753PA | 110 | 16.3 | Yes | Yes | 23 | 19.9 | 3.1 | 16C8FAC8CB1444F7B3DAECCE7701847B |  | R22 | Non-TXV |  | 14.82% | 0.85182 | 28.48% | [5 empty] | Non-TXV | 14.82%
Fresno | CA | 93703-1226 |  | 2014-05-20 | 2014-05-20 13:23 | 2014-05-20 13:27 | NORDYNE - GR6GD-X30K045X | 96 | 11 | Yes | Yes | 22.9 | 20.9 | 2 | 049EA613A96246E4AF2A8D8E4C9C8691 |  | R410A | TXV |  | 11.46% | 0.88542 | 22.02% | [5 empty] | TXV | 11.46%
Paradise | CA | 95969-6051 |  | 2014-05-23 | 2014-05-23 11:31 | 2014-05-23 13:10 | CARRIER - 480L003 | 65 | 2.6 | Yes | Yes | 17.8 | 20.4 | -2.6 | 1D65642D7D6B46EE9A74138936D83265 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95212-3144 |  | 2014-06-06 | 2014-06-06 14:13 | 2014-06-06 14:41 | YORK - H2RA036S06G | 63 | 5.7 | Yes | Yes | 20 | 21 | -1 | 97453474A0944B89BA923E3637A4BFF5 |  | R22 | Non-TXV |  | 9.048% | 0.90952 | 17.39% | [5 empty] | Non-TXV | 9.048%
Fresno | CA | 93726-2322 |  | 2014-07-02 | 2014-07-02 15:20 | 2014-07-02 15:50 | RHEEM - HC-100-42-21C | 72 | 10.4 | Yes | Yes | 21.5 | 22.1 | -0.6 | A78A962C784448DFA2EAC5107587469B |  | R22 | Non-TXV |  | 14.44% | 0.85556 | 27.76% | [5 empty] | Non-TXV | 14.44%
Durham | CA | 95938-9505 |  | 2014-06-02 | 2014-06-02 11:49 | 2014-06-02 12:05 | OTHER - N2A336AKB200 | 84 | 4.8 | Yes | Yes | 18.7 | 21.4 | -2.7 | EA11987698D54DFDB29087DC5796AD62 |  | R22 | TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | TXV | 5.714%
Paso Robles | CA | 93446-5094 |  | 2014-06-24 | 2014-06-24 10:51 | 2014-06-24 11:10 | CARRIER - 38EN024310 | 61 | -3.6 | Yes | Yes | 20 | 20.7 | -0.7 | 8263738BC21E4588900F291C4BEA08A2 |  | R22 | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Stockton | CA | 95210-3223 |  | 2014-08-07 | 2014-08-07 15:30 | 2014-08-07 15:49 | GE - BTB936A100C1 | 83 | -4.9 | Yes | Yes | 28.6 | 22.6 | 6 | 436ADD6A98744A1B958219D0124F7749 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Clovis | CA | 93612-1318 |  | 2014-06-03 | 2014-06-03 11:19 | 2014-06-03 11:31 | WEATHER KING - WRKA-A030JK06E | 54 | 8.4 | Yes | Yes | 19.9 | 22.9 | -3 | 068696A046344249BF9B2509AB1316CD |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Stockton | CA | 95207-8123 |  | 2014-05-29 | 2014-05-29 09:03 | 2014-05-29 09:20 | DAY & NIGHT - 585EJW024050ABAE | 54 | 2 | Yes | Yes | 23.5 | 19.9 | 3.6 | 040C90D3C05640DD9E6D719B50E4D9E1 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Chico | CA | 95973-1226 |  | 2014-05-21 | 2014-05-21 09:09 | 2014-05-21 09:28 | YORK - NA | 95 | 3 | Yes | Yes | 23.8 | 21 | 2.8 | 500EE893D4AC49AD9DFA47D9D3C54C3B |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Fresno | CA | 93722-2229 |  | 2014-05-28 | 2014-05-28 08:35 | 2014-05-28 09:12 | OTHER - H2DH048S06B | 190 | 20.1 | Yes | Yes | 20.5 | 18.7 | 1.8 | E620971C4D404752BBE7DE2B005A001B |  | R22 | Non-TXV |  | 10.58% | 0.89421 | 20.33% | [5 empty] | Non-TXV | 10.58%
Stockton | CA | 95206-5528 |  | 2014-06-05 | 2014-06-05 08:55 | 2014-06-05 09:21 | PAYNE - 591ANX042000ABAA | 85 | 2.5 | Yes | Yes | 19.6 | 19.9 | -0.3 | 9DCBDB50EFD0490EADCF5DFB0128D30F |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Paradise | CA | 95969-6008 |  | 2014-05-23 | 2014-05-23 15:12 | 2014-05-23 15:45 | BRYANT - 582AN11024060AAA | 85 | 2.8 | Yes | Yes | 26.5 | 21.3 | 5.3 | C24265CF099A4470B524714CFD26523A |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fresno | CA | 93722-2527 |  | 2014-07-02 | 2014-07-02 09:08 | 2014-07-02 09:09 | LENNOX - GCS26X042752PA | 133 | 29.4 | Yes | Yes | 22.8 | 18.8 | 4 | E7377F70E1844B02941942875A16C3A5 |  | R22 | Non-TXV |  | 22.11% | 0.77895 | 42.48% | [5 empty] | Non-TXV | 22.11%
Clovis | CA | 93612-5895 |  | 2014-06-07 | 2014-06-07 13:58 | 2014-06-07 14:19 | CARRIER - 38BR042300 | 131 | 4.1 | Yes | Yes | 20.8 | 22.1 | -1.3 | AB0EF6B82742424DA25292BED9A927C0 |  | R22 | Non-TXV |  | 3.13% | 0.9687 | 6.015% | [5 empty] | Non-TXV | 3.13%
Fresno | CA | 93705-4000 |  | 2014-05-28 | 2014-05-28 11:26 | 2014-05-28 11:27 | RHEEM - RAKA-048JAZ | 103 | 3.1 | Yes | Yes | 21.2 | 22.6 | -1.4 | 9398B841343A48C0B5DD02A1F14DBDB1 |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Clovis | CA | 93611-6280 |  | 2014-06-12 | 2014-06-12 13:58 | 2014-06-12 13:59 | OTHER - 38BRB042300 | 138 | 4.5 | Yes | Yes | 25.1 | 21.2 | 3.9 | 82D5FE17AB0F408B8D5B252AB8C33299 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Fresno | CA | 93726-2645 |  | 2014-05-26 | 2014-05-26 13:17 | 2014-05-26 13:46 | CARRIER - 48SX-036080321 | 84 | 2.5 | Yes | Yes | 20.6 | 21.3 | -0.7 | 919431F82C3243C1AA3C5FBFC7EE996E |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Paradise | CA | 95969-3046 |  | 2014-06-13 | 2014-06-13 12:11 | 2014-06-13 12:50 | GOODMAN - GPG13360901A | 112 | 3.8 | Yes | Yes | 27.8 | 21.8 | 6 | A0F2E3F02F3C4EF0AE1D796156345895 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Oroville | CA | 95965-8362 |  | 2014-06-04 | 2014-06-04 11:01 | 2014-06-04 11:17 | OTHER - BRCQ0361BDG | 52 | 2.7 | Yes | Yes | 18 | 18.8 | -0.8 | F2FD4E6EF3934293A1908811FACD8261 |  | R22 | Non-TXV |  | 5.192% | 0.94808 | 9.978% | [5 empty] | Non-TXV | 5.192%
Chico | CA | 95973-0679 |  | 2014-06-10 | 2014-06-10 15:00 | 2014-06-10 15:15 | RHEEM - RAFD-030JAS | 69 | 7.4 | Yes | Yes | 24 | 21.8 | 2.2 | C8715EC93D7D4AEC8035C0EB030ACBFD |  | R22 | Non-TXV |  | 10.72% | 0.89275 | 20.61% | [5 empty] | Non-TXV | 10.72%
Chico | CA | 95928-5926 |  | 2014-05-19 | 2014-05-19 12:53 | 2014-05-19 13:10 | UNK - UNK | 85 | 3.8 | Yes | Yes | 17.9 | 20.9 | -3 | E31F5415F7E341E4881AE53C0077A40A |  |  |  |  | 4.471% | 0.95529 | 8.591% | [5 empty] | 0 | 4.471%
Lathrop | CA | 95330-8918 |  | 2014-07-07 | 2014-07-07 12:33 | 2014-07-07 12:56 | GOODMAN - CKJ48-1A | 85 | 8.5 | Yes | Yes | 22.7 | 21 | 1.7 | F56D94EC40FE4C338BEAD0B66E4B2CC8 |  | R22 | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Atwater | CA | 95301-2924 |  | 2014-05-19 | 2014-05-19 13:55 | 2014-05-19 13:57 | RHEEM - RRKA-A018JK04X | 44 | 2.3 | Yes | Yes | 17.6 | 20.4 | -2.8 | 3275257FD7734CA5B8FD05FD416A9C04 |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Fresno | CA | 93703-4705 |  | 2014-05-20 | 2014-05-20 15:43 | 2014-05-20 16:20 | BDP - 585A030080 | 50 | 12.7 | Yes | Yes | 19.4 | 22.3 | -2.9 | C780E94E23FF4857B1AB8BDD8549BE5C |  | R22 | Non-TXV |  | 25.4% | 0.746 | 48.81% | [5 empty] | Non-TXV | 25.4%
Manteca | CA | 95336-3028 |  | 2014-05-16 | 2014-05-16 11:29 | 2014-05-16 11:51 | PAYNE - 593AN060-A | 249 | 8.4 | Yes | Yes | 23.5 | 23.1 | 0.4 | 86C24A08766F4BBF98F751008ADD6039 |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Paradise | CA | 95969-2222 |  | 2014-06-11 | 2014-06-11 14:22 | 2014-06-11 14:45 | CARRIER - 138TH030310 | 68 | 2.1 | Yes | Yes | 25.5 | 20.7 | 4.8 | D25D1E81E13449DDBDAF79A1A3D761D4 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Fresno | CA | 93727-5531 |  | 2014-07-07 | 2014-07-07 11:18 | 2014-07-07 11:37 | BDP - 563ANX042-A | 131 | 4.2 | Yes | Yes | 19.2 | 20.4 | -1.2 | D4EADD913BFD4944895AC0ADC7DC2820 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.206% | 0.96794 | 6.161% | [5 empty] | Non-TXV | 3.206%
Manteca | CA | 95336-3716 |  | 2014-05-14 | 2014-05-14 10:48 | 2014-05-14 11:13 | YORK - H1RD036S06A | 145 | 4.5 | Yes | Yes | 21.1 | 22 | -0.9 | 05B644186A16437F80C699D41923F0ED |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Stockton | CA | 95212-3043 |  | 2014-06-06 | 2014-06-06 09:31 | 2014-06-06 09:55 | CARRIER - UNK | 100 | 3.7 | Yes | Yes | 18 | 20.7 | -2.7 | 9FBB0FA404684867B2F813FA7B574DCE |  | R22 | Non-TXV |  | 3.7% | 0.963 | 7.111% | [5 empty] | Non-TXV | 3.7%
Fresno | CA | 93722-3731 |  | 2014-05-27 | 2014-05-27 11:05 | 2014-05-27 11:21 | LENNOX - 12ACB424P | 128 | 11.1 | Yes | Yes | 19.5 | 17.5 | 2 | 49A49754F2264593B202D9CFBB153B4A |  | R22 | TXV |  | 8.672% | 0.91328 | 16.67% | [5 empty] | TXV | 8.672%
Fresno | CA | 93705-3839 |  | 2014-08-15 | 2014-08-15 12:25 | 2014-08-15 12:46 | OTHER - UNK | 83 | 2.4 | Yes | Yes | 17.2 | 19 | -1.8 | 60346A2C91504E16A80674079BB7F392 |  | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Merced | CA | 95341-5600 |  | 2014-07-03 | 2014-07-03 08:54 | 2014-07-03 08:56 | LENNOX - 13ACD-060-230-01 | 214 | 6.3 | Yes | Yes | 22.9 | 20.4 | 2.5 | DB60F3EC7EEF46C19E45EA5782E91A82 |  | R22 | Non-TXV |  | 2.944% | 0.97056 | 5.658% | [5 empty] | Non-TXV | 2.944%
Fresno | CA | 93702-4617 |  | 2014-05-22 | 2014-05-22 12:51 | 2014-05-22 13:11 | TRANE - TTP036C100A3 | 132 | 4.9 | Yes | Yes | 20.6 | 21.5 | -0.9 | 02C90B10266346BBB6B6B895C1A7F6CD |  | R22 | Non-TXV |  | 3.712% | 0.96288 | 7.134% | [5 empty] | Non-TXV | 3.712%
Clovis | CA | 93612-2337 |  | 2014-06-30 | 2014-06-30 13:10 | 2014-06-30 13:11 | BRYANT - 574ANW036060NGB | 114 | 17.3 | Yes | Yes | 24.1 | 22.1 | 2 | DB04F8C6E64E4A76BC2005E85D36C863 |  | R22 | Non-TXV |  | 15.18% | 0.84825 | 29.16% | [5 empty] | Non-TXV | 15.18%
Selma | CA | 93662-2345 |  | 2014-06-13 | 2014-06-13 09:44 | 2014-06-13 10:04 | COLEMAN - D6NZ030N05606NXA | 64 | 2.6 | Yes | Yes | 19.9 | 19.3 | 0.6 | 72D44163C2EA4D7798D42F7F8F8F1B25 |  | R410A | TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | TXV | 4.062%
Fresno | CA | 93726-1829 |  | 2014-05-28 | 2014-05-28 13:52 | 2014-05-28 14:14 | BARD - PH1130 | 93 | 3.1 | Yes | Yes | 25.3 | 22.6 | 2.7 | 32F4E7B6CCFF4B8FAFD51CAA81BE2F9F |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Mendota | CA | 93640-2048 |  | 2014-07-11 | 2014-07-11 22:59 | 2014-07-11 23:04 | OTHER - 777UNK | 80 | 3.5 | Yes | Yes | 20.1 | 19.1 | 1.1 | 6386A1A1F2724A4BB03A027CCE6A1E30 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Atwater | CA | 95301-3179 |  | 2014-07-02 | 2014-07-02 08:17 | 2014-07-02 08:41 | OTHER - TZPA-330-2A | 85 | 2.6 | Yes | Yes | 21.1 | 19.8 | 1.3 | 1692ABF0538C453CAE23286242689F35 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93726-4306 |  | 2014-05-27 | 2014-05-27 15:34 | 2014-05-27 16:00 | PAYNE - PY3GNAA48090NA | 100 | 4.6 | Yes | Yes | 25.1 | 21.3 | 3.8 | FABB9065B8AC43F49C0FB272265CEFA9 |  | R410A | TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | TXV | 4.6%
Paradise | CA | 95969-4349 |  | 2014-07-25 | 2014-07-25 15:04 | 2014-07-25 15:21 | GOODMAN - GPG13300070M | 80 | 2.7 | Yes | Yes | 20.5 | 19.9 | 0.6 | 2B1DDAD511AA4CD3B8E2994F1770CDAE |  | R410A | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Yuba City | CA | 95993-7624 |  | 2014-05-28 | 2014-05-28 12:26 | 2014-05-28 12:53 | RUUD - UNK | 95 | 2.8 | Yes | Yes | 25 | 21.5 | 3.5 | 166C3692DA5B481985CB0C5A95E4E708 |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Fresno | CA | 93728-3450 |  | 2014-08-28 | 2014-08-28 12:40 | 2014-08-28 12:41 | GOODMAN - GPG1324045M41DA | 75 | 7.6 | Yes | Yes | 25.6 | 22.1 | 3.6 | 3570265F7F82478C838ABBA968627C4C |  | R410A | Non-TXV |  | 10.13% | 0.89867 | 19.47% | [5 empty] | Non-TXV | 10.13%
Paradise | CA | 95969-5428 |  | 2014-05-22 | 2014-05-22 14:57 | 2014-05-22 15:14 | GOODMAN - CDLJ48-1A | 152 | 5.2 | Yes | Yes | 20.9 | 21.5 | -0.6 | AC873CAAFC0E4C6FABF2B8E348B1C8D1 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Fresno | CA | 93722-3345 |  | 2014-06-05 | 2014-06-05 09:43 | 2014-06-05 10:03 | CARRIER - 4SNLT36200 | 90 | 14.1 | Yes | Yes | 19.4 | 20.4 | -1 | E108D3DB4B5B43EB86B8FE850992D7E0 |  | R22 | Non-TXV |  | 15.67% | 0.84333 | 30.11% | [5 empty] | Non-TXV | 15.67%
Chico | CA | 95928-6992 |  | 2014-05-21 | 2014-05-21 10:59 | 2014-05-21 12:23 | CARRIER - CNPVP3014ACAAABAA | 59 | 3.5 | Yes | Yes | 17.4 | 18.8 | -1.4 | 8DF9794BD1FA4A538B961117D7C7123A |  | R410A | Non-TXV |  | 5.932% | 0.94068 | 11.4% | [5 empty] | Non-TXV | 5.932%
Fresno | CA | 93727-5413 |  | 2014-06-27 | 2014-06-27 15:19 | 2014-06-27 15:43 | GOODMAN - GSC130601CB | 131 | 4.2 | Yes | Yes | 20.4 | 21.3 | -0.9 | 0F82BC734BF24009AFDB9E661D4AEA04 |  | R22 | Non-TXV |  | 3.206% | 0.96794 | 6.161% | [5 empty] | Non-TXV | 3.206%
Fresno | CA | 93727-5413 |  | 2014-06-27 | 2014-06-27 15:46 | 2014-06-27 16:06 | OTHER - N/A | 120 | 13.4 | Yes | Yes | 20 | 21.8 | -1.8 | 79417212319B423EA93074C063C602F9 |  | R22 | Non-TXV |  | 11.17% | 0.88833 | 21.46% | [5 empty] | Non-TXV | 11.17%
Paradise | CA | 95969-4240 |  | 2014-05-23 | 2014-05-23 16:14 | 2014-05-23 16:44 | OTHER - JS18BC030KA | 40 | 1.4 | Yes | Yes | 22.5 | 22 | 0.5 | A4F0F811421C4407AD8E205A22D27782 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Clovis | CA | 93611-3960 |  | 2014-06-03 | 2014-06-03 21:20 | 2014-06-03 21:23 | CARRIER - 38BRC030370 | 80 | 2.4 | Yes | Yes | 24.9 | 22.1 | 2.8 | 1BE3DD2280CB4E22ADE36D20571647D0 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93612-1945 |  | 2014-06-07 | 2014-06-07 12:44 | 2014-06-07 13:12 | CARRIER - N/A | 152 | -11.8 | Yes | Yes | 18.5 | 21.4 | -2.9 | 43EA0B33BFCD4E8790F1F0D4E4EC4A9B |  | R410A | TXV |  | -7.763% | 1.0776 | 2.174% |  |  |  |  | TXV |  |  | -7.763%
Firebaugh | CA | 93622-2136 |  | 2014-08-06 | 2014-08-06 13:54 | 2014-08-06 14:16 | GOODMAN - VSX130601BA | 125 | 3.7 | Yes | Yes | 24.8 | 20.6 | 4.2 | 1B4E899E50C44DA58C4753D3744E372A |  | R410A | Non-TXV |  | 2.96% | 0.9704 | 5.688% | [5 empty] | Non-TXV | 2.96%
Merced | CA | 95348-9544 |  | 2014-06-06 | 2014-06-06 09:44 | 2014-06-06 10:14 | LENNOX - 10ACC03023004 | 58 | 5.8 | Yes | Yes | 17.6 | 14.2 | 3.4 | 5CC541B405FE4A7F8654533731AF15AD |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Merced | CA | 95348-9544 |  | 2014-06-06 | 2014-06-06 10:15 | 2014-06-06 10:35 | LENNOX - 10ACC03023004 | 58 | 7.7 | Yes | Yes | 17.8 | 15.2 | 2.6 | C1B5D12C06C248F598D3A2896D609CAB |  | R22 | Non-TXV |  | 13.28% | 0.86724 | 25.51% | [5 empty] | Non-TXV | 13.28%
Fresno | CA | 93727-5611 |  | 2014-06-06 | 2014-06-06 08:47 | 2014-06-06 09:09 | ICP - PGC048K080D | 101 | 4 | Yes | Yes | 20.7 | 21.5 | -0.8 | FED35555835547DFAA8EA41A0C397807 |  | R22 | Non-TXV |  | 3.96% | 0.9604 | 7.611% | [5 empty] | Non-TXV | 3.96%
Fresno | CA | 93726-5233 |  | 2014-05-28 | 2014-05-28 12:47 | 2014-05-28 13:06 | PAYNE - N/A | 90 | 5.9 | Yes | Yes | 21 | 21.8 | -0.8 | 3164F9B1D8664BF6ABC8F1626527B392 |  | R22 | Non-TXV |  | 6.556% | 0.93444 | 12.6% | [5 empty] | Non-TXV | 6.556%
Fresno | CA | 93727-3680 |  | 2014-06-04 | 2014-06-04 12:48 | 2014-06-04 13:07 | LENNOX - 10GCS042-75-5PB | 133 | 4.4 | Yes | Yes | 18.3 | 18.3 | 0 | 35A8E8FC94D9427DAE7EF136997F7C35 |  | R22 | Non-TXV |  | 3.308% | 0.96692 | 6.358% | [5 empty] | Non-TXV | 3.308%
Madera | CA | 93638-0000 |  | 2014-06-03 | 2014-06-03 09:46 | 2014-06-03 10:05 | YORK - H2RD042S06B | 141 | 10.8 | Yes | Yes | 18.8 | 17.2 | 1.6 | 19FA2571326243C1B588D6B55F982F39 |  | R22 | Non-TXV |  | 7.66% | 0.9234 | 14.72% | [5 empty] | Non-TXV | 7.66%
Fresno | CA | 93705-2713 |  | 2014-05-27 | 2014-05-27 10:46 | 2014-05-27 10:48 | RHEEM - 7777UNK | 80 | 3 | Yes | Yes | 30.6 | 24.7 | 5.9 | 4E60C15A753C4723B628CD80E6E01E1B |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Reedley | CA | 93654-3507 |  | 2014-06-16 | 2014-06-16 13:25 | 2014-06-16 13:51 | ICP - PGAD30D1K5 | 78 | 7.8 | Yes | Yes | 22.2 | 22.3 | 0 | 282B025A5B244DE3BEC17FD9501DEC4D |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93704-4061 |  | 2014-06-25 | 2014-06-25 10:15 | 2014-06-25 10:16 | GOODMAN - GPG1324045M41AB | 80 | 6 | Yes | Yes | 22.8 | 18.2 | 4.6 | 903A6DBDFEAD428F88DD5B12F578497D |  | R410A | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95210-1864 |  | 2014-05-31 | 2014-05-31 08:49 | 2014-05-31 09:06 | YORK - CM30-1OA | 56 | -3.3 | Yes | Yes | 20.3 | 18.2 | 2.1 | 21F6056885C04E96A7918A68ED06A272 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Fresno | CA | 93722-3140 |  | 2014-05-28 | 2014-05-28 11:51 | 2014-05-28 12:14 | CARRIER - UNK | 58 | 6.5 | Yes | Yes | 21.3 | 18.8 | 2.5 | 69D21F2E4B6C4E94B3E613A2B8A50E9C |  | R22 | Non-TXV |  | 11.21% | 0.88793 | 21.54% | [5 empty] | Non-TXV | 11.21%
Fresno | CA | 93723-9289 |  | 2014-05-21 | 2014-05-21 13:35 | 2014-05-21 13:53 | DAY & NIGHT - UNK | 56 | 11.6 | Yes | Yes | 18.3 | 16.4 | 1.9 | C8DBFB355F4C40CBA42BF6DB09CC5F95 |  | R22 | Non-TXV |  | 20.71% | 0.79286 | 39.81% | [5 empty] | Non-TXV | 20.71%
Fowler | CA | 93625-9734 |  | 2014-08-23 | 2014-08-23 10:00 | 2014-08-23 10:27 | CARRIER - 48SX-042093311 | 167 | 6.1 | Yes | Yes | 21.6 | 20.4 | 1.2 | 4718C29B08D44D4F9B9345D005BD2B36 |  | R410A | TXV |  | 3.653% | 0.96347 | 7.02% | [5 empty] | TXV | 3.653%
Meadow Vista | CA | 95722-9302 |  | 2014-10-11 | 2014-10-11 09:02 | 2014-10-11 09:31 | RHEEM - RAFD-024JAS | 67 | 2.1 | Yes | Yes | 22 | 20.1 | 1.9 | A53FBCBF51AE47B087E37AA1C0F55EC0 |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Loomis | CA | 95650-9238 |  | 2014-05-22 | 2014-05-22 14:22 | 2014-05-22 14:22 | LENNOX - HS18-311-4P | 83 | 0 | Yes | Yes | 25 | 19.9 | 5.1 | 2DBC04BE30274F5B9EE0B80666C4D0A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-8123 |  | 2014-05-29 | 2014-05-29 09:23 | 2014-05-29 09:42 | RUUD - RRNL-B024JK06X | 77 | -4.5 | Yes | Yes | 22.9 | 19.7 | 3.2 | 15C68ADB7CE540DBBE09FF0088B41FCD |  | R410A | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Reedley | CA | 93654-3507 |  | 2014-06-16 | 2014-06-16 12:48 | 2014-06-16 13:22 | NORDYNE - N/A | 120 | 7.6 | Yes | Yes | 22 | 22.1 | -0.1 | F701F36234FF4908A74B9CAD9ADA2D92 |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Merced | CA | 95340-3436 |  | 2014-05-15 | 2014-05-15 11:47 | 2014-05-15 11:51 | TRANE - YCP030F1MOAB | 106 | 17.3 | Yes | Yes | 24.4 | 21.5 | 2.9 | 03D6922D1ACE415C9C4D88F7FF749F25 |  | R22 | Non-TXV |  | 16.32% | 0.83679 | 31.36% | [5 empty] | Non-TXV | 16.32%
Pollock Pines | CA | 95726-9305 |  | 2014-06-10 | 2014-06-10 11:13 | 2014-06-10 11:13 | PAYNE - UNK | 90 | 0 | Yes | Yes | 28 | 22.1 | 5.9 | 705B490EF3974371A3C53E52CEA80021 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-8702 |  | 2014-05-19 | 2014-05-19 11:31 | 2014-05-19 12:01 | UNK - UNK | 85 | 5.5 | Yes | Yes | 15.3 | 15.2 | 0.1 | F397E59094A244F88BDDDDAE08969644 |  |  |  |  | 6.471% | 0.93529 | 12.44% | [5 empty] | 0 | 6.471%
Merced | CA | 95348-8702 |  | 2014-05-19 | 2014-05-19 12:37 | 2014-05-19 12:44 | - | 85 | 3.3 | Yes | Yes | 15.5 | 15.5 | 0 | E84DF2072C8A4D1E903D78E08A885667 |  |  |  |  | 3.882% | 0.96118 | 7.461% | [5 empty] | 0 | 3.882%
Clovis | CA | 93611-2027 |  | 2014-06-02 | 2014-06-02 15:05 | 2014-06-02 15:07 | CARRIER - 48SX-030060331AA | 75 | 2.3 | Yes | Yes | 24.5 | 21.3 | 3.2 | 6ACCBF8CB83D4CF3AE855F750F1C18E2 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Merced | CA | 95348-8407 |  | 2014-08-16 | 2014-08-16 13:31 | 2014-08-16 13:36 | CARRIER - 7777UNK | 100 | 3.1 | Yes | Yes | 19.5 | 19.6 | -0.1 | 790C1E5060D047F6B90B54C1AC83078F |  | R410A | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Stockton | CA | 95209-2045 |  | 2014-05-20 | 2014-05-20 09:33 | 2014-05-20 09:51 | PAYNE - PY1PNB030060AAAA | 55 | 2.2 | Yes | Yes | 22.3 | 20.6 | 1.7 | 65334A6E750D4BDBA6CB2C4091DDA077 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Oroville | CA | 95965-4422 |  | 2014-05-27 | 2014-05-27 15:33 | 2014-05-27 15:50 | AMERICAN STANDARD - YCC024F1LOBJ | 67 | 2.6 | Yes | Yes | 23 | 21 | 2 | A4289B921CDD41489AFD51A56BB5C8B9 |  | R22 | Non-TXV |  | 3.881% | 0.96119 | 7.458% | [5 empty] | Non-TXV | 3.881%
Clovis | CA | 93619-7563 |  | 2014-06-26 | 2014-06-26 11:45 | 2014-06-26 12:02 | UNITARY PRODUCTS GROUP - H2RC048S06G | 119 | 3.7 | Yes | Yes | 18.8 | 20.4 | -1.6 | 0ABD12A78D164479AAB4CC6EF6C7D6EE |  | R22 | Non-TXV |  | 3.109% | 0.96891 | 5.975% | [5 empty] | Non-TXV | 3.109%
Merced | CA | 95340-1701 |  | 2014-05-15 | 2014-05-15 09:32 | 2014-05-15 09:36 | GOODMAN - PGB0480751 | 86 | 10.5 | Yes | Yes | 24.6 | 18.8 | 5.8 | 4BCC467D8B4E419D927FAF8F5020809E |  | R22 | Non-TXV |  | 12.21% | 0.87791 | 23.46% | [5 empty] | Non-TXV | 12.21%
Los Banos | CA | 93635-4037 |  | 2014-06-07 | 2014-06-07 09:43 | 2014-06-07 09:46 | OTHER - 7777UNK | 84 | 3.2 | Yes | Yes | 18.9 | 19.3 | -0.4 | 0958169245B549A48B71A7D3D3447CFE |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Coarsegold | CA | 93614-9305 |  | 2014-08-27 | 2014-08-27 13:35 | 2014-08-27 13:37 | RUUD - URGG05E30JKR | 46 | 6 | Yes | Yes | 25.1 | 20.9 | 4.2 | 7FD013112D994E4D965DE7A07674DCBC |  | R22 | Non-TXV |  | 13.04% | 0.86957 | 25.07% | [5 empty] | Non-TXV | 13.04%
Fresno | CA | 93706-5243 |  | 2014-05-20 | 2014-05-20 12:42 | 2014-05-20 13:00 | CARRIER - UNK | 70 | 6.8 | Yes | Yes | 23 | 20.4 | 2.6 | DFB671D1D50649BBA9FDC4CEA5E2F240 |  | R22 | Non-TXV |  | 9.714% | 0.90286 | 18.67% | [5 empty] | Non-TXV | 9.714%
Manteca | CA | 95337-5514 |  | 2014-05-15 | 2014-05-15 13:40 | 2014-05-15 14:07 | BRYANT - 113ANA036000BEAA | 114 | 4.8 | Yes | Yes | 21.2 | 21.1 | 0.1 | BC057EA086AC4890909104EF6868E4FD |  | R410A | TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | TXV | 4.211%
Stockton | CA | 95210-6744 |  | 2014-05-28 | 2014-05-28 13:56 | 2014-05-28 16:10 | BRYANT - 561CJ036-D | 84 | -6.9 | Yes | Yes | 18.6 | 19.3 | -0.7 | 4BF91A680264484A872C0E2923714D1D |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Fresno | CA | 93723-8107 |  | 2014-07-26 | 2014-07-26 08:31 | 2014-07-26 08:53 | LENNOX - 13ACD-060-230-01 | 85 | 2.6 | Yes | Yes | 22.1 | 18.8 | 3.3 | 98F4E33CA82A4575AB8A652BF90DFB92 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Yuba City | CA | 95993-9392 |  | 2014-05-19 | 2014-05-19 12:52 | 2014-05-19 12:09 | UNK - UNK | 85 | 0 | Yes | Yes | 21 | 19.9 | 1.1 | CBD4E23159934A40B45DE9B0C72A61B7 |  |  |  |  | 0% | 1 | 0%
Fresno | CA | 93726-1462 |  | 2014-05-28 | 2014-05-28 09:37 | 2014-05-28 10:00 | BDP - 585HJW030040 | 68 | 2 | Yes | Yes | 20.2 | 20.2 | 0 | F7B32F3931904D9F82ECC0766A73FE8E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95206-4755 |  | 2014-06-11 | 2014-06-11 11:12 | 2014-06-11 11:42 | RHEEM - RAKA-042JAS | 85 | -9 | Yes | Yes | 22.1 | 19.3 | 2.8 | AE14CD3027C5423AADFF3C7C4EE79763 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -10.59% | 1.1059 | 2.965% |  |  |  |  | Non-TXV |  |  | -10.59%
Stockton | CA | 95206-4751 |  | 2014-06-11 | 2014-06-11 15:27 | 2014-06-11 15:48 | BRYANT - 561CJ042-F | 93 | -10.7 | Yes | Yes | 22.7 | 21.1 | 1.6 | 7EB2C65F44BF419AB008737F940C8276 |  | R22 | TXV |  | -11.51% | 1.1151 | 3.222% |  |  |  |  | TXV |  |  | -11.51%
Fresno | CA | 93727-1917 |  | 2014-06-27 | 2014-06-27 11:32 | 2014-06-27 11:56 | PAYNE - PA10JA030-G | 77 | 2.4 | Yes | Yes | 18.5 | 20.4 | -1.9 | ED9A3793C8664A999EB04CB677806E33 |  | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Fowler | CA | 93625-2525 |  | 2014-09-11 | 2014-09-11 10:47 | 2014-09-11 10:49 | CARRIER - 588ANW042060ABAC | 82 | 2.9 | Yes | Yes | 19.4 | 21.5 | -2.1 | F165B73B1AD047AC9795B380967F094B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.537% | 0.96463 | 6.797% | [5 empty] | Non-TXV | 3.537%
Fresno | CA | 93722-6706 |  | 2014-05-23 | 2014-05-23 09:25 | 2014-05-23 09:48 | BDP - 585GJW030040ABAF | 58 | 10.6 | Yes | Yes | 19.2 | 16.8 | 2.4 | 7E19838AE7664730940E454E7349CEAB |  | R22 | Non-TXV |  | 18.28% | 0.81724 | 35.12% | [5 empty] | Non-TXV | 18.28%
Fresno | CA | 93722-7104 |  | 2014-05-23 | 2014-05-23 13:24 | 2014-05-23 13:35 | YORK - H1DS036S06A | 136 | 7 | Yes | Yes | 18.1 | 20.8 | -2.7 | 97B44835C3884E6B8CD67802F9E47DCF |  | R22 | Non-TXV |  | 5.147% | 0.94853 | 9.892% | [5 empty] | Non-TXV | 5.147%
Stockton | CA | 95209-3027 |  | 2014-05-19 | 2014-05-19 09:55 | 2014-05-19 10:18 | PAYNE - PA10JA024-A | 67 | 5.9 | Yes | Yes | 24.1 | 19.9 | 4.2 | 7D04F7F75F81413D8D4459D6C19F8884 |  | R22 | Non-TXV |  | 8.806% | 0.91194 | 16.92% | [5 empty] | Non-TXV | 8.806%
Fresno | CA | 93727-3676 |  | 2014-06-04 | 2014-06-04 13:28 | 2014-06-04 13:46 | LENNOX - 10GCS036X-75-3PB | 58 | 5.9 | Yes | Yes | 27.5 | 22.1 | 5.5 | 5F6F25E2863949C3845E4796CF508921 |  | R22 | Non-TXV |  | 10.17% | 0.89828 | 19.55% | [5 empty] | Non-TXV | 10.17%
Los Banos | CA | 93635-2816 |  | 2014-06-06 | 2014-06-06 10:50 | 2014-06-06 11:47 | TRANE - TTR024C100A1 | 58 | 7.9 | Yes | Yes | 23.9 | 21.5 | 2.4 | 2B544E965FE24DF2A70F21FEA2B07FF1 |  | R22 | Non-TXV |  | 13.62% | 0.86379 | 26.18% | [5 empty] | Non-TXV | 13.62%
Stockton | CA | 95210-2131 |  | 2014-06-13 | 2014-06-13 11:13 | 2014-06-13 11:31 | DAY & NIGHT - 567C030RCU | 63 | -3.7 | Yes | Yes | 23.6 | 19.3 | 4.3 | F7E792E7A1264FB686167CDE70275783 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Clovis | CA | 93619-9005 |  | 2014-06-26 | 2014-06-26 10:26 | 2014-06-26 10:44 | CARRIER - 48SDN036060311 | 130 | 4 | Yes | Yes | 19.3 | 21 | -1.7 | 181DEDB2A4214BEBA107206C303FFA45 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Clovis | CA | 93619-9005 |  | 2014-06-26 | 2014-06-26 10:47 | 2014-06-26 11:11 | PAYNE - PY3GNAA36060NA | 100 | 3.6 | Yes | Yes | 26.8 | 21.5 | 5.3 | 3B749E2EE6AB40F298AF9F5A843955B0 |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Merced | CA | 95348-1834 |  | 2014-05-15 | 2014-05-15 13:50 | 2014-05-15 14:08 | RHEEM - 13AJA36A01 | 85 | 9.7 | Yes | Yes | 17.7 | 18.9 | -1.2 | FA5DA413F2AC4D38B50FD49757B5C5E6 |  | R22 | Non-TXV |  | 11.41% | 0.88588 | 21.93% | [5 empty] | Non-TXV | 11.41%
Fresno | CA | 93704-1421 |  | 2014-06-16 | 2014-06-16 15:34 | 2014-06-16 15:35 | RHEEM - 7777UNK | 100 | 4.4 | Yes | Yes | 23.9 | 25.3 | -1.4 | 1ED09638719149D48D0034322C030151 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Merced | CA | 95348-2824 |  | 2014-05-19 | 2014-05-19 14:57 | 2014-05-19 15:14 | UNK - UNK | 85 | 19.2 | Yes | Yes | 22.9 | 18.2 | 4.7 | 4BDE799149C445828B07A0A0265BBCFC |  |  |  |  | 22.59% | 0.77412 | 43.41% | [5 empty] | 0 | 22.59%
Chico | CA | 95928-3810 |  | 2014-07-01 | 2014-07-01 11:30 | 2014-07-01 11:50 | RHEEM - RAKA-060JAS | 90 | 7.5 | Yes | Yes | 24.7 | 22.1 | 2.6 | 71A17F1D426E4DD588D8899CCA1F349F |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Paradise | CA | 95969-4349 |  | 2014-06-05 | 2014-06-05 11:36 | 2014-06-05 11:55 | DAY & NIGHT - 585HJW036060ACAF | 58 | 8.4 | Yes | Yes | 25.5 | 21.5 | 4 | DBAEDBD92E514052AFCB7E4B657ACA80 |  | R22 | Non-TXV |  | 14.48% | 0.85517 | 27.83% | [5 empty] | Non-TXV | 14.48%
Clovis | CA | 93619-9281 |  | 2014-06-30 | 2014-06-30 09:21 | 2014-06-30 09:22 | LENNOX - 13ACC06023002 | 168 | 36.2 | Yes | Yes | 20.4 | 18.2 | 2.2 | BF00F8D36B334B3193F8D5E0D2E91537 |  | R22 | Non-TXV |  | 21.55% | 0.78452 | 41.41% | [5 empty] | Non-TXV | 21.55%
Orange Cove | CA | 93646-2061 |  | 2014-09-04 | 2014-09-04 10:01 | 2014-09-04 10:21 | OTHER - DAYP-F024N045A | 74 | 2.5 | Yes | Yes | 18.9 | 20.9 | -2 | 36E052B5F2854EB685C3BDD0AAB1E136 |  | R22 | Non-TXV |  | 3.378% | 0.96622 | 6.492% | [5 empty] | Non-TXV | 3.378%
Fresno | CA | 93722-9150 |  | 2014-05-31 | 2014-05-31 13:14 | 2014-05-31 13:42 | BDP - 585HJW024040 | 68 | 4.2 | Yes | Yes | 21.5 | 20.7 | 0.8 | CC5B290478534E3AAE3DD3BB0E922BD7 |  | R22 | Non-TXV |  | 6.176% | 0.93824 | 11.87% | [5 empty] | Non-TXV | 6.176%
Orange Cove | CA | 93646-4000 |  | 2014-08-04 | 2014-08-04 10:33 | 2014-08-04 10:50 | RHEEM - RRNA-B042JK08X | 104 | 3.2 | Yes | Yes | 20.8 | 21.8 | -1 | CA889D066AD04580A96A9645304D4FC5 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Madera | CA | 93637-9615 |  | 2014-06-05 | 2014-06-05 15:03 | 2014-06-05 15:25 | RUUD - UPNO036J | 98 | 15.9 | Yes | Yes | 22 | 19.3 | 2.7 | 85A3786257DC43A39DA1DD31635CEA09 |  | R22 | Non-TXV |  | 16.22% | 0.83776 | 31.18% | [5 empty] | Non-TXV | 16.22%
Stockton | CA | 95210-2050 |  | 2014-05-26 | 2014-05-26 10:58 | 2014-05-26 11:15 | BRYANT - 585A030080YAC | 50 | 2.1 | Yes | Yes | 25.8 | 21.3 | 4.5 | 5A0B7FFD238E4CBC98B112A1D726800A |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Stockton | CA | 95210-1432 |  | 2014-05-16 | 2014-05-16 09:39 | 2014-05-16 10:02 | RHEEM - RRKA-A024JK06X | 50 | 2.6 | Yes | Yes | 22.7 | 19.5 | 3.2 | 83B339BF06424A89AC3BDBE89491882B |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Fresno | CA | 93726-1620 |  | 2014-05-23 | 2014-05-23 13:06 | 2014-05-23 13:38 | YORK - DCYZ0F042N080A | 78 | 3.9 | Yes | Yes | 22.3 | 19.4 | 2.9 | 0DA2E882CCFF475D97B541EF983B29D9 |  | R410A | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Fresno | CA | 93722-2415 |  | 2014-05-28 | 2014-05-28 10:11 | 2014-05-28 10:32 | LENNOX - 12ACB425P | 125 | 11 | Yes | Yes | 22.3 | 18.2 | 4.1 | 798A04980FD24C7AB1D59F4F83E9EA97 |  | R22 | Non-TXV |  | 8.8% | 0.912 | 16.91% | [5 empty] | Non-TXV | 8.8%
Fresno | CA | 93706-5224 |  | 2014-05-20 | 2014-05-20 12:17 | 2014-05-20 12:33 | LENNOX - 12GCS030753PA | 85 | 15.2 | Yes | Yes | 22 | 18.8 | 3.2 | E13E4EC509644EF4AA13644457D9D2FF |  | R22 | Non-TXV |  | 17.88% | 0.82118 | 34.37% | [5 empty] | Non-TXV | 17.88%
Fresno | CA | 93722-8606 |  | 2014-06-14 | 2014-06-14 12:49 | 2014-06-14 13:07 | LENNOX - 12GCS030-75-3PA | 85 | 7.4 | Yes | Yes | 21.9 | 21.4 | 0.5 | 2A1E956679C748DFB494B37560F6C589 |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Fresno | CA | 93703-4106 |  | 2014-05-19 | 2014-05-19 12:49 | 2014-05-19 13:00 | GOODMAN - GPG13360701AB | 112 | 5.3 | Yes | Yes | 27.1 | 21.2 | 5.9 | EFDA1C6362AA45248EAD4CFDAB1C488A |  | R22 | Non-TXV |  | 4.732% | 0.95268 | 9.094% | [5 empty] | Non-TXV | 4.732%
Fresno | CA | 93703-4106 |  | 2014-05-19 | 2014-05-19 13:04 | 2014-05-19 13:26 | GOODMAN - GPG13240451AB | 77 | 13.9 | Yes | Yes | 26.4 | 21.4 | 5 | 2ACBB938D7E04E529A8F1DBA4151CE32 |  | R22 | Non-TXV |  | 18.05% | 0.81948 | 34.69% | [5 empty] | Non-TXV | 18.05%
Fresno | CA | 93703-1052 |  | 2014-05-19 | 2014-05-19 11:21 | 2014-05-19 12:07 | YORK - D1NP048N09006A | 132 | 8.5 | Yes | Yes | 21.5 | 20.7 | 0.8 | 49AF2BD2BB2744E38129867B608FA40F |  | R22 | Non-TXV |  | 6.439% | 0.93561 | 12.38% | [5 empty] | Non-TXV | 6.439%
Oroville | CA | 95965-3522 |  | 2014-05-29 | 2014-05-29 15:39 | 2014-05-29 16:06 | CARRIER - 48GX-036-060301AD | 80 | 2.4 | Yes | Yes | 23 | 21.5 | 1.5 | D3EB454BDB644D96A28BBAF9C6517E72 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93711-2538 |  | 2014-05-29 | 2014-05-29 12:28 | 2014-05-29 12:44 | BDP - 585HJW042060ABAF | 100 | 12.3 | Yes | Yes | 26.7 | 20.9 | 5.8 | 5CBE7AFFC0994EC98961DFDABBAE4ACF |  | R22 | Non-TXV |  | 12.3% | 0.877 | 23.64% | [5 empty] | Non-TXV | 12.3%
Fresno | CA | 93711-2538 |  | 2014-05-29 | 2014-05-29 12:46 | 2014-05-29 13:02 | BDP - 585HJW042060ABAF | 100 | 17.6 | Yes | Yes | 20.5 | 18.2 | 2.3 | 34817942A0B641E583C7D41F3ACE12D6 |  | R22 | Non-TXV |  | 17.6% | 0.824 | 33.82% | [5 empty] | Non-TXV | 17.6%
Clovis | CA | 93612-4449 |  | 2014-06-05 | 2014-06-05 12:48 | 2014-06-05 13:04 | CARRIER - UNK | 57 | 11.7 | Yes | Yes | 25.5 | 21.7 | 3.8 | D517B1D2AAB7494887BBC0268D5E6D2C |  | R22 | Non-TXV |  | 20.53% | 0.79474 | 39.45% | [5 empty] | Non-TXV | 20.53%
Fresno | CA | 93727-3368 |  | 2014-06-04 | 2014-06-04 10:26 | 2014-06-04 10:54 | RHEEM - N/A | 90 | 4.9 | Yes | Yes | 24.4 | 22.6 | 1.8 | 26F7339221A3449DACBAC818839C5B37 |  | R22 | Non-TXV |  | 5.444% | 0.94556 | 10.46% | [5 empty] | Non-TXV | 5.444%
Fresno | CA | 93726-2321 |  | 2014-06-25 | 2014-06-25 09:01 | 2014-06-25 09:03 | RHEEM - RRKAA036JK06X | 62 | 13.2 | Yes | Yes | 20.5 | 18.6 | 1.9 | 72191136FD8648EC94F1870056EEBE71 |  | R22 | Non-TXV |  | 21.29% | 0.7871 | 40.92% | [5 empty] | Non-TXV | 21.29%
Clovis | CA | 93611-5044 |  | 2014-07-22 | 2014-07-22 11:58 | 2014-07-22 12:00 | OTHER - 13ACC04223001 | 126 | 17.6 | Yes | Yes | 20.7 | 19.2 | 1.5 | 350D8BFC38BA4372A260E0963BA4EC3D |  | R22 | Non-TXV |  | 13.97% | 0.86032 | 26.84% | [5 empty] | Non-TXV | 13.97%
Clovis | CA | 93611-5044 |  | 2014-07-22 | 2014-07-22 12:20 | 2014-07-22 12:21 | OTHER - 13ACC04223001 | 126 | 19.1 | Yes | Yes | 17.5 | 19.3 | -1.8 | 03782AA93E9849FE88F888476ED3FD29 |  | R22 | Non-TXV |  | 15.16% | 0.84841 | 29.13% | [5 empty] | Non-TXV | 15.16%
Rocklin | CA | 95677-3444 |  | 2014-06-28 | 2014-06-28 10:47 | 2014-06-28 11:24 | ARMSTRONG - SCU12E36A-1 | 99 | 3 | Yes | Yes | 25 | 20.4 | 4.6 | CE44376B5CBA46A499AE5FDACDBE3606 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Livingston | CA | 95334-9598 |  | 2014-06-06 | 2014-06-06 14:40 | 2014-06-06 14:57 | ICP - PGAD47D1K8 | 212 | 28.9 | Yes | Yes | 25.1 | 20.1 | 5 | 1C7504C405D74616817A4DC7E6335806 |  | R22 | Non-TXV |  | 13.63% | 0.86368 | 26.2% | [5 empty] | Non-TXV | 13.63%
Clovis | CA | 93619-9239 |  | 2014-06-12 | 2014-06-12 14:21 | 2014-06-12 14:23 | YORK - D1NH042N06506C | 94 | 3.6 | Yes | Yes | 21.6 | 18.5 | 3.1 | 0EF845674F024007AA16C168405BD63F |  | R22 | Non-TXV |  | 3.83% | 0.9617 | 7.36% | [5 empty] | Non-TXV | 3.83%
Clovis | CA | 93611-6547 |  | 2014-06-12 | 2014-06-12 13:18 | 2014-06-12 13:19 | OTHER - 38CK3060370 | 130 | 5.6 | Yes | Yes | 22.7 | 21 | 1.7 | 565BB6C71DF44EB8990467A2ED904DBB |  | R22 | Non-TXV |  | 4.308% | 0.95692 | 8.278% | [5 empty] | Non-TXV | 4.308%
Fresno | CA | 93704-1118 |  | 2014-06-13 | 2014-06-13 08:45 | 2014-06-13 09:14 | OTHER - PGB0360751 | 60 | 8.4 | Yes | Yes | 20.5 | 15.9 | 4.6 | 22E554ECD9DC400DA639A97EC7D0F3FA |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Wheatland | CA | 95692-9448 |  | 2014-06-13 | 2014-06-13 09:03 | 2014-06-13 09:24 | TRANE - TTP036D100A0 | 133 | 4.3 | Yes | Yes | 24 | 21 | 3 | 74774A6FBDB04D4285676BA869AE4B06 |  | R22 | Non-TXV |  | 3.233% | 0.96767 | 6.213% | [5 empty] | Non-TXV | 3.233%
Merced | CA | 95340-9161 |  | 2014-05-15 | 2014-05-15 14:40 | 2014-05-15 14:42 | RHEEM - RRNAB042JK08X | 104 | 20.8 | Yes | Yes | 26.8 | 22.6 | 4.2 | 955BF2C3CF79481EB471F8EE14E12CD6 |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Clovis | CA | 93612-5870 |  | 2014-06-12 | 2014-06-12 12:00 | 2014-06-12 12:02 | RHEEM - RRNL-B036JK06X | 93 | 3.1 | Yes | Yes | 23.7 | 20.4 | 3.3 | 1890C17F52ED40F98A32CC540D33F5B0 |  | R410A | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95340-3105 |  | 2014-05-15 | 2014-05-15 10:36 | 2014-05-15 10:40 | OTHER - HAG036AKA4 | 80 | 9.9 | Yes | Yes | 22 | 18.8 | 3.2 | 3490A4502D184B7BA625283701690439 |  | R22 | Non-TXV |  | 12.38% | 0.87625 | 23.78% | [5 empty] | Non-TXV | 12.38%
Chico | CA | 95926-4353 |  | 2014-06-18 | 2014-06-18 15:06 | 2014-06-18 15:45 | GOODMAN - GSC130301AC | 75 | 7.8 | Yes | Yes | 22.5 | 20.6 | 1.9 | 22A6C087AC924B2A8EA35C9934DBA37D |  | R22 | Non-TXV |  | 10.4% | 0.896 | 19.99% | [5 empty] | Non-TXV | 10.4%
Fresno | CA | 93725-1638 |  | 2014-06-21 | 2014-06-21 10:08 | 2014-06-21 10:08 | GOODMAN - GPG13360701AC | 113 | 0 | Yes | Yes | 22.7 | 21 | 1.7 | 9971E27A5D734728B7523E8241ECC33C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Kingsburg | CA | 93631-8842 |  | 2014-07-12 | 2014-07-12 10:35 | 2014-07-12 11:00 | DAY & NIGHT - 48/110YAC 104C | 128 | 8.5 | Yes | Yes | 26.1 | 20.4 | 5.7 | DD4C6CB904A0421BAE9F795DA06524AA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.641% | 0.93359 | 12.76% | [5 empty] | Non-TXV | 6.641%
Fresno | CA | 93705-5061 |  | 2014-05-28 | 2014-05-28 11:47 | 2014-05-28 11:49 | RHEEM - 7777UNK | 60 | 2.4 | Yes | Yes | 28.6 | 24.4 | 4.2 | 96C4A3B9CD1A4B129802CC946A3F855C |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Tracy | CA | 95376-3145 |  | 2014-05-22 | 2014-05-22 08:40 | 2014-05-22 09:01 | YORK - D1NY036N05606A | 120 | 9.3 | Yes | Yes | 18.9 | 20.1 | -1.2 | E2ABA2C49B704A3D887B64A716EC483F |  | R410A | TXV |  | 7.75% | 0.9225 | 14.89% | [5 empty] | TXV | 7.75%
Clovis | CA | 93612-4615 |  | 2014-06-05 | 2014-06-05 11:46 | 2014-06-05 12:02 | AMERICAN STANDARD - YCY036G1MOAB | 129 | 19.5 | Yes | Yes | 21.7 | 16.9 | 4.8 | B999F6BEF9B2435999F591C2BD596282 |  | R22 | Non-TXV |  | 15.12% | 0.84884 | 29.05% | [5 empty] | Non-TXV | 15.12%
Placerville | CA | 95667-5326 |  | 2014-07-21 | 2014-07-21 13:08 | 2014-07-21 13:27 | TRANE - YCP042F1M0AB | 128 | 3.8 | Yes | Yes | 25 | 19.3 | 5.7 | AA18F9FF65064786913B056B55672224 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Chico | CA | 95926-1415 |  | 2014-05-15 | 2014-05-15 09:56 | 2014-05-15 11:25 | LENNOX - 12GCS048X-100-4PA | 167 | 5.1 | Yes | Yes | 21.5 | 18.4 | 3.1 | 33E1931097394D0D81535F5470F8F153 |  | R22 | Non-TXV |  | 3.054% | 0.96946 | 5.869% | [5 empty] | Non-TXV | 3.054%
Selma | CA | 93662-2101 |  | 2014-06-13 | 2014-06-13 09:11 | 2014-06-13 09:32 | YORK - DCYZ-F036N070A | 64 | 3.1 | Yes | Yes | 24.9 | 19.4 | 5.5 | AF2D5C043EE3432FADBEC0C51158C585 |  | R410A | TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | TXV | 4.844%
Gridley | CA | 95948-9743 |  | 2014-05-30 | 2014-05-30 11:16 | 2014-05-30 11:34 | PAYNE - 591ANX048000ACAB | 128 | 3.8 | Yes | Yes | 18 | 20.1 | -2.1 | 5C0EF4239A69401A880F979B195E0EEF |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Fresno | CA | 93705-4516 |  | 2014-05-21 | 2014-05-21 11:51 | 2014-05-21 12:09 | GOODMAN - GPG10240451A | 50 | 7.5 | Yes | Yes | 18 | 17.8 | 0.3 | D4687ACED1C94E1388E860C1BC822106 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Fresno | CA | 93727-6547 |  | 2014-06-05 | 2014-06-05 16:57 | 2014-06-05 17:30 | LENNOX - 13ACC-048-230-01 | 158 | 8.6 | Yes | Yes | 21.5 | 21.6 | -0.1 | 6566A050D1B74300B90A8CBCB10316BC |  | R22 | Non-TXV |  | 5.443% | 0.94557 | 10.46% | [5 empty] | Non-TXV | 5.443%
Stockton | CA | 95204-1305 |  | 2014-06-02 | 2014-06-02 09:42 | 2014-06-02 10:01 | GE - BGTA930H1J01 | 84 | 9.4 | Yes | Yes | 18.5 | 19.1 | -0.6 | D24BC43C5C1C44D2A9749E3103EABE7C |  | R22 | Non-TXV |  | 11.19% | 0.8881 | 21.51% | [5 empty] | Non-TXV | 11.19%
Selma | CA | 93662-3040 |  | 2014-06-16 | 2014-06-16 10:01 | 2014-06-16 10:20 | ICP - PGD330060K001C1 | 98 | -3.8 | Yes | Yes | 21.8 | 20.3 | 1.5 | 6CE58D0020A540BC8D84E0F3756FBCD9 |  | R410A | TXV |  | -3.878% | 1.0388 | 1.086% |  |  |  |  | TXV |  |  | -3.878%
Stockton | CA | 95206-2801 |  | 2014-06-18 | 2014-06-18 12:58 | 2014-06-18 13:15 | RHEEM - RRNL-B024JK06X | 79 | 5.7 | Yes | Yes | 28.8 | 23.7 | 5.1 | 134D1368C2BA44CD820A30C895781568 |  | R410A | Non-TXV |  | 7.215% | 0.92785 | 13.87% | [5 empty] | Non-TXV | 7.215%
Stockton | CA | 95207-7765 |  | 2014-06-03 | 2014-06-03 08:43 | 2014-06-03 08:43 | CARRIER - 38CKC024320 | 69 | 0 | Yes | Yes | 19.3 | 17.7 | 1.6 | 0A9D4205A3AA472685FFBF982305552A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-5035 |  | 2014-05-14 | 2014-05-14 11:51 | 2014-05-14 12:18 | COLEMAN - AM024MA321A | 54 | 4.5 | Yes | Yes | 20.9 | 21.4 | -0.5 | 5BBA10BFBB7C4899B7CD330E85AA1737 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Chico | CA | 95926-3760 |  | 2014-05-15 | 2014-05-15 14:36 | 2014-05-15 15:16 | OTHER - NA | 61 | 4.9 | Yes | Yes | 15.6 | 16.8 | -1.2 | 84A01D0868CC49C4B07570466F43C8AB |  | R22 | Non-TXV |  | 8.033% | 0.91967 | 15.44% | [5 empty] | Non-TXV | 8.033%
Lathrop | CA | 95330-9492 |  | 2014-05-28 | 2014-05-28 12:59 | 2014-05-28 13:27 | PAYNE - PA13NR036-J | 115 | 9.1 | Yes | Yes | 21.3 | 23.7 | -2.4 | B50D6CA1EBCB4F84AAA33B6656617549 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.913% | 0.92087 | 15.21% | [5 empty] | Non-TXV | 7.913%
Stockton | CA | 95209-1561 |  | 2014-06-03 | 2014-06-03 17:12 | 2014-06-03 17:12 | GOODMAN - GSC130481AG | 147 | 0 | Yes | Yes | 30.5 | 24.8 | 5.7 | C5B0BF527B0F4DD6A6EEFF0FC026E61F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5038 |  | 2014-06-24 | 2014-06-24 10:32 | 2014-06-24 10:33 | PAYNE - UNK | 56 | 10.6 | Yes | Yes | 19 | 19.2 | -0.2 | DA3D1EE22D5040D0B6C4A6B0C019762B |  | R22 | Non-TXV |  | 18.93% | 0.81071 | 36.38% | [5 empty] | Non-TXV | 18.93%
Atwater | CA | 95301-3732 |  | 2014-05-16 | 2014-05-16 10:17 | 2014-05-16 10:20 | AMANA - PGB36C0702E | 64 | 5.6 | Yes | Yes | 21 | 21.5 | -0.5 | 84F9D5703B1949F9BE5780246A972256 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Clovis | CA | 93611-3031 |  | 2014-06-10 | 2014-06-10 08:46 | 2014-06-10 09:04 | DAY & NIGHT - 3080YAC106C | 64 | 13.1 | Yes | Yes | 28.1 | 22.8 | 5.3 | 37E9BA5C7A5E44C19C2387FED4A95931 |  | R22 | Non-TXV |  | 20.47% | 0.79531 | 39.34% | [5 empty] | Non-TXV | 20.47%
Lathrop | CA | 95330-8979 |  | 2014-06-03 | 2014-06-03 11:30 | 2014-06-03 12:04 | NORDYNE - JS3BC-060KA | 85 | -8 | Yes | Yes | 22.1 | 20.4 | 1.7 | 0055372532D74CDEAE836E150FAC0C5F |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Madera | CA | 93638-2294 |  | 2014-06-03 | 2014-06-03 13:17 | 2014-06-03 13:36 | CARRIER - 48SS036060301 | 67 | 13.7 | Yes | Yes | 23.3 | 19.6 | 3.7 | BBC16EC305C247598988E5F3CE7550EF |  | R22 | Non-TXV |  | 20.45% | 0.79552 | 39.3% | [5 empty] | Non-TXV | 20.45%
Manteca | CA | 95336-4445 |  | 2014-05-27 | 2014-05-27 09:53 | 2014-05-27 10:29 | GOODMAN - CK24-1B | 85 | 8.5 | Yes | Yes | 21.3 | 21 | 0.3 | 4C8982BE7A0940A2945ACC2663A312BA |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Chico | CA | 95973-7837 |  | 2014-06-19 | 2014-06-19 10:02 | 2014-06-19 10:18 | OTHER - CH18ABD1V | 103 | 5.6 | Yes | Yes | 19 | 20.9 | -1.9 | 114FF8BA2E24434FB35A87642C0CF74E |  | R22 | TXV |  | 5.437% | 0.94563 | 10.45% | [5 empty] | TXV | 5.437%
Madera | CA | 93638-2295 |  | 2014-06-03 | 2014-06-03 13:42 | 2014-06-03 14:08 | BDP - 585HJ036060 | 102 | 20.3 | Yes | Yes | 24.2 | 19.3 | 4.9 | 8E36371F994E4BB8B645DA838DBB2C23 |  | R22 | Non-TXV |  | 19.9% | 0.80098 | 38.25% | [5 empty] | Non-TXV | 19.9%
Madera | CA | 93638-2295 |  | 2014-06-05 | 2014-06-05 15:51 | 2014-06-05 16:30 | OTHER - TCGD48S21S2A | 69 | 22.1 | Yes | Yes | 26.5 | 21 | 5.5 | 1A76B287D1FA4647A8B263326239BB86 |  | R22 | Non-TXV |  | 32.03% | 0.67971 | 61.55% | [5 empty] | Non-TXV | 32.03%
Madera | CA | 93638-2296 |  | 2014-06-03 | 2014-06-03 14:13 | 2014-06-03 14:49 | COLEMAN - 9536C901 | 68 | 16.9 | Yes | Yes | 19.7 | 17.6 | 2.1 | FCA126B06EDB4CE8BF2151045FA68ADB |  | R22 | Non-TXV |  | 24.85% | 0.75147 | 47.76% | [5 empty] | Non-TXV | 24.85%
Gridley | CA | 95948-9503 |  | 2014-07-29 | 2014-07-29 08:50 | 2014-07-29 09:07 | PAYNE - PY2PNB036090AAAA | 82 | 2.4 | Yes | Yes | 20 | 19.8 | 0.2 | AD044C27EEB04730BF032EFB116E0A4D |  | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Oakdale | CA | 95361-2922 |  | 2014-06-04 | 2014-06-04 10:14 | 2014-06-04 10:36 | GMC - VSC130241AA | 85 | 9.5 | Yes | Yes | 18.7 | 19.8 | -1.1 | ACBE4E9310A049DD9608856B302B9976 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Fresno | CA | 93727-3082 |  | 2014-08-08 | 2014-08-08 12:58 | 2014-08-08 13:21 | RHEEM - N/A | 60 | 10.8 | Yes | Yes | 22.6 | 21.2 | 1.5 | E1E8CE7E673646729548F97673349D6C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Fresno | CA | 93702-4260 |  | 2014-05-22 | 2014-05-22 11:56 | 2014-05-22 12:16 | AMERICAN STANDARD - YCC030F1M0BJ | 69 | 4.1 | Yes | Yes | 24.9 | 21.3 | 3.7 | AD855E354F87485A985297F50A7F5E19 |  | R22 | Non-TXV |  | 5.942% | 0.94058 | 11.42% | [5 empty] | Non-TXV | 5.942%
Chico | CA | 95926-4260 |  | 2014-05-16 | 2014-05-16 11:33 | 2014-05-16 11:49 | PAYNE - NA | 44 | 3.1 | Yes | Yes | 20 | 19.6 | 0.4 | E5B13006E5A740819E828C0A0CAC1F58 |  | R22 | Non-TXV |  | 7.045% | 0.92955 | 13.54% | [5 empty] | Non-TXV | 7.045%
Selma | CA | 93662-2127 |  | 2014-06-21 | 2014-06-21 15:33 | 2014-06-21 15:52 | RHEEM - N/A | 120 | 22.1 | Yes | Yes | 21.5 | 22.6 | -1.1 | CB7309B8F3B2429B9FF7782571C44919 |  | R22 | Non-TXV |  | 18.42% | 0.81583 | 35.39% | [5 empty] | Non-TXV | 18.42%
Fresno | CA | 93727-3691 |  | 2014-07-08 | 2014-07-08 15:18 | 2014-07-08 15:44 | LENNOX - 10GCS036X-7-6PB | 58 | 3.9 | Yes | Yes | 22.9 | 22.6 | 0.3 | 2D9E58B9DE1743069C00E28994D4B525 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.724% | 0.93276 | 12.92% | [5 empty] | Non-TXV | 6.724%
Oakhurst | CA | 93644-8787 |  | 2014-07-31 | 2014-07-31 11:11 | 2014-07-31 11:12 | RHEEM - RRMAA024JK06X | 70 | 8.4 | Yes | Yes | 21.8 | 19.6 | 2.3 | 7215B8BD357048DEB2EA5DCBD6C20B87 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Chico | CA | 95973-1310 |  | 2014-06-19 | 2014-06-19 14:53 | 2014-06-19 15:09 | MAYTAG - DS5BD-030KA | 99 | 4.1 | Yes | Yes | 23 | 22 | 1 | A49E7F9457E84223B906F78ACE256839 |  | R22 | Non-TXV |  | 4.141% | 0.95859 | 7.959% | [5 empty] | Non-TXV | 4.141%
Oroville | CA | 95966-8028 |  | 2014-05-29 | 2014-05-29 13:06 | 2014-05-29 13:30 | AMERICAN STANDARD - 4A7B4030E1000AA | 112 | 4.1 | Yes | Yes | 24 | 20.4 | 3.6 | DB50DBC725B34E5F83CD13251143ADC9 |  | R410A | TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | TXV | 3.661%
Sanger | CA | 93657-8857 |  | 2014-08-19 | 2014-08-19 14:10 | 2014-08-19 14:11 | LENNOX - 13ACD-060-230-01 | 214 | 6.9 | Yes | Yes | 19.5 | 21.5 | -2 | BFD2E691FFEC4A4A9EA6DBD3439AC19B |  | R22 | Non-TXV |  | 3.224% | 0.96776 | 6.196% | [5 empty] | Non-TXV | 3.224%
Sanger | CA | 93657-8857 |  | 2014-08-19 | 2014-08-19 14:18 | 2014-08-19 15:13 | LENNOX - N/A | 90 | 4.7 | Yes | Yes | 19.7 | 21.5 | -1.8 | B2A316C788E34E08B857FCADF384D993 |  | R22 | Non-TXV |  | 5.222% | 0.94778 | 10.04% | [5 empty] | Non-TXV | 5.222%
Dinuba | CA | 93618-4050 |  | 2014-07-14 | 2014-07-14 10:25 | 2014-07-14 10:57 | NORDYNE - FS3BA-024KA | 64 | 3.5 | Yes | Yes | 17.4 | 20.2 | -2.7 | FA0A8D25460E4DEBA579755C1E694968 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.469% | 0.94531 | 10.51% | [5 empty] | Non-TXV | 5.469%
Fresno | CA | 93702-4701 |  | 2014-05-27 | 2014-05-27 10:51 | 2014-05-27 11:16 | RUUD - UAHE-036JAS | 91 | 6.2 | Yes | Yes | 19.9 | 21.3 | -1.4 | 4221E4F64CEC45C2BEA6ED00A3B51EDA |  | R22 | Non-TXV |  | 6.813% | 0.93187 | 13.09% | [5 empty] | Non-TXV | 6.813%
Kerman | CA | 93630-1461 |  | 2014-06-27 | 2014-06-27 14:08 | 2014-06-27 14:09 | LENNOX - GCS29-030-75-1PA | 52 | 2.6 | Yes | Yes | 23.8 | 20.6 | 3.2 | 31456C4B06DE4067A8CE60919EA4617F |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93722-8713 |  | 2014-05-23 | 2014-05-23 11:59 | 2014-05-23 12:30 | CARRIER - 38ETG060300 | 210 | 13.3 | Yes | Yes | 21.5 | 17.2 | 4.3 | D7E7C2C3C47F4642885FE925CF9FBDD2 |  | R410A | TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | TXV | 6.333%
Fresno | CA | 93727-5407 |  | 2014-07-16 | 2014-07-16 12:49 | 2014-07-16 12:50 | YORK - ACO18M1021CG | 49 | 2.1 | Yes | Yes | 25.7 | 19.9 | 5.8 | 669B34CFB762407D88991469E603C8BB |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Chico | CA | 95926-7360 |  | 2014-05-19 | 2014-05-19 11:31 | 2014-05-19 11:49 | UNK - UNK | 85 | 3.1 | Yes | Yes | 22.5 | 21.3 | 1.3 | C8982C36DFC74C83BAE71C3540C40586 |  |  |  |  | 3.647% | 0.96353 | 7.009% | [5 empty] | 0 | 3.647%
Yuba City | CA | 95993-9119 |  | 2014-05-19 | 2014-05-19 08:22 | 2014-05-19 09:30 | UNK - UNK | 85 | 3.9 | Yes | Yes | 20.5 | 21 | -0.5 | 23BBCF6D966F4F8ABB28D9A65CF6872F |  |  |  |  | 4.588% | 0.95412 | 8.818% | [5 empty] | 0 | 4.588%
Kerman | CA | 93630-1930 |  | 2014-06-18 | 2014-06-18 14:55 | 2014-06-18 14:56 | CARRIER - 48GS048090301 | 81 | 12.4 | Yes | Yes | 25.9 | 21.4 | 4.5 | 6BF80625C7264F8FB15AD8711B008E82 |  | R22 | Non-TXV |  | 15.31% | 0.84691 | 29.42% | [5 empty] | Non-TXV | 15.31%
Fresno | CA | 93711-3130 |  | 2014-05-26 | 2014-05-26 12:10 | 2014-05-26 12:29 | RHEEM - RAFD042JBS | 79 | 13.5 | Yes | Yes | 22 | 18.8 | 3.2 | 7395F97A0FC6434E98B811717DE0BF7A |  | R22 | Non-TXV |  | 17.09% | 0.82911 | 32.84% | [5 empty] | Non-TXV | 17.09%
Tracy | CA | 95376-2118 |  | 2014-06-09 | 2014-06-09 08:32 | 2014-06-09 08:49 | HEIL - PGC036K060B | 71 | 2.5 | Yes | Yes | 23.6 | 19.9 | 3.7 | 1AF83883BCE747ED9E93F3CF538D84E7 |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Fresno | CA | 93727-3380 |  | 2014-06-06 | 2014-06-06 10:58 | 2014-06-06 11:17 | RHEEM - N/A | 60 | 1.8 | Yes | Yes | 20.8 | 20.9 | -0.1 | 674B7571B05744E3A2AC9CD663F91E41 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93703-1624 |  | 2014-05-15 | 2014-05-15 16:14 | 2014-05-15 16:49 | AMERICAN STANDARD - YCC060F1M0BG | 178 | 9.8 | Yes | Yes | 20.3 | 18.7 | 1.7 | CC86C8F940C6471C87AA22B06A5B11A0 |  | R22 | Non-TXV |  | 5.506% | 0.94494 | 10.58% | [5 empty] | Non-TXV | 5.506%
Pinedale | CA | 93650-1382 |  | 2014-06-11 | 2014-06-11 14:39 | 2014-06-11 15:06 | GOODMAN - PGB024075 | 54 | 12.5 | Yes | Yes | 21.4 | 19.3 | 2.1 | 7DE598A1BCF747F8B38DDDC061C42DD2 |  | R22 | Non-TXV |  | 23.15% | 0.76852 | 44.49% | [5 empty] | Non-TXV | 23.15%
Chowchilla | CA | 93610-2036 |  | 2014-06-04 | 2014-06-04 10:51 | 2014-06-04 10:53 | TRANE - TTD736B10080 | 86 | 3.2 | Yes | Yes | 23 | 19.9 | 3.1 | 276F9853291643EC8A0159075E4E1188 |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Fresno | CA | 93727-4708 |  | 2014-06-26 | 2014-06-26 10:41 | 2014-06-26 10:43 | OTHER - 7777UNK | 54 | 2.7 | Yes | Yes | 23.9 | 19.2 | 4.7 | 3489F6617F954E52BFF2187E54DB85FB |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Oroville | CA | 95966-9700 |  | 2014-06-04 | 2014-06-04 12:57 | 2014-06-04 13:16 | OTHER - BRCQ0481BD | 103 | 3.7 | Yes | Yes | 26 | 20.9 | 5.1 | BB4AC91F3F4A469D811524B90A9B3EDB |  | R22 | Non-TXV |  | 3.592% | 0.96408 | 6.903% | [5 empty] | Non-TXV | 3.592%
Gridley | CA | 95948-9749 |  | 2014-07-01 | 2014-07-01 17:39 | 2014-07-01 18:08 | CARRIER - 38TRA060340 | 176 | 5.6 | Yes | Yes | 20 | 19.9 | 0.1 | E597D8F2A7154C66B1624558BB4046E9 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Stockton | CA | 95210-2122 |  | 2014-05-26 | 2014-05-26 12:08 | 2014-05-26 12:24 | WESTINGHOUSE - UNK | 64 | 4 | Yes | Yes | 22.8 | 20.2 | 2.7 | 48F2FFB914A4494193260E9D0870C706 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Lodi | CA | 95242-9420 |  | 2014-06-16 | 2014-06-16 10:33 | 2014-06-16 10:52 | YORK - BRCQ0361BD | 52 | 6.9 | Yes | Yes | 20.4 | 20.6 | -0.2 | 3F85AB59F72148288712144135E35B95 |  | R22 | Non-TXV |  | 13.27% | 0.86731 | 25.5% | [5 empty] | Non-TXV | 13.27%
Durham | CA | 95938-9443 |  | 2014-06-03 | 2014-06-03 09:08 | 2014-06-03 09:45 | RUUD - UAFO 025JAS | 55 | 5 | Yes | Yes | 17.8 | 20.7 | -2.9 | 05ADC44115C045EFBD52DE6687532C6E |  | R22 | Non-TXV |  | 9.091% | 0.90909 | 17.47% | [5 empty] | Non-TXV | 9.091%
Oroville | CA | 95966-9700 |  | 2014-06-04 | 2014-06-04 13:26 | 2014-06-04 13:45 | OTHER - DRC0421BE | 107 | 3.4 | Yes | Yes | 27 | 22 | 5 | 23FC6C8C61D849AC8FB5522CC6118D33 |  | R22 | Non-TXV |  | 3.178% | 0.96822 | 6.107% | [5 empty] | Non-TXV | 3.178%
Fresno | CA | 93726-2450 |  | 2014-05-23 | 2014-05-23 15:13 | 2014-05-23 15:34 | RUUD - N/A | 90 | 8.9 | Yes | Yes | 23.3 | 22.5 | 0.8 | 10C971F187424666ACECD31D8CC5E577 |  | R22 | Non-TXV |  | 9.889% | 0.90111 | 19% | [5 empty] | Non-TXV | 9.889%
Chico | CA | 95928-4111 |  | 2014-05-19 | 2014-05-19 16:45 | 2014-05-19 16:45 | UNK - UNK | 85 | 0 | Yes | Yes | 20.5 | 20.9 | -0.4 | 1F29FC052E5848EFB78C09015B65CCB9 |  |  |  |  | 0% | 1 | 0%
Marysville | CA | 95901-8272 |  | 2014-06-12 | 2014-06-12 08:25 | 2014-06-12 08:46 | YORK - H2RD036S06B | 96 | 4.8 | Yes | Yes | 17 | 19.9 | -2.9 | 75AEF65674384037ABE7E8713603DA40 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Chico | CA | 95926-4203 |  | 2014-06-18 | 2014-06-18 14:10 | 2014-06-18 14:44 | HEIL - EO83811646 | 55 | 6.3 | Yes | Yes | 16.5 | 19.5 | -3 | AD0A07598A61450EA836E35AF6C314C2 |  | R22 | TXV |  | 11.45% | 0.88545 | 22.01% | [5 empty] | TXV | 11.45%
Lodi | CA | 95242-9414 |  | 2014-06-16 | 2014-06-16 10:02 | 2014-06-16 10:21 | GUARDIAN - AC036X1322A | 96 | 22.9 | Yes | Yes | 16.9 | 19.3 | -2.4 | 719C4DDAA7A242588585873CD36940F8 |  | R22 | Non-TXV |  | 23.85% | 0.76146 | 45.84% | [5 empty] | Non-TXV | 23.85%
Fresno | CA | 93703-2644 |  | 2014-05-16 | 2014-05-16 13:05 | 2014-05-16 13:24 | LENNOX - GCS26-042-100-1PA | 133 | 19 | Yes | Yes | 21.5 | 24.2 | -2.7 | C59DB6B6024D4EE5BD4D48FB845089C6 |  | R22 | Non-TXV |  | 14.29% | 0.85714 | 27.45% | [5 empty] | Non-TXV | 14.29%
Fresno | CA | 93723-9298 |  | 2014-05-21 | 2014-05-21 12:33 | 2014-05-21 12:51 | TAPPAN - UNK | 76 | 8.9 | Yes | Yes | 19.2 | 15.2 | 4 | F37D3E20A2A9452BB8B88F403665BBFB |  | R22 | Non-TXV |  | 11.71% | 0.88289 | 22.51% | [5 empty] | Non-TXV | 11.71%
Stockton | CA | 95210-1432 |  | 2014-05-15 | 2014-05-15 14:41 | 2014-05-15 14:58 | RHEEM - RRKA-A024JK06X | 50 | 6.6 | Yes | Yes | 21.7 | 20.8 | 0.9 | 6EEDB44455A4420C97A2E7DBC552F3F8 |  | R22 | Non-TXV |  | 13.2% | 0.868 | 25.37% | [5 empty] | Non-TXV | 13.2%
Durham | CA | 95938-9606 |  | 2014-07-01 | 2014-07-01 10:46 | 2014-07-01 10:46 | PAYNE - 598AN048000AAA | 181 | 0 | Yes | Yes | 25.5 | 19.6 | 5.9 | 3C4F26826DB345839DFE5251A7360D76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-2959 |  | 2014-06-06 | 2014-06-06 12:55 | 2014-06-06 12:56 | DAY & NIGHT - 5190E14633 | 90 | 4.2 | Yes | Yes | 24.8 | 22.6 | 2.2 | 85FD306CEF734AF3B9E09F10BF7ED3BC |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Fresno | CA | 93727-3903 |  | 2014-06-10 | 2014-06-10 09:35 | 2014-06-10 10:04 | GOODMAN - GPG13600901BB | 164 | 5.5 | Yes | Yes | 18.6 | 19.9 | -1.3 | B301390ED32E4BD487D249AC4F47E761 |  | R22 | Non-TXV |  | 3.354% | 0.96646 | 6.445% | [5 empty] | Non-TXV | 3.354%
Clovis | CA | 93611-5447 |  | 2014-06-10 | 2014-06-10 09:12 | 2014-06-10 09:34 | OTHER - 5658J042 | 84 | 12.6 | Yes | Yes | 23.7 | 21 | 2.7 | 251584DA58CC46698C88A2B6EAF5EB17 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Atwater | CA | 95301-2241 |  | 2014-05-15 | 2014-05-15 14:40 | 2014-05-15 14:43 | PAYNE - 7777UNK | 96 | 8.1 | Yes | Yes | 19.9 | 22.8 | -2.9 | 50D05582C57A4370BC7ADD142BC251B9 |  | R22 | Non-TXV |  | 8.438% | 0.91563 | 16.22% | [5 empty] | Non-TXV | 8.438%
Lodi | CA | 95242-9414 |  | 2014-06-06 | 2014-06-06 16:22 | 2014-06-06 16:42 | OTHER - UK | 55 | 1.7 | Yes | Yes | 26 | 21.5 | 4.5 | DC6D5672D2E84538B6D97382E49F8F85 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Fresno | CA | 93705-1241 |  | 2014-07-10 | 2014-07-10 14:23 | 2014-07-10 14:46 | GOODMAN - UNK | 85 | 3.8 | Yes | Yes | 17.5 | 19.4 | -1.9 | 98944F400D3C443CA0EC402ED201F112 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Magalia | CA | 95954-8812 |  | 2014-06-05 | 2014-06-05 09:38 | 2014-06-05 09:56 | COLEMAN - NA | 50 | 8.3 | Yes | Yes | 16.5 | 19.3 | -2.8 | 675952C8238B49F0A871D039E465413C |  | R22 | Non-TXV |  | 16.6% | 0.834 | 31.9% | [5 empty] | Non-TXV | 16.6%
Fresno | CA | 93722-5423 |  | 2014-05-31 | 2014-05-31 12:42 | 2014-05-31 13:09 | ICP - PGF030K060A | 52 | 4.3 | Yes | Yes | 21.3 | 22 | -0.7 | BD78E60C930C4C92ADA058BC8CD3D258 |  | R22 | Non-TXV |  | 8.269% | 0.91731 | 15.89% | [5 empty] | Non-TXV | 8.269%
Fresno | CA | 93722-6731 |  | 2014-05-23 | 2014-05-23 22:45 | 2014-05-23 22:46 | OTHER - D6NZ030N05606 | 84 | 3.7 | Yes | Yes | 25.8 | 20.4 | 5.4 | B4E68B81D0BB4678A5C0B984CB03795A |  | R410A | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Lathrop | CA | 95330-9212 |  | 2014-05-28 | 2014-05-28 15:21 | 2014-05-28 15:46 | YORK - H1RA042S06D | 84 | 16.4 | Yes | Yes | 21.5 | 21.3 | 0.2 | C877B7464AB34C4F889920777DA70EDC |  | R22 | Non-TXV |  | 19.52% | 0.80476 | 37.52% | [5 empty] | Non-TXV | 19.52%
Chico | CA | 95926-4285 |  | 2014-06-24 | 2014-06-24 15:44 | 2014-06-24 16:06 | PAYNE - 585CJ030050 | 55 | 3.1 | Yes | Yes | 22 | 18.1 | 3.9 | 9B2F872C9EE344A8B8AC7F3A28B082A0 |  | R22 | Non-TXV |  | 5.636% | 0.94364 | 10.83% | [5 empty] | Non-TXV | 5.636%
Fresno | CA | 93704-2924 |  | 2014-06-13 | 2014-06-13 13:51 | 2014-06-13 14:14 | YORK - D1NH048N09006C | 128 | 22.7 | Yes | Yes | 25.7 | 20.7 | 5 | 603330DC762C4F6191EB123AA9D0E9E5 |  | R22 | Non-TXV |  | 17.73% | 0.82266 | 34.08% | [5 empty] | Non-TXV | 17.73%
Madera | CA | 93637-9616 |  | 2014-08-04 | 2014-08-04 10:55 | 2014-08-04 10:56 | GOODMAN - GPH1324M21AB | 108 | 13.7 | Yes | Yes | 18.5 | 17.7 | 0.8 | DBC10C39CBD744BEBADC2B7C5EEBF929 |  | R22 | Non-TXV |  | 12.69% | 0.87315 | 24.38% | [5 empty] | Non-TXV | 12.69%
Lathrop | CA | 95330-9431 |  | 2014-05-28 | 2014-05-28 10:44 | 2014-05-28 11:14 | NORDYNE - JS3BC-036KA | 85 | 7.6 | Yes | Yes | 22.1 | 22.6 | -0.5 | ACBD0D7D9E964F418DFEFF3760BB5B80 |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Madera | CA | 93637-9652 |  | 2014-06-12 | 2014-06-12 11:33 | 2014-06-12 11:49 | BRYANT - 661CJ024A | 71 | 8.8 | Yes | Yes | 21.5 | 20.4 | 1.1 | D6513F727E394BBA947B9A5B5E96A412 |  | R22 | TXV |  | 12.39% | 0.87606 | 23.82% | [5 empty] | TXV | 12.39%
Madera | CA | 93637-9652 |  | 2014-06-12 | 2014-06-12 12:08 | 2014-06-12 12:24 | OTHER - 661CJ030 | 86 | 8.9 | Yes | Yes | 22.6 | 21.5 | 1.1 | CA97FFF5538B499CB75AAD5ED24BE9C4 |  | R22 | TXV |  | 10.35% | 0.89651 | 19.89% | [5 empty] | TXV | 10.35%
Fresno | CA | 93726-7019 |  | 2014-05-29 | 2014-05-29 13:54 | 2014-05-29 14:13 | CARRIER - 38GB004300 | 120 | 25.3 | Yes | Yes | 21 | 22.4 | -1.4 | 31DCA823097944748F7AE83055E4B004 | Add refrigerant: 22.1 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 21.08% | 0.78917 | 40.52% | [5 empty] | Non-TXV | 21.08%
Fresno | CA | 93722-3300 |  | 2014-05-20 | 2014-05-20 13:34 | 2014-05-20 13:35 | PAYNE - PY1PJB048090ABAA | 91 | 2.8 | Yes | Yes | 25 | 20.6 | 4.4 | BEEA805D2CB744CE8658C678667C2429 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Madera | CA | 93637-9651 |  | 2014-08-04 | 2014-08-04 10:34 | 2014-08-04 10:35 | BRYANT - 661CJ030A | 86 | 8.9 | Yes | Yes | 21.8 | 18.8 | 3 | CF5B401BFF77436F8F6575F244FF45A6 |  | R22 | TXV |  | 10.35% | 0.89651 | 19.89% | [5 empty] | TXV | 10.35%
Lathrop | CA | 95330-8925 |  | 2014-05-28 | 2014-05-28 08:33 | 2014-05-28 09:04 | YORK - H1RA042S06D | 84 | 12.7 | Yes | Yes | 21.1 | 21.8 | -0.7 | 9861433F28874906B97A603779AB477C |  | R22 | Non-TXV |  | 15.12% | 0.84881 | 29.06% | [5 empty] | Non-TXV | 15.12%
Fresno | CA | 93711-3042 |  | 2014-07-24 | 2014-07-24 15:32 | 2014-07-24 15:53 | OTHER - PGF030K060E | 51 | 1.6 | Yes | Yes | 23.8 | 19.3 | 4.5 | 7F1C9D53C88B41219BDB55EA9DD1095C |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Clovis | CA | 93612-4842 |  | 2014-06-03 | 2014-06-03 14:55 | 2014-06-03 14:57 | BRYANT - 574BNW03609NA | 150 | 4.5 | Yes | Yes | 18.9 | 19.7 | -0.7 | 999C06EBC2764469B450D21320ACC982 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-4522 |  | 2014-05-21 | 2014-05-21 12:07 | 2014-05-21 12:09 | RHEEM - 7777UNK | 84 | 4.2 | Yes | Yes | 19.2 | 19.7 | -0.5 | 282827375FEB432795BABD432655F159 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95210-6733 |  | 2014-05-29 | 2014-05-29 14:07 | 2014-05-29 14:40 | BRYANT - 562CJ036-C | 96 | 9.8 | Yes | Yes | 28 | 23.3 | 4.7 | FD6DA45AF8674CAFB048C68B002B0DD4 |  | R22 | Non-TXV |  | 10.21% | 0.89792 | 19.62% | [5 empty] | Non-TXV | 10.21%
Fresno | CA | 93722-5329 |  | 2014-05-27 | 2014-05-27 09:18 | 2014-05-27 09:35 | CARRIER - 48BL003BC | 69 | 9.2 | Yes | Yes | 20.8 | 19.3 | 1.5 | D556605827CB4FB4A639DA213B43532C |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Fresno | CA | 93728-1713 |  | 2014-05-31 | 2014-05-31 15:29 | 2014-05-31 15:52 | ICP - PGAA48D1K1 | 124 | 27.7 | Yes | Yes | 25.2 | 25.3 | -0.1 | 9E531FB929DB44E8AAAEF8043E762F47 |  | R22 | Non-TXV |  | 22.34% | 0.77661 | 42.93% | [5 empty] | Non-TXV | 22.34%
Fresno | CA | 93705-3232 |  | 2014-05-28 | 2014-05-28 18:18 | 2014-05-28 18:20 | DAY & NIGHT - 593ANX042000ABAA | 105 | 4.2 | Yes | Yes | 24.6 | 22.5 | 2.1 | 0F0F9DCEE165429694CA21AA200C2964 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95207-2540 |  | 2014-05-30 | 2014-05-30 11:22 | 2014-05-30 11:39 | RHEEM - UNK | 64 | 4.3 | Yes | Yes | 24.1 | 21.4 | 2.7 | 24DC75410E064691811AF0DF1B3A7895 |  | R22 | Non-TXV |  | 6.719% | 0.93281 | 12.91% | [5 empty] | Non-TXV | 6.719%
Fresno | CA | 93727-6550 |  | 2014-08-14 | 2014-08-14 14:03 | 2014-08-14 14:05 | LENNOX - 13ACC-060-230-01 | 168 | 5.9 | Yes | Yes | 19.1 | 20.7 | -1.6 | BBC28820FEBA40F99FDF0D2D43F87168 |  | R22 | Non-TXV |  | 3.512% | 0.96488 | 6.749% | [5 empty] | Non-TXV | 3.512%
Stockton | CA | 95210-1644 |  | 2014-05-16 | 2014-05-16 11:45 | 2014-05-16 12:10 | BDP - 585A02405YACR | 51 | 1.8 | Yes | Yes | 27 | 23.5 | 3.6 | 149A9911D18D4380851DAE60AB0B745E |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93705-1248 |  | 2014-05-31 | 2014-05-31 10:49 | 2014-05-31 11:08 | DAY & NIGHT - 36/80 YAC-108 | 74 | 4.4 | Yes | Yes | 21.2 | 21.8 | -0.6 | 6440DDA02EBF411F8792B0FAC00820CB |  | R22 | Non-TXV |  | 5.946% | 0.94054 | 11.43% | [5 empty] | Non-TXV | 5.946%
Fresno | CA | 93703-4153 |  | 2014-05-30 | 2014-05-30 14:35 | 2014-05-30 15:03 | YORK - DCYZ-F030N070B | 64 | 3.1 | Yes | Yes | 28 | 24.2 | 3.8 | 409482B274EA4D39B5ED73F165D0AADF |  | R410A | TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | TXV | 4.844%
Fresno | CA | 93705-2631 |  | 2014-05-28 | 2014-05-28 14:12 | 2014-05-28 14:13 | GOODMAN - CK36-1B | 76 | 3.2 | Yes | Yes | 21.1 | 23.2 | -2.1 | 5AF00B58DA6C4782B7542A021B168657 |  | R22 | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Fresno | CA | 93727-3205 |  | 2014-06-27 | 2014-06-27 08:49 | 2014-06-27 08:51 | OTHER - N2A348KA400 | 120 | 5.7 | Yes | Yes | 23.9 | 20.9 | 3 | CDDBD731E77444BE96F52C713D8F9EA1 |  | R22 | Non-TXV |  | 4.75% | 0.9525 | 9.128% | [5 empty] | Non-TXV | 4.75%
Sanger | CA | 93657-1912 |  | 2014-06-17 | 2014-06-17 09:43 | 2014-06-17 10:10 | LENNOX - 13ACD-042-230-02 | 111 | 6.2 | Yes | Yes | 20.6 | 20.9 | -0.3 | 52474AE342D64B35900D1DC5D39BC9D8 |  | R22 | Non-TXV |  | 5.586% | 0.94414 | 10.73% | [5 empty] | Non-TXV | 5.586%
Red Bluff | CA | 96080-2582 |  | 2014-05-28 | 2014-05-28 16:16 | 2014-05-28 16:32 | YORK - AC036X1021G | 53 | 3.3 | Yes | Yes | 22 | 21.5 | 0.5 | 87FD71C3E22E4A1FABFF14483275079D |  | R22 | Non-TXV |  | 6.226% | 0.93774 | 11.97% | [5 empty] | Non-TXV | 6.226%
Yuba City | CA | 95991-5352 |  | 2014-05-19 | 2014-05-19 10:15 | 2014-05-19 11:00 | UNK - UNK | 85 | 3 | Yes | Yes | 18 | 20.4 | -2.4 | 8943DDC1E99A45EBA2E487C60882E7B5 |  |  |  |  | 3.529% | 0.96471 | 6.783% | [5 empty] | 0 | 3.529%
Browns Valley | CA | 95918-9673 |  | 2014-10-13 | 2014-10-13 08:46 | 2014-10-13 09:01 | COLEMAN - BRCQ0551BEG | 86 | 5.7 | Yes | Yes | 23.5 | 22.1 | 1.5 | 43C7BAAC48AE4245B2D528E35ED3CA6A |  | R22 | Non-TXV |  | 6.628% | 0.93372 | 12.74% | [5 empty] | Non-TXV | 6.628%
Fresno | CA | 93727-7249 |  | 2014-06-06 | 2014-06-06 13:42 | 2014-06-06 13:42 | GOODMAN - GPG1342070M41BA | 81 | 0 | Yes | Yes | 21.2 | 21.2 | 0 | DF677900AB144F92AE4D8F8049B96F08 |  | R410A | TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-9111 |  | 2014-05-29 | 2014-05-29 14:32 | 2014-05-29 15:06 | AMERICAN STANDARD - YCP048F1H0AA | 166 | 7.5 | Yes | Yes | 22 | 23.1 | -1.1 | 007FCCD2788A41F39B7B5A08221F5C87 |  | R22 | Non-TXV |  | 4.518% | 0.95482 | 8.683% | [5 empty] | Non-TXV | 4.518%
Stockton | CA | 95207-2252 |  | 2014-05-30 | 2014-05-30 10:08 | 2014-05-30 10:27 | OTHER - UNK | 54 | 10.9 | Yes | Yes | 19.5 | 20.4 | -0.9 | 36DFCEEAAF9C486C9E5A4D1414D2C82C |  | R22 | Non-TXV |  | 20.19% | 0.79815 | 38.79% | [5 empty] | Non-TXV | 20.19%
Fresno | CA | 93722-6735 |  | 2014-05-23 | 2014-05-23 10:38 | 2014-05-23 10:39 | CARRIER - 585HJW036060 | 102 | 4.4 | Yes | Yes | 22 | 21 | 1 | 36352B7DC42A463BB21DAC4472DD1A12 |  | R22 | Non-TXV |  | 4.314% | 0.95686 | 8.29% | [5 empty] | Non-TXV | 4.314%
Corning | CA | 96021-3321 |  | 2014-05-28 | 2014-05-28 17:55 | 2014-05-28 17:55 | RUUD - 14AJ136AD1 | 66 | 0 | Yes | Yes | 19.6 | 22.1 | -2.5 | ACE9418CC65E4A19A6ACAFF8CA853250 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2007 |  | 2014-07-23 | 2014-07-23 09:26 | 2014-07-23 09:27 | LENNOX - GCS29X030752PA | 51 | 6.1 | Yes | Yes | 23.1 | 18.8 | 4.3 | 8A619EC11E1D45199974BC9B905D0E5A |  | R22 | Non-TXV |  | 11.96% | 0.88039 | 22.99% | [5 empty] | Non-TXV | 11.96%
Tracy | CA | 95376-4145 |  | 2014-05-23 | 2014-05-23 09:06 | 2014-05-23 09:33 | NORDYNE - JS4BD-030KB | 85 | 10 | Yes | Yes | 21.7 | 20.8 | 0.9 | 5C131CA43EC54920A7AB1CB279BEFF44 |  | R410A | TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | TXV | 11.76%
Lathrop | CA | 95330-9573 |  | 2014-05-28 | 2014-05-28 13:36 | 2014-05-28 14:00 | RHEEM - RRNA-B024JK06X | 85 | 6.8 | Yes | Yes | 27.8 | 24.4 | 3.4 | CF65F7E2EA1C4105BEFC3850CE59C802 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Dinuba | CA | 93618-4039 |  | 2014-07-10 | 2014-07-10 12:59 | 2014-07-10 12:59 | OTHER - TZAA-330-2A757 | 75 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | C07D796B3D634A35B9151EBE157505F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-1816 |  | 2014-05-20 | 2014-05-20 09:09 | 2014-05-20 09:28 | RHEEM - UNK | 66 | 8.4 | Yes | Yes | 18.7 | 16.2 | 2.5 | 7F9150FFEE37411499D3B34882F3E236 |  | R22 | Non-TXV |  | 12.73% | 0.87273 | 24.46% | [5 empty] | Non-TXV | 12.73%
Fresno | CA | 93722-0443 |  | 2014-06-12 | 2014-06-12 10:45 | 2014-06-12 11:08 | WEATHER KING - 14AJA48A01 | 234 | 7.4 | Yes | Yes | 21.3 | 22.3 | -0.9 | A6B2FF05F17F43879E44ADE524BDE20A |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Chico | CA | 95973-0212 |  | 2014-05-20 | 2014-05-20 15:14 | 2014-05-20 15:47 | AMANA - APG348901AB | 145 | 4.8 | Yes | Yes | 25.6 | 21.2 | 4.4 | 15D619C52156498CAFD7B885A6B86404 |  | R22 | Non-TXV |  | 3.31% | 0.9669 | 6.362% | [5 empty] | Non-TXV | 3.31%
Fresno | CA | 93705-3229 |  | 2014-05-27 | 2014-05-27 14:11 | 2014-05-27 14:12 | BDP - 568DJ036 | 170 | 8.7 | Yes | Yes | 19.5 | 22.1 | -2.6 | 70F85B23110543F6B60C07858324A7C2 |  | R22 | Non-TXV |  | 5.118% | 0.94882 | 9.835% | [5 empty] | Non-TXV | 5.118%
Fresno | CA | 93722-6843 |  | 2014-06-12 | 2014-06-12 09:08 | 2014-06-12 09:30 | LENNOX - 12GS042-75-2PA | 133 | 4.4 | Yes | Yes | 21.5 | 19.9 | 1.6 | 69B73F75338C4D34919D020C8EB4FF8C |  | R22 | Non-TXV |  | 3.308% | 0.96692 | 6.358% | [5 empty] | Non-TXV | 3.308%
Lathrop | CA | 95330-8670 |  | 2014-05-27 | 2014-05-27 13:54 | 2014-05-27 14:14 | CARRIER - 24ABA342310 | 116 | 6.1 | Yes | Yes | 22.9 | 21.5 | 1.4 | 8FCCCCC7109447758C7A6A3BEC5BA01B |  | R410A | TXV |  | 5.259% | 0.94741 | 10.11% | [5 empty] | TXV | 5.259%
Stockton | CA | 95209-4293 |  | 2014-05-14 | 2014-05-14 13:15 | 2014-05-14 13:36 | CARRIER - 24ABA348A300 | 131 | 7.6 | Yes | Yes | 27.7 | 21.8 | 6 | C8EC46B222F54653BF1E33A93DBB3DBF |  | R410A | TXV |  | 5.802% | 0.94198 | 11.15% | [5 empty] | TXV | 5.802%
Madera | CA | 93638-1880 |  | 2014-08-16 | 2014-08-16 07:51 | 2014-08-16 08:07 | PAYNE - PY1PNB036060ABAA | 68 | 2 | Yes | Yes | 23.5 | 20.2 | 3.4 | F54995711A7F4936AF7D4ABD13EA8022 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93710-4125 |  | 2014-06-20 | 2014-06-20 11:06 | 2014-06-20 12:15 | RHEEM - RRPL-B042JK08X | 112 | 9.4 | Yes | Yes | 20.2 | 22.1 | -1.9 | 87410DC3DEE746059EB1B0724934FF6D |  | R410A | TXV |  | 8.393% | 0.91607 | 16.13% | [5 empty] | TXV | 8.393%
Dinuba | CA | 93618-4039 |  | 2014-07-10 | 2014-07-10 09:57 | 2014-07-10 10:24 | NORDYNE - FS3BA-030KA | 68 | 12.4 | Yes | Yes | 19 | 20.8 | -1.8 | 02A2375B34014201BC179BFE78C2CAF8 |  | R22 | Non-TXV |  | 18.24% | 0.81765 | 35.04% | [5 empty] | Non-TXV | 18.24%
Reedley | CA | 93654-4304 |  | 2014-06-16 | 2014-06-16 14:14 | 2014-06-16 14:45 | GOODMAN - PGJ030075-1 | 72 | 3.8 | Yes | Yes | 21.3 | 23.2 | -1.9 | 36CA214491DC4B0B935A7F14BE651A02 |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Dinuba | CA | 93618-4042 |  | 2014-07-10 | 2014-07-10 10:27 | 2014-07-10 11:08 | NORDYNE - N/A | 69 | 6.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | C8060C0DCE57401686961E234F03333D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95210-3328 |  | 2014-05-31 | 2014-05-31 09:24 | 2014-05-31 09:41 | RHEEM - RAKA-037JAZ | 79 | -4.6 | Yes | Yes | 21.2 | 18.7 | 2.5 | 44182AF625064F9EBBB5EEAF55CEACB7 |  | R22 | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Yuba City | CA | 95991-4449 |  | 2014-05-15 | 2014-05-15 09:54 | 2014-05-15 10:12 | TEMPSTAR - NPGAA36C14 | 69 | 2 | Yes | Yes | 19 | 21 | -2 | 98E4D3684D8D48078D4E57D15A9E93B6 |  | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
Fresno | CA | 93726-1462 |  | 2014-05-28 | 2014-05-28 13:22 | 2014-05-28 13:39 | BDP - 585HJW018040 | 61 | 4.5 | Yes | Yes | 22 | 22.6 | -0.6 | 3954B9A2C1CE426A99555E5A97536529 |  | R22 | Non-TXV |  | 7.377% | 0.92623 | 14.18% | [5 empty] | Non-TXV | 7.377%
Dinuba | CA | 93618-4042 |  | 2014-07-10 | 2014-07-10 18:34 | 2014-07-10 18:55 | NORDYNE - N/A | 64 | 8.6 | Yes | Yes | 18.9 | 20.8 | -1.9 | 0E03CB6EEBB74F6596FEBB33A30F512F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
Sanger | CA | 93657-3343 |  | 2014-07-22 | 2014-07-22 10:46 | 2014-07-22 11:03 | LENNOX - 12GCS036X-75-5PB | 110 | 5.2 | Yes | Yes | 19.3 | 20.4 | -1.1 | 1812BCE370404D71B7598FA7C21D5742 |  | R22 | Non-TXV |  | 4.727% | 0.95273 | 9.085% | [5 empty] | Non-TXV | 4.727%
Manteca | CA | 95337-5250 |  | 2014-05-15 | 2014-05-15 14:14 | 2014-05-15 14:49 | GOODMAN - GSC130301A | 85 | 8.2 | Yes | Yes | 22.3 | 21.1 | 1.3 | B28677F48966499BA6F6F0D55A7A60A3 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Fresno | CA | 93726-1462 |  | 2014-07-09 | 2014-07-09 11:30 | 2014-07-09 11:31 | BDP - 585HJ030040 | 68 | 7.5 | Yes | Yes | 19.2 | 19.5 | -0.3 | 722D7DBC87F841AB9A31BC76B4A8607D |  | R22 | Non-TXV |  | 11.03% | 0.88971 | 21.2% | [5 empty] | Non-TXV | 11.03%
Dinuba | CA | 93618-4039 |  | 2014-07-11 | 2014-07-11 20:15 | 2014-07-11 20:28 | NORDYNE - FS3BA-24KA | 64 | 6.8 | Yes | Yes | 19.8 | 21.5 | -1.7 | AA83FE718F654B21A0123994710AD3A0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.62% | 0.89375 | 20.42% | [5 empty] | Non-TXV | 10.62%
Fresno | CA | 93726-4210 |  | 2014-05-27 | 2014-05-27 13:24 | 2014-05-27 13:27 | TRANE - TTZ036A100A2 | 201 | 6 | Yes | Yes | 22.4 | 22.6 | -0.2 | EA02A10F5DBD44BCA7874BCF2C33402A |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Fresno | CA | 93726-4210 |  | 2014-05-27 | 2014-05-27 13:34 | 2014-05-27 13:53 | RUUD - URMA-A030JK06E | 80 | 5.6 | Yes | Yes | 22.5 | 21.5 | 1 | 4CACC8C7380442ABB8DBD6A7A9CA1A7E |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93727-4706 |  | 2014-07-02 | 2014-07-02 14:25 | 2014-07-02 14:43 | OTHER - 1261-500 | 39 | 3.5 | Yes | Yes | 20.5 | 21.5 | -1 | A4104E7F463C44A995588091C3FF5306 |  | R22 | Non-TXV |  | 8.974% | 0.91026 | 17.25% | [5 empty] | Non-TXV | 8.974%
Dinuba | CA | 93618-4039 |  | 2014-07-10 | 2014-07-10 11:10 | 2014-07-10 12:23 | NORDYNE - N/A | 69 | 4.2 | Yes | Yes | 18.6 | 20.4 | -1.8 | 83918BBDC0354E6790F6104D628AF97D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.087% | 0.93913 | 11.7% | [5 empty] | Non-TXV | 6.087%
Stockton | CA | 95210-3321 |  | 2014-05-27 | 2014-05-27 12:13 | 2014-05-27 12:31 | CARRIER - 38EN048300 | 118 | 4.1 | Yes | Yes | 27.7 | 23.7 | 4 | 691FC3D5A17F4FACA4F7C9CBC81E9FA2 |  | R22 | Non-TXV |  | 3.475% | 0.96525 | 6.677% | [5 empty] | Non-TXV | 3.475%
Chico | CA | 95973-1150 |  | 2014-05-21 | 2014-05-21 09:52 | 2014-05-21 10:15 | TEMPSTAR - TCA024AKA1 | 69 | 2.9 | Yes | Yes | 23.3 | 21.7 | 1.6 | 501E0C7DAB20408892EEE708CF30B26F |  | R22 | Non-TXV |  | 4.203% | 0.95797 | 8.077% | [5 empty] | Non-TXV | 4.203%
Oroville | CA | 95966-5238 |  | 2014-05-29 | 2014-05-29 08:48 | 2014-05-29 09:12 | GOODMAN - KT60-1B | 150 | 5.5 | Yes | Yes | 19 | 20.9 | -1.9 | A8E9C4F6BC024091896C29AD40F800B2 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Dinuba | CA | 93618-4034 |  | 2014-07-22 | 2014-07-22 12:35 | 2014-07-22 13:20 | YORK - D1NA036N05606C | 67 | 2.5 | Yes | Yes | 22.1 | 21.3 | 0.8 | F920B19066D64BC8B6B87B9437F20FDF |  | R22 | Non-TXV |  | 3.731% | 0.96269 | 7.171% | [5 empty] | Non-TXV | 3.731%
Fresno | CA | 93722-5287 |  | 2014-05-21 | 2014-05-21 14:38 | 2014-05-21 14:40 | BRYANT - 7777UNK | 84 | 2.8 | Yes | Yes | 16.8 | 19.7 | -2.9 | 1DDFBAD7AF974FA38408586C3231C9F8 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93727-4707 |  | 2014-06-25 | 2014-06-25 12:07 | 2014-06-25 12:10 | OTHER - AC018M1021CG | 49 | 2 | Yes | Yes | 17.8 | 19.9 | -2.1 | C1237A7ADE4440FC8A0AF3AE60E6D8AE |  | R22 | Non-TXV |  | 4.082% | 0.95918 | 7.844% | [5 empty] | Non-TXV | 4.082%
Fresno | CA | 93705-2807 |  | 2014-05-28 | 2014-05-28 15:06 | 2014-05-28 15:07 | CARRIER - 48KL13600BE | 76 | 2.3 | Yes | Yes | 23.6 | 23.7 | -0.1 | 625E3EFF5F4740B3A41634C683CC582A |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Paradise | CA | 95969-2904 |  | 2014-07-22 | 2014-07-22 12:15 | 2014-07-22 12:32 | OTHER - 36J0=105 | 83 | 3.5 | Yes | Yes | 18 | 20.4 | -2.4 | 8C105B4E468F49D491586D8B3F0B9496 |  | R22 | Non-TXV |  | 4.217% | 0.95783 | 8.104% | [5 empty] | Non-TXV | 4.217%
Atwater | CA | 95301-3441 |  | 2014-05-30 | 2014-05-30 08:48 | 2014-05-30 08:50 | OTHER - BRC024BD | 59 | 2.7 | Yes | Yes | 17.4 | 20.3 | -2.9 | 7DCA533910BD415E91CACAFBFCE50B21 |  | R22 | Non-TXV |  | 4.576% | 0.95424 | 8.795% | [5 empty] | Non-TXV | 4.576%
Stockton | CA | 95207-8126 |  | 2014-05-31 | 2014-05-31 10:13 | 2014-05-31 10:29 | DAY & NIGHT - 585EJW018050ABAC | 55 | 2.5 | Yes | Yes | 18.7 | 19.1 | -0.4 | A344E258073B4B4AB9F417BE9FD14CD7 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93701-1744 |  | 2014-07-10 | 2014-07-10 12:12 | 2014-07-10 12:33 | ICP - PGD33606K001C1 | 102 | -6 | Yes | Yes | 24.4 | 19.6 | 4.8 | B93572339F0048ACA05639420F00CC0E |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93704-4925 |  | 2014-08-12 | 2014-08-12 14:29 | 2014-08-12 14:29 | AMERICAN STANDARD - YCC030F1MOBJ | 69 | 0 | Yes | Yes | 25 | 21.3 | 3.7 | 667A59146A0641818C70B0B5364A308E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-1428 |  | 2014-05-30 | 2014-05-30 12:52 | 2014-05-30 12:55 | TEMPSTAR - N4A336AKB200 | 88 | 3.9 | Yes | Yes | 22.1 | 20.9 | 1.2 | F88666240BBA439AB85BD30DD00EEB78 |  | R410A | Non-TXV |  | 4.432% | 0.95568 | 8.517% | [5 empty] | Non-TXV | 4.432%
Fresno | CA | 93705-2202 |  | 2014-05-23 | 2014-05-23 13:24 | 2014-05-23 13:44 | AMERICAN STANDARD - YCC036F1MOBF | 83 | 15.1 | Yes | Yes | 20.2 | 21 | -0.8 | 1A5B2836E3E4435A991AADAC1EEF68E4 |  | R22 | Non-TXV |  | 18.19% | 0.81807 | 34.96% | [5 empty] | Non-TXV | 18.19%
Stockton | CA | 95207-8119 |  | 2014-05-29 | 2014-05-29 10:56 | 2014-05-29 11:35 | DAY & NIGHT - 585EJW024050ABAF | 54 | -3.2 | Yes | Yes | 22.5 | 20.1 | 2.4 | 0D92E5A3A83A490ABE807B931C9C7391 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Fresno | CA | 93722-5195 |  | 2014-05-22 | 2014-05-22 07:37 | 2014-05-22 07:39 | YORK - D2NP036N056006A | 108 | 3.8 | Yes | Yes | 24.1 | 22.5 | 1.6 | 122A4FB37FC643F995367E5C24EF4346 |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Chico | CA | 95973-9255 |  | 2014-06-20 | 2014-06-20 10:14 | 2014-06-20 10:38 | OTHER - 593BJ024-A | 67 | 5 | Yes | Yes | 19.5 | 22.1 | -2.6 | 9FA321F597A84FAA88742C30EE0A44E0 |  | R22 | Non-TXV |  | 7.463% | 0.92537 | 14.34% | [5 empty] | Non-TXV | 7.463%
Yuba City | CA | 95993-8223 |  | 2014-05-16 | 2014-05-16 12:52 | 2014-05-16 13:08 | BRYANT - 561CJ036-E | 70 | 2.1 | Yes | Yes | 21 | 21.9 | -0.9 | 70EF366408E54D78A5FE90243B47A546 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Dinuba | CA | 93618-4043 |  | 2014-07-10 | 2014-07-10 11:42 | 2014-07-10 12:19 | NORDYNE - FS3BA-024KA | 64 | 6.5 | Yes | Yes | 21.6 | 21 | 0.6 | 51BCD427A62A43E09D68DD4214B1D61B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.16% | 0.89844 | 19.52% | [5 empty] | Non-TXV | 10.16%
Stockton | CA | 95204-4944 |  | 2014-06-28 | 2014-06-28 13:30 | 2014-06-28 13:47 | GOODMAN - ASX140301AC | 140 | -8.2 | Yes | Yes | 18.6 | 18.7 | -0.1 | 84E602DDDA94423193AD003CB50637BF |  | R410A | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Stockton | CA | 95203-3168 |  | 2014-06-07 | 2014-06-07 10:46 | 2014-06-07 11:06 | GOODMAN - GSC130241DA | 83 | 2.6 | Yes | Yes | 22.2 | 19.4 | 2.8 | 4F1ECC0DA6074613800D06D0887E9F0B |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Fresno | CA | 93726-5040 |  | 2014-06-24 | 2014-06-24 10:52 | 2014-06-24 10:56 | DAY & NIGHT - UNK | 56 | 11.6 | Yes | Yes | 19.8 | 20.2 | -0.4 | E9BBBC061A774C08B95F70F8EBF70E28 |  | R22 | Non-TXV |  | 20.71% | 0.79286 | 39.81% | [5 empty] | Non-TXV | 20.71%
Dinuba | CA | 93618-4043 |  | 2014-07-14 | 2014-07-14 09:50 | 2014-07-14 10:16 | NORDYNE - FS3BA-024KA | 64 | 6.1 | Yes | Yes | 20.4 | 20.4 | 0 | 51634C5C65AB4DAD8BC9C707F5747E4A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.531% | 0.90469 | 18.32% | [5 empty] | Non-TXV | 9.531%
Dinuba | CA | 93618-4043 |  | 2014-07-10 | 2014-07-10 12:27 | 2014-07-10 12:56 | NORDYNE - N/A | 64 | 6.1 | Yes | Yes | 19.1 | 20.4 | -1.3 | 7FC5063B7F7442B1A90A25779E9C2CC8 |  | R22 | Non-TXV |  | 9.531% | 0.90469 | 18.32% | [5 empty] | Non-TXV | 9.531%
Tracy | CA | 95377-1146 |  | 2014-06-02 | 2014-06-02 12:59 | 2014-06-02 13:19 | CARRIER - 38BRC043340 | 171 | 7 | Yes | Yes | 23.8 | 21 | 2.8 | 8AD21B9E21F049EB87C6E2AA26460BDC |  | R22 | TXV |  | 4.094% | 0.95906 | 7.867% | [5 empty] | TXV | 4.094%
Fresno | CA | 93706-4740 |  | 2014-07-14 | 2014-07-14 14:13 | 2014-07-14 14:15 | OTHER - 7777UNK | 94 | 3.2 | Yes | Yes | 17.4 | 17.4 | 0 | 2CCC00C62845461280FC1092F8BC474D |  | R22 | Non-TXV |  | 3.404% | 0.96596 | 6.542% | [5 empty] | Non-TXV | 3.404%
Chico | CA | 95973-9638 |  | 2014-06-20 | 2014-06-20 11:18 | 2014-06-20 11:38 | OTHER - UNK UNK | 95 | 2.8 | Yes | Yes | 25.5 | 21.7 | 3.8 | BAFEB12EACC140E3AFB383E21D74F602 |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Fresno | CA | 93721-2432 |  | 2014-05-29 | 2014-05-29 08:26 | 2014-05-29 08:46 | CARRIER - 38CKB048300 | 102 | 14.2 | Yes | Yes | 23.1 | 17.7 | 5.4 | 1FBA022B0B9E48F0A769C447F0EE6FB6 |  | R22 | TXV |  | 13.92% | 0.86078 | 26.75% | [5 empty] | TXV | 13.92%
Fresno | CA | 93722-9005 |  | 2014-07-30 | 2014-07-30 13:33 | 2014-07-30 13:35 | BDP - 585HJW030040ABAF | 68 | 7.2 | Yes | Yes | 21.2 | 19.3 | 1.9 | 02CD36B9546F4BEEB4BF81EE6F36D3B3 |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Clovis | CA | 93611-2071 |  | 2014-05-30 | 2014-05-30 13:24 | 2014-05-30 13:25 | TRANE - YCX42G1M0AC | 128 | 5.5 | Yes | Yes | 30 | 25.9 | 4.1 | 20340D7858F247D4A16C91036EFE0B70 |  | R22 | Non-TXV |  | 4.297% | 0.95703 | 8.258% | [5 empty] | Non-TXV | 4.297%
Dinuba | CA | 93618-4048 |  | 2014-07-29 | 2014-07-29 15:09 | 2014-07-29 15:35 | NORDYNE - FS3BA-030KA | 68 | 9.6 | Yes | Yes | 20.2 | 21.9 | -1.7 | 128BA799B5504FB59B21DAFCBF284DC5 |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Manteca | CA | 95336-2520 |  | 2014-06-03 | 2014-06-03 14:51 | 2014-06-03 15:09 | HEIL - PGC030K060A | 52 | 2.2 | Yes | Yes | 25.1 | 21.7 | 3.4 | 073471A25A324372838E19F75181B52E |  | R22 | Non-TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | Non-TXV | 4.231%
Fresno | CA | 93703-2524 |  | 2014-05-31 | 2014-05-31 09:35 | 2014-05-31 10:01 | OTHER - PGHA048G100IN | 96 | 20 | Yes | Yes | 25.9 | 20.4 | 5.5 | 181FCFFE5EA44075A6030DBF49D9372B |  | R22 | Non-TXV |  | 20.83% | 0.79167 | 40.04% | [5 empty] | Non-TXV | 20.83%
Fresno | CA | 93703-2524 |  | 2014-05-31 | 2014-05-31 10:31 | 2014-05-31 10:48 | DAY & NIGHT - N/A | 90 | 3.3 | Yes | Yes | 23.4 | 20.1 | 3.3 | 76DFCC5481A3405982DF7EB05E9CDBC2 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Fresno | CA | 93702-3319 |  | 2014-05-29 | 2014-05-29 16:30 | 2014-05-29 17:00 | CARRIER - 48SX-030060331AA | 69 | 4.5 | Yes | Yes | 23 | 24 | -1 | 08852A6CA5DF4D29853D05A0262F5020 |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Stockton | CA | 95219-3519 |  | 2014-06-13 | 2014-06-13 08:57 | 2014-06-13 09:19 | GOODMAN - CKL36-1D | 85 | -9.5 | Yes | Yes | 18.8 | 21 | -2.2 | 60BDD8D1232D4781B742D9CB79B3CF89 |  | R22 | TXV |  | -11.18% | 1.1118 | 3.13% |  |  |  |  | TXV |  |  | -11.18%
Dinuba | CA | 93618-4048 |  | 2014-07-11 | 2014-07-11 16:20 | 2014-07-11 16:53 | NORDYNE - FS3BA-030KA | 68 | 4 | Yes | Yes | 22.6 | 22.6 | 0 | 9658C96229A34732A2FA9C1A08F0FA89 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Fresno | CA | 93711-2147 |  | 2014-09-19 | 2014-09-19 15:30 | 2014-09-19 15:32 | PAYNE - 42RAC1S8K | 87 | 13.8 | Yes | Yes | 21.6 | 21.5 | 0.1 | 4EB4D9E669BC45DE96022E6CA6D1D249 |  | R22 | Non-TXV |  | 15.86% | 0.84138 | 30.48% | [5 empty] | Non-TXV | 15.86%
Merced | CA | 95341-7715 |  | 2014-05-15 | 2014-05-15 11:58 | 2014-05-15 11:58 | GIBSON - JS3BA-036KA | 85 | 0 | Yes | Yes | 24.1 | 19.9 | 4.2 | 09D07493FF1843E1A649C9E58D69AC61 | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-3836 |  | 2014-06-02 | 2014-06-02 18:22 | 2014-06-02 18:50 | GOODMAN - CK49-1B | 90 | 6.3 | Yes | Yes | 24.4 | 22.3 | 2.1 | ED9679A2B0854317A159F3F6C4A4F91B |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Stockton | CA | 95205-7834 |  | 2014-06-18 | 2014-06-18 11:55 | 2014-06-18 12:14 | DAY & NIGHT - 585HJ024040 | 68 | 7.2 | Yes | Yes | 21 | 23.1 | -2.1 | B98796AB8F164A49945DA5C046E7728C |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Dinuba | CA | 93618-4049 |  | 2014-07-11 | 2014-07-11 09:18 | 2014-07-11 10:25 | NORDYNE - FS3BA-030KA | 68 | 5.1 | Yes | Yes | 19.2 | 20.8 | -1.6 | 9F76CF0B266046F3B4EC26DC2FE64B6B |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95203-3137 |  | 2014-06-21 | 2014-06-21 08:43 | 2014-06-21 09:00 | DAY & NIGHT - UNK | 54 | 4.9 | Yes | Yes | 22.6 | 20.1 | 2.5 | 219E2653C5DA4C7BACFBAEE4614ABD0F |  | R22 | Non-TXV |  | 9.074% | 0.90926 | 17.44% | [5 empty] | Non-TXV | 9.074%
Fresno | CA | 93720-1924 |  | 2014-07-29 | 2014-07-29 08:37 | 2014-07-29 08:57 | BRYANT - 577CNWA48090NATP | 149 | 15.3 | Yes | Yes | 19.2 | 20.7 | -1.5 | 3E52E317968641DF9691747A611FC208 |  | R410A | TXV |  | 10.27% | 0.89732 | 19.73% | [5 empty] | TXV | 10.27%
Marysville | CA | 95901-0000 |  | 2014-06-17 | 2014-06-17 08:45 | 2014-06-17 09:10 | CARRIER - 38CKC036350 | 70 | 8.3 | Yes | Yes | 17 | 19.7 | -2.7 | 495114006C07428B859B2B92C4D006DA |  | R22 | Non-TXV |  | 11.86% | 0.88143 | 22.79% | [5 empty] | Non-TXV | 11.86%
Fresno | CA | 93704-1725 |  | 2014-06-13 | 2014-06-13 12:02 | 2014-06-13 12:20 | CARRIER - 48DL045 | 70 | 13 | Yes | Yes | 19.5 | 17.4 | 2.1 | E6A1B4DA2FF246DA99087E8556A79230 |  | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Fresno | CA | 93727-4711 |  | 2014-06-25 | 2014-06-25 11:20 | 2014-06-25 11:21 | OTHER - AC024M1021A | 52 | 2.6 | Yes | Yes | 17.8 | 19.9 | -2.1 | 70EDB019D3914D08B07AC87584660735 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95210-1247 |  | 2014-05-15 | 2014-05-15 15:12 | 2014-05-15 15:28 | COLEMAN - BPGM0300701AA | 72 | 5.7 | Yes | Yes | 23.7 | 22.6 | 1.1 | A519AE8FEB864820B9D42399B4A02990 |  | R22 | Non-TXV |  | 7.917% | 0.92083 | 15.21% | [5 empty] | Non-TXV | 7.917%
Fresno | CA | 93706-4906 |  | 2014-05-20 | 2014-05-20 11:17 | 2014-05-20 11:39 | OTHER - 585HJW036060 | 102 | 5.8 | Yes | Yes | 18.4 | 16.5 | 1.9 | 69005FDEBDE64BE9B0644B74DE48B3F1 |  | R22 | Non-TXV |  | 5.686% | 0.94314 | 10.93% | [5 empty] | Non-TXV | 5.686%
Oroville | CA | 95966-7107 |  | 2014-05-29 | 2014-05-29 12:23 | 2014-05-29 12:45 | CARRIER - 48SX-036100331AA | 84 | 9 | Yes | Yes | 19 | 21.7 | -2.7 | C302B87F4E89485BA1562FA441EB183B |  | R22 | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Yuba City | CA | 95991-6730 |  | 2014-06-12 | 2014-06-12 15:58 | 2014-06-12 16:21 | PAYNE - PA10JA030-A | 72 | 2.4 | Yes | Yes | 18 | 21 | -3 | D2C6B41401D94A6CBBF56C81BD855ACA |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95203-3178 |  | 2014-06-07 | 2014-06-07 11:08 | 2014-06-07 11:28 | DAY & NIGHT - 585GJW024040ABAE | 54 | 2 | Yes | Yes | 19.2 | 18.2 | 1 | CF6A0D214B2F4BA591014D945F6B8B7C |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Fresno | CA | 93705-2144 |  | 2014-07-28 | 2014-07-28 13:21 | 2014-07-28 13:39 | BRYANT - 582ANW024040AAAB | 53 | 6.3 | Yes | Yes | 23.4 | 20.4 | 3 | 5B632D201EF049088E09E5C1ACA8F2F5 |  | R22 | Non-TXV |  | 11.89% | 0.88113 | 22.84% | [5 empty] | Non-TXV | 11.89%
Fresno | CA | 93726-5121 |  | 2014-06-11 | 2014-06-11 17:11 | 2014-06-11 17:32 | GOODMAN - VSX130481BA | 120 | 4.7 | Yes | Yes | 23.2 | 19.9 | 3.3 | B49435059713452AB7E0B20A8A80A0C7 |  | R410A | TXV |  | 3.917% | 0.96083 | 7.527% | [5 empty] | TXV | 3.917%
Stockton | CA | 95209-3810 |  | 2014-05-19 | 2014-05-19 09:22 | 2014-05-19 09:40 | YORK - H1RA048S06D | 117 | 3.4 | Yes | Yes | 24.7 | 20.1 | 4.6 | CA9E33C7BD324E73AAB08FA8FFBA14EE |  | R22 | Non-TXV |  | 2.906% | 0.97094 | 5.585% | [5 empty] | Non-TXV | 2.906%
Fresno | CA | 93702-3875 |  | 2014-06-18 | 2014-06-18 12:06 | 2014-06-18 12:08 | CARRIER - 48SS-024060331 | 40 | 2 | Yes | Yes | 19.5 | 22.1 | -2.6 | 06003CA1394B4577B9F6FB527A761636 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95207-1236 |  | 2014-05-20 | 2014-05-20 12:40 | 2014-05-20 12:40 | AMANA - RCE42A2D | 150 | 0 | Yes | Yes | 16.4 | 19.4 | -3 | 18580E3CB64B45D6B0CF164F3C5A4614 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-4953 |  | 2014-05-22 | 2014-05-22 14:36 | 2014-05-22 15:01 | JANITROL - CM42-1EC | 82 | 2.5 | Yes | Yes | 19 | 22 | -3 | D1AFAB5FD7BA4E7892F8FAE6CE71C7D2 |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Paso Robles | CA | 93446-1067 |  | 2014-06-25 | 2014-06-25 10:29 | 2014-06-25 10:29 | CARRIER - 38EN018300 | 58 | 0 | Yes | Yes | 32.5 | 20.4 | 12.1 | 947A3ECF312E4C2C8BCFE4D0B7936BFF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-4702 |  | 2014-05-19 | 2014-05-19 09:46 | 2014-05-19 10:04 | UNK - UNK | 85 | 3.1 | Yes | Yes | 21.5 | 19.7 | 1.8 | 26CF5A41D0334A148E0DDC596BCC6907 |  |  |  |  | 3.647% | 0.96353 | 7.009% | [5 empty] | 0 | 3.647%
Fresno | CA | 93702-1913 |  | 2014-07-07 | 2014-07-07 14:29 | 2014-07-07 20:03 | PAYNE - 585HJ030040 | 68 | 19.4 | Yes | Yes | 22.8 | 21.8 | 1.1 | B085D921B48D4A71A1300CEF660AB2E0 |  | R22 | Non-TXV |  | 28.53% | 0.71471 | 54.83% | [5 empty] | Non-TXV | 28.53%
Fresno | CA | 93722-2403 |  | 2014-05-31 | 2014-05-31 14:23 | 2014-05-31 14:47 | LENNOX - GCS29X-036-75-1PA | 58 | 5.4 | Yes | Yes | 26.1 | 22 | 4.1 | D667A797E172472F8C4145C6ABA463CE |  | R22 | Non-TXV |  | 9.31% | 0.9069 | 17.89% | [5 empty] | Non-TXV | 9.31%
Mariposa | CA | 95338-9236 |  | 2014-09-02 | 2014-09-02 08:43 | 2014-09-02 08:44 | OTHER - PGF042K080B | 87 | 13.7 | Yes | Yes | 21 | 19.8 | 1.2 | 469F88A3785047FF84CC2D9605C5A1C0 |  | R22 | Non-TXV |  | 15.75% | 0.84253 | 30.26% | [5 empty] | Non-TXV | 15.75%
Rocklin | CA | 95765-5021 |  | 2014-08-20 | 2014-08-20 15:46 | 2014-08-20 16:04 | RUUD - UAKB-060JAZ | 112 | 3.8 | Yes | Yes | 24 | 20.4 | 3.6 | 765F5B010AD2458C8B7A84B986316982 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Pollock Pines | CA | 95726-9722 |  | 2014-06-10 | 2014-06-10 11:46 | 2014-06-10 12:06 | PAYNE - PA12NA048-D | 135 | 4.3 | Yes | Yes | 29 | 23.9 | 5.1 | 695285AFE19540839E0B9EE1771FBCA2 |  | R22 | Non-TXV |  | 3.185% | 0.96815 | 6.121% | [5 empty] | Non-TXV | 3.185%
Chowchilla | CA | 93610-3311 |  | 2014-06-04 | 2014-06-04 11:17 | 2014-06-04 11:18 | OTHER - DCYZ-F042N080C | 78 | 3.8 | Yes | Yes | 26.9 | 21.3 | 5.6 | A1891E34D03F4E3BB47D530EEAEC14D6 |  | R410A | Non-TXV |  | 4.872% | 0.95128 | 9.363% | [5 empty] | Non-TXV | 4.872%
Fresno | CA | 93722-7310 |  | 2014-05-23 | 2014-05-23 15:17 | 2014-05-23 15:33 | BRYANT - CK38030300 | 75 | 8.8 | Yes | Yes | 21.4 | 20.3 | 1.2 | DEFAE3D9B21B46FCAB79BEDD4F51328C |  | R22 | Non-TXV |  | 11.73% | 0.88267 | 22.55% | [5 empty] | Non-TXV | 11.73%
Rocklin | CA | 95677-4211 |  | 2014-06-16 | 2014-06-16 15:23 | 2014-06-16 15:41 | RHEEM - RAFD-048JBS | 101 | 3 | Yes | Yes | 19 | 21.5 | -2.5 | 24DB9F6016DE45AAB2DA914FB6032AC1 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Stockton | CA | 95209-1313 |  | 2014-06-12 | 2014-06-12 10:02 | 2014-06-12 10:26 | PAYNE - PA13NR042-H | 113 | -6.6 | Yes | Yes | 15.5 | 18.5 | -3 | F371D75375EE462AB9199C6BE99ABCE4 |  | R22 | Non-TXV |  | -5.841% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.841%
Mariposa | CA | 95338-9587 |  | 2014-08-01 | 2014-08-01 08:17 | 2014-08-01 08:33 | ALLEGIANCE - 2A7A3030A1000AA | 88 | 2.7 | Yes | Yes | 26.8 | 21 | 5.8 | 91DF2742D242439CAC26C402877B0D86 |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Merced | CA | 95340-6916 |  | 2014-05-15 | 2014-05-15 13:57 | 2014-05-15 13:58 | AMERICAN STANDARD - YCC036F1MOBK | 83 | 12.8 | Yes | Yes | 21.7 | 19.9 | 1.8 | 7B115932868B427989A2C052AEE7EF0A |  | R22 | Non-TXV |  | 15.42% | 0.84578 | 29.64% | [5 empty] | Non-TXV | 15.42%
Chico | CA | 95928-4409 |  | 2014-05-29 | 2014-05-29 13:48 | 2014-05-29 13:43 | TRANE - TTRO24C100A0 | 58 | 13.3 | Yes | Yes | 21.9 | 21.2 | 0.7 | C2C8580A6B724781B291C1341B489B4D |  | R22 | Non-TXV |  | 22.93% | 0.77069 | 44.07% | [5 empty] | Non-TXV | 22.93%
Stockton | CA | 95210-1791 |  | 2014-05-26 | 2014-05-26 11:42 | 2014-05-26 11:42 | WESTINGHOUSE - IE024AAA0N | 52 | 0 | Yes | Yes | 17.5 | 19.8 | -2.3 | 58D7CB33693E4CC3AA7A184A23C9D674 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paso Robles | CA | 93446-3611 |  | 2014-06-23 | 2014-06-23 14:05 | 2014-06-23 14:22 | WESTINGHOUSE - 24KLB1L | 41 | -2.9 | Yes | Yes | 22.2 | 20.4 | 1.8 | 9AE8EFA967194BEABECAED68AB4525DF |  | R22 | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Merced | CA | 95348-2215 |  | 2014-07-18 | 2014-07-18 11:10 | 2014-07-18 11:28 | GOODMAN - UNK | 76 | 2.3 | Yes | Yes | 17.8 | 18.8 | -1 | 0F89E5EF710A4E988255D3BC4C17D390 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95209-5165 |  | 2014-05-14 | 2014-05-14 12:35 | 2014-05-14 12:55 | OTHER - UNK | 64 | 2.7 | Yes | Yes | 27.8 | 22.8 | 5 | 0A757724FCEE41709A6CBF34D7311D14 |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Fresno | CA | 93726-7300 |  | 2014-09-08 | 2014-09-08 10:44 | 2014-09-08 10:45 | GOODMAN - GPG1324045M41AC | 80 | 9.7 | Yes | Yes | 23.1 | 21 | 2.1 | DA29E5C574BA45B9B0AC908E5C330260 |  | R22 | Non-TXV |  | 12.12% | 0.87875 | 23.3% | [5 empty] | Non-TXV | 12.12%
Yuba City | CA | 95991-8308 |  | 2014-05-15 | 2014-05-15 11:30 | 2014-05-15 11:47 | LENNOX - 10CDB60-11P | 136 | 4 | Yes | Yes | 19 | 21.5 | -2.5 | 5E2755BBFED74924AAB88AC1184D9276 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95207-8123 |  | 2014-05-29 | 2014-05-29 09:44 | 2014-05-29 10:07 | BRYANT - 582ANW024060AAAD | 53 | 3.4 | Yes | Yes | 21.1 | 19.4 | 1.7 | 07791A0B5B9845F09E36A275BCAB9659 |  | R22 | Non-TXV |  | 6.415% | 0.93585 | 12.33% | [5 empty] | Non-TXV | 6.415%
Clovis | CA | 93611-0209 |  | 2014-06-02 | 2014-06-02 11:32 | 2014-06-02 11:33 | CARRIER - 48SX-030040321 | 70 | 3.4 | Yes | Yes | 23.1 | 20.4 | 2.7 | FD7BC0C2720D4726B223875928300D5F |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Fresno | CA | 93704-5864 |  | 2014-06-17 | 2014-06-17 09:04 | 2014-06-17 09:07 | TRANE - 4YCC3024B1064AA | 93 | 3.2 | Yes | Yes | 27 | 24.8 | 2.2 | E96F76DD08C343128C9FDAD47EB9B05A |  | R410A | Non-TXV |  | 3.441% | 0.96559 | 6.613% | [5 empty] | Non-TXV | 3.441%
Fresno | CA | 93725-1711 |  | 2014-06-16 | 2014-06-16 12:17 | 2014-06-16 12:34 | OTHER - UNK | 76 | 19 | Yes | Yes | 24.4 | 20.6 | 3.8 | 83E462E2D23F4F3E98A0DD6B881556CC |  | R22 | Non-TXV |  | 25% | 0.75 | 48.04% | [5 empty] | Non-TXV | 25%
Placerville | CA | 95667-3415 |  | 2014-06-03 | 2014-06-03 08:09 | 2014-06-03 08:09 | DAY & NIGHT - 540AJ030 | 88 | 0 | Yes | Yes | 25 | 20.7 | 4.3 | F590B43214FC4E5BB3BC7B428CFCA30B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-0115 |  | 2014-06-02 | 2014-06-02 13:07 | 2014-06-02 13:09 | WEATHER KING - WKKA-A048JK08E | 106 | 4.8 | Yes | Yes | 24.5 | 22.9 | 1.7 | 5D3AC3CF56EE482BBBD07C82556FA64E |  | R22 | Non-TXV |  | 4.528% | 0.95472 | 8.702% | [5 empty] | Non-TXV | 4.528%
Merced | CA | 95348-8718 |  | 2014-05-19 | 2014-05-19 10:46 | 2014-05-19 11:14 | UNK - UNK | 85 | 8.9 | Yes | Yes | 21.6 | 17.7 | 3.9 | A9D6803F839740808172470107525710 |  |  |  |  | 10.47% | 0.89529 | 20.12% | [5 empty] | 0 | 10.47%
Fresno | CA | 93702-2343 |  | 2014-05-29 | 2014-05-29 17:58 | 2014-05-29 18:38 | GOODMAN - GSC130481BB | 102 | 4.5 | Yes | Yes | 21.5 | 21.5 | 0 | F62D61800DD34AF1A6318DACB3ACD31A |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
French Camp | CA | 95231-9671 |  | 2014-07-10 | 2014-07-10 15:23 | 2014-07-10 16:02 | RUUD - UAPC-060JAZ | 296 | 12.5 | Yes | Yes | 26.9 | 21 | 5.9 | DF0580DF8D6B40FF99FB78D09C09BD70 |  | R22 | Non-TXV |  | 4.223% | 0.95777 | 8.116% | [5 empty] | Non-TXV | 4.223%
Los Banos | CA | 93635-7433 |  | 2014-06-11 | 2014-06-11 08:18 | 2014-06-11 08:20 | GIBSON - JS5BD-36K | 138 | 4.2 | Yes | Yes | 21.6 | 18.7 | 2.9 | 01F19167FBF34AB89316F6B90E5F74CE |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Fresno | CA | 93725-1511 |  | 2014-06-16 | 2014-06-16 10:37 | 2014-06-16 10:38 | OTHER - DCYZF036N070C | 64 | 6.7 | Yes | Yes | 22.4 | 18.2 | 4.2 | F0F803220973496FB6320411040DBBB9 |  | R410A | Non-TXV |  | 10.47% | 0.89531 | 20.12% | [5 empty] | Non-TXV | 10.47%
Gridley | CA | 95948-9511 |  | 2014-07-18 | 2014-07-18 11:35 | 2014-07-18 11:52 | BDP - 567GJ030-B | 80 | -4.7 | Yes | Yes | 21 | 18.8 | 2.2 | 935285801E9C4898A0DF7247F77DC5DB |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Tracy | CA | 95376-3250 |  | 2014-05-22 | 2014-05-22 09:41 | 2014-05-22 10:11 | GOODMAN - GSC1300361DF | 85 | -6 | Yes | Yes | 18.9 | 20.3 | -1.4 | AF585DE9B54C434AA33522FF54F98A73 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Clovis | CA | 93612-2670 |  | 2014-06-23 | 2014-06-23 14:14 | 2014-06-23 14:33 | AMERICAN STANDARD - YCC036F1M0BF | 83 | 6.5 | Yes | Yes | 24.6 | 22.1 | 2.5 | D50E56C1A36A4CA8BFEE680926D6FB39 |  | R22 | Non-TXV |  | 7.831% | 0.92169 | 15.05% | [5 empty] | Non-TXV | 7.831%
Fresno | CA | 93704-2103 |  | 2014-06-13 | 2014-06-13 12:33 | 2014-06-13 12:55 | CARRIER - 48DL002 | 39 | 17 | Yes | Yes | 28.6 | 23.3 | 5.3 | 8562885D4294490BACF96E556CC10269 |  | R22 | Non-TXV |  | 43.59% | 0.5641 | 83.77% | [5 empty] | Non-TXV | 43.59%
Stockton | CA | 95204-4944 |  | 2014-06-18 | 2014-06-18 10:02 | 2014-06-18 10:31 | YORK - H2RD024S06B | 88 | 9.3 | Yes | Yes | 19.3 | 20.8 | -1.5 | DA2D5221C3954F2D91723EAED2D889CB |  | R22 | Non-TXV |  | 10.57% | 0.89432 | 20.31% | [5 empty] | Non-TXV | 10.57%
Placerville | CA | 95667-4813 |  | 2014-06-10 | 2014-06-10 17:02 | 2014-06-10 17:02 | AMANA - RCC36A2B | 114 | 0 | Yes | Yes | 27 | 21.5 | 5.5 | 40053560D4604A77B873F364F1E314D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-1900 |  | 2014-06-20 | 2014-06-20 16:18 | 2014-06-20 16:39 | UNITARY PRODUCTS GROUP - H2RC042S06G | 109 | 6 | Yes | Yes | 21.6 | 22.1 | -0.5 | 03B49E7FB0FE4B3ABA494D7095F68F0D |  | R22 | Non-TXV |  | 5.505% | 0.94495 | 10.58% | [5 empty] | Non-TXV | 5.505%
Fresno | CA | 93727-4840 |  | 2014-07-08 | 2014-07-08 13:14 | 2014-07-08 13:45 | ICP - WPG3244040LKC1 | 72 | 2.9 | Yes | Yes | 19.1 | 19.8 | -0.7 | B0F1E468F7C94AC49242C53C43F068B4 |  | R410A | TXV |  | 4.028% | 0.95972 | 7.741% | [5 empty] | TXV | 4.028%
Stockton | CA | 95204-2737 |  | 2014-06-03 | 2014-06-03 08:17 | 2014-06-03 08:35 | WESTINGHOUSE - ID042NOA | 136 | 4 | Yes | Yes | 19 | 18.7 | 0.3 | AD6EEBC347BD47A98AA9A45A12D11066 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93705-2122 |  | 2014-07-28 | 2014-07-28 08:54 | 2014-07-28 09:17 | BRYANT - 582ANW024040AAAD | 53 | 6.2 | Yes | Yes | 22.8 | 19.1 | 3.7 | ABDB197CAD554AF48702E01F8B52D38F |  | R22 | TXV |  | 11.7% | 0.88302 | 22.48% | [5 empty] | TXV | 11.7%
Lathrop | CA | 95330-9367 |  | 2014-05-28 | 2014-05-28 10:10 | 2014-05-28 10:30 | CARRIER - 38CK048370 | 121 | 14.7 | Yes | Yes | 18.5 | 20.9 | -2.4 | A15E518532384A12B6C2115B5C7B9F53 |  | R22 | TXV |  | 12.15% | 0.87851 | 23.35% | [5 empty] | TXV | 12.15%
Stockton | CA | 95207-8129 |  | 2014-05-21 | 2014-05-21 10:26 | 2014-05-21 10:43 | BDP - 585EJ018050 | 55 | 2.6 | Yes | Yes | 19.1 | 18.7 | 0.4 | E88F250E4E0645CDAEF5304841A520F1 |  | R22 | Non-TXV |  | 4.727% | 0.95273 | 9.085% | [5 empty] | Non-TXV | 4.727%
Fresno | CA | 93702-4049 |  | 2014-05-21 | 2014-05-21 14:25 | 2014-05-21 14:48 | WESTINGHOUSE - IE024PCA0N | 84 | 2.7 | Yes | Yes | 22.8 | 21 | 1.8 | 2B5D3DB3D3564327B1736A6EA8E60B61 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Coalinga | CA | 93210-2116 |  | 2014-09-10 | 2014-09-10 08:14 | 2014-09-10 08:55 | CARRIER - UNK | 97 | 2.9 | Yes | Yes | 22.3 | 19.1 | 3.3 | 2C7598C1F449481CA09BBE01CF86FA4A |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Coalinga | CA | 93210-2100 |  | 2014-09-10 | 2014-09-10 12:31 | 2014-09-10 12:51 | CARRIER - UNK | 91 | 2.7 | Yes | Yes | 21.9 | 21 | 0.9 | 35A71948AFB44E99BC4989647585CC3E |  | R22 | Non-TXV |  | 2.967% | 0.97033 | 5.702% | [5 empty] | Non-TXV | 2.967%
Fresno | CA | 93722-9116 |  | 2014-05-29 | 2014-05-29 13:23 | 2014-05-29 13:39 | GOODMAN - GPG10360701A | 75 | 14.7 | Yes | Yes | 24.7 | 19.2 | 5.5 | B3F302C8ADC648D39D13B10A36C150D1 |  | R22 | Non-TXV |  | 19.6% | 0.804 | 37.67% | [5 empty] | Non-TXV | 19.6%
Fresno | CA | 93726-5249 |  | 2014-05-28 | 2014-05-28 15:22 | 2014-05-28 15:43 | HEIL - NRGF42DKB04 | 90 | 12.4 | Yes | Yes | 24 | 22.6 | 1.4 | F705E3C1FD424F099F600A22A040E526 |  | R22 | Non-TXV |  | 13.78% | 0.86222 | 26.48% | [5 empty] | Non-TXV | 13.78%
Fresno | CA | 93705-4335 |  | 2014-07-22 | 2014-07-22 18:01 | 2014-07-22 18:43 | YORK - D3NZ036N05606NXC | 64 | 2 | Yes | Yes | 25.3 | 20.4 | 4.9 | F63AC93AAADC4289A3A5FEE56F611FAE |  | R410A | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93722-6726 |  | 2014-05-23 | 2014-05-23 08:59 | 2014-05-23 09:16 | GOODMAN - PGJ0360751B | 81 | 5.2 | Yes | Yes | 18.8 | 15.8 | 3 | 20D7E29F15214B59BA05D59D24D481C6 |  | R22 | Non-TXV |  | 6.42% | 0.9358 | 12.34% | [5 empty] | Non-TXV | 6.42%
Clovis | CA | 93611-4505 |  | 2014-06-11 | 2014-06-11 12:20 | 2014-06-11 12:37 | BDP - 585A030080YAC | 50 | 8.1 | Yes | Yes | 24.9 | 20.4 | 4.5 | 9524A464006C4C329736500EF7C6DC4E |  | R22 | Non-TXV |  | 16.2% | 0.838 | 31.13% | [5 empty] | Non-TXV | 16.2%
Lathrop | CA | 95330-8699 |  | 2014-05-27 | 2014-05-27 14:28 | 2014-05-27 14:53 | CARRIER - 24ABA336A310 | 105 | 9.4 | Yes | Yes | 23.3 | 21 | 2.3 | 462D021432864EA3AC1CD32EBC63C718 |  | R410A | TXV |  | 8.952% | 0.91048 | 17.2% | [5 empty] | TXV | 8.952%
Tracy | CA | 95376-4850 |  | 2014-05-23 | 2014-05-23 10:33 | 2014-05-23 10:59 | AMERICAN STANDARD - 2A7A1024A1000AAA | 62 | 4.1 | Yes | Yes | 20.8 | 20.4 | 0.4 | 53EA07133E1A419C966A378F27C59C06 |  | R22 | Non-TXV |  | 6.613% | 0.93387 | 12.71% | [5 empty] | Non-TXV | 6.613%
Stockton | CA | 95210-2004 |  | 2014-06-13 | 2014-06-13 09:42 | 2014-06-13 10:00 | LENNOX - PGC036K080E | 85 | 4.1 | Yes | Yes | 23.4 | 20.3 | 3.1 | 82986D0C4C994A43B028C5AF6C4BAF85 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fresno | CA | 93726-7300 |  | 2014-07-14 | 2014-07-14 12:40 | 2014-07-14 12:41 | OTHER - UNK | 56 | 7.6 | Yes | Yes | 22.7 | 22.7 | 0 | 7355F7F82B9C4383BFEF34A3255F7360 |  | R22 | Non-TXV |  | 13.57% | 0.86429 | 26.08% | [5 empty] | Non-TXV | 13.57%
Fresno | CA | 93720-5421 |  | 2014-06-07 | 2014-06-07 09:21 | 2014-06-07 10:15 | LENNOX - 13ACC-042-230-01 | 123 | 3.8 | Yes | Yes | 19.2 | 21 | -1.8 | 0FC78286E82A40ADBC3E6E8B674CF265 |  | R22 | Non-TXV |  | 3.089% | 0.96911 | 5.937% | [5 empty] | Non-TXV | 3.089%
Fresno | CA | 93727-2536 |  | 2014-06-03 | 2014-06-03 12:57 | 2014-06-03 14:28 | ICP - GPFM48K080E | 100 | 3.5 | Yes | Yes | 21.5 | 21 | 0.5 | 029150E160AC44C2ABEBD5B7532481D5 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Fresno | CA | 93726-1632 |  | 2014-05-28 | 2014-05-28 11:14 | 2014-05-28 11:34 | YORK - D1NP042N090A6A | 150 | 5.8 | Yes | Yes | 22.4 | 23.1 | -0.7 | D68EEC132B9F484083F2CB907B004F53 |  | R22 | Non-TXV |  | 3.867% | 0.96133 | 7.431% | [5 empty] | Non-TXV | 3.867%
Clovis | CA | 93612-3413 |  | 2014-06-03 | 2014-06-03 12:04 | 2014-06-03 12:06 | CARRIER - 7777UNK | 90 | 3.2 | Yes | Yes | 21.7 | 19.9 | 1.8 | 25F94C0E495842719845B67D1099C540 |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Fresno | CA | 93704-4608 |  | 2014-06-17 | 2014-06-17 11:22 | 2014-06-17 11:24 | YORK - DAYP-FP24N045A | 74 | 4.3 | Yes | Yes | 21.2 | 21.1 | 0.1 | B3179F9590E24DCEA61B05E72F1005AF |  | R22 | Non-TXV |  | 5.811% | 0.94189 | 11.17% | [5 empty] | Non-TXV | 5.811%
Fresno | CA | 93705-2113 |  | 2014-08-14 | 2014-08-14 12:10 | 2014-08-14 12:27 | BRYANT - 582ANW024040AAD | 53 | 1.6 | Yes | Yes | 15.5 | 17.4 | -1.9 | 22A8C91CB5C54BA69A2C6866EBB89DE0 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Fresno | CA | 93722-6120 |  | 2014-07-28 | 2014-07-28 12:22 | 2014-07-28 12:40 | BDP - 585CJ030050AAAF | 78 | 2.4 | Yes | Yes | 24.6 | 20.4 | 4.2 | F52A6BD3AFA846D6934AE346579AEF8C |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Fresno | CA | 93726-6435 |  | 2014-05-29 | 2014-05-29 14:43 | 2014-05-29 15:06 | GOODMAN - GPH1324M21AB | 108 | 4.3 | Yes | Yes | 24.3 | 24.2 | 0.1 | 49F342E12CB54BC6BAD85CE7BC605656 |  | R22 | Non-TXV |  | 3.981% | 0.96019 | 7.652% | [5 empty] | Non-TXV | 3.981%
Stockton | CA | 95207-6004 |  | 2014-05-21 | 2014-05-21 11:55 | 2014-05-21 12:12 | RHEEM - UNK | 64 | 7.7 | Yes | Yes | 22.2 | 19.5 | 2.7 | 5FF2DF59C973400C92A8C0DA7171DB52 |  | R22 | Non-TXV |  | 12.03% | 0.87969 | 23.12% | [5 empty] | Non-TXV | 12.03%
Fresno | CA | 93705-2113 |  | 2014-07-28 | 2014-07-28 09:32 | 2014-07-28 09:51 | BRYANT - 582ANW030040AAAD | 55 | 4.1 | Yes | Yes | 23.8 | 18.3 | 5.5 | C42861690B874D3092A9AFFBA4754779 |  | R22 | Non-TXV |  | 7.455% | 0.92545 | 14.33% | [5 empty] | Non-TXV | 7.455%
Fresno | CA | 93703-1657 |  | 2014-05-15 | 2014-05-15 14:23 | 2014-05-15 14:46 | BDP - 585HJW036060 | 102 | 3.8 | Yes | Yes | 22.1 | 21 | 1.1 | 33D9528E30DD4C16B7C2764A79E15CBE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.725% | 0.96275 | 7.16% | [5 empty] | Non-TXV | 3.725%
Madera | CA | 93636-9245 |  | 2014-06-09 | 2014-06-09 09:34 | 2014-06-09 09:53 | RHEEM - RRKAA030JK06E | 54 | 9.6 | Yes | Yes | 25.2 | 22 | 3.2 | 3E6B51EDAD6C44E498AD98119158DBC7 |  | R22 | Non-TXV |  | 17.78% | 0.82222 | 34.16% | [5 empty] | Non-TXV | 17.78%
Firebaugh | CA | 93622-2103 |  | 2014-08-06 | 2014-08-06 14:18 | 2014-08-06 14:44 | YORK - D1NP030NO5606A | 73 | 2.2 | Yes | Yes | 16.8 | 14.5 | 2.3 | E0ABCA4A0B4347F8B47134BA26D8EC7C |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Fresno | CA | 93706-4306 |  | 2014-09-05 | 2014-09-05 16:15 | 2014-09-05 16:16 | WESTINGHOUSE - 1E036BAAON | 120 | 22.8 | Yes | Yes | 17.4 | 15.6 | 1.8 | 7CECBB3EAC6E48E2AA7CD988C2D7074A | Add refrigerant: 19.8 oz | R22 | Non-TXV |  | 19% | 0.81 | 36.51% | [5 empty] | Non-TXV | 19%
Selma | CA | 93662-3024 |  | 2014-06-13 | 2014-06-13 11:56 | 2014-06-13 12:23 | RHEEM - RRNA-B060JK10X | 145 | 5.9 | Yes | Yes | 26 | 20.4 | 5.6 | A4C7DB02DC8C4D05BE303F0BB62785F3 |  | R22 | Non-TXV |  | 4.069% | 0.95931 | 7.82% | [5 empty] | Non-TXV | 4.069%
Lathrop | CA | 95330-8973 |  | 2014-06-03 | 2014-06-03 13:00 | 2014-06-03 13:20 | NORDYNE - JS3BC-060KA | 85 | 10.3 | Yes | Yes | 21.9 | 21 | 0.9 | 0380227D19614B068110B54B2AA510F0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.12% | 0.87882 | 23.29% | [5 empty] | Non-TXV | 12.12%
Lincoln | CA | 95648-8449 |  | 2014-05-26 | 2014-05-26 11:42 | 2014-05-26 11:58 | YORK - H1RC036S06D | 98 | 3.8 | Yes | Yes | 17 | 19.9 | -2.9 | 769B417FDFE54CBBBCC6A29F98A76980 |  | R22 | Non-TXV |  | 3.878% | 0.96122 | 7.452% | [5 empty] | Non-TXV | 3.878%
Fresno | CA | 93711-2147 |  | 2014-05-26 | 2014-05-26 11:25 | 2014-05-26 11:49 | ICP - R2A336GKR2 | 83 | 9.8 | Yes | Yes | 22.5 | 22.6 | -0.1 | A5E2DB6353E74AABA59BFEAAB213112A |  | R22 | TXV |  | 11.81% | 0.88193 | 22.69% | [5 empty] | TXV | 11.81%
Stockton | CA | 95210-1253 |  | 2014-05-15 | 2014-05-15 13:28 | 2014-05-15 13:45 | GOODMAN - GPG13360701AC | 112 | 6 | Yes | Yes | 29.8 | 23.9 | 6 | 4DA0A76BC22C400E90CE171722A52401 |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Los Banos | CA | 93635-7408 |  | 2014-06-27 | 2014-06-27 08:10 | 2014-06-27 08:37 | GIBSON - JS3BC-036KA | 82 | 12.4 | Yes | Yes | 17 | 19.9 | -2.9 | 4F62B8815A054EACB73FE6E6F5DC6664 |  | R22 | Non-TXV |  | 15.12% | 0.84878 | 29.06% | [5 empty] | Non-TXV | 15.12%
Dinuba | CA | 93618-4044 |  | 2014-07-29 | 2014-07-29 14:35 | 2014-07-29 15:06 | NORDYNE - FS3BA-030KA | 68 | 11 | Yes | Yes | 22 | 22.1 | -0.1 | 6C1FE646E19249B983C14847D6A5391D |  | R22 | Non-TXV |  | 16.18% | 0.83824 | 31.09% | [5 empty] | Non-TXV | 16.18%
Tracy | CA | 95376-2528 |  | 2014-06-24 | 2014-06-24 14:13 | 2014-06-24 14:41 | RUUD - UAKA-307JAZ | 85 | 4.6 | Yes | Yes | 21.4 | 21.4 | 0 | 7C6951BD9BE141F986CF9475A9A5A9E2 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Dinuba | CA | 93618-4044 |  | 2014-07-11 | 2014-07-11 11:25 | 2014-07-11 12:27 | NORDYNE - FS3BA-030KA | 68 | 8 | Yes | Yes | 20.4 | 20.4 | 0 | 3BB6291BA2724DF79FA3D77DEF1570DF |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Fresno | CA | 93706-4923 |  | 2014-05-20 | 2014-05-20 11:53 | 2014-05-20 12:14 | OTHER - 4YCY4042B1096B4 | 112 | 7 | Yes | Yes | 20.5 | 16.5 | 4 | 78CCF55342E145E39B61BA0364F2F5F7 |  | R410A | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Stockton | CA | 95207-6027 |  | 2014-05-21 | 2014-05-21 12:42 | 2014-05-21 12:42 | GOODMAN - GSC130421AA | 143 | 0 | Yes | Yes | 16.3 | 18.7 | -2.4 | CEE46BA680FF492998EE8719B4C1BD4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3418 |  | 2014-06-17 | 2014-06-17 14:02 | 2014-06-17 14:24 | COLEMAN - UNK | 85 | 3 | Yes | Yes | 24.3 | 21.5 | 2.8 | A44D9E06C7B44967AB2CC9CD5C784F58 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93705-1328 |  | 2014-05-28 | 2014-05-28 13:42 | 2014-05-28 13:45 | YORK - D3GH036N07006A | 112 | 3.7 | Yes | Yes | 25.5 | 19.5 | 6 | E806929572C5476482A8967CB4609A6C |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Los Banos | CA | 93635-9227 |  | 2014-07-10 | 2014-07-10 14:51 | 2014-07-10 15:15 | GIBSON - JS5BD-036K | 85 | 18.2 | Yes | Yes | 24.2 | 20.1 | 4.1 | 7DE134B05FA14B82A0C22582D4B0A159 |  | R22 | Non-TXV |  | 21.41% | 0.78588 | 41.15% | [5 empty] | Non-TXV | 21.41%
Coarsegold | CA | 93614-9085 |  | 2014-07-07 | 2014-07-07 10:38 | 2014-07-07 10:39 | OTHER - HS294612P | 89 | 13.9 | Yes | Yes | 20.7 | 19.8 | 0.9 | 93E6AFD02D7444D083ADA49686FB4CE0 |  | R22 | Non-TXV |  | 15.62% | 0.84382 | 30.01% | [5 empty] | Non-TXV | 15.62%
Coarsegold | CA | 93614-9085 |  | 2014-07-07 | 2014-07-07 11:13 | 2014-07-07 11:14 | OTHER - HS294612P | 89 | 9.9 | Yes | Yes | 20.6 | 18.7 | 1.9 | C32086B616B04F33A836E058665437DA |  | R22 | Non-TXV |  | 11.12% | 0.88876 | 21.38% | [5 empty] | Non-TXV | 11.12%
Fresno | CA | 93705-3923 |  | 2014-05-26 | 2014-05-26 14:19 | 2014-05-26 14:36 | COLEMAN - DAYPF060N110A | 140 | 18.4 | Yes | Yes | 25.5 | 20.4 | 5.1 | 95289EDDF1444741998333187F8630CF |  | R22 | Non-TXV |  | 13.14% | 0.86857 | 25.26% | [5 empty] | Non-TXV | 13.14%
Atwater | CA | 95301-4732 |  | 2014-05-16 | 2014-05-16 13:11 | 2014-05-16 13:12 | GOODMAN - CK36-1B | 76 | 2.7 | Yes | Yes | 21.8 | 24.8 | -3 | 06D4401850D240D4BCE8A36D603AFEDA |  | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Dinuba | CA | 93618-4045 |  | 2014-07-14 | 2014-07-14 20:11 | 2014-07-14 20:33 | NORDYNE - FS3BA-030KA | 68 | 12.3 | Yes | Yes | 22.5 | 20.6 | 1.9 | 5AFED1FE6E744B12BD717B782A46E843 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.09% | 0.81912 | 34.76% | [5 empty] | Non-TXV | 18.09%
Selma | CA | 93662-3461 |  | 2014-06-21 | 2014-06-21 14:53 | 2014-06-21 15:16 | PAYNE - N/A | 60 | 4.5 | Yes | Yes | 20.6 | 22.6 | -2 | 2AD42681262E4206A0D750B6CC0EE953 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Stockton | CA | 95207-6065 |  | 2014-06-04 | 2014-06-04 08:58 | 2014-06-04 09:29 | PAYNE - PY1PNB024060AAAA | 53 | 4 | Yes | Yes | 22.1 | 19.5 | 2.6 | D7A32F0C3D9A4239BB83D3582C1D10DD |  | R22 | Non-TXV |  | 7.547% | 0.92453 | 14.5% | [5 empty] | Non-TXV | 7.547%
Fresno | CA | 93725-1217 |  | 2014-06-16 | 2014-06-16 09:12 | 2014-06-16 09:14 | OTHER - 585B03075YACR | 50 | 5.4 | Yes | Yes | 21.9 | 16.5 | 5.4 | C868B5AF17D84123A744397153B485FC |  | R22 | Non-TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | Non-TXV | 10.8%
Fresno | CA | 93727-3654 |  | 2014-06-04 | 2014-06-04 15:42 | 2014-06-04 16:12 | LENNOX - 12GCS042-75-3PA | 133 | 5.4 | Yes | Yes | 26.3 | 21.2 | 5.1 | 8A5AA95DF7B44994A9896315A33E2703 |  | R22 | Non-TXV |  | 4.06% | 0.9594 | 7.803% | [5 empty] | Non-TXV | 4.06%
Fresno | CA | 93705-3613 |  | 2014-09-09 | 2014-09-09 12:49 | 2014-09-09 12:51 | RUUD - URKA-A024JK06X | 50 | 2.9 | Yes | Yes | 21.7 | 21.5 | 0.2 | C2D222299E774715B7D1C8B09FDFAF72 |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Selma | CA | 93662-2916 |  | 2014-06-13 | 2014-06-13 11:12 | 2014-06-13 11:35 | RHEEM - URKA0A036JK08E | 62 | 5.6 | Yes | Yes | 21.1 | 21 | 0.1 | 8D15F8FC079C4E78A7031DC507B09C79 |  | R22 | Non-TXV |  | 9.032% | 0.90968 | 17.36% | [5 empty] | Non-TXV | 9.032%
Selma | CA | 93662-2028 |  | 2014-06-21 | 2014-06-21 16:13 | 2014-06-21 16:31 | NORDYNE - G4GD-036K072X | 100 | 4.8 | Yes | Yes | 18.6 | 20.9 | -2.3 | 98C6E89BB6524AB0BE1DA4BB9FC39828 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Fresno | CA | 93722-6704 |  | 2014-05-28 | 2014-05-28 13:09 | 2014-05-28 13:27 | GOODMAN - GSC130361DE | 119 | 14.5 | Yes | Yes | 22.6 | 19.8 | 2.8 | B1198F36582442F09FE3871F8665BEEE |  | R22 | Non-TXV |  | 12.18% | 0.87815 | 23.42% | [5 empty] | Non-TXV | 12.18%
Dinuba | CA | 93618-4046 |  | 2014-07-10 | 2014-07-10 13:32 | 2014-07-10 14:24 | NORDYNE - N/A | 64 | 11.3 | Yes | Yes | 20 | 21.4 | -1.4 | C26FB21942B340B2B8679FB327D95944 |  | R22 | Non-TXV |  | 17.66% | 0.82344 | 33.93% | [5 empty] | Non-TXV | 17.66%
Fresno | CA | 93725-9359 |  | 2014-06-21 | 2014-06-21 08:59 | 2014-06-21 09:23 | LENNOX - 12GCS036X-75-2PA | 110 | 5.4 | Yes | Yes | 23.8 | 20.8 | 3 | 713859CCB2884A0FAC2B65E131F9639B |  | R22 | Non-TXV |  | 4.909% | 0.95091 | 9.434% | [5 empty] | Non-TXV | 4.909%
Coarsegold | CA | 93614-9061 |  | 2014-07-11 | 2014-07-11 11:12 | 2014-07-11 11:13 | RUUD - URMAA042JK08E | 114 | 16.5 | Yes | Yes | 24.8 | 22.1 | 2.7 | 44A369A41D5C458DAD331BBF51FD8DD1 |  | R22 | Non-TXV |  | 14.47% | 0.85526 | 27.82% | [5 empty] | Non-TXV | 14.47%
Merced | CA | 95348-1809 |  | 2014-06-09 | 2014-06-09 17:11 | 2014-06-09 17:33 | GE - BTD724A100AO | 68 | 11.4 | Yes | Yes | 24.9 | 22 | 2.9 | F19DCA266D064865A67EFB8FB52A983D |  | R22 | Non-TXV |  | 16.76% | 0.83235 | 32.22% | [5 empty] | Non-TXV | 16.76%
Fresno | CA | 93726-0867 |  | 2014-05-23 | 2014-05-23 11:28 | 2014-05-23 11:51 | DAY & NIGHT - 24/60 YAC -108K | 56 | 3.2 | Yes | Yes | 21.6 | 21 | 0.6 | BBB33DB9CE7C42FBAD5C002D1DF6D3DA |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Stockton | CA | 95207-1345 |  | 2014-05-30 | 2014-05-30 10:48 | 2014-05-30 11:08 | BRYANT - 563CN036-D | 101 | 4.6 | Yes | Yes | 18.9 | 19.9 | -1 | CABFAF3DAAEC4D298A6194A8CDC85154 |  | R22 | Non-TXV |  | 4.554% | 0.95446 | 8.753% | [5 empty] | Non-TXV | 4.554%
Sanger | CA | 93657-8736 |  | 2014-06-18 | 2014-06-18 12:48 | 2014-06-18 13:18 | LENNOX - 10GCS042X-100-6PB | 73 | 6.8 | Yes | Yes | 23.1 | 21 | 2.1 | EA4A3FECE3BA41B3AEA18A77B2F81D8D |  | R22 | Non-TXV |  | 9.315% | 0.90685 | 17.9% | [5 empty] | Non-TXV | 9.315%
Fresno | CA | 93704-1214 |  | 2014-06-13 | 2014-06-13 09:52 | 2014-06-13 10:09 | OTHER - D1NP042N06506A | 150 | 16 | Yes | Yes | 20.1 | 17.6 | 2.5 | 3A9C29F7BA174AED87551364B8B2FAD1 |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Los Banos | CA | 93635-5229 |  | 2014-07-11 | 2014-07-11 08:25 | 2014-07-11 08:45 | BRYANT - 561CJ042-A | 85 | 5 | Yes | Yes | 23.2 | 19.4 | 3.8 | 2AEB2A5CBDD34D35A7F3AF81416233ED |  | R22 | TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | TXV | 5.882%
Fresno | CA | 93720-2304 |  | 2014-06-19 | 2014-06-19 15:00 | 2014-06-19 15:22 | CARRIER - N/A | 120 | 15 | Yes | Yes | 23 | 23 | 0 | CCAF716EF419475E9FF49C73F2D355A7 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Chico | CA | 95928-7354 |  | 2014-05-20 | 2014-05-20 12:13 | 2014-05-20 13:29 | YORK - H1RC036S060 | 98 | 6.4 | Yes | Yes | 19.3 | 21.5 | -2.2 | BCAC1F11B54F48AB98C592116235AF0E |  | R22 | Non-TXV |  | 6.531% | 0.93469 | 12.55% | [5 empty] | Non-TXV | 6.531%
Fresno | CA | 93720-2107 |  | 2014-06-04 | 2014-06-04 12:31 | 2014-06-04 12:52 | PAYNE - UNK | 76 | 12.9 | Yes | Yes | 20.8 | 20.1 | 0.7 | BB5D876CF8D64EAD8784481551A1E2C5 |  | R22 | Non-TXV |  | 16.97% | 0.83026 | 32.62% | [5 empty] | Non-TXV | 16.97%
Cameron Park | CA | 95682-8984 |  | 2014-06-03 | 2014-06-03 16:05 | 2014-06-03 16:22 | OTHER - 38BRG042300 | 101 | 3.5 | Yes | Yes | 22 | 20.2 | 1.8 | 77568BF34A3449E5B2E2008B5E0230F9 |  | R22 | Non-TXV |  | 3.465% | 0.96535 | 6.66% | [5 empty] | Non-TXV | 3.465%
Yuba City | CA | 95991-6169 |  | 2014-07-08 | 2014-07-08 12:42 | 2014-07-08 12:59 | AMERICAN STANDARD - YCC042F1MOBH | 104 | 3.1 | Yes | Yes | 22 | 20.4 | 1.6 | 8360A32C44BE49FCA2C3772D437ABC39 |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Oakhurst | CA | 93644-9548 |  | 2014-08-27 | 2014-08-27 11:05 | 2014-08-27 11:05 | OTHER - UNK | 76 | 0 | Yes | Yes | 18.3 | 20.6 | -2.3 | 472032AFAB4E42068856644D40B2F339 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1244 |  | 2014-09-30 | 2014-09-30 09:45 | 2014-09-30 10:07 | PAYNE - N/A | 90 | 14.2 | Yes | Yes | 22 | 20.6 | 1.4 | D0529C50481A496B80C294BC6E48F725 |  | R22 | Non-TXV |  | 15.78% | 0.84222 | 30.32% | [5 empty] | Non-TXV | 15.78%
Fresno | CA | 93703-2051 |  | 2014-05-16 | 2014-05-16 09:12 | 2014-05-16 09:30 | LENNOX - 12GCS060X-100-2PA | 159 | 4.9 | Yes | Yes | 25.5 | 20.9 | 4.6 | 9545A609FDAC413C9DAF8F1AE0FB1EC1 |  | R22 | Non-TXV |  | 3.082% | 0.96918 | 5.922% | [5 empty] | Non-TXV | 3.082%
Auburn | CA | 95603-3126 |  | 2014-05-22 | 2014-05-22 09:08 | 2014-05-22 09:37 | OTHER - 561CJX030000ABAA | 70 | -4.1 | Yes | Yes | 18 | 19.7 | -1.7 | 9173C9245336408495B69DAE1A94C95C |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Fresno | CA | 93704-1217 |  | 2014-06-20 | 2014-06-20 16:01 | 2014-06-20 16:17 | ICP - N2A342AKA200 | 104 | 14.6 | Yes | Yes | 23.5 | 20.9 | 2.6 | 9068961B115A4093A53FD38FF014E494 |  | R22 | TXV |  | 14.04% | 0.85962 | 26.98% | [5 empty] | TXV | 14.04%
Fresno | CA | 93720-4154 |  | 2014-06-04 | 2014-06-04 11:34 | 2014-06-04 11:50 | CARRIER - 48SX030040311 | 69 | 13.7 | Yes | Yes | 21.6 | 20.4 | 1.2 | 9C2DC992113246CBB4370A2FA5FB969D |  | R22 | Non-TXV |  | 19.86% | 0.80145 | 38.16% | [5 empty] | Non-TXV | 19.86%
Los Banos | CA | 93635-9507 |  | 2014-06-11 | 2014-06-11 16:38 | 2014-06-11 16:41 | YORK - D1NX048N09006A | 152 | 4.6 | Yes | Yes | 20.9 | 20.9 | 0 | 8DD6E62DF248416CA2776DD17DECF21F |  | R410A | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Lathrop | CA | 95330-8974 |  | 2014-06-03 | 2014-06-03 12:11 | 2014-06-03 12:58 | NORDYNE - JS3BC-060KA | 85 | 8.6 | Yes | Yes | 20.3 | 20.4 | -0.1 | 40F362B90F70468796B74F4A85791A6D |  | R22 | Non-TXV |  | 10.12% | 0.89882 | 19.44% | [5 empty] | Non-TXV | 10.12%
Stockton | CA | 95207-6065 |  | 2014-06-02 | 2014-06-02 10:11 | 2014-06-02 10:32 | RHEEM - UNK | 54 | 2 | Yes | Yes | 20.6 | 19.5 | 1.1 | 0E54BC59B533417FB6234A59AB6AAAED |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Fresno | CA | 93720-2331 |  | 2014-08-26 | 2014-08-26 13:42 | 2014-08-26 13:43 | DAY & NIGHT - 580A036 | 78 | 12.7 | Yes | Yes | 22.1 | 19.6 | 2.5 | 8F36C634CC53465791F01207DEC15CA2 |  | R22 | Non-TXV |  | 16.28% | 0.83718 | 31.29% | [5 empty] | Non-TXV | 16.28%
Fresno | CA | 93720-2331 |  | 2014-08-26 | 2014-08-26 13:47 | 2014-08-26 13:50 | DAY & NIGHT - 580A036 | 78 | 14.1 | Yes | Yes | 21.6 | 19.7 | 1.9 | 3C9B3F874D764F74B1A8C39A134E2001 |  | R22 | Non-TXV |  | 18.08% | 0.81923 | 34.74% | [5 empty] | Non-TXV | 18.08%
Atwater | CA | 95301-4522 |  | 2014-05-16 | 2014-05-16 12:02 | 2014-05-16 12:03 | AMANA - VCA36C2A | 60 | 3 | Yes | Yes | 23.5 | 22.6 | 0.9 | E539BA9C2CF84DAEA4576DCDFED26480 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Atwater | CA | 95301-4526 |  | 2014-05-19 | 2014-05-19 11:13 | 2014-05-19 11:15 | COLEMAN - AM030MA322A | 59 | 4.1 | Yes | Yes | 22.1 | 19.9 | 2.2 | F7D90E8840DB4E8EAFE5C10608E415AE |  | R22 | Non-TXV |  | 6.949% | 0.93051 | 13.35% | [5 empty] | Non-TXV | 6.949%
Fresno | CA | 93705-3103 |  | 2014-07-14 | 2014-07-14 12:41 | 2014-07-14 12:58 | GOODMAN - UNK | 80 | -4.7 | Yes | Yes | 19 | 18.9 | 0.1 | 0500EC2DC4C649909FA6AB449F6BB8F7 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Fresno | CA | 93710-4209 |  | 2014-05-29 | 2014-05-29 10:58 | 2014-05-29 11:28 | BDP - 585EJW036075 | 82 | 6.1 | Yes | Yes | 26.7 | 22 | 4.7 | 5662C6B0E9E347A29B61DCD07F07685A |  | R22 | Non-TXV |  | 7.439% | 0.92561 | 14.3% | [5 empty] | Non-TXV | 7.439%
Stockton | CA | 95207-6039 |  | 2014-05-22 | 2014-05-22 10:36 | 2014-05-22 10:36 | OTHER - UNK | 48 | 0 | Yes | Yes | 19.7 | 17.7 | 2 | D1FCA6D4FE784F0CA4EE9EFB5574D03D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3013 |  | 2014-06-11 | 2014-06-11 12:06 | 2014-06-11 12:07 | YORK - D3Z030N05606NXA | 64 | 2.4 | Yes | Yes | 22.6 | 19.3 | 3.3 | EF61911DDCC841159862690A55512E55 |  | R410A | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Dinuba | CA | 93618-4050 |  | 2014-07-11 | 2014-07-11 10:33 | 2014-07-11 11:20 | NORDYNE - FS3BA-024KA | 64 | 5.6 | Yes | Yes | 21.4 | 22.1 | -0.7 | 97988866CD1B4336808141890F086699 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Magalia | CA | 95954-9329 |  | 2014-06-04 | 2014-06-04 10:36 | 2014-06-04 10:57 | BRYANT - NA | 65 | 2 | Yes | Yes | 20.5 | 20.5 | 0 | FD0F4326F7A24DBFB347E41583B2D6DB |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Oroville | CA | 95965-3269 |  | 2014-06-06 | 2014-06-06 08:18 | 2014-06-06 08:42 | OTHER - TTBO24C100A2 | 54 | 5 | Yes | Yes | 16.6 | 19.5 | -2.9 | AE696AB0964A49E8A071B0BE00B92657 |  | R22 | Non-TXV |  | 9.259% | 0.90741 | 17.79% | [5 empty] | Non-TXV | 9.259%
Chico | CA | 95928-7075 |  | 2014-05-20 | 2014-05-20 11:55 | 2014-05-20 12:10 | LENNOX - GCS20R-411-75-1P | 85 | 6.2 | Yes | Yes | 22.5 | 20.4 | 2.1 | D6DA7740004445B3AA2ED8E8281BA5FD |  | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Los Banos | CA | 93635-2639 |  | 2014-06-06 | 2014-06-06 10:53 | 2014-06-06 10:53 | GOODMAN - CK36-1B | 76 | 2.6 | Yes | Yes | 20.5 | 21.2 | -0.7 | D0E68D7B6F6642F783CA673F621A6641 | Add refrigerant: 2.6 oz | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Dinuba | CA | 93618-4051 |  | 2014-07-21 | 2014-07-21 16:42 | 2014-07-21 17:24 | NORDYNE - FS3BA-024KA | 64 | 5.4 | Yes | Yes | 23.5 | 22.5 | 1 | 1AD97E48DC57412F90D54866769C4892 |  | R22 | Non-TXV |  | 8.438% | 0.91563 | 16.22% | [5 empty] | Non-TXV | 8.438%
Dinuba | CA | 93618-4051 |  | 2014-07-10 | 2014-07-10 14:27 | 2014-07-10 15:02 | NORDYNE - FS3BA-030KA | 67 | 2.9 | Yes | Yes | 22.1 | 22 | 0.1 | FDCD134D4817402CAA2D32BEFEBDB531 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.328% | 0.95672 | 8.318% | [5 empty] | Non-TXV | 4.328%
Stockton | CA | 95207-6041 |  | 2014-06-04 | 2014-06-04 10:29 | 2014-06-04 10:29 | RHEEM - UNK | 54 | 0 | Yes | Yes | 21.1 | 18.7 | 2.4 | ABE6686E3FAC4FA8A02059DF485D2D7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-3179 |  | 2014-06-07 | 2014-06-07 11:32 | 2014-06-07 11:50 | DAY & NIGHT - 585GJ030040 | 58 | 1.8 | Yes | Yes | 24.5 | 18.7 | 5.9 | C9B51265C059446392AC95F49BAE7743 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Sutter | CA | 95982-2507 |  | 2014-09-10 | 2014-09-10 16:18 | 2014-09-10 16:39 | BDP - 585B048T25YACR | 93 | 3 | Yes | Yes | 26 | 21.3 | 4.7 | 99F1C9984E7245DD9843DE8067497DB7 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Paradise | CA | 95969-3020 |  | 2014-06-13 | 2014-06-13 13:45 | 2014-06-13 14:18 | BRYANT - 574BNW036060NB | 85 | 4 | Yes | Yes | 23.6 | 21.3 | 2.3 | 6B28C5B9F3B64682BDEEF608327EA52F |  | R410A | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Atwater | CA | 95301-4521 |  | 2014-05-19 | 2014-05-19 10:41 | 2014-05-19 10:42 | GOODMAN - GSC130421AC | 137 | 5.1 | Yes | Yes | 25 | 19.1 | 5.9 | 09A6EA22502D46A9B39778207E303EAD |  | R22 | Non-TXV |  | 3.723% | 0.96277 | 7.154% | [5 empty] | Non-TXV | 3.723%
Dinuba | CA | 93618-4045 |  | 2014-07-14 | 2014-07-14 12:13 | 2014-07-14 12:46 | NORDYNE - FS3BA-030KA | 68 | 16.7 | Yes | Yes | 21.4 | 21.4 | 0 | 23B306FE12A845FFB7965A4B9FD0B8B1 |  | R22 | Non-TXV |  | 24.56% | 0.75441 | 47.2% | [5 empty] | Non-TXV | 24.56%
Oroville | CA | 95965-4727 |  | 2014-06-04 | 2014-06-04 09:53 | 2014-06-04 10:20 | CARRIER - 48SX-036060331AA | 84 | 2.5 | Yes | Yes | 26 | 20.6 | 5.4 | 63EC269C4A35447893EC7CE24BF7FA3E |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Fresno | CA | 93726-0939 |  | 2014-06-20 | 2014-06-20 09:27 | 2014-06-20 09:28 | DAY & NIGHT - 2460YAC108T | 54 | 7.1 | Yes | Yes | 18.3 | 16.9 | 1.5 | A02E8802724D4B22B7482E30C0A47115 |  | R22 | Non-TXV |  | 13.15% | 0.86852 | 25.27% | [5 empty] | Non-TXV | 13.15%
Merced | CA | 95341-7022 |  | 2014-07-03 | 2014-07-03 12:38 | 2014-07-03 12:40 | GOODMAN - CLJ36-1A | 109 | 5 | Yes | Yes | 18.7 | 20.4 | -1.7 | F5424792D25A437681F838202E279BD0 |  | R22 | Non-TXV |  | 4.587% | 0.95413 | 8.816% | [5 empty] | Non-TXV | 4.587%
Fresno | CA | 93727-5861 |  | 2014-06-10 | 2014-06-10 14:33 | 2014-06-10 15:04 | LENNOX - 13ACD06023002 | 214 | 36.4 | Yes | Yes | 19.4 | 20.6 | -1.2 | 5E9868566BA3404683B2515D10AF052E |  | R22 | Non-TXV |  | 17.01% | 0.82991 | 32.69% | [5 empty] | Non-TXV | 17.01%
Fresno | CA | 93728-3242 |  | 2014-06-13 | 2014-06-13 12:17 | 2014-06-13 12:19 | OTHER - 7777UNK | 84 | 3.7 | Yes | Yes | 15.9 | 18.5 | -2.6 | 425BC44BA14E44FFADBCDB3114AEDB70 |  | R22 | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Paradise | CA | 95969-4632 |  | 2014-06-04 | 2014-06-04 13:20 | 2014-06-04 13:43 | YORK - H1RA024506D311 | 104 | 14.7 | Yes | Yes | 20 | 20.9 | -0.9 | CCC3E82A0A0940DFB8AD3A27D2A51386 |  | R22 | Non-TXV |  | 14.13% | 0.85865 | 27.16% | [5 empty] | Non-TXV | 14.13%
Paso Robles | CA | 93446-3628 |  | 2014-06-24 | 2014-06-24 08:44 | 2014-06-24 09:03 | LUXAIRE - EEO024FAA | 38 | -5 | Yes | Yes | 20.6 | 19.5 | 1.1 | 6A52414CBE02479A93389085CD25A82A |  | R22 | Non-TXV |  | -13.16% | 1.1316 | 3.685% |  |  |  |  | Non-TXV |  |  | -13.16%
Lincoln | CA | 95648-8917 |  | 2014-05-20 | 2014-05-20 15:42 | 2014-05-20 16:34 | LENNOX - 13ACD042-230-02 | 111 | 3.7 | Yes | Yes | 22 | 21.3 | 0.7 | F9E4D1BEA54D40A08140D367E9C96BD6 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95215-1529 |  | 2014-06-04 | 2014-06-04 10:58 | 2014-06-04 11:19 | PAYNE - 591ANX030000ABAA | 68 | 12.3 | Yes | Yes | 19.1 | 19.3 | -0.2 | 69C252BB54D34ADD97A4032C2A96C33B |  | R22 | Non-TXV |  | 18.09% | 0.81912 | 34.76% | [5 empty] | Non-TXV | 18.09%
Los Banos | CA | 93635-9427 |  | 2014-07-10 | 2014-07-10 12:19 | 2014-07-10 12:44 | GOODMAN - CKJ36-1AB | 85 | -8 | Yes | Yes | 21.1 | 21.8 | -0.7 | 87ED53EF765946DF89BE826F84E4202C |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95207-6040 |  | 2014-06-04 | 2014-06-04 10:00 | 2014-06-04 10:28 | BRYANT - 574DNWA24060NA | 72 | 2.3 | Yes | Yes | 24 | 19.9 | 4.1 | 7457C9572A1540979249A3DD217FA5B6 |  | R410A | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Stockton | CA | 95209-1555 |  | 2014-05-31 | 2014-05-31 12:58 | 2014-05-31 13:17 | CONCORD - CCU10A30A-1 | 60 | 3.5 | Yes | Yes | 17.8 | 19.9 | -2.1 | 660A36EACA6B4B31AADB8223AC031071 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Dinuba | CA | 93618-4042 |  | 2014-07-10 | 2014-07-10 16:31 | 2014-07-10 16:32 | NORDYNE - FS3BA-030KA | 68 | 6.7 | Yes | Yes | 19.3 | 20.9 | -1.6 | F9D7F34B97E54FECBE791575D44DD9F5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | Non-TXV | 9.853%
Dinuba | CA | 93618-4044 |  | 2014-07-10 | 2014-07-10 15:04 | 2014-07-10 15:27 | NORDYNE - N/A | 60 | 5.5 | Yes | Yes | 20.1 | 22.1 | -2 | 0254EABF0B844C2281C88F0F86E72285 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Fresno | CA | 93703-1227 |  | 2014-05-15 | 2014-05-15 12:46 | 2014-05-15 12:46 | ICP - PGAA30C1K3 | 75 | 0 | Yes | Yes | 26 | 23.1 | 2.9 | 5CA49A1AE7A24C86BEA18F174C640A55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2042 |  | 2014-05-14 | 2014-05-14 09:15 | 2014-05-14 09:32 | GOODMAN - CE361GB | 60 | 2.9 | Yes | Yes | 22.7 | 19.8 | 2.9 | 423382930FB54F61ACA6E020CEE93935 |  | R22 | Non-TXV |  | 4.833% | 0.95167 | 9.289% | [5 empty] | Non-TXV | 4.833%
Chico | CA | 95926-7225 |  | 2014-06-06 | 2014-06-06 14:44 | 2014-06-06 15:00 | YORK - TCGD36S41SAAA | 73 | 2.2 | Yes | Yes | 21.9 | 16.4 | 5.5 | 52A3EEEE4AFF44F6BDFE3177D5D6C3F7 |  | R410A | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Chico | CA | 95973-0663 |  | 2014-06-30 | 2014-06-30 12:50 | 2014-06-30 13:17 | COLEMAN - DRC504813 | 85 | 4.5 | Yes | Yes | 22.6 | 21.7 | 0.9 | 7D55A9CA46A442B3AE74BD87E68C816D |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Fresno | CA | 93706-4929 |  | 2014-05-20 | 2014-05-20 13:14 | 2014-05-20 13:34 | DAY & NIGHT - UNK | 56 | 9 | Yes | Yes | 18.2 | 12.8 | 5.4 | F4B9DDE586194D4999FF73B0013E832F |  | R22 | Non-TXV |  | 16.07% | 0.83929 | 30.89% | [5 empty] | Non-TXV | 16.07%
Chico | CA | 95973-7232 |  | 2014-05-21 | 2014-05-21 13:57 | 2014-05-21 14:37 | TRANE - TTN048D100AO | 128 | 4 | Yes | Yes | 24.5 | 21.3 | 3.3 | 8F63BC39F27548169473933DBD9987EA |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93703-1235 |  | 2014-05-15 | 2014-05-15 10:50 | 2014-05-15 11:20 | GOODMAN - PGB036075-1 | 60 | 10.1 | Yes | Yes | 27.1 | 21.7 | 5.4 | 73F4CF09D0274E999895AC6727CFD05A |  | R22 | Non-TXV |  | 16.83% | 0.83167 | 32.35% | [5 empty] | Non-TXV | 16.83%
Dinuba | CA | 93618-4045 |  | 2014-07-25 | 2014-07-25 17:30 | 2014-07-25 17:33 | NORDYNE - F3BA-030KA | 68 | 6.1 | Yes | Yes | 23 | 22.5 | 0.5 | 22D67B059E7148A8B8929BB80723B80F |  | R22 | Non-TXV |  | 8.971% | 0.91029 | 17.24% | [5 empty] | Non-TXV | 8.971%
Dinuba | CA | 93618-4050 |  | 2014-07-10 | 2014-07-10 16:35 | 2014-07-10 17:03 | NORDYNE - FS3BA-024KA | 64 | 4.4 | Yes | Yes | 19.1 | 21 | -1.9 | 9A9CD4566D944BA2BC92F8DFE06325A8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Le Grand | CA | 95333-9691 |  | 2014-06-05 | 2014-06-05 23:18 | 2014-06-05 23:19 | TRANE - YCC036F1M0BF54 | 85 | 3.9 | Yes | Yes | 22.8 | 23.2 | -0.4 | E980702D5986441A9C38CF73CE017C7D |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Stockton | CA | 95206-3602 |  | 2014-07-07 | 2014-07-07 10:14 | 2014-07-07 10:38 | PAYNE - PY1PNB024060AAAA | 53 | 4.9 | Yes | Yes | 26.5 | 22.7 | 3.8 | 8787C6F70D464988B38E9D679909CB95 |  | R22 | Non-TXV |  | 9.245% | 0.90755 | 17.77% | [5 empty] | Non-TXV | 9.245%
Dinuba | CA | 93618-4051 |  | 2014-07-10 | 2014-07-10 17:07 | 2014-07-10 17:16 | NORDYNE - FS3BA-024KA | 69 | 5.7 | Yes | Yes | 18.8 | 20.8 | -2 | 664E51CF0C984DC48B4113555DD4A261 |  | R22 | Non-TXV |  | 8.261% | 0.91739 | 15.88% | [5 empty] | Non-TXV | 8.261%
Stockton | CA | 95212-3017 |  | 2014-05-15 | 2014-05-15 10:56 | 2014-05-15 11:19 | YORK - H2RC036S06G | 83 | 3.4 | Yes | Yes | 22.3 | 20.9 | 1.4 | 7D50A0AA1C564C699E2A65CD5DAA5F03 |  | R22 | Non-TXV |  | 4.096% | 0.95904 | 7.872% | [5 empty] | Non-TXV | 4.096%
Yuba City | CA | 95993-5009 |  | 2014-05-16 | 2014-05-16 10:33 | 2014-05-16 10:33 | LENNOX - 13ACC-036-230-01 | 115 | 0 | Yes | Yes | 24 | 21 | 3 | DD334AECAB684AD49B923AF841098D3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-5009 |  | 2014-05-16 | 2014-05-16 10:42 | 2014-05-16 10:58 | LENNOX - 13ACC-036-230-01 | 115 | 3.5 | Yes | Yes | 20 | 20.2 | -0.1 | 86CB190633E04C8AB845DF2143FE1533 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Rocklin | CA | 95677-1703 |  | 2014-06-18 | 2014-06-18 08:07 | 2014-06-18 08:28 | RHEEM - HC-100-36-21C | 49 | 3.9 | Yes | Yes | 26 | 21.1 | 4.9 | CA18FCD91D634C01A86679B37674F374 |  | R22 | Non-TXV |  | 7.959% | 0.92041 | 15.3% | [5 empty] | Non-TXV | 7.959%
Chico | CA | 95926-2453 |  | 2014-06-02 | 2014-06-02 13:08 | 2014-06-02 13:31 | PAYNE - 20RACCS-167 | 55 | 4.7 | Yes | Yes | 22.1 | 21.1 | 1 | 36E97D7461D046A68BD9FBD61C3364FB |  | R22 | Non-TXV |  | 8.545% | 0.91455 | 16.42% | [5 empty] | Non-TXV | 8.545%
Paradise | CA | 95969-4825 |  | 2014-06-13 | 2014-06-13 16:13 | 2014-06-13 16:49 | YORK - H2RC048S06A | 120 | 5.6 | Yes | Yes | 25 | 24.8 | 0.2 | F3BFA8D4822149D1847EF508A0EA887E |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Fresno | CA | 93710-5702 |  | 2014-06-23 | 2014-06-23 09:12 | 2014-06-23 09:32 | OTHER - 9GHA036G075AI | 70 | 2.9 | Yes | Yes | 21.1 | 21.4 | -0.3 | 181822AD197249678AE9BCD3BFCC6000 |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Fresno | CA | 93722-4313 |  | 2014-05-27 | 2014-05-27 09:58 | 2014-05-27 10:14 | YORK - D1NA036N05606C | 67 | 14.3 | Yes | Yes | 21.4 | 18.7 | 2.7 | 47162C6308C94C5E80A1A6A9C0E3EA9C |  | R22 | Non-TXV |  | 21.34% | 0.78657 | 41.02% | [5 empty] | Non-TXV | 21.34%
Stockton | CA | 95204-4813 |  | 2014-06-05 | 2014-06-05 10:46 | 2014-06-05 11:05 | LENNOX - HS19-411V-3P | 113 | 11 | Yes | Yes | 20.2 | 20.4 | -0.2 | 4B233F0F4B444830B4DE67BE90C02910 |  | R22 | TXV |  | 9.735% | 0.90265 | 18.71% | [5 empty] | TXV | 9.735%
Fresno | CA | 93727-5911 |  | 2014-06-05 | 2014-06-05 15:25 | 2014-06-05 15:51 | PAYNE - N/A | 120 | 5.4 | Yes | Yes | 20.3 | 21.3 | -1 | 86A77D2150B94AA7AEC615B0B407E23B |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Marysville | CA | 95901-6300 |  | 2014-06-12 | 2014-06-12 09:13 | 2014-06-12 09:30 | LENNOX - 1OACC-030-230-03 | 58 | 2.9 | Yes | Yes | 19 | 22 | -3 | 450AAC38AF8A451AA966F6E98BBE53F2 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95210-1907 |  | 2014-06-06 | 2014-06-06 08:42 | 2014-06-06 09:00 | GOODMAN - CK60-1 | 115 | -8.1 | Yes | Yes | 23.3 | 18.7 | 4.6 | 030F99CE2D49476FB3026EC2AAA42464 |  | R22 | Non-TXV |  | -7.043% | 1.0704 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.043%
Stockton | CA | 95210-4441 |  | 2014-05-28 | 2014-05-28 10:07 | 2014-05-28 10:24 | PAYNE - 591ANX030000AAAA | 72 | 10.5 | Yes | Yes | 26.8 | 20.9 | 6 | 1CB7682180714DE0A71BA858FB005B49 |  | R22 | Non-TXV |  | 14.58% | 0.85417 | 28.03% | [5 empty] | Non-TXV | 14.58%
Fresno | CA | 93726-0415 |  | 2014-05-23 | 2014-05-23 10:09 | 2014-05-23 10:29 | YORK - DCYP-F024N045B | 100 | 3.4 | Yes | Yes | 17.9 | 20.6 | -2.7 | DA4F54FF5B4248639726032F128D5377 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Chico | CA | 95973-7811 |  | 2014-07-26 | 2014-07-26 10:39 | 2014-07-26 11:09 | BRYANT - 663CJ024-E | 65 | 5.6 | Yes | Yes | 20.5 | 19 | 1.5 | BC945182C1C54CF6A94B467E3D36468F |  | R22 | Non-TXV |  | 8.615% | 0.91385 | 16.56% | [5 empty] | Non-TXV | 8.615%
Fresno | CA | 93727-4324 |  | 2014-08-25 | 2014-08-25 13:54 | 2014-08-25 13:54 | PAYNE - 2460YAC108TC | 56 | 0 | Yes | Yes | 20.1 | 22.2 | -2.1 | 8CDA07E0F7664A39AAD8780130CB0F01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-2519 |  | 2014-07-23 | 2014-07-23 16:59 | 2014-07-23 17:22 | BRYANT - 547BNW030040NA | 128 | 4.7 | Yes | Yes | 23.1 | 20.1 | 3 | 91E88EEC4D384321BD302B5D3946AAFE |  | R410A | TXV |  | 3.672% | 0.96328 | 7.057% | [5 empty] | TXV | 3.672%
Stevinson | CA | 95374-9733 |  | 2014-08-27 | 2014-08-27 11:34 | 2014-08-27 11:54 | PAYNE - PY3PNA030060NA | 130 | 5.8 | Yes | Yes | 19.2 | 18.9 | 0.4 | B632B8B0AC7E4279A106AD44D5DCF06C |  | R22 | Non-TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | Non-TXV | 4.462%
Fresno | CA | 93705-2147 |  | 2014-05-30 | 2014-05-30 16:08 | 2014-05-30 16:08 | YORK - H1DB030S060B | 70 | 0 | Yes | Yes | 26.4 | 22.3 | 4.1 | F7EB3AB072BC4C0ABEF63186DD0592C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-2536 |  | 2014-06-19 | 2014-06-19 11:02 | 2014-06-19 11:28 | ICP - PGC042K080D | 87 | 5.3 | Yes | Yes | 23.1 | 21.3 | 1.9 | AF6E074E6A784BDEA3420A09E41FE631 |  | R22 | Non-TXV |  | 6.092% | 0.93908 | 11.71% | [5 empty] | Non-TXV | 6.092%
Fresno | CA | 93726-5411 |  | 2014-06-10 | 2014-06-10 16:02 | 2014-06-10 16:27 | NORDYNE - GR6GD-X42K072C | 115 | 5.8 | Yes | Yes | 22.2 | 19.9 | 2.3 | 382B90634C08423D878CDE001C8794B2 | Add refrigerant: 8.4 oz | R410A | TXV |  | 5.043% | 0.94957 | 9.692% | [5 empty] | TXV | 5.043%
Fresno | CA | 93705-3328 |  | 2014-08-09 | 2014-08-09 12:53 | 2014-08-09 13:14 | GOODMAN - GPG1342070M41AD | 105 | 4.4 | Yes | Yes | 18.8 | 20.9 | -2.1 | 8A1F66E309464EEBA63A5D20501D8ADE |  | R410A | TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | TXV | 4.19%
Clovis | CA | 93612-2356 |  | 2014-07-17 | 2014-07-17 10:23 | 2014-07-17 10:24 | CARRIER - 480L045 | 81 | 15.2 | Yes | Yes | 19.2 | 18.5 | 0.7 | 2442415DB0654BB58BE426C8E5E1AE3D |  | R22 | Non-TXV |  | 18.77% | 0.81235 | 36.06% | [5 empty] | Non-TXV | 18.77%
Merced | CA | 95340-3120 |  | 2014-07-16 | 2014-07-16 10:30 | 2014-07-16 10:48 | OTHER - HABD-FO36G | 145 | 4.3 | Yes | Yes | 17.8 | 18.4 | -0.6 | B1ACC38B68EA432C8346A3A1CE932F58 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.699% | [5 empty] | Non-TXV | 2.966%
Merced | CA | 95340-1529 |  | 2014-05-29 | 2014-05-29 13:59 | 2014-05-29 14:00 | CARRIER - 48SX-036080321AA | 84 | 2.7 | Yes | Yes | 27.1 | 22.7 | 4.4 | AE60FDEA923C4DDF95BC1F5AB33B1FA3 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Fresno | CA | 93726-4106 |  | 2014-06-02 | 2014-06-02 13:52 | 2014-06-02 14:16 | AMERICAN STANDARD - YCC036F1M0BC | 83 | 5.4 | Yes | Yes | 22.1 | 19.6 | 2.5 | 05195E21901B42D099CA8EA15F3B32CD |  | R22 | Non-TXV |  | 6.506% | 0.93494 | 12.5% | [5 empty] | Non-TXV | 6.506%
Fresno | CA | 93727-7216 |  | 2014-06-26 | 2014-06-26 12:39 | 2014-06-26 12:40 | YORK - H2RD036S06B | 96 | 3.4 | Yes | Yes | 25.7 | 20.6 | 5.1 | F1C1217995314744AD23756995AAE766 |  | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Merced | CA | 95348-2138 |  | 2014-05-19 | 2014-05-19 15:28 | 2014-05-19 15:45 | UNK - UNK | 85 | 11.6 | Yes | Yes | 28.6 | 22.8 | 5.8 | DE8EBD85AA344A859B32BD348DB19AD5 |  |  |  |  | 13.65% | 0.86353 | 26.23% | [5 empty] | 0 | 13.65%
Oroville | CA | 95966-6622 |  | 2014-05-27 | 2014-05-27 14:14 | 2014-05-27 14:14 | TRANE - 2TTB3030A1000AA | 88 | 0 | Yes | Yes | 13 | 21.8 | -8.8 | BF0BDD9CA6BB42668406B9224C5166F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4841 |  | 2014-08-14 | 2014-08-14 15:34 | 2014-08-14 15:36 | ICP - WPG3244040LKC1 | 72 | 3 | Yes | Yes | 21.3 | 17.6 | 3.7 | DF390EB0777B47B2B54F09DA19BFFAE4 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Fresno | CA | 93727-5208 |  | 2014-07-07 | 2014-07-07 12:05 | 2014-07-07 12:36 | CARRIER - N/A | 120 | 4.8 | Yes | Yes | 18.2 | 20.4 | -2.2 | 0BB93BEC87274AFF806E8862788F446B |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93727-5208 |  | 2014-07-07 | 2014-07-07 12:39 | 2014-07-07 14:11 | UNITARY PRODUCTS GROUP - TCGF60S4151A | 89 | 3.9 | Yes | Yes | 23.1 | 19.9 | 3.2 | 926AEBDBD70849A594DBA7402745214B |  | R410A | TXV |  | 4.382% | 0.95618 | 8.421% | [5 empty] | TXV | 4.382%
Stockton | CA | 95207-6065 |  | 2014-06-06 | 2014-06-06 13:35 | 2014-06-06 13:54 | RHEEM - UNK | 54 | 3.2 | Yes | Yes | 21.1 | 19.1 | 2 | FC78202CB98F444DA896B684A94176DB |  | R22 | Non-TXV |  | 5.926% | 0.94074 | 11.39% | [5 empty] | Non-TXV | 5.926%
Stockton | CA | 95209-1958 |  | 2014-05-14 | 2014-05-14 08:38 | 2014-05-14 08:58 | YORK - H5DB048S064 | 96 | 7.2 | Yes | Yes | 26.1 | 20.2 | 5.9 | 25013D3B94D24434BAFA4BA7885B48FC |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Chico | CA | 95926-2796 |  | 2014-06-19 | 2014-06-19 14:54 | 2014-06-19 15:13 | GOODMAN - 0SC130241PA | 80 | 15.2 | Yes | Yes | 22.5 | 21 | 1.6 | E377115CA1BC485587BB079915A22ECF |  | R22 | Non-TXV |  | 19% | 0.81 | 36.51% | [5 empty] | Non-TXV | 19%
Fresno | CA | 93702-4259 |  | 2014-05-22 | 2014-05-22 10:18 | 2014-05-22 10:38 | NORDYNE - R8GD-030K045X | 64 | 3.2 | Yes | Yes | 23.7 | 21.4 | 2.4 | 0B73F50A4CA44169A920C1D2E2712957 |  | R410A | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Fresno | CA | 93727-4712 |  | 2014-06-26 | 2014-06-26 11:02 | 2014-06-26 11:04 | OTHER - AC018M1021CG | 49 | 1.8 | Yes | Yes | 19.6 | 19.5 | 0.1 | D2328E5F63F446468E7734860FED83DA |  | R22 | Non-TXV |  | 3.673% | 0.96327 | 7.06% | [5 empty] | Non-TXV | 3.673%
Atwater | CA | 95301-9599 |  | 2014-05-18 | 2014-05-18 20:21 | 2014-05-18 20:23 | OTHER - 7777UNK | 84 | 4.4 | Yes | Yes | 21 | 20.2 | 0.9 | 705003EFB20E44C6B11FC8928CD964FC |  | R22 | Non-TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | Non-TXV | 5.238%
Fresno | CA | 93703-2011 |  | 2014-05-15 | 2014-05-15 15:10 | 2014-05-15 15:24 | AMERICAN STANDARD - YCY036F1M0AC | 136 | 4.1 | Yes | Yes | 23.6 | 19.6 | 4 | C140886763464B598562A8F25AEBE24C |  | R22 | Non-TXV |  | 3.015% | 0.96985 | 5.794% | [5 empty] | Non-TXV | 3.015%
Manteca | CA | 95336-2553 |  | 2014-05-15 | 2014-05-15 11:15 | 2014-05-15 11:38 | OTHER - TZAA-336-2A | 85 | 6.5 | Yes | Yes | 21.3 | 22.7 | -1.4 | 608A3AEE6DE94930B26A2C0FF02C00D7 |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Stockton | CA | 95210-1778 |  | 2014-05-16 | 2014-05-16 12:11 | 2014-05-16 12:28 | CARRIER - 38EA024310 | 55 | 9.7 | Yes | Yes | 23.3 | 21.4 | 1.9 | 36A82DF0378D4069A7EE8A35DB9C3457 |  | R22 | Non-TXV |  | 17.64% | 0.82364 | 33.89% | [5 empty] | Non-TXV | 17.64%
Fresno | CA | 93702-2257 |  | 2014-07-30 | 2014-07-30 15:16 | 2014-07-30 15:18 | AMANA - PGD36C0702E | 110 | 6.3 | Yes | Yes | 24.8 | 19.3 | 5.5 | 3EF4664E7AAE4C32A828736AE4B13794 |  | R22 | Non-TXV |  | 5.727% | 0.94273 | 11.01% | [5 empty] | Non-TXV | 5.727%
Fresno | CA | 93722-8609 |  | 2014-05-23 | 2014-05-23 11:24 | 2014-05-23 11:44 | LENNOX - 12GCS036X753PA | 110 | 17.7 | Yes | Yes | 19.7 | 17.6 | 2.1 | D4DAB937FB0440A5993E21E0A49DF276 |  | R22 | Non-TXV |  | 16.09% | 0.83909 | 30.92% | [5 empty] | Non-TXV | 16.09%
Sanger | CA | 93657-2319 |  | 2014-06-17 | 2014-06-17 14:47 | 2014-06-17 15:07 | GOODMAN - GPG12360701A | 85 | 3 | Yes | Yes | 26.8 | 21.3 | 5.5 | F44DFC85FB504C51921ECB8D758449C3 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93726-2451 |  | 2014-05-26 | 2014-05-26 11:03 | 2014-05-26 11:03 | NORDYNE - GRD6GD-X48K096X | 224 | 0 | Yes | Yes | 17.6 | 20.4 | -2.8 | E85FC5F7D2094B3689E960E68EB79F22 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-6728 |  | 2014-05-28 | 2014-05-28 12:36 | 2014-05-28 13:00 | BRYANT - 562CJ036-C | 96 | 2.8 | Yes | Yes | 22.9 | 21.5 | 1.4 | A4450D331D8945328C2A4BF722D2BCC5 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Fresno | CA | 93702-3218 |  | 2014-05-21 | 2014-05-21 11:30 | 2014-05-21 11:57 | YORK - D2NP048N06506A | 132 | 4.4 | Yes | Yes | 25.6 | 19.9 | 5.7 | 5D5517BDFFDC48C3B36977705620B2E8 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93704-4334 |  | 2014-06-25 | 2014-06-25 13:01 | 2014-06-25 13:03 | GOODMAN - CLJ361A | 109 | 16.9 | Yes | Yes | 23.7 | 22 | 1.7 | 1B146F81FAC241C59329C6649C4B9B71 |  | R22 | Non-TXV |  | 15.5% | 0.84495 | 29.8% | [5 empty] | Non-TXV | 15.5%
Yuba City | CA | 95991-5451 |  | 2014-05-16 | 2014-05-16 15:21 | 2014-05-16 15:21 | BRYANT - 597CN030000AGAA | 97 | 0 | Yes | Yes | 23 | 22.5 | 0.5 | DD2F0E4E0F6149BFBBE7248EFA9D1EF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-8769 |  | 2014-06-02 | 2014-06-02 13:36 | 2014-06-02 14:03 | RUUD - UAMA-042JAS | 85 | 8.2 | Yes | Yes | 25.4 | 21.8 | 3.7 | 9F96CDAA40804233BB3947CAB16139B8 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Fresno | CA | 93726-0930 |  | 2014-06-24 | 2014-06-24 09:06 | 2014-06-24 09:07 | DAY & NIGHT - 2460YAC108T | 54 | 7.4 | Yes | Yes | 24.9 | 20.4 | 4.5 | 12917DF9771942D9908B70BFF480AD79 |  | R22 | Non-TXV |  | 13.7% | 0.86296 | 26.34% | [5 empty] | Non-TXV | 13.7%
Fresno | CA | 93726-3526 |  | 2014-06-20 | 2014-06-20 10:44 | 2014-06-20 10:45 | PAYNE - 2460YAC108 | 53 | 7.5 | Yes | Yes | 17.5 | 17 | 0.5 | EF151671F7EB4A949F83E6F215A75F76 |  | R22 | Non-TXV |  | 14.15% | 0.85849 | 27.2% | [5 empty] | Non-TXV | 14.15%
Coalinga | CA | 93210-2545 |  | 2014-08-11 | 2014-08-11 08:36 | 2014-08-11 08:54 | CARRIER - 48KL-024-311BF | 50 | 1.5 | Yes | Yes | 29.5 | 23.7 | 5.8 | 03220874CB74403683A46C2AE14ACDC7 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95205-7723 |  | 2014-06-04 | 2014-06-04 10:11 | 2014-06-04 10:32 | RHEEM - UKKA-A060JK10E | 131 | -12.3 | Yes | Yes | 27.9 | 21.9 | 6 | 90F9A9C641D041768B22FBC079757151 |  | R22 | Non-TXV |  | -9.389% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.389%
Stockton | CA | 95207-6040 |  | 2014-06-13 | 2014-06-13 09:46 | 2014-06-13 10:03 | RHEEM - UNK | 64 | -3.8 | Yes | Yes | 16.9 | 18.9 | -2 | 6A4B036C27A0413FACBBCB496B57B1E0 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Magalia | CA | 95954-9626 |  | 2014-06-04 | 2014-06-04 11:00 | 2014-06-04 11:18 | CARRIER - NA | 85 | 4.1 | Yes | Yes | 21.5 | 20 | 1.5 | FD4F8D2BDF164F34986583C22F720D54 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fresno | CA | 93722-4348 |  | 2014-05-28 | 2014-05-28 09:36 | 2014-05-28 09:55 | YORK - DAYQF036N070C | 58 | 6.4 | Yes | Yes | 20.3 | 18.1 | 2.2 | 395D0C1D94034204B13DB30AFCC4A908 |  | R410A | Non-TXV |  | 11.03% | 0.88966 | 21.21% | [5 empty] | Non-TXV | 11.03%
Fresno | CA | 93706-2930 |  | 2014-05-20 | 2014-05-20 10:48 | 2014-05-20 11:05 | CARRIER - 48DC003 | 69 | 8.5 | Yes | Yes | 23.4 | 17.7 | 5.7 | 043DBA551F5B4D0CB7A943CA77C1195A |  | R22 | Non-TXV |  | 12.32% | 0.87681 | 23.67% | [5 empty] | Non-TXV | 12.32%
Chico | CA | 95926-2969 |  | 2014-05-15 | 2014-05-15 12:10 | 2014-05-15 12:51 | LENNOX - DAYA-F030N45C | 75 | 4.5 | Yes | Yes | 18.5 | 17.7 | 0.8 | 0C8F7EBCA7504084B36C5EF77BF642C0 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Stockton | CA | 95212-3206 |  | 2014-05-15 | 2014-05-15 09:32 | 2014-05-15 09:53 | GOODMAN - CLJ48-1 | 117 | 3.9 | Yes | Yes | 26.1 | 20.4 | 5.7 | 66643E4A1C3748A092D29ACF0E75D22C |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Corning | CA | 96021-9812 |  | 2014-07-30 | 2014-07-30 16:48 | 2014-07-30 17:06 | GOODMAN - GSC140241AC | 129 | 5.2 | Yes | Yes | 15 | 17.9 | -2.9 | CEA67CB3618C48049E18D278FD508708 |  | R22 | Non-TXV |  | 4.031% | 0.95969 | 7.747% | [5 empty] | Non-TXV | 4.031%
Fresno | CA | 93726-5241 |  | 2014-05-28 | 2014-05-28 16:47 | 2014-05-28 17:05 | BDP - 585036080 | 60 | 4.3 | Yes | Yes | 30.1 | 24.2 | 5.9 | 8BEE69D579124EBF9D30B7E891ECD396 |  | R22 | Non-TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | Non-TXV | 7.167%
Paradise | CA | 95969-4631 |  | 2014-06-05 | 2014-06-05 09:41 | 2014-06-05 10:00 | TEMPSTAR - PGAAY2C1K4 | 95 | 2.8 | Yes | Yes | 26.1 | 21.5 | 4.6 | E7767C541A1B4B2284B58AD82A9D8E48 |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Fresno | CA | 93726-2519 |  | 2014-05-26 | 2014-05-26 14:13 | 2014-05-26 14:42 | BDP - 563AN042-A | 131 | 4.5 | Yes | Yes | 21.2 | 21.5 | -0.3 | D62DAF755BB94EF182691566418F2FFF |  | R22 | Non-TXV |  | 3.435% | 0.96565 | 6.602% | [5 empty] | Non-TXV | 3.435%
Oroville | CA | 95965-4757 |  | 2014-06-06 | 2014-06-06 09:44 | 2014-06-06 10:19 | CARRIER - NA | 60 | 4.4 | Yes | Yes | 16 | 18.8 | -2.8 | D14E76D0666046D3970606A6ECC69F89 |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Fresno | CA | 93722-4371 |  | 2014-05-21 | 2014-05-21 11:31 | 2014-05-21 11:32 | GOODMAN - GPG13420701A | 107 | 3.1 | Yes | Yes | 24.4 | 18.7 | 5.7 | 9A849854D4CD446EB3EF4A0B6B1B6E6C |  | R22 | Non-TXV |  | 2.897% | 0.97103 | 5.568% | [5 empty] | Non-TXV | 2.897%
Fresno | CA | 93711-0864 |  | 2014-05-26 | 2014-05-26 08:52 | 2014-05-26 09:18 | LENNOX - HS22461V2P | 133 | 18.2 | Yes | Yes | 19.3 | 19.2 | 0.1 | F24D07BF0329455E8A26817AE8EC8EDB |  | R22 | Non-TXV |  | 13.68% | 0.86316 | 26.3% | [5 empty] | Non-TXV | 13.68%
Stockton | CA | 95207-8127 |  | 2014-05-31 | 2014-05-31 09:19 | 2014-05-31 09:45 | DAY & NIGHT - 585EJW024050ABAF | 54 | 1.6 | Yes | Yes | 25 | 19.9 | 5.1 | 10ED35842A3543BAAA222A04D7F9C62D |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93727-4705 |  | 2014-07-02 | 2014-07-02 13:47 | 2014-07-02 14:41 | OTHER - 1261-500 | 39 | 9.3 | Yes | Yes | 20.7 | 22.1 | -1.4 | 6029FE2192D3477F8B4D159271BDE023 |  | R22 | Non-TXV |  | 23.85% | 0.76154 | 45.83% | [5 empty] | Non-TXV | 23.85%
Clovis | CA | 93611-6555 |  | 2014-05-30 | 2014-05-30 14:21 | 2014-05-30 14:23 | CARRIER - 38CK036350 | 70 | 3 | Yes | Yes | 22.9 | 25.2 | -2.3 | 46C70C957DF3422B86B7A704EFA92F70 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Fresno | CA | 93701-2321 |  | 2014-06-20 | 2014-06-20 15:15 | 2014-06-20 15:35 | RUUD - UAKA036JAS | 75 | 11.2 | Yes | Yes | 25.6 | 21.7 | 3.9 | C5601C74044749838FBD75ADF75C6ADE |  | R22 | Non-TXV |  | 14.93% | 0.85067 | 28.7% | [5 empty] | Non-TXV | 14.93%
Fresno | CA | 93725-1640 |  | 2014-06-16 | 2014-06-16 10:53 | 2014-06-16 10:54 | BDP - 585B042100YAVR | 89 | 9.9 | Yes | Yes | 24.8 | 19.7 | 5.1 | A612DDD951FD451599E960A353FBA3E0 |  | R22 | Non-TXV |  | 11.12% | 0.88876 | 21.38% | [5 empty] | Non-TXV | 11.12%
Fresno | CA | 93727-4324 |  | 2014-08-14 | 2014-08-14 15:55 | 2014-08-14 16:22 | YORK - DBYP-F030N070A | 73 | 3.8 | Yes | Yes | 18.8 | 21.2 | -2.4 | 615AC69D17BF487CA902A7A9EAEC9EAD |  | R22 | Non-TXV |  | 5.205% | 0.94795 | 10% | [5 empty] | Non-TXV | 5.205%
Chico | CA | 95973-0706 |  | 2014-06-10 | 2014-06-10 15:47 | 2014-06-10 16:23 | TRANE - YCXO36F1MOBA | 62 | 3.9 | Yes | Yes | 18.3 | 20.8 | -2.5 | 1880FA8BC4B447CBB7C3AF533D364C63 |  | R22 | Non-TXV |  | 6.29% | 0.9371 | 12.09% | [5 empty] | Non-TXV | 6.29%
Biggs | CA | 95917-9770 |  | 2014-07-18 | 2014-07-18 08:38 | 2014-07-18 08:53 | OTHER - SCU1236A-1 | 99 | 4.1 | Yes | Yes | 24 | 18.8 | 5.2 | 128A494DAA154AB98F8503D83E6F3D16 |  | R22 | TXV |  | 4.141% | 0.95859 | 7.959% | [5 empty] | TXV | 4.141%
Chico | CA | 95926-1742 |  | 2014-05-29 | 2014-05-29 11:31 | 2014-05-29 12:33 | LENNOX - 11522-411U-3P | 135 | 4.3 | Yes | Yes | 21.9 | 20.7 | 1.2 | DC10FD70D03848DA96F964AC8C700123 |  | R22 | Non-TXV |  | 3.185% | 0.96815 | 6.121% | [5 empty] | Non-TXV | 3.185%
Chico | CA | 95926-1742 |  | 2014-05-29 | 2014-05-29 11:34 | 2014-05-29 12:32 | LENNOX - HS18-511-5P | 130 | 5.9 | Yes | Yes | 19.5 | 19.9 | -0.4 | E4FCA985CF2747B7A1626A09FEDBA2BA |  | R22 | Non-TXV |  | 4.538% | 0.95462 | 8.722% | [5 empty] | Non-TXV | 4.538%
Fresno | CA | 93705-0750 |  | 2014-05-22 | 2014-05-22 11:21 | 2014-05-22 11:39 | RHEEM - RRNAB030JK06X | 72 | 9.3 | Yes | Yes | 24.9 | 21 | 3.9 | 237A1D5F2C194E3EB068668A446A8A77 |  | R22 | Non-TXV |  | 12.92% | 0.87083 | 24.82% | [5 empty] | Non-TXV | 12.92%
Fresno | CA | 93702-1242 |  | 2014-05-20 | 2014-05-20 09:14 | 2014-05-20 09:41 | YORK - DAYA-F024N045C | 54 | 5.6 | Yes | Yes | 22.7 | 20.9 | 1.8 | F99B7FBB07AB407A8574B48C21D2EA0A |  | R22 | Non-TXV |  | 10.37% | 0.8963 | 19.93% | [5 empty] | Non-TXV | 10.37%
Stockton | CA | 95207-6064 |  | 2014-06-17 | 2014-06-17 13:38 | 2014-06-17 14:27 | BRYANT - 582ANW018040AAAD | 39 | 3.8 | Yes | Yes | 23.2 | 21.7 | 1.6 | E95D97E9E9014ACDA346A4707C1A0145 |  | R22 | Non-TXV |  | 9.744% | 0.90256 | 18.73% | [5 empty] | Non-TXV | 9.744%
Wheatland | CA | 95692-9756 |  | 2014-06-16 | 2014-06-16 08:37 | 2014-06-16 09:08 | LENNOX - 12GCS042X-100-1PA | 133 | 4.3 | Yes | Yes | 23.5 | 19.7 | 3.8 | 0371992739ED49CAA424970F6DC59B09 |  | R22 | Non-TXV |  | 3.233% | 0.96767 | 6.213% | [5 empty] | Non-TXV | 3.233%
Mariposa | CA | 95338-0000 |  | 2014-08-02 | 2014-08-02 13:12 | 2014-08-02 13:12 | CARRIER - 50YQ048300 | 115 | 0 | Yes | Yes | 16.3 | 16.9 | -0.6 | 14B0861AA2C041E49AC4A079D282550A | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2011 |  | 2014-05-23 | 2014-05-23 12:55 | 2014-05-23 13:12 | BRYANT - 582ANW024040AAAD | 53 | 7.1 | Yes | Yes | 19.8 | 16.8 | 3.1 | 20D58A0C49E74E6EA658287772E50CAB |  | R22 | Non-TXV |  | 13.4% | 0.86604 | 25.74% | [5 empty] | Non-TXV | 13.4%
Oroville | CA | 95966-9233 |  | 2014-06-06 | 2014-06-06 10:22 | 2014-06-06 10:52 | PAYNE - PY0PNB036060AAAA | 75 | 5.5 | Yes | Yes | 19.7 | 21 | -1.3 | 7C24D1B3CB2B41ABA9044A5FCEC9F5BD |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Merced | CA | 95340-3121 |  | 2014-05-30 | 2014-05-30 08:42 | 2014-05-30 08:45 | TRANE - TTX030C100A0 | 120 | 3.7 | Yes | Yes | 22.6 | 22.9 | -0.3 | 471833B0B0DC4CEC9780970CFBC927ED |  | R22 | Non-TXV |  | 3.083% | 0.96917 | 5.925% | [5 empty] | Non-TXV | 3.083%
Wheatland | CA | 95692-9739 |  | 2014-09-25 | 2014-09-25 16:11 | 2014-09-25 16:31 | YORK - HDCB024S06B | 65 | 2 | Yes | Yes | 21 | 19.5 | 1.5 | 5C8755AF00814D0385A68B087E523B41 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Chico | CA | 95973-9155 |  | 2014-05-27 | 2014-05-27 12:53 | 2014-05-27 13:12 | DAY & NIGHT - N2A342AKA200 | 104 | 4.6 | Yes | Yes | 16.5 | 19.3 | -2.8 | 6C1B60380BEF48B78107B17B21FFD23A |  | R22 | Non-TXV |  | 4.423% | 0.95577 | 8.5% | [5 empty] | Non-TXV | 4.423%
Fresno | CA | 93704-5638 |  | 2014-06-17 | 2014-06-17 12:25 | 2014-06-17 12:26 | OTHER - 7777UNK | 80 | 3.3 | Yes | Yes | 21.6 | 22.7 | -1.1 | 1612D1C45FDA4833B245FB309CDDC5EC |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Coalinga | CA | 93210-2066 |  | 2014-10-16 | 2014-10-16 14:05 | 2014-10-16 17:03 | CARRIER - 38TH018300 | 48 | 2.8 | Yes | Yes | 25.9 | 20.2 | 5.8 | 8792377DAB2A40F1BA9533FCEFB880F5 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Tracy | CA | 95376-4609 |  | 2014-05-22 | 2014-05-22 12:19 | 2014-05-22 12:48 | DAY & NIGHT - 565BJ036-A | 85 | 13.7 | Yes | Yes | 19.8 | 19.3 | 0.5 | 937C7C680CDF43AE80AC1AB6CFF3CD48 |  | R22 | Non-TXV |  | 16.12% | 0.83882 | 30.97% | [5 empty] | Non-TXV | 16.12%
Fresno | CA | 93706-4325 |  | 2014-05-22 | 2014-05-22 10:02 | 2014-05-22 10:19 | HEIL - PGAA36D1K3 | 81 | 8.1 | Yes | Yes | 21.6 | 18.6 | 3 | 97C3476307544D2E9B34460BF8512ACE |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Marysville | CA | 95901-9753 |  | 2014-05-21 | 2014-05-21 15:07 | 2014-05-21 15:29 | OTHER - UNK | 95 | 3.1 | Yes | Yes | 27 | 23.7 | 3.3 | E569A101E0F34E7D83493BA5653F6D2D |  | R22 | Non-TXV |  | 3.263% | 0.96737 | 6.271% | [5 empty] | Non-TXV | 3.263%
Madera | CA | 93638-2606 |  | 2014-06-03 | 2014-06-03 11:17 | 2014-06-03 11:39 | OTHER - D1NA024N03606C | 54 | 8.7 | Yes | Yes | 19.4 | 18.2 | 1.2 | 7669B575AFC048BE9C5686CA52BE134D |  | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Fresno | CA | 93704-2734 |  | 2014-08-12 | 2014-08-12 12:28 | 2014-08-12 12:29 | BDP - 585HJ024040 | 68 | 8.1 | Yes | Yes | 17.6 | 14.7 | 2.9 | D23A5638A619458B86474ACA06A25222 |  | R22 | Non-TXV |  | 11.91% | 0.88088 | 22.89% | [5 empty] | Non-TXV | 11.91%
Clovis | CA | 93612-1741 |  | 2014-06-02 | 2014-06-02 14:37 | 2014-06-02 15:01 | NORDYNE - GR4GC-024K045X | 60 | 5.4 | Yes | Yes | 23.6 | 23.6 | 0 | 84358ECDFA0A4D47AADDF058ADF0DDBB |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Chico | CA | 95973-7214 |  | 2014-06-30 | 2014-06-30 09:26 | 2014-06-30 09:46 | PAYNE - PH10JA030-A | 50 | 4.3 | Yes | Yes | 28.5 | 24.8 | 3.7 | 527D207730324D9F880DFAE728F6257C |  | R22 | Non-TXV |  | 8.6% | 0.914 | 16.53% | [5 empty] | Non-TXV | 8.6%
Tracy | CA | 95376-9780 |  | 2014-05-22 | 2014-05-22 13:10 | 2014-05-22 13:29 | OTHER - UNK | 85 | -6 | Yes | Yes | 21.5 | 20.4 | 1.1 | 0B76F31842CB49CC8D64B99BCDCAC14B |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Paradise | CA | 95969-5703 |  | 2014-05-22 | 2014-05-22 09:21 | 2014-05-22 21:45 | TRANE - 4TT20024100AA | 161 | 5.6 | Yes | Yes | 25.5 | 22 | 3.5 | 5AF61489ADE54F948F04274DA3A2EA5E |  | R410A | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Paradise | CA | 95969-5703 |  | 2014-05-22 | 2014-05-22 10:25 | 2014-05-22 19:41 | TRANE - 4YC26048A1096AB | 133 | 5.8 | Yes | Yes | 22.4 | 22 | 0.4 | 77DC34E962284528A30F590B714DCFA4 |  | R410A | Non-TXV |  | 4.361% | 0.95639 | 8.381% | [5 empty] | Non-TXV | 4.361%
Clovis | CA | 93612-2384 |  | 2014-06-05 | 2014-06-05 11:12 | 2014-06-05 11:31 | BRYANT - 582ANW030060AAAD | 55 | 11.4 | Yes | Yes | 22.8 | 23.1 | -0.3 | A6A960306F30440F996894DDAB5F6325 |  | R22 | Non-TXV |  | 20.73% | 0.79273 | 39.83% | [5 empty] | Non-TXV | 20.73%
Los Banos | CA | 93635-5400 |  | 2014-06-26 | 2014-06-26 13:36 | 2014-06-26 14:06 | RUUD - UAKA-030JAZ | 66 | 2.7 | Yes | Yes | 21.6 | 21.2 | 0.4 | 7A4516F5412540ACBA0D114F188C5615 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Merced | CA | 95348-3306 |  | 2014-05-19 | 2014-05-19 12:55 | 2014-05-19 13:21 | UNK - UNK | 85 | 11 | Yes | Yes | 21.8 | 16.5 | 5.3 | B47D5CF635194425950C1DE3B5D18F6C |  |  |  |  | 12.94% | 0.87059 | 24.87% | [5 empty] | 0 | 12.94%
Tracy | CA | 95376-4611 |  | 2014-09-06 | 2014-09-06 09:20 | 2014-09-06 09:44 | BRYANT - 113RNA030-C | 82 | 8.5 | Yes | Yes | 20.9 | 18.4 | 2.5 | C630A814FD014773B625B53DE96E59DB |  | R22 | TXV |  | 10.37% | 0.89634 | 19.92% | [5 empty] | TXV | 10.37%
Stockton | CA | 95204-4006 |  | 2014-06-02 | 2014-06-02 13:55 | 2014-06-02 14:22 | BDP - 588ANW030060ADAD | 53 | 4.6 | Yes | Yes | 27.9 | 23.1 | 4.8 | 299D6EEA27FC4FB88FD54C7380DEEF84 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.679% | 0.91321 | 16.68% | [5 empty] | Non-TXV | 8.679%
Stockton | CA | 95204-4041 |  | 2014-06-03 | 2014-06-03 12:23 | 2014-06-03 12:51 | YORK - TCGD42S21S1HA | 72 | 14.2 | Yes | Yes | 20 | 18.7 | 1.3 | 990A8462B1D34BC080F8E8265577BB10 |  | R22 | Non-TXV |  | 19.72% | 0.80278 | 37.9% | [5 empty] | Non-TXV | 19.72%
Stockton | CA | 95210-2004 |  | 2014-06-14 | 2014-06-14 10:31 | 2014-06-14 10:48 | DAY & NIGHT - 585HJ024040 | 68 | -4.8 | Yes | Yes | 26.1 | 20.4 | 5.7 | 055AF39D6D6248A9A40F2C1955F38137 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Red Bluff | CA | 96080-9270 |  | 2014-06-17 | 2014-06-17 14:51 | 2014-06-17 14:55 | TRANE - BTD74CK10080 | 75 | 7.3 | Yes | Yes | 27 | 21.3 | 5.8 | 110E03827BDD4B2EA278D4B55422DFE6 |  | R22 | Non-TXV |  | 9.733% | 0.90267 | 18.71% | [5 empty] | Non-TXV | 9.733%
Atwater | CA | 95301-4521 |  | 2014-05-18 | 2014-05-18 19:41 | 2014-05-18 19:43 | OTHER - 7777UNK | 74 | 4.4 | Yes | Yes | 18.3 | 20.4 | -2.1 | B806C80F7F554608BA18641C8B2494CF |  | R22 | Non-TXV |  | 5.946% | 0.94054 | 11.43% | [5 empty] | Non-TXV | 5.946%
Madera | CA | 93638-2209 |  | 2014-06-03 | 2014-06-03 12:26 | 2014-06-03 12:43 | YORK - D1NP036N05606A | 108 | 16.1 | Yes | Yes | 21.3 | 17.6 | 3.7 | 210B038B26EE40CA944BC6B4EF8685C9 |  | R22 | Non-TXV |  | 14.91% | 0.85093 | 28.65% | [5 empty] | Non-TXV | 14.91%
San Joaquin | CA | 93660-0000 |  | 2014-06-27 | 2014-06-27 12:20 | 2014-06-27 12:21 | TRANE - YCC036F1MOBF | 82 | 3 | Yes | Yes | 21.3 | 20.7 | 0.6 | C8D2BE9504E24BE685FDE94FF776F7AA |  | R22 | Non-TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | Non-TXV | 3.659%
Manteca | CA | 95336-6311 |  | 2014-06-17 | 2014-06-17 14:30 | 2014-06-17 14:49 | PAYNE - PY1PNB036060ABAA | 68 | 2.5 | Yes | Yes | 25.9 | 22.1 | 3.8 | 39EE42D33EB546C286B5B7428DCE70F7 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Madera | CA | 93638-2606 |  | 2014-06-03 | 2014-06-03 11:42 | 2014-06-03 11:58 | AIRE-FLO - PGD324060K001C1 | 72 | 7 | Yes | Yes | 22.7 | 18.8 | 3.9 | 0010CF1F5891449FBF393B5E70BB9D8D |  | R410A | Non-TXV |  | 9.722% | 0.90278 | 18.68% | [5 empty] | Non-TXV | 9.722%
Fresno | CA | 93703-5229 |  | 2014-05-30 | 2014-05-30 09:33 | 2014-05-30 09:55 | CARRIER - 48KL124300BE | 50 | 3.2 | Yes | Yes | 22.8 | 20.9 | 1.9 | D67CC618FCCB428C9039A145892CC942 |  | R22 | Non-TXV |  | 6.4% | 0.936 | 12.3% | [5 empty] | Non-TXV | 6.4%
Fresno | CA | 93720-1492 |  | 2014-06-05 | 2014-06-05 08:50 | 2014-06-05 09:12 | CARRIER - UNK | 74 | 14.9 | Yes | Yes | 20.6 | 15.8 | 4.8 | EAEA513E44DF4F69A27284B284EE339B |  | R22 | Non-TXV |  | 20.14% | 0.79865 | 38.7% | [5 empty] | Non-TXV | 20.14%
Stockton | CA | 95212-2737 |  | 2014-06-17 | 2014-06-17 12:35 | 2014-06-17 13:05 | CARRIER - 38CKC042350 | 82 | 20 | Yes | Yes | 20.5 | 21.4 | -0.9 | 6A272C41B73049E08E8F6B0047161E9F |  | R22 | Non-TXV |  | 24.39% | 0.7561 | 46.87% | [5 empty] | Non-TXV | 24.39%
Tracy | CA | 95376-1824 |  | 2014-05-21 | 2014-05-21 14:43 | 2014-05-21 15:05 | YORK - PGAA36C1K6 | 69 | 2.8 | Yes | Yes | 21.9 | 22.1 | -0.2 | 5B67601458DE450AAFA2DAFDE65DF2DF |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Fresno | CA | 93704-4623 |  | 2014-06-17 | 2014-06-17 11:45 | 2014-06-17 11:46 | GOODMAN - PGB030050-1 REV A | 56 | 3.1 | Yes | Yes | 25.1 | 20.4 | 4.7 | 8733FD9165604AACA639A4D7B013DCCF |  | R22 | Non-TXV |  | 5.536% | 0.94464 | 10.64% | [5 empty] | Non-TXV | 5.536%
Fresno | CA | 93703-1417 |  | 2014-05-16 | 2014-05-16 10:09 | 2014-05-16 10:37 | BRYANT - 583ANW042090 | 70 | 6.9 | Yes | Yes | 21.3 | 21.3 | 0 | 22820E0D6FF64FFBBD4D44F56CC86351 |  | R22 | Non-TXV |  | 9.857% | 0.90143 | 18.94% | [5 empty] | Non-TXV | 9.857%
Stockton | CA | 95205-3342 |  | 2014-06-03 | 2014-06-03 14:42 | 2014-06-03 15:00 | BRYANT - 582ANW024040AAAD | 53 | 1.9 | Yes | Yes | 20.7 | 19.8 | 0.9 | A2150D4878194A81A568FB28A3A8344F |  | R22 | Non-TXV |  | 3.585% | 0.96415 | 6.889% | [5 empty] | Non-TXV | 3.585%
Coalinga | CA | 93210-2062 |  | 2014-08-11 | 2014-08-11 11:46 | 2014-08-11 12:07 | CARRIER - 38TH018300 | 48 | 1.4 | Yes | Yes | 18.5 | 21 | -2.5 | 0C24515A798842B78F17DB593E291C90 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Fresno | CA | 93705-2039 |  | 2014-06-20 | 2014-06-20 11:52 | 2014-06-20 11:53 | BRYANT - 582ANW024040AAAD | 53 | 3 | Yes | Yes | 20.2 | 22.6 | -2.4 | 97260009B3E74E0EA4EF76FE5073C013 |  | R22 | Non-TXV |  | 5.66% | 0.9434 | 10.88% | [5 empty] | Non-TXV | 5.66%
Fresno | CA | 93728-1548 |  | 2014-06-03 | 2014-06-03 16:17 | 2014-06-03 17:36 | WESTINGHOUSE - 1D036M1A | 112 | 4.9 | Yes | Yes | 23.2 | 20.9 | 2.3 | A2D0D8289D49436D9E94C0325D1352B8 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Fresno | CA | 93703-1329 |  | 2014-06-14 | 2014-06-14 09:49 | 2014-06-14 10:13 | ICP - GPFM36K060E | 68 | 5.7 | Yes | Yes | 19.5 | 19.9 | -0.4 | F1643F74710B4E49BB1C5FB39C99D39A |  | R22 | Non-TXV |  | 8.382% | 0.91618 | 16.11% | [5 empty] | Non-TXV | 8.382%
Coalinga | CA | 93210-2062 |  | 2014-08-11 | 2014-08-11 12:08 | 2014-08-11 12:26 | CARRIER - 38TH018300 | 49 | 1.4 | Yes | Yes | 18.2 | 21 | -2.8 | 1306FF4BBDD8497B847BD05FB4E3EA03 |  | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Fresno | CA | 93705-4021 |  | 2014-05-22 | 2014-05-22 11:49 | 2014-05-22 12:11 | CARRIER - 38ED048300 | 132 | 16.4 | Yes | Yes | 21.3 | 18.1 | 3.2 | 4F2E99F972FE4009ADB20D11BDB38072 |  | R22 | Non-TXV |  | 12.42% | 0.87576 | 23.88% | [5 empty] | Non-TXV | 12.42%
Clovis | CA | 93612-4447 |  | 2014-06-03 | 2014-06-03 14:22 | 2014-06-03 14:24 | CARRIER - 7777UNK | 80 | 2.9 | Yes | Yes | 28.1 | 23.9 | 4.2 | 274D3325EE4A46FA8189378C2A2206BE |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Merced | CA | 95341-5659 |  | 2014-05-16 | 2014-05-16 14:55 | 2014-05-16 14:57 | GE - BWB924A10001 | 81 | 9.9 | Yes | Yes | 24.1 | 23.7 | 0.4 | D2BB69F1CF6F4C30A7B1AF35301058C9 |  | R22 | Non-TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | Non-TXV | 12.22%
Fresno | CA | 93705-2124 |  | 2014-06-25 | 2014-06-25 08:03 | 2014-06-25 08:05 | OTHER - H1DB030S06A | 70 | 2.9 | Yes | Yes | 19.8 | 19.4 | 0.4 | ACE22E3574744CFCB25A4F51BB1EDC04 |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Fresno | CA | 93726-7118 |  | 2014-07-09 | 2014-07-09 14:57 | 2014-07-09 14:58 | YORK - DBYZF036N070A | 71 | 9.6 | Yes | Yes | 23.2 | 20.9 | 2.3 | 5593590A4BDF49C6B5CF693CBB768959 |  | R410A | Non-TXV |  | 13.52% | 0.86479 | 25.98% | [5 empty] | Non-TXV | 13.52%
Fresno | CA | 93723-9216 |  | 2014-05-21 | 2014-05-21 14:14 | 2014-05-21 14:34 | BRYANT - 563CN036 | 101 | 9.6 | Yes | Yes | 23 | 19.4 | 3.6 | AECD13A9D35D4C91B2525E093CDA78B4 |  | R22 | TXV |  | 9.505% | 0.90495 | 18.27% | [5 empty] | TXV | 9.505%
Stockton | CA | 95207-5946 |  | 2014-06-07 | 2014-06-07 08:20 | 2014-06-07 08:37 | DAY & NIGHT - UNK | 64 | -3.8 | Yes | Yes | 18.7 | 18.8 | -0.1 | 44B1763947AF4D4E8631F4624E96E941 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Fresno | CA | 93727-3737 |  | 2014-06-09 | 2014-06-09 16:52 | 2014-06-09 17:21 | ICP - PGMD036G0602 | 81 | 6.6 | Yes | Yes | 20.9 | 20.9 | 0 | 8977314DA1D247CF83E99DB1F5BD16C7 |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Fresno | CA | 93722-6736 |  | 2014-06-12 | 2014-06-12 10:04 | 2014-06-12 10:22 | BDP - 585HJW036060 | 102 | 14.1 | Yes | Yes | 19.8 | 19.8 | 0 | 797A77B3D4404D50A8B2633A5989A130 |  | R22 | Non-TXV |  | 13.82% | 0.86176 | 26.57% | [5 empty] | Non-TXV | 13.82%
Fresno | CA | 93722-3008 |  | 2014-05-20 | 2014-05-20 11:50 | 2014-05-20 11:51 | LENNOX - CA5042VKA1 | 135 | 4.1 | Yes | Yes | 19.7 | 19.1 | 0.6 | 301F17B5DFDD4446B07D6BAA59FBDFBD |  | R22 | Non-TXV |  | 3.037% | 0.96963 | 5.837% | [5 empty] | Non-TXV | 3.037%
Fresno | CA | 93727-7983 |  | 2014-06-06 | 2014-06-06 15:59 | 2014-06-06 16:22 | CARRIER - N/A | 90 | 3.7 | Yes | Yes | 22.6 | 22.5 | 0.1 | 77CAA1540E7C47D3941C2820E28DDF92 |  | R22 | Non-TXV |  | 4.111% | 0.95889 | 7.901% | [5 empty] | Non-TXV | 4.111%
Fresno | CA | 93705-2308 |  | 2014-07-11 | 2014-07-11 13:53 | 2014-07-11 14:19 | CARRIER - 48VLNA4809030TP | 152 | -8.9 | Yes | Yes | 24.1 | 19.7 | 4.4 | 4ACAC4E557C64156B8C53791C87ED21D |  | R410A | Non-TXV |  | -5.855% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.855%
Oroville | CA | 95965-8062 |  | 2014-05-27 | 2014-05-27 10:34 | 2014-05-27 11:06 | BRYANT - 113RN036-B | 88 | 4.9 | Yes | Yes | 25 | 21.7 | 3.4 | E0302658454246B1B96011BE7CE2CFFB |  | R22 | Non-TXV |  | 5.568% | 0.94432 | 10.7% | [5 empty] | Non-TXV | 5.568%
Paradise | CA | 95969-2216 |  | 2014-06-05 | 2014-06-05 16:28 | 2014-06-05 16:53 | YORK - D1NA030N056060 | 75 | 2.6 | Yes | Yes | 20.8 | 23.7 | -2.9 | FDA58D14FC4941F3929C7BC6CBBFA104 |  | R22 | Non-TXV |  | 3.467% | 0.96533 | 6.662% | [5 empty] | Non-TXV | 3.467%
Stockton | CA | 95204-3716 |  | 2014-06-02 | 2014-06-02 17:01 | 2014-06-02 17:18 | PAYNE - PY3PNA036060NA | 167 | 12.6 | Yes | Yes | 24.8 | 22.5 | 2.3 | 83672656382B4F2C82989167CEF2AB60 |  | R22 | Non-TXV |  | 7.545% | 0.92455 | 14.5% | [5 empty] | Non-TXV | 7.545%
Fresno | CA | 93726-6511 |  | 2014-07-02 | 2014-07-02 17:12 | 2014-07-02 17:35 | AMERICAN STANDARD - YCY042G1M0AD | 148 | 4.6 | Yes | Yes | 22.5 | 22.5 | 0 | C6BFC23D048D41AEA666C2B2A9D010AE |  | R22 | Non-TXV |  | 3.108% | 0.96892 | 5.973% | [5 empty] | Non-TXV | 3.108%
Stockton | CA | 95207-6908 |  | 2014-05-27 | 2014-05-27 14:21 | 2014-05-27 14:56 | GE - BTN936A100B0 | 144 | 10.4 | Yes | Yes | 24.1 | 21.9 | 2.2 | F17EFB6EA4284715BE474395F40FEEFD |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Stockton | CA | 95210-2310 |  | 2014-05-23 | 2014-05-23 11:03 | 2014-05-23 11:22 | GMC - VSC130241AA | 83 | 7.4 | Yes | Yes | 20.3 | 19.3 | 1 | 031FE1A435BD475BB80D445C6361AC11 |  | R22 | Non-TXV |  | 8.916% | 0.91084 | 17.13% | [5 empty] | Non-TXV | 8.916%
Oroville | CA | 95965-3184 |  | 2014-06-04 | 2014-06-04 09:08 | 2014-06-04 09:32 | TRANE - 2TTB3036A1000AA | 101 | 5.8 | Yes | Yes | 16.5 | 19.4 | -2.9 | 8F0EE310FE0E4541AB9C68B01A3F8611 |  | R22 | Non-TXV |  | 5.743% | 0.94257 | 11.04% | [5 empty] | Non-TXV | 5.743%
Fresno | CA | 93726-0939 |  | 2014-06-20 | 2014-06-20 09:48 | 2014-06-20 09:49 | DAY & NIGHT - 24YAC | 54 | 6.4 | Yes | Yes | 26 | 20.9 | 5.1 | E88F3C33777540088344E4074AEC954F |  | R22 | Non-TXV |  | 11.85% | 0.88148 | 22.78% | [5 empty] | Non-TXV | 11.85%
Auburn | CA | 95602-9162 |  | 2014-06-18 | 2014-06-18 10:00 | 2014-06-18 10:20 | OTHER - DRCS0481BE | 119 | 3.8 | Yes | Yes | 18 | 20.6 | -2.6 | 7188C01AC738420EAD72119FA5C8A591 |  | R22 | Non-TXV |  | 3.193% | 0.96807 | 6.137% | [5 empty] | Non-TXV | 3.193%
Chico | CA | 95928-5934 |  | 2014-06-20 | 2014-06-20 13:38 | 2014-06-20 13:54 | BRYANT - 561CJ036-F | 70 | 2.1 | Yes | Yes | 19 | 22 | -3 | E5AEE877B9E740A58135513AE5C41387 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Paso Robles | CA | 93446-1160 |  | 2014-06-23 | 2014-06-23 13:02 | 2014-06-23 13:21 | AMANA - PGB48C09020 | 91 | -5.4 | Yes | Yes | 25.5 | 20.6 | 5 | 62659DC4DB6C450E8B88FAD0895FE060 |  | R22 | Non-TXV |  | -5.934% | 1.0593 | 1.662% |  |  |  |  | Non-TXV |  |  | -5.934%
Lathrop | CA | 95330-9621 |  | 2014-06-03 | 2014-06-03 10:09 | 2014-06-03 10:36 | YORK - ACQ036GA | 85 | -8 | Yes | Yes | 20.7 | 20.3 | 0.4 | 2C640FD7C0984617A519EDBB8E94A914 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93720-2005 |  | 2014-06-04 | 2014-06-04 08:30 | 2014-06-04 08:47 | OTHER - PGHA024G075IN | 56 | 8.8 | Yes | Yes | 22.9 | 20.4 | 2.5 | 08B8E1C9C3D54EC2BDF5829F1C5E323B |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Fresno | CA | 93720-2005 |  | 2014-06-04 | 2014-06-04 08:48 | 2014-06-04 09:04 | OTHER - PGHA024G075IN | 56 | 7.4 | Yes | Yes | 21 | 19.3 | 1.7 | FA7796E872AD4D53920A1A9D8CA24654 |  | R22 | Non-TXV |  | 13.21% | 0.86786 | 25.39% | [5 empty] | Non-TXV | 13.21%
Stockton | CA | 95206-6357 |  | 2014-06-06 | 2014-06-06 14:34 | 2014-06-06 15:03 | GOODMAN - CLJ48-1 | 85 | 2.8 | Yes | Yes | 20.5 | 20.4 | 0.1 | 74643D87FC20466BB1D3C3812B7A2ABC |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Stockton | CA | 95206-1521 |  | 2014-06-06 | 2014-06-06 08:47 | 2014-06-06 08:47 | COMFORT AIRE - N2A324AKC200 | 55 | 0 | Yes | Yes | 24.5 | 20.5 | 4 | D04A2D9988CE402DA1A53EC2D4380C7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6612 |  | 2014-06-05 | 2014-06-05 12:40 | 2014-06-05 13:07 | RHEEM - RRAD-08E48JR | 104 | 3.1 | Yes | Yes | 22 | 21 | 1 | 54239D9FE7754FA49D163F0E69AE586B |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Stockton | CA | 95210-1480 |  | 2014-05-22 | 2014-05-22 09:28 | 2014-05-22 09:51 | ICP - PGAA30C1K3 | 75 | 3.4 | Yes | Yes | 23.3 | 19.1 | 4.2 | 0F41CBE71BCC45CB804EBA51B287EB5E |  | R22 | Non-TXV |  | 4.533% | 0.95467 | 8.712% | [5 empty] | Non-TXV | 4.533%
Merced | CA | 95340-3038 |  | 2014-05-16 | 2014-05-16 12:09 | 2014-05-16 12:11 | AMERICAN STANDARD - YCY030F1MOAB | 148 | 20.4 | Yes | Yes | 22.3 | 19.3 | 3 | 2BA9C1F9A4B04A5AA92D1070C59CD9E6 |  | R22 | Non-TXV |  | 13.78% | 0.86216 | 26.49% | [5 empty] | Non-TXV | 13.78%
Stockton | CA | 95207-6064 |  | 2014-06-04 | 2014-06-04 09:30 | 2014-06-04 09:58 | RHEEM - UNK | 55 | -3.2 | Yes | Yes | 22 | 18.7 | 3.3 | FDB4225F4E844D338FF95D871F1059E9 |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Oakhurst | CA | 93644-8748 |  | 2014-07-31 | 2014-07-31 10:36 | 2014-07-31 10:37 | OTHER - AT38B10 | 45 | 8.9 | Yes | Yes | 18.5 | 16.8 | 1.7 | C8750AAD79994A39A28607953EE42813 |  | R22 | Non-TXV |  | 19.78% | 0.80222 | 38.01% | [5 empty] | Non-TXV | 19.78%
Biggs | CA | 95917-9750 |  | 2014-07-18 | 2014-07-18 10:42 | 2014-07-18 11:02 | LENNOX - XC13-048-230-01 | 146 | 4.4 | Yes | Yes | 17 | 18.3 | -1.3 | 0502849D63B34E8CBD7F134E4C1EB601 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Manteca | CA | 95336-3156 |  | 2014-05-14 | 2014-05-14 08:17 | 2014-05-14 08:36 | CARRIER - PGF336060K01 | 146 | 5.9 | Yes | Yes | 22.3 | 19.9 | 2.4 | E415401441C241D2B90D023FCF4B2C0A |  | R22 | Non-TXV |  | 4.041% | 0.95959 | 7.766% | [5 empty] | Non-TXV | 4.041%
Stockton | CA | 95207-6004 |  | 2014-06-17 | 2014-06-17 09:11 | 2014-06-17 09:28 | BRYANT - 574ANW024040NB | 89 | 4.3 | Yes | Yes | 23.8 | 20.1 | 3.7 | AD07496766EE4218817B1EC5F2162A0B |  | R22 | Non-TXV |  | 4.831% | 0.95169 | 9.285% | [5 empty] | Non-TXV | 4.831%
Yuba City | CA | 95991-7559 |  | 2014-05-15 | 2014-05-15 14:16 | 2014-05-15 14:47 | GOODMAN - CM36-1EB | 86 | -5.1 | Yes | Yes | 19 | 19.9 | -0.9 | 52D32A8A44544951A029C553188DDD24 |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Stockton | CA | 95206-6109 |  | 2014-06-07 | 2014-06-07 08:22 | 2014-06-07 08:42 | BRYANT - 562CJ036-C | 85 | 9.1 | Yes | Yes | 19 | 20.4 | -1.4 | 9668919E84714BE9893DAE3EB2950167 |  | R22 | TXV |  | 10.71% | 0.89294 | 20.57% | [5 empty] | TXV | 10.71%
Fresno | CA | 93725-1225 |  | 2014-07-16 | 2014-07-16 08:56 | 2014-07-16 08:58 | GOODMAN - GPG13240451CB | 74 | 2.4 | Yes | Yes | 20.7 | 16.6 | 4.1 | DF40F964D979465EA411542DB66B026A |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Oroville | CA | 95966-6579 |  | 2014-06-04 | 2014-06-04 14:09 | 2014-06-04 14:27 | OTHER - 38CKC030340 | 69 | 2.1 | Yes | Yes | 19 | 21 | -2 | 75EBD8C82FDC47D68FE3A5071BF79370 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Stockton | CA | 95206-5924 |  | 2014-06-07 | 2014-06-07 12:37 | 2014-06-07 13:15 | CARRIER - 38CKC04830 | 159 | 7.5 | Yes | Yes | 22.8 | 19.5 | 3.3 | 5141A8E1D4C74192941006C4EAAAA57E |  | R22 | TXV |  | 4.717% | 0.95283 | 9.065% | [5 empty] | TXV | 4.717%
Sanger | CA | 93657-2569 |  | 2014-06-17 | 2014-06-17 11:38 | 2014-06-17 12:07 | PAYNE - N/A | 90 | 6.6 | Yes | Yes | 21.4 | 21.8 | -0.4 | 347F5012C08A40419F90D782264FC242 |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Los Banos | CA | 93635-3839 |  | 2014-06-27 | 2014-06-27 15:07 | 2014-06-27 15:29 | YORK - H1RA048S06G | 117 | -6.9 | Yes | Yes | 21.9 | 20.4 | 1.5 | 098B446A74E642D3A43ECF3F0F43DD53 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Grass Valley | CA | 95949-8321 |  | 2014-05-23 | 2014-05-23 14:10 | 2014-05-23 14:36 | BRYANT - 601ANX042000AAAG | 118 | 4.8 | Yes | Yes | 22 | 19.7 | 2.3 | 02D42EF3EF2449D48DADD965BD3100EA |  | R22 | Non-TXV |  | 4.068% | 0.95932 | 7.817% | [5 empty] | Non-TXV | 4.068%
Fresno | CA | 93705-3109 |  | 2014-05-28 | 2014-05-28 12:16 | 2014-05-28 12:17 | ICP - GPFM36K060E | 68 | 2.1 | Yes | Yes | 20.4 | 22.4 | -2 | 1D90B09596564905910419C4202F3F50 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Chowchilla | CA | 93610-1815 |  | 2014-07-01 | 2014-07-01 13:20 | 2014-07-01 13:21 | RUUD - UNK | 56 | 10.9 | Yes | Yes | 26.3 | 23.1 | 3.2 | 0729D5908C92468AB3382A7215FF3684 |  | R22 | Non-TXV |  | 19.46% | 0.80536 | 37.41% | [5 empty] | Non-TXV | 19.46%
Tracy | CA | 95376-0768 |  | 2014-06-17 | 2014-06-17 11:38 | 2014-06-17 12:01 | YORK - H1CF042S06A | 158 | 5.2 | Yes | Yes | 21.4 | 20.9 | 0.5 | 24E88CBFDD30440598EA5A8F058C02A8 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Merced | CA | 95341-5589 |  | 2014-05-20 | 2014-05-20 16:47 | 2014-05-20 16:49 | OTHER - 591ANX03000ABAA | 68 | 3.2 | Yes | Yes | 21 | 21.5 | -0.5 | E5510517767C4244940422FA011F293E |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Manteca | CA | 95336-3156 |  | 2014-05-14 | 2014-05-14 08:48 | 2014-05-14 09:10 | NORDYNE - JS3BA-042KA | 85 | -6 | Yes | Yes | 20.4 | 22.3 | -1.9 | 6067C322DCB643AA854849EAC9B8AA5F |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Planada | CA | 95365-0000 |  | 2014-09-02 | 2014-09-02 13:14 | 2014-09-02 13:16 | CARRIER - 24ABA348A310 | 121 | 23.1 | Yes | Yes | 20.6 | 17.5 | 3.1 | E84148C905EA402EBDD6943AD0CFD115 |  | R410A | TXV |  | 19.09% | 0.80909 | 36.69% | [5 empty] | TXV | 19.09%
Red Bluff | CA | 96080-9231 |  | 2014-06-03 | 2014-06-03 16:41 | 2014-06-03 16:58 | BRYANT - 698BN048-A | 214 | 8.1 | Yes | Yes | 23.5 | 20.8 | 2.7 | 58FDFFB45A1448038F4D2AAE50CC2397 |  | R410A | TXV |  | 3.785% | 0.96215 | 7.274% | [5 empty] | TXV | 3.785%
Chico | CA | 95926-4205 |  | 2014-05-19 | 2014-05-19 09:59 | 2014-05-19 09:43 | UNK - UNK | 85 | 3.2 | Yes | Yes | 22.2 | 19.7 | 2.6 | AD43B8436E5748748AC31D4B820AD3B7 |  |  |  |  | 3.765% | 0.96235 | 7.235% | [5 empty] | 0 | 3.765%
Fresno | CA | 93702-2706 |  | 2014-05-21 | 2014-05-21 13:43 | 2014-05-21 14:21 | GOODMAN - GPG1348070M41CA | 87 | 4.6 | Yes | Yes | 20.4 | 19.1 | 1.3 | 3566D40A46FD4F499E0D65C8C02671F7 |  | R410A | TXV |  | 5.287% | 0.94713 | 10.16% | [5 empty] | TXV | 5.287%
Fresno | CA | 93722-2332 |  | 2014-05-20 | 2014-05-20 10:50 | 2014-05-20 10:54 | YORK - H20H036S06B | 124 | 4.2 | Yes | Yes | 19 | 19.6 | -0.6 | 25E1635D0A11409B842B27D01E8DC5BD |  | R22 | Non-TXV |  | 3.387% | 0.96613 | 6.509% | [5 empty] | Non-TXV | 3.387%
Oakhurst | CA | 93644-8828 |  | 2014-07-31 | 2014-07-31 10:05 | 2014-07-31 10:11 | OTHER - THJD42S41S4B | 171 | 6.6 | Yes | Yes | 20.3 | 20.1 | 0.2 | 6D416274A5784DF0A44EC6FC43CDB0D0 |  | R410A | Non-TXV |  | 3.86% | 0.9614 | 7.417% | [5 empty] | Non-TXV | 3.86%
Tracy | CA | 95376-4506 |  | 2014-06-17 | 2014-06-17 10:52 | 2014-06-17 11:16 | RHEEM - 13AJA24A01757 | 85 | 2.6 | Yes | Yes | 18 | 19.4 | -1.4 | 13F8CA3F80284302BC839DC908B8AAF1 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Chico | CA | 95973-0588 |  | 2014-06-10 | 2014-06-10 14:41 | 2014-06-10 15:27 | LENNOX - HS18-2610-1P | 63 | 8.5 | Yes | Yes | 19.9 | 19.8 | 0.1 | 519C639B52014EEEAA18FB619B0D8E04 |  | R22 | Non-TXV |  | 13.49% | 0.86508 | 25.93% | [5 empty] | Non-TXV | 13.49%
Yuba City | CA | 95993-8881 |  | 2014-07-03 | 2014-07-03 12:07 | 2014-07-03 12:27 | LENNOX - 13ACC-060-230-01 | 168 | 4.9 | Yes | Yes | 22 | 19.1 | 2.9 | A8FD748590244A259A53533156DF25B0 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Fresno | CA | 93726-3004 |  | 2014-05-28 | 2014-05-28 10:30 | 2014-05-28 10:48 | YORK - D1NA30N05606C | 76 | 2.8 | Yes | Yes | 21.9 | 20.8 | 1.1 | 3DA3380E370C4BC79CF18E5FA60F7D12 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Fresno | CA | 93722-4402 |  | 2014-05-21 | 2014-05-21 20:19 | 2014-05-21 20:21 | OTHER - 7777UNK | 86 | 3.2 | Yes | Yes | 20.7 | 20.9 | -0.2 | 68FF8C7E139C4DEBADD231BD51B4CC0E |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Atwater | CA | 95301-3321 |  | 2014-05-19 | 2014-05-19 12:50 | 2014-05-19 12:51 | YORK - D1NP042N09006A | 150 | 7.2 | Yes | Yes | 20.6 | 19.3 | 1.3 | 18409AB4D9F146FCA0DD82EDE725199B |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Stockton | CA | 95204-2925 |  | 2014-06-04 | 2014-06-04 16:18 | 2014-06-04 16:37 | RHEEM - RRNA-BO30JK06X | 72 | 8.4 | Yes | Yes | 25.2 | 21.3 | 3.9 | BBF7030B90144389A0B39AFA9E5647EF |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Clovis | CA | 93611-4581 |  | 2014-06-10 | 2014-06-10 13:09 | 2014-06-10 13:25 | BDP - 585EJ036075 | 82 | 17.5 | Yes | Yes | 24.2 | 20.7 | 3.5 | 7FE228B6F96A468BB360E7422604219E |  | R22 | Non-TXV |  | 21.34% | 0.78659 | 41.01% | [5 empty] | Non-TXV | 21.34%
Yuba City | CA | 95993-9107 |  | 2014-06-12 | 2014-06-12 14:56 | 2014-06-12 15:12 | CARRIER - 38CKC036350 | 70 | 2.4 | Yes | Yes | 17 | 19.9 | -2.9 | ADD8A8AAC0064BE9895E556FDDCECABA |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Manteca | CA | 95336-5931 |  | 2014-05-16 | 2014-05-16 13:17 | 2014-05-16 13:39 | YORK - D1NQ042N06506NXA | 72 | 8.9 | Yes | Yes | 21 | 21.5 | -0.5 | 08254A2D838B4151B822F38C08816F4C |  | R410A | TXV |  | 12.36% | 0.87639 | 23.76% | [5 empty] | TXV | 12.36%
Lathrop | CA | 95330-8994 |  | 2014-06-17 | 2014-06-17 13:17 | 2014-06-17 13:41 | CARRIER - 38CKC060370 | 159 | -7.7 | Yes | Yes | 21.4 | 19.4 | 2 | 39460232DB2A4EDEA9112E7ACDF18B68 |  | R22 | TXV |  | -4.843% | 1.0484 | 1.356% |  |  |  |  | TXV |  |  | -4.843%
Riverbank | CA | 95367-3314 |  | 2014-05-20 | 2014-05-20 08:35 | 2014-05-20 09:02 | DAY & NIGHT - 598AN036-B | 217 | 8.4 | Yes | Yes | 18 | 18.8 | -0.8 | 39E14B90F4764D3A8BBF3F24258BD144 |  | R22 | Non-TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | Non-TXV | 3.871%
Kingsburg | CA | 93631-1700 |  | 2014-07-12 | 2014-07-12 09:21 | 2014-07-12 09:51 | RUUD - UAKA-048JAZ | 103 | 10.7 | Yes | Yes | 26.7 | 21.1 | 5.7 | D7548A48CD314092960E54F4AFAD4F88 |  | R22 | Non-TXV |  | 10.39% | 0.89612 | 19.96% | [5 empty] | Non-TXV | 10.39%
Fresno | CA | 93703-4357 |  | 2014-06-11 | 2014-06-11 12:09 | 2014-06-11 12:28 | BDP - N/A | 60 | 4.5 | Yes | Yes | 20.8 | 20.9 | -0.1 | 24A71BE916BB4BD8B6D4F21D8F319439 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Fresno | CA | 93705-0608 |  | 2014-07-16 | 2014-07-16 09:18 | 2014-07-16 09:18 | YORK - D1NH042N09006C | 94 | 0 | Yes | Yes | 35.3 | 21.5 | 13.8 | EE7054F247524D44A8E424A9203B99A6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-5657 |  | 2014-05-16 | 2014-05-16 14:29 | 2014-05-16 14:30 | GE - BWB9240100AO | 86 | 14.3 | Yes | Yes | 16.4 | 18.2 | -1.8 | E8689779B89048FE849B51B79693CC09 |  | R22 | Non-TXV |  | 16.63% | 0.83372 | 31.96% | [5 empty] | Non-TXV | 16.63%
Reedley | CA | 93654-7028 |  | 2014-07-28 | 2014-07-28 11:15 | 2014-07-28 11:34 | LENNOX - 13ACD-042-230-02 | 111 | 7.9 | Yes | Yes | 20.8 | 20.4 | 0.4 | A28BFB42E2E44ED6A6CBF486F59A1CC1 |  | R22 | Non-TXV |  | 7.117% | 0.92883 | 13.68% | [5 empty] | Non-TXV | 7.117%
Yuba City | CA | 95991-9210 |  | 2014-05-16 | 2014-05-16 09:33 | 2014-05-16 09:53 | LENNOX - HSX15-060-230-01 | 173 | 6.3 | Yes | Yes | 25 | 19.1 | 5.9 | BCE4BF6AE4DF4CEBA4BBD61A4ED72629 |  | R410A | TXV |  | 3.642% | 0.96358 | 6.998% | [5 empty] | TXV | 3.642%
Fresno | CA | 93705-3302 |  | 2014-05-27 | 2014-05-27 14:33 | 2014-05-27 14:35 | RHEEM - RRPL-B036JK06X | 93 | 3 | Yes | Yes | 25.9 | 22.9 | 3.1 | B9159AD13B1E48C68C5F54B6128E217D |  | R410A | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Fresno | CA | 93703-2156 |  | 2014-05-30 | 2014-05-30 11:22 | 2014-05-30 11:48 | CARRIER - 48TMX042---301 | 119 | 16.4 | Yes | Yes | 19.8 | 20.4 | -0.6 | 953407D14BAF439984912B18ACA93B55 |  | R22 | Non-TXV |  | 13.78% | 0.86218 | 26.49% | [5 empty] | Non-TXV | 13.78%
Fresno | CA | 93722-7356 |  | 2014-05-23 | 2014-05-23 14:02 | 2014-05-23 14:03 | LENNOX - 12GCS042-75-3P | 133 | 5.1 | Yes | Yes | 25.6 | 20.4 | 5.2 | 27C452F23B5C4B15B4A2E31631C767F3 |  | R22 | Non-TXV |  | 3.835% | 0.96165 | 7.369% | [5 empty] | Non-TXV | 3.835%
Fresno | CA | 93727-3955 |  | 2014-06-05 | 2014-06-05 12:31 | 2014-06-05 13:03 | CARRIER - KLA136---300BE | 102 | -7.2 | Yes | Yes | 19.9 | 18.3 | 1.7 | ABCF10CB62584489B0513278C53D4591 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Lathrop | CA | 95330-8651 |  | 2014-05-28 | 2014-05-28 11:59 | 2014-05-28 12:19 | CARRIER - 24ABA348A003001 | 207 | -8.3 | Yes | Yes | 18.4 | 18.7 | -0.3 | 6B79FF8A52204C02AABB492741466522 |  | R410A | TXV |  | -4.01% | 1.0401 | 1.123% |  |  |  |  | TXV |  |  | -4.01%
Los Banos | CA | 93635-2905 |  | 2014-06-06 | 2014-06-06 12:13 | 2014-06-06 12:15 | DAY & NIGHT - 7777UNK | 80 | 3.3 | Yes | Yes | 26 | 22.6 | 3.4 | B7F618C3A5C8448FAE9240A45ADA3A44 |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Durham | CA | 95938-9672 |  | 2014-06-03 | 2014-06-03 09:50 | 2014-06-03 10:24 | CARRIER - 38BR024300 | 86 | 3.5 | Yes | Yes | 21 | 20.2 | 0.8 | 7D9B4298DA724B359E3A4B70F59C8114 |  | R22 | TXV |  | 4.07% | 0.9593 | 7.821% | [5 empty] | TXV | 4.07%
Marysville | CA | 95901-9574 |  | 2014-05-21 | 2014-05-21 13:47 | 2014-05-21 14:13 | GOODMAN - CK36-1A | 73 | 3.4 | Yes | Yes | 16.3 | 18.8 | -2.5 | 4B648ACD8EA54A07A62444EFFC2DC7E2 |  | R22 | Non-TXV |  | 4.658% | 0.95342 | 8.951% | [5 empty] | Non-TXV | 4.658%
Shingle Springs | CA | 95682-9399 |  | 2014-06-03 | 2014-06-03 14:40 | 2014-06-03 15:03 | CARRIER - 24ACR348A300 | 145 | 7.8 | Yes | Yes | 17 | 19.8 | -2.8 | A00C7550BBD2446A924599287FF4A1DA |  | R22 | Non-TXV |  | 5.379% | 0.94621 | 10.34% | [5 empty] | Non-TXV | 5.379%
Merced | CA | 95348-2125 |  | 2014-05-15 | 2014-05-15 14:54 | 2014-05-15 15:15 | RHEEM - UNK | 72 | 2.4 | Yes | Yes | 26.1 | 22.1 | 4 | 9453E8D0A09247A4949F36DB0BC6E54B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Madera | CA | 93636-7901 |  | 2014-05-30 | 2014-05-30 09:51 | 2014-05-30 10:08 | RUUD - UNK | 66 | 4.7 | Yes | Yes | 25 | 19.6 | 5.4 | 38346E78A6B94256BC42722965CC3C4E |  | R22 | Non-TXV |  | 7.121% | 0.92879 | 13.69% | [5 empty] | Non-TXV | 7.121%
Fresno | CA | 93726-0929 |  | 2014-06-02 | 2014-06-02 11:24 | 2014-06-02 12:04 | CARRIER - N/A | 120 | 4.7 | Yes | Yes | 21.5 | 21.5 | 0 | A0E93B86A2DC4B0C9F1FD38FBDA303A0 |  | R22 | Non-TXV |  | 3.917% | 0.96083 | 7.527% | [5 empty] | Non-TXV | 3.917%
Fresno | CA | 93722-3728 |  | 2014-05-21 | 2014-05-21 09:58 | 2014-05-21 10:00 | CARRIER - 38BR036300 | 122 | 6 | Yes | Yes | 20 | 20.5 | -0.5 | 7C658D0C18B74FB496A6E8F5200DCBE5 |  | R22 | Non-TXV |  | 4.918% | 0.95082 | 9.451% | [5 empty] | Non-TXV | 4.918%
Fresno | CA | 93727-7916 |  | 2014-06-27 | 2014-06-27 09:57 | 2014-06-27 10:19 | DAY & NIGHT - N/A | 90 | 5.7 | Yes | Yes | 19.3 | 19.3 | 0 | 804EEE6C10ED4E67982CB942F62AC139 |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Fresno | CA | 93722-3734 |  | 2014-06-12 | 2014-06-12 11:46 | 2014-06-12 12:06 | CARRIER - 38BR030300 | 102 | 9.8 | Yes | Yes | 20.1 | 21.5 | -1.4 | 987422BFA1B14A20AACFCA7A720E3038 |  | R22 | Non-TXV |  | 9.608% | 0.90392 | 18.46% | [5 empty] | Non-TXV | 9.608%
Fresno | CA | 93705-4339 |  | 2014-05-21 | 2014-05-21 09:02 | 2014-05-21 09:19 | GOODMAN - GPG12240451A | 64 | 8.6 | Yes | Yes | 24.3 | 19.1 | 5.2 | 38FEC18B351D41F4933FCAD87E53B6A6 |  | R22 | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
Fresno | CA | 93705-4339 |  | 2014-05-21 | 2014-05-21 09:26 | 2014-05-21 09:46 | GOODMAN - GPG12240451A | 64 | 4.6 | Yes | Yes | 23.1 | 17.5 | 5.7 | 94D56EC67029456BA212BD77FB667A2C |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Fresno | CA | 93727-2015 |  | 2014-06-03 | 2014-06-03 10:14 | 2014-06-03 10:39 | ICP - PGC060K100D | 136 | 5.6 | Yes | Yes | 21.2 | 20.2 | 1.1 | 071A00FF213C47A69852A205585F783D |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fresno | CA | 93705-2250 |  | 2014-05-23 | 2014-05-23 14:45 | 2014-05-23 15:08 | GOODMAN - GSH130361CD | 188 | 23.7 | Yes | Yes | 21.1 | 18.1 | 3 | 143BFF7870044A2B97206CE3741DD4E2 |  | R22 | Non-TXV |  | 12.61% | 0.87394 | 24.23% | [5 empty] | Non-TXV | 12.61%
Fresno | CA | 93727-0000 |  | 2014-06-10 | 2014-06-10 10:45 | 2014-06-10 11:06 | NORDYNE - JS5BD-042KA | 122 | 4.2 | Yes | Yes | 18.4 | 20.4 | -2 | BFE48EEC914F4C4087D138D810C03411 |  | R22 | Non-TXV |  | 3.443% | 0.96557 | 6.616% | [5 empty] | Non-TXV | 3.443%
Paradise | CA | 95969-6660 |  | 2014-06-13 | 2014-06-13 14:54 | 2014-06-13 15:10 | PHILCO - RAMA060JAZ | 192 | 6 | Yes | Yes | 23 | 20.4 | 2.6 | 2D636F6D97D24003B354AB9954C3F6A7 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Paradise | CA | 95969-2325 |  | 2014-06-05 | 2014-06-05 14:18 | 2014-06-05 14:58 | BRYANT - 563CN036-D6E | 50 | 4.5 | Yes | Yes | 19.1 | 21 | -1.9 | B90B33206DD54632B8FAC3242AC6C7E6 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Parlier | CA | 93648-2116 |  | 2014-06-17 | 2014-06-17 16:37 | 2014-06-17 17:03 | GOODMAN - GPG1330070M41AD | 80 | -3.9 | Yes | Yes | 20.5 | 23.2 | -2.7 | 800F7652363A4CEC81D5E5E7A46C284D |  | R410A | TXV |  | -4.875% | 1.0488 | 1.365% |  |  |  |  | TXV |  |  | -4.875%
Stockton | CA | 95207-8131 |  | 2014-05-29 | 2014-05-29 10:13 | 2014-05-29 10:45 | DAY & NIGHT - 585EJW024050ABAF | 54 | 2.1 | Yes | Yes | 19.4 | 20.1 | -0.7 | 59EE1C10028B44F3900A9C21A2E95DD7 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Fresno | CA | 93703-1225 |  | 2014-05-16 | 2014-05-16 12:04 | 2014-05-16 12:31 | ICP - NPGAA36C1K6 | 69 | 14.3 | Yes | Yes | 20 | 22.8 | -2.8 | 3A6A419D0CD940C6A51215518CAED1D1 |  | R22 | Non-TXV |  | 20.72% | 0.79275 | 39.83% | [5 empty] | Non-TXV | 20.72%
Yuba City | CA | 95993-9400 |  | 2014-05-28 | 2014-05-28 11:54 | 2014-05-28 12:13 | TRANE - 4TTX4048B1000AA | 127 | 5.7 | Yes | Yes | 28 | 22.6 | 5.4 | AA93E2EAA89549CB8E477F99AD71A36F |  | R410A | TXV |  | 4.488% | 0.95512 | 8.625% | [5 empty] | TXV | 4.488%
Lodi | CA | 95242-0000 |  | 2014-08-22 | 2014-08-22 12:13 | 2014-08-22 12:13 | COLEMAN - N2A348AKA200 | 115 | 0 | Yes | Yes | 23.5 | 19.3 | 4.2 | 7FF409C25DAF407486E15D683A6AE649 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-5223 |  | 2014-05-19 | 2014-05-19 16:45 | 2014-05-19 17:06 | BDP - 585GJW024040 | 55 | 10.9 | Yes | Yes | 20.1 | 21.2 | -1.1 | BC7072C095844769ACB83009FC6EE448 |  | R22 | Non-TXV |  | 19.82% | 0.80182 | 38.09% | [5 empty] | Non-TXV | 19.82%
Cool | CA | 95614-2013 |  | 2014-09-17 | 2014-09-17 14:52 | 2014-09-17 15:32 | BRYANT - 550ANO48-E | 173 | 8.3 | Yes | Yes | 28.1 | 24.2 | 3.9 | 1E568A29B1CF40BF87164FC673B24EA8 |  | R22 | Non-TXV |  | 4.798% | 0.95202 | 9.22% | [5 empty] | Non-TXV | 4.798%
Penn Valley | CA | 95946-9618 |  | 2014-06-30 | 2014-06-30 09:27 | 2014-06-30 09:45 | OTHER - UNKEHAM326709 | 92 | 3.2 | Yes | Yes | 22 | 19.4 | 2.6 | A6BE9EEE646A4DC1AE219A0D83DA05E6 |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Stockton | CA | 95204-1242 |  | 2014-08-19 | 2014-08-19 14:23 | 2014-08-19 14:43 | TRANE - YCX036F1MOBC | 118 | -6.9 | Yes | Yes | 18.9 | 19.3 | -0.4 | 3F714EB6671A48688A306DF1F7505D0F |  | R22 | Non-TXV |  | -5.847% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.847%
Chico | CA | 95926-2453 |  | 2014-06-12 | 2014-06-12 11:39 | 2014-06-12 11:55 | PAYNE - NA | 55 | 8.1 | Yes | Yes | 20.6 | 20.9 | -0.3 | 26D5B75621B341C5977A3845F713484E |  | R22 | Non-TXV |  | 14.73% | 0.85273 | 28.3% | [5 empty] | Non-TXV | 14.73%
Madera | CA | 93637-6162 |  | 2014-05-30 | 2014-05-30 12:16 | 2014-05-30 12:36 | TRANE - 4YCC3036A1064AB | 124 | 20.7 | Yes | Yes | 20.2 | 19.3 | 0.9 | 30D44F7E69C5440BB7030FF0CE6B60BB |  | R410A | Non-TXV |  | 16.69% | 0.83306 | 32.08% | [5 empty] | Non-TXV | 16.69%
Colfax | CA | 95713-9002 |  | 2014-08-20 | 2014-08-20 08:37 | 2014-08-20 08:54 | TRANE - YCPO030F1L0AA | 106 | 3.9 | Yes | Yes | 24.5 | 20.2 | 4.4 | 852D290277A1468299A2AEE51078D9C3 |  | R22 | Non-TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | Non-TXV | 3.679%
Stockton | CA | 95212-3218 |  | 2014-05-15 | 2014-05-15 10:13 | 2014-05-15 10:31 | CARRIER - 38CKC042340 | 80 | 2.7 | Yes | Yes | 26.3 | 20.4 | 5.9 | 41CB2E10C4CD452F87E6CC5F56998417 |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Madera | CA | 93637-5141 |  | 2014-08-13 | 2014-08-13 10:42 | 2014-08-13 11:01 | YORK - D2NP024N05606A | 100 | 3 | Yes | Yes | 19.3 | 18.5 | 0.8 | 47CA8DBC0CA34F21AEF881C3EA2666F1 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Paradise | CA | 95969-4710 |  | 2014-05-23 | 2014-05-23 10:42 | 2014-05-23 11:30 | BRYANT - 585A024080YAC | 62 | 6.2 | Yes | Yes | 24.9 | 20.1 | 4.9 | 5F1840057AEA41F98D46189D2F650FD8 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Kingsburg | CA | 93631-1739 |  | 2014-08-06 | 2014-08-06 17:05 | 2014-08-06 17:30 | LENNOX - 13ACD-042-230-16 | 102 | 3.3 | Yes | Yes | 23.8 | 21 | 2.8 | 16A4C35FDA754CB6B49BAFED8C8D84D9 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Stockton | CA | 95209-4003 |  | 2014-06-19 | 2014-06-19 14:35 | 2014-06-19 14:56 | PAYNE - PA10JA048-C | 96 | 3.5 | Yes | Yes | 28.1 | 22.9 | 5.2 | 83443071950C4807BA4E48346F3ABBCD |  | R22 | Non-TXV |  | 3.646% | 0.96354 | 7.006% | [5 empty] | Non-TXV | 3.646%
Stockton | CA | 95207-6004 |  | 2014-05-22 | 2014-05-22 11:01 | 2014-05-22 11:33 | OTHER - UNK | 48 | 2.6 | Yes | Yes | 22.4 | 18.8 | 3.6 | C8A94CFB1B1B409EA90A1F715BC5ABDB |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Stockton | CA | 95207-8120 |  | 2014-06-19 | 2014-06-19 13:50 | 2014-06-19 14:13 | DAY & NIGHT - 585EJ024050 | 54 | 4.6 | Yes | Yes | 21.9 | 20.2 | 1.8 | 26DDB7C52E4742E88133201D735B36FA |  | R22 | Non-TXV |  | 8.519% | 0.91481 | 16.37% | [5 empty] | Non-TXV | 8.519%
Madera | CA | 93638-1515 |  | 2014-06-19 | 2014-06-19 11:59 | 2014-06-19 12:14 | OTHER - 80WR30G1NA | 86 | 20.8 | Yes | Yes | 21.8 | 21.3 | 0.5 | B88CF702D45543BD8951700FB58BACD1 |  | R22 | Non-TXV |  | 24.19% | 0.75814 | 46.48% | [5 empty] | Non-TXV | 24.19%
Manteca | CA | 95336-5112 |  | 2014-05-14 | 2014-05-14 13:37 | 2014-05-14 13:56 | YORK - H3RE030S06B | 130 | 4.9 | Yes | Yes | 19.3 | 20.2 | -0.9 | 25491B5491D645EAA5753C371CD48B4C |  | R22 | Non-TXV |  | 3.769% | 0.96231 | 7.244% | [5 empty] | Non-TXV | 3.769%
Fresno | CA | 93710-7342 |  | 2014-06-20 | 2014-06-20 11:54 | 2014-06-20 12:19 | BDP - 585A024055YAC | 51 | 2 | Yes | Yes | 19.1 | 19.9 | -0.8 | 549FA6E71BEF49F99333DAA6D420057D |  | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Oroville | CA | 95966-6619 |  | 2014-06-23 | 2014-06-23 12:25 | 2014-06-23 12:56 | DAY & NIGHT - NA | 55 | 1.7 | Yes | Yes | 12.5 | 15.5 | -3 | 1D3158ABB67D49BB84BFECC9FBAADA28 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Fresno | CA | 93702-2919 |  | 2014-06-18 | 2014-06-18 14:51 | 2014-06-18 14:53 | CARRIER - 48GS-03606031 | 85 | 2.9 | Yes | Yes | 19.2 | 20.6 | -1.4 | EF9A0260F4C540F48E1F5E102F554B47 |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Paradise | CA | 95969-4333 |  | 2014-07-25 | 2014-07-25 13:59 | 2014-07-25 14:15 | HEIL - CA3018UKA3 | 55 | 4.7 | Yes | Yes | 22.5 | 21.2 | 1.4 | F379419D2FE14984BD1AD52332FCECF3 |  | R22 | Non-TXV |  | 8.545% | 0.91455 | 16.42% | [5 empty] | Non-TXV | 8.545%
Paradise | CA | 95969-2622 |  | 2014-06-11 | 2014-06-11 15:10 | 2014-06-11 15:28 | GOODMAN - CKL36-1E | 70 | 7.2 | Yes | Yes | 18.3 | 19.3 | -1 | 69FAF5B3C4824D238B2ADDC3FE159D61 |  | R22 | Non-TXV |  | 10.29% | 0.89714 | 19.77% | [5 empty] | Non-TXV | 10.29%
Chico | CA | 95926-1957 |  | 2014-06-06 | 2014-06-06 11:41 | 2014-06-06 12:11 | TEMPSTAR - TCAO24AKA1 | 35 | 8.1 | Yes | Yes | 19 | 20.4 | -1.4 | 03186F3B827643FAADF19FEEB96C9210 |  | R22 | Non-TXV |  | 23.14% | 0.76857 | 44.48% | [5 empty] | Non-TXV | 23.14%
Sanger | CA | 93657-3407 |  | 2014-07-07 | 2014-07-07 17:25 | 2014-07-07 17:56 | ICP - PGF048K080 | 102 | 6.8 | Yes | Yes | 17.9 | 20.8 | -2.9 | 9681EA2025E44E8C8B1D64ACC23E9286 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93727-5519 |  | 2014-08-07 | 2014-08-07 15:58 | 2014-08-07 16:00 | GOODMAN - PGB024050 | 54 | 2.5 | Yes | Yes | 17.1 | 19.5 | -2.4 | 81A061F66A444744A88EFC54D58CA88D |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Fresno | CA | 93727-5519 |  | 2014-08-07 | 2014-08-07 16:02 | 2014-08-07 16:25 | BDP - 568EJ036 | 154 | 6.4 | Yes | Yes | 22.2 | 20.5 | 1.7 | 0C513B518AA54DC19003A0F0CCB03271 |  | R22 | Non-TXV |  | 4.156% | 0.95844 | 7.987% | [5 empty] | Non-TXV | 4.156%
Chico | CA | 95973-0670 |  | 2014-06-30 | 2014-06-30 15:29 | 2014-06-30 16:06 | GOODMAN - CKL36-11 | 65 | 8.3 | Yes | Yes | 28.3 | 22.8 | 5.5 | CAA8E85C5751490AB9122295F15F6D39 |  | R22 | Non-TXV |  | 12.77% | 0.87231 | 24.54% | [5 empty] | Non-TXV | 12.77%
Riverbank | CA | 95367-2230 |  | 2014-05-20 | 2014-05-20 09:41 | 2014-05-20 10:09 | YORK - D5YS024N04506A | 70 | -6.6 | Yes | Yes | 26 | 21.3 | 4.7 | 40AEB4AFA2F84834BFC6EE0AC7C83666 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Stockton | CA | 95206-5818 |  | 2014-06-09 | 2014-06-09 13:56 | 2014-06-09 14:13 | RUUD - UAFD-036JAS | 80 | 20.3 | Yes | Yes | 24 | 22.5 | 1.5 | DE5B4F681C2D4FB08128DD5D98614DAA |  | R22 | Non-TXV |  | 25.37% | 0.74625 | 48.77% | [5 empty] | Non-TXV | 25.37%
Madera | CA | 93637-5379 |  | 2014-06-09 | 2014-06-09 11:37 | 2014-06-09 11:55 | YORK - DCYZF036N070C | 64 | 8.6 | Yes | Yes | 25.8 | 22.5 | 3.3 | 1A69B3E3F97E4F8098C9444E565D40B0 |  | R410A | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
Atwater | CA | 95301-4810 |  | 2014-05-16 | 2014-05-16 16:10 | 2014-05-16 16:11 | DAY & NIGHT - 598NX036B | 204 | 6.9 | Yes | Yes | 20.2 | 22.6 | -2.4 | 4586B56307654AFF8D8C7DF038DF819E |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Atwater | CA | 95301-4862 |  | 2014-05-16 | 2014-05-16 16:06 | 2014-05-16 16:07 | LENNOX - HS9311-4P | 78 | 5.4 | Yes | Yes | 18.6 | 21.5 | -2.9 | 82F74DB57FBC4D03B524303E973FB6C0 |  | R22 | Non-TXV |  | 6.923% | 0.93077 | 13.3% | [5 empty] | Non-TXV | 6.923%
Oroville | CA | 95965-4701 |  | 2014-06-10 | 2014-06-10 09:34 | 2014-06-10 09:50 | AMANA - NA | 59 | 2.5 | Yes | Yes | 17.5 | 20.4 | -2.9 | E607D7125A7C456A807C97F29F82E9E1 |  | R22 | Non-TXV |  | 4.237% | 0.95763 | 8.143% | [5 empty] | Non-TXV | 4.237%
Ripon | CA | 95366-9664 |  | 2014-05-16 | 2014-05-16 15:06 | 2014-05-16 15:29 | PAYNE - PY3GNAA30060NA | 98 | -10.1 | Yes | Yes | 19.4 | 21.5 | -2.1 | 6BDA90245356483FAD420DFFA8441F63 |  | R410A | TXV |  | -10.31% | 1.1031 | 2.886% |  |  |  |  | TXV |  |  | -10.31%
Stockton | CA | 95210-3248 |  | 2014-05-27 | 2014-05-27 10:06 | 2014-05-27 10:37 | BRYANT - 574ANW024060NB | 89 | 5.5 | Yes | Yes | 23.5 | 20.4 | 3.1 | 59BBDFC923DD4FD3BF852AE75F4F22EF |  | R22 | Non-TXV |  | 6.18% | 0.9382 | 11.88% | [5 empty] | Non-TXV | 6.18%
Sutter | CA | 95982-2531 |  | 2014-09-10 | 2014-09-10 15:41 | 2014-09-10 15:41 | YORK - UNK | 100 | 0 | Yes | Yes | 18 | 20.2 | -2.2 | 54ACD33714C14126AB5ED1BCB4B8F737 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-8961 |  | 2014-06-27 | 2014-06-27 08:37 | 2014-06-27 08:59 | CARRIER - 24ABB330W310 | 74 | 5.4 | Yes | Yes | 21.2 | 20.3 | 0.9 | 62489C82D8904CDD9C642FE2192EB80C |  | R410A | TXV |  | 7.297% | 0.92703 | 14.02% | [5 empty] | TXV | 7.297%
Stockton | CA | 95210-3248 |  | 2014-05-27 | 2014-05-27 09:42 | 2014-05-27 10:05 | BRYANT - 5858024050YACR | 51 | 6.2 | Yes | Yes | 23.9 | 21.7 | 2.2 | 342ED5B0B5C541D5A07BCC1F73D3A7B1 |  | R22 | Non-TXV |  | 12.16% | 0.87843 | 23.36% | [5 empty] | Non-TXV | 12.16%
Fresno | CA | 93703-4245 |  | 2014-05-19 | 2014-05-19 15:16 | 2014-05-19 15:49 | RHEEM - N/A | 60 | 4.3 | Yes | Yes | 18.9 | 20.4 | -1.5 | 047AFC14B72543229125F8B20B37F23F |  | R22 | Non-TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | Non-TXV | 7.167%
Lodi | CA | 95242-9561 |  | 2014-08-05 | 2014-08-05 10:45 | 2014-08-05 11:10 | RUUD - UAFD-048JBS | 101 | -5.9 | Yes | Yes | 17.7 | 18.8 | -1.1 | 5B3189A973C245D0B8F81CCEFF7A234A |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Stockton | CA | 95204-4917 |  | 2014-06-13 | 2014-06-13 11:47 | 2014-06-13 12:05 | PAYNE - 561CJ024-B | 130 | 6.9 | Yes | Yes | 20.5 | 19.6 | 0.9 | 6FA69B8586E644F8A5A850562CCBDA9D |  | R22 | TXV |  | 5.308% | 0.94692 | 10.2% | [5 empty] | TXV | 5.308%
Durham | CA | 95938-9718 |  | 2014-07-01 | 2014-07-01 11:19 | 2014-07-01 11:38 | TRANE - YC036F1M0BC | 116 | 3.4 | Yes | Yes | 19.5 | 22.1 | -2.6 | 642763000C3D48AEB1CD44FA4C1F8373 |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Merced | CA | 95340-0941 |  | 2014-05-16 | 2014-05-16 08:52 | 2014-05-16 08:54 | OTHER - 80AW30106 | 98 | 14.5 | Yes | Yes | 20.4 | 18.2 | 2.2 | 490B42B8E4154B488F390529014EA189 |  | R22 | Non-TXV |  | 14.8% | 0.85204 | 28.43% | [5 empty] | Non-TXV | 14.8%
Paso Robles | CA | 93446-5179 |  | 2014-06-24 | 2014-06-24 13:44 | 2014-06-24 14:03 | CARRIER - 38EN024310 | 61 | -3.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | B29643AB90274838BBCAB3A61D7EB7FF |  | R22 | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Lathrop | CA | 95330-8517 |  | 2014-05-27 | 2014-05-27 13:23 | 2014-05-27 13:52 | CARRIER - 24ABB336A310 | 114 | 6.6 | Yes | Yes | 24 | 20.9 | 3.1 | F16032D49CB8438EA23C9237FD344130 |  | R410A | TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | TXV | 5.789%
Fresno | CA | 93705-4342 |  | 2014-05-26 | 2014-05-26 13:53 | 2014-05-26 14:10 | ICP - PGAD36D1K7 | 100 | 19.3 | Yes | Yes | 21.6 | 19.9 | 1.7 | 2731464F1E4146D8AD77B3CBC18AC5EB |  | R22 | Non-TXV |  | 19.3% | 0.807 | 37.09% | [5 empty] | Non-TXV | 19.3%
Fresno | CA | 93726-3917 |  | 2014-06-27 | 2014-06-27 12:46 | 2014-06-27 12:47 | BDP - 585A024055YACR | 51 | 6.3 | Yes | Yes | 23.9 | 19.3 | 4.6 | E39DC49B682B4FCBB004E25262CC8DCA |  | R22 | Non-TXV |  | 12.35% | 0.87647 | 23.74% | [5 empty] | Non-TXV | 12.35%
Chico | CA | 95973-8232 |  | 2014-06-30 | 2014-06-30 10:40 | 2014-06-30 11:00 | BRYANT - 563CN036-2 | 100 | 3.2 | Yes | Yes | 27.5 | 23.1 | 4.4 | AA9CF8F159FD441DB76CF7A8545AB011 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Merced | CA | 95340-1343 |  | 2014-05-15 | 2014-05-15 08:52 | 2014-05-15 08:59 | OTHER - BTD724A100AO | 68 | 4.8 | Yes | Yes | 20.3 | 15.2 | 5.1 | 2AA950BF233F4B94A4AD478FF71DF3F3 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Paradise | CA | 95969-4222 |  | 2014-06-05 | 2014-06-05 13:46 | 2014-06-05 14:04 | AIRE-FLO - AFAIR12B30-A | 85 | 7.8 | Yes | Yes | 18.9 | 21.5 | -2.6 | 619BB4DB58094A05BE3DF5DB4F71DF93 |  | R22 | Non-TXV |  | 9.176% | 0.90824 | 17.64% | [5 empty] | Non-TXV | 9.176%
Madera | CA | 93638-2228 |  | 2014-06-03 | 2014-06-03 09:02 | 2014-06-03 09:19 | YORK - D1NH036N05606C | 108 | 12.7 | Yes | Yes | 22.4 | 17.7 | 4.7 | 12E56353799B493499221270D7B12BD6 |  | R22 | Non-TXV |  | 11.76% | 0.88241 | 22.6% | [5 empty] | Non-TXV | 11.76%
Winton | CA | 95388-8735 |  | 2014-05-19 | 2014-05-19 14:48 | 2014-05-19 14:49 | GOODMAN - PGB024050-1 | 54 | 4.1 | Yes | Yes | 22.9 | 21.5 | 1.4 | 61D7E2EA9DBD4AFB97D00ECB3D00C936 |  | R22 | Non-TXV |  | 7.593% | 0.92407 | 14.59% | [5 empty] | Non-TXV | 7.593%
Kerman | CA | 93630-1373 |  | 2014-06-18 | 2014-06-18 09:41 | 2014-06-18 09:59 | CARRIER - 24ABR336A310 | 88 | 6.3 | Yes | Yes | 20.6 | 19.9 | 0.7 | D8BA370E967E480084B45ACB7A0B7B44 |  | R22 | TXV |  | 7.159% | 0.92841 | 13.76% | [5 empty] | TXV | 7.159%
Sanger | CA | 93657-2319 |  | 2014-06-20 | 2014-06-20 16:49 | 2014-06-20 17:09 | YORK - N/A | 120 | 4.7 | Yes | Yes | 20.5 | 20.8 | -0.3 | BBC88A20BFB146D89CD83EC37B96014C |  | R22 | Non-TXV |  | 3.917% | 0.96083 | 7.527% | [5 empty] | Non-TXV | 3.917%
Sanger | CA | 93657-2319 |  | 2014-06-20 | 2014-06-20 17:13 | 2014-06-20 17:34 | GOODMAN - GPG1336070M41AC | 85 | 3.5 | Yes | Yes | 26.5 | 22.4 | 4.2 | 9EFE8F9E3A124A749B9CFFBF084038AD |  | R410A | TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | TXV | 4.118%
Fresno | CA | 93726-3304 |  | 2014-06-02 | 2014-06-02 12:31 | 2014-06-02 13:08 | RHEEM - RRKA-A060JL10X | 185 | 5.8 | Yes | Yes | 22.6 | 21 | 1.6 | 28F5A7CE215249C986666598E031BB7B |  | R22 | Non-TXV |  | 3.135% | 0.96865 | 6.025% | [5 empty] | Non-TXV | 3.135%
Fresno | CA | 93727-1814 |  | 2014-06-03 | 2014-06-03 08:48 | 2014-06-03 09:16 | RHEEM - RRRL-B036JK08X | 155 | 5.7 | Yes | Yes | 20.1 | 21.8 | -1.7 | 5B7D363DD68F42339DEAEE8D88688795 |  | R410A | TXV |  | 3.677% | 0.96323 | 7.067% | [5 empty] | TXV | 3.677%
Clovis | CA | 93611-6961 |  | 2014-06-02 | 2014-06-02 12:22 | 2014-06-02 12:24 | LENNOX - 13ACC-036-230-01 | 115 | 4.4 | Yes | Yes | 25.3 | 22.6 | 2.7 | D258346A5AF042F9977B76FE9C4D5D1D |  | R410A | Non-TXV |  | 3.826% | 0.96174 | 7.353% | [5 empty] | Non-TXV | 3.826%
Clovis | CA | 93611-6961 |  | 2014-06-02 | 2014-06-02 12:26 | 2014-06-02 12:30 | LENNOX - 13ACC-036-230-01 | 115 | 5.6 | Yes | Yes | 23.6 | 22.6 | 1 | 99756C2F8F7F4F2C92915DCF92D7B7FE |  | R410A | Non-TXV |  | 4.87% | 0.9513 | 9.358% | [5 empty] | Non-TXV | 4.87%
Fresno | CA | 93705-3212 |  | 2014-05-27 | 2014-05-27 13:17 | 2014-05-27 13:19 | ARCOAIRE - PGF342080K01 | 182 | 6.6 | Yes | Yes | 16.2 | 18.5 | -2.3 | A6A0875D618E49D98F03164BBA5E19C0 |  | R22 | Non-TXV |  | 3.626% | 0.96374 | 6.969% | [5 empty] | Non-TXV | 3.626%
Paso Robles | CA | 93446-9316 |  | 2014-06-24 | 2014-06-24 14:36 | 2014-06-24 14:55 | DAY & NIGHT - 585HJ036060 | 102 | -6 | Yes | Yes | 28.1 | 22.6 | 5.5 | 19FBAC3DA984416181052D8207FA8019 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Rocklin | CA | 95765-5126 |  | 2014-06-09 | 2014-06-09 14:28 | 2014-06-09 14:48 | JANITROL - CJ36-1GB | 106 | 3.2 | Yes | Yes | 19 | 20.1 | -1.1 | 6081F2606568497FB895668E952F0183 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Granite Bay | CA | 95746-6723 |  | 2014-08-28 | 2014-08-28 16:16 | 2014-08-28 16:16 | CARRIER - 38CK036320 | 70 | 0 | Yes | Yes | 11.5 | 18.4 | -6.9 | 50FE724CEE334768B92462A81A896C92 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Granite Bay | CA | 95746-6723 |  | 2014-08-28 | 2014-08-28 16:18 | 2014-08-28 16:45 | TRANE - TTB036C100A1 | 90 | 3.2 | Yes | Yes | 21 | 19 | 2 | 10B76C6F113A44D3937C9519D8020AC9 |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Paso Robles | CA | 93446-3014 |  | 2014-06-24 | 2014-06-24 15:21 | 2014-06-24 15:51 | BRYANT - 563CN036-A | 114 | 3.8 | Yes | Yes | 20.7 | 19.9 | 0.8 | 5AA42046EE7B4DDD9400456248DD21B7 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Sonora | CA | 95370-9069 |  | 2014-08-13 | 2014-08-13 10:37 | 2014-08-13 11:38 | - 561AJ036-B | 152 | 6.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | 260B9B8B27BB4F4F8E46A87F7DC8B972 |  | R22 | TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | TXV | 4.211%
Chico | CA | 95926-9654 |  | 2014-05-19 | 2014-05-19 18:43 | 2014-05-19 08:23 | UNK - UNK | 85 | 1.9 | Yes | Yes | 26 | 21.7 | 4.3 | EA6B4A7BE9BE49A79F1DFE7FC4AEA3BB |  |  |  |  | 2.235% | 0.97765 | 4.296% | [5 empty] | 0 | 2.235%
Linden | CA | 95236-9711 |  | 2014-09-05 | 2014-09-05 14:20 | 2014-09-05 15:13 | OTHER - AA5YS0E0200NK92Q0007 | 259 | 9.6 | Yes | Yes | 17.1 | 18.5 | -1.4 | FD96792889134002A59F47154E1ECDFD |  | R22 | Non-TXV |  | 3.707% | 0.96293 | 7.123% | [5 empty] | Non-TXV | 3.707%
Stockton | CA | 95215-7302 |  | 2014-06-10 | 2014-06-10 08:00 | 2014-06-10 08:21 | RHEEM - RRKA-A030JK06E | 54 | -3.2 | Yes | Yes | 16.5 | 19.3 | -2.8 | E63832C5C7634F77B8A6E2F068E8FD9F |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Paso Robles | CA | 93446-5071 |  | 2014-10-22 | 2014-10-22 16:40 | 2014-10-22 17:05 | CARRIER - UKN | 56 | 6.4 | Yes | Yes | 18.3 | 21.2 | -2.9 | 0D8AA12ECF6248349B65DF63CADD01C1 |  | R22 | Non-TXV |  | 11.43% | 0.88571 | 21.96% | [5 empty] | Non-TXV | 11.43%
Fresno | CA | 93722-6346 |  | 2014-06-12 | 2014-06-12 14:20 | 2014-06-12 14:58 | PAYNE - N/A | 90 | 8.5 | Yes | Yes | 19.3 | 20.1 | -0.8 | 22521AD28B1E402FBA6E8178C50A4E38 |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Plumas Lake | CA | 95961-9171 |  | 2014-05-28 | 2014-05-28 17:40 | 2014-05-28 17:57 | YORK - H2RC048S06HG | 114 | 4.2 | Yes | Yes | 18.5 | 21.4 | -2.9 | C069D66BCE21477E9B41B044106E8F41 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Fresno | CA | 93723-9484 |  | 2014-05-22 | 2014-05-22 08:23 | 2014-05-22 08:44 | RHEEM - RRNAB036JK06X | 83 | 7.1 | Yes | Yes | 23.6 | 18.8 | 4.8 | BAC30C071FA74E2284B16795220DD135 |  | R22 | Non-TXV |  | 8.554% | 0.91446 | 16.44% | [5 empty] | Non-TXV | 8.554%
Chico | CA | 95926-2743 |  | 2014-05-21 | 2014-05-21 12:10 | 2014-05-21 13:54 | TEMPSTAR - TCA024AKA1 | 69 | 2.2 | Yes | Yes | 17 | 19.3 | -2.3 | 3109632BF48D4555A357FAE6B703025D |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Paso Robles | CA | 93446-5039 |  | 2014-06-23 | 2014-06-23 13:37 | 2014-06-23 13:55 | CARRIER - 38EN024310 | 61 | 2.3 | Yes | Yes | 17.6 | 19.6 | -2 | 3C6330E2A5B947E7B2A07A4889E44DEC |  | R22 | Non-TXV |  | 3.77% | 0.9623 | 7.246% | [5 empty] | Non-TXV | 3.77%
Auburn | CA | 95603-3614 |  | 2014-05-22 | 2014-05-22 09:39 | 2014-05-22 10:10 | BRYANT - 550AN060-E | 192 | 7 | Yes | Yes | 19 | 18.8 | 0.2 | B1AE4F80A9434ACE9FBE0E04AB1ACBB2 |  | R410A | TXV |  | 3.646% | 0.96354 | 7.006% | [5 empty] | TXV | 3.646%
Stockton | CA | 95209-2821 |  | 2014-06-13 | 2014-06-13 10:36 | 2014-06-13 10:59 | OTHER - UNK | 61 | 2.3 | Yes | Yes | 17.5 | 19.3 | -1.8 | BE547A609818453BA9E43353C18B66CA |  | R22 | Non-TXV |  | 3.77% | 0.9623 | 7.246% | [5 empty] | Non-TXV | 3.77%
Atwater | CA | 95301-4534 |  | 2014-05-19 | 2014-05-19 12:02 | 2014-05-19 12:08 | COLEMAN - ERCQ0301BBB | 93 | 12.5 | Yes | Yes | 23.3 | 21.2 | 2.1 | 440CAF8DF38A439EACFB1A3090A181DA |  | R22 | Non-TXV |  | 13.44% | 0.86559 | 25.83% | [5 empty] | Non-TXV | 13.44%
Fresno | CA | 93703-1336 |  | 2014-05-22 | 2014-05-22 16:45 | 2014-05-22 17:04 | ICP - PGAB3601K1 | 80 | 2.9 | Yes | Yes | 24.7 | 22.6 | 2.1 | 514EA3FE683243F3A704A839C5333804 |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Stockton | CA | 95206-3886 |  | 2014-07-07 | 2014-07-07 13:12 | 2014-07-07 13:31 | CARRIER - 38EZG030300 | 85 | 3.4 | Yes | Yes | 20.8 | 19.8 | 1 | 282CA414578C48D683864B8189A73710 |  | R410A | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Chico | CA | 95926-2771 |  | 2014-06-02 | 2014-06-02 15:34 | 2014-06-02 15:58 | DAY & NIGHT - E122623475 | 85 | 3.2 | Yes | Yes | 18 | 18.5 | -0.4 | FEB0E2E09C0546319AF254E48586E183 |  | R410A | TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | TXV | 3.765%
Dinuba | CA | 93618-4004 |  | 2014-07-21 | 2014-07-21 15:26 | 2014-07-21 16:06 | RUUD - N/A | 90 | 7.7 | Yes | Yes | 20 | 22.1 | -2.1 | 14EFEC8A2A2A462AB3B7456FD65117D7 |  | R22 | Non-TXV |  | 8.556% | 0.91444 | 16.44% | [5 empty] | Non-TXV | 8.556%
Stockton | CA | 95206-3886 |  | 2014-06-18 | 2014-06-18 14:31 | 2014-06-18 14:48 | COPELAND - VSX130361EA | 75 | 4 | Yes | Yes | 20.2 | 21 | -0.8 | 5C57B8FF0E854437AFA81F19F5B1DE4E |  | R410A | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Stockton | CA | 95209-1239 |  | 2014-05-19 | 2014-05-19 11:30 | 2014-05-19 11:57 | NORDYNE - JS3BA-048KA | 115 | 17 | Yes | Yes | 21.1 | 19.7 | 1.4 | 3511E27BCB1D49458A4FB35A4E4B9D51 |  | R22 | Non-TXV |  | 14.78% | 0.85217 | 28.41% | [5 empty] | Non-TXV | 14.78%
Chico | CA | 95926-1939 |  | 2014-05-20 | 2014-05-20 08:53 | 2014-05-20 10:57 | NORDYNE - FS580-024K | 59 | 2.5 | Yes | Yes | 20.5 | 21.7 | -1.2 | 80E2F0094492405989F9C0C766866735 |  | R22 | Non-TXV |  | 4.237% | 0.95763 | 8.143% | [5 empty] | Non-TXV | 4.237%
Stockton | CA | 95207-3131 |  | 2014-05-30 | 2014-05-30 12:37 | 2014-05-30 13:17 | OTHER - 55AW24-106 | 69 | 3.9 | Yes | Yes | 25 | 23.1 | 1.9 | 1159F076D48E43D985F2EF83FBC5E08F |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Chico | CA | 95926-2739 |  | 2014-07-17 | 2014-07-17 12:05 | 2014-07-17 13:25 | TEMPSTAR - TCA024AK1 | 40 | 6 | Yes | Yes | 19.5 | 18.3 | 1.3 | 65BE7ADF986C4C989B6FC1D4FFB2D9EA |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Stockton | CA | 95204-3510 |  | 2014-06-04 | 2014-06-04 17:14 | 2014-06-04 17:32 | YORK - TCGD36S21S2HA | 106 | 11.3 | Yes | Yes | 24 | 21.5 | 2.6 | 95CD4CDB52D84FB79946BE513C4DC88C |  | R22 | TXV |  | 10.66% | 0.8934 | 20.49% | [5 empty] | TXV | 10.66%
Clovis | CA | 93612-0411 |  | 2014-06-12 | 2014-06-12 10:20 | 2014-06-12 10:22 | YORK - D1GH036N04806C | 112 | 3.9 | Yes | Yes | 22.4 | 19.9 | 2.5 | 32A4AC9507AC43878E246971EC196DC8 |  | R22 | Non-TXV |  | 3.482% | 0.96518 | 6.692% | [5 empty] | Non-TXV | 3.482%
Fresno | CA | 93727-1945 |  | 2014-07-10 | 2014-07-10 09:16 | 2014-07-10 09:18 | OTHER - BRCS0361BD | 63 | 11.1 | Yes | Yes | 19.3 | 21.5 | -2.2 | 72970B467A7C4361A1313F5535305D2B |  | R22 | Non-TXV |  | 17.62% | 0.82381 | 33.86% | [5 empty] | Non-TXV | 17.62%
Stockton | CA | 95210-1728 |  | 2014-05-23 | 2014-05-23 12:11 | 2014-05-23 12:29 | TRANE - 2YCC3030A1040AA | 88 | 3.6 | Yes | Yes | 23 | 18 | 5 | C880A6ABDEED4161B1486C3BAA61CE4D |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Stockton | CA | 95205-7787 |  | 2014-06-03 | 2014-06-03 12:34 | 2014-06-03 12:52 | BRYANT - UNK | 54 | 3.6 | Yes | Yes | 26.1 | 20.4 | 5.7 | F9827CC6B0544FAB9F633A32E2D1E1B1 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93702-4037 |  | 2014-05-21 | 2014-05-21 12:45 | 2014-05-21 13:12 | CARRIER - 48DL004 | 70 | 6.8 | Yes | Yes | 26.8 | 20.9 | 5.9 | F36E41CEA5384E7F832C6CA7B770D30D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.714% | 0.90286 | 18.67% | [5 empty] | Non-TXV | 9.714%
Riverbank | CA | 95367-2828 |  | 2014-08-26 | 2014-08-26 12:33 | 2014-08-26 12:49 | RUUD - UNK | 42 | -3 | Yes | Yes | 23.7 | 19.5 | 4.2 | 8C40B10947E848199082D9C69E682357 |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Stockton | CA | 95203-2117 |  | 2014-06-05 | 2014-06-05 14:33 | 2014-06-05 14:33 | PAYNE - PA10JA036-C | 76 | 0 | Yes | Yes | 32.2 | 20.6 | 11.6 | 1856AC42AD2F48C4912E2D5A763BFDF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-1550 |  | 2014-05-28 | 2014-05-28 11:03 | 2014-05-28 11:23 | PAYNE - PY3GNAA30060NA | 98 | 4.6 | Yes | Yes | 22 | 21.2 | 0.8 | 28F233AA7DC74E008E8625F7DF9DD01E |  | R410A | TXV |  | 4.694% | 0.95306 | 9.021% | [5 empty] | TXV | 4.694%
Chico | CA | 95973-7699 |  | 2014-05-27 | 2014-05-27 10:14 | 2014-05-27 10:39 | LENNOX - 13ACD-036-230-02 | 111 | 5 | Yes | Yes | 20 | 20.4 | -0.4 | E3D74A10983A4086BC7193272289F09B |  | R22 | Non-TXV |  | 4.505% | 0.95495 | 8.657% | [5 empty] | Non-TXV | 4.505%
Fresno | CA | 93705-3209 |  | 2014-05-27 | 2014-05-27 12:55 | 2014-05-27 12:57 | OTHER - 7777UNK | 90 | 4.2 | Yes | Yes | 29.1 | 25.2 | 3.9 | 55D10F8E2399493CA9AFA9B49DEB902F |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Tracy | CA | 95376-1845 |  | 2014-05-23 | 2014-05-23 08:11 | 2014-05-23 08:38 | GE - BGTA730B1B | 53 | 2.1 | Yes | Yes | 17.4 | 19.9 | -2.5 | 57EDB106373142AD8B33BA63BE716049 |  | R22 | Non-TXV |  | 3.962% | 0.96038 | 7.615% | [5 empty] | Non-TXV | 3.962%
Los Banos | CA | 93635-9232 |  | 2014-06-10 | 2014-06-10 12:11 | 2014-06-10 12:12 | PAYNE - PA13NR048-E | 184 | 6 | Yes | Yes | 19.9 | 19.9 | 0 | 203245A03BD5404983751B18BAC2D5B2 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Fresno | CA | 93705-2827 |  | 2014-05-28 | 2014-05-28 10:55 | 2014-05-28 10:57 | BDP - 585HJ036060 | 102 | 3.3 | Yes | Yes | 24.8 | 19.5 | 5.3 | 275D6ED44E4641E1890137460F65AC37 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Stockton | CA | 95206-1945 |  | 2014-06-16 | 2014-06-16 15:08 | 2014-06-16 15:34 | PAYNE - 563CN036-B | 122 | -13.8 | Yes | Yes | 22.6 | 20.8 | 1.8 | D37E29B2713F466EB1AF3317808B996D |  | R22 | TXV |  | -11.31% | 1.1131 | 3.168% |  |  |  |  | TXV |  |  | -11.31%
Los Banos | CA | 93635-2700 |  | 2014-07-10 | 2014-07-10 09:21 | 2014-07-10 09:46 | BRYANT - 561CJX036-E | 124 | 11.4 | Yes | Yes | 24.7 | 20.7 | 4 | E4849E3242214AAA9437138F07034E7A |  | R22 | TXV |  | 9.194% | 0.90806 | 17.67% | [5 empty] | TXV | 9.194%
Fresno | CA | 93726-6629 |  | 2014-06-23 | 2014-06-23 14:33 | 2014-06-23 14:34 | RHEEM - RRPL-B036JK08X | 92 | 2.8 | Yes | Yes | 22.1 | 22.1 | 0 | 745B43E8D5914D94BCB409CA54DB2782 |  | R410A | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Fresno | CA | 93711-1690 |  | 2014-07-24 | 2014-07-24 10:45 | 2014-07-24 11:02 | PAYNE - 5A0AN036050 | 96 | 3 | Yes | Yes | 21.2 | 19 | 2.2 | D6C9BEA7D2254A58B624DA6F393255CC |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Coarsegold | CA | 93614-9653 |  | 2014-09-23 | 2014-09-23 11:44 | 2014-09-23 12:16 | ICP - PGAD47D1KG | 215 | 6.4 | Yes | Yes | 23.1 | 19.6 | 3.5 | 1B0EECABAE79456C9AE40F60E07489E1 |  | R22 | Non-TXV |  | 2.977% | 0.97023 | 5.721% | [5 empty] | Non-TXV | 2.977%
Stockton | CA | 95206-4606 |  | 2014-06-11 | 2014-06-11 08:51 | 2014-06-11 09:16 | GMC - VSX130361AA | 85 | 9.4 | Yes | Yes | 17.3 | 18.2 | -0.9 | 05FFF6D8515F4D7B9DD18FE57267FE4B |  | R410A | TXV |  | 11.06% | 0.88941 | 21.25% | [5 empty] | TXV | 11.06%
Fresno | CA | 93727-7983 |  | 2014-08-14 | 2014-08-14 11:06 | 2014-08-14 11:09 | LENNOX - 13ACD-060-230-02 | 214 | 10.1 | Yes | Yes | 20.7 | 19.3 | 1.4 | FB1661AE3C5E491C9A27EC68EA4597C1 |  | R22 | Non-TXV |  | 4.72% | 0.9528 | 9.07% | [5 empty] | Non-TXV | 4.72%
Fresno | CA | 93722-3605 |  | 2014-05-20 | 2014-05-20 14:14 | 2014-05-20 14:31 | CARRIER - UNK | 60 | 6.3 | Yes | Yes | 19.8 | 17.2 | 2.6 | EACDC668B1FF4B239966799C66D868B1 |  | R22 | Non-TXV |  | 10.5% | 0.895 | 20.18% | [5 empty] | Non-TXV | 10.5%
Fresno | CA | 93722-3719 |  | 2014-05-20 | 2014-05-20 14:48 | 2014-05-20 14:49 | BRYANT - 38CKB036320 | 77 | 3 | Yes | Yes | 19.3 | 22 | -2.7 | 14B9F2A3C4B6422BA61C05335E707DF3 |  | R22 | Non-TXV |  | 3.896% | 0.96104 | 7.487% | [5 empty] | Non-TXV | 3.896%
Stockton | CA | 95207-6004 |  | 2014-05-22 | 2014-05-22 11:35 | 2014-05-22 11:53 | BRYANT - 582ANW024040AAAD | 53 | 3 | Yes | Yes | 20.6 | 19.3 | 1.3 | 11FA4822BAF54E919BBD3E1AC68E7E37 |  | R22 | Non-TXV |  | 5.66% | 0.9434 | 10.88% | [5 empty] | Non-TXV | 5.66%
Paradise | CA | 95969-4811 |  | 2014-06-25 | 2014-06-25 13:37 | 2014-06-25 14:13 | DAY & NIGHT - NA | 55 | 7.5 | Yes | Yes | 20 | 20.7 | -0.7 | 70FECA568BB4418790F3529E342D8AE2 |  | R22 | Non-TXV |  | 13.64% | 0.86364 | 26.21% | [5 empty] | Non-TXV | 13.64%
Chico | CA | 95973-0493 |  | 2014-06-30 | 2014-06-30 14:25 | 2014-06-30 14:45 | GIBSON - J55BD-036K | 138 | 6 | Yes | Yes | 23.5 | 21.6 | 1.9 | 8FAA9694E0FC4176AB4343255A910A04 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Ione | CA | 95640-9611 |  | 2014-08-27 | 2014-08-27 13:21 | 2014-08-27 13:41 | DAY & NIGHT - 584ANW030040 | 80 | 3.1 | Yes | Yes | 19.8 | 18.7 | 1.1 | 60B4AD1B0586450BB1B0F0E7E93BA67C |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Chico | CA | 95926-4496 |  | 2014-06-12 | 2014-06-12 13:14 | 2014-06-12 13:31 | DAY & NIGHT - 569CJC30 | 85 | 11 | Yes | Yes | 22 | 20.8 | 1.2 | BD5605A10BD9487BB86274B0808E71ED |  | R22 | Non-TXV |  | 12.94% | 0.87059 | 24.87% | [5 empty] | Non-TXV | 12.94%
Stockton | CA | 95206-3220 |  | 2014-06-20 | 2014-06-20 10:53 | 2014-06-20 11:18 | CARRIER - 38CKC060370 | 131 | 5.2 | Yes | Yes | 25.5 | 19.5 | 6 | A2E3EDF0047642748A94BFF50C724023 |  | R22 | TXV |  | 3.969% | 0.96031 | 7.628% | [5 empty] | TXV | 3.969%
Placerville | CA | 95667-4719 |  | 2014-07-11 | 2014-07-11 10:42 | 2014-07-11 11:08 | OTHER - 565B030 | 72 | 2.2 | Yes | Yes | 17.5 | 20.4 | -2.9 | D2AECC276E424065A4011E3681DBAD76 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Clovis | CA | 93611-0206 |  | 2014-05-30 | 2014-05-30 10:42 | 2014-05-30 10:43 | LENNOX - 12ACB42-4P | 128 | 4.2 | Yes | Yes | 22.5 | 22.5 | 0 | B8B932190A264E4ABAEA726691614208 |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Chico | CA | 95973-0433 |  | 2014-06-20 | 2014-06-20 09:11 | 2014-06-20 09:27 | LENNOX - 12GCS036-50-3PA | 110 | 4 | Yes | Yes | 20 | 21.4 | -1.4 | A48A5A1190194ABA98378A9A726C1674 |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Chowchilla | CA | 93610-2655 |  | 2014-06-04 | 2014-06-04 10:09 | 2014-06-04 10:17 | YORK - DAYP-F036N070A | 108 | 9.3 | Yes | Yes | 17.5 | 20.4 | -2.9 | 9F2AC42FCBBC46DEB354D36349539282 |  | R22 | Non-TXV |  | 8.611% | 0.91389 | 16.55% | [5 empty] | Non-TXV | 8.611%
Chico | CA | 95926-1820 |  | 2014-05-29 | 2014-05-29 10:18 | 2014-05-29 10:55 | DAY & NIGHT - R2H324GKR2418 | 72 | 4.2 | Yes | Yes | 20.4 | 21.1 | -0.7 | 332D3032F6DF4989BAD950FCA34F7343 |  | R22 | TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | TXV | 5.833%
Stockton | CA | 95209-1564 |  | 2014-06-03 | 2014-06-03 13:09 | 2014-06-03 13:26 | HEIL - NAC048AKA1 | 108 | 6.4 | Yes | Yes | 21.1 | 20.4 | 0.7 | C73D3607396347ABBFDA5EF94ED6FB48 |  | R22 | TXV |  | 5.926% | 0.94074 | 11.39% | [5 empty] | TXV | 5.926%
Fresno | CA | 93720-5307 |  | 2014-06-07 | 2014-06-07 10:17 | 2014-06-07 10:41 | LENNOX - 12ACB48-5P | 171 | 5.6 | Yes | Yes | 20.5 | 22 | -1.5 | 5ED37BC2A1C94466ADA2419502FF60F4 |  | R22 | Non-TXV |  | 3.275% | 0.96725 | 6.294% | [5 empty] | Non-TXV | 3.275%
Paradise | CA | 95969-6614 |  | 2014-06-11 | 2014-06-11 12:18 | 2014-06-11 12:37 | RHEEM - NA | 70 | 8.7 | Yes | Yes | 14.8 | 17.5 | -2.7 | 24EB2FD5C261416C80E609D618D710CC |  | R22 | Non-TXV |  | 12.43% | 0.87571 | 23.88% | [5 empty] | Non-TXV | 12.43%
Fresno | CA | 93722-6827 |  | 2014-06-10 | 2014-06-10 17:10 | 2014-06-10 17:44 | CARRIER - N/A | 120 | 3.8 | Yes | Yes | 18.9 | 20.2 | -1.3 | B891455A7A014256AE90E296A9110640 |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Placerville | CA | 95667-5213 |  | 2014-06-03 | 2014-06-03 12:16 | 2014-06-03 12:34 | DAY & NIGHT - N2A34AKA200 | 103 | 3.3 | Yes | Yes | 25.5 | 21.8 | 3.8 | B3A3DD8591C94C8EAE230362DC374399 |  | R22 | Non-TXV |  | 3.204% | 0.96796 | 6.157% | [5 empty] | Non-TXV | 3.204%
Paradise | CA | 95969-2604 |  | 2014-05-22 | 2014-05-22 11:27 | 2014-05-22 19:49 | CARRIER - 38CKC030=330 | 66 | 9.7 | Yes | Yes | 22.8 | 20.4 | 2.4 | 9067E3BD77D64BC7A689F8010995A15F |  | R22 | TXV |  | 14.7% | 0.85303 | 28.24% | [5 empty] | TXV | 14.7%
Stockton | CA | 95209-2712 |  | 2014-05-19 | 2014-05-19 13:38 | 2014-05-19 13:56 | OTHER - UNK | 64 | 2 | Yes | Yes | 26.9 | 21 | 5.9 | CF79C185B8D240EE99BC1C0647D47D6C |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93722-6701 |  | 2014-05-31 | 2014-05-31 11:59 | 2014-05-31 12:25 | BDP - 585HJWO30040 | 68 | 4.8 | Yes | Yes | 24 | 23.6 | 0.4 | 3B55FBA23C634B8796A8FA2AC95F7AEB |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Chico | CA | 95926-2740 |  | 2014-05-16 | 2014-05-16 12:52 | 2014-05-16 13:13 | PAYNE - PA10JA024-C | 64 | 3.1 | Yes | Yes | 20.5 | 20.4 | 0.1 | 37D8D84E454F4AFAAB7A6F63B93B5AFF |  | R22 | TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | TXV | 4.844%
Stockton | CA | 95204-4035 |  | 2014-06-04 | 2014-06-04 12:57 | 2014-06-04 13:14 | CARRIER - 24ABR348A320 | 85 | 9.9 | Yes | Yes | 20 | 20.4 | -0.4 | BD065B64B4DD4C7785D4479EFFA2A7A5 |  | R22 | TXV |  | 11.65% | 0.88353 | 22.38% | [5 empty] | TXV | 11.65%
Clovis | CA | 93612-1916 |  | 2014-06-11 | 2014-06-11 10:21 | 2014-06-11 10:39 | OTHER - RAKB030JAZ | 66 | 12 | Yes | Yes | 21.8 | 20.8 | 1 | 9A5F01602BD747C7B3D8D3E1A6C081D4 |  | R22 | Non-TXV |  | 18.18% | 0.81818 | 34.94% | [5 empty] | Non-TXV | 18.18%
Stockton | CA | 95206-6101 |  | 2014-06-05 | 2014-06-05 11:15 | 2014-06-05 11:39 | RUUD - UAMA-036JBZ | 85 | 3.7 | Yes | Yes | 24.3 | 22.1 | 2.2 | DBF90A875E8449C3AE1D698FD66EE3DC |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Fresno | CA | 93727-7515 |  | 2014-06-09 | 2014-06-09 09:00 | 2014-06-09 09:25 | YORK - D1NA048N11006C | 92 | 4.2 | Yes | Yes | 20 | 22 | -2 | C2C67272832148299BD2FDA21EA07D19 |  | R22 | Non-TXV |  | 4.565% | 0.95435 | 8.773% | [5 empty] | Non-TXV | 4.565%
Stockton | CA | 95209-2344 |  | 2014-06-12 | 2014-06-12 08:58 | 2014-06-12 09:18 | RHEEM - UNK | 64 | -5.3 | Yes | Yes | 25.2 | 19.3 | 5.9 | 0D31794DED9A40FA8CEAD2D78881E750 |  | R22 | Non-TXV |  | -8.281% | 1.0828 | 2.319% |  |  |  |  | Non-TXV |  |  | -8.281%
Stockton | CA | 95204-1401 |  | 2014-06-14 | 2014-06-14 09:50 | 2014-06-14 10:08 | YORK - H2RC042S06HA | 109 | -7.7 | Yes | Yes | 25 | 19.1 | 5.9 | 6E38362D6FF9401998952705C5C880F4 |  | R22 | Non-TXV |  | -7.064% | 1.0706 | 1.978% |  |  |  |  | Non-TXV |  |  | -7.064%
Atwater | CA | 95301-4503 |  | 2014-05-16 | 2014-05-16 11:12 | 2014-05-16 11:13 | COLEMAN - 9536E901 | 64 | 2.9 | Yes | Yes | 21.3 | 21 | 0.3 | CFBDC438B0E3408B81BF70BAACFE1EF8 |  | R22 | Non-TXV |  | 4.531% | 0.95469 | 8.708% | [5 empty] | Non-TXV | 4.531%
Fresno | CA | 93727-8003 |  | 2014-06-06 | 2014-06-06 16:24 | 2014-06-06 16:46 | ICP - GPCM030K060D | 51 | 4.7 | Yes | Yes | 19.6 | 21.7 | -2.1 | 538FE840797B466B8518DC5A805BCC25 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.216% | 0.90784 | 17.71% | [5 empty] | Non-TXV | 9.216%
Fresno | CA | 93726-2646 |  | 2014-06-05 | 2014-06-05 10:31 | 2014-06-05 10:54 | BDP - 585HJW036100 | 84 | 7.6 | Yes | Yes | 22.5 | 21 | 1.5 | 6AE61CDAE5A246059E64ABCBCB87FE95 |  | R22 | Non-TXV |  | 9.048% | 0.90952 | 17.39% | [5 empty] | Non-TXV | 9.048%
Fresno | CA | 93703-4733 |  | 2014-05-22 | 2014-05-22 15:57 | 2014-05-22 16:32 | GOODMAN - PGB036075-1B | 50 | 4.8 | Yes | Yes | 26.5 | 23.1 | 3.4 | F1D13D285FA74FF1B58C3A594A58AE64 |  | R22 | Non-TXV |  | 9.6% | 0.904 | 18.45% | [5 empty] | Non-TXV | 9.6%
Merced | CA | 95341-7507 |  | 2014-05-30 | 2014-05-30 15:20 | 2014-05-30 15:38 | BRYANT - 561CJ048A | 102 | 18.6 | Yes | Yes | 21 | 20.4 | 0.6 | A3EFADD7166F48F1BBADFC6A401C9BAC |  | R22 | TXV |  | 18.24% | 0.81765 | 35.04% | [5 empty] | TXV | 18.24%
Chico | CA | 95926-4072 |  | 2014-08-21 | 2014-08-21 09:28 | 2014-08-21 09:52 | DAY & NIGHT - PGD324040K001C1 | 72 | 3.7 | Yes | Yes | 21.5 | 20.8 | 0.7 | 6C310D2FCDEE4E64AA8589C1D444DE4A |  | R22 | Non-TXV |  | 5.139% | 0.94861 | 9.876% | [5 empty] | Non-TXV | 5.139%
Oakhurst | CA | 93644-8665 |  | 2014-09-18 | 2014-09-18 10:15 | 2014-09-18 10:17 | LENNOX - 12GCS042X755PB | 133 | 25.9 | Yes | Yes | 25 | 21.2 | 3.8 | C5A858522EF748309F9EEE9C3D4E0565 |  | R22 | Non-TXV |  | 19.47% | 0.80526 | 37.42% | [5 empty] | Non-TXV | 19.47%
Kerman | CA | 93630-1731 |  | 2014-06-18 | 2014-06-18 15:23 | 2014-06-18 15:39 | CARRIER - UNK | 56 | 10.5 | Yes | Yes | 24.4 | 22.5 | 1.9 | B0FCBED149A445798188C5F74CD12DA1 |  | R22 | Non-TXV |  | 18.75% | 0.8125 | 36.03% | [5 empty] | Non-TXV | 18.75%
Fresno | CA | 93710-5254 |  | 2014-06-25 | 2014-06-25 15:38 | 2014-06-25 15:39 | TAPPAN - UNK | 64 | 13.7 | Yes | Yes | 26 | 22.6 | 3.4 | A4D01C44BA9A48BB871923C75CB97271 |  | R22 | Non-TXV |  | 21.41% | 0.78594 | 41.14% | [5 empty] | Non-TXV | 21.41%
Fresno | CA | 93723-9228 |  | 2014-05-21 | 2014-05-21 13:03 | 2014-05-21 13:18 | DAY & NIGHT - 585A042100YAC | 90 | 14 | Yes | Yes | 24.4 | 18.7 | 5.7 | 3CADCED166F04D5C8B02FA990781D00F |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Chico | CA | 95973-5610 |  | 2014-06-19 | 2014-06-19 17:48 | 2014-06-19 17:48 | LENNOX - HS29-036-5P | 70 | 0 | Yes | Yes | 20 | 22.6 | -2.6 | F6612E16CB19416F94C8BF86E4BC1121 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1502 |  | 2014-05-28 | 2014-05-28 09:05 | 2014-05-28 09:33 | TRANE - TTP042C100A4 | 140 | 5.3 | Yes | Yes | 23.3 | 20.8 | 2.5 | D8DCAF6023EB41699FA113DB444E9875 |  | R22 | Non-TXV |  | 3.786% | 0.96214 | 7.275% | [5 empty] | Non-TXV | 3.786%
Livingston | CA | 95334-1241 |  | 2014-06-06 | 2014-06-06 11:09 | 2014-06-06 11:29 | ICP - N4A348AKB200 | 112 | 9.6 | Yes | Yes | 23.1 | 17.1 | 6 | 75E70C38BBCD4A72B6EB3B92C4EC290B |  | R410A | TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | TXV | 8.571%
Stockton | CA | 95210-2523 |  | 2014-05-28 | 2014-05-28 09:27 | 2014-05-28 09:44 | OTHER - UNK | 64 | 3.9 | Yes | Yes | 21.7 | 20.1 | 1.6 | CC8102C01BA948468BFC30372B3612B7 |  | R22 | Non-TXV |  | 6.094% | 0.93906 | 11.71% | [5 empty] | Non-TXV | 6.094%
Dinuba | CA | 93618-9357 |  | 2014-07-22 | 2014-07-22 13:36 | 2014-07-22 13:59 | DUCANE - AC12B48 | 111 | 11 | Yes | Yes | 19.3 | 21 | -1.7 | 875292629F2F4C9483DF84AC046FB6E3 |  | R22 | Non-TXV |  | 9.91% | 0.9009 | 19.04% | [5 empty] | Non-TXV | 9.91%
Oakdale | CA | 95361-9563 |  | 2014-06-04 | 2014-06-04 10:53 | 2014-06-04 11:20 | YORK - 561ANJ060-C | 152 | -14.3 | Yes | Yes | 21.6 | 20.4 | 1.2 | 59D303AF07904341986D9936628A14FB |  | R22 | Non-TXV |  | -9.408% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.408%
Stockton | CA | 95215-7302 |  | 2014-06-10 | 2014-06-10 08:30 | 2014-06-10 08:48 | RHEEM - RRKA-A030JK06E | 54 | -3.8 | Yes | Yes | 20.5 | 19.5 | 1.1 | E90E70E7CDA243ABAE6A2FBBA3736004 |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Fresno | CA | 93730-4798 |  | 2014-07-31 | 2014-07-31 12:55 | 2014-07-31 13:16 | LENNOX - 12ACB48-4P | 174 | 5.2 | Yes | Yes | 23.8 | 21.2 | 2.6 | 1416F11305A1430C8E46C0A75E33DDC8 |  | R22 | Non-TXV |  | 2.989% | 0.97011 | 5.743% | [5 empty] | Non-TXV | 2.989%
Stockton | CA | 95206-2416 |  | 2014-06-06 | 2014-06-06 10:34 | 2014-06-06 10:57 | CARRIER - 24ABA348A300 | 132 | 25.2 | Yes | Yes | 27.1 | 21.3 | 5.8 | 150421403BA54AFCB2B5BEF0595DC8F8 |  | R410A | TXV |  | 19.09% | 0.80909 | 36.69% | [5 empty] | TXV | 19.09%
Stockton | CA | 95209-2452 |  | 2014-06-04 | 2014-06-04 18:06 | 2014-06-04 18:24 | YORK - H2RD042S06A | 141 | 16.3 | Yes | Yes | 19.1 | 19.9 | -0.8 | A594315D82A340F8A47D1F6A60D490DC |  | R22 | Non-TXV |  | 11.56% | 0.8844 | 22.22% | [5 empty] | Non-TXV | 11.56%
Stockton | CA | 95206-1729 |  | 2014-06-06 | 2014-06-06 16:01 | 2014-06-06 16:40 | RUUD - WRKAAO36JK06E | 62 | 7.8 | Yes | Yes | 24.2 | 21.3 | 3 | EA1A065EFD874C22A9E8FBCAC8EF8D4F |  | R22 | Non-TXV |  | 12.58% | 0.87419 | 24.18% | [5 empty] | Non-TXV | 12.58%
Newman | CA | 95360-1009 |  | 2014-06-20 | 2014-06-20 08:44 | 2014-06-20 09:04 | YORK - H2RA030S06G | 62 | 5.5 | Yes | Yes | 19.2 | 20.3 | -1.1 | 8E5861D458BD4C978BAD12A4AC5CB8DF |  | R22 | Non-TXV |  | 8.871% | 0.91129 | 17.05% | [5 empty] | Non-TXV | 8.871%
Yuba City | CA | 95991-7540 |  | 2014-05-15 | 2014-05-15 15:32 | 2014-05-15 15:49 | OTHER - UNK | 115 | 12.7 | Yes | Yes | 18.3 | 21 | -2.7 | F9855B07B33B46F1AA8B88C1E3B8A5FB |  | R22 | Non-TXV |  | 11.04% | 0.88957 | 21.22% | [5 empty] | Non-TXV | 11.04%
Olivehurst | CA | 95961-7059 |  | 2014-05-28 | 2014-05-28 15:57 | 2014-05-28 16:17 | PAYNE - PY3GNAA36060NA | 100 | 3.9 | Yes | Yes | 22 | 21.2 | 0.8 | 977E58E3C2654A30A03E61094CA36D25 |  | R410A | TXV |  | 3.9% | 0.961 | 7.495% | [5 empty] | TXV | 3.9%
Fresno | CA | 93704-5630 |  | 2014-06-17 | 2014-06-17 09:10 | 2014-06-17 09:14 | DAY & NIGHT - 565BJ036-A | 80 | 3.1 | Yes | Yes | 18.8 | 20.3 | -1.5 | F4CA03D6AEF84607B5F0592369E44FAC |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Madera | CA | 93637-4903 |  | 2014-05-30 | 2014-05-30 11:11 | 2014-05-30 11:27 | CARRIER - UNK | 88 | 9.3 | Yes | Yes | 23.7 | 18.2 | 5.5 | E9CD11B84B4E434A8A68AE57E7C9DB82 |  | R22 | Non-TXV |  | 10.57% | 0.89432 | 20.31% | [5 empty] | Non-TXV | 10.57%
Fowler | CA | 93625-2656 |  | 2014-07-31 | 2014-07-31 10:30 | 2014-07-31 10:54 | CARRIER - N/A | 90 | 6.7 | Yes | Yes | 18.9 | 21.2 | -2.3 | 525146B95B914B7F9E179E13ABCB9ABC |  | R22 | Non-TXV |  | 7.444% | 0.92556 | 14.31% | [5 empty] | Non-TXV | 7.444%
Fresno | CA | 93703-5229 |  | 2014-06-19 | 2014-06-19 12:44 | 2014-06-19 12:45 | CARRIER - 48KL124300BE | 50 | 2.6 | Yes | Yes | 24.9 | 21.8 | 3.2 | 27A4AAA7392C4F4C8E51C6308425F7B5 |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Stockton | CA | 95215-7302 |  | 2014-06-10 | 2014-06-10 09:00 | 2014-06-10 09:17 | RHEEM - RRKA-A030JK08E | 54 | -4.4 | Yes | Yes | 19.7 | 20.2 | -0.4 | 35F7CAB173884A79B716A02F3E9A43C1 |  | R22 | Non-TXV |  | -8.148% | 1.0815 | 2.282% |  |  |  |  | Non-TXV |  |  | -8.148%
Fresno | CA | 93727-3008 |  | 2014-06-09 | 2014-06-09 14:32 | 2014-06-09 14:53 | BDP - 585CJ030050 | 78 | 4.3 | Yes | Yes | 20.5 | 22.2 | -1.7 | C334400DE80740E0A1694C6F42B6AB4B |  | R22 | Non-TXV |  | 5.513% | 0.94487 | 10.59% | [5 empty] | Non-TXV | 5.513%
Merced | CA | 95340-3955 |  | 2014-05-16 | 2014-05-16 10:18 | 2014-05-16 10:20 | CARRIER - 48GS024040301 | 53 | 6.2 | Yes | Yes | 20.8 | 19.9 | 0.9 | 1D1CA898416B475E9EF7FFB3A04C6746 |  | R22 | Non-TXV |  | 11.7% | 0.88302 | 22.48% | [5 empty] | Non-TXV | 11.7%
Fresno | CA | 93727-5631 |  | 2014-06-05 | 2014-06-05 14:19 | 2014-06-05 14:41 | CARRIER - 38TRA036310 | 102 | 6.6 | Yes | Yes | 22.6 | 22.6 | 0 | 416B927600BE4738AF7D9E13A34E2F4F |  | R22 | TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | TXV | 6.471%
Chico | CA | 95928-5777 |  | 2014-05-19 | 2014-05-19 16:51 | 2014-05-19 16:23 | UNK - UNK | 85 | 7.2 | Yes | Yes | 18.9 | 21.1 | -2.2 | 652DD248C66C4B37AFA8FF0F14546328 |  |  |  |  | 8.471% | 0.91529 | 16.28% | [5 empty] | 0 | 8.471%
Merced | CA | 95340-1343 |  | 2014-05-16 | 2014-05-16 09:24 | 2014-05-16 09:46 | AIRE-FLO - BTD724A100AO | 68 | 7.4 | Yes | Yes | 24 | 18.7 | 5.3 | 9C0C1AD738E043FF9A0987655F764792 |  | R22 | Non-TXV |  | 10.88% | 0.89118 | 20.91% | [5 empty] | Non-TXV | 10.88%
Sheridan | CA | 95681-9746 |  | 2014-08-22 | 2014-08-22 10:47 | 2014-08-22 11:10 | OTHER - N2A336AKA20 | 88 | 3 | Yes | Yes | 18 | 19.3 | -1.3 | D0FA681EF193429B81733FC8785C9A16 |  | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Gustine | CA | 95322-1925 |  | 2014-06-20 | 2014-06-20 09:51 | 2014-06-20 10:08 | HEIL - GPCM036K060F | 68 | 4.7 | Yes | Yes | 27.8 | 22.3 | 5.5 | 5823AF9347194168A0E7172A54F223BA |  | R22 | Non-TXV |  | 6.912% | 0.93088 | 13.28% | [5 empty] | Non-TXV | 6.912%
Stockton | CA | 95210-3248 |  | 2014-05-27 | 2014-05-27 10:39 | 2014-05-27 10:57 | PAYNE - PY3GNAA24060NA | 72 | 4.7 | Yes | Yes | 27.3 | 23.1 | 4.2 | 749801DE093F4F27A1562470BDDA634D |  | R410A | Non-TXV |  | 6.528% | 0.93472 | 12.54% | [5 empty] | Non-TXV | 6.528%
Stockton | CA | 95205-5661 |  | 2014-06-14 | 2014-06-14 08:12 | 2014-06-14 08:29 | ICP - GPCM36K060F | 89 | -5.2 | Yes | Yes | 22 | 18.7 | 3.3 | 2A8F5C9F5EC94D1F8B2F0C187D6D563D |  | R22 | Non-TXV |  | -5.843% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.843%
Stockton | CA | 95204-5212 |  | 2014-06-06 | 2014-06-06 10:00 | 2014-06-06 10:28 | TRANE - UNK | 70 | 4.2 | Yes | Yes | 20.7 | 18.9 | 1.8 | E3C1B43148654CA5B8ADDD2B5264EEAC |  | R410A | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93727-4865 |  | 2014-06-25 | 2014-06-25 07:46 | 2014-06-25 07:47 | BDP - 585HJO24040 | 68 | 6.1 | Yes | Yes | 23.9 | 19.9 | 4 | 924667A07D654755AA4B9618EA0B3280 |  | R22 | Non-TXV |  | 8.971% | 0.91029 | 17.24% | [5 empty] | Non-TXV | 8.971%
Stockton | CA | 95209-1831 |  | 2014-05-19 | 2014-05-19 10:56 | 2014-05-19 11:14 | GOODMAN - GSC130421CB | 108 | 8.3 | Yes | Yes | 23.9 | 19.9 | 4 | 30D5E6394B884D8E9218DB2603D82165 |  | R22 | Non-TXV |  | 7.685% | 0.92315 | 14.77% | [5 empty] | Non-TXV | 7.685%
Stockton | CA | 95212-3400 |  | 2014-06-20 | 2014-06-20 11:38 | 2014-06-20 11:59 | CARRIER - 38CKC042340 | 80 | -6.6 | Yes | Yes | 22.2 | 21 | 1.2 | 05CCBA8B9D3C48B8BDB43DD23A3074C3 |  | R22 | Non-TXV |  | -8.25% | 1.0825 | 2.31% |  |  |  |  | Non-TXV |  |  | -8.25%
Chico | CA | 95973-0491 |  | 2014-05-20 | 2014-05-20 18:55 | 2014-05-20 14:11 | YORK - H2DB024506B | 58 | 5.4 | Yes | Yes | 17.2 | 19.6 | -2.4 | FB7C3C7B28B5429EA2854E2B28121B4E |  | R22 | Non-TXV |  | 9.31% | 0.9069 | 17.89% | [5 empty] | Non-TXV | 9.31%
Marysville | CA | 95901-9399 |  | 2014-05-21 | 2014-05-21 12:39 | 2014-05-21 12:39 | YORK - D1NQ060N09006NXA | 95 | 0 | Yes | Yes | 25.5 | 20.3 | 5.2 | 9B09A2070BEA49728A829B3645B10D83 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-7638 |  | 2014-05-20 | 2014-05-20 13:32 | 2014-05-20 13:49 | LENNOX - HS25-411-1P | 129 | 4.6 | Yes | Yes | 15.5 | 18.2 | -2.7 | E75EF900A43B4DBE8CB65B30096964BA |  | R22 | Non-TXV |  | 3.566% | 0.96434 | 6.853% | [5 empty] | Non-TXV | 3.566%
Fresno | CA | 93703-1611 |  | 2014-05-20 | 2014-05-20 14:47 | 2014-05-20 15:40 | PAYNE - PY3NA048090 | 193 | 5.7 | Yes | Yes | 24 | 18.8 | 5.2 | 62BE4792508C490283CD62713521AF16 |  | R22 | Non-TXV |  | 2.953% | 0.97047 | 5.676% | [5 empty] | Non-TXV | 2.953%
Stockton | CA | 95215-5314 |  | 2014-06-04 | 2014-06-04 12:07 | 2014-06-04 12:26 | RHEEM - RRKA-A030JK08E | 54 | 2.1 | Yes | Yes | 18.5 | 20.4 | -1.9 | 892DE458A6FA403A9431A1E4A275E079 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Pioneer | CA | 95666-9500 |  | 2014-07-31 | 2014-07-31 08:51 | 2014-07-31 09:10 | RUUD - UNK | 110 | 4.1 | Yes | Yes | 26 | 21 | 5 | 5392135412BB4BC08D4642079BC779AA |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.163% | [5 empty] | Non-TXV | 3.727%
Stockton | CA | 95207-4514 |  | 2014-05-21 | 2014-05-21 14:00 | 2014-05-21 14:18 | TRANE - TTP042C100A4 | 140 | 4.4 | Yes | Yes | 25.7 | 19.7 | 6 | D15F7ABA54DC4569B1D983799BEC8809 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Fresno | CA | 93703-5229 |  | 2014-07-08 | 2014-07-08 14:40 | 2014-07-08 15:00 | CARRIER - 48KL124300BF | 50 | 2.2 | Yes | Yes | 23.5 | 20.5 | 3.1 | 723685804D9E498383C27919B9C6C828 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Fresno | CA | 93704-6128 |  | 2014-08-08 | 2014-08-08 14:24 | 2014-08-08 14:25 | YORK - UNK | 68 | 7.8 | Yes | Yes | 21.8 | 18.5 | 3.3 | ABA64475E0004B08A936DE23AAB7FCA0 |  | R22 | Non-TXV |  | 11.47% | 0.88529 | 22.04% | [5 empty] | Non-TXV | 11.47%
Stockton | CA | 95215-1736 |  | 2014-06-20 | 2014-06-20 10:02 | 2014-06-20 10:21 | PAYNE - PA13NR036-E | 98 | 4.2 | Yes | Yes | 18.2 | 19.3 | -1.1 | 642BFA782F3C4D0AAFE74E60E833FEE8 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Fresno | CA | 93705-2124 |  | 2014-08-13 | 2014-08-13 09:15 | 2014-08-13 09:46 | BRYANT - 582ANW024040 | 53 | 1.6 | Yes | Yes | 17.8 | 20.4 | -2.6 | D0E70319856A47358D5671F35E9DBFEA |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Del Rey | CA | 93616-0000 |  | 2014-09-25 | 2014-09-25 09:50 | 2014-09-25 10:11 | LENNOX - 13GCSXA-48-138-230-1A | 189 | 6.9 | Yes | Yes | 22 | 21 | 1 | B46F3B77C5604DC0A3FB1B4B8FDEC331 |  | R410A | TXV |  | 3.651% | 0.96349 | 7.016% | [5 empty] | TXV | 3.651%
Fresno | CA | 93711-2627 |  | 2014-06-07 | 2014-06-07 11:06 | 2014-06-07 11:34 | PAYNE - 30/80 YAC-108C | 67 | 4.2 | Yes | Yes | 21.8 | 22 | -0.2 | 891B981ACF1B4BC8BAEC7BB36978E890 |  | R22 | Non-TXV |  | 6.269% | 0.93731 | 12.05% | [5 empty] | Non-TXV | 6.269%
Yuba City | CA | 95993-8621 |  | 2014-05-28 | 2014-05-28 09:48 | 2014-05-28 10:22 | LENNOX - HS26-042-2P | 107 | 7.4 | Yes | Yes | 22 | 20.9 | 1.1 | 4EF60D4C0D8F494BB58EB3782D1F9C16 |  | R22 | Non-TXV |  | 6.916% | 0.93084 | 13.29% | [5 empty] | Non-TXV | 6.916%
Yuba City | CA | 95993-8621 |  | 2014-05-28 | 2014-05-28 10:23 | 2014-05-28 10:44 | HEIL - H4A360GKA100 | 145 | 5.8 | Yes | Yes | 20 | 22 | -2 | 7FAC27BDD0F54C6CA1A5BBF117A2F0FA |  | R410A | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Merced | CA | 95340-3323 |  | 2014-07-01 | 2014-07-01 14:47 | 2014-07-01 14:47 | RHEEM - RRNA-A036JK08X | 99 | 3.1 | Yes | Yes | 18 | 19.5 | -1.5 | E37C6421017C4002997440B0B48B1F28 | Add refrigerant: 3.1 oz | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Stockton | CA | 95206-5524 |  | 2014-06-05 | 2014-06-05 10:05 | 2014-06-05 10:25 | BRYANT - 561CJX042000ABAA | 93 | 4.6 | Yes | Yes | 24.2 | 20.4 | 3.8 | F86F3EF06DB14795A4EA26714250C8BB |  | R22 | TXV |  | 4.946% | 0.95054 | 9.506% | [5 empty] | TXV | 4.946%
Fresno | CA | 93705-0602 |  | 2014-05-22 | 2014-05-22 09:13 | 2014-05-22 09:38 | ICP - GPFMGOK100E | 133 | 10.1 | Yes | Yes | 22.4 | 18.2 | 4.2 | 15320791268C42F4A3BB5EC3190F3FE2 |  | R22 | Non-TXV |  | 7.594% | 0.92406 | 14.59% | [5 empty] | Non-TXV | 7.594%
Stockton | CA | 95206-6343 |  | 2014-06-06 | 2014-06-06 12:07 | 2014-06-06 12:33 | GOODMAN - CLJ42-1 | 85 | 4.8 | Yes | Yes | 21.4 | 21.5 | -0.1 | 9D2CA54F815C47BE8538C0FED2DD599B |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Chico | CA | 95973-0489 |  | 2014-06-10 | 2014-06-10 12:07 | 2014-06-10 12:29 | OTHER - 2SCU13LB124R1 | 72 | 9.6 | Yes | Yes | 22.3 | 21.2 | 1.1 | 5156DFEB59D6478A830D1D700BC64B9A |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Kingsburg | CA | 93631-1741 |  | 2014-08-20 | 2014-08-20 17:03 | 2014-08-20 17:26 | COLEMAN - BRCQ030B | 48 | 2.7 | Yes | Yes | 22.4 | 21.5 | 0.9 | 7DE9D9F996EE4BE58707AF2C707E51BF |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Chico | CA | 95928-6898 |  | 2014-07-02 | 2014-07-02 12:59 | 2014-07-02 13:16 | CARRIER - 24ABA324A310 | 65 | 3.4 | Yes | Yes | 17 | 18.9 | -1.9 | DD8EB92EF9DE4C1CBABFA27148CC10F3 |  | R410A | TXV |  | 5.231% | 0.94769 | 10.05% | [5 empty] | TXV | 5.231%
Fresno | CA | 93705-1550 |  | 2014-06-20 | 2014-06-20 10:54 | 2014-06-20 10:54 | CARRIER - 38CKC048300 | 102 | 0 | Yes | Yes | 22 | 20.8 | 1.2 | 916868CC01F546DFA94607CD54492AB8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-7840 |  | 2014-05-27 | 2014-05-27 08:22 | 2014-05-27 20:41 | DAY & NIGHT - 690ANX01800ABAA | 72 | 4.5 | Yes | Yes | 17.4 | 20.1 | -2.6 | 5F4B4B7118B7458A82EBD19BF0B6F117 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fresno | CA | 93726-6201 |  | 2014-07-01 | 2014-07-01 12:10 | 2014-07-01 12:28 | ALLEGIANCE - 7A0036A100A1 | 95 | 5.7 | Yes | Yes | 22.2 | 22 | 0.2 | BFFDE8E520734D7198F4B6EE0AE663AE |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93720-4093 |  | 2014-06-04 | 2014-06-04 10:03 | 2014-06-04 10:19 | OTHER - TCJF60S41S4A | 84 | 5.7 | Yes | Yes | 21 | 18.1 | 2.9 | 9E8A7AA23D59422AA7AB23E808905365 |  | R410A | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Yuba City | CA | 95991-6944 |  | 2014-05-28 | 2014-05-28 08:10 | 2014-05-28 08:29 | TRANE - 4TTX4048B1000AA | 127 | 4.6 | Yes | Yes | 25 | 20.6 | 4.4 | D7F983FA1909418CA9ABB5E771199D41 |  | R410A | TXV |  | 3.622% | 0.96378 | 6.961% | [5 empty] | TXV | 3.622%
Tracy | CA | 95376-4527 |  | 2014-06-02 | 2014-06-02 10:11 | 2014-06-02 10:36 | DAY & NIGHT - 59042000ABAA1ANX | 85 | 18 | Yes | Yes | 24.6 | 22.1 | 2.5 | BA317C48371548CEAC44D9011E47ACB6 |  | R22 | Non-TXV |  | 21.18% | 0.78824 | 40.7% | [5 empty] | Non-TXV | 21.18%
Fresno | CA | 93720-2070 |  | 2014-06-04 | 2014-06-04 09:07 | 2014-06-04 09:23 | BDP - 585CJ036075 | 84 | 8.8 | Yes | Yes | 23.2 | 19.4 | 3.8 | 3B47C58D27A54E9E98CF0912B9152912 |  | R22 | Non-TXV |  | 10.48% | 0.89524 | 20.13% | [5 empty] | Non-TXV | 10.48%
Fresno | CA | 93711-1525 |  | 2014-05-29 | 2014-05-29 11:55 | 2014-05-29 12:12 | AIRE-FLO - 588ANW036060ACAF | 67 | 8.2 | Yes | Yes | 20 | 14.1 | 5.9 | 51C87D38B667405B853DD35196EEE6C8 |  | R22 | Non-TXV |  | 12.24% | 0.87761 | 23.52% | [5 empty] | Non-TXV | 12.24%
Fresno | CA | 93725-9509 |  | 2014-06-17 | 2014-06-17 10:36 | 2014-06-17 10:47 | PAYNE - PH13NB048 | 119 | 9.2 | Yes | Yes | 22.6 | 21.5 | 1.1 | CDACED6A655E4D7796BED2431C473025 |  | R410A | Non-TXV |  | 7.731% | 0.92269 | 14.86% | [5 empty] | Non-TXV | 7.731%
Chico | CA | 95928-6680 |  | 2014-06-20 | 2014-06-20 12:13 | 2014-06-20 12:29 | DAY & NIGHT - 585EJ024050 | 54 | 3 | Yes | Yes | 21 | 19 | 2 | 96A362B2B23C411DA6F8EBCDC2788BA7 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Oroville | CA | 95966-3970 |  | 2014-05-27 | 2014-05-27 12:20 | 2014-05-27 12:36 | TRANE - TTD736B100 | 86 | 2.8 | Yes | Yes | 26 | 23.2 | 2.8 | 998ABF94D3634251949E97E5395E5AD0 |  | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
Madera | CA | 93637-6149 |  | 2014-05-30 | 2014-05-30 13:42 | 2014-05-30 13:58 | BRYANT - 582ANW036060NBAF | 68 | 17.1 | Yes | Yes | 25.3 | 20.8 | 4.5 | C48B0B6A31B9489090DBF1252C380238 |  | R22 | Non-TXV |  | 25.15% | 0.74853 | 48.33% | [5 empty] | Non-TXV | 25.15%
Fresno | CA | 93727-3248 |  | 2014-06-12 | 2014-06-12 17:03 | 2014-06-12 17:23 | CARRIER - 48GX-036090301 | 82 | 4.2 | Yes | Yes | 22.1 | 21 | 1.1 | 350354A37ACE4E34867FA28B01E0F54C |  | R22 | Non-TXV |  | 5.122% | 0.94878 | 9.843% | [5 empty] | Non-TXV | 5.122%
Fresno | CA | 93727-5403 |  | 2014-07-16 | 2014-07-16 11:13 | 2014-07-16 11:14 | OTHER - 7777UNK | 64 | 2.3 | Yes | Yes | 16.6 | 19.5 | -2.9 | 3B9788BDB3D044F7AADC0F99B7388238 |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
Madera | CA | 93637-5418 |  | 2014-09-23 | 2014-09-23 16:35 | 2014-09-23 16:56 | OTHER - UNK | 72 | 2.2 | Yes | Yes | 22.2 | 19.3 | 2.9 | 535166FC181D4089A58E8A0E13B1D1F4 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Stockton | CA | 95207-7847 |  | 2014-06-18 | 2014-06-18 11:15 | 2014-06-18 11:31 | TRANE - YCC024F1L0BF | 85 | 7.3 | Yes | Yes | 20.8 | 20.9 | -0.1 | 6E126BA954A3433699C3974EF390FE19 |  | R22 | Non-TXV |  | 8.588% | 0.91412 | 16.5% | [5 empty] | Non-TXV | 8.588%
Madera | CA | 93637-6150 |  | 2014-06-02 | 2014-06-02 08:44 | 2014-06-02 09:03 | OTHER - RRNAB036JK06X | 83 | 9.2 | Yes | Yes | 20.3 | 14.4 | 5.9 | 4AF735D641DE4569BB196CE9B821E682 |  | R22 | Non-TXV |  | 11.08% | 0.88916 | 21.3% | [5 empty] | Non-TXV | 11.08%
Merced | CA | 95340-3317 |  | 2014-05-16 | 2014-05-16 10:55 | 2014-05-16 11:02 | GOODMAN - PGB0360751 | 60 | 14.4 | Yes | Yes | 23.9 | 19.3 | 4.7 | 8F5641994A8E47AFB81F74A498E6AED4 |  | R22 | Non-TXV |  | 24% | 0.76 | 46.12% | [5 empty] | Non-TXV | 24%
Fresno | CA | 93720-2367 |  | 2014-06-19 | 2014-06-19 10:27 | 2014-06-19 11:00 | TEMPSTAR - CA3048VKA1 | 120 | 3.6 | Yes | Yes | 18.8 | 21 | -2.2 | 85815D4486AD48BE8CC53CF7211833FF |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Clovis | CA | 93612-2324 |  | 2014-06-02 | 2014-06-02 16:30 | 2014-06-02 16:57 | ICP - PGAB30CK1K1 | 74 | 7.9 | Yes | Yes | 23.9 | 21 | 2.9 | 5E1DC933AE31413B8411932685893F93 |  | R22 | Non-TXV |  | 10.68% | 0.89324 | 20.52% | [5 empty] | Non-TXV | 10.68%
Fresno | CA | 93727-6717 |  | 2014-06-06 | 2014-06-06 11:33 | 2014-06-06 11:56 | OTHER - N/A | 120 | 10.2 | Yes | Yes | 28.6 | 22.6 | 6 | F2BC91CCD6BF4CBDA0DDD0DDED0C1740 |  | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Stockton | CA | 95212-3042 |  | 2014-06-06 | 2014-06-06 10:11 | 2014-06-06 10:29 | CARRIER - 38CK036350 | 70 | -4.1 | Yes | Yes | 22 | 21 | 1 | 89EC5027697E46E5AC91BF5A10F83E6A |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Lathrop | CA | 95330-8538 |  | 2014-07-17 | 2014-07-17 08:09 | 2014-07-17 08:32 | CARRIER - 24ABA342A310 | 116 | 13.2 | Yes | Yes | 23.7 | 19.6 | 4.1 | E716F55CDDB545B9B740CBA6F2F7BC63 |  | R410A | TXV |  | 11.38% | 0.88621 | 21.87% | [5 empty] | TXV | 11.38%
Red Bluff | CA | 96080-3083 |  | 2014-05-28 | 2014-05-28 15:13 | 2014-05-28 15:33 | RHEEM - NA | 50 | 9.6 | Yes | Yes | 21 | 21.3 | -0.3 | 607A8B16B10B43F4BB799769D344A813 |  | R22 | Non-TXV |  | 19.2% | 0.808 | 36.9% | [5 empty] | Non-TXV | 19.2%
Red Bluff | CA | 96080-2343 |  | 2014-06-17 | 2014-06-17 12:53 | 2014-06-17 13:33 | DAY & NIGHT - 567C024RC | 60 | 6.3 | Yes | Yes | 24 | 20.7 | 3.3 | 2BD99556C0E44674B1B67D8D10F231AD |  | R22 | Non-TXV |  | 10.5% | 0.895 | 20.18% | [5 empty] | Non-TXV | 10.5%
Stockton | CA | 95204-2526 |  | 2014-06-04 | 2014-06-04 11:55 | 2014-06-04 12:14 | LENNOX - GCS26X-042-100-2PA | 133 | 15.6 | Yes | Yes | 20.8 | 19.9 | 0.9 | 96A67FF4716348939F25F8FE513F7426 |  | R22 | Non-TXV |  | 11.73% | 0.88271 | 22.54% | [5 empty] | Non-TXV | 11.73%
Stockton | CA | 95205-8427 |  | 2014-06-10 | 2014-06-10 12:25 | 2014-06-10 12:43 | DAY & NIGHT - 588ANW060080ADAG | 112 | -6.6 | Yes | Yes | 21.5 | 17.6 | 3.9 | 32E0719D4D37402CAF94B70789E6C0B8 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Red Bluff | CA | 96080-2343 |  | 2014-06-21 | 2014-06-21 10:22 | 2014-06-21 10:49 | DAY & NIGHT - 567C024RCV | 60 | 4.4 | Yes | Yes | 18.6 | 21.4 | -2.8 | 23BD472DA7FD428FA402B566766DB9A9 |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Stockton | CA | 95207-7849 |  | 2014-06-05 | 2014-06-05 13:23 | 2014-06-05 13:40 | TRANE - YCC024F1LOBF | 64 | 3.9 | Yes | Yes | 22.6 | 22.1 | 0.5 | 8A27F18DAC8C465BB2F012E0074B247D |  | R22 | Non-TXV |  | 6.094% | 0.93906 | 11.71% | [5 empty] | Non-TXV | 6.094%
Olivehurst | CA | 95961-7435 |  | 2014-05-28 | 2014-05-28 15:02 | 2014-05-28 15:02 | OTHER - 113ANA036-1E | 83 | 0 | Yes | Yes | 21 | 23.1 | -2.1 | 521974D1DD6E4E3C9EC862B84F78C8AD |  | R410A | TXV |  | 0% | 1 | 0%
Riverbank | CA | 95367-2230 |  | 2014-05-20 | 2014-05-20 09:18 | 2014-05-20 09:39 | YORK - D5YS024N04506A | 70 | -4.9 | Yes | Yes | 20.1 | 20.9 | -0.8 | E281A96430D24EE6AF9E50FEAA6911F3 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93705-3416 |  | 2014-06-25 | 2014-06-25 08:11 | 2014-06-25 08:12 | GOODMAN - GPG1348090M41AD | 125 | 3.8 | Yes | Yes | 23.2 | 19.4 | 3.8 | 2854019925D1499B9E4B20F7BCCC6DE9 |  | R410A | Non-TXV |  | 3.04% | 0.9696 | 5.842% | [5 empty] | Non-TXV | 3.04%
Fresno | CA | 93725-1505 |  | 2014-06-18 | 2014-06-18 10:48 | 2014-06-18 11:32 | BDP - 585A036080 | 60 | 3.7 | Yes | Yes | 21.2 | 22.6 | -1.4 | 3BD64D39DAFA4994B87136CB15935FE0 |  | R22 | Non-TXV |  | 6.167% | 0.93833 | 11.85% | [5 empty] | Non-TXV | 6.167%
Nevada City | CA | 95959-9348 |  | 2014-05-23 | 2014-05-23 09:27 | 2014-05-23 09:54 | OTHER - UNK | 95 | 3 | Yes | Yes | 24 | 21.8 | 2.2 | 3E496480A5CA4E5A8A772D7A483E685E |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Rocklin | CA | 95765-4334 |  | 2014-06-28 | 2014-06-28 11:28 | 2014-06-28 12:14 | OTHER - CE60-1EB | 167 | 6.1 | Yes | Yes | 24 | 21 | 3 | 0FC617D6FDA64A1BAFBA5796AEDE783E |  | R22 | Non-TXV |  | 3.653% | 0.96347 | 7.02% | [5 empty] | Non-TXV | 3.653%
Coalinga | CA | 93210-2732 |  | 2014-08-11 | 2014-08-11 09:28 | 2014-08-11 09:48 | OTHER - PGD336060K001C1 | 100 | 3.6 | Yes | Yes | 25.1 | 19.5 | 5.6 | FD3DAAF1ED3747F98F25F2034416FB98 |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Stockton | CA | 95207-6041 |  | 2014-06-06 | 2014-06-06 11:26 | 2014-06-06 11:44 | PAYNE - PY3GNAA24040NA | 72 | 5.5 | Yes | Yes | 23.1 | 19.7 | 3.5 | A5340AFCEFC545C4853B77846680982A |  | R410A | Non-TXV |  | 7.639% | 0.92361 | 14.68% | [5 empty] | Non-TXV | 7.639%
Kerman | CA | 93630-1371 |  | 2014-06-18 | 2014-06-18 09:10 | 2014-06-18 09:27 | CARRIER - 24ABB336A0031010 | 83 | 11.5 | Yes | Yes | 21 | 18.5 | 2.5 | CFF4C04BC3EF43B2BA04885B00F84C42 |  | R410A | TXV |  | 13.86% | 0.86145 | 26.63% | [5 empty] | TXV | 13.86%
Riverbank | CA | 95367-3138 |  | 2014-05-20 | 2014-05-20 12:55 | 2014-05-20 13:22 | OTHER - PGC024K040A | 58 | -5.5 | Yes | Yes | 21.3 | 20.2 | 1.1 | 4557D500B8EC48699CBED79E478F09B5 |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Stockton | CA | 95207-7888 |  | 2014-05-29 | 2014-05-29 13:27 | 2014-05-29 14:06 | PAYNE - PY3GNAA24060NA | 72 | -4.2 | Yes | Yes | 25.7 | 20.1 | 5.6 | A4B442E8CEAF42FAA2B6DEAE98900400 |  | R410A | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95207-7847 |  | 2014-06-11 | 2014-06-11 12:49 | 2014-06-11 13:09 | TRANE - YCC024F1LOBF | 64 | -3.8 | Yes | Yes | 19.1 | 19 | 0.1 | 4290A6E05C5745C292B84A4C121D3097 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Stockton | CA | 95206-6427 |  | 2014-06-06 | 2014-06-06 13:10 | 2014-06-06 13:47 | CARRIER - 38CKC042350 | 93 | -13 | Yes | Yes | 23.6 | 21 | 2.6 | CF2FC215F17247FE97CBE9F83AA7BA6D |  | R22 | TXV |  | -13.98% | 1.1398 | 3.915% |  |  |  |  | TXV |  |  | -13.98%
Stockton | CA | 95206-2218 |  | 2014-06-13 | 2014-06-13 14:24 | 2014-06-13 14:42 | RHEEM - RRMA-A036JK08X | 85 | 7.5 | Yes | Yes | 20.9 | 20.5 | 0.4 | 4667CC1BD1CF4D1AB2DBBCAE3F910212 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Fresno | CA | 93725-1642 |  | 2014-06-21 | 2014-06-21 09:42 | 2014-06-21 09:42 | BDP - 585B030075YACR | 82 | 14.8 | Yes | Yes | 16.8 | 21.5 | -4.7 | 24CCC4C4B6CA4DE48E87E45DDA8AEE88 | Add refrigerant: 14.8 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 18.05% | 0.81951 | 34.69% | [5 empty] | Non-TXV | 18.05%
Fresno | CA | 93720-2612 |  | 2014-07-29 | 2014-07-29 10:31 | 2014-07-29 10:52 | GOODMAN - GPG153709041AA | 85 | 4.7 | Yes | Yes | 27.7 | 22 | 5.7 | 8C9B8B05AA1047D88194F4EB39FEDED2 |  | R410A | TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | TXV | 5.529%
Fresno | CA | 93702-1320 |  | 2014-05-20 | 2014-05-20 09:45 | 2014-05-20 10:00 | YORK - D1NZ030N05606A | 117 | 4.4 | Yes | Yes | 17 | 19.5 | -2.5 | 47719B9780924A7AA25C41FA6DC8202B |  | R410A | TXV |  | 3.761% | 0.96239 | 7.227% | [5 empty] | TXV | 3.761%
Rocklin | CA | 95765-4780 |  | 2014-06-09 | 2014-06-09 12:03 | 2014-06-09 12:20 | YORK - H1RA048S06D | 117 | 3.5 | Yes | Yes | 17 | 19.9 | -2.9 | B644388D4A33443BA0B560236DB17CF2 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Stockton | CA | 95206-6446 |  | 2014-06-07 | 2014-06-07 11:57 | 2014-06-07 12:19 | GOODMAN - CKL49-1A | 85 | 8.5 | Yes | Yes | 20.6 | 19.8 | 0.8 | FA78AD4DE48E47D799C17AE70DC8E6E4 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95215-5405 |  | 2014-06-10 | 2014-06-10 11:18 | 2014-06-10 11:35 | GIBSON - JS3BA-048KA | 115 | -6.8 | Yes | Yes | 23.6 | 19.9 | 3.7 | DA86A2DF58754A25A27210E1AB040377 |  | R22 | Non-TXV |  | -5.913% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.913%
Stockton | CA | 95206-3736 |  | 2014-06-16 | 2014-06-16 12:52 | 2014-06-16 13:12 | PAYNE - PY1PNB030060AAAA | 55 | -4.8 | Yes | Yes | 25.2 | 22 | 3.2 | F3AAA35F6C2A44548213EAE5350227CB |  | R22 | TXV |  | -8.727% | 1.0873 | 2.444% |  |  |  |  | TXV |  |  | -8.727%
Fresno | CA | 93722-6711 |  | 2014-05-31 | 2014-05-31 11:28 | 2014-05-31 11:45 | BDP - 585GJW030040 | 58 | 6.6 | Yes | Yes | 20.2 | 20.9 | -0.7 | 03440E1932334FF7B06C8F74F6B9FF11 |  | R22 | Non-TXV |  | 11.38% | 0.88621 | 21.87% | [5 empty] | Non-TXV | 11.38%
Madera | CA | 93637-5710 |  | 2014-07-22 | 2014-07-22 13:17 | 2014-07-22 13:34 | UNITARY PRODUCTS GROUP - GCGD03S21S2A | 55 | 1.7 | Yes | Yes | 17.6 | 17 | 0.6 | E47714D8577C4C8281E5D96B11724B7A |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Lodi | CA | 95242-9420 |  | 2014-06-06 | 2014-06-06 16:52 | 2014-06-06 16:52 | INTERTHERM - S5BD-042K | 170 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | ABE8D708C66C437BB8516E88447C1D42 | Liquid Temperature cannot be less than outdoor air temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2518 |  | 2014-07-09 | 2014-07-09 11:25 | 2014-07-09 12:44 | PAYNE - 585B036075YACR | 60 | -3.5 | Yes | Yes | 23 | 19.9 | 3.1 | 2A4C8A0E9CBF435C9B99B722F67B9FCD |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95207-7846 |  | 2014-06-11 | 2014-06-11 12:20 | 2014-06-11 12:47 | TRANE - YCC024F1LOBF | 64 | 1.9 | Yes | Yes | 16.5 | 18.8 | -2.3 | E159FFB2825E4D74A5701A3EF9B2E72C |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Lincoln | CA | 95648-8309 |  | 2014-05-20 | 2014-05-20 09:26 | 2014-05-20 09:44 | OTHER - 38BRC036320 | 100 | 3.2 | Yes | Yes | 18 | 20.9 | -2.9 | B8962C007D154D7797CFEA8A1FC876DA |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Paradise | CA | 95969-4765 |  | 2014-05-23 | 2014-05-23 08:53 | 2014-05-23 09:17 | DAY & NIGHT - PGP330060K001C1 | 98 | 4 | Yes | Yes | 22.5 | 19.3 | 3.2 | F92F43B73DBB4B669B6DBF03DAA11FE1 |  | R410A | Non-TXV |  | 4.082% | 0.95918 | 7.844% | [5 empty] | Non-TXV | 4.082%
Stockton | CA | 95215-5234 |  | 2014-08-14 | 2014-08-14 14:14 | 2014-08-14 14:39 | BDP - 588ANW030060ADAD | 53 | -5 | Yes | Yes | 18.4 | 20.8 | -2.4 | AADBAD8E264F49C9A1D05D18F7C239A0 |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Merced | CA | 95341-9518 |  | 2014-07-07 | 2014-07-07 22:17 | 2014-07-07 22:20 | ARCOAIRE - 7777UNK | 86 | 2.7 | Yes | Yes | 23.9 | 19.9 | 4 | 63AF395772F84F698D55F9B8D791EA3B |  | R22 | Non-TXV |  | 3.14% | 0.9686 | 6.033% | [5 empty] | Non-TXV | 3.14%
Chowchilla | CA | 93610-3058 |  | 2014-06-04 | 2014-06-04 09:36 | 2014-06-04 09:37 | OTHER - 7777UNK | 85 | 3.7 | Yes | Yes | 20.2 | 19.4 | 0.9 | 052FEE0E64F34A5A8A714A3E702DFF7E |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Fresno | CA | 93703-3348 |  | 2014-05-19 | 2014-05-19 17:49 | 2014-05-19 19:28 | PAYNE - 580ANW036060 | 96 | 8 | Yes | Yes | 29.1 | 23.2 | 5.9 | EBF7850247A042559A266F295371C1C6 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Stockton | CA | 95215-9167 |  | 2014-06-04 | 2014-06-04 14:15 | 2014-06-04 14:34 | BRYANT - 561CJ060-A | 158 | 5 | Yes | Yes | 26.5 | 20.9 | 5.6 | 4E94FF2AD9D94E5A919E38878464DC3C |  | R22 | Non-TXV |  | 3.165% | 0.96835 | 6.082% | [5 empty] | Non-TXV | 3.165%
Paso Robles | CA | 93446-5044 |  | 2014-06-23 | 2014-06-23 14:27 | 2014-06-23 14:44 | CARRIER - 38EN024310SM | 61 | 11.7 | Yes | Yes | 18.6 | 20.2 | -1.6 | 810EDE2C9C174F6F86BE63E31F4D4A55 |  | R22 | Non-TXV |  | 19.18% | 0.8082 | 36.86% | [5 empty] | Non-TXV | 19.18%
Tracy | CA | 95377-8885 |  | 2014-05-29 | 2014-05-29 14:02 | 2014-05-29 14:23 | RHEEM - RRKA-A036JK06X | 85 | 5.2 | Yes | Yes | 25.3 | 22.6 | 2.7 | 908A0749D5BE4D47AC56924EC004B29F |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Grass Valley | CA | 95949-8953 |  | 2014-09-22 | 2014-09-22 17:16 | 2014-09-22 17:32 | CARRIER - 38TH048320 | 118 | 9.8 | Yes | Yes | 21.6 | 20.4 | 1.2 | A4E90CCDE3D44E2ABEA0131B76F256B3 |  | R22 | Non-TXV |  | 8.305% | 0.91695 | 15.96% | [5 empty] | Non-TXV | 8.305%
Oakdale | CA | 95361-4165 |  | 2014-05-19 | 2014-05-19 10:03 | 2014-05-19 10:21 | RHEEM - RRNL-B024JK06X | 85 | 4 | Yes | Yes | 22.5 | 21.2 | 1.3 | 418C16646134436C92EAD11B753DFC8E |  | R410A | TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | TXV | 4.706%
Sheridan | CA | 95681-9785 |  | 2014-06-13 | 2014-06-13 08:13 | 2014-06-13 08:32 | CARRIER - 38TRA042310 | 141 | 4.1 | Yes | Yes | 23 | 19.5 | 3.5 | A1473CBC2A434FC182F8FFF479857FC6 |  | R22 | Non-TXV |  | 2.908% | 0.97092 | 5.588% | [5 empty] | Non-TXV | 2.908%
Clovis | CA | 93612-3877 |  | 2014-06-11 | 2014-06-11 11:41 | 2014-06-11 12:07 | BRYANT - 582ANW024060NAAD | 53 | 11.7 | Yes | Yes | 24.5 | 21.2 | 3.3 | 89B2289156A2493B9CA523C8CC129918 |  | R22 | Non-TXV |  | 22.08% | 0.77925 | 42.42% | [5 empty] | Non-TXV | 22.08%
Fresno | CA | 93727-7923 |  | 2014-07-18 | 2014-07-18 12:39 | 2014-07-18 12:40 | PAYNE - PY3GNAA30060NA | 98 | 3.9 | Yes | Yes | 22.6 | 19.3 | 3.3 | 044793F654804F048724A4957EB5A551 |  | R410A | Non-TXV |  | 3.98% | 0.9602 | 7.648% | [5 empty] | Non-TXV | 3.98%
Oakdale | CA | 95361-4165 |  | 2014-05-19 | 2014-05-19 10:23 | 2014-05-19 10:42 | RHEEM - RRNL-B024JK06X | 85 | 3.9 | Yes | Yes | 21.4 | 20.3 | 1.1 | 75E2DDF6094B478DA410D42D9F8A4B8E |  | R410A | TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | TXV | 4.588%
Merced | CA | 95340-1701 |  | 2014-05-16 | 2014-05-16 12:46 | 2014-05-16 12:48 | AMERICAN STANDARD - YCC048F1MOBE | 100 | 19.6 | Yes | Yes | 21 | 20.2 | 0.8 | 742F0091E1AA4135ADC575DD2A2F6F21 |  | R22 | Non-TXV |  | 19.6% | 0.804 | 37.67% | [5 empty] | Non-TXV | 19.6%
Fresno | CA | 93727-4708 |  | 2014-06-25 | 2014-06-25 12:45 | 2014-06-25 12:46 | OTHER - 7777UNK | 60 | 3.1 | Yes | Yes | 23.3 | 22.1 | 1.2 | 4E1685E1CEBE4030A48AC82E86DBA8CE |  | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Diamond Springs | CA | 95619-9212 |  | 2014-06-03 | 2014-06-03 13:10 | 2014-06-03 13:27 | COLEMAN - BRCQ0361CB | 55 | 9 | Yes | Yes | 21 | 21.2 | -0.2 | 83FC41777E8A4754A447CBC8DCFB21D3 |  | R22 | Non-TXV |  | 16.36% | 0.83636 | 31.45% | [5 empty] | Non-TXV | 16.36%
Stockton | CA | 95205-0000 |  | 2014-06-13 | 2014-06-13 13:39 | 2014-06-13 14:05 | RUUD - UAND-042JAZ | 85 | 5.2 | Yes | Yes | 21.9 | 20.7 | 1.2 | 3C591AFA0341448FB76BD6D55605BA07 |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Stockton | CA | 95207-7848 |  | 2014-06-11 | 2014-06-11 13:22 | 2014-06-11 13:40 | TRANE - YYC024F1LOBF | 64 | 2.7 | Yes | Yes | 19.1 | 18.4 | 0.8 | CB8E85CB6B2A4CD3BDABD5485930AB02 |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Stockton | CA | 95202-2808 |  | 2014-06-19 | 2014-06-19 10:54 | 2014-06-19 10:54 | DUCANE - 10HP24BAPA | 56 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | F6B0928D832E49D1857742B884BF4E90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3400 |  | 2014-05-19 | 2014-05-19 14:08 | 2014-05-19 19:29 | DAY & NIGHT - 36/80YAC 107-C | 67 | 3.1 | Yes | Yes | 27.6 | 22.1 | 5.5 | C4A538BE69E64006A63C5A541917597D |  | R22 | Non-TXV |  | 4.627% | 0.95373 | 8.892% | [5 empty] | Non-TXV | 4.627%
Diamond Springs | CA | 95619-9407 |  | 2014-06-03 | 2014-06-03 13:47 | 2014-06-03 14:05 | COLEMAN - TCGD3621S2A | 63 | 2.4 | Yes | Yes | 21 | 23.1 | -2.1 | BACCBF2E712F473391B6CEF635EFC210 |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Fresno | CA | 93726-2629 |  | 2014-05-26 | 2014-05-26 16:18 | 2014-05-26 16:42 | CARRIER - 48NMT042---301B | 90 | 4.8 | Yes | Yes | 22.9 | 21.9 | 1 | D2AA2F908AAD4B96AEFA8C52CCA1C08C |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Fresno | CA | 93706-2242 |  | 2014-05-20 | 2014-05-20 09:48 | 2014-05-20 10:15 | LENNOX - 13ACD04223001 | 111 | 13.6 | Yes | Yes | 19.9 | 16.5 | 3.4 | EE9658C2AA6941A694E484148535C6F0 |  | R22 | Non-TXV |  | 12.25% | 0.87748 | 23.55% | [5 empty] | Non-TXV | 12.25%
Fresno | CA | 93706-2242 |  | 2014-05-20 | 2014-05-20 10:17 | 2014-05-20 10:33 | LENNOX - 13ACD04223001 | 111 | 7.6 | Yes | Yes | 22.8 | 18.2 | 4.6 | A78DDAEDC5D34F16894F0E6991F2FC84 |  | R22 | Non-TXV |  | 6.847% | 0.93153 | 13.16% | [5 empty] | Non-TXV | 6.847%
Gustine | CA | 95322-1327 |  | 2014-08-05 | 2014-08-05 13:18 | 2014-08-05 13:44 | HEIL - CA5530BKD2 | 85 | 5.6 | Yes | Yes | 17 | 19.3 | -2.3 | F5766B2954174F30804CAD90094FD3F8 |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Stockton | CA | 95210-6713 |  | 2014-05-28 | 2014-05-28 12:08 | 2014-05-28 12:31 | CARRIER - 38TDA036300 | 184 | 6.5 | Yes | Yes | 29 | 25.1 | 3.9 | 9CDF3CB9051C48198A39D0075A213119 |  | R22 | Non-TXV |  | 3.533% | 0.96467 | 6.789% | [5 empty] | Non-TXV | 3.533%
Stockton | CA | 95209-1343 |  | 2014-05-20 | 2014-05-20 10:50 | 2014-05-20 11:09 | ICP - PGC048K080E | 100 | 4.6 | Yes | Yes | 22.8 | 19.7 | 3.1 | 56E6406A94D645B3A0DBCC1F382298A5 |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Los Banos | CA | 93635-3314 |  | 2014-06-06 | 2014-06-06 13:42 | 2014-06-06 13:52 | RHEEM - 7777UNK | 78 | 5.6 | Yes | Yes | 19.5 | 22.1 | -2.6 | 8261F2E77B9F437EBEBEC88A240F1D98 |  | R22 | Non-TXV |  | 7.179% | 0.92821 | 13.8% | [5 empty] | Non-TXV | 7.179%
Oakdale | CA | 95361-3923 |  | 2014-05-19 | 2014-05-19 08:34 | 2014-05-19 08:54 | BRYANT - N4A324AKB200 | 85 | -5 | Yes | Yes | 20.8 | 20.6 | 0.2 | 9F0D08D045CA497BBA6DFB3260F7775D |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93705-3213 |  | 2014-05-28 | 2014-05-28 08:35 | 2014-05-28 08:37 | GOODMAN - CE48-1EB | 100 | 4.6 | Yes | Yes | 27 | 22.6 | 4.4 | 267F8F5B48BC47DE8F6AC0FA9A985F6A |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Fresno | CA | 93725-1224 |  | 2014-06-17 | 2014-06-17 09:22 | 2014-06-17 09:23 | OTHER - 585CJ02450 | 72 | 9.6 | Yes | Yes | 20.3 | 18.2 | 2.1 | AF1207250F0E4F3283714C32D356A98C |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Fresno | CA | 93703-3344 |  | 2014-05-19 | 2014-05-19 10:17 | 2014-05-19 11:18 | GOODMAN - PGB036075-1A | 60 | 4.7 | Yes | Yes | 25.6 | 19.7 | 5.9 | D58AC579846E41D7ACC92E869735E772 |  | R22 | Non-TXV |  | 7.833% | 0.92167 | 15.05% | [5 empty] | Non-TXV | 7.833%
Chowchilla | CA | 93610-1815 |  | 2014-07-01 | 2014-07-01 13:41 | 2014-07-01 13:43 | RUUD - UNK | 56 | 7.6 | Yes | Yes | 23.9 | 22.3 | 1.6 | 72D9FA02A61842FAA935EE64E773AB91 |  | R22 | Non-TXV |  | 13.57% | 0.86429 | 26.08% | [5 empty] | Non-TXV | 13.57%
Paso Robles | CA | 93446-5022 |  | 2014-06-24 | 2014-06-24 18:21 | 2014-06-24 21:25 | CARRIER - 38EN024310 | 61 | 1.8 | Yes | Yes | 17 | 19.4 | -2.4 | AEF3E993476D45BE813CD2DB3F7C051D |  | R22 | Non-TXV |  | 2.951% | 0.97049 | 5.671% | [5 empty] | Non-TXV | 2.951%
Fresno | CA | 93703-1311 |  | 2014-05-16 | 2014-05-16 11:09 | 2014-05-16 11:09 | GOODMAN - GPG1336045M41AD | 85 | 0 | Yes | Yes | 23.9 | 20.4 | 3.5 | CC66809C5E7745738F764C4042E24A1D |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-7855 |  | 2014-06-07 | 2014-06-07 10:58 | 2014-06-07 11:18 | AMANA - PGB36C0702E | 64 | -3.8 | Yes | Yes | 21.4 | 18.8 | 2.6 | 36C1FE4C35CA41C49567092E132A1A79 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Fresno | CA | 93702-2633 |  | 2014-06-17 | 2014-06-17 13:22 | 2014-06-17 13:24 | YORK - DCYZF036N070A | 64 | 8 | Yes | Yes | 26.7 | 21 | 5.7 | A9A47C28FD4B438DB8B4A42621D75610 |  | R410A | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Paso Robles | CA | 93446-5055 |  | 2014-06-23 | 2014-06-23 14:55 | 2014-06-23 15:12 | GOODMAN - CKL24-1H | 72 | -4.2 | Yes | Yes | 20.9 | 21.5 | -0.6 | 32AF5C50316A4D29A28350477BB9B6BE |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95205-7810 |  | 2014-06-04 | 2014-06-04 09:47 | 2014-06-04 09:51 | DAY & NIGHT - 591AN42-D | 87 | -8.2 | Yes | Yes | 22.2 | 19 | 3.2 | 54D7865E60C2482FA445118157724FDB |  | R22 | Non-TXV |  | -9.425% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.425%
Stockton | CA | 95203-1004 |  | 2014-06-05 | 2014-06-05 10:39 | 2014-06-05 10:58 | YORK - D1NP048N09006A | 132 | 6.1 | Yes | Yes | 24.1 | 21.4 | 2.7 | 19356725E4934F4CAA1096B2C49BD028 |  | R22 | Non-TXV |  | 4.621% | 0.95379 | 8.881% | [5 empty] | Non-TXV | 4.621%
Tracy | CA | 95376-0772 |  | 2014-06-09 | 2014-06-09 13:07 | 2014-06-09 13:32 | BRYANT - 561CJ036-F | 124 | 11.5 | Yes | Yes | 27 | 22.1 | 4.9 | 27A51CF4469A4AD7901BF278E5ADAE95 |  | R22 | Non-TXV |  | 9.274% | 0.90726 | 17.82% | [5 empty] | Non-TXV | 9.274%
Madera | CA | 93638-0354 |  | 2014-06-03 | 2014-06-03 10:34 | 2014-06-03 10:53 | BRYANT - 583BNW048090NB | 149 | 8.6 | Yes | Yes | 24.9 | 19.8 | 5.1 | E2AB7E408986414885021480B3F271D0 |  | R410A | Non-TXV |  | 5.772% | 0.94228 | 11.09% | [5 empty] | Non-TXV | 5.772%
Placerville | CA | 95667-9208 |  | 2014-06-03 | 2014-06-03 10:45 | 2014-06-03 11:10 | KENMORE - UNK | 120 | 3.8 | Yes | Yes | 22 | 21.3 | 0.7 | 623288E98E3A40689282906149EC1D81 |  | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Madera | CA | 93638-8048 |  | 2014-06-02 | 2014-06-02 09:23 | 2014-06-02 09:43 | CARRIER - 591ANX048000ACAA | 128 | 7.8 | Yes | Yes | 19 | 17.5 | 1.5 | 5D583685EBB5477192882238D23EC598 |  | R22 | Non-TXV |  | 6.094% | 0.93906 | 11.71% | [5 empty] | Non-TXV | 6.094%
Madera | CA | 93638-8048 |  | 2014-06-02 | 2014-06-02 09:45 | 2014-06-02 10:05 | CARRIER - 591ANX048000ACAA | 128 | 11.6 | Yes | Yes | 21.3 | 16.4 | 4.9 | F5DF66A8EB964C6481AA9688710D020B |  | R22 | Non-TXV |  | 9.062% | 0.90938 | 17.42% | [5 empty] | Non-TXV | 9.062%
Lathrop | CA | 95330-8921 |  | 2014-06-03 | 2014-06-03 10:49 | 2014-06-03 11:25 | GOODMAN - GSC130481AF | 85 | 3.8 | Yes | Yes | 20.9 | 19.2 | 1.7 | 98C93B042B2E4993AC04DE9A45022422 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Fresno | CA | 93705-2340 |  | 2014-05-26 | 2014-05-26 12:52 | 2014-05-26 13:10 | YORK - D1NH030N05606C | 73 | 14.3 | Yes | Yes | 21.7 | 16.8 | 4.9 | 8E427890691E40E0842920B45ADE36D0 |  | R22 | Non-TXV |  | 19.59% | 0.80411 | 37.65% | [5 empty] | Non-TXV | 19.59%
Stockton | CA | 95210-4208 |  | 2014-05-31 | 2014-05-31 11:22 | 2014-05-31 11:39 | PAYNE - 561CJ024-C | 72 | 2.4 | Yes | Yes | 17.1 | 18.8 | -1.7 | 81DAF3FC3A1548BCB34C5FB5C9CF298F |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Jackson | CA | 95642-2161 |  | 2014-08-27 | 2014-08-27 09:40 | 2014-08-27 09:58 | DAY & NIGHT - 597CN030-A | 97 | 3.9 | Yes | Yes | 23.2 | 20.2 | 3.1 | DB426DD2D91C456993DA67A7CAF1C320 |  | R22 | Non-TXV |  | 4.021% | 0.95979 | 7.727% | [5 empty] | Non-TXV | 4.021%
Stockton | CA | 95204-3728 |  | 2014-06-02 | 2014-06-02 16:03 | 2014-06-02 16:24 | PAYNE - 113ANA024-D | 58 | 6.8 | Yes | Yes | 15.8 | 17.8 | -2 | F20F64EB4A39438EBC4F1F5311F63BA0 |  | R410A | TXV |  | 11.72% | 0.88276 | 22.53% | [5 empty] | TXV | 11.72%
Stockton | CA | 95205-4340 |  | 2014-06-14 | 2014-06-14 08:37 | 2014-06-14 08:54 | YORK - D1NA024N05606C | 54 | -3.2 | Yes | Yes | 16 | 18.9 | -2.9 | 70C0AFD1EA7246F2AA4F962353FC7D1D |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Stockton | CA | 95207-5132 |  | 2014-05-31 | 2014-05-31 12:04 | 2014-05-31 12:04 | PAYNE - PA13NR036-J | 83 | 0 | Yes | Yes | 23.2 | 18.7 | 4.5 | B6C4E00C1EF94BEEBB5AF0FC4311F9D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4051 |  | 2014-06-03 | 2014-06-03 11:22 | 2014-06-03 11:39 | ICP - NAC060AKA1 | 130 | -9.2 | Yes | Yes | 19.7 | 18.7 | 1 | 9C1C88CC91A64F4EB175CBCBD62FC7D1 |  | R22 | Non-TXV |  | -7.077% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.077%
Stockton | CA | 95204-4009 |  | 2014-06-06 | 2014-06-06 08:51 | 2014-06-06 09:21 | ICP - PGC030K060A | 52 | 5.4 | Yes | Yes | 22.2 | 19.9 | 2.3 | 04593969E2D2409397098CF36C9A87DA |  | R22 | Non-TXV |  | 10.38% | 0.89615 | 19.96% | [5 empty] | Non-TXV | 10.38%
Sanger | CA | 93657-3343 |  | 2014-06-20 | 2014-06-20 14:02 | 2014-06-20 14:24 | LENNOX - 12GCS036X-75-5PB | 110 | 4.8 | Yes | Yes | 20.8 | 21.3 | -0.5 | 942C277BBAF3427A87FE52C814AB4AA2 |  | R22 | Non-TXV |  | 4.364% | 0.95636 | 8.386% | [5 empty] | Non-TXV | 4.364%
Stockton | CA | 95207-4828 |  | 2014-05-23 | 2014-05-23 14:34 | 2014-05-23 15:03 | TRANE - TTN030C100C2 | 95 | 5.1 | Yes | Yes | 24.2 | 20 | 4.3 | B7025BA6B7734885A6A86BEA9C6433BE |  | R22 | Non-TXV |  | 5.368% | 0.94632 | 10.32% | [5 empty] | Non-TXV | 5.368%
Kingsburg | CA | 93631-1731 |  | 2014-07-12 | 2014-07-12 14:28 | 2014-07-12 14:50 | ICP - WCA3422GKR2 | 113 | -8 | Yes | Yes | 17.9 | 20.8 | -2.9 | CC0AE297760445138AB335702B54BDF6 |  | R22 | TXV |  | -7.08% | 1.0708 | 1.983% |  |  |  |  | TXV |  |  | -7.08%
Riverbank | CA | 95367-2287 |  | 2014-05-20 | 2014-05-20 10:24 | 2014-05-20 10:46 | RHEEM - UNK | 69 | 3.8 | Yes | Yes | 21.6 | 23.1 | -1.5 | C2AB0C407B9242568283752EA1781263 |  | R22 | Non-TXV |  | 5.507% | 0.94493 | 10.58% | [5 empty] | Non-TXV | 5.507%
Kingsburg | CA | 93631-1731 |  | 2014-08-20 | 2014-08-20 17:28 | 2014-08-20 17:56 | OTHER - N/A | 90 | 7.9 | Yes | Yes | 27 | 21.2 | 5.8 | E2FCC22F323D48DEAAD57031E0E2B46F |  | R22 | Non-TXV |  | 8.778% | 0.91222 | 16.87% | [5 empty] | Non-TXV | 8.778%
Shingle Springs | CA | 95682-8391 |  | 2014-06-23 | 2014-06-23 08:24 | 2014-06-23 08:43 | CARRIER - UNK | 152 | 4.5 | Yes | Yes | 25 | 19.9 | 5.1 | D3B1B43E5642448D846EF8581157F02C |  | R22 | Non-TXV |  | 2.961% | 0.97039 | 5.689% | [5 empty] | Non-TXV | 2.961%
Paradise | CA | 95969-3452 |  | 2014-06-13 | 2014-06-13 09:37 | 2014-06-13 09:57 | YORK - D1NPO42N09006H | 150 | 6.9 | Yes | Yes | 19 | 18.3 | 0.7 | 6CD8E5E08D0A486A93D5DA7BB644BBAB |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Fresno | CA | 93705-3317 |  | 2014-05-27 | 2014-05-27 15:08 | 2014-05-27 15:09 | GOODMAN - GPG13300451A | 77 | 3.3 | Yes | Yes | 28.9 | 22.9 | 6 | 3AE7701C80A741C09097B4FC27E29CD5 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Fresno | CA | 93705-3318 |  | 2014-07-30 | 2014-07-30 13:16 | 2014-07-30 13:34 | HEIL - NRGF30DDB03 | 53 | 1.6 | Yes | Yes | 25.6 | 20.2 | 5.4 | 4BEE9569080A47B8ACF5C2BBC4724BBF |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Tracy | CA | 95376-6751 |  | 2014-05-22 | 2014-05-22 15:20 | 2014-05-22 15:39 | CARRIER - 3BBRC030320 | 121 | 6.4 | Yes | Yes | 20.2 | 21 | -0.8 | B395AC5F75B04C4BA4E6162E77FD5D68 |  | R22 | TXV |  | 5.289% | 0.94711 | 10.16% | [5 empty] | TXV | 5.289%
Tracy | CA | 95376-6751 |  | 2014-05-22 | 2014-05-22 15:42 | 2014-05-22 16:01 | CARRIER - 38BRC042340 | 171 | 7.2 | Yes | Yes | 20.8 | 20.4 | 0.4 | CECC31AC5C284DE8AFB4414D237A7107 |  | R22 | TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | TXV | 4.211%
Stockton | CA | 95206-6447 |  | 2014-08-16 | 2014-08-16 10:43 | 2014-08-16 11:03 | GOODMAN - CKL48-1A | 112 | -6.6 | Yes | Yes | 25.9 | 20.1 | 5.8 | BCEF42AD61434CD4895C923BE9080DBA |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Orland | CA | 95963-2006 |  | 2014-06-16 | 2014-06-16 08:07 | 2014-06-16 08:25 | YORK - DAYH-F36N070C | 70 | 15.1 | Yes | Yes | 20.2 | 19.3 | 0.9 | 336664A61D854F46ADD03D91FA5BA4CC |  | R22 | Non-TXV |  | 21.57% | 0.78429 | 41.46% | [5 empty] | Non-TXV | 21.57%
Auburn | CA | 95602-8347 |  | 2014-06-02 | 2014-06-02 08:45 | 2014-06-02 09:01 | BARD - PH11361 | 80 | 3.2 | Yes | Yes | 22 | 19.3 | 2.7 | E5888004A84B49CAB94DF6B6621140D0 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Lathrop | CA | 95330-9209 |  | 2014-06-03 | 2014-06-03 08:03 | 2014-06-03 08:26 | YORK - H1RA042S06D | 84 | 5.8 | Yes | Yes | 20.8 | 19.8 | 1 | DFBE6E9562BD479DA5BF69C26BAA169B |  | R22 | Non-TXV |  | 6.905% | 0.93095 | 13.27% | [5 empty] | Non-TXV | 6.905%
Corning | CA | 96021-0000 |  | 2014-06-18 | 2014-06-18 17:16 | 2014-06-18 17:43 | COLEMAN - DRCO30361B66 | 55 | 14.8 | Yes | Yes | 20 | 21.5 | -1.5 | A64BC5A6F588407D9DE1344CFED5DBBC |  | R22 | Non-TXV |  | 26.91% | 0.73091 | 51.71% | [5 empty] | Non-TXV | 26.91%
Lincoln | CA | 95648-8753 |  | 2014-06-09 | 2014-06-09 09:00 | 2014-06-09 09:40 | YORK - H2RC030S06HA | 88 | 2.6 | Yes | Yes | 19 | 21 | -2 | 5522BE6919864030832DA289132EF758 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Oakhurst | CA | 93644-9412 |  | 2014-07-31 | 2014-07-31 13:49 | 2014-07-31 13:51 | BRYANT - 563CN048 | 136 | 17.8 | Yes | Yes | 20.7 | 19.3 | 1.4 | 16A479A8BB1845B1A3CE72DD5E70812B |  | R22 | TXV |  | 13.09% | 0.86912 | 25.15% | [5 empty] | TXV | 13.09%
Madera | CA | 93638-1540 |  | 2014-06-02 | 2014-06-02 15:33 | 2014-06-02 16:02 | CARRIER - 48TMX030301 | 100 | 25 | Yes | Yes | 22.3 | 19.3 | 3 | 69CCDCC414144C409E2258D1BDDA806B |  | R22 | Non-TXV |  | 25% | 0.75 | 48.04% | [5 empty] | Non-TXV | 25%
Vacaville | CA | 95688-5349 |  | 2014-10-22 | 2014-10-22 14:55 | 2014-10-22 15:15 | BDP - 561AJ024-B | 62 | 16.2 | Yes | Yes | 21.1 | 19.1 | 2 | DED4983FCFA64D8EB238A21D5FA83AF8 |  | R22 | Non-TXV |  | 26.13% | 0.73871 | 50.21% | [5 empty] | Non-TXV | 26.13%
Fresno | CA | 93703-2734 |  | 2014-05-16 | 2014-05-16 14:55 | 2014-05-16 15:21 | LENNOX - 12GCS060X-125-1PA | 125 | 9.4 | Yes | Yes | 29 | 23.4 | 5.7 | 9D8DB1F20C544196B183BCBAE9C08938 |  | R22 | Non-TXV |  | 7.52% | 0.9248 | 14.45% | [5 empty] | Non-TXV | 7.52%
Fresno | CA | 93725-1528 |  | 2014-06-17 | 2014-06-17 12:07 | 2014-06-17 12:09 | BDP - 585B036075 | 60 | 9 | Yes | Yes | 26.8 | 21.5 | 5.3 | CB43C278F8D446C995855A0F7BAE12E8 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Tracy | CA | 95376-2715 |  | 2014-05-22 | 2014-05-22 11:13 | 2014-05-22 11:31 | YORK - SA48G129N-10AA | 115 | 6.5 | Yes | Yes | 20.8 | 21.3 | -0.4 | 640EBF1CEC784D19BFD67A2F5B67789B |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Atwater | CA | 95301-4502 |  | 2014-06-30 | 2014-06-30 14:35 | 2014-06-30 15:00 | GOODMAN - GSC130361DB | 85 | 5.4 | Yes | Yes | 20 | 20.1 | -0.1 | A7C6F3DB4B18485DA71A90EF0A9A5907 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Merced | CA | 95340-5118 |  | 2014-05-16 | 2014-05-16 13:43 | 2014-05-16 13:45 | AMERICAN STANDARD - YCC024F11OBA | 64 | 11.6 | Yes | Yes | 23.8 | 20.6 | 3.2 | 764A82F51CC548BCA1D2A2F846D66B95 |  | R22 | Non-TXV |  | 18.12% | 0.81875 | 34.83% | [5 empty] | Non-TXV | 18.12%
Stockton | CA | 95207-7849 |  | 2014-06-05 | 2014-06-05 13:53 | 2014-06-05 13:53 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 20.5 | 19.9 | 0.6 | B985EDA643EB466585E451B2BBB91085 |  | R410A | TXV |  | 0% | 1 | 0%
Groveland | CA | 95321-9343 |  | 2014-11-03 | 2014-11-03 10:18 | 2014-11-03 10:18 | ICP - PGAA24B1K1 | 64 | 0 | Yes | Yes | 16.5 | 18.2 | -1.7 | CE8585CEE5194FC3B3719C26833EC059 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-9606 |  | 2014-05-30 | 2014-05-30 13:12 | 2014-05-30 13:28 | CARRIER - 48GP030060311 | 85 | 16.4 | Yes | Yes | 25 | 21 | 4 | C8A1B9A5EB11495DBDE14862C93566FB |  | R410A | Non-TXV |  | 19.29% | 0.80706 | 37.08% | [5 empty] | Non-TXV | 19.29%
Clovis | CA | 93612-1919 |  | 2014-06-02 | 2014-06-02 15:56 | 2014-06-02 16:15 | RHEEM - RRNA-B030JK06X | 72 | 4.4 | Yes | Yes | 22.3 | 21 | 1.3 | AEC85C4C42C14F13B3628ABB3BB66062 |  | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Orosi | CA | 93647-2632 |  | 2014-09-04 | 2014-09-04 15:23 | 2014-09-04 15:23 | GOODMAN - GSC130301CA | 106 | 0 | Yes | Yes | 18.8 | 21.3 | -2.5 | D2176059AA6241CF971174557E932047 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1320 |  | 2014-05-20 | 2014-05-20 10:14 | 2014-05-20 10:34 | RUUD - RRMA-A030JK06X | 80 | 4.8 | Yes | Yes | 22.2 | 20.4 | 1.8 | A1055CC4C23E45958A4253CD1F014839 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Tracy | CA | 95376-2105 |  | 2014-05-21 | 2014-05-21 14:25 | 2014-05-21 14:41 | OTHER - CAC230AKA1 | 85 | -8 | Yes | Yes | 17.3 | 19.3 | -2 | CEFF726C985F4F25AEADE1B24D06DB9B |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95207-7851 |  | 2014-06-06 | 2014-06-06 12:58 | 2014-06-06 13:15 | YORK - D1NA024N05606C | 54 | 2.7 | Yes | Yes | 17.9 | 17.5 | 0.4 | 6E0086E15D96495586E0289EE1BF56C8 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Lincoln | CA | 95648-2502 |  | 2014-06-21 | 2014-06-21 09:45 | 2014-06-21 10:01 | CARRIER - 38BRC03636 | 101 | 3.1 | Yes | Yes | 18 | 21 | -3 | B7068C1404034DBC80CDD30996F17FC2 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Lincoln | CA | 95648-8155 |  | 2014-05-26 | 2014-05-26 08:35 | 2014-05-26 08:51 | YORK - H2RC036S06A | 83 | 2.4 | Yes | Yes | 17 | 19.3 | -2.3 | A72D70432B1F4916B650AF1165DBFB85 |  | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Escalon | CA | 95320-2126 |  | 2014-08-26 | 2014-08-26 11:11 | 2014-08-26 11:31 | TAPPAN - UNK | 85 | 3.2 | Yes | Yes | 24.6 | 19.5 | 5.1 | 20DA2172208D416B9179EE3929A1CFCF |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Dos Palos | CA | 93620-2730 |  | 2014-07-08 | 2014-07-08 10:04 | 2014-07-08 10:05 | CARRIER - 48GS-036060301 | 56 | 3.5 | Yes | Yes | 22.1 | 21 | 1.1 | 27A9ACB6900644E1858A629BA97964DA |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Penn Valley | CA | 95946-9619 |  | 2014-06-30 | 2014-06-30 08:39 | 2014-06-30 09:14 | AMANA - ARCF30U01D | 80 | 2.4 | Yes | Yes | 15 | 17.7 | -2.7 | FA92C73CA2E74278984D21BB0388D3D4 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95210-1246 |  | 2014-05-16 | 2014-05-16 10:33 | 2014-05-16 10:54 | RUUD - URA-A030JK06X | 80 | 3.2 | Yes | Yes | 17.8 | 19.5 | -1.7 | 66F356D3DA374A53A0F94997AA0A9A26 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Merced | CA | 95348-1111 |  | 2014-05-15 | 2014-05-15 13:14 | 2014-05-15 13:14 | TRANE - YCC030F1MOBE | 85 | 0 | Yes | Yes | 17.5 | 19.1 | -1.6 | B7080FFC20B04980B9F068FA656ADEA4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4133 |  | 2014-06-07 | 2014-06-07 12:22 | 2014-06-07 12:44 | BRYANT - UNK | 70 | 3.3 | Yes | Yes | 27.4 | 21.5 | 5.9 | 2C723B44460F4856B60877584DE50879 |  | R410A | Non-TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | Non-TXV | 4.714%
Clovis | CA | 93612-1915 |  | 2014-06-02 | 2014-06-02 15:29 | 2014-06-02 15:53 | PAYNE - PA10JA030-C | 65 | 2 | Yes | Yes | 19.1 | 20.2 | -1.1 | 21536C0631E140929B2D8E3D7C5AA5D7 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Merced | CA | 95348-1563 |  | 2014-05-19 | 2014-05-19 16:01 | 2014-05-19 16:17 | UNK - UNK | 85 | 17.1 | Yes | Yes | 23.2 | 17.7 | 5.5 | 97B1AA6D96EB49D196A0AD1E0BC5A6C4 |  |  |  |  | 20.12% | 0.79882 | 38.66% | [5 empty] | 0 | 20.12%
Chico | CA | 95926-0000 |  | 2014-06-26 | 2014-06-26 15:25 | 2014-06-26 15:45 | LENNOX - 13ACD-036-230-05 | 80 | 7.6 | Yes | Yes | 19 | 19.6 | -0.6 | BB4374C0FEB64C87A4D3DE5CAD73B124 |  | R22 | Non-TXV |  | 9.5% | 0.905 | 18.26% | [5 empty] | Non-TXV | 9.5%
Lincoln | CA | 95648-8107 |  | 2014-05-20 | 2014-05-20 12:51 | 2014-05-20 13:25 | YORK - H2RC030S06A | 88 | 2.6 | Yes | Yes | 18 | 19.5 | -1.5 | 6A02109A44A042989AD99FF141AA8B67 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Chico | CA | 95926-1608 |  | 2014-06-06 | 2014-06-06 10:55 | 2014-06-06 11:13 | DAY & NIGHT - NA | 50 | 4.7 | Yes | Yes | 18.2 | 20.9 | -2.7 | A35161CAD28E451E8D2E0945188A65D4 |  | R22 | Non-TXV |  | 9.4% | 0.906 | 18.06% | [5 empty] | Non-TXV | 9.4%
Fresno | CA | 93727-2607 |  | 2014-06-03 | 2014-06-03 13:11 | 2014-06-03 13:44 | ICP - PGN436060K01 | 152 | 5.7 | Yes | Yes | 21.9 | 22.1 | -0.2 | A082B7D02EA04C0CB4FCB66D74D48077 |  | R410A | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Oroville | CA | 95966-6530 |  | 2014-05-27 | 2014-05-27 13:07 | 2014-05-27 13:24 | TRANE - YCC030F1L0BJ | 68 | 2.3 | Yes | Yes | 22 | 21.5 | 0.5 | B4C52521949947AD8C0A5A7AA55E8AAB |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Sanger | CA | 93657-2187 |  | 2014-06-17 | 2014-06-17 10:31 | 2014-06-17 10:55 | LENNOX - 12GCS030-75-5PB | 85 | 7.7 | Yes | Yes | 23 | 21.5 | 1.5 | 046B105A5A7B4F48BCEE68EB46395C0E |  | R22 | Non-TXV |  | 9.059% | 0.90941 | 17.41% | [5 empty] | Non-TXV | 9.059%
Clovis | CA | 93611-7509 |  | 2014-06-07 | 2014-06-07 17:46 | 2014-06-07 18:06 | CARRIER - N/A | 60 | 3.3 | Yes | Yes | 22 | 22.1 | -0.1 | 34C8E960A53F4EA5AE14012B97057577 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Clovis | CA | 93611-7509 |  | 2014-06-07 | 2014-06-07 18:08 | 2014-06-07 18:36 | CARRIER - N/A | 60 | 6.1 | Yes | Yes | 19.9 | 21.4 | -1.5 | 435BAA3974404164A4F4E2EDD8A60987 |  | R22 | Non-TXV |  | 10.17% | 0.89833 | 19.54% | [5 empty] | Non-TXV | 10.17%
Sanger | CA | 93657-2322 |  | 2014-06-17 | 2014-06-17 13:41 | 2014-06-17 14:06 | AMERICAN STANDARD - YCY042G1M0AA | 147 | 23.4 | Yes | Yes | 20.4 | 22.1 | -1.7 | 824B80B223F14B608DF1D16889813728 |  | R22 | Non-TXV |  | 15.92% | 0.84082 | 30.59% | [5 empty] | Non-TXV | 15.92%
Sanger | CA | 93657-2322 |  | 2014-06-17 | 2014-06-17 14:10 | 2014-06-17 14:44 | CARRIER - N/A | 90 | 17.2 | Yes | Yes | 24 | 24 | 0.1 | 23E7DB247127445EB8BFA022880E8707 |  | R22 | Non-TXV |  | 19.11% | 0.80889 | 36.73% | [5 empty] | Non-TXV | 19.11%
Tracy | CA | 95376-3617 |  | 2014-05-22 | 2014-05-22 09:12 | 2014-05-22 09:34 | BRYANT - NXA624GKA100 | 96 | 5.1 | Yes | Yes | 18.8 | 19.4 | -0.6 | C755AD4D9E6B4F6EA60E109E88027699 |  | R410A | TXV |  | 5.312% | 0.94688 | 10.21% | [5 empty] | TXV | 5.312%
Stockton | CA | 95206-4502 |  | 2014-06-11 | 2014-06-11 12:17 | 2014-06-11 12:41 | GOODMAN - GSC130421CB | 85 | 4.5 | Yes | Yes | 25.2 | 21 | 4.2 | 6EB9086327514F62AB3D8882B3C37203 |  | R22 | TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | TXV | 5.294%
Auburn | CA | 95603-3919 |  | 2014-06-28 | 2014-06-28 10:05 | 2014-06-28 10:26 | PAYNE - PY3GNAA36060NA | 100 | 3.6 | Yes | Yes | 21 | 18.3 | 2.7 | D00CBF11C2BC482C937D504EF8B14D32 |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Madera | CA | 93638-2296 |  | 2014-06-03 | 2014-06-03 14:54 | 2014-06-03 15:11 | CARRIER - 24ABB348W310 | 112 | 16.7 | Yes | Yes | 22.4 | 19.8 | 2.6 | 54D353E49B2D4CE0AE2A5E422C8C24C9 |  | R410A | TXV |  | 14.91% | 0.85089 | 28.66% | [5 empty] | TXV | 14.91%
Red Bluff | CA | 96080-9476 |  | 2014-06-08 | 2014-06-08 15:00 | 2014-06-08 15:54 | BRYANT - 583ANW03606NAAAF | 95 | 5.6 | Yes | Yes | 20 | 20.4 | -0.4 | 6D7A7B00AC944AEFB36956447CA5808D |  | R22 | Non-TXV |  | 5.895% | 0.94105 | 11.33% | [5 empty] | Non-TXV | 5.895%
Fresno | CA | 93722-3276 |  | 2014-05-20 | 2014-05-20 12:18 | 2014-05-20 12:20 | OTHER - EABD-037JAS | 85 | 5.8 | Yes | Yes | 19.3 | 22.3 | -3 | AF68F38B699E4F809F4A6160E14342F3 |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Merced | CA | 95340-3316 |  | 2014-05-29 | 2014-05-29 12:57 | 2014-05-29 12:59 | OTHER - 100WR42G1 | 85 | 4.2 | Yes | Yes | 21.5 | 22.2 | -0.7 | 45FA090E07F14399BE71DABD9B2B45AF |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Fresno | CA | 93711-1734 |  | 2014-07-24 | 2014-07-24 12:46 | 2014-07-24 13:02 | GOODMAN - GPG15481151AB | 172 | 7.3 | Yes | Yes | 19.2 | 15.7 | 3.5 | 921A7A9DFD2A40909B573F6004C9294F |  | R410A | TXV |  | 4.244% | 0.95756 | 8.156% | [5 empty] | TXV | 4.244%
Fresno | CA | 93711-1734 |  | 2014-07-24 | 2014-07-24 13:04 | 2014-07-24 13:21 | GOODMAN - GPG15481151AB | 172 | 6.3 | Yes | Yes | 20.1 | 20.2 | -0.1 | 15F8CDA3A50E4FF9A69B5FB60CAF4127 |  | R410A | TXV |  | 3.663% | 0.96337 | 7.039% | [5 empty] | TXV | 3.663%
Los Banos | CA | 93635-3064 |  | 2014-08-06 | 2014-08-06 15:56 | 2014-08-06 15:57 | CARRIER - 38CKC024330 | 55 | 3 | Yes | Yes | 19.3 | 19.7 | -0.4 | 000F75A9111543269160B28F88F49F39 |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Fresno | CA | 93730-1263 |  | 2014-09-20 | 2014-09-20 14:58 | 2014-09-20 14:59 | RUUD - 7777UNK | 80 | 2.5 | Yes | Yes | 20 | 19.6 | 0.4 | 126EE60E591E4B69874EFF0F6FAF741F |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Livingston | CA | 95334-1035 |  | 2014-06-19 | 2014-06-19 08:19 | 2014-06-19 08:37 | RHEEM - RRNA-B030JK06X | 85 | 3 | Yes | Yes | 24.4 | 21.3 | 3.1 | 53BEC73A3AC347B89614E778216CAC8F |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Chico | CA | 95926-4458 |  | 2014-06-12 | 2014-06-12 11:33 | 2014-06-12 12:09 | OTHER - AA1CJ018-C | 72 | 6.6 | Yes | Yes | 17 | 20 | -3 | C134BDD69C20473BA0A4121BA8816652 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Kerman | CA | 93630-1225 |  | 2014-06-27 | 2014-06-27 16:12 | 2014-06-27 16:15 | ARCOAIRE - 7777UNK | 110 | 6.9 | Yes | Yes | 21.8 | 20.7 | 1.1 | 7C16ED0D515D42D3879A93E3A334744C |  | R22 | Non-TXV |  | 6.273% | 0.93727 | 12.05% | [5 empty] | Non-TXV | 6.273%
Stockton | CA | 95204-4613 |  | 2014-06-03 | 2014-06-03 13:05 | 2014-06-03 13:24 | TRANE - YCY036G1MOAB | 130 | 17.1 | Yes | Yes | 19.8 | 18.2 | 1.6 | 951957B478E147468B3A845D1D8CD7F2 |  | R22 | Non-TXV |  | 13.15% | 0.86846 | 25.28% | [5 empty] | Non-TXV | 13.15%
Fresno | CA | 93725-9730 |  | 2014-06-18 | 2014-06-18 09:18 | 2014-06-18 09:47 | SEARS - N/A | 120 | 6 | Yes | Yes | 24 | 21.4 | 2.6 | EC7F7962646D49F1BE1D507D6A3445A8 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93726-5042 |  | 2014-06-20 | 2014-06-20 11:45 | 2014-06-20 11:47 | AMERICAN STANDARD - YCY048G1HOAB | 183 | 31 | Yes | Yes | 27.8 | 23.1 | 4.7 | 68DA9E9030CB478DA65F632FCEE39391 |  | R22 | Non-TXV |  | 16.94% | 0.8306 | 32.55% | [5 empty] | Non-TXV | 16.94%
Fresno | CA | 93704-6113 |  | 2014-07-02 | 2014-07-02 18:41 | 2014-07-02 19:09 | BRYANT - 561CJ042-F | 81 | 23.3 | Yes | Yes | 23.5 | 21.4 | 2.1 | 891E34D533BB4770A715C40EC98B0048 |  | R22 | Non-TXV |  | 28.77% | 0.71235 | 55.28% | [5 empty] | Non-TXV | 28.77%
Oroville | CA | 95966-5025 |  | 2014-07-01 | 2014-07-01 12:37 | 2014-07-01 12:54 | - 13ANJN42A01 | 106 | 3.1 | Yes | Yes | 24 | 21.9 | 2.1 | F887957801E443378E1D0B4EFA71E346 |  | R410A | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
Fresno | CA | 93726-1616 |  | 2014-05-28 | 2014-05-28 14:29 | 2014-05-28 14:55 | RHEEM - RRNA-B036JK08X | 83 | 6 | Yes | Yes | 22.6 | 20.7 | 1.9 | 0D542F1FFDBD4F5F99181E5873B9B153 |  | R22 | Non-TXV |  | 7.229% | 0.92771 | 13.89% | [5 empty] | Non-TXV | 7.229%
Fresno | CA | 93725-9508 |  | 2014-06-26 | 2014-06-26 18:12 | 2014-06-26 18:34 | RUUD - N/A | 90 | 4.3 | Yes | Yes | 25.8 | 23 | 2.8 | B998E462FDCB4D58870DC97E38E9ACFB |  | R22 | Non-TXV |  | 4.778% | 0.95222 | 9.182% | [5 empty] | Non-TXV | 4.778%
Stockton | CA | 95207-7851 |  | 2014-06-20 | 2014-06-20 09:00 | 2014-06-20 09:21 | RHEEM - HC-80-24-21C | 49 | 13 | Yes | Yes | 18.8 | 18.7 | 0.1 | 6C9D0AA3A66348DCB4C1A6D5630A7A1D |  | R22 | Non-TXV |  | 26.53% | 0.73469 | 50.99% | [5 empty] | Non-TXV | 26.53%
Stockton | CA | 95204-2525 |  | 2014-06-12 | 2014-06-12 13:44 | 2014-06-12 14:01 | AMANA - PGA36B0702C | 112 | 5.2 | Yes | Yes | 24 | 19.9 | 4.1 | 353FD48D9DC54903B54D2CBDB48C1781 |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Madera | CA | 93638-2269 |  | 2014-06-02 | 2014-06-02 13:32 | 2014-06-02 13:49 | COLEMAN - BRCQ0481BD | 103 | 15.5 | Yes | Yes | 27.9 | 22 | 5.9 | 8240BF0CC2D54151980F8E855D78051D |  | R22 | Non-TXV |  | 15.05% | 0.84951 | 28.92% | [5 empty] | Non-TXV | 15.05%
Stockton | CA | 95204-2010 |  | 2014-06-05 | 2014-06-05 09:48 | 2014-06-05 10:06 | DAY & NIGHT - PGN336060K01A1 | 131 | -7.7 | Yes | Yes | 20.2 | 19.1 | 1.1 | F3452F61755A4735AF4486B68D322305 |  | R22 | Non-TXV |  | -5.878% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.878%
Los Banos | CA | 93635-4117 |  | 2014-06-06 | 2014-06-06 16:09 | 2014-06-06 16:10 | GOODMAN - GPG13360701AA | 112 | 4.7 | Yes | Yes | 28.2 | 22.6 | 5.6 | 26F2FCE9BC9749E193CDF8EB4DE65E99 |  | R22 | Non-TXV |  | 4.196% | 0.95804 | 8.065% | [5 empty] | Non-TXV | 4.196%
Fresno | CA | 93703-2414 |  | 2014-05-16 | 2014-05-16 17:23 | 2014-05-16 19:29 | GOODMAN - GPG12420701AA | 107 | 3.5 | Yes | Yes | 24.4 | 20.4 | 4 | AFC82383F1EC42718DD7269EEF5B6381 |  | R22 | Non-TXV |  | 3.271% | 0.96729 | 6.286% | [5 empty] | Non-TXV | 3.271%
Fresno | CA | 93722-2275 |  | 2014-05-28 | 2014-05-28 10:53 | 2014-05-28 11:27 | CARRIER - 38BRC060360 | 200 | 16.9 | Yes | Yes | 20.3 | 17.4 | 2.9 | 2F68E9D58539454CAB7AA44B1877A0CE |  | R22 | TXV |  | 8.45% | 0.9155 | 16.24% | [5 empty] | TXV | 8.45%
Manteca | CA | 95336-6318 |  | 2014-05-15 | 2014-05-15 10:30 | 2014-05-15 10:54 | YORK - 585GJ030040 | 58 | 7.4 | Yes | Yes | 24.1 | 22.1 | 2 | EE07D978026C419A99C83D7ACF1A6C35 |  | R22 | Non-TXV |  | 12.76% | 0.87241 | 24.52% | [5 empty] | Non-TXV | 12.76%
Madera | CA | 93636-8868 |  | 2014-06-02 | 2014-06-02 11:06 | 2014-06-02 11:24 | RUUD - URKAA024JK06E | 70 | 18 | Yes | Yes | 22.6 | 19.2 | 3.4 | FCE87C383DB14E5F8FE4D5832931E4A5 |  | R22 | Non-TXV |  | 25.71% | 0.74286 | 49.42% | [5 empty] | Non-TXV | 25.71%
Madera | CA | 93636-8868 |  | 2014-06-02 | 2014-06-02 11:26 | 2014-06-02 11:42 | RUUD - URKAA024JK06E | 70 | 11.2 | Yes | Yes | 23.5 | 21.5 | 2 | B5F1B3940FF14B16908DA8F713E9DFE5 |  | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Chico | CA | 95926-4209 |  | 2014-06-26 | 2014-06-26 08:30 | 2014-06-26 08:58 | PAYNE - PH10JA024-E | 70 | 5.4 | Yes | Yes | 15.7 | 18.5 | -2.8 | 05EFFCE92AF74AAE97EE0FC588C7FA05 |  | R22 | Non-TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | Non-TXV | 7.714%
Atwater | CA | 95301-3920 |  | 2014-06-30 | 2014-06-30 13:57 | 2014-06-30 14:29 | GOODMAN - GPG13360701AA | 85 | 5.4 | Yes | Yes | 23.4 | 18.3 | 5.1 | 0E0467B6A8A74755AF1560D9780884C6 |  | R22 | TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | TXV | 6.353%
Fresno | CA | 93710-3609 |  | 2014-06-23 | 2014-06-23 10:37 | 2014-06-23 11:08 | BRYANT - 583ANW030040NBAD | 68 | 2 | Yes | Yes | 19.7 | 22.1 | -2.4 | E997E080A08945C6A4DA2C2AE611995D |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93722-5590 |  | 2014-05-22 | 2014-05-22 11:23 | 2014-05-22 11:25 | BRYANT - 574ENWA42060NA | 106 | 3.3 | Yes | Yes | 20.5 | 17.7 | 2.8 | 3E6DA69083E24423B48C45C7312D187C |  | R410A | Non-TXV |  | 3.113% | 0.96887 | 5.983% | [5 empty] | Non-TXV | 3.113%
Stockton | CA | 95207-7843 |  | 2014-08-19 | 2014-08-19 10:33 | 2014-08-19 10:54 | TRANE - YCC024F1LOBF | 64 | -3.8 | Yes | Yes | 18.9 | 17.4 | 1.6 | 4A49D2EF32554A079DC5DD55E642BB9E |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Rocklin | CA | 95677-3170 |  | 2014-05-26 | 2014-05-26 15:30 | 2014-05-26 15:30 | CARRIER - 38EN018318SM | 54 | 0 | Yes | Yes | 5 | 19 | -14 | A8D509A1901B467C89EF077823CA9824 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Cutler | CA | 93615-9772 |  | 2014-09-19 | 2014-09-19 16:56 | 2014-09-19 17:17 | RHEEM - RAND-036JAZ | 116 | 6.1 | Yes | Yes | 19.4 | 20.7 | -1.3 | 74C13570AADE44A685CF3EE868517BB6 |  | R22 | Non-TXV |  | 5.259% | 0.94741 | 10.11% | [5 empty] | Non-TXV | 5.259%
Fresno | CA | 93703-3224 |  | 2014-05-27 | 2014-05-27 11:35 | 2014-05-27 11:58 | LENNOX - 12GCS030X-75-2PA | 85 | 13.6 | Yes | Yes | 23.2 | 23.1 | 0.1 | 2301E135211C4BA3BB393181CB1BC798 |  | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Fresno | CA | 93722-2538 |  | 2014-05-21 | 2014-05-21 10:42 | 2014-05-21 10:44 | LENNOX - GCS26X-042-75-1PA | 133 | 3.9 | Yes | Yes | 19.9 | 19.8 | 0.1 | 6C9ADFF0FCEC44D18D085FD8796860B5 |  | R22 | Non-TXV |  | 2.932% | 0.97068 | 5.635% | [5 empty] | Non-TXV | 2.932%
Copperopolis | CA | 95228-9459 |  | 2014-07-03 | 2014-07-03 09:46 | 2014-07-03 10:03 | BDP - 538ANX060000B | 214 | 48.1 | Yes | Yes | 21.5 | 17.2 | 4.3 | 2ED74C80BE704915BC8D7942FF51E092 |  | R22 | Non-TXV |  | 22.48% | 0.77523 | 43.2% | [5 empty] | Non-TXV | 22.48%
Copperopolis | CA | 95228-9459 |  | 2014-07-03 | 2014-07-03 10:05 | 2014-07-03 10:43 | BDP - 538ANX036000B | 84 | 10.5 | Yes | Yes | 25.3 | 19.4 | 5.9 | 2FF09B01C9CF45C1B4D8B72022B6BF68 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Fresno | CA | 93710-6429 |  | 2014-06-20 | 2014-06-20 09:55 | 2014-06-20 10:12 | RHEEM - RAMA-036JAZ | 96 | 3 | Yes | Yes | 20.6 | 20.9 | -0.3 | 826DCFB37D8F435FA5D7302BF333F7D0 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93725-1707 |  | 2014-06-16 | 2014-06-16 11:37 | 2014-06-16 11:39 | OTHER - 80WR30A1NA | 52 | 8.3 | Yes | Yes | 22.6 | 19.5 | 3.1 | 37D4811D099F488BA485673604D219E7 |  | R22 | Non-TXV |  | 15.96% | 0.84038 | 30.67% | [5 empty] | Non-TXV | 15.96%
Madera | CA | 93637-4616 |  | 2014-05-30 | 2014-05-30 10:19 | 2014-05-30 10:37 | CARRIER - 48SDN030040301 | 130 | 28.4 | Yes | Yes | 25.1 | 20.9 | 4.2 | 7D2BBC635C4B4B9695EDB5B7778A83BD |  | R22 | Non-TXV |  | 21.85% | 0.78154 | 41.98% | [5 empty] | Non-TXV | 21.85%
Fresno | CA | 93703-2312 |  | 2014-05-30 | 2014-05-30 12:57 | 2014-05-30 13:23 | UNITARY PRODUCTS GROUP - TCGD30S21S1HA | 59 | 5.2 | Yes | Yes | 20.7 | 20.9 | -0.2 | 0E7D1E25EBCB4B64ACF1935657B8962B |  | R22 | Non-TXV |  | 8.814% | 0.91186 | 16.94% | [5 empty] | Non-TXV | 8.814%
Fresno | CA | 93727-4703 |  | 2014-07-02 | 2014-07-02 12:42 | 2014-07-02 13:07 | UNITARY PRODUCTS GROUP - A018M1021CA | 49 | 4.9 | Yes | Yes | 21.4 | 22.1 | -0.7 | BAED7F8464BB463D80DF59E44EF45CE8 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Oroville | CA | 95966-8937 |  | 2014-06-04 | 2014-06-04 16:35 | 2014-06-04 16:51 | AMANA - PGB48C0902E | 91 | 2.7 | Yes | Yes | 21 | 21 | 0 | 3468C3D73DD542CEB31272F0C59014FF |  | R22 | Non-TXV |  | 2.967% | 0.97033 | 5.702% | [5 empty] | Non-TXV | 2.967%
Stockton | CA | 95204-1538 |  | 2014-06-02 | 2014-06-02 11:22 | 2014-06-02 11:39 | DAY & NIGHT - 535A036000YACR | 60 | -4.9 | Yes | Yes | 20.8 | 20.2 | 0.6 | 38404E4A9425472080D49F94AE884F65 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.167% | 1.0817 | 2.287% |  |  |  |  | Non-TXV |  |  | -8.167%
Fresno | CA | 93703-2650 |  | 2014-05-16 | 2014-05-16 15:52 | 2014-05-16 15:52 | YORK - D1NH030N03606C | 73 | 0 | Yes | Yes | 24.8 | 23.5 | 1.3 | 36A39B544B1747FEAAF8E89D6AABD980 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95602-8220 |  | 2014-06-02 | 2014-06-02 09:28 | 2014-06-02 09:45 | DAY & NIGHT - 541DJ030 | 102 | 3.4 | Yes | Yes | 23.5 | 21.1 | 2.4 | 0728453E90C3497E942FBF8D64F1F2C2 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Yuba City | CA | 95991-6726 |  | 2014-05-15 | 2014-05-15 08:40 | 2014-05-15 09:08 | LENNOX - 10ACC-036-230-04 | 74 | 2.7 | Yes | Yes | 17 | 18.8 | -1.8 | CAE831A5F001418FAFC51AAFD0B7B46C |  | R22 | Non-TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | Non-TXV | 3.649%
Stockton | CA | 95207-2217 |  | 2014-05-30 | 2014-05-30 09:36 | 2014-05-30 10:05 | GE - UNK | 64 | -6 | Yes | Yes | 25.9 | 19.9 | 6 | 02F45E6EE28F45CC80652EF8583334B5 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Fresno | CA | 93705-3524 |  | 2014-05-21 | 2014-05-21 11:09 | 2014-05-21 11:35 | TRANE - 4YCC3036A1064AB | 124 | 7.4 | Yes | Yes | 23.3 | 17.7 | 5.6 | 29C23C4CD26A4995B5F80F7896F8D093 |  | R410A | Non-TXV |  | 5.968% | 0.94032 | 11.47% | [5 empty] | Non-TXV | 5.968%
Stockton | CA | 95207-2068 |  | 2014-06-05 | 2014-06-05 11:53 | 2014-06-05 12:10 | GIBSON - UNK | 70 | 5 | Yes | Yes | 25.5 | 23.4 | 2.1 | 5EB78F247A204A3692CB8F2C73EF578D |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Fresno | CA | 93727-4708 |  | 2014-07-02 | 2014-07-02 13:11 | 2014-07-02 13:39 | OTHER - 1262-01K | 45 | 12.4 | Yes | Yes | 24.2 | 21.2 | 3 | 9D3EE2DE81194726B62E5DAA69140AA6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 27.56% | 0.72444 | 52.96% | [5 empty] | Non-TXV | 27.56%
Newman | CA | 95360-1497 |  | 2014-06-20 | 2014-06-20 08:06 | 2014-06-20 08:35 | DAY & NIGHT - 591ANX048000ACAA | 85 | 6 | Yes | Yes | 21.1 | 20.9 | 0.2 | 0DB573E59DB149638CC9D5D0D6EF4313 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Stockton | CA | 95204-2632 |  | 2014-06-04 | 2014-06-04 14:27 | 2014-06-04 14:47 | AMANA - RCC36A2B | 114 | 8.7 | Yes | Yes | 21.6 | 19.8 | 1.8 | 1E29EAAD29D44D39BD28CCD786968DCB |  | R22 | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
Thornton | CA | 95686-0000 |  | 2014-08-26 | 2014-08-26 10:41 | 2014-08-26 11:13 | RUUD - 13AJN24A01 | 67 | -3.9 | Yes | Yes | 13.6 | 16.6 | -3 | 135CD9D55F39419F8BD7FE61B948103F |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Stockton | CA | 95209-2418 |  | 2014-05-19 | 2014-05-19 13:02 | 2014-05-19 13:21 | RUUD - UAPC-036JAZ | 150 | 8.5 | Yes | Yes | 24.7 | 18.7 | 6 | E309E455BAD649BA97280F501836D43E |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Valley Springs | CA | 95252-9565 |  | 2014-06-20 | 2014-06-20 14:46 | 2014-06-20 15:04 | HEIL - CH5536VKA1 | 125 | 4.2 | Yes | Yes | 24.8 | 23.7 | 1.1 | 53AAA7123EC948E29F4F970A421FE8EB |  | R22 | Non-TXV |  | 3.36% | 0.9664 | 6.457% | [5 empty] | Non-TXV | 3.36%
Manteca | CA | 95337-6716 |  | 2014-05-15 | 2014-05-15 12:49 | 2014-05-15 13:14 | PAYNE - 565BJ036-J | 85 | 3.9 | Yes | Yes | 23.3 | 21.2 | 2.1 | 550B3BE52D604716831067F6F66771B2 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Stockton | CA | 95204-1723 |  | 2014-06-12 | 2014-06-12 13:12 | 2014-06-12 13:30 | BDP - 561CJ048-A | 106 | 23.6 | Yes | Yes | 24.3 | 18.6 | 5.7 | 8D3B492280DC4BE4A6375F6CBF2EB296 |  | R22 | Non-TXV |  | 22.26% | 0.77736 | 42.79% | [5 empty] | Non-TXV | 22.26%
Oakdale | CA | 95361-4083 |  | 2014-05-19 | 2014-05-19 10:49 | 2014-05-19 11:11 | OTHER - TZAA-342-2A | 85 | 4 | Yes | Yes | 22.7 | 20.1 | 2.7 | 4BC3AA8D4C0640A3B594AA16189F9AE4 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Live Oak | CA | 95953-9545 |  | 2014-07-02 | 2014-07-02 10:16 | 2014-07-02 10:16 | TRANE - 2TTZ9030B1000BA | 224 | 0 | Yes | Yes | 22.9 | 18.5 | 4.4 | C6BDE1B7032F407B8A303DC9FD9ADD3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-6520 |  | 2014-06-28 | 2014-06-28 10:13 | 2014-06-28 10:30 | GOODMAN - CKL36-1D | 72 | -8 | Yes | Yes | 23.2 | 19.3 | 3.9 | 15B2F899741A4D7E800A0FCB28C8626C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -11.11% | 1.1111 | 3.112% |  |  |  |  | Non-TXV |  |  | -11.11%
Stockton | CA | 95210-4219 |  | 2014-06-06 | 2014-06-06 11:28 | 2014-06-06 11:51 | GOODMAN - GSC130241DB | 83 | 28.4 | Yes | Yes | 24.6 | 20 | 4.7 | F8ED2AF294BD4D779D65AC57B80198C2 |  | R22 | Non-TXV |  | 34.22% | 0.65783 | 65.76% | [5 empty] | Non-TXV | 34.22%
Stockton | CA | 95204-1764 |  | 2014-06-04 | 2014-06-04 13:47 | 2014-06-04 14:03 | RUUD - UAMB-060JAZ | 193 | 10.6 | Yes | Yes | 22.2 | 19.8 | 2.4 | 2D4686C4762746E893411C58D5BB643B |  | R22 | Non-TXV |  | 5.492% | 0.94508 | 10.55% | [5 empty] | Non-TXV | 5.492%
Lincoln | CA | 95648-8735 |  | 2014-06-16 | 2014-06-16 10:31 | 2014-06-16 10:47 | YORK - H2RC036S06A | 83 | 5 | Yes | Yes | 21 | 20.4 | 0.6 | DC0EAE98730E4F779E4745FAB9835EEF |  | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Stockton | CA | 95206-1931 |  | 2014-06-06 | 2014-06-06 09:29 | 2014-06-06 09:29 | RHEEM - RPPL-B030JK06X | 76 | 0 | Yes | Yes | 15.6 | 18 | -2.4 | 5D7C996DA4934CA6A1125A45991055E3 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3120 |  | 2014-06-06 | 2014-06-06 08:45 | 2014-06-06 09:03 | YORK - H2RC048S06G | 119 | 4.9 | Yes | Yes | 20 | 20.3 | -0.3 | 26948DFFA51D4277979DEB6F4FDF3B5B |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Grass Valley | CA | 95949-9129 |  | 2014-05-23 | 2014-05-23 12:20 | 2014-05-23 12:39 | GOODMAN - PGB030075 | 56 | 1.6 | Yes | Yes | 24 | 21.5 | 2.5 | F796B1411107486D8E5FD02664D61500 |  | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Red Bluff | CA | 96080-9656 |  | 2014-06-17 | 2014-06-17 11:22 | 2014-06-17 12:02 | BRYANT - 563CN036- | 60 | 6.6 | Yes | Yes | 21 | 19.6 | 1.4 | D2C825083D214F09BC4645968D4B981F |  | R22 | TXV |  | 11% | 0.89 | 21.14% | [5 empty] | TXV | 11%
Chico | CA | 95973-0912 |  | 2014-06-20 | 2014-06-20 08:06 | 2014-06-20 08:22 | LENNOX - 12GCS048X-100-4PA | 167 | 5 | Yes | Yes | 22.5 | 19.7 | 2.8 | 54E7EEEB71C5451ABA439B0D70E3B47B |  | R22 | Non-TXV |  | 2.994% | 0.97006 | 5.754% | [5 empty] | Non-TXV | 2.994%
Stockton | CA | 95207-3015 |  | 2014-05-31 | 2014-05-31 12:43 | 2014-05-31 13:19 | RHEEM - RACA-042AA0 | 70 | 10.2 | Yes | Yes | 19.7 | 20.1 | -0.4 | 2DB558E6A60445E38B9D0D5A567EE37D |  | R22 | Non-TXV |  | 14.57% | 0.85429 | 28% | [5 empty] | Non-TXV | 14.57%
Colusa | CA | 95932-3201 |  | 2014-07-03 | 2014-07-03 10:45 | 2014-07-03 11:16 | TEMPSTAR - TCGD3654153A | 85 | 3.1 | Yes | Yes | 22.5 | 21 | 1.5 | 1E13FB128D694B31BE8483491226ADDC |  | R410A | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Dos Palos | CA | 93620-2711 |  | 2014-07-09 | 2014-07-09 08:57 | 2014-07-09 09:02 | PAYNE - PY1PNB030040AAAA | 55 | 2.3 | Yes | Yes | 25.7 | 20.1 | 5.6 | B11E50A06B0E41E69E58BF8E345D8501 |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
San Miguel | CA | 93451-9118 |  | 2014-10-04 | 2014-10-04 12:06 | 2014-10-04 12:26 | BRYANT - 563CN030-C | 100 | -5.9 | Yes | Yes | 25.4 | 23.1 | 2.3 | B4AEC21DF9A04C6DB54BD96885190769 |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Lathrop | CA | 95330-9757 |  | 2014-05-28 | 2014-05-28 14:16 | 2014-05-28 14:42 | CARRIER - PGD336060K001C1 | 85 | -4.6 | Yes | Yes | 25 | 23.4 | 1.6 | BE0217E17D1D4349BEA00A66917E31F3 |  | R410A | TXV |  | -5.412% | 1.0541 | 1.516% |  |  |  |  | TXV |  |  | -5.412%
Fresno | CA | 93725-1708 |  | 2014-06-16 | 2014-06-16 12:00 | 2014-06-16 12:01 | YORK - D1NA036N05606C | 67 | 9.8 | Yes | Yes | 27.2 | 22.6 | 4.6 | C91F98D038344F9CBAEB5531D394A94B |  | R22 | Non-TXV |  | 14.63% | 0.85373 | 28.11% | [5 empty] | Non-TXV | 14.63%
Lincoln | CA | 95648-0000 |  | 2014-05-20 | 2014-05-20 14:59 | 2014-05-20 15:17 | LENNOX - 13ACD-060-230-05 | 160 | 4.8 | Yes | Yes | 21 | 20.9 | 0.1 | 7E29BDA90A2E4706872F50F0AA6A6B60 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Lincoln | CA | 95648-8107 |  | 2014-05-20 | 2014-05-20 12:06 | 2014-05-20 12:41 | YORK - H2RC036S06A | 83 | 2.4 | Yes | Yes | 23 | 20.1 | 2.9 | BE3DA313C5DD4F75B0E1A538DD682CBB |  | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Fresno | CA | 93705-1733 |  | 2014-05-22 | 2014-05-22 12:29 | 2014-05-22 12:49 | YORK - D1NP036N05606A | 108 | 16.6 | Yes | Yes | 19.9 | 19.5 | 0.4 | EA20BA9A14D04BFCA9AC231178B87E52 |  | R22 | Non-TXV |  | 15.37% | 0.8463 | 29.54% | [5 empty] | Non-TXV | 15.37%
Dinuba | CA | 93618-4046 |  | 2014-07-10 | 2014-07-10 17:48 | 2014-07-10 18:32 | NORDYNE - FS3BA-030KA | 68 | 7.7 | Yes | Yes | 20.8 | 20.8 | 0 | FE2AF3BAE1EE409886C28DAF93C14629 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.32% | 0.88676 | 21.76% | [5 empty] | Non-TXV | 11.32%
Williams | CA | 95987-0000 |  | 2014-09-18 | 2014-09-18 09:50 | 2014-09-18 10:16 | RHEEM - 13AJM48A0I | 144 | 11.4 | Yes | Yes | 22.6 | 19.4 | 3.2 | 715B0F30B1BC4B8AB9CF89E473A4296A |  | R410A | Non-TXV |  | 7.917% | 0.92083 | 15.21% | [5 empty] | Non-TXV | 7.917%
Stockton | CA | 95206-6159 |  | 2014-06-05 | 2014-06-05 15:08 | 2014-06-05 15:37 | BRYANT - 38CKC048360 | 109 | 9.2 | Yes | Yes | 19.7 | 19.9 | -0.2 | 9CA2C694F30E4FCF8BFE034BC4E0C43A |  | R22 | TXV |  | 8.44% | 0.9156 | 16.22% | [5 empty] | TXV | 8.44%
Fresno | CA | 93727-4859 |  | 2014-06-24 | 2014-06-24 12:41 | 2014-06-24 12:43 | BDP - 585HJ024040 | 68 | 4.4 | Yes | Yes | 20.4 | 20.2 | 0.2 | 09139C15ED30417094D8F1D562504141 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Merced | CA | 95340-3645 |  | 2014-05-19 | 2014-05-19 10:27 | 2014-05-19 10:44 | UNK - UNK | 85 | 3.3 | Yes | Yes | 22.8 | 17.7 | 5.1 | C0A2D79CB4B747519C77E15E4B98CF9C |  |  |  |  | 3.882% | 0.96118 | 7.461% | [5 empty] | 0 | 3.882%
Tracy | CA | 95376-2629 |  | 2014-05-21 | 2014-05-21 15:17 | 2014-05-21 15:40 | PAYNE - PY3GNAA30060NA | 98 | 8 | Yes | Yes | 25.6 | 21 | 4.6 | 920927CA721646B589E68F094A31C289 |  | R22 | Non-TXV |  | 8.163% | 0.91837 | 15.69% | [5 empty] | Non-TXV | 8.163%
Fresno | CA | 93727-7833 |  | 2014-06-26 | 2014-06-26 13:31 | 2014-06-26 13:33 | ARMSTRONG - 7777UNK | 84 | 2.7 | Yes | Yes | 24.2 | 20.1 | 4.1 | 2B8F410CB3444286A1CEAFBE18DC2453 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Fresno | CA | 93703-1313 |  | 2014-05-22 | 2014-05-22 13:34 | 2014-05-22 14:11 | CARRIER - N/A | 120 | 6.2 | Yes | Yes | 17.9 | 20.4 | -2.5 | 7ED6A7F12C8C4EA9B91E9926A2AA557C |  | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Fresno | CA | 93727-4861 |  | 2014-07-03 | 2014-07-03 14:11 | 2014-07-03 14:39 | BDP - 585HJW024040 | 68 | 5.1 | Yes | Yes | 20.3 | 20.6 | -0.2 | 1823F296E8174712A1BB5C828E794FD8 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Chico | CA | 95973-0920 |  | 2014-05-21 | 2014-05-21 12:25 | 2014-05-21 12:53 | OTHER - R2A348GKR2 | 136 | 11 | Yes | Yes | 24.8 | 20.7 | 4.1 | A34F0D5A19B640178033DB523BF0994D |  | R22 | TXV |  | 8.088% | 0.91912 | 15.54% | [5 empty] | TXV | 8.088%
Lincoln | CA | 95648-1538 |  | 2014-05-20 | 2014-05-20 14:00 | 2014-05-20 14:16 | ARMSTRONG - SCU12E24A-1A | 73 | 5.1 | Yes | Yes | 18 | 18.2 | -0.2 | D5D9BD89740340F3BA36D32AB35C70B5 |  | R22 | Non-TXV |  | 6.986% | 0.93014 | 13.43% | [5 empty] | Non-TXV | 6.986%
Lathrop | CA | 95330-9061 |  | 2014-05-28 | 2014-05-28 09:20 | 2014-05-28 09:41 | TRANE - 2TTB3042A1000AA | 109 | 5.8 | Yes | Yes | 22.8 | 21.1 | 1.8 | C2A40D13FDFA4852A97A59B70BED3E12 |  | R22 | Non-TXV |  | 5.321% | 0.94679 | 10.23% | [5 empty] | Non-TXV | 5.321%
Fresno | CA | 93705-3543 |  | 2014-05-23 | 2014-05-23 14:13 | 2014-05-23 14:31 | OTHER - 48D003 | 49 | 9.9 | Yes | Yes | 19.9 | 21.3 | -1.4 | FE6AECB78E254735BEF84D05AAF9327A |  | R22 | Non-TXV |  | 20.2% | 0.79796 | 38.83% | [5 empty] | Non-TXV | 20.2%
Friant | CA | 93626-9751 |  | 2014-10-22 | 2014-10-22 13:05 | 2014-10-22 13:06 | YORK - H2RC048S06G | 119 | 12.9 | Yes | Yes | 22.7 | 22 | 0.7 | 037583E0D1484E0B9801AEE1BEBCB15A |  | R22 | Non-TXV |  | 10.84% | 0.8916 | 20.83% | [5 empty] | Non-TXV | 10.84%
Friant | CA | 93626-9751 |  | 2014-10-22 | 2014-10-22 13:44 | 2014-10-22 13:45 | YORK - H2RC048S06G | 119 | 15.4 | Yes | Yes | 20.2 | 17.9 | 2.3 | 38EF80B5E8534606949116EB809F7D9D |  | R22 | Non-TXV |  | 12.94% | 0.87059 | 24.87% | [5 empty] | Non-TXV | 12.94%
Friant | CA | 93626-9751 |  | 2014-10-22 | 2014-10-22 13:46 | 2014-10-22 13:48 | YORK - H2RC048S06G | 119 | 6.7 | Yes | Yes | 20.4 | 20.4 | 0 | 349447A1F0B3445CB721BBB50FADD0B8 |  | R22 | Non-TXV |  | 5.63% | 0.9437 | 10.82% | [5 empty] | Non-TXV | 5.63%
Friant | CA | 93626-9751 |  | 2014-10-22 | 2014-10-22 13:49 | 2014-10-22 13:50 | YORK - H2RC048S06G | 119 | 11.8 | Yes | Yes | 20.8 | 20.8 | 0 | A0F9075583CF44469159B4B7E0B12897 |  | R22 | Non-TXV |  | 9.916% | 0.90084 | 19.06% | [5 empty] | Non-TXV | 9.916%
Friant | CA | 93626-9751 |  | 2014-10-22 | 2014-10-22 13:51 | 2014-10-22 13:52 | YORK - H2RC048S06G | 119 | 10.8 | Yes | Yes | 22 | 20.7 | 1.4 | 50290CB229054106B73D5F7B13770C1C |  | R22 | Non-TXV |  | 9.076% | 0.90924 | 17.44% | [5 empty] | Non-TXV | 9.076%
Stockton | CA | 95206-6326 |  | 2014-06-06 | 2014-06-06 09:05 | 2014-06-06 09:29 | YORK - H2RA036S06E | 63 | 7.1 | Yes | Yes | 20 | 19.9 | 0.1 | 614B7D8FCD5C4258BBD190CFFC9558BB |  | R22 | Non-TXV |  | 11.27% | 0.8873 | 21.66% | [5 empty] | Non-TXV | 11.27%
Fresno | CA | 93704-4521 |  | 2014-06-19 | 2014-06-19 13:20 | 2014-06-19 13:21 | DAY & NIGHT - 7777UNK | 100 | 5.1 | Yes | Yes | 21.4 | 20.9 | 0.5 | BC6829A6C0A441CD8BB5A1184D87B0C5 |  | R22 | Non-TXV |  | 5.1% | 0.949 | 9.801% | [5 empty] | Non-TXV | 5.1%
Clovis | CA | 93612-2447 |  | 2014-06-30 | 2014-06-30 11:54 | 2014-06-30 12:01 | CARRIER - 38CK024300 | 65 | 7.3 | Yes | Yes | 16.4 | 17.5 | -1.1 | 6DC290808CAF4E81AA9162DDBF512D77 |  | R22 | Non-TXV |  | 11.23% | 0.88769 | 21.58% | [5 empty] | Non-TXV | 11.23%
Tracy | CA | 95376-4350 |  | 2014-06-09 | 2014-06-09 09:51 | 2014-06-09 10:08 | PAYNE - 588NW0360606ABAF | 67 | 5.8 | Yes | Yes | 23.6 | 21.2 | 2.5 | 116C6CF88E724C7CB31B80F0D55682FC |  | R22 | Non-TXV |  | 8.657% | 0.91343 | 16.64% | [5 empty] | Non-TXV | 8.657%
Valley Springs | CA | 95252-8641 |  | 2014-06-19 | 2014-06-19 08:28 | 2014-06-19 08:47 | YORK - BRCQ0481BD | 103 | -6.1 | Yes | Yes | 28 | 22 | 6 | 795B763C6F8D4EDAA953C500739B3180 |  | R22 | Non-TXV |  | -5.922% | 1.0592 | 1.659% |  |  |  |  | Non-TXV |  |  | -5.922%
Olivehurst | CA | 95961-9335 |  | 2014-08-15 | 2014-08-15 08:07 | 2014-08-15 08:33 | COLEMAN - UNK | 55 | 1.6 | Yes | Yes | 20 | 18.2 | 1.8 | 1F42DF94533B448D9C53296798E6DE72 |  | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Lincoln | CA | 95648-2458 |  | 2014-05-20 | 2014-05-20 08:11 | 2014-05-20 08:58 | YORK - H1RA048S06D | 117 | 3.5 | Yes | Yes | 20 | 20.4 | -0.4 | 2A4BC79E92F047B3BB488919B2E45943 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Paradise | CA | 95969-2604 |  | 2014-05-22 | 2014-05-22 15:58 | 2014-05-22 16:15 | RHEEM - UANL-024-JEZ | 67 | 7.5 | Yes | Yes | 23 | 21 | 2 | C6927C81F0F44F61920BB9B33BACD919 |  | R22 | Non-TXV |  | 11.19% | 0.88806 | 21.51% | [5 empty] | Non-TXV | 11.19%
Fresno | CA | 93702-3810 |  | 2014-05-21 | 2014-05-21 12:00 | 2014-05-21 12:20 | GOODMAN - GPG13420701A | 107 | 3.3 | Yes | Yes | 25.7 | 20.4 | 5.3 | E534A6F7510B4306B5229E228E6FC2C7 |  | R22 | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Rocklin | CA | 95677-2856 |  | 2014-05-22 | 2014-05-22 15:36 | 2014-05-22 16:01 | AMERICAN STANDARD - 2A7A1036A1000A | 73 | 2.2 | Yes | Yes | 20 | 20.4 | -0.4 | DF29EF2D6A444D82A3A54AB6FE348929 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Lodi | CA | 95240-0822 |  | 2014-08-04 | 2014-08-04 09:13 | 2014-08-04 09:31 | GUARDIAN - GCGD42S21S2C | 112 | 4.3 | Yes | Yes | 17.3 | 18.2 | -0.9 | 29AA4F9633E4472E9592E62B04D4FC09 |  | R22 | Non-TXV |  | 3.839% | 0.96161 | 7.378% | [5 empty] | Non-TXV | 3.839%
Olivehurst | CA | 95961-0000 |  | 2014-05-28 | 2014-05-28 16:32 | 2014-05-28 16:32 | GIBSON - JT3BA-048KA | 134 | 0 | Yes | Yes | 23 | 24.7 | -1.7 | C2DD3A6C05B54B939A088123757A55AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-5777 |  | 2014-09-10 | 2014-09-10 08:57 | 2014-09-10 09:18 | PAYNE - 591ANX018000AAAA | 46 | 8.4 | Yes | Yes | 20.2 | 19.9 | 0.3 | C3AF894D545749EEA663186EAAC96E6C |  | R22 | Non-TXV |  | 18.26% | 0.81739 | 35.09% | [5 empty] | Non-TXV | 18.26%
Lathrop | CA | 95330-9192 |  | 2014-06-03 | 2014-06-03 09:13 | 2014-06-03 09:36 | CARRIER - 38BRC060350 | 280 | 12.5 | Yes | Yes | 17.8 | 19.4 | -1.6 | 6E968F49D1AF491D89E5605623735C37 |  | R22 | TXV |  | 4.464% | 0.95536 | 8.579% | [5 empty] | TXV | 4.464%
Manteca | CA | 95336-7092 |  | 2014-06-25 | 2014-06-25 14:07 | 2014-06-25 14:24 | BRYANT - 563CN048-H | 208 | 7.8 | Yes | Yes | 23.2 | 21 | 2.2 | 5957338CC47C4A60815D929A87584AEF |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Dos Palos | CA | 93620-2565 |  | 2014-07-09 | 2014-07-09 09:07 | 2014-07-09 09:09 | OTHER - ES4BD030KB | 76 | 2.5 | Yes | Yes | 24.8 | 20.1 | 4.7 | 66AE458288414CD1958ED4C16796A39A |  | R410A | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Paradise | CA | 95969-4231 |  | 2014-06-13 | 2014-06-13 11:08 | 2014-06-13 11:50 | PAYNE - 24/80YAC1060 | 59 | 8 | Yes | Yes | 18.7 | 21.5 | -2.8 | 96D487880FDD42EDBB3F5B759E2D66D3 |  | R22 | Non-TXV |  | 13.56% | 0.86441 | 26.06% | [5 empty] | Non-TXV | 13.56%
Corning | CA | 96021-2265 |  | 2014-05-28 | 2014-05-28 12:01 | 2014-05-28 12:26 | RHEEM - VAFD-024JAS | 67 | 6.5 | Yes | Yes | 27 | 21 | 6 | 58A45D8BD2764A4EA9297D4D0A28CF43 |  | R22 | Non-TXV |  | 9.701% | 0.90299 | 18.64% | [5 empty] | Non-TXV | 9.701%
Stockton | CA | 95207-8128 |  | 2014-05-22 | 2014-05-22 10:09 | 2014-05-22 10:27 | DAY & NIGHT - 585EJ24050 | 54 | 2.8 | Yes | Yes | 22.3 | 18.2 | 4.1 | 25D434DA4D4E4284B58AC7807C0C027E |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Fresno | CA | 93720-2537 |  | 2014-06-04 | 2014-06-04 09:34 | 2014-06-04 09:52 | TAPPAN - UNK | 67 | 11.2 | Yes | Yes | 22.2 | 19.4 | 2.8 | 77A3BBF4F5EB4A4BAA529BBD9EC4C03C |  | R22 | Non-TXV |  | 16.72% | 0.83284 | 32.13% | [5 empty] | Non-TXV | 16.72%
Fresno | CA | 93726-0939 |  | 2014-07-22 | 2014-07-22 08:25 | 2014-07-22 08:26 | GOODMAN - 7777UNK | 84 | 3 | Yes | Yes | 21.7 | 20.2 | 1.5 | C21C337D226C46CEA4DBA9C78C17DE6E |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Madera | CA | 93637-4925 |  | 2014-05-30 | 2014-05-30 10:50 | 2014-05-30 11:09 | CARRIER - 03060 | 76 | 6.3 | Yes | Yes | 25.8 | 21 | 4.8 | 7A0ED036DC904BA0BAC7F1C09104B927 |  | R22 | TXV |  | 8.289% | 0.91711 | 15.93% | [5 empty] | TXV | 8.289%
Fresno | CA | 93726-5110 |  | 2014-07-01 | 2014-07-01 14:09 | 2014-07-01 14:28 | LENNOX - 10GCS024X-7-50-5PA | 52 | 4.3 | Yes | Yes | 19.3 | 21.5 | -2.2 | BE741DF398C744FBA89B131466C6F38E |  | R22 | Non-TXV |  | 8.269% | 0.91731 | 15.89% | [5 empty] | Non-TXV | 8.269%
Tracy | CA | 95376-5443 |  | 2014-05-29 | 2014-05-29 08:17 | 2014-05-29 08:44 | RHEEM - RAFD-048JBS | 85 | -8 | Yes | Yes | 23 | 22.8 | 0.2 | CDB09443D6FB4979B8A5ADB910D40C2A |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
San Andreas | CA | 95249-9631 |  | 2014-09-08 | 2014-09-08 08:28 | 2014-09-08 08:28 | OTHER - UKN | 53 | 0 | Yes | Yes | 17.9 | 18.2 | -0.3 | F96EB1D961EA48C5ADB7EA065891894F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6417 |  | 2014-06-06 | 2014-06-06 11:26 | 2014-06-06 12:02 | CARRIER - 38BRC042340 | 171 | 10.7 | Yes | Yes | 20.9 | 21 | -0.1 | F7FA52D39FAB42A1B500119C3733E1F4 |  | R22 | TXV |  | 6.257% | 0.93743 | 12.03% | [5 empty] | TXV | 6.257%
Parlier | CA | 93648-2113 |  | 2014-06-17 | 2014-06-17 16:08 | 2014-06-17 16:41 | RUUD - N/A | 105 | 9.3 | Yes | Yes | 26.5 | 22.6 | 3.9 | CC002DE8B2474A7CAB5D77BFBD51CA2B |  | R22 | Non-TXV |  | 8.857% | 0.91143 | 17.02% | [5 empty] | Non-TXV | 8.857%
Fresno | CA | 93705-1751 |  | 2014-05-22 | 2014-05-22 13:03 | 2014-05-22 13:19 | BDP - 561CJ042 | 80 | 10.1 | Yes | Yes | 20.4 | 19.6 | 0.8 | 8F93DAD94BC04A01B00CCC7F1B658B5B |  | R22 | TXV |  | 12.62% | 0.87375 | 24.26% | [5 empty] | TXV | 12.62%
Caruthers | CA | 93609-9434 |  | 2014-10-06 | 2014-10-06 10:19 | 2014-10-06 10:36 | DAY & NIGHT - 597CN030-A | 87 | 3.7 | Yes | Yes | 19.6 | 19.3 | 0.3 | B1C98E9AF4C944E08D85C211551DCA46 |  | R22 | TXV |  | 4.253% | 0.95747 | 8.173% | [5 empty] | TXV | 4.253%
Yuba City | CA | 95991-4921 |  | 2014-05-21 | 2014-05-21 18:05 | 2014-05-21 18:27 | LENNOX - GCS10-261-50-1P | 62 | 2.3 | Yes | Yes | 23 | 23.1 | -0.1 | FB48E9450B0246969CFC53E0567A5014 |  | R22 | Non-TXV |  | 3.71% | 0.9629 | 7.129% | [5 empty] | Non-TXV | 3.71%
Dinuba | CA | 93618-4059 |  | 2014-07-15 | 2014-07-15 15:11 | 2014-07-15 15:39 | UNITARY PRODUCTS GROUP - H2RD030S6B | 93 | 2.9 | Yes | Yes | 20.9 | 20.8 | 0.1 | 7CDB88842A4B4CD6BCD76C098405D3E5 |  | R22 | Non-TXV |  | 3.118% | 0.96882 | 5.993% | [5 empty] | Non-TXV | 3.118%
Rocklin | CA | 95677-1701 |  | 2014-06-09 | 2014-06-09 13:18 | 2014-06-09 13:34 | RHEEM - RAKA-037JAZ | 79 | 2.4 | Yes | Yes | 19.5 | 21 | -1.5 | F6088668D9FC4AD293CF9F9B9BB65D83 |  | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Stockton | CA | 95206-6136 |  | 2014-06-09 | 2014-06-09 13:15 | 2014-06-09 13:15 | YORK - H2RA030S06A | 62 | 0 | Yes | Yes | 18.9 | 19.6 | -0.7 | 0684E1A9989D4482AAF32562883D7BA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1548 |  | 2014-06-02 | 2014-06-02 16:10 | 2014-06-02 16:28 | YORK - D1NH030N03606C | 73 | 12.6 | Yes | Yes | 21.7 | 18.4 | 3.3 | F2C1DE384B324A1198F61D7A89B7CED7 |  | R22 | Non-TXV |  | 17.26% | 0.8274 | 33.17% | [5 empty] | Non-TXV | 17.26%
Yuba City | CA | 95993-8283 |  | 2014-05-19 | 2014-05-19 13:17 | 2014-05-19 13:45 | UNK - UNK | 85 | 6.9 | Yes | Yes | 18 | 20.4 | -2.4 | 46BF82B8D3FA42A5BF1B829B4ACF92AA |  |  |  |  | 8.118% | 0.91882 | 15.6% | [5 empty] | 0 | 8.118%
Paradise | CA | 95969-5235 |  | 2014-06-13 | 2014-06-13 14:34 | 2014-06-13 14:45 | COLEMAN - 0RCSO481BB | 125 | 13.7 | Yes | Yes | 26.3 | 20.4 | 5.9 | 88542E9D902C4A668316717D62D38DCB |  | R22 | Non-TXV |  | 10.96% | 0.8904 | 21.06% | [5 empty] | Non-TXV | 10.96%
San Andreas | CA | 95249-9508 |  | 2014-08-28 | 2014-08-28 08:21 | 2014-08-28 08:41 | COLEMAN - BRC00361BD | 52 | 20.4 | Yes | Yes | 20.1 | 18.2 | 1.9 | FBCA2135365546B895D60C3C5F9BFE8F |  | R22 | Non-TXV |  | 39.23% | 0.60769 | 75.39% | [5 empty] | Non-TXV | 39.23%
Merced | CA | 95341-5242 |  | 2014-05-15 | 2014-05-15 10:51 | 2014-05-15 10:51 | ICP - GPC060K100F | 133 | 0 | Yes | Yes | 22.8 | 20.2 | 2.6 | D5282A2B66E841E39CF824D93394A385 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3404 |  | 2014-06-03 | 2014-06-03 10:36 | 2014-06-03 10:53 | DAY & NIGHT - 567C042RCU | 74 | -5.2 | Yes | Yes | 23 | 19.1 | 3.9 | 8965BAE796EF41F68C42ADE1956645EE |  | R22 | Non-TXV |  | -7.027% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.027%
Tracy | CA | 95376-7701 |  | 2014-06-17 | 2014-06-17 12:31 | 2014-06-17 12:51 | YORK - 585HJW024040A8BAE | 68 | 5.5 | Yes | Yes | 26.3 | 21 | 5.3 | 9F65A51EC9194DB7A4F35E11F1E828FA |  | R22 | Non-TXV |  | 8.088% | 0.91912 | 15.54% | [5 empty] | Non-TXV | 8.088%
Oakdale | CA | 95361-3201 |  | 2014-05-20 | 2014-05-20 14:41 | 2014-05-20 15:32 | RHEEM - 13ANJ48A01 | 85 | 4.6 | Yes | Yes | 22.5 | 20.4 | 2.1 | 73EB14DC7B36472E9F07B799887590F8 |  | R410A | TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | TXV | 5.412%
Fresno | CA | 93702-2408 |  | 2014-05-21 | 2014-05-21 10:46 | 2014-05-21 11:27 | YORK - D1NA024N03606C | 54 | 5.5 | Yes | Yes | 24.5 | 21.7 | 2.8 | 188649C334C2440FB59A51AEDEA6715F |  | R22 | Non-TXV |  | 10.19% | 0.89815 | 19.57% | [5 empty] | Non-TXV | 10.19%
Orland | CA | 95963-1500 |  | 2014-06-17 | 2014-06-17 08:36 | 2014-06-17 09:07 | ALLEGIANCE - | 135 | 5 | Yes | Yes | 19 | 19.8 | -0.8 | 65425E3B38414DB787CA195F89E0F70E |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Orland | CA | 95963-9349 |  | 2014-05-28 | 2014-05-28 21:35 | 2014-05-28 09:55 | PAYNE - NA | 55 | 10.2 | Yes | Yes | 20.5 | 22.9 | -2.4 | 3E6800FBC7AE464093676969BD5CCE42 |  | R22 | Non-TXV |  | 18.55% | 0.81455 | 35.64% | [5 empty] | Non-TXV | 18.55%
Stockton | CA | 95206-6018 |  | 2014-06-16 | 2014-06-16 08:14 | 2014-06-16 08:41 | GOODMAN - GSX160301FA | 85 | 9.3 | Yes | Yes | 21.1 | 20.3 | 0.8 | CF2F49FBEC6041549B222538725C503A |  | R410A | TXV |  | 10.94% | 0.89059 | 21.03% | [5 empty] | TXV | 10.94%
Fresno | CA | 93727-7954 |  | 2014-06-06 | 2014-06-06 14:18 | 2014-06-06 14:39 | CARRIER - 48GX-036060301 | 82 | 2.5 | Yes | Yes | 23 | 23.7 | -0.7 | 25E17329B1854A57A2BA24CECC076F5F |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Tracy | CA | 95376-1442 |  | 2014-05-21 | 2014-05-21 11:48 | 2014-05-21 12:09 | RHEEM - UNK | 85 | -8 | Yes | Yes | 19.8 | 21.5 | -1.7 | EE7D9745A2C748D287F63172B023E17A |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93727-5450 |  | 2014-07-16 | 2014-07-16 12:02 | 2014-07-16 12:04 | OTHER - 7777UNK | 74 | 3.7 | Yes | Yes | 17.1 | 19.8 | -2.7 | F0DB763454FC4349A5CD81B9ED941FBD |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Tracy | CA | 95376-5201 |  | 2014-05-29 | 2014-05-29 08:57 | 2014-05-29 09:22 | RUUD - JAHE-048JAS | 85 | 17.2 | Yes | Yes | 20.4 | 21.7 | -1.3 | D6AB93DE7B284BB79E4723B96B96493A |  | R22 | Non-TXV |  | 20.24% | 0.79765 | 38.89% | [5 empty] | Non-TXV | 20.24%
Clovis | CA | 93612-5868 |  | 2014-06-05 | 2014-06-05 13:41 | 2014-06-05 13:58 | PAYNE - 5BOAN036060 | 76 | 16.5 | Yes | Yes | 23.6 | 21.2 | 2.4 | 5C966329F39C43CD8258699442275808 |  | R22 | Non-TXV |  | 21.71% | 0.78289 | 41.72% | [5 empty] | Non-TXV | 21.71%
Fresno | CA | 93722-5802 |  | 2014-05-22 | 2014-05-22 10:49 | 2014-05-22 10:50 | RUUD - UKAKA-030JAZ | 66 | 2.8 | Yes | Yes | 21.7 | 19.3 | 2.4 | 25918BF31F0B43E5BD5311A902553A0B |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Stockton | CA | 95204-2009 |  | 2014-06-14 | 2014-06-14 09:16 | 2014-06-14 09:34 | TRANE - TTN030C100C2 | 95 | -5.6 | Yes | Yes | 23 | 19.5 | 3.5 | CC8C30BE82D7461BA3DB6AAF69F59605 |  | R22 | Non-TXV |  | -5.895% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Stockton | CA | 95207-2925 |  | 2014-05-30 | 2014-05-30 11:56 | 2014-05-30 12:21 | TRANE - 2TTB3036A1000AA | 101 | 21.9 | Yes | Yes | 20.7 | 20.8 | -0.1 | C38527AC189949A99DAFC12A548C30B8 |  | R22 | Non-TXV |  | 21.68% | 0.78317 | 41.67% | [5 empty] | Non-TXV | 21.68%
San Miguel | CA | 93451-9109 |  | 2014-10-04 | 2014-10-04 12:28 | 2014-10-04 12:58 | DUCANE - AC10B42-A | 98 | 3.4 | Yes | Yes | 19.7 | 21.1 | -1.4 | 77BD89BB2DDB441FA7E7C9200A4840D8 |  | R22 | Non-TXV |  | 3.469% | 0.96531 | 6.667% | [5 empty] | Non-TXV | 3.469%
Chico | CA | 95926-1033 |  | 2014-05-16 | 2014-05-16 11:15 | 2014-05-16 11:32 | RHEEM - NA | 59 | 3.5 | Yes | Yes | 20.8 | 20.3 | 0.5 | 198BDC5C715E4D8881C9D3198756A695 |  | R22 | Non-TXV |  | 5.932% | 0.94068 | 11.4% | [5 empty] | Non-TXV | 5.932%
Fresno | CA | 93727-5449 |  | 2014-07-16 | 2014-07-16 12:25 | 2014-07-16 12:27 | OTHER - 7777UNK | 64 | 2.3 | Yes | Yes | 16.7 | 19.5 | -2.8 | 09010171A9FC4522A591C7863E93B2C7 |  | R22 | Non-TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | Non-TXV | 3.594%
El Dorado Hills | CA | 95762-7561 |  | 2014-07-22 | 2014-07-22 11:20 | 2014-07-22 11:40 | YORK - H3RA060S06A | 106 | 3.7 | Yes | Yes | 19 | 18.6 | 0.4 | 486222735E3A49499DA01A72ACFA39C1 |  | R22 | Non-TXV |  | 3.491% | 0.96509 | 6.708% | [5 empty] | Non-TXV | 3.491%
Stockton | CA | 95207-3132 |  | 2014-06-18 | 2014-06-18 14:37 | 2014-06-18 14:54 | PAYNE - 582ANW024060AAAD | 53 | 3 | Yes | Yes | 22.6 | 22.1 | 0.5 | FCBDE7E620F240A387AE6C612BA6696A |  | R22 | Non-TXV |  | 5.66% | 0.9434 | 10.88% | [5 empty] | Non-TXV | 5.66%
Lincoln | CA | 95648-8382 |  | 2014-05-20 | 2014-05-20 11:18 | 2014-05-20 12:06 | YORK - H2RC036S06A | 83 | 2.4 | Yes | Yes | 19 | 20.4 | -1.4 | 3AC3A3FD83524B46A25011178A9AA304 |  | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Stockton | CA | 95206-4828 |  | 2014-06-11 | 2014-06-11 11:48 | 2014-06-11 12:07 | GOODMAN - CE36-1GB | 85 | 4.7 | Yes | Yes | 20.2 | 21 | -0.8 | CC734AD6094D456685500530B9656AE9 |  | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Fresno | CA | 93705-1238 |  | 2014-05-22 | 2014-05-22 10:39 | 2014-05-22 10:57 | ICP - GPFM36K060A | 71 | 7 | Yes | Yes | 25.5 | 21 | 4.5 | 25560B8C7C1045BE809B9674D4CF4E1F |  | R22 | Non-TXV |  | 9.859% | 0.90141 | 18.95% | [5 empty] | Non-TXV | 9.859%
Stockton | CA | 95215-1022 |  | 2014-06-04 | 2014-06-04 12:50 | 2014-06-04 13:10 | AMANA - PGD36C0702G | 132 | 4.2 | Yes | Yes | 25.1 | 19.1 | 6 | 3843A9FC25B548539329A5E7268C8743 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Paradise | CA | 95969-2204 |  | 2014-06-25 | 2014-06-25 13:35 | 2014-06-25 14:00 | OTHER - CFG048D3A | 50 | 2.6 | Yes | Yes | 23 | 18.7 | 4.3 | BE7628BCA99D4DE28E185FD32FAF7432 |  | R22 | Non-TXV |  | 5.2% | 0.948 | 9.993% | [5 empty] | Non-TXV | 5.2%
Merced | CA | 95340-1674 |  | 2014-05-21 | 2014-05-21 16:08 | 2014-05-21 16:10 | AMANA - 777UNK | 145 | 5.3 | Yes | Yes | 23.3 | 20.4 | 2.9 | 20D8B4D3856C4047A998CA7EA743077E |  | R410A | Non-TXV |  | 3.655% | 0.96345 | 7.024% | [5 empty] | Non-TXV | 3.655%
Parlier | CA | 93648-2126 |  | 2014-06-17 | 2014-06-17 17:24 | 2014-06-17 17:48 | RHEEM - RRNA-B042JK08X | 104 | 5.8 | Yes | Yes | 21 | 21.4 | -0.4 | F4C70566A9AC4976B2D8B490F24E2427 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Fresno | CA | 93726-5110 |  | 2014-06-24 | 2014-06-24 12:25 | 2014-06-24 12:27 | LENNOX - 10GCS024X503PA | 52 | 5.1 | Yes | Yes | 21 | 19.7 | 1.3 | FCA860B9C9B1498790588627EB560170 |  | R22 | Non-TXV |  | 9.808% | 0.90192 | 18.85% | [5 empty] | Non-TXV | 9.808%
Stockton | CA | 95206-6406 |  | 2014-06-06 | 2014-06-06 09:54 | 2014-06-06 10:16 | GOODMAN - CKL42-1A | 85 | -7 | Yes | Yes | 22.4 | 19.9 | 2.5 | 8D4BA0FE585A4F7B97CDA8F03179F640 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Chowchilla | CA | 93610-9465 |  | 2014-06-19 | 2014-06-19 15:40 | 2014-06-19 15:41 | TRANE - 4YCC3036A1075AB | 124 | 10.6 | Yes | Yes | 24.6 | 22 | 2.6 | 71324998F124409DA60C97CC5866B9E6 |  | R410A | Non-TXV |  | 8.548% | 0.91452 | 16.43% | [5 empty] | Non-TXV | 8.548%
Fresno | CA | 93726-5110 |  | 2014-07-15 | 2014-07-15 13:32 | 2014-07-15 13:33 | BDP - 585B024050YACR | 51 | 7.4 | Yes | Yes | 22.2 | 20.8 | 1.4 | 5B8DE074106740F6A2E756A29667CF6F |  | R22 | Non-TXV |  | 14.51% | 0.8549 | 27.88% | [5 empty] | Non-TXV | 14.51%
Fresno | CA | 93703-3304 |  | 2014-05-16 | 2014-05-16 16:37 | 2014-05-16 16:58 | GOODMAN - PGB036075-1A | 60 | 3.9 | Yes | Yes | 21.4 | 23.1 | -1.7 | 4272CF368CF349A58D237736C65EB1F3 |  | R22 | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Reedley | CA | 93654-2052 |  | 2014-08-04 | 2014-08-04 12:56 | 2014-08-04 13:16 | CARRIER - 48GS-030060301 | 55 | 3.6 | Yes | Yes | 17.8 | 20.4 | -2.6 | DFDA1822354843189993CB050901F2D9 |  | R22 | Non-TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | Non-TXV | 6.545%
Fresno | CA | 93722-8509 |  | 2014-05-23 | 2014-05-23 10:40 | 2014-05-23 10:58 | LENNOX - 13ACC06023002 | 168 | 12.5 | Yes | Yes | 21.4 | 15.9 | 5.5 | DFA53DA1FD054697BF9876B3067DA8BF |  | R22 | Non-TXV |  | 7.44% | 0.9256 | 14.3% | [5 empty] | Non-TXV | 7.44%
Fresno | CA | 93727-7506 |  | 2014-06-09 | 2014-06-09 16:00 | 2014-06-09 16:28 | AMERICAN STANDARD - 7A2060A100A2 | 288 | 8.8 | Yes | Yes | 24.3 | 20.8 | 3.5 | D7EA55FC027A498F9DFA2FE21C999838 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Stockton | CA | 95204-2635 |  | 2014-07-31 | 2014-07-31 13:48 | 2014-07-31 14:23 | CARRIER - 48DL045 | 82 | 3.1 | Yes | Yes | 17.9 | 17.7 | 0.2 | D54C5C1EEA48405580A5949E371C5A43 |  | R22 | Non-TXV |  | 3.78% | 0.9622 | 7.265% | [5 empty] | Non-TXV | 3.78%
Fresno | CA | 93704-1454 |  | 2014-06-13 | 2014-06-13 10:45 | 2014-06-13 11:07 | TRANE - TTB042C100AO | 107 | 21.1 | Yes | Yes | 25.6 | 20.9 | 4.7 | 1D8E3C20F6C64F9287E7B26781B07911 |  | R22 | Non-TXV |  | 19.72% | 0.8028 | 37.9% | [5 empty] | Non-TXV | 19.72%
Fresno | CA | 93726-5109 |  | 2014-06-24 | 2014-06-24 11:52 | 2014-06-24 11:53 | CARRIER - UNK | 56 | 10.4 | Yes | Yes | 23.8 | 21.8 | 2.1 | 40B757686E9443FFA3DD47A61773426C |  | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Tracy | CA | 95376-8772 |  | 2014-05-29 | 2014-05-29 13:06 | 2014-05-29 13:41 | RUUD - UNK | 85 | 7.5 | Yes | Yes | 21 | 22.9 | -1.9 | 8B19CE2C7B904807AD07ED87624317F7 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Tracy | CA | 95376-1469 |  | 2014-05-29 | 2014-05-29 11:28 | 2014-05-29 11:57 | BRYANT - 561CJ048-G | 121 | -13.1 | Yes | Yes | 23.3 | 22.5 | 0.8 | AB778846C2A54880BE93CD2B9147CBD0 |  | R22 | TXV |  | -10.83% | 1.1083 | 3.032% |  |  |  |  | TXV |  |  | -10.83%
Fresno | CA | 93726-5862 |  | 2014-07-14 | 2014-07-14 10:49 | 2014-07-14 10:50 | RHEEM - RRNAB042JK08X | 104 | 14.1 | Yes | Yes | 20.5 | 17.1 | 3.4 | 1137F53A98F34412BD821D762A236C59 |  | R22 | Non-TXV |  | 13.56% | 0.86442 | 26.05% | [5 empty] | Non-TXV | 13.56%
Fresno | CA | 93726-4123 |  | 2014-06-02 | 2014-06-02 13:23 | 2014-06-02 13:41 | ICP - PGAD47D1K6 | 215 | 6.5 | Yes | Yes | 21.3 | 21 | 0.3 | 26E0A6983E654CF1A92B4791B805DBF5 |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Stockton | CA | 95204-1225 |  | 2014-06-02 | 2014-06-02 11:50 | 2014-06-02 11:56 | RHEEM - HC-100-36-21C | 49 | -4.6 | Yes | Yes | 22 | 20.1 | 2 | 1F98577C1D6446D1AA2426652F35BA0C |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Atwater | CA | 95301-5208 |  | 2014-05-16 | 2014-05-16 14:31 | 2014-05-16 14:32 | OTHER - 10GCS060-100-3-PA | 110 | 7.5 | Yes | Yes | 27.9 | 23.4 | 4.6 | A166B0F594024158A2A45C3823F86D36 |  | R22 | Non-TXV |  | 6.818% | 0.93182 | 13.1% | [5 empty] | Non-TXV | 6.818%
Fresno | CA | 93726-6626 |  | 2014-07-16 | 2014-07-16 14:26 | 2014-07-16 14:27 | CARRIER - 48KLA136300BE | 102 | 3.3 | Yes | Yes | 17.8 | 19.5 | -1.7 | AD24829505904E89AB0DE888444FE7B4 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Clovis | CA | 93612-1226 |  | 2014-06-05 | 2014-06-05 10:21 | 2014-06-05 10:37 | LENNOX - PGE10A36D0751PA | 75 | 11.7 | Yes | Yes | 23.5 | 19.4 | 4.1 | E92E178AB779406CBD9110F29BDC8C94 |  | R22 | Non-TXV |  | 15.6% | 0.844 | 29.98% | [5 empty] | Non-TXV | 15.6%
Fresno | CA | 93722-4560 |  | 2014-06-14 | 2014-06-14 11:22 | 2014-06-14 11:40 | RHEEM - N/A | 60 | 4.3 | Yes | Yes | 20.1 | 20.8 | -0.7 | 63D8E42682DB4B67ACEC3488594EB8FE |  | R22 | Non-TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | Non-TXV | 7.167%
Stockton | CA | 95207-3150 |  | 2014-06-20 | 2014-06-20 10:03 | 2014-06-20 10:21 | HEIL - HAC036AKA4 | 80 | -4.7 | Yes | Yes | 23.2 | 19.5 | 3.7 | 7917F53438554A1E9F08B9639BEECC2E |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Tracy | CA | 95376-6720 |  | 2014-06-09 | 2014-06-09 12:22 | 2014-06-09 12:44 | YORK - H1RA048S06D | 117 | 7.3 | Yes | Yes | 22.2 | 20.4 | 1.8 | 0CA2569DBA984C4A86E9BDA95D47DCA4 |  | R22 | Non-TXV |  | 6.239% | 0.93761 | 11.99% | [5 empty] | Non-TXV | 6.239%
Madera | CA | 93637-9007 |  | 2014-05-30 | 2014-05-30 12:45 | 2014-05-30 13:01 | BDP - 655ANX048000AAAG | 128 | 32.2 | Yes | Yes | 23.8 | 19.7 | 4.1 | 5B1EA0559D1A458A9D56F06E2BA0E577 |  | R22 | Non-TXV |  | 25.16% | 0.74844 | 48.34% | [5 empty] | Non-TXV | 25.16%
Fresno | CA | 93711-1513 |  | 2014-05-26 | 2014-05-26 10:30 | 2014-05-26 10:48 | YORK - DCYZF042N080A | 78 | 10 | Yes | Yes | 20.1 | 18.8 | 1.3 | 618FA00A2F124B288FE5ED293AAB28E8 |  | R410A | Non-TXV |  | 12.82% | 0.87179 | 24.64% | [5 empty] | Non-TXV | 12.82%
Stockton | CA | 95206-3817 |  | 2014-07-02 | 2014-07-02 11:37 | 2014-07-02 11:57 | GUARDIAN - GCGD48S41S1A | 73 | 7.5 | Yes | Yes | 26.3 | 21.4 | 4.9 | FB125587374A48C4B8F98F3957F2B6FC |  | R410A | Non-TXV |  | 10.27% | 0.89726 | 19.74% | [5 empty] | Non-TXV | 10.27%
Fresno | CA | 93726-5202 |  | 2014-07-01 | 2014-07-01 16:46 | 2014-07-01 17:18 | CARRIER - 48KL-048-311BF | 80 | 12.8 | Yes | Yes | 21.2 | 21 | 0.2 | DFE89F7AE3704D6DBDB04AA8862B620D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Stockton | CA | 95206-3872 |  | 2014-06-09 | 2014-06-09 11:16 | 2014-06-09 11:36 | CARRIER - 38ETG036300 | 132 | 20.2 | Yes | Yes | 21.5 | 21.7 | -0.2 | BEB1D46EBBA24296BCDB385F5918AB99 |  | R410A | TXV |  | 15.3% | 0.84697 | 29.41% | [5 empty] | TXV | 15.3%
Atwater | CA | 95301-9108 |  | 2014-08-13 | 2014-08-13 10:23 | 2014-08-13 10:26 | GIBSON - JS4BD-048KA | 127 | 4.6 | Yes | Yes | 20.4 | 19.5 | 0.9 | FE6841FCB8C149BC8F69A51615F8757C |  | R410A | Non-TXV |  | 3.622% | 0.96378 | 6.961% | [5 empty] | Non-TXV | 3.622%
Oakhurst | CA | 93644-9532 |  | 2014-07-31 | 2014-07-31 14:20 | 2014-07-31 14:21 | RHEEM - RQMAA036JK000 | 106 | 13.9 | Yes | Yes | 21.3 | 21 | 0.3 | F44A088C95444449822AB90BD77FE62F |  | R22 | Non-TXV |  | 13.11% | 0.86887 | 25.2% | [5 empty] | Non-TXV | 13.11%
Fresno | CA | 93702-2038 |  | 2014-05-22 | 2014-05-22 11:02 | 2014-05-22 11:02 | RHEEM - RRPL-B024JK06X | 77 | 0 | Yes | Yes | 19.5 | 20.8 | -1.3 | 590F316014C040AC9BFE78B9F02681D6 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4255 |  | 2014-06-18 | 2014-06-18 09:07 | 2014-06-18 09:11 | RUUD - 7777UNK | 112 | 6.2 | Yes | Yes | 19.8 | 20.9 | -1.1 | A306C3CAE7474A54990C40D54BB28D1E |  | R22 | Non-TXV |  | 5.536% | 0.94464 | 10.64% | [5 empty] | Non-TXV | 5.536%
Stockton | CA | 95206-6028 |  | 2014-06-13 | 2014-06-13 10:52 | 2014-06-13 11:30 | OTHER - VCA42C2C | 85 | -8 | Yes | Yes | 22.8 | 20.4 | 2.4 | 5464B80661614FE68DC649FF0416883B |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95206-3003 |  | 2014-06-09 | 2014-06-09 10:29 | 2014-06-09 10:29 | YORK - H1RD030S06A | 121 | 0 | Yes | Yes | 15 | 16.7 | -1.7 | E650EF79377E49C59E4C44EE68CA8336 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2551 |  | 2014-05-20 | 2014-05-20 08:49 | 2014-05-20 09:07 | HEIL - HAC042AKA5 | 98 | 4.8 | Yes | Yes | 23.9 | 20.4 | 3.5 | 4C20427D3C0C4554A176A8408F1B7612 |  | R22 | Non-TXV |  | 4.898% | 0.95102 | 9.413% | [5 empty] | Non-TXV | 4.898%
Groveland | CA | 95321-9381 |  | 2014-11-03 | 2014-11-03 10:49 | 2014-11-03 12:10 | RUUD - URGG | 46 | 2.5 | Yes | Yes | 20.4 | 20.4 | 0 | B30AE0885EBC48D28F346244529317AA |  | R22 | Non-TXV |  | 5.435% | 0.94565 | 10.44% | [5 empty] | Non-TXV | 5.435%
Madera | CA | 93638-1536 |  | 2014-08-19 | 2014-08-19 08:34 | 2014-08-19 08:51 | PAYNE - 585P030075YACR | 44 | 1.3 | Yes | Yes | 17.4 | 19.7 | -2.3 | ABE0FF2BA32E4DED95A4BB0E5E31F879 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Fresno | CA | 93705-2310 |  | 2014-07-14 | 2014-07-14 12:11 | 2014-07-14 12:35 | CARRIER - UNK | 96 | -5.6 | Yes | Yes | 23.4 | 20.4 | 3 | C7EAE5C1C6AE44F98E07F49DBEA9BAA4 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95207-4828 |  | 2014-06-04 | 2014-06-04 12:05 | 2014-06-04 12:26 | YORK - D1NP036N05606A | 108 | 4.6 | Yes | Yes | 25.9 | 19.9 | 6 | A702BE4AE01A48158BA2DFC47775D901 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Fresno | CA | 93704-5631 |  | 2014-06-19 | 2014-06-19 14:13 | 2014-06-19 14:15 | LENNOX - 12GCS024-50-3PA | 72 | 3.3 | Yes | Yes | 21.4 | 20.7 | 0.7 | 642A4406008247448652F1D3E13925E8 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Fresno | CA | 93705-5036 |  | 2014-07-15 | 2014-07-15 16:09 | 2014-07-15 16:27 | BDP - 585HJ030040 | 68 | -4 | Yes | Yes | 25.2 | 20.1 | 5.1 | 9A58257E45164043B1C10168A8886191 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Paradise | CA | 95969-4724 |  | 2014-05-23 | 2014-05-23 09:30 | 2014-05-23 10:00 | DAY & NIGHT - 585A0E4080YAC | 66 | 2.9 | Yes | Yes | 23 | 21.2 | 1.8 | 27BCF9D9900B4893AEA4E8623BF05A97 |  | R22 | Non-TXV |  | 4.394% | 0.95606 | 8.444% | [5 empty] | Non-TXV | 4.394%
Red Bluff | CA | 96080-3528 |  | 2014-06-17 | 2014-06-17 16:10 | 2014-06-17 16:28 | YORK - DAYA-FO24NOAC | 54 | 8.7 | Yes | Yes | 21 | 19.7 | 1.3 | 63D640DD571844739B19CE9A1208C82B |  | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Merced | CA | 95348-3777 |  | 2014-05-19 | 2014-05-19 14:13 | 2014-05-19 14:46 | UNK - UNK | 85 | 12.3 | Yes | Yes | 27.9 | 22 | 5.9 | 9D9BCB4B005E4127B1746C7D16A5A287 |  |  |  |  | 14.47% | 0.85529 | 27.81% | [5 empty] | 0 | 14.47%
Dinuba | CA | 93618-4059 |  | 2014-07-14 | 2014-07-14 14:08 | 2014-07-14 14:29 | UNITARY PRODUCTS GROUP - 2RD024S06B | 88 | 11.6 | Yes | Yes | 19.9 | 21.4 | -1.5 | 6E105DD3A47F4698B5C349CB5062B896 |  | R22 | Non-TXV |  | 13.18% | 0.86818 | 25.33% | [5 empty] | Non-TXV | 13.18%
Stockton | CA | 95207-6040 |  | 2014-06-06 | 2014-06-06 11:49 | 2014-06-06 12:06 | BRYANT - 582ANW030060AAAD | 55 | 2.2 | Yes | Yes | 26.1 | 20.2 | 5.9 | 6B059F5677D345678CF1E4F0BF6B223E |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Manteca | CA | 95336-4918 |  | 2014-05-16 | 2014-05-16 10:04 | 2014-05-16 10:26 | BRYANT - 113ANA024-D | 128 | 7.7 | Yes | Yes | 21.2 | 23.2 | -2 | E29A86C6EBBC483E97853F9B5ABE17F2 |  | R410A | TXV |  | 6.016% | 0.93984 | 11.56% | [5 empty] | TXV | 6.016%
Stockton | CA | 95206-4950 |  | 2014-06-12 | 2014-06-12 08:00 | 2014-06-12 08:27 | GOODMAN - GSC130361AA | 85 | -5 | Yes | Yes | 21.9 | 20.4 | 1.5 | 9F1730D60A5E49F183EE019840AD26A5 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95207-4281 |  | 2014-05-21 | 2014-05-21 14:44 | 2014-05-21 15:01 | CARRIER - 38EN018310 | 55 | 1.9 | Yes | Yes | 24.6 | 20.4 | 4.2 | 273E5DF821B8464DAF7A36E8EFC592BC |  | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Fresno | CA | 93726-3241 |  | 2014-05-27 | 2014-05-27 16:17 | 2014-05-27 16:44 | YORK - D5YS036N08006A | 80 | 4.3 | Yes | Yes | 26.9 | 24.5 | 2.4 | 7D40FFF1D0444902B4C23BA170B225B3 |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Orosi | CA | 93647-9718 |  | 2014-09-04 | 2014-09-04 15:58 | 2014-09-04 16:19 | OTHER - 38BRB060300 | 70 | 5.8 | Yes | Yes | 21 | 22.1 | -1.1 | 6CB1A22DF5F74BD6B9AA971939FCDE9D |  | R22 | Non-TXV |  | 8.286% | 0.91714 | 15.92% | [5 empty] | Non-TXV | 8.286%
Red Bluff | CA | 96080-7822 |  | 2014-06-03 | 2014-06-03 15:37 | 2014-06-03 15:59 | OTHER - SCU12E48A-1A | 197 | 5.9 | Yes | Yes | 22.3 | 20.7 | 1.6 | 7F1409D0536D4BB19D78CB8403DF42FA |  | R22 | Non-TXV |  | 2.995% | 0.97005 | 5.756% | [5 empty] | Non-TXV | 2.995%
Fresno | CA | 93726-5104 |  | 2014-07-15 | 2014-07-15 09:10 | 2014-07-15 09:12 | OTHER - GPG10360701A | 75 | 9.5 | Yes | Yes | 22.6 | 17.9 | 4.7 | 08FD38F2DA744E66ADD94B4FB48DBA97 |  | R22 | Non-TXV |  | 12.67% | 0.87333 | 24.34% | [5 empty] | Non-TXV | 12.67%
Stockton | CA | 95210-4172 |  | 2014-05-31 | 2014-05-31 10:38 | 2014-05-31 11:06 | PAYNE - 593ANX048000AAAA | 172 | -10.1 | Yes | Yes | 26.9 | 20.9 | 6 | 6D9DB80048744B1D90BDCA690FE54D6E |  | R22 | Non-TXV |  | -5.872% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.872%
Fresno | CA | 93704-5837 |  | 2014-08-08 | 2014-08-08 13:14 | 2014-08-08 13:16 | GOODMAN - GPG10240451A | 50 | 9 | Yes | Yes | 19.9 | 18.2 | 1.7 | A10AF6DF78FE4BD5ACBE2E0F61BE03F7 |  | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Valley Springs | CA | 95252-9120 |  | 2014-06-19 | 2014-06-19 11:53 | 2014-06-19 12:10 | RUUD - UQMA-A036JK000 | 106 | 3.5 | Yes | Yes | 21.9 | 21.3 | 0.6 | 4BF45792733245DE81295EDE1B5C4C2F |  | R22 | Non-TXV |  | 3.302% | 0.96698 | 6.345% | [5 empty] | Non-TXV | 3.302%
Fresno | CA | 93705-2103 |  | 2014-06-25 | 2014-06-25 08:07 | 2014-06-25 08:08 | BRYANT - 58ANW024040AAAD | 53 | 2.6 | Yes | Yes | 17.8 | 18.8 | -1 | 3ACA468EB6434D8CA819301FFD679F74 |  | R22 | Non-TXV |  | 4.906% | 0.95094 | 9.428% | [5 empty] | Non-TXV | 4.906%
Valley Springs | CA | 95252-9123 |  | 2014-06-19 | 2014-06-19 10:00 | 2014-06-19 10:19 | RUUD - UNK | 80 | -4.7 | Yes | Yes | 19.9 | 22.6 | -2.7 | 82DA3B91C7C34E1480C1DC95D52B9EB2 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Stockton | CA | 95206-4955 |  | 2014-06-11 | 2014-06-11 13:50 | 2014-06-11 14:10 | OTHER - 13AXD-048-230-15 | 120 | 13.4 | Yes | Yes | 21.7 | 20.4 | 1.3 | AF6354B4FA7B4955A80F2496632DF502 |  | R22 | TXV |  | 11.17% | 0.88833 | 21.46% | [5 empty] | TXV | 11.17%
Fresno | CA | 93705-2147 |  | 2014-05-29 | 2014-05-29 10:03 | 2014-05-29 10:20 | BRYANT - 582ANW02440AAD | 53 | 7.4 | Yes | Yes | 21.1 | 16.4 | 4.7 | 08B1A3ECC6BF41F385B23AF5BC9EC2FE |  | R22 | Non-TXV |  | 13.96% | 0.86038 | 26.83% | [5 empty] | Non-TXV | 13.96%
Stockton | CA | 95206-4958 |  | 2014-06-12 | 2014-06-12 10:03 | 2014-06-12 10:25 | GOODMAN - GSC130601BC | 85 | 14.6 | Yes | Yes | 20.8 | 19.8 | 1 | 81621ECF85F3467B801138BCF67CD532 |  | R22 | Non-TXV |  | 17.18% | 0.82824 | 33.01% | [5 empty] | Non-TXV | 17.18%
Fresno | CA | 93722-7326 |  | 2014-06-07 | 2014-06-07 14:46 | 2014-06-07 15:16 | YORK - DR03030B | 96 | 3.1 | Yes | Yes | 19.4 | 20.6 | -1.2 | A619D01F314F4023AE0532E4E9010F7D |  | R22 | Non-TXV |  | 3.229% | 0.96771 | 6.206% | [5 empty] | Non-TXV | 3.229%
Stockton | CA | 95206-3880 |  | 2014-06-07 | 2014-06-07 08:57 | 2014-06-07 09:21 | CARRIER - 24ABA336A300 | 82 | 5 | Yes | Yes | 23.8 | 20.4 | 3.4 | F0637606C8AB435EB04418612AF762B1 |  | R410A | TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | TXV | 6.098%
Madera | CA | 93638-8171 |  | 2014-06-02 | 2014-06-02 10:18 | 2014-06-02 10:35 | CARRIER - 48GS048090301 | 81 | 9.4 | Yes | Yes | 23.4 | 19.9 | 3.5 | 354A727B476D4DB2924367EEBADDB879 |  | R22 | Non-TXV |  | 11.6% | 0.88395 | 22.3% | [5 empty] | Non-TXV | 11.6%
Oakdale | CA | 95361-3814 |  | 2014-09-08 | 2014-09-08 09:57 | 2014-09-08 10:28 | OTHER - N4A336AKB200 | 83 | 2.6 | Yes | Yes | 24.9 | 19.8 | 5.1 | 190D3F21131A41F38886B900B42E21F6 |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Clovis | CA | 93612-1671 |  | 2014-06-07 | 2014-06-07 12:03 | 2014-06-07 12:41 | BDP - 561CJX042000AAAA | 80 | 3.5 | Yes | Yes | 24.2 | 22.1 | 2.1 | 2CB7B5A7E6C347B1A9AE36AA1012C18E |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Oroville | CA | 95966-6322 |  | 2014-05-27 | 2014-05-27 13:37 | 2014-05-27 14:03 | AMANA - PGD42C0902E | 120 | 4.2 | Yes | Yes | 30 | 24.2 | 5.8 | C24D275302094D6E8D1CB986E4D0C4C7 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Lincoln | CA | 95648-7702 |  | 2014-06-09 | 2014-06-09 08:41 | 2014-06-09 08:59 | YORK - H2RC042S068 | 109 | 3.7 | Yes | Yes | 24 | 22.6 | 1.4 | D87E4998C4D34C15AFBF545FB2C47F86 |  | R22 | Non-TXV |  | 3.394% | 0.96606 | 6.523% | [5 empty] | Non-TXV | 3.394%
Tracy | CA | 95376-8748 |  | 2014-05-23 | 2014-05-23 14:07 | 2014-05-23 14:27 | PAYNE - PA13NR060-H | 222 | 7.9 | Yes | Yes | 21.3 | 19.7 | 1.6 | 41BF6BF403EB426389F12E8B4F8BD93F |  | R22 | Non-TXV |  | 3.559% | 0.96441 | 6.839% | [5 empty] | Non-TXV | 3.559%
Fresno | CA | 93705-2803 |  | 2014-05-28 | 2014-05-28 14:42 | 2014-05-28 14:46 | SEARS - 7777UNK | 80 | 3.9 | Yes | Yes | 27.4 | 22.8 | 4.6 | E1054821F5AB46D8B466ED44AF397557 |  | R22 | Non-TXV |  | 4.875% | 0.95125 | 9.369% | [5 empty] | Non-TXV | 4.875%
Tracy | CA | 95376-2929 |  | 2014-06-24 | 2014-06-24 09:46 | 2014-06-24 10:12 | AMERICAN STANDARD - 2A7A4030A1000AA | 105 | 5.3 | Yes | Yes | 23.8 | 20.8 | 3 | 76D15CA00E4549B2ABE8716063323A6E |  | R22 | Non-TXV |  | 5.048% | 0.94952 | 9.7% | [5 empty] | Non-TXV | 5.048%
Fresno | CA | 93704-4711 |  | 2014-06-16 | 2014-06-16 11:50 | 2014-06-16 11:51 | YORK - DAYP-F036N070A | 108 | 5.1 | Yes | Yes | 23.8 | 20.4 | 3.4 | BD3A9EBDBF4F4CC192A999BDBA65C65E |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Lincoln | CA | 95648-9535 |  | 2014-06-09 | 2014-06-09 10:23 | 2014-06-09 10:38 | AMANA - PGD30C0702E | 74 | 2.7 | Yes | Yes | 20 | 20.4 | -0.4 | CE7AB942BE97470792761CDCE164CF74 |  | R22 | Non-TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | Non-TXV | 3.649%
Angels Camp | CA | 95222-0000 |  | 2014-08-28 | 2014-08-28 12:24 | 2014-08-28 12:57 | RHEEM - RRNA-B048JK08X | 66 | 5.2 | Yes | Yes | 22.3 | 18.9 | 3.5 | D396DB0F31144A6CB532F6BA07064DCB |  | R22 | Non-TXV |  | 7.879% | 0.92121 | 15.14% | [5 empty] | Non-TXV | 7.879%
Stockton | CA | 95206-4966 |  | 2014-06-12 | 2014-06-12 15:36 | 2014-06-12 15:56 | GOODMAN - CKL49-1L | 85 | 3.8 | Yes | Yes | 20.4 | 19.9 | 0.5 | 33B4A99C182E4AE5906F9D7CA5855EE2 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Thornton | CA | 95686-0000 |  | 2014-08-26 | 2014-08-26 09:17 | 2014-08-26 09:35 | RHEEM - 14AJM42A01 | 145 | 6.3 | Yes | Yes | 16.4 | 18 | -1.5 | 16865DBB18594D67977CA9276AD45DCF |  | R410A | Non-TXV |  | 4.345% | 0.95655 | 8.35% | [5 empty] | Non-TXV | 4.345%
Stockton | CA | 95210-3328 |  | 2014-05-27 | 2014-05-27 12:41 | 2014-05-27 12:59 | INTERTHERM - ACC-042BCRAA | 81 | 5.6 | Yes | Yes | 28.8 | 22.8 | 6 | B2F3DB4E700C4B898826494E4A3F04E6 |  | R22 | Non-TXV |  | 6.914% | 0.93086 | 13.29% | [5 empty] | Non-TXV | 6.914%
Lincoln | CA | 95648-2836 |  | 2014-06-16 | 2014-06-16 13:55 | 2014-06-16 14:12 | YORK - H1RA048S06D | 117 | 3.6 | Yes | Yes | 19 | 22 | -3 | B9A6A89663F444B3B2BB4D57956C7491 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Dinuba | CA | 93618-4059 |  | 2014-07-29 | 2014-07-29 15:54 | 2014-07-29 16:20 | UNITARY PRODUCTS GROUP - H2RD024S06B | 88 | 3.9 | Yes | Yes | 21.6 | 20.6 | 1.1 | 60742FE37AD641FFBF5D5D6689BDA11C |  | R22 | Non-TXV |  | 4.432% | 0.95568 | 8.517% | [5 empty] | Non-TXV | 4.432%
Dinuba | CA | 93618-4059 |  | 2014-07-15 | 2014-07-15 16:14 | 2014-07-15 16:43 | UNITARY PRODUCTS GROUP - H2RD024S06B | 88 | 6 | Yes | Yes | 22.4 | 22.5 | -0.1 | 7A029C534562428BBB31DB7B5A6E857D |  | R22 | Non-TXV |  | 6.818% | 0.93182 | 13.1% | [5 empty] | Non-TXV | 6.818%
Fresno | CA | 93704-4539 |  | 2014-06-20 | 2014-06-20 08:56 | 2014-06-20 08:58 | GOODMAN - GPG1348090M41AD | 125 | 4 | Yes | Yes | 23 | 19.9 | 3.1 | 781491EFE1A24C3F9AEC21DC8DDC10A6 |  | R410A | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Merced | CA | 95340-4345 |  | 2014-05-30 | 2014-05-30 14:40 | 2014-05-30 14:56 | COLEMAN - 9536A901 | 67 | 10.1 | Yes | Yes | 27 | 21.5 | 5.5 | 5BB773B64D144295ACAAB59CA58BD3A3 |  | R22 | Non-TXV |  | 15.07% | 0.84925 | 28.97% | [5 empty] | Non-TXV | 15.07%
Fresno | CA | 93726-2122 |  | 2014-05-26 | 2014-05-26 10:23 | 2014-05-26 10:42 | YORK - SA36G080-10E | 57 | 2.1 | Yes | Yes | 24.9 | 22.1 | 2.8 | BA85CAC322924B56AABED2799B4F4025 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Dinuba | CA | 93618-4052 |  | 2014-07-25 | 2014-07-25 16:50 | 2014-07-25 17:32 | NORDYNE - F3BA-24KA | 64 | 4.4 | Yes | Yes | 21.7 | 21.9 | -0.2 | 0D16CD360C3A4CAA984F33D2CACE4991 |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Fresno | CA | 93705-2040 |  | 2014-05-28 | 2014-05-28 18:11 | 2014-05-28 18:14 | BRYANT - 82ANW024040AAAD | 55 | 3 | Yes | Yes | 16.7 | 19.1 | -2.4 | 67DB8EAE75C346A1AD31E29147AB3466 |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Fresno | CA | 93726-0239 |  | 2014-05-26 | 2014-05-26 09:21 | 2014-05-26 09:40 | UNITARY PRODUCTS GROUP - TCJD42SA1S3HA | 69 | 4.3 | Yes | Yes | 19 | 20.2 | -1.2 | 7750F5B1BAE1400986745D2464F2B520 |  | R410A | TXV |  | 6.232% | 0.93768 | 11.98% | [5 empty] | TXV | 6.232%
Stockton | CA | 95204-2606 |  | 2014-06-18 | 2014-06-18 10:37 | 2014-06-18 11:00 | RHEEM - RRPL-B036JK08X | 85 | 8.8 | Yes | Yes | 21.2 | 21.3 | -0.1 | 974E2BFBC29E44A7B8C0F7FF822F7240 |  | R410A | TXV |  | 10.35% | 0.89647 | 19.9% | [5 empty] | TXV | 10.35%
Madera | CA | 93638-5950 |  | 2014-06-12 | 2014-06-12 15:25 | 2014-06-12 15:49 | RHEEM - RRNLB030JK06X | 76 | 14.4 | Yes | Yes | 28.7 | 23.1 | 5.6 | 8C0BD317B61847499DB5201128B53E71 |  | R410A | Non-TXV |  | 18.95% | 0.81053 | 36.41% | [5 empty] | Non-TXV | 18.95%
Fresno | CA | 93705-5147 |  | 2014-08-02 | 2014-08-02 10:22 | 2014-08-02 10:41 | RHEEM - RRNL-B030JK06X | 78 | 2.8 | Yes | Yes | 20.1 | 20.1 | 0 | 6B27A202C8D84A28AB7AC67CD227228F |  | R410A | TXV |  | 3.59% | 0.9641 | 6.899% | [5 empty] | TXV | 3.59%
Pinedale | CA | 93650-1014 |  | 2014-06-11 | 2014-06-11 13:56 | 2014-06-11 14:17 | RHEEM - RRNLB024JK06X | 77 | 10.2 | Yes | Yes | 21.6 | 19.6 | 2 | D9A5DE8983104141825F2851F30F9AFE |  | R410A | Non-TXV |  | 13.25% | 0.86753 | 25.46% | [5 empty] | Non-TXV | 13.25%
Magalia | CA | 95954-9539 |  | 2014-07-22 | 2014-07-22 09:05 | 2014-07-22 09:27 | PAYNE - PH10JA042-C | 65 | 3 | Yes | Yes | 21.5 | 20.4 | 1.1 | 907005F2A42A4E2A851D7DFF21B82D95 |  | R22 | TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | TXV | 4.615%
Stockton | CA | 95209-2415 |  | 2014-06-03 | 2014-06-03 15:02 | 2014-06-03 15:20 | RHEEM - RAMC-048JBZ | 162 | 13.3 | Yes | Yes | 24.8 | 19.9 | 4.9 | 4A1A38F629C845C88805B802EFDD2882 |  | R22 | Non-TXV |  | 8.21% | 0.9179 | 15.78% | [5 empty] | Non-TXV | 8.21%
Stockton | CA | 95206-6412 |  | 2014-06-06 | 2014-06-06 10:30 | 2014-06-06 11:05 | GOODMAN - CKL49-1 | 85 | 8.5 | Yes | Yes | 20.3 | 20.7 | -0.4 | 902777C0AE9E4D82B349ABCBBF1FA90A |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93703-2127 |  | 2014-05-30 | 2014-05-30 10:06 | 2014-05-30 10:37 | GOODMAN - PGB030075-1A | 56 | 5.6 | Yes | Yes | 20.8 | 20.9 | -0.1 | 83FDA8E28976423EB2A27B8F0A16A06F |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93703-2127 |  | 2014-05-30 | 2014-05-30 10:40 | 2014-05-30 11:19 | BRYANT - 582ANW30040 | 55 | 1.8 | Yes | Yes | 23.5 | 20.5 | 3 | 882FD90C9C3E4040BC23341B2B87770F |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Fresno | CA | 93722-6756 |  | 2014-05-28 | 2014-05-28 12:49 | 2014-05-28 13:06 | YORK - D2GA036N04806C | 84 | 17.6 | Yes | Yes | 25.2 | 21.5 | 3.7 | 514F94A53E9F458691923347E47E5EE9 |  | R22 | Non-TXV |  | 20.95% | 0.79048 | 40.27% | [5 empty] | Non-TXV | 20.95%
Williams | CA | 95987-0000 |  | 2014-09-18 | 2014-09-18 11:40 | 2014-09-18 12:01 | AMERICAN STANDARD - YCC024F1L0BA | 64 | 5.9 | Yes | Yes | 18 | 19.9 | -1.9 | 9F136042EA644DE1BB1812D97C5A7736 |  | R22 | Non-TXV |  | 9.219% | 0.90781 | 17.72% | [5 empty] | Non-TXV | 9.219%
Stockton | CA | 95204-4414 |  | 2014-06-10 | 2014-06-10 09:50 | 2014-06-10 10:13 | PAYNE - PY3PNA030060NB | 85 | 4 | Yes | Yes | 21.8 | 19 | 2.8 | D612EAED2A3F4E70926352BC90439F81 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Lincoln | CA | 95648-8274 |  | 2014-06-16 | 2014-06-16 11:43 | 2014-06-16 12:03 | CARRIER - 38CKC030340 | 69 | 10.7 | Yes | Yes | 19 | 22 | -3 | 86DDCB950A1041A3946B32BA2C4F5A52 |  | R22 | Non-TXV |  | 15.51% | 0.84493 | 29.8% | [5 empty] | Non-TXV | 15.51%
Magalia | CA | 95954-9507 |  | 2014-06-05 | 2014-06-05 08:43 | 2014-06-05 09:00 | RHEEM - RQNLB024JK | 57 | 2 | Yes | Yes | 18.1 | 19.5 | -1.4 | 16EA357772EE44E19935A6349F424256 |  | R410A | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Winton | CA | 95388-9592 |  | 2014-06-11 | 2014-06-11 16:24 | 2014-06-11 16:25 | AMANA - 5CE36CZA | 110 | 4.9 | Yes | Yes | 23.1 | 20.3 | 2.8 | B5B9CC2D3F2C40FB8026D772FEAF007F |  | R22 | Non-TXV |  | 4.455% | 0.95545 | 8.561% | [5 empty] | Non-TXV | 4.455%
Stockton | CA | 95207-7519 |  | 2014-05-29 | 2014-05-29 14:42 | 2014-05-29 14:58 | GE - BGTA930E1A | 80 | 3.2 | Yes | Yes | 28.2 | 25.9 | 2.3 | 4E3B1EF9A45744DC9715DC5348D97486 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93728-2918 |  | 2014-06-13 | 2014-06-13 12:54 | 2014-06-13 12:56 | CARRIER - 480L003 | 50 | 1.9 | Yes | Yes | 20.2 | 23.2 | -3 | F5C9809BD81D4028B86A07EDE4D82BBB |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Oakdale | CA | 95361-9678 |  | 2014-06-04 | 2014-06-04 11:29 | 2014-06-04 11:51 | DAY & NIGHT - 591ANX024000AAA | 98 | -9.2 | Yes | Yes | 20.1 | 19.3 | 0.8 | 708CA59E8F8B4634B0F63244785C5EE2 |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Fresno | CA | 93705-2307 |  | 2014-05-29 | 2014-05-29 09:09 | 2014-05-29 09:25 | TRANE - YCY048G1HOAA | 183 | 25.8 | Yes | Yes | 22.9 | 19.3 | 3.6 | DC494925391D49699268AD32BDAC30B1 |  | R22 | Non-TXV |  | 14.1% | 0.85902 | 27.09% | [5 empty] | Non-TXV | 14.1%
Lodi | CA | 95240-9417 |  | 2014-06-16 | 2014-06-16 08:50 | 2014-06-16 09:08 | GMC - VSX130301AA | 78 | -4.6 | Yes | Yes | 18.5 | 19.1 | -0.6 | 81C3CE5C0E934A52B1D17FEE84FFB9F3 |  | R410A | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Stockton | CA | 95206-5141 |  | 2014-06-06 | 2014-06-06 13:58 | 2014-06-06 14:30 | CARRIER - 38CKC038350 | 85 | -4.4 | Yes | Yes | 18.9 | 19.3 | -0.4 | 9223356C90C047FCBCF56AE983AC10C7 |  | R22 | TXV |  | -5.176% | 1.0518 | 1.45% |  |  |  |  | TXV |  |  | -5.176%
Clovis | CA | 93612-0213 |  | 2014-06-26 | 2014-06-26 16:21 | 2014-06-26 16:38 | AMANA - PGB36A0452A | 117 | 5.8 | Yes | Yes | 21.1 | 21 | 0.1 | 859EF6567E034BBD89C9B5E9F2C2E8E9 |  | R22 | Non-TXV |  | 4.957% | 0.95043 | 9.527% | [5 empty] | Non-TXV | 4.957%
Clovis | CA | 93612-0213 |  | 2014-06-26 | 2014-06-26 16:40 | 2014-06-26 17:03 | AMANA - PGB36A0452A | 117 | 3.7 | Yes | Yes | 21.1 | 22.1 | -1 | A3E5BEA597D64A11900DABAEB0519F65 |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.077% | [5 empty] | Non-TXV | 3.162%
Fresno | CA | 93705-2038 |  | 2014-06-20 | 2014-06-20 12:07 | 2014-06-20 12:09 | BRYANT - 582ANW030040AAAD | 55 | 3.4 | Yes | Yes | 19.2 | 20.9 | -1.7 | 8C0CB62D097D4211B4E5AE60BAB9FFB4 |  | R22 | Non-TXV |  | 6.182% | 0.93818 | 11.88% | [5 empty] | Non-TXV | 6.182%
Oroville | CA | 95966-6259 |  | 2014-06-19 | 2014-06-19 09:48 | 2014-06-19 10:17 | DAY & NIGHT - 5888ANWB60080AABAG | 55 | 9.3 | Yes | Yes | 18.5 | 21.5 | -3 | 76A5A422D2104CD38FF6E4FF0564268A |  | R22 | Non-TXV |  | 16.91% | 0.83091 | 32.5% | [5 empty] | Non-TXV | 16.91%
Stockton | CA | 95206-6068 |  | 2014-06-05 | 2014-06-05 09:27 | 2014-06-05 09:54 | GOODMAN - CKJ48-1A | 85 | 6 | Yes | Yes | 22.2 | 21 | 1.2 | 4B680035C4234D5B898F437EDC2D9300 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Dinuba | CA | 93618-4046 |  | 2014-07-11 | 2014-07-11 16:58 | 2014-07-11 17:24 | NORDYNE - FS3BA-024KA | 64 | 4.7 | Yes | Yes | 23.7 | 22.3 | 1.4 | 248CA13C5FAC406992D8F48C5DF1D65A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.344% | 0.92656 | 14.11% | [5 empty] | Non-TXV | 7.344%
Lincoln | CA | 95648-3002 |  | 2014-05-26 | 2014-05-26 10:01 | 2014-05-26 10:33 | YORK - H4DE036S06A | 82 | 2.6 | Yes | Yes | 20 | 19.9 | 0.1 | C1FE2AB9842241AC91C9A5C8719D4791 |  | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Rocklin | CA | 95677-2653 |  | 2014-06-09 | 2014-06-09 15:14 | 2014-06-09 15:14 | FRIGIDAIRE - FS3BC-030KA | 68 | 0 | Yes | Yes | 17 | 19.5 | -2.5 | F341B14A0E5447C4BB7D66C2959DBEF9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-4045 |  | 2014-07-11 | 2014-07-11 18:27 | 2014-07-11 19:00 | NORDYNE - FS3BA-024KA | 64 | 2 | Yes | Yes | 19.6 | 20.7 | -1.1 | B030942C29004F3CAAD3E256A363F979 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Stockton | CA | 95204-5314 |  | 2014-06-10 | 2014-06-10 14:27 | 2014-06-10 14:49 | RUUD - UAKA-030JAZ | 85 | 5.9 | Yes | Yes | 22.1 | 20.2 | 1.9 | 9D49CC5A13D746C5BE60811803FCDB89 |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
Madera | CA | 93638-5843 |  | 2014-06-02 | 2014-06-02 11:49 | 2014-06-02 12:12 | YORK - D2GH030N06406C | 112 | 22.5 | Yes | Yes | 23.1 | 19.6 | 3.5 | 065E1C392154411D8D04FA10C159C4C8 |  | R22 | Non-TXV |  | 20.09% | 0.79911 | 38.61% | [5 empty] | Non-TXV | 20.09%
Williams | CA | 95987-0000 |  | 2014-09-18 | 2014-09-18 10:36 | 2014-09-18 11:12 | GOODMAN - GPG1330070M41AD | 80 | 4.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | 88B505B1DC01440B879930F309BB561E |  | R410A | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Fresno | CA | 93722-5328 |  | 2014-05-27 | 2014-05-27 11:24 | 2014-05-27 11:45 | GOODMAN - GPG1336070M41AB | 85 | 14.7 | Yes | Yes | 21.2 | 20.4 | 0.8 | BD16309D85A4496298C22583A75B6368 |  | R410A | Non-TXV |  | 17.29% | 0.82706 | 33.24% | [5 empty] | Non-TXV | 17.29%
Le Grand | CA | 95333-9661 |  | 2014-06-05 | 2014-06-05 23:22 | 2014-06-05 23:23 | RUUD - UPND-025J055 | 77 | 2.4 | Yes | Yes | 23 | 20.4 | 2.6 | 87F8DFF6172E4467A321715D04D4B89E |  | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Fresno | CA | 93704-4604 |  | 2014-06-16 | 2014-06-16 13:48 | 2014-06-16 13:49 | YORK - D3NZ036N05606NXC | 64 | 4.1 | Yes | Yes | 31 | 25.1 | 6 | 971D2CCDA17649748A0A866823C64A53 |  | R410A | Non-TXV |  | 6.406% | 0.93594 | 12.31% | [5 empty] | Non-TXV | 6.406%
Stockton | CA | 95207-2226 |  | 2014-06-03 | 2014-06-03 09:19 | 2014-06-03 09:37 | HEIL - CA3036UKB1 | 79 | 8.8 | Yes | Yes | 25.4 | 19.5 | 5.9 | F3426F8BF2FF4D87AD9259470AFA3A79 |  | R22 | Non-TXV |  | 11.14% | 0.88861 | 21.41% | [5 empty] | Non-TXV | 11.14%
Fresno | CA | 93727-8106 |  | 2014-06-09 | 2014-06-09 11:43 | 2014-06-09 12:01 | RHEEM - N/A | 60 | 3.7 | Yes | Yes | 21.5 | 21.5 | 0 | 053F2EA394FA4DEBA5A51F2CF859A584 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.167% | 0.93833 | 11.85% | [5 empty] | Non-TXV | 6.167%
Lincoln | CA | 95648-8281 |  | 2014-05-26 | 2014-05-26 09:10 | 2014-05-26 09:44 | OTHER - 38CKC036350 | 67 | -6.3 | Yes | Yes | 19 | 20.9 | -1.9 | 8A19A2F1968C411A8000828C6BD73B56 |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Stockton | CA | 95206-6015 |  | 2014-06-16 | 2014-06-16 09:29 | 2014-06-16 09:56 | RUUD - UAHE-048JAS | 85 | 12.2 | Yes | Yes | 24.9 | 20.4 | 4.5 | 439C70E0E59D4A0B8717A14B02E43CE4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | TXV | 14.35%
Selma | CA | 93662-4906 |  | 2014-06-16 | 2014-06-16 08:50 | 2014-06-16 09:09 | LENNOX - 13ACC-036-230-02 | 115 | 5.7 | Yes | Yes | 19 | 20.8 | -1.8 | D66007FF2AD2499C9A15068AA8469C48 |  | R22 | Non-TXV |  | 4.957% | 0.95043 | 9.525% | [5 empty] | Non-TXV | 4.957%
Williams | CA | 95987-0000 |  | 2014-10-08 | 2014-10-08 11:58 | 2014-10-08 12:40 | TRANE - YCC024F1L0AD | 65 | 3.2 | Yes | Yes | 19 | 20.7 | -1.7 | B5399A228C0046BEB919ACC288BC6A3A |  | R22 | Non-TXV |  | 4.923% | 0.95077 | 9.461% | [5 empty] | Non-TXV | 4.923%
Stockton | CA | 95206-6171 |  | 2014-06-12 | 2014-06-12 16:24 | 2014-06-12 16:40 | GOODMAN - CKL30-1G | 85 | 4.4 | Yes | Yes | 20.8 | 20.7 | 0.1 | DC6C0384DB8248E4896758EE8B55E40B |  | R22 | TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | TXV | 5.176%
Fresno | CA | 93705-2939 |  | 2014-05-27 | 2014-05-27 11:45 | 2014-05-27 11:46 | YORK - D2NPO30N0NO5606A | 73 | 2.5 | Yes | Yes | 24.2 | 23.1 | 1.1 | 0E3F2AD4DEB54675BBE50E7897EFF88F |  | R22 | Non-TXV |  | 3.425% | 0.96575 | 6.581% | [5 empty] | Non-TXV | 3.425%
Fresno | CA | 93705-2147 |  | 2014-05-29 | 2014-05-29 10:30 | 2014-05-29 10:49 | AIRE-FLO - GS3BA024KA | 64 | 10.8 | Yes | Yes | 20.4 | 17.4 | 3 | 59A262B423CC4A89AF4769610EDE0A1F |  | R22 | Non-TXV |  | 16.88% | 0.83125 | 32.43% | [5 empty] | Non-TXV | 16.88%
Riverbank | CA | 95367-3145 |  | 2014-08-26 | 2014-08-26 09:59 | 2014-08-26 10:18 | RUUD - URGG-05E24JKR | 42 | 10.6 | Yes | Yes | 21.7 | 18.8 | 2.9 | 4B8EA95722974BDA84F22247ECE8CEA2 |  | R22 | Non-TXV |  | 25.24% | 0.74762 | 48.5% | [5 empty] | Non-TXV | 25.24%
Yuba City | CA | 95993-9727 |  | 2014-05-28 | 2014-05-28 09:15 | 2014-05-28 09:33 | GIBSON - JS3BC-036KA | 82 | 3.4 | Yes | Yes | 17.5 | 20.5 | -3 | 0B6400C799914DD098B2CAE04B779FD3 |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Yuba City | CA | 95993-8857 |  | 2014-05-30 | 2014-05-30 15:47 | 2014-05-30 16:17 | LENNOX - HS26-060-2P | 168 | 8.1 | Yes | Yes | 20 | 22.4 | -2.4 | 4C4D6212D0AC4A4D9A33BAA940FF2FF5 |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Merced | CA | 95340-4345 |  | 2014-07-11 | 2014-07-11 07:48 | 2014-07-11 07:50 | COLEMAN - PRCS0421B2 | 107 | 4.3 | Yes | Yes | 17.6 | 19 | -1.4 | 95CF1A3F2E9247D9B0C09AF05BA0FCD6 |  | R22 | Non-TXV |  | 4.019% | 0.95981 | 7.723% | [5 empty] | Non-TXV | 4.019%
Stockton | CA | 95203-1137 |  | 2014-06-05 | 2014-06-05 11:31 | 2014-06-05 12:14 | WESTINGHOUSE - UNK | 56 | 5.9 | Yes | Yes | 19.1 | 20.1 | -1 | 4E277236C05C4B3A89232E213DE65192 |  | R22 | Non-TXV |  | 10.54% | 0.89464 | 20.25% | [5 empty] | Non-TXV | 10.54%
Marysville | CA | 95901-4017 |  | 2014-06-17 | 2014-06-17 10:07 | 2014-06-17 10:30 | LENNOX - GCS26X-030-75-1PA | 85 | 2.7 | Yes | Yes | 27.5 | 22.6 | 4.9 | E615FF9EA9044C58B4FD4B12A424166E |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Stockton | CA | 95205-5703 |  | 2014-06-12 | 2014-06-12 10:46 | 2014-06-12 11:03 | GOODMAN - CLJ30-1 | 96 | -5.6 | Yes | Yes | 16.9 | 18.8 | -1.9 | 79C6B02CEF984FCB9AB5818FE704D810 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Paradise | CA | 95969-7118 |  | 2014-06-05 | 2014-06-05 13:20 | 2014-06-05 13:57 | TEMPSTAR - E0691756 | 53 | 8.5 | Yes | Yes | 20 | 20.4 | -0.4 | C74ACBA345AA41F3B37CB7D78E7EB104 |  | R22 | Non-TXV |  | 16.04% | 0.83962 | 30.82% | [5 empty] | Non-TXV | 16.04%
Orland | CA | 95963-2318 |  | 2014-07-23 | 2014-07-23 09:27 | 2014-07-23 09:45 | DAY & NIGHT - N2A342AKA210 | 85 | 3.3 | Yes | Yes | 20.5 | 20.4 | 0.1 | 9BA3BDF4843C4E84AA628FD4734DC527 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Ione | CA | 95640-9417 |  | 2014-07-31 | 2014-07-31 13:10 | 2014-07-31 13:30 | COLEMAN - UNK | 80 | 2.6 | Yes | Yes | 23 | 20.8 | 2.2 | F66844E72E8E4F628B73C26456BE6363 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Willows | CA | 95988-3207 |  | 2014-09-03 | 2014-09-03 08:00 | 2014-09-03 20:16 | TRANE - 2YCC036A1064AA | 82 | 3.8 | Yes | Yes | 18 | 19.9 | -1.9 | 482B766A7FBD49379DBE3F878F5103B1 |  | R22 | Non-TXV |  | 4.634% | 0.95366 | 8.906% | [5 empty] | Non-TXV | 4.634%
Fresno | CA | 93722-7772 |  | 2014-05-28 | 2014-05-28 14:54 | 2014-05-28 15:24 | YORK - H2RC030S06HG | 88 | 15.6 | Yes | Yes | 22.1 | 16.8 | 5.3 | ADEE5976083C471191709A776E5A689A |  | R22 | Non-TXV |  | 17.73% | 0.82273 | 34.07% | [5 empty] | Non-TXV | 17.73%
Fresno | CA | 93722-7772 |  | 2014-05-28 | 2014-05-28 15:25 | 2014-05-28 15:49 | YORK - H2RC030S06HG | 88 | 14.9 | Yes | Yes | 27.2 | 22.4 | 4.8 | 93C2ED2D72734383ACF5F404F19FF569 |  | R22 | Non-TXV |  | 16.93% | 0.83068 | 32.54% | [5 empty] | Non-TXV | 16.93%
Merced | CA | 95340-4345 |  | 2014-08-27 | 2014-08-27 12:57 | 2014-08-27 13:13 | RHEEM - RAKA-037JAZ | 79 | 2.4 | Yes | Yes | 27.1 | 21.3 | 5.8 | 7B7580138707459F9109671021483B8D |  | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Fresno | CA | 93704-5102 |  | 2014-06-16 | 2014-06-16 11:20 | 2014-06-16 11:22 | YORK - DCYP-F024N045A | 100 | 5.4 | Yes | Yes | 26.5 | 22 | 4.5 | 94B0298451A349DF9BD49A58232CCB38 |  | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Fresno | CA | 93726-1513 |  | 2014-05-26 | 2014-05-26 11:48 | 2014-05-26 12:11 | GOODMAN - N/A | 60 | 2 | Yes | Yes | 25 | 19.3 | 5.7 | AF99EDBEDFAE42059ACD09955A377F08 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95207-5908 |  | 2014-06-11 | 2014-06-11 10:57 | 2014-06-11 11:14 | YORK - H1RA042S06D | 84 | -4.9 | Yes | Yes | 19.3 | 18.3 | 1 | 397686A187EE4D07952000CECB04CAEF |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93703-4352 |  | 2014-06-11 | 2014-06-11 11:28 | 2014-06-11 12:07 | BDP - 585CJ02450 | 72 | 5.6 | Yes | Yes | 20.6 | 21.4 | -0.8 | 97B135B4417B4EF2A4EBF75E9570FE39 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Merced | CA | 95340-4345 |  | 2014-06-06 | 2014-06-06 09:06 | 2014-06-06 09:24 | OTHER - DRCS0421BE | 107 | 16.7 | Yes | Yes | 21.2 | 18.8 | 2.4 | 92564937AA0F4FCD9F73893D5207A40A |  | R22 | Non-TXV |  | 15.61% | 0.84393 | 29.99% | [5 empty] | Non-TXV | 15.61%
Stockton | CA | 95203-2163 |  | 2014-06-10 | 2014-06-10 08:04 | 2014-06-10 08:25 | BRYANT - 561CJ030-C | 139 | 6.5 | Yes | Yes | 18.1 | 19.3 | -1.2 | 81CDAAA28F10483289A47E2048B684D6 |  | R22 | TXV |  | 4.676% | 0.95324 | 8.987% | [5 empty] | TXV | 4.676%
Stockton | CA | 95203-2163 |  | 2014-06-10 | 2014-06-10 08:29 | 2014-06-10 08:47 | BRYANT - PH13NR024-H | 123 | 11.3 | Yes | Yes | 22.4 | 20.9 | 1.5 | 5AB346814BB540C0BE88987DF92F81D8 |  | R22 | TXV |  | 9.187% | 0.90813 | 17.66% | [5 empty] | TXV | 9.187%
Selma | CA | 93662-4321 |  | 2014-06-13 | 2014-06-13 17:12 | 2014-06-13 17:32 | ICP - NA336AKB300 | 85 | 4.7 | Yes | Yes | 21 | 22.1 | -1.1 | D18B5EE54D504E5B830D2FD9F515AD48 |  | R410A | TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | TXV | 5.529%
Willows | CA | 95988-3235 |  | 2014-09-18 | 2014-09-18 12:53 | 2014-09-18 13:13 | BRYANT - 574NNWA024040NA | 50 | 5.6 | Yes | Yes | 25 | 21 | 4.1 | 554980DBCCF4414F9C3A865F5942F25A |  | R22 | Non-TXV |  | 11.2% | 0.888 | 21.52% | [5 empty] | Non-TXV | 11.2%
Valley Springs | CA | 95252-9419 |  | 2014-06-20 | 2014-06-20 15:15 | 2014-06-20 15:32 | YORK - D1NH060N09006C | 140 | 6.2 | Yes | Yes | 19 | 18.7 | 0.3 | F2F1843489B646AF8451287C8DD0984D |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Fresno | CA | 93722-6009 |  | 2014-05-27 | 2014-05-27 13:30 | 2014-05-27 13:55 | OTHER - CA3042VKA1 | 99 | 14 | Yes | Yes | 24.1 | 20.2 | 3.9 | 85DF8E7A02534ED4969CCA0B5468256A |  | R22 | Non-TXV |  | 14.14% | 0.85859 | 27.18% | [5 empty] | Non-TXV | 14.14%
Fresno | CA | 93726-6112 |  | 2014-06-20 | 2014-06-20 13:35 | 2014-06-20 13:54 | RUUD - URKAA048JK10E | 78 | 11.1 | Yes | Yes | 22.6 | 19.7 | 2.9 | D9EBBBA47D974FD3A6871759BC722101 |  | R22 | Non-TXV |  | 14.23% | 0.85769 | 27.35% | [5 empty] | Non-TXV | 14.23%
Stockton | CA | 95204-2841 |  | 2014-06-30 | 2014-06-30 09:01 | 2014-06-30 09:18 | ICP - PGAA30C1K1 | 74 | -4.4 | Yes | Yes | 25.3 | 20.4 | 4.9 | F26F446B39DA47F6BD49BD4026DD620F |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Dinuba | CA | 93618-9380 |  | 2014-07-14 | 2014-07-14 11:29 | 2014-07-14 12:10 | NORDYNE - FS3BA-024KA | 64 | 13.3 | Yes | Yes | 21.2 | 21 | 0.2 | 6DE9844C2C9A4504AF33B5B26C06D3DD |  | R22 | Non-TXV |  | 20.78% | 0.79219 | 39.94% | [5 empty] | Non-TXV | 20.78%
Stockton | CA | 95215-8226 |  | 2014-06-04 | 2014-06-04 15:11 | 2014-06-04 15:30 | COLEMAN - UNK | 96 | 30 | Yes | Yes | 18.8 | 20.9 | -2.1 | 9917592BC536498EB3F0EE848D9C08B9 |  | R22 | Non-TXV |  | 31.25% | 0.6875 | 60.06% | [5 empty] | Non-TXV | 31.25%
Riverdale | CA | 93656-9702 |  | 2014-10-24 | 2014-10-24 09:37 | 2014-10-24 10:00 | ICP - PGD50K000C14809 | 243 | 8.9 | Yes | Yes | 24.1 | 20.9 | 3.2 | 607C7B2AE8EB4C91846CC3FE254DCEFB |  | R410A | TXV |  | 3.663% | 0.96337 | 7.039% | [5 empty] | TXV | 3.663%
Jackson | CA | 95642-2628 |  | 2014-07-30 | 2014-07-30 14:04 | 2014-07-30 14:27 | AMERICAN STANDARD - 4A7A4036B1000AA | 91 | 3.3 | Yes | Yes | 28 | 22.6 | 5.4 | 9BD2AB373AD54C598DB053F5550190C1 |  | R410A | TXV |  | 3.626% | 0.96374 | 6.969% | [5 empty] | TXV | 3.626%
Merced | CA | 95340-4345 |  | 2014-06-09 | 2014-06-09 15:18 | 2014-06-09 15:39 | OTHER - UNK | 58 | 13.6 | Yes | Yes | 28.2 | 22.6 | 5.6 | 6476DAD3B08E47519735B83BAEE2AC4E |  | R22 | Non-TXV |  | 23.45% | 0.76552 | 45.06% | [5 empty] | Non-TXV | 23.45%
Madera | CA | 93637-5326 |  | 2014-06-09 | 2014-06-09 10:45 | 2014-06-09 11:01 | YORK - D2NZ042N09006NXA | 144 | 14.2 | Yes | Yes | 21.9 | 19.9 | 2 | 4D7D849813E645279CC28A9AA5387BC8 |  | R410A | Non-TXV |  | 9.861% | 0.90139 | 18.95% | [5 empty] | Non-TXV | 9.861%
Fresno | CA | 93703-3227 |  | 2014-05-30 | 2014-05-30 13:27 | 2014-05-30 13:46 | GOODMAN - PGB036075 | 60 | 4.6 | Yes | Yes | 24 | 22.9 | 1.1 | 17AF0EED35634F54A17467C348E3D48D |  | R22 | Non-TXV |  | 7.667% | 0.92333 | 14.73% | [5 empty] | Non-TXV | 7.667%
Selma | CA | 93662-9627 |  | 2014-06-13 | 2014-06-13 13:53 | 2014-06-13 14:11 | ICP - PGAD36D1KE | 136 | 4.3 | Yes | Yes | 22.7 | 21.5 | 1.2 | 4E94F8B953924E039F67204AD8620E88 |  | R22 | Non-TXV |  | 3.162% | 0.96838 | 6.076% | [5 empty] | Non-TXV | 3.162%
Dinuba | CA | 93618-4048 |  | 2014-07-11 | 2014-07-11 12:31 | 2014-07-11 13:38 | NORDYNE - FS3BA-024KA | 64 | 9.2 | Yes | Yes | 18.1 | 20.9 | -2.8 | 60451628202F46A8892DF6FC0577F2A7 |  | R22 | Non-TXV |  | 14.37% | 0.85625 | 27.63% | [5 empty] | Non-TXV | 14.37%
Selma | CA | 93662-3017 |  | 2014-06-21 | 2014-06-21 14:18 | 2014-06-21 14:37 | YORK - D1NP048N06506A | 132 | 5.8 | Yes | Yes | 24.2 | 22.6 | 1.6 | 3913E00432F34598BAEF45E8AF1D7CFC |  | R22 | Non-TXV |  | 4.394% | 0.95606 | 8.444% | [5 empty] | Non-TXV | 4.394%
Orland | CA | 95963-1917 |  | 2014-05-28 | 2014-05-28 08:16 | 2014-05-28 08:47 | LENNOX - GCS16-411-5P | 75 | 5.2 | Yes | Yes | 16.5 | 18.6 | -2.1 | 3128A7D36C5249E9AD3561B992B5A894 |  | R22 | Non-TXV |  | 6.933% | 0.93067 | 13.32% | [5 empty] | Non-TXV | 6.933%
Fresno | CA | 93722-5564 |  | 2014-05-27 | 2014-05-27 14:12 | 2014-05-27 15:04 | CARRIER - 48KLA136321BE | 102 | 15.8 | Yes | Yes | 25.8 | 22.3 | 3.5 | 6C0A732243EB448BA963978F96EA5385 |  | R22 | Non-TXV |  | 15.49% | 0.8451 | 29.77% | [5 empty] | Non-TXV | 15.49%
Stockton | CA | 95207-2145 |  | 2014-06-20 | 2014-06-20 08:16 | 2014-06-20 08:32 | RHEEM - UNK | 49 | -2.9 | Yes | Yes | 22.8 | 19.7 | 3.1 | 09D281BE79CF4B14AC2A88FE8AFEBEE4 |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Sanger | CA | 93657-8767 |  | 2014-08-26 | 2014-08-26 13:12 | 2014-08-26 13:19 | KENMORE - 13ACD-036-230-02 | 111 | 5 | Yes | Yes | 19.6 | 20.9 | -1.3 | DB3BA238536B432ABAA1B8BAAFD38687 |  | R22 | Non-TXV |  | 4.505% | 0.95495 | 8.657% | [5 empty] | Non-TXV | 4.505%
Sanger | CA | 93657-8767 |  | 2014-08-26 | 2014-08-26 13:20 | 2014-08-26 13:45 | KENMORE - 13ACD-036-230-02 | 111 | 3.3 | Yes | Yes | 17.9 | 19.8 | -1.9 | 7D44350C1231459D9E84388CA7ADA3BB |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Fresno | CA | 93703-2026 |  | 2014-05-31 | 2014-05-31 08:36 | 2014-05-31 09:31 | ICP - PGF048K080 | 102 | 3.6 | Yes | Yes | 20.9 | 19.5 | 1.4 | 91100C2C608444B38110AE23C27E4981 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fresno | CA | 93703-4103 |  | 2014-06-14 | 2014-06-14 10:39 | 2014-06-14 11:19 | GOODMAN - PGB024050-1 | 54 | 5.1 | Yes | Yes | 20.6 | 21 | -0.4 | 89FB9C13AD624292BCA7D0062C79B713 |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Fresno | CA | 93703-2434 |  | 2014-05-30 | 2014-05-30 12:03 | 2014-05-30 12:29 | BRYANT - 574ANW036060 | 167 | 6 | Yes | Yes | 20.7 | 21.7 | -1 | 3A8F1646AF934DFAB477C0B55E890BE2 |  | R22 | Non-TXV |  | 3.593% | 0.96407 | 6.905% | [5 empty] | Non-TXV | 3.593%
Madera | CA | 93638-4841 |  | 2014-06-02 | 2014-06-02 13:06 | 2014-06-02 13:22 | GOODMAN - GPG1336070M41CA | 108 | 13.1 | Yes | Yes | 21.7 | 19.9 | 1.8 | 84FB6C3190CE4DA1B7765DB7538603CB |  | R410A | Non-TXV |  | 12.13% | 0.8787 | 23.31% | [5 empty] | Non-TXV | 12.13%
Clovis | CA | 93611-5104 |  | 2014-06-11 | 2014-06-11 09:19 | 2014-06-11 09:36 | RHEEM - RRNLB036JK06X | 92 | 9.8 | Yes | Yes | 22.3 | 21.5 | 0.8 | 4A5F203F72AC4A06B602FA8FC582F11C |  | R410A | Non-TXV |  | 10.65% | 0.89348 | 20.47% | [5 empty] | Non-TXV | 10.65%
Stockton | CA | 95204-4861 |  | 2014-06-14 | 2014-06-14 13:09 | 2014-06-14 13:25 | TEMPSTAR - PGD330060K001C1 | 99 | -5.8 | Yes | Yes | 22.5 | 21 | 1.5 | BBD1B82D4616441B94B55B5086BD254C |  | R410A | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Madera | CA | 93638-1720 |  | 2014-06-26 | 2014-06-26 15:25 | 2014-06-26 15:27 | BDP - 585CJ024040 | 54 | 7.3 | Yes | Yes | 27.9 | 24.2 | 3.7 | 7864467413EB489DBEAF2E62042CC4C0 |  | R22 | Non-TXV |  | 13.52% | 0.86481 | 25.98% | [5 empty] | Non-TXV | 13.52%
Fresno | CA | 93705-2425 |  | 2014-05-29 | 2014-05-29 10:59 | 2014-05-29 11:16 | AIRE-FLO - PGD36C0702E | 110 | 15.1 | Yes | Yes | 25.6 | 19.9 | 5.7 | 040878430E8249FE99E03D6E0BE7896F |  | R22 | Non-TXV |  | 13.73% | 0.86273 | 26.38% | [5 empty] | Non-TXV | 13.73%
Madera | CA | 93638-1736 |  | 2014-06-02 | 2014-06-02 15:04 | 2014-06-02 15:20 | RUUD - URGG05E37JKR | 77 | 15.1 | Yes | Yes | 26.1 | 22.1 | 4 | 5C2DCE0D9EDC4FCABC33DE85F5D82E6E |  | R22 | Non-TXV |  | 19.61% | 0.8039 | 37.69% | [5 empty] | Non-TXV | 19.61%
Fresno | CA | 93726-4851 |  | 2014-06-20 | 2014-06-20 13:09 | 2014-06-20 13:11 | CARRIER - 48GS024060301 | 53 | 8 | Yes | Yes | 26 | 22.5 | 3.5 | F763491E45FE4EAB9DD631EB74D298C6 |  | R22 | Non-TXV |  | 15.09% | 0.84906 | 29.01% | [5 empty] | Non-TXV | 15.09%
Fresno | CA | 93727-1929 |  | 2014-06-10 | 2014-06-10 11:52 | 2014-06-10 12:12 | GOODMAN - GPG1336070M41AB | 85 | -3.7 | Yes | Yes | 22.5 | 19.3 | 3.2 | 883A5E566EDC438687A487563D5412D1 |  | R410A | TXV |  | -4.353% | 1.0435 | 1.219% |  |  |  |  | TXV |  |  | -4.353%
Fresno | CA | 93726-4851 |  | 2014-07-14 | 2014-07-14 11:54 | 2014-07-14 11:56 | PAYNE - F124RAC | 67 | 9.7 | Yes | Yes | 20.2 | 19.5 | 0.7 | 118130C007D94130AE1F693C076051C9 |  | R22 | Non-TXV |  | 14.48% | 0.85522 | 27.82% | [5 empty] | Non-TXV | 14.48%
Stockton | CA | 95210-1641 |  | 2014-05-23 | 2014-05-23 11:36 | 2014-05-23 11:53 | RUUD - URKA-A036JK08E | 62 | 5.8 | Yes | Yes | 22.9 | 19.1 | 3.8 | 789A7DDACC4C4FF09FD308360883FE4E |  | R22 | Non-TXV |  | 9.355% | 0.90645 | 17.98% | [5 empty] | Non-TXV | 9.355%
Chowchilla | CA | 93610-9081 |  | 2014-06-04 | 2014-06-04 12:58 | 2014-06-04 13:00 | RUUD - UKMA-A060JL10E | 184 | 7.4 | Yes | Yes | 27.4 | 21.5 | 5.9 | E09E725C2F684DE495F483A3B8322A5A |  | R22 | Non-TXV |  | 4.022% | 0.95978 | 7.729% | [5 empty] | Non-TXV | 4.022%
Selma | CA | 93662-2634 |  | 2014-06-13 | 2014-06-13 10:34 | 2014-06-13 10:34 | UNITARY PRODUCTS GROUP - BRCS0481BD | 117 | 0 | Yes | Yes | 24.5 | 20.4 | 4.1 | 5A79912FCA4C4B469C5A656C5E782BB3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-6772 |  | 2014-06-20 | 2014-06-20 13:34 | 2014-06-20 13:34 | YORK - H2RA060S06D | 118 | 0 | Yes | Yes | 21.1 | 21.9 | -0.8 | 94D4EE3F15334F52B4EF5DB7231447C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2645 |  | 2014-06-25 | 2014-06-25 19:04 | 2014-06-25 19:28 | CARRIER - 38ED048300 | 132 | 4 | Yes | Yes | 21 | 21.5 | -0.5 | 8A802C6CF6D34DFEAFE881DD35529E97 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Selma | CA | 93662-2643 |  | 2014-06-25 | 2014-06-25 18:41 | 2014-06-25 19:02 | UNITARY PRODUCTS GROUP - BRCS0301BD | 62 | 9.3 | Yes | Yes | 20.1 | 20.1 | 0 | C24DDF1EE1354657B6789BB6C4C2DD76 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Madera | CA | 93638-2107 |  | 2014-08-05 | 2014-08-05 12:15 | 2014-08-05 12:16 | YORK - D2NP024N03606A | 100 | 18.3 | Yes | Yes | 24.2 | 19.7 | 4.5 | C442655D6CEC4720AE06E9D35D4DD3BB |  | R22 | Non-TXV |  | 18.3% | 0.817 | 35.17% | [5 empty] | Non-TXV | 18.3%
Fresno | CA | 93705-2421 |  | 2014-07-30 | 2014-07-30 15:06 | 2014-07-30 15:23 | CARRIER - 490029-BB | 55 | 1.6 | Yes | Yes | 17.8 | 19.9 | -2.1 | 482CFA2A1ACF4C67A2F6FC25FF5350D1 |  | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Fresno | CA | 93705-5023 |  | 2014-07-29 | 2014-07-29 14:46 | 2014-07-29 15:33 | YORK - D2NZ036N05606 | 112 | 10 | Yes | Yes | 24.1 | 21 | 3.1 | B86B6CD9F6EA4A4C97F5E71882595428 |  | R410A | TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | TXV | 8.929%
Livingston | CA | 95334-1121 |  | 2014-06-06 | 2014-06-06 10:48 | 2014-06-06 11:05 | AIRE-FLO - GPCM36K060F | 85 | 10.7 | Yes | Yes | 20.6 | 17.9 | 2.7 | F6144C8D152546758F614745A807EA9F |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Chico | CA | 95926-7161 |  | 2014-06-12 | 2014-06-12 14:17 | 2014-06-12 14:32 | CARRIER - 38CKB048300 | 102 | 16.2 | Yes | Yes | 24.2 | 21.3 | 3 | EA44BD98A65D4E8E8CD8FA63334EE04C |  | R22 | Non-TXV |  | 15.88% | 0.84118 | 30.52% | [5 empty] | Non-TXV | 15.88%
Chico | CA | 95926-7161 |  | 2014-06-12 | 2014-06-12 15:20 | 2014-06-12 15:55 | CARRIER - 38CKB036320 | 70 | 13 | Yes | Yes | 22.5 | 21.5 | 1 | 08C0949DA0614E6CA198B82ABD97D34A |  | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Paradise | CA | 95969-3403 |  | 2014-06-04 | 2014-06-04 14:24 | 2014-06-04 14:43 | CARRIER - 48GX048115301A | 85 | 3.8 | Yes | Yes | 23.9 | 22 | 1.9 | DBE3D0ACFBF1465F8D21E390246A825E |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Corning | CA | 96021-2805 |  | 2014-06-16 | 2014-06-16 14:24 | 2014-06-16 14:44 | GOODMAN - CNL36-3L | 65 | 3 | Yes | Yes | 22 | 20.8 | 1.3 | 69C6465E681B4F6A96FB72355837791D |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Jackson | CA | 95642-9536 |  | 2014-08-27 | 2014-08-27 13:13 | 2014-08-27 13:30 | OTHER - UNK | 72 | 5.5 | Yes | Yes | 29 | 23 | 6 | 167403CA363144EA88597390A1F1BAF5 |  | R22 | Non-TXV |  | 7.639% | 0.92361 | 14.68% | [5 empty] | Non-TXV | 7.639%
Stockton | CA | 95206-4879 |  | 2014-06-11 | 2014-06-11 10:01 | 2014-06-11 10:19 | OTHER - WCA3362GKR2 | 115 | -5.8 | Yes | Yes | 25.4 | 19.8 | 5.6 | 21B5C43BE2F64C0EBB95AEA045C315C3 |  | R22 | TXV |  | -5.043% | 1.0504 | 1.412% |  |  |  |  | TXV |  |  | -5.043%
Fresno | CA | 93727-3908 |  | 2014-06-05 | 2014-06-05 11:20 | 2014-06-05 11:40 | BDP - 585EJW030050 | 58 | 2.4 | Yes | Yes | 27.6 | 21.9 | 5.7 | 01245817260347229B9A0D6EAEA626A5 |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Jackson | CA | 95642-2657 |  | 2014-07-30 | 2014-07-30 13:09 | 2014-07-30 13:31 | HEIL - CA3030VKB1 | 66 | 2.7 | Yes | Yes | 27 | 23.5 | 3.5 | 18CF79B5DA2C463E961699ADDE85624C |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Fresno | CA | 93704-4055 |  | 2014-06-13 | 2014-06-13 14:26 | 2014-06-13 14:46 | OTHER - GPCM036K060D | 68 | 12.7 | Yes | Yes | 21.4 | 21.3 | 0.1 | 7C53DEB52BC9402D91B78F73BD136A1D |  | R22 | Non-TXV |  | 18.68% | 0.81324 | 35.89% | [5 empty] | Non-TXV | 18.68%
Stockton | CA | 95212-2728 |  | 2014-06-06 | 2014-06-06 10:47 | 2014-06-06 11:04 | GOODMAN - CKJ42-1D | 99 | 3 | Yes | Yes | 23.5 | 20.9 | 2.6 | EB60F67E9A0544C0970E7CCD2252C9F8 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Coarsegold | CA | 93614-9655 |  | 2014-07-07 | 2014-07-07 13:34 | 2014-07-07 13:35 | OTHER - GPG12420701A | 105 | 14.4 | Yes | Yes | 22.9 | 21 | 1.9 | 36A2781098CC49949D420FEF7C2D4CCB |  | R22 | Non-TXV |  | 13.71% | 0.86286 | 26.36% | [5 empty] | Non-TXV | 13.71%
Fresno | CA | 93704-1013 |  | 2014-06-13 | 2014-06-13 11:29 | 2014-06-13 11:47 | YORK - D1NP048N09006A | 132 | 17 | Yes | Yes | 22.1 | 19.3 | 2.8 | F60545EF5AA54DFEBDBDAC1AB27499FB |  | R22 | Non-TXV |  | 12.88% | 0.87121 | 24.75% | [5 empty] | Non-TXV | 12.88%
Livingston | CA | 95334-9406 |  | 2014-06-06 | 2014-06-06 14:01 | 2014-06-06 14:19 | RHEEM - UNK | 76 | 15.7 | Yes | Yes | 30.7 | 24.7 | 6 | 394FCFDB3E564C1D93DE589DC137551C |  | R22 | Non-TXV |  | 20.66% | 0.79342 | 39.7% | [5 empty] | Non-TXV | 20.66%
Sutter Creek | CA | 95685-9709 |  | 2014-07-07 | 2014-07-07 11:57 | 2014-07-07 12:15 | BRYANT - 744DNWA36090NA | 100 | 3.6 | Yes | Yes | 26 | 21 | 5 | 78ACD1C5A44A4F20B4FBD51057E99FFC |  | R410A | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Fresno | CA | 93703-1154 |  | 2014-05-30 | 2014-05-30 15:22 | 2014-05-30 15:41 | BDP - 58GJW024040 | 54 | 3.8 | Yes | Yes | 23 | 23.7 | -0.7 | B87A53EA10FF4622B119417DE43BC09A |  | R22 | Non-TXV |  | 7.037% | 0.92963 | 13.52% | [5 empty] | Non-TXV | 7.037%
Stockton | CA | 95207-4282 |  | 2014-06-18 | 2014-06-18 12:44 | 2014-06-18 13:05 | CARRIER - 38EN018310 | 55 | 9.4 | Yes | Yes | 20.9 | 22.4 | -1.5 | EFFD3D0200F649638153E6F71E73F796 |  | R22 | Non-TXV |  | 17.09% | 0.82909 | 32.84% | [5 empty] | Non-TXV | 17.09%
Los Banos | CA | 93635-4572 |  | 2014-06-10 | 2014-06-10 13:11 | 2014-06-10 13:12 | GIBSON - JS3BA 048KA | 115 | 3.5 | Yes | Yes | 19.9 | 19.9 | 0 | 7733D8FDC1D5408888F4C39AE41DB159 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Stockton | CA | 95206-6235 |  | 2014-06-05 | 2014-06-05 13:39 | 2014-06-05 14:02 | BRYANT - 5610J036-D | 105 | 19.9 | Yes | Yes | 21.4 | 20.8 | 0.6 | D1E781CB64384EB39D7E515AB2C3B904 |  | R22 | Non-TXV |  | 18.95% | 0.81048 | 36.42% | [5 empty] | Non-TXV | 18.95%
Fresno | CA | 93703-1154 |  | 2014-06-11 | 2014-06-11 15:23 | 2014-06-11 15:44 | BDP - 585GJW024040 | 54 | 2.3 | Yes | Yes | 20.5 | 20.6 | -0.1 | CE72DEC235164DF78A21021184BBAB93 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Fresno | CA | 93726-4236 |  | 2014-06-27 | 2014-06-27 13:57 | 2014-06-27 14:06 | OTHER - CK601C | 122 | 22.2 | Yes | Yes | 26.8 | 22.8 | 4 | B08A8B10D8B2452A9A944ABA31DDD640 |  | R22 | Non-TXV |  | 18.2% | 0.81803 | 34.97% | [5 empty] | Non-TXV | 18.2%
Stockton | CA | 95206-4610 |  | 2014-06-11 | 2014-06-11 09:22 | 2014-06-11 09:51 | BRYANT - 561AJ036-C | 127 | 9.9 | Yes | Yes | 21.7 | 19.9 | 1.8 | B65742DDACE54852BE04BE2166BBD46A |  | R22 | TXV |  | 7.795% | 0.92205 | 14.98% | [5 empty] | TXV | 7.795%
Madera | CA | 93638-8151 |  | 2014-06-02 | 2014-06-02 12:36 | 2014-06-02 12:56 | CARRIER - 48ESNA3606030TP | 100 | 9.8 | Yes | Yes | 21.7 | 20.7 | 1 | 1301C925CE704D708C378A6D9E560838 |  | R410A | Non-TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | Non-TXV | 9.8%
Fresno | CA | 93710-5751 |  | 2014-05-29 | 2014-05-29 09:40 | 2014-05-29 10:01 | BDP - 585A048125YAC | 93 | 5.3 | Yes | Yes | 20.6 | 19.5 | 1.1 | C337B8BB35904E76ACEE3B12CA53B918 |  | R22 | Non-TXV |  | 5.699% | 0.94301 | 10.95% | [5 empty] | Non-TXV | 5.699%
Stockton | CA | 95204-5817 |  | 2014-06-05 | 2014-06-05 08:14 | 2014-06-05 08:36 | GOODMAN - CKL30-1F | 72 | -4.2 | Yes | Yes | 24 | 19.9 | 4.1 | 2A06F1686C4043F5819C9BB3128ADB30 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95205-2935 |  | 2014-06-03 | 2014-06-03 14:04 | 2014-06-03 14:21 | YORK - AC036X1021A | 62 | 3.6 | Yes | Yes | 25 | 20.6 | 4.4 | 1ED2C332A2DB4B089ACF680557D3C2F6 |  | R22 | Non-TXV |  | 5.806% | 0.94194 | 11.16% | [5 empty] | Non-TXV | 5.806%
Stockton | CA | 95219-3712 |  | 2014-06-06 | 2014-06-06 15:35 | 2014-06-06 15:53 | PAYNE - UNK | 90 | 2.6 | Yes | Yes | 20 | 20.7 | -0.7 | 0B7DE3B0FC7540F593236D6A69608739 |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Stockton | CA | 95205-5728 |  | 2014-06-03 | 2014-06-03 11:58 | 2014-06-03 12:16 | RHEEM - RAKA-024JAZ | 50 | -2.9 | Yes | Yes | 21 | 19.1 | 1.9 | 70EE3AE429F843E2ACAD20DEBC7BDB07 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Stockton | CA | 95210-1130 |  | 2014-05-23 | 2014-05-23 10:40 | 2014-05-23 11:01 | RHEEM - RAMB-036JBZ | 93 | 8.5 | Yes | Yes | 21.2 | 19.3 | 1.9 | 2D5F0064203B471BBF39D340B73BAAC6 |  | R22 | Non-TXV |  | 9.14% | 0.9086 | 17.56% | [5 empty] | Non-TXV | 9.14%
Tracy | CA | 95376-3605 |  | 2014-05-23 | 2014-05-23 09:49 | 2014-05-23 10:12 | PAYNE - PA10JAC30-A | 146 | 26.9 | Yes | Yes | 20.7 | 21 | -0.3 | 62292AAB63F145289CBC30419DD1142D |  | R22 | Non-TXV |  | 18.42% | 0.81575 | 35.41% | [5 empty] | Non-TXV | 18.42%
Tracy | CA | 95376-4324 |  | 2014-05-29 | 2014-05-29 15:24 | 2014-05-29 15:46 | GE - BTB930A100A0 | 53 | 5.5 | Yes | Yes | 21.6 | 22.6 | -1 | 5E6082742EF945EBBBCA92D2F53F38E7 |  | R22 | Non-TXV |  | 10.38% | 0.89623 | 19.94% | [5 empty] | Non-TXV | 10.38%
Chico | CA | 95973-0550 |  | 2014-06-10 | 2014-06-10 14:30 | 2014-06-10 14:46 | PAYNE - PA13N036036000ADAA | 50 | 4.9 | Yes | Yes | 25.9 | 20.6 | 5.3 | 6D78E0708A6A42D8952B813632835396 |  | R22 | Non-TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | Non-TXV | 9.8%
Stockton | CA | 95203-1636 |  | 2014-06-19 | 2014-06-19 09:32 | 2014-06-19 10:11 | PAYNE - PA13NR048-J | 136 | 7.5 | Yes | Yes | 24.3 | 19.8 | 4.5 | 9E9494D56510446AB95CEBC98AD6E877 |  | R22 | Non-TXV |  | 5.515% | 0.94485 | 10.6% | [5 empty] | Non-TXV | 5.515%
Corning | CA | 96021-2908 |  | 2014-05-28 | 2014-05-28 22:56 | 2014-05-28 11:12 | AMANA - NA | 70 | 5.5 | Yes | Yes | 20.5 | 20.4 | 0.1 | 426997DCE6D64055AC3343AA62C29191 |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Tracy | CA | 95376-3834 |  | 2014-06-02 | 2014-06-02 08:57 | 2014-06-02 09:14 | YORK - UNK | 85 | 4.5 | Yes | Yes | 21 | 20.3 | 0.7 | B107ACA95D254BD095E4319F8CD8D503 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Pine Grove | CA | 95665-9606 |  | 2014-07-07 | 2014-07-07 10:16 | 2014-07-07 10:40 | YORK - D1NA030N05606C | 76 | 5.7 | Yes | Yes | 23 | 22.3 | 0.7 | F522F10E14A24D55AAE6032913FDA5AE |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Selma | CA | 93662-2529 |  | 2014-08-06 | 2014-08-06 13:54 | 2014-08-06 14:19 | ICP - PGAD24D1KE | 69 | 4.7 | Yes | Yes | 18.5 | 18.2 | 0.3 | 8D4BCD5CAB854BB7983FE20885A47CB5 |  | R22 | Non-TXV |  | 6.812% | 0.93188 | 13.09% | [5 empty] | Non-TXV | 6.812%
Copperopolis | CA | 95228-9571 |  | 2014-08-20 | 2014-08-20 13:47 | 2014-08-20 14:04 | DAY & NIGHT - 541DJ030 | 80 | 13.5 | Yes | Yes | 17.1 | 18.5 | -1.4 | 890E762E00AE448BB9C11D19A173BEE7 |  | R22 | Non-TXV |  | 16.88% | 0.83125 | 32.43% | [5 empty] | Non-TXV | 16.88%
Red Bluff | CA | 96080-4144 |  | 2014-06-03 | 2014-06-03 13:15 | 2014-06-03 13:31 | GOODMAN - GBC130241DA | 83 | 10.7 | Yes | Yes | 24.2 | 21.4 | 2.8 | 6C3A3393E9254B14A3EE9D80E8EAEF16 |  | R22 | Non-TXV |  | 12.89% | 0.87108 | 24.77% | [5 empty] | Non-TXV | 12.89%
Tracy | CA | 95376-4877 |  | 2014-06-09 | 2014-06-09 10:58 | 2014-06-09 11:21 | OTHER - HAMC-F036AA | 85 | 4.3 | Yes | Yes | 23.7 | 21.4 | 2.3 | A5CC4BB2D3D6499F94888F4D1A229C07 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Lathrop | CA | 95330-8662 |  | 2014-05-28 | 2014-05-28 12:28 | 2014-05-28 12:53 | CARRIER - 24ABA336A300 | 105 | -5.7 | Yes | Yes | 22.3 | 20.7 | 1.7 | 98D3D1CEE8844CA79FF3ECB429398EEF |  | R410A | TXV |  | -5.429% | 1.0543 | 1.52% |  |  |  |  | TXV |  |  | -5.429%
Chico | CA | 95926-1823 |  | 2014-06-06 | 2014-06-06 13:16 | 2014-06-06 13:33 | BRYANT - 1H13NR024-K | 65 | 4.9 | Yes | Yes | 16.5 | 19.3 | -2.8 | DE5DB32D64164943B2075435627175FD |  | R22 | TXV |  | 7.538% | 0.92462 | 14.49% | [5 empty] | TXV | 7.538%
Tracy | CA | 95376-2125 |  | 2014-05-23 | 2014-05-23 12:21 | 2014-05-23 12:47 | OTHER - UNK | 85 | 3.9 | Yes | Yes | 21.9 | 20.9 | 1 | EBC4377D5E444D49854B51ED6E2F2194 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Dinuba | CA | 93618-3301 |  | 2014-07-16 | 2014-07-16 10:34 | 2014-07-16 11:26 | LUXAIRE - 80WE42G1 | 85 | 5.2 | Yes | Yes | 21.3 | 20.4 | 0.9 | 6085A2FBC89B4036B5930B88E60C482C |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Merced | CA | 95340-4345 |  | 2014-07-09 | 2014-07-09 09:13 | 2014-07-09 09:16 | COLEMAN - 4530A601 | 56 | 5.1 | Yes | Yes | 24.8 | 20.8 | 4 | C44CFBD0404C402983811926D3A861FF |  | R22 | Non-TXV |  | 9.107% | 0.90893 | 17.5% | [5 empty] | Non-TXV | 9.107%
Clovis | CA | 93612-4602 |  | 2014-06-12 | 2014-06-12 11:04 | 2014-06-12 11:05 | GOODMAN - GPG10300701A | 50 | 2.3 | Yes | Yes | 23.4 | 20.4 | 3 | 0124252238E64E2A91D0F54B491E4850 |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Clovis | CA | 93612-4602 |  | 2014-06-12 | 2014-06-12 11:12 | 2014-06-12 11:14 | GOODMAN - GPG10300701A | 50 | 1.6 | Yes | Yes | 21.2 | 19.8 | 1.4 | C079D3CA36AC44099ABA9BF0AEA064A8 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Stockton | CA | 95205-6905 |  | 2014-06-03 | 2014-06-03 10:57 | 2014-06-03 11:17 | GOODMAN - GSC130241AE | 93 | -8.8 | Yes | Yes | 18.6 | 19.3 | -0.7 | 631ED829373743A783F87CBABA6DC41D |  | R22 | Non-TXV |  | -9.462% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.462%
Merced | CA | 95340-4345 |  | 2014-07-03 | 2014-07-03 08:42 | 2014-07-03 08:44 | COLEMAN - 7777UNK | 84 | 3.7 | Yes | Yes | 22.5 | 19.5 | 3 | AF22DB963C8748DE95EFC78BD27F905B |  | R22 | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Stockton | CA | 95215-6806 |  | 2014-06-10 | 2014-06-10 09:29 | 2014-06-10 09:48 | LENNOX - 13GEP30075ALP-3A | 68 | -4 | Yes | Yes | 18.3 | 18.5 | -0.2 | AEFD7F037C3E4592897E2DF30E7B6853 |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93703-2022 |  | 2014-06-19 | 2014-06-19 12:09 | 2014-06-19 12:10 | LENNOX - 12GCS60X-100-4PA | 159 | 7 | Yes | Yes | 23.3 | 23.7 | -0.4 | 15FD3B9358CF45A8A92BE4B1A86101DA |  | R22 | Non-TXV |  | 4.403% | 0.95597 | 8.461% | [5 empty] | Non-TXV | 4.403%
Clovis | CA | 93612-4622 |  | 2014-06-05 | 2014-06-05 14:09 | 2014-06-05 14:34 | CARRIER - 48KLA136311BE | 95 | 18 | Yes | Yes | 25.2 | 22.8 | 2.4 | C3568114CF7446B3B633480F76F9FB8E |  | R22 | Non-TXV |  | 18.95% | 0.81053 | 36.41% | [5 empty] | Non-TXV | 18.95%
Clovis | CA | 93611-5051 |  | 2014-05-30 | 2014-05-30 15:52 | 2014-05-30 16:11 | LENNOX - 12ACB48-5P | 171 | 8.3 | Yes | Yes | 21.1 | 23.7 | -2.6 | B9BA97FA842A4975A078E5C6F29E9584 |  | R22 | Non-TXV |  | 4.854% | 0.95146 | 9.328% | [5 empty] | Non-TXV | 4.854%
Fresno | CA | 93704-5849 |  | 2014-08-12 | 2014-08-12 11:16 | 2014-08-12 11:18 | OTHER - PGAA18C1K1 | 57 | 12.6 | Yes | Yes | 21.1 | 21.9 | -0.8 | 4C86091908E34C88AF2E39B6A17F96F8 |  | R22 | Non-TXV |  | 22.11% | 0.77895 | 42.48% | [5 empty] | Non-TXV | 22.11%
Corning | CA | 96021-3541 |  | 2014-07-07 | 2014-07-07 13:51 | 2014-07-07 21:18 | YORK - H4DBC306 | 75 | 3.8 | Yes | Yes | 23.5 | 20.5 | 3 | 22173A6804F64A37992C108B132EB21C |  | R22 | Non-TXV |  | 5.067% | 0.94933 | 9.737% | [5 empty] | Non-TXV | 5.067%
Stockton | CA | 95207-2716 |  | 2014-05-31 | 2014-05-31 10:49 | 2014-05-31 11:06 | DAY & NIGHT - 84ANW030040 | 70 | 6.5 | Yes | Yes | 20.1 | 19.4 | 0.7 | EA6E61BDB2D04CAEBA792D1CB9E3B405 |  | R22 | Non-TXV |  | 9.286% | 0.90714 | 17.85% | [5 empty] | Non-TXV | 9.286%
Chico | CA | 95926-2758 |  | 2014-06-18 | 2014-06-18 10:28 | 2014-06-18 22:45 | CARRIER - 1892E46424 | 50 | 4.4 | Yes | Yes | 19 | 17.5 | 1.6 | BD1A5A5759C44882AD1C3ADB3F017FA1 |  | R22 | Non-TXV |  | 8.8% | 0.912 | 16.91% | [5 empty] | Non-TXV | 8.8%
Merced | CA | 95348-9521 |  | 2014-06-09 | 2014-06-09 14:35 | 2014-06-09 14:54 | GOODMAN - CKL301G | 74 | 10.3 | Yes | Yes | 22.3 | 23.7 | -1.4 | 2DC65C7406CF418BB3A043B0288A253F |  | R22 | Non-TXV |  | 13.92% | 0.86081 | 26.75% | [5 empty] | Non-TXV | 13.92%
Oroville | CA | 95966-5537 |  | 2014-05-27 | 2014-05-27 11:40 | 2014-05-27 11:58 | BRYANT - 563CN042-A | 130 | 3.8 | Yes | Yes | 21 | 20.8 | 0.2 | 96EC98AE14F0401C9270FB584F2B3EED |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Fresno | CA | 93726-1250 |  | 2014-07-01 | 2014-07-01 16:04 | 2014-07-01 16:25 | ICP - PGF024K040D | 58 | 4 | Yes | Yes | 20.5 | 20.6 | -0.1 | 43D93FA422654EE5810989751D439869 |  | R22 | Non-TXV |  | 6.897% | 0.93103 | 13.25% | [5 empty] | Non-TXV | 6.897%
Stockton | CA | 95210-2314 |  | 2014-05-31 | 2014-05-31 09:54 | 2014-05-31 10:20 | OTHER - 10AJB24A05 | 65 | -3.8 | Yes | Yes | 22.8 | 19.1 | 3.7 | 5968AB30917443058182F02377C62D3B |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Stockton | CA | 95203-1907 |  | 2014-06-17 | 2014-06-17 11:33 | 2014-06-17 11:50 | AMANA - PGD30C0702E | 74 | 2.7 | Yes | Yes | 24.8 | 18.9 | 5.9 | A7027C116BB6432AA6993BB1FCA91D8A |  | R22 | Non-TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | Non-TXV | 3.649%
Stockton | CA | 95206-6404 |  | 2014-06-16 | 2014-06-16 08:56 | 2014-06-16 09:17 | GOODMAN - CKL30-1E | 85 | 12.4 | Yes | Yes | 20.7 | 20.4 | 0.3 | F4D46D6677834E8EB63393261FBBD092 |  | R22 | Non-TXV |  | 14.59% | 0.85412 | 28.04% | [5 empty] | Non-TXV | 14.59%
Los Banos | CA | 93635-6507 |  | 2014-06-10 | 2014-06-10 13:56 | 2014-06-10 13:57 | GIBSON - JSBC-030KA | 68 | 2.5 | Yes | Yes | 19.5 | 19.4 | 0.1 | D571F415D0AF4855974D1F133232AAA3 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Fresno | CA | 93727-1931 |  | 2014-06-04 | 2014-06-04 09:48 | 2014-06-04 10:04 | RHEEM - RRNA-B042JK08X | 104 | 3.5 | Yes | Yes | 19.2 | 20.4 | -1.2 | 3BDE4F2A79F84E7E9FFDB4E9ED7E74C7 |  | R22 | Non-TXV |  | 3.365% | 0.96635 | 6.468% | [5 empty] | Non-TXV | 3.365%
Los Banos | CA | 93635-3210 |  | 2014-06-27 | 2014-06-27 14:36 | 2014-06-27 14:53 | DAY & NIGHT - PGN336060K01A1 | 131 | -7.7 | Yes | Yes | 23.1 | 22.1 | 1 | C545434FE7AF473B8D418C0F4511C010 |  | R22 | Non-TXV |  | -5.878% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.878%
Stockton | CA | 95207-1615 |  | 2014-05-30 | 2014-05-30 08:44 | 2014-05-30 09:02 | JANITROL - UNK | 54 | 2.3 | Yes | Yes | 18.2 | 20.1 | -1.9 | 727855CA1D494D4BB3BF2970F84DCE1B |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Stockton | CA | 95203-1239 |  | 2014-06-07 | 2014-06-07 10:09 | 2014-06-07 10:09 | YORK - D3Y5036N04506C | 78 | 0 | Yes | Yes | 26.6 | 20.6 | 6 | A2075BB380E642D4B25EF4AD873DEA8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2829 |  | 2014-06-17 | 2014-06-17 14:22 | 2014-06-17 14:24 | CARRIER - 585CJ03675 | 55 | 8.5 | Yes | Yes | 24.8 | 20.4 | 4.4 | 4D1D3077E6EC41D7A8C300C77B3F5E4C |  | R22 | Non-TXV |  | 15.45% | 0.84545 | 29.7% | [5 empty] | Non-TXV | 15.45%
Sanger | CA | 93657-3529 |  | 2014-06-20 | 2014-06-20 14:43 | 2014-06-20 15:04 | GOODMAN - GPG13360701AA | 112 | 3.5 | Yes | Yes | 20.5 | 21 | -0.5 | 04092036F6D64037B808587BED058DCC |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93702-2550 |  | 2014-06-30 | 2014-06-30 11:45 | 2014-06-30 12:11 | RHEEM - RRNL-B036JK08X | 92 | 3.5 | Yes | Yes | 21.2 | 19.2 | 2 | 63A68DC94BA14F4CAB8BE94F163A46F9 |  | R410A | TXV |  | 3.804% | 0.96196 | 7.311% | [5 empty] | TXV | 3.804%
Stockton | CA | 95206-6115 |  | 2014-06-05 | 2014-06-05 14:40 | 2014-06-05 14:56 | GOODMAN - CKJ42-1AB | 85 | -5 | Yes | Yes | 23.7 | 21 | 2.7 | F57453C6C4D948518A7E1E8B44E22767 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Chico | CA | 95928-4380 |  | 2014-06-19 | 2014-06-19 13:30 | 2014-06-19 13:50 | BRYANT - 563CN030-B | 98 | 4.6 | Yes | Yes | 18 | 20.9 | -2.9 | 3D0AD70D1B1B458C921D676D82789245 |  | R22 | Non-TXV |  | 4.694% | 0.95306 | 9.021% | [5 empty] | Non-TXV | 4.694%
Paradise | CA | 95969-2239 |  | 2014-05-23 | 2014-05-23 14:52 | 2014-05-23 15:08 | RUUD - NA | 55 | 12.6 | Yes | Yes | 18.6 | 20.9 | -2.3 | 5E0B0E128E2745FEA9C4965D6E72C751 |  | R22 | Non-TXV |  | 22.91% | 0.77091 | 44.03% | [5 empty] | Non-TXV | 22.91%
Fresno | CA | 93725-1512 |  | 2014-06-16 | 2014-06-16 10:11 | 2014-06-16 10:12 | OTHER - DAYAF042N090C | 76 | 7.5 | Yes | Yes | 26 | 21 | 5 | A3FFB0FAFE34441FA3D8F272FE02AC8B |  | R22 | Non-TXV |  | 9.868% | 0.90132 | 18.96% | [5 empty] | Non-TXV | 9.868%
Fresno | CA | 93728-1713 |  | 2014-06-09 | 2014-06-09 19:52 | 2014-06-09 20:55 | RHEEM - RRPL-B036JK06X | 92 | 8.9 | Yes | Yes | 21.9 | 21.9 | 0 | 2412284EBBED4AA9B725C3E9151D880E |  | R410A | TXV |  | 9.674% | 0.90326 | 18.59% | [5 empty] | TXV | 9.674%
Rocklin | CA | 95677-1618 |  | 2014-06-18 | 2014-06-18 12:30 | 2014-06-18 12:46 | ALLEGIANCE - 4A7Z00481000AA | 247 | 10.5 | Yes | Yes | 27 | 23.2 | 3.8 | 06BB367CEFE649A0A4F1702F267B4DAE |  | R410A | TXV |  | 4.251% | 0.95749 | 8.17% | [5 empty] | TXV | 4.251%
Stockton | CA | 95212-1123 |  | 2014-06-06 | 2014-06-06 12:45 | 2014-06-06 13:06 | COLEMAN - ERCS0481BBB | 134 | 4.3 | Yes | Yes | 23 | 21.5 | 1.5 | 5CCD7A5401EB43959400309D5E392E95 |  | R22 | Non-TXV |  | 3.209% | 0.96791 | 6.167% | [5 empty] | Non-TXV | 3.209%
Fresno | CA | 93727-1957 |  | 2014-06-03 | 2014-06-03 09:34 | 2014-06-03 09:56 | LENNOX - 12GCS042-75-3PA | 133 | 5.7 | Yes | Yes | 22.4 | 19.3 | 3.1 | 9C4B4E35ECCC45AA8D30DCF415CA0C07 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95207-7103 |  | 2014-06-21 | 2014-06-21 09:12 | 2014-06-21 09:42 | CARRIER - 38CKC060300 | 152 | 30.8 | Yes | Yes | 26.4 | 20.6 | 5.8 | 894B0867CC6D4121B8DA1F74EB7D81C5 |  | R22 | Non-TXV |  | 20.26% | 0.79737 | 38.94% | [5 empty] | Non-TXV | 20.26%
Nevada City | CA | 95959-2333 |  | 2014-06-26 | 2014-06-26 08:49 | 2014-06-26 09:08 | COPELAND - ZRCF36U01E | 107 | 3.1 | Yes | Yes | 24 | 20.2 | 3.8 | 4F75A62CF4B34D61808A299762E38D93 |  | R22 | Non-TXV |  | 2.897% | 0.97103 | 5.568% | [5 empty] | Non-TXV | 2.897%
Stockton | CA | 95203-1738 |  | 2014-06-20 | 2014-06-20 14:15 | 2014-06-20 14:33 | NORDYNE - S3BD-036K | 114 | 4.5 | Yes | Yes | 27.1 | 21.3 | 5.8 | 8BBC2181FD2F4CB68A7417259C6382C2 |  | R22 | Non-TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | Non-TXV | 3.947%
Stockton | CA | 95206-6052 |  | 2014-06-05 | 2014-06-05 10:36 | 2014-06-05 11:05 | GOODMAN - CLJ36-1 | 85 | 15.2 | Yes | Yes | 20.5 | 20.4 | 0.1 | A6064B1CF5C044AFA65001F5AB9162E7 |  | R22 | Non-TXV |  | 17.88% | 0.82118 | 34.37% | [5 empty] | Non-TXV | 17.88%
Stockton | CA | 95210-3334 |  | 2014-05-23 | 2014-05-23 09:48 | 2014-05-23 10:10 | CARRIER - PA10JA048-D | 97 | 5.9 | Yes | Yes | 22.9 | 21.5 | 1.4 | F284F5E49DC14B9CB8F02EC87A78C6CC |  | R22 | Non-TXV |  | 6.082% | 0.93918 | 11.69% | [5 empty] | Non-TXV | 6.082%
Dinuba | CA | 93618-4049 |  | 2014-07-11 | 2014-07-11 15:33 | 2014-07-11 15:54 | NORDYNE - FS3BA-024KA | 64 | 5.6 | Yes | Yes | 20.5 | 22.1 | -1.6 | AAECF6CB933C455BB5B24BDE3BEB561A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Oroville | CA | 95965-4122 |  | 2014-06-04 | 2014-06-04 08:45 | 2014-06-04 09:02 | TRANE - TTR042C100A2 | 110 | 3.8 | Yes | Yes | 23.6 | 18.8 | 4.8 | 0642B419F5244CA2A57848D43E14C8AD |  | R22 | Non-TXV |  | 3.455% | 0.96545 | 6.639% | [5 empty] | Non-TXV | 3.455%
Merced | CA | 95340-4345 |  | 2014-09-11 | 2014-09-11 16:50 | 2014-09-11 16:51 | ARCOAIRE - NAC042AKC3 | 112 | 3.7 | Yes | Yes | 23.8 | 19.5 | 4.3 | 329A4144AB9246F6BEA2564A7342B2C2 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Los Banos | CA | 93635-3626 |  | 2014-06-11 | 2014-06-11 13:21 | 2014-06-11 13:22 | OTHER - GS3BA-024KA | 64 | 3.4 | Yes | Yes | 23.1 | 20.8 | 2.3 | 2DF13D5825614A839A5A41A12340A839 |  | R22 | Non-TXV |  | 5.312% | 0.94688 | 10.21% | [5 empty] | Non-TXV | 5.312%
Clovis | CA | 93612-0431 |  | 2014-06-02 | 2014-06-02 14:39 | 2014-06-02 14:41 | RHEEM - RRKA-A024JK06E | 50 | 1.9 | Yes | Yes | 19.1 | 18.6 | 0.5 | 2DFE5EF38A72400A9BE79245855F4E1D |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Fresno | CA | 93726-1462 |  | 2014-07-09 | 2014-07-09 13:06 | 2014-07-09 13:07 | BDP - 585HJ018040 | 61 | 10.9 | Yes | Yes | 17.2 | 18.1 | -0.9 | A9B0D335E9CE42C2AC3A5D90EFA56796 |  | R22 | Non-TXV |  | 17.87% | 0.82131 | 34.34% | [5 empty] | Non-TXV | 17.87%
Lincoln | CA | 95648-2052 |  | 2014-06-16 | 2014-06-16 13:13 | 2014-06-16 13:30 | OTHER - DAYA-F030N070C | 76 | 2.3 | Yes | Yes | 25 | 21.5 | 3.5 | FAFB7AACD6A64537968F7A82B256A2BF |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Lincoln | CA | 95648-3243 |  | 2014-06-16 | 2014-06-16 12:39 | 2014-06-16 12:39 | OTHER - UNK | 85 | 0 | Yes | Yes | -1 | 19.9 | -20.9 | C0A6015466274E7095408BDE873C3D5D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-4049 |  | 2014-07-11 | 2014-07-11 19:02 | 2014-07-11 19:40 | NORDYNE - N/A | 68 | 3.7 | Yes | Yes | 22.4 | 21.5 | 0.9 | CB40D93CCA3A4CADBCBFD7EBCFE857A8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Madera | CA | 93638-1727 |  | 2014-06-12 | 2014-06-12 08:57 | 2014-06-12 09:18 | OTHER - 35024AQ111 | 56 | 12.7 | Yes | Yes | 22.8 | 19 | 3.8 | 0ABF204EE4AF44B2A672F8877DAFF3D4 |  | R22 | Non-TXV |  | 22.68% | 0.77321 | 43.58% | [5 empty] | Non-TXV | 22.68%
Grass Valley | CA | 95949-7356 |  | 2014-05-23 | 2014-05-23 11:31 | 2014-05-23 11:55 | LENNOX - GCS20-651-125-1P | 117 | 3.5 | Yes | Yes | 22 | 20.4 | 1.6 | 562C2FA61B034081811ADA68426479E9 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Clovis | CA | 93611-5219 |  | 2014-05-30 | 2014-05-30 13:53 | 2014-05-30 13:55 | CARRIER - 7777UNK | 84 | 3.6 | Yes | Yes | 22.1 | 23.6 | -1.5 | 05B66C627DB74C1788E3843A0A6E5535 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Dinuba | CA | 93618-4059 |  | 2014-07-23 | 2014-07-23 17:59 | 2014-07-23 18:26 | UNITARY PRODUCTS GROUP - H2RD024S06B | 88 | 4 | Yes | Yes | 21.2 | 22 | -0.8 | 4412ACEE1BA64B9CBFC72FE5B6A58756 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93727-3366 |  | 2014-06-03 | 2014-06-03 15:32 | 2014-06-03 15:57 | COLEMAN - 9541-901 | 53 | 14.3 | Yes | Yes | 22.2 | 22.5 | -0.3 | B0FE6413CC19410A9CAC55004D9BBD24 |  | R22 | Non-TXV |  | 26.98% | 0.73019 | 51.85% | [5 empty] | Non-TXV | 26.98%
Lincoln | CA | 95648-2839 |  | 2014-05-26 | 2014-05-26 10:48 | 2014-05-26 11:16 | OTHER - FADC-048JAS | 113 | 3.3 | Yes | Yes | 20 | 18.8 | 1.2 | ED3923CDC0E749BF9276454B36D89900 |  | R22 | Non-TXV |  | 2.92% | 0.9708 | 5.612% | [5 empty] | Non-TXV | 2.92%
Stockton | CA | 95207-7123 |  | 2014-06-06 | 2014-06-06 10:31 | 2014-06-06 10:54 | GOODMAN - GSC130421CA | 108 | 3.2 | Yes | Yes | 20.4 | 18.8 | 1.6 | 0CA3150BB8EB4A6FBE8CC4BCC683B049 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Auburn | CA | 95602-8012 |  | 2014-06-18 | 2014-06-18 09:25 | 2014-06-18 09:42 | OTHER - Q3RA-036K | 80 | 2.4 | Yes | Yes | 23 | 20.1 | 2.9 | E094A63532544D14AD77F64B297637F0 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Oroville | CA | 95966-9230 |  | 2014-06-12 | 2014-06-12 09:32 | 2014-06-12 09:57 | DAY & NIGHT - PGD33606K00K1 | 78 | 2.4 | Yes | Yes | 21 | 20.7 | 0.3 | 5B3E60C1ABE84FD3A197BCF6BBA77C30 |  | R410A | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Fresno | CA | 93722-3518 |  | 2014-05-27 | 2014-05-27 08:23 | 2014-05-27 08:50 | CARRIER - 591ANX060000AAAA | 166 | 23.9 | Yes | Yes | 20 | 17.1 | 2.9 | 605EB9EE1FDF438B8799E3A02EB26409 |  | R22 | Non-TXV |  | 14.4% | 0.85602 | 27.67% | [5 empty] | Non-TXV | 14.4%
Stockton | CA | 95212-1516 |  | 2014-06-06 | 2014-06-06 11:30 | 2014-06-06 11:51 | RHEEM - RRNA-B048JK10X | 153 | 4.6 | Yes | Yes | 20 | 19.9 | 0.1 | 25B84869632C4347B9A1D8B4FF9B9982 |  | R22 | Non-TXV |  | 3.007% | 0.96993 | 5.778% | [5 empty] | Non-TXV | 3.007%
Oakdale | CA | 95361-3359 |  | 2014-06-04 | 2014-06-04 08:41 | 2014-06-04 09:04 | CARRIER - N4A436AK200 | 193 | 22.5 | Yes | Yes | 19.7 | 19.7 | 0.1 | 2E30F8A1EC854D58A2127F37DB14D7AF |  | R410A | TXV |  | 11.66% | 0.88342 | 22.4% | [5 empty] | TXV | 11.66%
Livingston | CA | 95334-9209 |  | 2014-06-06 | 2014-06-06 11:44 | 2014-06-06 12:10 | WEATHER KING - 10AJB24A01 | 65 | 8.5 | Yes | Yes | 20.9 | 20.1 | 0.8 | 353287AB97994E919D3F555927552DA4 |  | R22 | Non-TXV |  | 13.08% | 0.86923 | 25.13% | [5 empty] | Non-TXV | 13.08%
Livingston | CA | 95334-9580 |  | 2014-06-06 | 2014-06-06 13:17 | 2014-06-06 13:43 | RUUD - UAKA03JAS | 68 | 10.6 | Yes | Yes | 23.9 | 23.6 | 0.3 | 44E412A167CC4426850F3653C41861B9 |  | R22 | Non-TXV |  | 15.59% | 0.84412 | 29.96% | [5 empty] | Non-TXV | 15.59%
Livingston | CA | 95334-1834 |  | 2014-06-06 | 2014-06-06 12:41 | 2014-06-06 13:03 | AMANA - VCA36C2A | 68 | 16.4 | Yes | Yes | 25.9 | 20.4 | 5.5 | 9C2901724B134A7BAE59235331DE3072 |  | R22 | Non-TXV |  | 24.12% | 0.75882 | 46.35% | [5 empty] | Non-TXV | 24.12%
Manteca | CA | 95337-9656 |  | 2014-05-27 | 2014-05-27 09:22 | 2014-05-27 09:46 | RUUD - UNK | 85 | -8 | Yes | Yes | 24.3 | 21.4 | 2.9 | 19ED12B8CCAE408C9ED796CCBB36AA4C |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Clovis | CA | 93612-0465 |  | 2014-06-02 | 2014-06-02 17:20 | 2014-06-02 17:45 | CARRIER - N/A | 90 | 4.7 | Yes | Yes | 22.1 | 22.4 | -0.3 | 5C17D878FF58476886CCC78E30C0CFFE |  | R22 | Non-TXV |  | 5.222% | 0.94778 | 10.04% | [5 empty] | Non-TXV | 5.222%
Red Bluff | CA | 96080-3830 |  | 2014-06-03 | 2014-06-03 14:34 | 2014-06-03 15:00 | WESTINGHOUSE - 5902SCA | 37 | 7.1 | Yes | Yes | 16.5 | 18.6 | -2.1 | CD8107C93B9343E588838BCB5C8930EB |  | R22 | Non-TXV |  | 19.19% | 0.80811 | 36.88% | [5 empty] | Non-TXV | 19.19%
Stockton | CA | 95210-4428 |  | 2014-05-28 | 2014-05-28 13:29 | 2014-05-28 13:48 | PAYNE - 591ANX060000AAAA | 166 | 6.7 | Yes | Yes | 26.8 | 22.6 | 4.2 | 2B7425B82CF8409FBADBD9C3C681653C |  | R22 | Non-TXV |  | 4.036% | 0.95964 | 7.757% | [5 empty] | Non-TXV | 4.036%
Merced | CA | 95340-1620 |  | 2014-08-27 | 2014-08-27 14:42 | 2014-08-27 14:58 | YORK - H2DH036S06A | 85 | 2.5 | Yes | Yes | 19 | 20.4 | -1.4 | 56CB846389E9446781833B561F14FF5D |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Chico | CA | 95928-5877 |  | 2014-06-26 | 2014-06-26 09:36 | 2014-06-26 09:53 | PAYNE - PY1PNB024060AAAA | 53 | 6.4 | Yes | Yes | 18.9 | 19.9 | -1 | C4F4030BF93D4FA28C8CA095225185D8 |  | R22 | Non-TXV |  | 12.08% | 0.87925 | 23.21% | [5 empty] | Non-TXV | 12.08%
Fresno | CA | 93727-4827 |  | 2014-06-07 | 2014-06-07 15:35 | 2014-06-07 15:53 | HEIL - NRGF24DDB04 | 53 | 1.8 | Yes | Yes | 21.5 | 19.1 | 2.5 | 2DFD10D6BD9140E69A89DAEB47AF93CF |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Stockton | CA | 95206-5131 |  | 2014-06-16 | 2014-06-16 11:36 | 2014-06-16 11:58 | CARRIER - 38CKC036350 | 124 | -8 | Yes | Yes | 19.8 | 19.9 | -0.1 | 699AAF17998B4519A670363CB373A2E6 |  | R22 | TXV |  | -6.452% | 1.0645 | 1.807% |  |  |  |  | TXV |  |  | -6.452%
Tracy | CA | 95377-1118 |  | 2014-06-02 | 2014-06-02 08:12 | 2014-06-02 08:41 | CARRIER - 38CKC048370 | 121 | 4.4 | Yes | Yes | 23.3 | 22.6 | 0.7 | 6037D107554A40AA9673C78D740E3409 |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Mendota | CA | 93640-2072 |  | 2014-08-27 | 2014-08-27 08:08 | 2014-08-27 08:25 | GOODMAN - GSX130361DA | 77 | 2.3 | Yes | Yes | 17.8 | 20.4 | -2.6 | 8957D452FFAE4DBD9C3D4D33B87A50D5 |  | R410A | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Tracy | CA | 95376-4618 |  | 2014-06-02 | 2014-06-02 09:26 | 2014-06-02 10:03 | CARRIER - 563AN048-A | 205 | 9.3 | Yes | Yes | 22 | 20.4 | 1.6 | C598E699DB694F9E98D9F3C10757F733 |  | R22 | Non-TXV |  | 4.537% | 0.95463 | 8.718% | [5 empty] | Non-TXV | 4.537%
Penn Valley | CA | 95946-8919 |  | 2014-05-23 | 2014-05-23 15:38 | 2014-05-23 16:04 | TRANE - YCX042F1M0BB | 119 | 3.6 | Yes | Yes | 17 | 18.8 | -1.8 | EEB07FD04FAE47ADAFC46904279FA697 |  | R22 | Non-TXV |  | 3.025% | 0.96975 | 5.814% | [5 empty] | Non-TXV | 3.025%
Paradise | CA | 95969-2242 |  | 2014-07-23 | 2014-07-23 15:03 | 2014-07-23 16:00 | COLEMAN - NA | 55 | 3.2 | Yes | Yes | 17.6 | 20.4 | -2.8 | DBE92BA31EDE48C19BDFE3DA68869DC3 |  | R22 | Non-TXV |  | 5.818% | 0.94182 | 11.18% | [5 empty] | Non-TXV | 5.818%
Yuba City | CA | 95991-4833 |  | 2014-07-02 | 2014-07-02 12:23 | 2014-07-02 12:53 | BRYANT - 582ANW036090AAAF | 56 | 3.8 | Yes | Yes | 23 | 20.4 | 2.6 | DFDBE40BB8C246578C36116913337FEF |  | R22 | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Stockton | CA | 95205-2530 |  | 2014-06-03 | 2014-06-03 09:38 | 2014-06-03 10:04 | DAY & NIGHT - UNK | 70 | 5.5 | Yes | Yes | 20.4 | 18.7 | 1.7 | 6E056D8A227D485E8661224B579233AB |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Fresno | CA | 93726-0933 |  | 2014-07-14 | 2014-07-14 09:58 | 2014-07-14 09:59 | BDP - 585A024055YAC | 51 | 13.4 | Yes | Yes | 21.5 | 21.5 | 0 | 0B79D0BE2A5F426884FCCB03302DD976 |  | R22 | Non-TXV |  | 26.27% | 0.73725 | 50.49% | [5 empty] | Non-TXV | 26.27%
Clovis | CA | 93611-4543 |  | 2014-06-10 | 2014-06-10 12:48 | 2014-06-10 13:06 | PAYNE - UNK | 76 | 14.3 | Yes | Yes | 23.9 | 22.1 | 1.8 | C6D78D6003F84209A0A07640B5F45E80 |  | R22 | Non-TXV |  | 18.82% | 0.81184 | 36.16% | [5 empty] | Non-TXV | 18.82%
Fresno | CA | 93730-3435 |  | 2014-07-31 | 2014-07-31 13:47 | 2014-07-31 14:05 | BDP - 598AN036-B | 197 | 5.8 | Yes | Yes | 17.5 | 19.3 | -1.8 | EFCB36A2D0D6403984C12E6B4F1FA4D0 |  | R22 | Non-TXV |  | 2.944% | 0.97056 | 5.658% | [5 empty] | Non-TXV | 2.944%
Dinuba | CA | 93618-3301 |  | 2014-07-16 | 2014-07-16 10:30 | 2014-07-16 10:30 | GOODMAN - GPG13240701AB | 105 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 3A90CA3FF5BB454BA6F936767A9F5283 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ripon | CA | 95366-2778 |  | 2014-10-14 | 2014-10-14 15:20 | 2014-10-15 06:48 | PAYNE - PA12NA030 | 96 | 15.1 | Yes | Yes | 19.8 | 21 | -1.2 | 232738716A3E4AD789F1EE4F2E33559F |  | R22 | Non-TXV |  | 15.73% | 0.84271 | 30.23% | [5 empty] | Non-TXV | 15.73%
Stockton | CA | 95207-9217 |  | 2014-06-02 | 2014-06-02 08:37 | 2014-06-02 08:37 | OTHER - UNK | 54 | 0 | Yes | Yes | 21.1 | 19.9 | 1.2 | 2ACA6674F0C34DD9B4155C62DD37F4DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-4059 |  | 2014-07-15 | 2014-07-15 12:50 | 2014-07-15 13:15 | UNITARY PRODUCTS GROUP - H2RD030S06B | 93 | 2.8 | Yes | Yes | 18.6 | 21 | -2.4 | B3F1BD5200BD4A70B0A36493422601EE |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Madera | CA | 93637-4505 |  | 2014-06-12 | 2014-06-12 14:14 | 2014-06-12 14:30 | BDP - 589ANW036060ADBF | 84 | 12.8 | Yes | Yes | 21.4 | 18.8 | 2.6 | 8F316CEBBAE746C8968BD0E0AFD0D201 |  | R22 | Non-TXV |  | 15.24% | 0.84762 | 29.28% | [5 empty] | Non-TXV | 15.24%
Dinuba | CA | 93618-4059 |  | 2014-07-15 | 2014-07-15 14:39 | 2014-07-15 14:59 | UNITARY PRODUCTS GROUP - H2RD030S06B | 93 | 3.4 | Yes | Yes | 21.3 | 20.8 | 0.5 | E585068B839F493DBBC0C812BD8E399F |  | R22 | Non-TXV |  | 3.656% | 0.96344 | 7.026% | [5 empty] | Non-TXV | 3.656%
Merced | CA | 95340-2415 |  | 2014-08-15 | 2014-08-15 13:18 | 2014-08-15 13:20 | RHEEM - RRGE-0742JKR | 100 | 3.9 | Yes | Yes | 18.2 | 20.7 | -2.5 | B55D115DDDCB4C0787BF0AFF2C2F870F |  | R22 | Non-TXV |  | 3.9% | 0.961 | 7.495% | [5 empty] | Non-TXV | 3.9%
Mendota | CA | 93640-0000 |  | 2014-08-06 | 2014-08-06 08:08 | 2014-08-06 08:24 | AMERICAN STANDARD - A47B3036B1000BA | 126 | 3.7 | Yes | Yes | 17.7 | 19.5 | -1.8 | 7B572708DC3C47B6BB780816CEF8E62D |  | R410A | Non-TXV |  | 2.937% | 0.97063 | 5.643% | [5 empty] | Non-TXV | 2.937%
Chico | CA | 95926-3066 |  | 2014-05-29 | 2014-05-29 09:53 | 2014-05-29 10:16 | AMERICAN STANDARD - 4A7A5042A1000BA | 112 | 3.9 | Yes | Yes | 19 | 20.1 | -1.1 | 4BF60F67A9F747FEA8B77BAA68F9D98F |  | R410A | Non-TXV |  | 3.482% | 0.96518 | 6.692% | [5 empty] | Non-TXV | 3.482%
Magalia | CA | 95954-9385 |  | 2014-06-04 | 2014-06-04 08:54 | 2014-06-04 21:15 | DAY & NIGHT - 591ANX0036000AAAA | 52 | 7.7 | Yes | Yes | 17 | 18.7 | -1.7 | 5EF640A2BFDE4335B13A45F7F9AC02E5 |  | R22 | Non-TXV |  | 14.81% | 0.85192 | 28.46% | [5 empty] | Non-TXV | 14.81%
Magalia | CA | 95954-9385 |  | 2014-06-04 | 2014-06-04 08:00 | 2014-06-04 09:15 | DAY & NIGHT - 591AX018-A | 48 | 2.2 | Yes | Yes | 16.1 | 18.7 | -2.6 | 878A99EDFCB549E299325DFE80CBEF42 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Stockton | CA | 95207-7848 |  | 2014-06-05 | 2014-06-05 13:09 | 2014-06-05 13:09 | TRANE - YCC024F1LOBF | 85 | 0 | Yes | Yes | 20 | 20.8 | -0.8 | EE65DBED62144994B4DC5FFCF99C8D73 |  | R22 | TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-7134 |  | 2014-06-25 | 2014-06-25 10:03 | 2014-06-25 10:19 | OTHER - 561AJ036A | 80 | 2.4 | Yes | Yes | 24 | 20.3 | 3.7 | 5555CDDB3A1F4451983DDAEFF31106D9 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Mendota | CA | 93640-4010 |  | 2014-08-06 | 2014-08-06 09:03 | 2014-08-06 09:24 | BRYANT - 113RNA036-B | 80 | 2.4 | Yes | Yes | 20.7 | 18.3 | 2.5 | 2D013803686C498D98B00E78F0074ED1 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Granite Bay | CA | 95746-6243 |  | 2014-08-28 | 2014-08-28 13:33 | 2014-08-28 13:54 | TRANE - 2TTX4024B1000AA | 105 | 4.1 | Yes | Yes | 20.5 | 19.3 | 1.2 | D30C263BC7CB47FE88A937B4119851AE |  | R22 | TXV |  | 3.905% | 0.96095 | 7.504% | [5 empty] | TXV | 3.905%
Ione | CA | 95640-9615 |  | 2014-08-27 | 2014-08-27 12:58 | 2014-08-27 13:19 | NORDYNE - UNK | 64 | -4.5 | Yes | Yes | 24.1 | 22.3 | 1.8 | 7F63CDF9CA2A47C993D3C86927AA4E56 |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Clovis | CA | 93612-0431 |  | 2014-06-05 | 2014-06-05 09:50 | 2014-06-05 10:08 | RHEEM - RRMAA036JK08E | 99 | 12.9 | Yes | Yes | 21.8 | 18.8 | 3 | 50D8D7C5899C445392576E2026EC78E3 |  | R22 | Non-TXV |  | 13.03% | 0.8697 | 25.04% | [5 empty] | Non-TXV | 13.03%
Fresno | CA | 93722-6828 |  | 2014-05-28 | 2014-05-28 13:42 | 2014-05-28 14:04 | CARRIER - 48NLT036300 | 96 | 14.2 | Yes | Yes | 25.6 | 20.9 | 4.7 | 363C4C452BA145BA8AB96CB522735159 |  | R22 | Non-TXV |  | 14.79% | 0.85208 | 28.43% | [5 empty] | Non-TXV | 14.79%
Tracy | CA | 95377-1161 |  | 2014-06-02 | 2014-06-02 12:24 | 2014-06-02 12:40 | NORDYNE - JS3BC-036KA | 85 | 10 | Yes | Yes | 20.5 | 21.5 | -1 | 38D598F87E6B45E096F42A8203600F3E |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Stockton | CA | 95209-1783 |  | 2014-05-31 | 2014-05-31 12:22 | 2014-05-31 12:39 | YORK - H1RC030S06D | 76 | -4.5 | Yes | Yes | 22.1 | 19.1 | 3 | 601CF67BA7CB47759D42BC6BBC71CB1E |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Stockton | CA | 95212-3835 |  | 2014-06-06 | 2014-06-06 13:34 | 2014-06-06 13:53 | CARRIER - 38CKC048320 | 98 | -9.2 | Yes | Yes | 28 | 23.1 | 4.9 | 961D18FD960F465A9BF66284FC8763B5 |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Paradise | CA | 95969-4428 |  | 2014-06-04 | 2014-06-04 15:47 | 2014-06-04 16:25 | AMERICAN STANDARD - YC2036F1M0BC | 112 | 3.8 | Yes | Yes | 19.8 | 21.8 | -2 | 8185DA44ED3341B483308119E872DD15 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Chico | CA | 95926-1445 |  | 2014-05-29 | 2014-05-29 12:35 | 2014-05-29 13:04 | LENNOX - HS25-411-1P | 129 | 3.8 | Yes | Yes | 25.5 | 21.9 | 3.6 | 3EC7B650CBE040DC8467137F940E26DF |  | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.661% | [5 empty] | Non-TXV | 2.946%
Williams | CA | 95987-0000 |  | 2014-09-22 | 2014-09-22 10:08 | 2014-09-22 10:31 | YORK - D6NZ036N5606NXA | 64 | 2.3 | Yes | Yes | 19 | 17.7 | 1.3 | A304607F95A84B60BD7D5F81052A11A4 |  | R410A | TXV |  | 3.594% | 0.96406 | 6.906% | [5 empty] | TXV | 3.594%
Merced | CA | 95340-1341 |  | 2014-08-29 | 2014-08-29 10:47 | 2014-08-29 10:58 | NORDYNE - JS3BA018KA | 63 | 8.9 | Yes | Yes | 20.5 | 20.4 | 0.1 | EEA0D159898C4DB7916C5293662D66A6 |  | R22 | Non-TXV |  | 14.13% | 0.85873 | 27.15% | [5 empty] | Non-TXV | 14.13%
Stockton | CA | 95207-7854 |  | 2014-06-06 | 2014-06-06 12:34 | 2014-06-06 12:57 | TRANE - YCC030F1M0BG | 69 | 2.3 | Yes | Yes | 21.2 | 19.8 | 1.4 | DD150FB2C32F49B8BC9A1C66E4C48F5D |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95210-3319 |  | 2014-05-27 | 2014-05-27 11:29 | 2014-05-27 11:51 | GOODMAN - G8C130481BA | 102 | 10.6 | Yes | Yes | 22.6 | 20.6 | 2 | 9F2526EB1D914F92BF51E0DE6B6A79C6 |  | R22 | Non-TXV |  | 10.39% | 0.89608 | 19.97% | [5 empty] | Non-TXV | 10.39%
Oroville | CA | 95966-9552 |  | 2014-06-10 | 2014-06-10 10:55 | 2014-06-10 11:11 | TRANE - YCX048G1H0AA | 91 | 5.2 | Yes | Yes | 23.7 | 21 | 2.7 | AF71A62BA4344A56A7BA0CBB82BF10EE |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Fresno | CA | 93702-2517 |  | 2014-06-07 | 2014-06-07 16:20 | 2014-06-07 16:37 | ICP - NAC042AKC3 | 112 | 3.6 | Yes | Yes | 20.9 | 20.8 | 0.1 | 960863C4CD284BD6A831EBA781C57D2C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Auburn | CA | 95602-9381 |  | 2014-06-28 | 2014-06-28 08:55 | 2014-06-28 09:25 | TRANE - BYC024H1LNAA | 51 | 7 | Yes | Yes | 20 | 19.3 | 0.7 | 888E06F382AF49CC8E2CBB4A2FC6C1E4 |  | R22 | Non-TXV |  | 13.73% | 0.86275 | 26.38% | [5 empty] | Non-TXV | 13.73%
Madera | CA | 93636-8623 |  | 2014-06-09 | 2014-06-09 08:58 | 2014-06-09 09:15 | BDP - UNK | 100 | 19.8 | Yes | Yes | 18 | 17.9 | 0.1 | 925B1736D64B4FD8861238613E138CE3 |  | R22 | Non-TXV |  | 19.8% | 0.802 | 38.05% | [5 empty] | Non-TXV | 19.8%
Fresno | CA | 93705-2436 |  | 2014-05-27 | 2014-05-27 10:15 | 2014-05-27 10:17 | BDP - 585HJO42060 | 80 | 3.5 | Yes | Yes | 26 | 23.5 | 2.5 | 5CB84DBC2F764C7A9E8A2D54FC688DDA |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Williams | CA | 95987-0000 |  | 2014-09-18 | 2014-09-18 17:47 | 2014-09-18 17:47 | TRANE - YCC024F1LOBA | 64 | 0 | Yes | Yes | 24.1 | 20.6 | 3.5 | 58911CA05FD24F0291D36A88D6B2631D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lockeford | CA | 95237-9760 |  | 2014-08-19 | 2014-08-19 12:55 | 2014-08-19 13:24 | BRYANT - 113RNA042-A | 127 | 16.4 | Yes | Yes | 22.3 | 18.7 | 3.7 | 08A62C511B0545F0BCE6A42694669453 |  | R22 | Non-TXV |  | 12.91% | 0.87087 | 24.82% | [5 empty] | Non-TXV | 12.91%
Madera | CA | 93636-7600 |  | 2014-05-30 | 2014-05-30 09:20 | 2014-05-30 09:36 | RHEEM - RRMAA042JK08X | 114 | 10.7 | Yes | Yes | 26.9 | 21.5 | 5.4 | 2CB80891B1844780B5CCC268BB50FF68 |  | R22 | Non-TXV |  | 9.386% | 0.90614 | 18.04% | [5 empty] | Non-TXV | 9.386%
Auburn | CA | 95603-4405 |  | 2014-06-02 | 2014-06-02 10:35 | 2014-06-02 10:57 | RUUD - 13AJM36A01 | 96 | 3.6 | Yes | Yes | 22 | 20.6 | 1.4 | 306F2E8E102041D4A9F82F759A7E3D6A |  | R410A | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Fresno | CA | 93726-6123 |  | 2014-08-06 | 2014-08-06 10:39 | 2014-08-06 10:53 | DAY & NIGHT - UNK | 75 | 2.4 | Yes | Yes | 18 | 18.8 | -0.8 | B6A47DA93A7F498BB250B20CC862D8D0 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Paradise | CA | 95969-4724 |  | 2014-05-23 | 2014-05-23 10:08 | 2014-05-23 10:30 | CARRIER - 48GS-02406301 | 53 | 3.9 | Yes | Yes | 19.4 | 21.2 | -1.8 | 761FBC48E12C4526A7F4DDC2A1593DC3 |  | R22 | Non-TXV |  | 7.358% | 0.92642 | 14.14% | [5 empty] | Non-TXV | 7.358%
Oroville | CA | 95966-3643 |  | 2014-05-27 | 2014-05-27 09:49 | 2014-05-27 10:08 | OTHER - CA5536VKD2 | 82 | 2.6 | Yes | Yes | 23.5 | 20.2 | 3.3 | 3BEEC0A3D6F74E2B8FA5D5DCD7AEA0B3 |  | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Stockton | CA | 95203-1413 |  | 2014-06-25 | 2014-06-25 08:44 | 2014-06-25 09:01 | COPELAND - V8X130301AC | 69 | 4.8 | Yes | Yes | 19.8 | 18.2 | 1.6 | 0336989B4EF548DDACE580903D6290C1 |  | R410A | Non-TXV |  | 6.957% | 0.93043 | 13.37% | [5 empty] | Non-TXV | 6.957%
Fresno | CA | 93722-5518 |  | 2014-05-27 | 2014-05-27 12:49 | 2014-05-27 13:06 | YORK - D1NH036N05606C | 108 | 20.3 | Yes | Yes | 24.4 | 22.1 | 2.3 | 435BAF8734704CDBBDDC2F9AB90A222A |  | R22 | Non-TXV |  | 18.8% | 0.81204 | 36.12% | [5 empty] | Non-TXV | 18.8%
Chico | CA | 95973-7629 |  | 2014-05-27 | 2014-05-27 12:11 | 2014-05-27 12:29 | INTERTHERM - S3QC-036K | 75 | 3.6 | Yes | Yes | 18.8 | 20.4 | -1.6 | A8FE2740938E4A5B8B5F7865A2744776 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Merced | CA | 95340-3279 |  | 2014-05-29 | 2014-05-29 12:32 | 2014-05-29 12:33 | RHEEM - HC-100-46-21C | 72 | 2.6 | Yes | Yes | 30.2 | 24.2 | 6 | 0CBA504F3E6F45CFA44AF36828A5C3CF |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Stockton | CA | 95210-4416 |  | 2014-06-07 | 2014-06-07 09:24 | 2014-06-07 09:41 | YORK - H2RD036S06B | 96 | -5.6 | Yes | Yes | 25.4 | 19.4 | 6 | 23C66842EF36414985C2B6B1001BB09D |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Paradise | CA | 95969-3161 |  | 2014-06-04 | 2014-06-04 16:50 | 2014-06-04 17:24 | LENNOX - 12GC5030-75-3PA | 60 | 6.6 | Yes | Yes | 23.8 | 22.1 | 1.7 | 9E91BA0B74D34259BB24CA4C192121E4 |  | R22 | Non-TXV |  | 11% | 0.89 | 21.14% | [5 empty] | Non-TXV | 11%
Yuba City | CA | 95993-5613 |  | 2014-05-28 | 2014-05-28 13:18 | 2014-05-28 13:47 | RHEEM - RACA-048ABO | 47 | 4.9 | Yes | Yes | 21 | 23.7 | -2.7 | 1E443D8A9E424281B41B5CA7B397E9E6 |  | R22 | Non-TXV |  | 10.43% | 0.89574 | 20.04% | [5 empty] | Non-TXV | 10.43%
Live Oak | CA | 95953-9419 |  | 2014-07-02 | 2014-07-02 08:28 | 2014-07-02 08:46 | DAY & NIGHT - NXA648GKA100 | 208 | 7.6 | Yes | Yes | 19 | 20.4 | -1.4 | 2D18A3AE852243D99EE55E3C8A6B566A |  | R410A | TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | TXV | 3.654%
Sanger | CA | 93657-3614 |  | 2014-06-19 | 2014-06-19 16:15 | 2014-06-19 16:49 | GOODMAN - GSC130361FA | 83 | 3 | Yes | Yes | 22 | 22.5 | -0.5 | E259848C499B46C8A0C16AFCCE1DF7D6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.614% | 0.96386 | 6.946% | [5 empty] | Non-TXV | 3.614%
Williams | CA | 95987-0000 |  | 2014-09-19 | 2014-09-19 13:49 | 2014-09-19 14:18 | AMERICAN STANDARD - D6NZ030N05606NX | 64 | 3.6 | Yes | Yes | 18.1 | 21 | -2.9 | 9D3009A22C894B538A5CD2AC7A4E9785 |  | R410A | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Chico | CA | 95926-4285 |  | 2014-06-12 | 2014-06-12 12:37 | 2014-06-12 13:10 | PAYNE - 585CJ030 00JO | 60 | 11.3 | Yes | Yes | 20.3 | 18.3 | 2 | 944706A344944BABA59C181CF048D951 |  | R22 | Non-TXV |  | 18.83% | 0.81167 | 36.19% | [5 empty] | Non-TXV | 18.83%
Stockton | CA | 95207-5114 |  | 2014-05-31 | 2014-05-31 11:33 | 2014-05-31 12:03 | ICP - R2H336GKR1 | 101 | 8.7 | Yes | Yes | 20.1 | 19.1 | 1 | 7DF78DCF300B415AB996CBD452037651 |  | R22 | Non-TXV |  | 8.614% | 0.91386 | 16.55% | [5 empty] | Non-TXV | 8.614%
Fresno | CA | 93726-6121 |  | 2014-08-06 | 2014-08-06 14:05 | 2014-08-06 14:21 | OTHER - UNK | 75 | 2.2 | Yes | Yes | 25 | 20 | 5 | 3E61EDB3A7664C54A9DCE03B80B2EE57 |  | R22 | Non-TXV |  | 2.933% | 0.97067 | 5.637% | [5 empty] | Non-TXV | 2.933%
Colusa | CA | 95932-3376 |  | 2014-07-03 | 2014-07-03 12:48 | 2014-07-03 13:15 | RUUD - NA | 60 | 8.7 | Yes | Yes | 20.1 | 19 | 1.1 | FB34D1F5E6ED40F79040E705B30BDCCD |  | R22 | Non-TXV |  | 14.5% | 0.855 | 27.87% | [5 empty] | Non-TXV | 14.5%
Clovis | CA | 93611-4102 |  | 2014-06-10 | 2014-06-10 12:24 | 2014-06-10 12:40 | AMERICAN STANDARD - YCY060G1MOAC | 151 | 34.7 | Yes | Yes | 27 | 21.4 | 5.6 | 99410716836340169BDC89EF448D6877 |  | R22 | Non-TXV |  | 22.98% | 0.7702 | 44.16% | [5 empty] | Non-TXV | 22.98%
Fresno | CA | 93726-6123 |  | 2014-06-24 | 2014-06-24 14:08 | 2014-06-24 14:10 | DAY & NIGHT - 2460YAC108T | 54 | 10.7 | Yes | Yes | 19.2 | 20.6 | -1.4 | D2266D78DA3B47659FB5E7D1FDF3964B |  | R22 | Non-TXV |  | 19.81% | 0.80185 | 38.08% | [5 empty] | Non-TXV | 19.81%
Jackson | CA | 95642-9450 |  | 2014-07-07 | 2014-07-07 13:15 | 2014-07-07 13:35 | COLEMAN - UK | 99 | 2.9 | Yes | Yes | 27 | 22 | 5 | 1B652FAD0248437DBF85F8644CB4F823 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Reedley | CA | 93654-9771 |  | 2014-08-28 | 2014-08-28 18:36 | 2014-08-28 18:56 | RHEEM - RRNA-A036JK08X | 114 | 9.5 | Yes | Yes | 21.5 | 20.2 | 1.3 | 4A674F389BD74ECBA9E3066B793F2DD3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Jackson | CA | 95642-9596 |  | 2014-09-16 | 2014-09-16 09:59 | 2014-09-16 10:30 | UNITARY PRODUCTS GROUP - BRCQ0301BE | 121 | 5.8 | Yes | Yes | 20.8 | 18 | 2.8 | E9AE80DDDB884411AFCBEF683D408FB3 |  | R22 | Non-TXV |  | 4.793% | 0.95207 | 9.212% | [5 empty] | Non-TXV | 4.793%
Jackson | CA | 95642-9574 |  | 2014-08-27 | 2014-08-27 12:42 | 2014-08-27 13:05 | AIRE-FLO - AFAIR10B36-B | 96 | 7.4 | Yes | Yes | 19.8 | 20.7 | -0.9 | 31E0FC87640A4E2EBED47219F4B83D36 |  | R22 | Non-TXV |  | 7.708% | 0.92292 | 14.81% | [5 empty] | Non-TXV | 7.708%
Stockton | CA | 95206-5660 |  | 2014-06-23 | 2014-06-23 09:12 | 2014-06-23 09:32 | AIRE-FLO - 13ACD-036-230-16 | 92 | -8.7 | Yes | Yes | 22.7 | 18.8 | 3.9 | 06DFE789BC5C476389B174963479D7A2 |  | R22 | Non-TXV |  | -9.457% | 1.0946 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.457%
Madera | CA | 93638-1716 |  | 2014-06-09 | 2014-06-09 13:04 | 2014-06-09 13:26 | RHEEM - UNK | 56 | 12.5 | Yes | Yes | 27 | 22.1 | 4.9 | 19D3E893A06C451395122413DCF57B56 |  | R22 | Non-TXV |  | 22.32% | 0.77679 | 42.9% | [5 empty] | Non-TXV | 22.32%
Fresno | CA | 93727-3060 |  | 2014-08-07 | 2014-08-07 16:41 | 2014-08-07 17:06 | ICP - NA348AKB200 | 111 | 4.2 | Yes | Yes | 19.8 | 20.9 | -1.1 | DA6A070EB54B44C1ABACA384BA471360 |  | R410A | TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | TXV | 3.784%
Fresno | CA | 93720-1867 |  | 2014-06-19 | 2014-06-19 09:32 | 2014-06-19 09:48 | BRYANT - 563CN048-F | 164 | 23 | Yes | Yes | 15.5 | 21 | -5.5 | 28BF7D18F0EB49169513A031EC4268D8 | Add refrigerant: 18.9 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 14.02% | 0.85976 | 26.95% | [5 empty] | Non-TXV | 14.02%
Fresno | CA | 93720-1867 |  | 2014-06-19 | 2014-06-19 09:50 | 2014-06-19 10:07 | BRYANT - 563CN024-B | 82 | 5.9 | Yes | Yes | 24.6 | 20.4 | 4.2 | 84A72C795C2946E38ABC3B863E11C58D |  | R22 | Non-TXV |  | 7.195% | 0.92805 | 13.83% | [5 empty] | Non-TXV | 7.195%
Firebaugh | CA | 93622-2803 |  | 2014-08-06 | 2014-08-06 12:46 | 2014-08-06 13:03 | BDP - 588ANW030040ABAD | 53 | 1.6 | Yes | Yes | 17.4 | 15 | 2.4 | 8A7A053CC58C446690EBF70A5843E664 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Jackson | CA | 95642-9448 |  | 2014-08-27 | 2014-08-27 12:20 | 2014-08-27 12:39 | COLEMAN - 7836-901 | 68 | 4.5 | Yes | Yes | 21.5 | 19.3 | 2.2 | 99AA2F7A6134413DA596952D9BA96A95 |  | R22 | Non-TXV |  | 6.618% | 0.93382 | 12.72% | [5 empty] | Non-TXV | 6.618%
Fresno | CA | 93727-3753 |  | 2014-08-22 | 2014-08-22 17:03 | 2014-08-22 17:46 | ICP - PGME36G0907 | 100 | 9.6 | Yes | Yes | 26.5 | 21 | 5.5 | 2B343670B57B4C699F957130221681C0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.6% | 0.904 | 18.45% | [5 empty] | Non-TXV | 9.6%
Fresno | CA | 93727-3031 |  | 2014-06-23 | 2014-06-23 08:46 | 2014-06-23 09:03 | BRYANT - 113ANA036E | 83 | 6.8 | Yes | Yes | 22.3 | 18.2 | 4.1 | 1E90ED2390A14645A7B7D873FB0AFE11 |  | R410A | TXV |  | 8.193% | 0.91807 | 15.74% | [5 empty] | TXV | 8.193%
Fresno | CA | 93727-3366 |  | 2014-06-10 | 2014-06-10 15:04 | 2014-06-10 15:26 | GOODMAN - GSC130481BB | 102 | 13.1 | Yes | Yes | 22 | 21 | 1 | E2F3B868CE3D4760B07BFB25757F3018 |  | R22 | Non-TXV |  | 12.84% | 0.87157 | 24.68% | [5 empty] | Non-TXV | 12.84%
Paradise | CA | 95969-2628 |  | 2014-06-11 | 2014-06-11 11:49 | 2014-06-11 12:12 | BRYANT - 113ANA036-E | 85 | 3 | Yes | Yes | 26.5 | 20.5 | 6 | 6377040FDB84409FA69FF9696B0C0EBC |  | R410A | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Parlier | CA | 93648-2116 |  | 2014-06-16 | 2014-06-16 15:38 | 2014-06-16 15:55 | UNITARY PRODUCTS GROUP - H2RD36S06B | 96 | 7.3 | Yes | Yes | 20.5 | 20.6 | 0 | E91F6199BA2B4F5F98EFA4E2BC6D8A4F |  | R22 | Non-TXV |  | 7.604% | 0.92396 | 14.61% | [5 empty] | Non-TXV | 7.604%
Merced | CA | 95341-5231 |  | 2014-07-02 | 2014-07-02 16:12 | 2014-07-02 16:15 | YORK - D1NY036N05606A | 120 | 3.6 | Yes | Yes | 17.3 | 19.7 | -2.4 | 86AD9AE27B294C28B4CA9DEF4F7F5A0F |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Livingston | CA | 95334-9542 |  | 2014-06-20 | 2014-06-20 12:35 | 2014-06-20 12:54 | GOODMAN - CK60-1C | 85 | 20.2 | Yes | Yes | 25.5 | 21 | 4.5 | 18EFB3F4AD0041D2B1E78728AD60E258 |  | R22 | Non-TXV |  | 23.76% | 0.76235 | 45.67% | [5 empty] | Non-TXV | 23.76%
Chico | CA | 95973-8729 |  | 2014-06-20 | 2014-06-20 14:10 | 2014-06-20 14:28 | BRYANT - 583BN024060NC | 80 | 2.9 | Yes | Yes | 24 | 20.4 | 3.6 | 60ED239884A74249A573521BF312917E |  | R410A | TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | TXV | 3.625%
Atwater | CA | 95301-2293 |  | 2014-07-01 | 2014-07-01 12:08 | 2014-07-01 12:28 | GOODMAN - GPG13360701AC | 85 | 7.2 | Yes | Yes | 20.7 | 21 | -0.3 | 8512B48FDA56437EBEEF53438BE050B9 |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Sanger | CA | 93657-3235 |  | 2014-06-17 | 2014-06-17 15:19 | 2014-06-17 15:43 | DAY & NIGHT - N/A | 90 | 6.8 | Yes | Yes | 20.8 | 20.8 | 0 | 21970C76D4C74E0C88FE862FEF5B4D3A |  | R22 | Non-TXV |  | 7.556% | 0.92444 | 14.52% | [5 empty] | Non-TXV | 7.556%
Oroville | CA | 95966-7151 |  | 2014-06-12 | 2014-06-12 10:14 | 2014-06-12 10:30 | PAYNE - 585HJ024040BAB12086C86941 | 61 | 4.4 | Yes | Yes | 19.7 | 20.1 | -0.4 | 48F462F3A34941FA96C6952DFD2DC45D |  | R22 | Non-TXV |  | 7.213% | 0.92787 | 13.86% | [5 empty] | Non-TXV | 7.213%
Grass Valley | CA | 95945-8477 |  | 2014-06-25 | 2014-06-25 08:11 | 2014-06-25 08:37 | PAYNE - PY1PJB048090AAAA | 81 | 3 | Yes | Yes | 25 | 20.1 | 4.9 | 38915474636A41208AF555F885207E4E |  | R22 | TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | TXV | 3.704%
Tracy | CA | 95376-2932 |  | 2014-06-09 | 2014-06-09 09:03 | 2014-06-09 09:25 | FRIGIDAIRE - UNK | 85 | 6.6 | Yes | Yes | 23.5 | 20.2 | 3.3 | 1BE17515230941499640CC2F3C4DC505 |  | R22 | Non-TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | Non-TXV | 7.765%
Stockton | CA | 95203-1501 |  | 2014-06-14 | 2014-06-14 14:43 | 2014-06-14 14:59 | GE - BGTA488R1D01 | 115 | 3.6 | Yes | Yes | 23.2 | 20.9 | 2.3 | DA366C8DF7054D95B61BDBEE9DCA0A74 |  | R22 | Non-TXV |  | 3.13% | 0.9687 | 6.016% | [5 empty] | Non-TXV | 3.13%
Red Bluff | CA | 96080-3528 |  | 2014-06-21 | 2014-06-21 11:26 | 2014-06-21 11:48 | OTHER - NA | 55 | 3.3 | Yes | Yes | 20 | 20.7 | -0.7 | B81520EE13F84BD3905E1B3E8AAE51B3 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Parlier | CA | 93648-9632 |  | 2014-06-18 | 2014-06-18 16:05 | 2014-06-18 16:35 | RUUD - N/A | 60 | 5.8 | Yes | Yes | 21.2 | 20.2 | 1 | EEA4DDE91CEF4E879CEB3579C60B3798 |  | R22 | Non-TXV |  | 9.667% | 0.90333 | 18.58% | [5 empty] | Non-TXV | 9.667%
Kerman | CA | 93630-1555 |  | 2014-06-18 | 2014-06-18 11:10 | 2014-06-18 11:12 | YORK - DAYPF042N080A | 150 | 14 | Yes | Yes | 24.2 | 19.3 | 4.9 | 6A4847CE2C97411BA59AC6F0F40AF478 |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Fresno | CA | 93727-3129 |  | 2014-06-10 | 2014-06-10 13:28 | 2014-06-10 13:52 | CARRIER - 38TR042300 | 73 | 3.9 | Yes | Yes | 20.9 | 20.9 | 0 | 482EC9B10DAC413EB7D33BA3E473E1E3 |  | R22 | Non-TXV |  | 5.342% | 0.94658 | 10.27% | [5 empty] | Non-TXV | 5.342%
Los Banos | CA | 93635-9229 |  | 2014-06-11 | 2014-06-11 08:13 | 2014-06-11 08:15 | GIBSON - JS5BD-048K | 124 | 3.8 | Yes | Yes | 20.4 | 22.8 | -2.4 | E4A95E9ED43E4A319D96A5DBA381DC60 |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Selma | CA | 93662-4423 |  | 2014-07-26 | 2014-07-26 11:11 | 2014-07-26 11:33 | LENNOX - N/A | 90 | 4.8 | Yes | Yes | 22 | 21.8 | 0.3 | 350065F1121A4112A5287C72FD020E45 |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Parlier | CA | 93648-9625 |  | 2014-06-16 | 2014-06-16 16:35 | 2014-06-16 17:59 | RUUD - N/A | 60 | 1.8 | Yes | Yes | 21.9 | 22.1 | -0.2 | 8137BF7786064AF09A544D1AE5C50C6A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Madera | CA | 93637-4610 |  | 2014-06-19 | 2014-06-19 13:02 | 2014-06-19 13:12 | ICP - PGC030K060A | 52 | 9.7 | Yes | Yes | 26.1 | 21.5 | 4.6 | D877A4FA0A9E463D9A3030C702A1B5F6 |  | R22 | Non-TXV |  | 18.65% | 0.81346 | 35.85% | [5 empty] | Non-TXV | 18.65%
Parlier | CA | 93648-9632 |  | 2014-06-18 | 2014-06-18 17:02 | 2014-06-18 17:24 | RUUD - N/A | 60 | 1.8 | Yes | Yes | 21.3 | 22.6 | -1.3 | 16EEC013E7F14C328E1D27FDCF1160DF |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95209-2400 |  | 2014-06-11 | 2014-06-11 14:59 | 2014-06-11 15:15 | LENNOX - HS25-461-1P | 133 | -7.8 | Yes | Yes | 25.6 | 19.7 | 5.9 | CAD19CE5690E43C082456C4D02FBF0E4 |  | R22 | Non-TXV |  | -5.865% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.865%
Paradise | CA | 95969-2868 |  | 2014-07-23 | 2014-07-23 15:34 | 2014-07-23 16:25 | CARRIER - 4801045B | 64 | 5 | Yes | Yes | 21 | 19.7 | 1.3 | 8C63E01406F648CB85292BF1203FF477 |  | R22 | Non-TXV |  | 7.812% | 0.92188 | 15.01% | [5 empty] | Non-TXV | 7.812%
Placerville | CA | 95667-8739 |  | 2014-06-10 | 2014-06-10 15:14 | 2014-06-10 15:35 | BRYANT - 551AN060-H | 180 | 6.6 | Yes | Yes | 21 | 19.5 | 1.5 | 0E792BC0098A430890C8290946A4608E |  | R410A | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Placerville | CA | 95667-8739 |  | 2014-06-10 | 2014-06-10 15:52 | 2014-06-10 16:12 | BRYANT - UNK | 90 | 8 | Yes | Yes | 20 | 22.1 | -2.1 | 83FB2CAB68A54227BD6EA98780B88755 |  | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Los Banos | CA | 93635-3097 |  | 2014-06-10 | 2014-06-10 11:31 | 2014-06-10 11:35 | GMC - JS3BC-030KA | 68 | 2.9 | Yes | Yes | 16.6 | 19 | -2.4 | 8D91C888525D4818B35E2369834FDDCB |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Corning | CA | 96021-0000 |  | 2014-06-16 | 2014-06-16 10:50 | 2014-06-09 11:19 | YORK - H4DB036506A | 73 | 9.1 | Yes | Yes | 21.5 | 20.4 | 1.1 | 238FA82B944A47CF80B51FB4BB7372EE |  | R22 | Non-TXV |  | 12.47% | 0.87534 | 23.96% | [5 empty] | Non-TXV | 12.47%
Fresno | CA | 93702-3932 |  | 2014-06-18 | 2014-06-18 14:09 | 2014-06-18 14:11 | YORK - D2NP036N05606A | 108 | 3.6 | Yes | Yes | 24.8 | 22 | 2.8 | 37D8280635F34C90A43C5230E19A3F0A |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Parlier | CA | 93648-9627 |  | 2014-08-26 | 2014-08-26 16:56 | 2014-08-26 17:19 | RHEEM - N/A | 60 | 5.3 | Yes | Yes | 17.7 | 20.4 | -2.7 | 8035237C95A5493EBC46DAF91CFFE852 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.833% | 0.91167 | 16.98% | [5 empty] | Non-TXV | 8.833%
Clovis | CA | 93611-1415 |  | 2014-06-10 | 2014-06-10 10:39 | 2014-06-10 10:57 | OTHER - 585HJW030060ABAF | 102 | 16 | Yes | Yes | 26.5 | 21.5 | 5 | 9B92E8275E054DC39488903122986323 |  | R22 | Non-TXV |  | 15.69% | 0.84314 | 30.15% | [5 empty] | Non-TXV | 15.69%
Chico | CA | 95926-3067 |  | 2014-08-13 | 2014-08-13 16:26 | 2014-08-13 16:42 | DAY & NIGHT - 593ANX03000ABAA | 100 | 3.8 | Yes | Yes | 22.5 | 18 | 4.5 | C9E57A31B8BF47CFB540FDB09C4A5C8C |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Stockton | CA | 95207-4321 |  | 2014-06-09 | 2014-06-09 10:19 | 2014-06-09 10:36 | LENNOX - UNK | 96 | -5.6 | Yes | Yes | 26.1 | 20.3 | 5.8 | 4182921769F54BB48BAB6CC815484BDD |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Los Banos | CA | 93635-3160 |  | 2014-06-11 | 2014-06-11 12:49 | 2014-06-11 12:51 | OTHER - 591ANX030000ABAA | 66 | 2.3 | Yes | Yes | 20.2 | 19.3 | 0.9 | 5C46FBE3878B4863B3412A0606F684D9 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Stockton | CA | 95203-1057 |  | 2014-06-10 | 2014-06-10 15:09 | 2014-06-10 15:36 | OTHER - UNK | 85 | 11.3 | Yes | Yes | 17.2 | 19 | -1.8 | 8CD4D7BBF5BC439C874DC90311EBF477 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.29% | 0.86706 | 25.55% | [5 empty] | Non-TXV | 13.29%
Stockton | CA | 95204-2839 |  | 2014-06-10 | 2014-06-10 10:36 | 2014-06-10 10:59 | CARRIER - 1BNHX030300 | 68 | 4.4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 3A295F61F9234140AACFE714F3FD4C2E |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Clovis | CA | 93612-4808 |  | 2014-06-11 | 2014-06-11 10:59 | 2014-06-11 11:16 | OTHER - GPCM036K060D | 68 | 16.1 | Yes | Yes | 23 | 22 | 1 | 69DAC82790B1473D8D6D70AB72EA81B1 |  | R22 | Non-TXV |  | 23.68% | 0.76324 | 45.5% | [5 empty] | Non-TXV | 23.68%
Merced | CA | 95341-5657 |  | 2014-07-11 | 2014-07-11 13:06 | 2014-07-11 13:08 | OTHER - CPE24-1AB | 93 | 3.2 | Yes | Yes | 20.8 | 20.2 | 0.6 | DF5B271272DB4E119FDD34EA8B99AD6D |  | R22 | Non-TXV |  | 3.441% | 0.96559 | 6.613% | [5 empty] | Non-TXV | 3.441%
Parlier | CA | 93648-9626 |  | 2014-06-17 | 2014-06-17 18:22 | 2014-06-17 18:47 | RUUD - N/A | 60 | 5.6 | Yes | Yes | 19.7 | 20.9 | -1.2 | 58D2BF6791EE48109D9FC03E0D01E35F |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Clovis | CA | 93611-1444 |  | 2014-06-10 | 2014-06-10 11:32 | 2014-06-10 11:48 | CARRIER - 48KLA136300BE | 102 | 17.7 | Yes | Yes | 27.8 | 23 | 4.8 | 0A992D845A7A4372BFFC7A982FB9DDD2 |  | R22 | Non-TXV |  | 17.35% | 0.82647 | 33.35% | [5 empty] | Non-TXV | 17.35%
Corning | CA | 96021-3246 |  | 2014-08-12 | 2014-08-12 14:50 | 2014-08-12 15:15 | RUUD - UAND-036JAZ | 116 | 4.2 | Yes | Yes | 24 | 19.8 | 4.2 | D89F8380D87C4F7886A8C4FE823C6B01 |  | R22 | Non-TXV |  | 3.621% | 0.96379 | 6.958% | [5 empty] | Non-TXV | 3.621%
Fresno | CA | 93703-2629 |  | 2014-08-04 | 2014-08-04 12:57 | 2014-08-04 13:29 | AMERICAN STANDARD - 2A7A2042B1000AA | 86 | 2.5 | Yes | Yes | 23 | 21.5 | 1.5 | 7720AAA99FAE454A93C03B8DFA766FA2 |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Chico | CA | 95926-7112 |  | 2014-06-19 | 2014-06-19 09:08 | 2014-06-19 09:31 | PAYNE - 565J030 | 86 | 2.5 | Yes | Yes | 23 | 21.9 | 1.1 | 6A3277DD65A54C70BB14AD8532791AED |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Corning | CA | 96021-3039 |  | 2014-07-14 | 2014-07-14 10:01 | 2014-07-14 10:25 | YORK - H20H425068 | 128 | 4.9 | Yes | Yes | 15 | 18 | -3 | C45B29F467F44F57B1DCFAF101DF7174 |  | R22 | Non-TXV |  | 3.828% | 0.96172 | 7.357% | [5 empty] | Non-TXV | 3.828%
Coarsegold | CA | 93614-9579 |  | 2014-07-07 | 2014-07-07 13:06 | 2014-07-07 13:20 | OTHER - URGG05E30JKR | 46 | 5.5 | Yes | Yes | 21.5 | 19.3 | 2.2 | 18D23AFCA0474A75A28C1A8A1C8506C8 |  | R22 | Non-TXV |  | 11.96% | 0.88043 | 22.98% | [5 empty] | Non-TXV | 11.96%
Corning | CA | 96021-3415 |  | 2014-06-17 | 2014-06-17 10:26 | 2014-06-17 11:00 | RUUD - 13AJN36A01 | 106 | 4.5 | Yes | Yes | 20 | 21.1 | -1.1 | 98C21D890BD54ABD9BF18331D64E49C7 |  | R410A | Non-TXV |  | 4.245% | 0.95755 | 8.159% | [5 empty] | Non-TXV | 4.245%
Stockton | CA | 95219-2043 |  | 2014-06-13 | 2014-06-13 08:16 | 2014-06-13 08:40 | GOODMAN - CLJ42-1A | 85 | -4.1 | Yes | Yes | 20.5 | 20.3 | 0.2 | 2A71BDA5550C4A80B9E46CB8F15E8134 |  | R22 | Non-TXV |  | -4.824% | 1.0482 | 1.351% |  |  |  |  | Non-TXV |  |  | -4.824%
Stockton | CA | 95204-2839 |  | 2014-06-10 | 2014-06-10 11:39 | 2014-06-10 12:02 | COMFORT AIRE - PGC036K060B | 71 | 4.3 | Yes | Yes | 20.5 | 19.3 | 1.2 | 7D05D290DCC14BEF915A857968DAA3BF |  | R22 | Non-TXV |  | 6.056% | 0.93944 | 11.64% | [5 empty] | Non-TXV | 6.056%
Los Banos | CA | 93635-6395 |  | 2014-06-27 | 2014-06-27 11:21 | 2014-06-27 11:38 | BRYANT - 563CN030-C | 100 | -5.9 | Yes | Yes | 18.9 | 19.3 | -0.4 | 7C253833F7624CEF8A9C3D6EAEAAFCA1 |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Sanger | CA | 93657-2584 |  | 2014-06-17 | 2014-06-17 12:09 | 2014-06-17 12:28 | LENNOX - 10GCS036X-75-3PA | 58 | 2.4 | Yes | Yes | 19.5 | 18.3 | 1.2 | 0DFCAD22F1E74C7DAC558BBBD3227851 |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Livingston | CA | 95334-9694 |  | 2014-06-19 | 2014-06-19 12:41 | 2014-06-19 13:03 | GOODMAN - CKJ36-1AB | 85 | 6.1 | Yes | Yes | 24.1 | 19.9 | 4.2 | 1CA0DEC023314CB798AA3AB7953DC349 |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Clovis | CA | 93611-6959 |  | 2014-06-25 | 2014-06-25 11:59 | 2014-06-25 12:18 | GOODMAN - VSC130481AA | 147 | 4.5 | Yes | Yes | 19.5 | 21.5 | -2 | B1AB9A7FF3574A47AC400BE188208D41 |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Stockton | CA | 95204-4404 |  | 2014-06-12 | 2014-06-12 14:11 | 2014-06-12 14:32 | RHEEM - RRMA-A042JK10X | 114 | 4.1 | Yes | Yes | 24 | 21.1 | 3 | 566F4DD0625A49D09304995ECD92749F |  | R22 | Non-TXV |  | 3.596% | 0.96404 | 6.912% | [5 empty] | Non-TXV | 3.596%
Fresno | CA | 93727-1846 |  | 2014-06-10 | 2014-06-10 11:24 | 2014-06-10 11:49 | GOODMAN - PC036-1A | 63 | 9.3 | Yes | Yes | 24.2 | 19.9 | 4.3 | DC924220FB2A4C2786DCDEC61D869675 |  | R22 | Non-TXV |  | 14.76% | 0.85238 | 28.37% | [5 empty] | Non-TXV | 14.76%
Placerville | CA | 95667-8193 |  | 2014-06-10 | 2014-06-10 18:47 | 2014-06-10 18:47 | RHEEM - RAPL-048JAZ | 152 | 0 | Yes | Yes | 3 | 25.9 | -22.9 | 68BFC92DFD9B4ED3B05C936DD81D2D82 | Actual Subcooling cannot be negative. Please check entries. Evaporator saturation temperature is <25°F. Please check entries. | R410A | TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-4059 |  | 2014-07-15 | 2014-07-15 13:21 | 2014-07-15 14:13 | UNITARY PRODUCTS GROUP - H2RD030S06B | 93 | 4.9 | Yes | Yes | 20.8 | 20.9 | -0.1 | AFBD5B4D20844C9EAFF30B7C63D92F0E |  | R22 | Non-TXV |  | 5.269% | 0.94731 | 10.13% | [5 empty] | Non-TXV | 5.269%
Merced | CA | 95341-8990 |  | 2014-09-15 | 2014-09-15 10:18 | 2014-09-15 10:19 | DAY & NIGHT - 7777UNK | 84 | 4.5 | Yes | Yes | 20.4 | 20.5 | -0.1 | A7D7880BC58D480FBF7EB2D75AA0872E |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Stockton | CA | 95209-1241 |  | 2014-06-12 | 2014-06-12 09:30 | 2014-06-12 09:47 | DAY & NIGHT - 585A024055YACR | 51 | -3.6 | Yes | Yes | 22.6 | 17.6 | 5 | 65BA4055825E4023B4731975926FD18A |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93701-2318 |  | 2014-06-13 | 2014-06-13 11:20 | 2014-06-13 11:22 | GOODMAN - PGB036050-1 REVA | 60 | 2.9 | Yes | Yes | 28.2 | 22.6 | 5.6 | B50AC805145F421C9154B4663E5C9FFF |  | R22 | Non-TXV |  | 4.833% | 0.95167 | 9.289% | [5 empty] | Non-TXV | 4.833%
Kerman | CA | 93630-1373 |  | 2014-06-18 | 2014-06-18 10:15 | 2014-06-18 10:34 | CARRIER - 24ABR330A320 | 82 | 6.7 | Yes | Yes | 21.7 | 18.8 | 2.9 | 02538CAF01D74C189421F63589AD3F0C |  | R22 | Non-TXV |  | 8.171% | 0.91829 | 15.7% | [5 empty] | Non-TXV | 8.171%
Corning | CA | 96021-3246 |  | 2014-07-07 | 2014-07-07 09:18 | 2014-07-07 09:36 | RUUD - VAND-036JAZ | 116 | 3.9 | Yes | Yes | 20.8 | 19.5 | 1.4 | BEDF52336D444F08B5EC0EAD954EC547 |  | R22 | Non-TXV |  | 3.362% | 0.96638 | 6.461% | [5 empty] | Non-TXV | 3.362%
Fresno | CA | 93703-1605 |  | 2014-06-11 | 2014-06-11 13:49 | 2014-06-11 15:08 | INTERTHERM - N/A | 60 | 6.8 | Yes | Yes | 21.2 | 21.8 | -0.6 | C3DA308513CE4774951145E244F471DE |  | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Fresno | CA | 93702-2217 |  | 2014-06-17 | 2014-06-17 12:51 | 2014-06-17 12:52 | BRYANT - 582ANW030060AAAD | 55 | 6.4 | Yes | Yes | 21.3 | 16.8 | 4.5 | 7286B5DA505A439D9FFE5182C4F8D37D |  | R22 | Non-TXV |  | 11.64% | 0.88364 | 22.36% | [5 empty] | Non-TXV | 11.64%
Los Banos | CA | 93635-3626 |  | 2014-06-11 | 2014-06-11 13:43 | 2014-06-11 13:44 | OTHER - GS3BA-024KA | 64 | 2.7 | Yes | Yes | 17.4 | 20.1 | -2.7 | 9446155676AE45B6B174EBC3548493EB |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Chico | CA | 95973-1153 |  | 2014-07-02 | 2014-07-02 08:05 | 2014-07-02 21:15 | TEMPSTAR - NPGAA24B1K1 | 65 | 3.6 | Yes | Yes | 21.5 | 19.6 | 2 | 5634B1E316E24A5DB35724D34DDFFC1D |  | R22 | Non-TXV |  | 5.538% | 0.94462 | 10.64% | [5 empty] | Non-TXV | 5.538%
Livingston | CA | 95334-9691 |  | 2014-06-20 | 2014-06-20 13:48 | 2014-06-20 14:11 | GOODMAN - CKJ36-1A | 85 | 16.6 | Yes | Yes | 25.6 | 20.9 | 4.7 | D85D215A001C4927AE594D0616E42BD0 |  | R22 | Non-TXV |  | 19.53% | 0.80471 | 37.53% | [5 empty] | Non-TXV | 19.53%
Stockton | CA | 95203-1410 |  | 2014-06-07 | 2014-06-07 13:03 | 2014-06-07 13:23 | BRYANT - 583ANW030060AAHD | 68 | 2.5 | Yes | Yes | 19.8 | 19.3 | 0.5 | 86042D2D65F349A5941F073ED53EF7ED |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Grass Valley | CA | 95945-9744 |  | 2014-06-25 | 2014-06-25 12:55 | 2014-06-25 13:11 | CARRIER - 38BRB042300 | 131 | 4.5 | Yes | Yes | 27.5 | 22.6 | 4.9 | 0D878F21DEDC472FA17460AAF95A918A |  | R22 | Non-TXV |  | 3.435% | 0.96565 | 6.602% | [5 empty] | Non-TXV | 3.435%
Madera | CA | 93638-2640 |  | 2014-06-12 | 2014-06-12 13:21 | 2014-06-12 13:38 | CARRIER - 38CK030310 | 66 | 13.3 | Yes | Yes | 23.4 | 21.9 | 1.5 | 1D1DCFC0A9514891B26F7F72BD9B74A6 |  | R22 | Non-TXV |  | 20.15% | 0.79848 | 38.73% | [5 empty] | Non-TXV | 20.15%
Stockton | CA | 95206-3632 |  | 2014-07-02 | 2014-07-02 10:27 | 2014-07-02 10:44 | NORDYNE - JS5BD-030KA | 99 | 13.3 | Yes | Yes | 21.6 | 20.1 | 1.5 | 9FBF9E9FF2544457AD7C2C4A602B1C88 |  | R22 | Non-TXV |  | 13.43% | 0.86566 | 25.82% | [5 empty] | Non-TXV | 13.43%
Corning | CA | 96021-3246 |  | 2014-07-23 | 2014-07-23 12:09 | 2014-07-23 12:25 | RUUD - UAND-036JAZ | 116 | 6.8 | Yes | Yes | 24 | 18.8 | 5.2 | 073FD4B028A54E7A9B613CF060E095FF |  | R22 | Non-TXV |  | 5.862% | 0.94138 | 11.27% | [5 empty] | Non-TXV | 5.862%
Fresno | CA | 93727-0000 |  | 2014-07-17 | 2014-07-17 11:01 | 2014-07-17 11:03 | GOODMAN - PGB030100-1 | 61 | 2 | Yes | Yes | 27 | 21 | 6 | 3FC16B73352F4E2AAC1A77DD01BE71F5 |  | R22 | Non-TXV |  | 3.279% | 0.96721 | 6.301% | [5 empty] | Non-TXV | 3.279%
Fresno | CA | 93727-0000 |  | 2014-07-17 | 2014-07-17 11:04 | 2014-07-17 11:09 | GOODMAN - PGB030100-1 | 61 | 3.5 | Yes | Yes | 16.9 | 19.9 | -3 | 9766BF32052D4B8887B911A3D3BB781F |  | R22 | Non-TXV |  | 5.738% | 0.94262 | 11.03% | [5 empty] | Non-TXV | 5.738%
Fresno | CA | 93726-4921 |  | 2014-06-20 | 2014-06-20 12:27 | 2014-06-20 12:48 | GOODMAN - PGB0360501B | 50 | 11.7 | Yes | Yes | 21.9 | 19.2 | 2.7 | 5CE275222269492DB4FB62B208E6878D |  | R22 | Non-TXV |  | 23.4% | 0.766 | 44.97% | [5 empty] | Non-TXV | 23.4%
Madera | CA | 93637-4657 |  | 2014-06-09 | 2014-06-09 11:18 | 2014-06-09 11:34 | OTHER - UNK | 56 | 13 | Yes | Yes | 21.2 | 20.6 | 0.6 | 419388A58F6F4AF18A514A5EE59AD713 |  | R22 | Non-TXV |  | 23.21% | 0.76786 | 44.61% | [5 empty] | Non-TXV | 23.21%
Stockton | CA | 95210-2603 |  | 2014-06-09 | 2014-06-09 11:09 | 2014-06-09 11:27 | GOODMAN - GSX130361BA | 89 | -8.4 | Yes | Yes | 26.6 | 20.6 | 6 | 0B80199488764321A0BA3020DDE38EEC |  | R410A | Non-TXV |  | -9.438% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.438%
Fresno | CA | 93703-1646 |  | 2014-06-11 | 2014-06-11 14:23 | 2014-06-11 14:43 | YORK - DCYZ-F036N070C | 64 | 2.7 | Yes | Yes | 26.1 | 21.9 | 4.2 | 2FF98FBB26C94B5689C7E90D07925DB1 |  | R410A | TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | TXV | 4.219%
Parlier | CA | 93648-9631 |  | 2014-06-18 | 2014-06-18 16:37 | 2014-06-18 17:00 | RUUD - N/A | 60 | 5.7 | Yes | Yes | 22.1 | 21.7 | 0.4 | A5D226A5966B428AA847D60ACFCA9C0B |  | R22 | Non-TXV |  | 9.5% | 0.905 | 18.26% | [5 empty] | Non-TXV | 9.5%
Fresno | CA | 93720-5360 |  | 2014-06-19 | 2014-06-19 13:08 | 2014-06-19 13:27 | RHEEM - RAKA-037JAZ | 79 | 10.6 | Yes | Yes | 20.6 | 20.9 | -0.3 | 0B05D81AADE0479681410D64CB4695DA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.42% | 0.86582 | 25.79% | [5 empty] | Non-TXV | 13.42%
Livingston | CA | 95334-9677 |  | 2014-06-20 | 2014-06-20 14:21 | 2014-06-20 14:45 | PAYNE - 588ANW030040ABAD | 53 | 8 | Yes | Yes | 22.7 | 20.2 | 2.5 | F7370A9E86CD4AB4B1BD76CA065F7BDA |  | R22 | Non-TXV |  | 15.09% | 0.84906 | 29.01% | [5 empty] | Non-TXV | 15.09%
Fresno | CA | 93702-2115 |  | 2014-06-18 | 2014-06-18 13:32 | 2014-06-18 13:34 | CARRIER - 7777UNK | 100 | 3.4 | Yes | Yes | 19.5 | 18.5 | 1 | 2F6806B078A0452690D8193D817DE5E5 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Lincoln | CA | 95648-0000 |  | 2014-06-16 | 2014-06-16 11:03 | 2014-06-16 11:21 | YORK - H2RC030S06G | 88 | 2.8 | Yes | Yes | 20 | 21.5 | -1.5 | 710A1885B8CE45E4B8383F3516A1D7BE |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Magalia | CA | 95954-9105 |  | 2014-06-25 | 2014-06-25 10:00 | 2014-06-25 10:33 | AMANA - NA | 60 | 1.8 | Yes | Yes | 16.8 | 19.6 | -2.8 | 65FAD39987BE483399C414C6A2C1AD0F |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95207-7108 |  | 2014-06-09 | 2014-06-09 15:02 | 2014-06-09 15:19 | GE - 21TA030H1A01 | 102 | 3.4 | Yes | Yes | 18.7 | 17.9 | 0.8 | 7E8D08411DA14414A0D1763145E19986 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Clovis | CA | 93611-5101 |  | 2014-06-11 | 2014-06-11 08:46 | 2014-06-11 09:08 | OTHER - 80WE30G1NA | 86 | 16.5 | Yes | Yes | 18.8 | 16.6 | 2.2 | 5DD9D87ACFC4416A91407A591FD1F82E |  | R22 | Non-TXV |  | 19.19% | 0.80814 | 36.87% | [5 empty] | Non-TXV | 19.19%
Grass Valley | CA | 95945-4902 |  | 2014-06-25 | 2014-06-25 09:28 | 2014-06-25 09:48 | DAY & NIGHT - 567GJ030-B | 90 | 2.9 | Yes | Yes | 18 | 20.3 | -2.3 | 612EC207565149B49B133EC8717B1636 |  | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Fresno | CA | 93703-1670 |  | 2014-06-14 | 2014-06-14 09:22 | 2014-06-14 09:46 | YORK - MC24-10D | 60 | 4 | Yes | Yes | 20.1 | 21.5 | -1.4 | E3644D9783B5414785952700CA8A57F7 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Stockton | CA | 95207-5818 |  | 2014-06-11 | 2014-06-11 11:26 | 2014-06-11 11:43 | DAY & NIGHT - 565BJ036 | 80 | -4.7 | Yes | Yes | 25.3 | 19.4 | 5.9 | E7ACBD5B4C914E6FA492970904A7B72B |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Madera | CA | 93637-4657 |  | 2014-08-05 | 2014-08-05 09:22 | 2014-08-05 09:24 | OTHER - UNK | 54 | 8.4 | Yes | Yes | 18.7 | 18.2 | 0.5 | E3660F5BA8704A6CAAAEBD77E3B847AD |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Paradise | CA | 95969-4333 |  | 2014-06-27 | 2014-06-27 15:03 | 2014-06-27 15:19 | PAYNE - PA10JA18-C | 60 | 6.4 | Yes | Yes | 22 | 20.1 | 1.9 | C76662226C494A9A9C5EB55A6C4B00B4 |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Nevada City | CA | 95959-9011 |  | 2014-06-26 | 2014-06-26 10:52 | 2014-06-26 11:12 | LENNOX - HS18-411-5P | 82 | 5.6 | Yes | Yes | 18 | 20.7 | -2.7 | 4AD3CBED0C8A442C8A2F5C4F1CF0E3FE |  | R22 | Non-TXV |  | 6.829% | 0.93171 | 13.12% | [5 empty] | Non-TXV | 6.829%
Stockton | CA | 95207-8124 |  | 2014-06-17 | 2014-06-17 09:45 | 2014-06-17 10:03 | RHEEM - RRNL-B024JK06X | 77 | 2.3 | Yes | Yes | 19.8 | 19.1 | 0.7 | 57C96B468DDC4B29889614F5B5A8D52D |  | R410A | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Stockton | CA | 95206-4858 |  | 2014-06-13 | 2014-06-13 12:21 | 2014-06-13 12:41 | BRYANT - 561CJ036-E | 124 | 22.8 | Yes | Yes | 22.9 | 21.4 | 1.5 | D61964EC7CFF46F8A417FD1B789E71E7 |  | R22 | TXV |  | 18.39% | 0.81613 | 35.34% | [5 empty] | TXV | 18.39%
Stockton | CA | 95207-2732 |  | 2014-06-09 | 2014-06-09 14:30 | 2014-06-09 14:50 | NORDYNE - GS3BA-030KA | 66 | 2.8 | Yes | Yes | 23.9 | 19.9 | 4 | A7BD84789E544FF0B8B7762F0571C301 |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Stockton | CA | 95207-8130 |  | 2014-06-26 | 2014-06-26 13:29 | 2014-06-26 13:45 | DAY & NIGHT - 585EJ018050 | 55 | 3.2 | Yes | Yes | 19.4 | 20.1 | -0.7 | 26F7BC2585CD415192545EF18A214D46 |  | R22 | Non-TXV |  | 5.818% | 0.94182 | 11.18% | [5 empty] | Non-TXV | 5.818%
Stockton | CA | 95207-7725 |  | 2014-06-16 | 2014-06-16 14:48 | 2014-06-16 15:09 | OTHER - TZAA-318-2A | 67 | -3.9 | Yes | Yes | 18 | 19.9 | -1.9 | 9E7E9382CE5D4C2C9B475EB3BF1AEC18 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Fresno | CA | 93726-5206 |  | 2014-07-01 | 2014-07-01 12:43 | 2014-07-01 13:03 | PAYNE - N/A | 120 | 3.6 | Yes | Yes | 17.1 | 20.1 | -3 | 162CA4EC4EAF49CCB691ADFB2A11D7E1 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-3718 |  | 2014-09-08 | 2014-09-08 14:59 | 2014-09-08 15:01 | OTHER - UNK | 68 | 8.6 | Yes | Yes | 20.5 | 18 | 2.5 | 21ED266486B34AE3B3CA479941A41FAB |  | R22 | Non-TXV |  | 12.65% | 0.87353 | 24.3% | [5 empty] | Non-TXV | 12.65%
Stockton | CA | 95205-7707 |  | 2014-06-18 | 2014-06-18 09:18 | 2014-06-18 09:48 | RHEEM - UNK | 85 | 5.1 | Yes | Yes | 22 | 20.8 | 1.2 | A7715F72B4ED47C7AEF390C4722EAEA3 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93727-6916 |  | 2014-07-07 | 2014-07-07 09:16 | 2014-07-07 09:55 | ICP - HAC024AKA1 | 69 | 2.5 | Yes | Yes | 18.9 | 19.8 | -0.9 | A956151185DC4FEEAD7E39D7CB6D347C |  | R22 | Non-TXV |  | 3.623% | 0.96377 | 6.963% | [5 empty] | Non-TXV | 3.623%
Fresno | CA | 93727-6921 |  | 2014-07-09 | 2014-07-09 09:52 | 2014-07-09 10:09 | UNITARY PRODUCTS GROUP - TCGD24S41S3HA | 61 | 6.3 | Yes | Yes | 20.1 | 22.6 | -2.5 | C8590DE9ED5A409BAB08A4D12772C1F3 |  | R410A | TXV |  | 10.33% | 0.89672 | 19.85% | [5 empty] | TXV | 10.33%
Fresno | CA | 93727-7906 |  | 2014-06-09 | 2014-06-09 12:44 | 2014-06-09 13:07 | GOODMAN - PGB030050-1 | 56 | 1.8 | Yes | Yes | 18.7 | 20.8 | -2.1 | 11E1D51BB23E47FCA9C933B0513779A9 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Lincoln | CA | 95648-8620 |  | 2014-06-09 | 2014-06-09 11:16 | 2014-06-09 11:41 | YORK - H2RA060S06D | 118 | 3.6 | Yes | Yes | 20 | 21 | -1 | 15B49A58F4194A44B9ECF2BE5BC78D53 |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Oakdale | CA | 95361-8869 |  | 2014-08-13 | 2014-08-13 15:30 | 2014-08-13 16:01 | RHEEM - RAKB--060JAZ | 85 | -6 | Yes | Yes | 22.5 | 18 | 4.5 | E4A93F214F81440C940D1B04B1FB1967 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Acampo | CA | 95220-9421 |  | 2014-10-13 | 2014-10-13 11:23 | 2014-10-13 11:23 | RHEEM - RRKA-A042JK08X | 69 | 7.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | 16841BD711F84F1FAA5A55ACC5E15630 | Add refrigerant: 7.9 oz | R22 | Non-TXV |  | 11.45% | 0.88551 | 22% | [5 empty] | Non-TXV | 11.45%
Fresno | CA | 93727-5405 |  | 2014-07-18 | 2014-07-18 11:54 | 2014-07-18 11:56 | OTHER - 7777UNK | 52 | 2.7 | Yes | Yes | 24.2 | 20.8 | 3.4 | 5A08325ACDD340309EB2F7AA60240C1B |  | R22 | Non-TXV |  | 5.192% | 0.94808 | 9.978% | [5 empty] | Non-TXV | 5.192%
Yuba City | CA | 95991-8244 |  | 2014-06-12 | 2014-06-12 16:54 | 2014-06-12 17:14 | BRYANT - 563CN060-E | 200 | 5.9 | Yes | Yes | 21 | 20.2 | 0.9 | D973E8A3414E4832B4FDE3769449ACA0 |  | R22 | Non-TXV |  | 2.95% | 0.9705 | 5.669% | [5 empty] | Non-TXV | 2.95%
Cameron Park | CA | 95682-9043 |  | 2014-07-15 | 2014-07-15 14:51 | 2014-07-15 15:18 | CARRIER - 38YCC036300 | 99 | 3 | Yes | Yes | 18 | 20.4 | -2.4 | 4C41B88A10EA4F5E93C548AD8D4C4AA4 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Tollhouse | CA | 93667-9602 |  | 2014-10-09 | 2014-10-09 09:55 | 2014-10-09 09:56 | RHEEM - RRKAA048JK10X | 78 | 10.3 | Yes | Yes | 24.5 | 19.8 | 4.7 | 393876A377BB478D8E817614ECA75C83 |  | R22 | Non-TXV |  | 13.21% | 0.86795 | 25.38% | [5 empty] | Non-TXV | 13.21%
Stockton | CA | 95206-5129 |  | 2014-06-12 | 2014-06-12 12:04 | 2014-06-12 12:28 | DAY & NIGHT - 561ANX048000ACAA | 85 | -6 | Yes | Yes | 20.1 | 21 | -0.9 | 86E06F9812174587BCC382A5B9E19411 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93726-6122 |  | 2014-07-16 | 2014-07-16 17:42 | 2014-07-16 17:43 | OTHER - 7777UNK | 74 | 3 | Yes | Yes | 21.3 | 21.3 | 0 | 031ECB3FD07B474DB03D904BEE4431D4 |  | R22 | Non-TXV |  | 4.054% | 0.95946 | 7.791% | [5 empty] | Non-TXV | 4.054%
Fresno | CA | 93705-2838 |  | 2014-06-20 | 2014-06-20 13:43 | 2014-06-20 13:45 | GOODMAN - 7777UNK | 110 | 5.4 | Yes | Yes | 21 | 20.9 | 0.1 | A300E39DF4B541AEAA26B66CB70CA3DC |  | R22 | Non-TXV |  | 4.909% | 0.95091 | 9.434% | [5 empty] | Non-TXV | 4.909%
Fresno | CA | 93727-4712 |  | 2014-06-26 | 2014-06-26 11:30 | 2014-06-26 11:51 | OTHER - 7777UNK | 54 | 5.6 | Yes | Yes | 24.9 | 19.3 | 5.6 | C2A661F6F5B243D686E44633B052FAB6 |  | R22 | Non-TXV |  | 10.37% | 0.8963 | 19.93% | [5 empty] | Non-TXV | 10.37%
Stockton | CA | 95204-3951 |  | 2014-06-18 | 2014-06-18 08:10 | 2014-06-18 08:35 | RHEEM - HC-80-24-21C | 85 | 7.2 | Yes | Yes | 20.1 | 19.3 | 0.8 | 2060C3586FAE4D9E9E8B91C6C49BD209 |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Stockton | CA | 95203-3032 |  | 2014-06-10 | 2014-06-10 09:08 | 2014-06-10 09:28 | TRANE - UNK | 85 | 5.6 | Yes | Yes | 22.7 | 20.9 | 1.8 | 2037B93B28184920A30082C426B43316 |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Rocklin | CA | 95677-4016 |  | 2014-06-30 | 2014-06-30 16:10 | 2014-06-30 16:30 | OTHER - R2A348GKR2 | 136 | 5 | Yes | Yes | 12 | 14.5 | -2.5 | A7488F30989F4DE884654755DCF683B8 |  | R22 | TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | TXV | 3.676%
Fresno | CA | 93702-4578 |  | 2014-06-18 | 2014-06-18 12:44 | 2014-06-18 12:46 | RHEEM - 7777UNK | 64 | 3.1 | Yes | Yes | 25.3 | 22 | 3.3 | C6F40B6DF8884D98803DDBF2D28408D5 |  | R22 | Non-TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | Non-TXV | 4.844%
Madera | CA | 93638-2457 |  | 2014-07-01 | 2014-07-01 10:13 | 2014-07-01 10:15 | CARRIER - 48SX030040821 | 69 | 12.5 | Yes | Yes | 22.5 | 21.4 | 1.1 | D78DF89AA20142BCB9F6D309CB726924 |  | R22 | Non-TXV |  | 18.12% | 0.81884 | 34.81% | [5 empty] | Non-TXV | 18.12%
Selma | CA | 93662-2265 |  | 2014-06-13 | 2014-06-13 08:24 | 2014-06-13 08:55 | UNITARY PRODUCTS GROUP - GCGD48S21S1A | 75 | 18.3 | Yes | Yes | 23.9 | 21.2 | 2.8 | D1922744535747BAA29AA4C386D78733 |  | R22 | Non-TXV |  | 24.4% | 0.756 | 46.89% | [5 empty] | Non-TXV | 24.4%
Chico | CA | 95926-2710 |  | 2014-06-18 | 2014-06-18 13:59 | 2014-06-18 14:16 | RHEEM - NA | 85 | 2.7 | Yes | Yes | 23.5 | 20.2 | 3.4 | DFD6C095FFC54BCAAAFC92377767C7C9 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Jackson | CA | 95642-9455 |  | 2014-07-07 | 2014-07-07 13:37 | 2014-07-07 13:54 | COLEMAN - 7830-901 | 63 | 1.9 | Yes | Yes | 20 | 21.5 | -1.5 | E9AB629EF7C5492F8F50521549697E35 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Stockton | CA | 95212-3128 |  | 2014-07-02 | 2014-07-02 13:32 | 2014-07-02 13:50 | YORK - H1RA042S06G6 | 84 | 3.1 | Yes | Yes | 20 | 19.9 | 0.1 | DDD17C35D4704F0DBE927CFD759A3243 |  | R22 | Non-TXV |  | 3.69% | 0.9631 | 7.092% | [5 empty] | Non-TXV | 3.69%
Livingston | CA | 95334-1801 |  | 2014-08-07 | 2014-08-07 14:25 | 2014-08-07 14:46 | WEATHER KING - 13AJA30A01 | 85 | 11.4 | Yes | Yes | 20.1 | 20.1 | 0 | 26D47523705D4916B1E652EEFF93405C |  | R22 | Non-TXV |  | 13.41% | 0.86588 | 25.77% | [5 empty] | Non-TXV | 13.41%
Stockton | CA | 95206-1857 |  | 2014-06-18 | 2014-06-18 09:58 | 2014-06-18 10:15 | PAYNE - 585HJ030040 | 68 | 9.7 | Yes | Yes | 25.6 | 21.5 | 4.1 | DB4D2237CC2E44A49003B57016761A26 |  | R22 | Non-TXV |  | 14.26% | 0.85735 | 27.41% | [5 empty] | Non-TXV | 14.26%
Clovis | CA | 93612-0130 |  | 2014-07-31 | 2014-07-31 09:26 | 2014-07-31 09:43 | BRYANT - 574BNW036090NA | 85 | 3.1 | Yes | Yes | 23 | 19.9 | 3.1 | 3CBBBC9CF60E455AAAD6B56289BA7056 |  | R410A | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Stockton | CA | 95207-1938 |  | 2014-06-12 | 2014-06-12 11:34 | 2014-06-12 11:56 | RHEEM - RAKA-024JAS | 51 | 2.5 | Yes | Yes | 21.5 | 19.3 | 2.2 | D1EF4F0EBE654B53888414ED348E3F0B |  | R22 | Non-TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | Non-TXV | 4.902%
Pinedale | CA | 93650-1106 |  | 2014-06-11 | 2014-06-11 13:21 | 2014-06-11 13:40 | YORK - D3CG048N06206E | 88 | 18.2 | Yes | Yes | 27.5 | 23.1 | 4.4 | 70ECF9284A974999A4D1E2854314BDFD |  | R22 | Non-TXV |  | 20.68% | 0.79318 | 39.75% | [5 empty] | Non-TXV | 20.68%
Madera | CA | 93638-2639 |  | 2014-06-12 | 2014-06-12 13:47 | 2014-06-12 14:03 | RHEEM - RRMAA036JK06X | 99 | 14.3 | Yes | Yes | 21.6 | 18.7 | 2.9 | F7C94B649CC9475383670DF1D28D8260 |  | R22 | Non-TXV |  | 14.44% | 0.85556 | 27.76% | [5 empty] | Non-TXV | 14.44%
Stockton | CA | 95209-2024 |  | 2014-06-09 | 2014-06-09 08:26 | 2014-06-09 08:46 | RUUD - UAMA-042JBZ | 95 | 7 | Yes | Yes | 25.6 | 20.7 | 4.9 | 1CF1D721F09D4D7EBBFF9814C8C74B6B |  | R22 | Non-TXV |  | 7.368% | 0.92632 | 14.16% | [5 empty] | Non-TXV | 7.368%
Fresno | CA | 93705-2007 |  | 2014-06-20 | 2014-06-20 11:15 | 2014-06-20 11:21 | GOODMAN - GPG1336070M41DA | 70 | 2.1 | Yes | Yes | 26.8 | 20.9 | 5.9 | 129D0BBB76D54486AB2CE54D98616FC2 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Madera | CA | 93637-2674 |  | 2014-06-19 | 2014-06-19 10:34 | 2014-06-19 10:35 | CARRIER - 48SS036060301 | 67 | 12.7 | Yes | Yes | 25.6 | 22.6 | 3 | 41ABECC31DD445E9A5213E8A9B7C160B |  | R22 | Non-TXV |  | 18.96% | 0.81045 | 36.43% | [5 empty] | Non-TXV | 18.96%
Madera | CA | 93638-2452 |  | 2014-06-09 | 2014-06-09 13:34 | 2014-06-09 13:54 | YORK - D1NH036N07206A | 104 | 17.4 | Yes | Yes | 26.6 | 22 | 4.6 | 27FCB33DEE1F482F96A4F5E5153079FF |  | R22 | Non-TXV |  | 16.73% | 0.83269 | 32.15% | [5 empty] | Non-TXV | 16.73%
Stockton | CA | 95206-1280 |  | 2014-07-24 | 2014-07-24 14:25 | 2014-07-24 14:42 | CARRIER - 584BNW030040AABE | 85 | -5 | Yes | Yes | 16.8 | 17.5 | -0.7 | CCE33171F102460DBA476886C95B8A53 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95206-1281 |  | 2014-07-25 | 2014-07-25 10:28 | 2014-07-25 10:57 | DAY & NIGHT - UKN | 80 | 2.9 | Yes | Yes | 24 | 19.3 | 4.7 | 0C8A5240106C46DB931EC58A6B98776F |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Fresno | CA | 93726-5206 |  | 2014-07-02 | 2014-07-02 16:13 | 2014-07-02 16:33 | AMERICAN STANDARD - YCX036F1M0BC | 116 | 7.4 | Yes | Yes | 21.5 | 21.5 | 0 | 83FEDB35A134485B994A0D811E17E181 |  | R22 | Non-TXV |  | 6.379% | 0.93621 | 12.26% | [5 empty] | Non-TXV | 6.379%
Selma | CA | 93662-9482 |  | 2014-06-13 | 2014-06-13 15:49 | 2014-06-13 16:22 | RHEEM - RQNA-B048JK000 | 66 | 5.6 | Yes | Yes | 23.1 | 23.1 | 0 | B6C6672D550B43AAA0C8E28E5F6D2FBB |  | R22 | Non-TXV |  | 8.485% | 0.91515 | 16.31% | [5 empty] | Non-TXV | 8.485%
Madera | CA | 93638-2636 |  | 2014-06-12 | 2014-06-12 12:50 | 2014-06-12 13:10 | GOODMAN - PGB0420751 | 68 | 14 | Yes | Yes | 23.9 | 20.4 | 3.5 | 5C7A9D6F3B1F4AEB8CA2F277E5BD5237 |  | R22 | Non-TXV |  | 20.59% | 0.79412 | 39.57% | [5 empty] | Non-TXV | 20.59%
Stockton | CA | 95206-1280 |  | 2014-07-25 | 2014-07-25 11:25 | 2014-07-25 11:56 | DAY & NIGHT - UKN | 80 | 4.1 | Yes | Yes | 23.9 | 18.5 | 5.4 | 6B3AA44FABC349D4B444730B6CDD76DA |  | R22 | Non-TXV |  | 5.125% | 0.94875 | 9.849% | [5 empty] | Non-TXV | 5.125%
Jackson | CA | 95642-9570 |  | 2014-07-30 | 2014-07-30 12:29 | 2014-07-30 12:46 | PAYNE - 593BJ024-A | 67 | 2 | Yes | Yes | 18.5 | 20.2 | -1.7 | A8C6453D0B534BD19FF42352325F940E |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Chico | CA | 95926-5305 |  | 2014-06-24 | 2014-06-24 13:00 | 2014-06-24 13:17 | PAYNE - 567GJ042 | 55 | 5.4 | Yes | Yes | 20.5 | 20.4 | 0.1 | 2DDA0B366D9440B4BC57311E54D0F969 |  | R22 | Non-TXV |  | 9.818% | 0.90182 | 18.87% | [5 empty] | Non-TXV | 9.818%
Sutter Creek | CA | 95685-4029 |  | 2014-07-07 | 2014-07-07 12:31 | 2014-07-07 12:52 | DAY & NIGHT - 585EJM030075ABAF | 58 | 5.5 | Yes | Yes | 28 | 22.9 | 5.1 | A4F1344639AC4CF4B360466A7720E507 |  | R22 | Non-TXV |  | 9.483% | 0.90517 | 18.22% | [5 empty] | Non-TXV | 9.483%
Magalia | CA | 95954-9449 |  | 2014-06-11 | 2014-06-11 09:09 | 2014-06-11 09:26 | CARRIER - 504Q0303000 | 87 | 5.4 | Yes | Yes | 17.1 | 19.9 | -2.8 | B5F3537544C8414F8F2CBFC259BCA389 |  | R22 | Non-TXV |  | 6.207% | 0.93793 | 11.93% | [5 empty] | Non-TXV | 6.207%
Williams | CA | 95987-0000 |  | 2014-09-19 | 2014-09-19 15:13 | 2014-09-19 15:13 | TRANE - YCC024FIL0BA | 64 | 0 | Yes | Yes | 22.5 | 19.1 | 3.4 | 1FAE3E794BED4BEBBDDE4F05B413406D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9453 |  | 2014-07-22 | 2014-07-22 08:20 | 2014-07-22 08:38 | BARD - PH13301-A | 50 | 2.8 | Yes | Yes | 17.5 | 19.8 | -2.3 | 760FBEC36D41430C85FCA166E0C00978 |  | R410A | Non-TXV |  | 5.6% | 0.944 | 10.76% | [5 empty] | Non-TXV | 5.6%
Williams | CA | 95987-0000 |  | 2014-10-22 | 2014-10-22 10:00 | 2014-10-22 10:30 | RUUD - NA | 55 | 4.7 | Yes | Yes | 16.5 | 18.8 | -2.3 | 7501B7E7D4954A79854AB501D86FEFDE |  | R22 | Non-TXV |  | 8.545% | 0.91455 | 16.42% | [5 empty] | Non-TXV | 8.545%
Orland | CA | 95963-2109 |  | 2014-06-16 | 2014-06-16 08:28 | 2014-06-16 09:02 | OTHER - ACO36X1021A | 54 | 10.7 | Yes | Yes | 17.3 | 19.1 | -1.8 | 5666E1568B9E4D37B3D98FA12D0376AB |  | R22 | Non-TXV |  | 19.81% | 0.80185 | 38.08% | [5 empty] | Non-TXV | 19.81%
Fresno | CA | 93726-5206 |  | 2014-06-24 | 2014-06-24 13:27 | 2014-06-24 13:31 | RHEEM - RACA042AAQ | 37 | 17.4 | Yes | Yes | 21.4 | 17.2 | 4.2 | 96C6EA1BF03F4B7D9821A1FC3D7B46BD |  | R22 | Non-TXV |  | 47.03% | 0.52973 | 90.38% | [5 empty] | Non-TXV | 47.03%
Fresno | CA | 93705-3825 |  | 2014-07-15 | 2014-07-15 14:49 | 2014-07-15 15:08 | ICP - N4A360AKC300 | 131 | 4.4 | Yes | Yes | 20.6 | 19.6 | 1 | 7BBEEB35086B45D7B0285B6BDF646A73 |  | R410A | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
Merced | CA | 95340-4345 |  | 2014-07-03 | 2014-07-03 13:37 | 2014-07-03 13:38 | OTHER - TTZAA-348-2A | 123 | 6.5 | Yes | Yes | 23.7 | 19.9 | 3.9 | B45785E491894AF2A111F8CCF77BE410 |  | R22 | Non-TXV |  | 5.285% | 0.94715 | 10.16% | [5 empty] | Non-TXV | 5.285%
Paradise | CA | 95969-4724 |  | 2014-06-13 | 2014-06-13 10:01 | 2014-06-13 22:52 | DAY & NIGHT - NA | 60 | 4.9 | Yes | Yes | 26.1 | 21.7 | 4.5 | FBC302F5A5354B168AABB9FF71A084EB |  | R22 | Non-TXV |  | 8.167% | 0.91833 | 15.69% | [5 empty] | Non-TXV | 8.167%
Fresno | CA | 93726-0233 |  | 2014-08-06 | 2014-08-06 16:25 | 2014-08-06 16:43 | OTHER - UNK | 94 | 2.8 | Yes | Yes | 18 | 15.4 | 2.6 | 53C620040BE1485482C6072C18D4A911 |  | R22 | Non-TXV |  | 2.979% | 0.97021 | 5.724% | [5 empty] | Non-TXV | 2.979%
Fresno | CA | 93728-2218 |  | 2014-07-30 | 2014-07-30 12:05 | 2014-07-30 12:24 | AMANA - APG12300701A | 73 | 2.7 | Yes | Yes | 21.1 | 20.1 | 1 | 14AF511744D649D689A936EA0F250BF8 |  | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Lathrop | CA | 95330-8923 |  | 2014-07-07 | 2014-07-07 13:35 | 2014-07-07 13:56 | GOODMAN - CKJ48-1A | 85 | 3.8 | Yes | Yes | 23.6 | 21 | 2.6 | B0136C3835174BCF82DEAE06F3AFF726 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Madera | CA | 93638-5102 |  | 2014-06-26 | 2014-06-26 15:49 | 2014-06-26 15:50 | YORK - DAYPF030N070A | 73 | 12.8 | Yes | Yes | 26.8 | 23.1 | 3.7 | 7A553AABF2E04932B0F39E981CF7F94F |  | R22 | Non-TXV |  | 17.53% | 0.82466 | 33.7% | [5 empty] | Non-TXV | 17.53%
Fowler | CA | 93625-9705 |  | 2014-07-31 | 2014-07-31 12:21 | 2014-07-31 12:43 | RUUD - URKA-A048JK10E | 78 | 4.3 | Yes | Yes | 21.4 | 19 | 2.4 | 5B36A46DB0FD486A9076BF5C02E63C88 |  | R22 | Non-TXV |  | 5.513% | 0.94487 | 10.59% | [5 empty] | Non-TXV | 5.513%
Paso Robles | CA | 93446-2725 |  | 2014-06-24 | 2014-06-24 09:19 | 2014-06-24 09:44 | RHEEM - RAFD-036JAS | 80 | 8.7 | Yes | Yes | 23.5 | 19.1 | 4.4 | F684086A69244993891907C9CF065333 |  | R22 | Non-TXV |  | 10.88% | 0.89125 | 20.9% | [5 empty] | Non-TXV | 10.88%
Merced | CA | 95340-0749 |  | 2014-06-30 | 2014-06-30 17:22 | 2014-06-30 17:24 | BRYANT - 563CNX048000AF | 167 | 8.3 | Yes | Yes | 21.4 | 19.9 | 1.5 | 99E7AB65C4A549A3A574862E6457DA29 |  | R410A | Non-TXV |  | 4.97% | 0.9503 | 9.551% | [5 empty] | Non-TXV | 4.97%
Fresno | CA | 93722-6551 |  | 2014-08-16 | 2014-08-16 11:14 | 2014-08-16 11:15 | ICP - PGAA361K2 | 81 | 11.6 | Yes | Yes | 21 | 19.9 | 1.1 | 9C8E77A0A5DE416B964E980F17CD8BAB |  | R22 | Non-TXV |  | 14.32% | 0.85679 | 27.52% | [5 empty] | Non-TXV | 14.32%
Williams | CA | 95987-0000 |  | 2014-09-18 | 2014-09-18 13:06 | 2014-09-18 13:27 | RUUD - UKN | 72 | 5.1 | Yes | Yes | 22 | 18.5 | 3.5 | 09E8A652335641CFB2E7924FD03E1C99 |  | R22 | Non-TXV |  | 7.083% | 0.92917 | 13.61% | [5 empty] | Non-TXV | 7.083%
Dinuba | CA | 93618-4059 |  | 2014-07-21 | 2014-07-21 17:56 | 2014-07-21 18:21 | UNITARY PRODUCTS GROUP - H2RD024S06B | 88 | 3.6 | Yes | Yes | 21.9 | 22.5 | -0.6 | AD08480CECC440E1A8F6D66E672CEA88 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Magalia | CA | 95954-9455 |  | 2014-06-11 | 2014-06-11 10:30 | 2014-06-11 10:46 | PAYNE - PA10JA036000AAAA | 85 | 6.2 | Yes | Yes | 23.5 | 21.5 | 2 | A716AEF7CA664A1983406091EE4E40F2 |  | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Fresno | CA | 93703-2551 |  | 2014-07-07 | 2014-07-07 11:59 | 2014-07-07 12:16 | GOODMAN - GPG1330045M41CA | 78 | -4.6 | Yes | Yes | 27.3 | 21.3 | 6 | FF5BD192675244B3AA9047168CF425E6 |  | R410A | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Fresno | CA | 93703-1238 |  | 2014-06-11 | 2014-06-11 10:31 | 2014-06-11 10:54 | YORK - DAYA-F030N070C | 76 | 2.4 | Yes | Yes | 23.7 | 19.7 | 4 | FC9ED44076BC4A2FA8DE216478223C5D |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Fresno | CA | 93703-1677 |  | 2014-06-20 | 2014-06-20 14:43 | 2014-06-20 14:46 | OTHER - UNK | 56 | 9.7 | Yes | Yes | 22.3 | 20.5 | 1.8 | BF1E7FCB8ECD41F7B8F4F173B083FC27 |  | R22 | Non-TXV |  | 17.32% | 0.82679 | 33.29% | [5 empty] | Non-TXV | 17.32%
Magalia | CA | 95954-9669 |  | 2014-07-15 | 2014-07-15 12:04 | 2014-07-15 12:20 | BRYANT - 113AN036-H | 85 | 3.3 | Yes | Yes | 20 | 20.9 | -0.9 | 0A67DA05A48F4A619EF2297EFA1D7440 |  | R410A | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Magalia | CA | 95954-9669 |  | 2014-07-15 | 2014-07-15 12:44 | 2014-07-15 13:09 | OTHER - CA9630VKO1 | 70 | 4.9 | Yes | Yes | 21 | 20.3 | 0.7 | 874E26F2EF9E4CE7B1C7B3ECF675A4FA |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Winton | CA | 95388-9322 |  | 2014-06-30 | 2014-06-30 12:35 | 2014-06-30 12:36 | GOODMAN - GPG13360701AC | 112 | 4.9 | Yes | Yes | 26.3 | 20.4 | 5.9 | 4813A78203D3464AB64E4D2F4AF5C657 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Diamond Springs | CA | 95619-9428 |  | 2014-06-23 | 2014-06-23 09:02 | 2014-06-23 09:22 | COLEMAN - ERCS0481CAH | 228 | 6.8 | Yes | Yes | 24 | 21.2 | 2.8 | BF8CCFFFF37F42439C218E2F3558B946 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Colusa | CA | 95932-3201 |  | 2014-07-03 | 2014-07-03 11:53 | 2014-07-03 12:10 | INTERTHERM - NA | 46 | 4.1 | Yes | Yes | 19.6 | 21.5 | -1.9 | C7DFBF94B0AC40FF9054ABA55866F79F |  | R22 | Non-TXV |  | 8.913% | 0.91087 | 17.13% | [5 empty] | Non-TXV | 8.913%
Dinuba | CA | 93618-4059 |  | 2014-07-14 | 2014-07-14 14:54 | 2014-07-14 15:28 | UNITARY PRODUCTS GROUP - H2RD030S6B | 93 | 3.9 | Yes | Yes | 19.6 | 20.8 | -1.2 | 9CB40A2C2B34462DAF5145A7CFB85A29 |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Acampo | CA | 95220-9397 |  | 2014-09-10 | 2014-09-10 12:31 | 2014-09-10 12:49 | BRYANT - 582AJW0481115AAAG | 81 | 3 | Yes | Yes | 21 | 17.5 | 3.6 | 4CD4E850FDEE40C9AEE0B139DBE5BB87 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Orland | CA | 95963-1436 |  | 2014-07-23 | 2014-07-23 11:00 | 2014-07-23 11:45 | AMERICAN STANDARD - 7A2A100AZ04 | 85 | 5 | Yes | Yes | 17.7 | 18.5 | -0.8 | 2BCBFD2C2DC7414985ED0FC03A767A0C |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Williams | CA | 95987-0000 |  | 2014-09-24 | 2014-09-24 09:35 | 2014-09-24 09:55 | TRANE - YCC024F1L0BA | 64 | 1.9 | Yes | Yes | 18 | 17.7 | 0.3 | AC7E9EB3992B4886B613F4DF2E162529 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Chico | CA | 95973-0849 |  | 2014-06-20 | 2014-06-20 14:58 | 2014-06-20 15:14 | OTHER - FS5BD-024KA | 94 | 3 | Yes | Yes | 26.5 | 22.3 | 4.2 | 0CB5447FBD83435DAF794BF9E6A07665 |  | R22 | Non-TXV |  | 3.191% | 0.96809 | 6.133% | [5 empty] | Non-TXV | 3.191%
Paradise | CA | 95969-2812 |  | 2014-06-13 | 2014-06-13 15:23 | 2014-06-13 15:43 | TRANE - 2YCC03036A1064AA | 80 | 2.9 | Yes | Yes | 21.6 | 19.8 | 1.8 | CABBC453D0154DC99716EA0FF1845AE0 |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Los Banos | CA | 93635-6382 |  | 2014-06-10 | 2014-06-10 14:35 | 2014-06-10 14:37 | GIBSON - JS3BA-036KA | 69 | 2.3 | Yes | Yes | 24.2 | 20.5 | 3.7 | F8503133F9A8442FBEA7E53F99AE82FF |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Oroville | CA | 95966-5447 |  | 2014-08-07 | 2014-08-07 15:14 | 2014-08-07 15:36 | BRYANT - 582AJWO48090NAAG | 82 | 3.3 | Yes | Yes | 23 | 21.4 | 1.6 | C9A433F6C45D447F951380CEA57A84B2 |  | R22 | Non-TXV |  | 4.024% | 0.95976 | 7.734% | [5 empty] | Non-TXV | 4.024%
Stockton | CA | 95206-5123 |  | 2014-06-16 | 2014-06-16 11:07 | 2014-06-16 11:29 | DAY & NIGHT - 591ANX036000AAA | 117 | 5.4 | Yes | Yes | 20.8 | 20.3 | 0.5 | 1DCE4CF2F39848B29E4C3C8E86DFCE12 |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Stockton | CA | 95207-1938 |  | 2014-06-18 | 2014-06-18 13:18 | 2014-06-18 13:42 | DAY & NIGHT - 591ANX030000ABA | 89 | -5.2 | Yes | Yes | 23.7 | 22.6 | 1.1 | 993D568AE4E34517A578119911B1F514 |  | R22 | Non-TXV |  | -5.843% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.843%
Livingston | CA | 95334-1846 |  | 2014-06-19 | 2014-06-19 11:23 | 2014-06-19 11:45 | YORK - H2RA036S06E | 63 | 11.5 | Yes | Yes | 25.6 | 20.6 | 5.1 | 3BEAB651DE704712AED2B5376E08202E |  | R22 | Non-TXV |  | 18.25% | 0.81746 | 35.08% | [5 empty] | Non-TXV | 18.25%
Merced | CA | 95340-2300 |  | 2014-07-01 | 2014-07-01 09:13 | 2014-07-01 09:14 | TRANE - TTB724-100A1 | 54 | 2.3 | Yes | Yes | 24.3 | 20.6 | 3.7 | E7C31837A52B475F9327E5F674165167 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Madera | CA | 93636-7406 |  | 2014-06-12 | 2014-06-12 09:56 | 2014-06-12 10:16 | YORK - B1HH024A06B | 85 | 10.8 | Yes | Yes | 21 | 19.9 | 1.1 | DD8758001C94419FBF4A4258F94958F1 |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
Madera | CA | 93636-7406 |  | 2014-06-12 | 2014-06-12 10:19 | 2014-06-12 10:22 | YORK - B1HH024A06B | 85 | 8.4 | Yes | Yes | 18.9 | 17.6 | 1.3 | AC5AFC958638411999EA3DA0EA2379F9 |  | R22 | Non-TXV |  | 9.882% | 0.90118 | 18.99% | [5 empty] | Non-TXV | 9.882%
Stockton | CA | 95219-4602 |  | 2014-07-01 | 2014-07-01 09:45 | 2014-07-01 10:04 | ICP - CA5530VKD2 | 74 | 3.6 | Yes | Yes | 20.8 | 18.6 | 2.2 | 7F3C0A90AAA44134BC137A0D5736D25F |  | R22 | Non-TXV |  | 4.865% | 0.95135 | 9.349% | [5 empty] | Non-TXV | 4.865%
Atwater | CA | 95301-4585 |  | 2014-06-30 | 2014-06-30 12:22 | 2014-06-30 12:46 | AMERICAN STANDARD - 2A7A3036A1000A | 101 | 7.2 | Yes | Yes | 23.1 | 19.9 | 3.2 | 16B792DD31D342B497921E212316A7EC |  | R22 | Non-TXV |  | 7.129% | 0.92871 | 13.7% | [5 empty] | Non-TXV | 7.129%
Oakdale | CA | 95361-3941 |  | 2014-06-26 | 2014-06-26 13:29 | 2014-06-26 13:53 | DAY & NIGHT - 567C024RCU | 60 | 2.4 | Yes | Yes | 23.5 | 19 | 4.5 | D7AD77C54DCB4A54A72BA28C602A5214 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Manteca | CA | 95337-6831 |  | 2014-06-17 | 2014-06-17 15:08 | 2014-06-17 15:29 | OTHER - CCU10A36A-1 | 85 | 7.9 | Yes | Yes | 22.9 | 21.5 | 1.4 | 3B4E1C5534AB49AF8F634785B0E73D44 |  | R22 | TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | TXV | 9.294%
Stockton | CA | 95212-3451 |  | 2014-06-20 | 2014-06-20 12:49 | 2014-06-20 13:09 | BRYANT - 561CJ048-F | 97 | 4.3 | Yes | Yes | 22.4 | 21.2 | 1.2 | F4ECF264DD0F4AA7A474DCFAC67A19DD |  | R22 | TXV |  | 4.433% | 0.95567 | 8.519% | [5 empty] | TXV | 4.433%
Fresno | CA | 93705-3422 |  | 2014-07-30 | 2014-07-30 13:42 | 2014-07-30 14:00 | CARRIER - 48SS-036080311 | 67 | 2 | Yes | Yes | 19.9 | 19.9 | 0 | DA3A25885EB843499D0A24FB2D57F408 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Stockton | CA | 95206-1280 |  | 2014-07-25 | 2014-07-25 11:01 | 2014-07-25 11:20 | CARRIER - 584BNW0300AAABE | 80 | 2.8 | Yes | Yes | 21.3 | 19.9 | 1.4 | E077FADC4D494EDB9AE21F9ECBEA5429 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Fresno | CA | 93727-6460 |  | 2014-06-09 | 2014-06-09 13:47 | 2014-06-09 14:09 | CARRIER - 28CKC024320 | 69 | 8.1 | Yes | Yes | 17.2 | 19.3 | -2.1 | C243C739E0FE482CA81B129948F50932 |  | R22 | TXV |  | 11.74% | 0.88261 | 22.56% | [5 empty] | TXV | 11.74%
Chico | CA | 95928-7414 |  | 2014-06-19 | 2014-06-19 16:05 | 2014-06-19 16:05 | DAY & NIGHT - PGN348090K01A1 | 196 | 0 | Yes | Yes | 23 | 22 | 1 | 97CBFD5174AD4FBE97C5D937CE107866 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9605 |  | 2014-08-13 | 2014-08-13 18:28 | 2014-08-13 19:09 | CARRIER - 561AJ024-B | 56 | 9.8 | Yes | Yes | 18.6 | 20.6 | -2 | 4AE154E46D71422090C0E3C1E4BA65B3 |  | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Coarsegold | CA | 93614-9649 |  | 2014-07-07 | 2014-07-07 14:54 | 2014-07-07 14:55 | OTHER - 574ANW048090NB | 196 | 22.1 | Yes | Yes | 23 | 19.9 | 3.1 | B11BD6AABFF94B2CB0257DC0E945FC36 |  | R22 | Non-TXV |  | 11.28% | 0.88724 | 21.67% | [5 empty] | Non-TXV | 11.28%
Stockton | CA | 95207-2736 |  | 2014-06-11 | 2014-06-11 08:11 | 2014-06-11 08:27 | RHEEM - RRKA-A030JK06X | 54 | -3.2 | Yes | Yes | 22.3 | 18.7 | 3.6 | 93E8B02633AD431C933718397C41FBB1 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Fresno | CA | 93726-5406 |  | 2014-06-24 | 2014-06-24 15:30 | 2014-06-24 15:32 | GOODMAN - GPG1330070M41BA | 78 | 11.9 | Yes | Yes | 23.6 | 20.8 | 2.8 | FD688521F2AE4350B331C9567BF30496 |  | R410A | Non-TXV |  | 15.26% | 0.84744 | 29.32% | [5 empty] | Non-TXV | 15.26%
Fresno | CA | 93727-4521 |  | 2014-07-08 | 2014-07-08 16:09 | 2014-07-08 16:48 | BDP - 588ANW036060ADAF | 67 | 3.1 | Yes | Yes | 17.9 | 19.9 | -2 | 11D685B3F6E34527874774280DB84701 |  | R22 | Non-TXV |  | 4.627% | 0.95373 | 8.892% | [5 empty] | Non-TXV | 4.627%
Coarsegold | CA | 93614-9183 |  | 2014-07-07 | 2014-07-07 11:50 | 2014-07-07 11:51 | AIRE-FLO - PY3GNAA48090NA | 100 | 5.9 | Yes | Yes | 21.3 | 16.4 | 4.9 | F74E5C1CF3B44B16BFC0533D38443EC7 |  | R410A | Non-TXV |  | 5.9% | 0.941 | 11.34% | [5 empty] | Non-TXV | 5.9%
Coarsegold | CA | 93614-9183 |  | 2014-07-07 | 2014-07-07 11:53 | 2014-07-07 12:01 | AIRE-FLO - PY3GNAA48090NA | 100 | 16.9 | Yes | Yes | 24.1 | 20.2 | 3.9 | 3AC2070284044AEBA4B85C609117398D |  | R410A | Non-TXV |  | 16.9% | 0.831 | 32.48% | [5 empty] | Non-TXV | 16.9%
Grass Valley | CA | 95945-4922 |  | 2014-06-25 | 2014-06-25 12:16 | 2014-06-25 12:39 | DAY & NIGHT - 588ANW042080AAAG | 82 | 2.4 | Yes | Yes | 25 | 21 | 4 | 67157767FEEB40608A43DE28DA9C3B26 |  | R22 | Non-TXV |  | 2.927% | 0.97073 | 5.625% | [5 empty] | Non-TXV | 2.927%
Los Banos | CA | 93635-3411 |  | 2014-06-27 | 2014-06-27 13:16 | 2014-06-27 13:33 | CARRIER - 38TH036300 | 82 | -4.8 | Yes | Yes | 26.8 | 20.8 | 6 | 24046EAAAC754300965391929B9B6148 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Fresno | CA | 93725-1257 |  | 2014-06-16 | 2014-06-16 09:46 | 2014-06-16 09:49 | OTHER - CE481CB | 96 | 13.2 | Yes | Yes | 23.9 | 19.2 | 4.7 | 8668A919AAB444A180231B3BEBEA8E48 |  | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
San Joaquin | CA | 93660-0000 |  | 2014-06-27 | 2014-06-27 12:50 | 2014-06-27 13:06 | CARRIER - 48SS-030040311 | 53 | 4.6 | Yes | Yes | 20.6 | 20.4 | 0.2 | C48A5407D9F143808F24484D6C53D97E |  | R22 | Non-TXV |  | 8.679% | 0.91321 | 16.68% | [5 empty] | Non-TXV | 8.679%
Fresno | CA | 93726-4851 |  | 2014-07-03 | 2014-07-03 17:52 | 2014-07-03 17:52 | BDP - 585CJ02450 | 70 | 0 | Yes | Yes | 15.9 | 18.7 | -2.8 | 57F34B3E9DDB45A9A6F71B2BFADD2ABC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-9608 |  | 2014-06-16 | 2014-06-16 11:55 | 2014-06-16 12:15 | RUUD - 13PJL48A01 | 100 | 3.5 | Yes | Yes | 28 | 22.3 | 5.8 | B4C3774268304DDCAA037FD992B68B89 |  | R410A | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Coarsegold | CA | 93614-9165 |  | 2014-07-07 | 2014-07-07 09:58 | 2014-07-07 10:00 | AIRE-FLO - RPNA038J000 | 76 | 8.8 | Yes | Yes | 21.8 | 22.6 | -0.8 | 689B73012C524050B075655B92AEE185 |  | R22 | Non-TXV |  | 11.58% | 0.88421 | 22.25% | [5 empty] | Non-TXV | 11.58%
Stockton | CA | 95206-5603 |  | 2014-06-12 | 2014-06-12 12:42 | 2014-06-12 13:05 | GOODMAN - GSX130421BC | 85 | 10 | Yes | Yes | 22.5 | 20.2 | 2.3 | 012FDA923C8F4E06932C68501465407B |  | R410A | TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | TXV | 11.76%
Chico | CA | 95926-1747 |  | 2014-06-18 | 2014-06-18 11:42 | 2014-06-18 12:02 | DAY & NIGHT - 5627GJ836 | 50 | 11 | Yes | Yes | 16.4 | 19.3 | -2.9 | 3F4C146A5D5F4E5E841B3C649AEADE70 |  | R22 | Non-TXV |  | 22% | 0.78 | 42.28% | [5 empty] | Non-TXV | 22%
Madera | CA | 93638-5702 |  | 2014-06-12 | 2014-06-12 14:45 | 2014-06-12 15:07 | YORK - D1NH060N09006C | 140 | 26.6 | Yes | Yes | 25 | 21.5 | 3.5 | 00703F0F5AEA42A49AEDEA8F4D80F9EC |  | R22 | Non-TXV |  | 19% | 0.81 | 36.51% | [5 empty] | Non-TXV | 19%
Merced | CA | 95348-2116 |  | 2014-07-18 | 2014-07-18 09:38 | 2014-07-18 09:59 | GOODMAN - GPG1336070M41AB | 85 | 3.7 | Yes | Yes | 23.7 | 18.2 | 5.5 | 8AF71E497D2248FDA8347803F475BEC3 |  | R410A | TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | TXV | 4.353%
Los Banos | CA | 93635-4718 |  | 2014-06-11 | 2014-06-11 16:31 | 2014-06-11 16:34 | AMERICAN STANDARD - 2A7A4048A100BA | 182 | 6.3 | Yes | Yes | 20.7 | 19.3 | 1.4 | 289E3C1CDCCA4E56B66C2CAF55F149B4 |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Merced | CA | 95340-5659 |  | 2014-07-11 | 2014-07-11 13:28 | 2014-07-11 13:29 | GOODMAN - CFKE24-1AE | 106 | 3.2 | Yes | Yes | 18.3 | 19.6 | -1.3 | BEDA45FDD94E4627B4BCDE96744A5B87 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Dinuba | CA | 93618-3354 |  | 2014-07-16 | 2014-07-16 11:07 | 2014-07-16 11:33 | CARRIER - 585HJWO36060 | 102 | 3.2 | Yes | Yes | 19.7 | 20.6 | -0.9 | 4F1E28E0B3A74538ABA8E24EC8ABA502 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Corning | CA | 96021-9729 |  | 2014-07-07 | 2014-07-07 12:46 | 2014-07-07 13:19 | YORK - H1RA048506B | 115 | 4.3 | Yes | Yes | 23.5 | 20.3 | 3.2 | F4BC2D6D7B0C41359613E11A1486754F |  | R22 | Non-TXV |  | 3.739% | 0.96261 | 7.186% | [5 empty] | Non-TXV | 3.739%
Clovis | CA | 93619-9544 |  | 2014-06-26 | 2014-06-26 12:32 | 2014-06-26 12:52 | RHEEM - RRGF010E60JKR | 138 | 4.5 | Yes | Yes | 23.8 | 21.5 | 2.3 | B8F89785DFBA4BEF8BB9C6D1C20FCBE8 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Clovis | CA | 93619-9544 |  | 2014-06-26 | 2014-06-26 12:54 | 2014-06-26 13:18 | RHEEM - N/A | 90 | 3.5 | Yes | Yes | 21.5 | 21.5 | 0 | 04244EE8D7464DEF9068EA8CD369FFB7 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Corning | CA | 96021-2935 |  | 2014-07-14 | 2014-07-14 08:03 | 2014-07-14 08:50 | RUUD - RRKA=A036JK06X | 62 | 3.9 | Yes | Yes | 16.7 | 19.4 | -2.7 | 56A14D28BA1C49CEA0C58A927A3068F4 |  | R22 | Non-TXV |  | 6.29% | 0.9371 | 12.09% | [5 empty] | Non-TXV | 6.29%
Merced | CA | 95341-5657 |  | 2014-07-07 | 2014-07-07 22:12 | 2014-07-07 22:15 | GOODMAN - CP1E241A | 106 | 5.4 | Yes | Yes | 21.6 | 19.6 | 2 | AED9A9E9B0F54D56BA9C89BCFA317938 |  | R22 | Non-TXV |  | 5.094% | 0.94906 | 9.79% | [5 empty] | Non-TXV | 5.094%
Sonora | CA | 95370-5269 |  | 2014-09-29 | 2014-09-29 12:26 | 2014-09-29 12:44 | CARRIER - 38TH048320 | 128 | 6.1 | Yes | Yes | 24.5 | 19.7 | 4.8 | 9227108ED70C4F7782644946AD6EABB3 |  | R22 | Non-TXV |  | 4.766% | 0.95234 | 9.158% | [5 empty] | Non-TXV | 4.766%
Livingston | CA | 95334-9798 |  | 2014-06-19 | 2014-06-19 12:16 | 2014-06-19 12:35 | RHEEM - RRNA-B036JK06X | 83 | 12.8 | Yes | Yes | 22.8 | 22.1 | 0.7 | 41CEE199C0B6420EA32E075929A88A55 |  | R22 | Non-TXV |  | 15.42% | 0.84578 | 29.64% | [5 empty] | Non-TXV | 15.42%
Stockton | CA | 95210-2287 |  | 2014-06-13 | 2014-06-13 10:11 | 2014-06-13 10:29 | DAY & NIGHT - 585HJ036060ABAF | 102 | -7.2 | Yes | Yes | 22.9 | 20.3 | 2.6 | CE5EF938E0054C419621B359F8E8F4C8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Stockton | CA | 95206-2001 |  | 2014-06-16 | 2014-06-16 12:18 | 2014-06-16 12:44 | CARRIER - N4A324AKB200 | 85 | 9.9 | Yes | Yes | 16.9 | 18.8 | -1.9 | 39AB2773164B4B48BFB16FB28CC0BA8A |  | R410A | TXV |  | 11.65% | 0.88353 | 22.38% | [5 empty] | TXV | 11.65%
Fresno | CA | 93727-4840 |  | 2014-07-08 | 2014-07-08 14:06 | 2014-07-08 14:36 | RHEEM - N/A | 60 | 2.2 | Yes | Yes | 20.9 | 21.5 | -0.6 | D8C2BDC12CB648C0ADDB3687BC2716DD |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Merced | CA | 95340-3102 |  | 2014-07-10 | 2014-07-10 13:39 | 2014-07-10 13:40 | DAY & NIGHT - 565AJ036 | 87 | 3.7 | Yes | Yes | 23 | 20.2 | 2.8 | 425BA2C75072455E98709B8A6ED98620 |  | R22 | Non-TXV |  | 4.253% | 0.95747 | 8.173% | [5 empty] | Non-TXV | 4.253%
Selma | CA | 93662-3828 |  | 2014-06-13 | 2014-06-13 12:54 | 2014-06-13 13:19 | CARRIER - 48SDM024040311 | 89 | 2.8 | Yes | Yes | 21.1 | 22.6 | -1.5 | F6EB2EB45D7D430E90CA0142BFD76B11 |  | R22 | Non-TXV |  | 3.146% | 0.96854 | 6.046% | [5 empty] | Non-TXV | 3.146%
Fresno | CA | 93710-5919 |  | 2014-08-14 | 2014-08-14 10:53 | 2014-08-14 11:12 | BDP - 585A042100YAC | 90 | 4.7 | Yes | Yes | 19.5 | 20.4 | -0.9 | 85A5628301A849288F955FFF20AD4320 |  | R22 | Non-TXV |  | 5.222% | 0.94778 | 10.04% | [5 empty] | Non-TXV | 5.222%
Madera | CA | 93638-0191 |  | 2014-06-09 | 2014-06-09 12:22 | 2014-06-09 12:45 | CARRIER - UNK | 76 | 11.2 | Yes | Yes | 18.9 | 17.1 | 1.8 | 0737185A9F7E49538586795B32EA47CE |  | R22 | Non-TXV |  | 14.74% | 0.85263 | 28.32% | [5 empty] | Non-TXV | 14.74%
Oakhurst | CA | 93644-8744 |  | 2014-07-31 | 2014-07-31 15:21 | 2014-07-31 15:22 | OTHER - 48XP036060311 | 149 | 12 | Yes | Yes | 20.8 | 17.6 | 3.2 | 6A298D469F96467786B210509AA554C0 |  | R410A | Non-TXV |  | 8.054% | 0.91946 | 15.48% | [5 empty] | Non-TXV | 8.054%
Paradise | CA | 95969-4200 |  | 2014-07-31 | 2014-07-31 12:27 | 2014-07-31 12:46 | LENNOX - 12GC036X-75-6PB | 85 | 5.4 | Yes | Yes | 18.8 | 21 | -2.2 | 5E2AE69941C042848188F95864C79CD9 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Placerville | CA | 95667-9384 |  | 2014-08-01 | 2014-08-01 09:01 | 2014-08-01 09:28 | GOODMAN - UNK | 112 | 3.4 | Yes | Yes | 26 | 21.3 | 4.7 | DF1458332EB84F9ABD93E184656A296D |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Placerville | CA | 95667-9384 |  | 2014-08-01 | 2014-08-01 09:18 | 2014-08-01 09:18 | GOODMAN - CKL36-1E | 90 | 0 | Yes | Yes | 27.5 | 21.7 | 5.8 | A3D0E993178447399A4FE86BBF787244 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Placerville | CA | 95667-9384 |  | 2014-08-01 | 2014-08-01 10:13 | 2014-08-01 10:35 | LENNOX - HSXA19-048-230-01 | 141 | -5.6 | Yes | Yes | 21 | 23.7 | -2.7 | 8200D21D2BBE4DFFBC0F44ED8805C1A6 |  | R410A | TXV |  | -3.972% | 1.0397 | 1.112% |  |  |  |  | TXV |  |  | -3.972%
Paradise | CA | 95969-4123 |  | 2014-06-11 | 2014-06-11 13:46 | 2014-06-11 14:03 | OTHER - 38CK024340 | 55 | 7.1 | Yes | Yes | 19 | 20.4 | -1.4 | D13443012EEE45DEA2898D762098E07F |  | R22 | TXV |  | 12.91% | 0.87091 | 24.81% | [5 empty] | TXV | 12.91%
Stockton | CA | 95205-7909 |  | 2014-06-13 | 2014-06-13 14:55 | 2014-06-13 15:21 | BRYANT - 561CJX030-B | 110 | 16.2 | Yes | Yes | 22.5 | 20.9 | 1.6 | BE7C0E17D4524CC2906E67F751DCAA7F |  | R22 | TXV |  | 14.73% | 0.85273 | 28.3% | [5 empty] | TXV | 14.73%
Corning | CA | 96021-3209 |  | 2014-06-16 | 2014-06-16 10:23 | 2014-06-16 10:45 | YORK - H4DB036506A | 86 | 8.6 | Yes | Yes | 24.2 | 21 | 3.2 | AEB7303235AA489AA99E4410C88F9F88 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93726-2227 |  | 2014-06-20 | 2014-06-20 10:13 | 2014-06-20 10:15 | YORK - D1NA036N05606C | 67 | 8.8 | Yes | Yes | 24.9 | 19.3 | 5.6 | 92819D587CCF4D92907A0669E976B79C |  | R22 | Non-TXV |  | 13.13% | 0.86866 | 25.24% | [5 empty] | Non-TXV | 13.13%
Fresno | CA | 93710-6814 |  | 2014-06-20 | 2014-06-20 12:36 | 2014-06-20 13:09 | YORK - D5NZ060N09006NXA | 82 | 3 | Yes | Yes | 28 | 22.1 | 5.9 | A0B54F9A5325494AAA9BA7BC1BD47F54 |  | R410A | TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | TXV | 3.659%