San Jose | CA | 95111-2842 |  | 2013-05-30 | 2013-05-30 20:09 | 2013-05-30 20:09 | CARRIER - 38CKC030340 | 89 | 0 | Yes | Yes | 0.6 | 19.2 | -18.6 | 8481D764F5D14C4782B3C9C6FC7B0055 | Actual Subcooling cannot be negative. Please check entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Union City | CA | 94587-5317 |  | 2013-07-01 | 2013-07-01 08:45 | 2013-07-01 09:18 | YORK - H2RA036S06E | 63 | 10.3 | Yes | Yes | 22.6 | 20.2 | 2.4 | 662683BFDD6242D49C04D4D5533166E3 |  | R22 | Non-TXV |  | 16.35% | 0.83651 | 31.42% | [5 empty] | Non-TXV | 16.35%
Sanger | CA | 93657-3907 |  | 2013-08-05 | 2013-08-05 13:08 | 2013-08-05 14:29 | ARCOAIRE - NAC024AKB1 | 67 | 3.4 | Yes | Yes | 16.9 | 19.8 | -2.9 | 2BE87803E677497989E007581242865B |  | R22 | Non-TXV |  | 5.075% | 0.94925 | 9.752% | [5 empty] | Non-TXV | 5.075%
Selma | CA | 93662-4323 |  | 2013-06-26 | 2013-06-26 16:00 | 2013-06-26 16:29 | GOODMAN - GSC130361GA | 77 | 9.7 | Yes | Yes | 12.6 | 14.5 | -1.9 | 03F1D318B70B4A3A8B8CACF6B6B41431 |  | R22 | Non-TXV |  | 12.6% | 0.87403 | 24.21% | [5 empty] | Non-TXV | 12.6%
Bakersfield | CA | 93308-5670 |  | 2013-05-29 | 2013-05-29 17:34 | 2013-05-29 17:34 | GOODMAN - GSC13031EB | 66 | 0 | Yes | Yes | 18.4 | 21.4 | -3 | 430A8BB1F5FC400398B6080CE0F897ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-6546 |  | 2013-05-28 | 2013-05-28 15:52 | 2013-05-28 16:14 | COPELAND - 541D0018 | 81 | 0 | Yes | Yes | 19.4 | 21.8 | -2.4 | 6C377E6B282644EB8B26293D78F189F0 | Add refrigerant: 14.1 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4369 |  | 2013-07-12 | 2013-07-12 12:36 | 2013-07-12 13:23 | GOODMAN - GPG10420701A | 88 | -6.2 | Yes | Yes | 24.5 | 20.7 | 3.8 | 6F73B992D2A1424EA347F98AC948D497 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Selma | CA | 93662-2126 |  | 2013-06-19 | 2013-06-19 10:32 | 2013-06-19 11:01 | ARCOAIRE - PGAA36D1K4 | 69 | 2.6 | Yes | Yes | 21.3 | 19.5 | 1.8 | AFFA60B062354462B607F24C2FBA1EFB |  | R22 | Non-TXV |  | 3.768% | 0.96232 | 7.241% | [5 empty] | Non-TXV | 3.768%
Sanger | CA | 93657-3905 |  | 2013-08-08 | 2013-08-08 11:07 | 2013-08-08 11:44 | ARCOAIRE - NAC224AKC3 | 86 | 4 | Yes | Yes | 19.6 | 19.3 | 0.3 | C85182D8C8D04E0E9242464504EBE884 |  | R22 | TXV |  | 4.651% | 0.95349 | 8.939% | [5 empty] | TXV | 4.651%
Selma | CA | 93662-4323 |  | 2013-06-18 | 2013-06-18 16:57 | 2013-06-18 17:24 | YORK - H2RC030S06G | 88 | 3.2 | Yes | Yes | 27.9 | 23.4 | 4.6 | 974EB082A00144ABB366FBA47E9C0332 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Sanger | CA | 93657-3907 |  | 2013-08-08 | 2013-08-08 09:38 | 2013-08-08 10:01 | ARCOAIRE - NAC0324AKB2 | 60 | 6.8 | Yes | Yes | 20.4 | 18.8 | 1.6 | 750E9D063F3F4A7B896DE1A09F3CC9A4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.33% | 0.88667 | 21.78% | [5 empty] | Non-TXV | 11.33%
Fresno | CA | 93701-1629 |  | 2013-08-02 | 2013-08-02 15:57 | 2013-08-02 16:35 | GOODMAN - G8C130361GA | 77 | 5.1 | Yes | Yes | 22.2 | 20.4 | 1.8 | EC2627A074834FC3A17E51709A775653 |  | R22 | Non-TXV |  | 6.623% | 0.93377 | 12.73% | [5 empty] | Non-TXV | 6.623%
Fresno | CA | 93701-1629 |  | 2013-08-02 | 2013-08-02 16:36 | 2013-08-02 16:36 | GOODMAN - GSH130301CA | 77 | 0 | Yes | Yes | 35 | 19.9 | 15.1 | B060ECCC4FA34F2B87791AEA3E85AA66 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5672 |  | 2013-05-28 | 2013-05-28 19:11 | 2013-05-28 19:11 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 19.4 | 21.5 | -2.1 | 4A83FD6B3358459CA84031C49DD0B158 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3222 |  | 2013-06-04 | 2013-06-04 14:06 | 2013-06-04 14:24 | YORK - AC048X1021A | 117 | 10.5 | Yes | Yes | 18.9 | 20.7 | -1.8 | 7A28F3E0D52B4DDC84F5E46F84ECC5CB |  | R22 | Non-TXV |  | 8.974% | 0.91026 | 17.25% | [5 empty] | Non-TXV | 8.974%
Fresno | CA | 93722-8637 |  | 2013-08-29 | 2013-08-29 13:34 | 2013-08-29 13:52 | LENNOX - 13ACD03623002 | 111 | 3.9 | Yes | Yes | 19.4 | 19.2 | 0.2 | 22907136E53242D88E1CFDC533EE547C |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Fresno | CA | 93722-8637 |  | 2013-08-29 | 2013-08-29 13:55 | 2013-08-29 14:33 | LENNOX - 13ACD03623002 | 111 | 3.6 | Yes | Yes | 19.9 | 18.6 | 1.3 | 8E4FF87A00C04D19B749147CEC215BFC |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Bakersfield | CA | 93311-9431 |  | 2013-06-28 | 2013-06-28 19:37 | 2013-06-28 19:37 | RUUD - EAFF-061JAZ | 90 | 0 | Yes | Yes | 20.8 | 19.2 | 1.6 | 7FC43993699D4BECA15C8E0C6F0F1946 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3202 |  | 2013-10-02 | 2013-10-02 17:59 | 2013-10-02 17:59 | YORK - AC048X1021A | 117 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 1FC588BBF62B4566AC491E09B5BF24C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5510 |  | 2013-08-02 | 2013-08-02 10:26 | 2013-08-02 10:46 | GOODMAN - GPG13360451AC | 112 | 13 | Yes | Yes | 22.8 | 21.5 | 1.3 | 5D9C1EE643F1413A85F02E91B5CE3601 |  | R22 | Non-TXV |  | 11.61% | 0.88393 | 22.31% | [5 empty] | Non-TXV | 11.61%
Santa Rosa | CA | 95407-4568 |  | 2013-07-11 | 2013-07-11 14:14 | 2013-07-11 14:36 | YORK - H2RA036S06E | 63 | 5.4 | Yes | Yes | 19.9 | 19.8 | 0.1 | 75DCD6A8F039453D8420CA43FDC59282 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Fresno | CA | 93722-8637 |  | 2013-06-19 | 2013-06-19 13:32 | 2013-06-19 14:01 | LENNOX - 13ACD0048-230-02 | 204 | 8.4 | Yes | Yes | 20 | 16.4 | 3.6 | C5417BB375BD4C188782E732C969CC23 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fresno | CA | 93722-9089 |  | 2013-07-12 | 2013-07-12 11:07 | 2013-07-12 12:05 | LENNOX - 12GCS036X75 | 110 | 14.7 | Yes | Yes | 26.9 | 21.1 | 5.8 | 544E62EAD77649019A23FAAF83A3CD7E |  | R22 | Non-TXV |  | 13.36% | 0.86636 | 25.68% | [5 empty] | Non-TXV | 13.36%
Bakersfield | CA | 93308-5669 |  | 2013-05-28 | 2013-05-28 16:48 | 2013-05-28 16:48 | BDP - 561CJ024-C | 69 | 0 | Yes | Yes | 19.7 | 21.6 | -1.9 | 81D8F32C0F914951809DB7448DBFEEA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-1434 |  | 2013-07-08 | 2013-07-08 10:20 | 2013-07-08 10:53 | INTERTHERM - CNS42 | 78 | 17.2 | Yes | Yes | 23.9 | 20.4 | 3.5 | 5CB7943ABBC44B949D416B784EF60CDB |  | R22 | Non-TXV |  | 22.05% | 0.77949 | 42.38% | [5 empty] | Non-TXV | 22.05%
Bakersfield | CA | 93308-5670 |  | 2013-05-29 | 2013-05-29 17:18 | 2013-05-29 17:18 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 20.3 | 20.1 | 0.2 | 60057A5E081C4A89BE3E13F09EC0F023 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5670 |  | 2013-05-28 | 2013-05-28 15:43 | 2013-05-28 15:43 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 19.5 | 22.2 | -2.7 | DF4C4B1AB79647A8B42F08195A174B04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6720 |  | 2013-06-17 | 2013-06-17 14:24 | 2013-06-17 15:29 | - UNK | 80 | 2.6 | Yes | Yes | 23 | 20.1 | 2.9 | 5D6E1513714043258F8F1F2E5925346C |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Byron | CA | 94505-1109 |  | 2013-08-09 | 2013-08-09 09:20 | 2013-08-09 10:51 | RHEEM - RACJ-048JAS | 157 | 9.5 | Yes | Yes | 17.4 | 18.1 | -0.7 | 5CB46052D1B84C66ACDF395789600E8F |  | R22 | Non-TXV |  | 6.051% | 0.93949 | 11.63% | [5 empty] | Non-TXV | 6.051%
Bakersfield | CA | 93311-2745 |  | 2013-06-04 | 2013-06-04 13:06 | 2013-06-04 13:06 | BRYANT - 561CJ036-3 | 70 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | 54561AFC3D2F4D89A729E1B2C163D509 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2285 |  | 2013-06-28 | 2013-06-28 18:50 | 2013-06-28 18:50 | RHEEM - PALA042JAZ | 79 | 0 | Yes | Yes | 20.6 | 19.8 | 0.8 | 9D2B72EB68BF4A41A71998EBC72777F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3904 |  | 2013-06-13 | 2013-06-13 10:48 | 2013-06-13 11:07 | GOODMAN - GPG1330045M41CA | 78 | -4.6 | Yes | Yes | 15.6 | 18.2 | -2.6 | 1CF977DB3F084D57B2CBE78D2C885EC4 |  | R410A | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Fresno | CA | 93722-8637 |  | 2013-07-08 | 2013-07-08 15:07 | 2013-07-08 15:25 | LENNOX - 13ACD036 | 111 | 13.5 | Yes | Yes | 25.6 | 19.9 | 5.7 | 55FE6701707B47EE98C9D74FD32190EC |  | R22 | TXV |  | 12.16% | 0.87838 | 23.37% | [5 empty] | TXV | 12.16%
Fresno | CA | 93722-8637 |  | 2013-07-08 | 2013-07-08 15:35 | 2013-07-08 15:59 | LENNOX - 13ACD036 | 111 | 12 | Yes | Yes | 21.1 | 18.4 | 2.7 | 8862396EB6F14AF58886C8AED1EC9219 |  | R22 | TXV |  | 10.81% | 0.89189 | 20.78% | [5 empty] | TXV | 10.81%
Bakersfield | CA | 93307-8829 |  | 2013-07-30 | 2013-07-30 19:43 | 2013-07-30 19:43 | YORK - D1NP048N0506A | 133 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | 91B0353741D94F5291DD5821706645BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5003 |  | 2013-06-21 | 2013-06-21 19:27 | 2013-06-21 19:27 | YORK - D1NA030N03606C | 76 | 0 | Yes | Yes | 17.5 | 19.3 | -1.8 | F7DC8A00572E477AB50D3A4CE9E274E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3224 |  | 2013-10-24 | 2013-10-24 13:52 | 2013-10-24 13:52 | YORK - AC036X1021A | 63 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 65D69FA6C2CE4384886371DDFBB6DAE5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-4067 |  | 2013-06-03 | 2013-06-03 09:36 | 2013-06-03 09:36 | MONTGOMERY WARD - SRM-51291A | 85 | 0 | Yes | Yes | 15.8 | 18.2 | -2.4 | C3489D32B39E43B098BDD9C59BC4EE91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3221 |  | 2013-10-04 | 2013-10-04 18:48 | 2013-10-04 18:48 | YORK - AC036X1021A | 63 | 0 | Yes | Yes | 21.7 | 21 | 0.7 | 337B86B2F9F743E5AF36CDF6BC438A52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4024 |  | 2013-06-12 | 2013-06-12 13:00 | 2013-06-12 14:39 | GOODMAN - PGB036075-1A | 60 | 4.4 | Yes | Yes | 15.1 | 17.6 | -2.5 | 1F1BB62A68944D2E8C919EE423B4B36E |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Crockett | CA | 94525-1502 |  | 2013-07-12 | 2013-07-12 12:08 | 2013-07-12 12:22 | RHEEM - NA | 84 | 11 | Yes | Yes | 19.4 | 17.6 | 1.8 | 2FDB0A8A60F2408FA22430DA8CB08F3F |  | R22 | Non-TXV |  | 13.1% | 0.86905 | 25.17% | [5 empty] | Non-TXV | 13.1%
Bakersfield | CA | 93311-9451 |  | 2013-10-24 | 2013-10-24 14:43 | 2013-10-24 14:43 | OTHER - FAFF-037JAZ | 94 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 06BF3A7603DA457A98E6C8481C32BCAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9451 |  | 2013-10-24 | 2013-10-24 15:00 | 2013-10-24 15:00 | OTHER - FAFF-030JAZ | 96 | 0 | Yes | Yes | 20.8 | 21.8 | -1 | 995AB46F4DB344DB88E97A9A411D046B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0000 |  | 2013-06-11 | 2013-06-11 09:58 | 2013-06-11 10:35 | LENNOX - 13ACD060230 | 214 | 35 | Yes | Yes | 23.7 | 18.9 | 4.8 | FFB356B0764047C4A5E8282BD7AC27CD |  | R22 | TXV |  | 16.36% | 0.83645 | 31.43% | [5 empty] | TXV | 16.36%
Sebastopol | CA | 95472-4211 |  | 2013-05-31 | 2013-05-31 12:02 | 2013-05-31 12:21 | CARRIER - 38CK3060370 | 130 | 7 | Yes | Yes | 23.4 | 19.8 | 3.6 | FEC36692CB5A4A24B63035F62F882E3A |  | R22 | Non-TXV |  | 5.385% | 0.94615 | 10.35% | [5 empty] | Non-TXV | 5.385%
Selma | CA | 93662-2633 |  | 2013-08-01 | 2013-08-01 12:47 | 2013-08-01 14:24 | GOODMAN - H2RC036S06G | 83 | 5 | Yes | Yes | 24.9 | 22.1 | 2.8 | F090FDAAC1C345AAB4628AD5DDC3C00B |  | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Suisun City | CA | 94585-2141 |  | 2013-06-04 | 2013-06-04 13:11 | 2013-06-04 13:32 | GE - | 50 | -5 | Yes | Yes | 16.1 | 16.4 | -0.3 | AF0F8EAE0DED452DA71500EE41907C30 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Pinedale | CA | 93650-1060 |  | 2013-09-10 | 2013-09-10 13:33 | 2013-09-10 13:53 | WEATHER KING - 13AJA30A01 | 86 | 3.9 | Yes | Yes | 19.6 | 22.3 | -2.7 | F139E378533E43C499522FF606F1D73B |  | R22 | Non-TXV |  | 4.535% | 0.95465 | 8.715% | [5 empty] | Non-TXV | 4.535%
Fresno | CA | 93722-5909 |  | 2013-06-19 | 2013-06-19 14:56 | 2013-06-19 14:56 | NA | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 074A97FECAAA480798D152CE23BDDD17 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6527 |  | 2013-06-26 | 2013-06-26 17:26 | 2013-06-26 17:45 | YORK - H1RA0485S06G | 117 | 27.5 | Yes | Yes | 22.6 | 21.5 | 1.1 | 04C784895C2A413F9D680E9DA2807C9F |  | R22 | Non-TXV |  | 23.5% | 0.76496 | 45.17% | [5 empty] | Non-TXV | 23.5%
Vacaville | CA | 95687-4939 |  | 2013-05-29 | 2013-05-29 10:55 | 2013-05-29 11:16 | BRYANT - 113RNA036-A | 92 | 5.6 | Yes | Yes | 14.6 | 13.9 | 0.7 | F7506298B6FD4389BC462D17681CAB36 |  | R22 | Non-TXV |  | 6.087% | 0.93913 | 11.7% | [5 empty] | Non-TXV | 6.087%
Bakersfield | CA | 93306-4804 |  | 2013-08-13 | 2013-08-13 09:06 | 2013-08-13 09:06 | BDP - 585BJ036-A | 80 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | 823E68FCB8B64FFE895F29A1B5B5C453 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1764 |  | 2013-07-11 | 2013-07-11 10:22 | 2013-07-11 10:49 | BDP - 598AN036-C | 196 | 31.7 | Yes | Yes | 21.1 | 20.1 | 1 | 953BFC02F6664BB78D141601B77BF68B |  | R22 | Non-TXV |  | 16.17% | 0.83827 | 31.08% | [5 empty] | Non-TXV | 16.17%
Bakersfield | CA | 93309-5633 |  | 2013-09-05 | 2013-09-05 23:16 | 2013-09-05 23:16 | BRYANT - 582ANW024AAAD | 56 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 26F0EA31DE2D452D9B167B38234D13F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1293 |  | 2013-09-21 | 2013-09-21 15:52 | 2013-09-21 15:52 | OTHER - UKN | 60 | 0 | Yes | Yes | 22.4 | 22.1 | 0.3 | 9439345C3AE24E8FA752CBF4F3A7E8FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2633 |  | 2013-08-05 | 2013-08-05 16:07 | 2013-08-05 16:07 | OTHER - TGCD36521S1A | 65 | 0 | Yes | Yes | 21 | 17.7 | 3.3 | 55C852777DA74712B602F2F6F534432C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2724 |  | 2013-08-20 | 2013-08-20 09:53 | 2013-08-20 10:25 | DAYTON - SG10B36100 | 108 | 5.1 | Yes | Yes | 18.6 | 21.5 | -2.9 | 2CF1670AFC644848B7CA17B9A1209E20 |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Bakersfield | CA | 93306-3438 |  | 2013-10-15 | 2013-10-15 18:59 | 2013-10-15 18:59 | HEIL - NRGF36DKB03 | 90 | 0 | Yes | Yes | 20.8 | 21.8 | -1 | 1CFEBEA3347A4C579251711DB42024E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5810 |  | 2013-10-01 | 2013-10-01 12:10 | 2013-10-01 12:26 | YORK - D1NA036N05606C | 67 | 5.2 | Yes | Yes | 22.2 | 21.5 | 0.7 | ED774F254EA8469F9139B225E74E7A42 |  | R22 | Non-TXV |  | 7.761% | 0.92239 | 14.92% | [5 empty] | Non-TXV | 7.761%
Vacaville | CA | 95687-5029 |  | 2013-05-28 | 2013-05-28 13:13 | 2013-05-28 14:36 | CARRIER - 38TKB030300 | 76 | 2.4 | Yes | Yes | 15.7 | 13 | 2.7 | B787CACF662B41728D1A08E4894F5899 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Selma | CA | 93662-2633 |  | 2013-06-18 | 2013-06-18 11:57 | 2013-06-18 12:22 | YORK - HBBD-F036SA | 96 | -9 | Yes | Yes | 18.8 | 19 | -0.2 | 8B182D0C5C384D71B61CC54F02441A8C |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
San Jose | CA | 95131-3815 |  | 2013-06-03 | 2013-06-03 20:16 | 2013-06-03 20:16 | CARRIER - 38CKB030300 | 85 | 0 | Yes | Yes | 18.2 | 19.9 | -1.7 | 25C7357588034022846BFF0AF4FBC834 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6209 |  | 2013-09-25 | 2013-09-25 14:30 | 2013-09-25 14:46 | RHEEM - FAFF049JAZ | 163 | 17.1 | Yes | Yes | 18.5 | 20.9 | -2.4 | B3A3252E243A4504ACDB3E7BF140C0E8 |  | R22 | TXV |  | 10.49% | 0.89509 | 20.16% | [5 empty] | TXV | 10.49%
Ukiah | CA | 95482-9401 |  | 2013-08-22 | 2013-08-22 10:04 | 2013-08-22 10:43 | TEMPSTAR - N2A348GKA200 | 121 | 13.2 | Yes | Yes | 23.8 | 19.8 | 4 | BB5D544B4EFE41AFB89FA616E37904DF |  | R22 | Non-TXV |  | 10.91% | 0.89091 | 20.96% | [5 empty] | Non-TXV | 10.91%
Fresno | CA | 93702-3006 |  | 2013-05-30 | 2013-05-30 10:12 | 2013-05-30 10:32 | GOODMAN - PGB036075 | 60 | -4.9 | Yes | Yes | 22.9 | 19.9 | 3 | 4493B5D31BFE4448AC6E566C84D39DD5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.167% | 1.0817 | 2.287% |  |  |  |  | Non-TXV |  |  | -8.167%
Bakersfield | CA | 93309-2720 |  | 2013-09-27 | 2013-09-27 16:44 | 2013-09-27 16:44 | PAYNE - PY3PNA24040NB | 89 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 84CA7D321FBE49B580BA6F3CA34568FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2720 |  | 2013-09-27 | 2013-09-27 16:59 | 2013-09-27 16:59 | PAYNE - PY3PNA24040NB | 89 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | EC3D7A8E3BEA4D71BBE35BE4F73BDCFB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-2041 |  | 2013-06-11 | 2013-06-11 09:29 | 2013-06-11 09:55 | GMC - UKN | 85 | 0 | Yes | Yes | 18 | 20.2 | -2.2 | 5D31055C085348B0BF4EB53354EE3DE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-4212 |  | 2013-10-22 | 2013-10-22 15:38 | 2013-10-22 16:28 | COLEMAN - 6930B801 | 56 | 5.5 | Yes | Yes | 23.9 | 21.3 | 2.6 | D0E7EE0F2B354E0989169BAD839A4D63 |  | R22 | Non-TXV |  | 9.821% | 0.90179 | 18.87% | [5 empty] | Non-TXV | 9.821%
Suisun City | CA | 94585-1857 |  | 2013-06-18 | 2013-06-18 11:18 | 2013-06-18 11:35 | RHEEM - | 85 | 2.6 | Yes | Yes | 16.1 | 18.2 | -2.1 | AAE3C9A3BF2744CD895A091AF05C6FEB |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93705-0744 |  | 2013-06-07 | 2013-06-07 11:13 | 2013-06-07 11:40 | GOODMAN - PG8036075 | 60 | 3.3 | Yes | Yes | 25 | 19.9 | 5.1 | 9444B288480542BEA6439B7EC8F8FEB0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Bakersfield | CA | 93308-2155 |  | 2013-06-05 | 2013-06-05 16:55 | 2013-06-05 16:55 | ICP - PGC030K060A | 52 | 0 | Yes | Yes | 20.1 | 20.4 | -0.3 | 58DB06C8C5644134BEAD9093EFEC1590 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7010 |  | 2013-06-18 | 2013-06-18 13:24 | 2013-06-18 14:01 | PAYNE - PA10JA042-H | 81 | 10.4 | Yes | Yes | 19 | 20.2 | -1.2 | 900FD0121AB446E7A5A028D10117B09D |  | R22 | Non-TXV |  | 12.84% | 0.8716 | 24.67% | [5 empty] | Non-TXV | 12.84%
Fresno | CA | 93725-1418 |  | 2013-06-06 | 2013-06-06 10:33 | 2013-06-06 11:08 | CARRIER - 48SS 036060331 | 67 | 2.3 | Yes | Yes | 21.2 | 20.1 | 1.1 | EA279B2881CB4A6DAAB342B709F062D6 |  | R22 | Non-TXV |  | 3.433% | 0.96567 | 6.597% | [5 empty] | Non-TXV | 3.433%
Kerman | CA | 93630-1225 |  | 2013-08-02 | 2013-08-02 09:46 | 2013-08-02 09:46 | DAY & NIGHT - 568036RCOH | 96 | 11.9 | Yes | Yes | 27.8 | 19.4 | 8.4 | A59BA86BC592412D98555091FCDF2B63 | Add refrigerant: 11.9 oz | R22 | Non-TXV |  | 12.4% | 0.87604 | 23.82% | [5 empty] | Non-TXV | 12.4%
Fresno | CA | 93711-1617 |  | 2013-07-16 | 2013-07-16 16:17 | 2013-07-16 16:17 | YORK - H2RC048S06HA | 120 | 0 | Yes | Yes | 21 | 20.2 | 0.8 | 80B050C630C94B47AD129B3DC8341172 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7334 |  | 2013-06-26 | 2013-06-26 08:21 | 2013-06-26 08:21 | YORK - D1NH042N06506-C | 94 | 0 | Yes | Yes | 20.3 | 19.6 | 0.7 | E37B0373A0B146D9A8FC2A8AD7C1ED81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4830 |  | 2013-07-23 | 2013-07-23 19:16 | 2013-07-23 19:16 | YORK - D1NA030N05606C | 76 | 0 | Yes | Yes | 21.9 | 21.3 | 0.6 | 191047537A2B48F4AC121CDF6D4771DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6534 |  | 2013-07-16 | 2013-07-16 11:26 | 2013-07-16 11:26 | HEIL - NRGF24SSB04 | 53 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 59B462D745F94C21BBDD749CADF7FBFA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6535 |  | 2013-07-16 | 2013-07-16 10:20 | 2013-07-16 10:20 | HEIL - NRGF24DDB04L | 53 | 0 | Yes | Yes | 17.3 | 18.9 | -1.6 | 3CC61759C1E64223B15D9FF37A26E6A8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1869 |  | 2013-09-12 | 2013-09-12 14:41 | 2013-09-12 14:41 | LENNOX - HS253111P | 129 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | AA17AEBDB68A4DEEBD7FB3FC349BFB0E | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1293 |  | 2013-09-21 | 2013-09-21 15:33 | 2013-09-21 15:33 | OTHER - UKN | 60 | 0 | Yes | Yes | 22.4 | 20.7 | 1.8 | 84882650B43A472CAFCED9FA585FB059 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1248 |  | 2013-09-21 | 2013-09-21 18:11 | 2013-09-21 18:11 | OTHER - UKN | 60 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 8FDA31391529417E8895D4688DF2DC48 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3326 |  | 2013-06-21 | 2013-06-21 14:45 | 2013-06-21 15:08 | GOODMAN - GPG13300701BB | 77 | 2.8 | Yes | Yes | 24.2 | 22.5 | 1.7 | EC9188C19D40490BAE002433E95ACFAC |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Bakersfield | CA | 93306-4162 |  | 2013-08-10 | 2013-08-10 15:35 | 2013-08-10 15:35 | CARRIER - UKN | 150 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 1CE81304163D4E70A828E6C7FAD24D19 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1618 |  | 2013-07-08 | 2013-07-08 10:54 | 2013-07-08 10:55 | PAYNE - PA13NR036-H | 83 | -6.8 | Yes | Yes | 16.7 | 17.1 | -0.4 | 1E063641D006404BA931C2E20784445B |  | R22 | Non-TXV |  | -8.193% | 1.0819 | 2.294% |  |  |  |  | Non-TXV |  |  | -8.193%
Bakersfield | CA | 93309-0508 |  | 2013-07-24 | 2013-07-24 15:33 | 2013-07-24 15:33 | YORK - D1NH042N06506C | 94 | 0 | Yes | Yes | 19.8 | 19.8 | 0 | 17154491B4EC4D60950986D825D6914A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4353 |  | 2013-06-12 | 2013-06-12 13:11 | 2013-06-12 13:42 | GOODMAN - GPG13360701A | 112 | 8.4 | Yes | Yes | 25.8 | 19.9 | 5.9 | BBDBB087D646451680A3F224D9C08372 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Bakersfield | CA | 93306-5735 |  | 2013-09-16 | 2013-09-16 14:46 | 2013-09-16 14:46 | ICP - CPCM074K040D | 58 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 2C5C942DFDA14DCA859BE55309FCCC02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7146 |  | 2013-06-13 | 2013-06-13 17:26 | 2013-06-13 17:26 | ICP - PGC036K060D | 71 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | 0677CC21F752430C863F89CC17DCF5E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3097 |  | 2013-06-05 | 2013-06-05 11:12 | 2013-06-05 11:12 | YORK - H1RA048S06D | 117 | 14.3 | Yes | Yes | 20.2 | 19.1 | 1.1 | A353A017492F4AF0BADD3ED5FAC65D01 | Add refrigerant: 14.3 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | Non-TXV | 12.22%
Sanger | CA | 93657-3137 |  | 2013-06-21 | 2013-06-21 16:25 | 2013-06-21 16:46 | OTHER - DAYAF048NO80C | 92 | 4.2 | Yes | Yes | 27.5 | 22 | 5.5 | 9E9076A12981408D80A9DD6C42B82A32 |  | R22 | Non-TXV |  | 4.565% | 0.95435 | 8.773% | [5 empty] | Non-TXV | 4.565%
Sanger | CA | 93657-3137 |  | 2013-06-21 | 2013-06-21 16:48 | 2013-06-21 17:06 | OTHER - DAYAF048NO80C | 92 | 9.5 | Yes | Yes | 22.7 | 21.5 | 1.2 | B05184CEC8604F319151F185C86CE457 |  | R22 | Non-TXV |  | 10.33% | 0.89674 | 19.84% | [5 empty] | Non-TXV | 10.33%
Bakersfield | CA | 93306-7006 |  | 2013-07-23 | 2013-07-23 16:51 | 2013-07-23 16:51 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.7 | 20.9 | 0.8 | 0609B5876B174D5B80739B20BD58CD06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2639 |  | 2013-06-24 | 2013-06-24 15:14 | 2013-06-24 16:18 | OTHER - PGAD36D1K6 | 102 | -7.7 | Yes | Yes | 17.9 | 19.9 | -2 | 8328A600D8FF48FAA3DDA9A182D23904 |  | R22 | TXV |  | -7.549% | 1.0755 | 2.114% |  |  |  |  | TXV |  |  | -7.549%
Sanger | CA | 93657-3564 |  | 2013-06-21 | 2013-06-21 09:27 | 2013-06-21 09:46 | YORK - H2CR036S06G | 83 | 5.6 | Yes | Yes | 24.8 | 19.3 | 5.5 | 82CE407FBEF64F579D7D456FB524D69E |  | R22 | Non-TXV |  | 6.747% | 0.93253 | 12.97% | [5 empty] | Non-TXV | 6.747%
Fresno | CA | 93722-2868 |  | 2013-06-13 | 2013-06-13 11:25 | 2013-06-13 11:50 | CARRIER - 38CKB042300 | 80 | 7 | Yes | Yes | 18.7 | 18.8 | -0.1 | 7A4F6DB0D7B346DD97FEE356529C080A |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Fairfield | CA | 94533-8953 |  | 2013-06-03 | 2013-06-03 11:33 | 2013-06-03 11:55 | OTHER - C1018BBD1V | 61 | 4.2 | Yes | Yes | 18.7 | 16.6 | 2.1 | 74BCBEA5F9D9448EB6E94960142CC3C9 |  | R22 | Non-TXV |  | 6.885% | 0.93115 | 13.23% | [5 empty] | Non-TXV | 6.885%
Coalinga | CA | 93210-3603 |  | 2013-11-08 | 2013-11-08 18:14 | 2013-11-08 18:14 | - | 85 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 29E7703676B34B3A9E4B501D81A56522 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3003 |  | 2013-06-18 | 2013-06-18 12:13 | 2013-06-18 12:33 | GOODMAN - PGB024050 | 52 | 6.8 | Yes | Yes | 21.2 | 21.5 | -0.3 | 8B9EE0789A0B441FA39B2ECD0141164F |  | R22 | Non-TXV |  | 13.08% | 0.86923 | 25.13% | [5 empty] | Non-TXV | 13.08%
Bakersfield | CA | 93308-1098 |  | 2013-10-22 | 2013-10-22 12:17 | 2013-10-22 12:17 | INTERTHERM - CN336E | 45 | 0 | Yes | Yes | 21.4 | 20.6 | 0.8 | 7B6AA1164B624F4A80643ECCE90752A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2633 |  | 2013-06-18 | 2013-06-18 10:42 | 2013-06-18 11:03 | OTHER - GCGD42S21S2A | 66 | -8.2 | Yes | Yes | 17.3 | 12.6 | 4.7 | 5470B16B8AD94463A928BDB047C820FA |  | R22 | Non-TXV |  | -12.42% | 1.1242 | 3.479% |  |  |  |  | Non-TXV |  |  | -12.42%
Fresno | CA | 93702-3003 |  | 2013-08-01 | 2013-08-01 15:15 | 2013-08-01 15:47 | OTHER - PGF036K080B | 71 | 7.1 | Yes | Yes | 18.8 | 21.2 | -2.4 | 939BC487E1D54DB19B24F0BAD6A2A0FC |  | R22 | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Fresno | CA | 93725-0000 |  | 2013-10-08 | 2013-10-08 14:36 | 2013-10-08 15:17 | PAYNE - UNK | 70 | 2.3 | Yes | Yes | 22 | 18.9 | 3.2 | 25A79536EB8F405B91C734ABAF6BE82F |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Bay Point | CA | 94565-6940 |  | 2013-06-26 | 2013-06-26 13:52 | 2013-06-26 14:14 | GOODMAN - GSH130241BA | 122 | 18.2 | Yes | Yes | 13.1 | 13.4 | -0.3 | 3DBF3E3ADEF049E4A05D56B68DD0F67C | Add refrigerant: 12.4 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.92% | 0.85082 | 28.67% | [5 empty] | Non-TXV | 14.92%
Fresno | CA | 93722-9085 |  | 2013-06-14 | 2013-06-14 10:05 | 2013-06-14 11:15 | LENNOX - 12GCS042 | 113 | 4.5 | Yes | Yes | 26.3 | 20.8 | 5.6 | CEECC7F668694A0F97574C94829F92DE |  | R22 | Non-TXV |  | 3.982% | 0.96018 | 7.653% | [5 empty] | Non-TXV | 3.982%
Brentwood | CA | 94513-1994 |  | 2013-07-02 | 2013-07-02 12:59 | 2013-07-02 13:01 | CARRIER - 38CKC060370 | 131 | -7.7 | Yes | Yes | 17.6 | 17.6 | 0 | 980F8096D52E441E8D052ADAA52C032F |  | R22 | Non-TXV |  | -5.878% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.878%
Fresno | CA | 93702-3003 |  | 2013-08-01 | 2013-08-01 15:53 | 2013-08-01 16:38 | GOODMAN - PGB0240501 | 54 | 4.3 | Yes | Yes | 22.6 | 24.8 | -2.2 | 4F15CF6A59B9450592BB33CDEA3A37DB |  | R22 | TXV |  | 7.963% | 0.92037 | 15.3% | [5 empty] | TXV | 7.963%
Vacaville | CA | 95687-6733 |  | 2013-06-07 | 2013-06-07 09:12 | 2013-06-07 09:44 | COLEMAN - BRCS048B | 108 | 14.7 | Yes | Yes | 16.7 | 18.2 | -1.5 | F32DD306C54C488CAE7DB516EED4FD16 |  | R22 | Non-TXV |  | 13.61% | 0.86389 | 26.16% | [5 empty] | Non-TXV | 13.61%
Fresno | CA | 93722-4900 |  | 2013-06-18 | 2013-06-18 13:46 | 2013-06-18 13:46 | GOODMAN - CA36-1A | 73 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 916A42570691492FB8938F0C86DE13EA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1713 |  | 2013-08-26 | 2013-08-26 09:17 | 2013-08-26 09:34 | - UNK | 80 | 2.6 | Yes | Yes | 19.3 | 18.6 | 0.7 | 87C8E02C57FD48E8A4CE00263B88CA64 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Coalinga | CA | 93210-2209 |  | 2013-10-02 | 2013-10-02 12:21 | 2013-10-02 12:59 | YORK - D1NP036N05606A | 108 | 4.4 | Yes | Yes | 21.2 | 19.9 | 1.3 | DA9F7C17D1594C90B753FFEBB0DE4A3C |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Bakersfield | CA | 93304-6995 |  | 2013-06-13 | 2013-06-13 19:10 | 2013-06-13 19:10 | RHEEM - FADC-036JAS | 80 | 0 | Yes | Yes | 18.8 | 21.3 | -2.5 | D72CF154D5E94CB1AD5A1F719CDD561E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6232 |  | 2013-06-28 | 2013-06-28 15:37 | 2013-06-28 15:58 | BRYANT - 563CN036-C | 104 | 3.8 | Yes | Yes | 17.1 | 18.7 | -1.6 | 9223A49B9A904790837417CD5A8AF2B0 |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Fresno | CA | 93722-8641 |  | 2013-06-13 | 2013-06-13 12:10 | 2013-06-13 12:31 | LENNOX - 13ACD060 | 214 | -19.9 | Yes | Yes | 18.8 | 19.7 | -0.9 | B36D02BF2E4A4FD7B78A50B0D90B8F55 |  | R22 | TXV |  | -9.299% | 1.093 | 2.604% |  |  |  |  | TXV |  |  | -9.299%
Fresno | CA | 93711-1622 |  | 2013-07-17 | 2013-07-17 17:33 | 2013-07-17 17:33 | RHEEM - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 2637A02685DA4879BD276C2E69700F75 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1622 |  | 2013-07-17 | 2013-07-17 17:52 | 2013-07-17 17:52 | BDP - 588ANW048080AEAG | 104 | 0 | Yes | Yes | 22 | 21.2 | 0.8 | 23111432F9044B5EB82BC035564AD8A2 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-9466 |  | 2013-06-25 | 2013-06-25 14:50 | 2013-06-25 15:08 | BDP - 5590042PAC | 84 | 20.3 | Yes | Yes | 20.1 | 21.5 | -1.4 | 2EEE3351A7D444328ADB5C5C7444A6C1 |  | R22 | Non-TXV |  | 24.17% | 0.75833 | 46.44% | [5 empty] | Non-TXV | 24.17%
Suisun City | CA | 94585-1764 |  | 2013-06-07 | 2013-06-07 12:52 | 2013-06-07 13:50 | CARRIER - 591ANX030000ABAA | 68 | 9.8 | Yes | Yes | 16.9 | 18.2 | -1.3 | 85ED879F9C4842BB8C2D67C443EB9DF5 |  | R22 | Non-TXV |  | 14.41% | 0.85588 | 27.7% | [5 empty] | Non-TXV | 14.41%
Brentwood | CA | 94513-6454 |  | 2013-10-03 | 2013-10-03 10:49 | 2013-10-03 10:50 | CARRIER - 38BRC030310 | 100 | -7.1 | Yes | Yes | 17.8 | 17 | 0.8 | 134C5226D8744860B29B0624F3B00FE5 |  | R22 | Non-TXV |  | -7.1% | 1.071 | 1.988% |  |  |  |  | Non-TXV |  |  | -7.1%
San Jose | CA | 95127-3704 |  | 2013-06-05 | 2013-06-05 09:57 | 2013-06-05 09:57 | FRIGIDAIRE - FS3BC-048KA | 85 | 0 | Yes | Yes | 21.8 | 21.9 | -0.1 | 6C8FE4D0917445CFBE166D6FC31FAEA3 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3003 |  | 2013-06-18 | 2013-06-18 12:35 | 2013-06-18 13:02 | RHEEM - PGB024050 | 53 | 7.6 | Yes | Yes | 22.1 | 20 | 2.1 | 929DCA0CDA51430B80E0127E5690DEF9 |  | R22 | Non-TXV |  | 14.34% | 0.8566 | 27.56% | [5 empty] | Non-TXV | 14.34%
Fremont | CA | 94539-7495 |  | 2013-07-03 | 2013-07-03 09:34 | 2013-07-03 09:34 | CARRIER - 38CKC048370 | 121 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | D8BE5A3A1C4B4790BAF5FFB05E788CF0 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2170 |  | 2013-06-05 | 2013-06-05 11:22 | 2013-06-05 11:45 | PAYNE - PY3PNA024040NB | 89 | 4.7 | Yes | Yes | 20.3 | 20.4 | -0.1 | 027C0AD447D045E78F46212031880602 |  | R22 | Non-TXV |  | 5.281% | 0.94719 | 10.15% | [5 empty] | Non-TXV | 5.281%
Fresno | CA | 93728-1521 |  | 2013-06-25 | 2013-06-25 09:06 | 2013-06-25 12:16 | OTHER - GCS29036 | 58 | 9.3 | Yes | Yes | 21.7 | 18.6 | 3.2 | 0AA5A73466AF4DB7ACFA191FA86B9E7B |  | R22 | Non-TXV |  | 16.03% | 0.83966 | 30.81% | [5 empty] | Non-TXV | 16.03%
Fresno | CA | 93705-2316 |  | 2013-10-04 | 2013-10-04 12:02 | 2013-10-04 12:02 | AMANA - PGB36C0702D | 64 | 0 | Yes | Yes | 35 | 19.9 | 15.1 | AFE0C490AB634532908710F1CFECBB02 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5130 |  | 2013-06-28 | 2013-06-28 14:55 | 2013-06-28 14:55 | CARRIER - 48SDN048090311 | 196 | 0 | Yes | Yes | 21.5 | 21.7 | -0.2 | 625BA6759014439495F8B6551B4A6467 |  | R22 | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3907 |  | 2013-08-05 | 2013-08-05 14:33 | 2013-08-05 14:59 | ARCOAIRE - UKN | 82 | 5 | Yes | Yes | 20 | 20.9 | -0.9 | 06AB42F200424A2E9CDB220FA54E828D |  | R22 | Non-TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | Non-TXV | 6.098%
San Jose | CA | 95121-1304 |  | 2013-06-06 | 2013-06-06 10:18 | 2013-06-06 11:06 | LENNOX - HS10311V-4P | 90 | 17.5 | Yes | Yes | 20.9 | 19.8 | 1.1 | 26EF5D23B7DD45F1BBC736BFDA480C27 |  | R22 | Non-TXV |  | 19.44% | 0.80556 | 37.37% | [5 empty] | Non-TXV | 19.44%
Antioch | CA | 94509-5638 |  | 2013-07-19 | 2013-07-19 12:04 | 2013-07-19 12:06 | PAYNE - PA13NA042-C | 100 | 8.6 | Yes | Yes | 18.2 | 17.6 | 0.6 | 90EBA120EFA148BEAD5126D913A3B59B |  | R22 | Non-TXV |  | 8.6% | 0.914 | 16.53% | [5 empty] | Non-TXV | 8.6%
Sanger | CA | 93657-3907 |  | 2013-08-13 | 2013-08-13 10:44 | 2013-08-13 11:03 | OTHER - NCA024AKB1 | 67 | 2.5 | Yes | Yes | 17.3 | 18.7 | -1.4 | 403D473AF4BE4C299570655A73051210 |  | R22 | Non-TXV |  | 3.731% | 0.96269 | 7.171% | [5 empty] | Non-TXV | 3.731%
Selma | CA | 93662-9638 |  | 2013-06-17 | 2013-06-17 10:01 | 2013-06-17 10:34 | CARRIER - 486X042090301 | 118 | 22.3 | Yes | Yes | 21.8 | 20.6 | 1.2 | 1D74436926F148C7A722C43F27BD7DAB |  | R22 | Non-TXV |  | 18.9% | 0.81102 | 36.32% | [5 empty] | Non-TXV | 18.9%
Selma | CA | 93662-9638 |  | 2013-06-17 | 2013-06-17 11:07 | 2013-06-17 11:34 | CARRIER - 486X042090301 | 118 | 4 | Yes | Yes | 24.7 | 21.1 | 3.6 | 36D6543D728A4D50ACB60303DCFC1ED2 |  | R22 | Non-TXV |  | 3.39% | 0.9661 | 6.515% | [5 empty] | Non-TXV | 3.39%
Bakersfield | CA | 93308-2166 |  | 2013-06-05 | 2013-06-05 09:27 | 2013-06-05 09:27 | TRANE - 4YCC3024B1064AA | 93 | 0 | Yes | Yes | 19.2 | 18.8 | 0.4 | BD43F4139313490EB12E1FC4DE9F66DD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3908 |  | 2013-08-05 | 2013-08-05 15:04 | 2013-08-05 17:48 | ARCOAIRE - UKN | 82 | 4.7 | Yes | Yes | 18.5 | 19.6 | -1.1 | A91352999FB242CEAED3C329920B4D2B |  | R22 | TXV |  | 5.732% | 0.94268 | 11.02% | [5 empty] | TXV | 5.732%
Sanger | CA | 93657-3908 |  | 2013-08-06 | 2013-08-06 12:01 | 2013-08-06 12:18 | CARRIER - NAC024A1011 | 67 | 7.9 | Yes | Yes | 16.5 | 17.9 | -1.4 | E5F66C9172504B2982285D41D5B84E8A |  | R22 | TXV |  | 11.79% | 0.88209 | 22.66% | [5 empty] | TXV | 11.79%
Fresno | CA | 93725-0920 |  | 2013-07-31 | 2013-07-31 12:18 | 2013-07-31 12:18 | OTHER - 563CNX036000AAAA | 113 | 0 | Yes | Yes | 20.9 | 18.9 | 2.1 | FFEF6E12924C4F828667A5716F05502C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4446 |  | 2013-09-26 | 2013-09-26 09:38 | 2013-09-26 15:43 | AMERICAN STANDARD - YCC030F1M0BC | 72 | -3.9 | Yes | Yes | 15.2 | 15.8 | -0.6 | A9CC9E73A40D4DC0B7DB17B9E7FB7107 |  | R22 | Non-TXV |  | -5.417% | 1.0542 | 1.517% |  |  |  |  | Non-TXV |  |  | -5.417%
Sanger | CA | 93657-3908 |  | 2013-08-06 | 2013-08-06 15:21 | 2013-08-06 15:40 | OTHER - UNK | 64 | -3.8 | Yes | Yes | 18.2 | 18.8 | -0.5 | 328916B9A6784730B0D6481F9C905EDA |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Bakersfield | CA | 93308-1804 |  | 2013-07-10 | 2013-07-10 10:05 | 2013-07-10 10:28 | ICP - PGP330060K00A2 | 89 | 18 | Yes | Yes | 22.7 | 23.1 | -0.4 | 5CC6FEA9CE09408482D95605AC4BE293 |  | R22 | Non-TXV |  | 20.22% | 0.79775 | 38.87% | [5 empty] | Non-TXV | 20.22%
Fresno | CA | 93725-1712 |  | 2013-06-17 | 2013-06-17 18:31 | 2013-06-18 06:17 | OTHER - DAYPF036N070A | 108 | -6.1 | Yes | Yes | 23.3 | 22.8 | 0.6 | 3EB11A18C28541D292AFC60A4CC4BE04 |  | R22 | TXV |  | -5.648% | 1.0565 | 1.582% |  |  |  |  | TXV |  |  | -5.648%
Oakley | CA | 94561-3078 |  | 2013-06-28 | 2013-06-28 08:59 | 2013-06-28 08:59 | PAYNE - PA10JA048-D | 106 | 0 | Yes | Yes | 17.6 | 18.2 | -0.6 | 2560C943895D48759C120501E61C523A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2013-06-07 | 2013-06-07 09:07 | 2013-06-07 09:07 | YORK - D1NP048N06506A | 132 | 0 | Yes | Yes | 19.2 | 19 | 0.3 | BFF7A7DE9807426991D6D30B93C82839 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-5913 |  | 2013-07-01 | 2013-07-01 15:11 | 2013-07-01 15:11 | RHEEM - UKN | 85 | 0 | Yes | Yes | 13.6 | 14.4 | -0.8 | 61959A6CBEB7403F97676E822FDB9760 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-1594 |  | 2013-06-05 | 2013-06-05 12:39 | 2013-06-05 13:24 | BRYANT - 538ANX018000D | 85 | 9 | Yes | Yes | 21.6 | 18.5 | 3.1 | A426CEF6822C4792B6F6099B1DAA59D8 |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Sonoma | CA | 95476-6420 |  | 2013-05-31 | 2013-05-31 16:01 | 2013-05-31 16:01 | OTHER - 567C024RC0 | 60 | 0 | Yes | Yes | 19.7 | 22.1 | -2.4 | 9DA1A68308C44948855212A86E6CD05C | Add refrigerant: 14.7 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95118-2918 |  | 2013-06-05 | 2013-06-05 13:33 | 2013-06-05 14:07 | HEIL - HAC036AKC4 | 85 | 4 | Yes | Yes | 21.2 | 19.3 | 1.9 | 51D3260DB04B4E3BB965C1122512A759 |  | R22 | TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | TXV | 4.706%
Fresno | CA | 93705-3742 |  | 2013-06-04 | 2013-06-04 11:56 | 2013-06-04 12:23 | DAY & NIGHT - 42/116YAC120AK | 124 | 29.6 | Yes | Yes | 18.8 | 21.3 | -2.5 | C4726BD592DA4545A0E783708C193FD9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 23.87% | 0.76129 | 45.87% | [5 empty] | Non-TXV | 23.87%
Fresno | CA | 93722-5562 |  | 2013-07-03 | 2013-07-03 17:02 | 2013-07-03 17:02 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 17.3 | 15 | 2.3 | FA903FCAEFAE44208F5228B80F345D7C | Add refrigerant: 2.4 oz | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Wasco | CA | 93280-3210 |  | 2013-07-31 | 2013-07-31 21:59 | 2013-07-31 22:02 | HEIL - PGC024K060A | 58 | 3.2 | Yes | Yes | 25.3 | 22.1 | 3.2 | C17032FC26134C94BE023A20E60C2801 |  | R22 | Non-TXV |  | 5.517% | 0.94483 | 10.6% | [5 empty] | Non-TXV | 5.517%
Coalinga | CA | 93210-2319 |  | 2013-10-02 | 2013-10-02 11:20 | 2013-10-02 11:45 | DAY & NIGHT - 585EJ030050 | 58 | 3.4 | Yes | Yes | 23.1 | 20.2 | 3 | 387D1AA1AFF34BAAB11176D04331EDF9 |  | R22 | Non-TXV |  | 5.862% | 0.94138 | 11.27% | [5 empty] | Non-TXV | 5.862%
Kerman | CA | 93630-1428 |  | 2013-07-19 | 2013-07-19 17:05 | 2013-07-19 18:02 | RHEEM - UNK | 79 | -4.6 | Yes | Yes | 19 | 18.6 | 0.4 | 1ABD22A79E30433FB8219A15A080DC97 |  | R22 | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Fresno | CA | 93702-2815 |  | 2013-05-31 | 2013-05-31 10:31 | 2013-05-31 11:22 | OTHER - 1DO36MIA | 114 | -10.7 | Yes | Yes | 19 | 20.2 | -1.2 | A0BAE4CBA11E454BBBE5ABB9B5825225 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | -9.386% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.386%
Bakersfield | CA | 93313-3384 |  | 2013-06-20 | 2013-06-20 14:54 | 2013-06-20 14:54 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.3 | 21 | -2.7 | ADE573CD3361477C9A1FE7EA7AACE76F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7501 |  | 2013-06-13 | 2013-06-13 13:10 | 2013-06-13 13:33 | YORK - H1DB036S0A | 72 | 8.3 | Yes | Yes | 21 | 20.2 | 0.9 | 12209FD16EAF4477A4A77FB37BD33DFF |  | R22 | Non-TXV |  | 11.53% | 0.88472 | 22.15% | [5 empty] | Non-TXV | 11.53%
Union City | CA | 94587-1732 |  | 2013-06-07 | 2013-06-07 12:49 | 2013-06-07 12:49 | OTHER - CCU10A36A-1 | 85 | 0 | Yes | Yes | 19.1 | 19.3 | -0.2 | F43B1F20B7F6472299F48E1FF99AD9D3 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1643 |  | 2013-06-03 | 2013-06-03 13:23 | 2013-06-03 13:48 | CARRIER - UNK | 80 | 5.5 | Yes | Yes | 23.1 | 19.5 | 3.6 | 72BD614322AB44A8A07A906CC8935CB2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Fresno | CA | 93705-1123 |  | 2013-06-20 | 2013-06-20 12:26 | 2013-06-20 13:48 | YORK - D2NP036NO5606A | 108 | 6.7 | Yes | Yes | 19.6 | 19.1 | 0.5 | EE81E926BC084200864BD880694F9EAB |  | R22 | TXV |  | 6.204% | 0.93796 | 11.92% | [5 empty] | TXV | 6.204%
Fresno | CA | 93705-1205 |  | 2013-06-03 | 2013-06-03 12:52 | 2013-06-03 12:52 | OTHER - 80AW30106 | 101 | 0 | Yes | Yes | 0 | 18.6 | -18.6 | 786FA1C98FD744138D53FF2311BC4635 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1236 |  | 2013-06-28 | 2013-06-28 17:35 | 2013-06-28 17:35 | BDP - 589ANW042060ADBF | 89 | 0 | Yes | Yes | 18.9 | 20.4 | -1.5 | 8E0AA287C9944BB794AF253E80C00C3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2182 |  | 2013-06-05 | 2013-06-05 11:49 | 2013-06-05 11:49 | TRANE - 4YCC303248108AAA | 93 | 0 | Yes | Yes | 19.9 | 21.4 | -1.5 | BB1047A590DD4C668D25B8436318DE9A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5811 |  | 2013-09-06 | 2013-09-06 00:43 | 2013-09-06 01:02 | AMANA - PGD42C0902E | 120 | 14.9 | Yes | Yes | 21.9 | 21.4 | 0.5 | 918B70A01C584AAD97D8424BF845816D |  | R22 | Non-TXV |  | 12.42% | 0.87583 | 23.86% | [5 empty] | Non-TXV | 12.42%
Fresno | CA | 93705-4808 |  | 2013-06-19 | 2013-06-19 16:46 | 2013-06-19 17:05 | AMERICAN STANDARD - YCX0300F1MOAD | 80 | 9 | Yes | Yes | 26.4 | 21.4 | 5 | 9BFE10E70F8B4145A900CE5104893371 |  | R22 | TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | TXV | 11.25%
Bakersfield | CA | 93308-2182 |  | 2013-06-05 | 2013-06-05 10:05 | 2013-06-05 10:24 | ICP - PGC030K060A | 64 | 3.6 | Yes | Yes | 20.2 | 19.9 | 0.3 | 1191577F77BB41CBB094ED4D8326238D |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Bakersfield | CA | 93308-7860 |  | 2013-07-12 | 2013-07-12 17:34 | 2013-07-12 17:34 | YORK - D1NH030N03606C | 73 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 3581227B6FA44AB88874A9DB2CB39C2D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-8707 |  | 2013-06-13 | 2013-06-13 15:53 | 2013-06-13 16:36 | LENNOX - 12GCS024 | 113 | 8 | Yes | Yes | 26.5 | 21.5 | 5 | 57E6614E1F0E47F7B7302EC1A4F47FBC |  | R22 | Non-TXV |  | 7.08% | 0.9292 | 13.61% | [5 empty] | Non-TXV | 7.08%
San Jose | CA | 95123-2429 |  | 2013-06-10 | 2013-06-10 09:41 | 2013-06-10 09:41 | OTHER - GS3BA-030KA | 85 | 0 | Yes | Yes | 20.4 | 19.3 | 1.1 | CA4139BFD40149CE8160CBA1DDFF669B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8824 |  | 2013-07-30 | 2013-07-30 15:29 | 2013-07-30 16:27 | YORK - D2NP048N06506A | 132 | 25.9 | Yes | Yes | 22.1 | 21.8 | 0.4 | 54B01E5613AA4E2E94C2A8E99D78B311 |  | R22 | Non-TXV |  | 19.62% | 0.80379 | 37.71% | [5 empty] | Non-TXV | 19.62%
San Jose | CA | 95123-2429 |  | 2013-06-06 | 2013-06-06 09:38 | 2013-06-06 09:38 | OTHER - BRCQ0181BE | 85 | 0 | Yes | Yes | 20.4 | 19.1 | 1.3 | DC3B1DE49E374AD69891B9F2D38743F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4468 |  | 2013-08-14 | 2013-08-14 13:44 | 2013-08-14 13:44 | RHEEM - RRNA-B042JK08X | 104 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 1ECD23E68F2F442184CE2B4966D5471C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-1301 |  | 2013-06-06 | 2013-06-06 13:32 | 2013-06-06 14:09 | CARRIER - 38TR048300 | 202 | 23.3 | Yes | Yes | 21 | 19.8 | 1.2 | 180CD390A675486EB98DF5D07DF67A48 |  | R22 | TXV |  | 11.53% | 0.88465 | 22.17% | [5 empty] | TXV | 11.53%
Bakersfield | CA | 93308-9507 |  | 2013-09-19 | 2013-09-19 13:46 | 2013-09-19 13:46 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 74D963C492C94C808FAD8D430FA77499 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5704 |  | 2013-06-12 | 2013-06-12 15:54 | 2013-06-12 16:17 | BRYANT - 550ANX042000AEAA | 140 | 9 | Yes | Yes | 24.1 | 19.3 | 4.8 | 898D192B4EC34CA2844E85D9824AE552 |  | R410A | TXV |  | 6.429% | 0.93571 | 12.35% | [5 empty] | TXV | 6.429%
Fremont | CA | 94536-5528 |  | 2013-06-05 | 2013-06-05 15:06 | 2013-06-06 07:49 | OTHER - 642GKA100 | 190 | 19.4 | Yes | Yes | 23.3 | 18.1 | 5.2 | 62CD26084BD243328D9AD545B2385026 |  | R410A | TXV |  | 10.21% | 0.89789 | 19.62% | [5 empty] | TXV | 10.21%
W Sacramento | CA | 95691-3136 |  | 2013-06-14 | 2013-06-14 13:38 | 2013-06-14 15:27 | PAYNE - 588ANW036080ABAF | 100 | -7.1 | Yes | Yes | 18.2 | 17 | 1.2 | BAFFA0FF4021489788E4217C01A7E92F |  | R22 | Non-TXV |  | -7.1% | 1.071 | 1.988% |  |  |  |  | Non-TXV |  |  | -7.1%
San Jose | CA | 95116-2973 |  | 2013-06-11 | 2013-06-11 12:31 | 2013-06-11 12:31 | CARRIER - 38CKC036330 | 105 | 0 | Yes | Yes | 22.1 | 19.9 | 2.2 | 3E55D3366F4D440C986B6DB2C2B3312B |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4017 |  | 2013-06-12 | 2013-06-12 09:47 | 2013-06-12 10:12 | MILLER - UNK | 80 | 5.2 | Yes | Yes | 23.3 | 19.9 | 3.4 | 99FEFA9B89464F85A62D39D993A9D649 |  | R22 | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Bakersfield | CA | 93307-7660 |  | 2013-06-11 | 2013-06-11 10:54 | 2013-06-11 11:12 | YORK - D1NH042N06506C | 94 | 7.2 | Yes | Yes | 20 | 20.6 | -0.5 | DBA0A920D21845F8B0C849EF4D91656B |  | R22 | Non-TXV |  | 7.66% | 0.9234 | 14.72% | [5 empty] | Non-TXV | 7.66%
Vallejo | CA | 94591-3832 |  | 2013-09-27 | 2013-09-27 11:07 | 2013-09-27 14:07 | CARRIER - 38CKC048370 | 100 | -5.1 | Yes | Yes | 17.9 | 18.3 | -0.4 | C1F2418699074CFCA73F0CFC2C118961 |  | R22 | Non-TXV |  | -5.1% | 1.051 | 1.428% |  |  |  |  | Non-TXV |  |  | -5.1%
Fresno | CA | 93705-3927 |  | 2013-06-20 | 2013-06-20 09:06 | 2013-06-20 10:16 | BDP - J85HJW036060 | 102 | -9.6 | Yes | Yes | 25.1 | 19.9 | 5.2 | 2BA2C1829EC04E58BA5A8F5CA984026E |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93721-2433 |  | 2013-08-30 | 2013-08-30 10:14 | 2013-08-30 10:59 | RUUD - UNK | 100 | 3.9 | Yes | Yes | 22.2 | 20.4 | 1.8 | C8117F770CD44504BF2AA42DDB5BA88E |  | R22 | Non-TXV |  | 3.9% | 0.961 | 7.495% | [5 empty] | Non-TXV | 3.9%
Vacaville | CA | 95688-6934 |  | 2013-06-11 | 2013-06-11 10:02 | 2013-06-11 10:29 | GIBSON - GS3BA-024KA | 64 | -3 | Yes | Yes | 17.9 | 20.4 | -2.5 | 87BDEBFF032F41F3B50E7F38D9CD6C52 |  | R22 | Non-TXV |  | -4.688% | 1.0469 | 1.313% |  |  |  |  | Non-TXV |  |  | -4.688%
Concord | CA | 94518-2845 |  | 2013-06-17 | 2013-06-17 10:26 | 2013-06-17 10:47 | CARRIER - 24ACA442A3000 | 164 | 7.6 | Yes | Yes | 20.8 | 19.9 | 0.9 | 2A5E412ABFE54901800EB4B38B7C9B16 |  | R410A | TXV |  | 4.634% | 0.95366 | 8.906% | [5 empty] | TXV | 4.634%
Bakersfield | CA | 93308-7133 |  | 2013-10-08 | 2013-10-08 18:57 | 2013-10-08 18:57 | YORK - AC060X1223A | 147 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | 9B28079E95404804949C2B3093DDF6E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4141 |  | 2013-05-31 | 2013-05-31 09:13 | 2013-05-31 09:13 | FRIGIDAIRE - UKN | 90 | 0 | Yes | Yes | 15.9 | 18.2 | -2.3 | 5BD99FEF808F4BAEA6F6C35B61E842B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6941 |  | 2013-07-30 | 2013-07-30 13:15 | 2013-07-30 13:15 | ICP - PGD342090K001C1 | 97 | 0 | Yes | Yes | 22.4 | 22 | 0.4 | BC197ABBD9294D3F8FD0749FAEED49DD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1905 |  | 2013-07-05 | 2013-07-05 12:24 | 2013-07-05 12:46 | RHEEM - RRGH-05N30JKR | 79 | -2.9 | Yes | Yes | 20 | 21 | -1 | 93015F779F07427F9409E2CCF92732EC |  | R22 | Non-TXV |  | -3.671% | 1.0367 | 1.028% |  |  |  |  | Non-TXV |  |  | -3.671%
Bakersfield | CA | 93311-1914 |  | 2013-06-27 | 2013-06-27 19:08 | 2013-06-27 19:08 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.3 | 19.3 | -1 | 253597974BD34526A3D97EE2356A8B79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2553 |  | 2013-05-29 | 2013-05-29 17:06 | 2013-05-29 17:06 | DAY & NIGHT - N2A336AKB300 | 88 | 0 | Yes | Yes | 21.8 | 19.9 | 2 | D0ED58715D8240C6926B14A77FBEC4B6 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5668 |  | 2013-05-29 | 2013-05-29 17:59 | 2013-05-29 17:59 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 16.9 | 18.3 | -1.4 | 8CC793C7E2344E438B1A8630C4DEEC4A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5669 |  | 2013-05-28 | 2013-05-28 13:58 | 2013-05-28 14:29 | BDP - 561CJ030-C | 71 | 9.9 | Yes | Yes | 22.6 | 21.9 | 0.7 | 4177676C05424B428636324C2625E9BB |  | R22 | Non-TXV |  | 13.94% | 0.86056 | 26.8% | [5 empty] | Non-TXV | 13.94%
Fresno | CA | 93722-4731 |  | 2013-06-14 | 2013-06-14 13:21 | 2013-06-14 14:09 | YORK - D1NA030N05606C | 76 | 2.6 | Yes | Yes | 21.2 | 19.5 | 1.8 | 0870C80B4722477FBF515908C60B0384 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Bakersfield | CA | 93308-5669 |  | 2013-05-28 | 2013-05-28 15:15 | 2013-05-28 15:15 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 21 | 18.7 | 2.3 | A3CED59550F246848E6A88327E180B07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5669 |  | 2013-05-28 | 2013-05-28 15:39 | 2013-05-28 16:14 | BDP - 561CJ024-C | 69 | 5.9 | Yes | Yes | 20.6 | 22.2 | -1.6 | F5E60716F8DD4971BDB9329163FB7E36 |  | R22 | Non-TXV |  | 8.551% | 0.91449 | 16.43% | [5 empty] | Non-TXV | 8.551%
Bay Point | CA | 94565-1557 |  | 2013-08-05 | 2013-08-05 14:58 | 2013-08-05 15:31 | OTHER - JS3BA-036KA | 64 | 8.3 | Yes | Yes | 22.5 | 19.5 | 3 | 23034D07FEC542888063BE0764EABB55 | Add refrigerant: 15.2 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.97% | 0.87031 | 24.92% | [5 empty] | Non-TXV | 12.97%
Livermore | CA | 94550-7205 |  | 2013-07-01 | 2013-07-01 13:17 | 2013-07-01 13:17 | TRANE - TTB042C100A1 | 97 | 0 | Yes | Yes | 22.6 | 19.8 | 2.8 | A38EE9ACAA3E49758345F4467C14A7AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livermore | CA | 94550-3534 |  | 2013-10-07 | 2013-10-07 12:18 | 2013-10-07 12:19 | BRYANT - 561CJ036-F | 70 | -4.9 | Yes | Yes | 17.6 | 17.3 | 0.4 | 6626D4CAC6744201908AC834F14782E6 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
San Jose | CA | 95111-3966 |  | 2013-06-11 | 2013-06-11 15:04 | 2013-06-11 15:44 | OTHER - RCE36A2A | 85 | 6 | Yes | Yes | 21 | 18.8 | 2.2 | 13B1F25D164A4A9CBB7D4A713D737F18 |  | R22 | TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | TXV | 7.059%
Milpitas | CA | 95035-2457 |  | 2013-06-04 | 2013-06-04 09:16 | 2013-06-04 09:16 | CARRIER - 38CKC030330 | 89 | 0 | Yes | Yes | 20.8 | 18.7 | 2.1 | EE5B92385C5E4BAF91DB7582B491E925 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3836 |  | 2013-07-22 | 2013-07-22 12:37 | 2013-07-22 12:37 | ICP - PGAA24B1K5 | 66 | 0 | Yes | Yes | 21.8 | 20.9 | 0.9 | B0C8B98E0F9A40FD878F736E2D0B3335 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3836 |  | 2013-07-22 | 2013-07-22 12:45 | 2013-07-22 12:45 | AMANA - PGD36C0702E | 110 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | 6A37D34E33FB441095C01EB6CCD6CD5A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2717 |  | 2013-06-20 | 2013-06-20 12:44 | 2013-06-20 12:44 | COLEMAN - 9548C901 | 60 | 0 | Yes | Yes | 19.8 | 20.9 | -1.1 | 057F40436C9647DEA6E1A03FBC79D9D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3336 |  | 2013-09-16 | 2013-09-16 19:12 | 2013-09-16 19:12 | BRYANT - 583ANW036090AAAF | 82 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 295678F16FCF463B8C682ABF71FD793C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-3802 |  | 2013-06-20 | 2013-06-20 11:19 | 2013-06-20 11:19 | GOODMAN - GP61336070M41AC | 85 | 0 | Yes | Yes | 21.4 | 19.7 | 1.7 | 7C625ADE4B2A4709BD5F1EF8371EE881 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-9528 |  | 2013-06-17 | 2013-06-17 12:40 | 2013-06-17 12:40 | OTHER - UNK | 85 | 0 | Yes | Yes | 19.8 | 16 | 3.8 | B0C79A6A36074D19AA8C3F859FF07B2F | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9324 |  | 2013-10-24 | 2013-10-24 13:29 | 2013-10-24 14:43 | CARRIER - 24ABR360A330 | 170 | 13.2 | Yes | Yes | 22.7 | 20.8 | 1.9 | 9588FE85317E4F9F83DA92DF1F092D5C |  | R22 | TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | TXV | 7.765%
Lemoore | CA | 93245-3744 |  | 2013-06-27 | 2013-06-27 10:46 | 2013-06-27 10:46 | YORK - D1NP042N06506A | 150 | 0 | Yes | Yes | 22.5 | 19.7 | 2.8 | DA40DC7ED8A2430AB48A32228F93069A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-6556 |  | 2013-06-17 | 2013-06-17 12:45 | 2013-06-17 13:08 | AMANA - RCB36B2A | 85 | 8.6 | Yes | Yes | 20.5 | 19.9 | 0.6 | 52B62BC7C88044A4B5936BB372EA60C3 |  | R22 | TXV |  | 10.12% | 0.89882 | 19.44% | [5 empty] | TXV | 10.12%
Fresno | CA | 93705-0622 |  | 2013-06-20 | 2013-06-20 10:20 | 2013-06-20 12:21 | DAY & NIGHT - 3680YAC107C | 67 | 6.4 | Yes | Yes | 24.7 | 19.9 | 4.8 | 668D331F18EA434790B99C7282C90D5A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.552% | 0.90448 | 18.36% | [5 empty] | Non-TXV | 9.552%
Fresno | CA | 93722-7136 |  | 2013-07-12 | 2013-07-12 14:33 | 2013-07-12 14:33 | YORK - H1RC048S06A | 80 | 12.3 | Yes | Yes | 28.1 | 17.6 | 10.5 | 863639ADAD544C4BBBD13B93C8FB5FD8 | Add refrigerant: 12.3 oz Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.38% | 0.84625 | 29.55% | [5 empty] | Non-TXV | 15.38%
Bakersfield | CA | 93307-5126 |  | 2013-06-07 | 2013-06-07 19:20 | 2013-06-07 19:20 | TRANE - 4YCC306A1064AB | 124 | 0 | Yes | Yes | 23.9 | 19.5 | 4.4 | 3B1CCD34B10D4B4FADD2639B49BCA405 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1292 |  | 2013-09-21 | 2013-09-21 17:31 | 2013-09-21 17:31 | RHEEM - RRNA-B024JK06X | 70 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 2480DFCF4E1447449D08C0439404F9CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6158 |  | 2013-10-10 | 2013-10-10 15:01 | 2013-10-10 15:01 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | A292FD02C48A489F8862C700343DBA2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3518 |  | 2013-06-20 | 2013-06-20 15:38 | 2013-06-20 16:12 | CARRIER - 8SB0360603 | 64 | 11.6 | Yes | Yes | 24.5 | 21.5 | 3 | D18B8070B65E4EF8A853D31BD3E433AF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.12% | 0.81875 | 34.83% | [5 empty] | Non-TXV | 18.12%
Sanger | CA | 93657-3720 |  | 2013-08-01 | 2013-08-01 09:53 | 2013-08-01 10:11 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 22.5 | 22.5 | 0 | 69B71E175A6442489438F208D5F2E35A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93308-2429 |  | 2013-07-29 | 2013-07-29 05:10 | 2013-07-29 05:10 | PAYNE - PYG3NAA24040NA | 77 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 9B2733484D694EB98F88DBDD349697F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1851 |  | 2013-07-02 | 2013-07-02 09:26 | 2013-07-02 09:26 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 16.4 | 17.3 | -0.9 | A3EA792A5D3340B9A41D97F08C190A91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-9787 |  | 2013-06-03 | 2013-06-03 09:38 | 2013-06-03 09:38 | GMC - CKJ48-1A | 118 | 0 | Yes | Yes | 12.1 | 13.7 | -1.6 | D88CFD6A277E475CB4C42815A0180761 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corcoran | CA | 93212-9799 |  | 2013-08-05 | 2013-08-05 09:38 | 2013-08-05 09:58 | TEMPSTAR - PGF354100K01A1 | 212 | 8.5 | Yes | Yes | 25.7 | 20.7 | 5 | AB90A1C9B329492AA57A75D488FED542 |  | R22 | TXV |  | 4.009% | 0.95991 | 7.705% | [5 empty] | TXV | 4.009%
Anderson | CA | 96007-2930 |  | 2013-07-08 | 2013-07-08 11:25 | 2013-07-08 12:02 | AMANA - PG036C0702E | 110 | 4.7 | Yes | Yes | 27 | 21.2 | 5.9 | 580CD5866F6A4C468D49EA60FD17348F |  | R22 | Non-TXV |  | 4.273% | 0.95727 | 8.211% | [5 empty] | Non-TXV | 4.273%
Sanger | CA | 93657-2904 |  | 2013-06-24 | 2013-06-24 09:49 | 2013-06-24 10:13 | CARRIER - UNK | 85 | 7.1 | Yes | Yes | 19.1 | 17.7 | 1.4 | 817DE45130774D6CA462449C63AD3D60 |  | R22 | Non-TXV |  | 8.353% | 0.91647 | 16.05% | [5 empty] | Non-TXV | 8.353%
Woodland | CA | 95695-2632 |  | 2013-06-13 | 2013-06-13 09:25 | 2013-06-13 09:42 | PAYNE - PY3PNA030040NB | 96 | 5.2 | Yes | Yes | 17.4 | 17.6 | -0.2 | C72B2D181C034C93880F3B73EE7EE5FB |  | R410A | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Vacaville | CA | 95687-5112 |  | 2013-05-28 | 2013-05-28 14:38 | 2013-05-28 15:29 | GOODMAN - CKL49-1 | 109 | 3.9 | Yes | Yes | 13.5 | 12.8 | 0.7 | EC1EC2E7DC9C40C18B21AFB97B4AE1AC |  | R22 | Non-TXV |  | 3.578% | 0.96422 | 6.876% | [5 empty] | Non-TXV | 3.578%
Oakley | CA | 94561-1836 |  | 2013-07-08 | 2013-07-08 09:09 | 2013-07-08 09:12 | RHEEM - 13AJN36A01 | 150 | -10.6 | Yes | Yes | 18.6 | 18.2 | 0.4 | E53ADD49A21543EDA2CDCBDBECA1B4CF |  | R410A | Non-TXV |  | -7.067% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.067%
Bakersfield | CA | 93308-7845 |  | 2013-07-12 | 2013-07-12 16:59 | 2013-07-12 16:59 | GOODMAN - PGB030050-1 | 56 | 0 | Yes | Yes | 21 | 20.9 | 0.1 | 3175574D0EEC4AC697028CC17770B1D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1974 |  | 2013-07-08 | 2013-07-08 14:22 | 2013-07-08 14:55 | CARRIER - 48GX036060301 | 85 | 5.5 | Yes | Yes | 22.7 | 19.7 | 3 | 5A9F875D1D2F4DD4A2B6E42E67F65C98 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
San Jose | CA | 95138-1738 |  | 2013-06-11 | 2013-06-11 11:33 | 2013-06-11 12:25 | OTHER - BRCS0481BD | 117 | 4.7 | Yes | Yes | 22.9 | 19.9 | 3 | 42AA423FA7644D149764CF440D05C8F1 |  | R22 | Non-TXV |  | 4.017% | 0.95983 | 7.72% | [5 empty] | Non-TXV | 4.017%
Bakersfield | CA | 93308-9507 |  | 2013-09-19 | 2013-09-19 14:14 | 2013-09-19 14:31 | ICP - PGC024K060A | 58 | 6.6 | Yes | Yes | 21.9 | 21.4 | 0.5 | 138583CC39FD4298AF1330F9D562644C |  | R22 | Non-TXV |  | 11.38% | 0.88621 | 21.87% | [5 empty] | Non-TXV | 11.38%
Fresno | CA | 93702-3431 |  | 2013-05-31 | 2013-05-31 16:15 | 2013-05-31 16:42 | CARRIER - 43NLT030300 | 88 | 7.6 | Yes | Yes | 22.7 | 22.6 | 0.1 | 290A67AAD666475F8A5D90DC46B91D92 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.636% | 0.91364 | 16.6% | [5 empty] | Non-TXV | 8.636%
Bakersfield | CA | 93304-4215 |  | 2013-07-02 | 2013-07-02 17:44 | 2013-07-02 17:44 | ICP - PGAA36C1K3 | 81 | 0 | Yes | Yes | 18.6 | 18.3 | 0.3 | 5F9525723EBA42489A235B93485E292F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1738 |  | 2013-06-04 | 2013-06-04 14:18 | 2013-06-04 15:19 | GE - BTN930A100A0 | 150 | -4 | Yes | Yes | 16.1 | 15.8 | 0.3 | B77E29752FFF4B20B42363EC15893AB7 |  | R22 | Non-TXV |  | -2.667% | 1.0267 | 0.7468% |  |  |  |  | Non-TXV |  |  | -2.667%
Fresno | CA | 93725-1868 |  | 2013-06-17 | 2013-06-17 14:17 | 2013-06-17 14:37 | LENNOX - HS25411 | 129 | 12.6 | Yes | Yes | 26.5 | 22.8 | 3.7 | 744A069CAECA4DDB8E6889D384B433F7 |  | R22 | Non-TXV |  | 9.767% | 0.90233 | 18.77% | [5 empty] | Non-TXV | 9.767%
Cottonwood | CA | 96022-7765 |  | 2013-06-25 | 2013-06-25 10:57 | 2013-06-25 11:23 | TEMPSTAR - 4WCZ6060A1000BA | 151 | -10.7 | Yes | Yes | 19.4 | 21 | -1.6 | 2FA658B3002F4602920B06C7D17A9C04 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | -7.086% | 1.0709 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.086%
Bakersfield | CA | 93308-9508 |  | 2013-09-19 | 2013-09-19 14:56 | 2013-09-19 14:56 | TRANE - 4YCC304B106AA | 58 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | F2510023DC9146098E1C2988F8DA8527 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1634 |  | 2013-09-12 | 2013-09-12 12:19 | 2013-09-12 13:46 | PAYNE - 585B042100YACR | 59 | 4.1 | Yes | Yes | 20.7 | 19.9 | 0.8 | 37CDF2D9AD1B42CEB53EE5D1D0F03066 |  | R22 | Non-TXV |  | 6.949% | 0.93051 | 13.35% | [5 empty] | Non-TXV | 6.949%
Vacaville | CA | 95687-4681 |  | 2013-06-03 | 2013-06-03 12:49 | 2013-06-03 13:14 | CARRIER - 38CK048310 | 108 | 3.6 | Yes | Yes | 17.5 | 20.2 | -2.7 | 0F269CD17C0143339E9A5929FC1AA5A8 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Davis | CA | 95616-0965 |  | 2013-06-19 | 2013-06-19 11:11 | 2013-06-19 11:11 | TRANE - TTX042C100A1 | 142 | 0 | Yes | Yes | 15.6 | 18.2 | -2.6 | CFFAA94074534BE08D76D075BADE89F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-7714 |  | 2013-06-26 | 2013-06-26 13:40 | 2013-06-26 14:13 | TRANE - YCY036G1MOAD | 130 | -9.2 | Yes | Yes | 21.4 | 20.4 | 1 | 36EE2265EE9E49B4BAB5BB006CD05BA2 |  | R22 | Non-TXV |  | -7.077% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.077%
Morgan Hill | CA | 95037-7513 |  | 2013-07-30 | 2013-07-30 12:23 | 2013-07-30 13:03 | RHEEM - RAKA-060JAZ | 85 | 12.2 | Yes | Yes | 21.1 | 18.2 | 2.9 | FAFE36C5C8494ED0946E6D221EE2BEBE |  | R22 | Non-TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | Non-TXV | 14.35%
Livermore | CA | 94550-5941 |  | 2013-10-07 | 2013-10-07 10:24 | 2013-10-07 10:24 | TEMPSTAR - PGAA36C1K4 | 80 | 0 | Yes | Yes | 15 | 15.7 | -0.7 | 35B878152C434A48BF3A80B9DF8BBAAD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3519 |  | 2013-06-24 | 2013-06-24 14:58 | 2013-06-24 15:15 | YORK - AC042X1021A | 84 | 18.3 | Yes | Yes | 19.5 | 19.8 | -0.3 | D1EC2B535E6F499986CCCA9D9BE06003 |  | R22 | Non-TXV |  | 21.79% | 0.78214 | 41.87% | [5 empty] | Non-TXV | 21.79%
San Jose | CA | 95131-2638 |  | 2013-06-06 | 2013-06-06 11:13 | 2013-06-06 11:55 | CARRIER - 24ACA436A300 | 193 | 8.2 | Yes | Yes | 20.1 | 19.3 | 0.8 | D3C25878B6694FF2BFF98D1A0ED38D9A |  | R410A | TXV |  | 4.249% | 0.95751 | 8.165% | [5 empty] | TXV | 4.249%
Bakersfield | CA | 93306-3845 |  | 2013-07-22 | 2013-07-22 14:04 | 2013-07-22 14:04 | RUUD - UACB 036JAQ | 35 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | 71F8958C4E72437CA382DEAB69BCA32A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3204 |  | 2013-09-27 | 2013-09-27 12:18 | 2013-09-27 12:18 | CARRIER - 48NMX036 | 90 | 0 | Yes | Yes | 22.6 | 19.7 | 2.9 | C02F85B1A0FE4751A1BC9C6F8E602A22 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3204 |  | 2013-09-27 | 2013-09-27 12:52 | 2013-09-27 12:52 | CARRIER - UKN | 90 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 6CA42B10895142BA9ACEAD2E18DE598F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4937 |  | 2013-06-07 | 2013-06-07 15:53 | 2013-06-07 16:13 | YORK - UNK | 80 | 2.7 | Yes | Yes | 21.8 | 20.2 | 1.6 | 7C97949340CF414A914BCEE35712E63B |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Fresno | CA | 93705-4937 |  | 2013-06-07 | 2013-06-07 16:18 | 2013-06-07 16:35 | YORK - UNK | 80 | 19.2 | Yes | Yes | 23.5 | 20.6 | 2.9 | 80F5946050134574B0AAFC003BE896A5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 24% | 0.76 | 46.12% | [5 empty] | Non-TXV | 24%
Bakersfield | CA | 93308-9507 |  | 2013-09-19 | 2013-09-19 17:22 | 2013-09-19 17:22 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.4 | 20.9 | 0.5 | 822D2404B2B744DC96EDD996A1FF23E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3240 |  | 2013-06-27 | 2013-06-27 12:59 | 2013-06-27 14:20 | YORK - AC0421X1021A | 84 | 20.6 | Yes | Yes | 23.2 | 22.4 | 0.8 | 575E81B292834C0994595711C3E01DB1 |  | R22 | Non-TXV |  | 24.52% | 0.75476 | 47.13% | [5 empty] | Non-TXV | 24.52%
Fresno | CA | 93722-4900 |  | 2013-06-18 | 2013-06-18 14:29 | 2013-06-18 14:29 | COLEMAN - 9548-90 | 71 | 6.3 | Yes | Yes | 25.4 | 18.2 | 7.2 | 94A3FAE8A0664DB0B7783B54727B18EC | Add refrigerant: 6.3 oz | R22 | Non-TXV |  | 8.873% | 0.91127 | 17.05% | [5 empty] | Non-TXV | 8.873%
Rohnert Park | CA | 94928-4824 |  | 2013-09-16 | 2013-09-16 13:13 | 2013-09-16 13:15 | YORK - H1D1B060506A | 122 | 10 | Yes | Yes | 18 | 17.6 | 0.4 | 6294361999804775AB0C8691F34CE682 |  | R22 | Non-TXV |  | 8.197% | 0.91803 | 15.75% | [5 empty] | Non-TXV | 8.197%
Bakersfield | CA | 93311-2519 |  | 2013-06-21 | 2013-06-21 17:58 | 2013-06-21 18:21 | DAY & NIGHT - 580AB060080 | 154 | 24.4 | Yes | Yes | 23.1 | 20.8 | 2.3 | 767F89AF37D3439AB54F54DEBFC95D0C |  | R22 | Non-TXV |  | 15.84% | 0.84156 | 30.45% | [5 empty] | Non-TXV | 15.84%
Oakley | CA | 94561-5006 |  | 2013-06-28 | 2013-06-28 10:10 | 2013-06-28 11:00 | CARRIER - 38YG024300 | 72 | 3 | Yes | Yes | 16.5 | 16.1 | 0.4 | F1C3FD3C64DB43DEBCDAD6DEFCBEFCD5 |  | R22 | TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | TXV | 4.167%
Bakersfield | CA | 93308-5672 |  | 2013-05-28 | 2013-05-28 19:08 | 2013-05-28 19:08 | BDP - 561CJ024-C | 69 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | BA69B8C5765A4424A850924CAF56E4B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5670 |  | 2013-05-28 | 2013-05-28 16:20 | 2013-05-28 16:20 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 17.6 | 20.3 | -2.7 | 0C7D48368700464D8BE9FEDA180D5E46 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-6669 |  | 2013-06-18 | 2013-06-18 13:47 | 2013-06-18 16:45 | RHEEM - NA | 62 | 16.1 | Yes | Yes | 19.3 | 18.2 | 1.1 | 41FE6D8F2BBC42439E760EBECE31A9B5 |  | R22 | Non-TXV |  | 25.97% | 0.74032 | 49.9% | [5 empty] | Non-TXV | 25.97%
Kingsburg | CA | 93631-1300 |  | 2013-07-15 | 2013-07-15 13:20 | 2013-07-15 13:54 | CARRIER - UNK | 67 | 13.1 | Yes | Yes | 20.2 | 21.4 | -1.2 | 0BFC96D965664BBFA467EA97D636A15B |  | R22 | Non-TXV |  | 19.55% | 0.80448 | 37.58% | [5 empty] | Non-TXV | 19.55%
Bakersfield | CA | 93308-5675 |  | 2013-05-31 | 2013-05-31 18:18 | 2013-05-31 18:18 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | 993C883E37B14DBD87011B334F8399D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3243 |  | 2013-08-09 | 2013-08-09 14:54 | 2013-08-09 14:54 | OTHER - UKN | 81 | 0 | Yes | Yes | 35.5 | 20.7 | 14.8 | D3076491DC754C3DA6251EACB782193D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5675 |  | 2013-05-30 | 2013-05-30 18:05 | 2013-05-30 18:22 | BDP - 561CJ030-C | 68 | 6.7 | Yes | Yes | 18.1 | 19.2 | -1.1 | 65828BC2A5134DC29C15E07FB6A2FD35 |  | R22 | Non-TXV |  | 9.853% | 0.90147 | 18.94% | [5 empty] | Non-TXV | 9.853%
Livermore | CA | 94550-4933 |  | 2013-09-13 | 2013-09-13 12:27 | 2013-09-13 12:27 | CARRIER - 38TK042300 | 164 | 0 | Yes | Yes | 21.7 | 23.2 | -1.5 | 27DC0111159945C68D061CF0D48629AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1822 |  | 2013-08-02 | 2013-08-02 09:17 | 2013-08-02 09:17 | - 591ANX048000ABAA | 116 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | DA6DC54C66FA40609524FAF8F959A76A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-2626 |  | 2013-10-15 | 2013-10-15 13:04 | 2013-10-15 14:23 | YORK - D2NP030N5606A | 73 | 3.1 | Yes | Yes | 23 | 20.4 | 2.7 | B08E217F0BC04931B1DC7D1C7E65D27C |  | R22 | Non-TXV |  | 4.247% | 0.95753 | 8.161% | [5 empty] | Non-TXV | 4.247%
Kingsburg | CA | 93631-1300 |  | 2013-07-12 | 2013-07-12 13:41 | 2013-07-12 14:05 | CARRIER - UNK | 70 | 10.2 | Yes | Yes | 20.9 | 20.3 | 0.7 | CBCD61BAE1744FC2B72AF425178726D6 |  | R22 | Non-TXV |  | 14.57% | 0.85429 | 28% | [5 empty] | Non-TXV | 14.57%
Woodland | CA | 95695-4813 |  | 2013-06-13 | 2013-06-13 11:09 | 2013-06-13 11:36 | CARRIER - 38TXA036340 | 108 | 6.9 | Yes | Yes | 16.1 | 17.1 | -1 | F7F8DD287D424E33BF2B0D89494E4B87 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | Non-TXV | 6.389%
Bakersfield | CA | 93311-1469 |  | 2013-06-04 | 2013-06-04 10:31 | 2013-06-04 10:48 | YORK - D1NH036N05606C | 108 | 5.7 | Yes | Yes | 21.5 | 19.8 | 1.7 | 37F70BFE19D8490A80E05BDB634FC4BB |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Corcoran | CA | 93212-1515 |  | 2013-07-05 | 2013-07-05 09:33 | 2013-07-05 09:51 | GOODMAN - UNK | 132 | 12.2 | Yes | Yes | 17.9 | 16.6 | 1.3 | 3A1F48C7D5ED458C8BC62E35B51C848B |  | R22 | Non-TXV |  | 9.242% | 0.90758 | 17.76% | [5 empty] | Non-TXV | 9.242%
Bakersfield | CA | 93312-5315 |  | 2013-08-16 | 2013-08-16 13:37 | 2013-08-16 13:37 | OTHER - 3893E03345 | 88 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 35CC7AD6C45744A4BF06C9449FA0E57D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3441 |  | 2013-05-31 | 2013-05-31 15:12 | 2013-05-31 15:45 | TRANE - YCY036F1M0AA | 137 | 12.9 | Yes | Yes | 24.2 | 20.7 | 3.5 | E2EA56A745824F9D96C0D1F43ADCE3F9 |  | R22 | TXV |  | 9.416% | 0.90584 | 18.1% | [5 empty] | TXV | 9.416%
Sebastopol | CA | 95472-5344 |  | 2013-10-22 | 2013-10-22 22:56 | 2013-10-22 22:56 | AMERICAN STANDARD - 7A0030A100A0 | 74 | 0 | Yes | Yes | 16.5 | 17 | -0.5 | AD9F446C810741AB91471B6969680CD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6607 |  | 2013-08-17 | 2013-08-17 17:50 | 2013-08-17 17:50 | YORK - AC042X1021A | 82 | 0 | Yes | Yes | 22.1 | 21 | 1.1 | 1BE321C76DA74042A7E043AFDCCF778A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2656 |  | 2013-06-17 | 2013-06-17 10:33 | 2013-06-17 11:21 | HEIL - NAC024AKC3 | 71 | -5 | Yes | Yes | 17.2 | 18.2 | -1 | D2CF413AD30340268D237D2AC8B400F9 |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
San Jose | CA | 95111-3333 |  | 2013-06-06 | 2013-06-06 12:00 | 2013-06-06 12:00 | DAY & NIGHT - N4A348AKB200 | 85 | 0 | Yes | Yes | 19 | 18.2 | 0.8 | 662156BBAD344A549D6E23F62539F4E7 |  | R410A | TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-3515 |  | 2013-07-03 | 2013-07-03 10:40 | 2013-07-03 11:12 | OTHER - 4091E05920 | 168 | 16 | Yes | Yes | 24.6 | 20.4 | 4.2 | 5353AA391F4844D187D9BB09F0F7A911 |  | R22 | Non-TXV |  | 9.524% | 0.90476 | 18.3% | [5 empty] | Non-TXV | 9.524%
Lemoore | CA | 93245-3659 |  | 2013-07-08 | 2013-07-08 11:42 | 2013-07-08 11:42 | GOODMAN - GPG13442070M41BA | 81 | 0 | Yes | Yes | 25.4 | 19.9 | 5.5 | C123BA69E8D94935AB2B3FDA806C7B42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livermore | CA | 94551-6135 |  | 2013-06-20 | 2013-06-20 12:32 | 2013-06-20 13:04 | BDP - 565BJ036-A | 85 | 14.9 | Yes | Yes | 24.1 | 20.4 | 3.7 | 0857AB4216A94BFA87469A893CEE3AFB |  | R22 | Non-TXV |  | 17.53% | 0.82471 | 33.69% | [5 empty] | Non-TXV | 17.53%
Bakersfield | CA | 93304-1245 |  | 2013-09-21 | 2013-09-21 16:31 | 2013-09-21 16:50 | YORK - DBRF024045 | 105 | 8.8 | Yes | Yes | 20.1 | 20.9 | -0.8 | ABEF4EEC8E4E418ABB670486E3CFFFA6 |  | R22 | Non-TXV |  | 8.381% | 0.91619 | 16.11% | [5 empty] | Non-TXV | 8.381%
Bakersfield | CA | 93308-1336 |  | 2013-07-10 | 2013-07-10 17:53 | 2013-07-10 17:53 | TRANE - YCY042G1M0AB | 85 | 0 | Yes | Yes | 19.4 | 20.1 | -0.7 | C34227CB756947A7BB01AD7708D4FE81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2436 |  | 2013-06-19 | 2013-06-19 11:57 | 2013-06-19 12:42 | YORK - D1NA036N05606C | 67 | 7 | Yes | Yes | 27.6 | 21.9 | 5.7 | 89754DF1343B4853984AE4D5B56E47E4 |  | R22 | Non-TXV |  | 10.45% | 0.89552 | 20.08% | [5 empty] | Non-TXV | 10.45%
Arvin | CA | 93203-1036 |  | 2013-08-21 | 2013-08-21 12:43 | 2013-08-21 12:59 | ICP - PGAD36D1KE | 136 | 4.7 | Yes | Yes | 20.9 | 19.5 | 1.4 | BAB5CDFB77EE47DF8B2194C523907F9A |  | R22 | Non-TXV |  | 3.456% | 0.96544 | 6.641% | [5 empty] | Non-TXV | 3.456%
Redding | CA | 96003-8910 |  | 2013-09-05 | 2013-09-05 14:48 | 2013-09-05 15:32 | CARRIER - 38CKC042310 | 93 | 4.9 | Yes | Yes | 27.3 | 23 | 4.3 | 68B539B85ADD4BF6AC4E96B5215F2D32 |  | R22 | Non-TXV |  | 5.269% | 0.94731 | 10.13% | [5 empty] | Non-TXV | 5.269%
Kingsburg | CA | 93631-1300 |  | 2013-07-12 | 2013-07-12 13:06 | 2013-07-12 13:33 | CARRIER - UNK | 70 | 7.8 | Yes | Yes | 20.2 | 19.3 | 0.9 | 02296EDA5D084B03ADD769164A79D03F |  | R22 | Non-TXV |  | 11.14% | 0.88857 | 21.41% | [5 empty] | Non-TXV | 11.14%
Pittsburg | CA | 94565-2328 |  | 2013-07-18 | 2013-07-18 12:05 | 2013-07-18 12:07 | TRANE - 2TTR4036A1000AA | 118 | 18.7 | Yes | Yes | 19.3 | 17.6 | 1.7 | 99818523156146D283D1F1CDC2BD4922 |  | R22 | Non-TXV |  | 15.85% | 0.84153 | 30.46% | [5 empty] | Non-TXV | 15.85%
Biola | CA | 93722-0000 |  | 2013-07-18 | 2013-07-18 09:53 | 2013-07-18 10:21 | GOODMAN - GSC130301AE | 117 | 13.2 | Yes | Yes | 16.8 | 19.4 | -2.6 | 1D71DCDA30294347A782D7470C9E8FBE |  | R22 | TXV |  | 11.28% | 0.88718 | 21.68% | [5 empty] | TXV | 11.28%
Kingsburg | CA | 93631-1700 |  | 2013-07-12 | 2013-07-12 16:21 | 2013-07-12 16:53 | RHEEM - RAKA0483AG | 103 | 4.6 | Yes | Yes | 24.1 | 19.3 | 4.8 | C7ADF705450F4BC7BC4319D7B3069090 |  | R22 | Non-TXV |  | 4.466% | 0.95534 | 8.583% | [5 empty] | Non-TXV | 4.466%
Bakersfield | CA | 93308-9509 |  | 2013-09-19 | 2013-09-19 16:40 | 2013-09-19 16:58 | ICP - PGC024K060A | 58 | 6.9 | Yes | Yes | 22 | 20.9 | 1.1 | 1C30963BCB3344878C5D16C9DD58D536 |  | R22 | Non-TXV |  | 11.9% | 0.88103 | 22.86% | [5 empty] | Non-TXV | 11.9%
Fresno | CA | 93711-2255 |  | 2013-06-20 | 2013-06-20 14:20 | 2013-06-20 14:20 | YORK - D1ND060N09006A | 142 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D19133585EFE446F9D17857189E2BAEE | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1757 |  | 2013-05-30 | 2013-05-30 12:27 | 2013-05-30 12:45 | ICP - PGME6061152 | 215 | 11.9 | Yes | Yes | 18.5 | 19.7 | -1.2 | ABC266EE863A492282B596790DCB3383 |  | R22 | Non-TXV |  | 5.535% | 0.94465 | 10.64% | [5 empty] | Non-TXV | 5.535%
Fresno | CA | 93706-5646 |  | 2013-06-24 | 2013-06-24 16:12 | 2013-06-24 19:11 | YORK - DBYP-F048N080A | 132 | -5.6 | Yes | Yes | 23.7 | 19.6 | 4.1 | 1BA8EF663A2843AFB64B59A6EE5B55B3 |  | R22 | TXV |  | -4.242% | 1.0424 | 1.188% |  |  |  |  | TXV |  |  | -4.242%
Bakersfield | CA | 93313-3820 |  | 2013-06-21 | 2013-06-21 18:50 | 2013-06-21 18:50 | YORK - ERCS0421BBA | 141 | 0 | Yes | Yes | 19.3 | 21 | -1.7 | 6ABB15364EFA4A4C9F1D760683CB4647 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4331 |  | 2013-08-28 | 2013-08-28 11:58 | 2013-08-28 12:27 | DAY & NIGHT - 585EJ024050 | 54 | 9 | Yes | Yes | 24 | 20.8 | 3.2 | 4C15465531A146B3AB8790F07C966E4A |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Bakersfield | CA | 93308-2991 |  | 2013-06-05 | 2013-06-05 15:04 | 2013-06-05 15:24 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.5 | 20.2 | -1.7 | 57B6C3F4021141939B6A251AAEA49F05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livermore | CA | 94551-4825 |  | 2013-06-20 | 2013-06-20 11:47 | 2013-06-20 12:12 | CARRIER - 38CMB048311 | 85 | 21.5 | Yes | Yes | 22.9 | 19.9 | 3 | BAC4887EC3C041779334760B25701B45 |  | R22 | Non-TXV |  | 25.29% | 0.74706 | 48.61% | [5 empty] | Non-TXV | 25.29%
Bakersfield | CA | 93309-5127 |  | 2013-08-04 | 2013-08-04 15:37 | 2013-08-04 15:37 | YORK - DAYP-F036N070A | 109 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 8C0ED49BF2FB49FE9F2A638D8F683A4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2969 |  | 2013-06-05 | 2013-06-05 14:06 | 2013-06-05 14:22 | RHEEM - UKN | 90 | 7.1 | Yes | Yes | 19.6 | 20.9 | -1.3 | 4DBE0DCEAAB84C539E70F940FB6307D4 |  | R22 | Non-TXV |  | 7.889% | 0.92111 | 15.16% | [5 empty] | Non-TXV | 7.889%
Fresno | CA | 93722-5803 |  | 2013-07-11 | 2013-07-11 09:55 | 2013-07-11 10:27 | COLEMAN - DAYHF036N070C | 108 | 5.1 | Yes | Yes | 23.8 | 20.4 | 3.4 | 8A3C85EA22D94086B374831A928D9360 |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Arvin | CA | 93203-9473 |  | 2013-08-21 | 2013-08-21 14:20 | 2013-08-21 14:40 | GOODMAN - GSC130481AF | 150 | 5 | Yes | Yes | 20.1 | 19.8 | 0.3 | 4441EDB866B944B0AB36F1287A5D7405 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93705-1052 |  | 2013-06-11 | 2013-06-11 12:28 | 2013-06-11 13:00 | RUUD - UNK | 80 | 7 | Yes | Yes | 19.8 | 18.8 | 1 | B41B148D758C45BC82AD6B26BF66CA6D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Bakersfield | CA | 93308-2967 |  | 2013-06-05 | 2013-06-05 19:14 | 2013-06-05 19:14 | RHEEM - UKN | 90 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | 1A42CC18E95942849613D52C9ABB2360 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3702 |  | 2013-06-04 | 2013-06-04 17:33 | 2013-06-04 17:55 | CARRIER - UNK | 75 | 3.7 | Yes | Yes | 19 | 19.9 | -0.9 | 9DE1A6D0674143F4AB8EDF5DBE5C8054 |  | R22 | Non-TXV |  | 4.933% | 0.95067 | 9.481% | [5 empty] | Non-TXV | 4.933%
Bakersfield | CA | 93306-1611 |  | 2013-07-16 | 2013-07-16 15:55 | 2013-07-16 16:14 | YORK - 5A36C0B0N-6AA | 99 | 15.7 | Yes | Yes | 19.7 | 21.5 | -1.8 | 7F3CB75D6DE64EBE9EF0990C969ACF5D |  | R22 | Non-TXV |  | 15.86% | 0.84141 | 30.48% | [5 empty] | Non-TXV | 15.86%
Fresno | CA | 93711-1525 |  | 2013-06-25 | 2013-06-25 10:49 | 2013-06-25 11:14 | ICP - PGC036K060E | 68 | -4.8 | Yes | Yes | 21.8 | 19.9 | 1.9 | 78C12E6016334F0FAFE62DAF06BA73A6 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Oakley | CA | 94561-1670 |  | 2013-06-28 | 2013-06-28 09:56 | 2013-06-28 10:13 | OTHER - | 74 | 2.5 | Yes | Yes | 19.9 | 19.1 | 0.8 | 673248BDD10B4037A748296F31C98847 |  | R22 | Non-TXV |  | 3.378% | 0.96622 | 6.492% | [5 empty] | Non-TXV | 3.378%
Fairfield | CA | 94533-4636 |  | 2013-06-04 | 2013-06-04 09:10 | 2013-06-04 09:45 | TRANE - 2TTB0030A1000AA | 64 | -4 | Yes | Yes | 10.9 | 14.7 | -3.8 | 1169219F2C724BAD8EE24EBB6AD71BB1 | Remove refrigerant: 6 oz | R22 | Non-TXV |  | -6.25% | 1.0625 | 1.75% |  |  |  |  | Non-TXV |  |  | -6.25%
Coalinga | CA | 93210-2419 |  | 2013-10-02 | 2013-10-02 11:03 | 2013-10-02 11:03 | BRYANT - 597CN048D | 168 | 0 | Yes | Yes | 18.7 | 20.4 | -1.7 | 3C0E95DFE6C34F58992153D9F2F1CF84 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5119 |  | 2013-06-19 | 2013-06-19 09:49 | 2013-06-19 10:21 | GOODMAN - GPG1336070M41BA | 70 | 10.4 | Yes | Yes | 21.7 | 18.8 | 2.9 | 07C2AD8BA7DE4A22B2A9978690D8ED7E |  | R22 | Non-TXV |  | 14.86% | 0.85143 | 28.55% | [5 empty] | Non-TXV | 14.86%
Suisun City | CA | 94585-1722 |  | 2013-06-05 | 2013-06-05 15:23 | 2013-06-05 15:23 | CARRIER - 38CKB30320 | 72 | 0 | Yes | Yes | 15.8 | 17.7 | -1.9 | DD335CBC32C44EE5932492AE042059C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5440 |  | 2013-06-13 | 2013-06-13 10:06 | 2013-06-13 10:46 | CARRIER - 38EH036300 | 118 | 16 | Yes | Yes | 16.3 | 17.6 | -1.3 | D27B347898B14930BAB5434203A08218 |  | R22 | Non-TXV |  | 13.56% | 0.86441 | 26.06% | [5 empty] | Non-TXV | 13.56%
Antioch | CA | 94531-7739 |  | 2013-06-04 | 2013-06-04 12:49 | 2013-06-04 12:49 | OTHER - R2A348GKR2 | 129 | 0 | Yes | Yes | 22.1 | 19.2 | 3 | 3096CF580E2440948A4B3E938FF1DF2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4320 |  | 2013-07-22 | 2013-07-22 19:09 | 2013-07-22 19:09 | RHEEM - RRKA-1060JK10X | 119 | 0 | Yes | Yes | 21.3 | 21.4 | -0.1 | DE5E1A90EFF249859AD13D8D1D12E180 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3417 |  | 2013-06-13 | 2013-06-13 13:31 | 2013-06-13 13:31 | ICP - T4A460GKAI00 | 213 | 0 | Yes | Yes | 22.3 | 19.8 | 2.5 | 47253DF29188435DB47F13847305BAFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3170 |  | 2013-06-13 | 2013-06-13 12:42 | 2013-06-13 13:02 | CARRIER - UNK | 80 | 7.5 | Yes | Yes | 19.7 | 19.4 | 0.3 | 9AAB3B7D50B3493EBD2AFEB7D5304038 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Coalinga | CA | 93210-2115 |  | 2013-11-08 | 2013-11-08 14:04 | 2013-11-08 14:37 | - PGD330060K001C1 | 99 | -5.6 | Yes | Yes | 22.3 | 18.9 | 3.4 | 5CB00F230A4A4097A05B9AD740A05CD7 |  | R410A | Non-TXV |  | -5.657% | 1.0566 | 1.584% |  |  |  |  | Non-TXV |  |  | -5.657%
Bakersfield | CA | 93308-3922 |  | 2013-07-12 | 2013-07-12 11:12 | 2013-07-12 11:40 | YORK - D1NP048N09006A | 132 | 22.8 | Yes | Yes | 20.5 | 20.2 | 0.3 | F2890197238F4C6C8854B774DA495CC2 |  | R22 | Non-TXV |  | 17.27% | 0.82727 | 33.19% | [5 empty] | Non-TXV | 17.27%
Lamont | CA | 93241-1212 |  | 2013-07-18 | 2013-07-18 12:52 | 2013-07-18 13:21 | YORK - D1NH048N06506C | 128 | 6.4 | Yes | Yes | 26.5 | 22.2 | 4.4 | 5CC2BCD1A8F3458582807AEFF5C1B215 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93313-3821 |  | 2013-06-25 | 2013-06-25 18:41 | 2013-06-25 18:41 | PAYNE - PA10JA048-C | 96 | 0 | Yes | Yes | 20.4 | 19.6 | 0.8 | 54C68C324322426797E16C2A228330BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1690 |  | 2013-10-04 | 2013-10-04 14:05 | 2013-10-04 14:05 | PAYNE - UNK | 96 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | ABF072F9273B478D848C046B09D7E864 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-3549 |  | 2013-06-18 | 2013-06-18 19:12 | 2013-06-18 19:12 | CARRIER - UNK | 85 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | 7D7E5BF545DA420980D6A6A484B34CF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3928 |  | 2013-06-21 | 2013-06-21 13:55 | 2013-06-21 17:50 | AMERICAN STANDARD - YCY030G1M0AA | 120 | 7.5 | Yes | Yes | 18.8 | 17.6 | 1.2 | 3E47F9A0B66648C2A50CE7C8A42913F6 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Sanger | CA | 93657-3417 |  | 2013-06-21 | 2013-06-21 15:53 | 2013-06-21 16:15 | YORK - UNK | 125 | 4.7 | Yes | Yes | 26.5 | 21.4 | 5.1 | 40F56FEDF7CD49949F6F88A46E8C8803 |  | R22 | Non-TXV |  | 3.76% | 0.9624 | 7.226% | [5 empty] | Non-TXV | 3.76%
Fresno | CA | 93702-3316 |  | 2013-05-31 | 2013-05-31 18:02 | 2013-05-31 18:37 | OTHER - DBRA7030N060C | 80 | 3.7 | Yes | Yes | 22.2 | 23.2 | -0.9 | FB6862D996C448C5B1876ABDA79061A9 |  | R22 | Non-TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | Non-TXV | 4.625%
Wasco | CA | 93280-3604 |  | 2013-07-20 | 2013-07-20 16:22 | 2013-07-20 16:43 | GOODMAN - GPG10360701A | 75 | 2.4 | Yes | Yes | 23.5 | 21.2 | 2.3 | CEF46152DADB49959D1BD468873DE48B |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
San Jose | CA | 95112-5009 |  | 2013-06-06 | 2013-06-06 12:51 | 2013-06-06 12:51 | CARRIER - 38CKC036310 | 152 | 0 | Yes | Yes | 22.9 | 21 | 1.9 | 7DAE883B6BA14B3D88128229424C58EF |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1640 |  | 2013-06-03 | 2013-06-03 12:27 | 2013-06-03 12:50 | OTHER - GCGD36S41S1A | 73 | 3.3 | Yes | Yes | 17.1 | 14.3 | 2.8 | 534F7775025940ABBD9BC80DD1E002F0 |  | R410A | TXV |  | 4.521% | 0.95479 | 8.687% | [5 empty] | TXV | 4.521%
Bakersfield | CA | 93309-6247 |  | 2013-06-04 | 2013-06-04 11:45 | 2013-06-04 11:45 | GOODMAN - GPG1330045M41AB | 80 | 0 | Yes | Yes | 26 | 20.4 | 5.6 | 3D9DEBF416964E86929DA1D590682DA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-9574 |  | 2013-06-27 | 2013-06-27 10:07 | 2013-06-27 10:32 | AMERICAN STANDARD - UNK | 83 | -5.9 | Yes | Yes | 23.4 | 20.4 | 3 | 2E55235546E744BEA9033C7C073525FC |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Concord | CA | 94519-2154 |  | 2013-06-11 | 2013-06-11 15:10 | 2013-06-11 15:55 | CARRIER - UKN | 85 | 0 | Yes | Yes | 15.8 | 18.6 | -2.8 | D3EA649EBC184B84A6DEF0926B6CD631 | Add refrigerant: 6.4 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Biola | CA | 93722-0000 |  | 2013-07-18 | 2013-07-18 11:26 | 2013-07-18 11:26 | GOODMAN - B9C13036IDE | 119 | 0 | Yes | Yes | 16.9 | 19.8 | -2.9 | F037B5534FDD494CA80ED41A354C4A51 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3835 |  | 2013-10-08 | 2013-10-08 10:25 | 2013-10-08 10:26 | WEATHER KING - 13AJM42A01 | 126 | 4.2 | Yes | Yes | 15.1 | 16.3 | -1.2 | 5C8F9C6F87D3468F89207CFC0C4DA231 |  | R410A | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93307-4898 |  | 2013-06-07 | 2013-06-07 15:57 | 2013-06-07 15:57 | LENNOX - UKN | 90 | 0 | Yes | Yes | 16.2 | 18.5 | -2.3 | D5BEC2F57C0C453EB35804D0C1D729D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-2001 |  | 2013-06-27 | 2013-06-27 09:32 | 2013-06-27 10:04 | GOODMAN - GPG1224701A | 64 | 2.4 | Yes | Yes | 24.9 | 19.9 | 5.1 | C6F6345DBB494BC1BB3389C7D59089A2 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Fresno | CA | 93702-3410 |  | 2013-07-11 | 2013-07-11 15:26 | 2013-07-11 21:04 | YORK - D3NP024N03606NXB | 100 | 8.6 | Yes | Yes | 22.9 | 20.8 | 2.1 | A623A53434A8428AA84D5730A7D592C9 |  | R22 | TXV |  | 8.6% | 0.914 | 16.53% | [5 empty] | TXV | 8.6%
Fresno | CA | 93722-4900 |  | 2013-06-18 | 2013-06-18 15:56 | 2013-06-18 16:13 | - AC030M10219 | 57 | 1.8 | Yes | Yes | 20.4 | 21.5 | -1.1 | C45D5BB7F3694E21B35C819FC07A7A4A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
San Jose | CA | 95135-2209 |  | 2013-06-11 | 2013-06-11 10:46 | 2013-06-11 10:46 | RHEEM - RAKA-042JAZ | 85 | 0 | Yes | Yes | 21.5 | 20.3 | 1.2 | 3DC07A62C7DF4FE9B4E46809B78ECA61 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1421 |  | 2013-06-21 | 2013-06-21 12:10 | 2013-06-21 12:31 | DAY & NIGHT - 30/80YAC106C | 80 | 2.5 | Yes | Yes | 27.6 | 23.1 | 4.5 | 19B6E3BE1622429FB31B14744025761A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Bakersfield | CA | 93308-2167 |  | 2013-06-05 | 2013-06-05 09:31 | 2013-06-05 09:31 | PAYNE - PY3NA024040NB | 89 | 0 | Yes | Yes | 21.2 | 19.3 | 1.9 | C0F148CB5A36492F9246D911E892C539 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8938 |  | 2013-09-17 | 2013-09-17 13:43 | 2013-09-17 13:53 | CARRIER - 38BRB042300 | 131 | 5.9 | Yes | Yes | 16.6 | 17 | -0.4 | 4C63C43AC31342D4AA8F3E60E8580089 |  | R22 | Non-TXV |  | 4.504% | 0.95496 | 8.655% | [5 empty] | Non-TXV | 4.504%
Sanger | CA | 93657-3566 |  | 2013-07-30 | 2013-07-30 14:26 | 2013-07-30 14:43 | YORK - H2RC030S0 | 88 | -3.2 | Yes | Yes | 18.1 | 20.6 | -2.5 | 34CBFA64FEF7418EBA65AC2FF9BC07EA |  | R22 | TXV |  | -3.636% | 1.0364 | 1.018% |  |  |  |  | TXV |  |  | -3.636%
Shafter | CA | 93280-0000 |  | 2013-08-07 | 2013-08-07 08:52 | 2013-08-07 09:18 | UNITARY PRODUCTS GROUP - H2RD060S06D | 162 | 7.1 | Yes | Yes | 21.5 | 20.4 | 1.1 | 699DABEA21424F73B9F8F642A1202419 |  | R22 | Non-TXV |  | 4.383% | 0.95617 | 8.423% | [5 empty] | Non-TXV | 4.383%
Bakersfield | CA | 93311-2294 |  | 2013-09-25 | 2013-09-25 16:14 | 2013-09-25 16:14 | RHEEM - RAJC030JAS | 88 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | FD43EDD401FA43868F9670D67855B1EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madison | CA | 95653-0000 |  | 2013-08-25 | 2013-08-25 08:49 | 2013-08-25 09:28 | RHEEM - RRGF-G5E24JKER | 42 | 1.2 | Yes | Yes | 16.1 | 15.2 | 0.9 | B7348AC0279B47CC90EDF68C3865BE12 |  | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Kerman | CA | 93630-1985 |  | 2013-07-08 | 2013-07-08 11:51 | 2013-07-08 12:31 | CARRIER - 48SDN042060301 | 165 | 5 | Yes | Yes | 25.1 | 22 | 3.1 | BB2F65A2EB74422D9875E128E8C96251 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Sanger | CA | 93657-2616 |  | 2013-06-21 | 2013-06-21 11:22 | 2013-06-21 13:36 | LENNOX - 10ACC03623001 | 115 | 4.9 | Yes | Yes | 23.6 | 20.4 | 3.2 | 6ECBC328E2C94C8395FFFA2EE7A6A397 |  | R22 | TXV |  | 4.261% | 0.95739 | 8.188% | [5 empty] | TXV | 4.261%
Fresno | CA | 93722-4127 |  | 2013-06-18 | 2013-06-18 12:27 | 2013-06-18 12:59 | GOODMAN - FGB036075 | 85 | 5.6 | Yes | Yes | 25.1 | 21 | 4.1 | 3C7520BEAC4245CFA12C83B943901C26 |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Sanger | CA | 93657-2299 |  | 2013-08-06 | 2013-08-06 10:52 | 2013-08-06 11:13 | GOODMAN - GSC130241FA | 77 | 2.4 | Yes | Yes | 18.9 | 19.8 | -0.9 | 7E90E7EE9E6E4BE5BF3F88443D553A88 |  | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
San Jose | CA | 95116-2978 |  | 2013-06-11 | 2013-06-11 13:25 | 2013-06-11 13:25 | CARRIER - 38CKC042310 | 93 | 0 | Yes | Yes | 24.9 | 19 | 5.9 | 4AD9B96EA27F4AA1AD1CCEF5B8FAB8CC |  | R22 | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2299 |  | 2013-08-08 | 2013-08-08 09:43 | 2013-08-08 10:03 | ARCOAIRE - NARC224AK5 | 79 | 3 | Yes | Yes | 20.3 | 19.9 | 0.4 | 21BFE0BB3E0942E3B1752EA09DABCA20 |  | R22 | TXV |  | 3.797% | 0.96203 | 7.298% | [5 empty] | TXV | 3.797%
Sanger | CA | 93657-4102 |  | 2013-06-21 | 2013-06-21 13:31 | 2013-06-21 13:56 | GOODMAN - PGB0361001AREVA | 57 | 4.1 | Yes | Yes | 19.7 | 22.6 | -2.9 | E226FB5779A94226A18AD715DD76DE6C |  | R22 | Non-TXV |  | 7.193% | 0.92807 | 13.82% | [5 empty] | Non-TXV | 7.193%
Bakersfield | CA | 93308-9511 |  | 2013-09-19 | 2013-09-19 12:57 | 2013-09-19 12:57 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 22.3 | 21.8 | 0.6 | 4373D83901514A13B4D80900B78ED699 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1510 |  | 2013-09-10 | 2013-09-10 11:56 | 2013-09-10 12:16 | YORK - D1NA036N05606C | 67 | 3.8 | Yes | Yes | 19.6 | 19.4 | 0.2 | F5A5EFD6A60F4193B8CC4F305ABFF5F0 |  | R22 | Non-TXV |  | 5.672% | 0.94328 | 10.9% | [5 empty] | Non-TXV | 5.672%
Lamont | CA | 93241-1016 |  | 2013-07-18 | 2013-07-18 10:31 | 2013-07-18 11:00 | TEMPSTAR - PGAA42C1K3 | 83 | 17.4 | Yes | Yes | 26.3 | 21.7 | 4.6 | 76B6B1A41A3F44C1A0532BBB6F627B0C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.96% | 0.79036 | 40.29% | [5 empty] | Non-TXV | 20.96%
Lamont | CA | 93241-1016 |  | 2013-07-18 | 2013-07-18 22:08 | 2013-07-18 22:08 | TEMPSTAR - PGAA42C1K3 | 83 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 840D8568544C453297415C19EB864819 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5669 |  | 2013-05-28 | 2013-05-28 12:17 | 2013-05-28 12:38 | BDP - 561CJ036-D | 82 | 5.1 | Yes | Yes | 20.4 | 21 | -0.6 | 5D0B1FF22318455A987FAFECD4CC1032 |  | R22 | Non-TXV |  | 6.22% | 0.9378 | 11.95% | [5 empty] | Non-TXV | 6.22%
Mc Farland | CA | 93250-1258 |  | 2013-07-26 | 2013-07-26 20:15 | 2013-07-26 20:54 | WEATHER KING - 13AJA48A01 | 123 | 4.4 | Yes | Yes | 20.5 | 22.1 | -1.6 | 69929766C4B64173AD537826EB93D735 |  | R22 | Non-TXV |  | 3.577% | 0.96423 | 6.875% | [5 empty] | Non-TXV | 3.577%
Woodland | CA | 95695-2646 |  | 2013-09-25 | 2013-09-25 10:13 | 2013-09-25 10:56 | AMANA - RCE36C2A | 225 | 12.4 | Yes | Yes | 14.6 | 17.3 | -2.7 | 15239DA6B0854563B18FD9845CEC960C |  | R22 | Non-TXV |  | 5.511% | 0.94489 | 10.59% | [5 empty] | Non-TXV | 5.511%
Bakersfield | CA | 93309-2038 |  | 2013-05-30 | 2013-05-30 16:53 | 2013-05-30 16:53 | PAYNE - PY3PNA048090N | 120 | 0 | Yes | Yes | 23.8 | 18 | 5.9 | 6966BF06CEFC4F9091C70349D458A9A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2815 |  | 2013-08-15 | 2013-08-15 19:48 | 2013-08-15 19:48 | ICP - CAC042AKA1 | 98 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 3D5DE4EBA21D474595140397E0306AB9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0514 |  | 2013-07-12 | 2013-07-12 12:18 | 2013-07-12 12:18 | YORK - D1NH048N1106C | 128 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 37838AEBA1D84D7FBC1E22C466A4C8DA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4808 |  | 2013-06-21 | 2013-06-21 12:13 | 2013-06-21 12:51 | CARRIER - 591ANX048000ACAA | 128 | 7.4 | Yes | Yes | 18 | 17.9 | 0.1 | D36106040CF14E93A92DCD4CBD394E4F |  | R22 | Non-TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | Non-TXV | 5.781%
Woodland | CA | 95695-4604 |  | 2013-06-17 | 2013-06-17 09:23 | 2013-06-17 09:52 | CARRIER - 48BL003-BC | 72 | 11.4 | Yes | Yes | 16.9 | 18.2 | -1.3 | CA6E8F9E46AA443099A096CC944A2492 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.83% | 0.84167 | 30.43% | [5 empty] | Non-TXV | 15.83%
Fresno | CA | 93705-2244 |  | 2013-06-03 | 2013-06-03 14:13 | 2013-06-03 14:41 | GOODMAN - GPG13442070M41AB | 105 | 4.4 | Yes | Yes | 21 | 21.3 | -0.3 | 273C64CD14844F1F952264FC3E407B7C |  | R410A | Non-TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | Non-TXV | 4.19%
Vacaville | CA | 95687-6314 |  | 2013-05-30 | 2013-05-30 11:55 | 2013-05-30 12:25 | BDP - 588ANW024060ACBD | 44 | -4.1 | Yes | Yes | 13.8 | 12.5 | 1.3 | DAE27831E8034176AD5965AA8B03567E |  | R22 | Non-TXV |  | -9.318% | 1.0932 | 2.61% |  |  |  |  | Non-TXV |  |  | -9.318%
Vacaville | CA | 95687-7106 |  | 2013-09-19 | 2013-09-19 12:25 | 2013-09-19 12:26 | CARRIER - 38CKC036340 | 70 | 2.4 | Yes | Yes | 18.1 | 17.6 | 0.5 | 86481E0AD9EB400EB3B2660813BC5FA1 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Arvin | CA | 93203-1643 |  | 2013-09-09 | 2013-09-09 14:06 | 2013-09-09 14:22 | BRYANT - 561CJ030 E | 83 | 2.6 | Yes | Yes | 21.8 | 20.1 | 1.7 | 9CB1D222FB0E4D4CB17E88002EEB9F0D |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Fresno | CA | 93722-2831 |  | 2013-06-13 | 2013-06-13 15:00 | 2013-06-13 15:23 | CARRIER - UNK | 80 | 11 | Yes | Yes | 24.3 | 20.6 | 3.7 | 4E36A3E6C76C4B5BAD06B5A8091E3144 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Bakersfield | CA | 93312-6854 |  | 2013-10-01 | 2013-10-01 11:06 | 2013-10-01 11:06 | LENNOX - 13ACD03623003 | 85 | 0 | Yes | Yes | 22 | 21 | 1 | A07289D5F1394E7F9AC9E9DCC5C62C60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-1335 |  | 2013-10-02 | 2013-10-02 14:05 | 2013-10-02 14:05 | CARRIER - 48NMX0363 | 80 | 0 | Yes | Yes | 35 | 19 | 16.1 | BA8B531C92BC477583A7889B56A4E2E8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0256 |  | 2013-06-19 | 2013-06-19 09:21 | 2013-06-19 09:56 | BDP - 568EJO48 | 80 | 12.8 | Yes | Yes | 24.9 | 20.1 | 4.8 | 179A77818E4742F4B855C36BE730C879 |  | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Vacaville | CA | 95687-9419 |  | 2013-06-20 | 2013-06-20 14:02 | 2013-06-20 14:23 | CARRIER - 38TKB036300 | 81 | -6.4 | Yes | Yes | 18.5 | 21.5 | -3 | 1AFE1DC2747F439CBAD489E548AD1CC3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.901% | 1.079 | 2.213% |  |  |  |  | Non-TXV |  |  | -7.901%
Sanger | CA | 93657-3907 |  | 2013-08-05 | 2013-08-05 14:31 | 2013-08-05 15:09 | ARCOAIRE - NAG024AKD1 | 77 | 6.7 | Yes | Yes | 20 | 20 | 0 | C0D694602A0B479F9866705B0E50A8A8 |  | R22 | TXV |  | 8.701% | 0.91299 | 16.72% | [5 empty] | TXV | 8.701%
Fresno | CA | 93705-4428 |  | 2013-06-07 | 2013-06-07 08:45 | 2013-06-07 09:42 | AMERICAN STANDARD - 2YCC3042A1064AA | 85 | -5 | Yes | Yes | 16.9 | 18.6 | -1.7 | 4B5D36E55D3748F78480DBAD281382CA |  | R22 | TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | TXV |  |  | -5.882%
Antioch | CA | 94531-6729 |  | 2013-06-04 | 2013-06-04 11:38 | 2013-06-04 11:58 | RHEEM - UKN | 85 | -8 | Yes | Yes | 13.8 | 17.9 | -4.1 | 5DB58D26AE6C4ACAA99F11DDA9663656 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
W Sacramento | CA | 95605-2125 |  | 2013-06-21 | 2013-06-21 11:07 | 2013-06-21 11:08 | GOODMAN - CK42-1C | 92 | -7.6 | Yes | Yes | 17.1 | 18.5 | -1.4 | E4893433C00041CDA87D7AD211A21E24 |  | R22 | Non-TXV |  | -8.261% | 1.0826 | 2.313% |  |  |  |  | Non-TXV |  |  | -8.261%
Vacaville | CA | 95688-2737 |  | 2013-05-30 | 2013-05-30 12:27 | 2013-05-30 12:56 | BDP - 588ANW036060ADAF | 70 | -4.1 | Yes | Yes | 12.2 | 13.4 | -1.2 | B343BA9425A94FE6B5881AF71645343E |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Mc Farland | CA | 93250-1666 |  | 2013-07-29 | 2013-07-29 19:15 | 2013-07-29 19:33 | WEATHER KING - 13A348A01 | 123 | 6.9 | Yes | Yes | 21.3 | 21.7 | -0.4 | 23E9EDCF832F45368604B7D01C5EA9E5 |  | R22 | Non-TXV |  | 5.61% | 0.9439 | 10.78% | [5 empty] | Non-TXV | 5.61%
Sanger | CA | 93657-3908 |  | 2013-08-13 | 2013-08-13 11:24 | 2013-08-13 11:44 | OTHER - NAC024AKB1 | 67 | -4.7 | Yes | Yes | 19 | 18.5 | 0.5 | 43EE9700A71B4780971A3A17883B2A8B |  | R22 | Non-TXV |  | -7.015% | 1.0701 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.015%
Napa | CA | 94558-4169 |  | 2013-06-05 | 2013-06-05 14:00 | 2013-06-05 14:00 | CARRIER - 38TH030310 | 70 | 0 | Yes | Yes | 15.5 | 18.5 | -3 | 57B16AB8B76C4304AB34E65F18F0E58D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8905 |  | 2013-05-31 | 2013-05-31 17:46 | 2013-05-31 18:03 | BRYANT - 582ANW0300400AAA | 55 | 4.8 | Yes | Yes | 19.6 | 21.5 | -1.9 | D575A32224E24F9DAAB6BBAC5F44573F |  | R22 | Non-TXV |  | 8.727% | 0.91273 | 16.77% | [5 empty] | Non-TXV | 8.727%
Winters | CA | 95694-1821 |  | 2013-08-15 | 2013-08-15 13:29 | 2013-08-15 13:29 | CARRIER - 38TX042300 | 135 | 0 | Yes | Yes | 21.6 | 19.9 | 1.8 | 3630BAC3189945338775324A977FF2BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6306 |  | 2013-06-19 | 2013-06-19 13:42 | 2013-06-19 14:01 | GOODMAN - CKH30-1B | 90 | 3.4 | Yes | Yes | 18.7 | 19.1 | -0.4 | AE6613C005B14F9F9D71383DB15D9A6B |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Sanger | CA | 93657-3905 |  | 2013-08-08 | 2013-08-08 12:21 | 2013-08-08 12:21 | ARCOAIRE - NAC224AKCJ | 86 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 070138D012734DBB935E2DF839B00DDF | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9504 |  | 2013-09-19 | 2013-09-19 17:28 | 2013-09-19 17:28 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 22 | 22.1 | -0.1 | B61899FA0B004B8AA9AF9C66714B9294 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3907 |  | 2013-08-05 | 2013-08-05 12:29 | 2013-08-05 12:54 | ARCOAIRE - NAC224AKC3 | 86 | -32.6 | Yes | Yes | 17.3 | 19.8 | -2.5 | 18A24BD5C309499EA458787C19E5BA5B |  | R22 | TXV |  | -37.91% | 1.3791 | 10.62% |  |  |  |  | TXV |  |  | -37.91%
Fresno | CA | 93650-1128 |  | 2013-07-09 | 2013-07-09 14:42 | 2013-07-09 15:09 | - UNK | 80 | 2.4 | Yes | Yes | 22.8 | 21.2 | 1.6 | 99C193D919F744FB812B364BD6119C82 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Kerman | CA | 93630-8922 |  | 2013-08-02 | 2013-08-02 12:07 | 2013-08-02 12:54 | BRYANT - 48GX042060301 | 121 | -10 | Yes | Yes | 23.8 | 19.9 | 3.9 | 737039E73E624DB3BF37CDEC705C869E |  | R22 | Non-TXV |  | -8.264% | 1.0826 | 2.314% |  |  |  |  | Non-TXV |  |  | -8.264%
Antioch | CA | 94509-6903 |  | 2013-06-04 | 2013-06-04 09:59 | 2013-06-04 10:18 | TRANE - BTD748A100B0 | 152 | 13.8 | Yes | Yes | 17.7 | 20.2 | -2.5 | 6831134865994013836F46BDBD60A192 |  | R22 | Non-TXV |  | 9.079% | 0.90921 | 17.45% | [5 empty] | Non-TXV | 9.079%
Bakersfield | CA | 93308-9503 |  | 2013-09-19 | 2013-09-19 13:42 | 2013-09-19 13:42 | ICP - PGC024K040A | 58 | 0 | Yes | Yes | 21.4 | 20.9 | 0.5 | 33B2BB77B5BE472F85597FD20BA20EF9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3905 |  | 2013-08-05 | 2013-08-05 14:42 | 2013-08-05 15:00 | ARCOAIRE - NAC224AKC3 | 86 | 3.1 | Yes | Yes | 19.3 | 20.4 | -1.1 | 1C1FE7DE7A014106B8E95F0479153EDB |  | R22 | TXV |  | 3.605% | 0.96395 | 6.927% | [5 empty] | TXV | 3.605%
San Jose | CA | 95134-1256 |  | 2013-07-08 | 2013-07-08 09:22 | 2013-07-08 10:10 | INTERTHERM - 0N36IB | 45 | 5.5 | Yes | Yes | 21.5 | 20.4 | 1.1 | D3F5B4A6C87F4108BB5FE472F04C7348 |  | R22 | Non-TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | Non-TXV | 12.22%
Fresno | CA | 93706-4647 |  | 2013-06-12 | 2013-06-12 12:55 | 2013-06-12 16:24 | - UNK | 80 | 20.8 | Yes | Yes | 18.7 | 18.7 | 0 | 6056FA993B4D4F86B8F24B20939C3AF9 |  | R22 | Non-TXV |  | 26% | 0.74 | 49.97% | [5 empty] | Non-TXV | 26%
Sanger | CA | 93657-3905 |  | 2013-08-06 | 2013-08-06 14:10 | 2013-08-06 14:36 | ARCOAIRE - NAC224AKC3 | 86 | 10.8 | Yes | Yes | 17.7 | 20.1 | -2.4 | FD9B0F4D7BB84EAAB029533FCFF6A333 |  | R22 | TXV |  | 12.56% | 0.87442 | 24.13% | [5 empty] | TXV | 12.56%
Mc Farland | CA | 93250-1259 |  | 2013-07-26 | 2013-07-26 19:59 | 2013-07-26 20:55 | OTHER - 113AN030-E | 74 | 6.1 | Yes | Yes | 20.8 | 23.7 | -2.9 | 7E856843BDAC4DAC871AA2D96A9DBE06 |  | R410A | Non-TXV |  | 8.243% | 0.91757 | 15.84% | [5 empty] | Non-TXV | 8.243%
Bakersfield | CA | 93313-3942 |  | 2013-06-27 | 2013-06-27 18:28 | 2013-06-27 18:28 | YORK - D1N1A048N06506C | 92 | 0 | Yes | Yes | 19.9 | 19.7 | 0.2 | 38AA123062E341A5B520873B80BD5923 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1237 |  | 2013-09-09 | 2013-09-09 11:51 | 2013-09-09 13:10 | UNITARY PRODUCTS GROUP - AC024X1222A | 71 | 3.1 | Yes | Yes | 20 | 20.1 | -0.1 | AE2D7B6A3C3B4CBC8BE26649790DE78B |  | R22 | Non-TXV |  | 4.366% | 0.95634 | 8.391% | [5 empty] | Non-TXV | 4.366%
Bakersfield | CA | 93308-2991 |  | 2013-06-05 | 2013-06-05 14:15 | 2013-06-05 14:15 | TRANE - 4YCC3018A1040AA | 94 | 0 | Yes | Yes | 19.3 | 22.1 | -2.8 | 8B469CE06DA2483EB03F121257840CAB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2080 |  | 2013-10-03 | 2013-10-03 13:36 | 2013-10-03 13:37 | CARRIER - 38CKC018320 | 68 | 5.4 | Yes | Yes | 14.3 | 16 | -1.7 | A0C030A0CB5D45FF8925CEFB0335CC7B |  | R22 | Non-TXV |  | 7.941% | 0.92059 | 15.26% | [5 empty] | Non-TXV | 7.941%
Bakersfield | CA | 93308-9509 |  | 2013-09-19 | 2013-09-19 15:42 | 2013-09-19 15:42 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.6 | 21.2 | 0.4 | C0BB01FACCF24BA6A53A9348AA78020F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madison | CA | 95653-0000 |  | 2013-09-09 | 2013-09-09 12:41 | 2013-09-09 13:08 | CARRIER - 50JX-036-301AD | 112 | 5.1 | Yes | Yes | 22.6 | 19.9 | 2.7 | BB5B9113C3DB45128C030312332DA93E |  | R22 | Non-TXV |  | 4.554% | 0.95446 | 8.751% | [5 empty] | Non-TXV | 4.554%
Fresno | CA | 93706-5059 |  | 2013-06-24 | 2013-06-24 13:55 | 2013-06-24 14:27 | - UNK | 80 | -3 | Yes | Yes | 19.2 | 18.5 | 0.7 | 0B90AA8E158B4DD79E0C7830C9862859 |  | R22 | TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | TXV |  |  | -3.75%
Fresno | CA | 93728-3014 |  | 2013-06-20 | 2013-06-20 10:23 | 2013-06-20 10:23 | - RRKA-A036JK06X | 62 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 27F0937D72084630B287BF6FEB61F6C2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2905 |  | 2013-06-18 | 2013-06-18 10:13 | 2013-06-18 10:14 | GOODMAN - PGB036075-1A | 60 | -5.6 | Yes | Yes | 15.8 | 18.2 | -2.4 | 3DA14278A6F7434C933D6066589558A3 |  | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Fresno | CA | 93722-6563 |  | 2013-10-31 | 2013-10-31 15:44 | 2013-10-31 16:22 | GIBSON - JS5BD048KA | 126 | 5.5 | Yes | Yes | 20.8 | 19.8 | 1 | EBCA34FAB5ED4E7EA53B98FFDE12E0CF |  | R22 | Non-TXV |  | 4.365% | 0.95635 | 8.389% | [5 empty] | Non-TXV | 4.365%
Bakersfield | CA | 93308-2969 |  | 2013-06-05 | 2013-06-05 13:28 | 2013-06-05 13:28 | TRANE - 4YCC3024B1064AA | 93 | 0 | Yes | Yes | 19.2 | 21.8 | -2.6 | 3072C1B7320A4BF1BAD43B154F77C07B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-0000 |  | 2013-07-05 | 2013-07-05 09:33 | 2013-07-05 09:52 | CARRIER - 48GX-042060311-- | 121 | 4.1 | Yes | Yes | 21.6 | 19.3 | 2.3 | 1A518FE409A546FE8621D6E8067AC799 |  | R22 | Non-TXV |  | 3.388% | 0.96612 | 6.512% | [5 empty] | Non-TXV | 3.388%
San Jose | CA | 95118-2433 |  | 2013-07-24 | 2013-07-24 09:54 | 2013-07-24 09:55 | CARRIER - 38CKB036320 | 71 | -5 | Yes | Yes | 16.3 | 17.6 | -1.3 | B5ECCDFFF93A4EE0A0405FF1C11B43B9 |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Bakersfield | CA | 93308-2969 |  | 2013-06-05 | 2013-06-05 15:52 | 2013-06-05 16:08 | ICP - PGC024K060A | 58 | 8.1 | Yes | Yes | 19.4 | 19.7 | -0.3 | FDC21D8A1CD743F286A3B8E2A7B193F2 |  | R22 | Non-TXV |  | 13.97% | 0.86034 | 26.84% | [5 empty] | Non-TXV | 13.97%
Kerman | CA | 93630-1974 |  | 2013-08-02 | 2013-08-02 11:02 | 2013-08-02 12:04 | CARRIER - 48GX042060301 | 123 | -11.6 | Yes | Yes | 21.4 | 19.6 | 1.9 | F2E92CE9642F43E1922E9A9710425254 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.431% | 1.0943 | 2.641% |  |  |  |  | Non-TXV |  |  | -9.431%
Fresno | CA | 93722-8602 |  | 2013-08-28 | 2013-08-28 12:59 | 2013-08-28 15:14 | LENNOX - 12GCS030X-75-3PA | 85 | -5 | Yes | Yes | 20.3 | 19.9 | 0.4 | B25DCD8908A94AF0B8D0B7D972EF9DDF |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93723-9466 |  | 2013-10-02 | 2013-10-02 11:17 | 2013-10-02 11:35 | YORK - D1NP048N09006A | 132 | 6.1 | Yes | Yes | 20.5 | 19.1 | 1.4 | BB9E1AD8DB944423BEC6A88771EADA5E |  | R22 | Non-TXV |  | 4.621% | 0.95379 | 8.881% | [5 empty] | Non-TXV | 4.621%
Bakersfield | CA | 93308-2966 |  | 2013-08-30 | 2013-08-30 15:54 | 2013-08-30 15:54 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | E15014EED4F442A6B90CC7E7D91D9B40 |  | R410A | TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-2113 |  | 2013-07-09 | 2013-07-09 10:23 | 2013-07-09 10:50 | LENNOX - 12GCS03675 | 58 | 7.8 | Yes | Yes | 23.6 | 20.4 | 3.2 | FA22D6C5B5E946F28DF536B5C003AE15 |  | R22 | Non-TXV |  | 13.45% | 0.86552 | 25.84% | [5 empty] | Non-TXV | 13.45%
Bakersfield | CA | 93308-2968 |  | 2013-06-05 | 2013-06-05 12:38 | 2013-06-05 12:38 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 18.6 | 21 | -2.4 | 3A5DE9CAA89147FEBBAB9AF2BD4EA1AC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2080 |  | 2013-09-17 | 2013-09-17 10:23 | 2013-09-17 10:23 | CARRIER - 38CKC036330 | 84 | -7.9 | Yes | Yes | 16.4 | 17.6 | -1.2 | 518D46404CF341E29B0EFA6CF9528779 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Kerman | CA | 93630-1974 |  | 2013-07-08 | 2013-07-08 10:31 | 2013-07-08 11:05 | CARRIER - 48GX036060301 | 85 | 5.1 | Yes | Yes | 20.9 | 19.7 | 1.2 | 74860156357645659E38A28091F69C1F |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93702-2159 |  | 2013-08-01 | 2013-08-01 11:50 | 2013-08-01 12:07 | YORK - DBYPFO48NAA0A | 132 | -17.7 | Yes | Yes | 22.6 | 20.4 | 2.2 | DCEB30DC289748DAA1220BB61CB56BD5 |  | R22 | TXV |  | -13.41% | 1.1341 | 3.755% |  |  |  |  | TXV |  |  | -13.41%
Fresno | CA | 93722-5826 |  | 2013-08-21 | 2013-08-21 11:43 | 2013-08-21 12:12 | AMERICAN STANDARD - YCY060F1M0AA | 190 | 5.7 | Yes | Yes | 20.3 | 19 | 1.3 | 0A031B4EEF364912A2A2558E704493BB |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Kerman | CA | 93630-9376 |  | 2013-07-08 | 2013-07-08 09:32 | 2013-07-08 09:57 | CARRIER - 38BRC060360 | 200 | 7.5 | Yes | Yes | 22.6 | 19.3 | 3.3 | 76E18D4D29234BBABCB8DA9693B86381 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
San Jose | CA | 95123-4302 |  | 2013-06-17 | 2013-06-17 09:52 | 2013-06-17 10:21 | DAY & NIGHT - N4A336KAKB200 | 114 | 11.9 | Yes | Yes | 23.1 | 19.9 | 3.2 | BF4C751CD19B4F9083163487D3F4C74A |  | R410A | TXV |  | 10.44% | 0.89561 | 20.06% | [5 empty] | TXV | 10.44%
San Jose | CA | 95148-1331 |  | 2013-06-19 | 2013-06-19 09:15 | 2013-06-19 09:57 | TRANE - UNK | 85 | 4 | Yes | Yes | 18.3 | 19.3 | -1 | C613B827C1644566B82101BD9811596F |  | R22 | TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | TXV | 4.706%
San Jose | CA | 95139-1104 |  | 2013-06-19 | 2013-06-19 10:02 | 2013-06-19 10:30 | CARRIER - 38CKC036350 | 124 | 16.9 | Yes | Yes | 22.4 | 20.4 | 2 | D4F7CDE4EFE845F6A737586AA7740F31 |  | R22 | TXV |  | 13.63% | 0.86371 | 26.19% | [5 empty] | TXV | 13.63%
Fresno | CA | 93711-6160 |  | 2013-11-07 | 2013-11-07 12:57 | 2013-11-07 13:23 | YORK - D2YS024N03206A | 62 | 11.4 | Yes | Yes | 23.4 | 19.5 | 3.9 | 40E9EBBF327249388BFFD7A2F60B6BD9 |  | R22 | Non-TXV |  | 18.39% | 0.81613 | 35.34% | [5 empty] | Non-TXV | 18.39%
Arvin | CA | 93203-1282 |  | 2013-09-10 | 2013-09-10 11:55 | 2013-09-10 12:11 | UNITARY PRODUCTS GROUP - AC024X1222A | 71 | -4.2 | Yes | Yes | 21.9 | 19.5 | 2.4 | CC962F26D001433F89E7235824E010BD |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Fresno | CA | 93728-1929 |  | 2013-06-04 | 2013-06-04 10:04 | 2013-06-04 10:23 | CARRIER - 38CKC042340 | 80 | 4.7 | Yes | Yes | 20.8 | 19.8 | 1 | 5D6357D74DAD406687C9AC618B3015FC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.875% | 0.94125 | 11.29% | [5 empty] | Non-TXV | 5.875%
Madison | CA | 95653-0000 |  | 2013-09-09 | 2013-09-09 09:01 | 2013-09-09 09:24 | RUUD - ILLEGIBLE | 80 | -5.6 | Yes | Yes | 25.2 | 21.5 | 3.7 | FA5C4AB4DBFB4001B92F5CA921CB4736 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Oakley | CA | 94561-1942 |  | 2013-07-02 | 2013-07-02 10:11 | 2013-07-02 10:27 | OTHER - 563CN060-A | 200 | 25.5 | Yes | Yes | 15.2 | 17.6 | -2.4 | 43FC20803ECE4488BFFDED23589D34CD |  | R22 | Non-TXV |  | 12.75% | 0.8725 | 24.5% | [5 empty] | Non-TXV | 12.75%
Davis | CA | 95616-2119 |  | 2013-10-08 | 2013-10-08 12:49 | 2013-10-08 12:49 | CARRIER - 38TXA042320 | 140 | 0 | Yes | Yes | 18.1 | 18.2 | -0.1 | D1110C1392774E2FAB36C2B4954353DF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2966 |  | 2013-07-03 | 2013-07-03 14:22 | 2013-07-03 14:46 | LENNOX - HS26-030-2P | 78 | -7.3 | Yes | Yes | 19.1 | 17.2 | 1.9 | 72170A5732E34E33A355963057F27F9D |  | R22 | Non-TXV |  | -9.359% | 1.0936 | 2.621% |  |  |  |  | Non-TXV |  |  | -9.359%
Vacaville | CA | 95687-6534 |  | 2013-05-30 | 2013-05-30 12:58 | 2013-05-30 13:17 | PAYNE - 591ANX036000AAAA | 88 | 3.3 | Yes | Yes | 13.5 | 12.5 | 1 | D502C7074B4448818669C77C2EC01F5D |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Vacaville | CA | 95688-3814 |  | 2013-05-30 | 2013-05-30 11:13 | 2013-05-30 11:52 | GOODMAN - GSC130421AC | 137 | -12.9 | Yes | Yes | 18.1 | 13.2 | 4.9 | 2A296219C1AF4226BE5B9C2E6FD70207 |  | R22 | Non-TXV |  | -9.416% | 1.0942 | 2.637% |  |  |  |  | Non-TXV |  |  | -9.416%
Davis | CA | 95618-4322 |  | 2013-07-09 | 2013-07-09 11:04 | 2013-07-09 11:04 | DAY & NIGHT - 593CJX030000AAAA | 77 | -13.7 | Yes | Yes | 17.2 | 19.7 | -2.5 | B587F3796AC84DCB9D90B96A96AB5CC1 | Remove refrigerant: 13.7 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -17.79% | 1.1779 | 4.983% |  |  |  |  | TXV |  |  | -17.79%
Vacaville | CA | 95688-5319 |  | 2013-06-03 | 2013-06-03 09:30 | 2013-06-03 09:50 | COLEMAN - DAYP-F030N070A | 73 | 2.8 | Yes | Yes | 16.8 | 18.2 | -1.4 | 2E31AC07D30E4A24B0FDDB389FF44661 |  | R22 | Non-TXV |  | 3.836% | 0.96164 | 7.371% | [5 empty] | Non-TXV | 3.836%
Redding | CA | 96002-9570 |  | 2013-07-17 | 2013-07-17 09:17 | 2013-07-17 09:47 | BARD - 1148 1 | 88 | 9.2 | Yes | Yes | 19.2 | 21 | -1.8 | 9843B4A0EF4246AA95CAAEE2E87AE73B |  | R22 | Non-TXV |  | 10.45% | 0.89545 | 20.09% | [5 empty] | Non-TXV | 10.45%
Vallejo | CA | 94591-3696 |  | 2013-06-03 | 2013-06-03 09:51 | 2013-06-03 09:51 | PAYNE - UKN | 85 | 0 | Yes | Yes | 15 | 18 | -3 | A5DDA1D6670146AA9B88A1CDA62B9DC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-1828 |  | 2013-07-03 | 2013-07-03 13:16 | 2013-07-03 13:16 | LENNOX - 13ACD-036-230-02 | 112 | -2.2 | Yes | Yes | 12.1 | 14.7 | -2.6 | 3F082FCD225E4CB19F57F1B9AEB2C423 | Remove refrigerant: 11.2 oz Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -1.964% | 1.0196 | 0.5501% |  |  |  |  | Non-TXV |  |  | -1.964%
Vacaville | CA | 95688-2806 |  | 2013-06-03 | 2013-06-03 10:41 | 2013-06-03 11:17 | CARRIER - 38BRC060360 | 204 | 9.3 | Yes | Yes | 19 | 19.7 | -0.6 | B67E5ECC898B40E988E22E3B3B00B239 |  | R22 | Non-TXV |  | 4.559% | 0.95441 | 8.761% | [5 empty] | Non-TXV | 4.559%
Cottonwood | CA | 96022-9403 |  | 2013-09-07 | 2013-09-07 11:22 | 2013-09-07 11:54 | YORK - D2YS030N04506A | 76 | 2.8 | Yes | Yes | 25.1 | 22.3 | 2.9 | 4590B2B5EBDF4C0399BD16832EFCA934 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Fresno | CA | 93722-4900 |  | 2013-06-19 | 2013-06-19 16:33 | 2013-06-19 16:57 | YORK - H1DB042S06B | 85 | 2.7 | Yes | Yes | 22.1 | 20.4 | 1.7 | A09F5F5A2EFC473B9737BBC09FE1ED74 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Vacaville | CA | 95687-5126 |  | 2013-06-11 | 2013-06-11 09:24 | 2013-06-11 09:24 | RHEEM - RAMB-036JBZ | 93 | 0 | Yes | Yes | 17 | 19.7 | -2.7 | 4F48ECA6E4A04FE3A8EAAF544EC353A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2499 |  | 2013-06-10 | 2013-06-10 12:45 | 2013-06-10 13:09 | YORK - H2R030506A | 83 | 9.6 | Yes | Yes | 21.2 | 20.9 | 0.3 | 0987A8F061C64D0795E9365FFACBFA6F |  | R22 | Non-TXV |  | 11.57% | 0.88434 | 22.23% | [5 empty] | Non-TXV | 11.57%
Fairfield | CA | 94533-1641 |  | 2013-08-02 | 2013-08-02 13:56 | 2013-08-02 13:56 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 18.5 | 20.7 | -2.2 | D25A4556F98745698D8152C446672B78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3097 |  | 2013-06-17 | 2013-06-17 11:22 | 2013-06-17 12:15 | OTHER - BRCS0421BD | 84 | 9.3 | Yes | Yes | 21.6 | 20.2 | 1.5 | A7C600BDE51644BE9D6A64DBD13E3115 |  | R22 | Non-TXV |  | 11.07% | 0.88929 | 21.28% | [5 empty] | Non-TXV | 11.07%
Livermore | CA | 94550-8613 |  | 2013-06-20 | 2013-06-20 11:00 | 2013-06-20 11:00 | YORK - H1RA048S06D | 117 | 0 | Yes | Yes | 25.3 | 20.4 | 4.9 | 8B942208D10C415399ED8BB34D00EC58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livermore | CA | 94550-8613 |  | 2013-06-20 | 2013-06-20 11:08 | 2013-06-20 11:41 | YORK - H1RA048S06D | 117 | 4.8 | Yes | Yes | 21.5 | 18.7 | 2.8 | CD28E853D2CC4F878EE3162022A3DA93 |  | R22 | Non-TXV |  | 4.103% | 0.95897 | 7.884% | [5 empty] | Non-TXV | 4.103%
Fresno | CA | 93722-4900 |  | 2013-07-31 | 2013-07-31 11:59 | 2013-07-31 11:59 | COLEMAN - AC38042 | 141 | 0 | Yes | Yes | 28.2 | 20.6 | 7.7 | 2D9AB1528C6C48EB9BDF59D35048C6DA |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-5001 |  | 2013-09-09 | 2013-09-09 13:47 | 2013-09-09 13:49 | DAY & NIGHT - 858J030 | 72 | 7.4 | Yes | Yes | 16.8 | 17.6 | -0.8 | B10932E1D07C4CBABC03FFA5EC4798ED |  | R22 | Non-TXV |  | 10.28% | 0.89722 | 19.75% | [5 empty] | Non-TXV | 10.28%
Woodland | CA | 95695-5308 |  | 2013-06-25 | 2013-06-25 10:08 | 2013-06-25 10:09 | CARRIER - 48DL004 | 81 | -4.4 | Yes | Yes | 16 | 15.5 | 0.5 | 27D94DC2703F419983F472F6A66D16AF |  | R22 | TXV |  | -5.432% | 1.0543 | 1.521% |  |  |  |  | TXV |  |  | -5.432%
Bakersfield | CA | 93304-4513 |  | 2013-06-13 | 2013-06-13 18:08 | 2013-06-13 18:08 | ICP - PGC042K030B | 87 | 0 | Yes | Yes | 20.3 | 21.3 | -1 | FF9288BC68594E978D2D2153BFF5208C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3034 |  | 2013-07-15 | 2013-07-15 16:37 | 2013-07-15 16:37 | ICP - PGF036K060A | 71 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 0E10B01E9A5D4090A3831AC45742278F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4144 |  | 2013-08-27 | 2013-08-27 14:21 | 2013-08-27 14:21 | RUUD - RRNLB030JK06X | 76 | 0 | Yes | Yes | 20.7 | 22 | -1.3 | D6DF0B0F1248432D8BA53D428B85A855 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2222 |  | 2013-06-20 | 2013-06-20 09:24 | 2013-06-20 09:26 | PAYNE - PY3GNAA30060NA | 98 | 7.7 | Yes | Yes | 18.3 | 18.2 | 0.1 | 13A2098BD073461ABB60063416B2C491 |  | R410A | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Bakersfield | CA | 93304-4611 |  | 2013-07-02 | 2013-07-02 19:06 | 2013-07-02 19:06 | GOODMAN - GPG13336045M41AC | 85 | 0 | Yes | Yes | 19.5 | 19 | 0.5 | FF61FDEF234C4A11AFB84600FE05FE64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2080 |  | 2013-06-28 | 2013-06-28 09:22 | 2013-06-28 09:24 | CARRIER - 38CKB024320 | 72 | -6.8 | Yes | Yes | 17.4 | 18.2 | -0.8 | 4F235D94B7C049A4BEEFA033174A31C8 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Fresno | CA | 93705-1219 |  | 2013-06-03 | 2013-06-03 11:39 | 2013-06-03 11:39 | AMERICAN STANDARD - YCC048F1MOBH | 102 | 44 | Yes | Yes | 2.2 | 20.6 | -18.4 | A7453C70650943FABE84C6F94EF44527 | Add refrigerant: 44 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 43.14% | 0.56863 | 82.9% | [5 empty] | Non-TXV | 43.14%
Bakersfield | CA | 93313-3506 |  | 2013-06-24 | 2013-06-24 12:56 | 2013-06-24 13:17 | BRYANT - 583ANW036060AAAF | 84 | 19.3 | Yes | Yes | 23.2 | 22.1 | 1.1 | E60B271B79174EC5B6349A117BCBE777 |  | R22 | Non-TXV |  | 22.98% | 0.77024 | 44.16% | [5 empty] | Non-TXV | 22.98%
Kerman | CA | 93630-1944 |  | 2013-07-09 | 2013-07-09 13:46 | 2013-07-09 14:05 | CARRIER - 48GS048090301 | 81 | 2.6 | Yes | Yes | 22.7 | 20.1 | 2.6 | 095B49FDD9F84DD2A8F11213E3EA1C2F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.21% | 0.9679 | 6.169% | [5 empty] | Non-TXV | 3.21%
Woodland | CA | 95695-4125 |  | 2013-09-25 | 2013-09-25 13:14 | 2013-09-25 16:22 | CARRIER - 48GX-036060301AD | 83 | 3.6 | Yes | Yes | 14.9 | 17.2 | -2.3 | D4A3BE27FAB64AD7B3D149E1969508B8 |  | R22 | Non-TXV |  | 4.337% | 0.95663 | 8.335% | [5 empty] | Non-TXV | 4.337%
Madison | CA | 95653-0000 |  | 2013-09-09 | 2013-09-09 09:58 | 2013-09-09 10:25 | RHEEM - ILLEGIBLE | 87 | 3.4 | Yes | Yes | 25.7 | 20.4 | 5.3 | FBD7B58F4AF147ADA839660183ABFFFE |  | R22 | Non-TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | Non-TXV | 3.908%
San Jose | CA | 95136-0000 |  | 2013-06-17 | 2013-06-17 15:32 | 2013-06-17 15:32 | COLEMAN - TCGD24S41S3A | 61 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | CAE5558AD008462696B49BBEC570FFF8 |  | R22 | TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1280 |  | 2013-09-10 | 2013-09-10 17:15 | 2013-09-10 18:03 | UNITARY PRODUCTS GROUP - AC024X122A | 114 | 3.9 | Yes | Yes | 19.8 | 20.5 | -0.6 | 4E1DE447040E4C128440F974B7E3E1D9 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Brentwood | CA | 94513-2082 |  | 2013-06-28 | 2013-06-28 10:31 | 2013-06-28 10:32 | CARRIER - 38CKC018320 | 68 | -4 | Yes | Yes | 17.1 | 18.2 | -1.1 | F3795918776D46A99FF0343BF81DEBBE |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93308-8020 |  | 2013-10-22 | 2013-10-22 17:22 | 2013-10-22 17:22 | GOODMAN - GPG13240451BA | 77 | 0 | Yes | Yes | 22.7 | 21.5 | 1.2 | B8E9E2B96F1B4D409AEFCB344C036366 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2299 |  | 2013-08-01 | 2013-08-01 12:01 | 2013-08-01 12:31 | ARCOAIRE - NAC224AKC3 | 86 | -5.1 | Yes | Yes | 19 | 21 | -2 | 86F351EFFFFE400AB4E2B395FD9CD118 |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Cottonwood | CA | 96022-8702 |  | 2013-07-12 | 2013-07-12 15:57 | 2013-07-12 16:38 | GOODMAN - CKJ30-1B | 92 | 3.7 | Yes | Yes | 25.9 | 21 | 4.9 | A891E2C985D44EDBA8CFC5BB1B1FE070 |  | R22 | Non-TXV |  | 4.022% | 0.95978 | 7.729% | [5 empty] | Non-TXV | 4.022%
Woodland | CA | 95695-3318 |  | 2013-06-13 | 2013-06-13 11:44 | 2013-06-13 11:44 | BDP - 585CJ024050 | 72 | 0 | Yes | Yes | 16 | 18.5 | -2.5 | 0B7F434CD53442D892D940C762F56E41 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-1025 |  | 2013-06-18 | 2013-06-18 11:11 | 2013-06-18 11:11 | GOODMAN - GSC130361DE | 85 | 0 | Yes | Yes | 19.6 | 19.8 | -0.2 | 78D167E0615A4119953268CB03A15492 |  | R22 | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2299 |  | 2013-08-01 | 2013-08-01 12:38 | 2013-08-01 12:57 | ARCOAIRE - NCA224AKC3 | 86 | 2.8 | Yes | Yes | 20.9 | 21.4 | -0.5 | F0045AAB261E4284964039BCE585842D |  | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
Sanger | CA | 93657-2299 |  | 2013-08-05 | 2013-08-05 15:41 | 2013-08-05 16:23 | GOODMAN - GSC130241FA | 77 | 8.6 | Yes | Yes | 16.8 | 19.7 | -2.9 | 4390B0C06B7E4169B23E26FF80AFA67E |  | R22 | TXV |  | 11.17% | 0.88831 | 21.46% | [5 empty] | TXV | 11.17%
Fresno | CA | 93722-4037 |  | 2013-06-12 | 2013-06-12 10:42 | 2013-06-12 11:03 | OTHER - UNKUNK | 80 | 5.4 | Yes | Yes | 23.2 | 19.2 | 4 | AB159999658A45F4A2F97897F37DE241 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.75% | 0.9325 | 12.97% | [5 empty] | Non-TXV | 6.75%
Arvin | CA | 93203-1281 |  | 2013-09-10 | 2013-09-10 13:37 | 2013-09-10 13:54 | UNITARY PRODUCTS GROUP - ACO18X1222A | 73 | 2.6 | Yes | Yes | 20.4 | 19.7 | 0.7 | CFEE4ABA5FDB49D5A6C542A682C66567 |  | R22 | Non-TXV |  | 3.562% | 0.96438 | 6.845% | [5 empty] | Non-TXV | 3.562%
Vallejo | CA | 94590-3943 |  | 2013-06-27 | 2013-06-27 10:21 | 2013-06-27 10:21 | TRANE - YCX030F1M0BA | 102 | 0 | Yes | Yes | 16.9 | 17.7 | -0.8 | AFD1FAF9A2844DEEA2DF51546B8CB82B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4501 |  | 2013-08-26 | 2013-08-26 09:58 | 2013-08-26 10:31 | YORK - D1NA036N05606C | 67 | 4.2 | Yes | Yes | 23.1 | 19.3 | 3.8 | 3C147BBF3A324B01885127D219627D95 |  | R22 | Non-TXV |  | 6.269% | 0.93731 | 12.05% | [5 empty] | Non-TXV | 6.269%
Arvin | CA | 93203-9447 |  | 2013-08-11 | 2013-08-11 10:41 | 2013-08-11 11:03 | GOODMAN - GSC130421BB | 96 | -9 | Yes | Yes | 22.2 | 19.7 | 2.5 | F341B6AFC3564688B7D68F5F32BB8891 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93313-3942 |  | 2013-06-20 | 2013-06-20 17:44 | 2013-06-20 17:44 | UNITARY PRODUCTS GROUP - GCGD42521S2B | 100 | 0 | Yes | Yes | 22.9 | 20.2 | 2.7 | 37BBF86EE415438BA5765DD7C18B6B87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-5883 |  | 2013-07-01 | 2013-07-01 10:45 | 2013-07-01 10:45 | BRYANT - 113RNA036-B | 160 | 0 | Yes | Yes | 23 | 18.2 | 4.8 | 412B22212D4D400193876FA855EF07AA |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94534-1656 |  | 2013-06-19 | 2013-06-19 14:32 | 2013-06-19 14:52 | DAY & NIGHT - N4A336AKB200 | 85 | -3 | Yes | Yes | 20.4 | 19.9 | 0.5 | 3A174C6625DD4333B90CF5A9A82A7827 |  | R22 | Non-TXV |  | -3.529% | 1.0353 | 0.9884% |  |  |  |  | Non-TXV |  |  | -3.529%
Fresno | CA | 93704-1510 |  | 2013-06-03 | 2013-06-03 08:25 | 2013-06-03 08:44 | YORK - H4DB030S06A | 71 | 2.9 | Yes | Yes | 21.4 | 21 | 0.4 | ACA75E09AD09451F9149DD921428F354 |  | R22 | Non-TXV |  | 4.085% | 0.95915 | 7.85% | [5 empty] | Non-TXV | 4.085%
San Jose | CA | 95125-4717 |  | 2013-06-27 | 2013-06-27 13:32 | 2013-06-27 14:00 | BRYANT - 113ANA030-E | 74 | 5.1 | Yes | Yes | 25.6 | 20.1 | 5.5 | 65DBF089FF3D4C0E98A352119905AFE7 |  | R410A | TXV |  | 6.892% | 0.93108 | 13.24% | [5 empty] | TXV | 6.892%
Antioch | CA | 94509-4764 |  | 2013-10-01 | 2013-10-01 11:47 | 2013-10-01 11:47 | OTHER - H1RA024S06D | 59 | 0 | Yes | Yes | 19.8 | 16.9 | 2.9 | 0FC231226A8441C8BF99592F36D35CAE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2317 |  | 2013-07-08 | 2013-07-08 14:09 | 2013-07-08 14:30 | OTHER - UNK | 57 | 5.6 | Yes | Yes | 23.2 | 18.3 | 4.9 | 029421CE8ADB42E98402E79862CD5430 |  | R22 | Non-TXV |  | 9.825% | 0.90175 | 18.88% | [5 empty] | Non-TXV | 9.825%
Fremont | CA | 94536-6594 |  | 2013-06-04 | 2013-06-04 12:14 | 2013-06-04 12:57 | YORK - H2RA036S06E | 85 | 4.2 | Yes | Yes | 19.5 | 20.3 | -0.8 | 5FA16AB5016C4B9FA216AAA58F2E485F |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Fremont | CA | 94536-6594 |  | 2013-06-05 | 2013-06-05 08:09 | 2013-06-05 08:09 | YORK - H2RA036S06E | 85 | 0 | Yes | Yes | 19.9 | 18.8 | 1.1 | 60297AA1DB7149A6A9B2375DD97FE78E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-5122 |  | 2013-06-04 | 2013-06-04 18:49 | 2013-06-04 18:49 | YORK - H2RC036S06HA | 83 | 0 | Yes | Yes | 19.7 | 22 | -2.3 | 5DF15A1E709A4AABB89855177BB2ED99 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-5122 |  | 2013-06-04 | 2013-06-04 19:10 | 2013-06-04 19:10 | YORK - H2RC036S06HA | 83 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 90BFF1C22E434B0EAC32FB5A73FC25A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2083 |  | 2013-06-28 | 2013-06-28 10:44 | 2013-06-28 10:45 | CARRIER - 38CKC018320 | 68 | 4.6 | Yes | Yes | 18.9 | 18.5 | 0.4 | C0E461C05B14493FBDD9DCB6C3427294 |  | R22 | Non-TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | Non-TXV | 6.765%
Vallejo | CA | 94591-7721 |  | 2013-06-28 | 2013-06-28 12:25 | 2013-06-28 12:25 | PAYNE - PA10JA048-A | 134 | 0 | Yes | Yes | 23 | 19.1 | 3.9 | 6195B9F082344BDDB9ACCEEEF5AD81BA |  | R22 | TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-4722 |  | 2013-07-09 | 2013-07-09 10:06 | 2013-07-09 10:36 | ARMSTRONG - SCU12G30A-1 | 260 | -29.7 | Yes | Yes | 13.4 | 16.1 | -2.7 | 01A208E6C4D64E5EA22C91C11CBA1948 |  | R22 | TXV |  | -11.42% | 1.1142 | 3.199% |  |  |  |  | TXV |  |  | -11.42%
Fresno | CA | 93705-0827 |  | 2013-06-07 | 2013-06-07 12:22 | 2013-06-07 12:39 | RUUD - LRKAA030JK06E | 54 | 8.7 | Yes | Yes | 24.4 | 20.2 | 4.2 | 1D102D38FD9D4304BE6EC2063831F979 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.11% | 0.83889 | 30.96% | [5 empty] | Non-TXV | 16.11%
Bakersfield | CA | 93313-3983 |  | 2013-06-21 | 2013-06-21 12:14 | 2013-06-21 12:37 | YORK - DINA048N0906C | 88 | 14.1 | Yes | Yes | 18.7 | 19.3 | -0.6 | 55A6867D24C74376A63BEA0A32CD9CCD |  | R22 | Non-TXV |  | 16.02% | 0.83977 | 30.79% | [5 empty] | Non-TXV | 16.02%
Selma | CA | 93662-2143 |  | 2013-06-20 | 2013-06-20 08:42 | 2013-06-20 09:02 | LENNOX - 12GCS036X-75-3PA | 110 | 11.2 | Yes | Yes | 26.9 | 20.9 | 6 | 5E2E889377834BC493DB5BA488CE2826 |  | R22 | Non-TXV |  | 10.18% | 0.89818 | 19.57% | [5 empty] | Non-TXV | 10.18%
Antioch | CA | 94531-8209 |  | 2013-05-30 | 2013-05-30 14:13 | 2013-05-30 14:13 | PAYNE - 593ANXO48000ABAA | 180 | 0 | Yes | Yes | 19.6 | 22.6 | -3 | DE377B7D8B2449819646FD11E292D0ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0210 |  | 2013-08-27 | 2013-08-27 14:22 | 2013-08-27 14:22 | OTHER - UKN | 81 | 0 | Yes | Yes | 34.6 | 20.2 | 14.5 | 7AC0AD59455544DE9E961953DA52AF36 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1874 |  | 2013-06-21 | 2013-06-21 13:48 | 2013-06-21 14:16 | LENNOX - HS25-311-1P | 129 | 5 | Yes | Yes | 23.9 | 18.8 | 5.1 | 762A88B126B843568966B2D0CF48AE2D |  | R22 | Non-TXV |  | 3.876% | 0.96124 | 7.449% | [5 empty] | Non-TXV | 3.876%
Bakersfield | CA | 93307-6208 |  | 2013-06-11 | 2013-06-11 11:01 | 2013-06-11 11:01 | YORK - D2NP036N05606NXA | 108 | 0 | Yes | Yes | 17.7 | 20.7 | -3 | 51B64D3C7247490F88BAF87F183E7B59 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livermore | CA | 94550-7255 |  | 2013-06-20 | 2013-06-20 13:11 | 2013-06-20 13:44 | CARRIER - 38TH018300 | 85 | 17.6 | Yes | Yes | 26.1 | 20.4 | 5.7 | 3C5E56528EA84A60AAD7A96732FCF48B |  | R22 | Non-TXV |  | 20.71% | 0.79294 | 39.79% | [5 empty] | Non-TXV | 20.71%
Bay Point | CA | 94565-6939 |  | 2013-07-08 | 2013-07-08 10:22 | 2013-07-08 10:34 | PAYNE - 541DJ018 | 83 | 4.1 | Yes | Yes | 15.5 | 17.6 | -2.1 | D07EC01BD73B456F9E88D8600A751D32 |  | R22 | Non-TXV |  | 4.94% | 0.9506 | 9.493% | [5 empty] | Non-TXV | 4.94%
Fremont | CA | 94539-8112 |  | 2013-06-07 | 2013-06-07 09:10 | 2013-06-07 09:10 | DAY & NIGHT - N2A330AKB200 | 154 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | 3BD1649EA1104B1681A287F9B7376FFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-1828 |  | 2013-06-04 | 2013-06-04 13:55 | 2013-06-04 14:42 | TRANE - TTR036C100A2 | 92 | 3.4 | Yes | Yes | 19.8 | 18.5 | 1.3 | 200662626C8B478C99F5F9B4F0250620 |  | R22 | TXV |  | 3.696% | 0.96304 | 7.102% | [5 empty] | TXV | 3.696%
Bakersfield | CA | 93308-2101 |  | 2013-07-10 | 2013-07-10 19:54 | 2013-07-10 19:54 | YORK - D1NH060N09006C | 140 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | 4EFDBACE58B943AF9D74C54EA9DD52BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2205 |  | 2013-08-12 | 2013-08-12 21:29 | 2013-08-12 21:37 | DAY & NIGHT - 589ANW042060ADBF | 87 | -5.1 | Yes | Yes | 22.4 | 21.2 | 1.3 | FEFCF0EAAC4546EFA6CA49C307E386C3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Arvin | CA | 93203-1241 |  | 2013-09-10 | 2013-09-10 13:55 | 2013-09-10 15:10 | UNITARY PRODUCTS GROUP - AC018X1222A | 73 | 2.8 | Yes | Yes | 20.3 | 21 | -0.7 | 667985C67A69415E845C2A2745F89806 |  | R22 | Non-TXV |  | 3.836% | 0.96164 | 7.371% | [5 empty] | Non-TXV | 3.836%
Fresno | CA | 93722-0411 |  | 2013-06-11 | 2013-06-11 17:14 | 2013-06-11 17:14 | LENNOX - 13ACD042 | 108 | 0 | Yes | Yes | 19.9 | 18.4 | 1.5 | E23DB344EC874B5FAC31160CE26468D6 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-2105 |  | 2013-06-04 | 2013-06-04 13:22 | 2013-06-04 14:18 | ICP - PGAD060E1K1 | 215 | 6.6 | Yes | Yes | 22.5 | 19.5 | 3 | 51C3F71F4FBA4594A70EF75FFF4771AE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.899% | [5 empty] | Non-TXV | 3.07%
Bakersfield | CA | 93308-3212 |  | 2013-07-29 | 2013-07-29 05:42 | 2013-07-29 05:42 | ICP - PGC048K080A | 102 | 0 | Yes | Yes | 21.7 | 20.9 | 0.8 | B3DCFDF1AE874A22BF24A85F91584533 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2203 |  | 2013-07-23 | 2013-07-23 19:07 | 2013-07-23 19:49 | FRIGIDAIRE - R6GDX36K072C | 112 | 5.1 | Yes | Yes | 19.5 | 19.3 | 0.3 | 2305842990164DA7B8F713263310B5D9 |  | R22 | TXV |  | 4.554% | 0.95446 | 8.751% | [5 empty] | TXV | 4.554%
Bakersfield | CA | 93308-5649 |  | 2013-07-12 | 2013-07-12 12:42 | 2013-07-12 12:59 | YORK - D1NH04806506B | 124 | 16.3 | Yes | Yes | 20.9 | 20.2 | 0.7 | ACCB980B2A704BFA9DA79FF0DACECE05 |  | R22 | Non-TXV |  | 13.15% | 0.86855 | 25.26% | [5 empty] | Non-TXV | 13.15%
Bakersfield | CA | 93307-5366 |  | 2013-06-07 | 2013-06-07 18:21 | 2013-06-07 18:21 | CARRIER - 48XPN036060311 | 149 | 0 | Yes | Yes | 26.7 | 20.8 | 5.9 | E3614496027F4FF2964B19E9F309A695 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4849 |  | 2013-09-25 | 2013-09-25 13:40 | 2013-09-25 16:25 | LENNOX - HS26-036-4P | 87 | 3 | Yes | Yes | 16.6 | 16.1 | 0.5 | E485DAC577C143CA9EA1F47BD475D2EE |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Fresno | CA | 93706-5552 |  | 2013-09-12 | 2013-09-12 10:57 | 2013-09-12 11:30 | YORK - 02GH036N06406C | 112 | 4.9 | Yes | Yes | 24.6 | 19.9 | 4.7 | F81141A0DE4D493DA10B7A6B0CF68589 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
San Jose | CA | 95127-2444 |  | 2013-07-05 | 2013-07-05 09:12 | 2013-07-05 09:59 | WEATHER KING - 3237-3-40A | 85 | 9.9 | Yes | Yes | 25.5 | 21.9 | 3.6 | 69D2D73FF7B94058A3ED0FFAE1349996 |  | R22 | Non-TXV |  | 11.65% | 0.88353 | 22.38% | [5 empty] | Non-TXV | 11.65%
Woodland | CA | 95695-4843 |  | 2013-06-13 | 2013-06-13 13:47 | 2013-06-13 13:59 | PAYNE - PA10JA036-C | 76 | 6.5 | Yes | Yes | 17.5 | 18.2 | -0.7 | F5873F454FA84097822EFE056F79BA08 |  | R22 | Non-TXV |  | 8.553% | 0.91447 | 16.44% | [5 empty] | Non-TXV | 8.553%
Cottonwood | CA | 96022-8540 |  | 2013-06-25 | 2013-06-25 11:39 | 2013-06-25 14:23 | ARMSTRONG - SCU12G42A1 | 115 | 4.4 | Yes | Yes | 18.4 | 21.3 | -2.9 | E025691998694AFFBDC440214D11576B |  | R22 | Non-TXV |  | 3.826% | 0.96174 | 7.353% | [5 empty] | Non-TXV | 3.826%
Cottonwood | CA | 96022-0000 |  | 2013-06-28 | 2013-06-28 13:58 | 2013-06-28 14:14 | GOODMAN - CK036 1AB | 152 | 5.5 | Yes | Yes | 19.1 | 20.7 | -1.6 | E3978C7BF21046549F6DA69D5BE9FC09 |  | R22 | Non-TXV |  | 3.618% | 0.96382 | 6.954% | [5 empty] | Non-TXV | 3.618%
Cottonwood | CA | 96022-0000 |  | 2013-06-28 | 2013-06-28 14:17 | 2013-06-28 14:36 | GOODMAN - CLJ24 1 | 73 | 5 | Yes | Yes | 20.3 | 20.2 | 0.1 | 3465A30F9AEB441D841B4594EB535EAA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.849% | 0.93151 | 13.16% | [5 empty] | Non-TXV | 6.849%
Selma | CA | 93662-2649 |  | 2013-06-19 | 2013-06-19 11:48 | 2013-06-19 11:48 | CARRIER - UNK | 74 | 0 | Yes | Yes | 21.6 | 20.6 | 1 | FEDEE7843B844888997820D5CDFBB750 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1282 |  | 2013-09-10 | 2013-09-10 11:37 | 2013-09-10 11:53 | UNITARY PRODUCTS GROUP - AC024X1222A | 71 | 2.3 | Yes | Yes | 20.8 | 19.5 | 1.3 | E21DA141114B423DB7E693E08A1D2D65 |  | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.225% | [5 empty] | Non-TXV | 3.239%
Bakersfield | CA | 93313-4949 |  | 2013-06-24 | 2013-06-24 19:04 | 2013-06-24 19:04 | YORK - H2RA036S06E | 63 | 0 | Yes | Yes | 21.2 | 21 | 0.2 | 3612365D48A84B6BAF2DE4FF444C0E5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2013-06-19 | 2013-06-19 12:56 | 2013-06-19 13:19 | YORK - DINP030N05606A | 73 | 13.4 | Yes | Yes | 18.4 | 19.9 | -1.5 | 64D61B061A464E66B7A71DFF1F43F2A0 |  | R22 | Non-TXV |  | 18.36% | 0.81644 | 35.28% | [5 empty] | Non-TXV | 18.36%
Bakersfield | CA | 93305-1877 |  | 2013-07-09 | 2013-07-09 09:15 | 2013-07-09 09:15 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.9 | 21 | -2.1 | 7D354C7FD8394C2F89649B2FEF39D9C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4229 |  | 2013-06-03 | 2013-06-03 15:35 | 2013-06-03 17:06 | RUUD - UNK | 83 | 2.9 | Yes | Yes | 23 | 20 | 3 | D237D3DE7525435AA39C05614E8B7D88 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
San Jose | CA | 95111-3097 |  | 2013-10-07 | 2013-10-07 13:13 | 2013-10-07 13:31 | INTERTHERM - UNK | 84 | 4.2 | Yes | Yes | 19.9 | 20.4 | -0.5 | 28160948FF32485184E7AC37649FF0DB |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Arvin | CA | 93203-1237 |  | 2013-09-10 | 2013-09-10 16:47 | 2013-09-10 17:14 | UNITARY PRODUCTS GROUP - AC024X122A | 116 | 9.3 | Yes | Yes | 20.9 | 20.8 | 0.1 | 319D90DB7FD34428B73A970D9E5DEFEB |  | R22 | Non-TXV |  | 8.017% | 0.91983 | 15.41% | [5 empty] | Non-TXV | 8.017%
Bakersfield | CA | 93312-6607 |  | 2013-06-26 | 2013-06-26 18:16 | 2013-06-26 18:36 | YORK - AC042X1021A | 84 | 19 | Yes | Yes | 23.3 | 22.1 | 1.2 | 167A09984C5940E29C4BD94C98F54F18 |  | R22 | Non-TXV |  | 22.62% | 0.77381 | 43.47% | [5 empty] | Non-TXV | 22.62%
Sanger | CA | 93657-2299 |  | 2013-08-08 | 2013-08-08 10:05 | 2013-08-08 10:27 | ARCOAIRE - NAC224AKA5 | 79 | 4 | Yes | Yes | 17.9 | 19 | -1.1 | BA46B0B2EE994082A79B798622D1685C |  | R22 | TXV |  | 5.063% | 0.94937 | 9.731% | [5 empty] | TXV | 5.063%
Bakersfield | CA | 93306-2114 |  | 2013-09-16 | 2013-09-16 12:13 | 2013-09-16 12:13 | AMANA - PGD60C0902E | 139 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | BA6CC94C5A91483899483E31B40EA691 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-0916 |  | 2013-06-05 | 2013-06-05 14:20 | 2013-06-05 14:57 | BRYANT - 563CNO36 C | 101 | 16.5 | Yes | Yes | 21.2 | 19.5 | 1.7 | A7B0786609DC401A95F582D53C45B25F |  | R22 | Non-TXV |  | 16.34% | 0.83663 | 31.4% | [5 empty] | Non-TXV | 16.34%
Arvin | CA | 93203-1237 |  | 2013-09-09 | 2013-09-09 13:11 | 2013-09-09 13:39 | UNITARY PRODUCTS GROUP - ACO24X1222A | 71 | 2.5 | Yes | Yes | 22.1 | 19.5 | 2.6 | 93B5BBB205114151A5F6DC737CCB5695 |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
Sanger | CA | 93657-2299 |  | 2013-08-13 | 2013-08-13 09:53 | 2013-08-13 10:12 | OTHER - NAC024AKC3 | 71 | -4.2 | Yes | Yes | 20 | 19.8 | 0.2 | 26A900DF9AE0458E8A30E6C6671580C3 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Selma | CA | 93662-3127 |  | 2013-06-19 | 2013-06-19 09:16 | 2013-06-19 09:41 | DAY & NIGHT - 585HJ030040 | 68 | 3.1 | Yes | Yes | 25.8 | 20.6 | 5.2 | 3DA055EE120446C38D0DF2A034AF3FA8 |  | R22 | Non-TXV |  | 4.559% | 0.95441 | 8.761% | [5 empty] | Non-TXV | 4.559%
Fresno | CA | 93725-1242 |  | 2013-06-25 | 2013-06-25 14:43 | 2013-06-25 15:19 | CARRIER - UNK | 80 | -4.7 | Yes | Yes | 19.8 | 18.6 | 1.2 | C258ADD09D3F4B75B67EFF336BF38317 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Sanger | CA | 93657-2299 |  | 2013-08-06 | 2013-08-06 09:19 | 2013-08-06 09:38 | ARCOAIRE - NACO24AKB1 | 67 | 3.9 | Yes | Yes | 16.5 | 18.6 | -2.1 | 61EA07F45C4E49C6A633A0BE14465CBD |  | R22 | TXV |  | 5.821% | 0.94179 | 11.19% | [5 empty] | TXV | 5.821%
Fresno | CA | 93722-2889 |  | 2013-07-12 | 2013-07-12 13:25 | 2013-07-12 13:52 | RHEEM - RARM036JNZ | 146 | -5.8 | Yes | Yes | 20.4 | 19.9 | 0.5 | 43D08B72207E46619CDA312A9754B54C |  | R410A | TXV |  | -3.973% | 1.0397 | 1.113% |  |  |  |  | TXV |  |  | -3.973%
Bakersfield | CA | 93306-3956 |  | 2013-07-22 | 2013-07-22 18:01 | 2013-07-22 18:01 | PAYNE - 42RAC158K | 88 | 0 | Yes | Yes | 21.1 | 20.8 | 0.3 | F1C3DE03BD7249BFAF516EF0569E442E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1553 |  | 2013-05-28 | 2013-05-28 09:14 | 2013-05-28 09:38 | RHEEM - 13AJN30A01 | 75 | 4.3 | Yes | Yes | 19.4 | 18.2 | 1.2 | 90CF0FD36A8449E5A087F4791BF53BDC |  | R410A | Non-TXV |  | 5.733% | 0.94267 | 11.02% | [5 empty] | Non-TXV | 5.733%
Sanger | CA | 93657-2747 |  | 2013-06-21 | 2013-06-21 13:41 | 2013-06-21 14:01 | TEMPSTAR - T2A369GKA100 | 218 | 10 | Yes | Yes | 22.7 | 21.5 | 1.2 | CD46DAFEEAD2488BAC2F60F814AC36A5 |  | R22 | TXV |  | 4.587% | 0.95413 | 8.816% | [5 empty] | TXV | 4.587%
Sanger | CA | 93657-2747 |  | 2013-06-21 | 2013-06-21 14:04 | 2013-06-21 16:20 | TEMPSTAR - T2A369GKA100 | 218 | 24.9 | Yes | Yes | 19.5 | 20.4 | -0.9 | 7364F03DD561436F868E45848DF58D71 |  | R22 | TXV |  | 11.42% | 0.88578 | 21.95% | [5 empty] | TXV | 11.42%
Fresno | CA | 93705-2646 |  | 2013-09-21 | 2013-09-21 12:02 | 2013-09-21 12:18 | GOODMAN - PGJ024050-A1 | 60 | 3.6 | Yes | Yes | 15.8 | 18.7 | -2.9 | CA14AC99809A46ECBDBE58CDB2CA0B2B |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Gilroy | CA | 95020-3935 |  | 2013-07-30 | 2013-07-30 09:41 | 2013-07-30 09:41 | GOODMAN - GSC130181CA | 85 | 0 | Yes | Yes | 20.4 | 18.2 | 2.2 | 83B16DDA410B4AC2A39FB3D396E61399 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3002 |  | 2013-09-25 | 2013-09-25 13:22 | 2013-09-25 13:40 | ICP - PGF348080K01A1 | 208 | 26.7 | Yes | Yes | 19.2 | 20.4 | -1.2 | BFE2AEA1F81049219B6F81A1A96D4BFA |  | R22 | TXV |  | 12.84% | 0.87163 | 24.67% | [5 empty] | TXV | 12.84%
Fresno | CA | 93705-2646 |  | 2013-09-21 | 2013-09-21 11:26 | 2013-09-21 11:45 | GOODMAN - PGJ024050-1 | 60 | 2.8 | Yes | Yes | 17.2 | 17.9 | -0.7 | 6D122718F33E43CC8A584F02941B5D6F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Sonoma | CA | 95476-8031 |  | 2013-05-31 | 2013-05-31 15:21 | 2013-05-31 15:21 | OTHER - C-3560-GA | 78 | 0 | Yes | Yes | 18.5 | 21 | -2.5 | E7D0A34E59C6497BA930A0214FD9A6EC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4419 |  | 2013-07-10 | 2013-07-10 16:56 | 2013-07-10 17:20 | LENNOX - 10GCS030753PA | 51 | 5.3 | Yes | Yes | 22.1 | 21.5 | 0.6 | 907E1224FD7548FAA469CCC4883D6276 |  | R22 | Non-TXV |  | 10.39% | 0.89608 | 19.97% | [5 empty] | Non-TXV | 10.39%
Brentwood | CA | 94513-2520 |  | 2013-07-03 | 2013-07-03 11:18 | 2013-07-03 12:03 | AMANA - ZRCF42U01D | 135 | 4 | Yes | Yes | 16.8 | 17.7 | -0.9 | B53D5F6AC6264F24AF93C2E63A496485 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Antioch | CA | 94509-5531 |  | 2013-06-04 | 2013-06-04 10:45 | 2013-06-04 10:45 | LENNOX - 14ACX-047-230-01 | 179 | 0 | Yes | Yes | 16.3 | 19.1 | -2.8 | DF428A40CDAC4A528EAE4209BC88A1A0 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95138-1728 |  | 2013-07-05 | 2013-07-05 10:08 | 2013-07-05 10:46 | BDP - 561CJ042-A | 85 | 12.9 | Yes | Yes | 20.8 | 18.5 | 2.4 | C9FAA8C090FA499F9E3F5FE871CED497 |  | R22 | TXV |  | 15.18% | 0.84824 | 29.17% | [5 empty] | TXV | 15.18%
Cottonwood | CA | 96022-0000 |  | 2013-07-18 | 2013-07-18 14:25 | 2013-07-18 15:24 | BDP - 563CN042 A | 131 | 5.6 | Yes | Yes | 22.4 | 20.4 | 2 | DC334CDA5486411AB70032B84803FB26 |  | R22 | Non-TXV |  | 4.275% | 0.95725 | 8.215% | [5 empty] | Non-TXV | 4.275%
San Jose | CA | 95117-4206 |  | 2013-06-27 | 2013-06-27 15:07 | 2013-06-27 15:07 | DAY & NIGHT - 597BN024-A | 134 | 0 | Yes | Yes | 22.2 | 19.2 | 3 | FA3954BE057F41F49B5164FDCF7523C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4957 |  | 2013-06-24 | 2013-06-24 16:13 | 2013-06-24 16:13 | RUUD - EAFF-043JAZ | 99 | 0 | Yes | Yes | 20.4 | 22 | -1.6 | 429FB729B56645FDB3E017FC6365ED91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2249 |  | 2013-05-31 | 2013-05-31 14:05 | 2013-05-31 14:35 | HEIL - PGC036K100A | 66 | 8.2 | Yes | Yes | 18.6 | 19.6 | -1 | ED0F7EE3BDC7492C9DAAFA6BF4F6BF6E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.42% | 0.87576 | 23.88% | [5 empty] | Non-TXV | 12.42%
Bakersfield | CA | 93308-7404 |  | 2013-07-12 | 2013-07-12 18:07 | 2013-07-12 18:07 | TRANE - 2A7A2036A1000AA | 96 | 0 | Yes | Yes | 20.7 | 21.1 | -0.4 | 17C44E6878314E008259ABC0204D3B2D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7404 |  | 2013-07-12 | 2013-07-12 18:26 | 2013-07-12 18:26 | TRANE - YCY036G1M0AC | 129 | 0 | Yes | Yes | 22.3 | 20.8 | 1.5 | 79C35A5A53B340499B204DC2618120CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7404 |  | 2013-07-12 | 2013-07-12 18:45 | 2013-07-12 18:45 | TRANE - YCY024G1M01C | 101 | 0 | Yes | Yes | 18.5 | 20.1 | -1.6 | 9F1C171FBC4B4592976C726BF690BE62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9329 |  | 2013-05-29 | 2013-05-29 12:51 | 2013-05-29 12:51 | BDP - 585HJ030040 | 68 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | 4C75EAF8D9C74326A5367DF4A02BF6D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2033 |  | 2013-06-03 | 2013-06-03 09:02 | 2013-06-03 09:27 | ICP - NAC036AKAQ5 | 87 | 10.7 | Yes | Yes | 21.2 | 20.1 | 1.1 | 880A29DCA702468BA28B3D5B1F25951D |  | R22 | Non-TXV |  | 12.3% | 0.87701 | 23.64% | [5 empty] | Non-TXV | 12.3%
Bakersfield | CA | 93308-3103 |  | 2013-07-11 | 2013-07-11 16:42 | 2013-07-11 17:12 | TRANE - YCP036F1M0AB | 109 | 18.4 | Yes | Yes | 21.5 | 20.2 | 1.3 | 80FEB0D1DA6C42B98551D0EE5AEA6414 |  | R22 | Non-TXV |  | 16.88% | 0.83119 | 32.44% | [5 empty] | Non-TXV | 16.88%
Fresno | CA | 93706-4364 |  | 2013-06-24 | 2013-06-24 19:09 | 2013-06-24 19:09 | - EABD-F0305B | 135 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 719C96824B6A489C8A0DEE7403493716 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2916 |  | 2013-06-28 | 2013-06-28 12:32 | 2013-06-28 12:32 | LENNOX - HS29-036-2P | 70 | 0 | Yes | Yes | 15.4 | 18.3 | -2.9 | D7F74B7546C24E56A2E8DA6D109972E0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1008 |  | 2013-07-19 | 2013-07-19 13:51 | 2013-07-19 14:11 | CARRIER - 48GX-036090301AD | 88 | 2.6 | Yes | Yes | 21.5 | 20.4 | 1.1 | 2E7F3C3C037742529C64D6FA740EE82C |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Cottonwood | CA | 96022-7709 |  | 2013-07-12 | 2013-07-12 09:01 | 2013-07-12 09:34 | YORK - TCGD30S21S1HA | 58 | -5.8 | Yes | Yes | 16.4 | 16.9 | -0.5 | 3A6D6E20760D4A99978E07A65AE7DAD4 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Redding | CA | 96003-7556 |  | 2013-07-15 | 2013-07-15 10:55 | 2013-07-15 11:15 | AMANA - PGD60C1152E | 169 | 7.5 | Yes | Yes | 18 | 20.4 | -2.4 | 8CDEABE8103B4B5A8F5F9657CC9124EB |  | R22 | Non-TXV |  | 4.438% | 0.95562 | 8.529% | [5 empty] | Non-TXV | 4.438%
Selma | CA | 93662-2932 |  | 2013-06-19 | 2013-06-19 13:03 | 2013-06-19 13:03 | CARRIER - 48ESNA3606030 | 100 | 0 | Yes | Yes | 20.1 | 19.7 | 0.4 | 07483369A9BD41FA9163AAAB533042C4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4693 |  | 2013-06-17 | 2013-06-17 11:05 | 2013-06-17 13:32 | YORK - H2RC048S06HG | 119 | 11.8 | Yes | Yes | 15.8 | 18.8 | -3 | E865514867704B508E83D9ED839B088E |  | R22 | Non-TXV |  | 9.916% | 0.90084 | 19.06% | [5 empty] | Non-TXV | 9.916%
Fresno | CA | 93722-2708 |  | 2013-10-31 | 2013-10-31 13:51 | 2013-10-31 14:21 | CARRIER - 38BR036300 | 122 | 4.6 | Yes | Yes | 20.4 | 19.3 | 1.1 | 60120C0455134D20BEFC8C5200E71CA2 |  | R22 | TXV |  | 3.77% | 0.9623 | 7.246% | [5 empty] | TXV | 3.77%
Shafter | CA | 93263-2209 |  | 2013-08-11 | 2013-08-11 17:26 | 2013-08-11 17:32 | PAYNE - PY2PNB042060AAAA | 118 | 4.3 | Yes | Yes | 26.7 | 20.9 | 5.8 | B71CE6CC58EF4269BA4C3ABB70817558 |  | R22 | Non-TXV |  | 3.644% | 0.96356 | 7.003% | [5 empty] | Non-TXV | 3.644%
Fresno | CA | 93728-1913 |  | 2013-06-04 | 2013-06-04 11:06 | 2013-06-04 11:42 | CARRIER - UNK | 81 | 2.9 | Yes | Yes | 22.3 | 20.9 | 1.4 | 1AD8F6DCE05F49568143EDFC47C5B3C2 |  | R22 | Non-TXV |  | 3.58% | 0.9642 | 6.88% | [5 empty] | Non-TXV | 3.58%
San Jose | CA | 95139-1205 |  | 2013-06-27 | 2013-06-27 14:07 | 2013-06-27 14:58 | CARRIER - 38BRC024330 | 105 | 12.5 | Yes | Yes | 22.4 | 18.5 | 3.9 | 82BE04D3E895440FB08D70F81139F3CC |  | R22 | TXV |  | 11.9% | 0.88095 | 22.88% | [5 empty] | TXV | 11.9%
Bakersfield | CA | 93308-5402 |  | 2013-06-05 | 2013-06-05 19:57 | 2013-06-05 19:57 | ICP - PGC030K060A | 56 | 0 | Yes | Yes | 22 | 22.1 | -0.1 | 170FEDFFD87A4D3FB31F6FE3535C127C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1106 |  | 2013-06-06 | 2013-06-06 08:47 | 2013-06-06 09:12 | BDP - 585A036080VAC | 67 | 2 | Yes | Yes | 20.7 | 20.7 | 0.1 | 9C8615FD2AD5438E8332842BE1C14833 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Hayward | CA | 94541-2300 |  | 2013-06-10 | 2013-06-10 13:31 | 2013-06-10 20:03 | TRANE - 5A1C0302-A | 85 | 5 | Yes | Yes | 18.9 | 19.4 | -0.5 | 2DF4589260A3408BBE8C1AAFB54009BC |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Fresno | CA | 93704-6039 |  | 2013-06-14 | 2013-06-14 14:50 | 2013-06-14 14:50 | BRYANT - 583ANW024040AAAD | 53 | 0 | Yes | Yes | 25.1 | 19.8 | 5.3 | 5ADE445948F846E9B3DC872E6E40716D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1106 |  | 2013-08-09 | 2013-08-09 10:27 | 2013-08-09 10:47 | AIRE-FLO - GPG13420701AB | 107 | -7.6 | Yes | Yes | 24.8 | 19.9 | 4.9 | ACC1A6B247F14AA095E416490022A665 |  | R22 | Non-TXV |  | -7.103% | 1.071 | 1.989% |  |  |  |  | Non-TXV |  |  | -7.103%
Bakersfield | CA | 93308-5403 |  | 2013-09-04 | 2013-09-04 17:54 | 2013-09-04 18:11 | ICP - PGC030K060A | 56 | 7.2 | Yes | Yes | 22.4 | 21.5 | 0.9 | F2D9A203C5DD42988AB6548A97EC2318 |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
Bakersfield | CA | 93306-7460 |  | 2013-07-23 | 2013-07-23 19:45 | 2013-07-23 19:45 | GOODMAN - GSC130601BC | 169 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | 7645969B4AC74A868FD0E18C5A501C55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94583-3706 |  | 2013-09-12 | 2013-09-12 12:54 | 2013-09-12 12:55 | RUUD - UACB-042JAS | 50 | 4.3 | Yes | Yes | 15.9 | 18.2 | -2.3 | CB9DB040180A45C0AB469E6533187214 |  | R22 | Non-TXV |  | 8.6% | 0.914 | 16.53% | [5 empty] | Non-TXV | 8.6%
Fresno | CA | 93722-5711 |  | 2013-06-13 | 2013-06-13 17:13 | 2013-06-13 18:25 | COLEMAN - DAYPF030N070A | 73 | 6.1 | Yes | Yes | 24.5 | 23.4 | 1.1 | 2088DB9421464550B423B65E29122EF6 |  | R22 | TXV |  | 8.356% | 0.91644 | 16.06% | [5 empty] | TXV | 8.356%
Fresno | CA | 93722-3321 |  | 2013-07-30 | 2013-07-30 09:49 | 2013-07-30 10:16 | CARRIER - 48NLT030300 | 85 | 3.9 | Yes | Yes | 22.5 | 20.7 | 1.8 | 903F103DCEBA4491B9732994A8C63246 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Cottonwood | CA | 96022-7766 |  | 2013-06-25 | 2013-06-25 17:11 | 2013-06-25 17:27 | RUUD - UAKB 042JAZ | 96 | 3 | Yes | Yes | 18.6 | 21 | -2.4 | 7B324A444CC445DBA0880FFC28463C0F |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Concord | CA | 94521-2910 |  | 2013-06-11 | 2013-06-11 14:10 | 2013-06-11 14:10 | CARRIER - 38CKC030---331 | 64 | -5.3 | Yes | Yes | 15.7 | 17.5 | -1.8 | DA83FAEF0AEE4E0E951F65D2E21FF1D4 | Remove refrigerant: 5.3 oz Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.281% | 1.0828 | 2.319% |  |  |  |  | Non-TXV |  |  | -8.281%
Sanger | CA | 93657-2042 |  | 2013-10-21 | 2013-10-21 12:59 | 2013-10-21 13:29 | DAY & NIGHT - 580ANW042060 | 102 | 20.4 | Yes | Yes | 23 | 19.9 | 3.1 | 617EFF34FA23468DA85545A647333967 |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Antioch | CA | 94509-3508 |  | 2013-05-30 | 2013-05-30 10:20 | 2013-05-30 10:36 | ARCOAIRE - R2A336GKC1 | 83 | -6 | Yes | Yes | 19.3 | 19.3 | 0 | 612F87B3885F46AF91B4531787BA8243 |  | R22 | TXV |  | -7.229% | 1.0723 | 2.024% |  |  |  |  | TXV |  |  | -7.229%
Shafter | CA | 93263-2256 |  | 2013-07-24 | 2013-07-24 20:17 | 2013-07-24 20:51 | GOODMAN - GPG103007C1A | 50 | 3 | Yes | Yes | 26.4 | 25.9 | 0.5 | 68B7B8501ED444398E8EE43EBD26978C |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Fresno | CA | 93722-9768 |  | 2013-06-14 | 2013-06-14 11:17 | 2013-06-14 11:43 | OTHER - UNK | 100 | 4.5 | Yes | Yes | 20.5 | 20.4 | 0.1 | 5D4752CC49EE4C5CBF572DE9A55C1E5F |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Concord | CA | 94521-4241 |  | 2013-06-21 | 2013-06-21 10:24 | 2013-06-21 10:44 | CARRIER - 24APA5360030010 | 161 | 9.3 | Yes | Yes | 19.5 | 21.5 | -2 | B19964F5F1E24E7184C65621EB428921 |  | R410A | TXV |  | 5.776% | 0.94224 | 11.1% | [5 empty] | TXV | 5.776%
Arvin | CA | 93203-1281 |  | 2013-09-10 | 2013-09-10 12:13 | 2013-09-10 12:34 | UNITARY PRODUCTS GROUP - AC024X1222A | 71 | 5.2 | Yes | Yes | 22.1 | 18.8 | 3.3 | FABBF7292F9E46708FA481B215F8B55E |  | R22 | Non-TXV |  | 7.324% | 0.92676 | 14.08% | [5 empty] | Non-TXV | 7.324%
Bakersfield | CA | 93307-0000 |  | 2013-06-07 | 2013-06-07 10:31 | 2013-06-07 11:09 | YORK - 18ECW045GA | 71 | 5.2 | Yes | Yes | 18.3 | 19.2 | -0.9 | 547C2C96E8614270BC4244D5BAF98B11 |  | R22 | Non-TXV |  | 7.324% | 0.92676 | 14.08% | [5 empty] | Non-TXV | 7.324%
Lamont | CA | 93241-1219 |  | 2013-09-11 | 2013-09-11 12:15 | 2013-09-11 12:46 | GOODMAN - GPG1336045M41BA | 70 | 2.1 | Yes | Yes | 20.8 | 19.3 | 1.5 | 68389298BB60406A88D0936227DB97B9 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93309-3227 |  | 2013-08-04 | 2013-08-04 11:20 | 2013-08-04 11:20 | BRYANT - 574DNWA36060NA | 100 | 0 | Yes | Yes | 21.8 | 21.3 | 0.5 | D00FCEAB11964B52BA5D7A4FD37FDEF1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3714 |  | 2013-10-21 | 2013-10-21 10:39 | 2013-10-21 11:12 | CARRIER - UNK | 84 | 3.7 | Yes | Yes | 19.3 | 19.7 | -0.4 | 2C8095E5A14E4FA3914FEE802B42EBC2 |  | R22 | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Fresno | CA | 93728-1742 |  | 2013-06-04 | 2013-06-04 11:45 | 2013-06-04 12:32 | LENNOX - 10GC036X 75 2PA | 58 | 2.9 | Yes | Yes | 22.6 | 20.1 | 2.5 | 472BB2F9248A4D2C88D663F536492522 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93705-5016 |  | 2013-07-03 | 2013-07-03 16:59 | 2013-07-03 19:33 | GOODMAN - GPG1360090BB | 164 | 8.7 | Yes | Yes | 23.4 | 19.2 | 4.2 | B18CEE7EEB2E499491D8CB4D44A9E947 |  | R22 | TXV |  | 5.305% | 0.94695 | 10.19% | [5 empty] | TXV | 5.305%
Fresno | CA | 93704-5847 |  | 2013-06-14 | 2013-06-14 13:24 | 2013-06-14 14:04 | YORK - DAYP-F036N070A | 108 | 4.1 | Yes | Yes | 21.5 | 20.4 | 1.1 | 7BDF3D6485C74E85B633E59592FF33AA |  | R22 | Non-TXV |  | 3.796% | 0.96204 | 7.296% | [5 empty] | Non-TXV | 3.796%
Fresno | CA | 93706-9236 |  | 2013-06-12 | 2013-06-12 14:56 | 2013-06-12 15:18 | YORK - DAYPF042N080A | 150 | 3 | Yes | Yes | 23.9 | 19.6 | 4.4 | 1C91921D0BBA4A07B22A9D7725F9BB79 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2% | 0.98 | 3.844% | [5 empty] | Non-TXV | 2%
Selma | CA | 93662-9489 |  | 2013-06-17 | 2013-06-17 16:53 | 2013-06-17 16:53 | YORK - D4NZ060N09006NXC | 98 | 0 | Yes | Yes | 26.4 | 21.2 | 5.2 | 720A4CEF6F6C4449A40A47AA99F259C1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4516 |  | 2013-07-01 | 2013-07-01 09:01 | 2013-07-01 09:20 | YORK - D1NP036N05606A | 108 | 5 | Yes | Yes | 21.4 | 18.6 | 2.8 | 58B1938A70F34E5392D715398F76CD72 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Antioch | CA | 94509-4231 |  | 2013-05-30 | 2013-05-30 12:37 | 2013-05-30 12:37 | GOODMAN - VSX130481AB | 104 | 0 | Yes | Yes | 17.3 | 19.8 | -2.5 | 5D506CD960104CAA9E5054A3B99FCF67 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9268 |  | 2013-05-31 | 2013-05-31 10:54 | 2013-05-31 11:13 | CARRIER - 38TH030310 | 68 | 4 | Yes | Yes | 15.9 | 13 | 2.9 | 18800B00CE59430CAC23B0AEEDCB5F52 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
San Jose | CA | 95111-2502 |  | 2013-06-27 | 2013-06-27 12:45 | 2013-06-27 13:22 | BRYANT - 5830N836-1 | 55 | 0 | Yes | Yes | 24.7 | 21.9 | 2.8 | 8F0C27DA2156441B9B0417D412DD22E4 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2538 |  | 2013-10-12 | 2013-10-12 11:25 | 2013-10-12 11:49 | RHEEM - RRNL-B-36JK08X | 92 | -11.6 | Yes | Yes | 18.8 | 19.6 | -0.8 | 4EA583090E8A4318A4A4AC248D5F8665 |  | R410A | TXV |  | -12.61% | 1.1261 | 3.531% |  |  |  |  | TXV |  |  | -12.61%
Arvin | CA | 93203-1643 |  | 2013-08-20 | 2013-08-20 13:11 | 2013-08-20 13:27 | BRYANT - 561C030 E | 98 | 5.6 | Yes | Yes | 20.9 | 20.6 | 0.3 | D480590150C84CE4A7178774DFCE8262 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Arvin | CA | 93203-1640 |  | 2013-08-20 | 2013-08-20 13:29 | 2013-08-20 13:45 | BRYANT - 561CJ024 E | 54 | 2 | Yes | Yes | 21.7 | 19.3 | 2.4 | C41855D3B97547ABB03E9351726560DA |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Fresno | CA | 93722-9104 |  | 2013-07-11 | 2013-07-11 13:27 | 2013-07-11 14:46 | DAY & NIGHT - 585EJWO36075ABAF | 82 | 4.8 | Yes | Yes | 23 | 23 | 0 | 1D98496985E74191927CC032CBACDC68 |  | R22 | Non-TXV |  | 5.854% | 0.94146 | 11.25% | [5 empty] | Non-TXV | 5.854%
Bakersfield | CA | 93313-4949 |  | 2013-06-24 | 2013-06-24 19:18 | 2013-06-24 19:34 | YORK - H2RA036506E | 63 | 12.6 | Yes | Yes | 20.6 | 20.4 | 0.2 | 7B2408F0E18C458381B44F403061DC60 |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Lemoore | CA | 93245-4725 |  | 2013-08-28 | 2013-08-28 11:22 | 2013-08-28 11:47 | GOODMAN - CK421C | 86 | 5 | Yes | Yes | 18.8 | 19.2 | -0.4 | 8C53DE2D892543E98EB962996E24245B |  | R22 | Non-TXV |  | 5.814% | 0.94186 | 11.17% | [5 empty] | Non-TXV | 5.814%
Davis | CA | 95616-0711 |  | 2013-06-12 | 2013-06-12 13:32 | 2013-06-12 13:51 | GMC - CKL30-1D | 71 | -5.8 | Yes | Yes | 23.2 | 18.6 | 4.6 | AF23A77A1AA04079B1B1F0A7A920AEF8 |  | R22 | Non-TXV |  | -8.169% | 1.0817 | 2.288% |  |  |  |  | Non-TXV |  |  | -8.169%
Lemoore | CA | 93245-4359 |  | 2013-06-27 | 2013-06-27 12:09 | 2013-06-27 12:40 | TEMPSTAR - PGAA36CIK1 | 77 | 3.7 | Yes | Yes | 22.9 | 19.5 | 3.4 | FD63F084D2614F82910AD347984F6782 |  | R22 | Non-TXV |  | 4.805% | 0.95195 | 9.235% | [5 empty] | Non-TXV | 4.805%
Bakersfield | CA | 93312-3162 |  | 2013-09-26 | 2013-09-26 22:15 | 2013-09-26 22:15 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.7 | 19.9 | -1.2 | 7596A2AB9C4846EEA20B2064999EB221 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-3824 |  | 2013-06-19 | 2013-06-19 15:12 | 2013-06-19 15:32 | CARRIER - UNK | 85 | 6.5 | Yes | Yes | 27.4 | 22.3 | 5.1 | A6E477BC108D4356A4075ACEED001C91 |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Concord | CA | 94521-1818 |  | 2013-06-17 | 2013-06-17 12:24 | 2013-06-17 12:43 | OTHER - TCGD48S41S3A | 73 | 6.9 | Yes | Yes | 17.6 | 20.2 | -2.6 | FC4964303C9148DCA7F7E6C04C27310D |  | R410A | TXV |  | 9.452% | 0.90548 | 18.16% | [5 empty] | TXV | 9.452%
Fresno | CA | 93725-0937 |  | 2013-06-05 | 2013-06-05 15:20 | 2013-06-05 16:45 | CARRIER - 24ABA342A310 | 98 | 4.1 | Yes | Yes | 23.3 | 20.6 | 2.7 | 036C5BB671FC463C8A0EEEBD78762E15 |  | R410A | Non-TXV |  | 4.184% | 0.95816 | 8.04% | [5 empty] | Non-TXV | 4.184%
Arvin | CA | 93203-1640 |  | 2013-08-20 | 2013-08-20 13:46 | 2013-08-20 14:51 | BRYANT - 561CJ024 E | 54 | 2.5 | Yes | Yes | 21.4 | 20.1 | 1.3 | 53F6AC8A125F48D3814E7B5F621041FA |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Concord | CA | 94521-1144 |  | 2013-06-17 | 2013-06-17 11:26 | 2013-06-17 11:50 | CARRIER - 38TXA036330 | 104 | 11 | Yes | Yes | 16.6 | 19.3 | -2.7 | 6572BFDDB9E940428D79F2F97B85EF1B |  | R22 | TXV |  | 10.58% | 0.89423 | 20.33% | [5 empty] | TXV | 10.58%
Bakersfield | CA | 93305-1218 |  | 2013-06-06 | 2013-06-06 19:26 | 2013-06-06 19:26 | BDP - 589ANW048100AEBG | 88 | 0 | Yes | Yes | 24.4 | 21.7 | 2.7 | C3ABC2DE11CE475A8D90C8D897C1BD87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madison | CA | 95653-0000 |  | 2013-08-25 | 2013-08-25 10:39 | 2013-08-25 10:58 | CARRIER - 38BRC036320 | 106 | 3.6 | Yes | Yes | 24.6 | 20.4 | 4.2 | A8B1E9511947491A932686CF2D5DF66C |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Woodland | CA | 95695-3630 |  | 2013-07-12 | 2013-07-12 11:13 | 2013-07-12 11:51 | YORK - H1RC048S06B | 122 | -6.3 | Yes | Yes | 18.1 | 19.5 | -1.4 | 3B38840BFC404628BB17B0EB0D5454FA |  | R22 | Non-TXV |  | -5.164% | 1.0516 | 1.446% |  |  |  |  | Non-TXV |  |  | -5.164%
Sanger | CA | 93657-3905 |  | 2013-08-05 | 2013-08-05 09:35 | 2013-08-05 10:04 | - NAC024AKC3 | 71 | 2.6 | Yes | Yes | 19.5 | 19.3 | 0.2 | A426E1829BA74D9283C4A0DFED82EB73 |  | R22 | TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | TXV | 3.662%
Bakersfield | CA | 93308-9502 |  | 2013-09-19 | 2013-09-19 13:00 | 2013-09-19 13:00 | ICP - PGC024K040A | 58 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 16222A2677C74AFDA52367570DF8F0D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3904 |  | 2013-08-05 | 2013-08-05 09:19 | 2013-08-05 09:38 | CARRIER - NAC024AKC3 | 71 | 6.1 | Yes | Yes | 22.8 | 19.2 | 3.6 | 5EF3C3347C18413CAB4C9123DC8F1A5B |  | R22 | Non-TXV |  | 8.592% | 0.91408 | 16.51% | [5 empty] | Non-TXV | 8.592%
Bakersfield | CA | 93308-2971 |  | 2013-08-29 | 2013-08-29 15:49 | 2013-08-29 16:05 | ICP - PGC024K060A | 58 | 8.7 | Yes | Yes | 22.3 | 21.8 | 0.5 | 61008B2A6FE949D88972269E91C55243 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Coalinga | CA | 93210-1832 |  | 2013-10-02 | 2013-10-02 13:01 | 2013-10-02 14:02 | BRYANT - 574ANW042060NB | 123 | 4 | Yes | Yes | 21 | 19.9 | 1.1 | 1E118AE1FBAC40ADAD2EB7F0CA21A366 |  | R22 | Non-TXV |  | 3.252% | 0.96748 | 6.25% | [5 empty] | Non-TXV | 3.252%
Bakersfield | CA | 93304-6052 |  | 2013-06-18 | 2013-06-18 12:36 | 2013-06-18 12:36 | YORK - SA36G080N-6AA | 99 | 0 | Yes | Yes | 24 | 19.8 | 4.2 | E8E6EE413B1943CFBE668BDF21E5BC0B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-1031 |  | 2013-07-03 | 2013-07-03 08:54 | 2013-07-03 08:54 | NORDYNE - JS5BD-048KA | 85 | 0 | Yes | Yes | 22 | 20.1 | 2 | E31A87E9F62B4E1BA7127E0842B9E261 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-2108 |  | 2013-07-09 | 2013-07-09 12:54 | 2013-07-09 13:14 | LENNOX - GCS2903975 | 58 | 5.5 | Yes | Yes | 25.8 | 21 | 4.8 | 178A1440B1544ABDA04FCF83BA9ABD18 |  | R22 | Non-TXV |  | 9.483% | 0.90517 | 18.22% | [5 empty] | Non-TXV | 9.483%
Bay Point | CA | 94565-6909 |  | 2013-07-01 | 2013-07-01 09:13 | 2013-07-01 09:13 | RHEEM - RAFD-030JAS | 69 | 0 | Yes | Yes | 17.7 | 17.1 | 0.6 | 861C9EB7EA234DCBAE153DF10E8C18B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-1833 |  | 2013-10-02 | 2013-10-02 15:28 | 2013-10-02 21:50 | OTHER - 80WE30GL | 90 | 4 | Yes | Yes | 23.3 | 21.8 | 1.5 | C4E5A20F75A148B3BCBCE14F7BF9DA3C |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Shafter | CA | 93263-9629 |  | 2013-08-05 | 2013-08-05 19:10 | 2013-08-05 19:13 | GOODMAN - GPG10300701A | 50 | 4.8 | Yes | Yes | 26.8 | 22 | 4.8 | 3FF16E96269C41FAA56967F1D996097C |  | R22 | Non-TXV |  | 9.6% | 0.904 | 18.45% | [5 empty] | Non-TXV | 9.6%
Willits | CA | 95490-4420 |  | 2013-08-19 | 2013-08-19 13:11 | 2013-08-19 13:32 | ALLEGIANCE - 2A7A2042A1000AA | 95 | 5.9 | Yes | Yes | 23.9 | 20.4 | 3.5 | 4926D0CD59E44F8F910DC590D414688E |  | R22 | TXV |  | 6.211% | 0.93789 | 11.94% | [5 empty] | TXV | 6.211%
Bakersfield | CA | 93306-5072 |  | 2013-07-23 | 2013-07-23 08:57 | 2013-07-23 08:57 | GOODMAN - GSC130301EB | 66 | 0 | Yes | Yes | 19.6 | 21 | -1.4 | 14560673E66747F08B6100E63FF984D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2423 |  | 2013-05-30 | 2013-05-30 10:17 | 2013-05-30 10:17 | PAYNE - PY2PNB042060AAAA | 118 | 0 | Yes | Yes | 24.4 | 19.9 | 4.5 | 6DD2E08C89D64E2C820A5DCF0943CC07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2729 |  | 2013-06-17 | 2013-06-17 10:50 | 2013-06-17 11:20 | PAYNE - PA13NR048-H | 140 | -9.9 | Yes | Yes | 17 | 17.6 | -0.6 | 0BC19235626D484BB972350572785EDE |  | R22 | Non-TXV |  | -7.071% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.071%
Redding | CA | 96003-9630 |  | 2013-07-16 | 2013-07-16 09:30 | 2013-07-16 10:12 | PAYNE - PA12NAD0484001E0030 | 144 | 7.9 | Yes | Yes | 20.4 | 20.2 | 0.2 | 3A541AE8784B440EAE01A086D006D2ED |  | R22 | Non-TXV |  | 5.486% | 0.94514 | 10.54% | [5 empty] | Non-TXV | 5.486%
Bakersfield | CA | 93309-5126 |  | 2013-08-15 | 2013-08-15 16:24 | 2013-08-15 18:00 | RHEEM - RAHE-042JAS | 85 | 5.6 | Yes | Yes | 19.9 | 21.1 | -1.2 | 9759B697856D45ECA54CB1E8B0E9C9B2 |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Arvin | CA | 93203-1237 |  | 2013-09-10 | 2013-09-10 15:11 | 2013-09-10 15:39 | UNITARY PRODUCTS GROUP - AC024X1222A | 73 | 3.6 | Yes | Yes | 22.7 | 20.1 | 2.6 | 3D3A3534A7654AEAA09FD575E7A32398 |  | R22 | Non-TXV |  | 4.932% | 0.95068 | 9.477% | [5 empty] | Non-TXV | 4.932%
Shafter | CA | 93268-0000 |  | 2013-08-11 | 2013-08-11 16:44 | 2013-08-11 17:07 | GOODMAN - PG13300451AA | 77 | -7.2 | Yes | Yes | 25.2 | 19.8 | 5.4 | C9EB53C0E1294817996E41DD7B568632 |  | R22 | Non-TXV |  | -9.351% | 1.0935 | 2.619% |  |  |  |  | Non-TXV |  |  | -9.351%
San Jose | CA | 95111-3097 |  | 2013-10-07 | 2013-10-07 13:37 | 2013-10-07 14:06 | UNITARY PRODUCTS GROUP - TCGD36S21S1A | 75 | 4.1 | Yes | Yes | 21.7 | 21.5 | 0.2 | 888A192C846F456CA2B3895C5E9E3482 |  | R22 | Non-TXV |  | 5.467% | 0.94533 | 10.51% | [5 empty] | Non-TXV | 5.467%
Bakersfield | CA | 93301-2563 |  | 2013-08-15 | 2013-08-15 18:14 | 2013-08-15 18:14 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 22 | 21.2 | 0.8 | 6DFD5F8E369A43FBA4B762285D06CB63 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3097 |  | 2013-10-07 | 2013-10-07 14:35 | 2013-10-07 16:57 | GIBSON - JS3BA 42 KA | 86 | 17.4 | Yes | Yes | 22.3 | 20.9 | 1.4 | F2A640B8675B4F31BB4F2A6544633BC7 |  | R22 | Non-TXV |  | 20.23% | 0.79767 | 38.88% | [5 empty] | Non-TXV | 20.23%
Sunnyvale | CA | 94086-8724 |  | 2013-09-27 | 2013-09-27 09:14 | 2013-09-27 09:14 | - BRCQ0241BE | 36 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | B12C9573933640528406F4087D616C0D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1282 |  | 2013-09-10 | 2013-09-10 15:40 | 2013-09-10 16:33 | UNITARY PRODUCTS GROUP - AC024X122A | 71 | 7.1 | Yes | Yes | 18.6 | 19.5 | -0.9 | 59EE1B0128A54BE99F554678DD70EE38 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Sanger | CA | 93657-3905 |  | 2013-08-05 | 2013-08-05 15:12 | 2013-08-05 15:38 | ARCOAIRE - NAC224AKC3 | 86 | 7.6 | Yes | Yes | 20.2 | 19.7 | 0.5 | A03C5227A3D944F0BC933901987F8D2A |  | R22 | TXV |  | 8.837% | 0.91163 | 16.98% | [5 empty] | TXV | 8.837%
San Jose | CA | 95123-3141 |  | 2013-10-09 | 2013-10-09 16:15 | 2013-10-09 18:52 | YORK - H1RA024S06A | 54 | 1.9 | Yes | Yes | 23.6 | 21.5 | 2.1 | 06124378024147EAAA9DA01037FAA7A9 |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
San Ramon | CA | 94583-2632 |  | 2013-09-12 | 2013-09-12 12:07 | 2013-09-12 12:19 | BRYANT - 563CN048-H | 131 | 13.2 | Yes | Yes | 18.1 | 17.6 | 0.5 | 4E78599838764F369C5CA1DD26B5A110 |  | R22 | Non-TXV |  | 10.08% | 0.89924 | 19.36% | [5 empty] | Non-TXV | 10.08%
Fresno | CA | 93725-0937 |  | 2013-06-21 | 2013-06-21 11:12 | 2013-06-21 11:12 | CARRIER - 24ABA2348A300 | 85 | 0 | Yes | Yes | 25.4 | 20.4 | 5 | E57A52DC44294FA6B2E6D4B510E4D5F7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Buttonwillow | CA | 93206-9701 |  | 2013-10-15 | 2013-10-15 17:36 | 2013-10-15 17:38 | RHEEM - RRNL-B036JK08X | 92 | 4.7 | Yes | Yes | 21.4 | 19.3 | 2.1 | 2A7F1CA58C254458A45119F103636424 |  | R22 | TXV |  | 5.109% | 0.94891 | 9.818% | [5 empty] | TXV | 5.109%
Fresno | CA | 93722-3370 |  | 2013-06-19 | 2013-06-19 10:24 | 2013-06-19 10:47 | CARRIER - UNK | 85 | -5 | Yes | Yes | 23.7 | 19.8 | 3.9 | 854ABD8B4AD04F67A8E4BFAA28102FD4 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93307-4368 |  | 2013-08-05 | 2013-08-05 09:35 | 2013-08-05 09:51 | GOODMAN - CPLJ42-1B | 147 | 22.8 | Yes | Yes | 19.2 | 21 | -1.8 | 5E166C7784714A618EC47DF012AAF530 |  | R22 | Non-TXV |  | 15.51% | 0.8449 | 29.81% | [5 empty] | Non-TXV | 15.51%
Pleasanton | CA | 94566-5506 |  | 2013-06-25 | 2013-06-25 11:29 | 2013-06-25 14:08 | TEMPSTAR - | 166 | 8.8 | Yes | Yes | 21.4 | 19.3 | 2.1 | CF01E70C40794C1190B4CE49F9DA05B0 |  | R22 | TXV |  | 5.301% | 0.94699 | 10.19% | [5 empty] | TXV | 5.301%
Bakersfield | CA | 93307-4369 |  | 2013-08-05 | 2013-08-05 15:52 | 2013-08-05 15:52 | GOODMAN - CPLJ36-1B | 134 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | 6FC7EB4D5AF14D2496B0CF1EF0DDC9CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94566-6784 |  | 2013-09-12 | 2013-09-12 12:04 | 2013-09-12 12:04 | PAYNE - 5653BJ030 | 40 | 0 | Yes | Yes | 19.7 | 17.6 | 2.1 | 36B2F3BF3065463F841296C94C8B0491 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5049 |  | 2013-06-03 | 2013-06-03 14:15 | 2013-06-03 14:52 | BRYANT - 583ANW036060AAF | 82 | -4.8 | Yes | Yes | 23.4 | 21 | 2.4 | 114D93823C014B13936F4EFBC0A01494 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Fresno | CA | 93705-5118 |  | 2013-06-04 | 2013-06-04 13:41 | 2013-06-04 14:24 | DAY & NIGHT - UNK | 80 | 9.2 | Yes | Yes | 22.9 | 21.3 | 1.6 | A91D9A3509114DD8AAAACB0DB082133B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.5% | 0.885 | 22.1% | [5 empty] | Non-TXV | 11.5%
Bakersfield | CA | 93308-9330 |  | 2013-05-29 | 2013-05-29 14:48 | 2013-05-29 15:15 | BDP - 585HJ024040 | 68 | 4.3 | Yes | Yes | 21.2 | 21.3 | -0.1 | 17A5842F3A57491B8ECCD023A876D569 |  | R22 | Non-TXV |  | 6.324% | 0.93676 | 12.15% | [5 empty] | Non-TXV | 6.324%
Fresno | CA | 93722-5847 |  | 2013-08-21 | 2013-08-21 10:09 | 2013-08-21 10:30 | BRYANT - 574DNWA42090NA-- | 97 | -3.5 | Yes | Yes | 22.3 | 19.9 | 2.4 | A715126FB23D4C8AB027A6DBCBFCF394 |  | R410A | TXV |  | -3.608% | 1.0361 | 1.01% |  |  |  |  | TXV |  |  | -3.608%
San Jose | CA | 95136-2740 |  | 2013-07-05 | 2013-07-05 14:14 | 2013-07-05 15:57 | GE - BGTA724B1A01 | 85 | 19.7 | Yes | Yes | 25.4 | 20.2 | 5.2 | 15662F6FB1314BCB93BE6BACA2951778 |  | R22 | Non-TXV |  | 23.18% | 0.76824 | 44.54% | [5 empty] | Non-TXV | 23.18%
Bakersfield | CA | 93313-3347 |  | 2013-06-20 | 2013-06-20 15:13 | 2013-06-20 15:29 | YORK - D1NH048N06506C | 128 | 8.7 | Yes | Yes | 17.9 | 19 | -1.1 | 0E1730644C0A4FD9A022CA625DABDADE |  | R22 | Non-TXV |  | 6.797% | 0.93203 | 13.06% | [5 empty] | Non-TXV | 6.797%
Bakersfield | CA | 93312-2373 |  | 2013-06-26 | 2013-06-26 16:43 | 2013-06-26 16:43 | RUUD - UKN | 90 | 0 | Yes | Yes | 18.7 | 19.8 | -1.1 | 95BED31184E443FE98EB016C736BDB05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4521 |  | 2013-06-17 | 2013-06-17 14:48 | 2013-06-17 14:49 | - YCC036F1MOBE | 84 | 6 | Yes | Yes | 17.1 | 17.6 | -0.5 | 8C36F64FCFA64D5D803CD761508F0DEA |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Fresno | CA | 93704-5312 |  | 2013-06-14 | 2013-06-14 16:09 | 2013-06-14 16:32 | PAYNE - 42/110YAC-102AK | 124 | 2.6 | Yes | Yes | 24.1 | 22.1 | 2 | 9E67F459B2BF4A52A92E86B2DA83CA94 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.097% | 0.97903 | 4.03% | [5 empty] | Non-TXV | 2.097%
Bakersfield | CA | 93308-9329 |  | 2013-05-29 | 2013-05-29 12:44 | 2013-05-29 12:44 | BDP - 585HJ030040 | 68 | 0 | Yes | Yes | 18 | 20.1 | -2.1 | B470AC7723AF44C3BFF8CD0CF8AEE4EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3610 |  | 2013-08-02 | 2013-08-02 12:56 | 2013-08-02 13:48 | LENNOX - | 85 | 4.3 | Yes | Yes | 14.7 | 15.2 | -0.5 | C8699F9F90474C5A9DD1C8DE88A597A3 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Fresno | CA | 93705-1751 |  | 2013-07-10 | 2013-07-10 15:39 | 2013-07-10 16:29 | GOODMAN - 561AJ048B | 102 | 6.2 | Yes | Yes | 22.5 | 22.1 | 0.4 | 69CDA7B5C34C43E7A0D584682374BCB1 |  | R22 | Non-TXV |  | 6.078% | 0.93922 | 11.68% | [5 empty] | Non-TXV | 6.078%
Fresno | CA | 93702-5617 |  | 2013-05-31 | 2013-05-31 11:30 | 2013-05-31 11:51 | LENNOX - 13ACD036023 | 95 | 11.7 | Yes | Yes | 23.7 | 22.8 | 1 | 2CEF873F12E74F0DBCB5E0D0C5F1636D |  | R22 | TXV |  | 12.32% | 0.87684 | 23.67% | [5 empty] | TXV | 12.32%
Fairfield | CA | 94533-4106 |  | 2013-06-21 | 2013-06-21 12:18 | 2013-06-21 12:49 | TRANE - TTP036D0100A | 133 | 2.1 | Yes | Yes | 21.8 | 18.2 | 3.6 | 2B61FE56A72C433B93CD8A26A7838B03 |  | R22 | Non-TXV |  | 1.579% | 0.98421 | 3.034% | [5 empty] | Non-TXV | 1.579%
Bakersfield | CA | 93308-9330 |  | 2013-05-29 | 2013-05-29 15:19 | 2013-05-29 15:38 | BDP - 585HJ024040 | 68 | 7.7 | Yes | Yes | 19.1 | 19.9 | -0.8 | 979A377D71E140829D8D84EBAA2D1CA2 |  | R22 | Non-TXV |  | 11.32% | 0.88676 | 21.76% | [5 empty] | Non-TXV | 11.32%
Sanger | CA | 93657-3904 |  | 2013-08-08 | 2013-08-08 12:19 | 2013-08-08 12:46 | ARCOAIRE - NACO24AKC3 | 71 | 4 | Yes | Yes | 19.2 | 20.2 | -1 | 5BA7F2313FEC4D2587F38FDCB79CFEAA |  | R22 | Non-TXV |  | 5.634% | 0.94366 | 10.83% | [5 empty] | Non-TXV | 5.634%
Sanger | CA | 93657-3904 |  | 2013-08-06 | 2013-08-06 09:42 | 2013-08-06 10:40 | ARCOAIRE - NAC024AKC3 | 71 | 3.2 | Yes | Yes | 20.1 | 19.4 | 0.7 | E11EFC1862DC48C8A9FF77C70FCC21BF |  | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
Bakersfield | CA | 93304-5755 |  | 2013-06-18 | 2013-06-18 09:45 | 2013-06-18 09:45 | ICP - PGAA36C1K3 | 80 | 0 | Yes | Yes | 20.1 | 20.4 | -0.3 | 0B5B54545E1C4EE38D9983A29FB9700D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9237 |  | 2013-08-02 | 2013-08-02 16:23 | 2013-08-02 17:14 | COLEMAN - DAYQF048N110A | 70 | -5.1 | Yes | Yes | 22.5 | 19.6 | 3 | 9BCE0D95B14048E7AEC22105EDC9B23D |  | R410A | TXV |  | -7.286% | 1.0729 | 2.04% |  |  |  |  | TXV |  |  | -7.286%
Fresno | CA | 93705-3227 |  | 2013-06-19 | 2013-06-19 15:00 | 2013-06-19 16:41 | GOODMAN - PGBO36100 | 57 | 3.3 | Yes | Yes | 27.6 | 23 | 4.6 | FA7A7562F6144E04B188E42F3D0CE7A8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Bakersfield | CA | 93305-2415 |  | 2013-07-09 | 2013-07-09 17:06 | 2013-07-09 17:06 | YORK - D1NH042N06506C | 84 | 0 | Yes | Yes | 20.8 | 19.2 | 1.6 | D01B7BB882C94F819C72A0ED92263F07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2415 |  | 2013-07-09 | 2013-07-09 17:09 | 2013-07-09 17:09 | WESTINGHOUSE - UKN | 100 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 198F11938F9C497CA95B2614BF6C6D67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1422 |  | 2013-05-30 | 2013-05-30 09:34 | 2013-05-30 09:34 | RUUD - URKAA042JK08C | 69 | 0 | Yes | Yes | 20.2 | 19.6 | 0.7 | E0C47DE9BDED43B78047A66C652A730F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-6317 |  | 2013-06-12 | 2013-06-12 14:27 | 2013-06-12 14:27 | CARRIER - 38TK030330 | 76 | 0 | Yes | Yes | 13.4 | 16.4 | -3 | EA283F26D8BD4E4BB180833BEB722F8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5114 |  | 2013-05-31 | 2013-05-31 12:21 | 2013-05-31 12:21 | AMANA - VCA36B2D | 74 | 0 | Yes | Yes | 20.6 | 18.8 | 1.8 | 820A9B6504134B32A452759F13DFF514 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2658 |  | 2013-06-17 | 2013-06-17 14:52 | 2013-06-17 14:52 | YORK - H2RA036S06E | 63 | 5.9 | Yes | Yes | 18.2 | 21 | -2.8 | A836CBB053EE45A49A61610EA748D8FB | Add refrigerant: 5.9 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.365% | 0.90635 | 18% | [5 empty] | Non-TXV | 9.365%
Fresno | CA | 93725-4003 |  | 2013-07-08 | 2013-07-08 17:54 | 2013-07-08 18:27 | CARRIER - | 80 | -11.4 | Yes | Yes | 18.3 | 19.8 | -1.5 | BD3CF4B8BC4C48B48275D6584A7966AD | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -14.25% | 1.1425 | 3.991% |  |  |  |  | TXV |  |  | -14.25%
Bakersfield | CA | 93307-4668 |  | 2013-09-27 | 2013-09-27 14:51 | 2013-09-27 14:51 | ICP - PGC024K040A | 58 | 0 | Yes | Yes | 21.1 | 19.8 | 1.3 | 292CDD5EEAEB45C68DFDDD9BD171E805 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-2209 |  | 2013-10-15 | 2013-10-15 16:00 | 2013-10-15 16:00 | - | 85 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 6F7C9AFF56354C10959752A6D8F8F930 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-3414 |  | 2013-06-25 | 2013-06-25 09:44 | 2013-06-25 10:18 | GOODMAN - CKT48-1B | 85 | 6.4 | Yes | Yes | 22 | 19.9 | 2.1 | 2B29FDC3714A4E368CE33EB21A9C4E65 |  | R22 | Non-TXV |  | 7.529% | 0.92471 | 14.47% | [5 empty] | Non-TXV | 7.529%
Santa Rosa | CA | 95407-8067 |  | 2013-07-01 | 2013-07-01 14:01 | 2013-07-01 14:01 | OTHER - HAC036AKA1 | 80 | 0 | Yes | Yes | 15.2 | 18.1 | -2.9 | 29B7E123BB4745DE88054CFCD618A343 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6349 |  | 2013-06-13 | 2013-06-13 09:48 | 2013-06-13 11:04 | CARRIER - UNK | 80 | 6.6 | Yes | Yes | 23.8 | 20.6 | 3.2 | 565D275F0C15453585A259BB462D703B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.25% | 0.9175 | 15.85% | [5 empty] | Non-TXV | 8.25%
Bakersfield | CA | 93311-2862 |  | 2013-06-27 | 2013-06-27 08:50 | 2013-06-27 08:50 | RHEEM - UKN | 90 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 9356CA088BBE478180C6CA9C40FFC0E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2862 |  | 2013-06-27 | 2013-06-27 08:53 | 2013-06-27 08:53 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | AA0C1EBE14B647A3A9E303265ED5546A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0331 |  | 2013-06-19 | 2013-06-19 10:35 | 2013-06-19 10:57 | BRYANT - 58SANWO36060NAAF | 123 | 12.2 | Yes | Yes | 22.5 | 19.9 | 2.6 | BE1D026E02A344C28AC05A305D7446D8 |  | R22 | Non-TXV |  | 9.919% | 0.90081 | 19.06% | [5 empty] | Non-TXV | 9.919%
Fresno | CA | 93711-0331 |  | 2013-06-19 | 2013-06-19 12:47 | 2013-06-19 14:16 | BRYANT - 58SANWO36060NAAF | 123 | 10.9 | Yes | Yes | 20.3 | 19.3 | 1 | 8BE374C4BA83405AA60057C7385EC76B |  | R22 | Non-TXV |  | 8.862% | 0.91138 | 17.03% | [5 empty] | Non-TXV | 8.862%
Fresno | CA | 93704-5212 |  | 2013-06-03 | 2013-06-03 09:51 | 2013-06-03 10:18 | CARRIER - 38EE004300 | 87 | 16.8 | Yes | Yes | 19.6 | 21 | -1.4 | 205BB76F05FC4E49AEAC634F7736ECBA |  | R22 | Non-TXV |  | 19.31% | 0.8069 | 37.11% | [5 empty] | Non-TXV | 19.31%
Coalinga | CA | 93210-2211 |  | 2013-10-15 | 2013-10-15 12:17 | 2013-10-15 12:50 | YORK - D2GA030N04806C | 80 | 7.1 | Yes | Yes | 22.7 | 19.9 | 2.8 | F16DD30783D342E39C0F77BAB2AC388C |  | R22 | Non-TXV |  | 8.875% | 0.91125 | 17.06% | [5 empty] | Non-TXV | 8.875%
San Jose | CA | 95111-4605 |  | 2013-07-08 | 2013-07-08 19:28 | 2013-07-08 21:21 | NORDYNE - JS3BA-048KA | 85 | 3.4 | Yes | Yes | 23.6 | 20.7 | 3 | 19E2D71006664D36BE780E6B7F2DE475 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Davis | CA | 95616-0000 |  | 2013-06-19 | 2013-06-19 15:02 | 2013-06-19 15:02 | CARRIER - 38TKB036300 | 83 | 0 | Yes | Yes | 19.1 | 21.8 | -2.7 | D55A233B156D446FA441CAEFCE3BAE47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3478 |  | 2013-06-20 | 2013-06-20 16:59 | 2013-06-20 16:59 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 21.9 | 21.4 | 0.5 | 1EF755F44E054ED0ACB1F1FA529411D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3108 |  | 2013-05-30 | 2013-05-30 14:35 | 2013-05-30 14:35 | BRYANT - 113RNA036 | 86 | 0 | Yes | Yes | 28.2 | 19.5 | 8.7 | 515464A55CD141FFB3CEE238E9C303AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madison | CA | 95653-0000 |  | 2013-09-09 | 2013-09-09 13:22 | 2013-09-09 13:51 | BRYANT - 213BNA036-A | 102 | 9.6 | Yes | Yes | 26.1 | 20.4 | 5.7 | CF7F177F15354470BF8985FE9F1FD188 | Add refrigerant: 9.1 oz Evaporator saturation temperature is <25°F. Please check entries. | R410A | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Bakersfield | CA | 93306-5546 |  | 2013-08-15 | 2013-08-15 12:23 | 2013-08-15 12:23 | YORK - DAYP-F036N070A | 108 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 293C0F216F3E4D1EB0309F9FC6E4E5F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2215 |  | 2013-06-24 | 2013-06-24 18:17 | 2013-06-24 18:17 | YORK - D1NP048N06506A | 132 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | F174470E071C4AB6A99A3156BD26756D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3350 |  | 2013-08-13 | 2013-08-13 11:40 | 2013-08-13 11:40 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.9 | 20.4 | 1.5 | 9D3D264667A24E8B97420026504E3AC7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4900 |  | 2013-06-19 | 2013-06-19 15:39 | 2013-06-19 16:01 | COLEMAN - 95480901 | 67 | 13.2 | Yes | Yes | 27.4 | 21.8 | 5.6 | BA7EF977EAA741C3BA675FCED2A0D6E1 |  | R22 | Non-TXV |  | 19.7% | 0.80299 | 37.86% | [5 empty] | Non-TXV | 19.7%
Bakersfield | CA | 93311-2283 |  | 2013-06-14 | 2013-06-14 19:33 | 2013-06-14 19:33 | ICP - ACS030A2A1FBA020GA1 | 69 | 0 | Yes | Yes | 19 | 22 | -3 | 9296FEF87DCE4B59B07F0B4DC3D65E6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1713 |  | 2013-06-06 | 2013-06-06 13:28 | 2013-06-06 14:56 | TRANE - BTD736A100B0 | 88 | 3.8 | Yes | Yes | 18 | 18.8 | -0.8 | 91A9A01C716040FB9E5863CB3971F6A9 |  | R22 | Non-TXV |  | 4.318% | 0.95682 | 8.299% | [5 empty] | Non-TXV | 4.318%
Bakersfield | CA | 93311-3092 |  | 2013-06-04 | 2013-06-04 18:27 | 2013-06-04 18:47 | YORK - AC042X1021A | 84 | 10.9 | Yes | Yes | 20.9 | 21.4 | -0.5 | 98E21F68A09A4A7497A5DFF87B03504A |  | R22 | Non-TXV |  | 12.98% | 0.87024 | 24.94% | [5 empty] | Non-TXV | 12.98%
Bakersfield | CA | 93306-4221 |  | 2013-07-23 | 2013-07-23 18:37 | 2013-07-23 18:37 | ICP - PGF348080K01A1 | 208 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 78744E8D5C4E4DF3AD9C1F57C97907D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1526 |  | 2013-06-04 | 2013-06-04 16:55 | 2013-06-04 17:23 | YORK - DCYZ F030N070A | 65 | -4.6 | Yes | Yes | 23.8 | 19.6 | 4.2 | 43ADA0F7286C412E85BF87079602467E |  | R410A | Non-TXV |  | -7.077% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.077%
Redding | CA | 96003-7018 |  | 2013-07-15 | 2013-07-15 10:02 | 2013-07-15 10:18 | LENNOX - AC13 048 230 02 | 156 | 9.4 | Yes | Yes | 20.9 | 19.5 | 1.4 | 50C7CB4167544945954F88187D3FDF04 |  | R22 | Non-TXV |  | 6.026% | 0.93974 | 11.58% | [5 empty] | Non-TXV | 6.026%
Redding | CA | 96003-7018 |  | 2013-07-15 | 2013-07-15 10:19 | 2013-07-15 10:52 | - | 85 | 3.7 | Yes | Yes | 20.9 | 19.5 | 1.4 | DA86FAED5E1D4E119B4C9CDF07EA181E |  |  |  |  | 4.353% | 0.95647 | 8.365% | [5 empty] | 0 | 4.353%
Davis | CA | 95616-0000 |  | 2013-06-12 | 2013-06-12 15:01 | 2013-06-12 15:22 | OTHER - UKN | 85 | 5.4 | Yes | Yes | 19.3 | 19.9 | -0.6 | 1D30DB52497D4102AD5BF65CFD19EE49 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Kingsburg | CA | 93631-2511 |  | 2013-07-15 | 2013-07-15 10:56 | 2013-07-15 11:17 | LENNOX - PGE10A30D0751PA | 64 | 6.6 | Yes | Yes | 21.9 | 20.1 | 1.8 | 89C981CA068844B39488BBBC1F72B3B6 |  | R22 | Non-TXV |  | 10.31% | 0.89687 | 19.82% | [5 empty] | Non-TXV | 10.31%
Fresno | CA | 93722-5473 |  | 2013-06-19 | 2013-06-19 11:51 | 2013-06-19 12:28 | - 38CK03610 | 78 | 10.7 | Yes | Yes | 25.2 | 19.7 | 5.5 | A992AC83746A4F599D4B05A9D182A0DA |  | R22 | Non-TXV |  | 13.72% | 0.86282 | 26.36% | [5 empty] | Non-TXV | 13.72%
Wasco | CA | 93280-2762 |  | 2013-09-17 | 2013-09-17 19:19 | 2013-09-17 19:21 | OTHER - H2RD042S06B | 141 | 5.1 | Yes | Yes | 23.4 | 20.5 | 2.9 | 7183FD311838446B80222EC572EBCFC7 |  | R22 | TXV |  | 3.617% | 0.96383 | 6.951% | [5 empty] | TXV | 3.617%
Fresno | CA | 93725-1229 |  | 2013-06-25 | 2013-06-25 13:52 | 2013-06-25 13:52 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 6D65CA5FCBF04B6D8E42C5AE0CE617EF | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2129 |  | 2013-06-20 | 2013-06-20 09:52 | 2013-06-20 10:14 | AMERICAN STANDARD - YCP036F1M0AC | 110 | 17 | Yes | Yes | 21.1 | 19.5 | 1.6 | 73EECB5C436B4DA9BCB721AB9188F0DD |  | R22 | Non-TXV |  | 15.45% | 0.84545 | 29.7% | [5 empty] | Non-TXV | 15.45%
Fresno | CA | 93702-3821 |  | 2013-06-17 | 2013-06-17 19:19 | 2013-06-17 19:19 | OTHER - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 13D4068DAB9A42A99F978F77375F29ED | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1926 |  | 2013-06-05 | 2013-06-05 11:17 | 2013-06-05 11:46 | TRANE - 2TTB0030A1000AA | 64 | -6 | Yes | Yes | 19.6 | 19.1 | 0.5 | 1ECB2A7F50034470B90B21D13E820362 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93307-4366 |  | 2013-08-05 | 2013-08-05 11:22 | 2013-08-05 11:22 | GOODMAN - CPLJ36-1B | 134 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | D4780DAB18C648F385DDE8EC47EEA914 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6056 |  | 2013-06-25 | 2013-06-25 16:27 | 2013-06-25 16:27 | RHEEM - FAFF-042JAZ | 163 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | FE0DD019E8A04635BD64D4B710A626FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1508 |  | 2013-06-10 | 2013-06-10 10:59 | 2013-06-10 11:18 | PAYNE - PA12NA036-B | 100 | -2.5 | Yes | Yes | 15.4 | 12.8 | 2.6 | 2C6637073BAA4E22B7A2FAA163C7EE95 |  | R22 | Non-TXV |  | -2.5% | 1.025 | 0.7001% |  |  |  |  | Non-TXV |  |  | -2.5%
Kerman | CA | 93630-1539 |  | 2013-07-05 | 2013-07-05 11:20 | 2013-07-05 11:45 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 19.3 | 17.6 | 1.7 | 008605397C35417CBB38F6D572D24D2C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Morgan Hill | CA | 95037-6125 |  | 2013-10-23 | 2013-10-23 11:26 | 2013-10-23 12:15 | INTERTHERM - CN421D | 67 | 2.7 | Yes | Yes | 20.9 | 20.9 | 0 | 7F941D1D09C6434EB57B40E9A2AA6259 |  | R22 | Non-TXV |  | 4.03% | 0.9597 | 7.744% | [5 empty] | Non-TXV | 4.03%
Pleasant Hill | CA | 94523-1533 |  | 2013-06-18 | 2013-06-18 19:25 | 2013-06-18 19:46 | BDP - 561AJ048-D | 85 | 12.5 | Yes | Yes | 23.9 | 20.7 | 3.3 | D24624C7CB9A4BCC8BB5BA19F423EAA1 |  | R22 | TXV |  | 14.71% | 0.85294 | 28.26% | [5 empty] | TXV | 14.71%
Davis | CA | 95616-0000 |  | 2013-06-19 | 2013-06-19 14:19 | 2013-06-19 14:19 | AMERICAN STANDARD - 4YCC3036A1075AB | 124 | 0 | Yes | Yes | 18.1 | 20.3 | -2.2 | 701089593FED49BE837AC111F14BE9DF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4775 |  | 2013-07-09 | 2013-07-09 09:21 | 2013-07-09 09:58 | CARRIER - UNK | 80 | 9.8 | Yes | Yes | 23.9 | 20.1 | 3.8 | B2F7588BFBF845BD94D8194613E978A9 |  | R22 | Non-TXV |  | 12.25% | 0.8775 | 23.54% | [5 empty] | Non-TXV | 12.25%
Fresno | CA | 93702-2531 |  | 2013-05-29 | 2013-05-29 13:48 | 2013-05-29 14:27 | ARCOAIRE - PGF042K0808 | 87 | 2.9 | Yes | Yes | 23.4 | 21 | 2.4 | AD9113543F1C4BE79B288B20AE84A98F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Brentwood | CA | 94513-6967 |  | 2013-07-02 | 2013-07-02 13:34 | 2013-07-02 13:34 | YORK - H2RC030S06A | 88 | 0 | Yes | Yes | 18.2 | 17.6 | 0.6 | F6CB13A2F33949A3AE32F4FFB96AD9D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4776 |  | 2013-06-14 | 2013-06-14 15:37 | 2013-06-14 16:22 | CARRIER - UNK | 80 | 4.3 | Yes | Yes | 22.7 | 20.5 | 2.2 | 600E8DE210C24FCFA510AFC83C3E25C1 |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Pleasant Hill | CA | 94523-1643 |  | 2013-07-15 | 2013-07-15 11:45 | 2013-07-15 11:48 | RHEEM - RAFD-030JAS | 69 | -5.7 | Yes | Yes | 19.6 | 17 | 2.6 | 03B9F01820E6422DBFBA1C6009C0457F |  | R22 | Non-TXV |  | -8.261% | 1.0826 | 2.313% |  |  |  |  | Non-TXV |  |  | -8.261%
Suisun City | CA | 94585-1798 |  | 2013-06-06 | 2013-06-06 13:11 | 2013-06-06 14:59 | GOODMAN - CJ30-1FB | 110 | 4.8 | Yes | Yes | 16.9 | 18.8 | -1.9 | 649A7643AE6E4EED96EA184349DFC2D9 |  | R22 | Non-TXV |  | 4.364% | 0.95636 | 8.386% | [5 empty] | Non-TXV | 4.364%
Vacaville | CA | 95687-6271 |  | 2013-05-31 | 2013-05-31 09:44 | 2013-05-31 10:17 | CARRIER - 38EN030300 | 90 | -5.3 | Yes | Yes | 15 | 13.4 | 1.6 | 9DF28EEF7C324A81BBAEA8D8B0D5D529 |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Fresno | CA | 93702-4328 |  | 2013-05-31 | 2013-05-31 09:33 | 2013-05-31 10:28 | RHEEM - RRNLB048JK08X | 161 | 8.5 | Yes | Yes | 23.6 | 19.1 | 4.5 | CC3853B62D824690B39DB58C30028A15 |  | R410A | TXV |  | 5.28% | 0.9472 | 10.15% | [5 empty] | TXV | 5.28%
Fresno | CA | 93702-3007 |  | 2013-05-29 | 2013-05-29 15:34 | 2013-05-29 16:14 | GOODMAN - GPG13360701AC | 112 | -7.9 | Yes | Yes | 25.3 | 20.4 | 4.9 | 4DBA7F3AAF7A40AABC49329FA33B57F1 |  | R22 | Non-TXV |  | -7.054% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.054%
Redding | CA | 96003-7524 |  | 2013-07-16 | 2013-07-16 10:14 | 2013-07-16 12:13 | RUUD - UAMB 036JBZ | 93 | -6.6 | Yes | Yes | 20.9 | 20.4 | 0.5 | 319FDCCF536E4AB3A9D1F6A64CF63282 |  | R22 | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Davis | CA | 95616-0000 |  | 2013-06-12 | 2013-06-12 15:27 | 2013-06-12 15:27 | COLEMAN - DRCQ0301BE | 70 | 0 | Yes | Yes | 16.1 | 19.1 | -3 | D0FB1393341349B8BB524DCAA6203BF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4329 |  | 2013-08-28 | 2013-08-28 15:23 | 2013-08-28 15:45 | YORK - H2RCO030S06G | 88 | 4 | Yes | Yes | 20 | 18.3 | 1.7 | A98188CA4E544EC7930318F2849626BA |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Davis | CA | 95616-0000 |  | 2013-06-19 | 2013-06-19 10:20 | 2013-06-19 10:39 | COLEMAN - DRCS0361BE | 83 | -5.9 | Yes | Yes | 25.5 | 20.4 | 5.1 | 3D324464BF284107914059EC13F142CB |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Woodland | CA | 95695-6811 |  | 2013-06-17 | 2013-06-17 10:03 | 2013-06-17 11:22 | CARRIER - 38TKB036300 | 82 | 4.6 | Yes | Yes | 16 | 17.7 | -1.7 | 540B75C883E2466597A3C4DA073318E8 |  | R22 | Non-TXV |  | 5.61% | 0.9439 | 10.78% | [5 empty] | Non-TXV | 5.61%
Sanger | CA | 93657-3904 |  | 2013-08-06 | 2013-08-06 09:38 | 2013-08-06 09:54 | ARCOAIRE - NAC024AKC3 | 71 | -5 | Yes | Yes | 21.4 | 19.4 | 2 | 0A7CEEAE9ECE4B1F8D12AA5380CB9156 |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Vacaville | CA | 95687-6621 |  | 2013-05-31 | 2013-05-31 14:22 | 2013-05-31 14:44 | PAYNE - PA10JA042-H | 90 | 6.6 | Yes | Yes | 18.1 | 20.9 | -2.8 | E346E75B492C43C38E00B16BC1F5D08F |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Sanger | CA | 93657-2299 |  | 2013-08-05 | 2013-08-05 16:35 | 2013-08-05 17:27 | ARCOAIRE - NAC024AKC3 | 71 | 2.8 | Yes | Yes | 18.9 | 20.7 | -1.8 | 4D50BD0DB9744C45BD8C37DDA31CCEF0 |  | R22 | TXV |  | 3.944% | 0.96056 | 7.579% | [5 empty] | TXV | 3.944%
Bakersfield | CA | 93313-2212 |  | 2013-06-20 | 2013-06-20 09:27 | 2013-06-20 10:12 | YORK - D1NP048N0656A | 132 | 13.5 | Yes | Yes | 19.5 | 19.6 | -0.1 | 458C0145E27B4C12ABF736D3D0D821C6 |  | R22 | Non-TXV |  | 10.23% | 0.89773 | 19.65% | [5 empty] | Non-TXV | 10.23%
Kerman | CA | 93630-1986 |  | 2013-10-01 | 2013-10-01 12:27 | 2013-10-01 20:09 | CARRIER - 48SDN042060301 | 168 | 4.9 | Yes | Yes | 21.2 | 21 | 0.2 | 3882ECC4C63547059F979A878369F120 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Sanger | CA | 93657-2299 |  | 2013-08-08 | 2013-08-08 14:56 | 2013-08-08 14:56 | ARCOAIRE - NAC024AKD1 | 67 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 3A80462AB3694D88B0AA71F0699AC274 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1812 |  | 2013-06-28 | 2013-06-28 09:50 | 2013-06-28 09:50 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 38A318F7CD9C4D90BE82EB50782C0A5A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1208 |  | 2013-06-06 | 2013-06-06 13:58 | 2013-06-06 14:38 | YORK - DBYP F048 N080A | 132 | -9.3 | Yes | Yes | 22.7 | 20.3 | 2.5 | 463A4107D70A4415B64F6E2C0570469A |  | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Bakersfield | CA | 93301-2535 |  | 2013-08-19 | 2013-08-19 17:23 | 2013-08-19 17:23 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | B97BE0B94A6F451ABD26D0DD8D396F7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8818 |  | 2013-06-11 | 2013-06-11 13:00 | 2013-06-11 13:00 | WEATHER KING - 13AV036A01 | 108 | 0 | Yes | Yes | 18.6 | 21.3 | -2.7 | 80A91E1B131E4BE493B036DE83535F40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4003 |  | 2013-09-13 | 2013-09-13 11:38 | 2013-09-13 11:38 | GOODMAN - GPG154811541AB | 172 | 0 | Yes | Yes | 21.3 | 21 | 0.3 | 5FD09BD9002E413D9A791829ECDA850E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1147 |  | 2013-06-03 | 2013-06-03 09:55 | 2013-06-03 10:16 | OTHER - RRKAA036JK08X | 61 | -4.3 | Yes | Yes | 20.9 | 19.9 | 1 | 15647D3275824E9394D50BBABDCA3903 |  | R22 | Non-TXV |  | -7.049% | 1.0705 | 1.974% |  |  |  |  | Non-TXV |  |  | -7.049%
Bakersfield | CA | 93311-9149 |  | 2013-10-04 | 2013-10-04 09:26 | 2013-10-04 09:26 | CARRIER - 38CKC03650 | 70 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | EC40938BDD464598AA23B4A7DE22595F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6307 |  | 2013-06-17 | 2013-06-17 12:18 | 2013-06-17 12:46 | INTERTHERM - ACC-036BAVAA | 43 | 5.7 | Yes | Yes | 17.4 | 18.2 | -0.8 | 0E806232476F49DDA2DD9020C82B1583 |  | R22 | Non-TXV |  | 13.26% | 0.86744 | 25.47% | [5 empty] | Non-TXV | 13.26%
Fresno | CA | 93704-5007 |  | 2013-06-03 | 2013-06-03 12:12 | 2013-06-03 12:59 | GOODMAN - UNK | 84 | 2.7 | Yes | Yes | 23.4 | 20.6 | 2.8 | B48EA321DD184A729507A48026FB980C |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Sanger | CA | 93657-3627 |  | 2013-07-16 | 2013-07-16 12:25 | 2013-07-16 12:25 | OTHER - 80WR236A1NB | 61 | 0 | Yes | Yes | 17.1 | 19.9 | -2.8 | 8CA4CEE44BC44C7A8DBA63CF39417301 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-1440 |  | 2013-07-05 | 2013-07-05 08:37 | 2013-07-05 08:37 | CARRIER - 38BRC030---311-- | 100 | 0 | Yes | Yes | 18 | 20.9 | -2.9 | 567AC288033C4425B43F7522C880977E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2241 |  | 2013-06-05 | 2013-06-05 13:18 | 2013-06-05 13:38 | DAY & NIGHT - 59C3JX048000AAAA | 105 | 8.9 | Yes | Yes | 17.3 | 19 | -1.7 | BA02AF1378564FD9BF38835AC7EB47C5 |  | R22 | Non-TXV |  | 8.476% | 0.91524 | 16.29% | [5 empty] | Non-TXV | 8.476%
Fresno | CA | 93701-1221 |  | 2013-08-02 | 2013-08-02 16:40 | 2013-08-02 16:40 | YORK - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 96BE0048522E4D0EB032BA596576A4BC | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4332 |  | 2013-05-31 | 2013-05-31 16:07 | 2013-05-31 16:29 | TRANE - 2TTB0036A1000AA | 76 | 4.4 | Yes | Yes | 17.8 | 19.3 | -1.5 | CE994BB9B60443AE8E3D5DE5574F2ED8 |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Davis | CA | 95616-0000 |  | 2013-06-19 | 2013-06-19 09:24 | 2013-06-19 09:47 | COLEMAN - BRCS0361BDG | 63 | 1.9 | Yes | Yes | 25.6 | 20.3 | 5.4 | 084322F2B2BC43F8A02D8A93742BA3F0 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Fresno | CA | 93706-4768 |  | 2013-06-12 | 2013-06-12 16:46 | 2013-06-12 17:52 | LENNOX - 10GCSO030 | 51 | 1.5 | Yes | Yes | 23.7 | 21.7 | 2 | B2CE55C0FBD8470DB7A799511F549496 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Union City | CA | 94587-8000 |  | 2013-10-02 | 2013-10-02 13:04 | 2013-10-02 13:24 | YORK - H2R030S06D | 62 | 9 | Yes | Yes | 21.5 | 15.5 | 6 | 936D0225B9D142D59C880B9BB271C5D8 |  | R22 | Non-TXV |  | 14.52% | 0.85484 | 27.9% | [5 empty] | Non-TXV | 14.52%
San Jose | CA | 95111-3097 |  | 2013-10-07 | 2013-10-07 14:07 | 2013-10-07 14:31 | COLEMAN - UNK | 70 | 6.3 | Yes | Yes | 19.3 | 21.8 | -2.5 | A967CB0534774CF98058B03B44FF9EE5 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Vacaville | CA | 95688-2630 |  | 2013-05-31 | 2013-05-31 11:28 | 2013-05-31 11:52 | CARRIER - 48ESNA3606030 | 102 | 3.3 | Yes | Yes | 16.2 | 13 | 3.2 | 00D471339F7B45E399B591733AA5ED16 |  | R410A | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Vacaville | CA | 95687-3222 |  | 2013-05-31 | 2013-05-31 10:52 | 2013-05-31 11:14 | AMERICAN STANDARD - 2A7B0036A1000AA | 76 | -5.4 | Yes | Yes | 15.7 | 13.9 | 1.8 | 5E40D5C280B84805929FF9047A182C1D |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Cottonwood | CA | 96022-8911 |  | 2013-06-26 | 2013-06-26 08:49 | 2013-06-26 09:34 | CARRIER - 561AJ024 B | 56 | 8.9 | Yes | Yes | 20.3 | 21.5 | -1.2 | 01C4CA9376014CD0A85F934A700EBBE9 |  | R22 | Non-TXV |  | 15.89% | 0.84107 | 30.54% | [5 empty] | Non-TXV | 15.89%
Davis | CA | 95616-0000 |  | 2013-07-09 | 2013-07-09 12:38 | 2013-07-09 12:38 | COLEMAN - 952901 | 58 | 0 | Yes | Yes | 16.8 | 19.6 | -2.8 | DF8D422C7CEA483A95F3BE81424601FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2343 |  | 2013-06-04 | 2013-06-04 10:57 | 2013-06-04 11:25 | YORK - D1NHO36N05606C | 108 | 3.4 | Yes | Yes | 22.4 | 19.9 | 2.5 | D235F839FA2A401AB6872CECC1F3874A |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Bakersfield | CA | 93308-9329 |  | 2013-05-29 | 2013-05-29 14:19 | 2013-05-29 14:19 | BDP - 585HJ024040 | 68 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 378A4D426A434F1183F0327AED4A6762 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2741 |  | 2013-07-03 | 2013-07-03 10:34 | 2013-07-03 10:34 | YORK - D3N2030N05606NXB | 64 | 0 | Yes | Yes | 20.9 | 18.3 | 2.6 | 531A8DD65FA14A37B021AC090E54DF92 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2437 |  | 2013-06-04 | 2013-06-04 09:13 | 2013-06-04 10:03 | GOODMAN - GPG1336090M41AC | 85 | -6 | Yes | Yes | 24.6 | 20.9 | 3.7 | B91D03C252C047229FAF205E6F0BC8A0 |  | R410A | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93711-2253 |  | 2013-06-20 | 2013-06-20 18:07 | 2013-06-20 18:44 | - 56AJ048-F | 106 | 3.4 | Yes | Yes | 19.4 | 19.3 | 0.1 | 157F8D7F8156427A810EEDC7B38C2CB6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.208% | 0.96792 | 6.164% | [5 empty] | Non-TXV | 3.208%
Bakersfield | CA | 93307-4668 |  | 2013-09-27 | 2013-09-27 15:14 | 2013-09-27 15:31 | ICP - UKN | 90 | 7 | Yes | Yes | 20.5 | 19.8 | 0.7 | 7B41A26DB8964A8195F5F04475040A6B |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Bakersfield | CA | 93309-6466 |  | 2013-09-24 | 2013-09-24 23:13 | 2013-09-24 23:13 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | C09611A91682453986F1F1D6020DCB01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3622 |  | 2013-06-10 | 2013-06-10 17:43 | 2013-06-10 18:19 | - 561CJ036-C | 76 | 2.3 | Yes | Yes | 18.4 | 18.2 | 0.2 | F663F413F74C456B9C0BE25E1F2EBCBE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Wasco | CA | 93280-2757 |  | 2013-07-31 | 2013-07-31 22:26 | 2013-07-31 22:28 | YORK - H2RD042S06B | 141 | 5.9 | Yes | Yes | 19.3 | 22.1 | -2.8 | 6FAE342A6EC04D51A6494FAD0DD0B3AB |  | R22 | Non-TXV |  | 4.184% | 0.95816 | 8.041% | [5 empty] | Non-TXV | 4.184%
San Jose | CA | 95148-3008 |  | 2013-10-12 | 2013-10-12 15:31 | 2013-10-12 16:14 | ICP - PGD336060H000C1 | 102 | -7.6 | Yes | Yes | 23.9 | 20.1 | 3.8 | 33135DCB8FCA429588E7A126EDB7AB71 |  | R410A | TXV |  | -7.451% | 1.0745 | 2.087% |  |  |  |  | TXV |  |  | -7.451%
Vacaville | CA | 95687-4718 |  | 2013-07-19 | 2013-07-19 10:34 | 2013-07-19 11:12 | AMERICAN STANDARD - 2A72036A1000AA | 96 | -5.6 | Yes | Yes | 18.1 | 18.6 | -0.5 | DE3CF6498E7044759CD3B3595D554DD9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Cottonwood | CA | 96022-8911 |  | 2013-06-26 | 2013-06-26 15:34 | 2013-06-26 16:54 | ARMSTRONG - SCU1OB24A | 66 | 6.3 | Yes | Yes | 21.6 | 20.4 | 1.2 | 4F59F8218DE44A11B8432557F90E1802 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
W Sacramento | CA | 95691-2557 |  | 2013-06-12 | 2013-06-12 10:30 | 2013-06-12 14:33 | GMC - VSX130361AA | 89 | 4.3 | Yes | Yes | 17.1 | 17.6 | -0.5 | D87BF6717F154BE899BA3F8A991FC5F7 |  | R410A | Non-TXV |  | 4.831% | 0.95169 | 9.285% | [5 empty] | Non-TXV | 4.831%
Sanger | CA | 93657-9711 |  | 2013-06-21 | 2013-06-21 17:01 | 2013-06-21 17:22 | YORK - DARAF030N060A | 81 | 25.2 | Yes | Yes | 18.8 | 21.1 | -2.3 | 93633886D51F4646AD9C23CC65E849C9 |  | R22 | Non-TXV |  | 31.11% | 0.68889 | 59.79% | [5 empty] | Non-TXV | 31.11%
Selma | CA | 93662-2125 |  | 2013-06-20 | 2013-06-20 16:45 | 2013-06-20 17:06 | OTHER - PGC042K080B | 87 | 4.1 | Yes | Yes | 24 | 22 | 2 | C284C256C4FF424EB1034583C1143356 |  | R22 | Non-TXV |  | 4.713% | 0.95287 | 9.057% | [5 empty] | Non-TXV | 4.713%
Fresno | CA | 93722-5189 |  | 2013-08-28 | 2013-08-28 11:20 | 2013-08-28 11:57 | - UNK | 80 | 2.4 | Yes | Yes | 17.3 | 20.3 | -3 | 32436E9C9311462E9410236900FCBA23 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Selma | CA | 93662-9479 |  | 2013-07-10 | 2013-07-10 13:40 | 2013-07-10 14:12 | GOODMAN - GPG13420701AA | 107 | 10 | Yes | Yes | 23.4 | 19.7 | 3.7 | E109403ECDB8431D9E47621D765AC81D |  | R22 | Non-TXV |  | 9.346% | 0.90654 | 17.96% | [5 empty] | Non-TXV | 9.346%
Fresno | CA | 93705-0114 |  | 2013-06-07 | 2013-06-07 09:45 | 2013-06-07 10:10 | OTHER - NACO24AKC3 | 71 | 5.5 | Yes | Yes | 23.7 | 17.7 | 6 | 50381464D87749509EFE1C6C277FFCE6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.746% | 0.92254 | 14.89% | [5 empty] | Non-TXV | 7.746%
Sanger | CA | 93657-8630 |  | 2013-07-16 | 2013-07-16 09:06 | 2013-07-16 09:25 | GOODMAN - CLJ361C | 109 | -10.3 | Yes | Yes | 20.7 | 18.8 | 1.9 | 602CF677E70548EEB62E1091A0820C21 |  | R22 | Non-TXV |  | -9.45% | 1.0945 | 2.646% |  |  |  |  | Non-TXV |  |  | -9.45%
Sunnyvale | CA | 94086-8957 |  | 2013-09-27 | 2013-09-27 15:34 | 2013-09-27 16:04 | CARRIER - 38BRC036330 | 104 | 7.9 | Yes | Yes | 23 | 21.7 | 1.3 | 3366E55C46E8406C9820DAC881CF44A5 |  | R22 | Non-TXV |  | 7.596% | 0.92404 | 14.6% | [5 empty] | Non-TXV | 7.596%
Selma | CA | 93662-3375 |  | 2013-06-20 | 2013-06-20 14:03 | 2013-06-20 14:39 | OTHER - UNK | 85 | 3.8 | Yes | Yes | 24.9 | 20.4 | 4.5 | F50818F038B14A7B827633AD8D542727 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Fresno | CA | 93702-4217 |  | 2013-06-24 | 2013-06-24 10:53 | 2013-06-24 11:13 | GOODMAN - GPH1330H21AB | 146 | 8.5 | Yes | Yes | 21.2 | 19.3 | 1.9 | 00048DEFA75240449FA16BD312A873C3 |  | R22 | Non-TXV |  | 5.822% | 0.94178 | 11.19% | [5 empty] | Non-TXV | 5.822%
Fairfield | CA | 94533-5860 |  | 2013-10-10 | 2013-10-10 12:33 | 2013-10-10 12:33 | PAYNE - PA10JA036-A | 83 | 0 | Yes | Yes | 17.8 | 17.4 | 0.4 | 906374CA5997446BB9C9955BBBF52B5B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94541-6620 |  | 2013-06-05 | 2013-06-05 07:51 | 2013-06-05 08:08 | OTHER - H2RA036S06E | 63 | 4.7 | Yes | Yes | 17.5 | 18.8 | -1.3 | 070E0C752CD64408A8BBDFA082D00970 |  | R22 | Non-TXV |  | 7.46% | 0.9254 | 14.34% | [5 empty] | Non-TXV | 7.46%
Fremont | CA | 94536-6711 |  | 2013-06-07 | 2013-06-07 15:56 | 2013-06-07 15:56 | TEMPSTAR - TCH036AKC3 | 85 | 0 | Yes | Yes | 18.8 | 18.7 | 0.1 | 50759851ACD34AC59D4CDCBE2EDA7846 |  | R22 | TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-8164 |  | 2013-06-25 | 2013-06-25 10:36 | 2013-06-25 10:36 | CARRIER - 38CK018310 | 79 | 0 | Yes | Yes | 9.5 | 19.3 | -9.8 | 3438E3C931C845D897DFE75D2ADF499F | Actual Subcooling cannot be negative. Please check entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1807 |  | 2013-06-04 | 2013-06-04 11:36 | 2013-06-04 11:36 | TRANE - TTX030C100A3 | 120 | 0 | Yes | Yes | 20.2 | 17.5 | 2.8 | 61C88B23DCBD48B2B6E0B37A6C3E8042 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-9701 |  | 2013-06-17 | 2013-06-17 16:49 | 2013-06-17 17:09 | DAY & NIGHT - 585HJW030040AB | 68 | 9.6 | Yes | Yes | 25.8 | 20.1 | 5.7 | 910A4C4770CF4673B7CCFA250C033D90 |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Bakersfield | CA | 93313-3682 |  | 2013-06-20 | 2013-06-20 13:32 | 2013-06-20 13:32 | RHEEM - UKN | 90 | 0 | Yes | Yes | 25.1 | 20.4 | 4.7 | 57F0722F4B354B11A12C60323B1EB226 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1914 |  | 2013-06-28 | 2013-06-28 11:24 | 2013-06-28 11:24 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.2 | 19.5 | -1.3 | 159822AEEDF44E38A4A41941480BA472 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7541 |  | 2013-06-18 | 2013-06-18 10:31 | 2013-06-18 11:37 | LENNOX - 12GCS036-75-5PB | 110 | 3.6 | Yes | Yes | 23.2 | 19.3 | 3.9 | B5FC8E0D85884E48B9EFFDF9EE5B0956 | OK: Verified Refrigerant Charge Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | TXV | 3.273%
Vacaville | CA | 95688-2003 |  | 2013-06-11 | 2013-06-11 10:36 | 2013-06-11 10:36 | TRANE - TTN042C100A2 | 126 | 0 | Yes | Yes | 16.9 | 18.7 | -1.8 | 42734BB0A2DC46E5BAC7D7A2F2948A16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3097 |  | 2013-09-09 | 2013-09-09 09:37 | 2013-09-09 09:37 | TAPPAN - CM3644S | 85 | 0 | Yes | Yes | 18.2 | 18.1 | 0.1 | 8917E206A6494DDAA13CE007D2E54C15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9329 |  | 2013-05-29 | 2013-05-29 14:11 | 2013-05-29 14:27 | BDP - 585HJ030040 | 68 | 5.5 | Yes | Yes | 20.8 | 20.6 | 0.3 | 640E5D6099644886B1883DCB9F4C5394 |  | R22 | Non-TXV |  | 8.088% | 0.91912 | 15.54% | [5 empty] | Non-TXV | 8.088%
Selma | CA | 93662-9650 |  | 2013-11-11 | 2013-11-11 16:05 | 2013-11-11 16:05 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | BFC951E4505641AB866FBC9D7B175485 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5114 |  | 2013-05-31 | 2013-05-31 12:29 | 2013-05-31 12:29 | YORK - D1NH042N06506C | 94 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | DB3523FD7C4A43EC81923EE85C5027C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6795 |  | 2013-07-01 | 2013-07-01 12:36 | 2013-07-01 13:37 | - 38CKB036320 | 76 | 2.6 | Yes | Yes | 12.6 | 13.9 | -1.3 | 5D47853E1EC6406CB9E5C915749DA3CE |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Davis | CA | 95616-0000 |  | 2013-06-19 | 2013-06-19 12:26 | 2013-06-19 12:26 | TRANE - TTN030100C2 | 95 | 0 | Yes | Yes | 21.1 | 22.2 | -1.1 | 6C9E151EBDF04DD29486298B9256CFB9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6246 |  | 2013-05-31 | 2013-05-31 13:59 | 2013-05-31 14:19 | AIRE-FLO - N4A330AKC200 | 74 | 4.7 | Yes | Yes | 18.4 | 21 | -2.6 | 55A31B54AA294C1C9DC1C07B0BDB7B30 |  | R410A | Non-TXV |  | 6.351% | 0.93649 | 12.21% | [5 empty] | Non-TXV | 6.351%
Fresno | CA | 93722-6705 |  | 2013-07-11 | 2013-07-11 11:21 | 2013-07-11 12:01 | RHEEM - RRNABO30JK06X | 72 | 4.5 | Yes | Yes | 20.3 | 21 | -0.7 | 39B8FE211BD047139E79646D9992C7DE |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Vacaville | CA | 95687-5538 |  | 2013-06-26 | 2013-06-26 13:25 | 2013-06-26 16:12 | GOODMAN - CK36-10 | 72 | -4.2 | Yes | Yes | 18.5 | 20.4 | -1.9 | 0E047DA23FA245B19BD858455066F5A9 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Redding | CA | 96003-7004 |  | 2013-07-15 | 2013-07-15 09:18 | 2013-07-15 09:48 | YORK - YHD4841SA4 | 236 | -16.7 | Yes | Yes | 21.7 | 20.2 | 1.5 | 74E08EA698C84F1BA784B1A38DDA97C8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.076% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.076%
Fresno | CA | 93725-9640 |  | 2013-06-17 | 2013-06-17 13:07 | 2013-06-17 13:25 | OTHER - HBBDF048SB | 134 | 14 | Yes | Yes | 25.6 | 22.7 | 3 | EBA287860A3D497683DF97A72ED4AA9B |  | R22 | Non-TXV |  | 10.45% | 0.89552 | 20.08% | [5 empty] | Non-TXV | 10.45%
San Jose | CA | 95111-3097 |  | 2013-09-17 | 2013-09-17 13:01 | 2013-09-17 13:55 | PAYNE - PA13NR042-C | 187 | 14.4 | Yes | Yes | 16.8 | 19.1 | -2.3 | AAEBA78036F34892A8F20C39B6C9E01F |  | R22 | Non-TXV |  | 7.701% | 0.92299 | 14.8% | [5 empty] | Non-TXV | 7.701%
Bakersfield | CA | 93313-3003 |  | 2013-06-20 | 2013-06-20 10:59 | 2013-06-20 10:59 | BDP - 585HJ048080 | 118 | 0 | Yes | Yes | 19.5 | 19.9 | -0.4 | 2C563CD12B364F6282098A7E0BD35705 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1240 |  | 2013-07-29 | 2013-07-29 14:28 | 2013-07-29 15:05 | CARRIER - 48SX-048080331AA | 90 | 17.2 | Yes | Yes | 21.9 | 22.1 | -0.2 | 1B4B27E5C2694C27A91D29A8CE1BD740 |  | R22 | Non-TXV |  | 19.11% | 0.80889 | 36.73% | [5 empty] | Non-TXV | 19.11%
Fresno | CA | 93711-4057 |  | 2013-06-20 | 2013-06-20 17:05 | 2013-06-20 17:28 | RHEEM - UNK | 80 | 2.5 | Yes | Yes | 21.1 | 21.5 | -0.4 | 6568A02C208E4D0E80C4624A441E43E3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93725-1706 |  | 2013-06-06 | 2013-06-06 16:01 | 2013-06-06 16:17 | GOODMAN - PGB048075 1 | 86 | 3.5 | Yes | Yes | 23.5 | 19.1 | 4.4 | 8C54362CFB9C40298BE8C2D43C87F7BA |  | R22 | Non-TXV |  | 4.07% | 0.9593 | 7.821% | [5 empty] | Non-TXV | 4.07%
Pleasanton | CA | 94566-6820 |  | 2013-07-03 | 2013-07-03 11:53 | 2013-07-03 12:35 | DAY & NIGHT - 568FJ048 | 180 | 14.6 | Yes | Yes | 24.2 | 19 | 5.2 | 9AA39D0A654B48938E874134C5FCE6C2 |  | R22 | Non-TXV |  | 8.111% | 0.91889 | 15.59% | [5 empty] | Non-TXV | 8.111%
San Jose | CA | 95111-3097 |  | 2013-09-17 | 2013-09-17 14:48 | 2013-09-17 15:40 | COLEMAN - ILLEGIBLE | 114 | 35.1 | Yes | Yes | 20.6 | 20.4 | 0.2 | 47259897BF0B4A37A21C9E58332FAC1E |  | R22 | Non-TXV |  | 30.79% | 0.69211 | 59.17% | [5 empty] | Non-TXV | 30.79%
W Sacramento | CA | 95691-4410 |  | 2013-06-12 | 2013-06-12 09:59 | 2013-06-12 10:25 | GE - BWD724A100A0 | 98 | -5.8 | Yes | Yes | 17.6 | 18.2 | -0.6 | 2044AD02E73F4EA5A1E99F18B2672539 |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Bakersfield | CA | 93304-4922 |  | 2013-06-18 | 2013-06-18 11:58 | 2013-06-18 11:58 | OTHER - UKN | 90 | 0 | Yes | Yes | 24.6 | 20.4 | 4.2 | 99CA30BF22C04FF69DD4879A7BDADB7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2528 |  | 2013-06-11 | 2013-06-11 11:43 | 2013-06-11 12:17 | GOODMAN - PGJ030050-1 | 72 | 3 | Yes | Yes | 17.2 | 18.2 | -1 | D36F9134D97F4DC8BEBFDA401E66FA3F |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Cottonwood | CA | 96022-7794 |  | 2013-06-25 | 2013-06-25 17:30 | 2013-06-25 19:09 | CARRIER - 48XP048090311 | 144 | -8.5 | Yes | Yes | 17.7 | 20.7 | -3 | 242C2050218D4B0FB5E32FFA3299440A |  | R410A | Non-TXV |  | -5.903% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.903%
Bakersfield | CA | 93306-1569 |  | 2013-07-16 | 2013-07-16 13:57 | 2013-07-16 13:57 | ICP - GPCM24K040F | 57 | 0 | Yes | Yes | 21.4 | 19.8 | 1.6 | 93AFF43FF70141019501E1F4B6E59081 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1863 |  | 2013-10-07 | 2013-10-07 11:09 | 2013-10-07 12:30 | CARRIER - 243ACR336A300 | 97 | 3.6 | Yes | Yes | 18.8 | 20.4 | -1.6 | 77B7A303822C44398A936222A1BD31C9 |  | R22 | Non-TXV |  | 3.711% | 0.96289 | 7.132% | [5 empty] | Non-TXV | 3.711%
Bakersfield | CA | 93309-6115 |  | 2013-05-31 | 2013-05-31 14:13 | 2013-05-31 14:13 | TRANE - 4YC260481096AB | 128 | 0 | Yes | Yes | 20.4 | 20.6 | -0.2 | 5F6C06C100E641A58DF82F167DF5D082 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1867 |  | 2013-06-27 | 2013-06-27 19:36 | 2013-06-27 19:36 | YORK - AC036X1221A | 98 | 0 | Yes | Yes | 19.6 | 20.7 | -1.1 | 9592B43BBA0040028DA70B6F5C83BC9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0343 |  | 2013-08-27 | 2013-08-27 15:18 | 2013-08-27 15:52 | LENNOX - PGC030K060A | 52 | 4.7 | Yes | Yes | 20 | 20.4 | -0.4 | B5C7EAF89AFA4B8D8FD09656EFB56863 |  | R22 | Non-TXV |  | 9.038% | 0.90962 | 17.37% | [5 empty] | Non-TXV | 9.038%
Calistoga | CA | 94515-1214 |  | 2013-06-05 | 2013-06-05 12:17 | 2013-06-05 12:17 | RHEEM - AT-38B10 | 85 | 0 | Yes | Yes | 19.2 | 18.7 | 0.5 | C5A073AB167748B5B0108ECD5BA5F0E0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6175 |  | 2013-06-29 | 2013-06-29 10:50 | 2013-06-29 11:19 | GOODMAN - PGB036100-1A | 57 | 10.2 | Yes | Yes | 21.4 | 22.6 | -1.2 | 135EFB85CF024234B9BA8F75EB450A0D |  | R22 | Non-TXV |  | 17.89% | 0.82105 | 34.39% | [5 empty] | Non-TXV | 17.89%
Fresno | CA | 93704-5529 |  | 2013-06-14 | 2013-06-14 11:30 | 2013-06-14 11:54 | YORK - DINH036N03606C | 108 | 3.2 | Yes | Yes | 27.4 | 21.4 | 6 | 6ADFC45E28EB4C709D2F25CDB17D8E10 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Bakersfield | CA | 93305-2325 |  | 2013-06-06 | 2013-06-06 13:16 | 2013-06-06 13:16 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 15.4 | 18.3 | -2.9 | D0FB040D81394E309883BD2180B7C1EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0404 |  | 2013-06-11 | 2013-06-11 11:33 | 2013-06-11 12:13 | LENNOX - 13ACD048 | 204 | 19.2 | Yes | Yes | 22.8 | 18.3 | 4.6 | 44B39010D7A14020B09D62A2F2F7E14D |  | R22 | TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | TXV | 9.412%
Bakersfield | CA | 93304-5975 |  | 2013-06-18 | 2013-06-18 09:51 | 2013-06-18 09:51 | AMANA - APG12600901A | 128 | 0 | Yes | Yes | 24.1 | 21 | 3.1 | 6E6760F369254924AF685EA5F9E681F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1143 |  | 2013-06-03 | 2013-06-03 16:48 | 2013-06-03 19:31 | CONCORD - RPG1CB42D075LA | 73 | 6.7 | Yes | Yes | 24.1 | 22.6 | 1.5 | 86469012C94F4599A6516049879C89E9 |  | R22 | Non-TXV |  | 9.178% | 0.90822 | 17.64% | [5 empty] | Non-TXV | 9.178%
Kerman | CA | 93630-1636 |  | 2013-09-23 | 2013-09-23 14:20 | 2013-09-23 21:39 | LENNOX - 12GCS036X753PA | 110 | 4 | Yes | Yes | 20.8 | 20.4 | 0.4 | 0999AC5DA4D14D69A574F9402D33595C |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Fremont | CA | 94555-1141 |  | 2013-07-01 | 2013-07-01 10:00 | 2013-07-01 10:00 | TAPPAN - CM-42-1A-C | 85 | 0 | Yes | Yes | 18.2 | 19.3 | -1.1 | D915759EB2224B70A4772FC0F3B45651 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1608 |  | 2013-06-03 | 2013-06-03 15:10 | 2013-06-03 16:06 | RHEEM - RRMAA036JK06X | 99 | 5.8 | Yes | Yes | 17.9 | 20.7 | -2.8 | 79CC7E860D0E4804BEB5FEEEE9BB9229 |  | R22 | TXV |  | 5.859% | 0.94141 | 11.26% | [5 empty] | TXV | 5.859%
Bakersfield | CA | 93305-2004 |  | 2013-06-06 | 2013-06-06 09:24 | 2013-06-06 09:42 | GOODMAN - PGB042100-1 | 68 | 3.1 | Yes | Yes | 20.4 | 19.5 | 0.9 | D22C061967E64E7ABC8B9D2C12E0C69C |  | R22 | Non-TXV |  | 4.559% | 0.95441 | 8.761% | [5 empty] | Non-TXV | 4.559%
Antioch | CA | 94509-3233 |  | 2013-05-30 | 2013-05-30 11:25 | 2013-05-30 11:47 | RUUD - UAKA-024-JAZ | 50 | 13.2 | Yes | Yes | 16.5 | 19.3 | -2.8 | 70FA28ACFC7843DD951A082F4818EED0 |  | R22 | Non-TXV |  | 26.4% | 0.736 | 50.73% | [5 empty] | Non-TXV | 26.4%
Fresno | CA | 93711-3143 |  | 2013-06-25 | 2013-06-25 09:18 | 2013-06-25 09:38 | PAYNE - 60RCAC-156 | 197 | 21.6 | Yes | Yes | 18 | 19 | -1 | 55C198F41938464FAB68DB96FC9ED3F6 |  | R22 | Non-TXV |  | 10.96% | 0.89036 | 21.07% | [5 empty] | Non-TXV | 10.96%
Cottonwood | CA | 96022-9669 |  | 2013-07-18 | 2013-07-18 15:26 | 2013-07-18 19:26 | COLEMAN - UNK | 130 | 5.4 | Yes | Yes | 22.9 | 20.1 | 2.8 | D09C7D8E223D41B387233AFEE95BD600 |  | R22 | Non-TXV |  | 4.154% | 0.95846 | 7.983% | [5 empty] | Non-TXV | 4.154%
Pittsburg | CA | 94565-2660 |  | 2013-07-15 | 2013-07-15 15:23 | 2013-07-15 15:55 | CARRIER - 38E0GB36300 | 136 | 2.5 | Yes | Yes | 17.6 | 13.5 | 4.2 | 07392C2F17EC426AAA2084D017334BCB |  | R410A | Non-TXV |  | 1.838% | 0.98162 | 3.533% | [5 empty] | Non-TXV | 1.838%
Fresno | CA | 93722-4362 |  | 2013-07-08 | 2013-07-08 15:43 | 2013-07-08 15:43 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | DB8FDF126EB14AFE8167F7313D547975 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6049 |  | 2013-06-25 | 2013-06-25 13:14 | 2013-06-25 13:14 | RHEEM - FAFF-037JAZ | 94 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | D280CC64E4B64CF7ABFA876E1D4E3707 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4606 |  | 2013-06-18 | 2013-06-18 10:33 | 2013-06-18 10:35 | AMERICAN STANDARD - 4YCC3030B1075AA | 85 | 3.7 | Yes | Yes | 15.3 | 17.7 | -2.4 | E41B0DC5AEEA4B35A90D088C997E364F |  | R410A | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Redding | CA | 96003-7642 |  | 2013-07-15 | 2013-07-15 13:38 | 2013-07-15 14:17 | RHEEM - RQNA B042JK | 158 | 5.3 | Yes | Yes | 23 | 20.2 | 2.8 | F6CFB2B9A992490EA6844994F1644CC2 |  | R22 | Non-TXV |  | 3.354% | 0.96646 | 6.446% | [5 empty] | Non-TXV | 3.354%
Sanger | CA | 93657-3904 |  | 2013-08-06 | 2013-08-06 14:58 | 2013-08-06 15:17 | ARCOAIRE - NAC024AKC3 | 71 | -5.8 | Yes | Yes | 19.7 | 19.2 | 0.5 | 817460B5DF104CDFB1F4452C86454603 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.169% | 1.0817 | 2.288% |  |  |  |  | Non-TXV |  |  | -8.169%
Bakersfield | CA | 93305-1910 |  | 2013-07-09 | 2013-07-09 14:11 | 2013-07-09 14:11 | RHEEM - UKN | 90 | 0 | Yes | Yes | 19.4 | 18.3 | 1.2 | ABC48A99FAAC4C14AA28C9CE13AB2C3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3904 |  | 2013-08-05 | 2013-08-05 14:01 | 2013-08-05 14:26 | ARCOAIRE - NAC024AKC3 | 71 | -2.6 | Yes | Yes | 18.1 | 19.9 | -1.8 | 1F9D871F89A440908A06D896D2BE6F16 |  | R22 | TXV |  | -3.662% | 1.0366 | 1.026% |  |  |  |  | TXV |  |  | -3.662%
Fresno | CA | 93702-3634 |  | 2013-05-30 | 2013-05-30 09:23 | 2013-05-30 09:43 | BRYANT - 48SS036080311 | 66 | 3.4 | Yes | Yes | 22.6 | 19.1 | 3.5 | 2278B676B8FF4634B7BAA5BAE402024F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | Non-TXV | 5.152%
Suisun City | CA | 94585-1763 |  | 2013-06-05 | 2013-06-05 12:41 | 2013-06-05 12:41 | COPELAND - GSC140361AE | 149 | 0 | Yes | Yes | 16.5 | 19.1 | -2.6 | F653F4CF67D34225BDE4494D295F44C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2911 |  | 2013-10-14 | 2013-10-14 13:36 | 2013-10-14 14:04 | PAYNE - PA10JA030-C | 77 | 5.4 | Yes | Yes | 19.6 | 16.4 | 3.2 | EA67C50F1AB3442E9572DF57B53FDB9B |  | R22 | TXV |  | 7.013% | 0.92987 | 13.48% | [5 empty] | TXV | 7.013%
Sanger | CA | 93657-3904 |  | 2013-08-06 | 2013-08-06 11:21 | 2013-08-06 12:31 | ARCOAIRE - NAC24AKC3 | 71 | 16.9 | Yes | Yes | 18.7 | 21 | -2.3 | F3108B1EB3AC4A3D97C9BB384E02C31D |  | R22 | Non-TXV |  | 23.8% | 0.76197 | 45.74% | [5 empty] | Non-TXV | 23.8%
Fresno | CA | 93722-1151 |  | 2013-09-18 | 2013-09-18 14:44 | 2013-09-18 18:28 | RHEEM - RAKA060JAZ | 112 | 4.5 | Yes | Yes | 21.6 | 20.8 | 0.8 | 738F849F1BA14AC68BBA0D3FB1F003EF |  | R22 | Non-TXV |  | 4.018% | 0.95982 | 7.721% | [5 empty] | Non-TXV | 4.018%
Fresno | CA | 93702-3127 |  | 2013-06-18 | 2013-06-18 10:09 | 2013-06-18 10:56 | CARRIER - 48SX030040311AA | 80 | 3.3 | Yes | Yes | 21.7 | 19.3 | 2.4 | 6A94BCA7E3424A6C94983B7991CAA5EA |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Fresno | CA | 93705-1308 |  | 2013-06-07 | 2013-06-07 13:27 | 2013-06-07 14:55 | RHEEM - HC803621C | 49 | -4.6 | Yes | Yes | 24.8 | 19.4 | 5.5 | 8737C0A4B3A344F7AA34D145C6574EA0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
San Jose | CA | 95122-3717 |  | 2013-10-21 | 2013-10-21 14:32 | 2013-10-21 15:32 | BRYANT - 113RNA048-B | 122 | 7.2 | Yes | Yes | 18.7 | 17.7 | 1 | 5AAF211838DB4E3592344EC631FB2DC2 |  | R22 | TXV |  | 5.902% | 0.94098 | 11.34% | [5 empty] | TXV | 5.902%
Bakersfield | CA | 93311-3095 |  | 2013-06-27 | 2013-06-27 11:06 | 2013-06-27 11:24 | YORK - AC042X1021A | 84 | 20.8 | Yes | Yes | 20.6 | 20.4 | 0.2 | F56CCF683AFE45D5A1100338905F2385 |  | R22 | Non-TXV |  | 24.76% | 0.75238 | 47.59% | [5 empty] | Non-TXV | 24.76%
Antioch | CA | 94509-4422 |  | 2013-05-29 | 2013-05-29 13:28 | 2013-05-29 13:28 | COLEMAN - 136-901 | 68 | 0 | Yes | Yes | 21.6 | 20.2 | 1.5 | 2F01B56999BB4F15B0A12389CB55988A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4336 |  | 2013-09-11 | 2013-09-11 11:10 | 2013-09-11 11:11 | CARRIER - 38EN036300 | 88 | 4.3 | Yes | Yes | 17.6 | 17.3 | 0.3 | E7B0299C2F44436B8259C71C6C5F7906 |  | R22 | Non-TXV |  | 4.886% | 0.95114 | 9.391% | [5 empty] | Non-TXV | 4.886%
Bakersfield | CA | 93308-5676 |  | 2013-06-14 | 2013-06-14 19:46 | 2013-06-14 19:46 | BDP - 561CJ030-C | 76 | 0 | Yes | Yes | 21.2 | 21 | 0.2 | E336441FAB464279B0B97E4E287D3154 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3010 |  | 2013-06-27 | 2013-06-27 18:56 | 2013-06-27 18:56 | BDP - 585HJ036060 | 102 | 0 | Yes | Yes | 18.8 | 20.6 | -1.8 | F2F5BBA8A7D4444FBAB143041DD5FC3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1707 |  | 2013-07-11 | 2013-07-11 10:20 | 2013-07-11 10:20 | CARRIER - 38TKB036300 | 81 | 0 | Yes | Yes | 20.8 | 17.4 | 3.4 | A572EDBF490549698F8E82B0B5C39870 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3097 |  | 2013-09-17 | 2013-09-17 16:56 | 2013-09-17 17:32 | COLEMAN - TCGD48S21SA | 69 | 2.2 | Yes | Yes | 23.4 | 19.9 | 3.5 | 7B581570827646FE8D856A9C5BFF425A |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Fresno | CA | 93722-4646 |  | 2013-08-21 | 2013-08-21 13:37 | 2013-08-21 13:58 | OTHER - PGA36B0702C | 112 | 3.4 | Yes | Yes | 19.3 | 21.2 | -1.9 | F71969EDFDA3497EBE1B386E6E548D32 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Fresno | CA | 93704-5438 |  | 2013-06-14 | 2013-06-14 08:42 | 2013-06-14 09:22 | CARRIER - 4865-036060301 | 60 | 5.5 | Yes | Yes | 23.7 | 20.3 | 3.5 | 6C597B4356F449319EBB5D28F454469F |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Bakersfield | CA | 93308-2130 |  | 2013-07-29 | 2013-07-29 10:47 | 2013-07-29 10:47 | ICP - PGAAD36D1KE | 100 | 0 | Yes | Yes | 21.5 | 21 | 0.5 | 86088E13EF524506AC26C20586A16380 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-1392 |  | 2013-06-17 | 2013-06-17 13:46 | 2013-06-17 14:05 | GE - BTB930A100A2 | 53 | -4.4 | Yes | Yes | 22.1 | 21.9 | 0.2 | 242595C594D94DDC8F8762D60A05E87F |  | R22 | Non-TXV |  | -8.302% | 1.083 | 2.325% |  |  |  |  | Non-TXV |  |  | -8.302%
Bakersfield | CA | 93304-3352 |  | 2013-06-12 | 2013-06-12 10:14 | 2013-06-12 10:14 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 18.2 | 21 | -2.8 | 310411ACECA34FE2BE4BF5DB817DE221 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2978 |  | 2013-08-28 | 2013-08-28 17:28 | 2013-08-28 17:28 | OTHER - UKN | 90 | 0 | Yes | Yes | 19.9 | 20.9 | -1 | 9F1A1E5B1FAC4B2DBDB31FF9FFDC811E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-0000 |  | 2013-10-01 | 2013-10-01 11:48 | 2013-10-01 12:24 | YORK - H1RD048S06H | 227 | 6.7 | Yes | Yes | 22 | 20.4 | 1.6 | 679AC2A0992A484EA9D11C29E92CA94E |  | R22 | Non-TXV |  | 2.952% | 0.97048 | 5.672% | [5 empty] | Non-TXV | 2.952%
Cottonwood | CA | 96022-8574 |  | 2013-07-13 | 2013-07-13 15:56 | 2013-07-13 15:56 | RHEEM - RRGG-05E36JKR | 75 | 0 | Yes | Yes | 17.7 | 20.2 | -2.5 | 43E68C999E8C4082BC5FE5C830337AB9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2979 |  | 2013-08-28 | 2013-08-28 18:20 | 2013-08-28 18:20 | OTHER - UKN | 90 | 0 | Yes | Yes | 20.2 | 19.6 | 0.7 | 91760ED31D154B9DBE2FD26F815105E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7827 |  | 2013-09-13 | 2013-09-13 15:37 | 2013-09-13 15:37 | GOODMAN - CKL36-10 | 72 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 40AD1BCD427D4C9BBAF502282403B505 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95403-6955 |  | 2013-10-03 | 2013-10-03 12:42 | 2013-10-03 16:13 | DAY & NIGHT - 541DJ018 | 83 | 2.9 | Yes | Yes | 16.6 | 19.5 | -2.9 | 854B3475450A45A99462A7401F80A755 |  | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
San Jose | CA | 95112-6071 |  | 2013-07-08 | 2013-07-08 14:26 | 2013-07-08 18:39 | NORDYNE - G3BA-024KA | 85 | 19.7 | Yes | Yes | 25.6 | 19.8 | 5.8 | 0CCDA593183744F1956733826232ADA9 |  | R22 | Non-TXV |  | 23.18% | 0.76824 | 44.54% | [5 empty] | Non-TXV | 23.18%
Madison | CA | 95653-0000 |  | 2013-09-09 | 2013-09-09 11:59 | 2013-09-09 12:21 | AMANA - PGB42B0902A | 112 | 4.1 | Yes | Yes | 23.6 | 21 | 2.6 | C2696024F3894879AE914186D3B82C4A |  | R22 | Non-TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | Non-TXV | 3.661%
Bakersfield | CA | 93306-3515 |  | 2013-10-01 | 2013-10-01 14:33 | 2013-10-01 14:33 | GOODMAN - CKJ48-1B | 110 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 6E7A1F9ECAAA48D7A4E4076BCF217A23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1856 |  | 2013-06-29 | 2013-06-29 13:26 | 2013-06-29 13:49 | RUUD - EAFF-037JAZ | 94 | 16 | Yes | Yes | 21.3 | 20.9 | 0.4 | FE68A814F05243E9B9957AF69D4DC98A |  | R22 | Non-TXV |  | 17.02% | 0.82979 | 32.71% | [5 empty] | Non-TXV | 17.02%
Bakersfield | CA | 93311-3093 |  | 2013-06-14 | 2013-06-14 18:05 | 2013-06-14 18:05 | YORK - AC048X1021A | 117 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | CF38295F8A6947B09AC9248410B96DDE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2976 |  | 2013-08-28 | 2013-08-28 17:09 | 2013-08-28 17:09 | ICP - GPCM24K040F | 54 | 0 | Yes | Yes | 19.6 | 19.8 | -0.2 | 82BCBFD477BA4FDAAA7D920225F74976 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7377 |  | 2013-06-05 | 2013-06-05 11:34 | 2013-06-05 12:14 | CARRIER - 38EH060330 | 236 | -16.7 | Yes | Yes | 17.5 | 19.7 | -2.2 | 201144D1BCD24FFA88E9BD189BA1599A |  | R22 | Non-TXV |  | -7.076% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.076%
Bakersfield | CA | 93311-3076 |  | 2013-06-04 | 2013-06-04 13:36 | 2013-06-04 13:51 | YORK - AC042X1021A | 84 | 7.2 | Yes | Yes | 20.5 | 20.1 | 0.4 | 75EDD37F12AB4976A921388898E8150D |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Bakersfield | CA | 93307-4308 |  | 2013-06-11 | 2013-06-11 12:04 | 2013-06-11 12:04 | GOODMAN - GPG132404518A | 77 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | 16B16BF66A0746FFB679CD1D4A363629 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3907 |  | 2013-08-05 | 2013-08-05 11:49 | 2013-08-05 12:22 | ARCOAIRE - NAC024AKC3 | 71 | 4 | Yes | Yes | 18.6 | 19.3 | -0.7 | E1ECE483EC1A4F9A8AA204E7C407CE3C |  | R22 | TXV |  | 5.634% | 0.94366 | 10.83% | [5 empty] | TXV | 5.634%
Bakersfield | CA | 93311-3075 |  | 2013-06-14 | 2013-06-14 09:44 | 2013-06-14 09:44 | YORK - AC048X1021A | 117 | 0 | Yes | Yes | 18.1 | 19.8 | -1.7 | 00CAFCB4CBDF4F988D193EE7EF2852CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-7930 |  | 2013-07-13 | 2013-07-13 11:49 | 2013-07-13 12:11 | ARMSTRONG - 2SCU13LB142P-1 | 111 | 7.2 | Yes | Yes | 25.7 | 20.2 | 5.6 | D9F416F93ABE4D3B80B3C694A24CFC83 |  | R22 | Non-TXV |  | 6.486% | 0.93514 | 12.47% | [5 empty] | Non-TXV | 6.486%
Fairfield | CA | 94533-2233 |  | 2013-06-03 | 2013-06-03 11:07 | 2013-06-03 11:07 | CONCORD - 13ACD-030-230-13 | 77 | 0 | Yes | Yes | 15.4 | 12 | 3.4 | 0DAC3C6A774B48A2A00AD753F48D18D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-5725 |  | 2013-06-18 | 2013-06-18 09:31 | 2013-06-18 09:51 | PAYNE - PA10JAO2400AAAA | 75 | -7.1 | Yes | Yes | 19 | 20.3 | -1.3 | 49EEA9AAA8474AE6AAC9E9E542492D5B |  | R22 | Non-TXV |  | -9.467% | 1.0947 | 2.651% |  |  |  |  | Non-TXV |  |  | -9.467%
Bakersfield | CA | 93308-2985 |  | 2013-10-13 | 2013-10-13 13:52 | 2013-10-13 13:52 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 19.6 | 20.7 | -1.1 | 3E69FDC952F8432CA63AE401A415BE8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakland | CA | 94603-3063 |  | 2013-07-02 | 2013-07-02 09:26 | 2013-07-02 09:55 | LENNOX - 13ACX-024 | 70 | 3.3 | Yes | Yes | 19.2 | 18.8 | 0.4 | 87543B66D8B2466BBB7BF90AB0B9D537 |  | R410A | Non-TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | Non-TXV | 4.714%
Kerman | CA | 93630-1306 |  | 2013-07-05 | 2013-07-05 10:27 | 2013-07-05 10:52 | AMERICAN STANDARD - YCC048F1H0BF | 80 | 2.5 | Yes | Yes | 17.1 | 19.6 | -2.5 | 5FD123F9F9B844AAA2CDF41071CADB86 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Kerman | CA | 93630-9309 |  | 2013-07-05 | 2013-07-05 16:09 | 2013-07-05 16:09 | - PGAA48D1K1 | 124 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | B1E42B5357F742C48F8A78A1169E1209 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2222 |  | 2013-06-04 | 2013-06-04 11:19 | 2013-06-04 12:09 | CARRIER - 38CKC030340 | 68 | 4.9 | Yes | Yes | 16.2 | 17.9 | -1.7 | 307D78AD40CB438BA9DD1D3D14AD897B |  | R22 | Non-TXV |  | 7.206% | 0.92794 | 13.85% | [5 empty] | Non-TXV | 7.206%
Mountain View | CA | 94041-1135 |  | 2013-10-02 | 2013-10-02 16:10 | 2013-10-02 16:27 | DAY & NIGHT - UNK | 87 | -6.1 | Yes | Yes | 20.6 | 21.5 | -0.9 | 95F144C0D20D45AABCF5F610D5023C56 |  | R410A | Non-TXV |  | -7.011% | 1.0701 | 1.964% |  |  |  |  | Non-TXV |  |  | -7.011%
Lemoore | CA | 93245-4423 |  | 2013-07-08 | 2013-07-08 15:34 | 2013-07-08 15:49 | OTHER - 561CJ030C | 72 | 4.2 | Yes | Yes | 19.3 | 17.9 | 1.4 | 2E567A0369FE4735A501230E8027B2A4 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Dixon | CA | 95620-3334 |  | 2013-06-05 | 2013-06-05 13:52 | 2013-06-05 14:14 | AMANA - RCC42A2A | 185 | 7.7 | Yes | Yes | 13.9 | 15.5 | -1.6 | 5AF132E34C984033822B39693EFE5731 |  | R22 | Non-TXV |  | 4.162% | 0.95838 | 7.999% | [5 empty] | Non-TXV | 4.162%
Pleasanton | CA | 94588-3839 |  | 2013-09-13 | 2013-09-13 09:35 | 2013-09-13 10:11 | NORDYNE - DS3BA-036KA | 85 | 9.4 | Yes | Yes | 22.6 | 16.8 | 5.8 | 3442E95201B342939BBFFD8AAEB4F7C1 |  | R22 | Non-TXV |  | 11.06% | 0.88941 | 21.25% | [5 empty] | Non-TXV | 11.06%
W Sacramento | CA | 95691-4608 |  | 2013-06-11 | 2013-06-11 12:40 | 2013-06-11 13:01 | LENNOX - HS29-030-1P | 68 | -5.6 | Yes | Yes | 17 | 18.2 | -1.2 | B9511C76C481487EBA86E02773423A16 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
W Sacramento | CA | 95691-2619 |  | 2013-06-11 | 2013-06-11 10:14 | 2013-06-11 10:39 | GOODMAN - GPG13240451BA | 85 | -5 | Yes | Yes | 16.1 | 18.2 | -2.1 | 65B5E56F5A6B496D8D6AE45381C6916B |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93706-3545 |  | 2013-06-10 | 2013-06-10 10:10 | 2013-06-10 10:35 | RHEEM - RRPLB03JK06X | 76 | 2.9 | Yes | Yes | 20.4 | 19.8 | 0.6 | AFEF5AE545F5485DA82CCA52CC1CE98C |  | R410A | TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | TXV | 3.816%
Bakersfield | CA | 93313-2225 |  | 2013-06-20 | 2013-06-20 10:33 | 2013-06-20 10:50 | RHEEM - RRNAC048JK10X | 85 | 4.7 | Yes | Yes | 20.3 | 20.1 | 0.3 | 624EF8AA4CB0481D8B7B148E7CE4BF67 |  | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Bakersfield | CA | 93307-4631 |  | 2013-09-27 | 2013-09-27 09:47 | 2013-09-27 09:47 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.6 | 21.5 | -2.9 | 6F6A87BE4527482B8ECDE00F0F6C0435 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sonoma | CA | 95476-8322 |  | 2013-05-31 | 2013-05-31 13:58 | 2013-05-31 14:19 | PAYNE - 591AN03600AAAA | 90 | 12.2 | Yes | Yes | 27.2 | 22.3 | 4.9 | B21ECEBA595F4C67872C00E583C2937E |  | R22 | Non-TXV |  | 13.56% | 0.86444 | 26.05% | [5 empty] | Non-TXV | 13.56%
Bakersfield | CA | 93308-1002 |  | 2013-07-26 | 2013-07-26 13:07 | 2013-07-26 13:38 | YORK - ERCS0421BBB | 141 | 19.9 | Yes | Yes | 22.3 | 20.4 | 1.9 | C97AD501534A41CDBDA2BB850F4D895D |  | R22 | Non-TXV |  | 14.11% | 0.85887 | 27.12% | [5 empty] | Non-TXV | 14.11%
San Jose | CA | 95148-2234 |  | 2013-07-23 | 2013-07-23 09:14 | 2013-07-23 09:14 | AMANA - RCC60A28 | 166 | 0 | Yes | Yes | 14.7 | 17 | -2.3 | C024A18FB3D048F48F6C30D0C65507CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5438 |  | 2013-06-03 | 2013-06-03 13:25 | 2013-06-03 13:25 | CARRIER - 24ABA342A300 | 102 | 0 | Yes | Yes | 17 | 19.7 | -2.7 | F8A15440069E4CDD9AFC5CBEEAABD7B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-4206 |  | 2013-07-09 | 2013-07-09 10:25 | 2013-07-09 10:48 | GOODMAN - CLJ361A | 109 | 4.6 | Yes | Yes | 19.9 | 18.3 | 1.6 | 6CDB20B34E8A4041BC9FAAE75B66EBE7 |  | R22 | Non-TXV |  | 4.22% | 0.9578 | 8.11% | [5 empty] | Non-TXV | 4.22%
Cottonwood | CA | 96022-9337 |  | 2013-07-13 | 2013-07-13 10:22 | 2013-07-13 11:15 | COLEMAN - BRCQ03618D | 52 | -3.7 | Yes | Yes | 26.5 | 21 | 5.5 | 98C5372281744ACB9AA0F69325B82D97 |  | R22 | Non-TXV |  | -7.115% | 1.0712 | 1.993% |  |  |  |  | Non-TXV |  |  | -7.115%
Bakersfield | CA | 93308-1002 |  | 2013-07-29 | 2013-07-29 08:42 | 2013-07-29 08:42 | YORK - TCGD48S21S1A | 75 | 0 | Yes | Yes | 21.6 | 22.1 | -0.5 | 09FFD4A5A1384E42A4AB4D93C5B98D1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1138 |  | 2013-06-10 | 2013-06-10 11:30 | 2013-06-10 11:30 | GE - | 85 | 0 | Yes | Yes | 15.5 | 15.9 | -0.4 | 03244988E40A4EDCB58761B5DCAE46AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2222 |  | 2013-06-21 | 2013-06-21 08:59 | 2013-06-21 08:59 | COMFORT AIRE - C2H348GKA100 | 210 | 0 | Yes | Yes | 17.4 | 20.3 | -2.9 | A6B6361CC1474BCFA7920126829B72B5 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2246 |  | 2013-06-04 | 2013-06-04 09:56 | 2013-06-04 09:56 | BRYANT - 561CJ024-D | 61 | -6.8 | Yes | Yes | 12.5 | 15.1 | -2.6 | 823EA8596A904A2686B61E7CDA159D67 | Remove refrigerant: 6.8 oz | R22 | Non-TXV |  | -11.15% | 1.1115 | 3.122% |  |  |  |  | Non-TXV |  |  | -11.15%
Bakersfield | CA | 93307-4631 |  | 2013-09-27 | 2013-09-27 08:55 | 2013-09-27 08:55 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 20.8 | 19.6 | 1.2 | 1CFCC336F4A64F42AC2F9CEB101CE799 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6758 |  | 2013-06-13 | 2013-06-13 11:07 | 2013-06-13 11:07 | YORK - D5YS036W04506A | 80 | 0 | Yes | Yes | 19.4 | 19.7 | -0.3 | F82BBFCB7EB6454A8AD0C27E7AFCD223 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3983 |  | 2013-06-18 | 2013-06-18 17:11 | 2013-06-18 17:59 | RHEEM - RACC024JAS | 49 | 5.2 | Yes | Yes | 20.2 | 21 | -0.8 | B0C768815B894C779DAF27DC168560BF |  | R22 | Non-TXV |  | 10.61% | 0.89388 | 20.39% | [5 empty] | Non-TXV | 10.61%
Fairfield | CA | 94534-1700 |  | 2013-06-04 | 2013-06-04 10:55 | 2013-06-04 11:14 | TRANE - 2TTR3042A1000AA | 109 | 8.2 | Yes | Yes | 18 | 18.5 | -0.4 | 748BAF7802CE47C2ABA1109064275949 |  | R22 | Non-TXV |  | 7.523% | 0.92477 | 14.46% | [5 empty] | Non-TXV | 7.523%
San Jose | CA | 95125-2304 |  | 2013-10-15 | 2013-10-15 14:04 | 2013-10-15 15:09 | TRANE - TT8T24A100A0 | 54 | 11.3 | Yes | Yes | 21.8 | 20.9 | 0.9 | 8BE94351441741BC89D7CA0012B45526 |  | R22 | Non-TXV |  | 20.93% | 0.79074 | 40.22% | [5 empty] | Non-TXV | 20.93%
Pacheco | CA | 94553-5002 |  | 2013-07-12 | 2013-07-12 14:48 | 2013-07-12 14:48 | CARRIER - N2A336AKB200 | 84 | 0 | Yes | Yes | 18.6 | 18.2 | 0.4 | 4A8C38151C7D44019DA97B93344B939D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2142 |  | 2013-07-31 | 2013-07-31 17:08 | 2013-07-31 18:59 | OTHER - GR6GDX36KO72X | 112 | 9.4 | Yes | Yes | 23.8 | 21.9 | 1.9 | 7BDE0A98911E44AF96150572ABC4A2C0 |  | R410A | TXV |  | 8.393% | 0.91607 | 16.13% | [5 empty] | TXV | 8.393%
Vacaville | CA | 95687-4004 |  | 2013-06-03 | 2013-06-03 11:19 | 2013-06-03 12:26 | COLEMAN - BRC00301BE | 41 | 10 | Yes | Yes | 17.1 | 19.1 | -2 | AF93BDD74192467287F83739B27F856D |  | R22 | Non-TXV |  | 24.39% | 0.7561 | 46.87% | [5 empty] | Non-TXV | 24.39%
Bakersfield | CA | 93307-4631 |  | 2013-09-27 | 2013-09-27 09:19 | 2013-09-27 09:19 | PAYNE - PYG3NAA24040NA | 72 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 05827749D93F470FA1E3B4C6A87EF0EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6809 |  | 2013-07-03 | 2013-07-03 13:22 | 2013-07-03 14:41 | CARRIER - UNK | 81 | -4.8 | Yes | Yes | 16.8 | 17.1 | -0.3 | 2390D6D20D504F73ABF15F409B5B56C3 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
W Sacramento | CA | 95691-5857 |  | 2013-06-21 | 2013-06-21 11:35 | 2013-06-21 12:51 | YORK - H2RA036600 | 63 | 1.9 | Yes | Yes | 19 | 17.9 | 1.1 | 7C319143B33B46AC8839EA8023AF7AB0 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Winters | CA | 95694-1825 |  | 2013-08-15 | 2013-08-15 14:02 | 2013-08-15 14:02 | LENNOX - HS9-042-2P | 87 | 0 | Yes | Yes | 20.6 | 16.4 | 4.2 | B812DF83612B4C8C8FAF4DAE6558AED4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-9712 |  | 2013-10-11 | 2013-10-11 11:18 | 2013-10-11 11:18 | DAY & NIGHT - UNK | 80 | 0 | Yes | Yes | 30 | 20.6 | 9.4 | 5E670C6D08814C3BBDBED887A13E5052 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2946 |  | 2013-06-10 | 2013-06-10 11:55 | 2013-06-10 12:16 | CARRIER - 585JJ048125 | 118 | -11.1 | Yes | Yes | 22.5 | 19.9 | 2.6 | 4A0C57ECD9264EF4B0838F65A26668EE |  | R22 | Non-TXV |  | -9.407% | 1.0941 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.407%
Suisun City | CA | 94585-2017 |  | 2013-08-08 | 2013-08-08 14:19 | 2013-08-08 14:40 | TRANE - 2TTB0042A1000AA | 95 | 4.4 | Yes | Yes | 16.1 | 17.7 | -1.6 | 1EDF3C81D1A54CD48564F45C08D5FD06 |  | R22 | Non-TXV |  | 4.632% | 0.95368 | 8.901% | [5 empty] | Non-TXV | 4.632%
Fresno | CA | 93725-1888 |  | 2013-06-21 | 2013-06-21 15:29 | 2013-06-21 15:29 | COLEMAN - PGB030050-1A | 56 | 0 | Yes | Yes | 24.8 | 21.5 | 3.3 | 7E2C2F0E22EC43648269792592B6FEC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5002 |  | 2013-06-03 | 2013-06-03 10:16 | 2013-06-03 10:38 | AMERICAN STANDARD - 4A7B3048A1000AA | 116 | 9.9 | Yes | Yes | 17 | 18.8 | -1.8 | 4DD9A2A682184632B770A8F511E8A013 |  | R410A | Non-TXV |  | 8.534% | 0.91466 | 16.4% | [5 empty] | Non-TXV | 8.534%
Concord | CA | 94519-1304 |  | 2013-06-21 | 2013-06-21 09:30 | 2013-06-21 09:54 | BRYANT - 561CJX024000ADA | 63 | -5.2 | Yes | Yes | 18.4 | 19.5 | -1.1 | 5CAA2AB662C548BF9937C29A35700CA4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -8.254% | 1.0825 | 2.311% |  |  |  |  | Non-TXV |  |  | -8.254%
Mc Farland | CA | 93250-1077 |  | 2013-07-26 | 2013-07-26 21:35 | 2013-07-26 21:57 | GOODMAN - GPG13360451AB | 112 | 4.7 | Yes | Yes | 24.4 | 20.4 | 4 | FAF32193A1934724B3578AC917B2EEC2 |  | R22 | Non-TXV |  | 4.196% | 0.95804 | 8.065% | [5 empty] | Non-TXV | 4.196%
Cottonwood | CA | 96022-7628 |  | 2013-06-28 | 2013-06-28 11:07 | 2013-06-28 12:10 | NORDYNE - FS3BD 048K | 99 | 6.3 | Yes | Yes | 22.5 | 20.2 | 2.3 | A91FF60EBAAD418996E1B8770547A3F3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Napa | CA | 94558-6703 |  | 2013-06-28 | 2013-06-28 10:02 | 2013-06-28 10:02 | PAYNE - PA13NA048-C | 129 | 0 | Yes | Yes | 22.8 | 19.8 | 3 | 5686DB8ABFD745AAAE209779CE24B037 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4640 |  | 2013-06-18 | 2013-06-18 18:34 | 2013-06-18 18:55 | TEMPSTAR - P6F324040K01A1 | 125 | 3.9 | Yes | Yes | 21.6 | 19.9 | 1.7 | 4C53563288DD4B8A84FAA5C766C3AD71 |  | R22 | Non-TXV |  | 3.12% | 0.9688 | 5.996% | [5 empty] | Non-TXV | 3.12%
Fairfield | CA | 94533-4510 |  | 2013-06-07 | 2013-06-07 12:20 | 2013-06-07 12:40 | AMERICAN STANDARD - YCC036F1MOBK | 83 | 3 | Yes | Yes | 20.6 | 17.7 | 2.9 | A324310371F145E99F80173C87C1CCEA |  | R22 | Non-TXV |  | 3.614% | 0.96386 | 6.946% | [5 empty] | Non-TXV | 3.614%
San Leandro | CA | 94578-1980 |  | 2013-06-26 | 2013-06-26 12:59 | 2013-06-26 14:39 | YORK - H2RC048S06G | 119 | 8.7 | Yes | Yes | 23.4 | 19.2 | 4.2 | 2F8171C7285343B9BB2ACE4D96045909 |  | R22 | TXV |  | 7.311% | 0.92689 | 14.05% | [5 empty] | TXV | 7.311%
Bakersfield | CA | 93305-1603 |  | 2013-06-06 | 2013-06-06 10:17 | 2013-06-06 10:17 | BDP - 585HJ036060 | 102 | 0 | Yes | Yes | 22.7 | 19.2 | 3.5 | 5406A67D935C49289616E20B9191C16A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1605 |  | 2013-09-18 | 2013-09-18 16:49 | 2013-09-18 17:48 | BRYANT - 1133ANA036 E | 83 | -6.8 | Yes | Yes | 22 | 20.6 | 1.5 | 4D88A720AB3A4E6285FA1390C12092BA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.193% | 1.0819 | 2.294% |  |  |  |  | Non-TXV |  |  | -8.193%
Fairfield | CA | 94533-2856 |  | 2013-06-21 | 2013-06-21 11:31 | 2013-06-21 12:14 | DAY & NIGHT - 591ANX042000ADAA | 90 | 0 | Yes | Yes | 18.5 | 18.7 | -0.2 | 85F20FC9A6064B93ADD697979B7A1A81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3934 |  | 2013-07-03 | 2013-07-03 12:27 | 2013-07-03 13:07 | YORK - D1NH036N05606 | 108 | 4.6 | Yes | Yes | 23.2 | 17.6 | 5.6 | 8D26B2EB06D342058B9A67E7B188F642 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Bakersfield | CA | 93305-4889 |  | 2013-08-19 | 2013-08-19 13:55 | 2013-08-19 13:55 | YORK - D3NZ024N03606NXA | 58 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 1001345FC51B4863AB0BD5F7E452FBA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-2376 |  | 2013-10-02 | 2013-10-02 16:55 | 2013-10-02 19:31 | BRYANT - 561CJ0W36-E | 71 | -2.8 | Yes | Yes | 24.4 | 18.8 | 5.6 | 335C734367F649E69F9E7DC04DDD7C2F |  | R22 | TXV |  | -3.944% | 1.0394 | 1.104% |  |  |  |  | TXV |  |  | -3.944%
Fresno | CA | 93702-3512 |  | 2013-08-01 | 2013-08-01 13:07 | 2013-08-01 13:34 | GOODMAN - PGB0300501 | 56 | 4.1 | Yes | Yes | 23.3 | 21.5 | 1.8 | EBB98AA271054F5BAB551C3BEDDA9B8C |  | R22 | Non-TXV |  | 7.321% | 0.92679 | 14.07% | [5 empty] | Non-TXV | 7.321%
Castro Valley | CA | 94546-2248 |  | 2013-07-03 | 2013-07-03 13:34 | 2013-07-03 13:34 | YORK - YCJD36S41S1HA | 73 | 0 | Yes | Yes | 23.8 | 18 | 5.8 | CE0632772EC848B8B740E69AF3D08A9A |  | R410A | TXV |  | 0% | 1 | 0%
Livermore | CA | 94550-6243 |  | 2013-07-01 | 2013-07-01 13:54 | 2013-07-01 18:50 | BDP - 568CJ036 | 152 | 18.1 | Yes | Yes | 22.4 | 17.7 | 4.7 | EBDCE9BC535041EFA5307219ABD6C3C4 |  | R22 | Non-TXV |  | 11.91% | 0.88092 | 22.88% | [5 empty] | Non-TXV | 11.91%
W Sacramento | CA | 95605-2238 |  | 2013-06-11 | 2013-06-11 09:34 | 2013-06-11 09:55 | OTHER - NA | 72 | 7.1 | Yes | Yes | 15.8 | 18.2 | -2.4 | 1BEAC305F1654EDE9F945FB4F574C31B |  | R22 | Non-TXV |  | 9.861% | 0.90139 | 18.95% | [5 empty] | Non-TXV | 9.861%
Bakersfield | CA | 93313-3516 |  | 2013-06-24 | 2013-06-24 08:41 | 2013-06-24 08:41 | ICP - PGC042K080E | 84 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 5D262913D73D453FA4DA3B577C6EDEE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95131-1970 |  | 2013-07-11 | 2013-07-11 12:42 | 2013-07-11 13:18 | SEARS - NCAFB36AB01 | 85 | 10.3 | Yes | Yes | 21.8 | 18.5 | 3.4 | 0C7EF549E69E4971AB1330B94AE0E1CC |  | R22 | Non-TXV |  | 12.12% | 0.87882 | 23.29% | [5 empty] | Non-TXV | 12.12%
Redding | CA | 96003-7631 |  | 2013-09-03 | 2013-09-03 11:09 | 2013-09-03 12:05 | NORDYNE - T5BD-024K | 110 | -9.8 | Yes | Yes | 26.6 | 21 | 5.6 | 6FD7848497D94EF8B47E119F1AA237F5 |  | R22 | Non-TXV |  | -8.909% | 1.0891 | 2.495% |  |  |  |  | Non-TXV |  |  | -8.909%
Fresno | CA | 93722-1123 |  | 2013-07-09 | 2013-07-09 10:40 | 2013-07-09 11:39 | YORK - D4NZ048N09006NXC | 68 | 2.6 | Yes | Yes | 27.7 | 21.8 | 5.9 | 74D2D9281F2B41B9881BF111FA8711A0 |  | R410A | TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | TXV | 3.824%
Concord | CA | 94521-3412 |  | 2013-06-18 | 2013-06-18 20:43 | 2013-06-18 20:43 | OTHER - UNK | 85 | 0 | Yes | Yes | 19 | 20.9 | -1.9 | 8B7EEEC6042F483CB9060F774E7B11AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2973 |  | 2013-08-28 | 2013-08-28 15:57 | 2013-08-28 16:15 | ICP - PGC024K060A | 58 | 9.5 | Yes | Yes | 20.6 | 21.3 | -0.7 | DA5DEC87CA7A4B8C8CF9D5F84CDA42BA |  | R22 | Non-TXV |  | 16.38% | 0.83621 | 31.48% | [5 empty] | Non-TXV | 16.38%
Cottonwood | CA | 96022-9405 |  | 2013-06-27 | 2013-06-27 13:41 | 2013-06-27 14:18 | DAY & NIGHT - NW048080ACAG | 88 | 3.1 | Yes | Yes | 25.3 | 20.8 | 4.5 | 53CB662A1F434BE29A7DC7CE20CE853B |  | R22 | Non-TXV |  | 3.523% | 0.96477 | 6.77% | [5 empty] | Non-TXV | 3.523%
Bakersfield | CA | 93308-2986 |  | 2013-08-28 | 2013-08-28 14:33 | 2013-08-28 14:50 | OTHER - CTG0244G7A | 60 | 7.7 | Yes | Yes | 20.7 | 20.1 | 0.6 | 9A07D4C34B33440E83D3F62D2452F652 |  | R22 | Non-TXV |  | 12.83% | 0.87167 | 24.66% | [5 empty] | Non-TXV | 12.83%
Bakersfield | CA | 93308-2987 |  | 2013-08-28 | 2013-08-28 15:38 | 2013-08-28 15:38 | BRYANT - 582ANW024040AAAD | 50 | 0 | Yes | Yes | 20.1 | 19.3 | 0.8 | F507470B2C644853A23FD9DC2B6A0CE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94566-8401 |  | 2013-07-03 | 2013-07-03 12:42 | 2013-07-03 13:24 | OTHER - 38TK036300 | 117 | 3.9 | Yes | Yes | 25.1 | 20.2 | 4.9 | C1FABB2C9316432CB0825705BC5028A6 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93722-4704 |  | 2013-06-12 | 2013-06-12 17:43 | 2013-06-12 22:43 | RHEEM - RRNAB036JK08X | 83 | -6.4 | Yes | Yes | 19.4 | 18.5 | 0.9 | 8D2C5EDBBD0246A4B9CFF67F213A55A4 |  | R22 | TXV |  | -7.711% | 1.0771 | 2.159% |  |  |  |  | TXV |  |  | -7.711%
Antioch | CA | 94531-9134 |  | 2013-06-10 | 2013-06-10 10:16 | 2013-06-10 10:36 | GMC - CKL60-1 | 115 | -10.8 | Yes | Yes | 18.4 | 19.8 | -1.4 | 6E511D4E19144545B157B1A7426BA0FC |  | R22 | Non-TXV |  | -9.391% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.391%
San Jose | CA | 95121-2311 |  | 2013-10-08 | 2013-10-08 13:46 | 2013-10-08 14:35 | TRANE - TTZ036A100A0 | 208 | 16.9 | Yes | Yes | 26.3 | 20.6 | 5.7 | 7B716982A63E4F72A2BD9DD640568240 |  | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Sanger | CA | 93657-3904 |  | 2013-08-08 | 2013-08-08 15:32 | 2013-08-08 15:55 | ARCOAIRE - NAC024AKC3 | 71 | 6.2 | Yes | Yes | 20 | 20.4 | -0.4 | EF79A3ECC78A4F4B98F6F89AE28DEB47 |  | R22 | TXV |  | 8.732% | 0.91268 | 16.78% | [5 empty] | TXV | 8.732%
Sanger | CA | 93657-2299 |  | 2013-08-08 | 2013-08-08 10:29 | 2013-08-08 11:09 | ARCOAIRE - NAC024AKC3 | 71 | 4 | Yes | Yes | 19.5 | 19.3 | 0.2 | 40F7F38D719B4E1A93F4DE49BFC8D7A8 |  | R22 | TXV |  | 5.634% | 0.94366 | 10.83% | [5 empty] | TXV | 5.634%
Sanger | CA | 93657-2299 |  | 2013-08-08 | 2013-08-08 17:03 | 2013-08-08 17:21 | ARCOAIRE - NAC024AKC3 | 71 | 5.6 | Yes | Yes | 18.9 | 19.2 | -0.3 | 0009D887FAB94BD2858B8078B5388519 |  | R22 | TXV |  | 7.887% | 0.92113 | 15.16% | [5 empty] | TXV | 7.887%
San Jose | CA | 95121-1257 |  | 2013-10-08 | 2013-10-08 14:56 | 2013-10-08 15:26 | TRANE - 2TTB0042A1000AA | 95 | -6.7 | Yes | Yes | 25.5 | 20.4 | 5.2 | CA21B75C27EE4E25B6CDB651BA343678 |  | R22 | Non-TXV |  | -7.053% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.053%
Bakersfield | CA | 93307-4632 |  | 2013-09-27 | 2013-09-27 16:13 | 2013-09-27 16:13 | RHEEM - RRKAA024JK06X | 50 | 0 | Yes | Yes | 20 | 19.3 | 0.7 | 60C3854233864523937A0E61F2008BB3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2136 |  | 2013-06-10 | 2013-06-10 12:33 | 2013-06-11 07:32 | CARRIER - 588ANW036080ABAF | 69 | -6.5 | Yes | Yes | 18.3 | 19.3 | -1 | 83664E543D184D2CB3929D9D50ACA4C3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.42% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.42%
Bakersfield | CA | 93307-4632 |  | 2013-09-27 | 2013-09-27 15:52 | 2013-09-27 15:52 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | 763652BC67844CFB86233E04831E4DDD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4039 |  | 2013-06-20 | 2013-06-20 12:38 | 2013-06-20 13:04 | HEIL - NAC042AKA1 | 105 | 4 | Yes | Yes | 25.3 | 19.4 | 5.9 | 2E7138E106E14A95969CA59835603B2C |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Fresno | CA | 93725-9500 |  | 2013-08-26 | 2013-08-26 10:21 | 2013-08-26 10:47 | CARRIER - 38TK048310 | 171 | 5.4 | Yes | Yes | 19.6 | 19.3 | 0.3 | 7BBE849916C34ED4836A46414F5E49C6 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
San Jose | CA | 95148-3112 |  | 2013-07-08 | 2013-07-08 11:40 | 2013-07-08 11:40 | TRANE - 2TTR2048A1000AA | 120 | 0 | Yes | Yes | 24.4 | 19.8 | 4.6 | 168D422F6D38400A854D7E68C2A82054 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6997 |  | 2013-06-12 | 2013-06-12 13:19 | 2013-06-12 13:19 | RHEEM - RAFF031JAZ | 96 | 0 | Yes | Yes | 20.3 | 20.9 | -0.6 | 8AD2BB2B49C145D1ADB8C9240AC71C70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-2209 |  | 2013-10-02 | 2013-10-02 11:47 | 2013-10-02 12:18 | HEIL - PGAA24B1K5 | 66 | 4 | Yes | Yes | 20.3 | 19.9 | 0.4 | 30425A1FDF524EC49B510D961FFD39E1 |  | R22 | Non-TXV |  | 6.061% | 0.93939 | 11.65% | [5 empty] | Non-TXV | 6.061%
Kingsburg | CA | 93631-2450 |  | 2013-07-12 | 2013-07-12 10:16 | 2013-07-12 10:45 | PAYNE - PY1PNB042060AAA | 100 | 14 | Yes | Yes | 26.3 | 21.3 | 5.1 | AEE909A92E0848278C6BC66618852528 |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Fresno | CA | 93722-4242 |  | 2013-06-12 | 2013-06-12 11:52 | 2013-06-12 12:12 | BRYANT - 582ANW036090AAAF | 60 | 3.9 | Yes | Yes | 21.7 | 19.9 | 1.8 | FDEF03178DA04B0BAC4C9DA7C8D64C94 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Bakersfield | CA | 93311-2740 |  | 2013-06-14 | 2013-06-14 19:53 | 2013-06-14 19:53 | ICP - NAC248AKC3 | 151 | 0 | Yes | Yes | 20.5 | 21.2 | -0.7 | B2A28BB40C764FE19638E4C7B03BAE24 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2651 |  | 2013-06-07 | 2013-06-07 15:33 | 2013-06-07 15:50 | LENNOX - 10ACC-036-230-02 | 74 | -7 | Yes | Yes | 16.4 | 17.7 | -1.3 | C7714FB7A22E4E54972FB75C349DDAC9 |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Fairfield | CA | 94533-2123 |  | 2013-08-05 | 2013-08-05 11:14 | 2013-08-05 11:14 | PAYNE - 561CJ030-B | 71 | 0 | Yes | Yes | 17.9 | 20.7 | -2.8 | 17189FB049E843FF9667681AC0FDB8CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1243 |  | 2013-07-05 | 2013-07-05 09:25 | 2013-07-05 09:25 | DAY & NIGHT - 580ANO30040 | 88 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | BE573F1224EF476F92DB993827DE1008 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1751 |  | 2013-06-11 | 2013-06-11 16:04 | 2013-06-11 16:25 | GOODMAN - CLJ48-1 | 117 | 6 | Yes | Yes | 24.3 | 20.2 | 4.1 | 63DC05407CD1407CA8F0BAEB86836BD0 |  | R22 | Non-TXV |  | 5.128% | 0.94872 | 9.855% | [5 empty] | Non-TXV | 5.128%
Fairfield | CA | 94533-1637 |  | 2013-06-12 | 2013-06-12 10:26 | 2013-06-12 10:47 | OTHER - 38CK030330 | 68 | 2.2 | Yes | Yes | 15.6 | 17.7 | -2.1 | 322337D2287148BB9B6F606F99CA83FF |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Bakersfield | CA | 93304-2739 |  | 2013-06-12 | 2013-06-12 08:50 | 2013-06-12 08:50 | ICP - CAC248AKA4 | 148 | 0 | Yes | Yes | 18.7 | 20.9 | -2.2 | 9B4793C6AE39428AB326C64EF1CD6569 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-3230 |  | 2013-07-11 | 2013-07-11 11:32 | 2013-07-11 12:34 | HEIL - CA3036VKB1 | 85 | 10.6 | Yes | Yes | 22.6 | 19.3 | 3.3 | 0FE5C362B4234F7CA2D5FB6523259EB3 |  | R22 | Non-TXV |  | 12.47% | 0.87529 | 23.97% | [5 empty] | Non-TXV | 12.47%
Fresno | CA | 93706-2832 |  | 2013-06-10 | 2013-06-10 09:01 | 2013-06-10 09:32 | GMC - PG08042 | 68 | 7.5 | Yes | Yes | 20.2 | 18.5 | 1.8 | 1F2D78E993614B3A9A9807D86DA57515 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.03% | 0.88971 | 21.2% | [5 empty] | Non-TXV | 11.03%
Concord | CA | 94520-3300 |  | 2013-06-21 | 2013-06-21 14:24 | 2013-06-21 14:53 | YORK - H1C001806A | 56 | 3.3 | Yes | Yes | 17.3 | 19.9 | -2.6 | A3E28DD9EEBE4426A0A56686FF0FE2ED |  | R22 | Non-TXV |  | 5.893% | 0.94107 | 11.32% | [5 empty] | Non-TXV | 5.893%
San Jose | CA | 95121-1215 |  | 2013-07-11 | 2013-07-11 13:26 | 2013-07-11 13:26 | PAYNE - PA13NR036-E | 121 | 70 | Yes | Yes | 22.4 | 18.5 | 3.9 | 64A3574547FC4BE5855C2FD210B0A3B6 | Add refrigerant: 7 oz | R22 | TXV |  | 57.85% | 0.42149 | 111.2% | [5 empty] | TXV | 57.85%
Bakersfield | CA | 93313-3633 |  | 2013-06-25 | 2013-06-25 17:12 | 2013-06-25 17:12 | GOODMAN - GPG1348070M41CA | 87 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | 564B5E1FFDD34BACA06D08CC6355E78E |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-1157 |  | 2013-07-11 | 2013-07-11 14:04 | 2013-07-11 14:04 | BRYANT - 561CJ036-E | 124 | 0 | Yes | Yes | 22 | 18.5 | 3.5 | 682EF8D7820A4AC4A3D5CE95E9CE1E85 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5531 |  | 2013-07-03 | 2013-07-03 15:39 | 2013-07-03 16:01 | GOODMAN - GPG13420701AB | 107 | 3.3 | Yes | Yes | 24.4 | 19.3 | 5.1 | F745F3289747422FB70608F0756F48D1 |  | R22 | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Fresno | CA | 93722-5531 |  | 2013-07-03 | 2013-07-03 16:04 | 2013-07-03 16:31 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 23.4 | 21.3 | 2.1 | F632686C53E743AB8E62FA319602EA7D |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Selma | CA | 93662-9775 |  | 2013-07-15 | 2013-07-15 15:40 | 2013-07-15 15:40 | HEIL - CA5542VK02 | 98 | 0 | Yes | Yes | 35 | 21.2 | 13.8 | 79F62EBA6E1E4B16A26F085F7DA286BA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Willits | CA | 95490-4509 |  | 2013-08-19 | 2013-08-19 12:03 | 2013-08-19 12:38 | OTHER - ILLEGIBLE | 60 | 5.5 | Yes | Yes | 24.1 | 21 | 3.1 | 5AA42D8AFCD5410E9117DB7700B786F6 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Bakersfield | CA | 93308-2978 |  | 2013-08-28 | 2013-08-28 17:46 | 2013-08-28 18:03 | OTHER - UKN | 90 | 13.1 | Yes | Yes | 19.9 | 21.1 | -1.2 | 78F2C3E8C47440B494609BEEBC22FAE2 |  | R22 | Non-TXV |  | 14.56% | 0.85444 | 27.97% | [5 empty] | Non-TXV | 14.56%
Bakersfield | CA | 93308-2976 |  | 2013-08-28 | 2013-08-28 16:34 | 2013-08-28 16:50 | CARRIER - UKN | 91 | 14 | Yes | Yes | 21.2 | 20.1 | 1.1 | 63087B2B66D24FF2926CEEEAF223AC48 |  | R22 | Non-TXV |  | 15.38% | 0.84615 | 29.57% | [5 empty] | Non-TXV | 15.38%
San Jose | CA | 95121-2325 |  | 2013-07-25 | 2013-07-25 13:06 | 2013-07-25 13:09 | RHEEM - NA | 76 | 2.7 | Yes | Yes | 15.8 | 16.3 | -0.5 | 85A6BCFA84D548B4A277D9E33D160ECE |  | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Willits | CA | 95490-8804 |  | 2013-08-21 | 2013-08-21 16:41 | 2013-08-21 17:07 | AMERICAN STANDARD - 2A7A5036A1000AA | 137 | 5.2 | Yes | Yes | 25.6 | 21.5 | 4.1 | 513544CC5F1842B1AFC0E6468189CF3F |  | R22 | Non-TXV |  | 3.796% | 0.96204 | 7.294% | [5 empty] | Non-TXV | 3.796%
Fairfield | CA | 94534-7443 |  | 2013-06-12 | 2013-06-12 09:06 | 2013-06-12 09:06 | CARRIER - 38TH036300 | 85 | 0 | Yes | Yes | 17.7 | 20.5 | -2.8 | 6FC9DF9FB5184DAF8E6467300C6E4CDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7606 |  | 2013-06-10 | 2013-06-10 09:18 | 2013-06-10 09:18 | RHEEM - RAFD-042JBS | 79 | 0 | Yes | Yes | 18.8 | 18.5 | 0.3 | 342E9A6680C2481A9103DB80340A6DFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4216 |  | 2013-08-23 | 2013-08-23 15:10 | 2013-08-23 15:10 | CARRIER - 485X-030060331AA | 72 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | E79FAB9C720F4737851B8A99E813E6EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4216 |  | 2013-08-23 | 2013-08-23 15:12 | 2013-08-23 15:12 | CARRIER - 485X-030080321AA | 84 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | 6D4E2585783641168E2B907CDCA36914 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-2110 |  | 2013-10-01 | 2013-10-01 09:11 | 2013-10-01 10:08 | LENNOX - 10GS030X751PA | 51 | -4.8 | Yes | Yes | 24.7 | 19.8 | 4.9 | 28E051A55D2C485388F141D3FA0A89DF |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Lamont | CA | 93241-1212 |  | 2013-07-18 | 2013-07-18 16:34 | 2013-07-18 16:56 | YORK - D1NP030N05606A | 73 | 6.6 | Yes | Yes | 25.6 | 20.4 | 5.2 | 2E88D44E7DBB483E91CF2D77C173E137 |  | R22 | TXV |  | 9.041% | 0.90959 | 17.37% | [5 empty] | TXV | 9.041%
Lamont | CA | 93241-1212 |  | 2013-07-18 | 2013-07-18 16:57 | 2013-07-18 17:20 | YORK - D1NP030N05606A | 73 | 8.9 | Yes | Yes | 23.5 | 19.6 | 3.9 | 6C38DC22CC284558B45723FD62853CFC |  | R22 | TXV |  | 12.19% | 0.87808 | 23.43% | [5 empty] | TXV | 12.19%
San Jose | CA | 95121-1352 |  | 2013-10-10 | 2013-10-10 11:28 | 2013-10-10 11:54 | AMANA - RCB30B2A | 84 | 3.2 | Yes | Yes | 20.1 | 20.7 | -0.6 | CFAEAB36ED344F2DAA5ED1975277B39A |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Mc Farland | CA | 93250-1079 |  | 2013-09-03 | 2013-09-03 21:11 | 2013-09-03 21:14 | YORK - D2NP036N05606A | 108 | -5.1 | Yes | Yes | 25.8 | 19.9 | 5.9 | 559880F5972749EC815FC61BFFBBA371 |  | R22 | Non-TXV |  | -4.722% | 1.0472 | 1.322% |  |  |  |  | Non-TXV |  |  | -4.722%
Davis | CA | 95616-3612 |  | 2013-06-28 | 2013-06-28 11:39 | 2013-06-28 11:59 | LENNOX - HS29-024-1P | 61 | 9.3 | Yes | Yes | 18.3 | 17.9 | 0.4 | 110C739E95334E05B6A2D7F99B543F6E |  | R22 | Non-TXV |  | 15.25% | 0.84754 | 29.3% | [5 empty] | Non-TXV | 15.25%
Fresno | CA | 93706-3134 |  | 2013-09-12 | 2013-09-12 11:55 | 2013-09-12 12:20 | GOODMAN - GPG12240701A | 64 | 10.5 | Yes | Yes | 25.8 | 19.9 | 5.9 | 84DE85D74593485DB20665557376A042 |  | R22 | Non-TXV |  | 16.41% | 0.83594 | 31.53% | [5 empty] | Non-TXV | 16.41%
Gilroy | CA | 95020-6734 |  | 2013-07-22 | 2013-07-22 21:28 | 2013-07-22 21:28 | AMANA - RCC48A2A | 85 | 0 | Yes | Yes | 17.9 | 17.8 | 0.1 | 9464EF9CF6F140E2B4E65CF7EFD61EF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2015 |  | 2013-06-07 | 2013-06-07 09:44 | 2013-06-07 10:15 | BRYANT - 86-567S | 83 | -7.8 | Yes | Yes | 17.7 | 17.1 | 0.6 | C6C58AFC1BA84EEEA37D6C1B5800A97E |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Lemoore | CA | 93245-3715 |  | 2013-08-02 | 2013-08-02 09:28 | 2013-08-02 09:28 | OTHER - UNK | 80 | 0 | Yes | Yes | 21.4 | 20.9 | 0.5 | 5A571B6572C44E18B83D34A57D1922D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1656 |  | 2013-09-03 | 2013-09-03 21:17 | 2013-09-03 21:20 | GOODMAN - GPG10360701A | 75 | 4 | Yes | Yes | 21 | 21.2 | -0.2 | 122332F8CDD5429889CB04AF5DD314CC |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Fairfield | CA | 94533-1637 |  | 2013-06-07 | 2013-06-07 11:05 | 2013-06-07 11:33 | - 38CKC036340 | 73 | -5.2 | Yes | Yes | 16.5 | 17 | -0.5 | 5288A5906F884214A9937BBAAAB36CF8 |  | R22 | Non-TXV |  | -7.123% | 1.0712 | 1.995% |  |  |  |  | Non-TXV |  |  | -7.123%
Fresno | CA | 93725-1889 |  | 2013-06-17 | 2013-06-17 11:19 | 2013-06-17 11:44 | OTHER - UNK | 80 | 5.2 | Yes | Yes | 22 | 20.5 | 1.5 | 215ED9F4D2D9485A9E8D2BA1F638706A |  | R410A | TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | TXV | 6.5%
Wasco | CA | 93280-2763 |  | 2013-10-29 | 2013-10-29 18:34 | 2013-10-29 18:36 | OTHER - H2RD030S06B | 92 | 3.9 | Yes | Yes | 24.2 | 19.7 | 4.5 | B47476BFE61546059BF0A50F71BEEB1D |  | R22 | TXV |  | 4.239% | 0.95761 | 8.147% | [5 empty] | TXV | 4.239%
Bakersfield | CA | 93312-8284 |  | 2013-06-26 | 2013-06-26 19:26 | 2013-06-26 19:26 | YORK - H2RRA036S06G | 63 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 6B4EB99811BD4B018E6E4500AACE6913 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-8284 |  | 2013-06-26 | 2013-06-26 19:33 | 2013-06-26 19:33 | YORK - H2RRA036S06G | 63 | 0 | Yes | Yes | 20.6 | 20.4 | 0.2 | 0B22D3C5126440B9812F595B7EFB3915 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3843 |  | 2013-06-18 | 2013-06-18 10:58 | 2013-06-18 11:42 | YORK - 48SX030040311AA | 108 | 5.6 | Yes | Yes | 22.7 | 19.7 | 3.1 | 060A6013FEED466FA55467160E6DBB72 |  | R22 | TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | TXV | 5.185%
San Jose | CA | 95133-1910 |  | 2013-10-21 | 2013-10-21 11:58 | 2013-10-21 13:14 | UNITARY PRODUCTS GROUP - TCGD36S21S1A | 68 | 2.5 | Yes | Yes | 19.3 | 20.5 | -1.2 | 7FC310EF88504061AA5FFE4E4D72B2F2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Lemoore | CA | 93245-1907 |  | 2013-07-08 | 2013-07-08 13:38 | 2013-07-08 13:38 | YORK - D1NP036N05606A | 76 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D0929763E78F42F592AD208C30D8E0C8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2059 |  | 2013-06-10 | 2013-06-10 10:23 | 2013-06-10 10:23 | - GS3BA-048KA | 115 | 0 | Yes | Yes | 14.4 | 14.4 | 0 | 88D81914DDB745E0B591DF1AAF217A7D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2809 |  | 2013-09-16 | 2013-09-16 09:21 | 2013-09-16 09:21 | PAYNE - PA13NA030-B | 111 | 0 | Yes | Yes | 22 | 18.6 | 3.4 | 0036070C9DA64D20A50275D0603CD0A9 |  | R410A | TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1655 |  | 2013-07-29 | 2013-07-29 19:20 | 2013-07-29 19:32 | GOODMAN - GPG10360701A | 75 | 3.4 | Yes | Yes | 24.7 | 21.3 | 3.4 | C420E9B918704286A343294016C6B7E5 |  | R22 | Non-TXV |  | 4.533% | 0.95467 | 8.712% | [5 empty] | Non-TXV | 4.533%
Fairfield | CA | 94533-2710 |  | 2013-06-07 | 2013-06-07 10:33 | 2013-06-07 10:50 | TRANE - 2TTR2036A1000AA | 96 | -3.5 | Yes | Yes | 16.8 | 17.5 | -0.7 | D3BDEAC4656342E1916F0491B52C2A37 |  | R22 | Non-TXV |  | -3.646% | 1.0365 | 1.021% |  |  |  |  | Non-TXV |  |  | -3.646%
Bakersfield | CA | 93311-2405 |  | 2013-06-14 | 2013-06-14 16:27 | 2013-06-14 16:27 | RUUD - UAPC-048JAZ | 288 | 0 | Yes | Yes | 20.5 | 18.5 | 2 | 6B69EF006C424594A8DAEF6FA864E922 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-7426 |  | 2013-10-23 | 2013-10-23 13:28 | 2013-10-23 14:07 | RHEEM - RACC-036JAO | 49 | -2.9 | Yes | Yes | 24.6 | 19.8 | 4.8 | 628B38FD093D465FB8C242FEA4C13284 |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Bakersfield | CA | 93308-2169 |  | 2013-08-31 | 2013-08-31 17:15 | 2013-08-31 17:35 | BRYANT - 582ANW024060AAAD | 53 | 7 | Yes | Yes | 22 | 21.5 | 0.5 | 26C597517A7A4ADBA774E9131FE1E755 |  | R22 | Non-TXV |  | 13.21% | 0.86792 | 25.38% | [5 empty] | Non-TXV | 13.21%
Livermore | CA | 94550-5531 |  | 2013-06-25 | 2013-06-25 08:56 | 2013-06-25 08:56 | ALLEGIANCE - 7A0048B100A1 | 97 | 0 | Yes | Yes | 19.5 | 18.8 | 0.7 | 337FF37753C14DE2AA82DFD1AC1E7AFD |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4712 |  | 2013-06-24 | 2013-06-24 13:43 | 2013-06-24 15:09 | LENNOX - 13ACX036 | 89 | 6.8 | Yes | Yes | 18.1 | 19.9 | -1.8 | 3A0282721F6A478FB8796633E3257978 |  | R410A | TXV |  | 7.64% | 0.9236 | 14.68% | [5 empty] | TXV | 7.64%
Willits | CA | 95490-4428 |  | 2013-08-19 | 2013-08-19 13:44 | 2013-08-19 14:01 | YORK - BRC00361BD | 52 | -3.7 | Yes | Yes | 24.6 | 20.4 | 4.2 | F75B40A186BB4EE38BB31F9CBA76868E |  | R22 | Non-TXV |  | -7.115% | 1.0712 | 1.993% |  |  |  |  | Non-TXV |  |  | -7.115%
Bakersfield | CA | 93308-2167 |  | 2013-08-31 | 2013-08-31 15:33 | 2013-08-31 15:33 | OTHER - CTG024G7A | 90 | 0 | Yes | Yes | 22.4 | 22.1 | 0.3 | 4507DC1CE25649CA907398AA972A0FE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5459 |  | 2013-06-12 | 2013-06-12 14:48 | 2013-06-12 14:48 | YORK - D1NH048N09006C | 124 | 0 | Yes | Yes | 19.4 | 20.2 | -0.8 | 7EDDC1312C1B47EA829573B718D553FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1650 |  | 2013-07-29 | 2013-07-29 19:07 | 2013-07-29 19:35 | GOODMAN - N/A | 85 | 2.9 | Yes | Yes | 22.6 | 23.1 | -0.5 | E10802A63BE342858A90DB9DE843EAAA |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Napa | CA | 94558-4613 |  | 2013-07-30 | 2013-07-30 09:43 | 2013-07-30 09:46 | CARRIER - 48GS-036060301 | 56 | -4.6 | Yes | Yes | 14.9 | 16.4 | -1.5 | BB342753C6634154939A12A9012715CA |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Woodland | CA | 95776-5768 |  | 2013-06-17 | 2013-06-17 11:55 | 2013-06-17 12:45 | TRANE - TTD736A100A0 | 100 | 3.6 | Yes | Yes | 17.1 | 17.9 | -0.8 | 68BF8DA0C566475CAAB63C987D231CF5 |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Bakersfield | CA | 93312-2028 |  | 2013-06-26 | 2013-06-26 18:22 | 2013-06-26 18:41 | ICP - PGF342080K01 | 184 | 37.3 | Yes | Yes | 23.1 | 20.1 | 3 | 75176B9B4A424665847EB24A7432ABCF |  | R22 | Non-TXV |  | 20.27% | 0.79728 | 38.96% | [5 empty] | Non-TXV | 20.27%
Vallejo | CA | 94589-3609 |  | 2013-06-18 | 2013-06-18 15:06 | 2013-06-18 15:25 | HEIL - CA5542VKD2 | 90 | -6.4 | Yes | Yes | 21 | 21.5 | -0.5 | E6341F5E26A64C52B5799CD272D91E8D |  | R22 | Non-TXV |  | -7.111% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.111%
Lemoore | CA | 93245-4724 |  | 2013-08-29 | 2013-08-29 13:24 | 2013-08-29 13:51 | GOODMAN - CK421C | 92 | 5.4 | Yes | Yes | 16.2 | 18.8 | -2.6 | 8B0E650380504DDFB4953A917EF3FFE3 |  | R22 | TXV |  | 5.87% | 0.9413 | 11.28% | [5 empty] | TXV | 5.87%
Bakersfield | CA | 93307-6132 |  | 2013-08-08 | 2013-08-08 18:51 | 2013-08-08 18:51 | ICP - UKN | 108 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 44157FEFCDD7438E8EA9EC19307B6C83 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2183 |  | 2013-08-30 | 2013-08-30 16:30 | 2013-08-30 16:30 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.6 | 21.2 | 0.4 | 173EF636C9E040DCB3C2D9E12B04BF63 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-6667 |  | 2013-09-18 | 2013-09-18 15:25 | 2013-09-18 15:25 | OTHER - FAFF-043JAZ | 99 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | DCF8F35C831947478A59B19BF3D00E12 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1146 |  | 2013-10-01 | 2013-10-01 16:06 | 2013-10-01 16:06 | OTHER - UKM | 41 | 0 | Yes | Yes | 21.8 | 22.1 | -0.3 | B27B4D7A48274ED49730DDB1679616EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3630 |  | 2013-08-01 | 2013-08-01 10:51 | 2013-08-01 11:15 | GUARDIAN - GCGD0521S2B | 85 | -5 | Yes | Yes | 23.3 | 22.1 | 1.2 | 638BE0E5968940F08BF2605878CC3AB2 |  | R22 | TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | TXV |  |  | -5.882%
Bakersfield | CA | 93308-2168 |  | 2013-08-31 | 2013-08-31 16:21 | 2013-08-31 16:44 | OTHER - CTG024G7A | 60 | 8.2 | Yes | Yes | 21.8 | 22.1 | -0.3 | FDA3AAE9866A44DAA5E1F7F43C0F0388 |  | R22 | Non-TXV |  | 13.67% | 0.86333 | 26.26% | [5 empty] | Non-TXV | 13.67%
Bakersfield | CA | 93309-1841 |  | 2013-08-01 | 2013-08-01 09:24 | 2013-08-01 09:24 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 21 | 20.9 | 0.1 | 2B6F4939569B423399146B3DEDEBF697 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4514 |  | 2013-06-24 | 2013-06-24 09:45 | 2013-06-24 10:41 | RHEEM - RRNAB0243K06X | 70 | 8.4 | Yes | Yes | 16.5 | 17.2 | -0.7 | 370019926793419CB06B22F2B2FAF0A6 |  | R22 | TXV |  | 12% | 0.88 | 23.06% | [5 empty] | TXV | 12%
Bakersfield | CA | 93312-6250 |  | 2013-10-01 | 2013-10-01 12:04 | 2013-10-01 12:04 | YORK - AC060X1223A | 147 | 0 | Yes | Yes | 21.2 | 19.8 | 1.4 | 13340B3E128943BDB1870DC041BB0272 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6250 |  | 2013-10-01 | 2013-10-01 12:27 | 2013-10-01 12:27 | YORK - AC024X1222A | 71 | 0 | Yes | Yes | 21.2 | 19.7 | 1.5 | 91E048144B5C429E9667E001627EE55A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4316 |  | 2013-07-09 | 2013-07-09 15:08 | 2013-07-09 15:08 | YORK - BRCS0361BD | 63 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 8C9AD34E68B04180B2E6A9EE423F0856 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-3932 |  | 2013-07-11 | 2013-07-11 10:19 | 2013-07-11 10:38 | COLEMAN - ILLEGIBLE | 100 | 22.1 | Yes | Yes | 27.8 | 22.1 | 5.7 | 26A2FFB7772E43BE99EDD908F358F73A |  | R22 | Non-TXV |  | 22.1% | 0.779 | 42.47% | [5 empty] | Non-TXV | 22.1%
Bakersfield | CA | 93304-1147 |  | 2013-10-01 | 2013-10-01 16:21 | 2013-10-01 16:21 | OTHER - UKN | 85 | 0 | Yes | Yes | 22.5 | 22 | 0.5 | 7B3EDFC46CC64683BF7E0C2FB1E96A27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-1910 |  | 2013-09-06 | 2013-09-06 10:26 | 2013-09-06 11:02 | COLEMAN - UNK | 85 | 2.6 | Yes | Yes | 20.6 | 16.6 | 4 | 8D3256AF685A4FD09D29C6F654ABFB2F |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93313-2218 |  | 2013-06-20 | 2013-06-20 18:57 | 2013-06-20 18:57 | YORK - DINP030N05606A | 73 | 0 | Yes | Yes | 19.6 | 21 | -1.4 | D9B79339C29A45748BC053A7C351EAE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1143 |  | 2013-10-01 | 2013-10-01 17:04 | 2013-10-01 17:04 | ICP - PGD3704K001C1 | 72 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 062A88FEC685415AAD4D60914870D466 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3720 |  | 2013-08-15 | 2013-08-15 12:07 | 2013-08-15 13:25 | YORK - D1NP036N05606A | 108 | 5.3 | Yes | Yes | 20.2 | 20.2 | 0 | 60D618E684424B428379EC4AAE78CD2B |  | R22 | Non-TXV |  | 4.907% | 0.95093 | 9.431% | [5 empty] | Non-TXV | 4.907%
Milpitas | CA | 95035-7853 |  | 2013-09-27 | 2013-09-27 13:13 | 2013-09-27 13:38 | COLEMAN - TCGD36WS2121A | 84 | 3 | Yes | Yes | 21.4 | 20.4 | 1 | B4949C161F4C43F68E66A5D186340104 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Reedley | CA | 93654-3425 |  | 2013-08-01 | 2013-08-01 17:24 | 2013-08-01 18:05 | CARRIER - 585CJ02450 | 72 | 5 | Yes | Yes | 26.5 | 22.1 | 4.4 | 197A5ABA510744EA888FE650A06A9BA0 |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Livermore | CA | 94550-5128 |  | 2013-06-20 | 2013-06-20 13:49 | 2013-06-20 15:31 | TRANE - TTX036C100A0 | 152 | 8.2 | Yes | Yes | 20.2 | 19.9 | 0.3 | A04437C240FB486BAD99F778BCDB9998 |  | R22 | Non-TXV |  | 5.395% | 0.94605 | 10.37% | [5 empty] | Non-TXV | 5.395%
Anderson | CA | 96007-4620 |  | 2013-07-08 | 2013-07-08 13:29 | 2013-07-08 14:09 | ARMSTRONG - 2SCU13LB136P-1 | 111 | 7.2 | Yes | Yes | 28.5 | 22.6 | 5.9 | 8AA21AE257D4435EAF475DF25683DAFB |  | R22 | Non-TXV |  | 6.486% | 0.93514 | 12.47% | [5 empty] | Non-TXV | 6.486%
Bakersfield | CA | 93304-1143 |  | 2013-10-01 | 2013-10-01 17:20 | 2013-10-01 17:20 | TRANE - 27CC3030A1040AA | 88 | 0 | Yes | Yes | 22.4 | 20.9 | 1.5 | AF90893FBE65489499DC9A2F080FA084 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1208 |  | 2013-06-25 | 2013-06-25 13:48 | 2013-06-25 13:48 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | EBE86F007E1144F8AB086FA7E0FF0513 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4613 |  | 2013-09-13 | 2013-09-13 14:52 | 2013-09-13 14:52 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 99B49E1639F64FB592877332A4F4D253 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1146 |  | 2013-10-01 | 2013-10-01 16:35 | 2013-10-01 16:35 | OTHER - UKN | 41 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 69466CCDB1974848B14BE3B770E3ACE6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-5754 |  | 2013-06-10 | 2013-06-10 11:41 | 2013-06-10 11:41 | TRANE - TTD730B100A1 | 69 | 0 | Yes | Yes | 19.2 | 18.8 | 0.4 | 19C59C84B23B44BD84393F5D114750C7 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4377 |  | 2013-06-17 | 2013-06-17 09:17 | 2013-06-17 09:17 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 21.3 | 20.6 | 0.8 | 737F8E02390746DE82B0DFD4B3F2D511 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6546 |  | 2013-09-24 | 2013-09-24 13:03 | 2013-09-24 15:41 | JANITROL - CE25-1EB | 85 | -3 | Yes | Yes | 18.5 | 16.2 | 2.4 | 348C6B16B8A14CDD916FFAA645509A90 |  | R22 | Non-TXV |  | -3.529% | 1.0353 | 0.9884% |  |  |  |  | Non-TXV |  |  | -3.529%
Fresno | CA | 93706-2930 |  | 2013-06-24 | 2013-06-24 10:50 | 2013-06-24 10:50 | CARRIER - 480L003 | 49 | 0 | Yes | Yes | 19.8 | 19.3 | 0.5 | 7018497E3B4A4721B4ED761EC3769048 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1746 |  | 2013-06-14 | 2013-06-14 09:10 | 2013-06-14 09:30 | OTHER - GCGD24S41S3A | 61 | 1.9 | Yes | Yes | 14.9 | 17.2 | -2.3 | 5484DC41644549999037336281E6782C |  | R410A | Non-TXV |  | 3.115% | 0.96885 | 5.986% | [5 empty] | Non-TXV | 3.115%
Bakersfield | CA | 93308-2978 |  | 2013-08-28 | 2013-08-28 17:52 | 2013-08-28 17:52 | ICP - PGC030K060A | 56 | 0 | Yes | Yes | 21.8 | 22.1 | -0.3 | C9BE0221883E42D2863D94FF6FB19E8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3481 |  | 2013-06-20 | 2013-06-20 11:51 | 2013-06-20 12:09 | CARRIER - 38CKC036350 | 73 | 2.4 | Yes | Yes | 18.7 | 18.7 | 0 | DDAB1C55CB4A4FA1B3077A431C7EE627 |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Napa | CA | 94558-3418 |  | 2013-09-11 | 2013-09-11 10:45 | 2013-09-11 10:46 | YORK - H4DB036S06A | 73 | -6.9 | Yes | Yes | 17.7 | 17.5 | 0.2 | DA07D087F66D4CB995A71CF37B7A97FF |  | R22 | Non-TXV |  | -9.452% | 1.0945 | 2.647% |  |  |  |  | Non-TXV |  |  | -9.452%
San Jose | CA | 95124-3416 |  | 2013-10-10 | 2013-10-10 10:44 | 2013-10-10 11:15 | AIRE-FLO - AFAIR10B42 | 89 | -8.4 | Yes | Yes | 24 | 20.2 | 3.8 | 7CE539202DCA4F2A978AA2CDE8DBBE3F |  | R22 | Non-TXV |  | -9.438% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.438%
Santa Rosa | CA | 95407-6656 |  | 2013-07-01 | 2013-07-01 11:20 | 2013-07-01 11:20 | CARRIER - 38CKC036---351--- | 70 | 0 | Yes | Yes | 11.4 | 14 | -2.6 | 986D44C87D0243C3AB2B2B34E2B8AD69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3412 |  | 2013-06-11 | 2013-06-11 11:38 | 2013-06-11 11:38 | CARRIER - 38CKC024---331-- | 60 | 0 | Yes | Yes | 14.7 | 17.2 | -2.5 | E889B85FFE0D4C70BBD394E43B7FC1AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ukiah | CA | 95482-3033 |  | 2013-08-22 | 2013-08-22 12:29 | 2013-08-22 13:01 | LENNOX - 10ACB36-11P | 80 | 3.1 | Yes | Yes | 25.9 | 21.5 | 4.4 | 7CDE7D62D2CE401C8B56E22FB3C5C366 |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Fresno | CA | 93702-2607 |  | 2013-07-10 | 2013-07-10 11:36 | 2013-07-10 12:21 | COLEMAN - DAYPF036N070A | 108 | 5 | Yes | Yes | 19.6 | 19.3 | 0.3 | 4A6B31405BAF4B99AFADA58891195251 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Shafter | CA | 93263-3412 |  | 2013-07-25 | 2013-07-25 20:33 | 2013-07-26 08:03 | GOODMAN - PGB0360501A | 60 | 2.4 | Yes | Yes | 21.1 | 22.5 | -1.4 | 3BB3D141F2B74ADF8E41A24147F113C1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93705-1909 |  | 2013-06-11 | 2013-06-11 14:37 | 2013-06-11 14:59 | YORK - AC024M1021CG | 52 | 9.4 | Yes | Yes | 19 | 19.5 | -0.5 | 757A8597CDED43239333FFFDA027EFF0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.08% | 0.81923 | 34.74% | [5 empty] | Non-TXV | 18.08%
Kerman | CA | 93630-1423 |  | 2013-07-09 | 2013-07-09 15:46 | 2013-07-09 15:46 | RHEEM - RRNAB036JK08X | 83 | 0 | Yes | Yes | 19.4 | 20.8 | -1.4 | 3D8AF4B1011A4BC89596E7C6574B6376 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2320 |  | 2013-06-07 | 2013-06-07 10:18 | 2013-06-07 11:12 | ALLEGIANCE - 7A2042A100A0 | 152 | 14.7 | Yes | Yes | 15.9 | 17.6 | -1.7 | 485EA4AE1F6144078C0A7FE3030F84C6 |  | R22 | Non-TXV |  | 9.671% | 0.90329 | 18.59% | [5 empty] | Non-TXV | 9.671%
Bakersfield | CA | 93313-4949 |  | 2013-06-21 | 2013-06-21 11:28 | 2013-06-21 11:28 | YORK - H1RA042S06A | 83 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | 25723F2CFEDE40299337C03E1D134C47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5618 |  | 2013-07-12 | 2013-07-12 14:54 | 2013-07-12 14:54 | RHEEM - UKN | 85 | 0 | Yes | Yes | 21.5 | 19.8 | 1.7 | 2A0E21628B7F4A24B7C040FB0FFA9126 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6287 |  | 2013-08-14 | 2013-08-14 18:25 | 2013-08-14 18:25 | CARRIER - 585HJ036060 | 108 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | E376370166F94C439363DB4B391134AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-7402 |  | 2013-07-29 | 2013-07-29 11:37 | 2013-07-29 13:10 | BRYANT - 561CJ048-A | 159 | 8.4 | Yes | Yes | 21.5 | 18.8 | 2.8 | 21CC2BB316E64BE784DF7777A9CAE8FD |  | R22 | TXV |  | 5.283% | 0.94717 | 10.15% | [5 empty] | TXV | 5.283%
Bakersfield | CA | 93308-2975 |  | 2013-08-28 | 2013-08-28 16:07 | 2013-08-28 16:26 | BRYANT - 582AWW024040AAAD | 53 | 6.5 | Yes | Yes | 21.6 | 21.5 | 0.1 | DD454A08F4AF4E9C809F2F7885E70736 |  | R22 | Non-TXV |  | 12.26% | 0.87736 | 23.57% | [5 empty] | Non-TXV | 12.26%
Fairfield | CA | 94534-1002 |  | 2013-06-07 | 2013-06-07 11:15 | 2013-06-07 13:44 | TRANE - BTD724A1001 | 68 | 8.4 | Yes | Yes | 18.3 | 18.8 | -0.5 | 0241125A62FA425088A38F9182840ED0 |  | R22 | Non-TXV |  | 12.35% | 0.87647 | 23.74% | [5 empty] | Non-TXV | 12.35%
Kerman | CA | 93630-2110 |  | 2013-07-09 | 2013-07-09 16:28 | 2013-07-09 17:10 | LENNOX - 10GCS30X75 | 51 | 6.1 | Yes | Yes | 21.3 | 19.9 | 1.4 | 8B4ABFCFED7F49358684C8F2EBC1D608 |  | R22 | Non-TXV |  | 11.96% | 0.88039 | 22.99% | [5 empty] | Non-TXV | 11.96%
Fresno | CA | 93728-1304 |  | 2013-06-20 | 2013-06-20 09:09 | 2013-06-20 09:34 | TRANE - YCY024F1M0AD | 105 | 3.3 | Yes | Yes | 26.3 | 20.4 | 5.9 | 932BF75C02E640CC816754B5A950F2C9 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Taft | CA | 93268-2405 |  | 2013-09-23 | 2013-09-23 19:20 | 2013-09-23 19:20 | DAY & NIGHT - | 85 | -7 | Yes | Yes | 24.3 | 23.1 | 1.2 | B3FE311606B142C08BFE2CF9528B9BD5 | Remove refrigerant: 7 oz | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Bakersfield | CA | 93304-1245 |  | 2013-09-21 | 2013-09-21 17:29 | 2013-09-21 17:29 | OTHER - UKN | 60 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | 955B6DB733114C46BE27564E3B4A752B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7177 |  | 2013-06-12 | 2013-06-12 12:01 | 2013-06-12 12:22 | BDP - 585EJ036075 | 80 | 4.7 | Yes | Yes | 18.9 | 20.2 | -1.3 | E76F89B589004CA7903AD2C1E7E40715 |  | R22 | Non-TXV |  | 5.875% | 0.94125 | 11.29% | [5 empty] | Non-TXV | 5.875%
Bakersfield | CA | 93307-4377 |  | 2013-06-17 | 2013-06-17 10:56 | 2013-06-17 10:56 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 11D9F76C62FE45A1987696E6F4B1D961 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2991 |  | 2013-08-30 | 2013-08-30 18:45 | 2013-08-30 18:45 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 20.2 | 18.6 | 1.6 | 8C196A0BF58240E38DA95301D6EE7E37 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4377 |  | 2013-06-17 | 2013-06-17 10:16 | 2013-06-17 10:16 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | 7C32E1AACD534ABDACC40E0B881EEE5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1802 |  | 2013-10-10 | 2013-10-10 15:26 | 2013-10-10 19:51 | RUUD - UNK | 68 | 3.8 | Yes | Yes | 19 | 20.4 | -1.4 | 61F9403466214064B39D8CF9D84884ED |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Bakersfield | CA | 93304-6446 |  | 2013-06-18 | 2013-06-18 12:33 | 2013-06-18 12:33 | YORK - DAYPFO36N070A | 108 | 0 | Yes | Yes | 25.4 | 20.6 | 4.8 | 5E55CDD3141E4ED5BBB490F5DED6B406 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2854 |  | 2013-07-12 | 2013-07-12 10:13 | 2013-07-12 10:42 | NORDYNE - GS3BA-048KA | 85 | 7.5 | Yes | Yes | 20.2 | 17 | 3.2 | 1E754C8A78E940D8A22A4FC66BBFCD69 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Willits | CA | 95490-4196 |  | 2013-08-19 | 2013-08-19 14:47 | 2013-08-19 15:06 | YORK - DRCS0361BD | 98 | 3.3 | Yes | Yes | 25.5 | 20.7 | 4.8 | CC46B00EB787421DBBD5C06A6A9A1A5A |  | R22 | Non-TXV |  | 3.367% | 0.96633 | 6.471% | [5 empty] | Non-TXV | 3.367%
Fresno | CA | 93725-0000 |  | 2013-06-05 | 2013-06-05 16:48 | 2013-06-05 17:05 | GOODMAN - GSX130060 | 125 | 6 | Yes | Yes | 20.9 | 20.6 | 0.4 | 490B0087BE99400DA76BE8D1730750C3 |  | R410A | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
San Jose | CA | 95121-3201 |  | 2013-07-11 | 2013-07-11 08:54 | 2013-07-11 09:37 | PAYNE - PA10JA036-C | 152 | 5.7 | Yes | Yes | 18.9 | 20.2 | -1.3 | 8FF74EC981534C53B4B3344E9CF81477 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Cottonwood | CA | 96022-7717 |  | 2013-06-26 | 2013-06-26 14:15 | 2013-06-26 15:32 | DAY & NIGHT - 588AQNW048100AEAG | 101 | -7.1 | Yes | Yes | 20.9 | 19.9 | 1.1 | D913C18AF8CD47C3A1094ACA61F6048D |  | R22 | Non-TXV |  | -7.03% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.03%
San Jose | CA | 95129-2850 |  | 2013-07-12 | 2013-07-12 13:26 | 2013-07-12 14:07 | TRANE - TTB036C100A1 | 90 | 14.8 | Yes | Yes | 23.3 | 18 | 5.3 | 9208A236E5D04C0C89E77FFC48FB0C89 |  | R22 | Non-TXV |  | 16.44% | 0.83556 | 31.6% | [5 empty] | Non-TXV | 16.44%
Gilroy | CA | 95020-8117 |  | 2013-10-23 | 2013-10-23 09:55 | 2013-10-23 10:17 | CARRIER - ILLEGIBLE | 74 | -7 | Yes | Yes | 22.4 | 20.1 | 2.3 | 67EF7F873BB64D03B032CF776956946B |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Santa Rosa | CA | 95405-5220 |  | 2013-07-05 | 2013-07-05 12:31 | 2013-07-05 12:31 | BRYANT - 561CJX48000AAAA | 102 | 0 | Yes | Yes | 20.6 | 17.7 | 2.9 | C20430EE2F1B4D21906BC965B4845325 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93723-9276 |  | 2013-06-18 | 2013-06-18 17:31 | 2013-06-18 17:31 | RHEEM - RRMA-A048JK10X | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D5287EF982134903B44277468EAA8D97 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-3256 |  | 2013-06-19 | 2013-06-19 11:15 | 2013-06-19 11:53 | ALLEGIANCE - 7A0030A100A1 | 62 | 6.7 | Yes | Yes | 24.3 | 19.8 | 4.5 | D74D4FA631634FF282009EE86A16FDA2 |  | R22 | Non-TXV |  | 10.81% | 0.89194 | 20.77% | [5 empty] | Non-TXV | 10.81%
W Sacramento | CA | 95691-5490 |  | 2013-06-20 | 2013-06-20 12:35 | 2013-06-20 14:24 | CARRIER - 38CKC060370 | 131 | 4.4 | Yes | Yes | 18.2 | 17.9 | 0.3 | B6A23410FBD44CD38CB1A367DE8C4828 |  | R22 | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
Bakersfield | CA | 93312-1877 |  | 2013-10-01 | 2013-10-01 09:43 | 2013-10-01 09:43 | YORK - H2RC048S06HG | 119 | 0 | Yes | Yes | 20.6 | 20.7 | -0.1 | 42E3A0CC4B5646618DFA2317DA1E2B32 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-1877 |  | 2013-10-01 | 2013-10-01 10:10 | 2013-10-01 10:10 | YORK - H2RC036S06HG | 83 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | 0B9FD7967F14489593CBE1244EF62BFE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2240 |  | 2013-06-18 | 2013-06-18 11:02 | 2013-06-18 11:27 | AMERICAN STANDARD - YCY0361M0AC | 129 | 5.5 | Yes | Yes | 17.9 | 18.7 | -0.8 | 1A8F1B76784B485FBFB06C70C8CDF8AF |  | R22 | Non-TXV |  | 4.264% | 0.95736 | 8.194% | [5 empty] | Non-TXV | 4.264%
Bakersfield | CA | 93308-2961 |  | 2013-08-29 | 2013-08-29 17:08 | 2013-08-29 17:25 | ICP - PGC024K06A | 58 | 8.7 | Yes | Yes | 21.5 | 20.2 | 1.3 | EAEAD8A9FA034DA2946270889C7D435E |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Bakersfield | CA | 93304-4514 |  | 2013-06-18 | 2013-06-18 11:16 | 2013-06-18 11:33 | - PGAD42D1K5 | 180 | 12.9 | Yes | Yes | 20.2 | 21.5 | -1.3 | 684F97F0794A4D74808E59764CAE7A11 |  | R22 | TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | TXV | 7.167%
Dixon | CA | 95620-2449 |  | 2013-07-01 | 2013-07-01 12:11 | 2013-07-01 13:19 | JANITROL - CM36-1FB | 85 | -5 | Yes | Yes | 18.1 | 17.9 | 0.2 | D9B1E2B2DD454569B0A8440BABC67B81 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 17:28 | 2013-06-18 17:28 | NORDYNE - UKN | 144 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 8C4C7A9768D84BEFB6ED69FCA1F7E890 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-2209 |  | 2013-10-02 | 2013-10-02 14:53 | 2013-10-02 15:26 | GOODMAN - GPG13360701AA | 112 | 4.9 | Yes | Yes | 24.2 | 22.6 | 1.6 | F8291450F2D746DFB87853E60CD2E2ED |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Bakersfield | CA | 93307-4386 |  | 2013-06-19 | 2013-06-19 18:41 | 2013-06-19 18:41 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 4FF53EA064494E2DAD049F51C7F0DC04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2961 |  | 2013-08-29 | 2013-08-29 16:14 | 2013-08-29 16:31 | RHEEM - UKN | 90 | 12.4 | Yes | Yes | 19.8 | 20.1 | -0.3 | 4AD8C83BB7924C68BEA0192B2C4B9D81 |  | R22 | Non-TXV |  | 13.78% | 0.86222 | 26.48% | [5 empty] | Non-TXV | 13.78%
Bakersfield | CA | 93307-4377 |  | 2013-06-17 | 2013-06-17 11:25 | 2013-06-17 11:25 | NORDYNE - JT5BD-030KA | 144 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 761BEBC244C74B40B9A98DF128E8D28E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1648 |  | 2013-06-06 | 2013-06-06 15:32 | 2013-06-06 16:00 | CARRIER - 24ABA342A003100 | 84 | 3 | Yes | Yes | 22.4 | 19.9 | 2.6 | CAAC83CD245D48C08791973865E66839 |  | R410A | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
W Sacramento | CA | 95691-4317 |  | 2013-06-12 | 2013-06-12 14:30 | 2013-06-12 14:42 | OTHER - NA | 76 | 3 | Yes | Yes | 18.7 | 18.2 | 0.5 | B4FF19AB5D1C4A2F86067292A7C010EE |  | R22 | Non-TXV |  | 3.947% | 0.96053 | 7.586% | [5 empty] | Non-TXV | 3.947%
Fresno | CA | 93725-1653 |  | 2013-06-24 | 2013-06-24 12:52 | 2013-06-24 12:52 | PAYNE - PAI3NA036 | 74 | 0 | Yes | Yes | 16 | 18.1 | -2.1 | B45E0FF7B88A4D01A336D213468C740A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2962 |  | 2013-08-29 | 2013-08-29 15:17 | 2013-08-29 15:33 | ICP - PGC024K060A | 58 | 7.3 | Yes | Yes | 20.5 | 20.1 | 0.4 | 356F0686862E43068F80BACE5A7E0BCE |  | R22 | Non-TXV |  | 12.59% | 0.87414 | 24.19% | [5 empty] | Non-TXV | 12.59%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 17:54 | 2013-06-18 17:54 | NORDYNE - UKN | 155 | 0 | Yes | Yes | 22.4 | 20.9 | 1.5 | D8510FB531FF4D64AC08D753FFAB95AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2040 |  | 2013-06-26 | 2013-06-26 10:16 | 2013-06-26 10:36 | BDP - 585H10300-0 | 68 | 12.8 | Yes | Yes | 21.3 | 20.4 | 0.9 | EB7133BCBB97473C9669430A4B0D269C |  | R22 | Non-TXV |  | 18.82% | 0.81176 | 36.17% | [5 empty] | Non-TXV | 18.82%
Sonoma | CA | 95476-7008 |  | 2013-06-13 | 2013-06-13 12:57 | 2013-06-13 12:57 | GE - UKN | 85 | 0 | Yes | Yes | 18.7 | 20.9 | -2.2 | 026BED2BEA7E40E08ADA18D5D17D2824 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2299 |  | 2013-08-06 | 2013-08-06 10:22 | 2013-08-06 10:44 | AMERICAN STANDARD - NAC024AKC3 | 71 | -4.2 | Yes | Yes | 20 | 21 | -1 | 2197EA214C6049B9B2B159BB530744BB |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Bakersfield | CA | 93309-6413 |  | 2013-09-24 | 2013-09-24 23:41 | 2013-09-25 12:02 | BDP - 588ANW048080AEAG | 105 | 10.3 | Yes | Yes | 22.4 | 21.5 | 0.9 | F7FE9B85EE80491B827E7EAF1D758971 |  | R22 | Non-TXV |  | 9.81% | 0.9019 | 18.85% | [5 empty] | Non-TXV | 9.81%
Bakersfield | CA | 93308-2962 |  | 2013-08-29 | 2013-08-29 14:56 | 2013-08-29 14:56 | TRANE - 4YCC3024B1064AA | 93 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 2AEFF8B5CBD04CE5B037FF8EC0E66C03 |  | R410A | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3904 |  | 2013-08-06 | 2013-08-06 14:02 | 2013-08-06 14:44 | OTHER - NAC024AKC3 | 71 | 5.6 | Yes | Yes | 18.7 | 18.3 | 0.4 | A5CA9A1B64C74CD882DC44E8B114F974 |  | R22 | Non-TXV |  | 7.887% | 0.92113 | 15.16% | [5 empty] | Non-TXV | 7.887%
W Sacramento | CA | 95691-6219 |  | 2013-06-12 | 2013-06-12 12:18 | 2013-06-12 14:40 | CARRIER - 38CKC048370 | 100 | 3 | Yes | Yes | 18.6 | 17.6 | 1 | 421EF3AD28354176886DECF4BA472E75 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Sanger | CA | 93657-3905 |  | 2013-08-05 | 2013-08-05 11:23 | 2013-08-05 11:56 | - GCGD24S21S2A | 61 | 2.4 | Yes | Yes | 20.6 | 19.5 | 1.1 | F639D0EE332142D3AD7107A298F56DCD |  | R22 | TXV |  | 3.934% | 0.96066 | 7.561% | [5 empty] | TXV | 3.934%
Sanger | CA | 93657-2583 |  | 2013-09-17 | 2013-09-17 14:55 | 2013-09-17 15:14 | LENNOX - 10GC030753PA | 51 | 3.2 | Yes | Yes | 24.8 | 20.4 | 4.4 | CBC47474ED5F4EE69E339C123BBD7997 |  | R22 | Non-TXV |  | 6.275% | 0.93725 | 12.06% | [5 empty] | Non-TXV | 6.275%
Sanger | CA | 93657-3905 |  | 2013-08-06 | 2013-08-06 11:26 | 2013-08-06 11:42 | GUARDIAN - TCGD24S21S1A | 64 | 3.8 | Yes | Yes | 19.7 | 19.5 | 0.2 | 15E1327E6B3441E79FBA32F2AC0ECE11 |  | R22 | TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | TXV | 5.938%
Fresno | CA | 93722-6874 |  | 2013-06-18 | 2013-06-18 09:11 | 2013-06-18 09:11 | - 485X-030040311 | 78 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F6FB68BDF4CA420A83ACA7CB8BEB538D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-3904 |  | 2013-10-16 | 2013-10-16 11:42 | 2013-10-16 14:00 | TRANE - RAUC302 A | 101 | 3.1 | Yes | Yes | 18.2 | 20.4 | -2.2 | B3F69D7B69DF40DA8EBA2BC3824C2A24 |  | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Fresno | CA | 93722-3321 |  | 2013-06-13 | 2013-06-13 13:52 | 2013-06-13 13:52 | CARRIER - UNK | 80 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | AA1964F4C53744168A601A3BDDA5FA3C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1392 |  | 2013-06-20 | 2013-06-20 13:28 | 2013-06-20 14:16 | PAYNE - PY2PNB036060AAAA | 83 | 2.7 | Yes | Yes | 26.5 | 22 | 4.5 | 37241ECA247147B3AA0D739781FB74CA |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Fresno | CA | 93722-2761 |  | 2013-06-25 | 2013-06-25 10:58 | 2013-06-25 11:38 | CARRIER - 48SX0360331 | 86 | 4 | Yes | Yes | 22 | 19.9 | 2.1 | F5B090919AD243B7A6EA1605BB5C2C61 |  | R22 | Non-TXV |  | 4.651% | 0.95349 | 8.939% | [5 empty] | Non-TXV | 4.651%
Bakersfield | CA | 93308-9505 |  | 2013-08-29 | 2013-08-29 19:11 | 2013-08-29 19:11 | ICP - PGC024060A | 58 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | E2C9FDA2C8014110951A35BA00A3BF2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1643 |  | 2013-09-16 | 2013-09-16 17:23 | 2013-09-16 17:23 | YORK - UKN | 90 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | 1B94C3BDBC0140D199786BF5348F4955 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2816 |  | 2013-06-17 | 2013-06-17 08:44 | 2013-06-17 19:17 | CARRIER - UNK | 85 | 11.4 | Yes | Yes | 19.2 | 19.7 | -0.4 | E9678013812541878AE5E0E11EBB9826 |  | R22 | Non-TXV |  | 13.41% | 0.86588 | 25.77% | [5 empty] | Non-TXV | 13.41%
Fresno | CA | 93722-1150 |  | 2013-06-13 | 2013-06-13 10:01 | 2013-06-13 10:28 | YORK - H20B036506A | 73 | 4.8 | Yes | Yes | 20.5 | 20.2 | 0.3 | 11814DE938BC4C42A37298D5CC7E3AA8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.575% | 0.93425 | 12.64% | [5 empty] | Non-TXV | 6.575%
Kerman | CA | 93630-1965 |  | 2013-10-01 | 2013-10-01 10:10 | 2013-10-01 10:51 | CARRIER - 48GS03606301 | 56 | 3.7 | Yes | Yes | 20.5 | 21 | -0.5 | 1413CC71264E4F93BED9EFDC666515C1 |  | R22 | Non-TXV |  | 6.607% | 0.93393 | 12.7% | [5 empty] | Non-TXV | 6.607%
Bakersfield | CA | 93308-2971 |  | 2013-08-29 | 2013-08-29 16:17 | 2013-08-29 16:17 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | 4C9A9CFCC81A4B84A6062EBBCA856A02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2971 |  | 2013-08-29 | 2013-08-29 15:25 | 2013-08-29 15:25 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.7 | 21.3 | 0.5 | 3EB6F38BB0E24C148C597A52EE73EE88 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6099 |  | 2013-06-24 | 2013-06-24 09:31 | 2013-06-24 09:31 | COLEMAN - 9548C901 | 68 | 0 | Yes | Yes | 18.1 | 19 | -0.9 | 122C23ECA0CB42C8AC61EB8620F5EE57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6816 |  | 2013-07-03 | 2013-07-03 09:16 | 2013-07-03 09:41 | GOODMAN - GPG1342070M41CA | 81 | 3 | Yes | Yes | 22.5 | 18.8 | 3.7 | CAE97A725C094A449D31D5A23C55EF70 |  | R410A | TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | TXV | 3.704%
Fresno | CA | 93722-4227 |  | 2013-06-14 | 2013-06-14 12:09 | 2013-06-14 12:37 | TRANE - YCP042F1MOAB | 128 | 21.2 | Yes | Yes | 26.3 | 20.7 | 5.7 | A721FBEF2547444EAFA8F11E5AEEAE84 |  | R22 | Non-TXV |  | 16.56% | 0.83437 | 31.83% | [5 empty] | Non-TXV | 16.56%
Bakersfield | CA | 93311-9005 |  | 2013-06-29 | 2013-06-29 09:22 | 2013-06-29 09:22 | BRYANT - 5636CN030-C | 100 | 0 | Yes | Yes | 18.3 | 19.2 | -0.9 | 85F4C951F5DC45199017978FCF7FFFE8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9005 |  | 2013-06-29 | 2013-06-29 15:10 | 2013-06-29 15:10 | BRYANT - 5636CN036-F | 108 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | C2F48FDEF62349718E11681A6412331C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1866 |  | 2013-06-17 | 2013-06-17 09:36 | 2013-06-17 10:08 | LENNOX - HS25411 | 129 | 8.2 | Yes | Yes | 23.2 | 20.9 | 2.3 | C77794019B374698BBAF7EBCDC27B6F3 |  | R22 | Non-TXV |  | 6.357% | 0.93643 | 12.22% | [5 empty] | Non-TXV | 6.357%
Fresno | CA | 93702-5617 |  | 2013-06-24 | 2013-06-24 16:38 | 2013-06-24 17:00 | LENNOX - 13ACD036230 | 111 | 5.5 | Yes | Yes | 21.1 | 19.3 | 1.8 | CF2DECEE31BF4407A8AE63028F338C64 |  | R22 | TXV |  | 4.955% | 0.95045 | 9.522% | [5 empty] | TXV | 4.955%
San Jose | CA | 95121-2910 |  | 2013-07-18 | 2013-07-18 13:43 | 2013-07-18 15:20 | TRANE - BWD724A100B0 | 98 | 8.2 | Yes | Yes | 22.4 | 17.7 | 4.8 | 357FE84B9F8048498477FD416195B2B6 |  | R22 | Non-TXV |  | 8.367% | 0.91633 | 16.08% | [5 empty] | Non-TXV | 8.367%
Vacaville | CA | 95687-5551 |  | 2013-06-07 | 2013-06-07 11:49 | 2013-06-07 13:47 | CARRIER - 593ANX060000AAAA | 240 | 7.9 | Yes | Yes | 17.2 | 18.5 | -1.3 | CEB8448AA3434B22882BEB3E3EC61081 |  | R22 | Non-TXV |  | 3.292% | 0.96708 | 6.326% | [5 empty] | Non-TXV | 3.292%
Wasco | CA | 93280-1357 |  | 2013-07-20 | 2013-07-20 17:03 | 2013-07-20 17:44 | GOODMAN - GPG1330045M41CA | 85 | 3.3 | Yes | Yes | 25.2 | 20.8 | 4.4 | A7B0E82C2BF844C3AF8F69D235911D4D |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Bakersfield | CA | 93304-1138 |  | 2013-10-16 | 2013-10-16 14:25 | 2013-10-16 14:52 | ICP - PGME42G080E | 179 | 14.5 | Yes | Yes | 22.1 | 20.4 | 1.7 | 21D3440FFAB5465196E06355ADEB6459 |  | R22 | Non-TXV |  | 8.101% | 0.91899 | 15.57% | [5 empty] | Non-TXV | 8.101%
Vacaville | CA | 95688-2613 |  | 2013-06-11 | 2013-06-11 12:20 | 2013-06-11 12:20 | HEIL - PGC024K060D | 58 | 0 | Yes | Yes | 14.7 | 17.4 | -2.7 | 7FF3FC6D880E4A9AA8ECEF94E946DCA4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dublin | CA | 94568-2146 |  | 2013-09-12 | 2013-09-12 11:05 | 2013-09-12 11:09 | LENNOX - XC13-042-230-02 | 138 | -9.7 | Yes | Yes | 18.7 | 15.7 | 3 | 61023B1E3315448AA4D6056F0CEB00F8 |  | R410A | Non-TXV |  | -7.029% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.029%
Fresno | CA | 93722-4900 |  | 2013-07-26 | 2013-07-26 09:22 | 2013-07-26 09:41 | COLEMAN - BRCQ0421BD | 66 | 8 | Yes | Yes | 20.4 | 19.9 | 0.5 | 661BE3D81EBC49E698BB90BA4DB58E70 |  | R22 | Non-TXV |  | 12.12% | 0.87879 | 23.29% | [5 empty] | Non-TXV | 12.12%
Fresno | CA | 93702-1940 |  | 2013-06-18 | 2013-06-18 08:50 | 2013-06-18 08:50 | RHEEM - 13AJM36A01 | 96 | -4.2 | Yes | Yes | 30 | 20 | 10 | E8F5D511B178437AA950CDA112C02C10 | Remove refrigerant: 4.2 oz | R410A | TXV |  | -4.375% | 1.0437 | 1.225% |  |  |  |  | TXV |  |  | -4.375%
San Jose | CA | 95110-3121 |  | 2013-10-15 | 2013-10-15 10:37 | 2013-10-15 10:58 | CARRIER - 38HDR030 311 | 135 | -9.5 | Yes | Yes | 19.6 | 20.5 | -0.9 | A283FF52BFF84305BD4B4B9E58CD22A2 |  | R410A | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Bakersfield | CA | 93308-2967 |  | 2013-08-30 | 2013-08-30 16:12 | 2013-08-30 16:12 | LUXAIRE - UKN | 90 | 0 | Yes | Yes | 18.5 | 20.2 | -1.7 | D7478D8FD43847B4930449A5FDE356B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5832 |  | 2013-07-15 | 2013-07-15 10:02 | 2013-07-15 10:04 | CARRIER - 38CKC0600370 | 132 | -10.9 | Yes | Yes | 18.3 | 17.5 | 0.8 | C04DFCB9E0074C4BAC49DF52E16B5067 |  | R22 | Non-TXV |  | -8.258% | 1.0826 | 2.313% |  |  |  |  | Non-TXV |  |  | -8.258%
Willits | CA | 95490-9748 |  | 2013-08-20 | 2013-08-20 09:30 | 2013-08-20 10:18 | COLEMAN - ERCS0481BBA | 134 | -9.5 | Yes | Yes | 25.8 | 21.3 | 4.6 | 533DC39A82C74B02ADCB35EB0CD1CC7B |  | R22 | Non-TXV |  | -7.09% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.09%
Fresno | CA | 93702-4733 |  | 2013-06-24 | 2013-06-24 12:02 | 2013-06-24 13:41 | CARRIER - 48NMX042 | 80 | -5.6 | Yes | Yes | 19.3 | 17.6 | 1.7 | 1EE61F6EC39B4B15AF8DDA376CEFCD1D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Bakersfield | CA | 93307-4382 |  | 2013-06-19 | 2013-06-19 16:44 | 2013-06-19 16:44 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 23.4 | 20.4 | 3 | F00571676C8C4A3E9254072745A873D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4724 |  | 2013-06-19 | 2013-06-19 15:46 | 2013-06-19 15:46 | WESTINGHOUSE - UKN | 90 | 0 | Yes | Yes | 20.3 | 21 | -0.7 | 21A21EAC9C3E4933AF31EE6B20057D22 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2832 |  | 2013-06-12 | 2013-06-12 17:11 | 2013-06-12 17:11 | ICP - WPG32440402KC1 | 72 | 0 | Yes | Yes | 24.8 | 21.7 | 3.1 | 659B52C37BC145348B303F5984090D61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5777 |  | 2013-08-20 | 2013-08-20 19:27 | 2013-08-20 19:27 | ICP - PGD442090K001C1 | 136 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | 8E277FDFB2CE4319B621D9623EE0AAC3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3017 |  | 2013-07-22 | 2013-07-22 09:25 | 2013-07-22 09:25 | YORK - H2RA035806E | 63 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 0A15C229D27D4CAF935C522A09AE76FE | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2325 |  | 2013-06-19 | 2013-06-19 11:59 | 2013-06-19 12:32 | OTHER - CA7536VKA1 | 85 | 19.7 | Yes | Yes | 19.1 | 20.3 | -1.2 | 3FA7A9984F8C49AD83756E51701B52CA |  | R22 | Non-TXV |  | 23.18% | 0.76824 | 44.54% | [5 empty] | Non-TXV | 23.18%
Vacaville | CA | 95687-5019 |  | 2013-06-07 | 2013-06-07 09:48 | 2013-06-07 13:47 | TRANE - 4TTX3048A1000AA | 126 | 5 | Yes | Yes | 15.3 | 17.7 | -2.4 | ED1FA4279D654BFBAD65C288D6D11583 |  | R410A | Non-TXV |  | 3.968% | 0.96032 | 7.626% | [5 empty] | Non-TXV | 3.968%
Bakersfield | CA | 93307-4377 |  | 2013-06-17 | 2013-06-17 08:29 | 2013-06-17 08:29 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 19.8 | 22.4 | -2.6 | 0CFB07FE4BCB401DBD9AFBFB54FB3329 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 15:10 | 2013-06-18 15:10 | NORDYNE - JT5B030KA | 144 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 083AE5263E734599830224DD0ADB25C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9292 |  | 2013-06-24 | 2013-06-24 12:07 | 2013-06-24 12:41 | DAY & NIGHT - 585EJW036075ABAF | 82 | -6.8 | Yes | Yes | 24.2 | 19.8 | 4.4 | 275F1557FAC2493DAC38C9F33E1CC393 |  | R22 | Non-TXV |  | -8.293% | 1.0829 | 2.322% |  |  |  |  | Non-TXV |  |  | -8.293%
Fairfield | CA | 94533-3833 |  | 2013-06-07 | 2013-06-07 13:16 | 2013-06-07 13:16 | BRYANT - 588ANW030060ADAD | 54 | 0 | Yes | Yes | 15.9 | 16.5 | -0.6 | B912EE7CA23F4DC29BE89F5C4D77823E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2207 |  | 2013-06-06 | 2013-06-06 10:44 | 2013-06-06 10:44 | ICP - PGF042K080B | 87 | 0 | Yes | Yes | 21.9 | 19.7 | 2.2 | 39EB417E42B143DA884970027A9EC91A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1108 |  | 2013-08-19 | 2013-08-19 11:16 | 2013-08-19 11:16 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | CDEEC59DD25F40A7A1216FF2C422FBA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2712 |  | 2013-06-19 | 2013-06-19 13:07 | 2013-06-19 13:08 | TRANE - 2YCX3036A1075AA | 82 | 4.4 | Yes | Yes | 15.8 | 18.2 | -2.4 | F09FBACC09D74F21B268B8109068C162 |  | R22 | Non-TXV |  | 5.366% | 0.94634 | 10.31% | [5 empty] | Non-TXV | 5.366%
Novato | CA | 94947-2922 |  | 2013-06-20 | 2013-06-20 12:00 | 2013-06-20 12:19 | TRANE - TTN042C100A2 | 133 | -12.5 | Yes | Yes | 27.5 | 21.7 | 5.8 | 5CA4BE8F151B4471AF53B0916095EA39 |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 16:49 | 2013-06-18 16:49 | NORDYNE - JT5BD042 | 166 | 0 | Yes | Yes | 22 | 20.5 | 1.5 | 75951F3316604616A622D24202BF4C38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1974 |  | 2013-08-02 | 2013-08-02 15:04 | 2013-08-02 16:21 | CARRIER - 48GX036060301 | 83 | 2.5 | Yes | Yes | 27.2 | 22 | 5.2 | 62A320BEDAD243FF9ADBED20791AF7AC |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Bakersfield | CA | 93307-4383 |  | 2013-06-18 | 2013-06-18 13:23 | 2013-06-18 13:23 | NORDYNE - JT5B042K | 166 | 0 | Yes | Yes | 24.4 | 21 | 3.4 | 9926E23A1EEB4C288FAE334BA1DBEBFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4378 |  | 2013-06-17 | 2013-06-17 12:03 | 2013-06-17 12:03 | - JT5BD-030KA | 144 | 0 | Yes | Yes | 22.1 | 22 | 0.1 | 9156895688914FCFBE7A51F2D68AA2C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2133 |  | 2013-07-16 | 2013-07-16 18:52 | 2013-07-16 19:17 | ICP - PGAD42D1K5 | 180 | 29.3 | Yes | Yes | 21.8 | 21 | 0.8 | 81A22481B5054DC4A352A4B6F57568E5 |  | R22 | Non-TXV |  | 16.28% | 0.83722 | 31.28% | [5 empty] | Non-TXV | 16.28%
Fresno | CA | 93702-1760 |  | 2013-08-09 | 2013-08-09 13:15 | 2013-08-09 13:53 | GOODMAN - GPG13300701AC | 71 | 4.1 | Yes | Yes | 22.9 | 20.8 | 2.1 | 4E9589508EAC40EC92DCEDD16A7E3506 |  | R22 | Non-TXV |  | 5.775% | 0.94225 | 11.1% | [5 empty] | Non-TXV | 5.775%
W Sacramento | CA | 95691-5498 |  | 2013-06-14 | 2013-06-14 10:53 | 2013-06-14 11:33 | CARRIER - 38CKC048370 | 100 | 9.7 | Yes | Yes | 16.2 | 17.6 | -1.4 | 03ACB7EB9656410EBDA286D2B2F63467 |  | R22 | Non-TXV |  | 9.7% | 0.903 | 18.64% | [5 empty] | Non-TXV | 9.7%
Bakersfield | CA | 93307-4378 |  | 2013-06-17 | 2013-06-17 14:36 | 2013-06-17 14:36 | NORDYNE - JT5BD-042K | 248 | 0 | Yes | Yes | 20.8 | 20.7 | 0.1 | 0D9C710CB9D24142B22AAEFBCD17F432 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2181 |  | 2013-08-30 | 2013-08-30 15:29 | 2013-08-30 15:29 | BRYANT - 574ANW030040NA | 130 | 0 | Yes | Yes | 21.8 | 22.1 | -0.3 | 2E15A2CF979941DABED4CBAAFF370F95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2607 |  | 2013-09-24 | 2013-09-24 10:36 | 2013-09-24 15:41 | AMANA - RCC42A2B | 116 | -5.2 | Yes | Yes | 15.2 | 17.7 | -2.5 | 6DF1C0CADFF5444E9DC3B8EB80134B73 |  | R22 | Non-TXV |  | -4.483% | 1.0448 | 1.255% |  |  |  |  | Non-TXV |  |  | -4.483%
Bakersfield | CA | 93308-2984 |  | 2013-08-28 | 2013-08-28 13:50 | 2013-08-28 13:50 | OTHER - UKN | 60 | 0 | Yes | Yes | 21.9 | 21.4 | 0.5 | 14800CD92C194D7C814872C50D6E5164 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2423 |  | 2013-06-11 | 2013-06-11 14:31 | 2013-06-11 14:31 | - CK42-1C | 92 | 0 | Yes | Yes | 16.6 | 19.1 | -2.5 | 3517C2C269D1429BA962391786A2CC7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-8735 |  | 2013-07-03 | 2013-07-03 14:43 | 2013-07-03 15:19 | WEATHER KING - 134A1A36401 | 108 | 31.6 | Yes | Yes | 19.6 | 19.7 | 0 | 6BE975EAB6064AC5A5B4D8564003B57E |  | R22 | Non-TXV |  | 29.26% | 0.70741 | 56.23% | [5 empty] | Non-TXV | 29.26%
Sanger | CA | 93657-8735 |  | 2013-07-03 | 2013-07-03 16:09 | 2013-07-03 16:30 | WEATHER KING - 134A1A36401 | 108 | 6.4 | Yes | Yes | 19.9 | 19.4 | 0.5 | 9EB3F458FB7E446797B1D54AC6D29994 |  | R22 | Non-TXV |  | 5.926% | 0.94074 | 11.39% | [5 empty] | Non-TXV | 5.926%
Bakersfield | CA | 93304-1294 |  | 2013-09-21 | 2013-09-21 18:27 | 2013-09-21 18:27 | PAYNE - PY3GNA240NA | 72 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 154ABB4A394048CF80FA714528D307D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5216 |  | 2013-07-03 | 2013-07-03 10:43 | 2013-07-03 10:43 | RHEEM - RRPL-B030JK06X | 76 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | E0841CE2FFD54D99A403525077D2AF16 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1614 |  | 2013-06-07 | 2013-06-07 14:14 | 2013-06-07 14:14 | BRYANT - 30-567S | 55 | 0 | Yes | Yes | 16.3 | 17.2 | -0.9 | F444B43A70834E72B54812DD1EAFA5B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1340 |  | 2013-08-06 | 2013-08-06 11:42 | 2013-08-06 11:42 | AMERICAN STANDARD - 2A7A5036A1000AA | 140 | 0 | Yes | Yes | 17.2 | 19.4 | -2.2 | 1F4D23CFB33E4D21B0C4F4E198040286 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0419 |  | 2013-06-25 | 2013-06-25 14:52 | 2013-06-25 15:34 | LENNOX - 13ACD04823003 | 152 | 5.2 | Yes | Yes | 18.4 | 18.6 | -0.2 | B7772827B90F443C826EFAB8BFC312E2 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Bakersfield | CA | 93308-9513 |  | 2013-09-19 | 2013-09-19 13:23 | 2013-09-19 13:23 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 22.2 | 21.4 | 0.8 | A2565B9D7B88467A98186B0A3305486A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ukiah | CA | 95482-3606 |  | 2013-08-24 | 2013-08-24 12:25 | 2013-08-24 13:06 | AMERICAN STANDARD - 4YCC3036A1096AA | 124 | 6.3 | Yes | Yes | 21 | 20.1 | 0.9 | 12831555C1D14DA78C9B88E13ED28C78 |  | R410A | Non-TXV |  | 5.081% | 0.94919 | 9.764% | [5 empty] | Non-TXV | 5.081%
Bakersfield | CA | 93309-4039 |  | 2013-10-22 | 2013-10-22 15:32 | 2013-10-22 15:55 | RUUD - UKN | 60 | 4.3 | Yes | Yes | 20.7 | 21 | -0.3 | 5778F18629494D96BFE59C42586259FA |  | R22 | Non-TXV |  | 7.167% | 0.92833 | 13.77% | [5 empty] | Non-TXV | 7.167%
Fresno | CA | 93722-6160 |  | 2013-06-17 | 2013-06-17 13:29 | 2013-06-17 12:40 | PAYNE - 585EJ030050 | 58 | 0 | Yes | Yes | 32.2 | 22.1 | 10.1 | A1F43F5D9285411E949D6DCCC71D55E3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6421 |  | 2013-09-24 | 2013-09-24 11:16 | 2013-09-24 11:16 | GOODMAN - CE30-1EB | 150 | 0 | Yes | Yes | 18.3 | 20.2 | -1.9 | 77DD1B6A444F4601A3E3CB5ED344D70B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1521 |  | 2013-06-13 | 2013-06-13 11:23 | 2013-06-13 11:51 | TRANE - BTD736A100B0 | 88 | -3.2 | Yes | Yes | 16.5 | 19.3 | -2.8 | 547A282B427A41D4B1F908A1FC9768EB |  | R22 | Non-TXV |  | -3.636% | 1.0364 | 1.018% |  |  |  |  | Non-TXV |  |  | -3.636%
Bakersfield | CA | 93309-4038 |  | 2013-10-22 | 2013-10-22 14:38 | 2013-10-22 14:38 | DAY & NIGHT - UKN | 60 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | E2F8FFA7D2CA4EB2933A0504F0775E6E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5671 |  | 2013-06-14 | 2013-06-14 18:11 | 2013-06-14 18:11 | BDP - 561CJ030-C | 71 | 0 | Yes | Yes | 21.9 | 21.1 | 0.8 | 43229C0583654FF2ACB3F8C677294BA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2311 |  | 2013-06-10 | 2013-06-10 14:28 | 2013-06-10 15:55 | AMERICAN STANDARD - 2A7A1036A1000AA | 73 | 2.3 | Yes | Yes | 19.6 | 19.1 | 0.5 | 6A790DF2F8E24952A959C18F00162B4F |  | R22 | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Bakersfield | CA | 93309-3120 |  | 2013-08-01 | 2013-08-01 10:02 | 2013-08-01 10:02 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 21.6 | 22.1 | -0.5 | 369BCF8053B247FBB51F08AF30149B71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 13:46 | 2013-06-18 13:46 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | AA666250620848F496CBB490ED8AEF0E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4377 |  | 2013-06-17 | 2013-06-17 15:09 | 2013-06-17 15:09 | - JT5BD-042K | 248 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | 122D4625FC8B4D45A86CF0927E956961 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4038 |  | 2013-10-22 | 2013-10-22 15:18 | 2013-10-22 15:18 | YORK - DC42-F024N045C | 58 | 0 | Yes | Yes | 21.3 | 21 | 0.3 | 18C5F10900744854ADA2853EC4DDE377 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3746 |  | 2013-06-07 | 2013-06-07 11:38 | 2013-06-07 11:38 | ICP - PGAD36D1K7 | 100 | 0 | Yes | Yes | 20.9 | 18 | 2.9 | 0E8EEBC5778E409EA621D652E9652980 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-2618 |  | 2013-07-22 | 2013-07-22 11:58 | 2013-07-22 15:36 | TRANE - 2TTB0030A1000AA | 85 | 7.5 | Yes | Yes | 21.7 | 17.7 | 4 | FF7A805DBF074762BD25BDEA9E99E7BD |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Fresno | CA | 93725-1525 |  | 2013-06-06 | 2013-06-06 11:10 | 2013-06-06 11:55 | YORK - DBYP F036N070A | 108 | 4 | Yes | Yes | 22.9 | 20.5 | 2.4 | 3108847211EE4B6697443C64A9EE96B0 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Bakersfield | CA | 93307-4378 |  | 2013-06-17 | 2013-06-17 13:13 | 2013-06-17 13:13 | - JT5BD-030KA | 144 | 0 | Yes | Yes | 22.9 | 20.4 | 2.5 | 6E6DB43AD1E44F88BFF1D906A036EB9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4300 |  | 2013-06-28 | 2013-06-28 10:54 | 2013-06-28 11:28 | BRYANT - 561CJX036000EAA | 67 | -6.3 | Yes | Yes | 22.5 | 19.2 | 3.3 | B35A7D7FF6A940F899672CAC06D91AEB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Gilroy | CA | 95020-2617 |  | 2013-10-23 | 2013-10-23 16:44 | 2013-10-24 14:56 | TRANE - TTB024 | 56 | 5.9 | Yes | Yes | 22.2 | 22 | 0.2 | 9DBCA058F7B1445BB9B23C39F46F2FA7 |  | R22 | Non-TXV |  | 10.54% | 0.89464 | 20.25% | [5 empty] | Non-TXV | 10.54%
Bakersfield | CA | 93308-5674 |  | 2013-06-14 | 2013-06-14 19:12 | 2013-06-14 19:28 | BDP - 561CJ030-C | 71 | 6.3 | Yes | Yes | 19.3 | 19.7 | -0.4 | 56A5C4E3E6BD424A856F3CDD3B7B3BCC |  | R22 | Non-TXV |  | 8.873% | 0.91127 | 17.05% | [5 empty] | Non-TXV | 8.873%
Bakersfield | CA | 93312-5536 |  | 2013-06-26 | 2013-06-26 14:44 | 2013-06-26 14:44 | GOODMAN - CK42-1C | 92 | 0 | Yes | Yes | 19.4 | 20.2 | -0.8 | E1369324DC6F4ECE81CA33762894850F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4385 |  | 2013-06-19 | 2013-06-19 17:10 | 2013-06-19 17:10 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 17.9 | 19.4 | -1.5 | 102FE05ACA034A89A8DB09D6B35C4D52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4379 |  | 2013-06-17 | 2013-06-17 15:43 | 2013-06-17 15:43 | NORDYNE - UKN | 155 | 0 | Yes | Yes | 20.8 | 20.2 | 0.6 | C8407F6E52E34EBABAC15C961F9CAD70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4385 |  | 2013-06-18 | 2013-06-18 14:30 | 2013-06-18 14:30 | NORDYNE - JT5BD-030KA | 144 | 0 | Yes | Yes | 22.6 | 21 | 1.6 | 1A5F2C4372CE4FF08D5705B37291634A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6219 |  | 2013-06-11 | 2013-06-11 09:06 | 2013-06-11 09:06 | OTHER - TCGD36S21SA | 63 | 0 | Yes | Yes | 19.1 | 21.5 | -2.4 | FF9BB22D62D34EBA94C13FA261E5A6F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-2618 |  | 2013-08-08 | 2013-08-08 10:05 | 2013-08-08 10:05 | TRANE - 2TTB0030A1000AA | 64 | 0 | Yes | Yes | 21.8 | 20.7 | 1.1 | ECBDAAA73BD34C78BA97FBE5DB95CE92 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2531 |  | 2013-06-28 | 2013-06-28 09:34 | 2013-06-28 09:57 | BDP - 588ANW048080AAAG | 101 | 8.1 | Yes | Yes | 21.2 | 18.9 | 2.3 | A9C0E0B7F5174E6A9B22E703815BAA0C |  | R22 | Non-TXV |  | 8.02% | 0.9198 | 15.41% | [5 empty] | Non-TXV | 8.02%
Vacaville | CA | 95687-7879 |  | 2013-06-17 | 2013-06-17 09:05 | 2013-06-17 09:25 | YORK - H1DE042S06B | 99 | 3 | Yes | Yes | 17.8 | 16.5 | 1.3 | E484099EE7A94639B6CAC118D0C15CD4 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Bakersfield | CA | 93304-1292 |  | 2013-09-21 | 2013-09-21 17:49 | 2013-09-21 17:49 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 2F4B2DF2321D4CB48D6CBB216CDA2920 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3330 |  | 2013-09-25 | 2013-09-25 15:37 | 2013-09-25 15:37 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | EDD6EDC443EC4DCCADD7028DDA1512D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4038 |  | 2013-10-22 | 2013-10-22 14:59 | 2013-10-22 14:59 | ICP - GPCM024K060D | 54 | 0 | Yes | Yes | 21.2 | 21.3 | 0 | D8CDA74B54E64FB3B7093613DC4A0262 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1924 |  | 2013-08-23 | 2013-08-23 13:18 | 2013-08-23 15:26 | ICP - CA5536VKD2 | 82 | 4.6 | Yes | Yes | 14.8 | 17.1 | -2.3 | 54570EA9908C4E54A988E808D080A76A |  | R22 | Non-TXV |  | 5.61% | 0.9439 | 10.78% | [5 empty] | Non-TXV | 5.61%
Bakersfield | CA | 93308-1833 |  | 2013-07-11 | 2013-07-11 08:47 | 2013-07-11 09:27 | ICP - PGAA4701K1 | 129 | 20.8 | Yes | Yes | 21.9 | 20.2 | 1.7 | EC552316331243ECB9AD40E130FD7737 |  | R22 | Non-TXV |  | 16.12% | 0.83876 | 30.99% | [5 empty] | Non-TXV | 16.12%
Bakersfield | CA | 93307-4379 |  | 2013-06-17 | 2013-06-17 16:27 | 2013-06-17 16:27 | NORDYNE - UKN | 155 | 0 | Yes | Yes | 20.7 | 18.5 | 2.2 | AD02E6CA89634887A3F3EB3917BC9E3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7610 |  | 2013-09-06 | 2013-09-06 01:45 | 2013-09-06 01:45 | YORK - D1NH030N05606C | 73 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 279A926BC85A4AC4AB93AEE32DEEF9FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4295 |  | 2013-06-17 | 2013-06-17 12:42 | 2013-06-17 12:42 | AMANA - RCE30C2C | 130 | 0 | Yes | Yes | 16.2 | 18.2 | -2 | 1CD6477094A94B51A9C8F831A32F0779 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2967 |  | 2013-08-30 | 2013-08-30 16:31 | 2013-08-30 16:47 | LUXAIRE - UKN | 90 | 14.6 | Yes | Yes | 20.1 | 20.6 | -0.5 | 1812D91094F04942BE40A0B574811EC5 |  | R22 | Non-TXV |  | 16.22% | 0.83778 | 31.18% | [5 empty] | Non-TXV | 16.22%
Bakersfield | CA | 93313-5461 |  | 2013-06-21 | 2013-06-21 19:54 | 2013-06-21 19:54 | ICP - CAC060AKA1 | 131 | 0 | Yes | Yes | 20.1 | 20.9 | -0.8 | C882CBB25592441EBBBDEC57D5B9EE10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4713 |  | 2013-09-23 | 2013-09-23 11:45 | 2013-09-23 12:12 | BRYANT - 561CJ024D | 58 | -5.5 | Yes | Yes | 19.4 | 17.9 | 1.5 | AEEC5DD50D9E44BDAEC458E0C38B399F |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Suisun City | CA | 94534-1308 |  | 2013-06-06 | 2013-06-06 12:16 | 2013-06-06 15:01 | GOODMAN - CK30-1T | 76 | 2.9 | Yes | Yes | 18.1 | 18.8 | -0.7 | BADD6C821DDA43298E3A27482A26044E |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Bakersfield | CA | 93309-2853 |  | 2013-06-28 | 2013-06-28 10:54 | 2013-06-28 10:54 | CARRIER - 24ACA430A0030010 | 113 | 0 | Yes | Yes | 19 | 19.9 | -0.9 | 3DE1531A08AE40C988DBA6E5AC933B33 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4381 |  | 2013-06-17 | 2013-06-17 13:47 | 2013-06-17 13:47 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | 3D15DC5813754CA98066C8FEF7CC52DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4377 |  | 2013-06-17 | 2013-06-17 09:05 | 2013-06-17 09:05 | NORDYNE - JT5BD036 | 155 | 0 | Yes | Yes | 21.8 | 20.2 | 1.7 | 4D9D76B990DE4C27B1322693612F69F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1239 |  | 2013-10-10 | 2013-10-10 13:25 | 2013-10-10 13:58 | CARRIER - 38HDC048 331 | 67 | -4.7 | Yes | Yes | 21.6 | 21.4 | 0.2 | 8582C3F8AB63414DBD9D29090DB1491F |  | R22 | Non-TXV |  | -7.015% | 1.0701 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.015%
Bakersfield | CA | 93313-2201 |  | 2013-06-24 | 2013-06-24 16:58 | 2013-06-24 17:16 | YORK - D1NP048N06506A | 132 | 27.3 | Yes | Yes | 18.8 | 20.2 | -1.4 | 6978A3990F11439F8BE5B1B2E9C1D78D |  | R22 | Non-TXV |  | 20.68% | 0.79318 | 39.75% | [5 empty] | Non-TXV | 20.68%
San Jose | CA | 95128-1442 |  | 2013-07-11 | 2013-07-11 09:43 | 2013-07-11 09:43 | PAYNE - PA13NR048-E | 231 | 0 | Yes | Yes | 20.9 | 18.8 | 2.1 | D2C804D3D9A54363966EA3785718D6A6 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4379 |  | 2013-06-17 | 2013-06-17 16:05 | 2013-06-17 16:05 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 21.6 | 20.1 | 1.5 | D4032675570C4BBDB50F4B1375059BAB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1837 |  | 2013-06-17 | 2013-06-17 13:03 | 2013-06-17 13:21 | LENNOX - HS18-411-6P | 49 | -3.6 | Yes | Yes | 16.8 | 16.5 | 0.3 | F9FCDBB6983447D08F4AE462EC2BAED4 |  | R22 | Non-TXV |  | -7.347% | 1.0735 | 2.057% |  |  |  |  | Non-TXV |  |  | -7.347%
Bakersfield | CA | 93307-4378 |  | 2013-06-17 | 2013-06-17 12:46 | 2013-06-17 12:46 | NORDYNE - JT5BD-030KA | 144 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | B1FB3991786A459CAB140AE04BCEDC4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-7928 |  | 2013-07-12 | 2013-07-12 12:12 | 2013-07-12 12:50 | ARMSTRONG - SCU10B30A-3 | 85 | 4.1 | Yes | Yes | 26.3 | 21.9 | 4.4 | E3DAB60920F2406CB57ABA7878AC7A5F |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fairfield | CA | 94533-2231 |  | 2013-08-09 | 2013-08-09 12:04 | 2013-08-09 12:05 | JANITROL - CM1EB30- | 67 | -5.5 | Yes | Yes | 17.4 | 17.6 | -0.2 | DC4D1F8889E44BE7A9C77208956393AA |  | R22 | Non-TXV |  | -8.209% | 1.0821 | 2.299% |  |  |  |  | Non-TXV |  |  | -8.209%
San Jose | CA | 95121-1402 |  | 2013-10-10 | 2013-10-10 10:11 | 2013-10-10 10:27 | CARRIER - UNK | 72 | 3.4 | Yes | Yes | 21.5 | 22 | -0.5 | 041B8B56A1D4412B8DB759141D4F9975 |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
San Jose | CA | 95121-1402 |  | 2013-10-10 | 2013-10-10 11:10 | 2013-10-10 11:26 | FRIGIDAIRE - SB3A 036KA | 84 | 2.9 | Yes | Yes | 21.8 | 21 | 0.8 | A6C30D5E73A3495B8380752AC05CD921 |  | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Bakersfield | CA | 93304-4142 |  | 2013-06-13 | 2013-06-13 16:08 | 2013-06-13 16:08 | ICP - CA5560VKC1 | 118 | 0 | Yes | Yes | 24.3 | 18.5 | 5.8 | E54C140D629A44D5B6D136A4B6709CC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4708 |  | 2013-09-23 | 2013-09-23 11:05 | 2013-09-23 11:33 | BRYANT - 561CJ024C | 70 | 2.8 | Yes | Yes | 19.9 | 19.1 | 0.8 | 14A8C86FB37A48E68743518BB948E2B6 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Cottonwood | CA | 96022-9304 |  | 2013-07-13 | 2013-07-13 09:21 | 2013-07-13 10:19 | AMANA - PGD42C0902G | 113 | 17.2 | Yes | Yes | 25.2 | 19.3 | 5.9 | 4513C0D9407446B3921E5B5BF981E800 |  | R22 | Non-TXV |  | 15.22% | 0.84779 | 29.25% | [5 empty] | Non-TXV | 15.22%
Fairfield | CA | 94533-2720 |  | 2013-08-02 | 2013-08-02 14:29 | 2013-08-02 14:29 | GE - | 85 | 0 | Yes | Yes | 14.5 | 16.5 | -2 | 08FAC4CB64B84A84988CA1F6B75E1891 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-9316 |  | 2013-07-01 | 2013-07-01 11:36 | 2013-07-01 11:37 | CARRIER - 38CK030300 | 69 | -4.9 | Yes | Yes | 17.9 | 18.2 | -0.3 | 4C479F61724D4871BB409241D79D84A0 |  | R22 | Non-TXV |  | -7.101% | 1.071 | 1.989% |  |  |  |  | Non-TXV |  |  | -7.101%
Bakersfield | CA | 93307-4385 |  | 2013-06-18 | 2013-06-18 15:32 | 2013-06-18 15:32 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 21.4 | 19.3 | 2.1 | 52FFDE0D8D0942D5892EDA6DC34050D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willits | CA | 95490-9583 |  | 2013-08-20 | 2013-08-20 17:11 | 2013-08-20 17:21 | COLEMAN - ILLEGIBLE | 51 | 9.1 | Yes | Yes | 26.7 | 22.6 | 4.1 | 62031E93B78B4CE2A3496621A26E1EC1 |  | R22 | Non-TXV |  | 17.84% | 0.82157 | 34.29% | [5 empty] | Non-TXV | 17.84%
Bakersfield | CA | 93307-4381 |  | 2013-06-17 | 2013-06-17 15:14 | 2013-06-17 15:14 | NORDYNE - JT5BD-036K | 155 | 0 | Yes | Yes | 23.8 | 21 | 2.8 | 15C0BF136849481487F2939F6E3271E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-3218 |  | 2013-07-11 | 2013-07-11 14:30 | 2013-07-11 14:30 | GOODMAN - CK36-1A | 85 | 0 | Yes | Yes | 24.3 | 19.4 | 5 | F57102FC372844D8BA34A849A17F69D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-3907 |  | 2013-09-27 | 2013-09-27 15:31 | 2013-09-27 15:46 | BRYANT - 561042 | 84 | 4.5 | Yes | Yes | 21.6 | 21.7 | -0.1 | 73692D9A984F47199B4D0DDA35080772 |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Milpitas | CA | 95035-3907 |  | 2013-09-27 | 2013-09-27 15:47 | 2013-09-27 19:23 | BRYANT - 561CJ024 | 84 | 2.6 | Yes | Yes | 21.7 | 21.8 | 0 | 770791C8A2C24D81994EBE56575D872A |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Suisun City | CA | 94585-4148 |  | 2013-06-14 | 2013-06-14 09:42 | 2013-06-14 10:05 | - DRCS0601BE | 136 | 3.5 | Yes | Yes | 13.6 | 16.4 | -2.8 | 05BEAEBD4EED477C8628DA40496BF5E3 |  | R22 | Non-TXV |  | 2.574% | 0.97426 | 4.946% | [5 empty] | Non-TXV | 2.574%
Fairfield | CA | 94533-5166 |  | 2013-10-02 | 2013-10-02 09:49 | 2013-10-02 14:25 | CARRIER - 38BRC036350 | 108 | 5.5 | Yes | Yes | 12.9 | 14.1 | -1.2 | 168410CFE34C4B08B18716094C79D8BD |  | R22 | Non-TXV |  | 5.093% | 0.94907 | 9.787% | [5 empty] | Non-TXV | 5.093%
Taft | CA | 93268-1503 |  | 2013-09-23 | 2013-09-23 19:11 | 2013-09-23 19:14 | RHEEM - RRNL-B036JK06X | 93 | 3.6 | Yes | Yes | 24.7 | 21 | 3.7 | 036769919DF8487DB8722A692A2CD46B |  | R410A | TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | TXV | 3.871%
San Jose | CA | 95128-2370 |  | 2013-07-09 | 2013-07-09 09:24 | 2013-07-09 09:51 | LENNOX - HS25-311-1P | 129 | 7.1 | Yes | Yes | 24.2 | 19.7 | 4.5 | A8E86D322B354C27A1B3773E58E6EE05 |  | R22 | Non-TXV |  | 5.504% | 0.94496 | 10.58% | [5 empty] | Non-TXV | 5.504%
Lamont | CA | 93241-1135 |  | 2013-08-22 | 2013-08-22 15:12 | 2013-08-22 15:30 | YORK - D3NZ036N05606NXA | 136 | 5 | Yes | Yes | 24.1 | 20.5 | 3.6 | C848C4832EDB4CE2B4DEF42F1CAFAF0B |  | R410A | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Woodland | CA | 95776-4950 |  | 2013-06-18 | 2013-06-18 11:54 | 2013-06-18 12:00 | RUUD - UAKA-037JAZ | 79 | 3.2 | Yes | Yes | 16.5 | 18.2 | -1.7 | F780602AB98D48939D6E4B826C67BDD1 |  | R22 | Non-TXV |  | 4.051% | 0.95949 | 7.784% | [5 empty] | Non-TXV | 4.051%
Bakersfield | CA | 93307-4385 |  | 2013-06-18 | 2013-06-18 16:22 | 2013-06-18 16:22 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 725C913AE4024375BF0BBCB553BF0676 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-1929 |  | 2013-06-13 | 2013-06-13 14:05 | 2013-06-13 14:34 | INTERTHERM - S30A-030KA | 68 | 2.8 | Yes | Yes | 18.5 | 19.9 | -1.4 | 9684B0EAAAC541F2803253AA620715AD |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93306-8408 |  | 2013-10-15 | 2013-10-15 13:44 | 2013-10-15 13:44 | RHEEM - 13AJA60A01 | 191 | 0 | Yes | Yes | 20.7 | 20.9 | -0.2 | EF1512A3C0BA4815A869D227B556E06A |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1815 |  | 2013-06-14 | 2013-06-14 10:23 | 2013-06-14 10:44 | GOODMAN - CE36-1GB | 79 | 2.4 | Yes | Yes | 18.3 | 19 | -0.7 | BA045C28171C492D82661A89181F78F9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Corcoran | CA | 93212-2411 |  | 2013-07-05 | 2013-07-05 10:32 | 2013-07-05 10:51 | OTHER - UNK | 72 | 7.7 | Yes | Yes | 23.6 | 20.9 | 2.7 | 60DFA1854A384983BC89BD53AEA79089 |  | R22 | Non-TXV |  | 10.69% | 0.89306 | 20.55% | [5 empty] | Non-TXV | 10.69%
Fairfield | CA | 94533-2015 |  | 2013-06-13 | 2013-06-13 12:18 | 2013-06-13 12:48 | - 591ANX03600AAAA | 83 | 2.9 | Yes | Yes | 19.6 | 18.7 | 0.9 | ABD421046BBF4CAB8787F4F52F7894B0 |  | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
Woodland | CA | 95776-4200 |  | 2013-06-18 | 2013-06-18 12:41 | 2013-06-18 12:45 | AMERICAN STANDARD - YCC036F1M0BK | 83 | -5.9 | Yes | Yes | 18.6 | 18.2 | 0.4 | 47A5676F315F42968AF435223A464F7B |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Bakersfield | CA | 93309-3216 |  | 2013-06-28 | 2013-06-28 18:53 | 2013-06-28 18:53 | ICP - GPCM042K00D | 91 | 0 | Yes | Yes | 19.9 | 20.8 | -0.9 | 01178A09B5CD471E94C8BC912229754E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1422 |  | 2013-07-22 | 2013-07-22 13:02 | 2013-07-22 13:26 | PAYNE - PA10JA060-G | 120 | 6.3 | Yes | Yes | 27.2 | 21.3 | 6 | 3F341030E85A471B8EB1FD1CAC4ADBC2 |  | R22 | Non-TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | Non-TXV | 5.25%
Bakersfield | CA | 93306-2737 |  | 2013-07-17 | 2013-07-17 08:09 | 2013-07-17 08:09 | DUCANE - SG12B36075 | 98 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 2C2D2C2A7A094642952771EEB96CEF71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4075 |  | 2013-10-01 | 2013-10-01 18:43 | 2013-10-01 18:43 | YORK - DCYZF036N070A | 64 | 0 | Yes | Yes | 21.7 | 20.9 | 0.8 | B389F001930C4F91A8B0FECDE774C504 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3114 |  | 2013-06-21 | 2013-06-21 09:42 | 2013-06-21 09:45 | ARMSTRONG - PGE12B36D075A-2A | 110 | 4.1 | Yes | Yes | 18.2 | 18.2 | 0 | 7F5F5EFFCA7F4A4AA603EC9C61E53A29 |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.163% | [5 empty] | Non-TXV | 3.727%
Bakersfield | CA | 93313-3425 |  | 2013-06-20 | 2013-06-20 18:20 | 2013-06-20 18:20 | AIRE-FLO - AFGP12B48100 | 126 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 7DF4B695F29141129F4F66A86A6A821A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4075 |  | 2013-10-01 | 2013-10-01 19:02 | 2013-10-01 19:02 | GOODMAN - GPG1324020M41AB | 80 | 0 | Yes | Yes | 22.2 | 21.2 | 1.1 | CC504EF44190473F8F9384A26EF714DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-6071 |  | 2013-07-09 | 2013-07-09 10:04 | 2013-07-09 10:27 | YORK - TCGD36S21S1HA | 65 | 0 | Yes | Yes | 25.8 | 19.1 | 6.7 | FECFBF1838A745ECA0ED360E068AFFA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4075 |  | 2013-10-01 | 2013-10-01 18:23 | 2013-10-01 18:23 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.1 | 20.4 | -0.3 | 4001609DD75F466FB4F0208D12CCE169 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-6815 |  | 2013-10-23 | 2013-10-23 16:02 | 2013-10-23 16:47 | BRYANT - 561CJ048-A | 104 | -7.3 | Yes | Yes | 23.2 | 18.8 | 4.4 | 65A427BE4CC649E3899D6CD95AB1D3E8 |  | R22 | Non-TXV |  | -7.019% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.019%
Bakersfield | CA | 93304-5895 |  | 2013-06-12 | 2013-06-12 09:52 | 2013-06-12 09:52 | GOODMAN - GPG1330045M41AD | 80 | 0 | Yes | Yes | 19.2 | 18.6 | 0.6 | E05D60D41A8B4455B92ACE8F2A984433 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-5618 |  | 2013-07-22 | 2013-07-22 10:14 | 2013-07-22 10:14 | OTHER - DXE36B | 85 | 0 | Yes | Yes | 19.2 | 18.2 | 1 | 88B56ED0048D40FA9EBD38B27B580D28 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1984 |  | 2013-07-09 | 2013-07-09 10:34 | 2013-07-09 11:08 | BRYANT - 561CJ042-E | 85 | 3.7 | Yes | Yes | 23.4 | 20.2 | 3.2 | 9E0AF31E7A8A4FC386CB6D1FCE613978 |  | R22 | TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | TXV | 4.353%
San Jose | CA | 95121-1984 |  | 2013-07-09 | 2013-07-09 11:10 | 2013-07-09 11:10 | BRYANT - 561CJ030-E | 89 | 0 | Yes | Yes | 18.9 | 18.8 | 0.1 | B3822EC05EAC4CD7B680547BF58072A8 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2777 |  | 2013-07-09 | 2013-07-09 11:20 | 2013-07-09 11:20 | TRANE - 4TT45042E1000AB | 132 | 0 | Yes | Yes | 20.8 | 19.3 | 1.5 | 9C12DB6EF8DE43BB856D862A0999BBE8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-0000 |  | 2013-06-19 | 2013-06-19 10:48 | 2013-06-19 10:56 | COLEMAN - DRCQ0301BEG | 70 | 9.4 | Yes | Yes | 16 | 17.6 | -1.6 | C769F5ED5BED4974B19EC065305A99B0 |  | R22 | Non-TXV |  | 13.43% | 0.86571 | 25.81% | [5 empty] | Non-TXV | 13.43%
Bakersfield | CA | 93307-4385 |  | 2013-06-19 | 2013-06-19 19:51 | 2013-06-19 19:51 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | 86CE12D264D0422DBF8E3418929EC8E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-9622 |  | 2013-07-18 | 2013-07-18 13:19 | 2013-07-18 13:35 | BDP - 655ANX04200ABAG | 54 | 4.2 | Yes | Yes | 18.8 | 20.2 | -1.4 | C7B0391276CD47CCAAA36ECD8F55CFB1 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Vacaville | CA | 95687-6763 |  | 2013-06-21 | 2013-06-21 09:26 | 2013-06-21 09:50 | DAY & NIGHT - 591ANX030000ABAA | 65 | -4.4 | Yes | Yes | 16.9 | 14.1 | 2.8 | 123F928C8D1942C88BD481E088069E5E |  | R22 | Non-TXV |  | -6.769% | 1.0677 | 1.896% |  |  |  |  | Non-TXV |  |  | -6.769%
Fairfield | CA | 94533-4160 |  | 2013-09-26 | 2013-09-26 14:37 | 2013-09-26 17:14 | CARRIER - 38BRC030320 | 121 | 5.7 | Yes | Yes | 22.9 | 16.9 | 6 | 0D2C91085670431E865E5000ABABBE65 |  | R22 | TXV |  | 4.711% | 0.95289 | 9.053% | [5 empty] | TXV | 4.711%
Bakersfield | CA | 93307-4382 |  | 2013-06-17 | 2013-06-17 09:39 | 2013-06-17 09:39 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 20.4 | 22.1 | -1.7 | C571D5DE1744486B8B14882C487437BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-1932 |  | 2013-07-12 | 2013-07-12 08:55 | 2013-07-12 09:31 | TEMPSTAR - TCA036AKA4 | 85 | 5.8 | Yes | Yes | 22.4 | 18.2 | 4.2 | 6AC6F38BA266479FBA7D1EADF8CE1AC8 |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
San Jose | CA | 95135-1301 |  | 2013-07-09 | 2013-07-09 12:26 | 2013-07-09 12:26 | GE - 21TA924H1H | 85 | 0 | Yes | Yes | 23.5 | 20.2 | 3.3 | DA18CAB2AF3E412E91FEA4DE07A23325 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4386 |  | 2013-06-19 | 2013-06-19 19:14 | 2013-06-19 19:14 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 22.7 | 20.7 | 2.1 | F2C684895A29419EBF472DE3BAE49B7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-3616 |  | 2013-10-14 | 2013-10-14 14:50 | 2013-10-14 16:00 | AMERICAN STANDARD - 7A0036A1000A0 | 106 | 4.1 | Yes | Yes | 18.1 | 21 | -2.9 | AF4E7202B5A747EF9346C98918B7BE71 |  | R22 | Non-TXV |  | 3.868% | 0.96132 | 7.433% | [5 empty] | Non-TXV | 3.868%
Bakersfield | CA | 93313-6049 |  | 2013-06-28 | 2013-06-28 17:28 | 2013-06-28 17:28 | RHEEM - RAMA-048JAZ | 172 | 0 | Yes | Yes | 20.9 | 20.7 | 0.2 | CD620984069E47A4A8FDBCE8102ED3E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2722 |  | 2013-07-31 | 2013-07-31 15:23 | 2013-07-31 21:15 | TEMPSTAR - PGAD30D1K4 | 78 | -4.1 | Yes | Yes | 24.7 | 22.3 | 2.4 | 5D6055BA93A04993BBB748D599F809A5 |  | R22 | TXV |  | -5.256% | 1.0526 | 1.472% |  |  |  |  | TXV |  |  | -5.256%
Madison | CA | 95653-0000 |  | 2013-09-09 | 2013-09-09 08:19 | 2013-09-09 09:00 | AMERICAN STANDARD - 7B0036B100AD | 90 | -6.4 | Yes | Yes | 25.5 | 21 | 4.5 | 7A39CC7F7E244CE18E2E24B07371078E |  | R22 | Non-TXV |  | -7.111% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.111%
Bakersfield | CA | 93309-1885 |  | 2013-10-15 | 2013-10-15 18:09 | 2013-10-15 18:09 | YORK - UKN | 60 | 0 | Yes | Yes | 22.1 | 21 | 1.1 | A3B02ED559944628B0AB2FA6C19ED08B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1885 |  | 2013-10-15 | 2013-10-15 19:48 | 2013-10-15 19:48 | PAYNE - PY3PNA024040NA | 121 | 0 | Yes | Yes | 19.9 | 21 | -1.1 | A98750C72EC24464B6937FB55F4FADA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1915 |  | 2013-07-23 | 2013-07-23 18:54 | 2013-07-23 19:00 | CARRIER - 48DL003 | 49 | 2.8 | Yes | Yes | 15.9 | 18.8 | -2.9 | B8041923958F4D60B00C48844BFBE925 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Shafter | CA | 93263-1915 |  | 2013-07-23 | 2013-07-23 19:02 | 2013-07-23 19:02 | CARRIER - 48DL003 | 49 | 0 | Yes | Yes | 19.5 | 20.2 | -0.7 | 4567EEE13FB84932AC6A3AACC0486507 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1808 |  | 2013-07-23 | 2013-07-23 18:46 | 2013-07-23 19:12 | LENNOX - 13ACX03623017 | 84 | 3.8 | Yes | Yes | 19.9 | 22.1 | -2.2 | 615FB1820DB745FA8277BEB7494F049D |  | R410A | TXV |  | 4.524% | 0.95476 | 8.694% | [5 empty] | TXV | 4.524%
Bakersfield | CA | 93304-4930 |  | 2013-06-18 | 2013-06-18 16:36 | 2013-06-18 16:36 | GOODMAN - PCB0300501 | 86 | 0 | Yes | Yes | 25.6 | 19.9 | 5.7 | 1C3BA4C598984E55AFE7DFF5FA5978FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4904 |  | 2013-06-11 | 2013-06-11 14:34 | 2013-06-11 14:34 | ICP - PGMC36G080E | 136 | 0 | Yes | Yes | 17.9 | 20.9 | -3 | 4363B292FF0541EBBC1F042E4769554E |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1851 |  | 2013-10-10 | 2013-10-10 11:55 | 2013-10-10 12:24 | RHEEM - UNK | 85 | 4.2 | Yes | Yes | 18.7 | 20.4 | -1.7 | 98325D60C5964DF29EB138B5665CC68A |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Cottonwood | CA | 96022-9771 |  | 2013-07-18 | 2013-07-18 14:06 | 2013-07-18 14:24 | ARMSTRONG - UNK | 84 | 2.7 | Yes | Yes | 20.5 | 20.6 | 0 | 777C7E39653F4DD799FE1A349B112C68 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Bakersfield | CA | 93309-5130 |  | 2013-06-28 | 2013-06-28 08:45 | 2013-06-28 08:45 | ICP - GPCM30K060F | 68 | 0 | Yes | Yes | 18.9 | 18.5 | 0.4 | D0B48989DE7C4460A4DC199D5B9763AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2927 |  | 2013-10-10 | 2013-10-10 15:09 | 2013-10-10 15:20 | TRANE - BWD730A10081 | 56 | 3.4 | Yes | Yes | 19.5 | 20.4 | -0.9 | E9410BA7FC2045F3B45C530057B683E7 |  | R22 | Non-TXV |  | 6.071% | 0.93929 | 11.67% | [5 empty] | Non-TXV | 6.071%
Fremont | CA | 94555-2435 |  | 2013-06-10 | 2013-06-10 12:29 | 2013-06-10 12:29 | OTHER - JS3BA0036KA | 85 | 0 | Yes | Yes | 23 | 19.8 | 3.2 | 8C9A9A72C1D745AE950DA3A70A82E3D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livermore | CA | 94550-3356 |  | 2013-06-20 | 2013-06-20 09:49 | 2013-06-20 09:49 | RHEEM - AT-24B10 | 85 | 0 | Yes | Yes | 20.9 | 19 | 1.9 | 93E0894017C549DAA88EAE0F898B3F94 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7308 |  | 2013-09-04 | 2013-09-04 16:41 | 2013-09-04 16:41 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | D439FDAC1AF64574B5081095A13C4318 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4848 |  | 2013-06-12 | 2013-06-12 14:24 | 2013-06-12 14:24 | PAYNE - PY3GNAA30060NA | 100 | 0 | Yes | Yes | 21.5 | 18 | 3.5 | 94915F8FEA444741A4FA022C7C0C6F4B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5230 |  | 2013-06-12 | 2013-06-12 11:08 | 2013-06-12 11:08 | BRYANT - 113ANA048-E | 112 | 0 | Yes | Yes | 16.8 | 18.2 | -1.4 | 78B8C85CF0CF4433A3AFB471A008C24E |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4599 |  | 2013-06-21 | 2013-06-21 18:58 | 2013-06-21 19:30 | ICP - CA9048VKD2 | 164 | 36.1 | Yes | Yes | 19.5 | 21.5 | -2 | 6957036ABC2E40DD943C247DEC9A876C |  | R22 | Non-TXV |  | 22.01% | 0.77988 | 42.3% | [5 empty] | Non-TXV | 22.01%
Bakersfield | CA | 93312-5382 |  | 2013-08-18 | 2013-08-18 13:51 | 2013-08-18 13:51 | YORK - H1RC036S06D | 98 | 0 | Yes | Yes | 22 | 20.6 | 1.5 | 5CDA21CD877E413A9A51C33FBEF32C66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2731 |  | 2013-06-25 | 2013-06-25 10:08 | 2013-06-25 10:32 | TRANE - 2TTB0036A1000AA | 76 | -2.5 | Yes | Yes | 13 | 15.9 | -2.9 | 2915FCCD1410413B984A53C052416174 |  | R22 | Non-TXV |  | -3.289% | 1.0329 | 0.9212% |  |  |  |  | Non-TXV |  |  | -3.289%
Fairfield | CA | 94533-1149 |  | 2013-06-12 | 2013-06-12 14:11 | 2013-06-12 14:11 | GE - | 85 | 0 | Yes | Yes | 18.5 | 17.7 | 0.8 | 3C673DDEFB0740C6954496477BC4D480 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2968 |  | 2013-08-30 | 2013-08-30 17:01 | 2013-08-30 17:01 | LUXAIRE - 24ECW045GA | 71 | 0 | Yes | Yes | 20.5 | 20.8 | -0.3 | C24902815BC94BB29CF534564153070C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2748 |  | 2013-07-12 | 2013-07-12 14:13 | 2013-07-12 14:13 | RUUD - UAMA-036JAZ | 85 | 0 | Yes | Yes | 20.8 | 15.7 | 5.1 | A1D2197B304B436F99032BDBDB086BF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2353 |  | 2013-08-22 | 2013-08-22 14:10 | 2013-08-22 14:10 | HEIL - NRGH30DDBO1 | 53 | 0 | Yes | Yes | 19.5 | 18.8 | 0.7 | C7877E3725034C0BAC7065DDC08A4EB9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2515 |  | 2013-10-10 | 2013-10-10 12:06 | 2013-10-10 12:07 | GE - NA | 72 | 9.6 | Yes | Yes | 17.3 | 17.6 | -0.3 | 56F4DF5BAD684789BD57F2EEAC7C395A |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Wasco | CA | 93280-1613 |  | 2013-07-20 | 2013-07-20 15:56 | 2013-07-20 16:18 | ARCOAIRE - PGD360090K001C1 | 160 | -8.5 | Yes | Yes | 25.9 | 20.2 | 5.7 | 60A7013EF9544A12B148EBD113E73AD7 |  | R410A | TXV |  | -5.312% | 1.0531 | 1.488% |  |  |  |  | TXV |  |  | -5.312%
San Jose | CA | 95136-1932 |  | 2013-07-22 | 2013-07-22 14:18 | 2013-07-22 14:47 | BRYANT - 56C1J048-A | 80 | 2.9 | Yes | Yes | 21 | 20.4 | 0.6 | FBED86CE0A17442A854EB1846991C25D |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Bakersfield | CA | 93307-4386 |  | 2013-06-19 | 2013-06-19 19:33 | 2013-06-19 19:33 | NORDYNE - JT5BD036 | 155 | 0 | Yes | Yes | 20 | 19.8 | 0.2 | 5E484588C69147ED8268FD1EBBA42473 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 14:09 | 2013-06-18 14:09 | NORDYNE - UKN | 144 | 0 | Yes | Yes | 22.5 | 20.9 | 1.6 | A8C807AC9D204061A1D5384B7C9B4FD4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9505 |  | 2013-08-29 | 2013-08-29 18:08 | 2013-08-29 18:08 | ICP - PGC024K06A | 58 | 0 | Yes | Yes | 21.2 | 20.6 | 0.7 | D38C0EB789FB4F0499CEA96E0F9888ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 14:47 | 2013-06-18 14:47 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 22.2 | 20.5 | 1.7 | 215BC36466C84A508F5B728B71B937B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willits | CA | 95490-5767 |  | 2013-08-21 | 2013-08-21 14:11 | 2013-08-21 15:39 | COLEMAN - TCJD24S41S3A | 61 | 3.9 | Yes | Yes | 18 | 21 | -3 | EC0B94AB8B8A4B5DA6F915431C64024E |  | R410A | Non-TXV |  | 6.393% | 0.93607 | 12.29% | [5 empty] | Non-TXV | 6.393%
San Jose | CA | 95138-1519 |  | 2013-07-19 | 2013-07-19 12:19 | 2013-07-19 12:19 | OTHER - BRCS-421BD | 84 | 0 | Yes | Yes | 20.5 | 17.7 | 2.9 | 7F2D92D5D2F749BFA04EF39B1A992A8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-0000 |  | 2013-08-16 | 2013-08-16 10:36 | 2013-08-16 10:54 | BDP - 588ANW04808AAAG | 101 | 15.3 | Yes | Yes | 21.7 | 22.1 | -0.4 | 694EBC9D02D14A299B2AD465A914BFCE |  | R22 | Non-TXV |  | 15.15% | 0.84851 | 29.11% | [5 empty] | Non-TXV | 15.15%
Vacaville | CA | 95687-5941 |  | 2013-06-19 | 2013-06-19 09:50 | 2013-06-19 10:11 | OTHER - JS5BD-042K | 172 | -5.3 | Yes | Yes | 16.6 | 18.2 | -1.6 | 9B386B67E98D4746A80C9A069A023FA6 |  | R22 | Non-TXV |  | -3.081% | 1.0308 | 0.8629% |  |  |  |  | Non-TXV |  |  | -3.081%
Livermore | CA | 94550-2392 |  | 2013-06-20 | 2013-06-20 08:52 | 2013-06-20 08:52 | OTHER - BTN942A100A2 | 159 | 0 | Yes | Yes | 25.4 | 19.7 | 5.7 | B7F7902C8D3741E989D51460E4296129 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3431 |  | 2013-08-12 | 2013-08-12 20:37 | 2013-08-12 20:47 | GOODMAN - PGB04207B-1 | 68 | 12.1 | Yes | Yes | 10.4 | 20.8 | -10.4 | 062DBD86E54D468DA57D1EA55406D0F8 | Add refrigerant: 15.3 oz | R22 | Non-TXV |  | 17.79% | 0.82206 | 34.2% | [5 empty] | Non-TXV | 17.79%
Bakersfield | CA | 93309-1886 |  | 2013-10-15 | 2013-10-15 19:59 | 2013-10-15 19:59 | PAYNE - PY3GNAA30040NA | 98 | 0 | Yes | Yes | 19 | 21.8 | -2.7 | DF020FC877FC4A269FD3DA5D01C36F10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6251 |  | 2013-06-20 | 2013-06-20 09:54 | 2013-06-20 10:15 | CARRIER - 38EH036300 | 117 | -3 | Yes | Yes | 21.4 | 19.5 | 1.9 | B3927CC4DA844430AB1E47CAEF2646D5 |  | R22 | Non-TXV |  | -2.564% | 1.0256 | 0.7181% |  |  |  |  | Non-TXV |  |  | -2.564%
Bakersfield | CA | 93307-4379 |  | 2013-06-17 | 2013-06-17 14:45 | 2013-06-17 14:45 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 21.9 | 20.4 | 1.5 | 06E6BE3ED4FC47FBB49DDF92F19651B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2302 |  | 2013-06-12 | 2013-06-12 09:55 | 2013-06-12 09:55 | CARRIER - 38TXA030320 | 96 | 0 | Yes | Yes | 16.5 | 19.1 | -2.6 | 052E27F3CAD4432888EEFF64972DFD43 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4392 |  | 2013-08-14 | 2013-08-14 15:30 | 2013-08-14 16:00 | ICP - GDFM24K040E | 54 | 7.9 | Yes | Yes | 21.8 | 22.1 | -0.3 | BDF54E20DEA64BB7AF701A78FDB11478 |  | R22 | Non-TXV |  | 14.63% | 0.8537 | 28.11% | [5 empty] | Non-TXV | 14.63%
Fresno | CA | 93726-0728 |  | 2013-08-23 | 2013-08-23 12:00 | 2013-08-23 13:48 | ARCOAIRE - 38BRC036320 | 104 | 3.9 | Yes | Yes | 18.2 | 19.8 | -1.6 | 891F95DFDF54409CBABAB0D49F115296 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Cottonwood | CA | 96022-9318 |  | 2013-06-26 | 2013-06-26 11:52 | 2013-06-26 12:32 | RUUD - UAPA 048JAZ | 85 | -6 | Yes | Yes | 20.4 | 20.9 | -0.5 | 60ABC53824C84CB1B18250C403E3DDE3 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Woodland | CA | 95695-9376 |  | 2013-09-26 | 2013-09-26 13:32 | 2013-09-26 13:32 | CARRIER - 48GS-0240400301 | 53 | 0 | Yes | Yes | 19.6 | 16.4 | 3.2 | B95AD25B8318434CB367B5681D29F636 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4381 |  | 2013-07-25 | 2013-07-25 13:31 | 2013-07-25 13:52 | NORDYNE - JT5BD036K | 155 | 18.5 | Yes | Yes | 20.2 | 20.6 | -0.4 | E11A25EB17584D11A6A3BE7A5584D0E5 |  | R22 | Non-TXV |  | 11.94% | 0.88065 | 22.94% | [5 empty] | Non-TXV | 11.94%
Pittsburg | CA | 94565-1943 |  | 2013-06-14 | 2013-06-14 11:29 | 2013-06-14 11:29 | RHEEM - UKN | 85 | 0 | Yes | Yes | 18.7 | 21.4 | -2.7 | 03573F5D1E4C4461801FFD4C95C39925 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4381 |  | 2013-06-17 | 2013-06-17 14:17 | 2013-06-17 14:17 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 20.3 | 19.3 | 1 | 711B8252A26548F1BC8A0B35C5E55880 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4989 |  | 2013-06-24 | 2013-06-24 19:56 | 2013-06-24 19:56 | PAYNE - PA10JA042-C | 81 | 0 | Yes | Yes | 21.4 | 21.3 | 0.1 | CE175D0E719642338EF404C84575CFBE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1142 |  | 2013-10-01 | 2013-10-01 16:50 | 2013-10-01 16:50 | OTHER - UKN | 41 | 0 | Yes | Yes | 22.4 | 21.8 | 0.7 | 9446A5DBD1584969BB156928B65E3AEA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2115 |  | 2013-06-13 | 2013-06-13 15:30 | 2013-06-13 15:48 | DAY & NIGHT - C4A442GKA200 | 172 | 3.2 | Yes | Yes | 15.2 | 17.2 | -2 | DEAB1AD280614BD0A63A82563E42E097 |  | R410A | Non-TXV |  | 1.86% | 0.9814 | 3.575% | [5 empty] | Non-TXV | 1.86%
Bakersfield | CA | 93313-5202 |  | 2013-06-25 | 2013-06-25 08:35 | 2013-06-25 09:00 | RUUD - UAMB-048JAZ | 162 | 33.2 | Yes | Yes | 20.8 | 21 | -0.2 | 6D59D16BB54D44D296BC1F9ADDBEC6BD |  | R22 | Non-TXV |  | 20.49% | 0.79506 | 39.38% | [5 empty] | Non-TXV | 20.49%
San Jose | CA | 95136-1633 |  | 2013-10-08 | 2013-10-08 11:07 | 2013-10-08 11:45 | ICP - RCB42A2A | 86 | 4.7 | Yes | Yes | 17.8 | 20.4 | -2.6 | 9CFD91F0D7C44E4A8B77F65D1CE7D391 |  | R22 | Non-TXV |  | 5.465% | 0.94535 | 10.5% | [5 empty] | Non-TXV | 5.465%
Bakersfield | CA | 93309-4039 |  | 2013-10-22 | 2013-10-22 16:09 | 2013-10-22 16:09 | YORK - D1NA024N03606C | 50 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | C9E79CAC71BD484D8B5820D80160CD6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2749 |  | 2013-07-22 | 2013-07-22 13:33 | 2013-07-22 14:18 | GOODMAN - GCS13042188 | 95 | 5.7 | Yes | Yes | 16.9 | 19.9 | -3 | 87412DAF6CBF4EA1A7D17F59B29A8018 |  | R22 | TXV |  | 6% | 0.94 | 11.53% | [5 empty] | TXV | 6%
Bakersfield | CA | 93309-6127 |  | 2013-06-29 | 2013-06-29 10:08 | 2013-06-29 10:08 | CARRIER - UKN | 90 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | DE59C7842D8D4298989A65D4483CACB4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7121 |  | 2013-06-11 | 2013-06-11 12:40 | 2013-06-11 12:40 | WEATHER KING - 13AJ0360C1 | 108 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | 7312D33759F04461B82CDD243C204B14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willits | CA | 95490-8927 |  | 2013-08-20 | 2013-08-20 15:04 | 2013-08-20 17:09 | COLEMAN - 9541F801 | 62 | 4 | Yes | Yes | 28.8 | 23.1 | 5.7 | CE26970F325245078132A1B2D84B9B7C |  | R22 | Non-TXV |  | 6.452% | 0.93548 | 12.4% | [5 empty] | Non-TXV | 6.452%
Shafter | CA | 93263-2744 |  | 2013-08-06 | 2013-08-06 19:41 | 2013-08-06 19:43 | BRYANT - 583ANW042060AAAF | 120 | 8.5 | Yes | Yes | 20.9 | 20.8 | 0.1 | DAC094FB761643179AA1BEA829F283C7 |  | R22 | Non-TXV |  | 7.083% | 0.92917 | 13.61% | [5 empty] | Non-TXV | 7.083%
Bakersfield | CA | 93304-4054 |  | 2013-07-02 | 2013-07-02 13:20 | 2013-07-02 13:20 | ICP - GPCM36K060F | 91 | 0 | Yes | Yes | 18.9 | 19 | 0 | 237BB986399349E48523F3FE91D47298 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2897 |  | 2013-08-05 | 2013-08-05 19:16 | 2013-08-05 19:19 | YORK - D1NA036N05606C | 67 | 5.8 | Yes | Yes | 19.8 | 19.3 | 0.5 | 497EC3D6FB7245AE856BDD44373FE6A5 |  | R22 | Non-TXV |  | 8.657% | 0.91343 | 16.64% | [5 empty] | Non-TXV | 8.657%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 15:56 | 2013-06-18 15:56 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 20.8 | 20.1 | 0.8 | 1C039FA056DF457BA8714A324CD669AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-2216 |  | 2013-09-19 | 2013-09-19 09:49 | 2013-09-19 10:06 | YORK - H2RC024S06G | 71 | -3 | Yes | Yes | 15 | 18 | -3 | FF54E3FCFB764251BA9BE650D81FC107 |  | R22 | Non-TXV |  | -4.225% | 1.0423 | 1.183% |  |  |  |  | Non-TXV |  |  | -4.225%
Morgan Hill | CA | 95037-4802 |  | 2013-10-24 | 2013-10-24 14:47 | 2013-10-24 15:36 | OTHER - ILLEGIBLE | 72 | 8 | Yes | Yes | 26.6 | 20.9 | 5.7 | FA320E7057A54586B5F1EF31F1C38DE6 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Bakersfield | CA | 93307-4378 |  | 2013-06-17 | 2013-06-17 12:23 | 2013-06-17 12:23 | NORDYNE - JT5BD-030KA | 144 | 0 | Yes | Yes | 23.9 | 20.2 | 3.7 | 1D90BFEFD3AC459589D125030B7CE337 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95117-2954 |  | 2013-07-12 | 2013-07-12 12:17 | 2013-07-12 12:17 | CARRIER - 38TRA048360 | 219 | 0 | Yes | Yes | 20 | 20.3 | -0.3 | 0BED426AE631442380B657E47A40818E |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4379 |  | 2013-06-17 | 2013-06-17 15:38 | 2013-06-17 15:38 | NORDYNE - JT5BD-030KA | 144 | 0 | Yes | Yes | 22.5 | 21 | 1.5 | EF216EADB74641EF85C7C8D9C071CEA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4829 |  | 2013-06-07 | 2013-06-07 13:31 | 2013-06-07 13:31 | CARRIER - 38BRC048330 | 167 | 0 | Yes | Yes | 19.3 | 18 | 1.3 | 669841FCC3CC48FFB3B5736B8F1637D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2013-06-19 | 2013-06-19 17:37 | 2013-06-19 17:57 | NORDYNE - JT5BD036K | 155 | 9.3 | Yes | Yes | 20.2 | 21.1 | -0.9 | 7D2A35541E124D7E856F4236A979CA08 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Bakersfield | CA | 93307-4384 |  | 2013-06-18 | 2013-06-18 18:19 | 2013-06-18 18:19 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 22 | 22.1 | -0.1 | F6134F73178F422AA9A033FD4D692F0B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2334 |  | 2013-06-14 | 2013-06-14 15:36 | 2013-06-14 15:53 | GE - BTR736B100A0 | 168 | 3 | Yes | Yes | 17.5 | 18.7 | -1.2 | 4892EFAA124C4AFC8F7C5603274EC713 |  | R22 | Non-TXV |  | 1.786% | 0.98214 | 3.432% | [5 empty] | Non-TXV | 1.786%
Vacaville | CA | 95687-7235 |  | 2013-06-20 | 2013-06-20 10:39 | 2013-06-20 11:01 | AMERICAN STANDARD - 4TTB4030E1000CA | 112 | 3 | Yes | Yes | 15.6 | 17.2 | -1.6 | 3E2B7653142E481486822C2D5FBD6DC0 |  | R410A | Non-TXV |  | 2.679% | 0.97321 | 5.148% | [5 empty] | Non-TXV | 2.679%
Bakersfield | CA | 93307-4385 |  | 2013-06-19 | 2013-06-19 16:19 | 2013-06-19 16:19 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | FE1A799CB8E643049A5BB18F58AAACDE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4508 |  | 2013-06-06 | 2013-06-06 11:45 | 2013-06-06 11:45 | RHEEM - RRMAA036JK08X | 99 | 0 | Yes | Yes | 17.1 | 19.6 | -2.5 | E89707C0FCCA4403B99EDFB2D2B13888 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4122 |  | 2013-07-22 | 2013-07-22 19:06 | 2013-07-22 19:06 | ICP - PGAA29C1K1 | 74 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | A572C118037643879FC813BC6A9A1C89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-8408 |  | 2013-10-15 | 2013-10-15 14:41 | 2013-10-15 14:41 | BDP - PA13NR048J | 136 | 0 | Yes | Yes | 19.9 | 22.4 | -2.5 | 8F5593C977E34EEE8CA9F9A3C320EBE5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2800 |  | 2013-07-02 | 2013-07-02 09:00 | 2013-07-02 09:01 | YORK - H2RA036S06D | 63 | -4.4 | Yes | Yes | 18.1 | 18.2 | -0.1 | 8B489465CA6F46329144709553A2B4AA |  | R22 | Non-TXV |  | -6.984% | 1.0698 | 1.956% |  |  |  |  | Non-TXV |  |  | -6.984%
Bakersfield | CA | 93307-4381 |  | 2013-06-17 | 2013-06-17 11:26 | 2013-06-17 11:26 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 19.4 | 21 | -1.6 | AF2F26403E5F433395CFB1804E9D4A6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-0000 |  | 2013-06-26 | 2013-06-26 09:35 | 2013-06-26 11:01 | DAY & NIGHT - UNK | 83 | 2.9 | Yes | Yes | 19.1 | 21 | -1.9 | 0F3E0139642B4B908CE1AB83AF80EABE |  | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
Bakersfield | CA | 93307-4378 |  | 2013-06-17 | 2013-06-17 13:41 | 2013-06-17 13:41 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 20 | 20.6 | -0.5 | DB4872A5B50E42C38B8204B5F1EDBEBF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5336 |  | 2013-09-26 | 2013-09-26 11:22 | 2013-09-26 11:49 | CARRIER - 24ABA342A310 | 116 | 6.6 | Yes | Yes | 22.7 | 16.8 | 5.9 | 9BC0BE744BC94802970F79EDDF251D86 |  | R410A | TXV |  | 5.69% | 0.9431 | 10.93% | [5 empty] | TXV | 5.69%
Bakersfield | CA | 93313-2419 |  | 2013-06-20 | 2013-06-20 13:56 | 2013-06-20 13:56 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.9 | 21.4 | -0.5 | F82081D92175412E9899D95079DEEA94 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1943 |  | 2013-07-12 | 2013-07-12 10:51 | 2013-07-12 12:10 | BRYANT - 561CJ036-F | 124 | 17.9 | Yes | Yes | 21.1 | 18.6 | 2.5 | A2FE3B61E4B541E09F705D4125E55D3A |  | R22 | TXV |  | 14.44% | 0.85565 | 27.74% | [5 empty] | TXV | 14.44%
Bakersfield | CA | 93313-3534 |  | 2013-06-20 | 2013-06-20 18:24 | 2013-06-20 18:24 | COLEMAN - 8742-801 | 94 | 0 | Yes | Yes | 25 | 20.2 | 4.8 | 57127AC8982E4A9287C562611F5FAB98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4382 |  | 2013-06-17 | 2013-06-17 08:25 | 2013-06-17 08:25 | NORDYNE - JT5BD036 | 155 | 0 | Yes | Yes | 20.9 | 22 | -1.1 | 0D95EC778C634B64BCB983E590E375FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2522 |  | 2013-07-25 | 2013-07-25 20:23 | 2013-07-25 20:30 | GOODMAN - PGB0360501A | 60 | 3.4 | Yes | Yes | 22.5 | 18.6 | 3.9 | 1DB894E912D34D3B8FF4A6B4F17501CD |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Bakersfield | CA | 93307-4386 |  | 2013-06-19 | 2013-06-19 18:19 | 2013-06-19 18:19 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 20.5 | 20.1 | 0.4 | 4D3C829D2BC74F18A0412ED6BE4534DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3727 |  | 2013-06-14 | 2013-06-14 14:39 | 2013-06-14 15:13 | PAYNE - 593ANX042000AAAA | 164 | 5 | Yes | Yes | 17 | 19.9 | -2.9 | 8E8B61A26754486DA025B7CBDD4FEDF3 |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Sonoma | CA | 95476-6343 |  | 2013-06-20 | 2013-06-20 09:45 | 2013-06-20 09:45 | RHEEM - MC-80-24-216 | 49 | 0 | Yes | Yes | 18.5 | 21.3 | -2.8 | 8E96BB1AE6124318943AD617B757E116 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4380 |  | 2013-06-17 | 2013-06-17 12:00 | 2013-06-17 12:00 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 19.7 | 21.4 | -1.7 | FE64106E752E47C094BB0A5CA3CB3190 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7008 |  | 2013-07-30 | 2013-07-30 19:08 | 2013-07-30 19:08 | CARRIER - 38BR030300 | 107 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 1198162C644E40BCBE8E481DCF21280E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2626 |  | 2013-09-04 | 2013-09-04 08:20 | 2013-09-04 08:20 | ICP - N2A360AKB300 | 146 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | 675EC55BBA804F1184847215F972B4F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rodeo | CA | 94572-1814 |  | 2013-07-10 | 2013-07-10 12:37 | 2013-07-10 12:38 | PAYNE - PA13NR036-H | 86 | -5.1 | Yes | Yes | 18.2 | 17.9 | 0.3 | 9403CB0FBEBE442BB50F269B35502C30 |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Bakersfield | CA | 93304-4946 |  | 2013-06-11 | 2013-06-11 17:44 | 2013-06-11 18:00 | GOODMAN - GPG1348070M41BA | 85 | 8.9 | Yes | Yes | 22 | 22 | 0 | 0ADAC24C4354404DBA64B1A9A4410085 |  | R22 | Non-TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | Non-TXV | 10.47%
Cottonwood | CA | 96022-9576 |  | 2013-09-07 | 2013-09-07 12:28 | 2013-09-07 13:31 | BRYANT - 550AN060-D | 192 | -47 | Yes | Yes | 24.7 | 20.9 | 3.8 | 60477DAF8CD04010B43FFA6856808B85 |  | R410A | TXV |  | -24.48% | 1.2448 | 6.855% |  |  |  |  | TXV |  |  | -24.48%
Bakersfield | CA | 93304-2718 |  | 2013-06-12 | 2013-06-12 11:47 | 2013-06-12 12:04 | PAYNE - PY1PNB036060AAAA | 56 | 5.5 | Yes | Yes | 19 | 20.4 | -1.4 | 83C3FBB0544242FCB183CF5F4F654DF7 |  | R22 | Non-TXV |  | 9.821% | 0.90179 | 18.87% | [5 empty] | Non-TXV | 9.821%
San Jose | CA | 95121-2229 |  | 2013-07-16 | 2013-07-16 09:15 | 2013-07-16 09:15 | OTHER - CA5536VKD2 | 85 | 0 | Yes | Yes | 20.5 | 19.8 | 0.7 | C67E502D341B4939BF32F2099490810B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-1666 |  | 2013-07-25 | 2013-07-25 09:37 | 2013-07-25 09:37 | DUCANE - SG12330050 | 85 | 0 | Yes | Yes | 21.1 | 19.7 | 1.4 | B5F5E994404C4CA1AC09B760253F91ED |  | R22 | TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-3713 |  | 2013-07-11 | 2013-07-11 15:05 | 2013-07-11 15:05 | TRANE - 2TTX4036B1000AA | 119 | 0 | Yes | Yes | 16.8 | 18.3 | -1.5 | 8D2958F174A549A9A55B67F10B0266EE |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-8740 |  | 2013-06-20 | 2013-06-20 09:14 | 2013-06-20 09:14 | GOODMAN - CKL42-1A | 95 | 0 | Yes | Yes | 16.9 | 19.6 | -2.7 | 2ACD16D9BFC643E89AE78A6AB70415FB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2043 |  | 2013-06-14 | 2013-06-14 13:33 | 2013-06-14 13:54 | GMC - VSX130301DB | 76 | 2.5 | Yes | Yes | 16.3 | 17.7 | -1.4 | E953A3FD31BD4B8DB9148D4A784CABAF |  | R410A | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Fremont | CA | 94536-5537 |  | 2013-06-19 | 2013-06-19 12:42 | 2013-06-19 13:01 | GOODMAN - CKL36-1 | 85 | 14.7 | Yes | Yes | 19.1 | 19.1 | 0.1 | 0963815080B8430EB56F3A22D55F060C |  | R22 | Non-TXV |  | 17.29% | 0.82706 | 33.24% | [5 empty] | Non-TXV | 17.29%
Antioch | CA | 94509-1828 |  | 2013-06-07 | 2013-06-07 11:47 | 2013-06-07 11:47 | RHEEM - RAMA048JAZ | 173 | 0 | Yes | Yes | 18.4 | 21 | -2.6 | EA355ABA3A6244488B09E8BB2FB7BFAA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-1502 |  | 2013-06-18 | 2013-06-18 12:30 | 2013-06-18 13:29 | CARRIER - 3588E15614 | 85 | 2.7 | Yes | Yes | 18.6 | 19.3 | -0.7 | 9DE2EFAA83244E3AB09DFA74D0EC6823 | Add refrigerant: 9.5 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Suisun City | CA | 94585-2249 |  | 2013-06-14 | 2013-06-14 13:00 | 2013-06-14 13:22 | BRYANT - 552AN036-E | 89 | 2.6 | Yes | Yes | 16.6 | 19.3 | -2.7 | 41B6E400B6CB4ADEA56473C6D6209FED |  | R22 | Non-TXV |  | 2.921% | 0.97079 | 5.614% | [5 empty] | Non-TXV | 2.921%
Santa Rosa | CA | 95403-3412 |  | 2013-10-03 | 2013-10-03 11:15 | 2013-10-03 16:13 | GOODMAN - CK24-1B | 71 | -5 | Yes | Yes | 19.3 | 20.4 | -1.1 | AE280EBEE53848759635B1B70311D833 |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Suisun City | CA | 94585-3014 |  | 2013-06-17 | 2013-06-17 14:09 | 2013-06-17 14:09 | TRANE - BTX730A100B0 | 106 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | E2D3BE56DEC64813A84914A607611E9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2220 |  | 2013-06-18 | 2013-06-18 09:38 | 2013-06-18 10:08 | CARRIER - 24ABB336W310 | 84 | 3 | Yes | Yes | 13.7 | 14.2 | -0.5 | 860D765C600F4BBBBEA9FB87936DCBE2 |  | R410A | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Dixon | CA | 95620-2907 |  | 2013-09-16 | 2013-09-16 09:50 | 2013-09-16 09:50 | LENNOX - UNK | 85 | 0 | Yes | Yes | 17.8 | 18.2 | -0.4 | EED2C9ADF00948A7BFE9B17419F4155E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Taft | CA | 93268-3234 |  | 2013-09-23 | 2013-09-23 18:32 | 2013-09-23 18:35 | YORK - D1NH036N05606C | 108 | 8 | Yes | Yes | 21.6 | 19.7 | 1.9 | 270B1F47F8214CE0BD353178DF66A973 |  | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
W Sacramento | CA | 95691-2603 |  | 2013-06-14 | 2013-06-14 11:41 | 2013-06-14 15:29 | ARCOAIRE - AC042GA | 67 | 9.3 | Yes | Yes | 18.5 | 17.5 | 1 | 590EDCBB53334934A00DD628661D4C57 |  | R22 | Non-TXV |  | 13.88% | 0.86119 | 26.68% | [5 empty] | Non-TXV | 13.88%
Bakersfield | CA | 93307-6198 |  | 2013-06-11 | 2013-06-11 18:43 | 2013-06-11 18:43 | DAY & NIGHT - 584AN03604CAF | 88 | 0 | Yes | Yes | 13.3 | 15.9 | -2.6 | A804FC046BAC49D1A1E3D4DD0C64AF12 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4539 |  | 2013-06-12 | 2013-06-12 10:59 | 2013-06-12 14:36 | LENNOX - 13ACX-036-230-02 | 85 | 5.9 | Yes | Yes | 17.7 | 18.2 | -0.5 | 645DE2AF0ABE4B788FA840CC709CF56C |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
San Jose | CA | 95121-2501 |  | 2013-10-10 | 2013-10-10 14:01 | 2013-10-10 15:07 | CARRIER - 24ABB348W310 | 112 | -9.2 | Yes | Yes | 21.3 | 19.9 | 1.4 | 682BA8DF71A7485DA0C68635B7BF507D |  | R410A | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
San Jose | CA | 95136-3329 |  | 2013-10-08 | 2013-10-08 09:52 | 2013-10-08 10:21 | ICP - HAC048AKA4 | 86 | -6.1 | Yes | Yes | 19.1 | 21.7 | -2.6 | 0DE10A242EB34E09B8947A51B6528EA3 |  | R22 | Non-TXV |  | -7.093% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.093%
Bakersfield | CA | 93308-1817 |  | 2013-09-13 | 2013-09-13 16:01 | 2013-09-13 16:18 | BRYANT - 583ANW036060AAAF | 82 | 10.4 | Yes | Yes | 22.5 | 21.5 | 1 | A51352DE2F054C2FBBA4F221016F2F0C |  | R22 | Non-TXV |  | 12.68% | 0.87317 | 24.37% | [5 empty] | Non-TXV | 12.68%
Milpitas | CA | 95035-6900 |  | 2013-09-27 | 2013-09-27 10:54 | 2013-09-27 11:29 | CARRIER - UNK | 131 | 4.3 | Yes | Yes | 21 | 21.7 | -0.7 | A9B5158628664F14AB79B0031C2A7668 |  | R22 | Non-TXV |  | 3.282% | 0.96718 | 6.308% | [5 empty] | Non-TXV | 3.282%
Bakersfield | CA | 93307-4381 |  | 2013-06-17 | 2013-06-17 12:36 | 2013-06-17 12:53 | NORDYNE - JT5BD036K | 155 | 13.9 | Yes | Yes | 20.1 | 21.1 | -0.9 | 970B7EEB228749138549E309BFACB694 |  | R22 | Non-TXV |  | 8.968% | 0.91032 | 17.23% | [5 empty] | Non-TXV | 8.968%
San Jose | CA | 95121-1464 |  | 2013-07-22 | 2013-07-22 15:09 | 2013-07-22 15:09 | BRYANT - 561CKX036000AEAA | 70 | 0 | Yes | Yes | 20.3 | 16 | 4.4 | 7FBB0A757B1446BD97ACBD1562789D61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1464 |  | 2013-07-22 | 2013-07-22 15:29 | 2013-07-23 07:19 | BRYANT - 561CKX036000AEAA | 70 | 5.8 | Yes | Yes | 17.1 | 19.6 | -2.5 | 9597F67B66F64307B96266D447D13A06 |  | R22 | Non-TXV |  | 8.286% | 0.91714 | 15.92% | [5 empty] | Non-TXV | 8.286%
Napa | CA | 94559-1414 |  | 2013-06-18 | 2013-06-18 11:44 | 2013-06-18 12:10 | DAY & NIGHT - 591AN024000AAAA | 53 | -5 | Yes | Yes | 17.4 | 18.2 | -0.8 | CD39915197C4480DBF3087FFAA0D4715 |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Redding | CA | 96003-0620 |  | 2013-09-03 | 2013-09-03 08:44 | 2013-09-03 09:16 | YORK - DAYP-F036N070A | 108 | -7.6 | Yes | Yes | 18.5 | 18.2 | 0.3 | 4188C124CA7945DCA1CD45B28356F4E0 |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Bakersfield | CA | 93305-3447 |  | 2013-10-16 | 2013-10-16 17:58 | 2013-10-16 17:58 | OTHER - 5SAW24106 | 72 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | 65DD4E9BF2894B38B1425C674FC2D621 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3447 |  | 2013-10-16 | 2013-10-16 16:40 | 2013-10-16 16:40 | ICP - GPCM024K060D | 56 | 0 | Yes | Yes | 22.1 | 21 | 1.1 | F95AFF0025FC4D51A9DB74BC84B3AC1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3447 |  | 2013-10-16 | 2013-10-16 18:18 | 2013-10-16 18:18 | OTHER - 5SAW24-106 | 72 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 8BE38850BB304011A3CC200CD6FBFF06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3143 |  | 2013-07-26 | 2013-07-26 11:24 | 2013-07-26 11:47 | CARRIER - 38CKC03640 | 124 | 7.9 | Yes | Yes | 23.5 | 18.9 | 4.6 | 9497519FA72E440E9C490BF0269DB900 |  | R22 | TXV |  | 6.371% | 0.93629 | 12.24% | [5 empty] | TXV | 6.371%
Morgan Hill | CA | 95037-3143 |  | 2013-07-26 | 2013-07-26 11:49 | 2013-07-26 11:49 | CARRIER - 38CKC03640 | 124 | 0 | Yes | Yes | 21.6 | 18.3 | 3.3 | 852ADF6EB14043A2B5216C67ECE0D9BB |  | R22 | TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4503 |  | 2013-06-13 | 2013-06-13 15:01 | 2013-06-13 15:01 | GIBSON - 561CJOX36000AEAA | 75 | 0 | Yes | Yes | 23.5 | 22.1 | 1.4 | 2F2C0962AE324ACE903D50986FAACA48 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3785 |  | 2013-10-24 | 2013-10-24 15:39 | 2013-10-24 16:19 | BRYANT - 561AJ036-C | 74 | -7 | Yes | Yes | 25.1 | 20.2 | 4.9 | 9E68064ECE5E490ABF4C19FDE4769668 |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Morgan Hill | CA | 95037-3785 |  | 2013-10-24 | 2013-10-24 16:21 | 2013-10-24 16:53 | BRYANT - 561AJX024-E | 57 | -4 | Yes | Yes | 21.6 | 20.2 | 1.5 | E840398ABACE48429F72622D60B00E3C |  | R22 | Non-TXV |  | -7.018% | 1.0702 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.018%
Bakersfield | CA | 93304-4974 |  | 2013-07-15 | 2013-07-15 09:01 | 2013-07-15 09:31 | GOODMAN - CK361C | 80 | 13.9 | Yes | Yes | 24.7 | 21.4 | 3.3 | A1BF683219A7475B9255A73111A10369 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.38% | 0.82625 | 33.39% | [5 empty] | Non-TXV | 17.38%
Woodland | CA | 95776-4206 |  | 2013-06-19 | 2013-06-19 09:45 | 2013-06-19 09:46 | BRYANT - 582ANW024060AAAD | 56 | -5.3 | Yes | Yes | 19.1 | 18.2 | 0.9 | 28286C6AED8545868577542B5B7A0DBF |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
Bakersfield | CA | 93309-6624 |  | 2013-08-19 | 2013-08-19 17:10 | 2013-08-19 17:33 | OTHER - BRCQ0481BD | 103 | -7.3 | Yes | Yes | 11.5 | 14.5 | -3 | 572D3E39EE7640CB8B7D059B7E82EDCB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -7.087% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.087%
Bakersfield | CA | 93306-6304 |  | 2013-10-15 | 2013-10-15 08:55 | 2013-10-15 09:14 | RHEEM - RRNA-B030J | 85 | 4.6 | Yes | Yes | 16.5 | 19 | -2.5 | 112D80593B8941B089EB3D9F543B2754 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
W Sacramento | CA | 95691-5987 |  | 2013-06-14 | 2013-06-14 12:24 | 2013-06-14 15:28 | CARRIER - 38CKC018340 | 85 | 7.9 | Yes | Yes | 17.7 | 18.2 | -0.5 | 65C8919FB06B4B37AD7F566653034F3E |  | R22 | Non-TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | Non-TXV | 9.294%
Bakersfield | CA | 93313-3110 |  | 2013-07-10 | 2013-07-10 08:51 | 2013-07-10 09:09 | TRANE - YCC048F1H0AA | 152 | 4.3 | Yes | Yes | 20.7 | 21 | -0.3 | 3E4F83952C954995B05D19DD756814F7 |  | R22 | Non-TXV |  | 2.829% | 0.97171 | 5.437% | [5 empty] | Non-TXV | 2.829%
Bakersfield | CA | 93307-9642 |  | 2013-07-08 | 2013-07-08 09:09 | 2013-07-08 09:33 | YORK - D1NH060N09006C | 140 | 4.2 | Yes | Yes | 23.6 | 18.2 | 5.4 | 48F3B99E34B9495FB7360A0580715386 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93307-7028 |  | 2013-07-08 | 2013-07-08 16:48 | 2013-07-08 17:55 | ICP - GPCM0420801 | 85 | 2.6 | Yes | Yes | 16.9 | 19.8 | -2.9 | 45495D85093B4D42813928ABBDBB3104 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93304-4975 |  | 2013-08-28 | 2013-08-28 11:29 | 2013-08-28 13:55 | OTHER - DCYZ-F036N070A | 85 | 3.1 | Yes | Yes | 17.3 | 20.3 | -3 | 078F1F2576CF44A3B713FCDB820D1DC6 |  | R410A | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Suisun City | CA | 94585-3079 |  | 2013-06-18 | 2013-06-18 11:44 | 2013-06-18 12:21 | TRANE - BTR730E1000A0 | 106 | 4.1 | Yes | Yes | 20.2 | 19.9 | 0.3 | B40D18DCC41F48D3B5526F5B2427224E |  | R22 | Non-TXV |  | 3.868% | 0.96132 | 7.433% | [5 empty] | Non-TXV | 3.868%
Woodland | CA | 95776-5377 |  | 2013-06-19 | 2013-06-19 13:14 | 2013-06-19 13:15 | LENNOX - XC13-030-230-03 | 68 | 7 | Yes | Yes | 15.9 | 18.2 | -2.3 | BF94DCB6DCFF41F8A28322DBA9F86A87 |  | R410A | Non-TXV |  | 10.29% | 0.89706 | 19.78% | [5 empty] | Non-TXV | 10.29%
Bakersfield | CA | 93306-7036 |  | 2013-08-06 | 2013-08-06 09:40 | 2013-08-06 10:02 | COLEMAN - BRCQ0481BD | 103 | 3 | Yes | Yes | 23.7 | 22.1 | 1.6 | E12E67AC9BCD4E3A87ACADC2A6F1919E |  | R22 | Non-TXV |  | 2.913% | 0.97087 | 5.597% | [5 empty] | Non-TXV | 2.913%
Anderson | CA | 96007-3228 |  | 2013-07-08 | 2013-07-08 14:57 | 2013-07-08 15:36 | GOODMAN - GSC130481AA | 138 | 5.1 | Yes | Yes | 26.6 | 21.5 | 5.1 | 07B7338D4FD541DCAF20149BCAA895FB |  | R22 | Non-TXV |  | 3.696% | 0.96304 | 7.102% | [5 empty] | Non-TXV | 3.696%
Bakersfield | CA | 93304-4908 |  | 2013-06-25 | 2013-06-25 13:32 | 2013-06-25 14:47 | TEMPSTAR - PGAD42D1K3 | 180 | -14.8 | Yes | Yes | 20 | 20.4 | -0.4 | 33D30935F8644403A30E0C2CCCD77D9B |  | R22 | Non-TXV |  | -8.222% | 1.0822 | 2.303% |  |  |  |  | Non-TXV |  |  | -8.222%
Bakersfield | CA | 93313-2954 |  | 2013-07-12 | 2013-07-12 10:06 | 2013-07-12 10:34 | CARRIER - 585CJ030050 | 78 | 3.6 | Yes | Yes | 26.4 | 20.7 | 5.7 | A87043E5A39944FCA7E11A1A0EEC2105 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Suisun City | CA | 94585-6338 |  | 2013-06-18 | 2013-06-18 14:21 | 2013-06-18 14:21 | LENNOX - 13ACD-048-230-02 | 204 | 0 | Yes | Yes | 14.9 | 17.6 | -2.7 | C899E9CD86BB4C6883341518EE79775A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-9322 |  | 2013-06-27 | 2013-06-27 09:13 | 2013-06-27 10:05 | ARMSTRONG - SCU12E48A | 123 | 6.7 | Yes | Yes | 20 | 20.4 | -0.4 | 57F728120271483389C0B1756F5C5EA7 |  | R22 | Non-TXV |  | 5.447% | 0.94553 | 10.47% | [5 empty] | Non-TXV | 5.447%
W Sacramento | CA | 95691-5960 |  | 2013-06-20 | 2013-06-20 10:07 | 2013-06-20 10:32 | CARRIER - 38CKC018340 | 85 | 7.6 | Yes | Yes | 16.7 | 18.2 | -1.5 | 60AC4B5618A740388170F1F18E89A320 |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
W Sacramento | CA | 95691-5978 |  | 2013-06-20 | 2013-06-20 11:44 | 2013-06-20 14:25 | CARRIER - 38CKC018340 | 51 | 10.6 | Yes | Yes | 19.2 | 18.8 | 0.4 | 9863A42607BA4CEBA19065F2343CDEFF |  | R22 | Non-TXV |  | 20.78% | 0.79216 | 39.94% | [5 empty] | Non-TXV | 20.78%
Bakersfield | CA | 93313-4588 |  | 2013-07-22 | 2013-07-22 15:46 | 2013-07-22 16:26 | OTHER - FAFF0493AZ | 163 | 15.9 | Yes | Yes | 16 | 19 | -3 | 560C75102B634EB6A258989C6DE6C3F8 |  | R22 | TXV |  | 9.755% | 0.90245 | 18.75% | [5 empty] | TXV | 9.755%
Hanford | CA | 93230-9229 |  | 2013-09-20 | 2013-09-20 13:16 | 2013-09-20 14:12 | OTHER - CA5036VKB1 | 86 | 3.7 | Yes | Yes | 22.5 | 20.5 | 2 | 5EF6EE3A46B24F19B0090FA8C40A658A |  | R22 | Non-TXV |  | 4.302% | 0.95698 | 8.268% | [5 empty] | Non-TXV | 4.302%
Woodland | CA | 95776-6707 |  | 2013-09-26 | 2013-09-26 10:14 | 2013-09-26 10:14 | CARRIER - 38EH0300340 | 200 | 0 | Yes | Yes | 21.8 | 17.7 | 4.1 | 2E70E0C87590489BA947833A02AE73F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4605 |  | 2013-08-08 | 2013-08-08 14:46 | 2013-08-08 15:35 | YORK - HBBD-F042SB | 141 | 43.4 | Yes | Yes | 28.3 | 22.6 | 5.7 | 6FB8801CD3834370ADBB68F77A01D5C0 |  | R22 | Non-TXV |  | 30.78% | 0.6922 | 59.15% | [5 empty] | Non-TXV | 30.78%
Bakersfield | CA | 93313-4605 |  | 2013-08-08 | 2013-08-08 15:37 | 2013-08-08 16:03 | UNITARY PRODUCTS GROUP - TCGDA42S21S1A | 70 | -4.9 | Yes | Yes | 24 | 19.8 | 4.2 | C0896469D6844C17A303D61E7FE10D77 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Ukiah | CA | 95482-6007 |  | 2013-08-24 | 2013-08-24 08:35 | 2013-08-24 08:57 | TRANE - 4TTB3024E1000AA | 88 | 4.1 | Yes | Yes | 22.1 | 19.3 | 2.8 | 144444E556EE4A9E8E5F92BC5A89DCED |  | R410A | TXV |  | 4.659% | 0.95341 | 8.954% | [5 empty] | TXV | 4.659%
Vallejo | CA | 94589-1775 |  | 2013-08-02 | 2013-08-02 12:37 | 2013-08-02 12:38 | TRANE - 2TTR1036A1000AA | 73 | 2.6 | Yes | Yes | 15.4 | 15.5 | -0.1 | C2071F3936AD47ED95A5E778570577A0 |  | R22 | Non-TXV |  | 3.562% | 0.96438 | 6.845% | [5 empty] | Non-TXV | 3.562%
Vacaville | CA | 95688-2118 |  | 2013-06-27 | 2013-06-27 11:18 | 2013-06-27 11:18 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 15.4 | 17.1 | -1.7 | 775E084B832E47B09BCCAF8147EB8DB9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6903 |  | 2013-08-23 | 2013-08-23 09:52 | 2013-08-23 15:23 | RUUD - UAKA-030JAZ | 66 | 4.9 | Yes | Yes | 14.4 | 16.5 | -2.1 | 33CCE0D5144B45038F7A6E9E87B5F394 |  | R22 | Non-TXV |  | 7.424% | 0.92576 | 14.27% | [5 empty] | Non-TXV | 7.424%
Bakersfield | CA | 93313-3104 |  | 2013-07-09 | 2013-07-09 18:34 | 2013-07-09 18:34 | PAYNE - N/A | 85 | 0 | Yes | Yes | 23.8 | 23.1 | 0.7 | 549178F733E74086BA0DABE4BBC4203A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3368 |  | 2013-07-23 | 2013-07-23 11:12 | 2013-07-23 11:42 | RHEEM - UAMA048JBZ | 172 | 5.9 | Yes | Yes | 20.5 | 20.2 | 0.3 | 7F0686A962BB4728B38B6E8838DA590B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.43% | 0.9657 | 6.592% | [5 empty] | Non-TXV | 3.43%
San Jose | CA | 95121-1563 |  | 2013-09-06 | 2013-09-06 11:49 | 2013-09-06 12:17 | OTHER - 24ACR336A300 | 106 | 6.6 | Yes | Yes | 23.6 | 17.7 | 5.9 | 5D6CE7D5584944CEA07E828FC559411A |  | R22 | TXV |  | 6.226% | 0.93774 | 11.97% | [5 empty] | TXV | 6.226%
W Sacramento | CA | 95691-5955 |  | 2013-06-21 | 2013-06-21 12:49 | 2013-06-21 12:50 | CARRIER - 38CKC018340 | 51 | 2.4 | Yes | Yes | 17.1 | 17.6 | -0.5 | 3D09C25E15BB4B16BCAC7A520C8CCDCE |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Suisun City | CA | 94585-3072 |  | 2013-06-18 | 2013-06-18 13:01 | 2013-06-18 13:29 | AMERICAN STANDARD - 2A7B3030A1000AA | 88 | -5.2 | Yes | Yes | 20.5 | 21 | -0.5 | 302BBDDA36344565AE81D272EB755E78 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Bakersfield | CA | 93307-6362 |  | 2013-07-01 | 2013-07-01 14:32 | 2013-07-01 15:06 | RHEEM - N/A | 85 | 0 | Yes | Yes | 20.5 | 22.1 | -1.6 | D74960E9A3DA4C8EA711CD19CEE88E23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8136 |  | 2013-10-15 | 2013-10-15 09:54 | 2013-10-15 13:42 | YORK - H1RA042S06D | 84 | -3.9 | Yes | Yes | 15 | 18 | -3 | 0E679222E6A4437D80FDA8CC61BB306B |  | R22 | Non-TXV |  | -4.643% | 1.0464 | 1.3% |  |  |  |  | Non-TXV |  |  | -4.643%
Bakersfield | CA | 93313-4945 |  | 2013-08-06 | 2013-08-06 13:50 | 2013-08-06 14:30 | RUUD - UAKA-037JAZ | 89 | -6.3 | Yes | Yes | 25.2 | 22.6 | 2.7 | 237C5F0F86484F85B4778B33521B8328 |  | R22 | Non-TXV |  | -7.079% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.079%
Cottonwood | CA | 96022-9366 |  | 2013-06-27 | 2013-06-27 13:06 | 2013-06-27 13:39 | GOODMAN - UNK | 86 | -5.1 | Yes | Yes | 23 | 19.7 | 3.3 | 0A9A88D583A240908B8B3A74A7B98F7C |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Bakersfield | CA | 93313-4156 |  | 2013-07-12 | 2013-07-12 11:40 | 2013-07-12 11:44 | DAY & NIGHT - 580ANW04206AAF | 85 | 17 | Yes | Yes | 25.5 | 21.2 | 4.3 | 402E6463130C48B6A8F59641BD0EAF58 |  | R410A | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Bakersfield | CA | 93313-4983 |  | 2013-08-02 | 2013-08-02 16:48 | 2013-08-02 16:57 | YORK - AC048Y1021A | 117 | -8.3 | Yes | Yes | 23.2 | 21 | 2.2 | 83936A01B50E47639B66CDCAC606AF29 |  | R22 | Non-TXV |  | -7.094% | 1.0709 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.094%
Los Molinos | CA | 96055-9771 |  | 2013-09-08 | 2013-09-08 12:47 | 2013-09-08 13:26 | ICP - CA5536VKD1 | 82 | 14.8 | Yes | Yes | 24.6 | 18.7 | 5.9 | DA9EB18A5E654D5E9FD72134002FEEFF |  | R22 | Non-TXV |  | 18.05% | 0.81951 | 34.69% | [5 empty] | Non-TXV | 18.05%
Anderson | CA | 96007-9317 |  | 2013-07-10 | 2013-07-10 14:00 | 2013-07-10 14:41 | DAY & NIGHT - 36PAC103C | 55 | 4.7 | Yes | Yes | 26.8 | 21.5 | 5.3 | 715DE636B08D4B1DBE9A1E76B1AE8F6A |  | R22 | Non-TXV |  | 8.545% | 0.91455 | 16.42% | [5 empty] | Non-TXV | 8.545%
Bakersfield | CA | 93306-1932 |  | 2013-06-24 | 2013-06-24 16:06 | 2013-06-24 16:44 | RHEEM - RRNA-B036JK06K | 88 | 14.6 | Yes | Yes | 17.4 | 19.6 | -2.2 | 997BF4AE0EC644C8A4B0CF7F0D48CABB |  | R22 | Non-TXV |  | 16.59% | 0.83409 | 31.88% | [5 empty] | Non-TXV | 16.59%
Vallejo | CA | 94591-7655 |  | 2013-08-02 | 2013-08-02 09:57 | 2013-08-02 10:04 | TRANE - TTN036C100B3 | 117 | 4.5 | Yes | Yes | 17.4 | 17.6 | -0.2 | 83E06C2D337F48008E4FA6AF23B2BF62 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Gilroy | CA | 95020-7285 |  | 2013-10-23 | 2013-10-23 11:59 | 2013-10-23 12:25 | ICP - TCA48AKA1 | 297 | 8.9 | Yes | Yes | 25.7 | 21.7 | 4 | A374CEE462B74CA4B5FBC0BC91C484D7 |  | R22 | Non-TXV |  | 2.997% | 0.97003 | 5.759% | [5 empty] | Non-TXV | 2.997%
Bakersfield | CA | 93304-2649 |  | 2013-07-15 | 2013-07-15 09:58 | 2013-07-15 10:15 | CARRIER - 588ANW03606AAAF | 70 | 8.2 | Yes | Yes | 26 | 21.6 | 4.5 | C1564AF4044546A6BD28BC404F919BE8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.71% | 0.88286 | 22.51% | [5 empty] | Non-TXV | 11.71%
Cottonwood | CA | 96022-7725 |  | 2013-07-13 | 2013-07-13 13:44 | 2013-07-13 14:13 | AMERICAN STANDARD - 4WCY4042A1000AA | 116 | 6 | Yes | Yes | 22.8 | 20.1 | 2.7 | E2239DEA2BB44421A8D8470DCCC2DC96 |  | R410A | Non-TXV |  | 5.172% | 0.94828 | 9.94% | [5 empty] | Non-TXV | 5.172%
Bakersfield | CA | 93304-2743 |  | 2013-06-25 | 2013-06-25 08:58 | 2013-06-25 09:20 | YORK - DINP036N05606A | 108 | 4.5 | Yes | Yes | 19.3 | 19.1 | 0.2 | F406C12282B74FA6B851AB88E2AF35C4 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Bakersfield | CA | 93313-4934 |  | 2013-07-24 | 2013-07-24 11:26 | 2013-07-24 12:01 | YORK - AC048X10102 | 117 | 5 | Yes | Yes | 19.9 | 19.7 | 0.2 | F2307EEC6A964DC0996B0ACB94A806D2 |  | R22 | Non-TXV |  | 4.274% | 0.95726 | 8.213% | [5 empty] | Non-TXV | 4.274%
Bakersfield | CA | 93304-2182 |  | 2013-06-13 | 2013-06-13 17:39 | 2013-06-13 17:59 | TEMPSTAR - DPCM048K080P | 103 | 3.1 | Yes | Yes | 24.2 | 20.9 | 3.3 | 5D632CE9815F49209DD0B9CCAF469F1F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Bakersfield | CA | 93304-1035 |  | 2013-07-16 | 2013-07-16 13:23 | 2013-07-16 13:23 | PAYNE - PY1PNB03606ABAA | 68 | 0 | Yes | Yes | 22.5 | 22 | 0.5 | 1FBFF2C676F546DA895E5BE5B100C743 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7208 |  | 2013-06-17 | 2013-06-17 10:05 | 2013-06-17 10:05 | PAYNE - PA13NR030-J | 66 | 0 | Yes | Yes | 14.4 | 14.4 | 0 | 2E5119022F844D4C928ACCD81F44A825 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-3341 |  | 2013-08-16 | 2013-08-16 12:46 | 2013-08-16 12:51 | TEMPSTAR - CA5536VKC1 | 74 | 18.3 | Yes | Yes | 15.4 | 17 | -1.6 | 4DD21C22BA8849A4B7F4360941378DEB |  | R22 | Non-TXV |  | 24.73% | 0.7527 | 47.53% | [5 empty] | Non-TXV | 24.73%
Bakersfield | CA | 93307-2932 |  | 2013-07-17 | 2013-07-17 23:14 | 2013-07-17 23:50 | DAY & NIGHT - 585CJ36075 | 84 | 3 | Yes | Yes | 23.6 | 20.3 | 3.3 | 2244C3D5567B487EB9A14939BC69A2FD |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Cottonwood | CA | 96022-7788 |  | 2013-06-25 | 2013-06-25 14:54 | 2013-06-25 15:37 | PAYNE - UNK | 128 | 4.4 | Yes | Yes | 23.5 | 22 | 1.5 | 62B75DE3062D47D2AA2F0A7FB3FCF849 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Lamont | CA | 93241-1522 |  | 2013-07-20 | 2013-07-20 13:20 | 2013-07-20 13:20 | GOODMAN - GPG1330045M41CA | 92 | 0 | Yes | Yes | 26 | 20.4 | 5.6 | E653D46C057141DBA88F33976EBD0E6F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4912 |  | 2013-08-06 | 2013-08-06 11:00 | 2013-08-06 11:37 | RUUD - EAFF-043JAZ | 99 | 7 | Yes | Yes | 23.2 | 21 | 2.2 | AE0526A1679F48CAAC2275B11EBFE24D |  | R22 | Non-TXV |  | 7.071% | 0.92929 | 13.59% | [5 empty] | Non-TXV | 7.071%
Bakersfield | CA | 93313-4919 |  | 2013-07-15 | 2013-07-15 13:06 | 2013-07-15 13:42 | OTHER - EAFF043JAZ | 99 | 4.9 | Yes | Yes | 19 | 21.9 | -2.9 | 678150D3BEB942D6BB710195737A1C6B |  | R22 | TXV |  | 4.949% | 0.95051 | 9.512% | [5 empty] | TXV | 4.949%
Lamont | CA | 93241-1015 |  | 2013-07-18 | 2013-07-18 15:29 | 2013-07-18 15:48 | TEMPSTAR - PGAA42C1K3 | 82 | 2.9 | Yes | Yes | 21.5 | 20.6 | 0.9 | A14DE086EB33471497D43F45D554AF2E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.537% | 0.96463 | 6.797% | [5 empty] | Non-TXV | 3.537%
Fairfield | CA | 94533-1906 |  | 2013-07-17 | 2013-07-17 12:21 | 2013-07-17 12:58 | AMERICAN STANDARD - 2A7A2036A1000AA | 96 | 5.8 | Yes | Yes | 17 | 18.7 | -1.7 | 5E19DF1189D346B1BB1923B4ABD9C9D2 |  | R22 | Non-TXV |  | 6.042% | 0.93958 | 11.61% | [5 empty] | Non-TXV | 6.042%
Shafter | CA | 93263-2791 |  | 2013-09-17 | 2013-09-17 18:53 | 2013-09-17 18:56 | HEIL - PGC324040K001C1 | 72 | -7 | Yes | Yes | 22.3 | 20.1 | 2.2 | 5CE754D30F2140A4A6B8EC26C01F935F |  | R410A | Non-TXV |  | -9.722% | 1.0972 | 2.723% |  |  |  |  | Non-TXV |  |  | -9.722%
Bakersfield | CA | 93307-7043 |  | 2013-07-08 | 2013-07-08 14:57 | 2013-07-08 15:18 | YORK - D1NP024N03606A | 74 | 2.4 | Yes | Yes | 16.5 | 18.1 | -1.6 | 6D93493D304040C7B024F789997B1CC2 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Bakersfield | CA | 93313-5124 |  | 2013-08-06 | 2013-08-06 14:45 | 2013-08-06 15:25 | RHEEM - ILLEGIBLE | 73 | 3.3 | Yes | Yes | 27.2 | 21.5 | 5.7 | 8E0D1C5A0C3F4E8E8EC53B280967DA10 |  | R22 | Non-TXV |  | 4.521% | 0.95479 | 8.687% | [5 empty] | Non-TXV | 4.521%
Fairfield | CA | 94533-1338 |  | 2013-07-17 | 2013-07-17 11:45 | 2013-07-17 12:03 | GE - BGTA848R1D01 | 119 | 10.4 | Yes | Yes | 30.1 | 25.9 | 4.2 | AF7F1E1D257D49FEB8B007C6347B5191 |  | R22 | Non-TXV |  | 8.739% | 0.91261 | 16.8% | [5 empty] | Non-TXV | 8.739%
Bakersfield | CA | 93308-4360 |  | 2013-08-02 | 2013-08-02 11:56 | 2013-08-02 12:22 | ICP - PGF336060K01A1 | 85 | 4.2 | Yes | Yes | 16.5 | 16.9 | -0.4 | F122FF302DF74096A4806A0A975CCE8A |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Woodland | CA | 95695-3518 |  | 2013-06-19 | 2013-06-19 14:17 | 2013-06-19 14:25 | RHEEM - RRGG-07E30JKR | 46 | -4.3 | Yes | Yes | 17.1 | 18.8 | -1.7 | 9FEA5165FC3F4D4F97A53FB318DAD7BC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.348% | 1.0935 | 2.618% |  |  |  |  | Non-TXV |  |  | -9.348%
Bakersfield | CA | 93304-2213 |  | 2013-07-26 | 2013-07-26 10:38 | 2013-07-26 10:55 | DAYTON - DAYA-F042N070C | 76 | 3.8 | Yes | Yes | 17.4 | 20.4 | -3 | FB4657DBD0CB4FCAA387F04714718A8C |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93304-3512 |  | 2013-06-20 | 2013-06-20 12:41 | 2013-06-20 13:07 | YORK - D1NA036N056060 | 67 | 2 | Yes | Yes | 26.3 | 20.4 | 6 | CCAEC5AD13E94462AF525050B82E0DCC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Fairfield | CA | 94533-1503 |  | 2013-06-12 | 2013-06-12 12:29 | 2013-06-12 12:29 | GE - | 85 | 0 | Yes | Yes | 16.7 | 19.6 | -2.9 | 5FAF0E8477D545C8AE16C3FE215588A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5866 |  | 2013-06-19 | 2013-06-19 13:45 | 2013-06-19 13:46 | RHEEM - RAKA-030JAZ | 62 | 3.6 | Yes | Yes | 20.7 | 18.8 | 1.9 | BE26E9BB41084DF9A4BF91E3EBB13844 |  | R22 | Non-TXV |  | 5.806% | 0.94194 | 11.16% | [5 empty] | Non-TXV | 5.806%
Napa | CA | 94559-3573 |  | 2013-06-28 | 2013-06-28 09:30 | 2013-06-28 09:30 | CARRIER - 38CKC042300 | 85 | 0 | Yes | Yes | 20.5 | 18.7 | 1.8 | 02BC2FE0CBDF420BB7D5A525E28B54EE |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5412 |  | 2013-07-26 | 2013-07-26 11:41 | 2013-07-26 12:17 | ICP - PGC042K080D | 87 | 4.4 | Yes | Yes | 19.9 | 20.1 | -0.2 | 9746E6D86A414BA387E3DCDBDAD4FCE5 |  | R22 | Non-TXV |  | 5.057% | 0.94943 | 9.719% | [5 empty] | Non-TXV | 5.057%
Bakersfield | CA | 93304-5435 |  | 2013-06-27 | 2013-06-27 15:01 | 2013-06-27 15:22 | TEMPSTAR - N/A | 85 | 6 | Yes | Yes | 18.5 | 18.6 | -0.1 | 1A9D87A4D3754CEF844D24A6C2F03A53 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Arvin | CA | 93203-0000 |  | 2013-08-11 | 2013-08-11 14:58 | 2013-08-11 15:39 | - 2AC13B60P-1A | 160 | 7.8 | Yes | Yes | 25.4 | 19.6 | 5.8 | 17343603A2374C32B6561B64AC6D83B4 |  | R22 | Non-TXV |  | 4.875% | 0.95125 | 9.369% | [5 empty] | Non-TXV | 4.875%
Cottonwood | CA | 96022-9529 |  | 2013-06-27 | 2013-06-27 14:20 | 2013-06-27 14:53 | ICP - PHRA30N1K1 | 70 | 2.8 | Yes | Yes | 20.2 | 20.2 | 0 | 476C304FD3C140D1B47CD913D80353EE |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93304-4009 |  | 2013-06-20 | 2013-06-20 10:45 | 2013-06-20 11:30 | PAYNE - PY3PNA042060NA | 168 | 31.7 | Yes | Yes | 19.4 | 21.3 | -1.9 | F45F5F9EE08146C8AC96AC9ACD932899 |  | R22 | Non-TXV |  | 18.87% | 0.81131 | 36.26% | [5 empty] | Non-TXV | 18.87%
Bakersfield | CA | 93304-5471 |  | 2013-08-28 | 2013-08-28 09:50 | 2013-08-28 10:25 | TRANE - YCY042G1M0AA | 85 | 3.6 | Yes | Yes | 17.4 | 19.9 | -2.5 | 2090BD6C775343CEB1DC6ABB22F8B5A1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Fairfield | CA | 94533-7219 |  | 2013-06-12 | 2013-06-12 13:08 | 2013-06-12 13:08 | RUUD - UAND-036JAZ | 116 | 0 | Yes | Yes | 14.7 | 17.2 | -2.5 | 5CDDDAB91E134951A5E3E7198DCBEB35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7215 |  | 2013-06-12 | 2013-06-12 14:42 | 2013-06-12 15:03 | DAY & NIGHT - 565BJO36-A | 80 | 2.4 | Yes | Yes | 17.1 | 19.1 | -2 | 6CF50656CC8D4A0686DFB526AD496FDC |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fairfield | CA | 94533-1444 |  | 2013-08-07 | 2013-08-07 10:29 | 2013-08-07 11:12 | OTHER - | 85 | 7.9 | Yes | Yes | 15.6 | 17.7 | -2.1 | 31A876C7CE7641CFB7C264C45FB4D456 |  | R22 | Non-TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | Non-TXV | 9.294%
Gilroy | CA | 95020-3619 |  | 2013-07-22 | 2013-07-22 10:43 | 2013-07-22 10:43 | RUUD - UAKA-042JAZ | 85 | 0 | Yes | Yes | 19.3 | 18.3 | 1.1 | D34676DD642B4D95AA30BD18F4A64558 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4385 |  | 2013-06-27 | 2013-06-27 13:29 | 2013-06-27 13:29 | RHEEM - 13AJM30A01 | 86 | 0 | Yes | Yes | 16.7 | 18.5 | -1.8 | 0468DE288A2E48848E0D9809F616FAFB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6477 |  | 2013-06-20 | 2013-06-20 18:45 | 2013-06-20 19:16 | BDP - 585CJ03005 | 78 | 2.3 | Yes | Yes | 24 | 20.4 | 3.6 | 9298B273C7584C2493AF1C5C2D26EA91 |  | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Bakersfield | CA | 93309-6477 |  | 2013-06-20 | 2013-06-20 19:19 | 2013-06-20 21:56 | BDP - 585CJ03005 | 78 | 2.5 | Yes | Yes | 24.8 | 21 | 3.8 | C5956074FEDC44718DC09518CE36EDD3 |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Bakersfield | CA | 93313-3691 |  | 2013-07-26 | 2013-07-26 13:45 | 2013-07-26 14:35 | RHEEM - ILLEGIBLE | 95 | 3.9 | Yes | Yes | 26.4 | 20.6 | 5.8 | 2838557FC0CA43FE978143C9B79CB641 |  | R22 | Non-TXV |  | 4.105% | 0.95895 | 7.889% | [5 empty] | Non-TXV | 4.105%
Gilroy | CA | 95020-7229 |  | 2013-10-22 | 2013-10-22 17:11 | 2013-10-22 17:27 | BDP - 5658J030-B | 76 | 11 | Yes | Yes | 25.5 | 20.2 | 5.3 | 44E96EBAB61548168AD0584E2E02E9D7 |  | R22 | Non-TXV |  | 14.47% | 0.85526 | 27.82% | [5 empty] | Non-TXV | 14.47%
Gilroy | CA | 95020-8240 |  | 2013-07-22 | 2013-07-22 09:46 | 2013-07-22 10:05 | CARRIER - 24ABA348A300 | 207 | 8.5 | Yes | Yes | 23.1 | 18.1 | 5 | E3ECB276DDAA48859B44CF30BDAA4735 |  | R410A | TXV |  | 4.106% | 0.95894 | 7.891% | [5 empty] | TXV | 4.106%
San Jose | CA | 95121-1040 |  | 2013-07-16 | 2013-07-16 09:44 | 2013-07-16 09:44 | CARRIER - 38CKC036340 | 124 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | 8137D516AE90473EA4E641CA1DFE2202 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6050 |  | 2013-07-10 | 2013-07-10 09:56 | 2013-07-10 10:15 | OTHER - DCYZ-F042N080C | 78 | 2.5 | Yes | Yes | 25.7 | 20.4 | 5.3 | FFDAF385CBD94368BD2288C53D3C821C |  | R410A | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Bakersfield | CA | 93304-2048 |  | 2013-07-15 | 2013-07-15 11:53 | 2013-07-15 12:17 | TEMPSTAR - PGF3300606K01 | 96 | -5.6 | Yes | Yes | 24.5 | 22.8 | 1.7 | 29AAF8D1639447779633916773C2A45B |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Bakersfield | CA | 93307-7064 |  | 2013-07-01 | 2013-07-01 10:06 | 2013-07-01 10:31 | HEIL - PGE1024D050A-3A | 85 | 2.5 | Yes | Yes | 18.1 | 19.9 | -1.8 | A91D2676862045468404B0A578D88195 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93307-7706 |  | 2013-07-24 | 2013-07-24 18:22 | 2013-07-24 18:46 | YORK - D1NA030N05606C | 85 | 3.9 | Yes | Yes | 17.1 | 19.7 | -2.6 | 77432726153649B691BB7817B14C785A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Mc Farland | CA | 93250-9741 |  | 2013-07-31 | 2013-07-31 21:23 | 2013-07-31 21:51 | GOODMAN - PGB036050-1A | 60 | 4.7 | Yes | Yes | 25.5 | 20.4 | 5.1 | 172E9D86960F4F42BA8E9D60F47F0FDB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.833% | 0.92167 | 15.05% | [5 empty] | Non-TXV | 7.833%
San Jose | CA | 95121-1563 |  | 2013-07-16 | 2013-07-16 10:07 | 2013-07-16 10:48 | PAYNE - PA10JA048-H | 106 | 5 | Yes | Yes | 21.5 | 17.8 | 3.7 | 82E957EF18E54876A1D429993DC8B6D0 |  | R22 | TXV |  | 4.717% | 0.95283 | 9.065% | [5 empty] | TXV | 4.717%
Vallejo | CA | 94589-1830 |  | 2013-06-27 | 2013-06-27 11:25 | 2013-06-27 11:49 | OTHER - UKN | 85 | -8 | Yes | Yes | 17.3 | 16.8 | 0.5 | 13185F91C6024BDEB25F0CCD1071BFA0 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Redding | CA | 96003-7540 |  | 2013-07-15 | 2013-07-15 14:19 | 2013-07-15 14:51 | TRANE - 4YY4036B1075AAC | 118 | 3.7 | Yes | Yes | 21.7 | 19.5 | 2.2 | E9CC2F749EEA4F6083C6A76402A483A3 |  | R410A | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Bakersfield | CA | 93305-4889 |  | 2013-06-21 | 2013-06-21 09:55 | 2013-06-21 10:24 | YORK - D3NZO24ND3606NXB | 58 | 2 | Yes | Yes | 25.2 | 19.5 | 5.7 | D22F7EB7CE644E678A3BD23C9A7DB8B4 |  | R410A | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Corcoran | CA | 93212-9605 |  | 2013-08-05 | 2013-08-05 13:11 | 2013-08-05 13:30 | ARCOAIRE - GPCM048K080D | 102 | 6.2 | Yes | Yes | 22.3 | 22.4 | -0.1 | 864A1B9BF3854B8E86C1F0EAD6593618 |  | R22 | Non-TXV |  | 6.078% | 0.93922 | 11.68% | [5 empty] | Non-TXV | 6.078%
Gilroy | CA | 95020-2617 |  | 2013-07-26 | 2013-07-26 09:23 | 2013-07-26 09:23 | TRANE - 2TTB0030A1000AA | 85 | 0 | Yes | Yes | 19.4 | 18.8 | 0.6 | E75511C74D2D4A889C2A3254FED0C78F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-4619 |  | 2013-07-26 | 2013-07-26 12:24 | 2013-07-26 12:59 | CARRIER - 38HDC036-321 | 84 | 0 | Yes | Yes | 23.5 | 18.2 | 5.3 | 65F88C578231463D988D0938390C5C8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-4243 |  | 2013-07-30 | 2013-07-30 11:12 | 2013-07-30 11:13 | CARRIER - 38TH048320 | 128 | 4.4 | Yes | Yes | 17.7 | 16.4 | 1.3 | 7D40D7F83F704F09B233F7D60C3F2DA6 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Lemoore | CA | 93245-4727 |  | 2013-08-02 | 2013-08-02 10:30 | 2013-08-02 10:58 | GOODMAN - CKL421A | 95 | 3.3 | Yes | Yes | 23.1 | 18.4 | 4.7 | 80D5B68A783D42A99BF1635C3E3A6B3A |  | R22 | Non-TXV |  | 3.474% | 0.96526 | 6.676% | [5 empty] | Non-TXV | 3.474%
Bakersfield | CA | 93304-1804 |  | 2013-07-15 | 2013-07-15 11:05 | 2013-07-15 11:22 | PAYNE - 585A0360807AC | 60 | -4.9 | Yes | Yes | 19.3 | 21 | -1.7 | 3177972B62DA469796F5F3F5019A8BC0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.167% | 1.0817 | 2.287% |  |  |  |  | Non-TXV |  |  | -8.167%
Arvin | CA | 93203-2504 |  | 2013-08-05 | 2013-08-05 11:07 | 2013-08-05 11:55 | GOODMAN - GPG13300451BB | 77 | 2.7 | Yes | Yes | 25.3 | 23.2 | 2.1 | 739717D71A91403BA07A756421004CE0 |  | R22 | Non-TXV |  | 3.506% | 0.96494 | 6.739% | [5 empty] | Non-TXV | 3.506%
San Jose | CA | 95121-1909 |  | 2013-10-08 | 2013-10-08 16:48 | 2013-10-08 18:47 | TRANE - TTRD42C100A2 | 174 | 12.5 | Yes | Yes | 27 | 21.1 | 6 | A6073290FB8B42E1A2254239D7061A25 |  | R22 | Non-TXV |  | 7.184% | 0.92816 | 13.81% | [5 empty] | Non-TXV | 7.184%
Gilroy | CA | 95020-5011 |  | 2013-10-23 | 2013-10-23 15:44 | 2013-10-23 16:15 | AMANA - RCC42A2Q | 121 | 3.7 | Yes | Yes | 21.2 | 20.4 | 0.8 | 0C0DE378DAC440FBBDE6E6913B166567 |  | R22 | Non-TXV |  | 3.058% | 0.96942 | 5.877% | [5 empty] | Non-TXV | 3.058%
Bakersfield | CA | 93309-2123 |  | 2013-06-21 | 2013-06-21 10:36 | 2013-06-21 11:00 | GOODMAN - GM580804BXBA | 196 | 5.9 | Yes | Yes | 14.5 | 14.2 | 0.3 | B01FB76CC63145019D25BCF90A2AD8C1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.785% | [5 empty] | Non-TXV | 3.01%
Woodland | CA | 95695-2655 |  | 2013-07-01 | 2013-07-01 09:48 | 2013-07-01 09:50 | CARRIER - 38TH042330 | 96 | 4.6 | Yes | Yes | 18.6 | 17.9 | 0.7 | B779F392C98B47DE9BAFC79AF48476BF |  | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Newark | CA | 94560-2229 |  | 2013-06-26 | 2013-06-26 09:22 | 2013-06-26 09:41 | YORK - H2RA036S06E | 63 | 12.1 | Yes | Yes | 19 | 19.3 | -0.3 | 0E30F4CFDD97486585BA542CF636C754 |  | R22 | Non-TXV |  | 19.21% | 0.80794 | 36.91% | [5 empty] | Non-TXV | 19.21%
Bakersfield | CA | 93304-5514 |  | 2013-07-23 | 2013-07-23 13:29 | 2013-07-23 14:24 | DAY & NIGHT - ‎ILLEGIBLE | 102 | 9.8 | Yes | Yes | 20.2 | 18.1 | 2.1 | 4E7C9FE090F148FEBDA284443E62BA24 |  | R22 | Non-TXV |  | 9.608% | 0.90392 | 18.46% | [5 empty] | Non-TXV | 9.608%
Bakersfield | CA | 93312-5502 |  | 2013-07-15 | 2013-07-15 21:25 | 2013-07-15 21:48 | RHEEM - N/A | 85 | 6.1 | Yes | Yes | 21.5 | 23.7 | -2.2 | 8F7C059854A346FA94AECA90CF401031 |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Bakersfield | CA | 93304-5431 |  | 2013-08-28 | 2013-08-28 10:28 | 2013-08-28 11:24 | YORK - D1P048N06506A | 132 | 14.7 | Yes | Yes | 27.5 | 21.5 | 6 | 1D1492C75C0E4AA79A898291D60A6574 |  | R22 | Non-TXV |  | 11.14% | 0.88864 | 21.4% | [5 empty] | Non-TXV | 11.14%
San Jose | CA | 95129-4724 |  | 2013-09-06 | 2013-09-06 11:08 | 2013-09-06 11:43 | TRANE - TTR048D100A1 | 86 | 9.4 | Yes | Yes | 21.8 | 16.6 | 5.2 | 503165AB1ECF4EA7B4A062C16F67C3F6 |  | R22 | Non-TXV |  | 10.93% | 0.8907 | 21.01% | [5 empty] | Non-TXV | 10.93%
Vallejo | CA | 94589-2059 |  | 2013-06-27 | 2013-06-27 12:15 | 2013-06-27 12:42 | YORK - H1RD042S06G | 152 | 12.3 | Yes | Yes | 13.7 | 16.4 | -2.7 | 633674B22E2E429590AAEBBCEDADF7D0 |  | R22 | Non-TXV |  | 8.092% | 0.91908 | 15.55% | [5 empty] | Non-TXV | 8.092%
Fairfield | CA | 94534-7408 |  | 2013-06-13 | 2013-06-13 13:15 | 2013-06-13 13:32 | TRANE - 2TTB0036A1000AA | 76 | 2.6 | Yes | Yes | 14.9 | 17.7 | -2.8 | FAE9B0E720384D78A209CDA2474CA392 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Novato | CA | 94947-4802 |  | 2013-06-20 | 2013-06-20 11:06 | 2013-06-20 11:29 | TRANE - 2TTX4036B1000AA | 120 | 16.7 | Yes | Yes | 22.6 | 18.2 | 4.4 | 99F04CA5438F4DEDA58E317F6F284DBC | Add refrigerant: 16.4 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.92% | 0.86083 | 26.74% | [5 empty] | Non-TXV | 13.92%
Anderson | CA | 96007-8535 |  | 2013-07-10 | 2013-07-10 10:31 | 2013-07-10 11:16 | PAYNE - PA12NA042-A | 102 | 8.6 | Yes | Yes | 26.5 | 21 | 5.5 | 3E06D4B85D174E1FB17979FE69B5A6EA |  | R22 | Non-TXV |  | 8.431% | 0.91569 | 16.2% | [5 empty] | Non-TXV | 8.431%
Anderson | CA | 96007-8535 |  | 2013-07-10 | 2013-07-10 10:40 | 2013-07-10 11:17 | PAYNE - PA12N042-A | 102 | 6.2 | Yes | Yes | 27 | 21.5 | 5.5 | 8C02A81F6C634B1089C8FB2E7A165A20 |  | R22 | Non-TXV |  | 6.078% | 0.93922 | 11.68% | [5 empty] | Non-TXV | 6.078%
Bakersfield | CA | 93304-4958 |  | 2013-06-25 | 2013-06-25 16:34 | 2013-06-25 16:57 | CARRIER - N/A | 85 | 3.7 | Yes | Yes | 22 | 19 | 3 | 563EFD7ABB6F47DDB190EDE11526884D |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Fairfield | CA | 94534-3462 |  | 2013-06-13 | 2013-06-13 10:49 | 2013-06-13 11:11 | LENNOX - 10ACB36-1P | 74 | -4.4 | Yes | Yes | 16.6 | 18.2 | -1.6 | DB00CF2CB4344150B096A63838284AF0 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Novato | CA | 94949-5938 |  | 2013-06-20 | 2013-06-20 12:49 | 2013-06-20 12:49 | AMERICAN STANDARD - 2A7A4042B1000AA | 137 | 0 | Yes | Yes | 23.6 | 21.3 | 2.3 | CE2032771C654F0BA10F8196D18B1033 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3314 |  | 2013-07-26 | 2013-07-26 13:11 | 2013-07-26 13:52 | BRYANT - 583ANN036060AAAF | 85 | 4.1 | Yes | Yes | 15.9 | 18.9 | -3 | B9C6B2A663ED4DE0A0053025BEB1229D |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Suisun City | CA | 94585-1780 |  | 2013-06-21 | 2013-06-21 13:54 | 2013-06-21 14:18 | - PA13NR036-E | 100 | 3.6 | Yes | Yes | 17.5 | 19.8 | -2.3 | 73FDD40106D84BD0824469B305E522B5 |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Bakersfield | CA | 93308-2820 |  | 2013-08-13 | 2013-08-13 17:30 | 2013-08-13 20:30 | GOODMAN - GPG1360090M41DA | 85 | 5.5 | Yes | Yes | 20.5 | 20.2 | 0.4 | 3634275FF07B4D4FBDEC3EEC6B244B93 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Bakersfield | CA | 93307-6528 |  | 2013-07-01 | 2013-07-01 10:31 | 2013-07-01 11:20 | RHEEM - N/A | 85 | 4.6 | Yes | Yes | 20 | 19.9 | 0.1 | 561F9C73C45649C08B238B960C4036AB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Bakersfield | CA | 93307-6053 |  | 2013-07-01 | 2013-07-01 17:09 | 2013-07-01 17:27 | CARRIER - N/A | 85 | 12 | Yes | Yes | 22 | 22.1 | -0.1 | 874F4EE9DCCB498D955FC8D3E88F10E8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Bakersfield | CA | 93306-6515 |  | 2013-06-24 | 2013-06-24 14:42 | 2013-06-24 14:58 | ARCOAIRE - PGF036K080B | 71 | -4.2 | Yes | Yes | 16 | 18.8 | -2.8 | 03144662544C42F59561B3775C69D0D8 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Bakersfield | CA | 93309-4039 |  | 2013-07-30 | 2013-07-30 17:31 | 2013-07-30 17:37 | RHEEM - RRNA-B024JK06X | 70 | 3.2 | Yes | Yes | 23 | 20.8 | 2.2 | 6E83B3371C584604ACE33C72DFB23315 |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Bakersfield | CA | 93312-6440 |  | 2013-07-30 | 2013-07-30 17:00 | 2013-07-30 17:18 | OTHER - 38BRCO6O340 | 94 | 3.8 | Yes | Yes | 22.1 | 22.6 | -0.5 | 20A9A37B28994196B71CFADC8E356A54 |  | R22 | Non-TXV |  | 4.043% | 0.95957 | 7.769% | [5 empty] | Non-TXV | 4.043%
San Jose | CA | 95138-1519 |  | 2013-10-17 | 2013-10-17 11:46 | 2013-10-17 13:44 | UNITARY PRODUCTS GROUP - AC030M1021AQ | 51 | 1.8 | Yes | Yes | 21.8 | 22 | -0.2 | 96C264874CCE497FAFF122632272B219 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93313-4414 |  | 2013-07-15 | 2013-07-15 09:22 | 2013-07-15 09:40 | RHEEM - RAKA-030JAS | 85 | 2.9 | Yes | Yes | 20 | 20.4 | -0.4 | ACAD91DE0DA1499BBEE81535BFEB77B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Bakersfield | CA | 93307-6053 |  | 2013-07-01 | 2013-07-01 16:35 | 2013-07-01 17:07 | CARRIER - N/A | 85 | 2.8 | Yes | Yes | 23.3 | 22.1 | 1.2 | 49316C5CA7C643A9899CB5567E2E1A1E |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Willits | CA | 95490-0000 |  | 2013-08-19 | 2013-08-19 10:29 | 2013-08-19 10:55 | COLEMAN - TCGD24S21S1A | 64 | -5.3 | Yes | Yes | 22.5 | 21 | 1.5 | 267740D0967540E8A21F8E7DA2DB6FCE |  | R22 | Non-TXV |  | -8.281% | 1.0828 | 2.319% |  |  |  |  | Non-TXV |  |  | -8.281%
Vacaville | CA | 95687-4352 |  | 2013-07-09 | 2013-07-09 09:20 | 2013-07-09 10:05 | GOODMAN - CLJ30-J | 85 | 5 | Yes | Yes | 15 | 17.7 | -2.7 | FF4E6E8B03AC4B25BB32BDB3630B322C |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Fairfield | CA | 94533-5910 |  | 2013-06-17 | 2013-06-17 13:32 | 2013-06-17 13:57 | CARRIER - 24ABB336A310 | 85 | 2.5 | Yes | Yes | 16.7 | 17.6 | -0.9 | 9FB354CD34234273A1A3F1B68C7FA48F |  | R410A | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93307-6519 |  | 2013-07-01 | 2013-07-01 09:04 | 2013-07-01 09:25 | BRYANT - 589ANW03606060ADBF | 84 | 3.8 | Yes | Yes | 22.5 | 17.4 | 5.1 | 2516BEB3F2BC4A1781D94AAC616EF4DA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.524% | 0.95476 | 8.694% | [5 empty] | Non-TXV | 4.524%
San Jose | CA | 95127-1051 |  | 2013-10-09 | 2013-10-09 14:07 | 2013-10-09 14:32 | CARRIER - 24ABB336W310 | 83 | 9.8 | Yes | Yes | 22.2 | 20.2 | 2 | 49A428B96CC74999BD8E19C4E2AFA5A1 |  | R410A | TXV |  | 11.81% | 0.88193 | 22.69% | [5 empty] | TXV | 11.81%
Bakersfield | CA | 93304-2201 |  | 2013-08-09 | 2013-08-09 13:38 | 2013-08-09 14:03 | GOODMAN - GPG1336070M41AA | 85 | 2.8 | Yes | Yes | 22 | 17.5 | 4.6 | A5A32C5EC0144C88AEBC56AC8DA57505 |  | R410A | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Bakersfield | CA | 93307-6523 |  | 2013-07-17 | 2013-07-17 11:57 | 2013-07-17 12:26 | YORK - DAYHF042N080C | 94 | 4.5 | Yes | Yes | 19.8 | 21 | -1.2 | 318BB788D28341A6A9CCD3E8034004F4 |  | R22 | Non-TXV |  | 4.787% | 0.95213 | 9.2% | [5 empty] | Non-TXV | 4.787%
Bakersfield | CA | 93304-4910 |  | 2013-06-26 | 2013-06-26 08:43 | 2013-06-26 09:23 | GOODMAN - GPG13360701AC | 85 | 2.7 | Yes | Yes | 17.2 | 19.3 | -2.1 | 3B56A803DBB040E08F0CA617FF65A7B0 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93304-5741 |  | 2013-07-16 | 2013-07-16 09:39 | 2013-07-16 13:18 | GOODMAN - GPG13360451AC | 112 | 10.2 | Yes | Yes | 24.6 | 20.3 | 4.3 | 495DC30CFDE04A74820821C84670B1FF |  | R22 | Non-TXV |  | 9.107% | 0.90893 | 17.5% | [5 empty] | Non-TXV | 9.107%
Bakersfield | CA | 93313-5141 |  | 2013-07-15 | 2013-07-15 11:22 | 2013-07-15 11:51 | OTHER - 28CKO42300 | 90 | 5 | Yes | Yes | 20.7 | 21 | -0.3 | B061306C32A040919F2A8BB2CF3BA118 |  | R22 | TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | TXV | 5.556%
Vacaville | CA | 95688-2739 |  | 2013-06-20 | 2013-06-20 15:32 | 2013-06-20 16:16 | -27000483000 | 61 | 1.9 | Yes | Yes | 17.2 | 19.4 | -2.2 | 631A623603C44FF08142196D43CBC0C8 |  | R22 | Non-TXV |  | 3.115% | 0.96885 | 5.986% | [5 empty] | Non-TXV | 3.115%
Bakersfield | CA | 93313-4415 |  | 2013-07-26 | 2013-07-26 12:53 | 2013-07-26 13:27 | RHEEM - RAHE-036JAS | 91 | 6.7 | Yes | Yes | 21.4 | 19.9 | 1.5 | 8682405FBB054EB8A79F0FFF14E956A8 |  | R22 | Non-TXV |  | 7.363% | 0.92637 | 14.15% | [5 empty] | Non-TXV | 7.363%
Bakersfield | CA | 93307-6001 |  | 2013-07-01 | 2013-07-01 15:57 | 2013-07-01 16:31 | CARRIER - ACP024C121B | 85 | 2.7 | Yes | Yes | 21.1 | 23.1 | -2 | 38D7607E36F74839A15C9C83CA769C32 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
W Sacramento | CA | 95691-5981 |  | 2013-06-20 | 2013-06-20 10:33 | 2013-06-20 14:26 | CARRIER - 38CKC024340 | 54 | 4.9 | Yes | Yes | 16.4 | 17.6 | -1.2 | 2A87BD1CE29C4DD68FF23982E3999003 |  | R22 | Non-TXV |  | 9.074% | 0.90926 | 17.44% | [5 empty] | Non-TXV | 9.074%
Bakersfield | CA | 93306-3126 |  | 2013-06-24 | 2013-06-24 13:14 | 2013-06-24 13:50 | - NA | 85 | -5.8 | Yes | Yes | 26.2 | 20.1 | 6.1 | 82B31A2241724C9C85D62C9AD85CD829 | Add refrigerant: 5.8 oz | R22 | Non-TXV |  | -6.824% | 1.0682 | 1.911% |  |  |  |  | Non-TXV |  |  | -6.824%
Cupertino | CA | 95014-0550 |  | 2013-10-02 | 2013-10-02 10:32 | 2013-10-02 10:32 | RUUD - UNK | 84 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | 06CBE7BA92D1407F8FA9B7C9AA7E5CEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-2960 |  | 2013-08-07 | 2013-08-07 15:08 | 2013-08-07 16:47 | GE - | 85 | 3.6 | Yes | Yes | 18.2 | 18.7 | -0.5 | 1A08A41FBAAD443D9B5E9A12C26EE52E |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Bakersfield | CA | 93314-9205 |  | 2013-07-23 | 2013-07-23 10:27 | 2013-07-23 12:24 | DAY & NIGHT - 591ANX060000AAAA | 170 | -12 | Yes | Yes | 29.2 | 19.7 | 9.6 | 48E9C2A35BE146FF8944CD8DFFA00200 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93313-4414 |  | 2013-07-24 | 2013-07-24 10:24 | 2013-07-24 10:55 | RHEEM - RAHE036JAS | 92 | 4.5 | Yes | Yes | 19.5 | 18.8 | 0.7 | B6BC268A207B402C9D0F946561837ED2 |  | R22 | TXV |  | 4.891% | 0.95109 | 9.4% | [5 empty] | TXV | 4.891%
Bakersfield | CA | 93305-2417 |  | 2013-07-16 | 2013-07-16 09:15 | 2013-07-16 09:31 | BRYANT - 583ANW36060AAAF | 83 | -7.8 | Yes | Yes | 24.5 | 19.9 | 4.6 | 63C99EF4BA9D461196A7B0B3BCBD5111 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Napa | CA | 94558-1687 |  | 2013-06-13 | 2013-06-13 15:39 | 2013-06-13 15:39 | DUCANE - 2AC13B30P-1A | 129 | 0 | Yes | Yes | 18.6 | 20.1 | -1.5 | 9E6BC3DB0DC04B33A548FC9EEDBF4115 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pacheco | CA | 94553-5114 |  | 2013-07-01 | 2013-07-01 14:16 | 2013-07-01 14:41 | GOODMAN - CK36-1B | 76 | 2.7 | Yes | Yes | 16.6 | 17.7 | -1.1 | B610448E014E4669AB99274253506754 |  | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Vacaville | CA | 95687-6729 |  | 2013-06-20 | 2013-06-20 14:50 | 2013-06-20 14:50 | GIBSON - JS3BC-042KA | 102 | 0 | Yes | Yes | 16.8 | 19.4 | -2.6 | 8D359912ECC248DA8DBE8A43C063E304 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6504 |  | 2013-07-22 | 2013-07-22 14:32 | 2013-07-22 16:11 | YORK - D2NP048N06506A | 132 | 6.2 | Yes | Yes | 17.4 | 20.2 | -2.8 | 5F1DF9F8A0424BE484BCC931DCD13D0E |  | R22 | Non-TXV |  | 4.697% | 0.95303 | 9.027% | [5 empty] | Non-TXV | 4.697%
Union City | CA | 94587-1317 |  | 2013-06-26 | 2013-06-26 10:14 | 2013-06-26 10:59 | RHEEM - 583 RX F09 1872 | 85 | 3.7 | Yes | Yes | 22.3 | 19.9 | 2.4 | DD78C1ECFFCF4ABFBADC2270B54C8AC2 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Bakersfield | CA | 93308-1810 |  | 2013-07-02 | 2013-07-02 18:02 | 2013-07-02 18:48 | AMANA - RCE60C2A | 245 | 7.9 | Yes | Yes | 20.6 | 23.2 | -2.6 | B4376D6FCC2C406C8DCA3640F8ECF836 |  | R22 | Non-TXV |  | 3.224% | 0.96776 | 6.197% | [5 empty] | Non-TXV | 3.224%
Bakersfield | CA | 93308-4360 |  | 2013-08-02 | 2013-08-02 11:11 | 2013-08-02 11:54 | PAYNE - PY3PNA030040NA | 85 | 2.8 | Yes | Yes | 25.9 | 20.4 | 5.5 | 4FE72494F34E4C8D99059A2D09436BF0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Bakersfield | CA | 93309-5138 |  | 2013-08-12 | 2013-08-12 13:38 | 2013-08-12 13:55 | CARRIER - UNK | 85 | 8.1 | Yes | Yes | 19.5 | 20.5 | -1 | 9DA122487C2D4CD2B41928BC38F7DABC |  | R22 | Non-TXV |  | 9.529% | 0.90471 | 18.31% | [5 empty] | Non-TXV | 9.529%
Bakersfield | CA | 93306-5074 |  | 2013-06-24 | 2013-06-24 10:16 | 2013-06-24 10:43 | PAYNE - PY3PNA060090NA | 184 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 6CA1CAE0B8704CEDBE94025FC5EEDF7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5978 |  | 2013-07-01 | 2013-07-01 10:43 | 2013-07-01 10:44 | CARRIER - CKC018340 | 51 | 1.9 | Yes | Yes | 18.7 | 18.2 | 0.5 | 893508DD0C9A4BEFB49CC46A6C290FAB |  | R22 | Non-TXV |  | 3.725% | 0.96275 | 7.16% | [5 empty] | Non-TXV | 3.725%
Suisun City | CA | 94585-1504 |  | 2013-06-18 | 2013-06-18 15:11 | 2013-06-18 15:11 | DAY & NIGHT - | 85 | 0 | Yes | Yes | 16.5 | 18.1 | -1.6 | F7D95E7FCD714A429BCAAE848CD24FF0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1203 |  | 2013-07-23 | 2013-07-23 12:27 | 2013-07-23 12:56 | COLEMAN - TCGD42S21SA2 | 66 | -3.9 | Yes | Yes | 20.2 | 17.2 | 3 | 13654DE76E8E45D9A8800C2F9849CEB8 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Bakersfield | CA | 93307-4823 |  | 2013-07-17 | 2013-07-17 14:57 | 2013-07-17 15:26 | RHEEM - HC-80-30-210 | 48 | 10.4 | Yes | Yes | 25.9 | 21.1 | 4.8 | 0A5362D16FC1493A87BD82EEFD9D6D60 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.67% | 0.78333 | 41.64% | [5 empty] | Non-TXV | 21.67%
Anderson | CA | 96007-8528 |  | 2013-07-10 | 2013-07-10 09:00 | 2013-07-10 09:25 | PAYNE - PA10JA042-A | 89 | 8.6 | Yes | Yes | 26.9 | 22.1 | 4.8 | 3285E2AE261744BCA150F8C0AEE5ADC2 |  | R22 | Non-TXV |  | 9.663% | 0.90337 | 18.57% | [5 empty] | Non-TXV | 9.663%
Napa | CA | 94559-4743 |  | 2013-06-18 | 2013-06-18 12:46 | 2013-06-18 12:46 | TRANE - TTB024C1GAX | 53 | 0 | Yes | Yes | 17.8 | 19.6 | -1.8 | A78CF0431EC74AF3B78B0F90F98CC614 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ukiah | CA | 95482-9558 |  | 2013-08-22 | 2013-08-22 14:27 | 2013-08-22 15:01 | COLEMAN - TCGD36S41S1A | 73 | 5.7 | Yes | Yes | 23.2 | 21 | 2.2 | D84FBDACC5984FEFB7A51C3E02539B58 |  | R410A | TXV |  | 7.808% | 0.92192 | 15.01% | [5 empty] | TXV | 7.808%
Woodland | CA | 95695-2524 |  | 2013-07-12 | 2013-07-12 09:42 | 2013-07-12 09:42 | AMERICAN STANDARD - 2A7AA4024B1000AA | 105 | 0 | Yes | Yes | 15.7 | 18.5 | -2.8 | 0BA331AE03E24816B6BC44557F10B5F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2316 |  | 2013-06-27 | 2013-06-27 18:52 | 2013-06-27 19:20 | TEMPSTAR - PGAA36C1K3 | 69 | 4.1 | Yes | Yes | 15.3 | 17.5 | -2.2 | 4CA318BFA06B42189541325A0A508EA6 |  | R22 | Non-TXV |  | 5.942% | 0.94058 | 11.42% | [5 empty] | Non-TXV | 5.942%
Anderson | CA | 96007-8512 |  | 2013-07-09 | 2013-07-09 08:41 | 2013-07-09 09:24 | BDP - 542DBX042000AAAF | 178 | 5.8 | Yes | Yes | 18.9 | 19.5 | -0.6 | 39A4B96D2FDB41C197FE663E66F36363 |  | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.262% | [5 empty] | Non-TXV | 3.258%
Novato | CA | 94947-4794 |  | 2013-06-20 | 2013-06-20 13:30 | 2013-06-20 13:30 | KENMORE - CA9630VKC1 | 122 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | 28DDC718391845D5A08AB03DC45651E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5590 |  | 2013-09-21 | 2013-09-21 16:38 | 2013-09-21 16:55 | GOODMAN - CK-42-1C | 85 | 7.2 | Yes | Yes | 20.3 | 20.6 | -0.3 | 8B91D48F5F0F45ADA5DC7D866D162858 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Bakersfield | CA | 93307-6525 |  | 2013-07-01 | 2013-07-01 13:37 | 2013-07-01 15:08 | RHEEM - N/A | 85 | 23.4 | Yes | Yes | 16 | 24.5 | -8.5 | 0850F034BD924B4190A949D4A8AD6433 | Add refrigerant: 23.5 oz | R22 | Non-TXV |  | 27.53% | 0.72471 | 52.91% | [5 empty] | Non-TXV | 27.53%
Fairfield | CA | 94534-3013 |  | 2013-06-21 | 2013-06-21 12:58 | 2013-06-21 13:27 | GOODMAN - CKJ36-10 | 90 | 4.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | 125AD6192B5F49208C410C910DE2E617 |  | R22 | Non-TXV |  | 4.889% | 0.95111 | 9.395% | [5 empty] | Non-TXV | 4.889%
Bakersfield | CA | 93307-5771 |  | 2013-07-01 | 2013-07-01 17:16 | 2013-07-01 17:46 | YORK - H2RD030S06B | 93 | 2.7 | Yes | Yes | 19 | 20.8 | -1.8 | 549F0D9F10FD4EC1961A96784531D7A3 |  | R22 | Non-TXV |  | 2.903% | 0.79231 | 39.91% | [5 empty] | Non-TXV | 2.903%
Anderson | CA | 96007-4716 |  | 2013-07-09 | 2013-07-09 17:18 | 2013-07-10 08:22 | ARMSTRONG - SCU12E30A-2 | 87 | 16.9 | Yes | Yes | 20 | 21.5 | -1.5 | 9D23E9F7D7F84A15BC2A83D7268B7705 |  | R22 | Non-TXV |  | 19.43% | 0.80575 | 37.33% | [5 empty] | Non-TXV | 19.43%
Bakersfield | CA | 93313-6009 |  | 2013-08-08 | 2013-08-08 10:13 | 2013-08-08 10:51 | CARRIER - AA1CJ060-A | 156 | 37.1 | Yes | Yes | 25.2 | 20.4 | 4.8 | 06C7734BC3634A25840A40123BAFB339 |  | R22 | Non-TXV |  | 23.78% | 0.76218 | 45.7% | [5 empty] | Non-TXV | 23.78%
San Jose | CA | 95135-1216 |  | 2013-09-23 | 2013-09-23 10:51 | 2013-09-23 11:17 | TRANE - TTX042C100A1 | 142 | 7.9 | Yes | Yes | 23.8 | 20.2 | 3.7 | F06C02C8C8AC409BB1E11699D48B58BC |  | R22 | TXV |  | 5.563% | 0.94437 | 10.69% | [5 empty] | TXV | 5.563%
Bakersfield | CA | 93313-3515 |  | 2013-07-10 | 2013-07-10 13:52 | 2013-07-10 14:30 | TEMPSTAR - GPCM30K060F | 70 | 2.2 | Yes | Yes | 20.4 | 21.5 | -1.1 | 1A1092FD6FD84DE1BA2D43EBFED1651D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
San Jose | CA | 95117-1619 |  | 2013-09-26 | 2013-09-26 09:49 | 2013-09-26 09:49 | CARRIER - 38TKB036300 | 80 | 0 | Yes | Yes | 30 | 17.7 | 12.3 | 9709A81528FC493F97CDDDD4ABA70326 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2814 |  | 2013-07-15 | 2013-07-15 13:55 | 2013-07-15 14:13 | PAYNE - PY3PNA042060NB | 123 | 7.9 | Yes | Yes | 23.5 | 21.8 | 1.8 | 5491143B2D794DD5BAAF3507DB1FDAA3 |  | R22 | Non-TXV |  | 6.423% | 0.93577 | 12.34% | [5 empty] | Non-TXV | 6.423%
Bakersfield | CA | 93304-2814 |  | 2013-07-15 | 2013-07-15 14:15 | 2013-07-15 20:46 | PAYNE - PY3PNA042060NB | 123 | 9.3 | Yes | Yes | 24 | 21 | 3 | 9B6AA610DF6F4673855259244151C157 |  | R22 | Non-TXV |  | 7.561% | 0.92439 | 14.53% | [5 empty] | Non-TXV | 7.561%
Bakersfield | CA | 93304-5440 |  | 2013-06-27 | 2013-06-27 17:06 | 2013-06-27 18:54 | PAYNE - PY3PNA048090NA | 195 | 5.8 | Yes | Yes | 15 | 16.6 | -1.6 | 2449A8DD6F5046B483FA7D638AB5AA98 |  | R22 | Non-TXV |  | 2.974% | 0.97026 | 5.716% | [5 empty] | Non-TXV | 2.974%
Bakersfield | CA | 93308-7863 |  | 2013-07-03 | 2013-07-03 10:09 | 2013-07-03 15:19 | YORK - D1NP030N0560A | 73 | 2.6 | Yes | Yes | 23.4 | 19.5 | 4 | 22C6F5D363D841CC9DD81C94F5FA3488 |  | R22 | Non-TXV |  | 3.562% | 0.96438 | 6.845% | [5 empty] | Non-TXV | 3.562%
Fairfield | CA | 94534-4151 |  | 2013-10-14 | 2013-10-14 12:08 | 2013-10-14 12:48 | GIBSON - JS3BC-048KA | 85 | 12.2 | Yes | Yes | 18.4 | 15.5 | 2.9 | 75BC4CD77D1E4EF7AB0426B9744D7A9D |  | R22 | Non-TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | Non-TXV | 14.35%
Cottonwood | CA | 96022-0000 |  | 2013-07-13 | 2013-07-13 14:35 | 2013-07-13 15:37 | RHEEM - UAKA-036JAS | 72 | 3.7 | Yes | Yes | 26.1 | 20.4 | 5.7 | EDD99954F6924B3682E7CED870128788 |  | R22 | Non-TXV |  | 5.139% | 0.94861 | 9.876% | [5 empty] | Non-TXV | 5.139%
Bakersfield | CA | 93307-7123 |  | 2013-07-08 | 2013-07-08 11:45 | 2013-07-08 12:14 | RHEEM - 13AJA36A01 | 108 | 3.5 | Yes | Yes | 19 | 19.8 | -0.8 | AA306291DD584C76B4D3D75EF546F40F |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Vacaville | CA | 95688-9236 |  | 2013-07-10 | 2013-07-10 13:55 | 2013-07-10 13:55 | CARRIER - 38EH30340 | 125 | 0 | Yes | Yes | 14.9 | 17.7 | -2.8 | 1C5A5A6E3D5A4A418F734176A36495D5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7841 |  | 2013-08-13 | 2013-08-13 14:54 | 2013-08-13 15:22 | GOODMAN - PGB036050-1A | 85 | 4 | Yes | Yes | 14.1 | 17.1 | -3 | 62E5D1D6980643A2B27889511BC465AF |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Bakersfield | CA | 93313-5442 |  | 2013-07-22 | 2013-07-22 18:30 | 2013-07-22 19:23 | GOODMAN - CKL49 | 109 | 17.8 | Yes | Yes | 20.7 | 19.9 | 0.8 | FE3322E873F24B6384A7239D2C1DAB77 |  | R22 | Non-TXV |  | 16.33% | 0.8367 | 31.38% | [5 empty] | Non-TXV | 16.33%
Bakersfield | CA | 93304-2406 |  | 2013-09-09 | 2013-09-09 19:12 | 2013-09-09 19:12 | BRYANT - 583BNW042060NC | 144 | 0 | Yes | Yes | 21.4 | 21.6 | -0.2 | 728C9A127D774B8D98917626B2F4C35C | Add refrigerant: 5.5 oz | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2369 |  | 2013-07-17 | 2013-07-17 22:42 | 2013-07-17 23:01 | ARCOAIRE - PGAA42E115B | 70 | 3.7 | Yes | Yes | 24.1 | 21.5 | 2.6 | EC430FE9EEA04CC3B7EEE67F79E57F86 |  | R22 | Non-TXV |  | 5.286% | 0.94714 | 10.16% | [5 empty] | Non-TXV | 5.286%
Bakersfield | CA | 93306-6650 |  | 2013-06-28 | 2013-06-28 14:10 | 2013-06-28 17:17 | HEIL - 1487C50535 | 85 | -5 | Yes | Yes | 20.5 | 16.3 | 4.2 | 9E7102A1449440BFA1EBA9AA392AFE2A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
San Jose | CA | 95125-6250 |  | 2013-09-25 | 2013-09-25 15:30 | 2013-09-25 16:11 | NORDYNE - JS3BA D42KA | 86 | 3 | Yes | Yes | 21.1 | 21.3 | -0.1 | DBD69FF85D92495895EF2AF06E245EB3 |  | R22 | Non-TXV |  | 3.488% | 0.96512 | 6.704% | [5 empty] | Non-TXV | 3.488%
San Jose | CA | 95123-3416 |  | 2013-09-19 | 2013-09-19 17:34 | 2013-09-19 18:54 | PAYNE - PA10JA042-H | 81 | 2.5 | Yes | Yes | 29.4 | 23.7 | 5.7 | CBB1A12FDE7D433B882E17353E2134B6 |  | R22 | Non-TXV |  | 3.086% | 0.96914 | 5.931% | [5 empty] | Non-TXV | 3.086%
Bakersfield | CA | 93307-7234 |  | 2013-07-24 | 2013-07-24 12:01 | 2013-07-24 13:47 | BRYANT - 56101042 | 85 | 2.7 | Yes | Yes | 19.1 | 22.1 | -3 | 20BD7BF23762412FBA5BD9113CB7B58E |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93307-6052 |  | 2013-08-23 | 2013-08-23 06:53 | 2013-08-23 07:14 | BRYANT - 4504E50511 | 85 | 3.1 | Yes | Yes | 17.4 | 20.4 | -3 | A6E98B012BFC4C66B00C7AFF1B94D9C2 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Bakersfield | CA | 93307-7098 |  | 2013-07-01 | 2013-07-01 11:40 | 2013-07-01 12:12 | YORK - AC033X1021A | 63 | 1.9 | Yes | Yes | 16.2 | 19.2 | -3 | 550DE43C8DFD40CEA03054017099892C |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Bakersfield | CA | 93304-4942 |  | 2013-06-26 | 2013-06-26 10:23 | 2013-06-26 11:02 | DAY & NIGHT - NA | 85 | 4.8 | Yes | Yes | 16.8 | 18.6 | -1.8 | 906EF42D080542BDACCE9E6BEFF4FF11 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Bakersfield | CA | 93311-2161 |  | 2013-07-11 | 2013-07-11 11:20 | 2013-07-11 11:48 | LENNOX - 13ACD-030-230-02 | 111 | 25.2 | Yes | Yes | 17.1 | 20.1 | -3 | 2E975D6D583B477CB84334A12AC2242B |  | R22 | Non-TXV |  | 22.7% | 0.77297 | 43.63% | [5 empty] | Non-TXV | 22.7%
Bakersfield | CA | 93311-2161 |  | 2013-07-11 | 2013-07-11 11:50 | 2013-07-11 12:14 | LENNOX - 13ACD-030-230-02 | 111 | 5.6 | Yes | Yes | 24 | 19.6 | 4.4 | B89F8B56C51D476DAEDD3DECEB673212 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.045% | 0.94955 | 9.695% | [5 empty] | Non-TXV | 5.045%
Anderson | CA | 96007-2746 |  | 2013-07-08 | 2013-07-08 18:01 | 2013-07-08 18:44 | COLEMAN - ILLEGIBLE | 159 | 52.9 | Yes | Yes | 25.8 | 20.8 | 5 | 3A69CCCDF30749DBAB470C90B423F414 |  | R22 | Non-TXV |  | 33.27% | 0.6673 | 63.94% | [5 empty] | Non-TXV | 33.27%
Bakersfield | CA | 93304-7266 |  | 2013-07-16 | 2013-07-16 13:52 | 2013-07-16 14:19 | DAY & NIGHT - 585EJ036075 | 82 | 3.4 | Yes | Yes | 22.5 | 17.9 | 4.6 | 18F8BBA5DBEB4EA4BAE7F8CFDE6D75F2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Novato | CA | 94949-8242 |  | 2013-09-17 | 2013-09-17 09:31 | 2013-09-17 09:31 | CARRIER - 38CKC060300 | 233 | 0 | Yes | Yes | 22.7 | 18.2 | 4.5 | 2CC6BC1068784FAC8D9ACE5504ACF1B7 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3505 |  | 2013-06-25 | 2013-06-25 10:57 | 2013-06-25 11:19 | YORK - D1NH060N9006B | 136 | -8 | Yes | Yes | 22.6 | 19.1 | 3.5 | ED12425C5BD840B38586AF2A1B2C92A9 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
American Canyon | CA | 94503-3129 |  | 2013-07-30 | 2013-07-30 11:48 | 2013-07-30 11:49 | CARRIER - 38CKC060370 | 131 | 6.6 | Yes | Yes | 18.8 | 17 | 1.8 | A12081B3BFC44CBDB26BB86CA09B5887 |  | R22 | Non-TXV |  | 5.038% | 0.94962 | 9.682% | [5 empty] | Non-TXV | 5.038%
San Jose | CA | 95120-2858 |  | 2013-09-30 | 2013-09-30 15:56 | 2013-09-30 16:16 | CARRIER - 38CKC030330 | 66 | 3 | Yes | Yes | 22.7 | 21.5 | 1.2 | 3CD3384392FF47479A63070D5C4D5149 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Vallejo | CA | 94591-7725 |  | 2013-06-27 | 2013-06-27 13:24 | 2013-06-27 14:42 | HEIL - HAC030AKA1 | 74 | -7 | Yes | Yes | 15.2 | 15.5 | -0.3 | 6AE1EE147E10456DA04492D2A27FC9FC |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Bakersfield | CA | 93309-3975 |  | 2013-07-25 | 2013-07-25 12:59 | 2013-07-25 13:45 | ICP - PCD330060K001C1 | 100 | 11.8 | Yes | Yes | 21.2 | 19.8 | 1.4 | 4A1BB279DEDD42EC87489880C82B64DC |  | R410A | TXV |  | 11.8% | 0.882 | 22.68% | [5 empty] | TXV | 11.8%
San Jose | CA | 95124-3601 |  | 2013-07-19 | 2013-07-19 10:08 | 2013-07-19 10:43 | INTERTHERM - UNK | 85 | 3.9 | Yes | Yes | 16.6 | 18.7 | -2.1 | B27F75519B1E450B84EF7B6ADAF1C432 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93308-7859 |  | 2013-08-05 | 2013-08-05 11:40 | 2013-08-05 12:18 | YORK - DAYH-F036N070C | 108 | 3.6 | Yes | Yes | 20 | 21 | -1 | D411C3E267624B408135F18E20C5D848 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93304-2136 |  | 2013-07-16 | 2013-07-16 13:38 | 2013-07-16 14:10 | HEIL - PGF336060K01 | 146 | 13 | Yes | Yes | 26.8 | 22 | 4.8 | 3955B5D4F3C84FE591D269E8E9B9FB45 |  | R22 | Non-TXV |  | 8.904% | 0.91096 | 17.11% | [5 empty] | Non-TXV | 8.904%
Woodland | CA | 95695-2728 |  | 2013-07-12 | 2013-07-12 10:30 | 2013-07-12 10:52 | TRANE - 2TTB0042A1000AA | 95 | -4.9 | Yes | Yes | 16.5 | 19.5 | -3 | CFF9827220C34D09990C90A49E99B60C |  | R22 | Non-TXV |  | -5.158% | 1.0516 | 1.444% |  |  |  |  | Non-TXV |  |  | -5.158%
Bakersfield | CA | 93309-2168 |  | 2013-07-05 | 2013-07-05 11:40 | 2013-07-05 12:20 | RUUD - N/A | 85 | 20.6 | Yes | Yes | 21.3 | 20.4 | 0.9 | 3235DB06BB7E491CB470976B9469208E |  | R22 | Non-TXV |  | 24.24% | 0.75765 | 46.57% | [5 empty] | Non-TXV | 24.24%
Antioch | CA | 94531-8125 |  | 2013-07-09 | 2013-07-09 08:55 | 2013-07-09 08:56 | GOODMAN - GSX130601BA | 125 | 3.8 | Yes | Yes | 15.6 | 17 | -1.4 | 91C95333C3AC40EFB3FBE12D5293B471 |  | R410A | Non-TXV |  | 3.04% | 0.9696 | 5.842% | [5 empty] | Non-TXV | 3.04%
Fairfield | CA | 94534-4156 |  | 2013-07-18 | 2013-07-18 09:53 | 2013-07-18 10:42 | GIBSON - JS3BC-042KA | 104 | -5.3 | Yes | Yes | 14.9 | 15.2 | -0.3 | C5C9C7A4DE3146F6A0F0364DCC0BBA4F |  | R22 | Non-TXV |  | -5.096% | 1.051 | 1.427% |  |  |  |  | Non-TXV |  |  | -5.096%
Ukiah | CA | 95482-9414 |  | 2013-08-24 | 2013-08-24 10:36 | 2013-08-24 10:57 | COLEMAN - 7836-301 | 72 | 23 | Yes | Yes | 24.4 | 21.2 | 3.3 | 3F209CD011834E4C82991D1E2E719E0F |  | R22 | Non-TXV |  | 31.94% | 0.68056 | 61.39% | [5 empty] | Non-TXV | 31.94%
Anderson | CA | 96007-4625 |  | 2013-07-09 | 2013-07-09 12:24 | 2013-07-09 12:48 | ICP - PGF336080K01A1 | 176 | 11.6 | Yes | Yes | 25.5 | 22.5 | 3 | 1776FEDD86FD40ABBCB9EFF84EB60F8B |  | R22 | Non-TXV |  | 6.591% | 0.93409 | 12.67% | [5 empty] | Non-TXV | 6.591%
Shafter | CA | 93263-2313 |  | 2013-07-24 | 2013-07-24 20:12 | 2013-07-24 20:52 | GOODMAN - GPG13360701AA | 100 | 3.3 | Yes | Yes | 21.1 | 21.5 | -0.4 | 875A12E30C20468BB085628BB9E16530 |  | R22 | Non-TXV |  | 3.3% | 0.967 | 6.342% | [5 empty] | Non-TXV | 3.3%
Shafter | CA | 93263-2414 |  | 2013-10-22 | 2013-10-22 17:20 | 2013-10-22 17:23 | YORK - DBYP-F036N070A | 108 | 6.2 | Yes | Yes | 26.2 | 21.3 | 4.9 | 18FA61B275CB4E388016B5AC51283011 |  | R22 | TXV |  | 5.741% | 0.94259 | 11.03% | [5 empty] | TXV | 5.741%
San Jose | CA | 95148-4332 |  | 2013-07-16 | 2013-07-16 12:09 | 2013-07-16 12:36 | NORDYNE - JS3BC-042KA | 85 | 9.1 | Yes | Yes | 22.7 | 17.9 | 4.8 | 8B1EE13105B44BCDAB2569D2DC2424C0 |  | R22 | Non-TXV |  | 10.71% | 0.89294 | 20.57% | [5 empty] | Non-TXV | 10.71%
San Jose | CA | 95148-4332 |  | 2013-07-16 | 2013-07-16 12:38 | 2013-07-16 13:03 | NORDYNE - JS3BC-036KA | 85 | 6.1 | Yes | Yes | 22 | 19.3 | 2.7 | BC2C0DFBA4944608B1DD1491D5A63D4B |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Livermore | CA | 94551-8764 |  | 2013-09-13 | 2013-09-13 13:30 | 2013-09-13 13:30 | CARRIER - 38CKC060300 | 159 | 0 | Yes | Yes | 17.4 | 20.1 | -2.7 | 0094EBF5A2924EF89B2752B86CCF78F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-3596 |  | 2013-07-11 | 2013-07-11 13:20 | 2013-07-11 13:56 | RHEEM - ILLEGIBLE | 85 | 10.8 | Yes | Yes | 26.9 | 21 | 5.9 | D72E3F882AE24C0CA3CF6B7889B77E80 |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
San Jose | CA | 95128-3654 |  | 2013-10-15 | 2013-10-15 11:05 | 2013-10-15 11:30 | TRANE - TTN030C100CA | 87 | -7.2 | Yes | Yes | 22.3 | 20.9 | 1.4 | DED724D04760449282F46C8111E98105 |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Bakersfield | CA | 93308-7859 |  | 2013-08-05 | 2013-08-05 10:34 | 2013-08-05 11:38 | YORK - D1NH030N03006C | 73 | 2.2 | Yes | Yes | 21.5 | 19.9 | 1.6 | 30B42D679DA6485182C610519A9D75FB |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Santa Rosa | CA | 95407-5025 |  | 2013-07-11 | 2013-07-11 13:47 | 2013-07-11 13:47 | OTHER - HABA-F048SD | 117 | 20.4 | Yes | Yes | 18 | 20.2 | -2.2 | 535A15762A11446FA8902296972C92B2 | Add refrigerant: 20.4 oz | R22 | Non-TXV |  | 17.44% | 0.82564 | 33.51% | [5 empty] | Non-TXV | 17.44%
San Jose | CA | 95133-2010 |  | 2013-07-22 | 2013-07-22 13:29 | 2013-07-22 14:12 | CARRIER - 38CKC024---341 | 59 | 6.6 | Yes | Yes | 17 | 19.5 | -2.5 | 9BD8D4BFD8C0433CAB10C860D29139A1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.19% | 0.88814 | 21.5% | [5 empty] | Non-TXV | 11.19%
Bakersfield | CA | 93306-6723 |  | 2013-07-22 | 2013-07-22 12:42 | 2013-07-22 13:25 | YORK - UNK | 85 | 2.5 | Yes | Yes | 16.6 | 19.5 | -2.9 | D2959884D0244EEC84D41A118CFB50BD |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93307-1266 |  | 2013-06-28 | 2013-06-28 11:40 | 2013-06-28 13:06 | PAYNE - PY1PNB024040AAAA | 56 | 0 | Yes | Yes | 21 | 19.1 | 1.9 | 1122E24CB4394695B00ABE0E0827985D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corcoran | CA | 93212-2006 |  | 2013-07-11 | 2013-07-11 14:44 | 2013-07-11 15:20 | RHEEM - UNK | 72 | 22.6 | Yes | Yes | 20.2 | 19.9 | 0.3 | 36CD309CC41D4CFCA9A625DBAA05E639 |  | R22 | Non-TXV |  | 31.39% | 0.68611 | 60.32% | [5 empty] | Non-TXV | 31.39%
Mc Farland | CA | 93250-0000 |  | 2013-07-31 | 2013-07-31 21:35 | 2013-07-31 21:53 | GOODMAN - PGB0420751A | 68 | 9.7 | Yes | Yes | 22 | 20.4 | 1.6 | 259A6C6292464A7C8E6E5ACDB38860EF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.26% | 0.85735 | 27.41% | [5 empty] | Non-TXV | 14.26%
Bakersfield | CA | 93312-5133 |  | 2013-07-15 | 2013-07-15 21:44 | 2013-07-15 22:06 | PAYNE - PA13NR060AAAA | 85 | 3.4 | Yes | Yes | 21 | 22.6 | -1.6 | 4F34271071BF4468A1284B28288B5191 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Ukiah | CA | 95482-8769 |  | 2013-08-23 | 2013-08-23 12:36 | 2013-08-23 13:37 | AMERICAN STANDARD - 2A7A3048A1000AA | 142 | 16.4 | Yes | Yes | 24.9 | 20.4 | 4.5 | 02BBA8AC054242B3872CA4D584869426 |  | R22 | TXV |  | 11.55% | 0.88451 | 22.2% | [5 empty] | TXV | 11.55%
Novato | CA | 94949-6282 |  | 2013-09-17 | 2013-09-17 10:50 | 2013-09-17 10:50 | CARRIER - 38CKC042300 | 85 | 0 | Yes | Yes | 20.9 | 16.4 | 4.5 | B446D7E908814978A487B82346EF3C78 |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8406 |  | 2013-07-10 | 2013-07-10 14:36 | 2013-07-10 15:09 | RHEEM - UKN | 86 | 18.6 | Yes | Yes | 16.5 | 19.5 | -3 | C5029FAEAFE8417FBF268EB6C207024F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 21.63% | 0.78372 | 41.56% | [5 empty] | Non-TXV | 21.63%
Arvin | CA | 93203-1806 |  | 2013-07-24 | 2013-07-24 14:47 | 2013-07-24 15:22 | YORK - D1NA036N05606C | 67 | 3.7 | Yes | Yes | 18.2 | 20.9 | -2.7 | A0AB1BDE72F34BB58D0C45CE91A2DCDA |  | R22 | Non-TXV |  | 5.522% | 0.94478 | 10.61% | [5 empty] | Non-TXV | 5.522%
Bakersfield | CA | 93308-6476 |  | 2013-08-02 | 2013-08-02 17:09 | 2013-08-02 17:12 | RHEEM - N/A | 85 | -7.1 | Yes | Yes | 28.4 | 22.6 | 5.8 | 4F566E0F487B4148B00151CBF7C2C0D2 |  | R22 | Non-TXV |  | -8.353% | 1.0835 | 2.339% |  |  |  |  | Non-TXV |  |  | -8.353%
Dublin | CA | 94568-8823 |  | 2013-09-12 | 2013-09-12 13:41 | 2013-09-12 13:43 | CARRIER - 38CKC060300 | 152 | 15.6 | Yes | Yes | 18.4 | 17.9 | 0.5 | 758326C2DA2E4D5DBB1C84DE50F510F1 |  | R22 | Non-TXV |  | 10.26% | 0.89737 | 19.72% | [5 empty] | Non-TXV | 10.26%
Suisun City | CA | 94534-1433 |  | 2013-07-12 | 2013-07-12 12:48 | 2013-07-12 15:26 | LENNOX - HS9-511-3P | 106 | 3.7 | Yes | Yes | 12 | 13 | -1 | 128431A2BDFB44969DFCE0F0C72A08B4 |  | R22 | Non-TXV |  | 3.491% | 0.96509 | 6.708% | [5 empty] | Non-TXV | 3.491%
Vacaville | CA | 95688-1013 |  | 2013-06-27 | 2013-06-27 13:08 | 2013-06-27 13:31 | GOODMAN - | 85 | 3.1 | Yes | Yes | 16.1 | 18.7 | -2.6 | 2C42C89D647C43C1AE8743744FDFB184 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Suisun City | CA | 94585-2267 |  | 2013-07-09 | 2013-07-09 15:17 | 2013-07-09 15:39 | TRANE - 2TTBOO42A1000AA | 95 | -4 | Yes | Yes | 14 | 15.9 | -1.9 | B6C044E9D60744E6AE47651DF12732C3 |  | R22 | Non-TXV |  | -4.211% | 1.0421 | 1.179% |  |  |  |  | Non-TXV |  |  | -4.211%
Morgan Hill | CA | 95037-9062 |  | 2013-10-23 | 2013-10-23 14:56 | 2013-10-23 15:40 | NORDYNE - F3BA 60 | 114 | 5.4 | Yes | Yes | 20.4 | 21.2 | -0.8 | 3A6506CF8EE245E483C5EB72B636F5ED |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Arvin | CA | 93203-2814 |  | 2013-08-19 | 2013-08-19 10:05 | 2013-08-19 10:29 | GOODMAN - UNK | 89 | 3.2 | Yes | Yes | 22.3 | 20.8 | 1.5 | 43383B6C628F4165B265D7D2873CD449 |  | R22 | Non-TXV |  | 3.596% | 0.96404 | 6.91% | [5 empty] | Non-TXV | 3.596%
Fairfield | CA | 94534-2952 |  | 2013-07-19 | 2013-07-19 12:12 | 2013-07-19 15:22 | YORK - TCGD60S21S2A | 84 | -5.9 | Yes | Yes | 20.1 | 20.8 | -0.7 | 4D1B1A3D3CF64B9FA7D923B4CF96C853 |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
San Jose | CA | 95135-2211 |  | 2013-09-30 | 2013-09-30 17:15 | 2013-09-30 17:57 | CARRIER - 38CKB060300 | 154 | -10.9 | Yes | Yes | 19.6 | 19.3 | 0.3 | 947E71F592A044CAA75FE2AED9D60D53 |  | R22 | Non-TXV |  | -7.078% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.078%
Bakersfield | CA | 93308-1334 |  | 2013-07-02 | 2013-07-02 10:13 | 2013-07-02 10:13 | CARRIER - N/A | 85 | 3.3 | Yes | Yes | 20.4 | 22.6 | -2.2 | 08E362626691486DAD5ABC9E604BC110 | Add refrigerant: 3.3 oz | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Sunnyvale | CA | 94085-3610 |  | 2013-09-27 | 2013-09-27 14:25 | 2013-09-27 14:59 | CARRIER - 38CKC024320 | 72 | 2.5 | Yes | Yes | 27.1 | 21.5 | 5.6 | 013B37DE5362450BA30002BE522ABC3A |  | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Bakersfield | CA | 93308-7883 |  | 2013-08-13 | 2013-08-13 11:12 | 2013-08-13 11:33 | GOODMAN - GPG10360701A | 85 | 8.2 | Yes | Yes | 18.2 | 21.2 | -3 | 9F105A6F059C4A8EA32E3BE72137D69B |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Bakersfield | CA | 93308-4772 |  | 2013-08-21 | 2013-08-21 19:26 | 2013-08-21 19:29 | COMFORT AIRE - GPCM024K0400 | 54 | 4.9 | Yes | Yes | 16.3 | 19.3 | -3 | 2175E917C6A04653B414EDA7D096CAFB |  | R22 | Non-TXV |  | 9.074% | 0.90926 | 17.44% | [5 empty] | Non-TXV | 9.074%
Bakersfield | CA | 93311-2861 |  | 2013-08-10 | 2013-08-10 12:35 | 2013-08-10 12:51 | RHEEM - RAMA-042JAZ | 94 | 7.9 | Yes | Yes | 25.5 | 21 | 4.5 | A03322E979354BBF8112D41004B48C28 |  | R22 | Non-TXV |  | 8.404% | 0.91596 | 16.15% | [5 empty] | Non-TXV | 8.404%
Bakersfield | CA | 93311-2861 |  | 2013-08-10 | 2013-08-10 12:52 | 2013-08-10 13:56 | RHEEM - ILLEGIBLE | 94 | 13.5 | Yes | Yes | 24.4 | 21 | 3.4 | 2DB62E021F664E2AAE6727B085D78B78 |  | R22 | Non-TXV |  | 14.36% | 0.85638 | 27.6% | [5 empty] | Non-TXV | 14.36%
Anderson | CA | 96007-3703 |  | 2013-07-08 | 2013-07-08 10:29 | 2013-07-08 10:49 | AMERICAN STANDARD - 2A7A4036B1000AA | 118 | 3.9 | Yes | Yes | 20.3 | 15.5 | 4.8 | D590CAA4D8234261BD0F3B5FA0CF132C |  | R22 | Non-TXV |  | 3.305% | 0.96695 | 6.352% | [5 empty] | Non-TXV | 3.305%
Bakersfield | CA | 93308-8026 |  | 2013-07-03 | 2013-07-03 14:29 | 2013-07-03 15:12 | TEMPSTAR - N/A | 85 | 4.4 | Yes | Yes | 20 | 20.4 | -0.4 | 8CBBB73CE9F74C93B2CA08DA9FDB4989 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Bakersfield | CA | 93313-4936 |  | 2013-07-15 | 2013-07-15 14:26 | 2013-07-15 14:49 | OTHER - AC042X1021A | 84 | 5.5 | Yes | Yes | 18.5 | 20.5 | -2 | 23070E7260AC4DA3BA6952F7A1878E90 |  | R22 | TXV |  | 6.548% | 0.93452 | 12.58% | [5 empty] | TXV | 6.548%
Bakersfield | CA | 93306-1403 |  | 2013-06-28 | 2013-06-28 11:09 | 2013-06-28 17:14 | RUUD - NA | 85 | 3.2 | Yes | Yes | 21 | 19.9 | 1.1 | 96982FBF61F244759C5B0534ADF1E61E |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Bakersfield | CA | 93313-4909 |  | 2013-07-15 | 2013-07-15 17:06 | 2013-07-15 17:25 | OTHER - EAFF-03754Z | 85 | 4.1 | Yes | Yes | 19 | 18.8 | 0.2 | C9B091C512F34701AEAAF9622ECDCE98 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Bakersfield | CA | 93307-2346 |  | 2013-07-17 | 2013-07-17 08:41 | 2013-07-17 09:37 | YORK - D1NH036N05606C | 108 | 7.7 | Yes | Yes | 21.4 | 19.8 | 1.6 | B8CA712520134C9184C18B9CDA9E1675 |  | R22 | Non-TXV |  | 7.13% | 0.9287 | 13.7% | [5 empty] | Non-TXV | 7.13%
Willits | CA | 95490-4167 |  | 2013-08-19 | 2013-08-19 11:05 | 2013-08-19 11:23 | ALLEGIANCE - 7A0036A100A0 | 106 | -6.2 | Yes | Yes | 23.6 | 20.7 | 2.9 | 271271DE8D644547954C2011D3B0FC8D |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Fairfield | CA | 94533-1471 |  | 2013-08-02 | 2013-08-02 10:58 | 2013-08-02 13:47 | DAY & NIGHT - N2A336AKB300 | 86 | 2.5 | Yes | Yes | 14.7 | 17.7 | -3 | F8C6463373AE48F1AE21D20C74FD54C0 |  | R22 | Non-TXV |  | 2.907% | 0.97093 | 5.587% | [5 empty] | Non-TXV | 2.907%
Bakersfield | CA | 93312-6609 |  | 2013-07-26 | 2013-07-26 12:15 | 2013-07-26 13:14 | YORK - ACO48X1021A | 117 | -4.4 | Yes | Yes | 20.5 | 20.4 | 0.1 | A54D6DC5893A4876B4EDD85DE70FFCA9 |  | R22 | TXV |  | -3.761% | 1.0376 | 1.053% |  |  |  |  | TXV |  |  | -3.761%
Arvin | CA | 93203-1125 |  | 2013-07-22 | 2013-07-22 11:54 | 2013-07-22 12:25 | BRYANT - 582ANW030040AAAD | 55 | 6.1 | Yes | Yes | 27.9 | 22.1 | 5.8 | 78F8B083FA6A4F728E397F9DFA14C02A |  | R22 | Non-TXV |  | 11.09% | 0.88909 | 21.31% | [5 empty] | Non-TXV | 11.09%
Vacaville | CA | 95688-2029 |  | 2013-07-02 | 2013-07-02 11:35 | 2013-07-02 12:05 | GE - BGTA736B1B | 118 | 12.3 | Yes | Yes | 25.7 | 20.4 | 5.3 | 658FBAB9ABD747B1873D24CD14A1162A |  | R22 | Non-TXV |  | 10.42% | 0.89576 | 20.03% | [5 empty] | Non-TXV | 10.42%
Bakersfield | CA | 93313-4910 |  | 2013-07-15 | 2013-07-15 12:53 | 2013-07-15 13:39 | OTHER - EAFF-043JAZ | 85 | 2.7 | Yes | Yes | 17.9 | 19.2 | -1.3 | 6099759699D84BFBBC9EB127AB0A5647 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93313-6076 |  | 2013-07-19 | 2013-07-19 14:46 | 2013-07-19 15:23 | ARCOAIRE - PGAA36C1K6 | 69 | 6.7 | Yes | Yes | 27.5 | 23.2 | 4.4 | D65AF3E680BE4BE1B3F65E8A7E87069A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.71% | 0.9029 | 18.66% | [5 empty] | Non-TXV | 9.71%
Bakersfield | CA | 93313-4380 |  | 2013-07-16 | 2013-07-16 09:01 | 2013-07-16 09:20 | HEIL - CA5536VKA1 | 85 | 2.6 | Yes | Yes | 19.5 | 19.8 | -0.3 | 10AA8310B2C749B5A4AB4424C3F9639A |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93307-7647 |  | 2013-07-17 | 2013-07-17 17:21 | 2013-07-17 17:52 | YORK - D1N030N05606C | 73 | 4.5 | Yes | Yes | 21 | 20.4 | 0.6 | 7CD399E98E4A412481C395C9A4166BE9 |  | R22 | Non-TXV |  | 6.164% | 0.93836 | 11.85% | [5 empty] | Non-TXV | 6.164%
Walnut Creek | CA | 94596-6134 |  | 2013-07-18 | 2013-07-18 13:04 | 2013-07-18 13:05 | ALLEGIANCE - 7A0042A100A1 | 86 | -6.1 | Yes | Yes | 18.7 | 17.9 | 0.8 | 86DE62E0E2464D4A8E15929ED47EC0E6 |  | R22 | Non-TXV |  | -7.093% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.093%
Bakersfield | CA | 93313-4912 |  | 2013-07-24 | 2013-07-24 09:07 | 2013-07-24 09:49 | OTHER - EAFF042JAZ | 99 | 8.4 | Yes | Yes | 23.5 | 19.9 | 3.6 | F27600E5E5F444DA8E73C2C492145CD9 |  | R22 | TXV |  | 8.485% | 0.91515 | 16.31% | [5 empty] | TXV | 8.485%
Fairfield | CA | 94534-1742 |  | 2013-07-18 | 2013-07-18 10:40 | 2013-07-18 12:51 | GIBSON - KS3BD-048K | 143 | 4.6 | Yes | Yes | 17.8 | 17.7 | 0.1 | D83033A85D1646A5B324156F69DC38E5 |  | R22 | Non-TXV |  | 3.217% | 0.96783 | 6.182% | [5 empty] | Non-TXV | 3.217%
Bakersfield | CA | 93309-2931 |  | 2013-10-17 | 2013-10-17 04:55 | 2013-10-17 05:13 | GOODMAN - GPG1336045M91CA | 85 | 5.5 | Yes | Yes | 24.4 | 18.6 | 5.9 | E3D5134F696043CC9C3C6E9A6DEA7010 |  | R410A | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Bakersfield | CA | 93305-2042 |  | 2013-07-16 | 2013-07-16 12:20 | 2013-07-16 12:44 | YORK - DINH030N05606C | 73 | 4.1 | Yes | Yes | 24 | 20.2 | 3.9 | 08CA70EAC9BA48499AD9602E49DA3CA2 |  | R22 | Non-TXV |  | 5.616% | 0.94384 | 10.79% | [5 empty] | Non-TXV | 5.616%
Shafter | CA | 93263-1735 |  | 2013-07-22 | 2013-07-22 19:45 | 2013-07-22 20:11 | BRYANT - 561GJ036-D | 84 | 3.2 | Yes | Yes | 20.9 | 23.7 | -2.8 | 6FA13EA70D9349B9860DFB5568775C09 |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Cottonwood | CA | 96022-8908 |  | 2013-06-25 | 2013-06-25 15:40 | 2013-06-25 17:07 | BDP - 588ANW030040 | 53 | 4.5 | Yes | Yes | 19.5 | 21.2 | -1.7 | B534AB1BE1834E64A1EC02226DC6AEF2 |  | R22 | Non-TXV |  | 8.491% | 0.91509 | 16.32% | [5 empty] | Non-TXV | 8.491%
Fremont | CA | 94536-4711 |  | 2013-07-01 | 2013-07-01 09:32 | 2013-07-01 09:52 | CARRIER - 561CJ030-C | 139 | 17.5 | Yes | Yes | 25.7 | 19.8 | 5.9 | F42D668D90DE4645A73418E95E1D7093 |  | R22 | Non-TXV |  | 12.59% | 0.8741 | 24.2% | [5 empty] | Non-TXV | 12.59%
Bakersfield | CA | 93308-1245 |  | 2013-07-02 | 2013-07-02 12:08 | 2013-07-02 12:31 | PAYNE - PY1PNB060090AAAA | 116 | 7.3 | Yes | Yes | 17 | 19.9 | -2.9 | BC2E18F5E6844E638E3CA5AE44F848F1 |  | R22 | Non-TXV |  | 6.293% | 0.93707 | 12.09% | [5 empty] | Non-TXV | 6.293%
Vacaville | CA | 95687-5716 |  | 2013-06-27 | 2013-06-27 12:12 | 2013-06-27 12:12 | BRYANT - 561CJ036-E | 73 | 0 | Yes | Yes | 13.4 | 16.3 | -2.9 | 002E6F89D9D74261990A97742532FB65 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-6401 |  | 2013-07-16 | 2013-07-16 13:08 | 2013-07-16 13:23 | BRYANT - 561CJ036-F | 124 | 6 | Yes | Yes | 23 | 17.2 | 5.8 | C130AA03943F474187AACA0002AABCE4 |  | R22 | TXV |  | 4.839% | 0.95161 | 9.299% | [5 empty] | TXV | 4.839%
San Jose | CA | 95122-3181 |  | 2013-09-17 | 2013-09-17 16:39 | 2013-09-17 19:37 | OTHER - CA369D | 112 | 3.7 | Yes | Yes | 19.4 | 20.9 | -1.5 | F335A2C8A3BE43B39FFC99C10A2669CD |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Arvin | CA | 93203-2750 |  | 2013-08-11 | 2013-08-11 09:42 | 2013-08-11 10:07 | ICP - PGC036K060B | 71 | 3.6 | Yes | Yes | 25.4 | 20.4 | 5 | 9C67A703B6464040BC45262DFDAC573D |  | R22 | Non-TXV |  | 5.07% | 0.9493 | 9.744% | [5 empty] | Non-TXV | 5.07%
Bakersfield | CA | 93308-7866 |  | 2013-08-02 | 2013-08-02 09:24 | 2013-08-02 11:08 | GOODMAN - CKL-49-1 | 85 | 2.8 | Yes | Yes | 16.5 | 19.5 | -3 | 9FF8DB5EA03F43809844C24EE5A59D57 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fairfield | CA | 94534-1035 |  | 2013-07-17 | 2013-07-17 13:17 | 2013-07-17 13:17 | MONTGOMERY WARD - UKN | 85 | 0 | Yes | Yes | 14.6 | 16.9 | -2.2 | 6CC976F35C064C18B183F6361433D106 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1887 |  | 2013-10-09 | 2013-10-09 11:01 | 2013-10-09 11:30 | BRYANT - 561CJ048-A | 102 | 21.5 | Yes | Yes | 23.4 | 21.7 | 1.7 | 66BB248A22534324BCE3745ECE6B43F6 |  | R22 | Non-TXV |  | 21.08% | 0.78922 | 40.51% | [5 empty] | Non-TXV | 21.08%
Bakersfield | CA | 93307-7098 |  | 2013-07-24 | 2013-07-24 09:52 | 2013-07-24 10:54 | OTHER - AC036X1021A | 63 | 16.3 | Yes | Yes | 17.3 | 20.2 | -2.9 | 0E794FE7A2E34FB0BE0DC7E9B3143494 |  | R22 | Non-TXV |  | 25.87% | 0.74127 | 49.72% | [5 empty] | Non-TXV | 25.87%
Vacaville | CA | 95688-2328 |  | 2013-07-02 | 2013-07-02 10:55 | 2013-07-02 11:27 | TRANE - 2TTB3048A1000AA | 142 | 0 | Yes | Yes | 16.5 | 18.2 | -1.7 | 30871CBF50D244A6B6D52F69E7F16E34 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3435 |  | 2013-08-21 | 2013-08-21 19:33 | 2013-08-21 19:33 | TEMPSTAR - N/A | 85 | -8 | Yes | Yes | 0 | 10.8 | -10.8 | 30B8EF7B949C4654824A01446941F91C | Remove refrigerant: 8 oz Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
San Jose | CA | 95127-4922 |  | 2013-09-19 | 2013-09-19 09:54 | 2013-09-19 10:28 | GOODMAN - GBC130601BC | 169 | 9.3 | Yes | Yes | 21.4 | 18.7 | 2.7 | 4AC9A884B71341C98E8EBE76910D4EF3 |  | R22 | Non-TXV |  | 5.503% | 0.94497 | 10.58% | [5 empty] | Non-TXV | 5.503%
Bakersfield | CA | 93308-2123 |  | 2013-07-02 | 2013-07-02 17:42 | 2013-07-02 18:06 | PAYNE - N/A | 70 | 8.2 | Yes | Yes | 21 | 20.4 | 0.6 | ED99EC90CE0C467B862D474DE759C9B1 |  | R410A | TXV |  | 11.71% | 0.88286 | 22.51% | [5 empty] | TXV | 11.71%
Santa Rosa | CA | 95404-6127 |  | 2013-07-05 | 2013-07-05 10:46 | 2013-07-05 11:10 | TRANE - 2TTB0048A1000AA | 109 | -7.3 | Yes | Yes | 21.7 | 19.5 | 2.2 | F8E40B7369A14F28AC7C718737B544CA |  | R22 | Non-TXV |  | -6.697% | 1.067 | 1.876% |  |  |  |  | Non-TXV |  |  | -6.697%
Pleasanton | CA | 94566-8648 |  | 2013-09-18 | 2013-09-18 10:21 | 2013-09-18 10:59 | TRANE - TTD760B100A0 | 129 | 16.6 | Yes | Yes | 20.1 | 17.2 | 2.9 | 0A46259B75B640AC80376E8F99399E29 |  | R22 | Non-TXV |  | 12.87% | 0.87132 | 24.73% | [5 empty] | Non-TXV | 12.87%
Bakersfield | CA | 93307-5904 |  | 2013-07-17 | 2013-07-17 18:20 | 2013-07-17 18:20 | AMERICAN STANDARD - YCY042G1M0AD | 148 | 0 | Yes | Yes | 24.1 | 20.7 | 3.4 | 7B4B31218184483699E0C9E32B2358F3 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6647 |  | 2013-06-27 | 2013-06-27 17:57 | 2013-06-27 18:28 | CARRIER - N/A | 85 | 10.2 | Yes | Yes | 23 | 20.7 | 2.3 | E2EA46CB15A24E1981E839F1D589D61F |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Livermore | CA | 94551-5408 |  | 2013-09-13 | 2013-09-13 12:59 | 2013-09-13 14:51 | CARRIER - 38CKC036350 | 74 | -5.2 | Yes | Yes | 13.2 | 15.8 | -2.6 | 523D64068B5347AC9FA0E897A92797B0 |  | R22 | Non-TXV |  | -7.027% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.027%
Oakland | CA | 94605-4443 |  | 2013-06-26 | 2013-06-26 11:48 | 2013-06-26 12:21 | CARRIER - UNK | 85 | 5.7 | Yes | Yes | 23.6 | 19.3 | 4.3 | 410797EA69D64071AD8D8A440DD6A71B |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Bakersfield | CA | 93313-5756 |  | 2013-07-19 | 2013-07-19 14:45 | 2013-07-19 15:24 | PAYNE - PA12NA036 | 100 | 16.8 | Yes | Yes | 24 | 22.2 | 1.9 | 13ADD0AAFE9D47E58BAF656B75A5BAEC |  | R22 | Non-TXV |  | 16.8% | 0.832 | 32.29% | [5 empty] | Non-TXV | 16.8%
San Jose | CA | 95122-1001 |  | 2013-07-19 | 2013-07-19 14:04 | 2013-07-19 14:04 | PAYNE - PA13NA036-B | 131 | 0 | Yes | Yes | 19.7 | 17.5 | 2.2 | 29C3ACB34C1F472F9E90A4FA6D276B4F |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2231 |  | 2013-09-18 | 2013-09-18 09:41 | 2013-09-18 11:10 | COPELAND - VSX13061AA | 69 | -4.1 | Yes | Yes | 20.4 | 21.7 | -1.3 | 5ABDF7120D164C388D54EB8E9FFC3870 |  | R410A | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Vacaville | CA | 95687-6152 |  | 2013-07-02 | 2013-07-02 12:11 | 2013-07-02 12:11 | CARRIER - 38CKC024330 | 113 | 0 | Yes | Yes | 22.2 | 19.5 | 2.7 | 47D110C1FBA840998BBAD0EBD7CA700A |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1010 |  | 2013-08-13 | 2013-08-13 12:16 | 2013-08-13 13:08 | RHEEM - RRNL-B030JK06X | 85 | 3 | Yes | Yes | 13 | 15.9 | -2.9 | D14BAB3F5B984A11A7F6589417972340 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Selma | CA | 93662-2634 |  | 2013-07-10 | 2013-07-10 14:46 | 2013-07-10 15:10 | WEATHER KING - UNK | 66 | 7.8 | Yes | Yes | 19.8 | 19.3 | 0.5 | 08A231F02ACE4C8EA56F83D7CC755767 |  | R22 | Non-TXV |  | 11.82% | 0.88182 | 22.71% | [5 empty] | Non-TXV | 11.82%
Los Molinos | CA | 96055-9786 |  | 2013-09-08 | 2013-09-08 09:07 | 2013-09-08 09:34 | YORK - H2RD036S06B | 96 | 11.6 | Yes | Yes | 24.6 | 21 | 3.6 | 2F0AD1C591E34F3D9DF4495099808760 |  | R22 | Non-TXV |  | 12.08% | 0.87917 | 23.22% | [5 empty] | Non-TXV | 12.08%
Fresno | CA | 93706-5941 |  | 2013-07-25 | 2013-07-25 12:13 | 2013-07-25 12:41 | RHEEM - RRNAB042JK08X | 104 | 12.4 | Yes | Yes | 24.8 | 20.7 | 4.1 | D2CC453570C44D91AA76C8CE49BDF85C |  | R22 | Non-TXV |  | 11.92% | 0.88077 | 22.91% | [5 empty] | Non-TXV | 11.92%
Woodland | CA | 95695-0000 |  | 2013-07-25 | 2013-07-25 10:50 | 2013-07-25 12:36 | OTHER - 38TKB48300 | 114 | 9.8 | Yes | Yes | 17 | 18.3 | -1.3 | C287B13956E2484EB93F16646BCC97AF |  | R22 | Non-TXV |  | 8.596% | 0.91404 | 16.52% | [5 empty] | Non-TXV | 8.596%
Fresno | CA | 93722-6756 |  | 2013-06-25 | 2013-06-25 15:55 | 2013-06-25 16:12 | YORK - D3N2042N06506NXA | 78 | 3.1 | Yes | Yes | 20 | 19.3 | 0.8 | A3FD7E76D79B451D8705EB9B253F5929 |  | R410A | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
Fresno | CA | 93725-1845 |  | 2013-06-25 | 2013-06-25 10:33 | 2013-06-25 11:08 | - GCGD4821S2A | 69 | 8 | Yes | Yes | 25 | 21 | 4 | 000A85BDA38044C194601A1D4BB9C6F2 |  | R22 | TXV |  | 11.59% | 0.88406 | 22.28% | [5 empty] | TXV | 11.59%
Fresno | CA | 93725-1838 |  | 2013-06-26 | 2013-06-26 22:20 | 2013-06-26 22:20 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 0ABDFED4F6574A91B549BC58A4FCD180 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1840 |  | 2013-07-31 | 2013-07-31 16:02 | 2013-07-31 16:36 | COLEMAN - ERCS0361BAG | 145 | 5.8 | Yes | Yes | 20.2 | 18.6 | 1.6 | EF2D4D6C58714F918290BB72C05BE1F6 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93705-2817 |  | 2013-07-06 | 2013-07-06 10:34 | 2013-07-06 11:14 | TRANE - 24CC3042A1064AA | 131 | -5.7 | Yes | Yes | 17.2 | 19.8 | -2.6 | BC78C65ABB0F474B8B9DAC5281A6A7A1 |  | R22 | TXV |  | -4.351% | 1.0435 | 1.219% |  |  |  |  | TXV |  |  | -4.351%
Pleasanton | CA | 94588-3445 |  | 2013-09-13 | 2013-09-13 10:21 | 2013-09-13 10:21 | YORK - H1RA024S06A | 49 | 0 | Yes | Yes | 21.1 | 17.4 | 3.7 | F3F0D24954FE449A8C78B9E0FD8F4C44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1452 |  | 2013-07-05 | 2013-07-05 08:44 | 2013-07-05 09:54 | GOODMAN - PGE10A48D100A-2A | 94 | 4.8 | Yes | Yes | 21.8 | 21.5 | 0.3 | 6F720DAA07284A519E795CC920735835 |  | R22 | Non-TXV |  | 5.106% | 0.94894 | 9.813% | [5 empty] | Non-TXV | 5.106%
Bakersfield | CA | 93308-5614 |  | 2013-08-02 | 2013-08-02 16:53 | 2013-08-02 17:02 | OTHER - 38TH036300 | 90 | 4.5 | Yes | Yes | 20.1 | 21 | -0.9 | F0301176B01A40DCAB3C911CFA7B2909 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93311-1877 |  | 2013-07-11 | 2013-07-11 09:39 | 2013-07-11 10:01 | OTHER - AC042X1221A | 107 | 3.4 | Yes | Yes | 16.5 | 19.1 | -2.6 | 11B31C334F394C798CF1D8A2B075A524 |  | R22 | Non-TXV |  | 3.178% | 0.96822 | 6.107% | [5 empty] | Non-TXV | 3.178%
Fresno | CA | 93705-5019 |  | 2013-07-02 | 2013-07-02 13:44 | 2013-07-02 13:44 | AMERICAN STANDARD - 44CC3024B1064AA | 93 | 0 | Yes | Yes | 18.4 | 16.6 | 1.8 | 32C4B3D44B3E4CA788E0DDD068F127A0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2526 |  | 2013-07-19 | 2013-07-19 14:44 | 2013-07-19 14:44 | OTHER - UNK | 85 | 0 | Yes | Yes | 22.3 | 17.5 | 4.8 | F54544F1FD7C4F9991B72D39BABD31D9 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6053 |  | 2013-07-01 | 2013-07-01 11:59 | 2013-07-01 12:17 | OTHER - 581CJX036000AFAA | 70 | 2.7 | Yes | Yes | 24.8 | 25.3 | -0.5 | D3E291C9CE704D8C97864EDDDFC16678 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
Fresno | CA | 93728-1608 |  | 2013-06-25 | 2013-06-25 11:07 | 2013-06-25 11:07 | OTHER - B0AW36106 | 115 | -9.5 | Yes | Yes | 8.3 | 18.5 | -10.2 | 51F148C4016D4EE7A81817087DF5FA7F | Remove refrigerant: 9.5 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -8.261% | 1.0826 | 2.313% |  |  |  |  | Non-TXV |  |  | -8.261%
Anderson | CA | 96007-9550 |  | 2013-07-14 | 2013-07-14 10:12 | 2013-07-14 10:58 | COLEMAN - DRC00481BEG | 100 | 3 | Yes | Yes | 27.3 | 21.5 | 5.8 | 974A43500DF641D9AB7639433AB467B6 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Shafter | CA | 93263-2240 |  | 2013-07-22 | 2013-07-22 18:47 | 2013-07-22 18:47 | RHEEM - SRM-51839A | 49 | 0 | Yes | Yes | 24.1 | 20.1 | 4 | 5A5FE8A614A34629AB946A218780C36A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3526 |  | 2013-07-01 | 2013-07-01 16:24 | 2013-07-01 16:50 | PAYNE - PA10JA036-A | 83 | 6.2 | Yes | Yes | 19.7 | 14.4 | 5.3 | 6675C71ECE0147C7BE30B8180D432FA2 |  | R22 | Non-TXV |  | 7.47% | 0.9253 | 14.36% | [5 empty] | Non-TXV | 7.47%
Reedley | CA | 93654-7016 |  | 2013-07-18 | 2013-07-18 13:48 | 2013-07-18 14:11 | CARRIER - 38TK048310 | 180 | 12 | Yes | Yes | 22.5 | 19.3 | 3.2 | 0142A2C258FD419F89314A6E96FB7DFC |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Livermore | CA | 94551-1327 |  | 2013-09-13 | 2013-09-13 10:06 | 2013-09-13 14:49 | TEMPSTAR - PGAA30C1K3 | 75 | -4.4 | Yes | Yes | 15.4 | 18 | -2.6 | C429C02AAD9D4F89B37A7AD49A385F05 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
San Jose | CA | 95132-2566 |  | 2013-09-24 | 2013-09-24 12:28 | 2013-09-24 14:33 | - 38CKC060300 | 95 | -5.6 | Yes | Yes | 22.8 | 19.9 | 2.9 | 361230647DEC443E875B862F40408B24 |  | R22 | Non-TXV |  | -5.895% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Cottonwood | CA | 96022-7725 |  | 2013-06-28 | 2013-06-28 09:43 | 2013-06-28 10:14 | ARMSTRONG - SCU12G60A1 | 199 | 8.2 | Yes | Yes | 21.4 | 19.9 | 1.6 | 5519110847DF4625B6804D845D9FD45A |  | R22 | Non-TXV |  | 4.121% | 0.95879 | 7.919% | [5 empty] | Non-TXV | 4.121%
Selma | CA | 93662-2655 |  | 2013-08-05 | 2013-08-05 16:50 | 2013-08-05 17:14 | DAY & NIGHT - UNK | 66 | 7.2 | Yes | Yes | 20.5 | 20 | 0.6 | 1E3E4AED1BE5439DBD99A5031AE8ECB9 |  | R22 | Non-TXV |  | 10.91% | 0.89091 | 20.96% | [5 empty] | Non-TXV | 10.91%
San Jose | CA | 95148-3404 |  | 2013-09-17 | 2013-09-17 16:11 | 2013-09-17 16:37 | GOODMAN - GSX130481B | 126 | -8.9 | Yes | Yes | 18.3 | 20.2 | -1.9 | F62823A940374FB996C411C518F7010C |  | R410A | Non-TXV |  | -7.063% | 1.0706 | 1.978% |  |  |  |  | Non-TXV |  |  | -7.063%
Bakersfield | CA | 93301-2579 |  | 2013-06-25 | 2013-06-25 09:12 | 2013-06-25 12:09 | HEIL - PGF324040K01 | 64 | -3.8 | Yes | Yes | 20 | 19.3 | 0.7 | 2A4CC3D6C0BA4A90873A8D19771CBC08 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Ukiah | CA | 95482-9534 |  | 2013-08-24 | 2013-08-24 10:01 | 2013-08-24 10:23 | COLEMAN - ILLEGIBLE | 91 | -7.5 | Yes | Yes | 23.3 | 20.3 | 3 | D41124F846174C88A6F0BDAE82DC434E |  | R22 | Non-TXV |  | -8.242% | 1.0824 | 2.308% |  |  |  |  | Non-TXV |  |  | -8.242%
Santa Rosa | CA | 95404-5633 |  | 2013-07-17 | 2013-07-17 10:36 | 2013-07-17 11:43 | PAYNE - 561CJ042-B | 93 | -6.6 | Yes | Yes | 16.5 | 18.2 | -1.7 | 97FE0DFD45AE43C6997E565575E35C39 |  | R22 | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Fresno | CA | 93725-1838 |  | 2013-08-26 | 2013-08-26 14:26 | 2013-08-26 15:13 | GOODMAN - CKL421B | 115 | -8.1 | Yes | Yes | 19.8 | 19.6 | 0.2 | 06122AD4CBB1403DB3C5D4DC10DD8AC8 |  | R22 | Non-TXV |  | -7.043% | 1.0704 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.043%
Fresno | CA | 93705-5142 |  | 2013-07-03 | 2013-07-03 11:17 | 2013-07-03 12:10 | RHEEM - RRKAA030JK06X | 54 | 6.8 | Yes | Yes | 20.1 | 20.1 | 0.1 | CEB387E2A3CF4E64A2A7810E8F27BB2C |  | R22 | Non-TXV |  | 12.59% | 0.87407 | 24.2% | [5 empty] | Non-TXV | 12.59%
Bakersfield | CA | 93306-4684 |  | 2013-06-28 | 2013-06-28 16:09 | 2013-06-28 18:11 | RHEEM - NA | 85 | 3 | Yes | Yes | 15.8 | 18.7 | -2.9 | 5C3EBA0F307649728C408E49B7677C04 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93304-2136 |  | 2013-07-24 | 2013-07-24 16:31 | 2013-07-24 17:08 | HEIL - PGF336060K01 | 148 | 8.7 | Yes | Yes | 22 | 19.8 | 2.2 | C79CEA2EBAD841DD8BEA137F005F9778 |  | R22 | Non-TXV |  | 5.878% | 0.94122 | 11.3% | [5 empty] | Non-TXV | 5.878%
Fresno | CA | 93705-4622 |  | 2013-06-26 | 2013-06-26 14:05 | 2013-06-26 14:51 | GOODMAN - GPG133064511X6 | 112 | 4.6 | Yes | Yes | 21.6 | 18.2 | 3.4 | 82447593B0AA4C7F85BC83BEDF4230B2 |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Bakersfield | CA | 93308-1405 |  | 2013-09-12 | 2013-09-12 19:10 | 2013-09-12 19:13 | YORK - D1NH060N09006C | 136 | -9.6 | Yes | Yes | 20.9 | 19.6 | 1.3 | 0661C1FA0F344435BB5099456F7964D6 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Vallejo | CA | 94590-5373 |  | 2013-06-28 | 2013-06-28 13:04 | 2013-06-28 13:23 | CARRIER - 48GX-024060301-- | 52 | 3.2 | Yes | Yes | 24 | 18.8 | 5.3 | BCFFE1668C7041E3B6DACA33193EF7BD |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Fairfield | CA | 94534-3033 |  | 2013-07-17 | 2013-07-17 14:23 | 2013-07-17 14:48 | UNITARY PRODUCTS GROUP - 2TTR042A1000A | 137 | 6.4 | Yes | Yes | 21.8 | 18.9 | 2.9 | B751F9965BCE421589190ECEB449C35D |  | R22 | TXV |  | 4.672% | 0.95328 | 8.978% | [5 empty] | TXV | 4.672%
Bakersfield | CA | 93313-5046 |  | 2013-07-24 | 2013-07-24 12:00 | 2013-07-24 12:29 | RHEEM - RAMC048JB2 | 163 | 20.3 | Yes | Yes | 17.9 | 19.8 | -1.9 | 280607E703DA45A682A45DD7A1F55815 |  | R22 | TXV |  | 12.45% | 0.87546 | 23.93% | [5 empty] | TXV | 12.45%
Fresno | CA | 93722-8610 |  | 2013-06-25 | 2013-06-25 16:38 | 2013-06-25 17:08 | LENNOX - 12GCS030X75 | 85 | 4.9 | Yes | Yes | 24 | 19.3 | 4.7 | BD543E80FDAB45E0AC84984DDDA12111 |  | R22 | Non-TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | Non-TXV | 5.765%
Sanger | CA | 93657-2915 |  | 2013-07-03 | 2013-07-03 09:10 | 2013-07-03 09:30 | ARCOAIRE - PGAA36D1K6 | 69 | 6.2 | Yes | Yes | 19.6 | 18.5 | 1.1 | 6013238452D344B2BCCDB30BFCE9299C |  | R22 | Non-TXV |  | 8.986% | 0.91014 | 17.27% | [5 empty] | Non-TXV | 8.986%
Bakersfield | CA | 93308-9253 |  | 2013-08-05 | 2013-08-05 12:22 | 2013-08-05 13:01 | YORK - CMA04211A | 120 | 3.5 | Yes | Yes | 19 | 20.7 | -1.7 | 0E9FF2EF5E344C758CCDDE063599B250 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Bakersfield | CA | 93307-2354 |  | 2013-07-17 | 2013-07-17 22:37 | 2013-07-17 22:58 | ICP - PGME60G100E | 85 | 2.6 | Yes | Yes | 22.8 | 20.2 | 2.7 | 113B5F2E28EC4EE5997FB6988E3D0D39 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93705-4417 |  | 2013-07-02 | 2013-07-02 12:43 | 2013-07-02 13:02 | GOODMAN - PGB024050 | 54 | 3.4 | Yes | Yes | 15.3 | 18.3 | -3 | 22C7711A1080446DBF7A113C275B9517 |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
San Jose | CA | 95138-1713 |  | 2013-08-01 | 2013-08-01 10:27 | 2013-08-01 11:02 | TRANE - TTY048B100A0 | 170 | 16.5 | Yes | Yes | 20.3 | 18.2 | 2.1 | 1622924E072A41978DE8F027DBB8BAAF |  | R22 | Non-TXV |  | 9.706% | 0.90294 | 18.65% | [5 empty] | Non-TXV | 9.706%
Bakersfield | CA | 93305-2216 |  | 2013-06-27 | 2013-06-27 13:28 | 2013-06-27 13:51 | GOODMAN - GPG1342070M41 | 85 | 4 | Yes | Yes | 23.2 | 19.9 | 3.3 | B7FE0F38237545F69490CFE8FBE3FF1B |  | R410A | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Dublin | CA | 94568-2288 |  | 2013-09-18 | 2013-09-18 14:24 | 2013-09-18 14:24 | CARRIER - 38EH030340 | 200 | 0 | Yes | Yes | 22 | 16.6 | 5.4 | 8ADF483BC0A149F780816E9700078D92 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5008 |  | 2013-08-20 | 2013-08-20 19:26 | 2013-08-20 19:29 | YORK - D1NA042N03606C | 72 | 4 | Yes | Yes | 26.2 | 22.1 | 4.1 | 0FD93C0E73DC4063832700BE0684B902 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Ukiah | CA | 95482-9617 |  | 2013-08-23 | 2013-08-23 14:31 | 2013-08-23 15:12 | CARRIER - 50MQ037300 | 114 | 6.9 | Yes | Yes | 26.1 | 20.9 | 5.2 | 1AC1B0754A4A40C5830F4915F7538ED6 |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
Bakersfield | CA | 93313-5005 |  | 2013-07-15 | 2013-07-15 10:33 | 2013-07-15 10:55 | YORK - D1NA03903606C | 76 | 4.2 | Yes | Yes | 17.7 | 19.2 | -1.5 | EB7F97B7403940B29FE1715CCE1F529F |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
San Jose | CA | 95122-1148 |  | 2013-09-16 | 2013-09-16 10:49 | 2013-09-16 11:35 | LENNOX - UNK | 83 | 3.2 | Yes | Yes | 19.9 | 20.2 | -0.3 | 32C90B33B7B34E33BA094F547582F17D |  | R22 | Non-TXV |  | 3.855% | 0.96145 | 7.409% | [5 empty] | Non-TXV | 3.855%
Bakersfield | CA | 93313-4419 |  | 2013-07-25 | 2013-07-25 11:34 | 2013-07-25 12:06 | RHEEM - RRG07N43JKR | 109 | 5.6 | Yes | Yes | 23.4 | 21.5 | 1.9 | FA6D74297D5E4A2DB7CB6BF0BFAEBA37 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.138% | 0.94862 | 9.873% | [5 empty] | Non-TXV | 5.138%
Vallejo | CA | 94589-1719 |  | 2013-06-27 | 2013-06-27 14:46 | 2013-06-27 15:12 | TRANE - TTR036D100AD | 79 | -7.4 | Yes | Yes | 15 | 17.4 | -2.4 | 8AFFF836916044098869BA536426FD8B |  | R22 | Non-TXV |  | -9.367% | 1.0937 | 2.623% |  |  |  |  | Non-TXV |  |  | -9.367%
Anderson | CA | 96007-8336 |  | 2013-07-09 | 2013-07-09 15:39 | 2013-07-09 16:43 | RHEEM - RRGF-05E30JKB | 46 | 10.8 | Yes | Yes | 27.7 | 22 | 5.7 | F6AF05235D1E4E3B82FC56B7FB716B2D |  | R22 | Non-TXV |  | 23.48% | 0.76522 | 45.12% | [5 empty] | Non-TXV | 23.48%
Sanger | CA | 93657-1916 |  | 2013-07-16 | 2013-07-16 10:36 | 2013-07-16 10:56 | LENNOX - 13ACD04823002 | 204 | 7.7 | Yes | Yes | 24.6 | 20.6 | 4.1 | 799D6B7663E945758E4CE8A497758CCA |  | R22 | Non-TXV |  | 3.775% | 0.96225 | 7.254% | [5 empty] | Non-TXV | 3.775%
Livermore | CA | 94551-1843 |  | 2013-10-07 | 2013-10-07 09:58 | 2013-10-07 09:58 | ARMSTRONG - SCU10B36A-3 | 71 | 2.7 | Yes | Yes | 17 | 17 | 0 | FD8497ED32374EEEB351ACD55716F00A |  | R22 | Non-TXV |  | 3.803% | 0.96197 | 7.308% | [5 empty] | Non-TXV | 3.803%
Bakersfield | CA | 93307-4513 |  | 2013-08-08 | 2013-08-08 22:37 | 2013-08-08 22:42 | HEIL - PGF354100K011A1 | 211 | 12.7 | Yes | Yes | 21 | 22.3 | -1.3 | F9096E0F49254CDE896F5B73A0ACACBB |  | R22 | TXV |  | 6.019% | 0.93981 | 11.57% | [5 empty] | TXV | 6.019%
Sanger | CA | 93657-2837 |  | 2013-07-03 | 2013-07-03 16:33 | 2013-07-03 16:33 | CARRIER - UNK | 70 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 2135BB3778734BFC954815CFDF5335A7 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1232 |  | 2013-06-28 | 2013-06-28 09:36 | 2013-06-28 10:35 | HEIL - PGAD36G0904 | 102 | 7 | Yes | Yes | 23.3 | 19.7 | 3.6 | F0E0EC22ACC642AF928A419D4EF65C25 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.863% | 0.93137 | 13.19% | [5 empty] | Non-TXV | 6.863%
Bakersfield | CA | 93313-6055 |  | 2013-07-19 | 2013-07-19 17:28 | 2013-07-19 18:06 | GUARDIAN - GCGD365S2152B | 80 | 6.7 | Yes | Yes | 22.8 | 20.8 | 2 | 3FDCD5F5B1E54E1CA0BBB81BEF842A20 |  | R22 | TXV |  | 8.375% | 0.91625 | 16.09% | [5 empty] | TXV | 8.375%
Bakersfield | CA | 93304-4551 |  | 2013-06-26 | 2013-06-26 11:59 | 2013-06-26 13:43 | HEIL - PGAA30C1K6 | 79 | 2.3 | Yes | Yes | 18.7 | 19.9 | -1.2 | 41BA6F096EF1435E856F4DBE3A6319D9 |  | R22 | Non-TXV |  | 2.911% | 0.97089 | 5.595% | [5 empty] | Non-TXV | 2.911%
Bakersfield | CA | 93313-3432 |  | 2013-07-10 | 2013-07-10 10:23 | 2013-07-10 10:56 | PAYNE - PY3PNA03606NB | 85 | 3.3 | Yes | Yes | 24.5 | 21 | 3.5 | 945F36F4E8EC44ECBC8186DFC978AA90 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Bakersfield | CA | 93307-3232 |  | 2013-06-28 | 2013-06-28 14:26 | 2013-06-28 14:45 | NORDYNE - DINP036N | 108 | 4.6 | Yes | Yes | 17.6 | 17.6 | 0 | AB17ED2FC12048D88AF388081E07001D |  | R22 | TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | TXV | 4.259%
Bakersfield | CA | 93308-2445 |  | 2013-08-02 | 2013-08-02 18:53 | 2013-08-02 19:11 | YORK - D1NA024L03606C | 54 | 1.6 | Yes | Yes | 26.7 | 24.2 | 2.5 | 9B5579900F11401894CE1636FC03DDCD |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Bakersfield | CA | 93308-2849 |  | 2013-07-02 | 2013-07-02 13:43 | 2013-07-02 17:40 | AMANA - RCE60C2A | 245 | 65.1 | Yes | Yes | 19.9 | 20.4 | -0.5 | 61FFF08B595345FCA45CFBDCC55A7C4E | Add refrigerant: 40.1 oz | R22 | Non-TXV |  | 26.57% | 0.73429 | 51.06% | [5 empty] | Non-TXV | 26.57%
San Jose | CA | 95123-5938 |  | 2013-09-25 | 2013-09-25 15:34 | 2013-09-25 16:01 | CARRIER - 38CKC048300 | 106 | -7.5 | Yes | Yes | 17.3 | 19.1 | -1.8 | 67EBA717C6014D32B3A62D791D0B8936 |  | R22 | Non-TXV |  | -7.075% | 1.0708 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.075%
Fresno | CA | 93722-4001 |  | 2013-06-25 | 2013-06-25 09:13 | 2013-06-25 09:33 | OTHER - 52624106 | 80 | 8 | Yes | Yes | 18.9 | 19.3 | -0.4 | 9299D303B9E7471D9DC359839615ED22 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Davis | CA | 95616-0111 |  | 2013-08-15 | 2013-08-15 09:41 | 2013-08-15 10:01 | CARRIER - 48GP-036090301 | 105 | 8.2 | Yes | Yes | 17 | 18.6 | -1.6 | 17F24A3515174863A7A1F279676BCE5E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 7.81% | 0.9219 | 15.01% | [5 empty] | Non-TXV | 7.81%
Cottonwood | CA | 96022-9325 |  | 2013-06-27 | 2013-06-27 16:42 | 2013-06-27 16:58 | CARRIER - UNK | 70 | 2.6 | Yes | Yes | 21.9 | 20.2 | 1.7 | C1C2919108184CD79860276157AB69F9 |  | R22 | Non-TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | Non-TXV | 3.714%
Bakersfield | CA | 93309-1532 |  | 2013-07-23 | 2013-07-23 16:01 | 2013-07-23 16:19 | OTHER - UNK | 85 | 2.7 | Yes | Yes | 20 | 22.2 | -2.2 | 78B4A03F003D4B66AEED0F26091550A6 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Fresno | CA | 93702-1338 |  | 2013-08-09 | 2013-08-09 11:52 | 2013-08-09 12:51 | GOODMAN - UKN | 80 | 4 | Yes | Yes | 20 | 20.4 | -0.4 | D087C598FE6C4FD1AFB31B5BC3EC0FFB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
San Jose | CA | 95112-1234 |  | 2013-09-25 | 2013-09-25 16:08 | 2013-09-25 16:42 | COLEMAN - ERCQ0241BBB | 69 | -4.1 | Yes | Yes | 16 | 19 | -3 | 0DA44BA2EC0E43FB98337CFB55A984FD |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Bakersfield | CA | 93306-3417 |  | 2013-06-28 | 2013-06-28 12:38 | 2013-06-28 17:10 | YORK - H2RD036506B | 85 | 4.6 | Yes | Yes | 20.5 | 20.6 | -0.1 | 4CA0E6D7889143EC89E0FAFE4D9F9A3A |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
San Jose | CA | 95117-3053 |  | 2013-10-14 | 2013-10-14 16:17 | 2013-10-14 17:02 | CARRIER - 3BHDC048321 | 117 | 29.8 | Yes | Yes | 20.4 | 20.4 | 0 | EA3B95A037254B749681FEA0516F108A |  | R22 | Non-TXV |  | 25.47% | 0.7453 | 48.95% | [5 empty] | Non-TXV | 25.47%
Fresno | CA | 93702-3996 |  | 2013-06-26 | 2013-06-26 09:36 | 2013-06-26 09:58 | RHEEM - URGG-07E43JKR | 80 | -5.6 | Yes | Yes | 19.2 | 18.7 | 0.5 | 0DEA6F7332D94B4F8DE6F79CB466BF3B |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Bakersfield | CA | 93308-1039 |  | 2013-07-02 | 2013-07-02 11:03 | 2013-07-02 11:31 | CARRIER - 585HJ030040 | 68 | 8.7 | Yes | Yes | 19.6 | 15.7 | 3.9 | 97CD7F570BCC473D93A4F347224FBD69 |  | R22 | Non-TXV |  | 12.79% | 0.87206 | 24.59% | [5 empty] | Non-TXV | 12.79%
Bakersfield | CA | 93308-7855 |  | 2013-07-03 | 2013-07-03 14:45 | 2013-07-03 15:17 | CARRIER - N/A | 85 | 3.4 | Yes | Yes | 21.8 | 21 | 0.8 | 73D390EA8D7C4280AD6E3927EB05CCB6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Oakland | CA | 94603-3941 |  | 2013-07-02 | 2013-07-02 10:32 | 2013-07-02 14:11 | GMC - CK42-C1 | 92 | -1 | Yes | Yes | 15.7 | 20.2 | -4.5 | 48C5272FF2F04BD5B434D5153D2B98F0 | Remove refrigerant: 7.6 oz Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -1.087% | 1.0109 | 0.3044% |  |  |  |  | Non-TXV |  |  | -1.087%
Ukiah | CA | 95482-3383 |  | 2013-08-22 | 2013-08-22 13:48 | 2013-08-22 14:13 | BRYANT - 561CJ030-C | 74 | 9.6 | Yes | Yes | 25.7 | 20.4 | 5.3 | B5EB46E3A2A2425F8A67F14E065B7B82 |  | R22 | Non-TXV |  | 12.97% | 0.87027 | 24.93% | [5 empty] | Non-TXV | 12.97%
Fresno | CA | 93705-1341 |  | 2013-07-02 | 2013-07-02 09:44 | 2013-07-02 10:29 | OTHER - DAYPF030N070A | 73 | -3.7 | Yes | Yes | 20.9 | 19.1 | 1.8 | 366BA34357CF4840B35EFF4D2E86ED99 |  | R22 | TXV |  | -5.068% | 1.0507 | 1.419% |  |  |  |  | TXV |  |  | -5.068%
Anderson | CA | 96007-8623 |  | 2013-09-06 | 2013-09-06 09:55 | 2013-09-06 10:25 | GOODMAN - GSC140361AE | 149 | -16 | Yes | Yes | 25.8 | 21.5 | 4.3 | E022B43CB89D4CF3895B48B5EB67CB94 |  | R22 | TXV |  | -10.74% | 1.1074 | 3.007% |  |  |  |  | TXV |  |  | -10.74%
Bakersfield | CA | 93309-6336 |  | 2013-07-30 | 2013-07-30 17:23 | 2013-07-30 17:27 | DAY & NIGHT - PGPD330060K001C1 | 98 | -5.4 | Yes | Yes | 25.5 | 20.4 | 5.1 | 5AF73523D3D34D55BA1C70E7D4F8FFA8 |  | R22 | Non-TXV |  | -5.51% | 1.0551 | 1.543% |  |  |  |  | Non-TXV |  |  | -5.51%
Bakersfield | CA | 93312-4338 |  | 2013-07-15 | 2013-07-15 17:02 | 2013-07-15 20:51 | CARRIER - 48SS-0360301 | 85 | 0 | Yes | Yes | 21.4 | 22.5 | -1.1 | 8CC2CAD8DEC944F383933FF3FB3D9D57 | Add refrigerant: 6.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1416 |  | 2013-07-02 | 2013-07-02 11:54 | 2013-07-02 12:41 | OTHER - PGF336060K101A1 | 176 | 5.3 | Yes | Yes | 22 | 19.9 | 2.1 | EEE11A14A4D9437E94C5D06F939A434E |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.787% | [5 empty] | Non-TXV | 3.011%
Cottonwood | CA | 96022-8041 |  | 2013-07-12 | 2013-07-12 14:44 | 2013-07-12 15:06 | BDP - 561AJ048-B | 104 | 4.5 | Yes | Yes | 24.5 | 18.7 | 5.8 | F69A72D3C2E04DF5A0D7207F4D1C2B07 |  | R22 | Non-TXV |  | 4.327% | 0.95673 | 8.315% | [5 empty] | Non-TXV | 4.327%
Bakersfield | CA | 93305-4412 |  | 2013-06-27 | 2013-06-27 13:42 | 2013-06-27 14:00 | TEMPSTAR - GPCM030K0600 | 51 | 2.4 | Yes | Yes | 20 | 21 | -1 | 28D3B13FF5F34AA5B5B10C98EDFE16BC |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Sanger | CA | 93657-3243 |  | 2013-06-24 | 2013-06-24 17:04 | 2013-06-24 17:25 | PAYNE - | 85 | 10.7 | Yes | Yes | 22.7 | 19.9 | 2.8 | 935FF53B36FC4AF1A4DE51C67EDE0948 |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Fresno | CA | 93722-4709 |  | 2013-07-16 | 2013-07-16 17:31 | 2013-07-16 17:48 | LENNOX - 12ACB36-5P | 103 | 4 | Yes | Yes | 20.2 | 18 | 2.2 | 178B93AED66B400F8F15577B7F2E9FFF |  | R22 | TXV |  | 3.883% | 0.96117 | 7.463% | [5 empty] | TXV | 3.883%
San Jose | CA | 95122-1509 |  | 2013-07-22 | 2013-07-22 10:17 | 2013-07-22 10:38 | GMC - 5658JO42OOOAAAA | 85 | -6 | Yes | Yes | 16.6 | 18.5 | -1.9 | BC89149092034BF0ACD7967BC1644185 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93311-2821 |  | 2013-07-11 | 2013-07-11 13:43 | 2013-07-11 13:43 | OTHER - H2RCO42S06HA | 109 | 0 | Yes | Yes | 9.1 | 17.2 | -8.1 | B1929E5A599F40F1A6C5B0E5C9F2AF1D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9237 |  | 2013-07-03 | 2013-07-03 11:45 | 2013-07-03 11:45 | YORK - D1NP030N05600A | 73 | 0 | Yes | Yes | 22.5 | 19.7 | 2.8 | 1C81F96D663743EE90F9BC06A406852C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5595 |  | 2013-08-23 | 2013-08-23 09:56 | 2013-08-23 10:31 | GOODMAN - CKL 49-1 | 85 | 4 | Yes | Yes | 17.4 | 20.3 | -2.9 | ACB818B8A18D4801A4F3F3EA089AA1DE |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Bakersfield | CA | 93301-2617 |  | 2013-06-25 | 2013-06-25 11:05 | 2013-06-25 12:07 | UNK - UNK | 85 | 9 | Yes | Yes | 25 | 19.9 | 5.1 | E651D1F312364E628DB78FDE8C5E58A0 |  |  |  |  | 10.59% | 0.89412 | 20.35% | [5 empty] | 0 | 10.59%
Bakersfield | CA | 93301-2617 |  | 2013-06-25 | 2013-06-25 11:08 | 2013-06-25 12:02 | - | 85 | 8 | Yes | Yes | 24.5 | 19.9 | 4.6 | 80B54A30DC6A42AAAF8AD8F479DC8630 |  |  |  |  | 9.412% | 0.90588 | 18.09% | [5 empty] | 0 | 9.412%
San Jose | CA | 95118-3430 |  | 2013-09-25 | 2013-09-25 10:34 | 2013-09-25 11:13 | CARRIER - 38TDB048300 | 184 | 9.1 | Yes | Yes | 22.7 | 17.2 | 5.5 | 4D5CF50B29504C4FB24C5E721FC6F1F2 |  | R410A | TXV |  | 4.946% | 0.95054 | 9.504% | [5 empty] | TXV | 4.946%
Pleasanton | CA | 94566-7202 |  | 2013-09-13 | 2013-09-13 13:34 | 2013-09-13 13:34 | CARRIER - 38CKC036340 | 124 | 0 | Yes | Yes | 18.5 | 17.2 | 1.3 | 03E8887613064983A55AE23D1772EEC2 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2932 |  | 2013-08-01 | 2013-08-01 08:58 | 2013-08-01 09:28 | ICP - PGC036060B | 71 | 3.5 | Yes | Yes | 17.3 | 19.3 | -2 | 24AEBB608A124BC19737E7E6302D3FDE |  | R22 | Non-TXV |  | 4.93% | 0.9507 | 9.474% | [5 empty] | Non-TXV | 4.93%
Fresno | CA | 93704-5112 |  | 2013-07-31 | 2013-07-31 12:45 | 2013-07-31 13:04 | ICP - PGX330040K1A1-- | 136 | -5.1 | Yes | Yes | 22.8 | 20.9 | 1.9 | 9E3587BC1E814223A503ADFD36DF0B33 |  | R410A | TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | TXV |  |  | -3.75%
Bakersfield | CA | 93313-5005 |  | 2013-07-21 | 2013-07-21 11:35 | 2013-07-21 11:57 | YORK - D1NA030N03606C | 76 | 5.8 | Yes | Yes | 28.9 | 23.2 | 5.7 | 3B47FA2EE36E47529C1DA3A06D4CF2A5 |  | R22 | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
Fresno | CA | 93722-3057 |  | 2013-06-25 | 2013-06-25 12:47 | 2013-06-25 13:57 | RHEEM - RAKA042JAZ | 79 | 3.3 | Yes | Yes | 20.5 | 20.1 | 0.5 | 34204A77490140C888ADC39B8DA683F0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.177% | 0.95823 | 8.028% | [5 empty] | Non-TXV | 4.177%
Fresno | CA | 93702-1833 |  | 2013-06-26 | 2013-06-26 15:20 | 2013-06-26 15:55 | BRYANT - 583ANW036060AAAF | 83 | 3.1 | Yes | Yes | 21.8 | 19.8 | 2.1 | DAF9312A793C4C3CBAB8DCA237B7C9C8 |  | R22 | Non-TXV |  | 3.735% | 0.96265 | 7.178% | [5 empty] | Non-TXV | 3.735%
Redding | CA | 96002-9481 |  | 2013-07-17 | 2013-07-17 15:09 | 2013-07-17 15:25 | BARD - UNK | 88 | 5.1 | Yes | Yes | 17.4 | 20.1 | -2.7 | E534EE7DEB9C4345B68F15AD69740319 |  | R22 | Non-TXV |  | 5.795% | 0.94205 | 11.14% | [5 empty] | Non-TXV | 5.795%
Anderson | CA | 96007-8469 |  | 2013-07-14 | 2013-07-14 08:18 | 2013-07-14 09:10 | RUUD - RKMA-A060JL10E | 184 | -13 | Yes | Yes | 22.4 | 19.8 | 2.6 | 225970FD2CAA489EA3A4C90231D8DA90 |  | R22 | Non-TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.065%
Bakersfield | CA | 93309-2169 |  | 2013-09-05 | 2013-09-05 20:02 | 2013-09-05 20:04 | DAY & NIGHT - 584AN0360606 | 54 | 3.2 | Yes | Yes | 23.9 | 20.7 | 3.3 | 6EB431A16F4F4F02AD09BE5B2B177C6A |  | R22 | Non-TXV |  | 5.926% | 0.94074 | 11.39% | [5 empty] | Non-TXV | 5.926%
Bakersfield | CA | 93309-6105 |  | 2013-07-11 | 2013-07-11 17:39 | 2013-07-11 18:02 | HEIL - GPCM036K060 | 70 | 2.4 | Yes | Yes | 23.6 | 21 | 2.6 | D0E34D49ADDB4927A1E5DCBD053B8F6C |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Fresno | CA | 93728-3022 |  | 2013-06-25 | 2013-06-25 09:58 | 2013-06-25 11:04 | LENNOX - 10GCS036X3PA | 58 | -3.4 | Yes | Yes | 16 | 18.1 | -2.1 | 2B3FF90774294CFF95F24985920D86E5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Lamont | CA | 93241-1204 |  | 2013-07-18 | 2013-07-18 21:29 | 2013-07-18 21:51 | BRYANT - 574ANW03606NA | 172 | 8.1 | Yes | Yes | 19.1 | 18.7 | 0.4 | D853F49D674F4D53A358F499AD065448 |  | R22 | Non-TXV |  | 4.709% | 0.95291 | 9.05% | [5 empty] | Non-TXV | 4.709%
Anderson | CA | 96007-8226 |  | 2013-09-05 | 2013-09-05 11:41 | 2013-09-05 12:06 | RHEEM - RQPL-B024JK | 97 | -4.7 | Yes | Yes | 25.6 | 19.7 | 5.9 | 2862AF8757434FABBC895E11C5D79966 |  | R410A | TXV |  | -4.845% | 1.0485 | 1.357% |  |  |  |  | TXV |  |  | -4.845%
Anderson | CA | 96007-8226 |  | 2013-09-05 | 2013-09-05 12:08 | 2013-09-05 13:30 | AMERICAN STANDARD - WCY036G100AB | 150 | 7.6 | Yes | Yes | 26.5 | 21 | 5.5 | 40B2316701B5456E9BEE15BFABC3D25F |  | R410A | TXV |  | 5.067% | 0.94933 | 9.737% | [5 empty] | TXV | 5.067%
Arvin | CA | 93203-2825 |  | 2013-08-21 | 2013-08-21 18:01 | 2013-08-21 18:20 | DUCANE - AFAIR12B42 | 106 | 3.2 | Yes | Yes | 21 | 19.3 | 1.7 | 563E5EADC4724A9E86FEF629B0588C73 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
San Jose | CA | 95138-1708 |  | 2013-07-17 | 2013-07-17 11:41 | 2013-07-17 12:16 | COLEMAN - BRCS0421BD | 84 | 12.8 | Yes | Yes | 21.1 | 18.1 | 3 | 76C230083C5F44999B62ED87C52AD62F |  | R22 | Non-TXV |  | 15.24% | 0.84762 | 29.28% | [5 empty] | Non-TXV | 15.24%
Bakersfield | CA | 93305-3864 |  | 2013-08-01 | 2013-08-01 10:45 | 2013-08-01 11:02 | ICP - PGC024K040E | 85 | 2.5 | Yes | Yes | 17.5 | 19.4 | -1.9 | 5AEB2DACB62844169FB80AC98B4138D3 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93727-2819 |  | 2013-07-29 | 2013-07-29 14:00 | 2013-07-29 15:03 | CARRIER - 36BRC048370 | 140 | -30.3 | Yes | Yes | 22.9 | 20.2 | 2.8 | 6BD3124CC31A48D1ABD576BA752A71F7 |  | R22 | TXV |  | -21.64% | 1.2164 | 6.061% |  |  |  |  | TXV |  |  | -21.64%
Fresno | CA | 93702-3446 |  | 2013-06-26 | 2013-06-26 18:35 | 2013-06-26 19:21 | ICP - GPFM36K060F | 88 | 3.9 | Yes | Yes | 23.6 | 20.2 | 3.4 | C9769051F05640E7A21E7EB3807F46D7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.432% | 0.95568 | 8.517% | [5 empty] | Non-TXV | 4.432%
Bakersfield | CA | 93305-3863 |  | 2013-08-01 | 2013-08-01 12:05 | 2013-08-01 12:21 | ICP - PGC024K040E | 85 | 2.5 | Yes | Yes | 18.7 | 18.5 | 0.2 | D356086E762F47D7B097456F3BA53F76 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Lamont | CA | 93241-1134 |  | 2013-08-22 | 2013-08-22 15:31 | 2013-08-22 20:20 | ICP - PGX442080K01A1 | 224 | 8.1 | Yes | Yes | 20.9 | 20.8 | 0.1 | E407D701D0174B40946F5A30A347B03E |  | R410A | Non-TXV |  | 3.616% | 0.96384 | 6.949% | [5 empty] | Non-TXV | 3.616%
Bakersfield | CA | 93307-4585 |  | 2013-06-29 | 2013-06-29 09:23 | 2013-06-29 09:42 | YORK - BRCQ0361BDG | 52 | 18.2 | Yes | Yes | 16.5 | 19.4 | -2.9 | EC6A68DD53D248F8BD25288CFF9F8E23 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 35% | 0.65 | 67.26% | [5 empty] | Non-TXV | 35%
Fresno | CA | 93726-4430 |  | 2013-07-02 | 2013-07-02 13:17 | 2013-07-02 13:39 | AMERICAN STANDARD - 2A7A2048A1000AA | 120 | 12.8 | Yes | Yes | 21.3 | 19.3 | 2 | 19EC8009EB1D40C5BD712D297BB3C6AA |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Bakersfield | CA | 93304-7130 |  | 2013-08-09 | 2013-08-09 11:37 | 2013-08-09 12:07 | GOODMAN - GPG1036070 | 85 | 2.7 | Yes | Yes | 18.2 | 21 | -2.8 | 388199E4EFFC40B99E81D1640475EE21 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Livermore | CA | 94551-5467 |  | 2013-09-13 | 2013-09-13 10:40 | 2013-09-13 10:40 | CARRIER - 5658J030 | 72 | 0 | Yes | Yes | 21.3 | 24.2 | -2.9 | D738BB00D1734E72BEC7BCF15863C8F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4382 |  | 2013-07-15 | 2013-07-15 13:42 | 2013-07-15 14:29 | OTHER - CA5530VKA1 | 85 | 3.8 | Yes | Yes | 15.5 | 18.5 | -3 | DB67F557DED749F584FB892AA9FDF763 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Kerman | CA | 93630-8947 |  | 2013-10-01 | 2013-10-01 10:53 | 2013-10-01 10:53 | PAYNE - 574DNW030040NA | 85 | 0 | Yes | Yes | 22.9 | 20.8 | 2.1 | E3C55B67E2BD464FB40F8B3CFC4EA5D7 |  | R410A | TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-2202 |  | 2013-07-09 | 2013-07-09 13:21 | 2013-07-09 13:45 | CARRIER - 48SX048100341AA | 88 | 9.9 | Yes | Yes | 18.7 | 19.9 | -1.2 | 29C788A8EC874F628D26268B301EBA36 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Kerman | CA | 93630-8948 |  | 2013-07-19 | 2013-07-19 19:26 | 2013-07-19 19:26 | BRYANT - 574DNW036060NA-- | 147 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 5A3948260B9746FDB1CB8FA4C1CB865E | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1416 |  | 2013-06-26 | 2013-06-26 18:18 | 2013-06-26 19:48 | AMANA - PGB60B0902C | 154 | -5.8 | Yes | Yes | 24 | 19.6 | 4.4 | 8C86F3F09E6E4FBC9864513072D8AA41 |  | R22 | TXV |  | -3.766% | 1.0377 | 1.055% |  |  |  |  | TXV |  |  | -3.766%
Fresno | CA | 93711-1415 |  | 2013-08-17 | 2013-08-17 12:39 | 2013-08-17 13:59 | RHEEM - RRAMAA042JK08X | 114 | 12.5 | Yes | Yes | 21.3 | 20.2 | 1.1 | 264E35833065401BA8877F7337EDE4ED |  | R22 | TXV |  | 10.96% | 0.89035 | 21.07% | [5 empty] | TXV | 10.96%
Kerman | CA | 93630-8950 |  | 2013-08-02 | 2013-08-02 13:27 | 2013-08-02 14:30 | BRYANT - 574DNW036060NA | 146 | 15.1 | Yes | Yes | 25.2 | 19.9 | 5.3 | 2D3B841F0E1044BA90B1E10B60EB5142 |  | R410A | TXV |  | 10.34% | 0.89658 | 19.88% | [5 empty] | TXV | 10.34%
Fresno | CA | 93711-1415 |  | 2013-06-25 | 2013-06-25 14:50 | 2013-06-25 15:17 | HEIL - PGC036K080B | 71 | 3.2 | Yes | Yes | 24.4 | 19.3 | 5.1 | C9523800DC55414384B6C98EE7D39050 |  | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
Bakersfield | CA | 93308-1840 |  | 2013-08-02 | 2013-08-02 18:32 | 2013-08-02 18:49 | AMERICAN STANDARD - YCY036G1M0AA | 85 | 2.5 | Yes | Yes | 19.9 | 22.9 | -3 | 941253F11BD645B99688E02B884FBB6B |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93725-4011 |  | 2013-06-25 | 2013-06-25 09:24 | 2013-06-25 09:24 | CARRIER - 24ABA342A300 | 99 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 1E158FDE07A64253868159AC7E1FE660 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1521 |  | 2013-07-02 | 2013-07-02 09:19 | 2013-07-02 10:10 | YORK - D1NH036N05606C | 108 | 5.3 | Yes | Yes | 18.7 | 20.4 | -1.7 | 2338F1461C7E4A4B8E35B7F7E572C0C4 |  | R22 | Non-TXV |  | 4.907% | 0.95093 | 9.431% | [5 empty] | Non-TXV | 4.907%
San Jose | CA | 95118-2831 |  | 2013-10-08 | 2013-10-08 14:59 | 2013-10-08 16:45 | RUUD - UAKA3 037JAZ | 95 | 5.8 | Yes | Yes | 19.8 | 21 | -1.2 | 136CF644D7CB4A4E978A9EA9681ABA87 |  | R22 | Non-TXV |  | 6.105% | 0.93895 | 11.73% | [5 empty] | Non-TXV | 6.105%
Bakersfield | CA | 93307-3613 |  | 2013-08-08 | 2013-08-08 22:25 | 2013-08-08 22:28 | GOODMAN - PGB030075-1A | 56 | 1.8 | Yes | Yes | 20.2 | 21.2 | -1 | C44BDA85A2D64E84AB3EABA3F4DFE9C5 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Fresno | CA | 93722-4787 |  | 2013-07-17 | 2013-07-17 13:52 | 2013-07-17 13:52 | RHEEM - RAHE030JAS | 78 | 0 | Yes | Yes | 23.2 | 20.6 | 2.6 | 61650ED9F87F4A608A2D2D40095F2B78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3008 |  | 2013-07-26 | 2013-07-26 10:56 | 2013-07-26 11:13 | BRYANT - 561CJ036-F | 124 | 12.7 | Yes | Yes | 22.4 | 19.2 | 3.2 | CD1374353BBC40B990538294687188B2 |  | R22 | Non-TXV |  | 10.24% | 0.89758 | 19.68% | [5 empty] | Non-TXV | 10.24%
Bakersfield | CA | 93313-3945 |  | 2013-07-10 | 2013-07-10 18:13 | 2013-07-10 18:59 | RHEEM - N/A | 85 | 3.3 | Yes | Yes | 20 | 21.4 | -1.4 | 99F71315F0FD40C58C63E867359E52B4 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Cottonwood | CA | 96022-8401 |  | 2013-07-12 | 2013-07-12 10:09 | 2013-07-12 10:43 | BDP - 561ANJ036-B | 74 | 10.6 | Yes | Yes | 22.6 | 19.9 | 2.7 | FCFFEA8F975D48C2846751DB99889782 |  | R22 | Non-TXV |  | 14.32% | 0.85676 | 27.53% | [5 empty] | Non-TXV | 14.32%
Pleasanton | CA | 94566-6804 |  | 2013-09-12 | 2013-09-12 09:25 | 2013-09-12 09:59 | AMERICAN STANDARD - 2A7A1036A1000AA | 73 | 9 | Yes | Yes | 23.3 | 17.5 | 5.8 | 06E15BDE4C334ACBB26CA555D815F48F |  | R22 | Non-TXV |  | 12.33% | 0.87671 | 23.69% | [5 empty] | Non-TXV | 12.33%
San Jose | CA | 95127-4335 |  | 2013-09-19 | 2013-09-19 11:38 | 2013-09-19 12:28 | NORDYNE - S3BA-042KA | 87 | -6.1 | Yes | Yes | 25.1 | 19.5 | 5.6 | F8F75E017A8D45FDB01C4EF102DA1777 |  | R22 | Non-TXV |  | -7.011% | 1.0701 | 1.964% |  |  |  |  | Non-TXV |  |  | -7.011%
San Jose | CA | 95127-4335 |  | 2013-09-19 | 2013-09-19 11:43 | 2013-09-19 12:27 | NORDYNE - S3BA-036KA | 69 | -4.1 | Yes | Yes | 25.2 | 20.4 | 4.8 | 1A4E1F1EB42C4FB7A699079C907DB7DE |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Bakersfield | CA | 93305-1514 |  | 2013-09-16 | 2013-09-16 07:38 | 2013-09-16 07:57 | GOODMAN - PGB036050-1A | 85 | 2.8 | Yes | Yes | 15.9 | 17.9 | -2 | 3A062FD28ED446F494EFE5F1D083EB0A |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fairfield | CA | 94533-3924 |  | 2013-07-18 | 2013-07-18 12:58 | 2013-07-18 13:27 | AIRE-FLO - 4AC13L24P | 70 | 3.7 | Yes | Yes | 19.6 | 18.2 | 1.4 | 837966D5BB9F4F978C1B2B8FF51E2CF2 |  | R410A | Non-TXV |  | 5.286% | 0.94714 | 10.16% | [5 empty] | Non-TXV | 5.286%
Fresno | CA | 93704-5004 |  | 2013-07-31 | 2013-07-31 13:56 | 2013-07-31 14:17 | BRYANT - 582ANW030040AAAD | 85 | 2.8 | Yes | Yes | 27.7 | 22 | 5.7 | F215A39248244830806E4894F660DF4D |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Corcoran | CA | 93212-1613 |  | 2013-07-11 | 2013-07-11 12:52 | 2013-07-11 13:09 | CARRIER - 483X042080311AA | 87 | 5.6 | Yes | Yes | 23.7 | 21.3 | 2.4 | 0A7A62CEE5594F3D891CC0908F96093D |  | R22 | Non-TXV |  | 6.437% | 0.93563 | 12.37% | [5 empty] | Non-TXV | 6.437%
Ukiah | CA | 95482-9534 |  | 2013-08-22 | 2013-08-22 15:10 | 2013-08-22 15:45 | COLEMAN - ERCS0361BAG | 145 | 5.7 | Yes | Yes | 23.4 | 20.4 | 3 | 38B2AB1679014F7A83DCD87EDA53478B |  | R22 | Non-TXV |  | 3.931% | 0.96069 | 7.555% | [5 empty] | Non-TXV | 3.931%
Bakersfield | CA | 93313-4379 |  | 2013-07-12 | 2013-07-12 18:56 | 2013-07-12 19:18 | OTHER - CA7524VKA1 | 85 | 15 | Yes | Yes | 22 | 22.1 | -0.1 | 45F1130974394BB8B1855BFC1FA0E3CE |  | R22 | Non-TXV |  | 17.65% | 0.82353 | 33.91% | [5 empty] | Non-TXV | 17.65%
San Jose | CA | 95117-1118 |  | 2013-10-15 | 2013-10-15 13:08 | 2013-10-15 13:45 | CARRIER - 38HDL030301 | 86 | 10.1 | Yes | Yes | 23.6 | 20.4 | 3.2 | A688F870ACC4490BA3BA6DD3A07E7B9A |  | R22 | Non-TXV |  | 11.74% | 0.88256 | 22.57% | [5 empty] | Non-TXV | 11.74%
San Jose | CA | 95124-5410 |  | 2013-09-26 | 2013-09-26 15:03 | 2013-09-26 15:03 | BRYANT - 53ANX036000B | 86 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | A95A461F3ECE4080AADEB5E5B9D1D7EF | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-1299 |  | 2013-09-03 | 2013-09-03 10:53 | 2013-09-03 11:35 | YORK - TCGD36S21S2HA | 63 | 3.4 | Yes | Yes | 22.4 | 16.6 | 5.8 | 60C98028BC264A5FB66AE64463E96ACC |  | R22 | Non-TXV |  | 5.397% | 0.94603 | 10.37% | [5 empty] | Non-TXV | 5.397%
Fresno | CA | 93722-5404 |  | 2013-06-25 | 2013-06-25 12:30 | 2013-06-25 13:22 | CARRIER - UKN | 80 | 5.2 | Yes | Yes | 22 | 19.1 | 2.9 | 7D245443ADCD45BDAFEF9738AAB83353 |  | R22 | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Bakersfield | CA | 93305-3204 |  | 2013-07-16 | 2013-07-16 10:42 | 2013-07-16 11:00 | PAYNE - PY1PNB036060ABAA | 70 | 3.8 | Yes | Yes | 23.5 | 20.7 | 2.8 | D1F132CB06FA4D39A61D165E370A19D7 |  | R22 | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Vallejo | CA | 94591-4846 |  | 2013-06-28 | 2013-06-28 11:11 | 2013-06-28 11:39 | AMANA - RCB30A2B | 85 | 11.9 | Yes | Yes | 24.2 | 19.2 | 5 | B601E5A200374DAFBD1582BAD99A0B67 |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Fremont | CA | 94536-5447 |  | 2013-09-11 | 2013-09-11 10:26 | 2013-09-11 12:02 | AMANA - RCC36A2B | 85 | 0 | Yes | Yes | 20.1 | 17.9 | 2.2 | C303E7C9E2364FF4BCFB145D21F7D010 | Add refrigerant: 6.2 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-0738 |  | 2013-10-14 | 2013-10-14 11:52 | 2013-10-14 12:32 | AMANA - P55200-48 | 24 | 17.3 | Yes | Yes | 26 | 20.3 | 5.7 | ECE7CCC6CF564605A027C7BEBAD285D4 |  | R22 | Non-TXV |  | 72.08% | 0.27917 | 138.5% | [5 empty] | Non-TXV | 72.08%
Fresno | CA | 93702-4632 |  | 2013-06-26 | 2013-06-26 10:46 | 2013-06-26 11:06 | YORK - H1DB036506B | 72 | 2.4 | Yes | Yes | 20.2 | 17 | 3.2 | B1B58ADA22634F6CBE5BD3CDBAE2B1CE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
San Rafael | CA | 94903-5109 |  | 2013-07-12 | 2013-07-12 10:19 | 2013-07-12 10:21 | PAYNE - 591ANX030000ABAA | 68 | -2.8 | Yes | Yes | 14.9 | 17.3 | -2.4 | CAA7B950DF144897A6D7BF2F6FA1815D |  | R22 | TXV |  | -4.118% | 1.0412 | 1.153% |  |  |  |  | TXV |  |  | -4.118%
San Jose | CA | 95139-1433 |  | 2013-07-17 | 2013-07-17 09:36 | 2013-07-17 09:36 | CARRIER - 24ABA348A310 | 187 | 0 | Yes | Yes | 23 | 19.3 | 3.7 | 2FDB553DD2684F44A1B1B290D58E83C7 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-3017 |  | 2013-10-09 | 2013-10-09 10:39 | 2013-10-09 11:02 | ICP - TCA236AKA1 | 96 | 5.5 | Yes | Yes | 20.1 | 20.9 | -0.8 | B9588A8CF49A44948C3897A1EF9922CA |  | R22 | Non-TXV |  | 5.729% | 0.94271 | 11.01% | [5 empty] | Non-TXV | 5.729%
Fresno | CA | 93702-3142 |  | 2013-06-26 | 2013-06-26 12:46 | 2013-06-26 12:46 | - UNK | 80 | 0 | Yes | Yes | 16.3 | 18.9 | -2.6 | 4EFFECCF715D4170A501C47B03DB4C70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7072 |  | 2013-07-15 | 2013-07-15 12:59 | 2013-07-15 13:24 | GOODMAN - GPG13420901AA | 107 | 10.9 | Yes | Yes | 23.5 | 20.2 | 3.3 | D5C6142CCA7E4A85B95E3051989AF763 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.19% | 0.89813 | 19.58% | [5 empty] | Non-TXV | 10.19%
Cottonwood | CA | 96022-9565 |  | 2013-06-27 | 2013-06-27 14:55 | 2013-06-27 16:41 | DAY & NIGHT - 9201232 | 130 | 3.8 | Yes | Yes | 21.4 | 21 | 0.4 | FF80C48C7C5B4248A86402ECE7D35FE0 |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Bakersfield | CA | 93313-4955 |  | 2013-07-24 | 2013-07-24 15:09 | 2013-07-24 15:34 | RHEEM - FAFF037JAZ | 94 | 6.4 | Yes | Yes | 23.7 | 21 | 2.7 | F37851A822D341ECBADED02794A7AA73 |  | R22 | TXV |  | 6.809% | 0.93191 | 13.08% | [5 empty] | TXV | 6.809%
Pleasanton | CA | 94588-3477 |  | 2013-09-18 | 2013-09-18 10:10 | 2013-09-18 10:10 | BDP - 569BJ036 | 93 | 0 | Yes | Yes | 20.7 | 17.7 | 3 | 5BA897CE33834936BF293D2392051831 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4364 |  | 2013-07-26 | 2013-07-26 15:54 | 2013-07-26 16:15 | ICP - CA5536VKA1 | 80 | -4 | Yes | Yes | 26.5 | 21.5 | 5 | 5C7E744847994967BE71C21442BD5935 |  | R22 | TXV |  | -5% | 1.05 | 1.4% |  |  |  |  | TXV |  |  | -5%
San Jose | CA | 95131-2600 |  | 2013-10-21 | 2013-10-21 15:17 | 2013-10-21 15:36 | BRYANT - UNK | 115 | 3.9 | Yes | Yes | 20.6 | 20.9 | -0.3 | 00C0839CB2B145C596F6644A454D2020 |  | R22 | Non-TXV |  | 3.391% | 0.96609 | 6.517% | [5 empty] | Non-TXV | 3.391%
Bakersfield | CA | 93305-1914 |  | 2013-07-16 | 2013-07-16 15:42 | 2013-07-16 15:42 | YORK - D3N2036N05606NXA | 64 | 0 | Yes | Yes | 25 | 22.3 | 2.8 | ADFC540A81F245478A3C197F27745F28 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7507 |  | 2013-09-18 | 2013-09-18 13:35 | 2013-09-18 14:06 | YORK - M10B036S06B | 59 | 3.1 | Yes | Yes | 24.3 | 20.1 | 4.2 | 78E360ABDC2F4043BAFC0AC8DC39746C |  | R22 | Non-TXV |  | 5.254% | 0.94746 | 10.1% | [5 empty] | Non-TXV | 5.254%
Sanger | CA | 93657-9422 |  | 2013-06-24 | 2013-06-24 15:52 | 2013-06-24 16:12 | YORK - D1NA048N11006C | 92 | 9.4 | Yes | Yes | 20.7 | 17.6 | 3.2 | 721166D025CD40C29BF9CECEBEFBB6C7 |  | R22 | Non-TXV |  | 10.22% | 0.89783 | 19.64% | [5 empty] | Non-TXV | 10.22%
Cottonwood | CA | 96022-9357 |  | 2013-07-13 | 2013-07-13 08:30 | 2013-07-13 09:19 | RHEEM - ILLEGIBLE | 93 | 5.6 | Yes | Yes | 24.8 | 19.1 | 5.7 | 2B957C58A4664F81B24354C8F10632B9 |  | R22 | Non-TXV |  | 6.022% | 0.93978 | 11.57% | [5 empty] | Non-TXV | 6.022%
Bakersfield | CA | 93305-2850 |  | 2013-10-09 | 2013-10-09 17:25 | 2013-10-09 17:27 | DAY & NIGHT - 24/60 | 85 | 4.6 | Yes | Yes | 25.4 | 20.9 | 4.5 | 0BD29E02DCA44E328D9CB04614FCE481 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Corcoran | CA | 93212-2729 |  | 2013-07-05 | 2013-07-05 13:30 | 2013-07-05 13:57 | OTHER - 561CJ036C | 72 | 14.8 | Yes | Yes | 13 | 15.5 | -2.5 | 0C20C1BBBAE84F369FEAEE7274BEA69C |  | R22 | Non-TXV |  | 20.56% | 0.79444 | 39.5% | [5 empty] | Non-TXV | 20.56%
San Jose | CA | 95118-1817 |  | 2013-07-17 | 2013-07-17 10:11 | 2013-07-17 10:11 | TRANE - TTR042D100B0 | 81 | 0 | Yes | Yes | 23.2 | 20.1 | 3.1 | 480799E4CCC0476B85EFA15E6FAAE194 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Rafael | CA | 94903-2212 |  | 2013-07-12 | 2013-07-12 10:50 | 2013-07-12 10:55 | COLEMAN - BRC0036B | 67 | 5.6 | Yes | Yes | 18.3 | 17.7 | 0.6 | 57E514491962481AB05AF84B5EDC8DC4 |  | R22 | Non-TXV |  | 8.358% | 0.91642 | 16.06% | [5 empty] | Non-TXV | 8.358%
Antioch | CA | 94509-5210 |  | 2013-07-03 | 2013-07-03 15:33 | 2013-07-03 16:19 | CARRIER - 38EN036320 | 91 | 2.9 | Yes | Yes | 12.8 | 14.4 | -1.6 | B88D631FA6A54ADCB75EB271727C5005 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.187% | 0.96813 | 6.124% | [5 empty] | Non-TXV | 3.187%
Anderson | CA | 96007-4921 |  | 2013-07-09 | 2013-07-09 14:14 | 2013-07-09 15:02 | COLEMAN - ILLEGIBLE | 108 | 20.2 | Yes | Yes | 27.1 | 21.5 | 5.6 | 2447407B6C7248399FAFA904ECC1FB6E |  | R22 | Non-TXV |  | 18.7% | 0.81296 | 35.94% | [5 empty] | Non-TXV | 18.7%
Bakersfield | CA | 93309-2246 |  | 2013-07-05 | 2013-07-05 14:40 | 2013-07-05 15:02 | - | 85 | 16 | Yes | Yes | 20.7 | 20.7 | 0 | 51F000950D9042759E3C2082EDB3A628 |  | R22 | Non-TXV |  | 18.82% | 0.81176 | 36.17% | [5 empty] | Non-TXV | 18.82%
Kerman | CA | 93630-8925 |  | 2013-08-07 | 2013-08-07 10:05 | 2013-08-07 10:05 | BRYANT - 574BNW042060NB | 169 | 0 | Yes | Yes | 20.3 | 18.8 | 1.5 | C00A2BB602624B7A894125B5874AC504 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4379 |  | 2013-07-25 | 2013-07-25 14:10 | 2013-07-25 14:10 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 19.2 | 18.7 | 0.5 | 18C33AA32A684B3EB984FB82DFEF4991 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-7516 |  | 2013-10-23 | 2013-10-23 14:30 | 2013-10-23 14:55 | CARRIER - 38BRCFO48 | 164 | 7.2 | Yes | Yes | 21.2 | 21.5 | -0.3 | 86C87DC5BA9A47849DE2F07BA5FF3194 |  | R22 | Non-TXV |  | 4.39% | 0.9561 | 8.437% | [5 empty] | Non-TXV | 4.39%
San Jose | CA | 95116-2304 |  | 2013-10-16 | 2013-10-16 15:50 | 2013-10-16 17:11 | NORDYNE - FS3BA-036KA | 69 | -4.1 | Yes | Yes | 24.2 | 20.4 | 3.8 | 606F55D4AD904C969CEF698E3CEB8348 |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Bakersfield | CA | 93304-5631 |  | 2013-08-09 | 2013-08-09 13:22 | 2013-08-09 13:22 | YORK - DAYY-F036NJ10A | 120 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | ED91E997FF6045969C91055E945042E1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94086-6446 |  | 2013-09-27 | 2013-09-27 11:53 | 2013-09-27 12:34 | - | 85 | 3.1 | Yes | Yes | 21.8 | 20.1 | 1.7 | 7C9CF707093C4DF7BD55D10F5B0F14AB |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
San Jose | CA | 95116-3608 |  | 2013-10-15 | 2013-10-15 14:13 | 2013-10-15 14:58 | CARRIER - UNK | 86 | 4.7 | Yes | Yes | 19.5 | 20.7 | -1.2 | 51D08FF2FB2C42FDA4F8213BD4FDFA38 |  | R22 | Non-TXV |  | 5.465% | 0.94535 | 10.5% | [5 empty] | Non-TXV | 5.465%
Morgan Hill | CA | 95037-4104 |  | 2013-10-23 | 2013-10-23 12:17 | 2013-10-23 13:02 | GOODMAN - CE361G | 83 | 8 | Yes | Yes | 21.2 | 21.3 | -0.1 | FDBB4F6B63CD4FDC96002CF1C4D646A2 |  | R22 | Non-TXV |  | 9.639% | 0.90361 | 18.52% | [5 empty] | Non-TXV | 9.639%
Bakersfield | CA | 93313-4516 |  | 2013-07-19 | 2013-07-19 10:22 | 2013-07-19 11:12 | GOODMAN - CE36B3B140L004 | 85 | -3.2 | Yes | Yes | 18.8 | 21.5 | -2.7 | 593E70C7213D4D229DCAF986B08DF756 |  | R22 | TXV |  | -3.765% | 1.0376 | 1.054% |  |  |  |  | TXV |  |  | -3.765%
Davis | CA | 95616-6653 |  | 2013-07-24 | 2013-07-24 09:29 | 2013-07-24 15:29 | RHEEM - RAMA-030JAZ | 96 | 2.8 | Yes | Yes | 11.1 | 14.1 | -3 | 579E6BE8249045838F19C30C1E314AE3 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Bakersfield | CA | 93304-3821 |  | 2013-07-02 | 2013-07-02 15:34 | 2013-07-02 15:34 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.1 | 20.4 | -2.3 | 80F4E27C2A5C4D4CA47FF8BB0B7EFB00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9508 |  | 2013-09-19 | 2013-09-19 15:19 | 2013-09-19 15:19 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 22 | 21.4 | 0.6 | AF2B85E0E3BE4B7CB7FB40F6F5F2977E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4932 |  | 2013-07-24 | 2013-07-24 16:04 | 2013-07-24 17:11 | YORK - H1RC0485060 | 85 | 4.9 | Yes | Yes | 24.5 | 19.2 | 5.4 | 347E36588AC84F30938FE516231F9130 |  | R22 | TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | TXV | 5.765%
Dixon | CA | 95620-4839 |  | 2013-09-16 | 2013-09-16 12:38 | 2013-09-16 12:38 | CARRIER - 38BRC036350 | 171 | 0 | Yes | Yes | 21.1 | 17.9 | 3.2 | 700A040E92E74113BD2E449369F385D7 |  | R22 | TXV |  | 0% | 1 | 0%
Davis | CA | 95616-6656 |  | 2013-07-24 | 2013-07-24 09:56 | 2013-07-24 15:37 | RHEEM - | 96 | 3.4 | Yes | Yes | 14.7 | 15.9 | -1.2 | DD073695383F4FB58B705A29EFFB1B13 |  | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Bakersfield | CA | 93308-9509 |  | 2013-09-19 | 2013-09-19 16:10 | 2013-09-19 16:10 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 8A01160D49AE46A5A34939D911CCF4EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2200 |  | 2013-07-17 | 2013-07-17 13:32 | 2013-07-17 13:59 | TRANE - TTP042C100A3 | 162 | 18.9 | Yes | Yes | 21.1 | 16.1 | 5 | 88E70ED3B5D64B738C2D36E8E55AD825 |  | R22 | TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | TXV | 11.67%
Bakersfield | CA | 93309-5320 |  | 2013-07-03 | 2013-07-03 14:42 | 2013-07-03 15:03 | GOODMAN - GPG1324045KB | 85 | 2.8 | Yes | Yes | 17.5 | 19.7 | -2.2 | E7341AB72F24464182E7A51AD1366C6C |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Bakersfield | CA | 93309-5320 |  | 2013-07-03 | 2013-07-03 14:12 | 2013-07-03 14:32 | GOODMAN - GPG1330045M41AB | 85 | 2.6 | Yes | Yes | 16.7 | 19.5 | -2.8 | 714F6D16B3284A08BCD726C6C3BDC3BE |  | R410A | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93313-2527 |  | 2013-09-11 | 2013-09-11 19:29 | 2013-09-11 19:33 | GOODMAN - GPG13360701AB | 112 | -6.6 | Yes | Yes | 25.8 | 20.4 | 5.4 | 59CFF4B4F2004D8A8151CFB1F39D5B84 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Bakersfield | CA | 93313-5408 |  | 2013-07-16 | 2013-07-16 11:00 | 2013-07-16 11:00 | OTHER - CA9042VKD2 | 128 | 0 | Yes | Yes | 17.6 | 22.1 | -4.5 | F9F1B19E4EA24D8090E2DF59E6B72311 | Actual Subcooling cannot be negative. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4386 |  | 2013-07-25 | 2013-07-25 16:16 | 2013-07-25 16:16 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 23.9 | 20.6 | 3.3 | F4CCE680CA7E4C0AB90AB0DFD4536D02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-6118 |  | 2013-10-02 | 2013-10-02 08:20 | 2013-10-02 09:17 | LENNOX - HS10-651V1P | 147 | 11.8 | Yes | Yes | 27.1 | 21.5 | 5.6 | 1F7E5790A45C46A0BAB094568A965386 |  | R22 | TXV |  | 8.027% | 0.91973 | 15.43% | [5 empty] | TXV | 8.027%
San Jose | CA | 95122-3803 |  | 2013-10-16 | 2013-10-16 14:01 | 2013-10-16 16:17 | YORK - H2RA036S06E | 63 | 4.5 | Yes | Yes | 19.2 | 21.9 | -2.7 | 65CBE23F27A34564A0E63D4217055EDC |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Dixon | CA | 95620-2167 |  | 2013-08-16 | 2013-08-16 13:11 | 2013-08-16 16:00 | RHEEM - | 85 | 2.8 | Yes | Yes | 15.5 | 17.6 | -2.1 | 36F555491F7D43118FC4B5D3E80B9D2E |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
San Jose | CA | 95122-1147 |  | 2013-10-16 | 2013-10-16 11:15 | 2013-10-16 11:37 | CARRIER - 38BRC036300 | 113 | 9.1 | Yes | Yes | 21.5 | 20.3 | 1.2 | D9E0AF9E6A1F44F1B79B24C8575FE375 |  | R22 | Non-TXV |  | 8.053% | 0.91947 | 15.48% | [5 empty] | Non-TXV | 8.053%
Dixon | CA | 95620-2201 |  | 2013-09-16 | 2013-09-16 21:18 | 2013-09-16 21:41 | AMERICAN STANDARD - 4A7A2036A1000AB | 78 | 9.2 | Yes | Yes | 18.5 | 15.5 | 3 | 7EB50B9380F741B4BBE0721FCB0F4B2C |  | R410A | TXV |  | 11.79% | 0.88205 | 22.67% | [5 empty] | TXV | 11.79%
San Jose | CA | 95131-3220 |  | 2013-07-29 | 2013-07-29 12:42 | 2013-07-29 12:42 | TRANE - TTB724B100A1 | 67 | 0 | Yes | Yes | 18.2 | 18.5 | -0.3 | CCC94D76B1844695878C7CD09E244833 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1640 |  | 2013-07-29 | 2013-07-29 18:42 | 2013-07-29 19:00 | DUCANE - SG10B36075 | 85 | 3.3 | Yes | Yes | 21 | 20.8 | 0.2 | 0B9561CDCAA945CF897BC6AFDE47EE55 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Bakersfield | CA | 93309-4551 |  | 2013-07-26 | 2013-07-26 08:17 | 2013-07-26 09:11 | ICP - GPCM036K060F | 86 | -7.1 | Yes | Yes | 24.7 | 19.9 | 4.8 | 3D5F6F52D5334382A1AF093FA00B46F1 |  | R22 | Non-TXV |  | -8.256% | 1.0826 | 2.312% |  |  |  |  | Non-TXV |  |  | -8.256%
Gilroy | CA | 95020-3909 |  | 2013-10-22 | 2013-10-22 09:55 | 2013-10-22 10:23 | LENNOX - 13ACX-036-230-17 | 84 | 8.4 | Yes | Yes | 18.7 | 19.1 | -0.4 | B8211B92B9E44B27BC15F0D55877875F |  | R410A | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Gilroy | CA | 95020-4428 |  | 2013-07-29 | 2013-07-29 10:05 | 2013-07-29 10:36 | CARRIER - 38CKC036330 | 100 | 8.9 | Yes | Yes | 20.6 | 18.2 | 2.4 | 0859AD0A3C8F49F0A82954F56EA11EA4 |  | R22 | Non-TXV |  | 8.9% | 0.911 | 17.1% | [5 empty] | Non-TXV | 8.9%
Bakersfield | CA | 93309-6828 |  | 2013-09-05 | 2013-09-05 20:09 | 2013-09-05 20:13 | TRANE - YCY036G1M0AC | 130 | 16.7 | Yes | Yes | 21.8 | 21.3 | 0.5 | C60D7D8D4F014D25B6DF6C3CB78A353A | Add refrigerant: 12.2 oz | R22 | TXV |  | 12.85% | 0.87154 | 24.69% | [5 empty] | TXV | 12.85%
Davis | CA | 95616-7311 |  | 2013-07-03 | 2013-07-03 09:19 | 2013-07-03 09:41 | BRYANT - 563CNX036000AACA | 101 | -9.5 | Yes | Yes | 15.8 | 18.6 | -2.8 | D82608BFA55046979369B0A3D0527793 |  | R22 | Non-TXV |  | -9.406% | 1.0941 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.406%
Davis | CA | 95616-7311 |  | 2013-07-03 | 2013-07-03 09:52 | 2013-07-03 10:14 | BRYANT - 563CN036000ACAA | 101 | -7.1 | Yes | Yes | 17.3 | 19.3 | -2 | D5465BAF9C234D5C83AAE20F4468B7F4 |  | R22 | Non-TXV |  | -7.03% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.03%
San Jose | CA | 95148-2614 |  | 2013-09-17 | 2013-09-17 11:31 | 2013-09-17 12:00 | YORK - CMA06011A | 206 | 7.2 | Yes | Yes | 20.2 | 20.5 | -0.3 | AC11C8C0AC074A0CAE7A0D7CC3E2A58F |  | R22 | Non-TXV |  | 3.495% | 0.96505 | 6.717% | [5 empty] | Non-TXV | 3.495%
Cottonwood | CA | 96022-7604 |  | 2013-06-28 | 2013-06-28 10:40 | 2013-06-28 11:04 | ARMSTRONG - SCU10G24A | 63 | 2.4 | Yes | Yes | 19.9 | 20.9 | -1 | 03022C9FE6D24D72AB73B17F5DE0BE12 |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Bakersfield | CA | 93313-9813 |  | 2013-08-14 | 2013-08-14 19:29 | 2013-08-14 19:31 | OTHER - H4RC060506HG | 143 | 5.6 | Yes | Yes | 21.8 | 22.1 | -0.3 | D58A2AA73CCE4D0EA3CEE13EEEB930B7 |  | R22 | Non-TXV |  | 3.916% | 0.96084 | 7.526% | [5 empty] | Non-TXV | 3.916%
Pleasanton | CA | 94588-3734 |  | 2013-09-13 | 2013-09-13 12:27 | 2013-09-13 12:27 | CARRIER - 38CKC030340 | 89 | 0 | Yes | Yes | 19.6 | 16.9 | 2.7 | BBC62A12665F426CBA609F0B8D3A06C2 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-3186 |  | 2013-09-16 | 2013-09-16 14:28 | 2013-09-16 14:45 | HEIL - ACS036A2C1 | 69 | 3.2 | Yes | Yes | 20.2 | 18.8 | 1.4 | 2989DDF8114849B98A58D5930475FD2D |  | R22 | Non-TXV |  | 4.638% | 0.95362 | 8.913% | [5 empty] | Non-TXV | 4.638%
Clovis | CA | 93612-4636 |  | 2013-07-10 | 2013-07-10 19:59 | 2013-07-10 20:43 | PAYNE - UNK | 80 | 2.7 | Yes | Yes | 18.2 | 19.5 | -1.3 | 139280F0D4234B8698454F1C8216EE85 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Fresno | CA | 93720-3686 |  | 2013-07-11 | 2013-07-11 13:28 | 2013-07-11 14:33 | YORK - H1DE030506A | 80 | -3 | Yes | Yes | 20.6 | 21.5 | -0.9 | 4B18A0D5AB994903A5ABA59D076D6FA2 |  | R22 | TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | TXV |  |  | -3.75%
Fresno | CA | 93705-3345 |  | 2013-07-10 | 2013-07-10 10:24 | 2013-07-10 11:08 | OTHER - UKN | 80 | 5.6 | Yes | Yes | 24.2 | 19.6 | 4.7 | 3B78DCAF427E42EF85F59DDE673315FD |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93705-3230 |  | 2013-07-02 | 2013-07-02 16:06 | 2013-07-02 16:28 | BDP - 568EJ042 | 144 | 17.3 | Yes | Yes | 18.9 | 20.7 | -1.8 | 41B8748CED824C37A1542830BB805630 |  | R22 | TXV |  | 12.01% | 0.87986 | 23.09% | [5 empty] | TXV | 12.01%
Sanger | CA | 93657-1925 |  | 2013-06-28 | 2013-06-28 11:22 | 2013-06-28 11:50 | LENNOX - 13ACD04823002 | 204 | -10.8 | Yes | Yes | 21.2 | 19.3 | 1.9 | 9D1F59339F644ECBBAA271504A1C3FDC |  | R22 | Non-TXV |  | -5.294% | 1.0529 | 1.483% |  |  |  |  | Non-TXV |  |  | -5.294%
San Jose | CA | 95122-1299 |  | 2013-09-16 | 2013-09-16 11:57 | 2013-09-16 13:46 | CARRIER - 38CKCB036 321 | 71 | 7.8 | Yes | Yes | 21.4 | 19.3 | 2.1 | E0F6A4668F804A268CDD35CDB102F6FC |  | R22 | Non-TXV |  | 10.99% | 0.89014 | 21.11% | [5 empty] | Non-TXV | 10.99%
Fresno | CA | 93710-6314 |  | 2013-07-29 | 2013-07-29 11:03 | 2013-07-29 11:21 | DAY & NIGHT - UKN | 80 | 15.6 | Yes | Yes | 20.8 | 20.1 | 0.7 | BF247AD77CAC4ED5A0E468F3DFB6FBFD |  | R22 | Non-TXV |  | 19.5% | 0.805 | 37.47% | [5 empty] | Non-TXV | 19.5%
Fresno | CA | 93726-7002 |  | 2013-07-12 | 2013-07-12 10:44 | 2013-07-12 11:24 | GOODMAN - CK36-1B | 76 | 11.4 | Yes | Yes | 22.7 | 19.3 | 3.4 | DE58EFA76B0B4F20BCCAE22E0837E6DB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Cottonwood | CA | 96022-0000 |  | 2013-06-28 | 2013-06-28 12:13 | 2013-06-28 13:14 | YORK - UNK | 64 | 7.5 | Yes | Yes | 21.9 | 20.2 | 1.7 | B625A1F93CF7412E962BFB8F4514D56C |  | R22 | Non-TXV |  | 11.72% | 0.88281 | 22.52% | [5 empty] | Non-TXV | 11.72%
Bakersfield | CA | 93305-3606 |  | 2013-09-12 | 2013-09-12 19:27 | 2013-09-12 19:27 | DAY & NIGHT - 481H0AC | 85 | 0 | Yes | Yes | 20.2 | 20.1 | 0.1 | 33A457721535412A8F1D12D22BEEE78E | Add refrigerant: 10.7 oz Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1232 |  | 2013-07-03 | 2013-07-03 11:38 | 2013-07-03 12:41 | CARRIER - 4855024040311 | 92 | 7.1 | Yes | Yes | 19.9 | 18.8 | 1.1 | 7B6CF67E95CA49D6A80070CB87321B55 |  | R22 | Non-TXV |  | 7.717% | 0.92283 | 14.83% | [5 empty] | Non-TXV | 7.717%
Cottonwood | CA | 96022-0000 |  | 2013-06-28 | 2013-06-28 10:22 | 2013-06-28 10:38 | ARMSTRONG - SC U12E36A | 70 | 2.2 | Yes | Yes | 20.8 | 19 | 1.8 | 0EE86302066A4AF2A7CAF35536FEB141 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Clovis | CA | 93612-0713 |  | 2013-06-26 | 2013-06-26 12:53 | 2013-06-26 13:39 | DAY & NIGHT - 30/80YAC106T | 64 | 12 | Yes | Yes | 22.7 | 19.1 | 3.6 | 61407EF40EA74E70B4D13AB3B43EBB91 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.75% | 0.8125 | 36.03% | [5 empty] | Non-TXV | 18.75%
Bakersfield | CA | 93308-2961 |  | 2013-08-29 | 2013-08-29 15:52 | 2013-08-29 15:52 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.2 | 18.7 | 1.5 | 4C514DAEC19E40E8A993E4A65EE96296 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4009 |  | 2013-08-24 | 2013-08-24 09:38 | 2013-08-24 10:00 | DAY & NIGHT - UNK | 80 | -6.6 | Yes | Yes | 22.3 | 20.7 | 1.6 | BA2F3A62132D42A58CB7BAC57974EEB6 |  | R22 | Non-TXV |  | -8.25% | 1.0825 | 2.31% |  |  |  |  | Non-TXV |  |  | -8.25%
Fresno | CA | 93702-3963 |  | 2013-06-26 | 2013-06-26 17:45 | 2013-06-26 17:45 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | B8B00697605F488684D07DE36F383F3D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9717 |  | 2013-07-05 | 2013-07-05 13:51 | 2013-07-05 13:51 | BDP - 588ANW036080AAAF | 68 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | A89AA1115FD54460A773033052F4255A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-1299 |  | 2013-10-21 | 2013-10-21 15:34 | 2013-10-21 16:54 | COLEMAN - 2436-90J | 62 | 2.4 | Yes | Yes | 24.1 | 19.3 | 4.8 | 7E747C260FBC4A44AC787B2DBC35DD31 |  | R22 | Non-TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | Non-TXV | 3.871%
Vacaville | CA | 95688-3622 |  | 2013-06-27 | 2013-06-27 14:10 | 2013-06-27 14:10 | PHILCO - RAKA-037JAZ | 79 | 0 | Yes | Yes | 15.5 | 13.9 | 1.7 | 9ED7CCB4DEA24C518085A2138DA1BD1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-6575 |  | 2013-07-03 | 2013-07-03 12:10 | 2013-07-03 12:10 | PAYNE - PA10JA0300000AGAA | 71 | 13 | Yes | Yes | 15.2 | 17.5 | -2.3 | F935EC9B55E3496595402E06F85EFC0F | Add refrigerant: 13 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.31% | 0.8169 | 35.19% | [5 empty] | Non-TXV | 18.31%
Clovis | CA | 93611-1481 |  | 2013-07-03 | 2013-07-03 09:32 | 2013-07-03 10:27 | CARRIER - 58OAN048050 | 88 | 5.1 | Yes | Yes | 23.3 | 20.5 | 2.8 | FC8E30F3E0B24538B85A42054B6BA7A0 |  | R22 | Non-TXV |  | 5.795% | 0.94205 | 11.14% | [5 empty] | Non-TXV | 5.795%
Fresno | CA | 93710-4036 |  | 2013-07-02 | 2013-07-02 10:14 | 2013-07-02 10:41 | BRYANT - 582ANW036090AAAF | 56 | 4.4 | Yes | Yes | 19 | 19.6 | -0.6 | 6390A40689134057857822C9F7A8D379 |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
San Jose | CA | 95122-1299 |  | 2013-09-30 | 2013-09-30 09:48 | 2013-09-30 10:23 | COLEMAN - 7842-991 | 93 | 11.6 | Yes | Yes | 25.9 | 20.4 | 5.5 | DFFCF904DE94480982B25A4D2BB0A04D |  | R22 | Non-TXV |  | 12.47% | 0.87527 | 23.97% | [5 empty] | Non-TXV | 12.47%
Clovis | CA | 93612-2257 |  | 2013-07-10 | 2013-07-10 09:57 | 2013-07-10 13:36 | GOODMAN - GPG1324045M41AC | 80 | 0 | Yes | Yes | 20.6 | 14.7 | 5.9 | A5F5AD52E3CA4095A854F3268237660C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2543 |  | 2013-07-09 | 2013-07-09 14:40 | 2013-07-09 14:59 | GOODMAN - GPG13360451AB | 112 | 5.2 | Yes | Yes | 20.6 | 21.8 | -1.2 | 23CA8B67BD6B4B5BA99271F4BD6ED8C4 |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
San Jose | CA | 95122-1299 |  | 2013-07-25 | 2013-07-25 14:43 | 2013-07-25 14:43 | OTHER - 2436-901 | 140 | 0 | Yes | Yes | 20.1 | 17.3 | 2.8 | 6030C5DB96E440BD867D20773F53D1CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2143 |  | 2013-08-02 | 2013-08-02 10:08 | 2013-08-02 10:24 | TRANE - YCY048F1H0AB | 177 | 5.9 | Yes | Yes | 27 | 21 | 6 | BE3FC4DB9E9D40C99066277AE7A5710A |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Clovis | CA | 93619-8214 |  | 2013-07-03 | 2013-07-03 14:45 | 2013-07-03 15:56 | CARRIER - 48NMX0601LBE | 118 | 13 | Yes | Yes | 22.2 | 20.2 | 2 | 332A7086F938420BA758AB4D0104D8E6 |  | R22 | Non-TXV |  | 11.02% | 0.88983 | 21.17% | [5 empty] | Non-TXV | 11.02%
Bakersfield | CA | 93313-2412 |  | 2013-07-09 | 2013-07-09 18:44 | 2013-07-09 18:55 | PAYNE - PYPNB03360090AAAA | 116 | 4.4 | Yes | Yes | 23.3 | 21.5 | 1.8 | C3493F76AA62403ABE72AB8BE8B5E858 |  | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Clovis | CA | 93612-2257 |  | 2013-07-10 | 2013-07-10 13:39 | 2013-07-10 13:39 | GOODMAN - GPG1324045M41AC | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F3829FF6BBB14AD1880F13268B485D4F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6232 |  | 2013-07-11 | 2013-07-11 17:55 | 2013-07-11 18:04 | GOODMAN - GPG15370904AA | 112 | 5.5 | Yes | Yes | 26.8 | 21 | 5.8 | B01352727BDB48E8BB1422E7EC8FB413 |  | R410A | Non-TXV |  | 4.911% | 0.95089 | 9.437% | [5 empty] | Non-TXV | 4.911%
Bakersfield | CA | 93307-5582 |  | 2013-08-08 | 2013-08-08 01:31 | 2013-08-08 01:50 | YORK - D1NP036N05606A | 108 | 14.1 | Yes | Yes | 21.4 | 21.5 | -0.1 | 5C36A8CD3A0A4C72A7589FC5B0392EFA |  | R22 | Non-TXV |  | 13.06% | 0.86944 | 25.09% | [5 empty] | Non-TXV | 13.06%
Selma | CA | 93662-4515 |  | 2013-07-17 | 2013-07-17 10:36 | 2013-07-17 10:55 | LENNOX - HS260366P | 103 | 25.9 | Yes | Yes | 17.5 | 18.2 | -0.7 | 298F94E85A024C94B110A28F6DD16206 |  | R22 | Non-TXV |  | 25.15% | 0.74854 | 48.32% | [5 empty] | Non-TXV | 25.15%
Redding | CA | 96001-9776 |  | 2013-07-17 | 2013-07-17 12:45 | 2013-07-17 13:11 | RHEEM - RQNA B036JIK 00 | 122 | 10.8 | Yes | Yes | 23.1 | 20.8 | 2.3 | 7FE9251E2C5B4DC49D1BAF65DC0CC752 |  | R22 | Non-TXV |  | 8.852% | 0.91148 | 17.01% | [5 empty] | Non-TXV | 8.852%
Fresno | CA | 93705-0748 |  | 2013-07-05 | 2013-07-05 14:49 | 2013-07-05 16:11 | GOODMAN - GPG1524070407041AA | 84 | 7 | Yes | Yes | 26.8 | 21 | 5.8 | 647FD43FB5F14AA2836E5DF7D47B89D2 |  | R410A | TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | TXV | 8.333%
Sanger | CA | 93657-2722 |  | 2013-06-28 | 2013-06-28 16:25 | 2013-06-28 16:25 | NORDYNE - GR6GDX36K072X | 112 | 0 | Yes | Yes | 28.1 | 24.2 | 3.9 | 96E842210FFA43F387B22EFF6C5E45AB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1286 |  | 2013-07-02 | 2013-07-02 10:28 | 2013-07-02 10:28 | CARRIER - UKN | 80 | 0 | Yes | Yes | 18.2 | 17.5 | 0.7 | 88D393589E064E69AF2666EDEDAFDF57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1738 |  | 2013-06-27 | 2013-06-27 10:04 | 2013-06-27 10:53 | TEMPSTAR - PGF324040K01 | 64 | 4.4 | Yes | Yes | 20.6 | 19.3 | 1.3 | 58975E64AD7C4C6E807D525B42FEA5FB |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
San Jose | CA | 95132-1786 |  | 2013-10-14 | 2013-10-14 11:52 | 2013-10-14 13:55 | CARRIER - 24ACR34BA300 | 146 | 7.2 | Yes | Yes | 20.7 | 21.7 | -1 | 2CBB9651B7D342F88E2AB24F51D0C55F |  | R22 | Non-TXV |  | 4.932% | 0.95068 | 9.477% | [5 empty] | Non-TXV | 4.932%
Fresno | CA | 93710-4020 |  | 2013-07-10 | 2013-07-10 15:43 | 2013-07-10 15:43 | AMERICAN STANDARD - YCP060F1M0AA | 160 | 0 | Yes | Yes | 15 | 16.1 | -1.1 | 5B913F329C564F4682F05AF572F70D85 | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
San Rafael | CA | 94901-8325 |  | 2013-07-10 | 2013-07-10 10:30 | 2013-07-10 10:31 | CARRIER - 38TZA030300 | 82 | -5.8 | Yes | Yes | 17 | 17.6 | -0.6 | 537FD7362AAC4F80BF78D7ABB5061A54 |  | R410A | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Fresno | CA | 93726-0210 |  | 2013-07-10 | 2013-07-10 11:24 | 2013-07-10 11:24 | OTHER - 10AJB360A5 | 80 | 0 | Yes | Yes | 24.1 | 19.2 | 4.9 | 7A2EF26D0AA8466C8D82B2BB86FD3615 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-1747 |  | 2013-07-20 | 2013-07-20 10:44 | 2013-07-20 10:44 | YORK - HP036X1021A | 92 | 31.8 | Yes | Yes | 12.5 | 17.5 | -5 | 35C23F4B17124B82A6F6F79222061201 | Add refrigerant: 31.8 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 34.57% | 0.65435 | 66.43% | [5 empty] | Non-TXV | 34.57%
Bakersfield | CA | 93304-4227 |  | 2013-07-02 | 2013-07-02 16:58 | 2013-07-02 16:58 | YORK - D3NZ042N06506NXA | 78 | 0 | Yes | Yes | 19.6 | 19.2 | 0.4 | 5E5612ED04A84EB8949C31680EA98B64 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-3320 |  | 2013-10-16 | 2013-10-16 14:56 | 2013-10-16 15:28 | TRANE - 2TTR3036A1000AA | 101 | -12.1 | Yes | Yes | 25.2 | 19.7 | 5.5 | C08BF3DF9AA7490592DE39CCCEDA440D |  | R22 | TXV |  | -11.98% | 1.1198 | 3.355% |  |  |  |  | TXV |  |  | -11.98%
Bakersfield | CA | 93305-2404 |  | 2013-06-27 | 2013-06-27 13:56 | 2013-06-27 13:56 | AMERICAN STANDARD - YCY036G1M0AD | 129 | 0 | Yes | Yes | 13.5 | 16.5 | -3 | C83858C0986745E6A725ECEA1BFD24D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1017 |  | 2013-07-08 | 2013-07-08 11:19 | 2013-07-08 11:45 | - UNK | 215 | 6.4 | Yes | Yes | 25.2 | 19.7 | 5.5 | DF556ADD313D43B9A65FAC8BBD0A501F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.977% | 0.97023 | 5.721% | [5 empty] | Non-TXV | 2.977%
Davis | CA | 95618-6373 |  | 2013-09-26 | 2013-09-26 13:14 | 2013-09-26 15:44 | DAY & NIGHT - 598AN036-B | 196 | 3.5 | Yes | Yes | 14.5 | 17.2 | -2.6 | 325B4DA9FA63464E916074C203ECE332 |  | R22 | Non-TXV |  | 1.786% | 0.98214 | 3.432% | [5 empty] | Non-TXV | 1.786%
Fresno | CA | 93710-4210 |  | 2013-07-01 | 2013-07-01 14:42 | 2013-07-01 15:04 | GOODMAN - PGB03675 | 60 | 3.8 | Yes | Yes | 20.7 | 19.1 | 1.6 | 90710648208B451FAB0697E2FFA0AE23 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Bakersfield | CA | 93313-3032 |  | 2013-07-09 | 2013-07-09 18:29 | 2013-07-09 18:48 | RUUD - N/A | 85 | 4.1 | Yes | Yes | 22.2 | 20.8 | 1.4 | 0312304A89AB4F15B8F0F631B796C67A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fresno | CA | 93705-0357 |  | 2013-07-06 | 2013-07-06 11:17 | 2013-07-06 11:35 | LENNOX - 12GCS036X75 | 110 | 3.3 | Yes | Yes | 24.9 | 21.5 | 3.4 | 0C9B8B1933D749B78248C51EE6ADB32E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Sanger | CA | 93657-4102 |  | 2013-07-03 | 2013-07-03 10:14 | 2013-07-03 10:45 | YORK - D1NA030N03606A | 72 | 6.5 | Yes | Yes | 19.2 | 19.3 | -0.1 | 0FB976D3146F43B688E52C5E479DFDE2 |  | R22 | Non-TXV |  | 9.028% | 0.90972 | 17.35% | [5 empty] | Non-TXV | 9.028%
Fairfield | CA | 94534-6865 |  | 2013-10-10 | 2013-10-10 09:40 | 2013-10-10 09:41 | KENMORE - TCA448AKA1 | 297 | -17.5 | Yes | Yes | 16.9 | 17 | -0.1 | 15B201FB7BEF41F7BA3730E82BD82C59 |  | R22 | Non-TXV |  | -5.892% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.892%
Bakersfield | CA | 93313-4131 |  | 2013-08-14 | 2013-08-14 19:05 | 2013-08-14 19:08 | YORK - D1NH048N06506G | 128 | 4.4 | Yes | Yes | 25 | 21 | 4.1 | 09D4F1EF876B4D6B8ECFAE48080C610C |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Fresno | CA | 93703-2664 |  | 2013-07-31 | 2013-07-31 16:34 | 2013-07-31 17:06 | YORK - DCYZF024NO45B | 51 | 2 | Yes | Yes | 25.6 | 20.8 | 4.8 | C131620DC79F4D38893B6FD652F5D26D |  | R410A | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Fresno | CA | 93710-4229 |  | 2013-07-09 | 2013-07-09 15:38 | 2013-07-09 15:57 | RHEEM - RRKA-A042JK08X | 69 | 3.3 | Yes | Yes | 22.2 | 20.7 | 1.6 | 2A35712A7E9647C2BC0E44D508D6323C |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Kerman | CA | 93630-2516 |  | 2013-07-08 | 2013-07-08 13:19 | 2013-07-08 14:05 | CARRIER - 48GX042060301 | 117 | 5.6 | Yes | Yes | 22.4 | 21 | 1.5 | A94C8A0B2DF14658A1698753631FF6F4 |  | R22 | Non-TXV |  | 4.786% | 0.95214 | 9.198% | [5 empty] | Non-TXV | 4.786%
Bakersfield | CA | 93313-9812 |  | 2013-07-19 | 2013-07-19 16:01 | 2013-07-19 16:36 | YORK - H2RC048S06HG | 119 | 5.9 | Yes | Yes | 21.5 | 19.1 | 2.5 | BFBD348B4A414066B815D74254655290 |  | R22 | TXV |  | 4.958% | 0.95042 | 9.528% | [5 empty] | TXV | 4.958%
Clovis | CA | 93611-4519 |  | 2013-08-02 | 2013-08-02 16:39 | 2013-08-02 16:39 | DAY & NIGHT - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | B6244EBD9CCC4342A938B664F3132EB4 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1278 |  | 2013-07-02 | 2013-07-02 09:38 | 2013-07-02 10:02 | CARRIER - UKN | 80 | 4 | Yes | Yes | 23 | 18.9 | 4.1 | 86DBAC17BD9D459FA8491A41848A3B6A |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Lamont | CA | 93241-1747 |  | 2013-07-20 | 2013-07-20 11:06 | 2013-07-20 12:27 | YORK - HP06X1021A | 92 | -6.5 | Yes | Yes | 23.5 | 18.3 | 5.2 | 6543C9F56F24490BBA616B1E47C363BB |  | R22 | Non-TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.065%
Fresno | CA | 93704-1353 |  | 2013-07-12 | 2013-07-12 13:34 | 2013-07-12 14:11 | LENNOX - GCS20H-311-75-`P | 85 | 3.2 | Yes | Yes | 20.9 | 20.4 | 0.5 | C24BCEACC4B44BB18E09039009AB73AE |  | R22 | TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | TXV | 3.765%
Bakersfield | CA | 93304-4339 |  | 2013-07-01 | 2013-07-01 10:02 | 2013-07-01 10:22 | PAYNE - P42PNB036060AAAA | 82 | 12.5 | Yes | Yes | 19.2 | 20.4 | -1.2 | C700F8ECCCB443E3B207F35E9C0FF851 |  | R22 | Non-TXV |  | 15.24% | 0.84756 | 29.3% | [5 empty] | Non-TXV | 15.24%
Mc Farland | CA | 93250-1608 |  | 2013-07-29 | 2013-07-29 18:28 | 2013-07-29 18:45 | RHEEM - CH803621C | 49 | 10.3 | Yes | Yes | 23.4 | 19.7 | 3.7 | F54E81CC816E425CAD72EE18EB9A882A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.02% | 0.7898 | 40.4% | [5 empty] | Non-TXV | 21.02%
Bakersfield | CA | 93313-9813 |  | 2013-07-19 | 2013-07-19 12:45 | 2013-07-19 12:45 | YORK - H4RC060S06HG | 143 | 0 | Yes | Yes | 21 | 21.8 | -0.8 | A655DFAC736243A18BA90E3A3CBADDA6 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-24 | 2013-07-24 17:56 | 2013-07-24 17:56 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19 | 19.7 | -0.7 | 46F7652F5B6B489395501437BD85E176 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ukiah | CA | 95482-3391 |  | 2013-08-22 | 2013-08-22 13:14 | 2013-08-22 13:37 | DAY & NIGHT - 593BJX030000AAAA | 84 | 10.6 | Yes | Yes | 25.4 | 20.4 | 5 | 135B6C1F8DA9405D983D29396AD68BD9 |  | R22 | Non-TXV |  | 12.62% | 0.87381 | 24.25% | [5 empty] | Non-TXV | 12.62%
San Rafael | CA | 94903-1844 |  | 2013-09-17 | 2013-09-17 13:26 | 2013-09-17 13:26 | PAYNE - PA13NR048-C | 195 | 0 | Yes | Yes | 17.2 | 17.1 | 0.1 | 0EA3A6B028014E67A304E8C4391AA39B |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2168 |  | 2013-08-31 | 2013-08-31 15:57 | 2013-08-31 15:57 | ICP - PGC030K060A | 80 | 0 | Yes | Yes | 21.8 | 21.4 | 0.4 | 9B43797A49474566967A2D8B470BB6D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4305 |  | 2013-11-01 | 2013-11-01 14:02 | 2013-11-01 14:25 | YORK - D1NA036N05606C | 67 | 2 | Yes | Yes | 23.1 | 19.5 | 3.6 | B005D2EE15E9479C80D6D28F7487704E |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Bakersfield | CA | 93304-6020 |  | 2013-07-03 | 2013-07-03 12:17 | 2013-07-03 13:01 | GOODMAN - GPG13420901AB | 107 | 14.3 | Yes | Yes | 19.6 | 18.8 | 0.8 | 58BD0E1912BD469DA7DB6CE16B5FD5D2 |  | R22 | Non-TXV |  | 13.36% | 0.86636 | 25.68% | [5 empty] | Non-TXV | 13.36%
Bakersfield | CA | 93304-4511 |  | 2013-08-09 | 2013-08-09 11:54 | 2013-08-09 12:21 | YORK - DAYP-F036N070A | 108 | 13.7 | Yes | Yes | 22 | 21.5 | 0.5 | B344C91F2911469E97F4C8861A29BE21 |  | R22 | Non-TXV |  | 12.69% | 0.87315 | 24.38% | [5 empty] | Non-TXV | 12.69%
Fresno | CA | 93710-4347 |  | 2013-07-02 | 2013-07-02 11:55 | 2013-07-02 12:29 | TRANE - YCC030F1M0BE | 69 | 6.7 | Yes | Yes | 21.3 | 19.9 | 1.4 | 87B9A0488AD040A0982288D7C6F258F8 |  | R22 | Non-TXV |  | 9.71% | 0.9029 | 18.66% | [5 empty] | Non-TXV | 9.71%
Clovis | CA | 93612-1671 |  | 2013-08-02 | 2013-08-02 11:36 | 2013-08-02 11:54 | OTHER - UKN | 80 | 5.7 | Yes | Yes | 16 | 18.8 | -2.8 | 2773720165814C369F893DDD24A7B7C8 |  | R22 | TXV |  | 7.125% | 0.92875 | 13.69% | [5 empty] | TXV | 7.125%
Bakersfield | CA | 93313-0000 |  | 2013-08-06 | 2013-08-06 08:44 | 2013-08-06 09:15 | UNITARY PRODUCTS GROUP - H4RC060S06HG | 143 | 4.7 | Yes | Yes | 27.3 | 21.5 | 5.8 | 6A619E919D1F43259201074EDF947D2B |  | R22 | Non-TXV |  | 3.287% | 0.96713 | 6.316% | [5 empty] | Non-TXV | 3.287%
Selma | CA | 93662-3036 |  | 2013-06-26 | 2013-06-26 09:34 | 2013-06-26 09:59 | AMANA - UNK | 85 | 6.3 | Yes | Yes | 22.9 | 17.5 | 5.4 | 08789F3E23FB4EB0B93737778471C732 |  | R22 | Non-TXV |  | 7.412% | 0.92588 | 14.24% | [5 empty] | Non-TXV | 7.412%
San Jose | CA | 95127-2646 |  | 2013-07-19 | 2013-07-19 10:45 | 2013-07-19 11:27 | AMERICAN STANDARD - 7A0048A100A0 | 123 | 19 | Yes | Yes | 16.5 | 17.1 | -0.6 | 180FFC7813814DD39449A85652E4C339 |  | R22 | Non-TXV |  | 15.45% | 0.84553 | 29.69% | [5 empty] | Non-TXV | 15.45%
Bakersfield | CA | 93313-4304 |  | 2013-07-12 | 2013-07-12 18:46 | 2013-07-12 19:09 | CARRIER - NLT036---3--C-2 | 85 | 3.6 | Yes | Yes | 21.2 | 20.9 | 0.3 | BC03DA55BBA84765A6E355FC93B34B63 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
San Jose | CA | 95111-1552 |  | 2013-10-08 | 2013-10-08 11:54 | 2013-10-08 12:27 | NORDYNE - JS3BA-036KA | 69 | 6 | Yes | Yes | 24.8 | 19.7 | 5.1 | 2065BDE997204C35ABA72A68D9781C26 |  | R22 | Non-TXV |  | 8.696% | 0.91304 | 16.71% | [5 empty] | Non-TXV | 8.696%
Clovis | CA | 93611-6657 |  | 2013-06-26 | 2013-06-26 15:30 | 2013-06-26 15:51 | LENNOX - 10ACB42 | 87 | 6.3 | Yes | Yes | 19 | 16.2 | 2.8 | 79CE37606D8848C3BA231B08959A674E |  | R22 | TXV |  | 7.241% | 0.92759 | 13.92% | [5 empty] | TXV | 7.241%
Bakersfield | CA | 93313-4106 |  | 2013-08-09 | 2013-08-09 15:23 | 2013-08-09 16:04 | RUUD - ILLEGIBLE | 97 | 16.4 | Yes | Yes | 27.2 | 21.4 | 5.8 | 34C6398CA2AB4703966C831E07307822 |  | R22 | Non-TXV |  | 16.91% | 0.83093 | 32.49% | [5 empty] | Non-TXV | 16.91%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 16:48 | 2013-07-23 16:48 | CARRIER - 38YCC024340 | 68 | 0 | Yes | Yes | 22.1 | 19.5 | 2.7 | CA3FEF12481C4C2ABA857E25AC72FB3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5442 |  | 2013-07-10 | 2013-07-10 15:56 | 2013-07-10 15:56 | PAYNE - 565BJ042 | 94 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 1E13BB4E729F4940B1A2EF2D085DD2AD | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5301 |  | 2013-07-01 | 2013-07-01 10:12 | 2013-07-01 10:12 | RHEEM - UNK | 85 | 0 | Yes | Yes | 22.1 | 20.4 | 1.7 | 63F733889717460FB53A97F4DCC4F483 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-8945 |  | 2013-07-09 | 2013-07-09 12:07 | 2013-07-09 12:32 | AMERICAN STANDARD - 24CC3036AC064AA | 82 | -6.7 | Yes | Yes | 19.5 | 19.5 | 0.1 | 1DB6D830D11048F893A4A7C94590654D |  | R22 | TXV |  | -8.171% | 1.0817 | 2.288% |  |  |  |  | TXV |  |  | -8.171%
Selma | CA | 93662-2508 |  | 2013-08-28 | 2013-08-28 13:42 | 2013-08-28 13:42 | RHEEM - RRKAA042JK08X | 71 | 0 | Yes | Yes | 26.1 | 22.4 | 3.7 | B655CB7A1F7649B78997226100661559 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2508 |  | 2013-08-28 | 2013-08-28 14:03 | 2013-08-28 14:33 | LENNOX - UNK | 77 | 12.4 | Yes | Yes | 15.9 | 17.4 | -1.5 | D20C09AEC3A64799AD6C046257ECA49D |  | R22 | Non-TXV |  | 16.1% | 0.83896 | 30.95% | [5 empty] | Non-TXV | 16.1%
Selma | CA | 93662-2508 |  | 2013-06-26 | 2013-06-26 10:45 | 2013-06-26 11:04 | RHEEM - PRKAA042JK08X | 69 | 2.9 | Yes | Yes | 22.2 | 18.5 | 3.7 | A4FBC27E11FF497BA5775C0E7FB445CB |  | R22 | Non-TXV |  | 4.203% | 0.95797 | 8.077% | [5 empty] | Non-TXV | 4.203%
San Jose | CA | 95122-3045 |  | 2013-09-16 | 2013-09-16 14:47 | 2013-09-16 17:33 | TRANE - 2TTB0036A1000 | 76 | 2.5 | Yes | Yes | 22 | 20.1 | 1.9 | F84263A03D1E43738C0E8777688BB78E |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Santa Rosa | CA | 95405-8152 |  | 2013-07-22 | 2013-07-22 09:30 | 2013-07-22 09:30 | RUUD - UAKA-037JAZ | 79 | 0 | Yes | Yes | 15.1 | 17.6 | -2.5 | 1856453F4776498B9733E51DFC7AFA60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5505 |  | 2013-07-01 | 2013-07-01 10:47 | 2013-07-01 11:04 | CARRIER - 48NLX042 | 80 | 4.4 | Yes | Yes | 20.5 | 15.5 | 5 | 1EFD49DA335B4420B3E91F55156B0D34 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Fresno | CA | 93727-1828 |  | 2013-07-31 | 2013-07-31 14:51 | 2013-07-31 14:51 | OTHER - DCYZF030N070C | 64 | 2.5 | Yes | Yes | 27.6 | 21.5 | 6.1 | 83185A681A454CB087AE59DB52ED94EA | Add refrigerant: 2.5 oz | R410A | Non-TXV |  | 3.906% | 0.96094 | 7.507% | [5 empty] | Non-TXV | 3.906%
Selma | CA | 93662-2561 |  | 2013-07-10 | 2013-07-10 15:50 | 2013-07-10 16:14 | OTHER - 585GJ036060 | 82 | 6.2 | Yes | Yes | 23.3 | 20.4 | 2.9 | 52C4E96E7E4341CAAA768B4D4B57B107 |  | R22 | Non-TXV |  | 7.561% | 0.92439 | 14.53% | [5 empty] | Non-TXV | 7.561%
Vacaville | CA | 95687-5114 |  | 2013-09-06 | 2013-09-06 12:22 | 2013-09-06 12:22 | AMANA - RCB48C2B | 116 | 0 | Yes | Yes | 14.6 | 17.2 | -2.6 | 7BCC50AB26374982B75AD996BB09D82E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-8398 |  | 2013-07-09 | 2013-07-09 11:24 | 2013-07-09 12:02 | LENNOX - HS26-042-2P | 107 | 11.6 | Yes | Yes | 23.2 | 20.1 | 3.2 | CA1AE5C81ED546FC9BBB695A98C74B6F |  | R22 | TXV |  | 10.84% | 0.89159 | 20.83% | [5 empty] | TXV | 10.84%
Cottonwood | CA | 96022-8553 |  | 2013-06-28 | 2013-06-28 08:57 | 2013-06-28 09:42 | CARRIER - UNK | 67 | 3.4 | Yes | Yes | 18.8 | 20.2 | -1.4 | 212EACD2C29E49A9B608B935286A8187 |  | R22 | Non-TXV |  | 5.075% | 0.94925 | 9.752% | [5 empty] | Non-TXV | 5.075%
Fresno | CA | 93710-4734 |  | 2013-07-01 | 2013-07-01 10:52 | 2013-07-01 11:20 | PAYNE - UNK | 80 | 8 | Yes | Yes | 17 | 19.9 | -2.9 | 05DDCD32509B41E488685F1CC0128F1C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Sanger | CA | 93657-4104 |  | 2013-08-06 | 2013-08-06 17:01 | 2013-08-06 17:01 | BRYANT - 582ANW030040AAAD | 59 | 0 | Yes | Yes | 23.5 | 21.4 | 2.1 | 5A9053EB005141B3B7A3C54283FA2040 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4382 |  | 2013-07-25 | 2013-07-25 14:46 | 2013-07-25 14:46 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 20.4 | 19.3 | 1.1 | F9A7E1C899E846B8B3A4C2B50A1D47AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-7901 |  | 2013-07-13 | 2013-07-13 12:39 | 2013-07-13 13:14 | WEATHER KING - 10AJB60A01 | 114 | 3.7 | Yes | Yes | 26.2 | 20.6 | 5.6 | 622CFC528E01489983DA6748E7010599 |  | R22 | Non-TXV |  | 3.246% | 0.96754 | 6.237% | [5 empty] | Non-TXV | 3.246%
Bakersfield | CA | 93306-5835 |  | 2013-10-01 | 2013-10-01 13:12 | 2013-10-01 13:12 | ICP - PGF030K060A | 52 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | EE2B53755D794C8493541DA0B85A70EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-3240 |  | 2013-09-05 | 2013-09-05 08:42 | 2013-09-05 09:24 | PAYNE - PY1PNB030060AAAA | 57 | -5.7 | Yes | Yes | 19.4 | 18.2 | 1.2 | 9462EAF40D5F4B4088512893C83EF37D |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Fairfield | CA | 94534-4334 |  | 2013-09-19 | 2013-09-19 10:30 | 2013-09-19 10:31 | TRANE - 2TTB3042A1000AA | 109 | 4 | Yes | Yes | 18.3 | 17.9 | 0.4 | CED382F9FC1B451284A824B810209AC0 |  | R22 | Non-TXV |  | 3.67% | 0.9633 | 7.052% | [5 empty] | Non-TXV | 3.67%
Bakersfield | CA | 93304-1200 |  | 2013-09-21 | 2013-09-21 16:11 | 2013-09-21 16:11 | OTHER - UKN | 60 | 0 | Yes | Yes | 22.2 | 21.4 | 0.8 | F18119D9F83946D6BE7C15F9B7142125 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-5310 |  | 2013-06-27 | 2013-06-27 13:41 | 2013-06-27 13:41 | - RCE36A2A | 150 | 0 | Yes | Yes | 17.1 | 18.7 | -1.6 | EC9E3FD75A27436A8F7DAFC21C4A4F21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4101 |  | 2013-09-25 | 2013-09-25 12:46 | 2013-09-25 12:46 | BDP - 589ANW04280ACBF | 87 | 0 | Yes | Yes | 22.4 | 22.1 | 0.3 | A9325C36DC404E9CA08A58545651F108 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4314 |  | 2013-11-07 | 2013-11-07 15:18 | 2013-11-07 15:53 | RHEEM - RRNLB030JK06X | 77 | 5 | Yes | Yes | 21.8 | 19.5 | 2.3 | 9A36C2292DDA4FE7B7501412C7B918E6 |  | R410A | Non-TXV |  | 6.494% | 0.93506 | 12.48% | [5 empty] | Non-TXV | 6.494%
Fresno | CA | 93710-4214 |  | 2013-07-10 | 2013-07-10 12:19 | 2013-07-10 12:43 | YORK - D1NH036N05606C | 108 | 7.9 | Yes | Yes | 25 | 20.2 | 4.9 | 6687F5F927EB4862B1AF72EDF253A4DF |  | R22 | Non-TXV |  | 7.315% | 0.92685 | 14.06% | [5 empty] | Non-TXV | 7.315%
Sanger | CA | 93657-3326 |  | 2013-06-28 | 2013-06-28 15:23 | 2013-06-28 15:23 | RHEEM - RRPLB030JK06X | 77 | 0 | Yes | Yes | 18.1 | 19.3 | -1.2 | 0E479328F382477B98CBB4A4CC42AC7D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9810 |  | 2013-07-19 | 2013-07-19 11:31 | 2013-07-19 12:02 | YORK - H2RC048S06HG | 125 | 6 | Yes | Yes | 19 | 20.1 | -1.1 | 522524295E2A45B2A751B37C94762B2D |  | R22 | TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | TXV | 4.8%
Cottonwood | CA | 96022-9358 |  | 2013-06-27 | 2013-06-27 08:16 | 2013-06-27 08:44 | WESTINGHOUSE - FS3BA 060 | 114 | -8 | Yes | Yes | 20.4 | 21 | -0.6 | 9C71DC3DDF7B4EAC9110F2AB2EA298B3 |  | R22 | Non-TXV |  | -7.018% | 1.0702 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.018%
Cottonwood | CA | 96022-9358 |  | 2013-06-27 | 2013-06-27 11:01 | 2013-06-27 11:17 | WESTINGHOUSE - FS3BA 024 | 82 | 2.7 | Yes | Yes | 21.3 | 21 | 0.3 | CC84E23BC7C84451AC08C6CB6026B9F0 |  | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Bakersfield | CA | 93304-1246 |  | 2013-09-21 | 2013-09-21 15:55 | 2013-09-21 15:55 | YORK - D3N2024N03600NXC | 58 | 0 | Yes | Yes | 22 | 22.1 | -0.1 | 655DF657AED2407D980B6FD08E3ACF82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9107 |  | 2013-07-01 | 2013-07-01 15:30 | 2013-07-01 16:00 | - 585EJ024050 | 85 | -5 | Yes | Yes | 18.4 | 17.6 | 0.8 | 0E90C2B0FB8F43D0A80E9482001FB1C7 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93722-3080 |  | 2013-07-08 | 2013-07-08 12:49 | 2013-07-08 13:36 | OTHER - FADC048JAS | 112 | 5.8 | Yes | Yes | 17.1 | 19.7 | -2.6 | 0FC6D64A21294BB782484350D8993541 |  | R22 | Non-TXV |  | 5.179% | 0.94821 | 9.952% | [5 empty] | Non-TXV | 5.179%
Bakersfield | CA | 93307-4380 |  | 2013-07-25 | 2013-07-25 15:54 | 2013-07-25 15:54 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 20.5 | 20.8 | -0.3 | 74FB7EB303DB4736BBC663E42462839F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3522 |  | 2013-07-30 | 2013-07-30 13:11 | 2013-07-30 13:36 | YORK - H2RC036506G | 83 | -22.1 | Yes | Yes | 15.5 | 18.5 | -3 | 0E3B1F53E5A24D9D967D215BD5C152C6 |  | R22 | TXV |  | -26.63% | 1.2663 | 7.457% |  |  |  |  | TXV |  |  | -26.63%
Bakersfield | CA | 93307-4383 |  | 2013-07-25 | 2013-07-25 15:35 | 2013-07-25 15:35 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 20.7 | 19.8 | 0.9 | 9C06BE37C2934FE09847F214FC97D310 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4115 |  | 2013-06-26 | 2013-06-26 11:32 | 2013-06-26 11:56 | CARRIER - UNK | 85 | 6.2 | Yes | Yes | 19.6 | 19.1 | 0.5 | A886B06418644D7BBF334CE63D8F699F |  | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Fresno | CA | 93703-1441 |  | 2013-09-05 | 2013-09-05 09:41 | 2013-09-05 09:41 | OTHER - DBYZ-F036N070A | 112 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 9F5579CFC4B84A9FBFC003E201E4CEB2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Davis | CA | 95616-4012 |  | 2013-08-14 | 2013-08-14 11:03 | 2013-08-14 11:03 | YORK - D2NZ036N05606NXA | 112 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | FBC034E90B444B9AACEEE428851C2AEC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2930 |  | 2013-07-10 | 2013-07-10 14:10 | 2013-07-10 15:07 | CARRIER - 48GS042090301 | 100 | 5.6 | Yes | Yes | 25 | 21.3 | 3.7 | 2663B675BF8440A4953F5EB5BFACAD18 |  | R22 | Non-TXV |  | 5.6% | 0.944 | 10.76% | [5 empty] | Non-TXV | 5.6%
Fresno | CA | 93702-3523 |  | 2013-10-15 | 2013-10-15 11:48 | 2013-10-15 12:34 | RHEEM - RRKAA036JK06X | 62 | -5.8 | Yes | Yes | 21.3 | 18.8 | 2.5 | 999831D6870C44B4AB6703C07BF06395 |  | R22 | Non-TXV |  | -9.355% | 1.0935 | 2.62% |  |  |  |  | Non-TXV |  |  | -9.355%
Sanger | CA | 93657-4121 |  | 2013-07-16 | 2013-07-16 13:29 | 2013-07-16 13:47 | LENNOX - 10GCS036753PA | 58 | 5.4 | Yes | Yes | 26.1 | 21.5 | 4.6 | C9EF02CD8DE844B2A8604CDEF2198609 |  | R22 | Non-TXV |  | 9.31% | 0.9069 | 17.89% | [5 empty] | Non-TXV | 9.31%
Morgan Hill | CA | 95037-7502 |  | 2013-10-24 | 2013-10-24 13:03 | 2013-10-24 13:24 | ICP - CA5542VKD2 | 98 | 7 | Yes | Yes | 22.2 | 19.9 | 2.3 | 024D4BD6D41D43BCAB8D6D527A1849FA |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Shafter | CA | 93263-0000 |  | 2013-08-07 | 2013-08-07 10:03 | 2013-08-07 10:41 | COLEMAN - BRC0048B | 81 | 12.1 | Yes | Yes | 27.8 | 22.4 | 5.5 | 1B989FE836B44075927AF78DD867AE23 |  | R22 | Non-TXV |  | 14.94% | 0.85062 | 28.71% | [5 empty] | Non-TXV | 14.94%
Santa Rosa | CA | 95407-7773 |  | 2013-07-11 | 2013-07-11 11:33 | 2013-07-11 12:38 | CARRIER - 24ABA336A310 | 91 | 3.2 | Yes | Yes | 19.9 | 19.8 | 0.1 | 56EC6ECC37EE4D21B81384AB552FAE27 |  | R410A | Non-TXV |  | 3.516% | 0.96484 | 6.758% | [5 empty] | Non-TXV | 3.516%
Woodland | CA | 95695-3110 |  | 2013-07-25 | 2013-07-25 13:31 | 2013-07-25 14:14 | RHEEM - RAKA-0360JAZ | 66 | -6.2 | Yes | Yes | 22.4 | 17.5 | 4.9 | 381B40E433454DD7AA8B5C605BECC459 |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
Vacaville | CA | 95687-4969 |  | 2013-10-09 | 2013-10-09 09:21 | 2013-10-09 09:22 | CARRIER - 38TZA036320 | 84 | 5.5 | Yes | Yes | 17.4 | 17.3 | 0.1 | D76B07E870AA4CA3B22D3A5874E5EA17 |  | R410A | Non-TXV |  | 6.548% | 0.93452 | 12.58% | [5 empty] | Non-TXV | 6.548%
Bakersfield | CA | 93304-1246 |  | 2013-09-21 | 2013-09-21 16:13 | 2013-09-21 16:13 | OTHER - UKN | 60 | 0 | Yes | Yes | 22.5 | 21.7 | 0.8 | 5D2C2FE36FCE411C8C52AD1AB02EDEDD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2637 |  | 2013-06-27 | 2013-06-27 15:26 | 2013-06-27 15:42 | YORK - D1NA036N07206A | 63 | -3.7 | Yes | Yes | 15.9 | 17 | -1.1 | 13DC85A12F1C4784ACDC03DC4B738F06 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Morgan Hill | CA | 95037-4308 |  | 2013-07-30 | 2013-07-30 10:43 | 2013-07-30 12:15 | AMANA - RCB30A2C | 85 | 8.2 | Yes | Yes | 18.5 | 18.2 | 0.3 | 56F61013345F4C22899D208276346DDF |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Antioch | CA | 94509-2313 |  | 2013-07-09 | 2013-07-09 11:12 | 2013-07-09 11:13 | HEIL - PGAA30C1K0 | 75 | -6.2 | Yes | Yes | 18.6 | 17.3 | 1.4 | 39BCE797D1914F69870756628D5B81DC |  | R22 | Non-TXV |  | -8.267% | 1.0827 | 2.315% |  |  |  |  | Non-TXV |  |  | -8.267%
Morgan Hill | CA | 95037-4204 |  | 2013-10-24 | 2013-10-24 12:08 | 2013-10-24 13:01 | PAYNE - PA10JA024-C | 64 | 6.4 | Yes | Yes | 25 | 19.9 | 5.1 | FCC2074315514FDAB369D3F1F5A920C9 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Woodland | CA | 95695-2922 |  | 2013-07-26 | 2013-07-26 11:45 | 2013-07-26 12:25 | AMANA - ASX130301CA | 78 | 9.1 | Yes | Yes | 14.6 | 17.5 | -2.9 | 2E216576007B44DABD20B3F4CFC5D32A | Add refrigerant: 7.7 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | TXV | 11.67%
Bakersfield | CA | 93304-1270 |  | 2013-09-21 | 2013-09-21 18:30 | 2013-09-21 18:30 | GOODMAN - GPG132405M410A | 75 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 6DA0B48D0E774D8EA2EA27101D456FA8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4385 |  | 2013-07-25 | 2013-07-25 14:28 | 2013-07-25 14:28 | NORDYNE - JT5BD030KA | 144 | 0 | Yes | Yes | 20.3 | 19.7 | 0.6 | 01A910112F4B4821BDF2995F518A8120 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1146 |  | 2013-10-01 | 2013-10-01 15:51 | 2013-10-01 15:51 | BDP - 588ANW024040ACAD | 41 | 0 | Yes | Yes | 22 | 21.8 | 0.3 | 1DE09131B96F40ACB3573EB00E81D38A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-1243 |  | 2013-09-23 | 2013-09-23 15:21 | 2013-09-23 16:26 | - FS3BA-036KA | 80 | 2.4 | Yes | Yes | 16.2 | 18.8 | -2.6 | FC43E22DBF2D49C69B8CEDA9555443F1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93304-1146 |  | 2013-10-01 | 2013-10-01 15:32 | 2013-10-01 15:32 | BDP - 588ANW024040ACAD | 38 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | BAF3FA72ADC44256B936B2B6DAE88883 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1160 |  | 2013-10-01 | 2013-10-01 15:15 | 2013-10-01 15:15 | OTHER - UKN | 75 | 0 | Yes | Yes | 21.7 | 22.1 | -0.4 | 394AF7562F0D4C0CAD54DADA230256D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95110-3302 |  | 2013-09-30 | 2013-09-30 12:11 | 2013-09-30 14:08 | CARRIER - 38QR018C 341 | 41 | 1.8 | Yes | Yes | 22.1 | 21 | 1.1 | 0DF6DB5E7F4D4407BCB16AC638C964C2 |  | R22 | Non-TXV |  | 4.39% | 0.9561 | 8.437% | [5 empty] | Non-TXV | 4.39%
Fairfield | CA | 94533-4742 |  | 2013-07-18 | 2013-07-18 14:15 | 2013-07-18 15:15 | TRANE - 2TTB0048A1000AA | 109 | 3.5 | Yes | Yes | 16.8 | 18.2 | -1.4 | 6316CEED68644F7AABE9392BA174715F |  | R22 | Non-TXV |  | 3.211% | 0.96789 | 6.171% | [5 empty] | Non-TXV | 3.211%
Bakersfield | CA | 93304-2303 |  | 2013-07-01 | 2013-07-01 17:13 | 2013-07-01 17:13 | ICP - GPFM60K100E | 133 | 0 | Yes | Yes | 19.7 | 20.7 | -1 | CE87B0E9A3ED4916AB27076192A31EAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2660 |  | 2013-07-26 | 2013-07-26 12:49 | 2013-07-26 13:11 | AMERICAN STANDARD - YCC036F1M0BJ | 99 | 16.4 | Yes | Yes | 16.9 | 18.8 | -1.9 | 47AC2FE79DD94C91BFECBAADEB086354 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.57% | 0.83434 | 31.84% | [5 empty] | Non-TXV | 16.57%
Bakersfield | CA | 93313-3990 |  | 2013-07-10 | 2013-07-10 18:08 | 2013-07-10 18:59 | RHEEM - N/A | 85 | 4.1 | Yes | Yes | 20.5 | 21.5 | -1 | 66E08FC2EBDF47E4B663A995519C8CC8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Bakersfield | CA | 93309-3228 |  | 2013-10-15 | 2013-10-15 17:41 | 2013-10-15 17:43 | YORK - D1NH036N056C | 108 | 7.8 | Yes | Yes | 22.6 | 20.1 | 2.5 | A25BB77F8D034C10AE78B9FE7D2964E7 |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Davis | CA | 95618-1442 |  | 2013-07-09 | 2013-07-09 12:00 | 2013-07-09 12:00 | LENNOX - GCS20-030-75-1P | 74 | 0 | Yes | Yes | 19.1 | 20.2 | -1.1 | F51C0A270EB14FBB8E06B1C00E0F5397 |  | R22 | TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-2619 |  | 2013-10-22 | 2013-10-22 10:42 | 2013-10-22 11:12 | TRANE - 2TTB0030A10000AA | 64 | -6.8 | Yes | Yes | 21.8 | 19.1 | 2.7 | 947D9F92ECE84D7AB962DBBEB9267ACF |  | R22 | Non-TXV |  | -10.62% | 1.1062 | 2.975% |  |  |  |  | Non-TXV |  |  | -10.62%
Fairfield | CA | 94533-5044 |  | 2013-07-18 | 2013-07-18 13:24 | 2013-07-18 13:43 | GE - | 85 | 3.2 | Yes | Yes | 15.4 | 17.7 | -2.3 | 74C6D0B2B87F4D608D6B1EED69705CE9 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Milpitas | CA | 95035-6654 |  | 2013-10-02 | 2013-10-02 11:19 | 2013-10-02 11:52 | BRYANT - 113RNA036-B | 88 | 9.5 | Yes | Yes | 26.1 | 20.9 | 5.2 | D6335BECAC064CE789CD6D3139C42B63 |  | R22 | TXV |  | 10.8% | 0.89205 | 20.75% | [5 empty] | TXV | 10.8%
Davis | CA | 95618-1447 |  | 2013-09-26 | 2013-09-26 10:57 | 2013-09-26 15:46 | LENNOX - | 85 | -4 | Yes | Yes | 21.1 | 22 | -0.9 | D7EB53059D7D4E73950AC6CE9A2A85F6 |  | R22 | Non-TXV |  | -4.706% | 1.0471 | 1.318% |  |  |  |  | Non-TXV |  |  | -4.706%
San Jose | CA | 95110-3309 |  | 2013-10-15 | 2013-10-15 15:00 | 2013-10-15 16:11 | CARRIER - UNK | 67 | 5.3 | Yes | Yes | 19.7 | 20.9 | -1.2 | 4488173EE7144E6CADC0CF387FE90090 |  | R22 | Non-TXV |  | 7.91% | 0.9209 | 15.2% | [5 empty] | Non-TXV | 7.91%
Bakersfield | CA | 93313-4116 |  | 2013-07-12 | 2013-07-12 18:40 | 2013-07-12 19:07 | PAYNE - PY3GNAA48090NA | 100 | 3.2 | Yes | Yes | 23.1 | 21 | 2.1 | 5AC22AF77ACE45A29FE7709B64CCB77A |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Hayward | CA | 94541-1943 |  | 2013-09-24 | 2013-09-24 10:04 | 2013-09-24 10:45 | GOODMAN - CKL30-1G | 85 | 3 | Yes | Yes | 21.1 | 17.6 | 3.5 | 50B171C5848C4B9EB841F25B618FBA00 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
San Jose | CA | 95110-3309 |  | 2013-09-24 | 2013-09-24 13:15 | 2013-09-24 13:33 | CARRIER - UNK | 70 | 2.2 | Yes | Yes | 22.7 | 21.5 | 1.2 | CE415326ECD94E46B88E5D67221DCC1F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Cottonwood | CA | 96022-7651 |  | 2013-07-12 | 2013-07-12 11:01 | 2013-07-12 11:35 | BDP - 542EX024000AAACD | 98 | 3.9 | Yes | Yes | 22.5 | 21.7 | 0.8 | E88F2B3C1856413D9782E2D689BECA9A |  | R22 | Non-TXV |  | 3.98% | 0.9602 | 7.648% | [5 empty] | Non-TXV | 3.98%
Bakersfield | CA | 93307-6062 |  | 2013-08-08 | 2013-08-08 00:03 | 2013-08-08 00:03 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 756AFCA0E1F04A4E9AF3E4C748BA5A32 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4621 |  | 2013-07-15 | 2013-07-15 10:37 | 2013-07-15 11:03 | OTHER - N2A360AK200 | 85 | 5.1 | Yes | Yes | 19.6 | 19.4 | 0.3 | B691895A811F419FB9239737C72C35C9 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Lamont | CA | 93241-2710 |  | 2013-09-12 | 2013-09-12 13:53 | 2013-09-12 14:19 | DUCANE - 24C13B24P 2B | 98 | 13.3 | Yes | Yes | 20.3 | 20.5 | -0.2 | 746FD9D57A9845698E923F0FAE1BE067 |  | R22 | Non-TXV |  | 13.57% | 0.86429 | 26.08% | [5 empty] | Non-TXV | 13.57%
Bakersfield | CA | 93313-5558 |  | 2013-07-17 | 2013-07-17 10:34 | 2013-07-17 10:53 | YORK - H2RD048506B | 134 | 6.3 | Yes | Yes | 20.5 | 19.6 | 0.9 | 1A7D76CCC3754AE38437A0600CB8957C |  | R22 | Non-TXV |  | 4.701% | 0.95299 | 9.035% | [5 empty] | Non-TXV | 4.701%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 21:07 | 2013-09-30 21:09 | LENNOX - 13HPD-024-01 | 99 | -5.4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 972C12F38ED0464383C57329D12F0558 |  | R22 | TXV |  | -5.455% | 1.0545 | 1.528% |  |  |  |  | TXV |  |  | -5.455%
Bakersfield | CA | 93305-1230 |  | 2013-08-27 | 2013-08-27 15:37 | 2013-08-27 21:05 | GOODMAN - PGX036075 | 85 | 4 | Yes | Yes | 16.9 | 19.9 | -3 | 9D69061881824BFFB0544E048A1DCA54 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Anderson | CA | 96007-9126 |  | 2013-07-10 | 2013-07-10 11:44 | 2013-07-10 13:16 | BRYANT - 602BNX048000AB | 167 | 10.4 | Yes | Yes | 22.7 | 20.7 | 2 | CD16CA3E1BDD44DEB87C65B14FD0EBAB |  | R410A | Non-TXV |  | 6.228% | 0.93772 | 11.97% | [5 empty] | Non-TXV | 6.228%
Bakersfield | CA | 93313-4547 |  | 2013-07-15 | 2013-07-15 15:22 | 2013-07-15 16:52 | ALLEGIANCE - AC1CN048-A | 85 | -3.1 | Yes | Yes | 16.6 | 19.5 | -2.9 | 580990B7B9704A4CB42264478117A90B |  | R22 | Non-TXV |  | -3.647% | 1.0365 | 1.021% |  |  |  |  | Non-TXV |  |  | -3.647%
San Rafael | CA | 94903-4520 |  | 2013-07-05 | 2013-07-05 11:07 | 2013-07-05 11:10 | ARMSTRONG - SCU10G60A | 131 | -7.7 | Yes | Yes | 16.8 | 18.1 | -1.3 | C31612FC0F2648DB879C1137FF3FF912 |  | R22 | Non-TXV |  | -5.878% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.878%
Wasco | CA | 93280-2375 |  | 2013-10-03 | 2013-10-03 21:05 | 2013-10-03 21:07 | LENNOX - 13HPD-024-01 | 99 | 8 | Yes | Yes | 21.4 | 20.3 | 1.1 | 39CCF9A5E01E458B9786FEA4ACA07E5F |  | R22 | TXV |  | 8.081% | 0.91919 | 15.53% | [5 empty] | TXV | 8.081%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 21:17 | 2013-09-30 21:18 | LENNOX - 13HPD-024-01 | 99 | 5.8 | Yes | Yes | 22.7 | 21 | 1.7 | 2FDC6873ACAA4B09983129E96DC47B6A |  | R22 | TXV |  | 5.859% | 0.94141 | 11.26% | [5 empty] | TXV | 5.859%
Bakersfield | CA | 93313-5588 |  | 2013-07-17 | 2013-07-17 12:31 | 2013-07-17 13:47 | YORK - H2RD0485U6A | 134 | 6.5 | Yes | Yes | 20.5 | 19.7 | 0.8 | 522D64D4C0A5409CB3D43DADF97BF31E |  | R22 | Non-TXV |  | 4.851% | 0.95149 | 9.322% | [5 empty] | Non-TXV | 4.851%
Fairfield | CA | 94533-1856 |  | 2013-07-19 | 2013-07-19 14:19 | 2013-07-19 15:20 | PAYNE - 597BN036-A | 144 | 5.8 | Yes | Yes | 15.5 | 17.6 | -2.1 | 0251E7C5E98C4D8D8DEAABC03DA33675 |  | R22 | TXV |  | 4.028% | 0.95972 | 7.741% | [5 empty] | TXV | 4.028%
Milpitas | CA | 95035-6653 |  | 2013-09-27 | 2013-09-27 12:31 | 2013-09-27 13:11 | ICP - NXA660GKA100 | 229 | -13.5 | Yes | Yes | 20.6 | 21.1 | -0.5 | 388A350B9668413EB2B3FCCCFBF7964F |  | R410A | Non-TXV |  | -5.895% | 1.059 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Wasco | CA | 93280-2375 |  | 2013-10-07 | 2013-10-07 15:15 | 2013-10-07 15:18 | LENNOX - 13HPD-0240-230-01 | 102 | 5.8 | Yes | Yes | 24.4 | 21.3 | 3.1 | 5EFEFC46BE634C90B4FC262B8A6BA2CB |  | R22 | TXV |  | 5.686% | 0.94314 | 10.93% | [5 empty] | TXV | 5.686%
Redding | CA | 96003-0473 |  | 2013-09-05 | 2013-09-05 17:13 | 2013-09-06 08:14 | BDP - 542EBX042000AAAE | 136 | 5 | Yes | Yes | 27.9 | 22.6 | 5.3 | 1B326509A2524862B33DB3AE6E5F8089 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Bakersfield | CA | 93309-6178 |  | 2013-08-21 | 2013-08-21 18:52 | 2013-08-21 18:55 | PAYNE - PY36GNAA36060NA | 102 | -3.8 | Yes | Yes | 24.3 | 21.4 | 2.9 | 50124F3BF3CB498FA24FB2BB48D32602 |  | R410A | TXV |  | -3.725% | 1.0373 | 1.043% |  |  |  |  | TXV |  |  | -3.725%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 19:43 | 2013-09-30 19:47 | LENNOX - 13HPD-024-230-01 | 99 | 5.5 | Yes | Yes | 22.5 | 20.4 | 2.1 | 9C60A48566BB4404BCF480E19A4DE25C |  | R22 | TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | TXV | 5.556%
Bakersfield | CA | 93304-4324 |  | 2013-07-01 | 2013-07-01 13:39 | 2013-07-01 13:39 | TEMPSTAR - YCY036G1MAA | 129 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | ABE0F5302F8C4D299ADAC9E0FE8BC585 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corcoran | CA | 93212-1731 |  | 2013-07-05 | 2013-07-05 11:33 | 2013-07-05 13:15 | TEMPSTAR - GPFM42K080F | 84 | 3.8 | Yes | Yes | 17.6 | 20.1 | -2.5 | 970CD247D7984D5CAFB7AFD1F08884FC |  | R22 | Non-TXV |  | 4.524% | 0.95476 | 8.694% | [5 empty] | Non-TXV | 4.524%
Bakersfield | CA | 93313-5625 |  | 2013-07-17 | 2013-07-17 13:55 | 2013-07-17 14:21 | TRANE - 2TTB3048A1000AA | 142 | 7.4 | Yes | Yes | 16.3 | 19.2 | -2.9 | B814F86A87CC466EB8535E9EC5D070D3 |  | R22 | TXV |  | 5.211% | 0.94789 | 10.01% | [5 empty] | TXV | 5.211%
Redding | CA | 96003-1696 |  | 2013-07-16 | 2013-07-16 13:15 | 2013-07-16 14:02 | YORK - ERC0361BBB | 85 | 7.2 | Yes | Yes | 20.2 | 19.7 | 0.5 | 1966AAA34A304F2C86A0522E73567A78 |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Wasco | CA | 93280-0000 |  | 2013-10-04 | 2013-10-04 21:51 | 2013-10-04 22:09 | LENNOX - 13HPD-024-230-02 | 99 | 9.4 | Yes | Yes | 20.5 | 21 | -0.4 | 689B45C5DB334C28951B040FCACED135 |  | R22 | TXV |  | 9.495% | 0.90505 | 18.25% | [5 empty] | TXV | 9.495%
San Rafael | CA | 94903-1636 |  | 2013-07-12 | 2013-07-12 09:37 | 2013-07-12 09:47 | TRANE - 2TTR1024A1000AA | 62 | 4.7 | Yes | Yes | 16.6 | 17.3 | -0.7 | FF3C8106A1FB4802BE8517AA743AD9F1 |  | R22 | Non-TXV |  | 7.581% | 0.92419 | 14.57% | [5 empty] | Non-TXV | 7.581%
Wasco | CA | 93280-2375 |  | 2013-10-07 | 2013-10-07 15:06 | 2013-10-07 15:08 | LENNOX - 13HPD=024-230-01 | 102 | 4 | Yes | Yes | 24.5 | 21.5 | 3 | 5A61B8E14CA2407B8A127CDFE3F6068B |  | R22 | TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | TXV | 3.922%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 19:19 | 2013-10-04 19:21 | LENNOX - 13HPD-024-230-01 | 99 | 12.3 | Yes | Yes | 22.5 | 20.4 | 2.1 | 2FD27EE3CA7C4B049A0A0EC93BCA4388 |  | R22 | TXV |  | 12.42% | 0.87576 | 23.88% | [5 empty] | TXV | 12.42%
San Jose | CA | 95111-3800 |  | 2013-10-01 | 2013-10-01 10:35 | 2013-10-01 10:57 | YORK - UNK | 86 | 11.5 | Yes | Yes | 18 | 20.7 | -2.7 | E0C8BBBE8C5B454D9ACDF0A9705801EE |  | R22 | Non-TXV |  | 13.37% | 0.86628 | 25.7% | [5 empty] | Non-TXV | 13.37%
Bakersfield | CA | 93313-6031 |  | 2013-07-23 | 2013-07-23 16:08 | 2013-07-23 16:42 | RUUD - UNK | 96 | 6 | Yes | Yes | 19.6 | 18.9 | 0.7 | 0B128BB2AB5840CE989D4FEF8299EF42 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | TXV | 6.25%
Bakersfield | CA | 93304-4414 |  | 2013-07-01 | 2013-07-01 08:44 | 2013-07-01 08:44 | BRYANT - 574BN0480090NB | 178 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | 624F0419184D4A48A2626F07A6A281B3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2377 |  | 2013-10-05 | 2013-10-05 11:30 | 2013-10-05 11:47 | LENNOX - 13HPD-024-230-02 | 99 | 4.4 | Yes | Yes | 17.7 | 20.5 | -2.8 | 82D3290C83744F68B6793CF19C1DB9A0 |  | R22 | TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | TXV | 4.444%
Bakersfield | CA | 93304-4202 |  | 2013-07-02 | 2013-07-02 16:21 | 2013-07-02 16:21 | RUUD - UKN | 90 | 0 | Yes | Yes | 19.3 | 19.2 | 0.2 | DCC0CDA2C47C40899ED0C7621C0468FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2377 |  | 2013-10-04 | 2013-10-04 21:19 | 2013-10-04 21:42 | LENNOX - 13HPD-024-230-02 | 99 | 8.8 | Yes | Yes | 20 | 20.1 | -0.1 | C918EDD33CA440299D08B539C7127578 |  | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Wasco | CA | 93280-2377 |  | 2013-10-04 | 2013-10-04 20:51 | 2013-10-04 21:14 | LENNOX - 13HPD-024-230-01 | 99 | 10.5 | Yes | Yes | 20.3 | 21.3 | -1 | A3BA607D0DD24E60B5818810450BC943 |  | R22 | TXV |  | 10.61% | 0.89394 | 20.38% | [5 empty] | TXV | 10.61%
Fresno | CA | 93727-8317 |  | 2013-11-08 | 2013-11-08 12:46 | 2013-11-08 13:10 | ICP - PGF024K040E | 57 | 1.7 | Yes | Yes | 23.4 | 20.8 | 2.6 | 78FBD1BFE62A4A48A01DA76DAF09A6AA |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Vallejo | CA | 94589-2043 |  | 2013-06-28 | 2013-06-28 11:50 | 2013-06-28 12:16 | AMERICAN STANDARD - YCC048F1M0BF | 100 | 3.1 | Yes | Yes | 22.9 | 18.5 | 4.4 | 21B267178A244123B25538BD5DAF4D88 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Fresno | CA | 93727-4883 |  | 2013-08-31 | 2013-08-31 11:36 | 2013-08-31 12:18 | OTHER - 50WE24G1NA | 55 | -5.2 | Yes | Yes | 23.1 | 19.8 | 3.3 | 781394CB76DC4CB68F7C23E6FE633D9D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Pinedale | CA | 93650-1172 |  | 2013-07-11 | 2013-07-11 11:14 | 2013-07-11 11:34 | - DRCS0481BD | 122 | 3.9 | Yes | Yes | 24.5 | 21.5 | 3 | 27CD35D3EEF941FCBF21EDAB6248F0D8 |  | R22 | Non-TXV |  | 3.197% | 0.96803 | 6.143% | [5 empty] | Non-TXV | 3.197%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 20:02 | 2013-10-01 20:13 | LENNOX - 13HPD-0240230-01 | 99 | -5.1 | Yes | Yes | 23.2 | 20.4 | 2.8 | B70E64B5B5D94F58A3975452B26DF305 |  | R22 | TXV |  | -5.152% | 1.0515 | 1.443% |  |  |  |  | TXV |  |  | -5.152%
Fresno | CA | 93725-1726 |  | 2013-10-02 | 2013-10-02 13:40 | 2013-10-02 14:13 | GOODMAN - GPG10300701A | 50 | 2.4 | Yes | Yes | 19.9 | 18.8 | 1.1 | FAEF9959764549C1A1B0B729721B41FB |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Clovis | CA | 93611-5137 |  | 2013-07-03 | 2013-07-03 13:20 | 2013-07-03 13:58 | RHEEM - RRNAB030JK06X | 80 | 5.5 | Yes | Yes | 23 | 20.4 | 2.6 | F84B39D233C3431BB14EE755F7D8164D |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 20:47 | 2013-09-30 20:51 | LENNOX - 13HPD-024-230-01 | 99 | 0 | Yes | Yes | 23.4 | 20.7 | 2.8 | 15DEC851EDE843E0B524BD2B9B87E3AC |  | R22 | TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 17:34 | 2013-09-30 17:37 | LENNOX - 13HPD-024-230-01 | 99 | 7 | Yes | Yes | 23.1 | 19.6 | 3.5 | 1B19296F0F8F460392E3F953FE1993B4 |  | R22 | TXV |  | 7.071% | 0.92929 | 13.59% | [5 empty] | TXV | 7.071%
Wasco | CA | 93280-2373 |  | 2013-09-30 | 2013-09-30 21:45 | 2013-09-30 21:48 | LENNOX - 13HPD-024-01 | 99 | 5.5 | Yes | Yes | 23.7 | 20.7 | 3 | 54E82E7452C544A1B4DCDA315F1711D5 |  | R22 | TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | TXV | 5.556%
Fresno | CA | 93722-2289 |  | 2013-07-08 | 2013-07-08 11:42 | 2013-07-08 12:15 | CARRIER - 38BRC048350 | 167 | 21 | Yes | Yes | 21.4 | 21.5 | -0.1 | 27E32183B9D34BA9AD552043EE1DEEA4 |  | R22 | TXV |  | 12.57% | 0.87425 | 24.17% | [5 empty] | TXV | 12.57%
Bakersfield | CA | 93304-7220 |  | 2013-09-04 | 2013-09-04 10:36 | 2013-09-04 10:36 | TRANE - 4YCY4030A1075AB | 97 | 0 | Yes | Yes | 21.8 | 21.2 | 0.6 | 0F715C92BF9C4153B6BACC0DCCDEBE19 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-0000 |  | 2013-07-26 | 2013-07-26 15:29 | 2013-07-26 15:29 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 26.1 | 20.7 | 5.4 | 6CA06F3E71DB4520ACD696C19DADB4C4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2373 |  | 2013-09-30 | 2013-09-30 21:23 | 2013-09-30 21:28 | LENNOX - 13HPD-024-230-01 | 99 | -5.8 | Yes | Yes | 23.1 | 20.4 | 2.7 | 123A8207A8C7408481FD30FEA097DEB8 |  | R22 | TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | TXV |  |  | -5.859%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 19:50 | 2013-09-30 19:52 | LENNOX - 13HPD-024-230-01 | 99 | 7 | Yes | Yes | 23.7 | 20.7 | 3.1 | CE508FDEEF084B2A8A1202C422862A8C |  | R22 | TXV |  | 7.071% | 0.92929 | 13.59% | [5 empty] | TXV | 7.071%
Fresno | CA | 93726-1632 |  | 2013-07-29 | 2013-07-29 16:45 | 2013-07-29 16:45 | YORK - 2NZ036N05606NXA | 112 | 0 | Yes | Yes | 23.8 | 20.4 | 3.4 | 3BB29EBB81134BD4B1FDF4614E7B20D9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2373 |  | 2013-09-30 | 2013-09-30 16:24 | 2013-09-30 16:28 | LENNOX - 13HPD-024-230-01 | 101 | 4.5 | Yes | Yes | 23.1 | 21.5 | 1.6 | EE9520AB545349D1BFBDBF84224DF820 |  | R22 | TXV |  | 4.455% | 0.95545 | 8.562% | [5 empty] | TXV | 4.455%
Fresno | CA | 93725-4022 |  | 2013-08-14 | 2013-08-14 09:31 | 2013-08-14 10:08 | CARRIER - UNK | 80 | 3 | Yes | Yes | 19 | 17.6 | 1.4 | 538147102FDF494B896883E2E2730350 |  | R410A | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Fresno | CA | 93722-2828 |  | 2013-08-27 | 2013-08-27 10:32 | 2013-08-27 11:08 | CARRIER - UKN | 80 | 4.3 | Yes | Yes | 20.2 | 19.9 | 0.3 | 05DBF126A6AC4EDBA0596884BF6FB9A4 |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Fresno | CA | 93711-1166 |  | 2013-08-23 | 2013-08-23 10:48 | 2013-08-23 11:06 | CARRIER - 33TR060300 | 224 | 7.5 | Yes | Yes | 15.8 | 18.7 | -2.9 | A6E746EBD0CA4FBFB8AD2C500FB5B871 |  | R22 | Non-TXV |  | 3.348% | 0.96652 | 6.435% | [5 empty] | Non-TXV | 3.348%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 19:24 | 2013-10-01 19:26 | LENNOX - 13HPD-024-230-01 | 99 | 4.1 | Yes | Yes | 21.9 | 20.4 | 1.5 | 6D503CA65FA14FD394A1B78362204DF2 |  | R22 | TXV |  | 4.141% | 0.95859 | 7.959% | [5 empty] | TXV | 4.141%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 20:33 | 2013-10-01 20:39 | LENNOX - 13HPD-024-230-01 | 85 | 3.6 | Yes | Yes | 22 | 19.9 | 2.1 | CCD26A7E9A6F429B83F4E83CACC8F633 |  | R22 | TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | TXV | 4.235%
Wasco | CA | 93280-1642 |  | 2013-07-31 | 2013-07-31 22:06 | 2013-07-31 22:21 | GE - 21TA936N1A | 162 | 6.7 | Yes | Yes | 22.7 | 23.1 | -0.4 | 92119D8A2EF64C9C815DD46BF36C8EBF |  | R22 | Non-TXV |  | 4.136% | 0.95864 | 7.948% | [5 empty] | Non-TXV | 4.136%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 19:03 | 2013-10-01 19:05 | LENNOX - 13HPD-024-230-01 | 99 | 5.9 | Yes | Yes | 22 | 20.4 | 1.6 | 617ED4DB0C184009902DBA080C1CB97A |  | R22 | TXV |  | 5.96% | 0.9404 | 11.45% | [5 empty] | TXV | 5.96%
Bakersfield | CA | 93313-2428 |  | 2013-07-09 | 2013-07-09 18:14 | 2013-07-09 18:14 | GOODMAN - GPG1342070M41CA | 85 | 0 | Yes | Yes | 23.2 | 22.3 | 0.9 | FA35B616E00A482D888A9A40B7AF3BBD | Add refrigerant: 12.3 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2630 |  | 2013-08-28 | 2013-08-28 16:08 | 2013-08-28 16:45 | CARRIER - S030040321 | 53 | 0 | Yes | Yes | 19.7 | 20.8 | -1.1 | B7D40448589947F58CF91C3BE4EA1E97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pinedale | CA | 93650-1318 |  | 2013-07-09 | 2013-07-09 13:35 | 2013-07-09 14:04 | RUUD - UNK | 80 | 2.4 | Yes | Yes | 26.2 | 20.7 | 5.5 | 35B30F85E8534B98AEC064876C237369 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Wasco | CA | 93280-2377 |  | 2013-10-05 | 2013-10-05 12:44 | 2013-10-05 13:00 | LENNOX - 13HPD-024-230-02 | 99 | 11.5 | Yes | Yes | 17.7 | 19.9 | -2.2 | 15D30A051D0E48C3920519BA207D8084 |  | R22 | TXV |  | 11.62% | 0.88384 | 22.32% | [5 empty] | TXV | 11.62%
Novato | CA | 94947-5266 |  | 2013-07-05 | 2013-07-05 11:42 | 2013-07-05 11:43 | AMANA - ASX140181CA | 70 | -4.9 | Yes | Yes | 18.6 | 17.9 | 0.7 | 9F2278C620E14D2B9F583428DEDC97BD |  | R410A | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93722-2302 |  | 2013-07-19 | 2013-07-19 14:21 | 2013-07-19 15:19 | RHEEM - RAND042JAZ | 136 | -5.1 | Yes | Yes | 19.5 | 19.3 | 0.2 | 0F5158D70B78441CBF2F3DD38ADF9111 |  | R22 | Non-TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | Non-TXV |  |  | -3.75%
Fresno | CA | 93710-4840 |  | 2013-07-01 | 2013-07-01 13:02 | 2013-07-01 13:21 | OTHER - 563CN036 | 114 | 15.2 | Yes | Yes | 20.8 | 15.6 | 5.2 | D50C4339C0024ACA9D80F9B74E6FE9DA |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Fresno | CA | 93722-3001 |  | 2013-07-24 | 2013-07-24 17:51 | 2013-07-24 17:51 | - CA5036VKB1867.830340 | 86 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 127D7CCB72DE485FAD56F5163857C095 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2373 |  | 2013-09-30 | 2013-09-30 21:56 | 2013-09-30 21:58 | LENNOX - 13HPD-024-01 | 99 | 4.8 | Yes | Yes | 23.5 | 20.7 | 2.8 | 4118ED2E652A43649427ACD82E5D573D |  | R22 | TXV |  | 4.848% | 0.95152 | 9.318% | [5 empty] | TXV | 4.848%
San Rafael | CA | 94903-2214 |  | 2013-07-05 | 2013-07-05 10:11 | 2013-07-05 10:12 | COLEMAN - BRCQ0361BD | 52 | -4.9 | Yes | Yes | 18.5 | 17.6 | 0.9 | 1202B1D79F104ED48DA02BD3C73FA38D |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Wasco | CA | 93280-2375 |  | 2013-10-04 | 2013-10-04 19:42 | 2013-10-04 19:43 | LENNOX - 13HPD-024-230-01 | 99 | 8.9 | Yes | Yes | 21.2 | 20.3 | 0.9 | CA43D8284CAA454482D983A4A617E6B0 |  | R22 | TXV |  | 8.99% | 0.9101 | 17.28% | [5 empty] | TXV | 8.99%
San Jose | CA | 95128-5132 |  | 2013-10-15 | 2013-10-15 10:08 | 2013-10-15 10:38 | COMFORT AIRE - BRCS04816D | 117 | -6.9 | Yes | Yes | 22.1 | 20.4 | 1.7 | 87C6CA2D53614817B2A13647D6854373 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Redding | CA | 96001-9727 |  | 2013-07-17 | 2013-07-17 14:25 | 2013-07-17 14:42 | HEIL - UNK | 88 | 29.4 | Yes | Yes | 16.8 | 19.7 | -2.9 | A3C443EB18954437A3BFA43BA9098BEC |  | R22 | Non-TXV |  | 33.41% | 0.66591 | 64.2% | [5 empty] | Non-TXV | 33.41%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 18:42 | 2013-10-04 18:44 | LENNOX - 13PD-024-230-01 | 99 | -4.5 | Yes | Yes | 23.2 | 21 | 2.2 | F166FCBFC52C48F89C8D79CF8E9A0A2F |  | R22 | TXV |  | -4.545% | 1.0455 | 1.273% |  |  |  |  | TXV |  |  | -4.545%
Fresno | CA | 93725-1145 |  | 2013-07-02 | 2013-07-02 08:40 | 2013-07-02 08:40 | OTHER - 585B036075 | 80 | 0 | Yes | Yes | 16.5 | 18.8 | -2.3 | 97D1A24845614B758868A5F910410ECB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2246 |  | 2013-11-11 | 2013-11-11 15:45 | 2013-11-11 15:45 | RHEEM - RRNLB036JK08X | 92 | 0 | Yes | Yes | 20.1 | 19.9 | 0.2 | 5149650995884993B5F873B49738D536 |  | R410A | TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 19:33 | 2013-10-04 19:34 | LENNOX - 13HPD-024-230-01 | 99 | 10.2 | Yes | Yes | 20.4 | 19.8 | 0.6 | A084D3F4B7604E9C84030263458C2F7B |  | R22 | TXV |  | 10.3% | 0.89697 | 19.8% | [5 empty] | TXV | 10.3%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 17:21 | 2013-09-30 17:25 | LENNOX - 13HPD-24-230-01 | 99 | 7 | Yes | Yes | 22.7 | 20.1 | 2.6 | 0158A3263A674134AA8E8B23B5615903 |  | R22 | TXV |  | 7.071% | 0.92929 | 13.59% | [5 empty] | TXV | 7.071%
Fresno | CA | 93710-5517 |  | 2013-07-01 | 2013-07-01 13:53 | 2013-07-01 13:53 | YORK - D2NP042N09006NXA | 154 | -12.7 | Yes | Yes | 26 | 19.5 | 6.5 | 926D5C9C17DC4B9188A301AEE4FD2EE5 | Remove refrigerant: 12.7 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | -8.247% | 1.0825 | 2.309% |  |  |  |  | TXV |  |  | -8.247%
Cottonwood | CA | 96022-8543 |  | 2013-07-13 | 2013-07-13 16:54 | 2013-07-14 07:37 | INTERTHERM - ILLEGIBLE | 89 | 5.7 | Yes | Yes | 27.2 | 21.5 | 5.7 | C931491EE3A64A1F87E67ACA489FD53D |  | R22 | Non-TXV |  | 6.404% | 0.93596 | 12.31% | [5 empty] | Non-TXV | 6.404%
Wasco | CA | 93280-0000 |  | 2013-10-04 | 2013-10-04 18:46 | 2013-10-04 18:48 | LENNOX - 13HPD-024-230-01 | 99 | 7.2 | Yes | Yes | 21.9 | 20.4 | 1.5 | 56D17B60B31B45AD902E17CCD5BA6F1B |  | R22 | TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | TXV | 7.273%
San Jose | CA | 95110-3309 |  | 2013-09-30 | 2013-09-30 11:17 | 2013-09-30 11:33 | CARRIER - 38QRC024C 341 | 41 | 1.4 | Yes | Yes | 20.8 | 20.4 | 0.4 | D7F429A96CB04B05BA2E57BE99C8E2F1 |  | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 19:29 | 2013-10-02 19:31 | LENNOX - 13HPD-0240230-01 | 99 | 5.1 | Yes | Yes | 22.7 | 19.9 | 2.8 | 838E92F5D29F46DF8BDE01883217B70C |  | R22 | TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | TXV | 5.152%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 21:11 | 2013-09-30 21:13 | LENNOX - 13HPD024-01 | 99 | 5.8 | Yes | Yes | 23.1 | 20.4 | 2.7 | 5051580868704790BE0722F148446745 |  | R22 | TXV |  | 5.859% | 0.94141 | 11.26% | [5 empty] | TXV | 5.859%
Fresno | CA | 93703-4074 |  | 2013-06-26 | 2013-06-26 11:29 | 2013-06-26 11:56 | CARRIER - 585JH036060 | 102 | 5.5 | Yes | Yes | 20.9 | 15.5 | 5.4 | F35C9EB1C5E54375B337A014EC929228 |  | R22 | Non-TXV |  | 5.392% | 0.94608 | 10.36% | [5 empty] | Non-TXV | 5.392%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 19:11 | 2013-10-02 19:13 | LENNOX - 13HPD-024-230-01 | 99 | 6.4 | Yes | Yes | 22.9 | 19.9 | 3 | DA28937CA8C748B49D386FCD9A5F6F7D |  | R22 | TXV |  | 6.465% | 0.93535 | 12.42% | [5 empty] | TXV | 6.465%
Wasco | CA | 93280-0000 |  | 2013-09-30 | 2013-09-30 20:00 | 2013-09-30 20:02 | LENNOX - 13HPD-024-230-01 | 99 | -6.3 | Yes | Yes | 23.4 | 20.2 | 3.3 | C9BC669455E242F9A54E09A6A238CBE8 |  | R22 | TXV |  | -6.364% | 1.0636 | 1.782% |  |  |  |  | TXV |  |  | -6.364%
San Jose | CA | 95138-1367 |  | 2013-07-18 | 2013-07-18 11:18 | 2013-07-18 11:41 | BRYANT - 561CJ048-A | 159 | 15 | Yes | Yes | 24.3 | 18.3 | 6 | 777086DD4CA84B6D9D7CEAE4ED33A24F |  | R22 | TXV |  | 9.434% | 0.90566 | 18.13% | [5 empty] | TXV | 9.434%
Morgan Hill | CA | 95037-9404 |  | 2013-07-29 | 2013-07-29 13:20 | 2013-07-29 20:54 | DAY & NIGHT - 545AB060 | 222 | 33.2 | Yes | Yes | 16.9 | 17.5 | -0.6 | 94167FF40D914E7E8672F87A37C5706A |  | R22 | Non-TXV |  | 14.95% | 0.85045 | 28.74% | [5 empty] | Non-TXV | 14.95%
Morgan Hill | CA | 95037-9404 |  | 2013-07-29 | 2013-07-29 20:59 | 2013-07-29 21:16 | DAY & NIGHT - 661CJ036-E | 134 | 14.3 | Yes | Yes | 18.8 | 18.7 | 0.1 | E76EBE1980404FE19D3AC8BDC2A45853 |  | R22 | TXV |  | 10.67% | 0.89328 | 20.51% | [5 empty] | TXV | 10.67%
Fresno | CA | 93722-3492 |  | 2013-07-24 | 2013-07-24 16:42 | 2013-07-24 16:42 | - CA9048UJA2 | 206 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 9C4D73BAC5DF476B99048C8E7F576184 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7915 |  | 2013-06-28 | 2013-06-28 09:32 | 2013-06-28 09:32 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F5B329AFA21E496DBF0884F273669FC1 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 18:25 | 2013-10-04 18:29 | LENNOX - 13HPD-024-230-01 | 99 | 4 | Yes | Yes | 21.7 | 19.6 | 2.2 | 31310B4EFB294BC09C2143BBAF531971 |  | R22 | TXV |  | 4.04% | 0.9596 | 7.765% | [5 empty] | TXV | 4.04%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 19:38 | 2013-10-02 19:40 | LENNOX - 13HPD-024-230-01 | 99 | 4.2 | Yes | Yes | 23.1 | 20.4 | 2.7 | ACFA8352D928428A8EA59FEE1A8F712A |  | R22 | TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | TXV | 4.242%
Vallejo | CA | 94591-6823 |  | 2013-08-05 | 2013-08-05 10:15 | 2013-08-05 13:25 | TRANE - 2TTR304BA1000AA | 142 | 4.3 | Yes | Yes | 14.9 | 17.7 | -2.8 | 019F1F723A294E8DAF7F943487A1DAFB |  | R22 | Non-TXV |  | 3.028% | 0.96972 | 5.819% | [5 empty] | Non-TXV | 3.028%
Fresno | CA | 93720-1928 |  | 2013-07-01 | 2013-07-01 12:17 | 2013-07-01 13:02 | CARRIER - UKN | 80 | 5.6 | Yes | Yes | 17.6 | 17.6 | 0 | C1E7C45E9E2741D8935406316B633DFE |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93725-0000 |  | 2013-10-08 | 2013-10-08 18:37 | 2013-10-08 18:37 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D6F799BD2C544D5F8C8F7D10FB0F36A7 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 19:19 | 2013-10-01 19:21 | LENNOX - 13HPD-024-230-01 | 99 | 5 | Yes | Yes | 21 | 19.7 | 1.4 | 5325F324681A4532AE33EE6A24BAC30E |  | R22 | TXV |  | 5.051% | 0.94949 | 9.706% | [5 empty] | TXV | 5.051%
Fresno | CA | 93722-2207 |  | 2013-08-14 | 2013-08-14 10:22 | 2013-08-14 10:54 | CARRIER - 38BRB048321 | 167 | 13.4 | Yes | Yes | 19.7 | 20.4 | -0.7 | 58A28580198A4163AB3FE5431FA84DCF |  | R22 | Non-TXV |  | 8.024% | 0.91976 | 15.42% | [5 empty] | Non-TXV | 8.024%
Fresno | CA | 93710-5719 |  | 2013-07-01 | 2013-07-01 16:59 | 2013-07-01 16:59 | HEIL - NRGF36D0B03 | 90 | 0 | Yes | Yes | 20 | 19.3 | 0.8 | 51EB1F84D956442880FC47CC883DD790 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2377 |  | 2013-10-04 | 2013-10-04 18:21 | 2013-10-04 18:23 | LENNOX - 13HPD-024-230-01 | 99 | 8.3 | Yes | Yes | 23 | 19.9 | 3.1 | 66EF0F9F0AC440A2AFA2EFC1161E13D2 |  | R22 | TXV |  | 8.384% | 0.91616 | 16.11% | [5 empty] | TXV | 8.384%
San Jose | CA | 95110-3309 |  | 2013-09-30 | 2013-09-30 11:34 | 2013-09-30 12:09 | CARRIER - 38QRC024C 341 | 45 | 1.4 | Yes | Yes | 20.8 | 20.4 | 0.4 | E8DB956443FB4768B7B005024D2726F3 |  | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
San Jose | CA | 95122-1299 |  | 2013-09-16 | 2013-09-16 11:37 | 2013-09-16 11:55 | YORK - H`1RA036506A | 84 | 8 | Yes | Yes | 20.7 | 20.1 | 0.6 | D6AC9399B6044A8DADD9DCD44DF1153B |  | R22 | Non-TXV |  | 9.524% | 0.90476 | 18.3% | [5 empty] | Non-TXV | 9.524%
Fresno | CA | 93722-2230 |  | 2013-07-08 | 2013-07-08 09:58 | 2013-07-08 10:21 | LENNOX - 12ACB36 | 106 | 7.9 | Yes | Yes | 25.1 | 21.3 | 3.9 | 7600E71F0AE14923AA3860A12C712A4B |  | R22 | TXV |  | 7.453% | 0.92547 | 14.32% | [5 empty] | TXV | 7.453%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 19:46 | 2013-10-02 19:48 | LENNOX - 13HPD-024-230-01 | 99 | 7 | Yes | Yes | 22.8 | 20.4 | 2.4 | DA6268523E8B4B2BA2E4BF1ADC6FFCC5 |  | R22 | TXV |  | 7.071% | 0.92929 | 13.59% | [5 empty] | TXV | 7.071%
Wasco | CA | 93280-2374 |  | 2013-10-01 | 2013-10-01 19:14 | 2013-10-01 19:16 | LENNOX - 13HPD-024-230-01 | 99 | 5.1 | Yes | Yes | 23 | 20.2 | 2.9 | 515A6A34F64E4E2ABC72383E4BB23545 |  | R22 | TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | TXV | 5.152%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 18:48 | 2013-10-02 18:50 | LENNOX - 13HPD-024-230-01 | 99 | 5.2 | Yes | Yes | 21.7 | 20.4 | 1.3 | 02371A2C07324089AEF7658B1B4B9BC7 |  | R22 | TXV |  | 5.253% | 0.94747 | 10.09% | [5 empty] | TXV | 5.253%
Fresno | CA | 93720-0138 |  | 2013-07-11 | 2013-07-11 10:08 | 2013-07-11 11:12 | RUUD - UAFO-O48JBS | 101 | -5.9 | Yes | Yes | 16.1 | 19 | -2.9 | D5F394657B7B4B7585BCDA497227E66B |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Lemoore | CA | 93245-1904 |  | 2013-07-08 | 2013-07-08 13:11 | 2013-07-08 13:33 | YORK - D1NH036N05606C | 108 | 5.6 | Yes | Yes | 25 | 19.9 | 5.1 | EFEB921FAC1A45EFB5386EE3E8794023 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Wasco | CA | 93280-2375 |  | 2013-10-03 | 2013-10-03 20:59 | 2013-10-03 21:01 | LENNOX - 13HPD-024-01 | 99 | 9.1 | Yes | Yes | 22.2 | 20.2 | 2.1 | 5732FEBC183241F4B675FA4493632836 |  | R22 | TXV |  | 9.192% | 0.90808 | 17.66% | [5 empty] | TXV | 9.192%
Wasco | CA | 93280-2374 |  | 2013-10-07 | 2013-10-07 15:19 | 2013-10-07 15:21 | LENNOX - 13HPD-024-230-01 | 99 | -5.6 | Yes | Yes | 24.1 | 21.8 | 2.3 | 276B07865FE244A0A899CFB6E471B855 |  | R22 | TXV |  | -5.657% | 1.0566 | 1.584% |  |  |  |  | TXV |  |  | -5.657%
Wasco | CA | 93280-2375 |  | 2013-10-02 | 2013-10-02 19:32 | 2013-10-02 19:42 | LENNOX - 13HPD-024-230-01 | 99 | 4.2 | Yes | Yes | 23 | 20.4 | 2.6 | D3DD7AD2CC0E4F82B28187E0D6021566 |  | R22 | TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | TXV | 4.242%
Sanger | CA | 93657-3905 |  | 2013-08-05 | 2013-08-05 11:31 | 2013-08-05 11:49 | ARCOAIRE - NAC024AKB1 | 71 | 7 | Yes | Yes | 16.6 | 18.9 | -2.3 | 82276534DA7048188DCEA3A7418BECBF |  | R22 | TXV |  | 9.859% | 0.90141 | 18.95% | [5 empty] | TXV | 9.859%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 19:04 | 2013-10-04 19:06 | LENNOX - 13HPD-024-230-01 | 99 | 10.4 | Yes | Yes | 21.8 | 20.6 | 1.3 | 7B727B94C5F04B14B1DA3E539EE1F775 |  | R22 | TXV |  | 10.51% | 0.89495 | 20.19% | [5 empty] | TXV | 10.51%
Fairfield | CA | 94533-2188 |  | 2013-08-16 | 2013-08-16 12:14 | 2013-08-16 12:14 | PAYNE - PA10JA024000ACAA | 64 | -6 | Yes | Yes | 11.8 | 14.7 | -2.9 | 238EB87E7A9B4C8C8B40ABCC327A4429 | Remove refrigerant: 6 oz Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 19:03 | 2013-10-02 19:05 | LENNOX - 13HPD024-230-01 | 99 | 5.9 | Yes | Yes | 22.3 | 20.7 | 1.6 | 717E1101B2064819A2C4C19AB8CF93D4 |  | R22 | TXV |  | 5.96% | 0.9404 | 11.45% | [5 empty] | TXV | 5.96%
Sanger | CA | 93657-3905 |  | 2013-08-05 | 2013-08-05 12:20 | 2013-08-05 12:40 | ARCOAIRE - NACO24AKD1 | 87 | 9.9 | Yes | Yes | 19.9 | 19.2 | 0.7 | E41D7C4661DC438AAD5B4268EFDDAF3B |  | R22 | TXV |  | 11.38% | 0.88621 | 21.87% | [5 empty] | TXV | 11.38%
Bakersfield | CA | 93309-5769 |  | 2013-08-26 | 2013-08-26 13:45 | 2013-08-27 07:55 | ICP - PGAD36D1K6 | 102 | 6.1 | Yes | Yes | 19.6 | 20.4 | -0.8 | 36832C47DA3D408EB820534B849A412A |  | R22 | Non-TXV |  | 5.98% | 0.9402 | 11.49% | [5 empty] | Non-TXV | 5.98%
Lemoore | CA | 93245-2028 |  | 2013-06-27 | 2013-06-27 14:18 | 2013-06-27 14:51 | TRANE - Y0Y036F1M0AA | 136 | 23.6 | Yes | Yes | 18.6 | 20.4 | -1.8 | 2D706938B3FA419A84B18756AFD97C38 |  | R22 | Non-TXV |  | 17.35% | 0.82647 | 33.35% | [5 empty] | Non-TXV | 17.35%
Fresno | CA | 93706-3008 |  | 2013-07-25 | 2013-07-25 14:12 | 2013-07-25 14:30 | CARRIER - 535A048125YACR | 93 | 15.9 | Yes | Yes | 18.4 | 18.4 | 0 | 8546B797EABB47F5BF4278E012B61309 |  | R22 | Non-TXV |  | 17.1% | 0.82903 | 32.86% | [5 empty] | Non-TXV | 17.1%
Sanger | CA | 93657-4108 |  | 2013-07-03 | 2013-07-03 13:50 | 2013-07-03 14:15 | BRYANT - 588ANW030040ACAD | 53 | 4.3 | Yes | Yes | 21 | 19.6 | 1.4 | 0D2D10A5405C437B9CD20560CDC2CC07 |  | R22 | Non-TXV |  | 8.113% | 0.91887 | 15.59% | [5 empty] | Non-TXV | 8.113%
Sanger | CA | 93657-3905 |  | 2013-08-13 | 2013-08-13 09:08 | 2013-08-13 09:19 | OTHER - UNK | 87 | 6.3 | Yes | Yes | 18.4 | 19.4 | -1 | 0A840A7051844EC9A09FE3D5F7BAFA91 |  | R22 | Non-TXV |  | 7.241% | 0.92759 | 13.92% | [5 empty] | Non-TXV | 7.241%
Suisun City | CA | 94585-2730 |  | 2013-07-12 | 2013-07-12 13:45 | 2013-07-12 13:45 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 16.4 | 16.4 | 0 | A3C3C0E2DBF14FFEA1B6FD6757D3E9A3 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2299 |  | 2013-08-05 | 2013-08-05 10:36 | 2013-08-05 10:55 | ARCOAIRE - NAC224AKC3 | 86 | 4.9 | Yes | Yes | 20.2 | 19.1 | 1.1 | 8DE4E7B143B7409B8850945CDC7A7F61 |  | R22 | Non-TXV |  | 5.698% | 0.94302 | 10.95% | [5 empty] | Non-TXV | 5.698%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 19:09 | 2013-10-01 19:11 | LENNOX - 13HPD-024-230-01 | 99 | 4.7 | Yes | Yes | 22.3 | 20.2 | 2.2 | 1824C2326C5046BD94A1396DB2117D5F |  | R22 | TXV |  | 4.747% | 0.95253 | 9.124% | [5 empty] | TXV | 4.747%
Wasco | CA | 93280-2375 |  | 2013-10-03 | 2013-10-03 20:44 | 2013-10-03 20:45 | LENNOX - 13HPD-024-01 | 99 | 9.6 | Yes | Yes | 23.4 | 20.4 | 3 | 559F24BC94B84D2AA153DA2A5C49AFEE |  | R22 | TXV |  | 9.697% | 0.90303 | 18.64% | [5 empty] | TXV | 9.697%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 19:53 | 2013-10-01 19:54 | LENNOX - 13HPD-0240230-01 | 99 | -4.3 | Yes | Yes | 23.2 | 20.2 | 3.1 | C626D831BB8742B5BE906BAC2EC542A8 |  | R22 | TXV |  | -4.343% | 1.0434 | 1.216% |  |  |  |  | TXV |  |  | -4.343%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 19:00 | 2013-10-04 19:01 | LENNOX - 13HPD-024-230-01 | 99 | 8.4 | Yes | Yes | 22.6 | 20 | 2.6 | 987C59640F3F41A8A680E3D11EF3C324 |  | R22 | TXV |  | 8.485% | 0.91515 | 16.31% | [5 empty] | TXV | 8.485%
Wasco | CA | 93280-2375 |  | 2013-10-03 | 2013-10-03 21:19 | 2013-10-03 21:21 | LENNOX - 13HPD-024-01 | 99 | 5.9 | Yes | Yes | 22.2 | 20.8 | 1.4 | 0216F555C75A4E759529BE002FC781BA |  | R22 | TXV |  | 5.96% | 0.9404 | 11.45% | [5 empty] | TXV | 5.96%
Sanger | CA | 93657-3907 |  | 2013-08-06 | 2013-08-06 15:44 | 2013-08-06 16:03 | OTHER - GCGD24S21S2A | 61 | 7.4 | Yes | Yes | 16 | 18.8 | -2.8 | B346BBE73D3D4C65B235356BD435A5EF |  | R22 | TXV |  | 12.13% | 0.87869 | 23.31% | [5 empty] | TXV | 12.13%
Fresno | CA | 93727-0000 |  | 2013-06-28 | 2013-06-28 16:26 | 2013-06-28 16:26 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 7ED97224E1704C7986EE80E9810B2B01 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1538 |  | 2013-07-10 | 2013-07-10 12:45 | 2013-07-10 13:30 | GOODMAN - GPG13300451BB | 77 | 5.1 | Yes | Yes | 21.8 | 19.9 | 1.9 | 9A0862CBCA2F4D82A54E1A9BDF4C9494 |  | R22 | Non-TXV |  | 6.623% | 0.93377 | 12.73% | [5 empty] | Non-TXV | 6.623%
Wasco | CA | 93280-0000 |  | 2013-10-03 | 2013-10-03 21:10 | 2013-10-03 21:13 | LENNOX - 13HP07C29744 | 99 | -4.8 | Yes | Yes | 21.3 | 20.2 | 1.1 | 7534B0B3991D4C8FB218268E35DA058F |  | R22 | TXV |  | -4.848% | 1.0485 | 1.358% |  |  |  |  | TXV |  |  | -4.848%
Fresno | CA | 93702-4440 |  | 2013-10-15 | 2013-10-15 12:37 | 2013-10-15 13:13 | GOODMAN - GPG10420901A | 88 | 4.1 | Yes | Yes | 22.4 | 20.4 | 2 | A0A9310F497B436CA6E6DC6B53527E84 |  | R22 | TXV |  | 4.659% | 0.95341 | 8.954% | [5 empty] | TXV | 4.659%
Sanger | CA | 93657-2186 |  | 2013-09-30 | 2013-09-30 11:38 | 2013-09-30 12:05 | LENNOX - 12GCS030X756PA | 85 | 4.2 | Yes | Yes | 22.6 | 20.4 | 2.2 | AA4794DC42284A85892663C5F9FD82C2 |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Wasco | CA | 93280-2377 |  | 2013-10-05 | 2013-10-05 13:04 | 2013-10-05 13:20 | LENNOX - 13HPD-024-230-02 | 99 | 11.8 | Yes | Yes | 17.6 | 20.4 | -2.8 | 2DDC7AF9936D4C448D37234A72CE7933 |  | R22 | Non-TXV |  | 11.92% | 0.88081 | 22.91% | [5 empty] | Non-TXV | 11.92%
Wasco | CA | 93280-2372 |  | 2013-10-04 | 2013-10-04 19:46 | 2013-10-04 19:47 | LENNOX - 13HPD-024-230 | 99 | 8.7 | Yes | Yes | 21.2 | 20.8 | 0.4 | 41D5BAA390894C8D8EBDE87D1EC8E6C2 |  | R22 | TXV |  | 8.788% | 0.91212 | 16.89% | [5 empty] | TXV | 8.788%
Clovis | CA | 93611-5117 |  | 2013-06-26 | 2013-06-26 16:41 | 2013-06-26 18:12 | CARRIER - 48GS036060301 | 59 | 2.4 | Yes | Yes | 20 | 19.8 | 0.2 | EB60296BC66A41B9A3DC2B60A7A91498 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.068% | 0.95932 | 7.817% | [5 empty] | Non-TXV | 4.068%
San Jose | CA | 95124-5719 |  | 2013-07-18 | 2013-07-18 09:06 | 2013-07-18 09:35 | GOODMAN - CE30-1HR | 85 | 6.6 | Yes | Yes | 21 | 18.7 | 2.3 | 739995B5213943AFA26A34B20A822F7A |  | R22 | Non-TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | Non-TXV | 7.765%
Bakersfield | CA | 93313-5755 |  | 2013-08-08 | 2013-08-08 13:52 | 2013-08-08 14:23 | PAYNE - PA12NA036-H | 102 | 10.9 | Yes | Yes | 18.6 | 21.4 | -2.8 | D3D2A11CF2534F91B0F92F78FA9D7288 |  | R22 | Non-TXV |  | 10.69% | 0.89314 | 20.54% | [5 empty] | Non-TXV | 10.69%
Woodland | CA | 95695-2648 |  | 2013-07-26 | 2013-07-26 13:27 | 2013-07-26 13:47 | COLEMAN - UKN | 85 | 10.2 | Yes | Yes | 15.6 | 18.3 | -2.7 | 762D6EA6385247B88F7B1110E294E29F |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Sanger | CA | 93657-3907 |  | 2013-08-08 | 2013-08-08 13:04 | 2013-08-08 13:42 | ARCOAIRE - NAC24AKB1 | 67 | 4.4 | Yes | Yes | 16 | 18.4 | -2.4 | A7BAB881DAB64992BC7B3BAA525E133B |  | R22 | TXV |  | 6.567% | 0.93433 | 12.62% | [5 empty] | TXV | 6.567%
Novato | CA | 94947-4915 |  | 2013-07-05 | 2013-07-05 12:07 | 2013-07-05 13:04 | CARRIER - 24ABA336A310 | 84 | 3.2 | Yes | Yes | 19.2 | 17.5 | 1.7 | 614EB5E56919423B808B8DCCBAAC147E |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Sanger | CA | 93657-3904 |  | 2013-08-08 | 2013-08-08 17:24 | 2013-08-08 17:24 | ARCOAIRE - NACO24AKC3 | 71 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 929BDC60ED5542EA8BA66F3AD39425C8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3907 |  | 2013-08-05 | 2013-08-05 16:10 | 2013-08-05 17:27 | ARCOAIRE - NAC024AKC3 | 71 | 9.2 | Yes | Yes | 17.9 | 20.7 | -2.8 | 080F54A144584F48BE7562B437BF987D |  | R22 | TXV |  | 12.96% | 0.87042 | 24.9% | [5 empty] | TXV | 12.96%
Sanger | CA | 93657-3904 |  | 2013-08-05 | 2013-08-05 10:16 | 2013-08-05 10:48 | - NAC024AKC3 | 71 | 2.8 | Yes | Yes | 16.5 | 19 | -2.5 | C039325997444F95BCAC9435C2D8BD7E |  | R22 | TXV |  | 3.944% | 0.96056 | 7.579% | [5 empty] | TXV | 3.944%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 19:24 | 2013-10-02 19:34 | LENNOX - 13HPD-024-230-01 | 99 | 4.2 | Yes | Yes | 22.7 | 19.9 | 2.8 | D6A4375DE038456E8E888CFBD0318F46 |  | R22 | TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | TXV | 4.242%
Morgan Hill | CA | 95037-3763 |  | 2013-07-29 | 2013-07-29 12:40 | 2013-07-29 13:09 | OTHER - CA5548VKA1 | 85 | 2.8 | Yes | Yes | 16.5 | 18.2 | -1.7 | 12DF678C252349BF8298F202309A0FE3 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Sanger | CA | 93657-3908 |  | 2013-08-05 | 2013-08-05 15:44 | 2013-08-05 16:04 | ARCOAIRE - NAC024AKB1 | 67 | 4.4 | Yes | Yes | 18.9 | 20.2 | -1.3 | BB61E06FF4634E3691440D31E91D2969 |  | R22 | TXV |  | 6.567% | 0.93433 | 12.62% | [5 empty] | TXV | 6.567%
Fresno | CA | 93725-1866 |  | 2013-07-02 | 2013-07-02 13:01 | 2013-07-02 13:57 | OTHER - UKN | 88 | 4.5 | Yes | Yes | 19.6 | 19.9 | -0.3 | 5A4C52BC3C2B48028A63FBEEB41CAA1B |  | R22 | TXV |  | 5.114% | 0.94886 | 9.827% | [5 empty] | TXV | 5.114%
Sanger | CA | 93657-3907 |  | 2013-08-08 | 2013-08-08 17:23 | 2013-08-08 17:23 | ARCOAIRE - UKN | 71 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 17AB53C745584490AF80032D41C23A7C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3152 |  | 2013-09-26 | 2013-09-26 10:52 | 2013-09-26 11:14 | CARRIER - 38GS018240 | 58 | 9.4 | Yes | Yes | 17.6 | 17.6 | 0 | C62C3F92D8BB433AAB149788431A912A |  | R22 | Non-TXV |  | 16.21% | 0.83793 | 31.15% | [5 empty] | Non-TXV | 16.21%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 18:56 | 2013-10-01 18:59 | LENNOX - 13HPD-024-230-01 | 99 | 4 | Yes | Yes | 22 | 19.9 | 2.1 | C11633A9773F40388CF70B39B24F1337 |  | R22 | TXV |  | 4.04% | 0.9596 | 7.765% | [5 empty] | TXV | 4.04%
Wasco | CA | 93280-0000 |  | 2013-10-02 | 2013-10-02 19:17 | 2013-10-02 19:20 | LENNOX - 13HPD-024-230-01 | 99 | 5.7 | Yes | Yes | 22.6 | 20.4 | 2.2 | A5698EC36D494D8999A163EC0D39898E |  | R22 | TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | TXV | 5.758%
Fresno | CA | 93710-5422 |  | 2013-07-01 | 2013-07-01 16:42 | 2013-07-01 20:42 | BRYANT - 561CJ36 | 71 | 9 | Yes | Yes | 23.2 | 19.5 | 3.7 | 35CE1668CBBE4F68BA3B0A722E219958 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.68% | 0.87324 | 24.36% | [5 empty] | Non-TXV | 12.68%
Vacaville | CA | 95688-2304 |  | 2013-06-27 | 2013-06-27 15:00 | 2013-06-27 15:00 | RUUD - UAMB-036JAZ | 93 | 0 | Yes | Yes | 14.1 | 16.9 | -2.8 | 9932174D24464C6E9ED7DD3B9C15FA72 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93737-9522 |  | 2013-08-31 | 2013-08-31 14:11 | 2013-08-31 14:28 | RHEEM - RAHE048JAS | 114 | -9.4 | Yes | Yes | 23.6 | 19.9 | 3.7 | BB7C336F97F144C19CC544DB115E4D0C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -8.246% | 1.0825 | 2.309% |  |  |  |  | Non-TXV |  |  | -8.246%
Fresno | CA | 93722-9085 |  | 2013-07-03 | 2013-07-03 10:23 | 2013-07-03 11:26 | LENNOX - 12GCS030-75-3PA | 85 | 2.5 | Yes | Yes | 25.6 | 21.2 | 4.4 | C8E68261E7934DF38E300BC2E3CCC5C4 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Sanger | CA | 93657-3904 |  | 2013-08-08 | 2013-08-08 16:55 | 2013-08-08 17:22 | ARCOAIRE - NAC024AKC3 | 71 | 7.7 | Yes | Yes | 17.7 | 19.7 | -2 | 2C2DCF2EB15542C68F2F9ACC27162BBE |  | R22 | TXV |  | 10.85% | 0.89155 | 20.84% | [5 empty] | TXV | 10.85%
Clovis | CA | 93612-4682 |  | 2013-07-10 | 2013-07-10 19:26 | 2013-07-10 19:54 | PAYNE - UNK | 80 | 2.5 | Yes | Yes | 18.3 | 19.9 | -1.6 | E3F8E91B056D4F8F8B52C54F7C5F0FB9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
San Jose | CA | 95116-2616 |  | 2013-09-23 | 2013-09-23 10:50 | 2013-09-23 11:12 | - GCGD48S4153A | 73 | -4.3 | Yes | Yes | 19.8 | 18.2 | 1.6 | 4A8DE9B3F1BF4D94857F07F16EC57129 |  | R410A | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Bakersfield | CA | 93304-3535 |  | 2013-08-09 | 2013-08-09 10:05 | 2013-08-09 10:21 | YORK - D1NH036NH05606C | 111 | 15.5 | Yes | Yes | 21.9 | 20.9 | 1 | B7504F8B139042C898F399F618BD6C0C |  | R22 | Non-TXV |  | 13.96% | 0.86036 | 26.84% | [5 empty] | Non-TXV | 13.96%
Fresno | CA | 93711-0824 |  | 2013-09-19 | 2013-09-19 09:39 | 2013-09-19 10:08 | PAYNE - PY3GNAA60090N0 | 160 | -6.4 | Yes | Yes | 24 | 19.5 | 4.5 | 574C69E1A8C14F39A7BC1BAE4165B1DC |  | R410A | Non-TXV |  | -4% | 1.04 | 1.12% |  |  |  |  | Non-TXV |  |  | -4%
Wasco | CA | 93280-2375 |  | 2013-10-03 | 2013-10-03 20:37 | 2013-10-03 20:37 | LENNOX - 13HPD-024-01 | 99 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 7510FA4FEF054342BE96DE6252950881 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6027 |  | 2013-07-03 | 2013-07-03 14:14 | 2013-07-03 14:14 | RHEEM - RRMA-A036JK06E | 99 | 0 | Yes | Yes | 18.4 | 20.4 | -2 | 9EB2BCB5C18B4A168CF477CC4EF6ED34 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94087-1352 |  | 2013-10-03 | 2013-10-03 15:24 | 2013-10-03 15:59 | CARRIER - UNK | 70 | 8.6 | Yes | Yes | 23.6 | 21.4 | 2.2 | C01ED22C51F4425897C5296FC6B531A6 |  | R22 | Non-TXV |  | 12.29% | 0.87714 | 23.61% | [5 empty] | Non-TXV | 12.29%
Lamont | CA | 93241-2771 |  | 2013-09-11 | 2013-09-11 14:42 | 2013-09-11 15:55 | ARMSTRONG - 2AC13B24P213 | 89 | 2.9 | Yes | Yes | 20.2 | 19.5 | 0.7 | 90F7973E818343ECB49DA49B946168F1 |  | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.262% | [5 empty] | Non-TXV | 3.258%
Lamont | CA | 93241-2716 |  | 2013-09-12 | 2013-09-12 11:26 | 2013-09-12 11:43 | DUCANE - 2AC1324P 2B | 89 | 9.2 | Yes | Yes | 18.5 | 19.5 | -1 | B6DC5794AB1D4A3ABF37D3765D05F818 |  | R22 | Non-TXV |  | 10.34% | 0.89663 | 19.87% | [5 empty] | Non-TXV | 10.34%
Sanger | CA | 93657-3905 |  | 2013-08-08 | 2013-08-08 11:22 | 2013-08-08 12:04 | ARCOAIRE - NAC024AKB2 | 60 | 3.2 | Yes | Yes | 18.3 | 18.8 | -0.5 | 988B814522394A24B93DEB547E4C9B65 |  | R22 | TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | TXV | 5.333%
Kerman | CA | 93630-0000 |  | 2013-08-07 | 2013-08-07 09:29 | 2013-08-07 09:59 | AMERICAN STANDARD - 4YCC3036A1064AB | 124 | -8.8 | Yes | Yes | 21.9 | 18.2 | 3.7 | E69307CCE567466D9E560472ACDEAB9F |  | R410A | TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | TXV |  |  | -7.097%
Petaluma | CA | 94954-1476 |  | 2013-07-17 | 2013-07-17 11:45 | 2013-07-17 11:48 | CARRIER - 38CKC036350 | 70 | 8.5 | Yes | Yes | 17.7 | 17.6 | 0.1 | F0964DAF85544F088A03E95BA4047C0E |  | R22 | Non-TXV |  | 12.14% | 0.87857 | 23.34% | [5 empty] | Non-TXV | 12.14%
San Jose | CA | 95116-3086 |  | 2013-09-23 | 2013-09-23 14:16 | 2013-09-23 14:38 | GOODMAN - CK36-1B | 76 | -4.5 | Yes | Yes | 17.6 | 19.5 | -1.9 | EE95161073A74EB68482FD3645E84D97 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Fresno | CA | 93711-6662 |  | 2013-07-11 | 2013-07-11 16:23 | 2013-07-11 16:52 | RHEEM - RRNA-B030JK06X | 72 | 2.4 | Yes | Yes | 24.1 | 21 | 3.1 | 042691CF5E97468ABAF113C8078C7888 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93304-3562 |  | 2013-09-25 | 2013-09-25 18:03 | 2013-09-25 18:20 | BRYANT - 574BNW060090NA | 210 | 15.3 | Yes | Yes | 20.8 | 21 | -0.2 | 5CD8393F120A4A27AC1B2D87DD3939ED |  | R22 | Non-TXV |  | 7.286% | 0.92714 | 14% | [5 empty] | Non-TXV | 7.286%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 19:35 | 2013-09-30 19:37 | LENNOX - 13HPD-024-230-01 | 99 | 5.9 | Yes | Yes | 21.5 | 19.9 | 1.6 | 8761A59B05A54DCB9C8BB60E4E942A14 |  | R22 | TXV |  | 5.96% | 0.9404 | 11.45% | [5 empty] | TXV | 5.96%
Bakersfield | CA | 93304-1561 |  | 2013-07-20 | 2013-07-20 16:05 | 2013-07-20 16:05 | CARRIER - 38YCC0124340 | 68 | 0 | Yes | Yes | 21.6 | 21.4 | 0.2 | E59BAB2DACF84E3A805BAA56A342202F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1562 |  | 2013-07-18 | 2013-07-18 15:12 | 2013-07-18 15:12 | CARRIER - 38YC018340 | 66 | 0 | Yes | Yes | 20.6 | 19.3 | 1.3 | 29CBA30F155D4D3F84F36FDAFA663587 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 15:24 | 2013-07-23 15:24 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 20 | 20.8 | -0.8 | A5555E71CC8A4979AAF140642C40B7F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2377 |  | 2013-10-04 | 2013-10-04 20:27 | 2013-10-04 20:45 | LENNOX - 13HP-024-230-02 | 99 | 10 | Yes | Yes | 24 | 20.5 | 3.5 | 08BD0F98CDA14024AD3FA9EA4416C31A | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 10.1% | 0.89899 | 19.41% | [5 empty] | TXV | 10.1%
Fresno | CA | 93703-1135 |  | 2013-07-02 | 2013-07-02 16:54 | 2013-07-02 16:54 | OTHER - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | FB5AC6031A2944B891409D6757078612 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 15:10 | 2013-07-23 15:10 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 18.7 | 19.8 | -1.1 | 46AFD6E8BB2A458D85FC9C28EEC27E6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 15:40 | 2013-07-23 15:40 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 21.3 | 20.6 | 0.7 | A8DCAB89F84F478AA0DBD82CCCD8E2F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 16:08 | 2013-07-23 16:08 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 20.8 | 20.8 | 0 | 65A58A88AE9245029B6759D1CE576CA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 15:58 | 2013-07-23 15:58 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 21.2 | 19.7 | 1.5 | 55107323AB244E53A12B1383C335F991 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1214 |  | 2013-07-09 | 2013-07-09 09:39 | 2013-07-09 10:24 | YORK - DBYPF042N080 | 150 | 12.1 | Yes | Yes | 19.2 | 18.7 | 0.5 | D811CCE0F2F24A52849CCB7C5EC61A70 |  | R22 | Non-TXV |  | 8.067% | 0.91933 | 15.5% | [5 empty] | Non-TXV | 8.067%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 18:30 | 2013-07-22 18:30 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 18.4 | 20.4 | -2 | C047191502DE4B7E97A35DBA92671446 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3908 |  | 2013-08-05 | 2013-08-05 16:16 | 2013-08-05 16:38 | ARCOAIRE - NAC024AKB1 | 67 | -5.6 | Yes | Yes | 20 | 19.3 | 0.7 | CA7917DB13CE4392AE76455918D29239 |  | R22 | TXV |  | -8.358% | 1.0836 | 2.341% |  |  |  |  | TXV |  |  | -8.358%
Wasco | CA | 93280-2377 |  | 2013-10-04 | 2013-10-04 22:13 | 2013-10-04 22:30 | LENNOX - 13HPD-024-230-02 | 99 | 11.5 | Yes | Yes | 16.6 | 19.6 | -3 | A5B72C72BB6440DA88E6FECE9505D454 |  | R22 | TXV |  | 11.62% | 0.88384 | 22.32% | [5 empty] | TXV | 11.62%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 14:23 | 2013-07-23 14:39 | CARRIER - 38YCC018340 | 66 | 8.9 | Yes | Yes | 20.4 | 20.1 | 0.3 | D21A76D9AE084A4D846B3A67E114D84F |  | R22 | Non-TXV |  | 13.48% | 0.86515 | 25.91% | [5 empty] | Non-TXV | 13.48%
Wasco | CA | 93280-2375 |  | 2013-10-03 | 2013-10-03 20:26 | 2013-10-03 20:28 | LENNOX - 13HPD-024-01 | 99 | 11.1 | Yes | Yes | 24.6 | 19.9 | 4.7 | 37459924A203457A984DB8036DA04397 |  | R22 | TXV |  | 11.21% | 0.88788 | 21.55% | [5 empty] | TXV | 11.21%
Bakersfield | CA | 93307-6076 |  | 2013-08-08 | 2013-08-08 15:02 | 2013-08-08 15:02 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | 697F7C3A06454F60AD56B1DF57A6471D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-4803 |  | 2013-07-17 | 2013-07-17 12:27 | 2013-07-17 12:56 | OTHER - 13AJA36A01 | 85 | 8.2 | Yes | Yes | 19 | 17.1 | 1.9 | 33E29DDB4FC84FFE8895827DB715DB46 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Fresno | CA | 93720-0220 |  | 2013-07-12 | 2013-07-12 09:43 | 2013-07-12 10:15 | CARRIER - UNK | 80 | 2.6 | Yes | Yes | 20 | 20.4 | -0.4 | 02F35C8D2F264552B4060D02CA308B14 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Bakersfield | CA | 93304-3424 |  | 2013-07-02 | 2013-07-02 08:57 | 2013-07-02 09:56 | GOODMAN - VSC130301AA | 106 | 22.4 | Yes | Yes | 18.3 | 19.6 | -1.3 | EC607BD5C9FE469FB7C7A2E864801CDF |  | R22 | Non-TXV |  | 21.13% | 0.78868 | 40.61% | [5 empty] | Non-TXV | 21.13%
Bakersfield | CA | 93309-5126 |  | 2013-07-02 | 2013-07-02 09:05 | 2013-07-02 09:30 | TEMPSTAR - PGAD36D1K | 102 | 3 | Yes | Yes | 19.1 | 19.8 | -0.7 | 46274AEA073C47E882503A8A73748023 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Wasco | CA | 93280-2377 |  | 2013-10-05 | 2013-10-05 10:55 | 2013-10-05 11:27 | LENNOX - 13HPD-024-230-02 | 99 | 8 | Yes | Yes | 18 | 20 | -2 | 97591A70F0FF44548BF3A99F6E8DEC69 |  | R22 | TXV |  | 8.081% | 0.91919 | 15.53% | [5 empty] | TXV | 8.081%
Wasco | CA | 93280-2377 |  | 2013-10-05 | 2013-10-05 13:23 | 2013-10-05 13:40 | LENNOX - 13HPD-024-230-02 | 99 | 10.6 | Yes | Yes | 17.2 | 20.2 | -3 | 25AE62FA4AAA4905AAB0819F11D53E8E |  | R22 | TXV |  | 10.71% | 0.89293 | 20.58% | [5 empty] | TXV | 10.71%
Clovis | CA | 93611-3038 |  | 2013-11-07 | 2013-11-07 15:34 | 2013-11-07 15:34 | CARRIER - 48SS-030060331 | 56 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | 0ED72B19C0864D4480AEEC920AAE5264 | Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 21:00 | 2013-09-30 21:03 | LENNOX - 13HPD-024-230-01 | 99 | 4 | Yes | Yes | 23 | 19.9 | 3.1 | 929C1FA358B8481F9024C4F2F14EE862 |  | R22 | TXV |  | 4.04% | 0.9596 | 7.765% | [5 empty] | TXV | 4.04%
Fresno | CA | 93702-3809 |  | 2013-07-15 | 2013-07-15 14:01 | 2013-07-15 14:20 | ICP - GCPM036K060F | 88 | 3 | Yes | Yes | 27.8 | 23.2 | 4.6 | D0C8648BBDDA4FBB9C091DC1A9A2E486 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Fresno | CA | 93728-1035 |  | 2013-07-09 | 2013-07-09 12:26 | 2013-07-09 12:53 | OTHER - UKN | 80 | 8.7 | Yes | Yes | 22.5 | 17.1 | 5.4 | B672DEA29C9047D296CD7F1126183155 |  | R22 | Non-TXV |  | 10.88% | 0.89125 | 20.9% | [5 empty] | Non-TXV | 10.88%
Bakersfield | CA | 93304-2361 |  | 2013-07-01 | 2013-07-01 18:39 | 2013-07-01 18:39 | ICP - BCUP-F030AA | 92 | 0 | Yes | Yes | 18.5 | 19.3 | -0.8 | 3019AC5971F84676A53321ABA066AC26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3062 |  | 2013-06-28 | 2013-06-28 12:23 | 2013-06-28 12:23 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | B16AA7749B2A4008A813CE0F321DF291 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-2414 |  | 2013-08-30 | 2013-08-30 15:46 | 2013-08-30 15:46 | OTHER - UKN | 74 | 0 | Yes | Yes | 0 | N/A | N/A | 4C9AA04E6530420DB40E6E19E4E7F992 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5032 |  | 2013-06-27 | 2013-06-27 14:40 | 2013-06-27 15:23 | RHEEM - RRKA030JKO6E | 54 | -4.4 | Yes | Yes | 20.8 | 16.8 | 4 | FBC340EE16934098B84D8A30A8BC83F3 |  | R22 | Non-TXV |  | -8.148% | 1.0815 | 2.282% |  |  |  |  | Non-TXV |  |  | -8.148%
Fresno | CA | 93711-1415 |  | 2013-06-27 | 2013-06-27 17:55 | 2013-06-27 20:00 | RHEEM - RRKAA060JK10X | 119 | -10.2 | Yes | Yes | 21.5 | 19.7 | 1.8 | 4E77C31A96464FBE8B03C76DE790041A |  | R22 | TXV |  | -8.571% | 1.0857 | 2.4% |  |  |  |  | TXV |  |  | -8.571%
Fresno | CA | 93705-3528 |  | 2013-07-06 | 2013-07-06 12:47 | 2013-07-24 22:54 | TEMPSTAR - PGAD60E1K1 | 112 | 4.1 | Yes | Yes | 25.6 | 22.1 | 3.5 | 841CF6B394B248979A1BE27647DAF47B | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | TXV | 3.661%
Fresno | CA | 93722-9096 |  | 2013-07-12 | 2013-07-12 13:12 | 2013-07-12 14:09 | LENNOX - 12GCS042X753PA | 133 | 5.2 | Yes | Yes | 24.1 | 21 | 3.1 | 99C5DB4097744191B1280DB6D15B707E |  | R22 | Non-TXV |  | 3.91% | 0.9609 | 7.514% | [5 empty] | Non-TXV | 3.91%
Fresno | CA | 93704-4809 |  | 2013-07-05 | 2013-07-05 10:38 | 2013-07-05 12:36 | RUUD - UNK | 128 | 5 | Yes | Yes | 23.7 | 18.8 | 4.9 | 6D60300C4E5A45F78554F25BE49F08E5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.906% | 0.96094 | 7.507% | [5 empty] | Non-TXV | 3.906%
Fresno | CA | 93728-1415 |  | 2013-06-27 | 2013-06-27 13:54 | 2013-06-27 14:26 | CARRIER - 48TMX036----301-- | 108 | 3.2 | Yes | Yes | 16.2 | 17.1 | -0.9 | F118FF0F766A49D09AF3A5AB706DEA32 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Wasco | CA | 93280-2375 |  | 2013-10-03 | 2013-10-03 20:51 | 2013-10-03 20:53 | LENNOX - 13HPD-024-01 | 99 | 10.2 | Yes | Yes | 22.2 | 20.4 | 1.8 | EE3F8541B5F5485FAD5F6B529BA0DAF4 |  | R22 | TXV |  | 10.3% | 0.89697 | 19.8% | [5 empty] | TXV | 10.3%
Fresno | CA | 93720-0502 |  | 2013-07-31 | 2013-07-31 10:10 | 2013-07-31 10:47 | OTHER - EAFF061JAZ | 192 | 9.3 | Yes | Yes | 25.8 | 20.9 | 4.9 | BAA068569AE94181A1F33D4C047256D6 |  | R22 | TXV |  | 4.844% | 0.95156 | 9.309% | [5 empty] | TXV | 4.844%
Wasco | CA | 93280-2377 |  | 2013-10-05 | 2013-10-05 11:50 | 2013-10-05 12:14 | LENNOX - 13HPD-024-230-02 | 99 | -9.1 | Yes | Yes | 18.3 | 20.5 | -2.2 | 31BE2643FBC94B628B548117A470ED6C |  | R22 | TXV |  | -9.192% | 1.0919 | 2.574% |  |  |  |  | TXV |  |  | -9.192%
Bakersfield | CA | 93311-9017 |  | 2013-07-09 | 2013-07-09 18:43 | 2013-07-09 19:06 | WEATHER KING - 13AJA36A01 | 85 | 2.5 | Yes | Yes | 18 | 17.6 | 0.4 | 1A808D96AB14408B86EC5F4166A75649 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93311-9017 |  | 2013-07-09 | 2013-07-09 19:08 | 2013-07-09 19:41 | WEATHER KING - 13AJA36A01 | 85 | 3 | Yes | Yes | 15.7 | 18.3 | -2.6 | FCCD720242FA46FEA2F740C9A0D7BF42 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
San Jose | CA | 95127-4540 |  | 2013-07-18 | 2013-07-18 11:50 | 2013-07-18 12:30 | RHEEM - RAKA-042JAZ | 85 | 6.9 | Yes | Yes | 22.1 | 16.1 | 6 | D9445177B69B416FB57F356C22649870 |  | R22 | Non-TXV |  | 8.118% | 0.91882 | 15.6% | [5 empty] | Non-TXV | 8.118%
Fresno | CA | 93722-4007 |  | 2013-07-01 | 2013-07-01 09:39 | 2013-07-01 10:11 | ICP - PGF354100K01 | 212 | -8.5 | Yes | Yes | 18.9 | 19.1 | -0.2 | 5D7B098CB030477EA4026A96E28169DD |  | R22 | TXV |  | -4.009% | 1.0401 | 1.123% |  |  |  |  | TXV |  |  | -4.009%
Fresno | CA | 93725-4001 |  | 2013-07-31 | 2013-07-31 15:05 | 2013-07-31 15:31 | GOODMAN - GPG13360451AB | 112 | 7 | Yes | Yes | 25.1 | 19.6 | 5.5 | 6DFF5AC79512484199351E3949BAECD9 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fresno | CA | 93704-3800 |  | 2013-10-10 | 2013-10-10 13:00 | 2013-10-10 18:24 | YORK - D1NH036N05606C | 108 | 10.4 | Yes | Yes | 21.1 | 19.1 | 2 | 16131C286BE94870ADD9C9092FABECE6 |  | R22 | Non-TXV |  | 9.63% | 0.9037 | 18.51% | [5 empty] | Non-TXV | 9.63%
Fresno | CA | 93704-4482 |  | 2013-07-12 | 2013-07-12 15:44 | 2013-07-12 15:44 | - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | FFFD3018447B434FBA83765B557FAF69 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3551 |  | 2013-08-07 | 2013-08-07 17:16 | 2013-08-07 18:27 | ICP - N2A436GKA100 | 160 | 4.8 | Yes | Yes | 28.2 | 22.6 | 5.6 | 1F829CC7F3054CD184859C25F3212102 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93308-0000 |  | 2013-07-09 | 2013-07-09 11:09 | 2013-07-09 11:31 | YORK - D1NP030N056A | 73 | 12.9 | Yes | Yes | 20.3 | 22.6 | -2.3 | 741899E14BBC458F8F40E0FDD88324DE |  | R22 | Non-TXV |  | 17.67% | 0.82329 | 33.96% | [5 empty] | Non-TXV | 17.67%
Wasco | CA | 93280-0000 |  | 2013-10-05 | 2013-10-05 03:55 | 2013-10-05 04:17 | LENNOX - 13HPD-024-230-02 | 99 | 12 | Yes | Yes | 14.9 | 17.9 | -3 | F8E1EF3F6BA64733BF9EF2B857E5BAC9 |  | R22 | TXV |  | 12.12% | 0.87879 | 23.29% | [5 empty] | TXV | 12.12%
Redding | CA | 96003-0377 |  | 2013-07-16 | 2013-07-16 12:17 | 2013-07-16 13:13 | RUUD - UAMC 042JAZ | 96 | -5.6 | Yes | Yes | 22.2 | 20.1 | 2.1 | D14664F7ADB44756BA1A1F075E3AD640 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Vacaville | CA | 95688-2324 |  | 2013-07-09 | 2013-07-09 10:13 | 2013-07-09 10:35 | TRANE - 4TTR2036A1000AA | 78 | 3.1 | Yes | Yes | 14.9 | 16.3 | -1.4 | 228ABA277BFA4ACA9620E2CEFD6011BC |  | R410A | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
San Jose | CA | 95118-1458 |  | 2013-10-08 | 2013-10-08 13:29 | 2013-10-08 14:57 | DAY & NIGHT - 597CN036 | 102 | 9.1 | Yes | Yes | 20.7 | 21.5 | -0.8 | 9EDAD11192E44BE3B9BC953C59AA8D03 |  | R22 | Non-TXV |  | 8.922% | 0.91078 | 17.15% | [5 empty] | Non-TXV | 8.922%
Bakersfield | CA | 93306-2424 |  | 2013-08-10 | 2013-08-10 17:13 | 2013-08-10 17:13 | BDP - 585B048125YACR | 85 | 0 | Yes | Yes | 21.8 | 22.1 | -0.3 | E080EC7FA7EC4B7897C2CE9C535AA0C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95405-8356 |  | 2013-07-22 | 2013-07-22 11:17 | 2013-07-22 11:18 | CARRIER - 38CKC036330 | 70 | 2.8 | Yes | Yes | 15.3 | 16.3 | -1 | 50E3669A082848FFA1396C2B577ED0DE |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Vallejo | CA | 94589-2035 |  | 2013-06-28 | 2013-06-28 13:29 | 2013-06-28 13:29 | AMERICAN STANDARD - YCC030F1M0BH | 69 | 5 | Yes | Yes | 20.5 | 18 | 2.5 | 819EDE12271840DFAD60F066FB1AA076 | Add refrigerant: 5 oz | R22 | Non-TXV |  | 7.246% | 0.92754 | 13.93% | [5 empty] | Non-TXV | 7.246%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 18:51 | 2013-10-04 18:53 | LENNOX - 13HPD-0240230-01 | 99 | 5.9 | Yes | Yes | 22.6 | 20.4 | 2.2 | CFFD0426D1084790BE33C92E3A171C5A |  | R22 | TXV |  | 5.96% | 0.9404 | 11.45% | [5 empty] | TXV | 5.96%
Bakersfield | CA | 93308-3462 |  | 2013-07-11 | 2013-07-11 19:20 | 2013-07-11 19:20 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | B2DCE26A93DE4E3A8083C10B6BE90B01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2372 |  | 2013-09-30 | 2013-09-30 19:56 | 2013-09-30 19:58 | LENNOX - 13HPD-0240230-01 | 99 | -4.7 | Yes | Yes | 22.9 | 20.4 | 2.5 | 29A4529CBE9940AE9993150696A236EA |  | R22 | TXV |  | -4.747% | 1.0475 | 1.33% |  |  |  |  | TXV |  |  | -4.747%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 18:52 | 2013-10-02 18:55 | LENNOX - 13HPD-024-230-01 | 99 | 6.1 | Yes | Yes | 23.7 | 21 | 2.7 | 5FE04C5605364AA782CDE903E2E59ADC |  | R22 | TXV |  | 6.162% | 0.93838 | 11.84% | [5 empty] | TXV | 6.162%
Arvin | CA | 93203-9452 |  | 2013-08-11 | 2013-08-11 11:35 | 2013-08-11 12:05 | GOODMAN - GSC130481AC | 85 | -8 | Yes | Yes | 20.9 | 20.6 | 0.3 | E19E26E305E947D9966E307746F334BF |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93305-3068 |  | 2013-06-27 | 2013-06-27 18:10 | 2013-06-27 18:35 | CARRIER - 48GSN024040301 | 85 | -8 | Yes | Yes | 17 | 17.5 | -0.5 | 183343E0211447F2A2666D6897063567 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Vacaville | CA | 95687-7709 |  | 2013-07-02 | 2013-07-02 09:52 | 2013-07-02 10:17 | YORK - 1DE060S06B | 122 | 18.5 | Yes | Yes | 21.4 | 20.3 | 1.1 | 57677C0181CC4B17A3FDCDB750AAF513 |  | R22 | Non-TXV |  | 15.16% | 0.84836 | 29.14% | [5 empty] | Non-TXV | 15.16%
Livermore | CA | 94550-5350 |  | 2013-07-23 | 2013-07-23 14:57 | 2013-07-23 14:57 | CARRIER - 38CKB035330 | 90 | 0 | Yes | Yes | 17.2 | 17.7 | -0.5 | 792C4F4171BC43D99E83D86CCE45D67A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2714 |  | 2013-09-12 | 2013-09-12 14:39 | 2013-09-12 15:04 | DUCANE - 2AC13B24P 2B | 89 | 4.7 | Yes | Yes | 20.4 | 20.2 | 0.2 | 3C65A6712EB54B94A730D69BD144A70E |  | R22 | Non-TXV |  | 5.281% | 0.94719 | 10.15% | [5 empty] | Non-TXV | 5.281%
Lamont | CA | 93241-2714 |  | 2013-09-12 | 2013-09-12 16:22 | 2013-09-12 20:03 | DUCANE - 2413B24P 2B | 98 | 8.3 | Yes | Yes | 20.1 | 20.1 | 0 | BAC45C1A0CC742909A347BA03D8384EF |  | R22 | Non-TXV |  | 8.469% | 0.91531 | 16.28% | [5 empty] | Non-TXV | 8.469%
San Jose | CA | 95122-1299 |  | 2013-09-25 | 2013-09-25 14:07 | 2013-09-25 14:07 | CARRIER - UNK | 70 | 0 | Yes | Yes | 2.3 | 19.7 | -17.4 | 26D95D60062F45B2AB7B39528DFEA290 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6511 |  | 2013-08-23 | 2013-08-23 16:48 | 2013-08-23 16:48 | ICP - PGD330040K001C1 | 100 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 60A75A6287B94DDDB3CC07DD333FFAED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4919 |  | 2013-07-26 | 2013-07-26 10:43 | 2013-07-26 11:19 | AMERICAN STANDARD - YCC024F1L0BJ | 66 | -0.2 | Yes | Yes | 16.7 | 18.2 | -1.5 | 9007A4EDE0E74D1585B3680E51F0DCE8 |  | R22 | Non-TXV |  | -0.303% | 1.003 | 0.08486% |  |  |  |  | Non-TXV |  |  | -0.303%
Bakersfield | CA | 93309-4259 |  | 2013-08-07 | 2013-08-07 21:09 | 2013-08-07 21:18 | YORK - D1NP036N05606A | 108 | 8.8 | Yes | Yes | 23.1 | 17.2 | 5.9 | 56D36DA668874874B977FD9CC36CFC4A |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Bakersfield | CA | 93309-4259 |  | 2013-08-07 | 2013-08-07 21:19 | 2013-08-07 21:22 | YORK - D1NP036N05606A | 108 | 4.4 | Yes | Yes | 20.9 | 19.8 | 1.1 | 7BCA10767C8E4D9283C0EE5552BB152C |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Fairfield | CA | 94533-2132 |  | 2013-09-19 | 2013-09-19 11:09 | 2013-09-19 11:11 | OTHER - NA | 68 | 3.3 | Yes | Yes | 17.5 | 17.6 | -0.1 | A524DE94ED504C2C8C65DA74263AB81C |  | R22 | Non-TXV |  | 4.853% | 0.95147 | 9.326% | [5 empty] | Non-TXV | 4.853%
Vallejo | CA | 94591-8382 |  | 2013-07-15 | 2013-07-15 11:59 | 2013-07-15 12:25 | CARRIER - 38CK0423-311 | 90 | 14.1 | Yes | Yes | 17.8 | 20.6 | -2.8 | 06B5183774424BAEB39743F6C96B725A |  | R22 | Non-TXV |  | 15.67% | 0.84333 | 30.11% | [5 empty] | Non-TXV | 15.67%
Fairfield | CA | 94533-2131 |  | 2013-08-13 | 2013-08-13 10:12 | 2013-08-13 10:12 | PAYNE - PA13NA024-B | 63 | 0 | Yes | Yes | 14.6 | 17.5 | -2.9 | 93C31CD39F6746029F72637F273ADAD7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4114 |  | 2013-07-12 | 2013-07-12 18:33 | 2013-07-12 19:03 | RHEEM - N/A | 85 | 17.6 | Yes | Yes | 19.3 | 20.8 | -1.5 | 1F35D084B6D5475399362F75CCBFCAAE |  | R22 | Non-TXV |  | 20.71% | 0.79294 | 39.79% | [5 empty] | Non-TXV | 20.71%
Bakersfield | CA | 93313-4321 |  | 2013-07-12 | 2013-07-12 19:25 | 2013-07-12 19:43 | YORK - D1NA036N05606C | 67 | 2.4 | Yes | Yes | 21.7 | 21.5 | 0.2 | 1829CD931D3C4E54B8633BAA99747677 |  | R22 | Non-TXV |  | 3.582% | 0.96418 | 6.884% | [5 empty] | Non-TXV | 3.582%
Bakersfield | CA | 93304-1577 |  | 2013-07-18 | 2013-07-18 18:37 | 2013-07-18 18:37 | CARRIER - 38YCC0183450 | 70 | 0 | Yes | Yes | 18.5 | 20.7 | -2.2 | F3FD56E9BF8D487BB6E4F3604286DF84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 18:18 | 2013-07-22 18:18 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 20.2 | 19.9 | 0.3 | 4B7368A7C52246988293AE937AB0AEDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 18:01 | 2013-07-22 18:01 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 20 | 20.2 | -0.2 | 0B003D268416462FBDA299605A01B091 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 16:28 | 2013-07-23 16:28 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 22.3 | 19 | 3.3 | F03C071809FC40349B03D35842C66E68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5747 |  | 2013-07-19 | 2013-07-19 13:22 | 2013-07-19 13:44 | PAYNE - PA12NA036 | 100 | 4.1 | Yes | Yes | 17.2 | 18.8 | -1.6 | 40CBF8E4B53942AB8EC76C19696ABC0D |  | R22 | Non-TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | Non-TXV | 4.1%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 15:08 | 2013-07-22 15:26 | CARRIER - 38YCC018340 | 66 | 8.8 | Yes | Yes | 21.5 | 21.6 | -0.1 | 254B683AC0C940CE9045F5B6BC0E8188 |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
San Jose | CA | 95135-1333 |  | 2013-07-18 | 2013-07-18 09:48 | 2013-07-18 09:48 | GOODMAN - GSX130241BA | 85 | 0 | Yes | Yes | 21.8 | 17.7 | 4.1 | AE99C3F310D44CC7A003E19C27A17725 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4025 |  | 2013-06-26 | 2013-06-26 13:43 | 2013-06-26 13:43 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.9 | 19.9 | -1 | 2E31A600BC57438580CDF34B434A7C0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1074 |  | 2013-09-26 | 2013-09-26 10:32 | 2013-09-26 10:55 | WESTINGHOUSE - UKN | 90 | 4 | Yes | Yes | 20.7 | 20.4 | 0.3 | 9372F926337C417E871D7D6440507503 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Bakersfield | CA | 93306-3877 |  | 2013-08-15 | 2013-08-15 15:12 | 2013-08-15 15:12 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 22 | 22.1 | -0.1 | 350B0782D1CC4246B69B587F730039EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-24 | 2013-07-24 16:08 | 2013-07-24 16:08 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 22 | 21.4 | 0.6 | DF2FC420952F4B50A3804D814F861479 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6279 |  | 2013-07-23 | 2013-07-23 14:59 | 2013-07-23 14:59 | RUUD - 13AJA36A01757 | 90 | 0 | Yes | Yes | 21.6 | 20.8 | 0.8 | F0F57A6C24864DE297ECAC02C1B60414 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1301 |  | 2013-07-29 | 2013-07-29 13:44 | 2013-07-29 14:06 | GE - UKN | 85 | 10.4 | Yes | Yes | 18.8 | 18.7 | 0.1 | 47B1A4B2111146BDB71569BEA3CDD62D |  | R22 | Non-TXV |  | 12.24% | 0.87765 | 23.51% | [5 empty] | Non-TXV | 12.24%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 17:15 | 2013-07-23 17:15 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.9 | 20.8 | 1.1 | A771A4DB7B674EB0B429CE0D9623FAC7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-24 | 2013-07-24 16:39 | 2013-07-24 16:55 | CARRIER - 38YCC018340 | 66 | 8.7 | Yes | Yes | 20.8 | 20.6 | 0.2 | 830F5CDF4EBB48F086E9D08EA4F237B8 |  | R22 | Non-TXV |  | 13.18% | 0.86818 | 25.33% | [5 empty] | Non-TXV | 13.18%
Bakersfield | CA | 93304-1563 |  | 2013-07-18 | 2013-07-18 17:50 | 2013-07-18 17:50 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 20.2 | 20.2 | 0.1 | 7B237754D1FB4B8E9D632A6BB7FCBE46 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1563 |  | 2013-07-18 | 2013-07-18 17:31 | 2013-07-18 17:31 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.9 | 19.8 | 0.1 | F0B2E9C508054383AE40A3A2E7866995 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1574 |  | 2013-07-19 | 2013-07-19 15:03 | 2013-07-19 15:03 | CARRIER - 38YCC024340 | 70 | 0 | Yes | Yes | 19.6 | 20.9 | -1.3 | 7CD40267AFD2401C88978794B838F47C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1574 |  | 2013-07-19 | 2013-07-19 14:38 | 2013-07-19 14:38 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 24.7 | 19.9 | 4.8 | D9461AFC88C4476BB6F310EF55DEAD6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6001 |  | 2013-08-14 | 2013-08-14 18:45 | 2013-08-14 18:52 | RHEEM - RAKA-042-JAZ | 79 | 4.6 | Yes | Yes | 21.4 | 21.2 | 0.2 | 37283C6FA5B54D07A2C278E1182D4D77 |  | R22 | Non-TXV |  | 5.823% | 0.94177 | 11.19% | [5 empty] | Non-TXV | 5.823%
Bakersfield | CA | 93313-4198 |  | 2013-07-12 | 2013-07-12 19:30 | 2013-07-12 19:59 | RHEEM - RAMA-042JBZ | 95 | 3.6 | Yes | Yes | 20.5 | 23.1 | -2.6 | E6B8AB4EBD804FF38708515F13A402E6 |  | R22 | Non-TXV |  | 3.789% | 0.96211 | 7.283% | [5 empty] | Non-TXV | 3.789%
Bakersfield | CA | 93306-8408 |  | 2013-10-15 | 2013-10-15 12:48 | 2013-10-15 13:05 | RHEEM - 13AJA36A01 | 108 | 11.2 | Yes | Yes | 20.3 | 22.8 | -2.5 | 4CACDE1450614AD291CB2D71A68583CD |  | R22 | Non-TXV |  | 10.37% | 0.8963 | 19.93% | [5 empty] | Non-TXV | 10.37%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 16:15 | 2013-07-22 16:41 | CARRIER - 38YCC018340 | 66 | 6.9 | Yes | Yes | 21.5 | 20.4 | 1.1 | 004901301D5949B7B3F0A4C585789E9B |  | R22 | Non-TXV |  | 10.45% | 0.89545 | 20.09% | [5 empty] | Non-TXV | 10.45%
Bakersfield | CA | 93308-3465 |  | 2013-07-11 | 2013-07-11 18:13 | 2013-07-11 18:13 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.8 | 20.9 | -0.1 | A911EF9497524A9DA008D60696D76638 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-24 | 2013-07-24 17:05 | 2013-07-24 17:05 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 21.5 | 20.1 | 1.5 | B1482C487C6C469A95FB5F9D77BADD58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 14:42 | 2013-07-22 14:42 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 21.7 | 20.2 | 1.5 | 1153F0BBBD8542A9A9D39B7C0AA1EFE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 18:37 | 2013-10-04 18:39 | LENNOX - 13HPD-024-230-01 | 99 | 9.6 | Yes | Yes | 21.8 | 20.3 | 1.5 | 1BB6DE41A7E749A89C457096997D167A |  | R22 | TXV |  | 9.697% | 0.90303 | 18.64% | [5 empty] | TXV | 9.697%
Bakersfield | CA | 93307-4382 |  | 2013-07-25 | 2013-07-25 15:15 | 2013-07-25 15:15 | NORDYNE - JT5BD036K | 155 | 0 | Yes | Yes | 21.4 | 20.8 | 0.6 | B4C5C6616F1B48AD85BE129E04CC7534 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1578 |  | 2013-07-18 | 2013-07-18 15:39 | 2013-07-18 15:39 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.6 | 20.9 | -1.3 | 7B9FD16519D143DABCD02D4B1F52D9FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1562 |  | 2013-07-18 | 2013-07-18 14:28 | 2013-07-18 14:45 | CARRIER - 38YCC018340 | 66 | 9 | Yes | Yes | 17.8 | 20.7 | -2.9 | 5ED20DAE471149D2B7E8B2884CC0EFEB |  | R22 | Non-TXV |  | 13.64% | 0.86364 | 26.21% | [5 empty] | Non-TXV | 13.64%
Bakersfield | CA | 93304-1578 |  | 2013-07-18 | 2013-07-18 16:04 | 2013-07-18 16:21 | CARRIER - 38YCC18340 | 66 | 6.5 | Yes | Yes | 17.6 | 20.4 | -2.8 | A30A839BF73C49829A5894488AC62608 |  | R22 | Non-TXV |  | 9.848% | 0.90152 | 18.93% | [5 empty] | Non-TXV | 9.848%
Bakersfield | CA | 93304-1562 |  | 2013-07-18 | 2013-07-18 13:47 | 2013-07-18 13:47 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 18.7 | 21.4 | -2.7 | D35B939E77E0434882A58F459ACF8614 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1562 |  | 2013-07-18 | 2013-07-18 13:22 | 2013-07-18 13:22 | CARRIER - 384CC018340 | 66 | 0 | Yes | Yes | 19.2 | 19.9 | -0.7 | E84AEA3BDD01479C9B79EC718EE13992 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1566 |  | 2013-07-18 | 2013-07-18 16:49 | 2013-07-18 17:07 | CARRIER - 38YCC018340 | 66 | 9.4 | Yes | Yes | 18.7 | 21.7 | -3 | 07F49000A53E4BA08E6A7AFCD2085E75 |  | R22 | Non-TXV |  | 14.24% | 0.85758 | 27.37% | [5 empty] | Non-TXV | 14.24%
Bakersfield | CA | 93304-1574 |  | 2013-07-19 | 2013-07-19 12:58 | 2013-07-19 13:26 | CARRIER - 38YCC018340 | 66 | 10.5 | Yes | Yes | 17.1 | 20.1 | -3 | BFCFA168F36E44C2858EF24DC5F48D63 |  | R22 | Non-TXV |  | 15.91% | 0.84091 | 30.57% | [5 empty] | Non-TXV | 15.91%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 17:01 | 2013-07-22 17:01 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 20.3 | 19.8 | 0.5 | AFF1E2E7F0FA432CAEF59BA967E2B124 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 15:47 | 2013-07-22 15:47 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.5 | 19.3 | 0.2 | 379DCB991C994AF88E1C2F9C775B2D2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Redding | CA | 96001-9714 |  | 2013-07-17 | 2013-07-17 14:07 | 2013-07-17 14:24 | RHEEM - RRKA A042JK08 | 120 | 10.5 | Yes | Yes | 18.6 | 20.4 | -1.8 | 562BB05F8897477C895098F5505B0D4B |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
San Jose | CA | 95132-2013 |  | 2013-09-26 | 2013-09-26 15:56 | 2013-09-26 16:17 | PAYNE - PA13NR042-C | 191 | 7 | Yes | Yes | 25.8 | 21.3 | 4.5 | 6784830048CA453E959577749731173D |  | R22 | TXV |  | 3.665% | 0.96335 | 7.043% | [5 empty] | TXV | 3.665%
Bakersfield | CA | 93309-2944 |  | 2013-07-07 | 2013-07-07 22:20 | 2013-07-07 22:46 | CARRIER - N/A | 85 | 0 | Yes | Yes | 23.9 | 21.2 | 2.7 | 1D5E0F73F858481E9651557339212D6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Molinos | CA | 96055-9740 |  | 2013-09-08 | 2013-09-08 09:44 | 2013-09-08 10:40 | COMFORT AIRE - HBCG0361B8 | 81 | 10.2 | Yes | Yes | 24.1 | 21 | 3.1 | 0CA3B74C9C72405ABA117ABC9BC2D520 |  | R22 | Non-TXV |  | 12.59% | 0.87407 | 24.2% | [5 empty] | Non-TXV | 12.59%
Bakersfield | CA | 93306-8375 |  | 2013-07-24 | 2013-07-24 16:06 | 2013-07-24 16:06 | WEATHER KING - 13JA36A01 | 108 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | F8AF8EB7AB5842B887E4EEE46CEE661F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-8905 |  | 2013-07-14 | 2013-07-14 09:36 | 2013-07-14 10:04 | RHEEM - RRNL-B042JK08E | 112 | 4.5 | Yes | Yes | 24.1 | 21.4 | 2.7 | B4B208F8A8EE43659D3E7285637C8047 |  | R410A | Non-TXV |  | 4.018% | 0.95982 | 7.721% | [5 empty] | Non-TXV | 4.018%
Lamont | CA | 93241-2771 |  | 2013-09-13 | 2013-09-13 18:24 | 2013-09-13 18:30 | PAYNE - 2AC13B24P-2B | 89 | -4.3 | Yes | Yes | 23.3 | 20.4 | 2.9 | 9FB3F44EF7BB4F73993ED6D1BAF70D4B |  | R22 | Non-TXV |  | -4.831% | 1.0483 | 1.353% |  |  |  |  | Non-TXV |  |  | -4.831%
Bakersfield | CA | 93311-9196 |  | 2013-07-09 | 2013-07-09 17:45 | 2013-07-09 18:04 | YORK - H4RC060S060 | 143 | 5.7 | Yes | Yes | 19 | 19.3 | -0.3 | 1CEE55C23A2645FCABEAAC590F83E942 |  | R22 | Non-TXV |  | 3.986% | 0.96014 | 7.66% | [5 empty] | Non-TXV | 3.986%
San Jose | CA | 95124-2529 |  | 2013-10-10 | 2013-10-10 11:42 | 2013-10-10 12:31 | PAYNE - PA13NA024-B | 61 | -7.6 | Yes | Yes | 25.9 | 20.3 | 5.6 | 0FD798ABA09143E196CB639E72D980A2 |  | R410A | TXV |  | -12.46% | 1.1246 | 3.489% |  |  |  |  | TXV |  |  | -12.46%
Suisun City | CA | 94585-2049 |  | 2013-10-15 | 2013-10-15 12:24 | 2013-10-15 13:40 | CARRIER - 38CKC036340 | 74 | -3.2 | Yes | Yes | 14.6 | 17.5 | -2.9 | F98B718DD79B4AA6B52C5811BC597D7E |  | R22 | Non-TXV |  | -4.324% | 1.0432 | 1.211% |  |  |  |  | Non-TXV |  |  | -4.324%
Bakersfield | CA | 93314-3703 |  | 2013-07-23 | 2013-07-23 09:03 | 2013-07-23 09:36 | OTHER - JS4BD042KB | 85 | 5.5 | Yes | Yes | 25.5 | 20.2 | 5.4 | 713E90BA56B145D9B96EEDAC68B22019 |  | R410A | TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | TXV | 6.471%
Santa Rosa | CA | 95407-4211 |  | 2013-07-10 | 2013-07-10 11:18 | 2013-07-10 12:10 | NORDYNE - JS3BC-048KA | 85 | 11.7 | Yes | Yes | 20.6 | 18.7 | 1.9 | 8F1889130A214EE8912D3A1DFF7A18A1 |  | R22 | Non-TXV |  | 13.76% | 0.86235 | 26.45% | [5 empty] | Non-TXV | 13.76%
Fairfield | CA | 94533-2451 |  | 2013-09-24 | 2013-09-24 09:30 | 2013-09-24 15:39 | BDP - 567024RCU | 60 | 3.8 | Yes | Yes | 17.1 | 14.4 | 2.7 | 596AF5B4D8A341E8845DD4924AECAAC0 |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
San Jose | CA | 95111-1517 |  | 2013-09-18 | 2013-09-18 16:22 | 2013-09-18 16:47 | NORDYNE - FS3BA036KA | 71 | 6.7 | Yes | Yes | 19.6 | 20.4 | -0.8 | E4651BD4F73740E7B2030365DEDB8C3D |  | R22 | Non-TXV |  | 9.437% | 0.90563 | 18.14% | [5 empty] | Non-TXV | 9.437%
San Jose | CA | 95111-1586 |  | 2013-07-18 | 2013-07-18 09:43 | 2013-07-18 09:43 | CARRIER - 561CJ060-A | 150 | 0 | Yes | Yes | 15.7 | 18.6 | -2.9 | 4D0394A00425456CB3303276FC56D79C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95407-2535 |  | 2013-07-05 | 2013-07-05 09:29 | 2013-07-05 09:29 | GMC - CKL-36-1D | 72 | 0 | Yes | Yes | 18.3 | 19.4 | -1.1 | 52D1C0EB035844639AC134CA0AE1B9BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5822 |  | 2013-06-26 | 2013-06-26 13:10 | 2013-06-26 13:47 | CARRIER - 585CJ024050 | 72 | 0 | Yes | Yes | 18.3 | 18.7 | -0.4 | 7352E81999CC422B9C4FC68400992ED6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-2853 |  | 2013-09-17 | 2013-09-17 15:42 | 2013-09-17 16:40 | AMANA - ARCF30U01D | 61 | 9.5 | Yes | Yes | 22.5 | 18.7 | 3.9 | C936D45BAEC0485689996F06C4A12589 |  | R22 | Non-TXV |  | 15.57% | 0.84426 | 29.93% | [5 empty] | Non-TXV | 15.57%
San Jose | CA | 95135-1301 |  | 2013-10-19 | 2013-10-19 10:11 | 2013-10-19 10:45 | BRYANT - PA10JA024-C | 64 | -6 | Yes | Yes | 23.2 | 18.2 | 5 | F6AC92797BC7401ABC38B07AECDF144B |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
San Rafael | CA | 94903-2206 |  | 2013-07-05 | 2013-07-05 10:34 | 2013-07-05 10:35 | BRYANT - 113RNA024-F | 60 | -4.2 | Yes | Yes | 16.9 | 16.8 | 0.1 | 510BB9F2CD944E7383EBF6E54AF4764D |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
San Jose | CA | 95111-3921 |  | 2013-10-08 | 2013-10-08 08:32 | 2013-10-08 09:19 | YORK - TCGD42S21S1A | 72 | -5.1 | Yes | Yes | 24 | 19.9 | 4.1 | 525F690C3670438BB4093F3E2D8A4618 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Santa Rosa | CA | 95407-4577 |  | 2013-10-07 | 2013-10-07 11:26 | 2013-10-08 00:12 | YORK - H2RA036S06E | 63 | 10.2 | Yes | Yes | 19.8 | 17.5 | 2.3 | DAB540B4D41D45DA8D531A59912CC4CD |  | R22 | Non-TXV |  | 16.19% | 0.8381 | 31.11% | [5 empty] | Non-TXV | 16.19%
Bakersfield | CA | 93304-6604 |  | 2013-07-10 | 2013-07-10 19:29 | 2013-07-10 19:29 | PAYNE - PA12NA042-B | 101 | 0 | Yes | Yes | 21.2 | 20.7 | 0.5 | 7C2250CB4521465FA80AEA146BE72CE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2065 |  | 2013-09-09 | 2013-09-09 10:46 | 2013-09-09 11:09 | GOODMAN - CPLE36 | 103 | 3.5 | Yes | Yes | 23.2 | 20.1 | 3.1 | 121F689D74E64C4B906725DD65CA6CB0 |  | R22 | Non-TXV |  | 3.398% | 0.96602 | 6.53% | [5 empty] | Non-TXV | 3.398%
Arvin | CA | 93203-2061 |  | 2013-08-19 | 2013-08-19 16:58 | 2013-08-19 17:00 | GOODMAN - CPLE36-1 | 103 | 4.9 | Yes | Yes | 21.7 | 20.9 | 0.8 | F6D018F0438E4248ADA33A2B6D23C898 |  | R22 | Non-TXV |  | 4.757% | 0.95243 | 9.142% | [5 empty] | Non-TXV | 4.757%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 17:23 | 2013-07-22 17:23 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.6 | 21 | -1.4 | 20C740A958EB45E6AFFA75DE35E6CE21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2060 |  | 2013-08-19 | 2013-08-19 13:23 | 2013-08-19 13:41 | GOODMAN - CPLE36 1A | 110 | 3.6 | Yes | Yes | 20.2 | 20.1 | 0.1 | 5673E1C52AB140D6A26F2B094A55B767 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Bakersfield | CA | 93304-1488 |  | 2013-07-24 | 2013-07-24 18:19 | 2013-07-24 18:19 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.4 | 21.1 | -1.7 | 13265E683E7142E38DA495E74743E3AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1328 |  | 2013-10-22 | 2013-10-22 15:31 | 2013-10-22 18:22 | TRANE - 2TTR024A1000AA | 80 | 3.1 | Yes | Yes | 20.8 | 21 | -0.2 | 5D58E4A2807C4C02A7733326BDF7BB80 |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Bakersfield | CA | 93304-1488 |  | 2013-07-24 | 2013-07-24 16:22 | 2013-07-24 16:22 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.2 | 20.9 | -1.7 | 1E4000DD0C6145BC87B82FEB4F582460 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-2410 |  | 2013-07-18 | 2013-07-18 12:36 | 2013-07-18 12:36 | DAY & NIGHT - N4A336AKB200 | 114 | 0 | Yes | Yes | 21.7 | 16.6 | 5.1 | 31F2254B6C79434B9D0E9503208CC42D |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95126-4304 |  | 2013-10-19 | 2013-10-19 12:40 | 2013-10-19 13:20 | BRYANT - 567A024 | 81 | 23.4 | Yes | Yes | 26.5 | 21.5 | 5 | 9A0F87B840C845189CDDB444CAB6BFFF |  | R22 | Non-TXV |  | 28.89% | 0.71111 | 55.52% | [5 empty] | Non-TXV | 28.89%
Bakersfield | CA | 93307-6517 |  | 2013-07-30 | 2013-07-30 09:17 | 2013-07-30 09:17 | GOODMAN - UKN | 90 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 32B93A0541F0403180E42438DAB49DA4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2061 |  | 2013-08-19 | 2013-08-19 17:03 | 2013-08-19 17:04 | GOODMAN - CPLE36-1A | 110 | 4.9 | Yes | Yes | 22.3 | 21.5 | 0.8 | 4A441889F1114B58949B0016BDB42F27 |  | R22 | Non-TXV |  | 4.455% | 0.95545 | 8.561% | [5 empty] | Non-TXV | 4.455%
San Jose | CA | 95125-3957 |  | 2013-10-16 | 2013-10-16 09:08 | 2013-10-16 09:40 | YORK - H5DB048S06A | 127 | 7.4 | Yes | Yes | 24.9 | 20.4 | 4.5 | 0C434600FC5043FF944AA31B335CF87F |  | R22 | Non-TXV |  | 5.827% | 0.94173 | 11.2% | [5 empty] | Non-TXV | 5.827%
Arvin | CA | 93203-2062 |  | 2013-08-19 | 2013-08-19 17:41 | 2013-08-19 17:42 | GOODMAN - CPLE42-1B | 128 | 10.2 | Yes | Yes | 24 | 23.1 | 0.9 | 0FE3C0F90B924999B655E0C7C0E1ED7D |  | R22 | Non-TXV |  | 7.969% | 0.92031 | 15.31% | [5 empty] | Non-TXV | 7.969%
Bakersfield | CA | 93307-5667 |  | 2013-07-30 | 2013-07-30 08:38 | 2013-07-30 08:38 | YORK - D3NZ030N0560NXA | 64 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | 13078955755B49719ACAF3364717EDF3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2064 |  | 2013-08-21 | 2013-08-21 11:50 | 2013-08-21 12:42 | GOODMAN - CPLE36 1A | 102 | 3.1 | Yes | Yes | 22.2 | 21.1 | 1.1 | 9334511720944DAF95EFA3E179E847A3 |  | R22 | Non-TXV |  | 3.039% | 0.69 | 59.58% | [5 empty] | Non-TXV | 3.039%
Bakersfield | CA | 93301-2634 |  | 2013-09-25 | 2013-09-25 15:35 | 2013-09-25 15:58 | GOODMAN - GPG1330045M41AB | 85 | 8.2 | Yes | Yes | 17.2 | 19.4 | -2.2 | 194DA57FE68E4FEAB67D9CAD06E41DCD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Lamont | CA | 93241-2774 |  | 2013-09-13 | 2013-09-13 18:03 | 2013-09-13 18:05 | GOODMAN - GSC130301EB | 66 | 4 | Yes | Yes | 22.8 | 20.7 | 2.1 | 69EC95F7F00C42F6B80C65F953096892 |  | R22 | TXV |  | 6.061% | 0.93939 | 11.65% | [5 empty] | TXV | 6.061%
Lamont | CA | 93241-2725 |  | 2013-09-12 | 2013-09-12 12:08 | 2013-09-12 13:51 | DUCANE - 2AC13830P 2B | 97 | 3.1 | Yes | Yes | 19.7 | 20.1 | -0.4 | E4AF0E0B3C504088921FE2365EC0625D |  | R22 | Non-TXV |  | 3.196% | 0.96804 | 6.142% | [5 empty] | Non-TXV | 3.196%
Cottonwood | CA | 96022-9421 |  | 2013-06-27 | 2013-06-27 10:34 | 2013-06-27 11:00 | WESTINGHOUSE - UNK | 67 | 3.5 | Yes | Yes | 20.1 | 19.8 | 0.3 | 3DBE056FB84A4C37ADEAC466E7A0A778 |  | R22 | Non-TXV |  | 5.224% | 0.94776 | 10.04% | [5 empty] | Non-TXV | 5.224%
Redding | CA | 96002-9746 |  | 2013-07-17 | 2013-07-17 14:44 | 2013-07-17 15:07 | DAY & NIGHT - UNK | 168 | 9.2 | Yes | Yes | 22.4 | 20.3 | 2.2 | 82A2840119A94F89AC49BCAE7E2C85F2 |  | R22 | Non-TXV |  | 5.476% | 0.94524 | 10.52% | [5 empty] | Non-TXV | 5.476%
Anderson | CA | 96007-9203 |  | 2013-09-04 | 2013-09-04 13:13 | 2013-09-04 14:09 | YORK - D1NA036N05606C | 67 | 4.6 | Yes | Yes | 21.8 | 21.3 | 0.5 | D271C51755704ED9AB920B3BCBDC6B96 |  | R22 | Non-TXV |  | 6.866% | 0.93134 | 13.19% | [5 empty] | Non-TXV | 6.866%
Anderson | CA | 96007-3026 |  | 2013-07-08 | 2013-07-08 09:18 | 2013-07-08 09:44 | TRANE - 2TTB2030A1000AA | 68 | 2.8 | Yes | Yes | 19.5 | 18.8 | 0.7 | 4E8FD88D5D2A4130A99E5E3F5F483879 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Anderson | CA | 96007-8316 |  | 2013-07-11 | 2013-07-11 11:39 | 2013-07-11 12:41 | ARMSTRONG - 2SCU13LB125P-1 | 72 | 5.2 | Yes | Yes | 24.9 | 21 | 3.9 | DFE7105EE00446A5A2DE2140B0FC2508 |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Pleasanton | CA | 94566-5339 |  | 2013-09-13 | 2013-09-13 13:08 | 2013-09-13 13:08 | CARRIER - 24ACR348A300 | 169 | 0 | Yes | Yes | 20.3 | 17.2 | 3.1 | 51BE5700AA0A412A925D82CE59615B1A |  | R22 | TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2067 |  | 2013-08-19 | 2013-08-19 11:19 | 2013-08-19 13:22 | GOODMAN - CPLE42 1B | 128 | 4.2 | Yes | Yes | 21.7 | 19.8 | 1.9 | AC58EE728712476EAA731D1988471FD1 |  | R22 | Non-TXV |  | 3.281% | 0.96719 | 6.306% | [5 empty] | Non-TXV | 3.281%
Arvin | CA | 93203-2058 |  | 2013-08-19 | 2013-08-19 17:21 | 2013-08-19 17:22 | GOODMAN - CPLE42-1B | 128 | 7.1 | Yes | Yes | 24.1 | 22.1 | 2 | 68EEC86CB2B647C0A84E0861BD93C069 |  | R22 | Non-TXV |  | 5.547% | 0.94453 | 10.66% | [5 empty] | Non-TXV | 5.547%
Arvin | CA | 93203-2063 |  | 2013-09-09 | 2013-09-09 11:11 | 2013-09-09 11:29 | GOODMAN - CPLE42 1B | 122 | 3.9 | Yes | Yes | 21.2 | 20.1 | 1.1 | 8BD1EDFA4A6643CFA33C70D191DCCB7C |  | R22 | Non-TXV |  | 3.197% | 0.96803 | 6.143% | [5 empty] | Non-TXV | 3.197%
Woodland | CA | 95695-2574 |  | 2013-09-26 | 2013-09-26 12:34 | 2013-09-26 13:01 | GOODMAN - GSH130241BA | 85 | 7.6 | Yes | Yes | 21.7 | 16.8 | 4.9 | 9765250DE30E4E9984C17B3979C753F7 |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Bakersfield | CA | 93313-5747 |  | 2013-08-14 | 2013-08-14 19:12 | 2013-08-14 19:15 | PAYNE - PA12NA036000ABAA | 100 | 13.5 | Yes | Yes | 23.2 | 22 | 1.2 | 1E37F23FA2B045A19B0D9BE93BF581D3 |  | R22 | Non-TXV |  | 13.5% | 0.865 | 25.94% | [5 empty] | Non-TXV | 13.5%
Woodland | CA | 95695-2581 |  | 2013-07-26 | 2013-07-26 14:40 | 2013-07-26 14:40 | GOODMAN - GSH130241CA | 122 | 10 | Yes | Yes | 16.1 | 17.9 | -1.8 | A2A5D5190CDB4E0AB0DBDD759A42D8F5 | Add refrigerant: 10 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.197% | 0.91803 | 15.75% | [5 empty] | Non-TXV | 8.197%
Bakersfield | CA | 93313-5240 |  | 2013-07-16 | 2013-07-16 15:01 | 2013-07-16 15:36 | HEIL - PA12NA036CH | 85 | 4.1 | Yes | Yes | 19.5 | 20 | -0.4 | B59FFF29FCC444A1B1AB3757D6196A03 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
San Jose | CA | 95111-2645 |  | 2013-07-18 | 2013-07-18 11:03 | 2013-07-18 11:03 | BRYANT - 538ANX036000B | 84 | 0 | Yes | Yes | 19.5 | 17.5 | 2 | 2D8AA076ECBF4828B9B2EB380169010B |  | R22 | TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2798 |  | 2013-07-24 | 2013-07-24 08:32 | 2013-07-24 08:51 | GOODMAN - GPG1324045AAA | 77 | 8.7 | Yes | Yes | 26.2 | 21 | 5.2 | 03F483749F794B12BD05D8746C43F37F |  | R22 | Non-TXV |  | 11.3% | 0.88701 | 21.71% | [5 empty] | Non-TXV | 11.3%
Arvin | CA | 93203-2798 |  | 2013-07-24 | 2013-07-24 08:53 | 2013-07-24 09:23 | GOODMAN - GPG1324045AAA | 77 | 6.4 | Yes | Yes | 27.5 | 22 | 5.5 | 628750BD4D264DB28416AE78E9046F31 |  | R22 | Non-TXV |  | 8.312% | 0.91688 | 15.97% | [5 empty] | Non-TXV | 8.312%
Bakersfield | CA | 93304-1576 |  | 2013-07-19 | 2013-07-19 16:18 | 2013-07-19 16:18 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 21.2 | 20.7 | 0.6 | DBC0FF3DB8B245EDB7A64AD305D0A0B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-22 | 2013-07-22 17:40 | 2013-07-22 17:40 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | D407DA0C38DC4E81A39E1D7EAD6D4191 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1315 |  | 2013-09-23 | 2013-09-23 15:53 | 2013-09-23 16:23 | CARRIER - 24ABA336A300 | 72 | 7.2 | Yes | Yes | 20.3 | 19.4 | 0.9 | D165C49775B04554BF9DFE855E2C1EDD |  | R410A | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93304-1556 |  | 2013-07-18 | 2013-07-18 19:46 | 2013-07-18 19:46 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | E5E807B64D53435BB397650B932A3D68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1560 |  | 2013-07-19 | 2013-07-19 11:53 | 2013-07-19 11:53 | PAYNE - PH13NR0818-H | 85 | 0 | Yes | Yes | 21.2 | 20.9 | 0.3 | 4D0DEDE63158411EA3437ABE0A0A270C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1558 |  | 2013-07-18 | 2013-07-18 17:15 | 2013-07-18 17:15 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | D54CE09444924F1F9765C19FF1866A7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5239 |  | 2013-07-23 | 2013-07-23 15:15 | 2013-07-23 15:15 | PAYNE - PA12NAO36000AHAA | 100 | 0 | Yes | Yes | 18.9 | 20.4 | -1.5 | B2F7FF90F9D647B6825F2F8E2D1D15EC |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-8123 |  | 2013-07-10 | 2013-07-10 11:20 | 2013-07-10 11:38 | PAYNE - 591ANX024000AAAA | 51 | -4.8 | Yes | Yes | 16.5 | 18 | -1.5 | CD3029364D114A15B75B303A82D3F0F3 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Arvin | CA | 93203-2063 |  | 2013-08-19 | 2013-08-19 17:07 | 2013-08-19 17:09 | GOODMAN - CPLE42-1B | 128 | 8 | Yes | Yes | 22.2 | 22.1 | 0.1 | 1DF06FB753854390B9F4400F47F726F5 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Bakersfield | CA | 93307-3976 |  | 2013-07-25 | 2013-07-25 09:42 | 2013-07-25 10:08 | OTHER - 2AC13B30P-1A | 129 | 22.6 | Yes | Yes | 21.7 | 22.4 | -0.6 | 78F10444842A48C4BB67A0817BAE33C5 |  | R22 | Non-TXV |  | 17.52% | 0.82481 | 33.67% | [5 empty] | Non-TXV | 17.52%
Bakersfield | CA | 93306-8362 |  | 2013-10-15 | 2013-10-15 17:19 | 2013-10-15 17:19 | ICP - N4A336AKB200 | 83 | 0 | Yes | Yes | 21.2 | 22.4 | -1.2 | 07131DAAAE604459B7B25E9361CB2C5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2842 |  | 2013-08-20 | 2013-08-20 10:27 | 2013-08-20 10:58 | GOODMAN - GPG1330045M41AC | 80 | 6.3 | Yes | Yes | 20.8 | 20.2 | 0.6 | 56AC187632B6462BA033533370B2C8AC |  | R22 | Non-TXV |  | 7.875% | 0.92125 | 15.13% | [5 empty] | Non-TXV | 7.875%
San Jose | CA | 95135-1326 |  | 2013-07-23 | 2013-07-23 10:42 | 2013-07-23 10:42 | TRANE - 2TTR2024A10000AA | 80 | 0 | Yes | Yes | 17.8 | 20.4 | -2.6 | E67122B25A424C41A8F7FA63931DAD28 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1556 |  | 2013-07-18 | 2013-07-18 13:26 | 2013-07-18 13:26 | - 38YCC018340 | 68 | 0 | Yes | Yes | 21.5 | 21.4 | 0.1 | A0EE933545444A04A3E106290A417DAE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1557 |  | 2013-07-18 | 2013-07-18 14:31 | 2013-07-18 14:53 | CARRIER - 38YCC018340 | 68 | 10.9 | Yes | Yes | 21.1 | 21.5 | -0.4 | FCCCECAD4DEF48568871624C60F1A39D |  | R22 | Non-TXV |  | 16.03% | 0.83971 | 30.81% | [5 empty] | Non-TXV | 16.03%
San Jose | CA | 95116-3747 |  | 2013-07-18 | 2013-07-18 14:26 | 2013-07-18 15:15 | RUUD - UKN | 79 | -6.5 | Yes | Yes | 23.9 | 21.9 | 2 | 2C1C76E79DDC459588BD95A9C8365C4B |  | R22 | Non-TXV |  | -8.228% | 1.0823 | 2.304% |  |  |  |  | Non-TXV |  |  | -8.228%
Winters | CA | 95694-1711 |  | 2013-08-16 | 2013-08-16 11:35 | 2013-08-16 15:55 | GIBSON - JS5BD-048K | 147 | -6.6 | Yes | Yes | 20.2 | 20.7 | -0.5 | A223FDD04BC14401BACBEA7F5263EE2D |  | R22 | Non-TXV |  | -4.49% | 1.0449 | 1.257% |  |  |  |  | Non-TXV |  |  | -4.49%
Bakersfield | CA | 93306-6260 |  | 2013-07-23 | 2013-07-23 14:16 | 2013-07-23 14:16 | DUCANE - SG10B30050 | 62 | 0 | Yes | Yes | 21.8 | 21.2 | 0.6 | 96CF00DE3D1A48B2BE61F77034F1DEEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-2149 |  | 2013-08-06 | 2013-08-06 10:11 | 2013-08-06 10:39 | YORK - H2R0324S06A | 85 | 5.5 | Yes | Yes | 16.1 | 17.7 | -1.6 | F749F51E2D884F68AD2F69CD62ECAB6D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Woodland | CA | 95695-2870 |  | 2013-09-27 | 2013-09-27 09:36 | 2013-09-27 09:36 | BRYANT - 537GN036-A | 210 | 0 | Yes | Yes | 23.2 | 17.6 | 5.6 | 7E78A1C8D38E440C8ECA9259565F2407 |  | R410A | TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6939 |  | 2013-08-28 | 2013-08-28 11:51 | 2013-08-28 11:52 | GOODMAN - CPLE24-1C | 110 | 5.7 | Yes | Yes | 17.6 | 17.6 | 0 | 853152BEB8F146E5A6FEF0C8EF836853 |  | R22 | Non-TXV |  | 5.182% | 0.94818 | 9.958% | [5 empty] | Non-TXV | 5.182%
Benicia | CA | 94510-2007 |  | 2013-09-10 | 2013-09-10 12:53 | 2013-09-10 13:35 | TRANE - TTB042C100A1 | 96 | 3.3 | Yes | Yes | 13.5 | 16.5 | -3 | 0A35123DC2CC4D5DAC1FEA392EA23357 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Bakersfield | CA | 93312-6216 |  | 2013-10-16 | 2013-10-16 15:05 | 2013-10-16 15:05 | RHEEM - FAFF043JAZ | 99 | 0 | Yes | Yes | 19.8 | 22.8 | -3 | 5D838521A8204608A8A05ECE4852A107 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5568 |  | 2013-07-08 | 2013-07-08 16:55 | 2013-07-08 17:14 | TEMPSTAR - | 85 | 6.2 | Yes | Yes | 20.3 | 21.3 | -1 | F28D16E18E3D42008BDA5394A50112C4 | Add refrigerant: 9.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Willits | CA | 95490-3931 |  | 2013-08-21 | 2013-08-21 17:19 | 2013-08-21 17:50 | RUUD - ILLEGIBLE | 89 | 13.9 | Yes | Yes | 27.2 | 21.5 | 5.7 | 7F3D67D83B1F4E598608CC01016DC6C3 |  | R22 | Non-TXV |  | 15.62% | 0.84382 | 30.01% | [5 empty] | Non-TXV | 15.62%
Bakersfield | CA | 93311-9111 |  | 2013-07-09 | 2013-07-09 19:51 | 2013-07-09 21:10 | CARRIER - 38CKC036350 | 85 | 2.7 | Yes | Yes | 15.4 | 18 | -2.6 | E61C9F63E15E48E0AE65EF62AF693C85 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93311-9111 |  | 2013-07-09 | 2013-07-09 21:16 | 2013-07-09 22:21 | CARRIER - 38CKC036350 | 85 | 2.5 | Yes | Yes | 16.1 | 18.8 | -2.7 | 890560497C3E47A6AA30FD377588EF91 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
San Jose | CA | 95111-1603 |  | 2013-10-08 | 2013-10-08 09:45 | 2013-10-08 10:37 | TAPPAN - GM-48-14-0 | 95 | 19.9 | Yes | Yes | 24.7 | 20.4 | 4.3 | 9141505C2D4745698665BFD75592138B |  | R22 | Non-TXV |  | 20.95% | 0.79053 | 40.26% | [5 empty] | Non-TXV | 20.95%
Oakley | CA | 94561-2818 |  | 2013-10-03 | 2013-10-03 11:25 | 2013-10-03 11:25 | RHEEM - NA | 76 | 0 | Yes | Yes | 17.9 | 17.6 | 0.3 | 42BE3126ACD34663838409612E3F7683 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8345 |  | 2013-07-26 | 2013-07-26 15:39 | 2013-07-26 16:01 | YORK - DBYP-F042N080A | 150 | 25.2 | Yes | Yes | 21.9 | 21.5 | 0.4 | CF3F3B09B53E4F9C8F35C227D89E5519 |  | R22 | Non-TXV |  | 16.8% | 0.832 | 32.29% | [5 empty] | Non-TXV | 16.8%
Woodland | CA | 95695-2993 |  | 2013-08-01 | 2013-08-01 11:20 | 2013-08-01 11:23 | COMFORT AIRE - S8BA-018KA | 63 | 3.1 | Yes | Yes | 16.9 | 17.1 | -0.2 | 11F42D07A7E94A20A6088671B64B54BA |  | R22 | Non-TXV |  | 4.921% | 0.95079 | 9.456% | [5 empty] | Non-TXV | 4.921%
Bakersfield | CA | 93313-5754 |  | 2013-07-22 | 2013-07-22 12:26 | 2013-07-22 13:01 | CARRIER - 113KNA042 | 117 | 6 | Yes | Yes | 22.9 | 20.4 | 2.5 | F966BD76E4724DC8B7582B1A8EE2EB6D |  | R22 | Non-TXV |  | 5.128% | 0.94872 | 9.855% | [5 empty] | Non-TXV | 5.128%
Lamont | CA | 93241-2773 |  | 2013-09-13 | 2013-09-13 18:08 | 2013-09-13 18:10 | PAYNE - 2AC13B30P-2B | 40 | -1.9 | Yes | Yes | 25.9 | 21.5 | 4.4 | 547AB789CC8B47D3A6942B8FC327625F |  | R22 | TXV |  | -4.75% | 1.0475 | 1.33% |  |  |  |  | TXV |  |  | -4.75%
Bakersfield | CA | 93306-6043 |  | 2013-09-16 | 2013-09-16 15:40 | 2013-09-16 16:07 | PAYNE - PY1PNB042060AAAA | 100 | 11.8 | Yes | Yes | 22.4 | 21.2 | 1.2 | 8FD85272EF0B4A15A79F4323E34F0D70 |  | R22 | Non-TXV |  | 11.8% | 0.882 | 22.68% | [5 empty] | Non-TXV | 11.8%
Woodland | CA | 95695-2962 |  | 2013-08-01 | 2013-08-01 11:10 | 2013-08-01 11:10 | BDP - 567024RCU | 56 | 0 | Yes | Yes | 16.5 | 17.9 | -1.4 | 5F022CBD33304A6A94AFB8A8F3F56753 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2773 |  | 2013-09-13 | 2013-09-13 18:12 | 2013-09-13 18:14 | PAYNE - 2AC1B30P-2B | 97 | -4.9 | Yes | Yes | 22.2 | 20.4 | 1.8 | 2A2D87DB46274DA3BBE972EEDFFEB5CD |  | R22 | TXV |  | -5.052% | 1.0505 | 1.415% |  |  |  |  | TXV |  |  | -5.052%
Bakersfield | CA | 93304-1551 |  | 2013-07-19 | 2013-07-19 14:31 | 2013-07-19 14:31 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.9 | 20.2 | 1.7 | F7BF251DB4D1450993A6B43C3E0EBAD1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1569 |  | 2013-07-20 | 2013-07-20 10:58 | 2013-07-20 10:58 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.2 | 20.2 | 1 | F69016B7D96D436191D17ED83B6E794F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1551 |  | 2013-07-19 | 2013-07-19 16:33 | 2013-07-19 16:33 | CARRIER - 38YCC024340 | 71 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 1C687E0045664A33ACDA1A9FB485C48E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1561 |  | 2013-07-20 | 2013-07-20 15:07 | 2013-07-20 15:34 | CARRIER - 38YCC018340 | 68 | 11.4 | Yes | Yes | 21.4 | 21 | 0.4 | D4EAE11776FC4D7784F4BF01C0B6506B |  | R22 | Non-TXV |  | 16.76% | 0.83235 | 32.22% | [5 empty] | Non-TXV | 16.76%
Bakersfield | CA | 93304-1569 |  | 2013-07-20 | 2013-07-20 13:33 | 2013-07-20 13:33 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 22 | 21.4 | 0.6 | 4968B0877FFE45F2A5C6EA1834E9F130 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1569 |  | 2013-07-20 | 2013-07-20 11:23 | 2013-07-20 12:00 | CARRIER - 38YCC081340 | 68 | 10.6 | Yes | Yes | 22.3 | 21.8 | 0.5 | BE3289BCB2BC43E69191222A5C0EB324 |  | R22 | Non-TXV |  | 15.59% | 0.84412 | 29.96% | [5 empty] | Non-TXV | 15.59%
Bakersfield | CA | 93304-1561 |  | 2013-07-20 | 2013-07-20 19:18 | 2013-07-20 19:18 | CARRIER - 38YCC024340 | 68 | 0 | Yes | Yes | 21.8 | 20.2 | 1.6 | 1BAED46C8AA848928B89E0EE8532D5EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1561 |  | 2013-07-20 | 2013-07-20 17:24 | 2013-07-20 17:40 | CARRIER - 38YCC018340 | 68 | 11.4 | Yes | Yes | 21.7 | 21.5 | 0.2 | A1A78529CDE74BD9AC3DE61B5F040517 |  | R22 | Non-TXV |  | 16.76% | 0.83235 | 32.22% | [5 empty] | Non-TXV | 16.76%
Bakersfield | CA | 93313-5278 |  | 2013-07-23 | 2013-07-23 17:03 | 2013-07-23 18:04 | YORK - H2RD048S06B | 134 | 5.2 | Yes | Yes | 24.8 | 19.7 | 5.1 | 120BBDD114984A4D860B5A71D1DBF50A |  | R22 | TXV |  | 3.881% | 0.96119 | 7.458% | [5 empty] | TXV | 3.881%
San Jose | CA | 95123-1504 |  | 2013-07-18 | 2013-07-18 13:36 | 2013-07-18 13:36 | RHEEM - UKN | 85 | 0 | Yes | Yes | 17 | 17.4 | -0.4 | 3F8D5E50D88A4DB6A0EEBDDFE2565991 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1534 |  | 2013-07-19 | 2013-07-19 12:47 | 2013-07-19 12:47 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.5 | 21 | 0.5 | 59C1DA64693648008A491B2037D44A46 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1559 |  | 2013-07-18 | 2013-07-18 19:19 | 2013-07-18 19:19 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 21.7 | 21 | 0.8 | DFE9AC295E324B38B8C27BFD9A0B42FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1573 |  | 2013-07-19 | 2013-07-19 18:18 | 2013-07-19 18:18 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.9 | 21.4 | 0.5 | 596C07C2AB984F0DADA8559C5480EAFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1534 |  | 2013-07-19 | 2013-07-19 13:23 | 2013-07-19 13:23 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 22.4 | 20.8 | 1.6 | 4D9600BB0A144464B4854E5362BE2603 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4940 |  | 2013-09-27 | 2013-09-27 11:15 | 2013-09-27 11:15 | YORK - H1RA024S06D | 59 | 0 | Yes | Yes | 20.9 | 17.4 | 3.5 | 4BC1D7E4A37E4BC887144D285FE909A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1557 |  | 2013-07-18 | 2013-07-18 15:51 | 2013-07-18 15:51 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 82D09B24A40744FBB42C434E278B981E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1575 |  | 2013-07-19 | 2013-07-19 15:24 | 2013-07-19 15:24 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | ACFC17C735134CABADAC703AF816DD9F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1558 |  | 2013-07-18 | 2013-07-18 16:18 | 2013-07-18 16:36 | CARRIER - 38YCC018340 | 68 | 11.4 | Yes | Yes | 21.7 | 21 | 0.7 | D7C6831EC0FB4F0199C8D294CD100354 |  | R22 | Non-TXV |  | 16.76% | 0.83235 | 32.22% | [5 empty] | Non-TXV | 16.76%
Bakersfield | CA | 93304-1556 |  | 2013-07-18 | 2013-07-18 12:49 | 2013-07-18 12:49 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.5 | 23.1 | -1.6 | B5FAAF142FCB477083B56858E6A24666 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-0000 |  | 2013-08-01 | 2013-08-01 12:09 | 2013-08-01 12:10 | CARRIER - N4A336AKB200 | 83 | 4.4 | Yes | Yes | 15.9 | 15.7 | 0.2 | 2EDEDA43EAB54BDC9BAEC69E6C1D052C |  | R22 | Non-TXV |  | 5.301% | 0.94699 | 10.19% | [5 empty] | Non-TXV | 5.301%
Davis | CA | 95616-1842 |  | 2013-07-09 | 2013-07-09 13:39 | 2013-07-09 13:39 | CARRIER - 48GS-036090301 | 56 | 2.3 | Yes | Yes | 16.2 | 18.1 | -1.9 | D69D315304E542C99A2CA4392DCC560C | Add refrigerant: 2.3 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Bakersfield | CA | 93313-5748 |  | 2013-07-21 | 2013-07-21 15:06 | 2013-07-21 15:36 | PAYNE - PA12NA036-B | 100 | 5.4 | Yes | Yes | 22.9 | 21 | 1.9 | 9A24817F1EEF431CA4574D8CDAAE09F9 |  | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Vallejo | CA | 94589-1621 |  | 2013-07-10 | 2013-07-10 12:56 | 2013-07-10 12:56 | TRANE - TTR036C100AZ | 92 | 0 | Yes | Yes | 17 | 19.7 | -2.7 | 9567041332F548CCA2124D57FD14115F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-1447 |  | 2013-10-11 | 2013-10-11 11:16 | 2013-10-11 11:17 | CARRIER - 48GX-030040301AD | 68 | 2.9 | Yes | Yes | 14.7 | 15.5 | -0.8 | 7949C26CC83643DABD5484BA06C4A215 |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Arvin | CA | 93203-2059 |  | 2013-08-19 | 2013-08-19 17:33 | 2013-08-19 17:36 | GOODMAN - CPLE36-1A | 110 | 9.8 | Yes | Yes | 24.2 | 22.8 | 1.4 | 8736878574EF4CD89439B9FBB30C61DD |  | R22 | Non-TXV |  | 8.909% | 0.91091 | 17.12% | [5 empty] | Non-TXV | 8.909%
Bakersfield | CA | 93309-5116 |  | 2013-08-14 | 2013-08-14 12:53 | 2013-08-14 13:32 | ICP - PGD336060K001C1 | 85 | 4.8 | Yes | Yes | 16.9 | 19.8 | -2.9 | 64EACCADE0EE42D0B0E2BF6EC2143497 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Bakersfield | CA | 93306-6926 |  | 2013-07-23 | 2013-07-23 16:22 | 2013-07-23 16:22 | BDP - 585CJ030050 | 78 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | D57EAE68BEC34C188F8AF85E025642D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-7003 |  | 2013-07-05 | 2013-07-05 09:06 | 2013-07-05 09:08 | RUUD - UAMC-030JAZ | 77 | 2.7 | Yes | Yes | 18.1 | 17.9 | 0.2 | F4ABCE68BDC749EAB83E671F524DE809 |  | R22 | Non-TXV |  | 3.506% | 0.96494 | 6.739% | [5 empty] | Non-TXV | 3.506%
Vallejo | CA | 94589-1903 |  | 2013-08-15 | 2013-08-15 15:08 | 2013-08-15 16:01 | PAYNE - PA10JA036-C | 77 | 6.7 | Yes | Yes | 14.4 | 14.4 | 0 | DB2D459B010F44439A6958BBE931A4D0 |  | R22 | Non-TXV |  | 8.701% | 0.91299 | 16.72% | [5 empty] | Non-TXV | 8.701%
Arvin | CA | 93203-2064 |  | 2013-08-19 | 2013-08-19 10:31 | 2013-08-19 10:47 | GOODMAN - CPLE361A | 110 | 4.4 | Yes | Yes | 21.3 | 20.2 | 1.1 | 0238ACDD5B334E88A8EE03F0D1F80EFC |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93313-3366 |  | 2013-07-25 | 2013-07-25 12:36 | 2013-07-25 13:01 | RHEEM - HC803021C | 80 | 4.5 | Yes | Yes | 23.9 | 19.3 | 4.6 | 731C020FBAE0498D86078E471CBB2B43 |  | R22 | TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | TXV | 5.625%
Arvin | CA | 93203-2061 |  | 2013-08-21 | 2013-08-21 17:10 | 2013-08-21 17:59 | GOODMAN - CPLE36 1A | 110 | 3.4 | Yes | Yes | 21.7 | 21 | 0.7 | A2A58AB5DCD045338D7AB4362AE7AB3E |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Fremont | CA | 94536-3810 |  | 2013-08-22 | 2013-08-22 11:02 | 2013-08-22 11:02 | OTHER - NCAFB30AB01 | 67 | 0 | Yes | Yes | 16.5 | 17.6 | -1.1 | FC9F18B371944C85BCD8600033596779 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-5010 |  | 2013-09-25 | 2013-09-25 16:24 | 2013-09-25 18:33 | GOODMAN - GSX130481BB | 125 | 12.2 | Yes | Yes | 24.6 | 20.4 | 4.2 | 6F62A352BE244FECBB301F5EDCFAF141 |  | R410A | TXV |  | 9.76% | 0.9024 | 18.76% | [5 empty] | TXV | 9.76%
Arvin | CA | 93203-2066 |  | 2013-08-19 | 2013-08-19 14:13 | 2013-08-19 14:37 | GOODMAN - CPLE36 1A | 108 | 4.7 | Yes | Yes | 21 | 20.1 | 0.9 | 91607C72D7094BDC9D56B2081F8ADFDB |  | R22 | Non-TXV |  | 4.352% | 0.95648 | 8.363% | [5 empty] | Non-TXV | 4.352%
Woodland | CA | 95695-2564 |  | 2013-09-27 | 2013-09-27 10:13 | 2013-09-27 10:13 | NORDYNE - JT5BU-024 | 85 | 0 | Yes | Yes | 21.3 | 17.7 | 3.6 | 68555EAE525C4AD39E83D8E2A699C67E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4060 |  | 2013-08-14 | 2013-08-14 11:27 | 2013-08-14 12:03 | GOODMAN - GPG1336045M41BA | 70 | 2.6 | Yes | Yes | 19.1 | 18.8 | 0.3 | 1EEF31D400D44A1BACE5C37CFA066691 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | Non-TXV | 3.714%
Bakersfield | CA | 93309-7611 |  | 2013-07-10 | 2013-07-10 13:24 | 2013-07-10 13:45 | DAY & NIGHT - DAYP-F036N079F | 108 | 3.5 | Yes | Yes | 20.1 | 19.8 | 0.3 | E613BEB22AF746A28DA43D44A301CD2B |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
San Jose | CA | 95111-3702 |  | 2013-07-23 | 2013-07-23 09:50 | 2013-07-23 10:26 | OTHER - GS3B1-036KA | 69 | -4.5 | Yes | Yes | 14.5 | 17.4 | -2.9 | 59A9DB45E75A4EDCBDEA42667C8FD3D7 |  | R22 | Non-TXV |  | -6.522% | 1.0652 | 1.826% |  |  |  |  | Non-TXV |  |  | -6.522%
Bakersfield | CA | 93308-1345 |  | 2013-07-10 | 2013-07-10 16:28 | 2013-07-10 16:47 | CARRIER - 38EH036360 | 137 | 23.7 | Yes | Yes | 22.1 | 20.9 | 1.2 | CA46EA587DCE414C988D016CB183BD96 |  | R22 | Non-TXV |  | 17.3% | 0.82701 | 33.25% | [5 empty] | Non-TXV | 17.3%
Bakersfield | CA | 93304-6061 |  | 2013-07-03 | 2013-07-03 17:36 | 2013-07-03 17:54 | OTHER - DBYP-F042N080A | 150 | 25 | Yes | Yes | 23 | 21.7 | 1.3 | E9CDA1670AAD4F48AD2CD36FE3ECC127 |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Winters | CA | 95694-1624 |  | 2013-10-08 | 2013-10-08 11:44 | 2013-10-08 11:44 | ICP - PGC042K080 | 84 | 0 | Yes | Yes | 17.4 | 17.5 | -0.1 | 7F6CC1A7B0EA46B6885E3A64272FA320 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-2429 |  | 2013-08-07 | 2013-08-07 09:18 | 2013-08-07 09:18 | TRANE - TTR036D100A0 | 79 | 0 | Yes | Yes | 19.9 | 17.7 | 2.2 | E2EF955658E94BA89C9D56121501B836 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5761 |  | 2013-07-03 | 2013-07-03 15:15 | 2013-07-03 15:15 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 19.1 | 19.5 | -0.4 | A04CBCF914184FF2A66D3842D7CDA246 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-2634 |  | 2013-09-25 | 2013-09-25 14:53 | 2013-09-25 15:10 | GOODMAN - GPG13300451AB | 85 | 5.5 | Yes | Yes | 19.7 | 22.6 | -2.8 | 05FE92B3A34A4DD696F73A97E43B521A |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Bakersfield | CA | 93306-6042 |  | 2013-08-16 | 2013-08-16 09:40 | 2013-08-16 09:40 | RHEEM - UKB | 90 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 471A1595CB7F48AEACA300A9A8535411 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6620 |  | 2013-08-18 | 2013-08-18 10:30 | 2013-08-18 10:50 | ICP - R2A36GKR2 | 84 | 11.8 | Yes | Yes | 20.2 | 21.5 | -1.3 | 839F99A3E70643DBBDA62E4187839C87 |  | R22 | Non-TXV |  | 14.05% | 0.85952 | 27% | [5 empty] | Non-TXV | 14.05%
Lamont | CA | 93241-2773 |  | 2013-09-13 | 2013-09-13 18:20 | 2013-09-13 18:22 | PAYNE - 2AC13B30P-2B | 97 | -3.7 | Yes | Yes | 24.1 | 21.5 | 2.6 | DB7A9F33ECCD4362B60D6BE88D8AA997 |  | R22 | TXV |  | -3.814% | 1.0381 | 1.068% |  |  |  |  | TXV |  |  | -3.814%
San Jose | CA | 95133-1203 |  | 2013-09-25 | 2013-09-25 12:46 | 2013-09-25 13:04 | TRANE - UNK | 80 | 7.9 | Yes | Yes | 22.7 | 19.3 | 3.4 | 6D2C5431E2A0493CBC455D387FCEEE72 |  | R410A | TXV |  | 9.875% | 0.90125 | 18.98% | [5 empty] | TXV | 9.875%
Bakersfield | CA | 93301-2634 |  | 2013-09-25 | 2013-09-25 11:27 | 2013-09-25 11:47 | CARRIER - 48DC003 | 85 | 3.9 | Yes | Yes | 21.9 | 21.9 | 0 | B106F428BB4240C6A9D489CCBC9BCC7E |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Milpitas | CA | 95035-3103 |  | 2013-09-26 | 2013-09-26 09:37 | 2013-09-26 10:15 | YORK - H3RAQ060S06G | 98 | 3.3 | Yes | Yes | 19 | 22 | -3 | 78DE1CF5AF28426B8F7EDBBBAC72DD39 |  | R22 | Non-TXV |  | 3.367% | 0.96633 | 6.471% | [5 empty] | Non-TXV | 3.367%
Bakersfield | CA | 93309-2035 |  | 2013-08-21 | 2013-08-21 19:01 | 2013-08-21 19:03 | PAYNE - PY3PNA030060NB | 96 | 20.2 | Yes | Yes | 19.4 | 18.2 | 1.2 | 392BD1B3ECCB46CAABE8069305A48630 |  | R22 | Non-TXV |  | 21.04% | 0.78958 | 40.44% | [5 empty] | Non-TXV | 21.04%
Bakersfield | CA | 93307-3251 |  | 2013-10-24 | 2013-10-24 09:47 | 2013-10-24 09:47 | GOODMAN - GSX130481BB | 125 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | C5995E2B58C143DA9B9C68C38A82A06C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3251 |  | 2013-10-24 | 2013-10-24 09:58 | 2013-10-24 09:58 | GOODMAN - GSX1303610A | 138 | 0 | Yes | Yes | 23.4 | 20.9 | 2.5 | 0E13BCD5E6D9458F9E0E4C628EC5541E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3772 |  | 2013-07-25 | 2013-07-25 09:52 | 2013-07-25 10:55 | YORK - DARA-F024N040B | 68 | 6.1 | Yes | Yes | 25.5 | 20.1 | 5.4 | 1BB4875196AE44ADB7723FCDCF34349C |  | R22 | Non-TXV |  | 8.971% | 0.91029 | 17.24% | [5 empty] | Non-TXV | 8.971%
Bakersfield | CA | 93308-2514 |  | 2013-07-11 | 2013-07-11 16:04 | 2013-07-11 16:04 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 21.4 | 20.7 | 0.7 | D1D65834ACA74F659076ABACC2E3380B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5429 |  | 2013-07-03 | 2013-07-03 09:35 | 2013-07-03 14:01 | DAY & NIGHT - 585CJ030050 | 78 | 2.5 | Yes | Yes | 26.6 | 20.6 | 6 | DD7411F6841045C39486DECF05EE2469 |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Bakersfield | CA | 93304-6051 |  | 2013-07-03 | 2013-07-03 09:43 | 2013-07-03 09:43 | TRANE - 4YCZ6036A1075AA | 111 | 0 | Yes | Yes | 18.4 | 19.3 | -0.9 | 951E79A50763475BB0CD521EF37A8151 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1318 |  | 2013-07-24 | 2013-07-24 14:21 | 2013-07-24 14:22 | GE - BGT924H1 | 42 | -3 | Yes | Yes | 18.4 | 17.3 | 1.1 | F6D51FF260704C6A9F8E3035ADFEABBF |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Bakersfield | CA | 93305-3772 |  | 2013-07-25 | 2013-07-25 09:33 | 2013-07-25 09:50 | YORK - DCHG-F024N05613 | 62 | 3.4 | Yes | Yes | 21.5 | 20.8 | 0.7 | 1E6B6311738741448B762E66282E9E04 |  | R22 | Non-TXV |  | 5.484% | 0.94516 | 10.54% | [5 empty] | Non-TXV | 5.484%
Fairfield | CA | 94533-2214 |  | 2013-07-22 | 2013-07-22 10:35 | 2013-07-22 12:21 | TRANE - TTD48A100A0 | 118 | 4.2 | Yes | Yes | 16.3 | 17.7 | -1.4 | 310A596927684933966BE64B0DB69FE6 |  | R22 | Non-TXV |  | 3.559% | 0.96441 | 6.84% | [5 empty] | Non-TXV | 3.559%
Bakersfield | CA | 93309-3936 |  | 2013-07-25 | 2013-07-25 12:27 | 2013-07-25 12:58 | ICP - GFCM30K080A | 52 | 1.6 | Yes | Yes | 26.2 | 23.1 | 3.1 | 2D5620F2676648F1BBC26B6C6A005E12 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Benicia | CA | 94510-2745 |  | 2013-08-13 | 2013-08-13 08:36 | 2013-08-13 08:38 | CARRIER - 38HDC024-341 | 84 | -6.9 | Yes | Yes | 16.9 | 17.6 | -0.7 | 3E41FDCCCCEA44E3A9DC3D31FB407C5F |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Arvin | CA | 93203-2064 |  | 2013-08-19 | 2013-08-19 16:26 | 2013-08-19 17:26 | GOODMAN - CKJE36 1B | 108 | 4 | Yes | Yes | 17.5 | 20.3 | -2.8 | C4B4BB2C33C84CEF90548ABFF2918CAA |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Benicia | CA | 94510-1615 |  | 2013-08-13 | 2013-08-13 09:52 | 2013-08-13 09:53 | TRANE - 2TTR2042B1000AAA | 86 | 2.8 | Yes | Yes | 14.4 | 15.9 | -1.5 | 3E29DB09DCD04C62B869A2170C03EA2F |  | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
San Jose | CA | 95135-1322 |  | 2013-07-18 | 2013-07-18 15:18 | 2013-07-18 15:18 | GE - N/A | 85 | 0 | Yes | Yes | 17.8 | 19.5 | -1.7 | F0E80A2409C746B196DCF993FC1B53A2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95140-9733 |  | 2013-10-04 | 2013-10-04 14:27 | 2013-10-04 14:50 | RUUD - UAKA-048JAZ | 103 | -7.3 | Yes | Yes | 24.1 | 20.4 | 3.7 | 4ABBF1A7AF614C56BBC1F2D2B4108DC4 |  | R22 | Non-TXV |  | -7.087% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.087%
San Jose | CA | 95140-9733 |  | 2013-10-04 | 2013-10-04 14:52 | 2013-10-04 15:26 | RUUD - UAKA-030JAZ | 66 | -4.7 | Yes | Yes | 21.3 | 20.3 | 1 | 0532F89E81554D03B06A782098BB4429 |  | R22 | Non-TXV |  | -7.121% | 1.0712 | 1.994% |  |  |  |  | Non-TXV |  |  | -7.121%
Bakersfield | CA | 93301-2634 |  | 2013-09-25 | 2013-09-25 16:49 | 2013-09-25 17:06 | BRYANT - 582ANW030040NAAD | 85 | 4.9 | Yes | Yes | 16.8 | 19.6 | -2.8 | E7B8E254009640BD93A62E1040E95086 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | Non-TXV | 5.765%
San Jose | CA | 95133-1539 |  | 2013-07-24 | 2013-07-24 12:27 | 2013-07-24 12:27 | RHEEM - RACB-036JAS | 48 | 1.8 | Yes | Yes | 16.3 | 17.3 | -1 | C9CF47C8EC3C4DE6B685DC54BF72C2B0 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
San Jose | CA | 95133-1250 |  | 2013-07-24 | 2013-07-24 13:40 | 2013-07-24 13:42 | GOODMAN - CK24-1B | 71 | 5.6 | Yes | Yes | 17.1 | 17.6 | -0.5 | 13CD4B3956D84A569ED227074C3C5E55 |  | R22 | Non-TXV |  | 7.887% | 0.92113 | 15.16% | [5 empty] | Non-TXV | 7.887%
Arvin | CA | 93203-2066 |  | 2013-08-21 | 2013-08-21 14:41 | 2013-08-21 17:09 | GOODMAN - CPLE36 1A | 102 | 3.5 | Yes | Yes | 21 | 20.1 | 0.9 | 295C50180CEC41059D4747FED14A2DB6 |  | R22 | Non-TXV |  | 3.431% | 0.96569 | 6.594% | [5 empty] | Non-TXV | 3.431%
San Jose | CA | 95125-4006 |  | 2013-09-25 | 2013-09-25 16:12 | 2013-09-25 18:54 | TRANE - UNK | 73 | 4.2 | Yes | Yes | 25 | 20.2 | 4.8 | C76C339A816E4D578C952116138BB0BD |  | R22 | Non-TXV |  | 5.753% | 0.94247 | 11.06% | [5 empty] | Non-TXV | 5.753%
Arvin | CA | 93203-2063 |  | 2013-09-09 | 2013-09-09 11:30 | 2013-09-09 11:47 | GOODMAN - CPLE42 1B | 122 | 5 | Yes | Yes | 20.4 | 20.1 | 0.3 | B4B46339F2FD4197AB3612AC6CE932D1 |  | R22 | Non-TXV |  | 4.098% | 0.95902 | 7.876% | [5 empty] | Non-TXV | 4.098%
Arvin | CA | 93203-2067 |  | 2013-09-09 | 2013-09-09 16:01 | 2013-09-09 16:18 | GOODMAN - CPLE 42 1B | 115 | 3.5 | Yes | Yes | 21 | 20.1 | 0.9 | 8AC298CD89984A02BFB5FDCDDE713387 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Bakersfield | CA | 93301-2634 |  | 2013-09-25 | 2013-09-25 15:14 | 2013-09-25 15:31 | GOODMAN - GPG13300451AB | 85 | 6.2 | Yes | Yes | 18.4 | 21.3 | -2.9 | E759F56F3C7B408B990DD1BEF995135A |  | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Dixon | CA | 95620-2437 |  | 2013-10-21 | 2013-10-21 10:14 | 2013-10-21 10:54 | AMERICAN STANDARD - 2TTB3024A1000AA | 82 | -1.8 | Yes | Yes | 15.8 | 18.7 | -2.9 | 492B9B385FDC48A3B874D4AAC9487363 |  | R22 | Non-TXV |  | -2.195% | 1.022 | 0.6147% |  |  |  |  | Non-TXV |  |  | -2.195%
Lamont | CA | 93241-2772 |  | 2013-09-26 | 2013-09-26 22:15 | 2013-09-27 04:50 | OTHER - 24C13B24P | 89 | 3.8 | Yes | Yes | 22.2 | 18.8 | 3.4 | B3E0875222644EF7A4CA2C456F6E6FBF |  | R22 | Non-TXV |  | 4.27% | 0.9573 | 8.205% | [5 empty] | Non-TXV | 4.27%
Benicia | CA | 94510-2506 |  | 2013-08-07 | 2013-08-07 10:29 | 2013-08-07 11:19 | PAYNE - PA13N024000AHAA | 64 | 4 | Yes | Yes | 22.1 | 19.3 | 2.8 | CFE7220815B643279D80E7759AF920D3 |  | R22 | TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | TXV | 6.25%
Vacaville | CA | 95688-3826 |  | 2013-07-02 | 2013-07-02 12:38 | 2013-07-02 13:00 | DAY & NIGHT - 565B036-A | 85 | 2.8 | Yes | Yes | 25.1 | 19.6 | 5.5 | B5D3F42005C54F08BEEFCFC646A756AF |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fresno | CA | 93704-4484 |  | 2013-10-25 | 2013-10-25 12:57 | 2013-10-25 13:44 | YORK - D1NA024N03606C | 54 | 4.9 | Yes | Yes | 21.4 | 19.4 | 2 | 6B854D1EC5C744A8A90522AAE5B98C0B |  | R22 | Non-TXV |  | 9.074% | 0.90926 | 17.44% | [5 empty] | Non-TXV | 9.074%
Fresno | CA | 93711-2756 |  | 2013-06-27 | 2013-06-27 12:15 | 2013-06-27 12:51 | YORK - H1RD036S06G | 145 | 10.1 | Yes | Yes | 20.7 | 20.5 | 0.2 | 3AC529D18F4A4AD39E1C5FCD8FBF1DEB |  | R22 | TXV |  | 6.966% | 0.93034 | 13.39% | [5 empty] | TXV | 6.966%
Fresno | CA | 93705-1330 |  | 2013-07-03 | 2013-07-03 13:41 | 2013-07-03 14:05 | GOODMAN - PGB036075 | 60 | 18.8 | Yes | Yes | 23.2 | 19.6 | 3.6 | 9CFD7223E296427BA77955D47E754B96 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 31.33% | 0.68667 | 60.22% | [5 empty] | Non-TXV | 31.33%
Fresno | CA | 93726-5707 |  | 2013-06-28 | 2013-06-28 09:53 | 2013-06-28 10:43 | CARRIER - 48DL004 | 81 | 4 | Yes | Yes | 18 | 19.4 | -1.4 | 703E90422044468CBBEFCA6EB7B1CB48 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.938% | 0.95062 | 9.49% | [5 empty] | Non-TXV | 4.938%
Bakersfield | CA | 93306-7547 |  | 2013-07-24 | 2013-07-24 08:45 | 2013-07-24 08:45 | YORK - BRCS0361BD | 63 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | 941DED5478B04365A29ACACFC695019B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3968 |  | 2013-06-28 | 2013-06-28 14:07 | 2013-06-28 14:44 | - 00HR24E1NA | 58 | 6.2 | Yes | Yes | 19.6 | 18.3 | 1.3 | 2340CD077AE44172891B6636DB53896B |  | R22 | Non-TXV |  | 10.69% | 0.8931 | 20.54% | [5 empty] | Non-TXV | 10.69%
Shafter | CA | 93263-1822 |  | 2013-07-22 | 2013-07-22 19:14 | 2013-07-22 19:33 | RUUD - UAJB-048JAZ | 156 | 8.7 | Yes | Yes | 18.5 | 19.9 | -1.4 | 894ED92D40A044AF9BE7958ED0B47525 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
San Jose | CA | 95123-4620 |  | 2013-07-24 | 2013-07-24 11:01 | 2013-07-24 11:02 | RHEEM - RAKA-036JAS | 75 | 15.1 | Yes | Yes | 18.2 | 18.8 | -0.6 | 6136A29AE66A43A082F63789FAB464E3 |  | R22 | Non-TXV |  | 20.13% | 0.79867 | 38.69% | [5 empty] | Non-TXV | 20.13%
San Jose | CA | 95123-2438 |  | 2013-09-19 | 2013-09-19 11:06 | 2013-09-19 11:27 | CARRIER - 38QH018310 | 148 | 5.9 | Yes | Yes | 21.3 | 21 | 0.3 | 8299B28FADC647918CE2F66BB67DC0CE |  | R22 | Non-TXV |  | 3.986% | 0.96014 | 7.661% | [5 empty] | Non-TXV | 3.986%
Fresno | CA | 93711-2622 |  | 2013-07-08 | 2013-07-08 18:06 | 2013-07-08 18:24 | BDP - 589NW036080ACBF | 86 | 17.8 | Yes | Yes | 26.5 | 20.7 | 5.8 | 28A9DAF25F714DA4A2EB3E6129E181AC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.7% | 0.79302 | 39.78% | [5 empty] | Non-TXV | 20.7%
Fresno | CA | 93704-5439 |  | 2013-08-17 | 2013-08-17 17:36 | 2013-08-17 18:10 | CARRIER - 48ESNA3606030TP | 102 | 9.5 | Yes | Yes | 26.8 | 21.5 | 5.3 | C110FAA1666646B3B5E58C7AB7F7ABC1 |  | R410A | TXV |  | 9.314% | 0.90686 | 17.9% | [5 empty] | TXV | 9.314%
Fresno | CA | 93705-4522 |  | 2013-07-26 | 2013-07-26 10:22 | 2013-07-26 11:00 | YORK - H2RD042S06A | 141 | 8.5 | Yes | Yes | 23.2 | 18.9 | 4.3 | CA1F851B3437451D910927FE2F577CE7 |  | R22 | Non-TXV |  | 6.028% | 0.93972 | 11.59% | [5 empty] | Non-TXV | 6.028%
Woodland | CA | 95695-5408 |  | 2013-08-01 | 2013-08-01 09:20 | 2013-08-01 09:22 | AMANA - RCC36A2A | 180 | -12.7 | Yes | Yes | 14.9 | 17.6 | -2.7 | 1520CE481A424CF08559C873A39FC8C6 |  | R22 | Non-TXV |  | -7.056% | 1.0706 | 1.976% |  |  |  |  | Non-TXV |  |  | -7.056%
Sunnyvale | CA | 94089-5001 |  | 2013-10-07 | 2013-10-07 13:07 | 2013-10-07 14:17 | COLEMAN - BRCQ0361CB | 49 | -4 | Yes | Yes | 25.4 | 20.4 | 5 | F2EFF7CFDE484FF29C0A4DF3340B41FF |  | R22 | Non-TXV |  | -8.163% | 1.0816 | 2.286% |  |  |  |  | Non-TXV |  |  | -8.163%
Bakersfield | CA | 93313-0000 |  | 2013-09-11 | 2013-09-11 19:08 | 2013-09-11 19:10 | OTHER - H2RC048S06A | 119 | 6.4 | Yes | Yes | 25.1 | 21.5 | 3.6 | 06241A1A0379478DA9D99BE5ACEDF01D |  | R22 | TXV |  | 5.378% | 0.94622 | 10.34% | [5 empty] | TXV | 5.378%
Bakersfield | CA | 93313-5236 |  | 2013-07-16 | 2013-07-16 11:11 | 2013-07-16 11:35 | PAYNE - PA12NA036-H | 85 | 10.8 | Yes | Yes | 18.5 | 21.5 | -3 | 18E469F644EB450EA0A5BE693E2D7760 |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
Fresno | CA | 93711-1673 |  | 2013-10-25 | 2013-10-25 13:56 | 2013-10-25 14:15 | GOODMAN - GPF13420701AA | 107 | 3.4 | Yes | Yes | 21.2 | 19.7 | 1.5 | 79A8A7B8ED2246FA9BA55FB2AC4F6D5D |  | R22 | Non-TXV |  | 3.178% | 0.96822 | 6.107% | [5 empty] | Non-TXV | 3.178%
Fresno | CA | 93711-0708 |  | 2013-08-23 | 2013-08-23 13:18 | 2013-08-23 13:56 | - DAYH-F036N070C | 108 | 16.1 | Yes | Yes | 23.4 | 20.4 | 3 | 1BDF5595F8304356B2C668D06DDFBD10 |  | R22 | Non-TXV |  | 14.91% | 0.85093 | 28.65% | [5 empty] | Non-TXV | 14.91%
San Jose | CA | 95110-2861 |  | 2013-10-15 | 2013-10-15 16:12 | 2013-10-15 16:47 | CARRIER - 38HDC036 | 84 | 4.8 | Yes | Yes | 19.7 | 21.4 | -1.7 | DD21820338A24B95B8F3676EF99E1C9B |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Bakersfield | CA | 93306-7667 |  | 2013-07-24 | 2013-07-24 10:05 | 2013-07-24 10:05 | YORK - H1RD042S06G | 152 | 0 | Yes | Yes | 21.5 | 20.9 | 0.6 | BCA80BBC80624804B53C80A11D357C76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7667 |  | 2013-07-24 | 2013-07-24 10:12 | 2013-07-24 10:12 | YORK - H1RD060S06G | 253 | 0 | Yes | Yes | 20.7 | 20.9 | -0.2 | D0B884C48A3649588521F0BC6E37A048 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2078 |  | 2013-09-05 | 2013-09-05 09:07 | 2013-09-05 09:07 | OTHER - EBA4200 | 85 | 0 | Yes | Yes | 22.3 | 18.2 | 4.1 | FB7A6F80F4CE4E70A0C49C5D6410F4FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2202 |  | 2013-07-22 | 2013-07-22 09:48 | 2013-07-22 12:19 | RHEEM - RAMA-048JAZ | 172 | 3 | Yes | Yes | 13.1 | 16.1 | -3 | 30386E8D064C4B0CB4BF2767A9C57048 |  | R22 | Non-TXV |  | 1.744% | 0.98256 | 3.352% | [5 empty] | Non-TXV | 1.744%
San Jose | CA | 95111-2670 |  | 2013-10-08 | 2013-10-08 10:54 | 2013-10-08 11:33 | DAY & NIGHT - 591ANX036000AAAA | 83 | 17.8 | Yes | Yes | 25.4 | 20.1 | 5.3 | 4F3BF2867D1E43D98B9351D6A5B962A9 |  | R22 | Non-TXV |  | 21.45% | 0.78554 | 41.21% | [5 empty] | Non-TXV | 21.45%
Sanger | CA | 93657-2415 |  | 2013-07-30 | 2013-07-30 10:45 | 2013-07-30 11:13 | YORK - D1NA030N03606C | 76 | -4.5 | Yes | Yes | 19.4 | 19.3 | 0.1 | 760DDC529E50451585D9B954D1BA1EEC |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Bakersfield | CA | 93313-5736 |  | 2013-07-19 | 2013-07-19 09:53 | 2013-07-19 10:15 | OTHER - H2RC048S06A | 119 | 9 | Yes | Yes | 25.8 | 20.1 | 5.7 | DA3CDB6D66AD4F1699654477DE3278C2 |  | R22 | Non-TXV |  | 7.563% | 0.92437 | 14.53% | [5 empty] | Non-TXV | 7.563%
Bakersfield | CA | 93313-5734 |  | 2013-07-22 | 2013-07-22 12:06 | 2013-07-22 12:44 | YORK - H2RC048S06A | 119 | 9.7 | Yes | Yes | 20.1 | 21 | -0.9 | 3FC532A97627442E86DF9573812BC5D8 |  | R22 | TXV |  | 8.151% | 0.91849 | 15.66% | [5 empty] | TXV | 8.151%
Pittsburg | CA | 94565-5149 |  | 2013-10-02 | 2013-10-02 10:22 | 2013-10-02 10:22 | GOODMAN - GSH130241AC | 106 | 0 | Yes | Yes | 17.4 | 16.7 | 0.7 | 953167669DE94199BC24A224864A3A93 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1344 |  | 2013-08-02 | 2013-08-02 09:19 | 2013-08-02 09:19 | TRANE - BTD736A100B0 | 88 | 0 | Yes | Yes | 21.3 | 18.2 | 3.1 | F669DB4A06F3449B9102B12160A33EB4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4933 |  | 2013-08-09 | 2013-08-09 11:05 | 2013-08-09 11:05 | PAYNE - PY1PNB036060ABAA | 70 | 0 | Yes | Yes | 21.6 | 21.8 | -0.2 | F923EAF5EFBD4CAB99FEFB097BB8F1D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6622 |  | 2013-07-10 | 2013-07-10 19:57 | 2013-07-10 19:57 | YORK - D1NH048N06506C | 85 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | D0B069AC936441B992FF8C7CCD752210 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4535 |  | 2013-08-01 | 2013-08-01 10:11 | 2013-08-01 10:18 | PAYNE - PY3PNA030060NB | 96 | 5.2 | Yes | Yes | 17.4 | 17 | 0.4 | 234BA14698384AE692A48A4EDD01BC9C |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Shafter | CA | 93263-2340 |  | 2013-08-05 | 2013-08-05 17:24 | 2013-08-05 18:46 | GOODMAN - GPG1336045M41AB | 85 | 16.5 | Yes | Yes | 23.7 | 21.5 | 2.2 | 48D43A7864CA4F7F9F2E260A7CFCCD4F |  | R410A | Non-TXV |  | 19.41% | 0.80588 | 37.31% | [5 empty] | Non-TXV | 19.41%
Fresno | CA | 93703-2409 |  | 2013-06-26 | 2013-06-26 09:19 | 2013-06-26 10:11 | OTHER - GPC036K06E | 70 | 5.3 | Yes | Yes | 19.9 | 19.2 | 0.7 | 1E02F9E9527C48CB925EA9A3890A3D82 |  | R22 | Non-TXV |  | 7.571% | 0.92429 | 14.55% | [5 empty] | Non-TXV | 7.571%
Wasco | CA | 93280-2373 |  | 2013-10-01 | 2013-10-01 20:20 | 2013-10-01 20:23 | LENNOX - 13HPD-024-24-230-01 | 99 | -5.2 | Yes | Yes | 22.5 | 20.2 | 2.4 | CB8C9FBABA7A4E739E3D236C90F85705 |  | R22 | TXV |  | -5.253% | 1.0525 | 1.471% |  |  |  |  | TXV |  |  | -5.253%
Bakersfield | CA | 93313-2762 |  | 2013-07-09 | 2013-07-09 15:30 | 2013-07-09 18:11 | UNK - UNK | 85 | 7.4 | Yes | Yes | 21.4 | 22.6 | -1.2 | 5E78902D341E4AA1A79FE648746FAE16 |  |  |  |  | 8.706% | 0.91294 | 16.73% | [5 empty] | 0 | 8.706%
Fresno | CA | 93727-0000 |  | 2013-08-15 | 2013-08-15 14:46 | 2013-08-15 15:18 | OTHER - UNK | 180 | 33 | Yes | Yes | 20.1 | 18.8 | 1.3 | FFD6D0CCEDFF4261B1816E3B0CF0833D |  | R410A | Non-TXV |  | 18.33% | 0.81667 | 35.23% | [5 empty] | Non-TXV | 18.33%
Wasco | CA | 93280-2374 |  | 2013-10-02 | 2013-10-02 18:58 | 2013-10-02 19:00 | LENNOX - 13HPD-024-230-01 | 99 | 7.8 | Yes | Yes | 23.3 | 20.4 | 2.9 | 60079A46B774406C876E7919B0710D3E |  | R22 | TXV |  | 7.879% | 0.92121 | 15.14% | [5 empty] | TXV | 7.879%
Bakersfield | CA | 93301-2636 |  | 2013-09-24 | 2013-09-24 16:20 | 2013-09-24 16:42 | GOODMAN - GPG134045M41CA | 85 | 6.2 | Yes | Yes | 13.5 | 16.5 | -3 | 43EF079C139F415B9BF638B9864ABA8D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Wasco | CA | 93280-2375 |  | 2013-10-04 | 2013-10-04 19:38 | 2013-10-04 19:39 | LENNOX - 13HPD-024-230-01 | 99 | 11.9 | Yes | Yes | 22 | 20.2 | 1.8 | 69872F75C00141AB89184964E2260FF8 |  | R22 | TXV |  | 12.02% | 0.8798 | 23.1% | [5 empty] | TXV | 12.02%
Bakersfield | CA | 93306-2325 |  | 2013-07-16 | 2013-07-16 19:52 | 2013-07-16 19:52 | BDP - 585CJ030050 | 78 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | 95BC582110374EF6BFA35112B973D486 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2124 |  | 2013-08-17 | 2013-08-17 11:19 | 2013-08-17 11:40 | DAY & NIGHT - 36/80YAC | 85 | 9.3 | Yes | Yes | 21 | 19 | 2 | 4C53F70504824F00BC77434707F926A0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.94% | 0.89059 | 21.03% | [5 empty] | Non-TXV | 10.94%
Vallejo | CA | 94589-1782 |  | 2013-09-25 | 2013-09-25 09:26 | 2013-09-25 09:27 | RUUD - UACB-048JAQ | 47 | -4.4 | Yes | Yes | 18 | 17 | 1 | 08B6B5E4D54F4FFBBB2F53783F4590FE |  | R22 | Non-TXV |  | -9.362% | 1.0936 | 2.622% |  |  |  |  | Non-TXV |  |  | -9.362%
Fresno | CA | 93710-5616 |  | 2013-07-01 | 2013-07-01 09:50 | 2013-07-01 10:21 | TEMPSTAR - PGAD42D1K1 | 180 | 5.5 | Yes | Yes | 23.1 | 20.8 | 2.3 | 1A9C8AB6889C459FA5970D6AC3FD48E3 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Fresno | CA | 93728-3214 |  | 2013-06-27 | 2013-06-27 11:57 | 2013-06-27 11:57 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 2D984DECCD7A4F1798E4175DE932AF9F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5229 |  | 2013-06-27 | 2013-06-27 17:02 | 2013-06-27 17:23 | OTHER - UKN | 80 | 16 | Yes | Yes | 16.4 | 19 | -2.6 | FA9C6155BDC449669877935869FDC93F |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
San Jose | CA | 95118-1841 |  | 2013-07-24 | 2013-07-24 11:38 | 2013-07-24 11:39 | DAY & NIGHT - 561CJ036-D | 84 | 16.6 | Yes | Yes | 17.5 | 17 | 0.5 | 90CEF741B7CA45308F6EF04820120815 |  | R22 | Non-TXV |  | 19.76% | 0.80238 | 37.98% | [5 empty] | Non-TXV | 19.76%
Bakersfield | CA | 93304-1573 |  | 2013-07-20 | 2013-07-20 10:11 | 2013-07-20 10:11 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.7 | 22.1 | -0.4 | 65E4C3FB017A46CFBF690E1A16BE7400 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5330 |  | 2013-07-05 | 2013-07-05 12:20 | 2013-07-05 12:20 | GUARDIAN - GCGD4854153A | 73 | 0 | Yes | Yes | 12 | 19.3 | -7.3 | 1708919C7FF14EEAA33A0D682363C285 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5840 |  | 2013-07-26 | 2013-07-26 12:00 | 2013-07-26 12:48 | CARRIER - 48SX060100321AA | 104 | -9.8 | Yes | Yes | 20 | 16.1 | 3.9 | 1122EBF2F563437E9CF5BFC05D8E3585 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Arvin | CA | 93203-9464 |  | 2013-08-05 | 2013-08-05 09:14 | 2013-08-05 09:37 | GOODMAN - GSC130421AC | 135 | 8.5 | Yes | Yes | 19.1 | 19.8 | -0.7 | 0A99100B37CC40B2BF41F97C4133A711 |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Wasco | CA | 93280-1133 |  | 2013-07-20 | 2013-07-20 16:28 | 2013-07-20 16:35 | AMERICAN STANDARD - R4GDY30K072X | 85 | 3.9 | Yes | Yes | 19.5 | 22.4 | -2.9 | 0B9F70D12E3D41EB95E0C7BA399C8523 |  | R22 | TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | TXV | 4.588%
Shafter | CA | 93263-2329 |  | 2013-08-30 | 2013-08-30 18:53 | 2013-08-30 18:56 | GOODMAN - GPG13480701AC | 145 | 6 | Yes | Yes | 26.2 | 20.4 | 5.8 | A67E6671B0F34F8F9477568F1EDA5CAA |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Santa Rosa | CA | 95404-8905 |  | 2013-10-03 | 2013-10-03 13:24 | 2013-10-03 16:14 | CARRIER - 38YCC048300 | 148 | 4.9 | Yes | Yes | 16.8 | 19.5 | -2.7 | 5047808059164D868B0DEB02C49B9B78 |  | R22 | Non-TXV |  | 3.311% | 0.96689 | 6.363% | [5 empty] | Non-TXV | 3.311%
Bakersfield | CA | 93313-2769 |  | 2013-09-11 | 2013-09-11 19:11 | 2013-09-11 19:13 | RHEEM - N/A | 85 | -3.4 | Yes | Yes | 26.3 | 22 | 4.3 | 8E91D501C879466C831C98E2D16BD45B |  | R22 | TXV |  | -4% | 1.04 | 1.12% |  |  |  |  | TXV |  |  | -4%
Sunnyvale | CA | 94089-5001 |  | 2013-10-07 | 2013-10-07 11:18 | 2013-10-07 12:03 | COLEMAN - ILLEGIBLE | 57 | 12.6 | Yes | Yes | 23 | 20.7 | 2.4 | BC96FCDC986C439597BB6CE7A8DB3AB3 |  | R22 | Non-TXV |  | 22.11% | 0.77895 | 42.48% | [5 empty] | Non-TXV | 22.11%
Bakersfield | CA | 93305-4961 |  | 2013-07-25 | 2013-07-25 14:55 | 2013-07-25 15:39 | PAYNE - PY3PNA030040NB | 96 | 3.8 | Yes | Yes | 25.6 | 21.5 | 4.1 | 6099430D001B479BA5ADA072DE164662 |  | R22 | Non-TXV |  | 3.958% | 0.96042 | 7.607% | [5 empty] | Non-TXV | 3.958%
Woodland | CA | 95695-2565 |  | 2013-09-27 | 2013-09-27 09:51 | 2013-09-27 09:51 | NORDYNE - JT3BA-024KA | 85 | 0 | Yes | Yes | 20.6 | 17.2 | 3.4 | 18F2419CC4F942C48D1AE56320FDFEDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1442 |  | 2013-09-27 | 2013-09-27 10:33 | 2013-09-27 14:05 | CARRIER - 38CKCKC048370 | 100 | -5.1 | Yes | Yes | 12 | 15 | -3 | 40490DCB25CA4981BAC0C312820431C6 |  | R22 | Non-TXV |  | -5.1% | 1.051 | 1.428% |  |  |  |  | Non-TXV |  |  | -5.1%
Bakersfield | CA | 93305-3341 |  | 2013-07-25 | 2013-07-25 08:38 | 2013-07-25 09:06 | BDP - 585J4024050AAA5 | 54 | 5.9 | Yes | Yes | 23.6 | 21 | 2.6 | F812FDC002FF4C318CC42CC1383B02E6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.93% | 0.89074 | 21% | [5 empty] | Non-TXV | 10.93%
Fremont | CA | 94555-2080 |  | 2013-07-01 | 2013-07-01 12:10 | 2013-07-01 12:10 | GOODMAN - CK36-1A | 85 | 0 | Yes | Yes | 23.8 | 19.3 | 4.5 | B5A7D761252C454FA06A7C48D12BA8C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4910 |  | 2013-07-02 | 2013-07-02 10:24 | 2013-07-02 10:50 | BDP - 561CJ036-C | 142 | 6 | Yes | Yes | 21.1 | 18.8 | 2.3 | 7BF65324C92F4D74B4DD1F7E6749BAB5 |  | R22 | TXV |  | 4.225% | 0.95775 | 8.12% | [5 empty] | TXV | 4.225%
Kerman | CA | 93630-1460 |  | 2013-07-19 | 2013-07-19 15:08 | 2013-07-19 15:27 | LENNOX - GCS29X-030-75-1PA | 51 | 1.5 | Yes | Yes | 20.2 | 20.4 | -0.2 | 582A5F5FF4D849D4BE023CCCEC43E6B0 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93313-5736 |  | 2013-07-19 | 2013-07-19 11:02 | 2013-07-19 12:04 | OTHER - H2RC048S06A | 119 | 5.4 | Yes | Yes | 17.3 | 20.2 | -2.9 | 8FE58594DEB34527A9844E1951C1440A |  | R22 | Non-TXV |  | 4.538% | 0.95462 | 8.721% | [5 empty] | Non-TXV | 4.538%
Bakersfield | CA | 93304-1559 |  | 2013-07-18 | 2013-07-18 17:48 | 2013-07-18 18:05 | PAYNE - PH13NR018-H | 95 | 11.5 | Yes | Yes | 22.1 | 19.8 | 2.3 | 68D413CD5EF64B9BA0BE721B57B488DB |  | R22 | TXV |  | 12.11% | 0.87895 | 23.26% | [5 empty] | TXV | 12.11%
Bakersfield | CA | 93304-1560 |  | 2013-07-19 | 2013-07-19 11:01 | 2013-07-19 11:01 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.8 | 19.7 | 2.1 | 1C4D65949FFE4ADC8E80DA9A739CF45F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2077 |  | 2013-08-22 | 2013-08-22 09:11 | 2013-08-22 09:14 | OTHER - BRCQ0421BD | 66 | 2.8 | Yes | Yes | 17.7 | 17.6 | 0.1 | 849053EF8B27429996EAC8462CEF5D90 |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Bakersfield | CA | 93304-1560 |  | 2013-07-19 | 2013-07-19 11:26 | 2013-07-19 11:26 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.7 | 20.6 | 1.2 | D2292B7F809642B6A5C79DE197D2DB9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1551 |  | 2013-07-19 | 2013-07-19 14:59 | 2013-07-19 14:59 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | E487AF4F23BB4895B1F057596A83C260 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1551 |  | 2013-07-19 | 2013-07-19 17:00 | 2013-07-19 17:00 | CARRIER - 38YCC018340 | 68 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 2BA0E805729D49A7A7808E6AA8074B6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1455 |  | 2013-07-09 | 2013-07-09 08:51 | 2013-07-09 09:56 | LENNOX - GCS29X03675 | 58 | 3.1 | Yes | Yes | 26.2 | 20.6 | 5.6 | D181B2DF30AF4B54BC6B03D644E685E0 |  | R22 | Non-TXV |  | 5.345% | 0.94655 | 10.27% | [5 empty] | Non-TXV | 5.345%
Bakersfield | CA | 93304-7187 |  | 2013-08-09 | 2013-08-09 14:25 | 2013-08-09 14:25 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.2 | 21 | 0.2 | 6E618EA350B541FA817E9FD60BFBBC80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2013-07-23 | 2013-07-23 14:57 | 2013-07-23 14:57 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | AD9135EC19AB4CBDBA6267F4FB7892A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3512 |  | 2013-08-09 | 2013-08-09 08:48 | 2013-08-09 08:48 | RHEEM - RRGC-05N31JKR | 48 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 9A10DEF85AB9404887E55BEF15211558 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2013-07-19 | 2013-07-19 12:35 | 2013-07-19 12:35 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 21.6 | 21.1 | 0.5 | AA0A962F64EE4D558167B3974587FD8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2714 |  | 2013-09-12 | 2013-09-12 11:45 | 2013-09-12 12:06 | DUCANE - 24AC13824P 2B | 89 | 3.3 | Yes | Yes | 19.5 | 19.5 | 0 | DFDE4056CF4146228C04986F14ADBED0 |  | R22 | Non-TXV |  | 3.708% | 0.96292 | 7.126% | [5 empty] | Non-TXV | 3.708%
Fresno | CA | 93711-1505 |  | 2013-09-19 | 2013-09-19 10:30 | 2013-09-19 11:09 | CARRIER - 48SS036060301 | 69 | 3.9 | Yes | Yes | 23.5 | 19.7 | 3.8 | 219B1450496F40FB92EC4F99BC0A2B9F |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Bakersfield | CA | 93306-1809 |  | 2013-10-15 | 2013-10-15 11:51 | 2013-10-15 11:51 | RHEEM - RRPLB048JK10X | 161 | 0 | Yes | Yes | 19.6 | 19.1 | 0.5 | 05E1EBE20BDE48EB8D57DBE5D98F1400 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2013-07-19 | 2013-07-19 11:10 | 2013-07-19 11:10 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.2 | 19.9 | -0.7 | 3316E943ADED4F66B4B2DB36344867FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2013-07-19 | 2013-07-19 12:04 | 2013-07-19 12:04 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 21.4 | 21.3 | 0.1 | 9472DEDBCB6144C79CC6D87F6EA4D428 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2013-07-19 | 2013-07-19 11:32 | 2013-07-19 11:50 | ICP - WCH3184GKA1 | 64 | 5.6 | Yes | Yes | 17.9 | 20.9 | -3 | 9442610BBD6F4314A4C323B669970FCB |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Bakersfield | CA | 93304-1574 |  | 2013-07-19 | 2013-07-19 13:50 | 2013-07-19 13:50 | CARRIER - 38YCC018340 | 66 | 0 | Yes | Yes | 19.2 | 20.4 | -1.2 | E1583B550A634DD5A24A059971880D1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1367 |  | 2013-09-23 | 2013-09-23 13:29 | 2013-09-23 14:18 | CARRIER - 24AB5330A0030010 | 85 | 4.1 | Yes | Yes | 20.4 | 18.6 | 1.8 | 0DC771E6BCF94620A02585FEE762710A |  | R22 | TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | TXV | 4.824%
Antioch | CA | 94531-8242 |  | 2013-08-27 | 2013-08-27 11:04 | 2013-08-27 11:19 | PAYNE - 561AJ060-B | 131 | 15.3 | Yes | Yes | 17.1 | 17.3 | -0.2 | BF871F3B840741F493E8F5095EB133FC |  | R22 | Non-TXV |  | 11.68% | 0.88321 | 22.45% | [5 empty] | Non-TXV | 11.68%
Clovis | CA | 93619-9247 |  | 2013-07-10 | 2013-07-10 16:59 | 2013-07-10 17:19 | LENNOX - 13ACD-048-230-02 | 204 | -7.4 | Yes | Yes | 21.4 | 19.6 | 1.8 | 07090450304F43899C73C758BD689B25 |  | R22 | TXV |  | -3.627% | 1.0363 | 1.016% |  |  |  |  | TXV |  |  | -3.627%
Fresno | CA | 93711-1515 |  | 2013-07-11 | 2013-07-11 17:18 | 2013-07-11 19:39 | AMERICAN STANDARD - YCP036F1M0AB | 109 | 3.2 | Yes | Yes | 27.7 | 22.7 | 5 | 077DF75965444AE387AA9B31B9BAAC8F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.936% | 0.97064 | 5.642% | [5 empty] | Non-TXV | 2.936%
Fresno | CA | 93728-1806 |  | 2013-08-26 | 2013-08-26 11:42 | 2013-08-26 12:07 | DAY & NIGHT - UNK | 80 | 2.4 | Yes | Yes | 20.1 | 18.1 | 2 | A373ABB9EC854A23B56CBF304A8D5D66 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
San Jose | CA | 95136-3205 |  | 2013-07-24 | 2013-07-24 13:07 | 2013-07-24 13:09 | TRANE - TTY036B100A1 | 170 | 11.2 | Yes | Yes | 17.4 | 17.1 | 0.3 | D65D447211F24B80B0C0BEBB151B045C |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Woodland | CA | 95695-5412 |  | 2013-08-01 | 2013-08-01 11:45 | 2013-08-01 11:46 | TAPPAN - YCY048G1H0AD | 176 | 5.7 | Yes | Yes | 18.3 | 18.2 | 0.1 | 9D33E63340814878A6243E2BB2C49F94 |  | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.224% | [5 empty] | Non-TXV | 3.239%
Fresno | CA | 93728-1035 |  | 2013-06-27 | 2013-06-27 15:34 | 2013-06-27 15:34 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C734AEFB03004DD78992269B09DC7771 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4908 |  | 2013-07-02 | 2013-07-02 16:25 | 2013-07-02 16:25 | YORK - DCYZF030N070B | 64 | 0 | Yes | Yes | 22.6 | 20.4 | 2.2 | 26E933ACAAB149B9B825A5E205A8D866 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2724 |  | 2013-07-24 | 2013-07-24 15:37 | 2013-07-24 16:22 | GOODMAN - PGB030020-1A | 56 | 4.1 | Yes | Yes | 29.7 | 24.8 | 4.9 | 8593FCB7091343FFA218484507C67089 |  | R22 | Non-TXV |  | 7.321% | 0.92679 | 14.07% | [5 empty] | Non-TXV | 7.321%
Sanger | CA | 93657-3300 |  | 2013-11-11 | 2013-11-11 14:53 | 2013-11-11 16:03 | RHEEM - RRPLB036JK06X | 93 | 3.6 | Yes | Yes | 21.4 | 19.5 | 1.9 | 5BF84B011EAB40A28990D5E0BC35E900 |  | R410A | Non-TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | Non-TXV | 3.871%
Fresno | CA | 93727-3549 |  | 2013-06-28 | 2013-06-28 17:41 | 2013-06-28 17:41 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C1B47D825F2748B68AA1535355E9927A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2714 |  | 2013-09-12 | 2013-09-12 15:05 | 2013-09-12 16:20 | DUCANE - 2AC13B24P 2B | 86 | 3.1 | Yes | Yes | 20.1 | 19.5 | 0.6 | BEA1F69A7BD24E2C9382718C5F00927F |  | R22 | Non-TXV |  | 3.605% | 0.96395 | 6.927% | [5 empty] | Non-TXV | 3.605%
San Jose | CA | 95122-1720 |  | 2013-07-25 | 2013-07-25 09:19 | 2013-07-25 09:19 | TRANE - TTR030C100A3 | 66 | 0 | Yes | Yes | 21.8 | 19.3 | 2.5 | 42E2F71A247048AB92A7D4000B051BDA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9341 |  | 2013-07-02 | 2013-07-02 13:57 | 2013-07-02 13:57 | DAY & NIGHT - 565AJA042 | 84 | 0 | Yes | Yes | 22.2 | 17 | 5.2 | 343AB4FBD76042D59A59261E851372A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-5326 |  | 2013-10-01 | 2013-10-01 11:39 | 2013-10-01 11:57 | LENNOX - 10ACB307P | 69 | 3 | Yes | Yes | 21.8 | 18.7 | 3.1 | F33F0886CEF34441B350BF7DC6514853 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Fresno | CA | 93705-3704 |  | 2013-06-28 | 2013-06-28 13:56 | 2013-06-28 14:43 | RHEEM - RRKAA048JK10X | 75 | 8 | Yes | Yes | 19.8 | 19.3 | 0.5 | 883C04E7EE454825A1B6A94664627AE1 |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Lamont | CA | 93241-2710 |  | 2013-09-12 | 2013-09-12 10:49 | 2013-09-12 11:24 | OTHER - 2AC131324P 28 | 89 | 3.2 | Yes | Yes | 20.1 | 20.5 | -0.4 | CFC59845E31544ECBD7F435C25ADE9D6 |  | R22 | Non-TXV |  | 3.596% | 0.96404 | 6.91% | [5 empty] | Non-TXV | 3.596%
Antioch | CA | 94531-8054 |  | 2013-08-19 | 2013-08-19 10:13 | 2013-08-19 10:19 | RUUD - RAKA-0600JAZ | 112 | 21 | Yes | Yes | 16.6 | 17.4 | -0.8 | E0AE43F6765545249FA40CDB97050001 |  | R22 | Non-TXV |  | 18.75% | 0.8125 | 36.03% | [5 empty] | Non-TXV | 18.75%
San Jose | CA | 95110-2857 |  | 2013-09-24 | 2013-09-24 11:28 | 2013-09-24 13:14 | CARRIER - 38HDC030 331 | 72 | 3 | Yes | Yes | 20.7 | 21 | -0.3 | 335C5D9C1F434C53870AF37BB0F1BC24 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Vallejo | CA | 94589-1489 |  | 2013-07-10 | 2013-07-10 13:29 | 2013-07-10 13:29 | TRANE - 4TTX6036B1000AA | 106 | 0 | Yes | Yes | 16.2 | 18.2 | -2 | 360EB5E8DEA047DAA522954EAA52643E |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4401 |  | 2013-07-15 | 2013-07-15 14:27 | 2013-07-15 14:27 | GE - | 85 | 0 | Yes | Yes | 13.2 | 13.9 | -0.6 | 8BD4B488C38E43C7A40B39A4F87AC65D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 19:26 | 2013-10-04 19:28 | LENNOX - 13HPD-024-230-01 | 99 | 5.7 | Yes | Yes | 22.8 | 20.4 | 2.4 | BB3016D178FE48A1BC0EA137A2F2962F |  | R22 | TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | TXV | 5.758%
San Jose | CA | 95138-1358 |  | 2013-10-17 | 2013-10-17 10:39 | 2013-10-17 11:24 | CARRIER - 38CKC036330 | 86 | 11.6 | Yes | Yes | 21.1 | 22.9 | -1.8 | 8CDA01719C264864B554CCE02F13B781 |  | R22 | Non-TXV |  | 13.49% | 0.86512 | 25.92% | [5 empty] | Non-TXV | 13.49%
Lemoore | CA | 93245-1752 |  | 2013-06-27 | 2013-06-27 16:41 | 2013-06-27 17:04 | DAY & NIGHT - UNK | 118 | -6.9 | Yes | Yes | 25.4 | 19.5 | 5.9 | 142E0CA2FEA74399A79665544DC4879F |  | R22 | Non-TXV |  | -5.847% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.847%
Bakersfield | CA | 93313-4433 |  | 2013-08-06 | 2013-08-06 09:36 | 2013-08-06 10:21 | RHEEM - RRGH-07N42JKR | 118 | 19.6 | Yes | Yes | 18.6 | 19.3 | -0.7 | 03D2157CF62642E081C3B1E08B14C77B |  | R22 | Non-TXV |  | 16.61% | 0.8339 | 31.92% | [5 empty] | Non-TXV | 16.61%
Fresno | CA | 93711-2555 |  | 2013-07-08 | 2013-07-08 12:28 | 2013-07-08 14:26 | GE - 582ANW6009AAAG | 118 | 4 | Yes | Yes | 24.2 | 21.3 | 2.9 | CF0FFB7C961B4F43ADFC27AB9889C7A7 |  | R22 | Non-TXV |  | 3.39% | 0.9661 | 6.515% | [5 empty] | Non-TXV | 3.39%
Fresno | CA | 93711-2555 |  | 2013-07-08 | 2013-07-08 13:11 | 2013-07-08 13:11 | GOODMAN - PGB042075-1REVA | 68 | 0 | Yes | Yes | 33.1 | 22.1 | 11 | 93DDD697DCE140D29C2AB636214FF059 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2376 |  | 2013-10-04 | 2013-10-04 19:12 | 2013-10-04 19:17 | LENNOX - 13HPD-024-230-01 | 99 | 10.7 | Yes | Yes | 22.6 | 20.2 | 2.5 | 8697A94A7779471C98AA05152AAF8F18 |  | R22 | TXV |  | 10.81% | 0.89192 | 20.77% | [5 empty] | TXV | 10.81%
Bakersfield | CA | 93305-3726 |  | 2013-07-23 | 2013-07-23 11:45 | 2013-07-23 12:15 | ICP - PGF33060K01A1 | 157 | 16.6 | Yes | Yes | 26.8 | 22.9 | 3.9 | D5ED379DCD6143F4B9E284D7BB3605A9 |  | R22 | Non-TXV |  | 10.57% | 0.89427 | 20.32% | [5 empty] | Non-TXV | 10.57%
Fremont | CA | 94555-2078 |  | 2013-08-22 | 2013-08-22 09:32 | 2013-08-22 09:33 | COLEMAN - BRC00361BD | 52 | 5 | Yes | Yes | 17 | 17 | 0 | 76C0C49A1E8246AD8BB6E97F9302E08A |  | R22 | Non-TXV |  | 9.615% | 0.90385 | 18.48% | [5 empty] | Non-TXV | 9.615%
Wasco | CA | 93280-2377 |  | 2013-10-05 | 2013-10-05 03:33 | 2013-10-05 03:50 | LENNOX - 13HPD-024-230-02 | 99 | 9.6 | Yes | Yes | 15 | 17.9 | -2.9 | 0BA089A543B040B084C54D9B1CE441A3 |  | R22 | TXV |  | 9.697% | 0.90303 | 18.64% | [5 empty] | TXV | 9.697%
Bakersfield | CA | 93305-3726 |  | 2013-06-28 | 2013-06-28 12:53 | 2013-06-28 13:13 | PAYNE - PY1PNB024040AAAA | 56 | -5.3 | Yes | Yes | 22.1 | 19.5 | 2.6 | FFFD1ADA9540428991C4D02F81517FE4 |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
San Jose | CA | 95132-1920 |  | 2013-09-25 | 2013-09-25 09:35 | 2013-09-25 09:57 | CARRIER - FS3BA 048KA | 86 | 7.3 | Yes | Yes | 18 | 20.2 | -2.2 | 9EBFB24DB3A046B5A197B088681826DC |  | R22 | Non-TXV |  | 8.488% | 0.91512 | 16.31% | [5 empty] | Non-TXV | 8.488%
Vallejo | CA | 94589-4334 |  | 2013-07-10 | 2013-07-10 09:21 | 2013-07-10 09:49 | CARRIER - 38CK-030-301 | 77 | 11.5 | Yes | Yes | 17.6 | 19.7 | -2.1 | EA260AC62CC74599952296F3773789B2 |  | R22 | Non-TXV |  | 14.94% | 0.85065 | 28.7% | [5 empty] | Non-TXV | 14.94%
San Jose | CA | 95135-1320 |  | 2013-10-19 | 2013-10-19 10:47 | 2013-10-19 11:17 | TRANE - 2TTR1030A100AA | 64 | 1.9 | Yes | Yes | 22.1 | 20.8 | 1.3 | 19D3665861EC4663993CCC75210A63BC |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
San Jose | CA | 95110-3144 |  | 2013-10-15 | 2013-10-15 13:18 | 2013-10-15 13:44 | CARRIER - 3DR018 | 70 | 4.8 | Yes | Yes | 20.1 | 21.7 | -1.6 | 93238E221EFD491486C64984BC35428A |  | R22 | Non-TXV |  | 6.857% | 0.93143 | 13.18% | [5 empty] | Non-TXV | 6.857%
Bakersfield | CA | 93307-1414 |  | 2013-09-07 | 2013-09-07 08:58 | 2013-09-07 09:20 | GOODMAN - VSX120361BA | 89 | 6.2 | Yes | Yes | 21.3 | 21 | 0.3 | DB8F2CD5D0744F989B3612D1B76F94A3 |  | R22 | Non-TXV |  | 6.966% | 0.93034 | 13.39% | [5 empty] | Non-TXV | 6.966%
Davis | CA | 95618-7677 |  | 2013-08-14 | 2013-08-14 13:29 | 2013-08-14 13:29 | CARRIER - 38CK018340 | 51 | 0 | Yes | Yes | 16.2 | 17.9 | -1.7 | 89E33062047749BD84A2CF49817C1D5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4541 |  | 2013-09-27 | 2013-09-27 08:29 | 2013-09-27 08:29 | RHEEM - RRPLB036JK08X | 92 | 0 | Yes | Yes | 19.6 | 20.1 | -0.5 | 5485E5CB3B9545A9BE347AF62A4C5D1F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4904 |  | 2013-07-10 | 2013-07-10 13:52 | 2013-07-10 15:40 | CARRIER - 584BNW036060B | 64 | 2.6 | Yes | Yes | 17.7 | 20.4 | -2.7 | 1F17262EC26949E48FF7BF34A0EB8E6F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Bakersfield | CA | 93301-2635 |  | 2013-09-26 | 2013-09-26 21:46 | 2013-09-26 22:06 | CARRIER - 48DC003 | 85 | 3.3 | Yes | Yes | 20.1 | 23.1 | -3 | 64093AECDEEA42AD87044A8784736E7C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Bakersfield | CA | 93301-2635 |  | 2013-09-25 | 2013-09-25 17:11 | 2013-09-25 17:28 | CARRIER - 48DC003 | 85 | 2.8 | Yes | Yes | 16.8 | 19.8 | -3 | B895FFE8223E4CBA8E57B12E42231027 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Bakersfield | CA | 93301-2636 |  | 2013-09-25 | 2013-09-25 16:17 | 2013-09-25 16:36 | GOODMAN - GPG1330045M41BA | 85 | 11.3 | Yes | Yes | 18.4 | 21.3 | -2.9 | E11D4659EEE54195B432AC9873176985 |  | R410A | Non-TXV |  | 13.29% | 0.86706 | 25.55% | [5 empty] | Non-TXV | 13.29%
Lamont | CA | 93241-2774 |  | 2013-09-13 | 2013-09-13 18:16 | 2013-09-13 18:18 | PAYNE - 2AC13B30P-2B | 97 | 3.5 | Yes | Yes | 25 | 20.9 | 4.1 | E2342F30E70446819710450989C4AAEF |  | R22 | TXV |  | 3.608% | 0.96392 | 6.934% | [5 empty] | TXV | 3.608%
Bakersfield | CA | 93301-2636 |  | 2013-09-24 | 2013-09-24 17:11 | 2013-09-24 17:30 | OTHER - UNK | 85 | 4 | Yes | Yes | 16.3 | 19.1 | -2.8 | 7C3969051EE14EA2AD828221B13580E9 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fresno | CA | 93704-5809 |  | 2013-07-05 | 2013-07-05 15:44 | 2013-07-05 16:06 | GOODMAN - GPG13360451AC | 112 | 5.3 | Yes | Yes | 28.1 | 22.1 | 6 | C000BF2804CB45EF9C0A2C6D28854D58 |  | R22 | Non-TXV |  | 4.732% | 0.95268 | 9.094% | [5 empty] | Non-TXV | 4.732%
Bakersfield | CA | 93307-5630 |  | 2013-08-07 | 2013-08-07 22:48 | 2013-08-07 23:21 | PAYNE - 2004E07539 | 97 | 15.7 | Yes | Yes | 19.9 | 21.5 | -1.6 | 179793DE129E4A86B636B36E0A6FD303 |  | R22 | Non-TXV |  | 16.19% | 0.83814 | 31.11% | [5 empty] | Non-TXV | 16.19%
San Jose | CA | 95110-3139 |  | 2013-09-24 | 2013-09-24 11:01 | 2013-09-24 11:26 | CARRIER - UNK | 83 | 2.6 | Yes | Yes | 18.8 | 20.4 | -1.6 | 5600B70FAF254A2F957B86B8B46C2FBE |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Antioch | CA | 94531-8472 |  | 2013-07-09 | 2013-07-09 09:17 | 2013-07-09 09:19 | CARRIER - 38CK036310 | 72 | -5.1 | Yes | Yes | 16.6 | 16.4 | 0.2 | D66173118EA7480BA527390ED5310EC1 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Vacaville | CA | 95687-3306 |  | 2013-07-10 | 2013-07-10 12:06 | 2013-07-10 12:06 | DAY & NIGHT - 24DNR-108C | 48 | 0 | Yes | Yes | 14.4 | 15.9 | -1.5 | DEF26197D90D4D61A255211F862C0110 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1116 |  | 2013-06-28 | 2013-06-28 09:00 | 2013-06-28 09:25 | AMERICAN STANDARD - 7A2048A100A2 | 142 | 6 | Yes | Yes | 23 | 17.2 | 5.8 | 6E01BE38ABDC4A0A8144C301F464A12F |  | R22 | TXV |  | 4.225% | 0.95775 | 8.12% | [5 empty] | TXV | 4.225%
Bakersfield | CA | 93301-2634 |  | 2013-09-25 | 2013-09-25 17:33 | 2013-09-25 17:58 | CARRIER - 48DC0U3 | 85 | 3.7 | Yes | Yes | 19.9 | 22.4 | -2.5 | 79812D8B25D647D0B8E66828645E2F66 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Vacaville | CA | 95687-7427 |  | 2013-07-05 | 2013-07-05 13:59 | 2013-07-05 14:15 | GOODMAN - CKJ36-1B | 97 | -3.7 | Yes | Yes | 14.8 | 17.7 | -2.9 | 9898A31E82CB4E149A8A93963429F744 |  | R22 | Non-TXV |  | -3.814% | 1.0381 | 1.068% |  |  |  |  | Non-TXV |  |  | -3.814%
Fresno | CA | 93722-6837 |  | 2013-07-01 | 2013-07-01 10:56 | 2013-07-01 11:32 | CARRIER - UNK | 80 | 11.8 | Yes | Yes | 23.6 | 20.4 | 3.2 | B44A50097A9D4AA2AE7BA76ABF42AF25 |  | R22 | Non-TXV |  | 14.75% | 0.8525 | 28.35% | [5 empty] | Non-TXV | 14.75%
Corcoran | CA | 93212-9643 |  | 2013-08-05 | 2013-08-05 12:07 | 2013-08-05 12:30 | TEMPSTAR - GPFM42K080F | 86 | 9.1 | Yes | Yes | 20.7 | 20.2 | 0.5 | 9DC66B15562347FCAE621971691A5F4C |  | R22 | Non-TXV |  | 10.58% | 0.89419 | 20.34% | [5 empty] | Non-TXV | 10.58%
San Jose | CA | 95135-1321 |  | 2013-07-25 | 2013-07-25 10:07 | 2013-07-25 10:07 | PAYNE - PA13NA024-B | 63 | 0 | Yes | Yes | 21.7 | 18.7 | 3 | D212A27F6A0745B3954A6CD83CA74023 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4519 |  | 2013-08-26 | 2013-08-26 08:44 | 2013-08-26 09:26 | YORK - D1NP030N05606A | 73 | 4 | Yes | Yes | 20.4 | 18.8 | 1.6 | 6B4417D5EA634602841A172D12142198 |  | R22 | Non-TXV |  | 5.479% | 0.94521 | 10.53% | [5 empty] | Non-TXV | 5.479%
Gilroy | CA | 95020-2501 |  | 2013-10-22 | 2013-10-22 13:00 | 2013-10-22 13:30 | BRYANT - 538JNX024000ABAA | 68 | -4.8 | Yes | Yes | 20.2 | 18.8 | 1.4 | 1219C30921F042BBA78C520C341091AD |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93706-5632 |  | 2013-07-26 | 2013-07-26 13:54 | 2013-07-26 14:36 | YORK - DAYAF036N070C | 67 | 20.5 | Yes | Yes | 20.3 | 18.8 | 1.5 | 1536E62C8E6C44CE9FF83EC33C98968B |  | R22 | Non-TXV |  | 30.6% | 0.69403 | 58.8% | [5 empty] | Non-TXV | 30.6%
San Jose | CA | 95111-3965 |  | 2013-09-18 | 2013-09-18 09:02 | 2013-09-18 09:39 | AMANA - ZRCF48016 | 70 | 2.2 | Yes | Yes | 19.4 | 20.4 | -1 | 67EC1E832F8E4FA7940F2F259B6929C9 |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Bakersfield | CA | 93313-5735 |  | 2013-07-21 | 2013-07-21 14:15 | 2013-07-21 14:41 | YORK - H3RC060S06G | 144 | 15.4 | Yes | Yes | 24.5 | 19.3 | 5.2 | 6DD2D330D5E4406CB833A8F368DAD59C |  | R22 | TXV |  | 10.69% | 0.89306 | 20.55% | [5 empty] | TXV | 10.69%
Fresno | CA | 93711-2118 |  | 2013-06-27 | 2013-06-27 10:28 | 2013-06-27 10:46 | CARRIER - 38TRA048360 | 85 | 5.8 | Yes | Yes | 22.6 | 18.5 | 4.1 | BEAC646A8A0A43B2B92DA91D2A9BA22D |  | R22 | TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | TXV | 6.824%
Vallejo | CA | 94589-1726 |  | 2013-07-24 | 2013-07-24 14:37 | 2013-07-24 14:37 | TRANE - TTPO42D100A0 | 139 | 0 | Yes | Yes | 14.9 | 15.2 | -0.3 | E618B333789847E19C21D278B367A3E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1866 |  | 2013-07-22 | 2013-07-22 20:08 | 2013-07-22 21:22 | PAYNE - PA12NA060 | 85 | 5 | Yes | Yes | 19.4 | 21.5 | -2.1 | D9F674EA0E2943AEB4B4CBDAF37453F5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Fresno | CA | 93704-3860 |  | 2013-10-10 | 2013-10-10 12:17 | 2013-10-10 12:36 | YORK - D1NH036N05606C | 108 | 4.8 | Yes | Yes | 23.9 | 18.7 | 5.2 | 6F291BC24D714258A23680008417BDCB |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Bakersfield | CA | 93307-6163 |  | 2013-08-08 | 2013-08-08 15:42 | 2013-08-08 15:42 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 64E50A82C33E41E59B17DC482396338D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2146 |  | 2013-07-16 | 2013-07-16 17:05 | 2013-07-16 17:29 | GOODMAN - CR421B | 95 | 19.3 | Yes | Yes | 19 | 19.7 | -0.7 | E9DC4652CDE44A7CA7C3090ACA8D02A8 |  | R22 | Non-TXV |  | 20.32% | 0.79684 | 39.04% | [5 empty] | Non-TXV | 20.32%
Shafter | CA | 93263-1866 |  | 2013-07-22 | 2013-07-22 19:57 | 2013-07-22 21:21 | OTHER - CA5548VKD2 | 85 | 5.5 | Yes | Yes | 20.3 | 21.8 | -1.5 | BC652D34841C48D3928AE51CEFB66C67 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | TXV | 6.471%
Arvin | CA | 93203-2065 |  | 2013-08-19 | 2013-08-19 14:39 | 2013-08-19 16:25 | GOODMAN - CPLE36 1A | 108 | 3.2 | Yes | Yes | 20.4 | 20.1 | 0.3 | 6ED4EFC0B9734659BD8CE16002A8D76C |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Sanger | CA | 93657-1919 |  | 2013-07-30 | 2013-07-30 12:07 | 2013-07-30 12:24 | OTHER - NA2342AKA100 | 114 | 4.6 | Yes | Yes | 20 | 19.6 | 0.4 | 0724DE3E3D3B48E8B8BB692AFE3C0580 |  | R22 | TXV |  | 4.035% | 0.95965 | 7.755% | [5 empty] | TXV | 4.035%
Fresno | CA | 93722-3505 |  | 2013-07-01 | 2013-07-01 17:52 | 2013-07-02 00:48 | - | 71 | 3.7 | Yes | Yes | 20 | 19.5 | 0.5 | C6C55090E93E4B45A070E904F563D4D4 |  | R22 | Non-TXV |  | 5.211% | 0.94789 | 10.01% | [5 empty] | Non-TXV | 5.211%
Fresno | CA | 93706-9265 |  | 2013-08-30 | 2013-08-30 11:03 | 2013-08-30 11:36 | GOODMAN - ERC00421BBB | 128 | 4.1 | Yes | Yes | 19.9 | 19.2 | 0.7 | 3F61D8CCC07740F3A35797F222D4FCD3 |  | R22 | Non-TXV |  | 3.203% | 0.96797 | 6.156% | [5 empty] | Non-TXV | 3.203%
Bakersfield | CA | 93304-1249 |  | 2013-09-21 | 2013-09-21 17:21 | 2013-09-21 17:21 | OTHER - UKN | 60 | 0 | Yes | Yes | 22.4 | 21.5 | 0.9 | 0FA983A157C344EF8096AD66860473C8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-9577 |  | 2013-07-15 | 2013-07-15 18:11 | 2013-07-15 18:11 | RHEEM - RAPC-060JAZ | 296 | 0 | Yes | Yes | 25.6 | 21.3 | 4.3 | 12E24B69C3CD484DAC8154F5AD94A54F |  | R22 | TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-7737 |  | 2013-08-22 | 2013-08-22 10:12 | 2013-08-22 10:13 | OTHER - H1RA042S06D | 84 | -6.9 | Yes | Yes | 18.9 | 17.9 | 1 | A3375B07FADA495BAA0C40C716340055 |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Fresno | CA | 93711-6156 |  | 2013-10-25 | 2013-10-25 13:29 | 2013-10-25 13:49 | YORK - D2YS018N03206A | 52 | 1.5 | Yes | Yes | 21.9 | 20.7 | 1.2 | 8403A485ED1F4E0493A9DE531A4673E6 |  | R22 | Non-TXV |  | 2.885% | 0.97115 | 5.544% | [5 empty] | Non-TXV | 2.885%
Fresno | CA | 93722-7351 |  | 2013-07-03 | 2013-07-03 12:20 | 2013-07-03 12:53 | LENNOX - 12GCS042-75-3PB | 133 | 4.3 | Yes | Yes | 22.8 | 18.5 | 4.3 | 06D294DD68024F1BAC08496E35860272 |  | R22 | Non-TXV |  | 3.233% | 0.96767 | 6.213% | [5 empty] | Non-TXV | 3.233%
Fresno | CA | 93711-6175 |  | 2013-09-27 | 2013-09-27 14:51 | 2013-09-27 15:21 | YORK - D2YS018N03206A | 52 | 2.5 | Yes | Yes | 20.2 | 19.4 | 0.8 | 8B406ECAF1604E059A842A88110486B4 |  | R22 | Non-TXV |  | 4.808% | 0.95192 | 9.239% | [5 empty] | Non-TXV | 4.808%
Bakersfield | CA | 93305-5260 |  | 2013-09-04 | 2013-09-04 19:29 | 2013-09-04 19:34 | OTHER - RPG10B24D050LA-9A | 52 | 4.2 | Yes | Yes | 23.2 | 22.1 | 1.1 | 26D71E448DCF48D9BF8023C9515BEBDC |  | R22 | Non-TXV |  | 8.077% | 0.91923 | 15.52% | [5 empty] | Non-TXV | 8.077%
Clovis | CA | 93612-2320 |  | 2013-10-30 | 2013-10-30 12:58 | 2013-10-30 13:18 | RHEEM - HBB0F036SB | 96 | 13.2 | Yes | Yes | 22.1 | 19.4 | 2.7 | D45B806939DF4FB0AB3F73E109E5117A |  | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Fresno | CA | 93722-3368 |  | 2013-07-01 | 2013-07-01 12:05 | 2013-07-01 13:07 | CARRIER - UNK | 88 | 2.8 | Yes | Yes | 17.5 | 20.1 | -2.6 | 900627928EF042A284AE562383D2CD74 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Fresno | CA | 93710-6117 |  | 2013-07-01 | 2013-07-01 15:55 | 2013-07-01 16:17 | LENNOX - 13GCSXA36068X230 | 125 | 10.8 | Yes | Yes | 18.4 | 16.6 | 1.8 | 51125B93CF2C4A37A74FAE8A50B2F510 |  | R410A | Non-TXV |  | 8.64% | 0.9136 | 16.6% | [5 empty] | Non-TXV | 8.64%
Bakersfield | CA | 93304-1842 |  | 2013-07-01 | 2013-07-01 19:20 | 2013-07-01 19:20 | TRANE - YCP042F1M0AC | 128 | 0 | Yes | Yes | 20.3 | 19.7 | 0.6 | 5445600898E0471B9D1267D6C3C03681 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-6159 |  | 2013-10-25 | 2013-10-25 14:02 | 2013-10-25 14:28 | YORK - 02Y6024N0326A | 85 | 9.4 | Yes | Yes | 26 | 20.4 | 5.6 | B0ED7E75B938463AA68DD3F567BAB158 |  | R22 | Non-TXV |  | 11.06% | 0.88941 | 21.25% | [5 empty] | Non-TXV | 11.06%
Fresno | CA | 93722-4203 |  | 2013-07-11 | 2013-07-11 14:51 | 2013-07-11 16:03 | YORK - D1NP036N05606A | 98 | 5.9 | Yes | Yes | 26.4 | 21.2 | 5.2 | AD572B6AF6844A69A900248144637342 |  | R22 | Non-TXV |  | 6.02% | 0.9398 | 11.57% | [5 empty] | Non-TXV | 6.02%
Bakersfield | CA | 93301-2635 |  | 2013-09-24 | 2013-09-24 16:45 | 2013-09-24 17:08 | OTHER - UNK | 85 | 6 | Yes | Yes | 17.4 | 20.4 | -3 | 11E14AB91F6A42F3B28DECB31091D8B9 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Fresno | CA | 93704-5618 |  | 2013-07-05 | 2013-07-05 14:20 | 2013-07-05 14:36 | GOODMAN - GPG12300701A | 73 | 12 | Yes | Yes | 24.6 | 19 | 5.6 | 728D411A2C384135A7B59F084CA19E1D |  | R22 | Non-TXV |  | 16.44% | 0.83562 | 31.59% | [5 empty] | Non-TXV | 16.44%
Reedley | CA | 93654-2314 |  | 2013-07-18 | 2013-07-18 12:21 | 2013-07-18 12:21 | TRANE - 2YCC3030A1075AA | 88 | 23.7 | Yes | Yes | 10.1 | 18.5 | -8.4 | 89E1FFC08DCA4B39AD2A702C82B3F315 | Add refrigerant: 23.7 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 26.93% | 0.73068 | 51.76% | [5 empty] | Non-TXV | 26.93%
Bakersfield | CA | 93301-1194 |  | 2013-06-26 | 2013-06-26 11:02 | 2013-06-26 13:03 | CARRIER - | 85 | 0 | Yes | Yes | 25.6 | 20.2 | 5.4 | 233DD70B73C5486B978035981F3500F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2725 |  | 2013-09-26 | 2013-09-26 22:10 | 2013-09-27 04:48 | OTHER - 2AC13B30P-B | 97 | 3.7 | Yes | Yes | 17.4 | 20.4 | -3 | 26D05287D2A14D99B5DB612811E1EEEC |  | R22 | Non-TXV |  | 3.814% | 0.96186 | 7.331% | [5 empty] | Non-TXV | 3.814%
Vallejo | CA | 94589-2197 |  | 2013-08-19 | 2013-08-19 13:08 | 2013-08-19 15:08 | DAY & NIGHT - | 85 | 5.9 | Yes | Yes | 13 | 14.8 | -1.8 | 870BB9F4008345E4A181365F4E0212F4 |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
Shafter | CA | 93263-2413 |  | 2013-07-24 | 2013-07-24 19:38 | 2013-07-24 20:01 | PAYNE - PY2PNB048090AAAA | 114 | 4.4 | Yes | Yes | 26.3 | 21.3 | 5.1 | 283EBBC6243F41A78B2E1A716394FF1F |  | R22 | TXV |  | 3.86% | 0.9614 | 7.417% | [5 empty] | TXV | 3.86%
Clovis | CA | 93611-0000 |  | 2013-06-26 | 2013-06-26 11:03 | 2013-06-26 11:26 | TRANE - WCC036F100BB | 131 | -9.2 | Yes | Yes | 21.5 | 20.1 | 1.4 | 5A219BAD5A4B4CDD93D908B727DDF36D |  | R22 | TXV |  | -7.023% | 1.0702 | 1.967% |  |  |  |  | TXV |  |  | -7.023%
Fresno | CA | 93722-2734 |  | 2013-10-31 | 2013-10-31 14:22 | 2013-10-31 14:59 | CARRIER - 38BRB036311 | 122 | 5.7 | Yes | Yes | 20.6 | 19.5 | 1.1 | E848A4CDBD6E49F9ACBAA7473B8941DB |  | R22 | TXV |  | 4.672% | 0.95328 | 8.979% | [5 empty] | TXV | 4.672%
Fresno | CA | 93710-4614 |  | 2013-07-01 | 2013-07-01 12:15 | 2013-07-01 12:41 | YORK - ACO30M1021A | 80 | 12.3 | Yes | Yes | 18.9 | 19.6 | -0.7 | A31D8E3567294B43BF3249EFE26A113E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.38% | 0.84625 | 29.55% | [5 empty] | Non-TXV | 15.38%
Fresno | CA | 93726-0225 |  | 2013-07-10 | 2013-07-10 10:17 | 2013-07-10 11:21 | JANITROL - UNK | 80 | 8 | Yes | Yes | 23.9 | 18.5 | 5.4 | 0E16F13D30584B82A59545732EE3719D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93309-5919 |  | 2013-09-05 | 2013-09-05 19:56 | 2013-09-05 19:58 | OTHER - 24ABS336A300 | 84 | 4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 5F051D8B01794D99B6FC4373955D2599 |  | R22 | TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | TXV | 4.762%
Vacaville | CA | 95687-4949 |  | 2013-07-05 | 2013-07-05 12:42 | 2013-07-05 13:06 | CARRIER - 38EB030600 | 81 | -4.6 | Yes | Yes | 14.9 | 17.2 | -2.3 | 0A28C602667F4BE988B8E299DB4F834D |  | R22 | Non-TXV |  | -5.679% | 1.0568 | 1.59% |  |  |  |  | Non-TXV |  |  | -5.679%
Fresno | CA | 93710-4334 |  | 2013-07-10 | 2013-07-10 16:08 | 2013-07-10 16:50 | AMANA - PGA36B0702C | 112 | 7.9 | Yes | Yes | 16.9 | 19.6 | -2.7 | 2BF6FD6B0A6149D2B6A8C797DFD75ECD |  | R22 | Non-TXV |  | 7.054% | 0.92946 | 13.56% | [5 empty] | Non-TXV | 7.054%
Corcoran | CA | 93212-2871 |  | 2013-07-05 | 2013-07-05 16:41 | 2013-07-05 17:04 | GOODMAN - GSC130301AB | 123 | 25.5 | Yes | Yes | 21.8 | 17.9 | 3.9 | 3C32421E47DC460EB064E25F71D5C47B |  | R22 | Non-TXV |  | 20.73% | 0.79268 | 39.84% | [5 empty] | Non-TXV | 20.73%
Fresno | CA | 93711-6161 |  | 2013-09-25 | 2013-09-25 13:09 | 2013-09-25 13:30 | YORK - DY2S024N03206A | 62 | 4.8 | Yes | Yes | 22 | 18.8 | 3.2 | 8DE040F60456449F8C33699253EFE920 |  | R22 | Non-TXV |  | 7.742% | 0.92258 | 14.88% | [5 empty] | Non-TXV | 7.742%
Fresno | CA | 93711-1501 |  | 2013-06-27 | 2013-06-27 16:19 | 2013-06-27 17:52 | CARRIER - UNK | 83 | -4.9 | Yes | Yes | 17.5 | 16.8 | 0.7 | E8412CD70D7942F9847F35781E179FAF |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Fresno | CA | 93725-1727 |  | 2013-09-12 | 2013-09-12 14:43 | 2013-09-12 23:16 | GOODMAN - GPG360701 | 85 | 3.5 | Yes | Yes | 22.3 | 20.1 | 2.2 | 492B74754E0743A999FF5EC2733E7620 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Shafter | CA | 93263-3529 |  | 2013-08-12 | 2013-08-12 21:51 | 2013-08-12 21:55 | GOODMAN - GPG10300701A | 50 | 2.3 | Yes | Yes | 22.5 | 20.2 | 2.3 | 6ED88C58E9564C76A2388DCBF0A73D6B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Shafter | CA | 93263-3529 |  | 2013-08-12 | 2013-08-12 21:58 | 2013-08-12 22:00 | GOODMAN - GPG10300701A | 50 | 2.9 | Yes | Yes | 21 | 21 | 0 | 25440F7B0BD347A698263AAC55D018D7 |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Fresno | CA | 93703-1734 |  | 2013-07-02 | 2013-07-02 16:33 | 2013-07-02 16:33 | RUUD - RRNLB042JK08Y | 112 | 0 | Yes | Yes | 20.5 | 18.6 | 1.9 | 5BB0942D2AB74CA097E31FEFBB7B4BA9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3735 |  | 2013-06-27 | 2013-06-27 16:46 | 2013-06-27 17:27 | - GCGD60S21S2B | 80 | -4 | Yes | Yes | 19.8 | 16.6 | 3.2 | 0776F7CC24C2406C974682C679B0EC42 |  | R22 | TXV |  | -5% | 1.05 | 1.4% |  |  |  |  | TXV |  |  | -5%
Fresno | CA | 93704-2634 |  | 2013-07-12 | 2013-07-12 16:28 | 2013-07-12 17:35 | - TCJD60S4153A | 86 | 3.1 | Yes | Yes | 25.8 | 20.4 | 5.4 | 52B7D0DE926B492B973B6DFF5395C7D1 |  | R410A | TXV |  | 3.605% | 0.96395 | 6.927% | [5 empty] | TXV | 3.605%
Clovis | CA | 93612-5826 |  | 2013-07-10 | 2013-07-10 18:27 | 2013-07-10 18:48 | DAY & NIGHT - 585HJ36060 | 102 | 3.4 | Yes | Yes | 23.4 | 19.9 | 3.5 | CEA898B05FAA433CB67A9DF26FC70715 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93705-3660 |  | 2013-07-02 | 2013-07-02 11:01 | 2013-07-02 11:32 | BRYANT - 583ANW02404NBAD | 55 | 6 | Yes | Yes | 15.5 | 18.3 | -2.8 | 80052FDF5D0B49C2B4310F090D9F0A24 |  | R22 | Non-TXV |  | 10.91% | 0.89091 | 20.96% | [5 empty] | Non-TXV | 10.91%
Bakersfield | CA | 93306-5940 |  | 2013-07-23 | 2013-07-23 10:59 | 2013-07-23 10:59 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.5 | 20.8 | 0.7 | 21B295A4CC5E434CA05D19B4BAA66CD2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-4717 |  | 2013-07-11 | 2013-07-11 14:46 | 2013-07-11 15:39 | ARMSTRONG - SCU12E36A-1 | 99 | 4.2 | Yes | Yes | 23.9 | 21.5 | 2.4 | 3FB7E91237024C64AEEE6339D8F28130 |  | R22 | TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | TXV | 4.242%
Fresno | CA | 93705-3839 |  | 2013-07-10 | 2013-07-10 09:16 | 2013-07-10 09:46 | COLEMAN - DAYPF042N080A | 150 | 6.5 | Yes | Yes | 19.8 | 19.3 | 0.5 | A0EEBF1F498944029269CCDC479BF229 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Fresno | CA | 93705-4442 |  | 2013-06-28 | 2013-06-28 12:25 | 2013-06-28 13:08 | YORK - D1NH04806506B | 124 | 4.3 | Yes | Yes | 22.2 | 18.8 | 3.4 | E62FA68FE4E24234A4CED0613B2EF0CF |  | R22 | Non-TXV |  | 3.468% | 0.96532 | 6.664% | [5 empty] | Non-TXV | 3.468%
Sanger | CA | 93657-9327 |  | 2013-07-29 | 2013-07-29 10:30 | 2013-07-29 10:58 | CARRIER - 585HJ042060 | 80 | 7.1 | Yes | Yes | 26.1 | 20.4 | 5.7 | EA48FD2D8C4C4BF3ACA4E37A944850EC |  | R22 | Non-TXV |  | 8.875% | 0.91125 | 17.06% | [5 empty] | Non-TXV | 8.875%
Clovis | CA | 93611-4564 |  | 2013-06-26 | 2013-06-26 09:33 | 2013-06-26 10:28 | COMFORT AIRE - PGF036K060 | 70 | 3.1 | Yes | Yes | 16.4 | 18.2 | -1.8 | E964CDA6F1534D74A3F8105D0E619A0E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Fresno | CA | 93722-5744 |  | 2013-07-09 | 2013-07-09 11:43 | 2013-07-09 12:50 | BRYANT - 574ANW036060NB | 131 | 4.1 | Yes | Yes | 26.5 | 20.5 | 6 | 2BF93D193BA841A9B81F35832951ECED |  | R22 | Non-TXV |  | 3.13% | 0.9687 | 6.015% | [5 empty] | Non-TXV | 3.13%
Vallejo | CA | 94589-1944 |  | 2013-07-16 | 2013-07-16 11:50 | 2013-07-16 11:52 | GOODMAN - GSC130361AA | 125 | 10.6 | Yes | Yes | 17.5 | 17.6 | -0.1 | 7DD08C9002B548D3A93365BC26ED40E6 |  | R22 | Non-TXV |  | 8.48% | 0.9152 | 16.3% | [5 empty] | Non-TXV | 8.48%
Vacaville | CA | 95687-4924 |  | 2013-07-05 | 2013-07-05 11:34 | 2013-07-05 12:02 | AMANA - RCC42A2A | 185 | 3.9 | Yes | Yes | 14.4 | 17.2 | -2.8 | 1ACAF5C0DA354CABADEE9B1C0EC1508F |  | R22 | Non-TXV |  | 2.108% | 0.97892 | 4.051% | [5 empty] | Non-TXV | 2.108%
Bakersfield | CA | 93306-3123 |  | 2013-08-23 | 2013-08-23 14:25 | 2013-08-23 14:25 | CARRIER - UKN | 90 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | DD08890B751B471882B2069592A663DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1211 |  | 2013-08-14 | 2013-08-14 10:23 | 2013-08-14 10:23 | AMERICAN STANDARD - 2A7A71036A1000AA | 73 | 0 | Yes | Yes | 14.4 | 17.2 | -2.8 | 9B6B6AECAC6448A98CBE17F1024773D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9710 |  | 2013-07-23 | 2013-07-23 16:51 | 2013-07-23 16:51 | DAY & NIGHT - N4A348AKB200 | 112 | 0 | Yes | Yes | 34.9 | 20.2 | 14.8 | AB948FB709F248558A03076DFAD2E2B3 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2080 |  | 2013-10-04 | 2013-10-04 08:33 | 2013-10-04 08:33 | GE - BTD748A100A0 | 152 | 0 | Yes | Yes | 18.9 | 16.5 | 2.4 | 654D7BBE3CCA45BF95A59C66571F4187 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6260 |  | 2013-08-23 | 2013-08-23 15:53 | 2013-08-23 15:53 | RUUD - URKA-A024JK06A | 50 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 4DEB42CD24DB4EEB8C68714D3712A9BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-4093 |  | 2013-07-10 | 2013-07-10 12:23 | 2013-07-10 12:45 | CARRIER - 591ANX060000AAAA | 222 | 10.3 | Yes | Yes | 17.1 | 17.6 | -0.5 | 37DC94CEAF504E5AB7D8559A29E62B95 |  | R22 | Non-TXV |  | 4.64% | 0.9536 | 8.916% | [5 empty] | Non-TXV | 4.64%
Fairfield | CA | 94533-2760 |  | 2013-07-22 | 2013-07-22 12:31 | 2013-07-22 14:45 | - BRCQ0361BD | 52 | 3.1 | Yes | Yes | 15.2 | 18.2 | -3 | 4142FA3117AF4940B8F567E82C57F034 |  | R22 | Non-TXV |  | 5.962% | 0.94038 | 11.46% | [5 empty] | Non-TXV | 5.962%
Fresno | CA | 93711-2012 |  | 2013-08-23 | 2013-08-23 11:43 | 2013-08-23 11:43 | - 597BN060-A | 224 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 4F0ED0C6566849E2A740FD4B1EC96001 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5957 |  | 2013-07-11 | 2013-07-11 14:11 | 2013-07-11 14:11 | TEMPSTAR - N4A336AKB200 | 84 | 0 | Yes | Yes | 14.7 | 16.5 | -1.8 | 84633A9B770B4A68A4D8C7CCB92720E1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2794 |  | 2013-08-05 | 2013-08-05 12:59 | 2013-08-05 13:19 | GOODMAN - GPG13240451A | 77 | 5.5 | Yes | Yes | 27.1 | 21.7 | 5.4 | 4FD4BAD2B56C40EB88F7D39A897469EB |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Arvin | CA | 93203-2794 |  | 2013-08-05 | 2013-08-05 13:21 | 2013-08-05 14:05 | GOODMAN - GPG13240451A | 72 | 2.5 | Yes | Yes | 26.1 | 20.2 | 6 | 67A545AFF78E43D2AE1755AB78135BC3 |  | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Bakersfield | CA | 93313-2512 |  | 2013-07-09 | 2013-07-09 18:21 | 2013-07-09 18:58 | GOODMAN - PGP15421141AB | 85 | 0 | Yes | Yes | 31.3 | 21.4 | 9.9 | EEA622861DC84AEDB4E9A47036E6161F | Add refrigerant: 12.3 oz | R410A | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-6649 |  | 2013-08-14 | 2013-08-14 14:02 | 2013-08-14 14:02 | OTHER - AC1BNX024000AAAA | 96 | 0 | Yes | Yes | 18.1 | 18.6 | -0.5 | 894C0E77CF774322B2827534E0213311 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-2818 |  | 2013-10-02 | 2013-10-02 10:35 | 2013-10-02 11:17 | CARRIER - 38TH036300 | 83 | -5.9 | Yes | Yes | 19 | 17.2 | 1.8 | A995BBF99FDF4FEA84CBDEC64CF0DAD8 |  | R22 | TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | TXV |  |  | -7.108%
Bakersfield | CA | 93306-6045 |  | 2013-09-16 | 2013-09-16 16:37 | 2013-09-16 16:37 | TRANE - 2CYX3048A1096AA | 144 | 0 | Yes | Yes | 22.4 | 22.1 | 0.3 | B9EF43EDFF304DE58DE5B70E55A9DA4C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4837 |  | 2013-10-09 | 2013-10-09 12:51 | 2013-10-09 12:51 | YORK - H4DB024S06A | 58 | 0 | Yes | Yes | 18.3 | 16.6 | 1.8 | 4C27F758E077433D80543C3249071D72 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-6372 |  | 2013-07-03 | 2013-07-03 10:42 | 2013-07-03 11:24 | OTHER - 598ANX03600ABAA | 178 | 5.7 | Yes | Yes | 19.4 | 17.5 | 1.9 | 5516883A39AE476DAAC7D6CCAEC07C38 |  | R22 | Non-TXV |  | 3.202% | 0.96798 | 6.154% | [5 empty] | Non-TXV | 3.202%
Bakersfield | CA | 93313-5235 |  | 2013-07-16 | 2013-07-16 10:17 | 2013-07-16 11:07 | OTHER - 113RNAU36-B | 85 | 2.9 | Yes | Yes | 17 | 19.2 | -2.2 | 42F58D7897D14802BEDB7D954B8A4978 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
San Jose | CA | 95138-1351 |  | 2013-07-25 | 2013-07-25 10:38 | 2013-07-25 11:01 | CARRIER - 38HDC030321 | 82 | 14.6 | Yes | Yes | 19 | 18.1 | 0.9 | 415C0A4E68E3404685B1F0FB3B033F43 |  | R22 | Non-TXV |  | 17.8% | 0.82195 | 34.22% | [5 empty] | Non-TXV | 17.8%
Kerman | CA | 93630-1230 |  | 2013-07-09 | 2013-07-09 14:30 | 2013-07-09 15:03 | COLEMAN - DAYPF036N070A | 108 | 6.2 | Yes | Yes | 17.5 | 19.3 | -1.8 | 57DB1EBF39624F1DBF22732E47D6A2B5 |  | R22 | TXV |  | 5.741% | 0.94259 | 11.03% | [5 empty] | TXV | 5.741%
Fresno | CA | 93711-1581 |  | 2013-07-04 | 2013-07-04 11:38 | 2013-07-04 11:38 | YORK - D245030N04506A | 76 | 0 | Yes | Yes | 21 | 22 | -1 | CB6FF68EB4254F3399467E8163AF5585 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2434 |  | 2013-06-26 | 2013-06-26 08:40 | 2013-06-26 09:01 | YORK - D2NP024N03606A | 100 | 4.6 | Yes | Yes | 23.4 | 19.3 | 4.2 | 069AB2E65C444A3BBCF71DF64CB961AA |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Arvin | CA | 93203-9452 |  | 2013-08-20 | 2013-08-20 14:53 | 2013-08-20 16:49 | GOODMAN - GSC13048LAF | 152 | -8.9 | Yes | Yes | 17.6 | 19.6 | -2 | 03E3A44B25AD48B780D5F2F7ABA7B389 |  | R22 | Non-TXV |  | -5.855% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.855%
Bakersfield | CA | 93308-4857 |  | 2013-10-22 | 2013-10-22 18:06 | 2013-10-22 18:25 | OTHER - UKN | 90 | 9 | Yes | Yes | 20.6 | 22.6 | -2 | 3C17C7E9DE34435FAA420354F59F2B48 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93710-4841 |  | 2013-07-09 | 2013-07-09 16:31 | 2013-07-09 18:11 | COMFORT AIRE - NAC242AKC3 | 127 | 7.4 | Yes | Yes | 21.4 | 19.5 | 1.9 | 35A0B63467954B45A65EBCC5A0868E68 |  | R22 | Non-TXV |  | 5.827% | 0.94173 | 11.2% | [5 empty] | Non-TXV | 5.827%
Bakersfield | CA | 93313-5137 |  | 2013-07-15 | 2013-07-15 15:22 | 2013-07-15 15:54 | OTHER - 38CK042301 | 90 | 5.9 | Yes | Yes | 19.8 | 18.6 | 1.2 | A7E553F77CE544A8968C03693BAD8486 |  | R22 | TXV |  | 6.556% | 0.93444 | 12.6% | [5 empty] | TXV | 6.556%
Fresno | CA | 93723-9296 |  | 2013-10-02 | 2013-10-02 09:54 | 2013-10-02 10:35 | TRANE - YCC042F1M0BF | 104 | 3.5 | Yes | Yes | 20.2 | 18.2 | 2 | 2A9106278BAD4DA79685A9AE9A0B58C6 |  | R22 | Non-TXV |  | 3.365% | 0.96635 | 6.468% | [5 empty] | Non-TXV | 3.365%
Bakersfield | CA | 93306-6219 |  | 2013-07-23 | 2013-07-23 12:31 | 2013-07-23 12:31 | YORK - D1NA030N0G606C | 76 | 0 | Yes | Yes | 21.9 | 21.4 | 0.5 | 1DECDB933BA642F5A3B1CA9903613083 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1836 |  | 2013-07-29 | 2013-07-29 18:24 | 2013-07-29 18:56 | BDP - 5850J036075 | 84 | 4.9 | Yes | Yes | 25.3 | 20.4 | 4.9 | BECB18A300924819B7356D5FC885A004 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Milpitas | CA | 95035-4502 |  | 2013-09-26 | 2013-09-26 17:55 | 2013-09-26 18:11 | GOODMAN - YCJD60S41WS1C | 86 | 2.7 | Yes | Yes | 19.8 | 21 | -1.2 | 4AE9FE743118403FBCAC62CF8EC19C59 |  | R410A | Non-TXV |  | 3.14% | 0.9686 | 6.033% | [5 empty] | Non-TXV | 3.14%
Bakersfield | CA | 93313-4619 |  | 2013-07-15 | 2013-07-15 11:32 | 2013-07-15 12:46 | OTHER - 24ABB360W310 | 85 | -4.1 | Yes | Yes | 20.5 | 19.7 | 0.8 | 9A8F25CE58A34475B83554EAB6B10F6E |  | R410A | Non-TXV |  | -4.824% | 1.0482 | 1.351% |  |  |  |  | Non-TXV |  |  | -4.824%
Bakersfield | CA | 93306-4840 |  | 2013-07-22 | 2013-07-22 19:48 | 2013-07-22 19:48 | BRYANT - 583ANW036090AAAF | 82 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 91891E8A17ED4DF587D651EDBE39C4CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1314 |  | 2013-07-25 | 2013-07-25 10:07 | 2013-07-25 10:08 | KENMORE - TCA024AKA1 | 69 | -6.5 | Yes | Yes | 17.3 | 17.6 | -0.3 | 0DFDF68EF1B147BAA41D734D39E3CD8D |  | R22 | Non-TXV |  | -9.42% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.42%
Bakersfield | CA | 93307-3202 |  | 2013-07-25 | 2013-07-25 18:32 | 2013-07-25 19:03 | YORK - D1NH060N09006C | 140 | 25.2 | Yes | Yes | 22.2 | 22.6 | -0.4 | 6A41E060AF724E1BBA1D7C4247562A63 |  | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Bakersfield | CA | 93307-7171 |  | 2013-07-30 | 2013-07-30 10:35 | 2013-07-30 10:35 | RUUD - UAKA-037JAZ | 79 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | FA8A7E7F7CF248448CF7A3298750B376 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2065 |  | 2013-09-09 | 2013-09-09 14:34 | 2013-09-09 15:52 | GOODMAN - CPLE36 1A | 120 | 6.6 | Yes | Yes | 22.6 | 20.1 | 2.5 | C1D0077250C2496695295FE607F8D226 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Fresno | CA | 93722-2900 |  | 2013-07-11 | 2013-07-11 16:15 | 2013-07-11 17:47 | DAY & NIGHT - 8KLA136300B | 98 | 4.9 | Yes | Yes | 21.9 | 21.5 | 0.4 | 4EA79DD0D91745EA8040562D26AB0008 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Anderson | CA | 96007-9139 |  | 2013-07-11 | 2013-07-11 08:50 | 2013-07-11 09:14 | ARMSTRONG - SCU12E42A-2 | 115 | 10.8 | Yes | Yes | 26.8 | 21 | 5.8 | 0534D74A4AB74CF0B6F52FAA6C536D2D |  | R22 | Non-TXV |  | 9.391% | 0.90609 | 18.05% | [5 empty] | Non-TXV | 9.391%
San Jose | CA | 95133-1910 |  | 2013-07-25 | 2013-07-25 11:39 | 2013-07-25 11:42 | COLEMAN - BRCQ0361CB | 56 | 2.2 | Yes | Yes | 18.2 | 17.6 | 0.6 | 0730D45B0D6B4C49A67D9C6481BE7397 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Fresno | CA | 93702-4475 |  | 2013-06-26 | 2013-06-26 13:50 | 2013-06-26 13:50 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F6A4569221B245B5851F6ACAC3EF88AE | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-0000 |  | 2013-07-12 | 2013-07-12 10:25 | 2013-07-12 10:54 | GOODMAN - GSG130601BB | 175 | -38.7 | Yes | Yes | 21.7 | 20.4 | 1.3 | C2B73F2AB2404B64B23661ECE9B99B68 |  | R22 | TXV |  | -22.11% | 1.2211 | 6.193% |  |  |  |  | TXV |  |  | -22.11%
Pittsburg | CA | 94565-5612 |  | 2013-07-15 | 2013-07-15 13:57 | 2013-07-15 16:01 | RHEEM - AT-48B1 | 55 | 0 | Yes | Yes | 14.2 | 18 | -3.8 | A2F0FC39950B4BE3862CBF0AB9E270CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4837 |  | 2013-07-24 | 2013-07-24 17:52 | 2013-07-24 18:43 | GOODMAN - GSC130421AC | 137 | -8.1 | Yes | Yes | 21.2 | 17.1 | 4.1 | 82B0C0777E3841108E52953C97CB3DB3 |  | R22 | Non-TXV |  | -5.912% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.912%
Bakersfield | CA | 93307-6855 |  | 2013-07-30 | 2013-07-30 11:31 | 2013-07-30 12:08 | YORK - D1NH036N05606C | 108 | 18 | Yes | Yes | 21.6 | 21.3 | 0.4 | 88C26EF07F844862B046F4996658145D |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Bakersfield | CA | 93313-5803 |  | 2013-07-19 | 2013-07-19 09:52 | 2013-07-19 09:52 | GIBSON - JS3BC036KA | 82 | -28.3 | Yes | Yes | 22 | 21 | 1 | 8A1BF4B737644C6FB8DC3D28F0E43080 | Remove refrigerant: 28.3 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -34.51% | 1.3451 | 9.665% |  |  |  |  | TXV |  |  | -34.51%
Fresno | CA | 93711-1949 |  | 2013-07-11 | 2013-07-11 15:21 | 2013-07-11 15:39 | CARRIER - 38EH060330 | 233 | -9 | Yes | Yes | 22 | 22.8 | -0.8 | 374BD1AC8ACB4304B9D1DB05BD762CF0 |  | R22 | TXV |  | -3.863% | 1.0386 | 1.082% |  |  |  |  | TXV |  |  | -3.863%
Kingsburg | CA | 93631-1050 |  | 2013-07-15 | 2013-07-15 12:07 | 2013-07-15 12:47 | RUUD - UNK | 67 | 7.2 | Yes | Yes | 24.7 | 22 | 2.7 | 46AE31E5266144C58DD270BDF30927DB |  | R22 | Non-TXV |  | 10.75% | 0.89254 | 20.65% | [5 empty] | Non-TXV | 10.75%
Davis | CA | 95618-4454 |  | 2013-07-12 | 2013-07-12 12:35 | 2013-07-12 13:00 | OTHER - JT5BD-018K | 93 | 4.1 | Yes | Yes | 21.9 | 21.3 | 0.6 | 3674C9A7451A4038BD3F9F85B241C2DD |  | R22 | Non-TXV |  | 4.409% | 0.95591 | 8.472% | [5 empty] | Non-TXV | 4.409%
Fresno | CA | 93701-1219 |  | 2013-06-27 | 2013-06-27 10:51 | 2013-06-27 11:19 | YORK - DCYP-F024N045A | 100 | -5.9 | Yes | Yes | 18 | 17.6 | 0.4 | F4830AC9F13E4AF4A2B97E8E8E0FF71D |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Vacaville | CA | 95687-6794 |  | 2013-07-17 | 2013-07-17 10:29 | 2013-07-17 10:51 | JANITROL - UKN | 85 | -8 | Yes | Yes | 23.5 | 22.1 | 1.4 | C7B5D65C57C643EEB58D6EF43C78DEFF |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Kingsburg | CA | 93631-1051 |  | 2013-07-12 | 2013-07-12 11:55 | 2013-07-12 12:21 | RUUD - UNK | 70 | -6.6 | Yes | Yes | 23.3 | 20.1 | 3.2 | DDFD37EE4A824320815A102265C3D671 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Bakersfield | CA | 93304-2623 |  | 2013-07-01 | 2013-07-01 16:25 | 2013-07-01 16:42 | YORK - D1NH036N05606C | 111 | 15.5 | Yes | Yes | 18.1 | 20.1 | -2 | 4C0950BD56674E839F4754A36FB422BB |  | R22 | Non-TXV |  | 13.96% | 0.86036 | 26.84% | [5 empty] | Non-TXV | 13.96%
Bakersfield | CA | 93304-4518 |  | 2013-09-04 | 2013-09-04 09:26 | 2013-09-04 09:45 | OTHER - UKN | 90 | 9.6 | Yes | Yes | 22.3 | 22.1 | 0.2 | F7E0DFBB4B6B457E9E6216FC20E391FA |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Lamont | CA | 93241-2716 |  | 2013-09-12 | 2013-09-12 14:21 | 2013-09-12 14:38 | DUCANE - 2AC13B24P2B | 89 | 2.7 | Yes | Yes | 20 | 20.2 | -0.2 | D280853E9F2E4511B63B23BB08BE42CF |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
San Jose | CA | 95111-3549 |  | 2013-08-01 | 2013-08-01 11:09 | 2013-08-01 11:09 | PAYNE - PA13NA036-C | 131 | 0 | Yes | Yes | 18.7 | 16.8 | 1.9 | 3753AB67AFB245AE865DAA297C25F4A8 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-9759 |  | 2013-07-01 | 2013-07-01 17:42 | 2013-07-01 17:42 | OTHER - WPH324400RKC1 | 150 | 0 | Yes | Yes | 24.8 | 22 | 2.8 | FB5EE17E6A9146FFA0B477B5467CBE0C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-9759 |  | 2013-07-01 | 2013-07-01 17:49 | 2013-07-01 17:49 | OTHER - WPH324400RKC1 | 150 | 0 | Yes | Yes | 17.4 | 17.5 | -0.1 | 4C103839591644BD8EEFDB8B2AA49E51 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93723-9211 |  | 2013-08-29 | 2013-08-29 09:35 | 2013-08-29 10:08 | YORK - D1NA036N05606C | 67 | 2 | Yes | Yes | 18.4 | 19.9 | -1.5 | 83FF43FB582D4B4CAB8F1962078D9263 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Fresno | CA | 93723-9211 |  | 2013-08-29 | 2013-08-29 10:50 | 2013-08-29 11:13 | YORK - D1NA024N03606C | 54 | 1.6 | Yes | Yes | 22.8 | 20.7 | 2.1 | A2EB73974C274D1AA7CE4FA9DC1A52C1 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93711-1654 |  | 2013-07-16 | 2013-07-16 15:15 | 2013-07-16 15:15 | CARRIER - 38TDB60310 | 219 | 0 | Yes | Yes | 21.9 | 20.7 | 1.2 | 5C0DE006B10E497BA416645BB2155539 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5808 |  | 2013-08-09 | 2013-08-09 16:41 | 2013-08-09 17:25 | COLEMAN - ERCQ0481BBB | 134 | 26.7 | Yes | Yes | 25.8 | 20.4 | 5.4 | 382AE8BC83904D5DA5A65F566C0DD31D |  | R22 | Non-TXV |  | 19.93% | 0.80075 | 38.29% | [5 empty] | Non-TXV | 19.93%
Kingsburg | CA | 93631-1050 |  | 2013-07-15 | 2013-07-15 09:22 | 2013-07-15 10:13 | RUUD - UNK | 67 | 14.3 | Yes | Yes | 20.3 | 20.4 | -0.1 | 02EC19F29C6748FE8DD84DE3283E1FB5 |  | R22 | Non-TXV |  | 21.34% | 0.78657 | 41.02% | [5 empty] | Non-TXV | 21.34%
Brentwood | CA | 94513-1602 |  | 2013-07-03 | 2013-07-03 12:48 | 2013-07-03 12:48 | AMANA - PGD36C0902E | 110 | 0 | Yes | Yes | 17.8 | 17.7 | 0.1 | 3CA3A7A99D6047CDA77306C5D42002C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1303 |  | 2013-08-01 | 2013-08-01 09:37 | 2013-08-01 10:21 | YORK - H1RA024S06D | 59 | 5.6 | Yes | Yes | 21.3 | 19.1 | 2.2 | 19B06FAC7BD843C7BF9774C789AC4744 |  | R22 | Non-TXV |  | 9.492% | 0.90508 | 18.24% | [5 empty] | Non-TXV | 9.492%
Vacaville | CA | 95687-6421 |  | 2013-07-05 | 2013-07-05 14:38 | 2013-07-05 14:38 | TRANE - 2TTX4036A1000AA | 118 | 0 | Yes | Yes | 16 | 16.4 | -0.4 | B828FA69E6F14CC0AC0D9AD9794E332F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4454 |  | 2013-09-26 | 2013-09-26 12:48 | 2013-09-26 15:45 | GOODMAN - GSH1301818A | 127 | 4.4 | Yes | Yes | 14.7 | 17.7 | -3 | F6F71FBBC5BA4E9B84EBEA1173A02948 |  | R22 | Non-TXV |  | 3.465% | 0.96535 | 6.658% | [5 empty] | Non-TXV | 3.465%
Bakersfield | CA | 93313-5245 |  | 2013-07-24 | 2013-07-24 12:35 | 2013-07-24 13:36 | YORK - H1RD042S06G | 152 | 13.1 | Yes | Yes | 16.9 | 18.6 | -1.7 | 9CA7A95FD5684ACFACBD32580315F19C |  | R22 | TXV |  | 8.618% | 0.91382 | 16.56% | [5 empty] | TXV | 8.618%
Fresno | CA | 93725-1890 |  | 2013-08-30 | 2013-08-30 12:12 | 2013-08-30 13:23 | GOODMAN - GPG13360451AB | 112 | 3.8 | Yes | Yes | 21.1 | 21 | 0.1 | 1A5D0830F9874FF487FCB85F0AB79B9A |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
San Jose | CA | 95133-2015 |  | 2013-09-25 | 2013-09-25 10:15 | 2013-09-25 10:15 | - 7A0036A100A1 | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | A776917A96064BC6BB2D9BF92240C1F4 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0206 |  | 2013-07-05 | 2013-07-05 09:20 | 2013-07-05 09:55 | YORK - H1CB036S06A | 94 | 13.7 | Yes | Yes | 20.2 | 19.9 | 0.3 | DD6755E6170645418B41CD748AB61B86 |  | R22 | Non-TXV |  | 14.57% | 0.85426 | 28.01% | [5 empty] | Non-TXV | 14.57%
Bakersfield | CA | 93313-4563 |  | 2013-07-24 | 2013-07-24 13:31 | 2013-07-24 14:38 | OTHER - AH048GA2 | 162 | 9 | Yes | Yes | 22.1 | 20.2 | 1.9 | 3FE42FE622E04C77896797DA600F428D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Fairfield | CA | 94533-2530 |  | 2013-10-11 | 2013-10-11 13:00 | 2013-10-11 13:00 | TRANE - BFD7184100B0 | 45 | 0 | Yes | Yes | 19 | 22 | -3 | ADFACCC71E7943BB8507FF0D30A46CE8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-4602 |  | 2013-07-01 | 2013-07-01 13:34 | 2013-07-01 14:04 | LENNOX - 12ACB484P | 174 | 6.3 | Yes | Yes | 19.4 | 19.9 | -0.5 | 07497205BB154FA1B490448F7439FC47 |  | R22 | TXV |  | 3.621% | 0.96379 | 6.958% | [5 empty] | TXV | 3.621%
Bakersfield | CA | 93304-6340 |  | 2013-07-03 | 2013-07-03 18:38 | 2013-07-03 18:38 | BDP - 595A024055YAC | 51 | 0 | Yes | Yes | 19.3 | 19.5 | -0.2 | EF367658160246B0A73549E66A6D287A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9632 |  | 2013-08-20 | 2013-08-20 10:56 | 2013-08-20 11:35 | RUUD - UNK | 70 | -4.9 | Yes | Yes | 18.7 | 17.9 | 0.8 | D24DAF851C8148819BDBA21DEFFADA75 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93711-1951 |  | 2013-06-27 | 2013-06-27 11:14 | 2013-06-27 11:40 | OTHER - UNK | 80 | -7.5 | Yes | Yes | 21.3 | 17.7 | 3.6 | D724EF79A35B477EA819CC21070E243B |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Fresno | CA | 93722-2259 |  | 2013-07-08 | 2013-07-08 10:51 | 2013-07-08 11:09 | OTHER - FADC060JAS | 112 | 6.2 | Yes | Yes | 23.2 | 19.3 | 3.9 | 2C2B98C8071D44DBBD561E6F8325D64B |  | R22 | Non-TXV |  | 5.536% | 0.94464 | 10.64% | [5 empty] | Non-TXV | 5.536%
Fresno | CA | 93723-9265 |  | 2013-07-01 | 2013-07-01 13:25 | 2013-07-01 13:49 | YORK - D2NP048N09006A | 132 | 5.8 | Yes | Yes | 24.8 | 19.5 | 5.3 | AB2BEC2C19A44C529509B397C043B6B0 |  | R22 | Non-TXV |  | 4.394% | 0.95606 | 8.444% | [5 empty] | Non-TXV | 4.394%
Antioch | CA | 94531-6685 |  | 2013-07-09 | 2013-07-09 09:45 | 2013-07-09 09:46 | GOODMAN - CK42-1C | 92 | -6.5 | Yes | Yes | 18.3 | 17.6 | 0.7 | 4A428999A1B349888E6220DA8EEF75E8 |  | R22 | Non-TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.065%
Parlier | CA | 93648-9633 |  | 2013-08-21 | 2013-08-21 12:27 | 2013-08-21 13:11 | RUUD - UAMA024JAZ | 85 | 4.3 | Yes | Yes | 18.5 | 19.3 | -0.8 | 82EAFBCAB2554A13821DF6C4A79BF70C |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Fresno | CA | 93722-3149 |  | 2013-07-01 | 2013-07-01 13:48 | 2013-07-01 14:26 | - HBBD-F036SB | 96 | 0 | Yes | Yes | 19.8 | 19.8 | 0 | B0A0CADDB9AC4A2F8FFB1E3786D9EE63 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1906 |  | 2013-06-27 | 2013-06-27 13:33 | 2013-07-24 22:51 | RHEEM - RRNLB048JK10X | 161 | 24.4 | Yes | Yes | 21.9 | 18.5 | 3.4 | 1EA71818C0944B9C8CC766DD00541B23 |  | R410A | TXV |  | 15.16% | 0.84845 | 29.13% | [5 empty] | TXV | 15.16%
Lemoore | CA | 93245-2307 |  | 2013-07-08 | 2013-07-08 17:25 | 2013-07-08 17:46 | COMFORT AIRE - UNK | 76 | 12.3 | Yes | Yes | 20.4 | 15.9 | 4.5 | 9C0998F68CE146159E2B6075067A9621 |  | R22 | Non-TXV |  | 16.18% | 0.83816 | 31.1% | [5 empty] | Non-TXV | 16.18%
Parlier | CA | 93648-9629 |  | 2013-08-20 | 2013-08-20 10:11 | 2013-08-20 10:36 | RUUD - UNK | 80 | -4.7 | Yes | Yes | 18.1 | 19.8 | -1.7 | B182FD292BEA4518AC92478260D84203 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Wasco | CA | 93280-2564 |  | 2013-07-20 | 2013-07-20 16:13 | 2013-07-20 16:33 | HEIL - HARHF036N060B | 112 | 4.7 | Yes | Yes | 27.3 | 22 | 5.3 | AF3E6A0DD4504D85A1624AA1E5D1A9DE |  | R22 | TXV |  | 4.196% | 0.95804 | 8.065% | [5 empty] | TXV | 4.196%
Fairfield | CA | 94533-2573 |  | 2013-09-13 | 2013-09-13 09:48 | 2013-09-13 09:49 | TRANE - BTD718A100B0 | 46 | 2.1 | Yes | Yes | 17.4 | 17.6 | -0.2 | 80575AF68ED843989F984D82D3D1366F |  | R22 | Non-TXV |  | 4.565% | 0.95435 | 8.773% | [5 empty] | Non-TXV | 4.565%
San Jose | CA | 95138-1501 |  | 2013-10-17 | 2013-10-17 13:46 | 2013-10-17 15:05 | DAY & NIGHT - N4A336AKB200 | 83 | -6.8 | Yes | Yes | 20.7 | 20.4 | 0.3 | F999229D2DF44E6491E38B8D932942FF |  | R22 | Non-TXV |  | -8.193% | 1.0819 | 2.294% |  |  |  |  | Non-TXV |  |  | -8.193%
Fairfield | CA | 94533-2578 |  | 2013-07-22 | 2013-07-22 13:00 | 2013-07-22 14:47 | TRANE - TTR018D100A2 | 56 | 2.4 | Yes | Yes | 20.2 | 19.1 | 1.1 | 9AB1202A054041A0A9CF022A595FD6B9 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Fresno | CA | 93705-4851 |  | 2013-06-28 | 2013-06-28 10:35 | 2013-06-28 11:16 | CONCORD - RPG12B36D050A | 110 | 6.7 | Yes | Yes | 22.3 | 22 | 0.3 | 887A356D882D4C0DBF8746A81119123A |  | R22 | Non-TXV |  | 6.091% | 0.93909 | 11.71% | [5 empty] | Non-TXV | 6.091%
Parlier | CA | 93648-9625 |  | 2013-08-19 | 2013-08-19 10:35 | 2013-08-19 10:53 | RUUD - UNK | 80 | -5.6 | Yes | Yes | 17.9 | 19.2 | -1.3 | 6B6EF8B14A0B4E50923000FA4D3E453E |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Parlier | CA | 93648-9629 |  | 2013-08-21 | 2013-08-21 11:43 | 2013-08-21 12:22 | RUUD - UNK | 70 | 3.1 | Yes | Yes | 18.9 | 19.4 | -0.5 | 3C3E4D3AD67C4806B138113A6B475BE7 |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Fresno | CA | 93705-4545 |  | 2013-07-06 | 2013-07-06 09:11 | 2013-07-06 09:11 | GOODMAN - GPG13240451BB | 77 | 9.6 | Yes | Yes | 28 | 19.3 | 8.7 | 5D2C7E561DED4084A15C0E267502D173 | Add refrigerant: 9.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.47% | 0.87532 | 23.96% | [5 empty] | Non-TXV | 12.47%
Clovis | CA | 93612-5047 |  | 2013-07-31 | 2013-07-31 13:29 | 2013-07-31 14:40 | RHEEM - RRPLB042JK08X | 112 | 7.1 | Yes | Yes | 22.6 | 21.3 | 1.3 | 388A9580E27440F5A288E538D1CA73EA |  | R410A | TXV |  | 6.339% | 0.93661 | 12.18% | [5 empty] | TXV | 6.339%
Shafter | CA | 93263-2906 |  | 2013-08-09 | 2013-08-09 14:33 | 2013-08-09 14:36 | HEIL - GPCMB30K060F | 68 | -16.3 | Yes | Yes | 22 | 20.6 | 1.4 | F65D151C00734EBA9C0DFABE86FAF236 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -23.97% | 1.2397 | 6.713% |  |  |  |  | Non-TXV |  |  | -23.97%
Parlier | CA | 93648-9630 |  | 2013-08-20 | 2013-08-20 14:25 | 2013-08-20 14:57 | RUUD - UNK | 70 | -4.9 | Yes | Yes | 20 | 19.3 | 0.7 | D88BE72A59AB4471BD27A3934A991E42 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93705-4547 |  | 2013-06-28 | 2013-06-28 09:10 | 2013-06-28 09:42 | OTHER - UKN | 80 | -4.7 | Yes | Yes | 20 | 18.8 | 1.2 | E1B1FF069A694F93B8CD9C7B629E8E53 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Parlier | CA | 93648-9628 |  | 2013-08-19 | 2013-08-19 12:45 | 2013-08-19 13:20 | OTHER - TZAA-330-2A | 98 | -6.9 | Yes | Yes | 16.2 | 18.3 | -2.1 | 3C2C2FE9CC754CF68F16C749A8D2178F |  | R22 | Non-TXV |  | -7.041% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.041%
San Jose | CA | 95127-2030 |  | 2013-10-07 | 2013-10-07 17:47 | 2013-10-07 18:44 | AMANA - RCB48B2A | 112 | 9.9 | Yes | Yes | 25.3 | 21.3 | 4.1 | B6FAB788C1FC4B9F813F8743EC028E27 |  | R22 | Non-TXV |  | 8.839% | 0.91161 | 16.99% | [5 empty] | Non-TXV | 8.839%
Vallejo | CA | 94590-7206 |  | 2013-07-15 | 2013-07-15 13:35 | 2013-07-15 13:35 | GMC - UKN | 85 | 0 | Yes | Yes | 16.9 | 19.3 | -2.4 | CB0BE28332DD4DAD87ACBD6E15EE0EB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-4139 |  | 2013-07-31 | 2013-07-31 13:50 | 2013-07-31 13:50 | GOODMAN - G1342070M41CA | 81 | 0 | Yes | Yes | 18.5 | 20.6 | -2.1 | 01B540001FC349FE930A58C56F641C8E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-0000 |  | 2013-08-01 | 2013-08-01 15:32 | 2013-08-01 16:07 | LENNOX - 13ACX04823013 | 120 | 12.1 | Yes | Yes | 26.5 | 21 | 5.5 | 528B1E326EEB47A88801E98BFEE74570 |  | R410A | Non-TXV |  | 10.08% | 0.89917 | 19.38% | [5 empty] | Non-TXV | 10.08%
Concord | CA | 94520-1703 |  | 2013-07-02 | 2013-07-02 14:05 | 2013-07-02 14:05 | TRANE - TTR030C100A3 | 66 | 0 | Yes | Yes | 20.8 | 20.4 | 0.4 | 979BA08699A64A6B918A99A876C2BC97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9624 |  | 2013-08-19 | 2013-08-19 10:08 | 2013-08-19 10:46 | RUUD - UNK | 72 | 3.3 | Yes | Yes | 20.4 | 18.8 | 1.6 | 298F9CB0A7684855926BBCADC328C86C |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Clovis | CA | 93612-2217 |  | 2013-06-26 | 2013-06-26 14:15 | 2013-06-26 14:15 | RHEEM - UNK | 80 | 0 | Yes | Yes | 19 | 18.8 | 0.2 | DF03F404B61D46A5A81AB720C1E81BB1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9625 |  | 2013-08-30 | 2013-08-30 13:49 | 2013-08-30 14:17 | RUUD - UNK | 85 | 5.2 | Yes | Yes | 20.1 | 21.3 | -1.2 | BC30471436714F3E86917DC897B21526 |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Bakersfield | CA | 93309-6463 |  | 2013-07-23 | 2013-07-23 16:25 | 2013-07-23 16:49 | GOODMAN - GPG10360701A | 85 | 4.1 | Yes | Yes | 16.9 | 19.3 | -2.4 | E92C5BBEF7814A5C9D3FE4FA3A96190E |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Bakersfield | CA | 93309-5722 |  | 2013-07-11 | 2013-07-11 17:34 | 2013-07-11 18:00 | DAY & NIGHT - N/A | 85 | 3.1 | Yes | Yes | 22.6 | 22.5 | 0.1 | 9E847FB456D743FCAB9E6565B786844F |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Bakersfield | CA | 93306-5806 |  | 2013-07-23 | 2013-07-23 11:48 | 2013-07-23 11:48 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.3 | 21.4 | -0.1 | D69FB13CDDF54D6785BABF4D6D4859FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9629 |  | 2013-08-20 | 2013-08-20 10:15 | 2013-08-20 10:52 | RUUD - UNK | 70 | -5.8 | Yes | Yes | 18.3 | 19.3 | -1 | 5DE8D394B07C4AE3B7A931CA0821560E |  | R22 | Non-TXV |  | -8.286% | 1.0829 | 2.32% |  |  |  |  | Non-TXV |  |  | -8.286%
Fairfield | CA | 94533-2579 |  | 2013-09-19 | 2013-09-19 09:39 | 2013-09-19 09:40 | GOODMAN - K1B-1B | 59 | 2.3 | Yes | Yes | 16.4 | 16.4 | 0 | 4D3AB48C02D2481BA2F16C29A7FA2414 |  | R22 | Non-TXV |  | 3.898% | 0.96102 | 7.492% | [5 empty] | Non-TXV | 3.898%
Bakersfield | CA | 93307-2926 |  | 2013-09-07 | 2013-09-07 10:46 | 2013-09-07 11:06 | GOODMAN - GPG13360451AC | 112 | 10.6 | Yes | Yes | 22.2 | 22.1 | 0.1 | 70C80E5F4DF84F769988D4EBB7895314 |  | R22 | Non-TXV |  | 9.464% | 0.90536 | 18.19% | [5 empty] | Non-TXV | 9.464%
Bakersfield | CA | 93311-1864 |  | 2013-07-09 | 2013-07-09 10:41 | 2013-07-09 11:02 | YORK - H1RC060506D | 147 | 4.9 | Yes | Yes | 18 | 20.1 | -2.1 | 84F22EB00E984C93BCEB14CE202865FB |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Parlier | CA | 93648-9628 |  | 2013-08-20 | 2013-08-20 12:43 | 2013-08-20 12:59 | RUUD - UNK | 80 | -4.7 | Yes | Yes | 18.2 | 19 | -0.8 | FAA789D629434E81871284A0091D0E53 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Bakersfield | CA | 93309-4463 |  | 2013-08-14 | 2013-08-14 12:10 | 2013-08-14 12:47 | RHEEM - RRNA-B024JK06X | 85 | 5 | Yes | Yes | 19.9 | 19.5 | 0.4 | 442F8D7AE3BC4D8E938CA00BE8360D4B |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Antioch | CA | 94531-9041 |  | 2013-07-09 | 2013-07-09 11:53 | 2013-07-09 11:54 | PAYNE - PA13NR048000AHAA | 136 | 5.4 | Yes | Yes | 16.4 | 17 | -0.6 | 1640F8FFB05E46A0B9150C9E284AEEF6 |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Bakersfield | CA | 93306-1420 |  | 2013-07-16 | 2013-07-16 12:06 | 2013-07-16 12:06 | RUUD - UAND-036JAZ | 116 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 5F905EEB53C84143815B2A74BE03DE71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3836 |  | 2013-07-15 | 2013-07-15 14:50 | 2013-07-15 14:50 | RHEEM - RAFD-036JAS | 80 | 0 | Yes | Yes | 16.7 | 19.7 | -3 | 25C5EDBDF2614656906356AE95E04EE0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4221 |  | 2013-11-01 | 2013-11-01 11:39 | 2013-11-01 12:28 | OTHER - 561CJX036C | 76 | 4.1 | Yes | Yes | 20.5 | 19.3 | 1.2 | 5A97D4EEB1D6433791DE2E4398C20E32 |  | R22 | Non-TXV |  | 5.395% | 0.94605 | 10.37% | [5 empty] | Non-TXV | 5.395%
Fresno | CA | 93720-5422 |  | 2013-07-01 | 2013-07-01 16:00 | 2013-07-01 16:38 | LENNOX - 13ACC04223001 | 123 | 4.9 | Yes | Yes | 19.3 | 21.7 | -2.4 | E7C07260F484405F9CBD52F5AEDB4DAB |  | R22 | TXV |  | 3.984% | 0.96016 | 7.656% | [5 empty] | TXV | 3.984%
Antioch | CA | 94531-7105 |  | 2013-07-09 | 2013-07-09 11:36 | 2013-07-09 11:37 | RHEEM - RAFD-036JAS | 80 | 6.2 | Yes | Yes | 17.7 | 16.1 | 1.6 | 2458FF4F780B41F2B87B6CA20B114BB8 |  | R22 | Non-TXV |  | 7.75% | 0.9225 | 14.89% | [5 empty] | Non-TXV | 7.75%
Fresno | CA | 93711-2167 |  | 2013-08-23 | 2013-08-23 12:30 | 2013-08-23 13:00 | RHEEM - RRNL-B048JKK08X | 161 | 38.5 | Yes | Yes | 21 | 19.6 | 1.5 | 6BDBD4453557480D88C7F17864C088BB |  | R410A | TXV |  | 23.91% | 0.76087 | 45.96% | [5 empty] | TXV | 23.91%
Fresno | CA | 93702-3302 |  | 2013-09-30 | 2013-09-30 09:16 | 2013-09-30 10:18 | GOODMAN - GPG12420701A | 105 | 3.4 | Yes | Yes | 22.8 | 19.7 | 3.1 | 223BDC48C2B7492A847FB18486BD6602 |  | R22 | Non-TXV |  | 3.238% | 0.96762 | 6.223% | [5 empty] | Non-TXV | 3.238%
Santa Rosa | CA | 95403-1852 |  | 2013-07-10 | 2013-07-10 09:52 | 2013-07-10 09:52 | BRYANT - 561CJ036-E | 124 | 0 | Yes | Yes | 23.5 | 19.7 | 3.8 | FBDDAFC854EC4A4FB7520933C25FAB46 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7539 |  | 2013-06-28 | 2013-06-28 09:30 | 2013-06-28 09:30 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 8F0FEAA232A24833840CA9045A8433F9 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3565 |  | 2013-10-31 | 2013-10-31 12:03 | 2013-10-31 12:20 | DUCANE - AC10B24 | 60 | 1.8 | Yes | Yes | 26.4 | 20.4 | 6 | 2CFD511844074793B508008E3EBB77F8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93727-3565 |  | 2013-07-12 | 2013-07-12 11:44 | 2013-07-12 12:11 | DAY & NIGHT - 565HJ036060 | 102 | 4.9 | Yes | Yes | 23.7 | 19.9 | 3.8 | 4AFF4B19E696447A95352D4D9AC5DD7F |  | R22 | Non-TXV |  | 4.804% | 0.95196 | 9.232% | [5 empty] | Non-TXV | 4.804%
Fresno | CA | 93726-2641 |  | 2013-06-28 | 2013-06-28 11:33 | 2013-06-28 11:53 | RUUD - RRNAB030JK06X | 66 | 2.6 | Yes | Yes | 19.7 | 19.8 | -0.1 | 130F76C3CA9743DCAF33BEACF4F20E03 |  | R22 | TXV |  | 3.939% | 0.96061 | 7.571% | [5 empty] | TXV | 3.939%
San Jose | CA | 95127-2152 |  | 2013-10-07 | 2013-10-07 16:56 | 2013-10-07 17:17 | BRYANT - PA10JA036-C | 74 | 7.5 | Yes | Yes | 23.4 | 21.5 | 1.9 | 6F91EB81714E42299E69F651F460F899 |  | R22 | Non-TXV |  | 10.14% | 0.89865 | 19.48% | [5 empty] | Non-TXV | 10.14%
Fresno | CA | 93726-3426 |  | 2013-11-07 | 2013-11-07 16:51 | 2013-11-07 17:09 | PAYNE - PA13NR036-J | 85 | -7.1 | Yes | Yes | 24.3 | 21.4 | 2.9 | CBFBB7BD083B4183AA9AA5BEEA3F50F3 |  | R22 | TXV |  | -8.353% | 1.0835 | 2.339% |  |  |  |  | TXV |  |  | -8.353%
Vacaville | CA | 95687-4661 |  | 2013-07-08 | 2013-07-08 12:49 | 2013-07-08 13:27 | GOODMAN - GSX130601BA | 125 | 3.8 | Yes | Yes | 16.6 | 15.9 | 0.7 | AAC2900376E34E75874CD58C9DC11674 |  | R410A | Non-TXV |  | 3.04% | 0.9696 | 5.842% | [5 empty] | Non-TXV | 3.04%
Vallejo | CA | 94589-2393 |  | 2013-07-16 | 2013-07-16 12:49 | 2013-07-16 12:51 | PAYNE - PA13NR036-C | 128 | -6.5 | Yes | Yes | 14.7 | 17 | -2.3 | A09913BB84AC4DBBBC1E4153972BFD1E |  | R22 | Non-TXV |  | -5.078% | 1.0508 | 1.422% |  |  |  |  | Non-TXV |  |  | -5.078%
Antioch | CA | 94531-9336 |  | 2013-09-18 | 2013-09-18 12:29 | 2013-09-18 12:29 | YORK - H2RA060S06D | 118 | -8.3 | Yes | Yes | 17 | 17.6 | -0.6 | 635092D2889F4EE598969A94CC64A43D |  | R22 | Non-TXV |  | -7.034% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.034%
Fresno | CA | 93704-1219 |  | 2013-06-27 | 2013-06-27 09:04 | 2013-06-27 09:35 | BRYANT - 574ANW042090NA | 172 | 5.5 | Yes | Yes | 22.1 | 18.5 | 3.6 | 4B23042279CE4917A2334C1ECDCD29A6 |  | R22 | Non-TXV |  | 3.198% | 0.96802 | 6.145% | [5 empty] | Non-TXV | 3.198%
Bakersfield | CA | 93308-4857 |  | 2013-10-22 | 2013-10-22 18:45 | 2013-10-22 18:45 | OTHER - UKN | 90 | 0 | Yes | Yes | 18.9 | 21.5 | -2.6 | DD1D051FCDFB4F23817C237B99E05908 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-1512 |  | 2013-08-01 | 2013-08-01 11:46 | 2013-08-01 11:46 | TRANE - TTP042C100A4 | 147 | 0 | Yes | Yes | 20.5 | 16.6 | 3.9 | 9BDE1F50146D48F796F8B1DD3D4AB992 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2309 |  | 2013-07-16 | 2013-07-16 17:51 | 2013-07-16 17:51 | ICP - GPCM036K060F | 51 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 75464D5DB3454A9DB77AF852192C7869 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-3522 |  | 2013-09-19 | 2013-09-19 13:43 | 2013-09-19 14:18 | BRYANT - PA13NR048-H | 134 | 17.1 | Yes | Yes | 23.9 | 21.2 | 2.8 | 41CA9B4276A24948B49404D3EDA636B0 |  | R22 | Non-TXV |  | 12.76% | 0.87239 | 24.52% | [5 empty] | Non-TXV | 12.76%
Bakersfield | CA | 93309-5793 |  | 2013-07-11 | 2013-07-11 17:51 | 2013-07-11 18:03 | YORK - D3NZ036N05606NXA | 85 | 3.3 | Yes | Yes | 20.9 | 21.5 | -0.6 | 4A7EA7AD131F476FAF55B954E0728030 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
San Jose | CA | 95132-3603 |  | 2013-09-25 | 2013-09-25 10:01 | 2013-09-25 11:46 | TRANE - TTX048C100A1 | 148 | 4.8 | Yes | Yes | 21.6 | 21.7 | -0.1 | 695206C3D2244A189AF028E80F4EFB19 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Bakersfield | CA | 93306-1273 |  | 2013-07-16 | 2013-07-16 10:12 | 2013-07-16 10:35 | RUUD - URA-JK04810E | 117 | 17.5 | Yes | Yes | 21.3 | 22.8 | -1.5 | DAD103A0BB3C4A0FA48DF2A454BD8BDA |  | R22 | Non-TXV |  | 14.96% | 0.85043 | 28.74% | [5 empty] | Non-TXV | 14.96%
Bakersfield | CA | 93311-2186 |  | 2013-07-09 | 2013-07-09 11:12 | 2013-07-09 11:37 | COMFORT AIRE - M2A336AKAA200 | 85 | 2.7 | Yes | Yes | 18 | 20.4 | -2.4 | DB528EDFF75D4D65846A9EF37AD22D01 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93311-2186 |  | 2013-07-09 | 2013-07-09 11:45 | 2013-07-09 12:07 | COMFORT AIRE - M2A336AKAA200 | 85 | 2.8 | Yes | Yes | 19.5 | 20.4 | -0.9 | 52A2169E6540482F9E29FD53BD9FA36D |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Vacaville | CA | 95687-7824 |  | 2013-07-08 | 2013-07-08 13:58 | 2013-07-08 14:18 | GOODMAN - CPE24-1AB | 93 | 2.8 | Yes | Yes | 12.6 | 13.9 | -1.3 | 9DAFFD097A7543809B48712D10985C24 |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Redding | CA | 96002-9521 |  | 2013-09-03 | 2013-09-03 14:58 | 2013-09-03 15:25 | RUUD - URGG-07N49JKR | 136 | 19.8 | Yes | Yes | 24.4 | 21 | 3.4 | B26F1837380F42E19E956C57EFD85953 |  | R22 | Non-TXV |  | 14.56% | 0.85441 | 27.98% | [5 empty] | Non-TXV | 14.56%
Arvin | CA | 93203-2058 |  | 2013-08-19 | 2013-08-19 17:28 | 2013-08-19 17:29 | GOODMAN - CPLE42-1B | 128 | 11.2 | Yes | Yes | 23.2 | 22.6 | 0.6 | A3DEB545CFF44027B296C6FD423369EC |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Bakersfield | CA | 93313-3500 |  | 2013-07-12 | 2013-07-12 18:15 | 2013-07-12 18:38 | YORK - | 85 | 4.1 | Yes | Yes | 19.2 | 19.2 | 0 | D5C9518C3EFE4D01845F134B9193990C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
San Jose | CA | 95127-1805 |  | 2013-10-07 | 2013-10-07 15:58 | 2013-10-07 16:36 | GIBSON - JS3BC-036KA | 91 | 35 | Yes | Yes | 26.1 | 20.4 | 5.7 | 45B84F3892CF4AAE85DF9C06C275FFFA |  | R22 | Non-TXV |  | 38.46% | 0.61538 | 73.91% | [5 empty] | Non-TXV | 38.46%
Vallejo | CA | 94589-4368 |  | 2013-07-16 | 2013-07-16 12:25 | 2013-07-16 12:25 | AMERICAN STANDARD - 2A7B0036A1000AA | 76 | -5.4 | Yes | Yes | 16.5 | 17.6 | -1.1 | 5FC96E4C3B6E49629AD65A36D95313A0 |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Bakersfield | CA | 93307-6072 |  | 2013-10-15 | 2013-10-15 11:23 | 2013-10-15 11:23 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 18.9 | 21.3 | -2.4 | 90D1DD1C935D4A01B3AA5C2E73F86C17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-3943 |  | 2013-11-01 | 2013-11-01 11:59 | 2013-11-01 12:19 | OTHER - TCGD3652152HA | 63 | 2.4 | Yes | Yes | 21.5 | 20.4 | 1.1 | 2B52212526A84A32A4DB217353DEFAB0 |  | R22 | TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | TXV | 3.81%
Santa Rosa | CA | 95409-6306 |  | 2013-07-17 | 2013-07-17 09:56 | 2013-07-17 11:42 | CARRIER - 38ED048300 | 132 | -12.4 | Yes | Yes | 18.6 | 17.6 | 1 | 64C09856EE67457BB5E4ADDA85C3073F |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
San Jose | CA | 95135-1308 |  | 2013-07-25 | 2013-07-25 11:08 | 2013-07-25 11:47 | CARRIER - 24ACR330A300 | 95 | 9.6 | Yes | Yes | 20.4 | 18.2 | 2.2 | 9B5D42DD6A074B218A452CBF336740CE |  | R22 | TXV |  | 10.11% | 0.89895 | 19.42% | [5 empty] | TXV | 10.11%
Vallejo | CA | 94589-1948 |  | 2013-09-03 | 2013-09-03 14:05 | 2013-09-03 14:55 | TRANE - 4TTR5024E1000AC | 85 | -6 | Yes | Yes | 20.9 | 20.8 | 0.2 | 0B9244657CD0498CA379367112F3C0DE |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
San Jose | CA | 95111-2276 |  | 2013-09-18 | 2013-09-18 15:27 | 2013-09-18 16:18 | COPELAND - GSX130361BA | 89 | -7.3 | Yes | Yes | 22 | 20.9 | 1.1 | 00FFAAEBAD464EEB862754858AC7A599 |  | R410A | Non-TXV |  | -8.202% | 1.082 | 2.297% |  |  |  |  | Non-TXV |  |  | -8.202%
San Jose | CA | 95135-1323 |  | 2013-07-25 | 2013-07-25 12:59 | 2013-07-25 12:59 | GE - BGTA924H1L | 42 | 0 | Yes | Yes | 20.9 | 17.2 | 3.7 | 4B7C22FB4E864B29A1C1C5640FC0D5E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95403-3437 |  | 2013-07-10 | 2013-07-10 13:24 | 2013-07-10 13:24 | AMERICAN STANDARD - CM18-41-T | 85 | 0 | Yes | Yes | 17.9 | 18.5 | -0.6 | 17C1F53C68AC4EB3B3CF0D88AA9BF516 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8675 |  | 2013-08-15 | 2013-08-15 12:55 | 2013-08-15 15:57 | TRANE - TTP048D100A0 | 131 | 5.8 | Yes | Yes | 15.6 | 17.7 | -2.1 | C8A3B6979DCC484D94E7E799529CCB48 |  | R22 | Non-TXV |  | 4.427% | 0.95573 | 8.509% | [5 empty] | Non-TXV | 4.427%
Bakersfield | CA | 93313-5600 |  | 2013-07-23 | 2013-07-23 12:27 | 2013-07-23 13:02 | TRANE - 2TTB3036A1000AA | 101 | 12.7 | Yes | Yes | 20.8 | 19 | 1.8 | 9DD95F4A9FB748599EAEE6EB20FF0C62 |  | R22 | TXV |  | 12.57% | 0.87426 | 24.16% | [5 empty] | TXV | 12.57%
Bakersfield | CA | 93309-5741 |  | 2013-07-08 | 2013-07-08 13:00 | 2013-07-08 16:08 | OTHER - CA5536VKD2 | 88 | 2.9 | Yes | Yes | 20 | 21.3 | -1.3 | 23D11B2125CC42048DFA37415CCCC525 |  | R22 | Non-TXV |  | 3.295% | 0.96705 | 6.333% | [5 empty] | Non-TXV | 3.295%
Vallejo | CA | 94591-6352 |  | 2013-09-03 | 2013-09-03 12:59 | 2013-09-03 14:58 | CARRIER - 38CK048300 | 106 | -6.2 | Yes | Yes | 17.1 | 19.1 | -2 | 12B5207D72FA4990ABB08DF1C1835030 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Fairfield | CA | 94533-2565 |  | 2013-07-24 | 2013-07-24 13:32 | 2013-07-24 15:34 | TRANE - BTD718A100B0 | 46 | 1.5 | Yes | Yes | 14.5 | 17.5 | -3 | DF6364226D9246CC81386B1E289C2F30 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Vacaville | CA | 95687-7825 |  | 2013-07-08 | 2013-07-08 11:03 | 2013-07-08 11:26 | GOODMAN - CPH30-1FB | 114 | -3.7 | Yes | Yes | 14.9 | 15.2 | -0.3 | A9301910EAE247BB8656315849DCD04C |  | R22 | Non-TXV |  | -3.246% | 1.0325 | 0.9089% |  |  |  |  | Non-TXV |  |  | -3.246%
Vacaville | CA | 95687-6774 |  | 2013-07-12 | 2013-07-12 09:29 | 2013-07-12 09:29 | DAY & NIGHT - 591ANX036000AAA | 90 | 0 | Yes | Yes | 14.9 | 17.7 | -2.8 | F91F8A1254944028BCAAE133899C5C7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5497 |  | 2013-07-08 | 2013-07-08 14:26 | 2013-07-08 15:47 | OTHER - 561AJ024-A | 77 | 2.5 | Yes | Yes | 14.2 | 14.1 | 0.2 | 6C318AC22F0F4452A3010DAA5EEA9536 |  | R22 | Non-TXV |  | 3.247% | 0.96753 | 6.24% | [5 empty] | Non-TXV | 3.247%
Corcoran | CA | 93212-9738 |  | 2013-08-05 | 2013-08-05 10:47 | 2013-08-05 11:09 | OTHER - BRC8048105 | 119 | 22 | Yes | Yes | 22 | 20.4 | 1.6 | E74B330492E54E129F17A8AA032D1968 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.49% | 0.81513 | 35.53% | [5 empty] | Non-TXV | 18.49%
Davis | CA | 95618-4827 |  | 2013-08-07 | 2013-08-07 09:26 | 2013-08-07 09:32 | GOODMAN - CKL18-1 | 53 | 5.6 | Yes | Yes | 17.9 | 17.6 | 0.3 | 866836333ACC4E82BA4CCBF98B60CF60 |  | R22 | Non-TXV |  | 10.57% | 0.89434 | 20.31% | [5 empty] | Non-TXV | 10.57%
Vacaville | CA | 95687-5247 |  | 2013-10-23 | 2013-10-23 14:04 | 2013-10-23 15:55 | TRANE - TTY036B100A0 | 170 | 4.4 | Yes | Yes | 12.5 | 15.5 | -3 | 4B84875DDA034E95A2132CD0C48BB5A7 |  | R22 | Non-TXV |  | 2.588% | 0.97412 | 4.974% | [5 empty] | Non-TXV | 2.588%
Corcoran | CA | 93212-1715 |  | 2013-07-11 | 2013-07-11 11:55 | 2013-07-11 12:21 | DUCANE - SG1042075 | 88 | 8.6 | Yes | Yes | 24.3 | 19.8 | 4.5 | E4542DC3B20F4EAA87A40C2D729F2B8F |  | R22 | Non-TXV |  | 9.773% | 0.90227 | 18.78% | [5 empty] | Non-TXV | 9.773%
Bakersfield | CA | 93313-5239 |  | 2013-07-23 | 2013-07-23 14:16 | 2013-07-23 14:35 | PAYNE - PA12NA036 | 100 | -5.9 | Yes | Yes | 25 | 21.4 | 3.6 | 212A3E5A1E6A4259B720AC1DB0DD89DA |  | R22 | TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | TXV |  |  | -5.9%
San Jose | CA | 95117-1612 |  | 2013-07-25 | 2013-07-25 12:35 | 2013-07-25 12:38 | GOODMAN - GSC130481AC | 158 | 5.7 | Yes | Yes | 17.6 | 18.2 | -0.6 | 9D80A214779C4329BAA9E07F63F9681F |  | R22 | Non-TXV |  | 3.608% | 0.96392 | 6.933% | [5 empty] | Non-TXV | 3.608%
Bakersfield | CA | 93309-6403 |  | 2013-08-07 | 2013-08-07 21:27 | 2013-08-07 21:29 | RHEEM - RRNLB024JK06X | 78 | 3 | Yes | Yes | 20 | 19.8 | 0.2 | 4EA0E56CD7E3444A882FB51E77E86E51 |  | R410A | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
San Jose | CA | 95135-1322 |  | 2013-07-29 | 2013-07-29 14:19 | 2013-07-29 14:19 | GE - UKN | 85 | 31.6 | Yes | Yes | 24.8 | 21.3 | 3.5 | 3D8FB909AD74401BAF1F9D5C00774A7E | Add refrigerant: 31.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 37.18% | 0.62824 | 71.44% | [5 empty] | Non-TXV | 37.18%
Bay Point | CA | 94565-6939 |  | 2013-07-03 | 2013-07-03 10:03 | 2013-07-03 11:08 | GOODMAN - GSH1301B1AC | 127 | 3.9 | Yes | Yes | 14.2 | 16.5 | -2.3 | 5562F7BB55704B9B895A2A4BEBBCA238 |  | R22 | Non-TXV |  | 3.071% | 0.96929 | 5.902% | [5 empty] | Non-TXV | 3.071%
Fresno | CA | 93706-1427 |  | 2013-07-01 | 2013-07-01 16:21 | 2013-07-01 16:21 | OTHER - UNK | 68 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 29B72FF4A69645E1B66BAD6306532A5D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-4436 |  | 2013-07-10 | 2013-07-10 10:48 | 2013-07-10 11:11 | COLEMAN - DRCQ0481BD | 104 | 3.6 | Yes | Yes | 22.3 | 19 | 3.3 | 6AC6C7668F534034AA9F2C8E6B4EB616 |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
San Jose | CA | 95128-3697 |  | 2013-07-25 | 2013-07-25 13:56 | 2013-07-25 13:56 | NORDYNE - JT38BA-024KA | 85 | 0 | Yes | Yes | 22.4 | 18.5 | 3.9 | 6BF8F061EC604DB99058F0757F18F42D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4833 |  | 2013-08-07 | 2013-08-07 10:42 | 2013-08-07 10:42 | GE - NA | 69 | 0 | Yes | Yes | 17.7 | 17.6 | 0.1 | 7553E18B38284AD788EE498F1EB715B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9625 |  | 2013-08-21 | 2013-08-21 16:07 | 2013-08-21 16:29 | RUUD - UNK | 85 | 2.8 | Yes | Yes | 19.6 | 20.2 | -0.5 | 1E4E27C162C6408ABC6AAA63CEBFE4D8 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Sanger | CA | 93657-1930 |  | 2013-07-30 | 2013-07-30 09:31 | 2013-07-30 09:48 | WEATHER KING - 14AJ48A01 | 234 | -8.5 | Yes | Yes | 25.2 | 20.6 | 4.6 | 48FFA1CE9E4A4767B6442305E2F80CC2 |  | R22 | TXV |  | -3.632% | 1.0363 | 1.017% |  |  |  |  | TXV |  |  | -3.632%
Antioch | CA | 94509-1234 |  | 2013-09-19 | 2013-09-19 15:46 | 2013-09-19 16:07 | ALLEGIANCE - 7A0030A100A2 | 62 | 3.5 | Yes | Yes | 13.3 | 16.1 | -2.8 | 0FFF3CDA06994AEBB1322FBE5010FE51 |  | R22 | Non-TXV |  | 5.645% | 0.94355 | 10.85% | [5 empty] | Non-TXV | 5.645%
Davis | CA | 95618-4870 |  | 2013-09-26 | 2013-09-26 11:23 | 2013-09-26 15:46 | OTHER - DADD-018J | 52 | 1.6 | Yes | Yes | 16.9 | 19.3 | -2.4 | 8C105E02560646EC890901EDFCC0BE43 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Bakersfield | CA | 93309-5733 |  | 2013-07-08 | 2013-07-08 16:11 | 2013-07-08 16:53 | DAY & NIGHT - N/A | 85 | 4.5 | Yes | Yes | 20.8 | 22.5 | -1.7 | 342C91F76CC14D95A188BE455DB29E8C |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Parlier | CA | 93648-9624 |  | 2013-08-19 | 2013-08-19 15:11 | 2013-08-19 15:11 | RUUD - UNK | 70 | 0 | Yes | Yes | 24.6 | 20.7 | 3.9 | CF1FCB34AB924B68913A4F0BD71D3E98 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5494 |  | 2013-07-10 | 2013-07-10 13:21 | 2013-07-10 13:21 | YORK - H1CB042506A | 94 | 0 | Yes | Yes | 17.5 | 17.5 | 0.1 | A5B1DF30D965486F82B5EF9DC3A4257B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1606 |  | 2013-09-03 | 2013-09-03 10:58 | 2013-09-03 11:16 | RHEEM - RRNAB030JK06X | 65 | 2.9 | Yes | Yes | 19.5 | 19.3 | 0.2 | F2DBDD1D44A04EB6A12E6C2916E3CCD5 |  | R22 | Non-TXV |  | 4.462% | 0.95538 | 8.574% | [5 empty] | Non-TXV | 4.462%
Fresno | CA | 93711-1687 |  | 2013-07-25 | 2013-07-25 17:27 | 2013-07-25 17:45 | PAYNE - UNK | 66 | 4.1 | Yes | Yes | 21.7 | 19.6 | 2.1 | C0B5CD91F90E4362976C693DC42DB78D |  | R22 | Non-TXV |  | 6.212% | 0.93788 | 11.94% | [5 empty] | Non-TXV | 6.212%
Gilroy | CA | 95020-6565 |  | 2013-10-23 | 2013-10-23 08:49 | 2013-10-23 09:30 | COLEMAN - BRCQD361CB | 58 | 8.7 | Yes | Yes | 21 | 21.1 | -0.1 | 55F712888CDB4111A9799005C2025F08 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Sanger | CA | 93657-3827 |  | 2013-06-28 | 2013-06-28 10:42 | 2013-06-28 11:09 | OTHER - 563AN042A | 131 | 6.4 | Yes | Yes | 19.7 | 19.3 | 0.4 | C88327CACD49469C809DCCF177E3C8B8 |  | R22 | Non-TXV |  | 4.885% | 0.95115 | 9.389% | [5 empty] | Non-TXV | 4.885%
Parlier | CA | 93648-9631 |  | 2013-08-20 | 2013-08-20 12:33 | 2013-08-20 13:38 | RUUD - UNK | 70 | 3.2 | Yes | Yes | 17.8 | 18.8 | -1 | E7EFC4F00B5E4508AD48A6E0C608CB2F |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Bakersfield | CA | 93313-3028 |  | 2013-07-26 | 2013-07-26 14:52 | 2013-07-26 15:20 | ICP - PGC042K0808 | 103 | 5.8 | Yes | Yes | 21.5 | 21.5 | 0 | 58DAA28FFC0449778638581367451B81 |  | R22 | Non-TXV |  | 5.631% | 0.94369 | 10.82% | [5 empty] | Non-TXV | 5.631%
Bakersfield | CA | 93309-5794 |  | 2013-07-11 | 2013-07-11 11:02 | 2013-07-11 11:24 | DAY & NIGHT - DAYH-F036N070C | 108 | 6.8 | Yes | Yes | 24.5 | 20.4 | 4.1 | A40E3AFFCD1B4DC58FD5F78172F80F6A |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Davis | CA | 95618-4834 |  | 2013-08-07 | 2013-08-07 11:14 | 2013-08-07 11:16 | GOODMAN - CKL18-1B | 72 | 4 | Yes | Yes | 17.9 | 17.6 | 0.3 | 06BE2E6D4944449B9B0CD5728FBD19D8 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Parlier | CA | 93648-9625 |  | 2013-08-20 | 2013-08-20 11:14 | 2013-08-20 11:35 | RUUD - UNK | 80 | -4.7 | Yes | Yes | 16 | 18.5 | -2.5 | 3189E3DE259F4859BB39148B858B8800 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Bakersfield | CA | 93307-2886 |  | 2013-07-25 | 2013-07-25 11:24 | 2013-07-25 11:24 | RHEEM - RRNA-B036JK06X | 83 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | 125BCAD30F2C4C5EABB481AE3A76587B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-3014 |  | 2013-07-08 | 2013-07-08 16:53 | 2013-07-08 17:26 | YORK - ERCS0481CA | 227 | 18.6 | Yes | Yes | 21.7 | 23.3 | -1.6 | 7F983BD273674A8FB0D38FB943DB06F5 |  | R22 | Non-TXV |  | 8.194% | 0.91806 | 15.75% | [5 empty] | Non-TXV | 8.194%
Parlier | CA | 93648-9627 |  | 2013-08-30 | 2013-08-30 17:02 | 2013-08-30 17:43 | RUUD - UNK | 85 | 3.2 | Yes | Yes | 21.5 | 19.7 | 1.9 | 34C99C57CC8E476EBD8ED23276825B15 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Sunnyvale | CA | 94089-1814 |  | 2013-09-27 | 2013-09-27 09:40 | 2013-09-27 10:02 | UNITARY PRODUCTS GROUP - TCGD36S41S3A | 73 | 8 | Yes | Yes | 24.5 | 18.8 | 5.7 | 286F414D1353438496B7940B554AA3D3 |  | R410A | TXV |  | 10.96% | 0.89041 | 21.06% | [5 empty] | TXV | 10.96%
Parlier | CA | 93648-9625 |  | 2013-08-19 | 2013-08-19 13:47 | 2013-08-19 14:41 | RUUD - UNK | 70 | 2.6 | Yes | Yes | 19.1 | 18.1 | 1 | 226C9EF5EE7C45BD800C745449BE92C0 |  | R22 | Non-TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | Non-TXV | 3.714%
Fresno | CA | 93711-0554 |  | 2013-07-04 | 2013-07-04 10:16 | 2013-07-04 10:51 | GOODMAN - GPG1336070M41DA | 70 | 10.6 | Yes | Yes | 21.6 | 18.8 | 2.8 | CC3E29763503467890D7F3519337C4DB |  | R410A | Non-TXV |  | 15.14% | 0.84857 | 29.1% | [5 empty] | Non-TXV | 15.14%
Fresno | CA | 93702-2257 |  | 2013-10-12 | 2013-10-12 12:13 | 2013-10-12 12:13 | GOODMAN - GPG10360701A | 75 | 5.8 | Yes | Yes | 29.6 | 20.4 | 9.2 | 340470B7ACCA4FF0B33FAF4012F2BADA | Add refrigerant: 5.8 oz | R22 | Non-TXV |  | 7.733% | 0.92267 | 14.86% | [5 empty] | Non-TXV | 7.733%
Fresno | CA | 93705-1104 |  | 2013-07-03 | 2013-07-03 14:32 | 2013-07-03 14:32 | DAY & NIGHT - PG0342090K001C1 | 97 | 6.6 | Yes | Yes | 28.4 | 21.3 | 7.1 | 5DB663BB80DC479FA96D96C309B952AD | Add refrigerant: 6.6 oz | R410A | TXV |  | 6.804% | 0.93196 | 13.08% | [5 empty] | TXV | 6.804%
Fresno | CA | 93704-1917 |  | 2013-06-27 | 2013-06-27 12:12 | 2013-06-27 12:12 | BRYANT - 563CNX060ADA | 204 | 0 | Yes | Yes | 19.1 | 17.7 | 1.5 | 62AE9B3200AE43888E369B532A80A59B |  | R22 | TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9631 |  | 2013-08-20 | 2013-08-20 11:59 | 2013-08-20 12:42 | RUUD - UNK | 80 | -4.7 | Yes | Yes | 16.1 | 16.9 | -0.8 | AA0672F52BFA4FDEACBC0E5295FEAB9E |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
San Jose | CA | 95135-1306 |  | 2013-07-25 | 2013-07-25 10:44 | 2013-07-25 10:45 | INTERTHERM - NA | 69 | 3.4 | Yes | Yes | 18.3 | 17.9 | 0.4 | E9436494B7DC40E282D456551E8F0C33 |  | R22 | Non-TXV |  | 4.928% | 0.95072 | 9.47% | [5 empty] | Non-TXV | 4.928%
Fresno | CA | 93711-1408 |  | 2013-08-23 | 2013-08-23 13:51 | 2013-08-23 14:13 | PAYNE - 567C042RC0 | 86 | 9.2 | Yes | Yes | 18.9 | 19 | -0.1 | 44DB71B4AE504202B4828BD28EFA3FC2 |  | R22 | Non-TXV |  | 10.7% | 0.89302 | 20.56% | [5 empty] | Non-TXV | 10.7%
Parlier | CA | 93648-9625 |  | 2013-11-01 | 2013-11-01 10:49 | 2013-11-01 11:34 | RUUD - UNK | 74 | 11 | Yes | Yes | 21.2 | 19.5 | 1.7 | 2A26571114F849F4AEF5AD05FDC8FEC8 |  | R22 | Non-TXV |  | 14.86% | 0.85135 | 28.57% | [5 empty] | Non-TXV | 14.86%
Fresno | CA | 93727-5007 |  | 2013-06-28 | 2013-06-28 10:29 | 2013-06-28 10:52 | COPELAND - C1048-1 | 243 | -22.9 | Yes | Yes | 17.5 | 14.9 | 2.6 | 5DF8F690D3E7421DA33BB0919195D426 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.424% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.424%
Sanger | CA | 93657-3343 |  | 2013-06-28 | 2013-06-28 13:04 | 2013-06-28 13:31 | CARRIER - 48NLT300600 | 80 | 10.3 | Yes | Yes | 20.7 | 19.4 | 1.3 | 7A833C6C589A4DE0A3547BCD3466BF43 |  | R22 | Non-TXV |  | 12.88% | 0.87125 | 24.74% | [5 empty] | Non-TXV | 12.88%
Bakersfield | CA | 93309-5776 |  | 2013-09-11 | 2013-09-11 19:36 | 2013-09-11 19:36 | DAY & NIGHT - PGD336060K001C1 | 100 | -7.2 | Yes | Yes | 24.7 | 20.4 | 4.3 | 78E55A62468F4CADAED0EC8A120E6388 | Remove refrigerant: 7.2 oz | R410A | TXV |  | -7.2% | 1.072 | 2.016% |  |  |  |  | TXV |  |  | -7.2%
Selma | CA | 93662-4217 |  | 2013-06-26 | 2013-06-26 14:22 | 2013-06-26 14:22 | RHEEM - RRKAA030JK06X | 54 | 0 | Yes | Yes | 40 | 20.9 | 19.1 | FADD00E37EF54D4AB69EF9E81205A94E | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5730 |  | 2013-07-11 | 2013-07-11 17:31 | 2013-07-11 17:59 | CARRIER - 48SS0360G0331 | 85 | 10.5 | Yes | Yes | 23.1 | 19.9 | 3.2 | 9E65F08A2ACB4178951A0D00AFC0613D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.35% | 0.87647 | 23.74% | [5 empty] | Non-TXV | 12.35%
Selma | CA | 93662-2113 |  | 2013-06-26 | 2013-06-26 14:51 | 2013-06-26 15:17 | OTHER - UNK | 118 | -8.3 | Yes | Yes | 16.9 | 16.6 | 0.3 | DE865F5AFC054FE39592B730FE1AD2E7 |  | R22 | Non-TXV |  | -7.034% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.034%
Parlier | CA | 93648-9626 |  | 2013-08-19 | 2013-08-19 10:49 | 2013-08-19 11:12 | RUUD - UNK | 70 | 4.1 | Yes | Yes | 18.5 | 18.6 | -0.1 | 953A2A9416FB401FA5F1ED27AF0A32D7 |  | R22 | Non-TXV |  | 5.857% | 0.94143 | 11.26% | [5 empty] | Non-TXV | 5.857%
Bay Point | CA | 94565-6718 |  | 2013-08-05 | 2013-08-05 14:24 | 2013-08-05 15:46 | TRANE - BTD736A100B | 88 | 8.1 | Yes | Yes | 16.7 | 18.8 | -2.1 | 74A6F9DD615148CCADA10E1657873FE0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.205% | 0.90795 | 17.69% | [5 empty] | Non-TXV | 9.205%
San Jose | CA | 95116-1315 |  | 2013-09-23 | 2013-09-23 12:14 | 2013-09-23 12:38 | GOODMAN - GSX130361CA | 89 | 3.2 | Yes | Yes | 21.2 | 15.3 | 6 | F7DE7220BE504896A166870341EAA19F |  | R410A | TXV |  | 3.596% | 0.96404 | 6.91% | [5 empty] | TXV | 3.596%
Fresno | CA | 93705-3911 |  | 2013-10-29 | 2013-10-29 15:37 | 2013-10-29 16:40 | YORK - D1NA048N06506C | 92 | 4.4 | Yes | Yes | 19.6 | 19.3 | 0.3 | 03CA1B6B5F34439EAF00E87845FFE248 |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Bakersfield | CA | 93306-3444 |  | 2013-09-16 | 2013-09-16 09:49 | 2013-09-16 10:09 | YORK - D1NH04246506B | 90 | 5.4 | Yes | Yes | 22.5 | 22.1 | 0.4 | B497B25E30FB46A390BAA756191B28E2 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Vallejo | CA | 94591-8413 |  | 2013-07-17 | 2013-07-17 15:14 | 2013-07-17 16:13 | TRANE - TTB030C100A2 | 66 | 3.8 | Yes | Yes | 14 | 15.9 | -1.9 | 4997EE8C0C344CAAA2576197BA3F05FE |  | R22 | Non-TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | Non-TXV | 5.758%
Bakersfield | CA | 93309-5659 |  | 2013-07-08 | 2013-07-08 11:29 | 2013-07-08 11:49 | DAY & NIGHT - 587AN2036060 | 105 | 5.5 | Yes | Yes | 21.2 | 21 | 0.2 | FAA9BF5FBAA04866BACB7A57F73C7D93 |  | R22 | Non-TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | Non-TXV | 5.238%
San Jose | CA | 95135-1301 |  | 2013-09-23 | 2013-09-23 11:37 | 2013-09-23 12:06 | GE - 21TA924H1H | 58 | -5.5 | Yes | Yes | 24.6 | 19.7 | 4.9 | 479664E789C1451BBF4247C8F3BB1868 |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Parlier | CA | 93648-9628 |  | 2013-08-20 | 2013-08-20 11:44 | 2013-08-20 12:30 | RUUD - UNK | 70 | 3.1 | Yes | Yes | 17.7 | 19 | -1.3 | 3B339A7C18F7434B95A179DE2C727C10 |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Fresno | CA | 93703-3596 |  | 2013-10-21 | 2013-10-21 11:35 | 2013-10-21 11:54 | GOODMAN - GPG10300701 | 50 | 2.7 | Yes | Yes | 21.4 | 18.2 | 3.2 | 9E794B2D551842488C54F0E4C9DE91B1 |  | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Fresno | CA | 93722-3503 |  | 2013-08-28 | 2013-08-28 09:51 | 2013-08-28 10:16 | BDP - 6858B060 | 120 | 29.4 | Yes | Yes | 17.9 | 20.3 | -2.4 | 3C02C3BDF81C4F169D7475674FC1B32A |  | R22 | Non-TXV |  | 24.5% | 0.755 | 47.08% | [5 empty] | Non-TXV | 24.5%
Parlier | CA | 93648-9630 |  | 2013-09-03 | 2013-09-03 15:18 | 2013-09-03 15:55 | RUUD - UNK | 85 | 6.2 | Yes | Yes | 19.7 | 19.9 | -0.2 | 73D14C71BCB441D9BBE3B66F359CF9C7 |  | R22 | Non-TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | Non-TXV | 7.294%
Lemoore | CA | 93245-4307 |  | 2013-08-02 | 2013-08-02 11:25 | 2013-08-02 11:46 | COLEMAN - BRCQ0421BB | 64 | 2 | Yes | Yes | 22 | 17.5 | 4.5 | 145F843F2F3A4524A09A125689EE8AD7 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Fresno | CA | 93711-1330 |  | 2013-07-11 | 2013-07-11 12:53 | 2013-07-11 12:53 | - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 6B730CB47E784CC0B00CD89DD056362D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-7146 |  | 2013-07-08 | 2013-07-08 16:24 | 2013-07-08 16:24 | CARRIER - 38BRB048300 | 167 | 61.3 | Yes | Yes | 8.8 | 24.2 | -15.4 | CA5F49E2949A4EC99ECC816BE9455074 | Add refrigerant: 61.3 oz | R22 | Non-TXV |  | 36.71% | 0.63293 | 70.54% | [5 empty] | Non-TXV | 36.71%
Vacaville | CA | 95687-6718 |  | 2013-07-08 | 2013-07-08 11:39 | 2013-07-08 12:38 | TRANE - 2TTR1030A1000AA | 64 | 3 | Yes | Yes | 16.5 | 17.1 | -0.6 | 314112DE05504DB9BC14B65960F1EF4E |  | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Parlier | CA | 93648-9627 |  | 2013-08-20 | 2013-08-20 10:42 | 2013-08-20 11:13 | RUUD - UNK | 80 | 2.6 | Yes | Yes | 20.3 | 20.3 | 0 | F0E634305DAC4265A61926958FA0CBAB |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Parlier | CA | 93648-9628 |  | 2013-08-19 | 2013-08-19 11:16 | 2013-08-19 12:05 | GOODMAN - VSC130241AA | 80 | -4.7 | Yes | Yes | 17 | 16.6 | 0.4 | ECABEBD6A5C243EFB9C60AC42154D776 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Bakersfield | CA | 93304-5143 |  | 2013-07-03 | 2013-07-03 17:51 | 2013-07-03 18:09 | ICP - PGC048K0800 | 100 | 11.9 | Yes | Yes | 20.6 | 19.1 | 1.5 | FF78A54AF57B423D9CFDAE57B7148521 |  | R22 | Non-TXV |  | 11.9% | 0.881 | 22.87% | [5 empty] | Non-TXV | 11.9%
Fairfield | CA | 94533-6472 |  | 2013-09-25 | 2013-09-25 14:57 | 2013-09-25 16:28 | CARRIER - 38CKC036350 | 74 | -4.1 | Yes | Yes | 18.5 | 21.3 | -2.8 | 1A80D3362CFC4C9F88EE46FC68AB0136 |  | R22 | Non-TXV |  | -5.541% | 1.0554 | 1.552% |  |  |  |  | Non-TXV |  |  | -5.541%
Fresno | CA | 93723-7600 |  | 2013-07-31 | 2013-07-31 15:32 | 2013-07-31 15:32 | RHEEM - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | F9EE512B75C2425796127D3A3A2D12C2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8656 |  | 2013-07-17 | 2013-07-17 12:32 | 2013-07-17 13:07 | YORK - TCGD24S1SHA | 61 | -3.6 | Yes | Yes | 14.9 | 17.2 | -2.3 | D704BB809CD54836B43A7CCD69918ABB |  | R22 | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Parlier | CA | 93648-9627 |  | 2013-08-19 | 2013-08-19 09:50 | 2013-08-19 10:08 | RUUD - UNK | 80 | 2.4 | Yes | Yes | 19.2 | 17.7 | 1.5 | BE433BC1135D4D11A0425544B7F2A02A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Corcoran | CA | 93212-2845 |  | 2013-07-11 | 2013-07-11 09:37 | 2013-07-11 09:59 | HEIL - NRGF36AK02 | 80 | 5.8 | Yes | Yes | 23.4 | 19.1 | 4.3 | 167134C5C4444A2F83CC76A28C4744ED |  | R22 | Non-TXV |  | 7.25% | 0.9275 | 13.93% | [5 empty] | Non-TXV | 7.25%
Fresno | CA | 93726-6005 |  | 2013-08-31 | 2013-08-31 09:32 | 2013-08-31 09:57 | HEIL - PGAA30C1K1 | 75 | -6.2 | Yes | Yes | 26.1 | 16.8 | 9.4 | A88DA4C56B2D49989D81BC2C24D4C915 | Remove refrigerant: 7.1 oz Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.267% | 1.0827 | 2.315% |  |  |  |  | Non-TXV |  |  | -8.267%
Fresno | CA | 93704-1621 |  | 2013-07-31 | 2013-07-31 10:14 | 2013-07-31 10:41 | GOODMAN - CLJ42-1C | 84 | -4.9 | Yes | Yes | 18 | 20.2 | -2.2 | 8C96550611984363863CFCD27DA2706D |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Sanger | CA | 93657-2964 |  | 2013-07-03 | 2013-07-03 11:26 | 2013-07-03 11:47 | PAYNE - UNK | 70 | 4.8 | Yes | Yes | 22.3 | 17.9 | 4.4 | A54D1F88E21D45CF9083EA8B980E7B9A |  | R22 | Non-TXV |  | 6.857% | 0.93143 | 13.18% | [5 empty] | Non-TXV | 6.857%
Sanger | CA | 93657-2963 |  | 2013-07-29 | 2013-07-29 15:34 | 2013-07-29 16:00 | PAYNE - 585HJ036060 | 102 | 7.1 | Yes | Yes | 23.4 | 21 | 2.4 | AC3C6CAD7E794096BBB5447423F3ED8E |  | R22 | Non-TXV |  | 6.961% | 0.93039 | 13.38% | [5 empty] | Non-TXV | 6.961%
Fresno | CA | 93705-4452 |  | 2013-07-06 | 2013-07-06 12:05 | 2013-07-06 12:23 | GOODMAN - PGB036075 | 60 | 5 | Yes | Yes | 21.5 | 17.2 | 4.3 | 4C95105F93D941C980AE3E65A806C9A1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Fresno | CA | 93710-5618 |  | 2013-07-29 | 2013-07-29 13:00 | 2013-07-29 13:29 | DAY & NIGHT - 84ANW048100 | 80 | 4.7 | Yes | Yes | 26.2 | 21 | 5.2 | 8B40E3EE16054447883E2F9C74070330 |  | R22 | Non-TXV |  | 5.875% | 0.94125 | 11.29% | [5 empty] | Non-TXV | 5.875%
San Jose | CA | 95127-1906 |  | 2013-08-01 | 2013-08-01 13:21 | 2013-08-01 13:47 | PAYNE - PA10JA048-D | 106 | 13.3 | Yes | Yes | 19.8 | 16.9 | 2.9 | 6A283391DF634EDB90D94F407565E6FD |  | R22 | TXV |  | 12.55% | 0.87453 | 24.11% | [5 empty] | TXV | 12.55%
Sanger | CA | 93657-0000 |  | 2013-06-28 | 2013-06-28 09:27 | 2013-06-28 09:52 | - | 85 | 5.2 | Yes | Yes | 19.4 | 18.2 | 1.2 | 8249856336F14FD38E8E4B95212D850F |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Bakersfield | CA | 93304-1817 |  | 2013-07-01 | 2013-07-01 15:19 | 2013-07-01 15:39 | TRANE - YCP036F1M0AD | 109 | 10.8 | Yes | Yes | 20.3 | 18.3 | 2 | 18CE295D2635400AA4321BEAE09907C5 |  | R22 | Non-TXV |  | 9.908% | 0.90092 | 19.04% | [5 empty] | Non-TXV | 9.908%
Fresno | CA | 93703-1254 |  | 2013-10-15 | 2013-10-15 13:15 | 2013-10-15 16:37 | GOODMAN - PGB0480751 | 86 | 4.1 | Yes | Yes | 21.3 | 19.9 | 1.4 | 2B3BD58842954C17BB1AA5FC61A2A937 |  | R22 | Non-TXV |  | 4.767% | 0.95233 | 9.162% | [5 empty] | Non-TXV | 4.767%
Fresno | CA | 93704-3861 |  | 2013-07-12 | 2013-07-12 15:01 | 2013-07-12 15:17 | YORK - D1NH036N05606C | 108 | 3.2 | Yes | Yes | 20.5 | 21 | -0.5 | D56B14DADF764A719C3D79B4D3907B90 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Bakersfield | CA | 93309-5793 |  | 2013-08-21 | 2013-08-21 18:42 | 2013-08-21 18:44 | TEMPSTAR - PGF342080K01A1 | 184 | 11 | Yes | Yes | 23.8 | 21.3 | 2.5 | E96C69B91A4C408098087E8F0D94BD0D |  | R22 | TXV |  | 5.978% | 0.94022 | 11.49% | [5 empty] | TXV | 5.978%
Fresno | CA | 93722-3137 |  | 2013-10-25 | 2013-10-25 16:04 | 2013-10-25 16:49 | CARRIER - UNK | 74 | 4.4 | Yes | Yes | 21.8 | 19.5 | 2.3 | D3AA15D787FD44B8ADB0ECC840AA531C |  | R22 | Non-TXV |  | 5.946% | 0.94054 | 11.43% | [5 empty] | Non-TXV | 5.946%
San Jose | CA | 95132-1304 |  | 2013-10-14 | 2013-10-14 16:02 | 2013-10-14 18:05 | GOODMAN - VSX13004B1AB | 104 | -7.3 | Yes | Yes | 20.3 | 21.2 | -0.9 | 4F856502D7834E0FA8F89DFADABDCC07 |  | R410A | Non-TXV |  | -7.019% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.019%
Clovis | CA | 93612-1714 |  | 2013-09-26 | 2013-09-26 11:33 | 2013-09-26 12:23 | GOODMAN - PGB0240501 | 54 | -4.4 | Yes | Yes | 18.5 | 18.8 | -0.3 | 0CFFB42B960C48969D43AE3B3CFFE97C |  | R22 | Non-TXV |  | -8.148% | 1.0815 | 2.282% |  |  |  |  | Non-TXV |  |  | -8.148%
Fresno | CA | 93726-6814 |  | 2013-06-28 | 2013-06-28 14:47 | 2013-06-28 14:47 | AMERICAN STANDARD - YCC030F1MGBJ | 72 | 0 | Yes | Yes | 29.5 | 23.3 | 6.3 | 8DC48D7A397F412FB183C41C8B41391A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4967 |  | 2013-07-24 | 2013-07-24 10:36 | 2013-07-24 11:04 | YORK - AC030X1021A | 62 | 2.7 | Yes | Yes | 14.3 | 16.6 | -2.3 | 074175C9730D4B78ACBB6AD86F21A800 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.355% | 0.95645 | 8.369% | [5 empty] | Non-TXV | 4.355%
Clovis | CA | 93612-1714 |  | 2013-09-26 | 2013-09-26 10:59 | 2013-09-26 11:29 | CARRIER - 48GS024040301 | 55 | -4.5 | Yes | Yes | 17.7 | 18.3 | -0.6 | 609215AC95804C1FBE8D96EF05F06770 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Fresno | CA | 93720-0248 |  | 2013-07-01 | 2013-07-01 14:56 | 2013-07-01 15:35 | RHEEM - RAND036JA2 | 116 | 5.9 | Yes | Yes | 17.3 | 20.1 | -2.8 | 48CC4399305B4A4DBED061376311A669 |  | R22 | TXV |  | 5.086% | 0.94914 | 9.775% | [5 empty] | TXV | 5.086%
Fresno | CA | 93702-3981 |  | 2013-06-26 | 2013-06-26 17:43 | 2013-06-26 17:43 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 0FD6F4926C064FD1BA45B94A6B6FFC86 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1717 |  | 2013-09-26 | 2013-09-26 13:41 | 2013-09-26 21:17 | CARRIER - 48GS024040301 | 52 | 3.9 | Yes | Yes | 20.9 | 18.8 | 2.1 | 933CDFBE858E4864A147E86D988B371F |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Clovis | CA | 93611-5930 |  | 2013-07-10 | 2013-07-10 14:36 | 2013-07-10 15:03 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 20.5 | 19.3 | 1.2 | AF0096B9814B4CADA907F5A51E658E9A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93710-5438 |  | 2013-07-02 | 2013-07-02 17:38 | 2013-07-02 18:04 | YORK - UNK | 80 | 2.4 | Yes | Yes | 24.3 | 19.3 | 5 | 2CC7CE2DC6924E529964CB5BA6B72092 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Gilroy | CA | 95020-9032 |  | 2013-09-04 | 2013-09-04 10:03 | 2013-09-04 10:03 | CARRIER - 38CKB060300 | 233 | 0 | Yes | Yes | 19.8 | 18.5 | 1.4 | CBA8A3DC1D054C23B8E1D2A65DB9DCA6 |  | R22 | TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-9032 |  | 2013-09-04 | 2013-09-04 10:29 | 2013-09-04 11:07 | CARRIER - 38CKB060300 | 233 | 28.8 | Yes | Yes | 15.9 | 18.2 | -2.3 | C79FD46920D849CD828B4BB4F42A3456 |  | R22 | TXV |  | 12.36% | 0.87639 | 23.75% | [5 empty] | TXV | 12.36%
Gilroy | CA | 95020-9032 |  | 2013-07-29 | 2013-07-29 10:39 | 2013-07-29 10:39 | CARRIER - 38CKC060300 | 233 | 0 | Yes | Yes | 17.3 | 18.7 | -1.4 | EB762B9329EA4F1B8E9ECA6C229C7404 |  | R22 | TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-9032 |  | 2013-07-29 | 2013-07-29 10:53 | 2013-07-29 11:29 | CARRIER - 38YCC024300 | 139 | 8.7 | Yes | Yes | 18.7 | 17.5 | 1.2 | 9BCF5F43F5974FF1B55AE0B8DBB26CBC |  | R22 | TXV |  | 6.259% | 0.93741 | 12.03% | [5 empty] | TXV | 6.259%
Hayward | CA | 94544-6431 |  | 2013-07-31 | 2013-07-31 12:37 | 2013-07-31 12:53 | CARRIER - 38CKB03620 | 142 | 5.2 | Yes | Yes | 18.9 | 17.4 | 1.5 | 3D4983B465A148D18AE2E6EDE2EE026A |  | R22 | TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | TXV | 3.662%
Lamont | CA | 93241-1227 |  | 2013-07-18 | 2013-07-18 13:45 | 2013-07-18 14:03 | OTHER - PGC042K080E | 85 | 8.1 | Yes | Yes | 23.5 | 22 | 1.5 | 5840652CF2474DF6BFFD0730BA1961B6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.529% | 0.90471 | 18.31% | [5 empty] | Non-TXV | 9.529%
Fresno | CA | 93702-4717 |  | 2013-11-08 | 2013-11-08 13:42 | 2013-11-08 13:42 | OTHER - 3A-80-CH-1-5 | 87 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F82259962E77475A8E3FDD2A2986DBF7 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7792 |  | 2013-07-11 | 2013-07-11 10:08 | 2013-07-11 10:09 | CARRIER - 38CMB060300 | 160 | -9.4 | Yes | Yes | 17 | 17 | 0 | BCB59156DC0A40E987D5FFCDB8C61A7D |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Vacaville | CA | 95687-7401 |  | 2013-07-08 | 2013-07-08 15:01 | 2013-07-08 15:46 | PAYNE - 591ANX048000ACAA | 128 | 3.9 | Yes | Yes | 17.5 | 20.4 | -2.9 | D3CF344A428D475BBA218E24732D82BB |  | R22 | Non-TXV |  | 3.047% | 0.96953 | 5.855% | [5 empty] | Non-TXV | 3.047%
Clovis | CA | 93612-1721 |  | 2013-09-26 | 2013-09-26 12:26 | 2013-09-26 12:51 | CARRIER - 48GS02404040301 | 53 | 0 | Yes | Yes | 23.8 | 18.2 | 5.6 | E983B6045C064386B4E4AC6F2BCB704D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-0232 |  | 2013-07-02 | 2013-07-02 09:13 | 2013-07-02 09:34 | HEIL - 867815051 | 113 | 7.3 | Yes | Yes | 22.4 | 18.7 | 3.7 | 20E98F61FE534D90BF67ECA1923AF7E7 |  | R22 | Non-TXV |  | 6.46% | 0.9354 | 12.42% | [5 empty] | Non-TXV | 6.46%
Clovis | CA | 93612-1721 |  | 2013-09-26 | 2013-09-26 13:09 | 2013-09-26 13:39 | GOODMAN - PGB0240501 | 52 | 3.8 | Yes | Yes | 21.1 | 19.9 | 1.2 | B741541F20B54B209EE7F256A08C6B84 |  | R22 | Non-TXV |  | 7.308% | 0.92692 | 14.04% | [5 empty] | Non-TXV | 7.308%
Vacaville | CA | 95687-6502 |  | 2013-07-12 | 2013-07-12 11:30 | 2013-07-12 11:30 | AMERICAN STANDARD - 2A7A1036A1000AA | 73 | 0 | Yes | Yes | 14.2 | 16.5 | -2.3 | 2627C4065CEC4765B3899699AB015568 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-4105 |  | 2013-09-17 | 2013-09-17 10:41 | 2013-09-17 11:02 | TRANE - 2TTR3036A1000AA | 101 | 3.7 | Yes | Yes | 20.5 | 20.4 | 0.1 | B259CF84A1674245B03754C2DA87DD2F |  | R22 | Non-TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | Non-TXV | 3.663%
San Jose | CA | 95148-4105 |  | 2013-09-17 | 2013-09-17 11:07 | 2013-09-17 11:29 | TRANE - MED4TTX4036B | 91 | -6.4 | Yes | Yes | 21.7 | 20.9 | 0.8 | 3EEFD8CD8F084C3CA0830294A1AE1162 |  | R410A | Non-TXV |  | -7.033% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.033%
Vacaville | CA | 95687-7209 |  | 2013-08-06 | 2013-08-06 12:36 | 2013-08-06 12:36 | CARRIER - 38EH0363000 | 116 | 0 | Yes | Yes | 19.6 | 17.2 | 2.4 | 5DC5CB4D58484728827A939ABA3E1CC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5385 |  | 2013-07-16 | 2013-07-16 10:07 | 2013-07-16 10:07 | GIBSON - JS5BD048KA | 126 | 6.5 | Yes | Yes | 31.6 | 22.2 | 9.5 | AB2A1663666349559FD49892E14A9731 | Add refrigerant: 6.5 oz | R22 | TXV |  | 5.159% | 0.94841 | 9.914% | [5 empty] | TXV | 5.159%
Gilroy | CA | 95020-9135 |  | 2013-07-29 | 2013-07-29 09:40 | 2013-07-29 09:40 | OTHER - UNK | 85 | 0 | Yes | Yes | 18.7 | 18.7 | 0 | 9919E9091C3E46569C312C98E9023CA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6435 |  | 2013-09-24 | 2013-09-24 14:11 | 2013-09-24 14:11 | HEIL - CA5548UKB1 | 85 | 0 | Yes | Yes | 22.7 | 18.1 | 4.6 | 303B09FCDC8F4536BC3E57E2EB26CEF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1082 |  | 2013-07-29 | 2013-07-29 18:54 | 2013-07-29 19:02 | YORK - D2NP036N05606A | 108 | 4.7 | Yes | Yes | 22 | 23.7 | -1.7 | A7FB3D1CF64B43819EA1940FF2D68A25 |  | R22 | TXV |  | 4.352% | 0.95648 | 8.363% | [5 empty] | TXV | 4.352%
Fresno | CA | 93705-3140 |  | 2013-06-28 | 2013-06-28 15:48 | 2013-06-28 15:48 | TAPPAN - UKN | 80 | 0 | Yes | Yes | 19.9 | 19.1 | 0.8 | 206A10D73BBB4F68BD3F16A96F21C640 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5807 |  | 2013-08-15 | 2013-08-15 09:31 | 2013-08-15 09:49 | ICP - PGD342060K001C1 | 97 | 12.9 | Yes | Yes | 21.8 | 21.5 | 0.3 | 34B20F8F49C54917BCDA0560FFD55822 |  | R22 | Non-TXV |  | 13.3% | 0.86701 | 25.56% | [5 empty] | Non-TXV | 13.3%
Fresno | CA | 93728-3724 |  | 2013-08-02 | 2013-08-02 12:19 | 2013-08-02 12:36 | - HBBD-FG36SB | 96 | -3.7 | Yes | Yes | 21.8 | 20.7 | 1.1 | CE148151952F44F3A5439D029445966C |  | R22 | TXV |  | -3.854% | 1.0385 | 1.079% |  |  |  |  | TXV |  |  | -3.854%
Bakersfield | CA | 93309-6005 |  | 2013-10-15 | 2013-10-15 17:46 | 2013-10-15 17:49 | HEIL - GPCM036060D | 68 | 2.6 | Yes | Yes | 22.8 | 20.4 | 2.4 | 0EA968589308487FA2BA40E4B3493681 |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Reedley | CA | 93654-3658 |  | 2013-07-09 | 2013-07-09 09:21 | 2013-07-09 09:56 | OTHER - LSR50-1 | 103 | 8.7 | Yes | Yes | 23.9 | 18.6 | 5.3 | 2821D338A0DE48FA908E27FE8EA0F0FD |  | R22 | Non-TXV |  | 8.447% | 0.91553 | 16.23% | [5 empty] | Non-TXV | 8.447%
Fresno | CA | 93711-1691 |  | 2013-06-27 | 2013-06-27 09:32 | 2013-06-27 10:05 | YORK - D1NP042N09006A | 150 | 9.7 | Yes | Yes | 19.4 | 18 | 1.4 | 453B07E831D04A87B69663D8974F51EB |  | R22 | TXV |  | 6.467% | 0.93533 | 12.43% | [5 empty] | TXV | 6.467%
Hayward | CA | 94544-6455 |  | 2013-09-24 | 2013-09-24 12:18 | 2013-09-24 12:37 | TRANE - TTN036C100B4 | 100 | -11.2 | Yes | Yes | 18.7 | 16.9 | 1.8 | 64B7799CD85E4ACEA701012D77395C40 |  | R22 | Non-TXV |  | -11.2% | 1.112 | 3.137% |  |  |  |  | Non-TXV |  |  | -11.2%
Mc Farland | CA | 93250-1077 |  | 2013-07-26 | 2013-07-26 19:48 | 2013-07-26 20:11 | GOODMAN - GPG13360451AB | 112 | 3.7 | Yes | Yes | 23.8 | 19.3 | 4.5 | 019FD91C8D0441CABC9CD2322D8FA837 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
Bakersfield | CA | 93313-5382 |  | 2013-07-23 | 2013-07-23 14:30 | 2013-07-23 15:03 | YORK - TCG060S21S1A | 90 | -6.1 | Yes | Yes | 24.2 | 18.3 | 5.9 | 93706015F635481086C212E79A295D56 |  | R22 | TXV |  | -6.778% | 1.0678 | 1.898% |  |  |  |  | TXV |  |  | -6.778%
Bakersfield | CA | 93306-6653 |  | 2013-08-23 | 2013-08-23 16:37 | 2013-08-23 16:37 | BDP - 585GJW030040ABAF | 58 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | C6785C97BCE9431BBECFBE2E6C86EA76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1837 |  | 2013-07-31 | 2013-07-31 13:49 | 2013-07-31 15:01 | GOODMAN - CKL361L | 84 | 3.5 | Yes | Yes | 20.7 | 17.9 | 2.8 | 915AD69FE98E445AA5F38CDC01F2D28D |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Fresno | CA | 93711-0704 |  | 2013-06-27 | 2013-06-27 15:00 | 2013-06-27 15:28 | DAY & NIGHT - 585A036080YAC | 60 | 10.1 | Yes | Yes | 15.6 | 13.7 | 1.9 | B8E249B0A707411B84E9F070A86A78FC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.83% | 0.83167 | 32.35% | [5 empty] | Non-TXV | 16.83%
Fresno | CA | 93723-9204 |  | 2013-10-25 | 2013-10-25 13:10 | 2013-10-25 14:00 | CARRIER - 38EH042300 | 113 | 4.1 | Yes | Yes | 20.1 | 20.1 | 0 | 10BFF6E4CED243629E1F1E4A5D5BB1FF |  | R22 | TXV |  | 3.628% | 0.96372 | 6.973% | [5 empty] | TXV | 3.628%
Gilroy | CA | 95020-5224 |  | 2013-10-23 | 2013-10-23 16:48 | 2013-10-23 17:16 | NORDYNE - ILLEGIBLE | 80 | 10.9 | Yes | Yes | 25.1 | 20.2 | 4.9 | 972C629D81FF46D2903986F872C6C6FA |  | R22 | Non-TXV |  | 13.63% | 0.86375 | 26.18% | [5 empty] | Non-TXV | 13.63%
Fresno | CA | 93705-4445 |  | 2013-07-03 | 2013-07-03 15:44 | 2013-07-03 16:24 | PAYNE - UNK | 80 | 18.1 | Yes | Yes | 22.7 | 18.6 | 4.1 | 2D44E38F767E4BD8818F2B5EF9816710 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.62% | 0.77375 | 43.48% | [5 empty] | Non-TXV | 22.62%
Parlier | CA | 93648-9630 |  | 2013-08-20 | 2013-08-20 09:24 | 2013-08-20 09:45 | RUUD - UNK | 70 | -4.1 | Yes | Yes | 19 | 19.4 | -0.4 | 5AA755491AFC417CAC812D06574F0FA9 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Fresno | CA | 93725-1837 |  | 2013-07-15 | 2013-07-15 19:38 | 2013-07-15 20:09 | GOODMAN - CK49-1B | 97 | 22.4 | Yes | Yes | 27.9 | 21.9 | 6 | 637A1D9F461E417F9BC75D50296984A1 |  | R22 | Non-TXV |  | 23.09% | 0.76907 | 44.38% | [5 empty] | Non-TXV | 23.09%
Parlier | CA | 93648-9631 |  | 2013-08-30 | 2013-08-30 17:45 | 2013-08-30 17:45 | RUUD - UNK | 85 | 0 | Yes | Yes | 18.6 | 19.9 | -1.3 | B016B3ECEF604165A269AF6876A1693B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3703 |  | 2013-08-23 | 2013-08-23 10:34 | 2013-08-23 10:34 | YORK - D3NZ036N05606NXA | 64 | 0 | Yes | Yes | 21.7 | 19.3 | 2.4 | 892FA7FBA7EC4D86BC6C1B1850BA1CD1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4534 |  | 2013-08-27 | 2013-08-27 15:54 | 2013-08-27 17:05 | DAY & NIGHT - UKN | 83 | 3.9 | Yes | Yes | 21.2 | 20.6 | 0.6 | 3DC33298B3BD4669B7913DFC064A127A |  | R22 | TXV |  | 4.699% | 0.95301 | 9.03% | [5 empty] | TXV | 4.699%
San Jose | CA | 95117-1612 |  | 2013-08-01 | 2013-08-01 12:31 | 2013-08-01 12:31 | COMFORT AIRE - 3115-13180 | 53 | 0 | Yes | Yes | 18.5 | 16.9 | 1.6 | 5BF4CD3FA8744046B445E0B8CE80E842 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1650 |  | 2013-07-31 | 2013-07-31 21:28 | 2013-07-31 22:03 | GOODMAN - GPG10360701A | 75 | 3.3 | Yes | Yes | 27.3 | 21.6 | 5.7 | 5FCF576336374C90ADE58E8B59C3591A |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Bakersfield | CA | 93313-3393 |  | 2013-07-26 | 2013-07-26 11:03 | 2013-07-26 11:43 | YORK - D1NP030N05606A | 73 | -4.6 | Yes | Yes | 26.4 | 20.8 | 5.6 | 875754EAF9564CC9B1D8E23270FF2A8D |  | R22 | TXV |  | -6.301% | 1.063 | 1.765% |  |  |  |  | TXV |  |  | -6.301%
Gilroy | CA | 95020-5224 |  | 2013-10-23 | 2013-10-23 16:19 | 2013-10-23 16:43 | NORDYNE - FS3BA 036KA | 69 | 4.5 | Yes | Yes | 19.9 | 21.9 | -2 | FDBC7A6771B24C9DBF27AB40B6CCD252 |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Bakersfield | CA | 93313-4621 |  | 2013-08-08 | 2013-08-08 11:38 | 2013-08-08 12:06 | HEIL - N2A360AKA200 | 148 | 14.6 | Yes | Yes | 24.6 | 21.2 | 3.5 | 078023241B5A4A8EB608B64B4C40582F |  | R22 | Non-TXV |  | 9.865% | 0.90135 | 18.96% | [5 empty] | Non-TXV | 9.865%
Bakersfield | CA | 93309-6009 |  | 2013-10-15 | 2013-10-15 18:19 | 2013-10-15 18:22 | HEIL - PGC048K080A | 102 | 6.5 | Yes | Yes | 18 | 20.4 | -2.4 | 6F43DB4C594B466E8B42944A0CF8784C |  | R22 | Non-TXV |  | 6.373% | 0.93627 | 12.25% | [5 empty] | Non-TXV | 6.373%
Antioch | CA | 94509-4431 |  | 2013-10-01 | 2013-10-01 12:51 | 2013-10-01 13:23 | GMC - VSC130361AA | 85 | 14.8 | Yes | Yes | 18 | 18.1 | -0.1 | 25AD4F5115F64CAD838FEAABDAFCC70F |  | R22 | Non-TXV |  | 17.41% | 0.82588 | 33.46% | [5 empty] | Non-TXV | 17.41%
Parlier | CA | 93648-9627 |  | 2013-08-19 | 2013-08-19 11:50 | 2013-08-19 12:34 | RUUD - UNK | 70 | 2.3 | Yes | Yes | 18.6 | 17.4 | 1.2 | 95D02F920FA348E5889B33568FE75989 |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Bakersfield | CA | 93309-6009 |  | 2013-07-08 | 2013-07-08 16:17 | 2013-07-08 16:52 | DUCANE - AC10B36-B | 85 | 3.2 | Yes | Yes | 21.7 | 19.3 | 2.5 | 36DD9B9449E549ACA80BB27E960CEEFC |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
San Jose | CA | 95127-3904 |  | 2013-10-09 | 2013-10-09 11:03 | 2013-10-09 11:43 | BRYANT - 113RNA042 A | 113 | 12.9 | Yes | Yes | 21.5 | 19.9 | 1.6 | 4B197B1A6924497481AF470B9C517C28 |  | R410A | Non-TXV |  | 11.42% | 0.88584 | 21.94% | [5 empty] | Non-TXV | 11.42%
Bakersfield | CA | 93307-0000 |  | 2013-07-24 | 2013-07-24 17:47 | 2013-07-24 18:06 | OTHER - 2AC13B36P-1A | 139 | 19.7 | Yes | Yes | 22.2 | 21.5 | 0.7 | 8E188F7370E74073BBE2E7F2622382D5 |  | R22 | Non-TXV |  | 14.17% | 0.85827 | 27.24% | [5 empty] | Non-TXV | 14.17%
Vacaville | CA | 95687-5710 |  | 2013-10-09 | 2013-10-09 11:49 | 2013-10-09 11:50 | AMERICAN STANDARD - 2A7A4036A1000AA | 118 | 4.9 | Yes | Yes | 15.1 | 15.5 | -0.4 | 9054E40AC1084639917295EC6B43FCBF |  | R22 | Non-TXV |  | 4.153% | 0.95847 | 7.98% | [5 empty] | Non-TXV | 4.153%
Bakersfield | CA | 93313-5388 |  | 2013-07-16 | 2013-07-16 14:12 | 2013-07-16 14:12 | OTHER - JS5BD042KA | 122 | 0 | Yes | Yes | 22.9 | 21.4 | 1.5 | 8CBA2733885641EC85988D46B21F6C74 | Actual Subcooling cannot be negative. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3975 |  | 2013-07-25 | 2013-07-25 16:32 | 2013-07-25 16:32 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 21.9 | 20.2 | 1.7 | 2AD484FF68774BACADF8F12CAAC007C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5194 |  | 2013-07-25 | 2013-07-25 14:50 | 2013-07-25 14:50 | OTHER - C18789E3 | 100 | 0 | Yes | Yes | 21.8 | 21.4 | 0.4 | 77E2BE7C81624E5D8D5AB0CC90FF8015 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1001 |  | 2013-09-24 | 2013-09-24 10:18 | 2013-09-24 10:42 | FRIGIDAIRE - FS3BA-060KB | 114 | 7.2 | Yes | Yes | 23.7 | 19.3 | 4.4 | 513EB1A19778433FA0CAE0B04143A1BD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.316% | 0.93684 | 12.14% | [5 empty] | Non-TXV | 6.316%
Oakley | CA | 94561-1636 |  | 2013-10-03 | 2013-10-03 11:57 | 2013-10-03 11:57 | CARRIER - 38CKC036330 | 84 | -7.9 | Yes | Yes | 17 | 17 | 0 | 211FF655668942A9946D0694E7D8C38B |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Bakersfield | CA | 93313-0000 |  | 2013-07-22 | 2013-07-22 17:35 | 2013-07-22 17:57 | - | 141 | 5.9 | Yes | Yes | 14.4 | 16.8 | -2.4 | 119EBE49BCA44E75B98A02A3D3B3FC92 |  | R22 | Non-TXV |  | 4.184% | 0.95816 | 8.041% | [5 empty] | Non-TXV | 4.184%
San Jose | CA | 95148-4102 |  | 2013-10-12 | 2013-10-12 16:32 | 2013-10-12 16:57 | BDP - 561AJ030-A | 65 | -3.8 | Yes | Yes | 25.8 | 20.6 | 5.2 | 1BB90C44156A43D989B924A6C7CF6EA9 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
San Jose | CA | 95148-4102 |  | 2013-10-12 | 2013-10-12 16:58 | 2013-10-12 17:15 | BDP - 561AJ030-A | 65 | -6.1 | Yes | Yes | 25.2 | 20.3 | 4.9 | 8804C12DE54A448A92292CB73BB1AD35 |  | R22 | Non-TXV |  | -9.385% | 1.0938 | 2.628% |  |  |  |  | Non-TXV |  |  | -9.385%
Antioch | CA | 94509-4372 |  | 2013-07-09 | 2013-07-09 10:18 | 2013-07-09 10:20 | CARRIER - 24ABC648A310 | 208 | 7.7 | Yes | Yes | 18.1 | 17.6 | 0.5 | 388D4CF7D31F4B38B251DEB935FA473D |  | R410A | Non-TXV |  | 3.702% | 0.96298 | 7.114% | [5 empty] | Non-TXV | 3.702%
Pleasant Hill | CA | 94523-1600 |  | 2013-07-01 | 2013-07-01 14:55 | 2013-07-01 15:27 | CARRIER - 38EH036300 | 119 | 3.5 | Yes | Yes | 14.2 | 17.2 | -3 | C04505EF44CE4BA8A490E83FECBA1BEB |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93313-5797 |  | 2013-07-22 | 2013-07-22 11:17 | 2013-07-22 11:49 | YORK - PA12NA036 | 85 | 6 | Yes | Yes | 22 | 20.5 | 1.5 | A859448BD08D4CCA88C0FA95B4A880DB |  | R22 | TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | TXV | 7.059%
Arvin | CA | 93203-9602 |  | 2013-08-11 | 2013-08-11 13:53 | 2013-08-11 14:17 | GOODMAN - GPG134807M41AC | 125 | 9.2 | Yes | Yes | 27.3 | 21.5 | 5.8 | 80C430CA3BCD4416A125C7A56D9FC1FA |  | R410A | Non-TXV |  | 7.36% | 0.9264 | 14.14% | [5 empty] | Non-TXV | 7.36%
San Jose | CA | 95127-3747 |  | 2013-10-09 | 2013-10-09 16:43 | 2013-10-09 17:38 | CARRIER - N4A336AKB200 | 89 | 3.6 | Yes | Yes | 26.4 | 20.9 | 5.5 | 2D4E32B8E8034AB89B959CA8BC95130E |  | R410A | TXV |  | 4.045% | 0.95955 | 7.773% | [5 empty] | TXV | 4.045%
Bakersfield | CA | 93313-3504 |  | 2013-07-26 | 2013-07-26 12:04 | 2013-07-26 12:28 | PAYNE - PY3PNA048090NB | 196 | 8 | Yes | Yes | 24.7 | 19.9 | 4.8 | 650CE4FBD242475CA3A02DB27305D14D |  | R22 | Non-TXV |  | 4.082% | 0.95918 | 7.844% | [5 empty] | Non-TXV | 4.082%
Hayward | CA | 94544-6414 |  | 2013-09-24 | 2013-09-24 12:56 | 2013-09-24 13:20 | CARRIER - 38CKC036350 | 124 | 7.4 | Yes | Yes | 22 | 17.7 | 4.3 | 15F75D4A5E9343278D58BC98E3A710C3 |  | R22 | TXV |  | 5.968% | 0.94032 | 11.47% | [5 empty] | TXV | 5.968%
San Jose | CA | 95133-2424 |  | 2013-10-21 | 2013-10-21 15:39 | 2013-10-21 18:24 | DAY & NIGHT - 36DNR | 85 | 3.5 | Yes | Yes | 20.6 | 20.4 | 0.2 | 312F9987A5E64B8A8CF180261F68C433 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93307-0000 |  | 2013-07-24 | 2013-07-24 18:52 | 2013-07-24 19:09 | OTHER - 2AC13B30P-1A | 129 | 22 | Yes | Yes | 21.8 | 22.1 | -0.3 | 095F1F5E805642CD8956644AE439BE18 |  | R22 | Non-TXV |  | 17.05% | 0.82946 | 32.77% | [5 empty] | Non-TXV | 17.05%
Davis | CA | 95618-4839 |  | 2013-08-07 | 2013-08-07 10:21 | 2013-08-07 10:23 | NORDYNE - JS3BA-024KA | 64 | 4 | Yes | Yes | 18.3 | 17.3 | 1 | 3F6F3C940B5A4E1B995332509FDC1507 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fresno | CA | 93725-1880 |  | 2013-08-09 | 2013-08-09 14:22 | 2013-08-09 14:22 | LENNOX - HS25-311-1P | 129 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 743E92E729E544B890C47ED5A74BDC2D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4835 |  | 2013-08-07 | 2013-08-07 10:59 | 2013-08-07 11:00 | GOODMAN - GSC130241FA | 77 | 6.3 | Yes | Yes | 17.4 | 17.6 | -0.2 | AB7F12B6648048EFBA7E914BF0FBCA80 |  | R22 | Non-TXV |  | 8.182% | 0.91818 | 15.72% | [5 empty] | Non-TXV | 8.182%
Bakersfield | CA | 93307-3975 |  | 2013-07-25 | 2013-07-25 17:15 | 2013-07-25 17:38 | DUCANE - 2AC13B36P-1A | 139 | 23.5 | Yes | Yes | 20.3 | 20.4 | -0.1 | 123867E2BDDE471E9265E4D883862F2F |  | R22 | Non-TXV |  | 16.91% | 0.83094 | 32.49% | [5 empty] | Non-TXV | 16.91%
Bakersfield | CA | 93305-2867 |  | 2013-06-28 | 2013-06-28 15:17 | 2013-06-28 15:36 | PAYNE - RRKAA030JK060X | 54 | 2.7 | Yes | Yes | 25.7 | 20.8 | 4.9 | C42B3F9722434EE8A7455CA4202ACF44 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
San Jose | CA | 95127-1115 |  | 2013-08-02 | 2013-08-02 10:12 | 2013-08-02 10:57 | LENNOX - HSXB15-024-230-01 | 74 | 7.4 | Yes | Yes | 21.6 | 18.8 | 2.8 | 9A79F4B7071646D6B4552D55648F99DB |  | R410A | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
San Jose | CA | 95135-1431 |  | 2013-10-01 | 2013-10-01 12:20 | 2013-10-01 12:56 | CARRIER - UNK | 70 | 4.2 | Yes | Yes | 23.3 | 21 | 2.3 | 2E13D51A5EBF485DBB19E237B3A72CB9 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Hayward | CA | 94544-6455 |  | 2013-07-29 | 2013-07-29 21:58 | 2013-07-29 21:58 | GOODMAN - GSC130421AC | 85 | 0 | Yes | Yes | 22.6 | 18.5 | 4.1 | 1A3728F13F7C41E494AF87208E2A2C23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6645 |  | 2013-07-09 | 2013-07-09 11:47 | 2013-07-09 13:09 | TRANE - 4TTX3036A1000AA | 78 | 2.6 | Yes | Yes | 16.3 | 18.6 | -2.3 | 8E9FEDA39E45434C8FC2C580E78177DC |  | R410A | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Mc Farland | CA | 93250-1082 |  | 2013-07-26 | 2013-07-26 21:42 | 2013-07-26 21:59 | GOODMAN - GPG13420701AA | 107 | 4.1 | Yes | Yes | 21.6 | 20.4 | 1.2 | CD75534C467C459AB6218EE8C7578F66 |  | R22 | Non-TXV |  | 3.832% | 0.96168 | 7.364% | [5 empty] | Non-TXV | 3.832%
Bakersfield | CA | 93313-5468 |  | 2013-07-17 | 2013-07-17 09:06 | 2013-07-17 09:27 | WESTINGHOUSE - FS3BC-060KA | 85 | 4 | Yes | Yes | 20.5 | 20.4 | 0.1 | 66D8822FAC03409D820256F1C7AFA5AF |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Vallejo | CA | 94591-4148 |  | 2013-07-17 | 2013-07-17 14:36 | 2013-07-17 14:55 | OTHER - | 85 | -3 | Yes | Yes | 16.1 | 17.2 | -1.1 | 2A0FD01609994A26AF8994315C3FAB3A |  | R22 | Non-TXV |  | -3.529% | 1.0353 | 0.9884% |  |  |  |  | Non-TXV |  |  | -3.529%
Mc Farland | CA | 93250-1082 |  | 2013-07-26 | 2013-07-26 21:29 | 2013-07-26 22:00 | GOODMAN - GPG13360451AB | 112 | 4.3 | Yes | Yes | 22.4 | 18.9 | 3.5 | 077A374F2BBD4DE0BC34DF76BA113B6C |  | R22 | Non-TXV |  | 3.839% | 0.96161 | 7.378% | [5 empty] | Non-TXV | 3.839%
Vallejo | CA | 94591-8653 |  | 2013-07-31 | 2013-07-31 10:09 | 2013-07-31 10:32 | CARRIER - 38EN018310SM | 55 | 20.9 | Yes | Yes | 19.7 | 21.4 | -1.7 | EFF05738A1BE474FB2BAF4C667261DB3 |  | R22 | Non-TXV |  | 38% | 0.62 | 73.03% | [5 empty] | Non-TXV | 38%
Vallejo | CA | 94591-8654 |  | 2013-07-31 | 2013-07-31 10:47 | 2013-07-31 10:47 | GUARDIAN - TCGD18S21SHA | 54 | 0 | Yes | Yes | 14.9 | 17.7 | -2.8 | 0457BE9D21074D41B4674A87F22BC3F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5801 |  | 2013-07-22 | 2013-07-22 15:52 | 2013-07-22 16:23 | GIBSON - JS3BC042KA | 102 | 6.6 | Yes | Yes | 24.9 | 20.4 | 4.5 | 51EB1695C96244CDAA633FF01535CCE9 |  | R22 | TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | TXV | 6.471%
Corcoran | CA | 93212-2727 |  | 2013-07-05 | 2013-07-05 12:34 | 2013-07-05 12:54 | GOODMAN - GPG13480701AB | 145 | 4.6 | Yes | Yes | 25.2 | 19.3 | 5.9 | BFBD033D40754F5E8341D57CD8B97EF6 |  | R22 | Non-TXV |  | 3.172% | 0.96828 | 6.097% | [5 empty] | Non-TXV | 3.172%
Shafter | CA | 93263-3538 |  | 2013-08-07 | 2013-08-07 13:02 | 2013-08-07 13:21 | GOODMAN - GPG13300451AA | 77 | 2.9 | Yes | Yes | 27.8 | 22.3 | 5.5 | FA66F3E35C7440D884D9F20A10226552 |  | R22 | Non-TXV |  | 3.766% | 0.96234 | 7.238% | [5 empty] | Non-TXV | 3.766%
Shafter | CA | 93263-3538 |  | 2013-08-07 | 2013-08-07 13:22 | 2013-08-07 13:55 | GOODMAN - GPG13300451AA | 77 | 15.3 | Yes | Yes | 27.2 | 21.4 | 5.8 | FD44C7E430D24796B2CF79494BBC81C9 |  | R22 | Non-TXV |  | 19.87% | 0.8013 | 38.19% | [5 empty] | Non-TXV | 19.87%
Bakersfield | CA | 93306-7926 |  | 2013-07-24 | 2013-07-24 13:28 | 2013-07-24 13:41 | YORK - AC036X1222A | 98 | 13.6 | Yes | Yes | 21.6 | 21.8 | -0.2 | 079028325A994033988630AF08B267EA |  | R22 | Non-TXV |  | 13.88% | 0.86122 | 26.67% | [5 empty] | Non-TXV | 13.88%
Bakersfield | CA | 93313-5908 |  | 2013-07-19 | 2013-07-19 16:17 | 2013-07-19 16:52 | OTHER - JS3050503914 | 102 | 7.2 | Yes | Yes | 21.5 | 24.2 | -2.7 | 7B50AB76EAFA4216A366A967DF6B53B1 |  | R22 | TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | TXV | 7.059%
Bakersfield | CA | 93305-1810 |  | 2013-07-16 | 2013-07-16 14:43 | 2013-07-16 15:08 | TEMPSTAR - PGAD36D1K4 | 102 | 14.2 | Yes | Yes | 20.2 | 21.3 | -1.1 | 3721A999C7FC49B4A736E07A1B5A6637 |  | R22 | TXV |  | 13.92% | 0.86078 | 26.75% | [5 empty] | TXV | 13.92%
Vallejo | CA | 94589-2116 |  | 2013-09-18 | 2013-09-18 11:08 | 2013-09-18 11:45 | TRANE - TTR036C100A3 | 87 | 2.9 | Yes | Yes | 13.6 | 16.6 | -3 | B55426DE53D543799DE796D895DD9F59 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Davis | CA | 95618-7142 |  | 2013-10-11 | 2013-10-11 09:21 | 2013-10-11 09:22 | YORK - H1RA018S06A | 54 | -4.4 | Yes | Yes | 17.4 | 17.5 | -0.1 | F2731843DD914399A58F5FBC83BAE378 |  | R22 | Non-TXV |  | -8.148% | 1.0815 | 2.282% |  |  |  |  | Non-TXV |  |  | -8.148%
Bakersfield | CA | 93309-3459 |  | 2013-07-30 | 2013-07-30 17:16 | 2013-07-30 17:19 | HEIL - PGF324040K01A1 | 120 | 4.4 | Yes | Yes | 20.2 | 19.9 | 0.3 | 100C603EEF054012A3D94A10C6B6324C |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
San Jose | CA | 95117-1612 |  | 2013-08-02 | 2013-08-02 11:06 | 2013-08-02 11:45 | NORDYNE - GS3BA-042KA | 85 | 12 | Yes | Yes | 22.1 | 18.6 | 3.5 | 8399560C467E49D3A1720BE8B228770B |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Bakersfield | CA | 93307-3976 |  | 2013-09-27 | 2013-09-27 13:58 | 2013-09-27 13:58 | OTHER - 2AC13B30P-1A | 129 | 0 | Yes | Yes | 17.8 | 20.6 | -2.8 | 6662DC799AB74818ADD3C22177A1147A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5717 |  | 2013-07-08 | 2013-07-08 11:34 | 2013-07-08 11:54 | YORK - DINH048NO6506C | 85 | 3 | Yes | Yes | 29 | 23.1 | 5.9 | 3ED6EC37419347F68F54093584BADD22 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
San Jose | CA | 95135-1318 |  | 2013-08-02 | 2013-08-02 12:22 | 2013-08-02 12:56 | GE - RGT49241L | 42 | 8 | Yes | Yes | 20.6 | 18.1 | 2.5 | CD67095818504932920EBBBAB369B243 |  | R22 | Non-TXV |  | 19.05% | 0.80952 | 36.61% | [5 empty] | Non-TXV | 19.05%
Vallejo | CA | 94591-8658 |  | 2013-07-31 | 2013-07-31 11:12 | 2013-07-31 11:32 | CARRIER - 4387E555848 | 62 | 12 | Yes | Yes | 17.3 | 18.2 | -0.9 | C7BF3FC2E5534219934BAC664506A245 |  | R22 | Non-TXV |  | 19.35% | 0.80645 | 37.2% | [5 empty] | Non-TXV | 19.35%
Vacaville | CA | 95687-3402 |  | 2013-07-10 | 2013-07-10 11:21 | 2013-07-10 11:40 | GOODMAN - GSC130301CA | 106 | 3.1 | Yes | Yes | 16.6 | 17.7 | -1.1 | 44702E8716964D29A7ADBEDAA7E4CEC2 |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
San Jose | CA | 95127-2524 |  | 2013-10-09 | 2013-10-09 09:19 | 2013-10-09 09:45 | TRANE - 2TTR1060A1000AA | 132 | -12.4 | Yes | Yes | 22.1 | 19.9 | 2.2 | 90DF3AF2D24040609B74253164C0770D |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
Davis | CA | 95618-4896 |  | 2013-09-30 | 2013-09-30 12:08 | 2013-09-30 20:58 | GE - BGTA712B1A | 30 | 11.5 | Yes | Yes | 21 | 15.2 | 5.8 | 0B1A0E0FA43847048922A2830E5563C2 |  | R22 | Non-TXV |  | 38.33% | 0.61667 | 73.67% | [5 empty] | Non-TXV | 38.33%
Bakersfield | CA | 93309-4510 |  | 2013-08-21 | 2013-08-21 11:12 | 2013-08-21 12:14 | RHEEM - RRNL-B030JK06X | 85 | 11.7 | Yes | Yes | 18.5 | 19.7 | -1.2 | 99E5E2FC6261463CA3A38E3670F337DD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.76% | 0.86235 | 26.45% | [5 empty] | Non-TXV | 13.76%
Pittsburg | CA | 94565-1766 |  | 2013-07-23 | 2013-07-23 10:06 | 2013-07-23 10:31 | HEIL - CA3060VKA2 | 144 | 12.6 | Yes | Yes | 16.6 | 17.6 | -1 | A45FD419182348E5AE9F6E8C3700A56A |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Bakersfield | CA | 93313-2530 |  | 2013-07-09 | 2013-07-09 18:25 | 2013-07-09 19:00 | BRYANT - 57BNW04809NA | 85 | 4.8 | Yes | Yes | 23.3 | 21.5 | 1.8 | D462774984764ECA9F5A71712D3BDDA5 | Add refrigerant: 4.8 oz | R410A | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Lemoore | CA | 93245-5276 |  | 2013-06-27 | 2013-06-27 15:42 | 2013-06-27 16:09 | YORK - H2RC048S060 | 119 | 14 | Yes | Yes | 21.3 | 19.5 | 1.9 | B6374BF8C4DD49BA8996EF1A55D42BE6 |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Vacaville | CA | 95687-4841 |  | 2013-08-21 | 2013-08-21 10:20 | 2013-08-21 14:52 | CARRIER - 38CKC018330 | 51 | 1.9 | Yes | Yes | 15.6 | 17.2 | -1.6 | 2A29574BBCC54A4EB292A9F806E314F8 |  | R22 | Non-TXV |  | 3.725% | 0.96275 | 7.16% | [5 empty] | Non-TXV | 3.725%
Davis | CA | 95616-7549 |  | 2013-08-12 | 2013-08-12 10:57 | 2013-08-12 11:47 | BRYANT - 561CJX018000ACAA | 61 | 4.6 | Yes | Yes | 15.3 | 17 | -1.7 | E62F5C2132CF493086013F13458CC1A9 |  | R22 | Non-TXV |  | 7.541% | 0.92459 | 14.49% | [5 empty] | Non-TXV | 7.541%
Lemoore | CA | 93245-2928 |  | 2013-06-27 | 2013-06-27 09:18 | 2013-06-27 09:41 | CARRIER - 48GX03006030IAD | 68 | 5.7 | Yes | Yes | 21 | 18.8 | 2.2 | 6BECC407BD2546B9ADB58EB541716E9E |  | R22 | Non-TXV |  | 8.382% | 0.91618 | 16.11% | [5 empty] | Non-TXV | 8.382%
Vacaville | CA | 95687-6215 |  | 2013-10-09 | 2013-10-09 10:48 | 2013-10-09 10:49 | TRANE - 2TTR3036A1000AA | 101 | -8.3 | Yes | Yes | 20.4 | 18.1 | 2.3 | C329CAE029E4437887B48DF1A0915F3B |  | R22 | Non-TXV |  | -8.218% | 1.0822 | 2.301% |  |  |  |  | Non-TXV |  |  | -8.218%
San Jose | CA | 95127-4722 |  | 2013-10-14 | 2013-10-14 13:56 | 2013-10-14 14:29 | LUXAIRE - UNK | 120 | 8.4 | Yes | Yes | 18.2 | 19.6 | -1.4 | C979BA71BC5D48F1BAA506604071518B |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Lemoore | CA | 93245-4344 |  | 2013-07-08 | 2013-07-08 16:25 | 2013-07-08 16:43 | RHEEM - RRKAA036JK06X | 62 | 6.2 | Yes | Yes | 22.2 | 21.4 | 0.8 | 9738AB86146445C8B53F9790B4E497EF |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Vallejo | CA | 94591-8655 |  | 2013-08-02 | 2013-08-02 12:18 | 2013-08-02 12:19 | CARRIER - 38EN030340 | 97 | -8 | Yes | Yes | 16.7 | 17.6 | -0.9 | DA130A37632A46BAB124D99F95873540 |  | R22 | Non-TXV |  | -8.247% | 1.0825 | 2.31% |  |  |  |  | Non-TXV |  |  | -8.247%
Antioch | CA | 94509-1533 |  | 2013-07-11 | 2013-07-11 10:55 | 2013-07-11 10:56 | TRANE - YCC030F1L0BH | 68 | 2.3 | Yes | Yes | 17.9 | 18.6 | -0.7 | DDD379C26CCB4A5E9B10993B42C69DB2 |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Fairfield | CA | 94533-2429 |  | 2013-07-22 | 2013-07-22 14:56 | 2013-07-22 16:04 | GE - | 85 | -3 | Yes | Yes | 16.8 | 18.2 | -1.4 | 07CE89B4D5D8401F9A8F432C442FC9C6 |  | R22 | Non-TXV |  | -3.529% | 1.0353 | 0.9884% |  |  |  |  | Non-TXV |  |  | -3.529%
Fairfield | CA | 94533-2708 |  | 2013-07-19 | 2013-07-19 15:33 | 2013-07-19 15:33 | TRANE - TTR036C100A2 | 92 | 0 | Yes | Yes | 15.6 | 17.9 | -2.3 | 94ADA980A74E4914B0EEEA6AEBCA3CB3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1333 |  | 2013-08-02 | 2013-08-02 11:51 | 2013-08-02 12:13 | GE - TA924H1F | 85 | 19.7 | Yes | Yes | 22.1 | 18.4 | 3.7 | CA340EBAB36B49E78BA1E6AC363AA4D1 |  | R22 | Non-TXV |  | 23.18% | 0.76824 | 44.54% | [5 empty] | Non-TXV | 23.18%
Suisun City | CA | 94585-6602 |  | 2013-08-01 | 2013-08-01 09:37 | 2013-08-01 10:02 | CARRIER - 38ETC042300 | 133 | 5.2 | Yes | Yes | 19.6 | 20.2 | -0.5 | 032A10DE15254BE7B86FB918C239F9A1 |  | R410A | TXV |  | 3.91% | 0.9609 | 7.514% | [5 empty] | TXV | 3.91%
Fairfield | CA | 94533-6826 |  | 2013-07-22 | 2013-07-22 14:07 | 2013-07-22 14:43 | PAYNE - 591ANX048000ACAA | 128 | 4.5 | Yes | Yes | 19.5 | 18.2 | 1.3 | 597A8911B5D0483C9084756CF8EC5492 |  | R22 | Non-TXV |  | 3.516% | 0.96484 | 6.756% | [5 empty] | Non-TXV | 3.516%
Fresno | CA | 93720-2453 |  | 2013-09-20 | 2013-09-20 09:30 | 2013-09-20 10:13 | OTHER - UKN | 80 | 3.7 | Yes | Yes | 19.9 | 20.4 | -0.5 | 1E3EBB3978A840898D5D48BA12726EC5 |  | R22 | Non-TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | Non-TXV | 4.625%
Bakersfield | CA | 93305-2843 |  | 2013-07-23 | 2013-07-23 11:07 | 2013-07-23 11:43 | RHEEM - ILLEGIBLE | 98 | 6.3 | Yes | Yes | 24.3 | 20.1 | 4.2 | 02FA35A623BB4D0D92028BCAD1CEDCB1 |  | R22 | Non-TXV |  | 6.429% | 0.93571 | 12.35% | [5 empty] | Non-TXV | 6.429%
San Jose | CA | 95148-3015 |  | 2013-09-17 | 2013-09-17 15:40 | 2013-09-17 16:10 | MONTGOMERY WARD - SRM51254A | 97 | 3 | Yes | Yes | 19.6 | 19.7 | -0.1 | EBD3281BF880495E8E04F47EC53AE466 |  | R22 | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Shafter | CA | 93263-2429 |  | 2013-08-05 | 2013-08-05 19:03 | 2013-08-05 19:06 | BRYANT - 582AJW0481090AAAG | 81 | 4.5 | Yes | Yes | 22.4 | 21 | 1.4 | 3363FFBBE8704165832FC450E7E6F01B |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Vacaville | CA | 95687-5752 |  | 2013-07-12 | 2013-07-12 11:01 | 2013-07-12 11:01 | GE - | 85 | 0 | Yes | Yes | 16.1 | 16.5 | -0.4 | D38F88A216CE4B2EA28C651B8BF7CA9C | Liquid Temperature cannot be less than outdoor air temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-5278 |  | 2013-08-02 | 2013-08-02 14:34 | 2013-08-02 14:55 | YORK - H2RC042S06G | 109 | 13.3 | Yes | Yes | 21 | 18.7 | 2.3 | 8AEE025399134EEBAE7729C1B3CBEBF9 |  | R22 | Non-TXV |  | 12.2% | 0.87798 | 23.45% | [5 empty] | Non-TXV | 12.2%
San Jose | CA | 95121-1802 |  | 2013-08-02 | 2013-08-02 13:20 | 2013-08-02 13:20 | LENNOX - 13ACX-036-230-17 | 84 | 0 | Yes | Yes | 17.6 | 17.5 | 0.1 | 534899D3DE524BE4B553D37DC514368B |  | R410A | TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2232 |  | 2013-08-07 | 2013-08-07 10:55 | 2013-08-07 11:41 | YORK - D1NA036N05606C | 67 | -6.3 | Yes | Yes | 23 | 20.1 | 3 | 074325269FD4457F9BCEEC2E91D85EE2 |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
San Jose | CA | 95127-2935 |  | 2013-10-09 | 2013-10-09 10:06 | 2013-10-09 10:37 | CARRIER - 38CKC030340 | 66 | 3.4 | Yes | Yes | 18.6 | 19.9 | -1.3 | 0C16D9E71DB8484AA4495BF70CFA1C76 |  | R22 | Non-TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | Non-TXV | 5.152%
Lemoore | CA | 93245-1933 |  | 2013-08-27 | 2013-08-27 15:46 | 2013-08-27 16:05 | CARRIER - 48GX042090301AD | 121 | 3.8 | Yes | Yes | 19.9 | 21.7 | -1.8 | 0CFBE318591343CE895336A5DC25904D |  | R22 | Non-TXV |  | 3.14% | 0.9686 | 6.035% | [5 empty] | Non-TXV | 3.14%
Bakersfield | CA | 93311-9027 |  | 2013-07-09 | 2013-07-09 18:13 | 2013-07-09 18:38 | YORK - H2C048S06G | 119 | 3.8 | Yes | Yes | 19.5 | 17.8 | 1.8 | DEB8C72B6AC443BEA0F78058BCE527AA |  | R22 | Non-TXV |  | 3.193% | 0.96807 | 6.137% | [5 empty] | Non-TXV | 3.193%
Antioch | CA | 94509-3806 |  | 2013-08-21 | 2013-08-21 10:07 | 2013-08-21 10:07 | TRANE - 2TTB0030A1000AA | 64 | 2.4 | Yes | Yes | 16.4 | 17.3 | -0.9 | 7BF99814D23744F790190B061134EBB0 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Lemoore | CA | 93245-4139 |  | 2013-08-27 | 2013-08-27 13:28 | 2013-08-27 13:50 | LENNOX - GCS29030751PA | 51 | 2.6 | Yes | Yes | 20.6 | 20.5 | 0.2 | C782CCC5FC074939B2A3ECAFF7C59AE2 |  | R22 | Non-TXV |  | 5.098% | 0.94902 | 9.797% | [5 empty] | Non-TXV | 5.098%
Bakersfield | CA | 93305-2408 |  | 2013-06-27 | 2013-06-27 08:31 | 2013-06-27 08:56 | ICP - PGC0300K060D | 52 | 1.7 | Yes | Yes | 18 | 19.6 | -1.6 | 46F6862EF1F44C2887CC23E60DB3AC0A |  | R22 | Non-TXV |  | 3.269% | 0.96731 | 6.283% | [5 empty] | Non-TXV | 3.269%
Bakersfield | CA | 93309-6242 |  | 2013-07-10 | 2013-07-10 10:47 | 2013-07-10 11:14 | GOODMAN - GPG1330045M4YAB | 65 | 1.9 | Yes | Yes | 17.5 | 19.9 | -2.4 | 71435AE5CE294B15924DC7B49C60AC14 |  | R410A | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Bakersfield | CA | 93309-6280 |  | 2013-08-27 | 2013-08-27 07:59 | 2013-08-27 08:18 | GOODMAN - PGB030050-1 | 85 | 2.6 | Yes | Yes | 15.5 | 17.7 | -2.2 | F7E3D82223CB4542B450AF7C918D281F |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Antioch | CA | 94531-8324 |  | 2013-07-11 | 2013-07-11 11:33 | 2013-07-11 11:34 | RHEEM - RAFD-060JBS | 118 | 6.4 | Yes | Yes | 16.7 | 17.6 | -0.9 | 6E3291445EF648448D1DDFCF026AF74F |  | R22 | Non-TXV |  | 5.424% | 0.94576 | 10.42% | [5 empty] | Non-TXV | 5.424%
Bakersfield | CA | 93305-2030 |  | 2013-07-25 | 2013-07-25 14:10 | 2013-07-25 14:41 | RHEEM - RRNA-B036JK06X | 83 | -5.9 | Yes | Yes | 18.6 | 21.5 | -2.9 | 98EF131E34A34C509198CBE977B3014F |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Antioch | CA | 94531-7416 |  | 2013-07-11 | 2013-07-11 11:18 | 2013-07-11 11:19 | GOODMAN - CK36-1T | 76 | -5.4 | Yes | Yes | 15.6 | 17.6 | -2 | DE626D68721A41A0B8D8C5BB23210188 |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Fresno | CA | 93711-1512 |  | 2013-07-18 | 2013-07-18 18:36 | 2013-07-18 18:36 | TRANE - YCY036G1MOAB | 129 | 0 | Yes | Yes | 21.8 | 21.4 | 0.4 | B2AB326B54A247458E2D1C104BF6C765 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-5000 |  | 2013-07-29 | 2013-07-29 09:13 | 2013-07-29 09:13 | GOODMAN - UNK | 125 | 0 | Yes | Yes | 35 | 21.4 | 13.6 | 05947A2CCA934218B8C3820448A7362F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8928 |  | 2013-07-11 | 2013-07-11 12:30 | 2013-07-11 12:30 | CARRIER - 38CK042300 | 88 | 0 | Yes | Yes | 14.6 | 16.8 | -2.2 | 4F1E60D5340240F1A9A26A28D5A65837 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-2416 |  | 2013-10-15 | 2013-10-15 17:03 | 2013-10-15 18:01 | RUUD - UAKA-048JAZ | 103 | -8.5 | Yes | Yes | 20.9 | 18.6 | 2.4 | C55BDA2EDF4F4278AC128F113FA776A2 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -8.252% | 1.0825 | 2.311% |  |  |  |  | Non-TXV |  |  | -8.252%
Fremont | CA | 94539-8109 |  | 2013-09-23 | 2013-09-23 11:42 | 2013-09-23 11:42 | CARRIER - 38CKC00330 | 89 | 0 | Yes | Yes | 19.5 | 17.2 | 2.3 | F5E20AAFF3144E448193487E1F3F3E66 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2814 |  | 2013-07-16 | 2013-07-16 19:51 | 2013-07-16 19:51 | OTHER - CA48K-1S | 115 | 0 | Yes | Yes | 20.6 | 19.8 | 0.8 | 87825FCA968F4869B2A857CB0A6D3B7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2650 |  | 2013-09-16 | 2013-09-16 11:01 | 2013-09-16 11:18 | YORK - D1NH048N06506C | 128 | 10.7 | Yes | Yes | 22 | 22.1 | -0.1 | 63B8817D10694045BE9A58059557019C |  | R22 | Non-TXV |  | 8.359% | 0.91641 | 16.06% | [5 empty] | Non-TXV | 8.359%
Bakersfield | CA | 93309-2012 |  | 2013-07-05 | 2013-07-05 09:57 | 2013-07-05 10:19 | CARRIER - 585WJ036ACAF | 85 | 17.3 | Yes | Yes | 22.8 | 20.4 | 2.4 | 4A8B24F34E7A46A985DAF5019284C54F |  | R22 | Non-TXV |  | 20.35% | 0.79647 | 39.11% | [5 empty] | Non-TXV | 20.35%
Vallejo | CA | 94591-8214 |  | 2013-07-31 | 2013-07-31 13:01 | 2013-07-31 14:56 | TRANE - TTN036D100A0 | 86 | 12 | Yes | Yes | 17 | 19.3 | -2.3 | 190535AAA6FC48DAA9CD005992E8351C |  | R22 | Non-TXV |  | 13.95% | 0.86047 | 26.82% | [5 empty] | Non-TXV | 13.95%
Bakersfield | CA | 93313-4988 |  | 2013-07-24 | 2013-07-24 14:40 | 2013-07-24 15:27 | RHEEM - VAKA037JAZ | 79 | 17.2 | Yes | Yes | 23.5 | 21.3 | 2.3 | EAE1C586D8864204B65D99B3221637CC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.77% | 0.78228 | 41.84% | [5 empty] | Non-TXV | 21.77%
Bakersfield | CA | 93306-8302 |  | 2013-07-24 | 2013-07-24 14:24 | 2013-07-24 14:24 | YORK - H1RA042506A | 84 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 4EC4587AF1084AA4B4929090A7C13545 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-08-27 | 2013-08-27 20:01 | 2013-08-27 20:13 | YORK - D1NA036N05606C | 67 | 2.8 | Yes | Yes | 26.1 | 20.7 | 5.4 | D4DEBAFB4AC44539BE84EC38346A983B |  | R22 | Non-TXV |  | 4.179% | 0.95821 | 8.031% | [5 empty] | Non-TXV | 4.179%
Arvin | CA | 93203-9464 |  | 2013-08-20 | 2013-08-20 11:51 | 2013-08-20 12:51 | GOODMAN - GSC130481AF | 152 | 5.4 | Yes | Yes | 20.4 | 20.8 | -0.4 | 995056A6E732493E961189213A6C2D91 |  | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
San Jose | CA | 95127-4212 |  | 2013-08-05 | 2013-08-05 09:05 | 2013-08-05 09:25 | CARRIER - 38CK036310 | 152 | 13 | Yes | Yes | 23.8 | 18.2 | 5.6 | DD0767A8C6414DBF9CC7CE6E33875E94 |  | R22 | Non-TXV |  | 8.553% | 0.91447 | 16.44% | [5 empty] | Non-TXV | 8.553%
Davis | CA | 95618-7141 |  | 2013-10-15 | 2013-10-15 10:33 | 2013-10-15 10:33 | OTHER - N2A318AKC200 | 53 | -3.1 | Yes | Yes | 17.5 | 17.9 | -0.4 | 701BF8CC221B446E9103DD08E5BB5814 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
San Jose | CA | 95127-4321 |  | 2013-10-09 | 2013-10-09 11:46 | 2013-10-09 12:05 | CARRIER - 593CJ042 A | 88 | 22.4 | Yes | Yes | 18.1 | 20.2 | -2.1 | 5F945D7D498B41B0923535DF12323AB2 |  | R22 | Non-TXV |  | 25.45% | 0.74545 | 48.92% | [5 empty] | Non-TXV | 25.45%
Bakersfield | CA | 93309-6256 |  | 2013-08-27 | 2013-08-27 11:39 | 2013-08-27 12:11 | GOODMAN - GPG1330C451BB | 77 | 5.8 | Yes | Yes | 15.7 | 18.6 | -2.9 | F555B2CB66CF49F58BB6030016CE1958 |  | R22 | Non-TXV |  | 7.532% | 0.92468 | 14.48% | [5 empty] | Non-TXV | 7.532%
Bakersfield | CA | 93309-5715 |  | 2013-07-08 | 2013-07-08 11:41 | 2013-07-08 12:56 | YORK - D2NP036N05606NXA | 108 | 6 | Yes | Yes | 24.7 | 21 | 3.7 | 6E8F2E81EE844EA888429A2757F64B7A |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Davis | CA | 95618-7141 |  | 2013-08-12 | 2013-08-12 12:03 | 2013-08-12 12:50 | YORK - H1RA018S06D | 54 | 5.4 | Yes | Yes | 17.8 | 17.4 | 0.4 | EC13AC31DD7840FF9185688969E6D2A1 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93309-6250 |  | 2013-07-10 | 2013-07-10 09:02 | 2013-07-10 09:26 | CARRIER - 585A030080YACR | 50 | 1.5 | Yes | Yes | 13.9 | 16.9 | -3 | 8A96BD33222643DB879F44CC45B05450 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93308-1949 |  | 2013-07-10 | 2013-07-10 18:58 | 2013-07-10 18:58 | RHEEM - RRGH-07N36JKR | 81 | 0 | Yes | Yes | 20.7 | 20.7 | 0 | 20B199A4D74E4F83AA5B0877E27FA8AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1587 |  | 2013-09-11 | 2013-09-11 14:09 | 2013-09-11 14:10 | TRANE - YCY030G1M0A | 120 | 4.7 | Yes | Yes | 17.3 | 17 | 0.3 | A94143904E4C4495BB7D0F96CF58A54F |  | R22 | Non-TXV |  | 3.917% | 0.96083 | 7.527% | [5 empty] | Non-TXV | 3.917%
Bakersfield | CA | 93309-4119 |  | 2013-08-14 | 2013-08-14 10:29 | 2013-08-14 10:57 | RHEEM - RRNA-B03 | 85 | 4.1 | Yes | Yes | 16.4 | 19.3 | -2.9 | E343CF4BE74641CB936975FD920453E5 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Cupertino | CA | 95014-0533 |  | 2013-10-02 | 2013-10-02 11:04 | 2013-10-02 13:16 | LENNOX - HS23 261 1P | 85 | 8 | Yes | Yes | 23.2 | 20.7 | 2.6 | B36EB75F734A4E20A8FB41D0DF1F5FB9 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
San Jose | CA | 95148-2901 |  | 2013-09-17 | 2013-09-17 14:05 | 2013-09-17 15:38 | CARRIER - 24ABB2336A310 | 83 | -5.9 | Yes | Yes | 22.1 | 19.5 | 2.6 | C71B3783CAF347A4AE1516E5D57AA7A4 |  | R410A | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Bakersfield | CA | 93309-7318 |  | 2013-09-04 | 2013-09-04 15:42 | 2013-09-04 15:49 | YORK - D1NH036N05606C | 108 | 14 | Yes | Yes | 21.9 | 21.5 | 0.4 | B069C31EFDA04995B4E901C3DE74ABAF |  | R22 | Non-TXV |  | 12.96% | 0.87037 | 24.91% | [5 empty] | Non-TXV | 12.96%
Bakersfield | CA | 93309-4153 |  | 2013-07-23 | 2013-07-23 17:21 | 2013-07-23 17:50 | GOODMAN - GM580603AX | 75 | 2.3 | Yes | Yes | 18 | 20.4 | -2.4 | 031EF112195040308C39982A119E8748 |  | R410A | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Bakersfield | CA | 93313-4621 |  | 2013-08-06 | 2013-08-06 15:37 | 2013-08-06 16:15 | ICP - N2A348AKA200 | 115 | 14.7 | Yes | Yes | 24.2 | 22.1 | 2.1 | 81C5F52680F34319AB0B95B6A0E3F0EF |  | R22 | TXV |  | 12.78% | 0.87217 | 24.57% | [5 empty] | TXV | 12.78%
Lamont | CA | 93241-2847 |  | 2013-09-11 | 2013-09-11 11:52 | 2013-09-11 12:14 | YORK - DARA F024N040A | 68 | 2.4 | Yes | Yes | 22.2 | 23.2 | -1 | 3F5EB9690ABC4F50B664339296CDB6CF |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93308-6589 |  | 2013-10-08 | 2013-10-08 14:20 | 2013-10-08 14:37 | YORK - AC048X1221A | 122 | 11.7 | Yes | Yes | 20.8 | 21.2 | -0.4 | AB4195CA20FD4877A32D4B7CBA412A92 |  | R22 | Non-TXV |  | 9.59% | 0.9041 | 18.43% | [5 empty] | Non-TXV | 9.59%
Fresno | CA | 93726-1249 |  | 2013-10-31 | 2013-10-31 11:34 | 2013-10-31 12:09 | TAPPAN - IRTA227541S | 41 | 3.6 | Yes | Yes | 21.9 | 19.1 | 2.8 | 982AE3CED65D4A158ACA5C58E545F997 |  | R22 | Non-TXV |  | 8.78% | 0.9122 | 16.87% | [5 empty] | Non-TXV | 8.78%
Fairfield | CA | 94534-3459 |  | 2013-07-24 | 2013-07-24 12:55 | 2013-07-24 15:31 | TRANE - 2TTB3036A1000AA | 101 | 4.1 | Yes | Yes | 15.4 | 17.7 | -2.3 | B9FCBA0FD37440B0BA093B9ABF95780C |  | R22 | Non-TXV |  | 4.059% | 0.95941 | 7.801% | [5 empty] | Non-TXV | 4.059%
San Jose | CA | 95117-1612 |  | 2013-09-26 | 2013-09-26 10:33 | 2013-09-26 10:51 | COLEMAN - DRCS0361BE | 83 | -4.9 | Yes | Yes | 22 | 19.5 | 2.5 | 695710721CCA46628304B5679AA322F3 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Bakersfield | CA | 93309-5665 |  | 2013-08-20 | 2013-08-20 13:55 | 2013-08-20 13:55 | WESTINGHOUSE - JE030AAA0N | 86 | 0 | Yes | Yes | 21.5 | 22.1 | -0.6 | DBB6AA1C2A604483B45214D4AD732B97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-7712 |  | 2013-08-12 | 2013-08-12 12:41 | 2013-08-12 13:04 | YORK - H1DE024S06B | 80 | 7.7 | Yes | Yes | 18.3 | 21 | -2.7 | 6BC2040CCC004B868273E9B5BB34A5D0 |  | R22 | Non-TXV |  | 9.625% | 0.90375 | 18.5% | [5 empty] | Non-TXV | 9.625%
Vacaville | CA | 95687-5934 |  | 2013-08-28 | 2013-08-28 11:16 | 2013-08-28 15:10 | CARRIER - 38CKC048300 | 105 | 4.5 | Yes | Yes | 12.8 | 15.2 | -2.4 | 8008B2203FBD46FD840622B967606F91 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Suisun City | CA | 94585-2126 |  | 2013-08-01 | 2013-08-01 11:21 | 2013-08-01 15:34 | GE - B1B942A100A3 | 80 | -7.5 | Yes | Yes | 15.7 | 18.6 | -2.9 | 52BBA19FE3C84436B543E1E3C1870A50 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Anderson | CA | 96007-3526 |  | 2013-09-04 | 2013-09-04 08:50 | 2013-09-04 09:23 | LENNOX - 10CCS060-100-12A | 110 | 4.6 | Yes | Yes | 24.9 | 19.1 | 5.8 | 8D8C96C5923C4332B605FEB05AC1AB76 |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
San Jose | CA | 95117-1612 |  | 2013-10-14 | 2013-10-14 15:33 | 2013-10-14 16:00 | NORDYNE - JS3BA-042KA | 87 | 2.8 | Yes | Yes | 24.6 | 21.4 | 3.2 | 34C12C578D76433AAD339A07D4DB6860 |  | R22 | Non-TXV |  | 3.218% | 0.96782 | 6.185% | [5 empty] | Non-TXV | 3.218%
Bakersfield | CA | 93307-6954 |  | 2013-08-08 | 2013-08-08 19:47 | 2013-08-08 19:47 | YORK - D1NH042N06506C | 94 | 0 | Yes | Yes | 21.8 | 21.8 | 0 | 5D02DC54B91B40BD833794F0F5D27DD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4706 |  | 2013-07-19 | 2013-07-19 09:27 | 2013-07-19 09:45 | GUARDIAN - GCGD42S41S1A | 69 | -4.1 | Yes | Yes | 23.6 | 19.3 | 4.3 | 25536BDBB7CA40CCB731E2CE1EDA9AE0 |  | R410A | TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | TXV |  |  | -5.942%
Antioch | CA | 94531-8434 |  | 2013-07-15 | 2013-07-15 09:01 | 2013-07-15 09:03 | PAYNE - 561AJ060-F | 156 | -4.7 | Yes | Yes | 14.3 | 17.1 | -2.8 | 8A6DCC737894426A9A4FADEFFC4F16A5 |  | R22 | Non-TXV |  | -3.013% | 1.0301 | 0.8437% |  |  |  |  | Non-TXV |  |  | -3.013%
Vallejo | CA | 94591-7000 |  | 2013-09-06 | 2013-09-06 14:23 | 2013-09-06 16:01 | CARRIER - 38ENO24310 | 62 | 3.1 | Yes | Yes | 18 | 19.8 | -1.8 | C09B6401C4CA4C90909955E2D295E5FA |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Hanford | CA | 93230-9650 |  | 2013-09-23 | 2013-09-23 16:16 | 2013-09-23 16:54 | GOODMAN - G6C130361FA | 83 | 8.5 | Yes | Yes | 21.4 | 20.1 | 1.3 | BC4BFEAD7F0342E5ADF24DAF4BDD437D |  | R22 | Non-TXV |  | 10.24% | 0.89759 | 19.68% | [5 empty] | Non-TXV | 10.24%
Bakersfield | CA | 93309-6245 |  | 2013-08-08 | 2013-08-08 18:16 | 2013-08-08 18:16 | ICP - PSC030K060 | 108 | 0 | Yes | Yes | 21.7 | 20.9 | 0.8 | A4A46C93256946F88A5E74FCEE1E9E39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1754 |  | 2013-09-30 | 2013-09-30 14:55 | 2013-09-30 15:49 | BDP - 561CJ030 | 135 | 6.7 | Yes | Yes | 21.3 | 20.4 | 0.9 | 8E4389B9F98C43A5A713A01FDAB59BA1 |  | R22 | Non-TXV |  | 4.963% | 0.95037 | 9.538% | [5 empty] | Non-TXV | 4.963%
Vacaville | CA | 95687-5218 |  | 2013-10-09 | 2013-10-09 13:33 | 2013-10-09 13:33 | PAYNE - 561CJ036-D | 84 | 0 | Yes | Yes | 17.1 | 16.3 | 0.8 | 933430952E2D4C3FB99DCBAAC4CCCB49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6240 |  | 2013-07-11 | 2013-07-11 17:43 | 2013-07-11 18:03 | TEMPSTAR - PGF330060K01 | 89 | 3 | Yes | Yes | 16.9 | 20.4 | -3.5 | B17ED5F841A140469F4947FB4412351F |  | R22 | Non-TXV |  | 3.371% | 0.96629 | 6.478% | [5 empty] | Non-TXV | 3.371%
San Jose | CA | 95135-1319 |  | 2013-10-02 | 2013-10-02 15:29 | 2013-10-02 16:07 | GE - ILLEGIBLE | 85 | 7.8 | Yes | Yes | 23.9 | 21 | 2.9 | 14CBEF194D9C4C9BB6098DF0D27A55DE |  | R22 | Non-TXV |  | 9.176% | 0.90824 | 17.64% | [5 empty] | Non-TXV | 9.176%
Bakersfield | CA | 93313-5386 |  | 2013-07-21 | 2013-07-21 13:11 | 2013-07-21 14:13 | TRANE - TS5BD-48KA | 126 | 15 | Yes | Yes | 26.7 | 21.2 | 5.5 | E39F3675ADDC4D9EA28A055E7616A023 |  | R22 | TXV |  | 11.9% | 0.88095 | 22.88% | [5 empty] | TXV | 11.9%
Santa Rosa | CA | 95409-6345 |  | 2013-07-11 | 2013-07-11 12:41 | 2013-07-11 12:41 | CARRIER - 38TE042300 | 119 | 0 | Yes | Yes | 18.2 | 19.6 | -1.4 | 371427BF2AC44A008B1BA38152BED1F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1829 |  | 2013-09-19 | 2013-09-19 14:36 | 2013-09-19 15:30 | DAYTON - MAKA-048JAZ | 103 | 12.2 | Yes | Yes | 25.1 | 19.8 | 5.3 | EA4A4B9AE43247C38DFD96A3CF3FFAFD |  | R22 | Non-TXV |  | 11.84% | 0.88155 | 22.76% | [5 empty] | Non-TXV | 11.84%
Bakersfield | CA | 93309-5639 |  | 2013-08-20 | 2013-08-20 13:21 | 2013-08-20 13:21 | ICP - UKN | 90 | 0 | Yes | Yes | 22.6 | 22.1 | 0.5 | DEFF07DB5F2D4A1CA0FCA17A80182326 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6314 |  | 2013-07-09 | 2013-07-09 13:56 | 2013-07-09 13:56 | BRYANT - 574ANW030060NA-- | 129 | 0 | Yes | Yes | 15.6 | 16.5 | -0.9 | B71A24AA92904153BA038C7440291391 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5639 |  | 2013-08-20 | 2013-08-20 10:23 | 2013-08-20 10:56 | YORK - D1NP036N05606A | 108 | 15.6 | Yes | Yes | 21.7 | 21.5 | 0.2 | F92CD75F360548C685394ED7290AD039 |  | R22 | Non-TXV |  | 14.44% | 0.85556 | 27.76% | [5 empty] | Non-TXV | 14.44%
Bakersfield | CA | 93313-2957 |  | 2013-07-10 | 2013-07-10 10:58 | 2013-07-10 11:30 | TRANE - YCPO036F1MOAC | 109 | 3.5 | Yes | Yes | 21.7 | 20.4 | 1.3 | ACAFD15E3FBC49A7848CA630DB203AE0 |  | R22 | Non-TXV |  | 3.211% | 0.96789 | 6.171% | [5 empty] | Non-TXV | 3.211%
Hanford | CA | 93230-9722 |  | 2013-09-20 | 2013-09-20 11:51 | 2013-09-20 12:12 | RHEEM - RRNAB042JK08X | 104 | 6.6 | Yes | Yes | 24.3 | 19.9 | 4.4 | C1A77B9F48D749EF9DF0BFF5ACB231AA |  | R22 | Non-TXV |  | 6.346% | 0.93654 | 12.2% | [5 empty] | Non-TXV | 6.346%
Bakersfield | CA | 93313-4252 |  | 2013-07-12 | 2013-07-12 16:56 | 2013-07-12 18:26 | RHEEM - UAKA-06JAZ | 112 | 12.1 | Yes | Yes | 20.7 | 21.4 | -0.7 | 70806CC653CC441FBC578DF166C0C2ED |  | R22 | Non-TXV |  | 10.8% | 0.89196 | 20.76% | [5 empty] | Non-TXV | 10.8%
Bakersfield | CA | 93313-3941 |  | 2013-07-10 | 2013-07-10 15:26 | 2013-07-10 18:05 | RHEEM - N/A | 85 | 2.5 | Yes | Yes | 20.2 | 22.1 | -1.9 | 12807FBF96B04D57AFC2A32021C84AAF |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93313-5589 |  | 2013-07-24 | 2013-07-24 17:45 | 2013-07-24 18:57 | YORK - H2RD060S06B | 85 | 6.2 | Yes | Yes | 23.1 | 22.4 | 0.8 | E5402A0FCF794246B724650691497ACC |  | R22 | TXV |  | 7.294% | 0.92706 | 14.02% | [5 empty] | TXV | 7.294%
Fairfield | CA | 94534-6866 |  | 2013-08-07 | 2013-08-07 14:10 | 2013-08-07 14:10 | TRANE - TTB048D100A0 | 82 | 0 | Yes | Yes | 16.8 | 18.7 | -1.9 | 9077ACB677444CBCB03CC24ED110FC1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2807 |  | 2013-08-09 | 2013-08-09 12:12 | 2013-08-09 13:40 | DAY & NIGHT - ILLEGIBLE | 68 | 5.6 | Yes | Yes | 25.9 | 20.2 | 5.7 | AF72683D30AF4F01852D126D1CAF4192 |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Bakersfield | CA | 93307-7700 |  | 2013-07-30 | 2013-07-30 14:01 | 2013-07-30 14:19 | YORK - D1NA036N05606C | 67 | 12.3 | Yes | Yes | 19.5 | 22 | -2.5 | 8FCF1CF7181B488DAAB935D10CD65B8A |  | R22 | Non-TXV |  | 18.36% | 0.81642 | 35.28% | [5 empty] | Non-TXV | 18.36%
Bakersfield | CA | 93313-5587 |  | 2013-07-17 | 2013-07-17 11:27 | 2013-07-17 11:49 | YORK - H2RD060S06B | 162 | 7.9 | Yes | Yes | 21.1 | 19.7 | 1.4 | 6DEDCA867B564FE2808A07801912EC3F |  | R22 | Non-TXV |  | 4.877% | 0.95123 | 9.372% | [5 empty] | Non-TXV | 4.877%
Vallejo | CA | 94591-4338 |  | 2013-09-19 | 2013-09-19 08:47 | 2013-09-19 08:47 | OTHER - 561CJ042-A | 85 | 0 | Yes | Yes | 18.9 | 17.1 | 1.8 | 8F3C8F4A134649CAA7F44961BC7F4B04 |  | R22 | TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-5244 |  | 2013-09-23 | 2013-09-23 13:21 | 2013-09-23 13:57 | CARRIER - 38CKC024310 | 136 | 11.8 | Yes | Yes | 21.8 | 16.5 | 5.3 | BB3ADBA5A28246A09DEB220B5E771C83 |  | R22 | TXV |  | 8.676% | 0.91324 | 16.67% | [5 empty] | TXV | 8.676%
Bakersfield | CA | 93304-1143 |  | 2013-10-01 | 2013-10-01 17:35 | 2013-10-01 17:35 | ICP - GPCM30K060F | 70 | 0 | Yes | Yes | 22.2 | 22.1 | 0.1 | BDD567C5DCEE4634A9CE61CF864EC1CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1960 |  | 2013-07-02 | 2013-07-02 11:14 | 2013-07-02 13:00 | TRANE - TTR036100A0 | 79 | 3.5 | Yes | Yes | 17.8 | 17.6 | 0.2 | C73776CEA1774BAC847896066219A9C9 |  | R22 | Non-TXV |  | 4.43% | 0.9557 | 8.514% | [5 empty] | Non-TXV | 4.43%
Antioch | CA | 94509-4519 |  | 2013-07-19 | 2013-07-19 09:16 | 2013-07-19 10:23 | KENMORE - NA | 72 | 2.4 | Yes | Yes | 18.4 | 17.6 | 0.8 | 2480C71B2C4A4961ABAF056F225F4FFD |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Lamont | CA | 93241-1665 |  | 2013-07-18 | 2013-07-18 12:04 | 2013-07-18 12:21 | YORK - D1NH030N03606C | 73 | -6.9 | Yes | Yes | 21.4 | 21.8 | -0.4 | 2173A72FBBC14FDF9C314CF99BD97B1D |  | R22 | Non-TXV |  | -9.452% | 1.0945 | 2.647% |  |  |  |  | Non-TXV |  |  | -9.452%
Bakersfield | CA | 93309-4129 |  | 2013-07-26 | 2013-07-26 09:05 | 2013-07-26 09:27 | PAYNE - PY1PNB042060AAAA | 85 | 2.5 | Yes | Yes | 24.7 | 19.8 | 4.9 | 2DF1B8FF32784558931B5C835E7B0094 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Antioch | CA | 94531-8402 |  | 2013-07-11 | 2013-07-11 13:02 | 2013-07-11 13:05 | DAY & NIGHT - 591AN060-A | 168 | 4.9 | Yes | Yes | 17.1 | 17.6 | -0.5 | F91F9E0F6AE545A7A53AC0EC6ED50A65 |  | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Bakersfield | CA | 93307-3409 |  | 2013-08-16 | 2013-08-16 16:51 | 2013-08-16 17:16 | OTHER - UNK | 85 | 4 | Yes | Yes | 23.2 | 17.5 | 5.7 | 80643C555E234B7998660C570FD7CA11 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
San Jose | CA | 95127-4657 |  | 2013-08-05 | 2013-08-05 09:32 | 2013-08-05 09:32 | OTHER - HAC048AKA1 | 85 | 0 | Yes | Yes | 21.2 | 19.3 | 1.9 | A816F255E01749D79A6D398D1EA327E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-2178 |  | 2013-07-15 | 2013-07-15 09:04 | 2013-07-15 15:59 | CARRIER - 38CKC024340 | 58 | 2.1 | Yes | Yes | 13.7 | 15 | -1.3 | 814AAEA25BBC48B2991E5D6CC6967FF6 |  | R22 | Non-TXV |  | 3.621% | 0.96379 | 6.958% | [5 empty] | Non-TXV | 3.621%
Shafter | CA | 93263-1718 |  | 2013-07-22 | 2013-07-22 18:42 | 2013-07-22 19:04 | PAYNE - PY3PNA060090NB | 192 | 6.2 | Yes | Yes | 20.5 | 18.8 | 1.7 | 85F52928C2BC4891A708D643CEE9548A |  | R22 | Non-TXV |  | 3.229% | 0.96771 | 6.206% | [5 empty] | Non-TXV | 3.229%
Milpitas | CA | 95035-2627 |  | 2013-10-02 | 2013-10-02 12:38 | 2013-10-02 13:13 | YORK - H2RA036S06E | 63 | -3.7 | Yes | Yes | 23.4 | 20.8 | 2.6 | 093F259A33934DE0AA9F2D970F17F72D |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Antioch | CA | 94531-7138 |  | 2013-09-18 | 2013-09-18 11:39 | 2013-09-18 11:53 | CARRIER - 38EH036300 | 116 | 20.5 | Yes | Yes | 18.7 | 18.2 | 0.5 | E5C226E39A044030828D710BD5063B17 |  | R22 | Non-TXV |  | 17.67% | 0.82328 | 33.96% | [5 empty] | Non-TXV | 17.67%
Bakersfield | CA | 93309-5127 |  | 2013-07-03 | 2013-07-03 16:27 | 2013-07-03 17:08 | YORK - DINP03 | 108 | 3.2 | Yes | Yes | 21 | 18.1 | 2.9 | C6D47DBF7A7E41AD9D6298A81D820C0C |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Vallejo | CA | 94591-8157 |  | 2013-08-02 | 2013-08-02 11:55 | 2013-08-02 11:56 | GOODMAN - GSC130481AF | 152 | -10.7 | Yes | Yes | 18.3 | 17.6 | 0.7 | 0FF50F68B3E447DBA2205F44EFCAF67F |  | R22 | Non-TXV |  | -7.039% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.039%
Lemoore | CA | 93245-4373 |  | 2013-08-02 | 2013-08-02 13:32 | 2013-08-02 13:51 | RUUD - UAMA060JAG | 192 | 20.9 | Yes | Yes | 20.4 | 18.7 | 1.7 | 86B8FBE801424FAEB3D554030CD8B6EB |  | R22 | Non-TXV |  | 10.89% | 0.89115 | 20.92% | [5 empty] | Non-TXV | 10.89%
Bakersfield | CA | 93308-5656 |  | 2013-07-12 | 2013-07-12 16:14 | 2013-07-12 16:14 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | DD88F556621D49FCAE55A73E9672FDE0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4663 |  | 2013-07-09 | 2013-07-09 13:15 | 2013-07-09 13:35 | CARRIER - 38CK048320 | 108 | 3.6 | Yes | Yes | 14.8 | 17.2 | -2.4 | CEA3ACADD5FD42E186DF248D6E2A34FF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Santa Rosa | CA | 95409-4141 |  | 2013-07-05 | 2013-07-05 13:48 | 2013-07-05 14:28 | COLEMAN - UKN | 85 | 3.8 | Yes | Yes | 15.8 | 18.6 | -2.8 | BAB4BCA46DB44CC9A281FE65C079D807 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Bakersfield | CA | 93309-6217 |  | 2013-08-14 | 2013-08-14 19:02 | 2013-08-14 19:26 | ICP - PGF336060K01A2 | 148 | 20.8 | Yes | Yes | 21.6 | 22.1 | -0.5 | 017339966F5C408BB79B96D28174D4F5 |  | R22 | Non-TXV |  | 14.05% | 0.85946 | 27.01% | [5 empty] | Non-TXV | 14.05%
Redding | CA | 96003-0000 |  | 2013-07-16 | 2013-07-16 14:04 | 2013-07-16 15:01 | YORK - D2NP042N06506A | 150 | 6.9 | Yes | Yes | 22 | 20.8 | 1.2 | B6F47C0F7A854B528AA649BF0CD91B60 |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Antioch | CA | 94531-7152 |  | 2013-07-16 | 2013-07-16 12:57 | 2013-07-16 12:57 | YORK - E1RA024S06D | 89 | 0 | Yes | Yes | 16.3 | 18.3 | -2 | 989F690F7FD64AA6A237BC934EBAF349 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5640 |  | 2013-08-20 | 2013-08-20 09:46 | 2013-08-20 09:46 | ICP - PGAD-30D1K4 | 78 | 0 | Yes | Yes | 21.7 | 20.9 | 0.8 | FC8D1486EFF34C3AAA49FF935E240637 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2502 |  | 2013-08-05 | 2013-08-05 10:52 | 2013-08-05 11:25 | OTHER - CE30-1HB | 85 | 8.5 | Yes | Yes | 20.9 | 17.4 | 3.5 | AA39F05B434F4CCEB60C6575D9A2FB03 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
San Jose | CA | 95127-2450 |  | 2013-10-09 | 2013-10-09 10:06 | 2013-10-09 10:36 | WEATHER KING - 13AJA36A01 | 108 | 8.8 | Yes | Yes | 24.9 | 20.7 | 4.2 | D29CAB601C504B628AD2D447805B7C2B |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Vacaville | CA | 95687-9403 |  | 2013-07-11 | 2013-07-11 12:35 | 2013-07-11 12:54 | CARRIER - 38TKB042300 | 99 | 3.8 | Yes | Yes | 19.9 | 15.2 | 4.7 | C8F10684601048BC8EDA49BA072EE4EE |  | R22 | Non-TXV |  | 3.838% | 0.96162 | 7.377% | [5 empty] | Non-TXV | 3.838%
San Jose | CA | 95127-4051 |  | 2013-10-14 | 2013-10-14 11:00 | 2013-10-14 11:30 | CARRIER - 38O360G | 99 | 4.9 | Yes | Yes | 20 | 21.7 | -1.7 | C13319AAC1964DB38E67E4B5D22270C5 |  | R22 | Non-TXV |  | 4.949% | 0.95051 | 9.512% | [5 empty] | Non-TXV | 4.949%
San Jose | CA | 95127-2441 |  | 2013-08-05 | 2013-08-05 10:20 | 2013-08-05 10:20 | CARRIER - 38CKC036340 | 124 | 0 | Yes | Yes | 20.6 | 17.4 | 3.2 | F0A89D26CCCE4A0DA25B56013B6BC6ED |  | R22 | TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2441 |  | 2013-07-25 | 2013-07-25 16:00 | 2013-07-25 19:43 | GOODMAN - GPG1336045M41AC | 85 | 3.7 | Yes | Yes | 25.4 | 21.5 | 3.9 | 231B7B4D35F14B8D8CDB685B690765E7 |  | R410A | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Shafter | CA | 93263-2441 |  | 2013-07-25 | 2013-07-25 20:08 | 2013-07-25 20:08 | COMFORT AIRE - CAC048KA1 | 123 | 0 | Yes | Yes | 20.6 | 22.4 | -1.8 | A9EF535FA36F413AA95E2CEDB7D30FD2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3771 |  | 2013-07-29 | 2013-07-29 07:51 | 2013-07-29 07:51 | ICP - PGD360090K001C1 | 101 | 0 | Yes | Yes | 21.5 | 21 | 0.5 | 5AE38C7A85694895820FC10AF7CE823B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Novato | CA | 94949-4931 |  | 2013-08-02 | 2013-08-02 09:17 | 2013-08-02 09:17 | AMANA - RSD30A2A | 125 | 0 | Yes | Yes | 17.1 | 19.9 | -2.8 | D6F0A5138E8E42498C3E558F12D520FD |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-3385 |  | 2013-08-05 | 2013-08-05 13:09 | 2013-08-05 13:56 | YORK - E1RA036S060 | 92 | 15.4 | Yes | Yes | 23.5 | 17.6 | 5.9 | BA933F57F9AE40DFA2F46A3489A1E4B6 |  | R22 | Non-TXV |  | 16.74% | 0.83261 | 32.17% | [5 empty] | Non-TXV | 16.74%
Santa Rosa | CA | 95407-2504 |  | 2013-07-22 | 2013-07-22 10:05 | 2013-07-22 10:06 | CARRIER - 38CKC036340 | 70 | -6.6 | Yes | Yes | 18.9 | 17.6 | 1.3 | 18192F78544A4891A3345A7D5DA165DB |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Bakersfield | CA | 93308-3907 |  | 2013-07-29 | 2013-07-29 06:47 | 2013-07-29 06:47 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | F55BFAA7A57C4A3FB9CA52F6F45D1331 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2515 |  | 2013-07-01 | 2013-07-01 19:54 | 2013-07-01 19:54 | RHEEM - RRNA-B036JK06X | 83 | 0 | Yes | Yes | 19.1 | 19.5 | -0.4 | 69C785B6F22747E8B58105F8D178575D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9109 |  | 2013-07-11 | 2013-07-11 13:20 | 2013-07-11 13:41 | OTHER - 563CN030-A | 103 | 3.1 | Yes | Yes | 13 | 15.9 | -2.9 | 7BE83F49A31942CE826157E515AEE6D9 |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Bakersfield | CA | 93312-1893 |  | 2013-06-26 | 2013-06-26 11:51 | 2013-06-26 12:09 | YORK - H3RC060S06HG | 144 | 30.7 | Yes | Yes | 20.1 | 18.5 | 1.6 | B216F99B940F4A3584B208686417E598 |  | R22 | Non-TXV |  | 21.32% | 0.78681 | 40.97% | [5 empty] | Non-TXV | 21.32%
Bakersfield | CA | 93307-7707 |  | 2013-07-26 | 2013-07-26 12:15 | 2013-07-26 12:15 | ICP - PGF030K060A | 52 | 0 | Yes | Yes | 21.9 | 21.4 | 0.5 | B43636EE0597437A95BB7953EB305333 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5753 |  | 2013-07-12 | 2013-07-12 13:14 | 2013-07-12 13:14 | RHEEM - NA | 72 | 2.2 | Yes | Yes | 18.4 | 17.6 | 0.8 | DF1D4B2AA20A4E14AFCCC85AE5474EDF |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Bakersfield | CA | 93313-5442 |  | 2013-07-16 | 2013-07-16 12:48 | 2013-07-16 13:51 | OTHER - CKL3010 | 70 | 4.2 | Yes | Yes | 20 | 19.9 | 0.1 | BCBB4582BB86490C941BDD173C3435A1 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
San Jose | CA | 95121-2365 |  | 2013-10-08 | 2013-10-08 15:49 | 2013-10-08 16:21 | GOODMAN - GSC130421BA | 95 | 4.5 | Yes | Yes | 25.4 | 19.9 | 5.5 | 57313EC66CEB4A88A67CB6F1A4F16897 |  | R22 | TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | TXV | 4.737%
Bakersfield | CA | 93307-2237 |  | 2013-07-25 | 2013-07-25 12:52 | 2013-07-25 12:52 | GOODMAN - VSC130361BA | 83 | 0 | Yes | Yes | 21.8 | 21.4 | 0.4 | 32BD573BD0514C9680AF9FE30CC86B19 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6243 |  | 2013-07-16 | 2013-07-16 15:55 | 2013-07-16 15:55 | PAYNE - PA13NA036000ABAA | 72 | 0 | Yes | Yes | 17.9 | 19.5 | -1.6 | 4B6A67AC03D142258D2A13568F4561EA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2305 |  | 2013-06-28 | 2013-06-28 12:43 | 2013-06-28 13:10 | CARRIER - 565BJ036-A | 80 | 2.4 | Yes | Yes | 15.1 | 17.7 | -2.6 | AD0D337D5BC146568F90F5705B738409 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Antioch | CA | 94509-5678 |  | 2013-07-16 | 2013-07-16 11:45 | 2013-07-16 11:45 | RHEEM - AP 48B30 | 85 | 0 | Yes | Yes | 18.3 | 19.9 | -1.6 | 3B32C9272AAF4EDABE905998E566EFA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3910 |  | 2013-06-28 | 2013-06-28 13:23 | 2013-06-28 13:39 | RHEEM - RAJC-036JAS | 93 | 3 | Yes | Yes | 12.8 | 14.4 | -1.6 | D12AA6217AE84082BDFDF9E29A1A0C48 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Lamont | CA | 93241-1937 |  | 2013-07-20 | 2013-07-20 12:30 | 2013-07-20 12:30 | GOODMAN - GPG1330045M41AD | 80 | 0 | Yes | Yes | 23.5 | 20.2 | 3.3 | 960049B07F9E4318B9FBDF1689C52600 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1327 |  | 2013-10-17 | 2013-10-17 09:41 | 2013-10-17 10:37 | BRYANT - 561CJ024-D | 51 | 1.8 | Yes | Yes | 22.4 | 20.7 | 1.7 | B150B0E426E54E0CAA1CB11D5EBAA67D |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Antioch | CA | 94509-2131 |  | 2013-07-16 | 2013-07-16 09:37 | 2013-07-16 09:58 | RHEEM - RACA-036JAS | 93 | 4 | Yes | Yes | 16.8 | 18.8 | -2 | F56F884736724C35A6F87B1727105634 |  | R22 | Non-TXV |  | 4.301% | 0.95699 | 8.266% | [5 empty] | Non-TXV | 4.301%
San Jose | CA | 95116-2674 |  | 2013-10-16 | 2013-10-16 13:36 | 2013-10-16 14:18 | NORDYNE - S3BA-036KA | 69 | -4.9 | Yes | Yes | 20.2 | 19.8 | 0.4 | 8C4BBDF0090942E5ACB1647B9DEBEB77 |  | R22 | Non-TXV |  | -7.101% | 1.071 | 1.989% |  |  |  |  | Non-TXV |  |  | -7.101%
Antioch | CA | 94531-8120 |  | 2013-07-15 | 2013-07-15 10:28 | 2013-07-15 10:28 | CARRIER - 38TH042310 | 112 | 0 | Yes | Yes | 17.9 | 17.3 | 0.6 | 270EA9760F03407BBF5114F49E6C46F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6404 |  | 2013-08-09 | 2013-08-09 17:15 | 2013-08-09 17:15 | ICP - PGAA36C1K3 | 81 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 8668C15C7D81414391DACF04D94D2E9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2111 |  | 2013-07-09 | 2013-07-09 12:51 | 2013-07-09 12:52 | GOODMAN - CE36-1GB | 79 | 3.6 | Yes | Yes | 17.4 | 17.6 | -0.2 | 4F54F8A2646B461099ED000D40E8241A |  | R22 | Non-TXV |  | 4.557% | 0.95443 | 8.757% | [5 empty] | Non-TXV | 4.557%
Bakersfield | CA | 93308-4763 |  | 2013-08-14 | 2013-08-14 08:26 | 2013-08-14 09:03 | ICP - PGAA24C1K3 | 64 | 8.6 | Yes | Yes | 21.8 | 21.5 | 0.3 | 78C4840941FF42D6B64C0F9F46FAE1A3 |  | R22 | Non-TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | Non-TXV | 13.44%
San Jose | CA | 95127-3549 |  | 2013-09-19 | 2013-09-19 18:55 | 2013-09-19 20:30 | YORK - H2RA036S06G | 62 | -4.4 | Yes | Yes | 23.4 | 20.4 | 3 | 2D0EC9F8E1EE4F7A9988B2DE91AC9724 |  | R22 | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Antioch | CA | 94531-8412 |  | 2013-07-15 | 2013-07-15 09:24 | 2013-07-15 09:27 | PAYNE - 591AN036-A | 84 | -5.9 | Yes | Yes | 19.4 | 17.9 | 1.5 | 59007A6FE8064B43B20EF0143FF5A776 |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Pittsburg | CA | 94565-4417 |  | 2013-07-18 | 2013-07-18 12:25 | 2013-07-18 12:27 | BRYANT - 561CJ036-E | 70 | 2.7 | Yes | Yes | 18 | 17 | 1 | 52AF0BF190FE478584F4CED7B295AC52 |  | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
Vallejo | CA | 94589-2005 |  | 2013-07-31 | 2013-07-31 12:49 | 2013-07-31 14:47 | HEIL - PGF336060K01A2-- | 146 | 4.7 | Yes | Yes | 15.4 | 17.2 | -1.8 | EA923E015E194599A55BB4C68E9F4CE6 |  | R22 | Non-TXV |  | 3.219% | 0.96781 | 6.187% | [5 empty] | Non-TXV | 3.219%
Arvin | CA | 93203-2783 |  | 2013-08-21 | 2013-08-21 13:54 | 2013-08-21 14:18 | GOODMAN - GPG10420701 | 150 | 5 | Yes | Yes | 22.6 | 20.1 | 2.5 | 9ABA5AD1669B4112A9B6A7F54AD0EDE2 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Sunnyvale | CA | 94086-8724 |  | 2013-09-27 | 2013-09-27 09:43 | 2013-09-27 09:43 | - DRCS0181BD | 67 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | DCA3729562C047FC9D7099CB7431EEF3 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5544 |  | 2013-09-19 | 2013-09-19 12:49 | 2013-09-19 13:28 | RHEEM - RAKA-042JAZ | 79 | 4.7 | Yes | Yes | 13.9 | 16.8 | -2.9 | 9E878E8BBFA04BB69CB6A573C61BFE73 |  | R22 | Non-TXV |  | 5.949% | 0.94051 | 11.43% | [5 empty] | Non-TXV | 5.949%
San Jose | CA | 95116-7011 |  | 2013-09-23 | 2013-09-23 09:30 | 2013-09-23 10:24 | GOODMAN - CKL24-1K | 76 | 12.5 | Yes | Yes | 26.7 | 21.5 | 5.2 | F65F0EF03734401F85CEB9CC42DEC3C1 |  | R22 | Non-TXV |  | 16.45% | 0.83553 | 31.61% | [5 empty] | Non-TXV | 16.45%
Mc Farland | CA | 93250-0000 |  | 2013-07-31 | 2013-07-31 21:18 | 2013-07-31 21:50 | TEMPSTAR - PGAD42D1K3 | 180 | -8 | Yes | Yes | 24.4 | 20.7 | 3.7 | 186CFE765FE048DCA0C3FF832585774F |  | R22 | Non-TXV |  | -4.444% | 1.0444 | 1.245% |  |  |  |  | Non-TXV |  |  | -4.444%
Redding | CA | 96002-9579 |  | 2013-07-17 | 2013-07-17 10:05 | 2013-07-17 11:49 | TEMPSTAR - PGC042K080B | 85 | 7.7 | Yes | Yes | 20.9 | 20.6 | 0.3 | E39230B7984B4E86994D150F5D3E4501 |  | R22 | Non-TXV |  | 9.059% | 0.90941 | 17.41% | [5 empty] | Non-TXV | 9.059%
Antioch | CA | 94531-9056 |  | 2013-07-11 | 2013-07-11 11:56 | 2013-07-11 11:57 | CARRIER - 38CKC036340 | 70 | 6.3 | Yes | Yes | 18.3 | 20.4 | -2.1 | A6E97D3045F14A989E54D975BC5B8339 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Antioch | CA | 94531-9056 |  | 2013-07-11 | 2013-07-11 12:04 | 2013-07-11 12:05 | CARRIER - 38CKC036340 | 70 | 2.9 | Yes | Yes | 16.8 | 17.6 | -0.8 | 20AD4B03EB95419B9351B6B9E0312E6B |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Santa Rosa | CA | 95409-3847 |  | 2013-07-11 | 2013-07-11 10:42 | 2013-07-11 10:42 | DAY & NIGHT - UKN | 85 | -8 | Yes | Yes | 19.2 | 20.4 | -1.2 | B99FDB9825A94E13940AADE5C67657EF | Remove refrigerant: 8 oz Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Vacaville | CA | 95687-5241 |  | 2013-07-11 | 2013-07-11 10:25 | 2013-07-11 10:47 | CARRIER - 360S0330 | 63 | 2 | Yes | Yes | 15.3 | 17.7 | -2.4 | AFC936B9211943CAA500D54C89075968 |  | R22 | Non-TXV |  | 3.175% | 0.96825 | 6.101% | [5 empty] | Non-TXV | 3.175%
Antioch | CA | 94509-4503 |  | 2013-09-30 | 2013-09-30 12:47 | 2013-09-30 12:48 | TRANE - TTR042C100A3 | 92 | 9.3 | Yes | Yes | 17.7 | 17.6 | 0.1 | CFA10C1714094FDDBDE76268A526FEF3 |  | R22 | Non-TXV |  | 10.11% | 0.89891 | 19.43% | [5 empty] | Non-TXV | 10.11%
Bakersfield | CA | 93313-5018 |  | 2013-07-15 | 2013-07-15 09:30 | 2013-07-15 09:53 | TRANE - 2TTR2042B1000AA | 86 | -4.2 | Yes | Yes | 23.5 | 20.6 | 2.9 | 14BE41C51BAC4C36BCAE207F512F707A |  | R22 | TXV |  | -4.884% | 1.0488 | 1.368% |  |  |  |  | TXV |  |  | -4.884%
Shafter | CA | 93263-3524 |  | 2013-08-07 | 2013-08-07 11:43 | 2013-08-07 12:46 | GOODMAN - PGB042075-1B | 80 | -7.5 | Yes | Yes | 19.9 | 19.9 | 0 | B05E041B2D984A3EB97F0065098DFB9E |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93309-4682 |  | 2013-08-05 | 2013-08-05 16:21 | 2013-08-05 16:21 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 19.5 | 20.2 | -0.6 | CC30CD54F7134135A419515B9F3D9CDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-6649 |  | 2013-09-30 | 2013-09-30 20:59 | 2013-09-30 20:59 | GOODMAN - ASC13030014A | 85 | 0 | Yes | Yes | 22.4 | 17.4 | 5 | 953AD81E3B0941C7A88B857113730659 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4692 |  | 2013-08-05 | 2013-08-05 15:41 | 2013-08-05 15:41 | PAYNE - UKN | 90 | 0 | Yes | Yes | 20.9 | 23.1 | -2.2 | 00AAFBE1E1B7446BAE2D9CC20F6B37D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4638 |  | 2013-08-05 | 2013-08-05 18:05 | 2013-08-05 18:05 | BRYANT - 561CJ018D | 51 | 0 | Yes | Yes | 21 | 20.8 | 0.2 | 72069200343648A780D2CFB45428FD6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8828 |  | 2013-07-30 | 2013-07-30 18:12 | 2013-07-30 18:12 | YORK - D2NP030N05606A | 73 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 34A44C2F185541F3A539CA6918630A3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4683 |  | 2013-08-05 | 2013-08-05 17:48 | 2013-08-05 17:48 | ICP - X0946625 | 70 | 0 | Yes | Yes | 20.8 | 18.8 | 2.1 | 04C50CD4D5BE44D88A88A00207BC2ACF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4637 |  | 2013-08-05 | 2013-08-05 19:33 | 2013-08-05 19:33 | BDP - 507C024RCU | 60 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | 4013F6793B2240A798258EEB1FB3C132 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7080 |  | 2013-07-23 | 2013-07-23 14:27 | 2013-07-23 15:33 | ICP - PGAD36D1K3 | 68 | 2.8 | Yes | Yes | 21.3 | 17.1 | 4.2 | D7D5E93269A141B0870FDE400B96F5D8 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93306-4665 |  | 2013-07-17 | 2013-07-17 08:50 | 2013-07-17 09:16 | GOODMAN - GPG153009041AA | 102 | 4.3 | Yes | Yes | 26 | 20.2 | 5.9 | 586E7D28341B42A196FEF7CB8E389D82 |  | R410A | Non-TXV |  | 4.216% | 0.95784 | 8.102% | [5 empty] | Non-TXV | 4.216%
Bakersfield | CA | 93306-4665 |  | 2013-07-17 | 2013-07-17 09:19 | 2013-07-17 09:19 | GOODMAN - GPG153009041AA | 102 | 8 | Yes | Yes | 23.9 | 20.4 | 3.5 | C67CDBF666374BD398F287CED018E708 | Add refrigerant: 8 oz | R410A | Non-TXV |  | 7.843% | 0.92157 | 15.07% | [5 empty] | Non-TXV | 7.843%
Bakersfield | CA | 93308-1406 |  | 2013-07-10 | 2013-07-10 18:28 | 2013-07-10 18:28 | ICP - N2A360AKB200 | 145 | 0 | Yes | Yes | 21 | 19.5 | 1.5 | C194D444566D40CDAA05481529661C16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8819 |  | 2013-07-17 | 2013-07-17 19:57 | 2013-07-17 20:19 | WEATHER KING - 13AJA30A01 | 98 | -4.2 | Yes | Yes | 18.7 | 19.9 | -1.2 | 434031F6F6EA47AD9630859E1F6B7AFF |  | R22 | TXV |  | -4.286% | 1.0429 | 1.2% |  |  |  |  | TXV |  |  | -4.286%
Fresno | CA | 93722-3514 |  | 2013-07-18 | 2013-07-18 14:04 | 2013-07-18 14:04 | CARRIER - UNK | 96 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 286053999BC2429A8AAEC15209721288 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1409 |  | 2013-07-10 | 2013-07-10 16:33 | 2013-07-10 17:44 | RUUD - UAMB-060JAZ | 192 | 36 | Yes | Yes | 19.8 | 20.4 | -0.6 | 103DDE85DE744716B806A08684F6C44A |  | R22 | Non-TXV |  | 18.75% | 0.8125 | 36.03% | [5 empty] | Non-TXV | 18.75%
Bakersfield | CA | 93304-3417 |  | 2013-07-02 | 2013-07-02 11:58 | 2013-07-02 12:25 | NORDYNE - FS58BD-048K | 147 | 30.5 | Yes | Yes | 20.5 | 22.6 | -2.1 | 48310DEAE24948DD8E670A1CD4DAB5A5 |  | R22 | Non-TXV |  | 20.75% | 0.79252 | 39.87% | [5 empty] | Non-TXV | 20.75%
Suisun City | CA | 94585-2173 |  | 2013-07-02 | 2013-07-02 14:06 | 2013-07-02 14:06 | TRANE - BTD730A100A0 | 74 | 0 | Yes | Yes | 23.8 | 19.9 | 3.9 | 43877EC09C544B05B89EE993558B3310 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5122 |  | 2013-08-14 | 2013-08-14 19:20 | 2013-08-14 19:22 | RHEEM - RRGG-07N43JKR | 109 | 4.3 | Yes | Yes | 22.8 | 20.6 | 2.3 | C41128C07B5A4B59980A389A8850A227 |  | R22 | Non-TXV |  | 3.945% | 0.96055 | 7.581% | [5 empty] | Non-TXV | 3.945%
Fresno | CA | 93726-1516 |  | 2013-07-22 | 2013-07-22 13:46 | 2013-07-22 14:16 | RUUD - UAKA037JAZ | 79 | -4.6 | Yes | Yes | 19.1 | 21.9 | -2.8 | A826DB9477C2403EB10EC2A7051AF014 |  | R22 | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Antioch | CA | 94509-5510 |  | 2013-07-16 | 2013-07-16 14:56 | 2013-07-16 14:56 | CARRIER - UKN | 81 | 0 | Yes | Yes | 24.7 | 20.4 | 4.3 | D47130C0AE294438B3962BA4ED27B964 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-8366 |  | 2013-07-24 | 2013-07-24 15:12 | 2013-07-24 15:12 | WEATHER KING - 13JA36A01 | 108 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | E341A5A7C74448A683160C16B4AD50B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1861 |  | 2013-07-10 | 2013-07-10 14:01 | 2013-07-10 14:21 | ICP - PGAA4701K3 | 129 | 27 | Yes | Yes | 24.4 | 22.6 | 1.8 | BFE6E78C2A10403285413015A4D87B94 |  | R22 | Non-TXV |  | 20.93% | 0.7907 | 40.22% | [5 empty] | Non-TXV | 20.93%
Bay Point | CA | 94565-6937 |  | 2013-07-12 | 2013-07-12 14:50 | 2013-07-12 15:23 | GOODMAN - OP1E24-1C | 85 | 3.4 | Yes | Yes | 10.4 | 12.8 | -2.4 | 38C58939E7C9463D89BBE9C25BC0D4E2 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Antioch | CA | 94509-5402 |  | 2013-07-15 | 2013-07-15 10:57 | 2013-07-15 10:57 | BRYANT - 538JNX036000ABAA | 88 | 0 | Yes | Yes | 15.2 | 17.4 | -2.2 | 128EB4D4B14843968ECA4E5A8626291C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5827 |  | 2013-07-24 | 2013-07-24 11:23 | 2013-07-24 15:36 | TRANE - 2TTB0030A1000AA | 64 | 2.9 | Yes | Yes | 15.2 | 17.7 | -2.5 | D7AC6992407E48069FD2FC375251BB11 |  | R22 | Non-TXV |  | 4.531% | 0.95469 | 8.708% | [5 empty] | Non-TXV | 4.531%
Bakersfield | CA | 93313-5388 |  | 2013-07-21 | 2013-07-21 15:59 | 2013-07-21 16:56 | ICP - N2A348AKA200 | 123 | 10 | Yes | Yes | 25.2 | 22.1 | 3.1 | 125DD6F57254481CB3FA5D0257B9935F |  | R22 | TXV |  | 8.13% | 0.9187 | 15.62% | [5 empty] | TXV | 8.13%
Bakersfield | CA | 93309-4358 |  | 2013-09-23 | 2013-09-23 16:28 | 2013-09-23 16:46 | BDP - 585B042100AAAE | 89 | 8.2 | Yes | Yes | 18.8 | 19.5 | -0.7 | F8A24C0F33A8493E9AC047F1C61112CA |  | R22 | Non-TXV |  | 9.213% | 0.90787 | 17.71% | [5 empty] | Non-TXV | 9.213%
Shafter | CA | 93263-2712 |  | 2013-08-30 | 2013-08-30 17:34 | 2013-08-30 17:47 | TRANE - YCY48G1H0AB | 183 | -10.5 | Yes | Yes | 24.1 | 20.4 | 3.7 | C7A04C9396094C2B9530F5312F40B39C |  | R22 | TXV |  | -5.738% | 1.0574 | 1.607% |  |  |  |  | TXV |  |  | -5.738%
Bakersfield | CA | 93307-8825 |  | 2013-08-08 | 2013-08-08 10:04 | 2013-08-08 22:19 | YORK - D2NP036N05606A | 108 | -10.5 | Yes | Yes | 23.1 | 20.4 | 2.7 | 26CC9171D98A4B178DD29F6E9CEFC989 |  | R22 | TXV |  | -9.722% | 1.0972 | 2.723% |  |  |  |  | TXV |  |  | -9.722%
Bakersfield | CA | 93309-4682 |  | 2013-08-05 | 2013-08-05 17:16 | 2013-08-05 17:16 | BDP - UKN | 90 | 0 | Yes | Yes | 22.3 | 21 | 1.3 | 67A986260E954977B31991E688253DD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-9546 |  | 2013-09-07 | 2013-09-07 14:01 | 2013-09-07 14:37 | YORK - PGE10B30D050A-3A | 51 | 5.8 | Yes | Yes | 28.8 | 23.1 | 5.7 | A2203C204DE04D9E87727B915BFA6B00 |  | R22 | Non-TXV |  | 11.37% | 0.88627 | 21.86% | [5 empty] | Non-TXV | 11.37%
Bakersfield | CA | 93309-4680 |  | 2013-08-05 | 2013-08-05 19:02 | 2013-08-05 19:02 | OTHER - UKN | 60 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | FA79ADCCFEF84ACD905C415E0BEB64FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3813 |  | 2013-07-16 | 2013-07-16 10:32 | 2013-07-16 11:43 | CARRIER - 48SS-03606331AA | 66 | -3.3 | Yes | Yes | 20.6 | 21.2 | -0.5 | 31558AF25F4C47FF8E85C90E1324D386 |  | R22 | Non-TXV |  | -5% | 1.05 | 1.4% |  |  |  |  | Non-TXV |  |  | -5%
Bakersfield | CA | 93313-5590 |  | 2013-07-21 | 2013-07-21 09:31 | 2013-07-21 10:04 | YORK - H2RD048S06B | 132 | 25.4 | Yes | Yes | 24.6 | 20.4 | 4.2 | FBAEB0814C5143F6A9080BC9740055AA |  | R22 | Non-TXV |  | 19.24% | 0.80758 | 36.98% | [5 empty] | Non-TXV | 19.24%
San Jose | CA | 95135-1310 |  | 2013-09-30 | 2013-09-30 16:02 | 2013-09-30 16:37 | BRYANT - PA10JA24-B | 64 | 5.1 | Yes | Yes | 22.7 | 17.4 | 5.3 | 9772D64FE41B4CCBB3DBC7E0ACA31DC9 |  | R22 | Non-TXV |  | 7.969% | 0.92031 | 15.31% | [5 empty] | Non-TXV | 7.969%
Bakersfield | CA | 93309-4681 |  | 2013-08-05 | 2013-08-05 17:13 | 2013-08-05 17:13 | GOODMAN - GSC130181FA | 75 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | FD4A128CB3854C36981BF90226EAD795 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8826 |  | 2013-07-25 | 2013-07-25 10:23 | 2013-07-25 11:26 | YORK - D1NP042N06506A | 150 | 7.2 | Yes | Yes | 20.3 | 19.2 | 1.2 | 159B52A2D6D4483BA407929B1E2AA806 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Bakersfield | CA | 93309-4681 |  | 2013-08-05 | 2013-08-05 17:34 | 2013-08-05 17:51 | GOODMAN - GSC13011FA | 75 | 12.3 | Yes | Yes | 21.6 | 21.5 | 0.1 | 000EF5F6FCEC4450AF0A53D034248175 |  | R22 | Non-TXV |  | 16.4% | 0.836 | 31.52% | [5 empty] | Non-TXV | 16.4%
Woodland | CA | 95776-6301 |  | 2013-08-02 | 2013-08-02 09:24 | 2013-08-02 09:24 | AMANA - RCE36C2A | 230 | 0 | Yes | Yes | 16.8 | 19.3 | -2.5 | 69155C32EC2746C49B36AFFDD94BAEFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2690 |  | 2013-09-09 | 2013-09-09 18:14 | 2013-09-09 18:30 | PAYNE - PA1SNR030-K | 65 | 1.9 | Yes | Yes | 18.4 | 19.9 | -1.5 | E29E7B2841AC48CBA9A4EDD88C83AB2C |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Bakersfield | CA | 93309-4618 |  | 2013-08-15 | 2013-08-15 19:09 | 2013-08-15 19:09 | GOODMAN - UKN | 90 | 0 | Yes | Yes | 20.1 | 20.2 | -0.1 | 914702F7C9C042418E7DC183DA96489F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8819 |  | 2013-07-25 | 2013-07-25 11:34 | 2013-07-25 12:00 | WEATHER KING - 13AJA30A01 | 85 | 4.1 | Yes | Yes | 15.1 | 18 | -2.9 | 5B9AF077C830405B879FD1BFC4482136 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fresno | CA | 93711-4049 |  | 2013-09-07 | 2013-09-07 10:46 | 2013-09-07 11:11 | OTHER - UNK | 80 | -7.5 | Yes | Yes | 18.9 | 18.2 | 0.7 | 012C46665F74414888F178160357ECCD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93309-4636 |  | 2013-08-15 | 2013-08-15 16:20 | 2013-08-15 16:20 | HEIL - AV42P0000 | 70 | 0 | Yes | Yes | 18.3 | 19.6 | -1.3 | 15DD872CE41246D0BB3914607B536CE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4684 |  | 2013-08-06 | 2013-08-06 18:36 | 2013-08-06 18:36 | GOODMAN - VSC130181AA | 58 | 0 | Yes | Yes | 21.7 | 20.7 | 1 | 00E97FA6F3134AFF9355696CCB9B89C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8819 |  | 2013-07-25 | 2013-07-25 16:21 | 2013-07-25 20:32 | RHEEM - RRNA-C048JA0X | 85 | 3.9 | Yes | Yes | 15.6 | 18.6 | -3 | 98061481C91B44F2BA26336B3C8FBC1B |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93307-8818 |  | 2013-07-17 | 2013-07-17 10:53 | 2013-07-17 11:33 | RHEEM - RRNAB042JK08X | 104 | 11.9 | Yes | Yes | 21.5 | 20.4 | 1.1 | 6A8C009B87A948558B94C21E7258C168 |  | R22 | TXV |  | 11.44% | 0.88558 | 21.99% | [5 empty] | TXV | 11.44%
Bakersfield | CA | 93312-6685 |  | 2013-07-26 | 2013-07-26 14:33 | 2013-07-26 15:04 | YORK - H2RD048S06B | 134 | 8 | Yes | Yes | 19.7 | 19.3 | 0.4 | AD6C6DCECFBD4815A36B6B28C416948A |  | R22 | TXV |  | 5.97% | 0.9403 | 11.47% | [5 empty] | TXV | 5.97%
Bakersfield | CA | 93313-5238 |  | 2013-07-23 | 2013-07-23 12:13 | 2013-07-23 12:50 | BRYANT - 113RNA036000BBAA | 91 | 6.7 | Yes | Yes | 21.1 | 20.6 | 0.5 | 52BDB030524540D48BFDCF0266F5FB50 |  | R22 | TXV |  | 7.363% | 0.92637 | 14.15% | [5 empty] | TXV | 7.363%
Fairfield | CA | 94534-1049 |  | 2013-07-25 | 2013-07-25 15:44 | 2013-07-25 15:44 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 17.9 | 16.4 | 1.5 | 7053A6A2FBF948FC908D45C7783E7E92 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-1360 |  | 2013-09-19 | 2013-09-19 11:44 | 2013-09-19 12:16 | DUCANE - UNK | 86 | 6.1 | Yes | Yes | 19.5 | 21.8 | -2.3 | DEAEC631DA064D5C95904A6AA1CE0573 |  | R22 | Non-TXV |  | 7.093% | 0.92907 | 13.63% | [5 empty] | Non-TXV | 7.093%
San Jose | CA | 95123-1360 |  | 2013-09-19 | 2013-09-19 12:18 | 2013-09-19 13:26 | - | 85 | 3 | Yes | Yes | 18.6 | 19.8 | -1.2 | F6CB3C1D387948CD971337FB4A8E4082 |  |  |  |  | 3.529% | 0.96471 | 6.783% | [5 empty] | 0 | 3.529%
Suisun City | CA | 94585-4147 |  | 2013-08-01 | 2013-08-01 10:21 | 2013-08-01 10:48 | OTHER - DRCS0481BE | 119 | -11.2 | Yes | Yes | 17.3 | 19.6 | -2.3 | 18FE51D8D9224550BAEC14E970D57910 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93312-6560 |  | 2013-07-26 | 2013-07-26 13:45 | 2013-07-26 14:04 | PAYNE - 113RNA048B | 85 | 4 | Yes | Yes | 18.6 | 18.1 | 0.5 | 66DB02F2710541A6A2926A98FF9191A0 |  | R22 | TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | TXV | 4.706%
Bakersfield | CA | 93306-2377 |  | 2013-07-17 | 2013-07-17 12:31 | 2013-07-17 13:05 | CARRIER - 38TXA042330 | 140 | -8.9 | Yes | Yes | 25.8 | 21 | 4.8 | 996BFC9938E74E20A1DC1BCE019B8477 |  | R410A | TXV |  | -6.357% | 1.0636 | 1.78% |  |  |  |  | TXV |  |  | -6.357%
Bakersfield | CA | 93312-6461 |  | 2013-07-26 | 2013-07-26 09:35 | 2013-07-26 10:13 | CARRIER - 38BRC036321 | 104 | -5.8 | Yes | Yes | 21.1 | 18.7 | 2.4 | 43227C905DB047A9B7492F8BBCCF836B |  | R22 | TXV |  | -5.577% | 1.0558 | 1.562% |  |  |  |  | TXV |  |  | -5.577%
Bakersfield | CA | 93313-5805 |  | 2013-07-19 | 2013-07-19 17:40 | 2013-07-19 18:37 | YORK - H2RD042S06A | 141 | 9.9 | Yes | Yes | 18.2 | 20.8 | -2.6 | D248B56D9EC54F68A87D40F699C77487 |  | R22 | Non-TXV |  | 7.021% | 0.92979 | 13.49% | [5 empty] | Non-TXV | 7.021%
Parlier | CA | 93648-9671 |  | 2013-08-21 | 2013-08-21 13:15 | 2013-08-21 13:15 | LENNOX - 13ACD04223002 | 111 | 0 | Yes | Yes | 18.4 | 19.2 | -0.8 | 8783D5A948004C6184F48F399C9E0C02 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2744 |  | 2013-07-12 | 2013-07-12 13:52 | 2013-07-12 13:55 | PAYNE - PA10JA048-A | 99 | 3.3 | Yes | Yes | 18.4 | 18.2 | 0.2 | EEEF24B21AA14EE099BD3FCC2A6ED689 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93726-4015 |  | 2013-07-22 | 2013-07-22 16:17 | 2013-07-22 17:10 | RHEEM - RRMAA024JK06X | 70 | 9.1 | Yes | Yes | 22.6 | 22.5 | 0.1 | 643AE59A232246CF890BA7D3F792A7B5 |  | R22 | Non-TXV |  | 13% | 0.87 | 24.98% | [5 empty] | Non-TXV | 13%
Fresno | CA | 93726-4015 |  | 2013-07-22 | 2013-07-22 17:14 | 2013-07-22 17:14 | RHEEM - RRMAA024JK06X | 70 | 0 | Yes | Yes | 19.3 | 19.9 | -0.6 | 58000EF16FEF40B79BFA4B63ADB28860 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9671 |  | 2013-08-01 | 2013-08-01 09:04 | 2013-08-01 09:38 | LENNOX - 13GCSXA42083X2301A | 181 | 9.7 | Yes | Yes | 21.4 | 19.5 | 1.9 | BE0D5643D2F44B65AADDEC379D965B65 |  | R410A | Non-TXV |  | 5.359% | 0.94641 | 10.3% | [5 empty] | Non-TXV | 5.359%
Fresno | CA | 93705-2718 |  | 2013-10-30 | 2013-10-30 13:51 | 2013-10-30 20:30 | GOODMAN - PGB030100 | 61 | 4.5 | Yes | Yes | 20.6 | 19.3 | 1.3 | B6BDAAC1FFB84D7CBFEE3A580032946D |  | R22 | Non-TXV |  | 7.377% | 0.92623 | 14.18% | [5 empty] | Non-TXV | 7.377%
Bakersfield | CA | 93308-1405 |  | 2013-07-10 | 2013-07-10 18:21 | 2013-07-10 18:21 | RUUD - UAFB-048JAQ | 106 | 0 | Yes | Yes | 21.4 | 19.5 | 2 | 12BA9AB7E9194AE9801183CF5E396C7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9671 |  | 2013-08-01 | 2013-08-01 10:35 | 2013-08-01 10:35 | LENNOX - 13GCSA42083X2301A | 122 | 0 | Yes | Yes | 9.7 | 20.4 | -10.7 | 49C5A4C6CF2A46048E8A139602996689 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1310 |  | 2013-08-05 | 2013-08-05 12:28 | 2013-08-05 13:01 | PAYNE - PA12NA036-B | 121 | 11.2 | Yes | Yes | 20.9 | 16.6 | 4.3 | 568656F0079248C4A93EEBCB6E0866A9 |  | R22 | TXV |  | 9.256% | 0.90744 | 17.79% | [5 empty] | TXV | 9.256%
Bakersfield | CA | 93309-4678 |  | 2013-08-15 | 2013-08-15 16:53 | 2013-08-15 17:12 | GOODMAN - VSC130181AA | 82 | 12.5 | Yes | Yes | 19.9 | 19.7 | 0.2 | 0FA442AF2BFD423098B8F8956A857C1A |  | R22 | Non-TXV |  | 15.24% | 0.84756 | 29.3% | [5 empty] | Non-TXV | 15.24%
Bakersfield | CA | 93309-4679 |  | 2013-08-15 | 2013-08-15 18:26 | 2013-08-15 18:26 | BDP - 567C024RCU | 60 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | B74C4A05DFC94C87B5FD89ED55F0E114 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4678 |  | 2013-08-15 | 2013-08-15 17:30 | 2013-08-15 17:48 | ICP - N2A318AKA100 | 73 | 11 | Yes | Yes | 21.4 | 21.3 | 0.1 | 1187D21F5DF7435185A2E8CE6B1073E2 |  | R22 | Non-TXV |  | 15.07% | 0.84932 | 28.96% | [5 empty] | Non-TXV | 15.07%
Bakersfield | CA | 93306-6656 |  | 2013-08-07 | 2013-08-07 11:51 | 2013-08-07 12:38 | OTHER - UNK | 85 | 2.7 | Yes | Yes | 18.2 | 19.9 | -1.7 | 2DEBA3DEF61944EBA46261A05B9EB99C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Benicia | CA | 94510-2133 |  | 2013-08-13 | 2013-08-13 10:17 | 2013-08-13 10:18 | OTHER - HAC048AKA1 | 123 | -11.6 | Yes | Yes | 18.5 | 17.6 | 0.9 | 7B0485DA98DE46B78FD8D4E6230E4454 |  | R22 | Non-TXV |  | -9.431% | 1.0943 | 2.641% |  |  |  |  | Non-TXV |  |  | -9.431%
Fresno | CA | 93726-0420 |  | 2013-07-23 | 2013-07-23 10:39 | 2013-07-23 11:02 | GOODMAN - CK491A | 112 | 6.1 | Yes | Yes | 20.4 | 19.7 | 0.8 | 2CF900B60AF846AE9C56BCCCDC05EA68 |  | R22 | Non-TXV |  | 5.446% | 0.94554 | 10.47% | [5 empty] | Non-TXV | 5.446%
Bakersfield | CA | 93308-7141 |  | 2013-09-18 | 2013-09-18 14:43 | 2013-09-18 14:43 | YORK - AC036X1222 | 83 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 89CB14320F5B4AD29B14807350636942 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5126 |  | 2013-08-21 | 2013-08-21 09:43 | 2013-08-21 09:43 | YORK - D1NH04206506C | 94 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 7ADA7AB4EAC248D6A0AA326DB629D6EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2677 |  | 2013-09-06 | 2013-09-06 16:54 | 2013-09-06 17:18 | CARRIER - 24ABS330A300 | 78 | 4.4 | Yes | Yes | 21 | 19.3 | 1.7 | E8B2860E6F77468CBA19BC0499E06F2E |  | R22 | Non-TXV |  | 5.641% | 0.94359 | 10.84% | [5 empty] | Non-TXV | 5.641%
San Jose | CA | 95124-6340 |  | 2013-09-26 | 2013-09-26 11:56 | 2013-09-26 11:56 | - 29TD94443T99927 | 37 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | CD163D5B5D3246948BBEA8D72A69260C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2313 |  | 2013-07-22 | 2013-07-22 15:14 | 2013-07-22 15:14 | CARRIER - 50DA004330 | 108 | 0 | Yes | Yes | 35 | 21.2 | 13.8 | 96ED98964D6740DC9ABD1FAF88E443A4 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3531 |  | 2013-09-05 | 2013-09-05 10:22 | 2013-09-05 10:22 | YORK - DCYGF024N045C | 58 | 0 | Yes | Yes | 22.1 | 18.7 | 3.4 | B5D73F8C814F4722B14F34EF8980E225 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-2262 |  | 2013-11-07 | 2013-11-07 13:54 | 2013-11-07 14:50 | TAPPAN - UKN | 61 | 0 | Yes | Yes | 21.6 | 20.2 | 1.4 | 38ACFA8C40A34B5C8CB0266E2C870E58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2190 |  | 2013-09-03 | 2013-09-03 19:40 | 2013-09-03 19:40 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.1 | 20.9 | 0.2 | 6066FA671FCF4DC8A37C2BA0BB2BF3C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3654 |  | 2013-07-18 | 2013-07-18 14:43 | 2013-07-18 14:43 | LENNOX - 10GCS042X-75-1PA | 73 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F1A7CC08614D4B908D55DA919D0D786C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2806 |  | 2013-08-05 | 2013-08-05 08:49 | 2013-08-05 08:49 | TRANE - TTB042D100A0 | 78 | 0 | Yes | Yes | 14.7 | 17.5 | -2.8 | 9A556E9D0B504572ADF0887BD5E1E09D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3531 |  | 2013-09-05 | 2013-09-05 09:48 | 2013-09-05 10:18 | PAYNE - UNK | 58 | -3.4 | Yes | Yes | 22.4 | 19.1 | 3.3 | 0E253B1DBAAD43B0A143C06042251A39 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Fairfield | CA | 94533-3586 |  | 2013-09-19 | 2013-09-19 08:54 | 2013-09-19 08:55 | TRANE - BWD718A1000B0 | 88 | 5.1 | Yes | Yes | 17.5 | 17.6 | -0.1 | B9C1BE63C5D24026A70DCA77247D8C25 |  | R22 | Non-TXV |  | 5.795% | 0.94205 | 11.14% | [5 empty] | Non-TXV | 5.795%
Fresno | CA | 93726-3526 |  | 2013-09-05 | 2013-09-05 10:54 | 2013-09-05 11:14 | OTHER - DCYA-F024N045C | 58 | 1.7 | Yes | Yes | 23.5 | 19.1 | 4.4 | FDEC0F6F75EB429188069348FC8ACBB0 |  | R410A | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Fresno | CA | 93726-3526 |  | 2013-09-05 | 2013-09-05 11:33 | 2013-09-05 12:00 | OTHER - YAC-108-C | 80 | 2.4 | Yes | Yes | 19.5 | 19.6 | -0.1 | 7298CDE200CF4BD39B7A0D8883DA7180 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
San Jose | CA | 95133-3002 |  | 2013-08-06 | 2013-08-06 14:40 | 2013-08-06 14:40 | RUUD - UAKA-042JAZ | 85 | 0 | Yes | Yes | 20.6 | 18.4 | 2.3 | AB094D41703441D1838E432067415DBC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5207 |  | 2013-07-03 | 2013-07-03 18:44 | 2013-07-03 18:44 | ICP - PGF348080K01A1 | 131 | 0 | Yes | Yes | 19 | 19.6 | -0.6 | EF7B5505F84D4E248C32D566995C4A04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5207 |  | 2013-07-03 | 2013-07-03 18:48 | 2013-07-03 18:48 | ICP - PF324040K01A1 | 120 | 0 | Yes | Yes | 21 | 20.1 | 0.9 | A2EE8FC19288417CAAC70A020E5BA578 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2515 |  | 2013-08-09 | 2013-08-09 13:54 | 2013-08-09 13:54 | BRYANT - 561CJ018 | 54 | 0 | Yes | Yes | 14 | 19.4 | -5.4 | 527105D7F3184042B32D266A99DA0CBE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5124 |  | 2013-08-03 | 2013-08-03 10:54 | 2013-08-03 10:54 | ICP - CAC442AKA1 | 272 | 0 | Yes | Yes | 21.7 | 20.4 | 1.3 | 97377D71BD0345058D3CBD6BAA677040 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-9382 |  | 2013-07-18 | 2013-07-18 09:02 | 2013-07-18 09:47 | ARMSTRONG - PGE10B24D050A 9A | 53 | 1.8 | Yes | Yes | 21.9 | 19.5 | 2.4 | 6C2ABBBB4097417DAC157B95AA620EFE |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Fresno | CA | 93727-6482 |  | 2013-07-30 | 2013-07-30 12:47 | 2013-07-30 13:08 | LENNOX - 12ACB42 | 125 | 10.3 | Yes | Yes | 22.5 | 20.4 | 2.1 | 6DB577F6832F4F74AE08A5EE49191794 |  | R22 | TXV |  | 8.24% | 0.9176 | 15.84% | [5 empty] | TXV | 8.24%
San Jose | CA | 95127-4517 |  | 2013-10-14 | 2013-10-14 10:41 | 2013-10-14 10:57 | UNITARY PRODUCTS GROUP - TCGD36221S | 134 | 4.9 | Yes | Yes | 20.6 | 20.6 | 0 | 85EA7E51A85C4A5FBE414B6A41E4FFE1 |  | R22 | Non-TXV |  | 3.657% | 0.96343 | 7.027% | [5 empty] | Non-TXV | 3.657%
Fresno | CA | 93726-3529 |  | 2013-09-05 | 2013-09-05 12:31 | 2013-09-05 13:12 | TRANE - YCC024F1L0BH | 66 | 21 | Yes | Yes | 20.5 | 20.4 | 0.1 | F3DFDBF5B2644D119D573E85E2D4029A |  | R22 | Non-TXV |  | 31.82% | 0.68182 | 61.15% | [5 empty] | Non-TXV | 31.82%
Willits | CA | 95490-8750 |  | 2013-08-21 | 2013-08-21 09:57 | 2013-08-21 11:01 | GE - B7R736D100AC | 116 | -10.9 | Yes | Yes | 25.5 | 20.7 | 4.8 | EB315BE8252C4FC295C5919C2613562C |  | R22 | Non-TXV |  | -9.397% | 1.094 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.397%
Fresno | CA | 93727-6484 |  | 2013-07-29 | 2013-07-29 11:17 | 2013-07-29 11:49 | LENNOX - 12ACB48 | 171 | 11.3 | Yes | Yes | 25.6 | 19.7 | 5.9 | 9A80CC0CD9B842B08F1911EC44757CC3 |  | R22 | TXV |  | 6.608% | 0.93392 | 12.7% | [5 empty] | TXV | 6.608%
Fairfield | CA | 94533-2235 |  | 2013-07-25 | 2013-07-25 11:06 | 2013-07-25 13:02 | AMERICAN STANDARD - 7A0036A100A2 | 95 | 3 | Yes | Yes | 18.5 | 17.7 | 0.8 | 0A9E676EC488466D94A43B5C66918D25 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
San Jose | CA | 95124-2448 |  | 2013-10-15 | 2013-10-15 15:13 | 2013-10-15 17:00 | TRANE - RAUB-302-F | 69 | 3.7 | Yes | Yes | 20.9 | 20.3 | 0.6 | 7C839DFA960547369C976127E8E693D3 |  | R22 | Non-TXV |  | 5.362% | 0.94638 | 10.31% | [5 empty] | Non-TXV | 5.362%
Fresno | CA | 93727-6475 |  | 2013-07-29 | 2013-07-29 09:31 | 2013-07-29 10:26 | LENNOX - 12ACB60 | 172 | 17 | Yes | Yes | 27.4 | 20.6 | 6.8 | 38EAC751851A4E0EBB5F0495D28EED10 | Add refrigerant: 14 oz | R22 | TXV |  | 9.884% | 0.90116 | 18.99% | [5 empty] | TXV | 9.884%
Bakersfield | CA | 93309-4716 |  | 2013-07-02 | 2013-07-02 17:40 | 2013-07-02 18:14 | DAY & NIGHT - 580ANO36 | 85 | 2.7 | Yes | Yes | 19.4 | 19.5 | -0.1 | 770C4ED50E41411ABC371C7E333AFDB4 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93308-5402 |  | 2013-09-04 | 2013-09-04 17:33 | 2013-09-04 17:33 | TRANE - 4YCC3024B1064AA | 93 | 0 | Yes | Yes | 21.9 | 21.3 | 0.6 | D62E98BB663B48A08E5915B678831338 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6439 |  | 2013-09-24 | 2013-09-24 13:29 | 2013-09-24 14:00 | YORK - H5DB042S06A | 91 | 9.2 | Yes | Yes | 22 | 16.4 | 5.6 | C393FFAE7713469ABE74E279D9FF6E3E |  | R22 | Non-TXV |  | 10.11% | 0.8989 | 19.43% | [5 empty] | Non-TXV | 10.11%
Fresno | CA | 93726-3527 |  | 2013-09-05 | 2013-09-05 13:45 | 2013-09-05 14:02 | AMERICAN STANDARD - YCC024F1L0BJ | 65 | 3.1 | Yes | Yes | 22.4 | 21.7 | 0.7 | 80714FCAA02142F086E71B6F36F73DA3 |  | R22 | Non-TXV |  | 4.769% | 0.95231 | 9.165% | [5 empty] | Non-TXV | 4.769%
Clovis | CA | 93612-2525 |  | 2013-08-12 | 2013-08-12 13:40 | 2013-08-12 15:14 | BRYANT - 561CJD18-D | 85 | 2.8 | Yes | Yes | 20 | 20.4 | -0.4 | 6A13ACE080F04A8993D76E0CF120BE1D |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Fresno | CA | 93726-3528 |  | 2013-09-05 | 2013-09-05 11:52 | 2013-09-05 12:21 | YORK - D2NP02405606A | 100 | 4.4 | Yes | Yes | 23.3 | 19.6 | 3.7 | F53E116C127442EEB2651D48473B2665 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Bakersfield | CA | 93308-5403 |  | 2013-09-04 | 2013-09-04 18:30 | 2013-09-04 18:30 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 214F6321EC4F4D77819D070E923BBBDE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2515 |  | 2013-08-09 | 2013-08-09 13:08 | 2013-08-09 13:31 | BRYANT - 561CJ024D | 58 | 2.2 | Yes | Yes | 18.2 | 17.9 | 0.3 | F97BB20BA46D4A3EA6E076C2409D74AC |  | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Fresno | CA | 93726-3529 |  | 2013-09-05 | 2013-09-05 13:14 | 2013-09-05 13:43 | YORK - D2NP024N05606A | 100 | 6.1 | Yes | Yes | 21.1 | 22.1 | -1 | EF7545B085C7439C9F58F6BB6F4BBF03 |  | R22 | Non-TXV |  | 6.1% | 0.939 | 11.72% | [5 empty] | Non-TXV | 6.1%
Cottonwood | CA | 96022-9022 |  | 2013-06-26 | 2013-06-26 11:03 | 2013-06-26 11:51 | YORK - DRC0421BE | 89 | 3.8 | Yes | Yes | 21.5 | 20.4 | 1.1 | 674F66856FF94AA887E1777D8314C2E4 |  | R22 | Non-TXV |  | 4.27% | 0.9573 | 8.205% | [5 empty] | Non-TXV | 4.27%
Santa Rosa | CA | 95409-4141 |  | 2013-09-16 | 2013-09-16 11:42 | 2013-09-16 11:43 | RHEEM - NA | 52 | 2.4 | Yes | Yes | 19.1 | 17.6 | 1.5 | 9B4F7CABBC544BFBBA4D05CB45A92B55 |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
San Jose | CA | 95135-1312 |  | 2013-08-06 | 2013-08-06 13:54 | 2013-08-06 13:54 | CARRIER - 38CKC024330 | 113 | 0 | Yes | Yes | 22.6 | 18.2 | 4.4 | 75A3584D9A3F4AF28F350B83DE533FCF |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2154 |  | 2013-09-03 | 2013-09-03 19:58 | 2013-09-03 19:58 | BRYANT - 58ANW0240NAAD | 56 | 0 | Yes | Yes | 22.2 | 21.8 | 0.4 | 1B0C05FE188B4A6AA9920CC3F5A4E7B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1938 |  | 2013-07-31 | 2013-07-31 13:04 | 2013-07-31 13:47 | YORK - D1NP030N05606A | 73 | 4 | Yes | Yes | 24.1 | 20.9 | 3.2 | 67426AC889C34A9CA6586DCA80A3CA08 |  | R22 | Non-TXV |  | 5.479% | 0.94521 | 10.53% | [5 empty] | Non-TXV | 5.479%
Fresno | CA | 93726-3527 |  | 2013-09-05 | 2013-09-05 14:04 | 2013-09-06 00:38 | PAYNE - UKN | 67 | 3.4 | Yes | Yes | 21.4 | 23.2 | -1.8 | F06B37B32857449DAD57D941CA271205 |  | R22 | Non-TXV |  | 5.075% | 0.94925 | 9.752% | [5 empty] | Non-TXV | 5.075%
Clovis | CA | 93612-2529 |  | 2013-09-04 | 2013-09-04 10:28 | 2013-09-04 10:49 | BRYANT - 561CJ024D | 58 | 2 | Yes | Yes | 20.5 | 19.3 | 1.2 | 79E8F073C7C54436A29D0E10BA7080AF |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Davis | CA | 95618-6139 |  | 2013-08-14 | 2013-08-14 11:48 | 2013-08-14 16:08 | BRYANT - 563CN024-B-1BAA | 81 | 5.2 | Yes | Yes | 19.9 | 20.4 | -0.5 | 57AB03A3840A48B9AAF0C3A7E3341992 |  | R22 | Non-TXV |  | 6.42% | 0.9358 | 12.34% | [5 empty] | Non-TXV | 6.42%
Selma | CA | 93662-4801 |  | 2013-07-30 | 2013-07-30 15:01 | 2013-07-30 15:26 | TEMPSTAR - PCAD30D1K3 | 78 | 7.8 | Yes | Yes | 23.6 | 19.5 | 4.1 | 23D5328813BC4456AF6A721B80C50698 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Sanger | CA | 93657-4109 |  | 2013-08-06 | 2013-08-06 16:12 | 2013-08-06 16:31 | LENNOX - 10GCS036752PA | 58 | 8.1 | Yes | Yes | 25.2 | 21.2 | 4 | 838BB56F61EA41C5B60DBB41A31EFF77 |  | R22 | Non-TXV |  | 13.97% | 0.86034 | 26.84% | [5 empty] | Non-TXV | 13.97%
Fresno | CA | 93728-2903 |  | 2013-07-30 | 2013-07-30 09:44 | 2013-07-30 12:37 | YORK - BRCS0421BD | 84 | 12.1 | Yes | Yes | 22.8 | 20.1 | 2.7 | 23E98A7B839A48128C910838D18341C6 |  | R22 | Non-TXV |  | 14.4% | 0.85595 | 27.68% | [5 empty] | Non-TXV | 14.4%
Fresno | CA | 93728-2903 |  | 2013-07-30 | 2013-07-30 16:03 | 2013-07-30 16:03 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 7B7695A0E0D44588A05281204A15CA16 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4246 |  | 2013-09-20 | 2013-09-20 10:23 | 2013-09-20 10:23 | PAYNE - PA10JA018-A | 56 | 0 | Yes | Yes | 19.6 | 18.1 | 1.5 | ABEF528FDF734AC7A7C8F77F1C47C795 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2154 |  | 2013-09-03 | 2013-09-03 18:52 | 2013-09-03 19:10 | ICP - PGCA024K060A | 56 | 7.3 | Yes | Yes | 21.6 | 21 | 0.6 | 05AE495A46724C429A18DD51DF7D4C88 |  | R22 | Non-TXV |  | 13.04% | 0.86964 | 25.05% | [5 empty] | Non-TXV | 13.04%
Clovis | CA | 93612-2514 |  | 2013-08-12 | 2013-08-12 11:29 | 2013-08-12 11:59 | BRYANT - 561CJ018-D | 52 | 8.2 | Yes | Yes | 15.5 | 18.5 | -3 | 211FDE63C8DF44999222C0FCE253E8BC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.77% | 0.84231 | 30.3% | [5 empty] | Non-TXV | 15.77%
Woodland | CA | 95695-4857 |  | 2013-08-05 | 2013-08-05 09:38 | 2013-08-05 09:44 | GOODMAN - PGB030075-1 | 56 | -4 | Yes | Yes | 14 | 15.7 | -1.7 | EC62DEE8CC0347159C15D04A3DD8F842 |  | R22 | Non-TXV |  | -7.143% | 1.0714 | 2% |  |  |  |  | Non-TXV |  |  | -7.143%
Fresno | CA | 93725-1853 |  | 2013-08-26 | 2013-08-26 15:16 | 2013-08-26 15:16 | GOODMAN - CK491B | 97 | 0 | Yes | Yes | 22.2 | 20.9 | 1.3 | 216F4F87E5C944CAB3AA0858EE173303 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2414 |  | 2013-08-07 | 2013-08-07 15:27 | 2013-08-07 15:59 | LENNOX - 13GCSXA-42-083X-230-1A | 181 | 20.2 | Yes | Yes | 26.2 | 20.4 | 5.8 | 769BAD21B70D4CB4945FAD4BD59657BD |  | R410A | Non-TXV |  | 11.16% | 0.8884 | 21.45% | [5 empty] | Non-TXV | 11.16%
Hanford | CA | 93230-9554 |  | 2013-08-05 | 2013-08-05 14:27 | 2013-08-05 14:48 | YORK - F036N070A | 108 | 4.3 | Yes | Yes | 28.2 | 22.5 | 5.7 | B6F6990BF6304870BEDCBFA44ADCB98E |  | R22 | Non-TXV |  | 3.981% | 0.96019 | 7.652% | [5 empty] | Non-TXV | 3.981%
Fresno | CA | 93726-3529 |  | 2013-09-05 | 2013-09-05 11:47 | 2013-09-05 12:07 | AMERICAN STANDARD - YCC024F1L0BJ | 66 | 5.7 | Yes | Yes | 22.8 | 19.7 | 3.2 | 15F5E4EAA3E442788A48745A897BA8FA |  | R22 | Non-TXV |  | 8.636% | 0.91364 | 16.6% | [5 empty] | Non-TXV | 8.636%
Fairfield | CA | 94533-5241 |  | 2013-07-26 | 2013-07-26 12:21 | 2013-07-26 12:22 | OTHER - 29TF7025910 | 69 | 3.5 | Yes | Yes | 16.3 | 17 | -0.7 | A0B557DBAEEC4F199039FD49224FF2A5 |  | R22 | Non-TXV |  | 5.072% | 0.94928 | 9.748% | [5 empty] | Non-TXV | 5.072%
Fresno | CA | 93726-3528 |  | 2013-09-06 | 2013-09-06 11:48 | 2013-09-06 12:10 | PAYNE - YAC-108-C | 58 | 1.7 | Yes | Yes | 16.9 | 19 | -2.1 | 37D094682B69458E92BACF7D173FC8CF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Fresno | CA | 93711-4035 |  | 2013-09-06 | 2013-09-06 15:45 | 2013-09-06 16:11 | RUUD - UNK | 66 | 2.8 | Yes | Yes | 18.5 | 18.5 | 0 | 63E044C7C6B94AD2ADAF298B4A2F3E7F |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Vacaville | CA | 95688-2909 |  | 2013-07-12 | 2013-07-12 09:58 | 2013-07-12 09:58 | TEMPSTAR - PGF024K040A | 58 | 0 | Yes | Yes | 15.9 | 17.7 | -1.8 | 929C30D7781F47F894DE01F7E4D69CF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-2901 |  | 2013-10-14 | 2013-10-14 12:53 | 2013-10-14 13:33 | CARRIER - 24ACR342A310 | 105 | 8.8 | Yes | Yes | 22.9 | 20.9 | 2 | AB7AF47CB1DA45B3BA217DFFA47C8C78 |  | R22 | TXV |  | 8.381% | 0.91619 | 16.11% | [5 empty] | TXV | 8.381%
Fresno | CA | 93726-3527 |  | 2013-09-05 | 2013-09-05 12:01 | 2013-09-05 12:22 | OTHER - YAC-108-C | 58 | -3.4 | Yes | Yes | 24.1 | 19.1 | 5 | EE81CF6686EA4534B06A2B264B422985 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Parlier | CA | 93648-9671 |  | 2013-08-01 | 2013-08-01 11:33 | 2013-08-01 12:57 | LENNOX - 13GCSXA36068X2301A | 125 | 20.2 | Yes | Yes | 22.7 | 21.4 | 1.3 | 0383C76F28094E18A3CA59074F354FE6 |  | R410A | Non-TXV |  | 16.16% | 0.8384 | 31.06% | [5 empty] | Non-TXV | 16.16%
Fairfield | CA | 94534-6686 |  | 2013-07-25 | 2013-07-25 11:41 | 2013-07-25 13:04 | CARRIER - 38CKC030340 | 68 | 2.5 | Yes | Yes | 14.9 | 17.7 | -2.8 | 6DD646EBCD314E2A8F12BC10C5B4FB64 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Clovis | CA | 93612-2513 |  | 2013-08-12 | 2013-08-12 16:06 | 2013-08-12 16:24 | BRYANT - 5613J024D | 59 | 5.1 | Yes | Yes | 21.2 | 18.7 | 2.5 | C6F7B412515841A194AFCBCBF0D3B3E0 |  | R22 | Non-TXV |  | 8.644% | 0.91356 | 16.61% | [5 empty] | Non-TXV | 8.644%
Bakersfield | CA | 93308-2183 |  | 2013-08-30 | 2013-08-30 15:43 | 2013-08-30 16:04 | TEMPSTAR - 4YCC3024B1064AA | 93 | 11.6 | Yes | Yes | 22.3 | 22.1 | 0.2 | 4A503CBCCCF74DB58A53F2197D1EC2A1 |  | R22 | Non-TXV |  | 12.47% | 0.87527 | 23.97% | [5 empty] | Non-TXV | 12.47%
Parlier | CA | 93648-9668 |  | 2013-08-21 | 2013-08-21 17:17 | 2013-08-21 17:47 | LENNOX - 13ACD04223002 | 111 | -4.4 | Yes | Yes | 22.6 | 23.6 | -1 | 4202C33EE68F495A9CB13CEF2A708901 |  | R22 | TXV |  | -3.964% | 1.0396 | 1.11% |  |  |  |  | TXV |  |  | -3.964%
Vallejo | CA | 94589-3302 |  | 2013-08-02 | 2013-08-02 13:01 | 2013-08-02 13:10 | OTHER - NA | 72 | 5.6 | Yes | Yes | 18.6 | 17.6 | 1 | 2B2EB2BE8AB94ACB9DAF6F761E9FEA4A |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Fresno | CA | 93706-3058 |  | 2013-07-25 | 2013-07-25 10:35 | 2013-07-25 10:54 | YORK - DAYPF036N070A | 108 | 5.2 | Yes | Yes | 21.6 | 19.9 | 1.7 | 611BC5D454604DD2807E6108AD272598 |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Fresno | CA | 93726-3531 |  | 2013-09-05 | 2013-09-05 13:15 | 2013-09-05 13:37 | PAYNE - UNK | 58 | 2.3 | Yes | Yes | 19.7 | 18.8 | 0.9 | B1D1A8D4DD1F4CB2B459253318D1A125 |  | R22 | Non-TXV |  | 3.966% | 0.96034 | 7.621% | [5 empty] | Non-TXV | 3.966%
Woodland | CA | 95695-2565 |  | 2013-07-25 | 2013-07-25 13:04 | 2013-07-25 13:04 | GOODMAN - GSH130241AA | 105 | 0 | Yes | Yes | 14.6 | 16.4 | -1.8 | D6383AD4787749EE82558D069852C503 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3528 |  | 2013-09-05 | 2013-09-05 12:23 | 2013-09-05 12:47 | YORK - D2NP024N05606A | 100 | 4.6 | Yes | Yes | 20.5 | 19.1 | 1.5 | AB14BC1A15E3418B918DCADD6DF92AA3 |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Fresno | CA | 93711-2682 |  | 2013-09-07 | 2013-09-07 09:24 | 2013-09-07 10:19 | OTHER - UNK | 80 | -4.7 | Yes | Yes | 16.4 | 18.7 | -2.3 | 665377B154174A46A44C88182E95151A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Bakersfield | CA | 93308-2191 |  | 2013-09-04 | 2013-09-04 16:44 | 2013-09-04 16:44 | TRANE - 4YCC024B1064AA | 93 | 0 | Yes | Yes | 22.1 | 22.1 | 0 | 04C5CFC36B7A4606A13EA1A494922594 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2177 |  | 2013-09-03 | 2013-09-03 17:41 | 2013-09-03 17:41 | RHEEM - UKN | 75 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | A923000A77DB4FA8A6AE8A22A2507320 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2513 |  | 2013-08-13 | 2013-08-13 10:55 | 2013-08-13 11:43 | BRYANT - 561C018D | 54 | 4.1 | Yes | Yes | 19.5 | 19.7 | -0.2 | F721A1AE2A294196B352C0FFC1899C8B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.593% | 0.92407 | 14.59% | [5 empty] | Non-TXV | 7.593%
Fresno | CA | 93726-3526 |  | 2013-09-05 | 2013-09-05 10:54 | 2013-09-05 11:10 | TRANE - YCC024F1L0BJ | 55 | 4 | Yes | Yes | 20.6 | 21 | -0.4 | 5BC8FB38B99B408D8550FB0245F3DA7D |  | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Bakersfield | CA | 93308-2188 |  | 2013-09-03 | 2013-09-03 18:54 | 2013-09-03 18:54 | PAYNE - PY3PNA0240NB | 53 | 0 | Yes | Yes | 19.5 | 20 | -0.4 | 582EA2E56F48408EADF1A2CC8BAF64AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2514 |  | 2013-08-12 | 2013-08-12 12:02 | 2013-08-12 14:37 | OTHER - 561CJ024 | 58 | 4 | Yes | Yes | 18 | 19.9 | -1.9 | 38CDD008B7F5459B865435BE1E11830C |  | R22 | Non-TXV |  | 6.897% | 0.93103 | 13.25% | [5 empty] | Non-TXV | 6.897%
Fresno | CA | 93726-3525 |  | 2013-09-06 | 2013-09-06 10:43 | 2013-09-06 11:05 | RHEEM - RRNL-B024JK06X | 77 | 2.3 | Yes | Yes | 17.2 | 19.1 | -1.9 | 36B947212AE74AE68EFBBFBA13972089 |  | R410A | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Bakersfield | CA | 93308-2166 |  | 2013-08-30 | 2013-08-30 16:54 | 2013-08-30 16:54 | OTHER - CT0024G7A | 60 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | 11CCDA99B0DA4D3788FBE7AFFCE09250 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1010 |  | 2013-07-22 | 2013-07-22 08:46 | 2013-07-22 09:20 | DAY & NIGHT - ILLEGIBLE | 97 | 16 | Yes | Yes | 25.6 | 21 | 4.6 | 2A87238B20704845B10B8B4A1F84A445 |  | R22 | Non-TXV |  | 16.49% | 0.83505 | 31.7% | [5 empty] | Non-TXV | 16.49%
Bakersfield | CA | 93309-4683 |  | 2013-08-05 | 2013-08-05 17:34 | 2013-08-05 17:34 | GOODMAN - GSC130181FA | 75 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 0405A4AF0EDE4913A928071CA1819B8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3528 |  | 2013-09-05 | 2013-09-05 12:49 | 2013-09-05 13:12 | YORK - D2NP024N05606 | 100 | 4.3 | Yes | Yes | 20.5 | 21.5 | -1 | B54D88CADB834FE99D84A1C31857850A |  | R22 | Non-TXV |  | 4.3% | 0.957 | 8.264% | [5 empty] | Non-TXV | 4.3%
Bakersfield | CA | 93309-4680 |  | 2013-08-05 | 2013-08-05 18:24 | 2013-08-05 18:24 | ICP - E03251188 | 85 | 0 | Yes | Yes | 21.7 | 20.7 | 1.1 | AD5A5A471AFF47DFB2CE7FB79CEC70F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1428 |  | 2013-08-22 | 2013-08-22 09:07 | 2013-08-22 09:29 | GOODMAN - GPG13360701AC | 112 | 7.6 | Yes | Yes | 19.8 | 19.1 | 0.7 | 4E7C9C147ED543CE82A3E68723E2929E |  | R22 | Non-TXV |  | 6.786% | 0.93214 | 13.04% | [5 empty] | Non-TXV | 6.786%
Fresno | CA | 93705-1428 |  | 2013-08-22 | 2013-08-22 09:42 | 2013-08-22 10:09 | FRIGIDKING - UNK | 70 | 5 | Yes | Yes | 21.2 | 20.9 | 0.3 | 3D6D4C2DACD1427B80938EF8FB9F6EEC |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Bakersfield | CA | 93307-3976 |  | 2013-08-08 | 2013-08-08 22:48 | 2013-08-08 22:50 | OTHER - 2AC13B0P-1A | 129 | -12.6 | Yes | Yes | 20.4 | 22.1 | -1.7 | D8F54AF6C6274168BBC4B6468E66F3B7 |  | R22 | Non-TXV |  | -9.767% | 1.0977 | 2.735% |  |  |  |  | Non-TXV |  |  | -9.767%
Fresno | CA | 93726-3531 |  | 2013-09-05 | 2013-09-05 10:55 | 2013-09-05 11:13 | RHEEM - RRNAB024JK06X | 70 | 3 | Yes | Yes | 17.9 | 18.2 | -0.3 | 6AA8FCE3BEFC408DBFE9406527901194 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Bakersfield | CA | 93309-4692 |  | 2013-08-05 | 2013-08-05 16:03 | 2013-08-05 16:03 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | EEB512F28E414849B2633622AF363CBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1048 |  | 2013-08-22 | 2013-08-22 13:13 | 2013-08-22 14:08 | ICP - UNK | 96 | 8.4 | Yes | Yes | 20.1 | 19.3 | 0.8 | B46FEFD3201142759E9F46E401A25F82 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Bakersfield | CA | 93308-2185 |  | 2013-09-03 | 2013-09-03 18:01 | 2013-09-03 18:17 | RUUD - UKN | 90 | 13.2 | Yes | Yes | 18.9 | 20.4 | -1.5 | 114BB9E8A18740258124AC65C582FA05 |  | R22 | Non-TXV |  | 14.67% | 0.85333 | 28.19% | [5 empty] | Non-TXV | 14.67%
San Jose | CA | 95133-2333 |  | 2013-08-06 | 2013-08-06 12:42 | 2013-08-06 12:42 | BRYANT - 561CJ036-D | 105 | 0 | Yes | Yes | 21.5 | 16.9 | 4.6 | D314056FC1474B0F92C36979E9D12507 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4681 |  | 2013-08-05 | 2013-08-05 16:52 | 2013-08-05 16:52 | BDP - 5C7018RCU | 37 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 5EA1C721A69540AB82231722BC494B0E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2514 |  | 2013-09-04 | 2013-09-04 13:37 | 2013-09-04 23:15 | BRYANT - 561CJ024D | 52 | 3.4 | Yes | Yes | 20.2 | 18.8 | 1.4 | 4BEB79179B984E3982DFB5C147DA2975 |  | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Clovis | CA | 93612-2512 |  | 2013-08-13 | 2013-08-13 12:09 | 2013-08-13 13:02 | BRYANT - 561CJ0180 | 53 | 4 | Yes | Yes | 20.2 | 19.2 | 1 | 46103A88BF224FA280B2AFD5D4FA3F68 |  | R22 | Non-TXV |  | 7.547% | 0.92453 | 14.5% | [5 empty] | Non-TXV | 7.547%
Antioch | CA | 94509-4517 |  | 2013-07-24 | 2013-07-24 11:39 | 2013-07-24 11:39 | RHEEM - UKN | 85 | 0 | Yes | Yes | 18.7 | 21.3 | -2.6 | F382583337314911823B52DDBEF14DB1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2512 |  | 2013-09-03 | 2013-09-03 13:03 | 2013-09-03 13:27 | BRYANT - 561CJ024 | 54 | 4.4 | Yes | Yes | 17.1 | 19.9 | -2.8 | 9ACEE75CAB7B419CBBC4E3DCFD12D010 |  | R22 | TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | TXV | 8.148%
Clovis | CA | 93612-2523 |  | 2013-08-24 | 2013-08-24 16:07 | 2013-08-24 16:07 | GOODMAN - CK18 | 59 | 0 | Yes | Yes | 11.3 | 17.2 | -5.9 | E9345C5A4F5F4C148EFAAB00BF80C430 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2523 |  | 2013-08-12 | 2013-08-12 12:41 | 2013-08-12 13:05 | RHEEM - 561CJ02-D | 52 | 1.6 | Yes | Yes | 21.1 | 19.3 | 1.8 | 2C4A7805E23D4D69AC8D1BDDD8F2E509 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Bakersfield | CA | 93309-4685 |  | 2013-08-06 | 2013-08-06 19:34 | 2013-08-06 19:34 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 929BDD0FCBE348C095F4F013E0CE669B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4684 |  | 2013-08-06 | 2013-08-06 18:53 | 2013-08-06 18:53 | OTHER - UKN | 35 | 0 | Yes | Yes | 21.7 | 21.8 | -0.1 | 814DC2F68C9C45AD9D965D2F13C72AED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2524 |  | 2013-08-12 | 2013-08-12 10:31 | 2013-08-12 11:09 | OTHER - CK24LB | 80 | 4.6 | Yes | Yes | 19.3 | 19.9 | -0.6 | 3DCDAAC254AA44BFAF09AEBA046EF9BD |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Bakersfield | CA | 93309-6022 |  | 2013-08-04 | 2013-08-04 12:14 | 2013-08-04 12:43 | GOODMAN - GPG1360090M41AD | 185 | 21.3 | Yes | Yes | 21.4 | 21 | 0.4 | 86580B8678DE4D4C9BBC8D1F60FA18C3 |  | R410A | Non-TXV |  | 11.51% | 0.88486 | 22.13% | [5 empty] | Non-TXV | 11.51%
Fresno | CA | 93726-5044 |  | 2013-08-23 | 2013-08-23 13:49 | 2013-08-23 16:24 | YORK - DAYPF036N070A | 108 | 4.5 | Yes | Yes | 23.5 | 19.7 | 3.8 | BD06863223AC42408AE3F36C3D8D9BA1 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Bakersfield | CA | 93309-4617 |  | 2013-08-06 | 2013-08-06 20:55 | 2013-08-06 20:55 | BDP - 567C08RCU | 42 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | D5F50351D3504B25AA6E60E172B3A26C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4682 |  | 2013-08-05 | 2013-08-05 16:40 | 2013-08-05 16:57 | PAYNE - 567C024RCU | 60 | 8.8 | Yes | Yes | 20.7 | 20.7 | 0.1 | 5E567E38221948EAAE7F599F4A2E5660 |  | R22 | Non-TXV |  | 14.67% | 0.85333 | 28.19% | [5 empty] | Non-TXV | 14.67%
Bakersfield | CA | 93309-4686 |  | 2013-08-06 | 2013-08-06 16:53 | 2013-08-06 16:53 | GOODMAN - GSC130181FA | 75 | 0 | Yes | Yes | 21.8 | 20.9 | 0.9 | 07C49D1B36EB469C8C5CF087798FFCDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4638 |  | 2013-08-05 | 2013-08-05 18:21 | 2013-08-05 18:21 | BDP - UKN | 90 | 0 | Yes | Yes | 22.2 | 19.7 | 2.5 | 75A1C6F982DE4F21AF58FAE3B0F25B82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2525 |  | 2013-09-04 | 2013-09-04 12:08 | 2013-09-04 12:32 | BRYANT - 561CJ024D | 58 | 3.8 | Yes | Yes | 19.7 | 19.3 | 0.4 | 3E81F4080DFB49368D61676E9AE7A385 |  | R22 | Non-TXV |  | 6.552% | 0.93448 | 12.59% | [5 empty] | Non-TXV | 6.552%
Clovis | CA | 93612-2514 |  | 2013-08-12 | 2013-08-12 11:18 | 2013-08-12 12:00 | OTHER - 561CJ018 | 80 | 5.8 | Yes | Yes | 20 | 20.4 | -0.4 | 62EE085F6266474EABEAEB29825D576C |  | R22 | Non-TXV |  | 7.25% | 0.9275 | 13.93% | [5 empty] | Non-TXV | 7.25%
Fresno | CA | 93704-1468 |  | 2013-09-03 | 2013-09-03 09:19 | 2013-09-03 09:43 | CARRIER - 38CE004300 | 82 | 8.2 | Yes | Yes | 19.9 | 19.3 | 0.6 | 78EDB420784E40F0A6485E3354BC6139 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Clovis | CA | 93612-2516 |  | 2013-09-04 | 2013-09-04 10:47 | 2013-09-04 13:35 | BRYANT - 561CJ024 | 60 | 3.1 | Yes | Yes | 20 | 19.1 | 0.9 | 9A3C1A288F124EFFAF691D5E19CF526F |  | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Vacaville | CA | 95688-9366 |  | 2013-08-01 | 2013-08-01 14:02 | 2013-08-01 15:29 | AMERICAN STANDARD - 2A7B0030A1000AA | 64 | 2.7 | Yes | Yes | 16.3 | 17.7 | -1.4 | 07786DB9BCAE47DDBE7B37C63AF1F8FF |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Clovis | CA | 93612-2526 |  | 2013-08-12 | 2013-08-12 16:54 | 2013-08-12 16:54 | BRYANT - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 6526C09F70A9487F806FD407A97121C4 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2013-07-18 | 2013-07-18 23:00 | 2013-07-18 23:29 | YORK - D1NP042N06506A | 85 | 5.7 | Yes | Yes | 24.7 | 21.3 | 3.4 | E3A61831C1AC424281E37D9670F43CD3 |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
San Jose | CA | 95133-0901 |  | 2013-08-06 | 2013-08-06 13:10 | 2013-08-06 13:10 | CARRIER - 38CKC060300 | 233 | 0 | Yes | Yes | 19.8 | 18.7 | 1.1 | CE2713F16C6340068AE76E6B10F647F3 |  | R22 | TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4803 |  | 2013-08-01 | 2013-08-01 09:04 | 2013-08-01 09:45 | TEMPSTAR - PGAD30D1K3 | 78 | -12 | Yes | Yes | 22.2 | 20 | 2.2 | BEF7D161737F4C0A9CA546EA09624830 |  | R22 | TXV |  | -15.38% | 1.1538 | 4.308% |  |  |  |  | TXV |  |  | -15.38%
Selma | CA | 93662-3376 |  | 2013-07-17 | 2013-07-17 14:34 | 2013-07-17 14:55 | PAYNE - UNK | 62 | 6 | Yes | Yes | 18.4 | 19.9 | -1.5 | 34F712CF2EDC470693E745FE42D0328F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.677% | 0.90323 | 18.6% | [5 empty] | Non-TXV | 9.677%
Parlier | CA | 93648-9630 |  | 2013-08-30 | 2013-08-30 12:47 | 2013-08-30 13:11 | PAYNE - PA13NR030H | 66 | -3.9 | Yes | Yes | 21.9 | 20.4 | 1.5 | AE383DBD20974B9CB5E0B8DA643D211C |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Parlier | CA | 93648-9633 |  | 2013-08-30 | 2013-08-30 16:33 | 2013-08-30 16:59 | RUUD - UNK | 85 | 3.2 | Yes | Yes | 19.6 | 20.7 | -1.1 | 38A36CFCDA8A4CCB8DF8879CA1C80D24 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Antioch | CA | 94509-5216 |  | 2013-07-24 | 2013-07-24 12:17 | 2013-07-24 12:17 | RHEEM - UKN | 85 | 0 | Yes | Yes | 16.9 | 18.8 | -1.9 | 34C5091E8F734DAAABB1F00A28F66C26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1598 |  | 2013-07-23 | 2013-07-23 15:35 | 2013-07-23 16:02 | BDP - 585HJM024040ABAE | 68 | 2.9 | Yes | Yes | 23.3 | 23 | 0.3 | AF8B81B3F0BE42DABDC6A8C7B4C557E8 |  | R22 | Non-TXV |  | 4.265% | 0.95735 | 8.196% | [5 empty] | Non-TXV | 4.265%
Clovis | CA | 93612-2524 |  | 2013-08-12 | 2013-08-12 16:25 | 2013-08-12 16:51 | OTHER - UKN | 57 | 4.3 | Yes | Yes | 21 | 17.6 | 3.5 | 612B8BE5DD44485D8CFDCFA0537BF2A4 |  | R22 | Non-TXV |  | 7.544% | 0.92456 | 14.5% | [5 empty] | Non-TXV | 7.544%
Parlier | CA | 93648-9633 |  | 2013-09-03 | 2013-09-03 16:00 | 2013-09-03 16:18 | RUUD - UNK | 85 | 5.1 | Yes | Yes | 22 | 21 | 1 | 5272D17C6ED84E90800A831FEE02FC92 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Clovis | CA | 93612-2525 |  | 2013-08-16 | 2013-08-16 09:59 | 2013-08-16 10:26 | BRYANT - 561CJ024-D | 58 | -3.4 | Yes | Yes | 19.3 | 20.4 | -1.1 | BAC3F91DFAC94E57B3DF2644167EE914 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Parlier | CA | 93648-9633 |  | 2013-08-21 | 2013-08-21 15:30 | 2013-08-21 16:04 | RUUD - UAMA024JAZ | 85 | 4.5 | Yes | Yes | 19.4 | 20.4 | -1 | A028B29B64854161A4DDCB10FE3F8A42 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Clovis | CA | 93612-2515 |  | 2013-08-09 | 2013-08-09 14:39 | 2013-08-09 15:03 | GOODMAN - CK241B | 71 | 3.2 | Yes | Yes | 18.7 | 15.6 | 3.1 | 4674827203984E18B727F09FF4955161 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
Bakersfield | CA | 93308-2154 |  | 2013-09-03 | 2013-09-03 19:38 | 2013-09-03 19:38 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | 487E6BDD49EB4A2DA493540DCCA0E725 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3247 |  | 2013-08-08 | 2013-08-08 22:31 | 2013-08-08 22:33 | OTHER - H1RD048S064 | 227 | 8.7 | Yes | Yes | 21.5 | 22.1 | -0.6 | 685F69AAFB0642DB89282FD66D630054 |  | R22 | Non-TXV |  | 3.833% | 0.96167 | 7.365% | [5 empty] | Non-TXV | 3.833%
Bakersfield | CA | 93308-2176 |  | 2013-09-04 | 2013-09-04 17:05 | 2013-09-04 17:05 | BRYANT - 582ANW024040AAAD | 53 | 0 | Yes | Yes | 19.7 | 20.6 | -0.9 | 3ADF1AC29B9A4596BEA911DAD5000AA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-2734 |  | 2013-07-18 | 2013-07-18 09:21 | 2013-07-18 09:43 | PAYNE - UNK | 118 | 5.2 | Yes | Yes | 23.9 | 19.3 | 4.6 | 39DA615591084872AEFCB3A7FA55453D |  | R22 | Non-TXV |  | 4.407% | 0.95593 | 8.469% | [5 empty] | Non-TXV | 4.407%
Pleasanton | CA | 94566-6384 |  | 2013-09-13 | 2013-09-13 10:53 | 2013-09-13 11:29 | OTHER - ERCQ0421BBA | 85 | 12.4 | Yes | Yes | 21.7 | 17.7 | 4.1 | B899D2E2881C4CC1A194F0443BFE80AF |  | R22 | Non-TXV |  | 14.59% | 0.85412 | 28.04% | [5 empty] | Non-TXV | 14.59%
Pleasanton | CA | 94566-6384 |  | 2013-09-12 | 2013-09-12 13:25 | 2013-09-12 13:25 | COLEMAN - 2142-911 | 154 | 0 | Yes | Yes | 20.8 | 19.2 | 1.6 | 80873F3933EE4E778E9F1308FA2E41BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9144 |  | 2013-08-10 | 2013-08-10 08:46 | 2013-08-10 09:10 | CARRIER - ILLEGIBLE | 93 | 27.8 | Yes | Yes | 28 | 22.4 | 5.7 | DAFB658903D3416FB35D2B781D2B7570 |  | R22 | Non-TXV |  | 29.89% | 0.70108 | 57.45% | [5 empty] | Non-TXV | 29.89%
Bakersfield | CA | 93311-9144 |  | 2013-08-10 | 2013-08-10 09:11 | 2013-08-10 09:45 | CARRIER - ILLEGIBLE | 93 | 38.6 | Yes | Yes | 27.4 | 21.5 | 5.9 | D6A374E22D9448F2B0D12D76804C860E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 41.51% | 0.58495 | 79.76% | [5 empty] | Non-TXV | 41.51%
Pleasanton | CA | 94566-6384 |  | 2013-09-12 | 2013-09-12 09:46 | 2013-09-12 09:47 | OTHER - 2SCU12LB130P-1 | 85 | -7 | Yes | Yes | 17.8 | 17.6 | 0.2 | 12D0BC1F14A541B6B9C90968573738A6 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Fresno | CA | 93728-1539 |  | 2013-08-02 | 2013-08-02 13:09 | 2013-08-03 05:33 | YORK - D3N2036N05606NXA | 64 | 2.4 | Yes | Yes | 17.2 | 17.1 | 0.1 | B6302E81A51640B397EEA95EBFF95EF6 |  | R410A | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Fresno | CA | 93726-0228 |  | 2013-07-22 | 2013-07-22 09:06 | 2013-07-22 09:24 | RHEEM - HC803621C | 66 | 16.9 | Yes | Yes | 22.8 | 20.2 | 2.7 | 5CD9404EB9DD494189EFF04623459D01 |  | R22 | Non-TXV |  | 25.61% | 0.74394 | 49.21% | [5 empty] | Non-TXV | 25.61%
Fresno | CA | 93728-2911 |  | 2013-07-22 | 2013-07-22 11:24 | 2013-07-22 11:24 | RHEEM - RRNL-B036JK06X | 92 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 36DC29DAF31B45C08ACF57BD2BADAAC9 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-8626 |  | 2013-07-29 | 2013-07-29 16:58 | 2013-07-29 16:58 | GOODMAN - D5C130361AA | 125 | 0 | Yes | Yes | 19.6 | 18 | 1.6 | E4692D34BC6B4EC3A0C6C6C5601576E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2167 |  | 2013-08-30 | 2013-08-30 17:37 | 2013-08-30 17:37 | PAYNE - PY3PNA02404DNB | 89 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 1BBD6585639641ADA7565D718CF11D65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4618 |  | 2013-08-05 | 2013-08-05 19:50 | 2013-08-05 19:50 | BDP - 567C024RCV | 60 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | C6E009E1EF174423BA8160C2B3A3740D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2515 |  | 2013-08-09 | 2013-08-09 15:13 | 2013-08-09 17:54 | BRYANT - 561CJ024 | 60 | 3.2 | Yes | Yes | 18.6 | 17.7 | 0.9 | F8DCC0DF4C4D4C0FACEFE47FFBFD5A5A |  | R22 | Non-TXV |  | 5.333% | 0.94667 | 10.25% | [5 empty] | Non-TXV | 5.333%
Reedley | CA | 93654-3829 |  | 2013-07-18 | 2013-07-18 14:51 | 2013-07-18 15:15 | YORK - D1NP036N05606A | 108 | 6.8 | Yes | Yes | 20.9 | 20.4 | 0.5 | 55056FBE2D864E109FC894C44B146568 |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Sanger | CA | 93657-8624 |  | 2013-09-17 | 2013-09-17 14:10 | 2013-09-17 14:35 | GOODMAN - UNK | 125 | 9.4 | Yes | Yes | 20.1 | 19.3 | 0.8 | 0AF88BCDB435471AB16795C44A9BC3CE |  | R22 | Non-TXV |  | 7.52% | 0.9248 | 14.45% | [5 empty] | Non-TXV | 7.52%
Fresno | CA | 93726-3530 |  | 2013-09-05 | 2013-09-05 14:30 | 2013-09-05 14:48 | PAYNE - UNK | 58 | 4.3 | Yes | Yes | 19.7 | 18.6 | 1.1 | 12B9D25B2F464F51BDAF96F3AC2D891A |  | R22 | Non-TXV |  | 7.414% | 0.92586 | 14.25% | [5 empty] | Non-TXV | 7.414%
Bakersfield | CA | 93305-4708 |  | 2013-08-16 | 2013-08-16 09:34 | 2013-08-16 10:50 | BDP - 589ANW036060ADBF | 85 | 2.5 | Yes | Yes | 20 | 21.6 | -1.6 | 456A2F5F9B64457BA83C5033CD5EB5B0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93308-2178 |  | 2013-09-03 | 2013-09-03 18:27 | 2013-09-03 18:27 | ICP - GPCM24K040F | 57 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | A4D5EAB2B0D3468D845779DB82C951EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4686 |  | 2013-08-06 | 2013-08-06 16:12 | 2013-08-06 16:33 | GOODMAN - 0806044591 | 89 | 12.8 | Yes | Yes | 21.5 | 21 | 0.5 | 6D48B961158C496CA7340631306F61DC |  | R22 | Non-TXV |  | 14.38% | 0.85618 | 27.64% | [5 empty] | Non-TXV | 14.38%
Bakersfield | CA | 93309-4686 |  | 2013-08-06 | 2013-08-06 17:12 | 2013-08-06 17:12 | BDP - 567C024RCU | 60 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 7B62FF1B0EBB4D999705D6BE4A10CBD2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4127 |  | 2013-08-01 | 2013-08-01 11:55 | 2013-08-01 11:55 | GOODMAN - PGB036075-1A | 60 | 0 | Yes | Yes | 22.1 | 22.6 | -0.5 | F8F2BD7772D541F8A469A52D963415C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4636 |  | 2013-08-15 | 2013-08-15 15:15 | 2013-08-15 16:00 | BDP - 567C024RCU | 60 | 9.8 | Yes | Yes | 20.6 | 20.4 | 0.2 | 490B5BB6F0294F70A537F51D92F04CE2 |  | R22 | Non-TXV |  | 16.33% | 0.83667 | 31.39% | [5 empty] | Non-TXV | 16.33%
Clovis | CA | 93612-2526 |  | 2013-09-03 | 2013-09-03 13:29 | 2013-09-03 13:45 | BRYANT - 561CJ021 | 51 | 3.7 | Yes | Yes | 18 | 20.2 | -2.1 | 1EEA1C3977124FFABE082BEBC2D8392B |  | R22 | TXV |  | 7.255% | 0.92745 | 13.94% | [5 empty] | TXV | 7.255%
Parlier | CA | 93648-9626 |  | 2013-08-19 | 2013-08-19 09:10 | 2013-08-19 10:05 | RUUD - UNK | 72 | 5.1 | Yes | Yes | 20.7 | 19.8 | 0.9 | 042B9637C9034B5AB1C69DA8D557C9D3 |  | R22 | Non-TXV |  | 7.083% | 0.92917 | 13.61% | [5 empty] | Non-TXV | 7.083%
Fresno | CA | 93705-4332 |  | 2013-07-19 | 2013-07-19 16:35 | 2013-07-19 16:35 | GOODMAN - GPG1348070M41BA | 87 | 0 | Yes | Yes | 21.8 | 18.9 | 3 | 9AB4627F87764BF0AE665D50A2B7459A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-5313 |  | 2013-07-31 | 2013-07-31 10:28 | 2013-07-31 12:13 | CARRIER - 38CKB030321 | 76 | 4.3 | Yes | Yes | 18.2 | 17.4 | 0.8 | 13205D728C36473A9FFE860790E04FE2 |  | R22 | Non-TXV |  | 5.658% | 0.94342 | 10.87% | [5 empty] | Non-TXV | 5.658%
Fresno | CA | 93705-5149 |  | 2013-07-19 | 2013-07-19 12:19 | 2013-07-19 12:19 | YORK - DN3NZ042N0656NXC | 78 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | BA8516B3EF0C4834A2B0DC4E0606D9A4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2079 |  | 2013-10-02 | 2013-10-02 10:19 | 2013-10-02 11:02 | GE - BTR724A100A0 | 70 | 7.2 | Yes | Yes | 20.2 | 16.4 | 3.8 | 086F986A8C4048C0920372632405675C |  | R22 | Non-TXV |  | 10.29% | 0.89714 | 19.77% | [5 empty] | Non-TXV | 10.29%
Fresno | CA | 93722-3425 |  | 2013-07-24 | 2013-07-24 09:31 | 2013-07-24 09:48 | - CA5036UKB1867.830340 | 86 | 7.8 | Yes | Yes | 25.2 | 21.4 | 3.8 | DA10FD9B52DB4D5EB630B19D7DA28A85 |  | R22 | Non-TXV |  | 9.07% | 0.9093 | 17.43% | [5 empty] | Non-TXV | 9.07%
Fresno | CA | 93722-3425 |  | 2013-07-24 | 2013-07-24 09:51 | 2013-07-24 10:10 | - CA5024UKB1867.830320 | 67 | 8.9 | Yes | Yes | 26.9 | 21 | 5.9 | AE94C052F7DA4940BB59803E8FB57237 |  | R22 | Non-TXV |  | 13.28% | 0.86716 | 25.53% | [5 empty] | Non-TXV | 13.28%
Fresno | CA | 93726-2808 |  | 2013-11-01 | 2013-11-01 12:30 | 2013-11-01 12:30 | TRANE - 4YCY4042B1096AA | 109 | 0 | Yes | Yes | 19.8 | 19.1 | 0.7 | 763E1E855EF64D1B9DA7CB6A95EACB20 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2528 |  | 2013-08-12 | 2013-08-12 14:39 | 2013-08-12 14:39 | OTHER - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 89A7EC6DA04A4FF88EA105605E9D2136 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2015 |  | 2013-09-26 | 2013-09-26 13:10 | 2013-09-26 13:31 | RHEEM - UKN | 90 | 5.3 | Yes | Yes | 24 | 20.9 | 3.1 | 4730D7F1632B4DEF84311E369AC0B12B |  | R22 | Non-TXV |  | 5.889% | 0.94111 | 11.32% | [5 empty] | Non-TXV | 5.889%
Fairfield | CA | 94533-3625 |  | 2013-07-25 | 2013-07-25 12:50 | 2013-07-25 12:50 | GE - | 85 | 0 | Yes | Yes | 14.7 | 15.9 | -1.2 | DACC22DDDAFD40A3A948CE285D9E36F1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2525 |  | 2013-08-13 | 2013-08-13 11:45 | 2013-08-13 12:07 | BRYANT - UKN | 51 | 4.6 | Yes | Yes | 18.9 | 19.3 | -0.4 | 3DE0A3DC7F554E1FB659DB66B8899414 |  | R22 | TXV |  | 9.02% | 0.9098 | 17.33% | [5 empty] | TXV | 9.02%
Bakersfield | CA | 93306-3846 |  | 2013-07-17 | 2013-07-17 13:38 | 2013-07-17 14:08 | HEIL - PGC036K06013 | 87 | -6.1 | Yes | Yes | 18.5 | 21.1 | -2.6 | 542854558E18457F8C02FE2E31E18216 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.011% | 1.0701 | 1.964% |  |  |  |  | Non-TXV |  |  | -7.011%
Fresno | CA | 93720-2449 |  | 2013-10-24 | 2013-10-24 14:29 | 2013-10-24 14:47 | GE - CK24-1B | 71 | 10.7 | Yes | Yes | 18 | 20.3 | -2.3 | 5C21D8063A1D4B198139A2C63C143232 |  | R22 | Non-TXV |  | 15.07% | 0.8493 | 28.96% | [5 empty] | Non-TXV | 15.07%
Fresno | CA | 93726-4013 |  | 2013-07-24 | 2013-07-24 16:03 | 2013-07-24 16:03 | GOODMAN - CKL491C | 112 | 0 | Yes | Yes | 22.8 | 19.9 | 2.9 | 75A754BAB3574C05AA7D70A926FAB241 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4825 |  | 2013-07-24 | 2013-07-24 12:35 | 2013-07-24 12:35 | BRYANT - 113ANA042C | 93 | 0 | Yes | Yes | 22.1 | 19.3 | 2.8 | FD9E441F9D7B4B98846B040E68974E61 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-2856 |  | 2013-08-30 | 2013-08-30 18:24 | 2013-08-30 18:24 | AMANA - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 12156893BC824BF0A632AE85B14D5EFE | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5411 |  | 2013-08-07 | 2013-08-07 12:43 | 2013-08-07 13:07 | TEMPSTAR - PGAD24B1KB | 85 | 2.8 | Yes | Yes | 25.5 | 21.9 | 3.6 | 999BA7DE51D945F0981A60E928879D80 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
American Canyon | CA | 94503-1408 |  | 2013-07-30 | 2013-07-30 12:10 | 2013-07-30 12:11 | RHEEM - 13AJA60A01757 | 134 | -9.5 | Yes | Yes | 18.2 | 17.6 | 0.6 | 85A78E66914D4A87803FB8E577CB9463 |  | R22 | Non-TXV |  | -7.09% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.09%
Clovis | CA | 93612-2512 |  | 2013-09-04 | 2013-09-04 11:25 | 2013-09-04 11:44 | BRYANT - 561CJ024D | 58 | 2 | Yes | Yes | 19.7 | 18.6 | 1.1 | ED42BB616A9C414E995E5415DDBD8141 |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Fresno | CA | 93726-6627 |  | 2013-07-23 | 2013-07-23 12:46 | 2013-07-23 13:30 | OTHER - PGC036K060D | 71 | 2.7 | Yes | Yes | 18.2 | 19.3 | -1.1 | 8BDF556A59A0497E8586A565D24C9F33 |  | R22 | Non-TXV |  | 3.803% | 0.96197 | 7.308% | [5 empty] | Non-TXV | 3.803%
Bakersfield | CA | 93313-5749 |  | 2013-07-22 | 2013-07-22 10:01 | 2013-07-22 11:15 | PAYNE - PA12NA036 | 100 | -8.2 | Yes | Yes | 22.5 | 19 | 3.6 | 6D735EDF1DCE4EF5AFBF01975AABBAC2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.2% | 1.082 | 2.296% |  |  |  |  | Non-TXV |  |  | -8.2%
Bakersfield | CA | 93308-2991 |  | 2013-08-30 | 2013-08-30 18:26 | 2013-08-30 18:26 | LUXAIRE - 18ECWG45GA | 71 | 0 | Yes | Yes | 19.2 | 20.9 | -1.7 | 1E000F749FF94291BB53807AB0FB463C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8818 |  | 2013-07-17 | 2013-07-17 16:06 | 2013-07-17 16:53 | RHEEM - RRNAB036JK06X | 83 | 4.1 | Yes | Yes | 19.4 | 21.2 | -1.8 | 68B6B7B4C3D94A359D06F2773BADA1F4 |  | R22 | TXV |  | 4.94% | 0.9506 | 9.493% | [5 empty] | TXV | 4.94%
Bakersfield | CA | 93307-6888 |  | 2013-08-08 | 2013-08-08 22:54 | 2013-08-08 22:56 | YORK - D1NHO4206506C | 84 | 4 | Yes | Yes | 23 | 20.8 | 2.2 | EE57AFE3862A4BC68E78714C321A9784 |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Fresno | CA | 93710-6218 |  | 2013-08-07 | 2013-08-07 10:26 | 2013-08-07 10:58 | CARRIER - UKN | 80 | -13.5 | Yes | Yes | 22.1 | 18.2 | 3.9 | 90531B811791421494636DE2C341AB24 |  | R22 | TXV |  | -16.88% | 1.1687 | 4.726% |  |  |  |  | TXV |  |  | -16.88%
Bakersfield | CA | 93313-5182 |  | 2013-07-22 | 2013-07-22 16:33 | 2013-07-22 16:59 | RHEEM - UKN | 80 | 4 | Yes | Yes | 21.2 | 20.4 | 0.8 | 37AA2968492747A1AAB6A49D47CFD65E |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93309-4687 |  | 2013-08-06 | 2013-08-06 17:36 | 2013-08-06 17:36 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 21.1 | 19.8 | 1.3 | DBA4F97C8FDC4077AC6E9DABD98CBF5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cupertino | CA | 95014-0501 |  | 2013-10-02 | 2013-10-02 13:17 | 2013-10-02 14:52 | TRANE - UNK | 86 | 3.3 | Yes | Yes | 18 | 20.7 | -2.7 | F5FBA1843FDA4C28A9772096A8B2D8F1 |  | R22 | Non-TXV |  | 3.837% | 0.96163 | 7.374% | [5 empty] | Non-TXV | 3.837%
Bakersfield | CA | 93307-4952 |  | 2013-07-24 | 2013-07-24 11:10 | 2013-07-24 11:31 | PAYNE - PYPNB036060ABAA | 85 | 3.9 | Yes | Yes | 23.7 | 21.1 | 2.6 | 006BEBA0A2864973B61FF6B23861DE25 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93307-8819 |  | 2013-08-01 | 2013-08-01 13:05 | 2013-08-01 16:13 | RHEEM - RRNA-B042JK08X | 85 | 2.5 | Yes | Yes | 23 | 21.5 | 1.5 | 717273D34CEA44EB96BD439AE7250DA1 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Selma | CA | 93662-4422 |  | 2013-07-30 | 2013-07-30 17:50 | 2013-07-30 18:15 | LENNOX - 10GCS036753PA | 58 | 2.9 | Yes | Yes | 24 | 20.2 | 3.8 | ED71746004A64C7AA0B0BE35ABF8AB7D |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93307-5757 |  | 2013-08-06 | 2013-08-06 12:48 | 2013-08-06 18:14 | BRYANT - 113RNA048-C | 185 | 7.2 | Yes | Yes | 18.7 | 21.7 | -3 | C874C49FA9544B028487D46A6362664E |  | R22 | TXV |  | 3.892% | 0.96108 | 7.479% | [5 empty] | TXV | 3.892%
Selma | CA | 93662-9008 |  | 2013-07-17 | 2013-07-17 12:53 | 2013-07-17 12:53 | GUARDIAN - GCG36S41S3A | 73 | 0 | Yes | Yes | 21.2 | 20.9 | 0.3 | AE2A7BE1B125467FA7168F59C4476E5F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4617 |  | 2013-08-06 | 2013-08-06 16:24 | 2013-08-06 16:24 | GOODMAN - GSC1301AE | 90 | 0 | Yes | Yes | 20 | 20.1 | -0.1 | 62A4985F1BD6452F9345AE77691C217C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4714 |  | 2013-08-15 | 2013-08-15 16:50 | 2013-08-15 17:16 | CARRIER - 38BRC036330 | 104 | 5.3 | Yes | Yes | 20.2 | 21.7 | -1.5 | 1B2DF71FB2484A2ABFB340E6DD1E6B28 |  | R22 | Non-TXV |  | 5.096% | 0.94904 | 9.794% | [5 empty] | Non-TXV | 5.096%
Vallejo | CA | 94589-3611 |  | 2013-08-02 | 2013-08-02 10:34 | 2013-08-02 10:35 | TRANE - 4TTB3030D100AA | 82 | 7.6 | Yes | Yes | 17.9 | 17 | 0.9 | 2A2A317EE7664A2C9EF419E4A699D230 |  | R22 | Non-TXV |  | 9.268% | 0.90732 | 17.81% | [5 empty] | Non-TXV | 9.268%
Fresno | CA | 93703-4802 |  | 2013-10-12 | 2013-10-12 13:55 | 2013-10-12 14:11 | DAY & NIGHT - 585GJW024040ABAF | 54 | 2.2 | Yes | Yes | 25.5 | 20.7 | 4.8 | 4E02BA17DDED4955B3FE5847D85F7DCF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Mc Farland | CA | 93250-1081 |  | 2013-07-26 | 2013-07-26 21:53 | 2013-07-26 21:58 | GOODMAN - GSC130301DA | 87 | 3.6 | Yes | Yes | 21.2 | 21 | 0.2 | 7F4B65F2588B428F92AAB2CCCCCB6445 |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Vallejo | CA | 94591-4737 |  | 2013-07-31 | 2013-07-31 14:28 | 2013-07-31 14:45 | HEIL - ACS042A2C1 | 90 | 3.8 | Yes | Yes | 16.6 | 16.5 | 0.1 | BC3B435E105B4264B0F65EC3E7C0EABE |  | R22 | Non-TXV |  | 4.222% | 0.95778 | 8.114% | [5 empty] | Non-TXV | 4.222%
Fresno | CA | 93705-0605 |  | 2013-08-26 | 2013-08-26 09:28 | 2013-08-26 09:56 | ARCOAIRE - PGAD36D1K7 | 102 | 3.2 | Yes | Yes | 21.3 | 19.8 | 1.5 | 7BE3BBE4C8664243A351DC81566560B7 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Ukiah | CA | 95482-8707 |  | 2013-08-23 | 2013-08-23 08:54 | 2013-08-23 09:14 | YORK - BRCS03018D | 62 | 4.7 | Yes | Yes | 21.1 | 20.8 | 0.3 | 0934883FD7E840B1813A6CF1427BEA91 |  | R22 | Non-TXV |  | 7.581% | 0.92419 | 14.57% | [5 empty] | Non-TXV | 7.581%
Fresno | CA | 93705-5133 |  | 2013-07-31 | 2013-07-31 15:33 | 2013-07-31 15:33 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 830756EC37794CE7B726CEBF960AE801 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8932 |  | 2013-10-11 | 2013-10-11 14:28 | 2013-10-11 16:07 | CARRIER - 38CKC042350 | 82 | 3.4 | Yes | Yes | 17.9 | 20.4 | -2.5 | EA6CEA548B034B3580FE08E48709A423 |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Parlier | CA | 93648-9672 |  | 2013-08-01 | 2013-08-01 13:02 | 2013-08-01 13:43 | LENNOX - 13GCSA36068X2301A | 101 | 5.9 | Yes | Yes | 22.5 | 19.1 | 3.4 | 6779BC2BABD746BFBED1646120F44305 |  | R22 | Non-TXV |  | 5.842% | 0.94158 | 11.23% | [5 empty] | Non-TXV | 5.842%
Fresno | CA | 93726-2306 |  | 2013-07-29 | 2013-07-29 13:54 | 2013-07-29 14:57 | OTHER - GPFM36K060 | 68 | 5 | Yes | Yes | 20 | 21.7 | -1.7 | 2D7F44B4AEFB402FA52435CBD8D3976F |  | R22 | TXV |  | 7.353% | 0.92647 | 14.13% | [5 empty] | TXV | 7.353%
Bakersfield | CA | 93309-4679 |  | 2013-08-15 | 2013-08-15 18:36 | 2013-08-15 18:36 | BDP - 567024RCU | 60 | 0 | Yes | Yes | 21.1 | 19.8 | 1.3 | 8A2B2741BA9240F39342CD40E18BA488 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2716 |  | 2013-09-11 | 2013-09-11 15:57 | 2013-09-11 16:13 | ARMSTRONG - 2AC13B24P2B | 89 | 3 | Yes | Yes | 20.5 | 20.8 | -0.3 | D17A416A83694532A9C7A8DC64CC3E76 |  | R22 | Non-TXV |  | 3.371% | 0.96629 | 6.478% | [5 empty] | Non-TXV | 3.371%
Bakersfield | CA | 93309-4636 |  | 2013-08-15 | 2013-08-15 16:38 | 2013-08-15 16:38 | BDP - 567C018RCU | 51 | 0 | Yes | Yes | 21.9 | 20.6 | 1.4 | 005979C8DFDF476CA0979BB8716DC0B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5170 |  | 2013-07-26 | 2013-07-26 12:49 | 2013-07-26 12:49 | TRANE - 2TTX4042B1000AA | 137 | 0 | Yes | Yes | 16.1 | 16.4 | -0.3 | A73D3A4514894BD4B0430A0D993F67B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9656 |  | 2013-11-01 | 2013-11-01 15:00 | 2013-11-01 15:38 | LENNOX - 10ACC04223004 | 81 | 3.2 | Yes | Yes | 22.4 | 19 | 3.4 | 2F357460B062425899D75B421ABC2E6B |  | R22 | Non-TXV |  | 3.951% | 0.96049 | 7.592% | [5 empty] | Non-TXV | 3.951%
Bakersfield | CA | 93307-0000 |  | 2013-07-18 | 2013-07-18 22:26 | 2013-07-18 22:59 | YORK - DINP042N06506A | 102 | -7.8 | Yes | Yes | 24.7 | 21.3 | 3.4 | D6838D9E6ACD45E9AA24F828FE2F072A |  | R22 | TXV |  | -7.647% | 1.0765 | 2.142% |  |  |  |  | TXV |  |  | -7.647%
Selma | CA | 93662-4422 |  | 2013-07-17 | 2013-07-17 13:39 | 2013-07-17 14:03 | LENNOX - 10GCS036753PA | 58 | 4.9 | Yes | Yes | 26.8 | 20.8 | 6 | 2592391AF512476AA897088FCF55D580 |  | R22 | Non-TXV |  | 8.448% | 0.91552 | 16.24% | [5 empty] | Non-TXV | 8.448%
Fresno | CA | 93705-1225 |  | 2013-08-21 | 2013-08-21 09:34 | 2013-08-21 10:20 | OTHER - UKN | 80 | 5.3 | Yes | Yes | 19.7 | 20.4 | -0.7 | AC1AE869B4E144E3A3B2B6F3AB61E762 |  | R22 | Non-TXV |  | 6.625% | 0.93375 | 12.73% | [5 empty] | Non-TXV | 6.625%
Bakersfield | CA | 93309-4616 |  | 2013-08-06 | 2013-08-06 18:47 | 2013-08-06 18:47 | OTHER - T2AA3182A | 67 | 0 | Yes | Yes | 21.1 | 20.8 | 0.3 | B2CEE9F1CEE94066A6A3C31B3812323E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4687 |  | 2013-08-06 | 2013-08-06 16:43 | 2013-08-06 16:43 | ICP - PHF024K000A | 77 | 0 | Yes | Yes | 19 | 20.9 | -1.9 | AF1EF33CC3B644D5AB0CE40A7DE8F77D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4616 |  | 2013-08-06 | 2013-08-06 19:05 | 2013-08-06 19:05 | BDP - 567C024RCU | 75 | 0 | Yes | Yes | 20.9 | 20.2 | 0.7 | 2D25623B83D246CCBBCDC7204F007D12 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0250 |  | 2013-07-30 | 2013-07-30 11:33 | 2013-07-30 11:55 | OTHER - UNK | 66 | -4.7 | Yes | Yes | 23.7 | 21.2 | 2.5 | DCC8254E6776445FA1DE7C5ACD0DC482 |  | R22 | Non-TXV |  | -7.121% | 1.0712 | 1.994% |  |  |  |  | Non-TXV |  |  | -7.121%
Fresno | CA | 93711-0250 |  | 2013-07-30 | 2013-07-30 11:57 | 2013-07-30 11:57 | OTHER - UNK | 66 | 0 | Yes | Yes | 35 | 21 | 14 | 47E0C3F9F35B4DD1A1A0D7F9575EE11C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4640 |  | 2013-08-06 | 2013-08-06 17:52 | 2013-08-06 18:10 | DAY & NIGHT - 591ANX018000AAAA | 48 | 6.7 | Yes | Yes | 22.7 | 21 | 1.8 | 0E04B73595A74D71B372ED6C085857CF |  | R22 | Non-TXV |  | 13.96% | 0.86042 | 26.82% | [5 empty] | Non-TXV | 13.96%
Parlier | CA | 93648-9672 |  | 2013-08-01 | 2013-08-01 14:28 | 2013-08-01 14:50 | LENNOX - 13ACD04223002 | 111 | 6.5 | Yes | Yes | 21.9 | 21.2 | 0.8 | 6FBE6ABFA7DD4F4B928B2DC90BD41997 |  | R22 | Non-TXV |  | 5.856% | 0.94144 | 11.25% | [5 empty] | Non-TXV | 5.856%
Parlier | CA | 93648-9624 |  | 2013-08-19 | 2013-08-19 12:37 | 2013-08-19 12:59 | RUUD - UNK | 70 | 3.9 | Yes | Yes | 18 | 17.5 | 0.5 | 2C08E92F6AFC485493661FE237911140 |  | R22 | Non-TXV |  | 5.571% | 0.94429 | 10.71% | [5 empty] | Non-TXV | 5.571%
Bakersfield | CA | 93309-6010 |  | 2013-08-02 | 2013-08-02 13:37 | 2013-08-02 13:37 | RUUD - UKN | 90 | 0 | Yes | Yes | 22.2 | 20.9 | 1.3 | DF3D061417B44F2CA14671B7D7D294AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5186 |  | 2013-07-17 | 2013-07-17 10:27 | 2013-07-17 10:44 | LENNOX - UNK | 88 | -5.2 | Yes | Yes | 24.1 | 19.8 | 4.3 | F7A0BDFB783543DB9F8E8CE64B58A9F1 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Parlier | CA | 93648-9633 |  | 2013-11-01 | 2013-11-01 11:37 | 2013-11-01 12:01 | RUUD - UNK | 74 | -4.4 | Yes | Yes | 21.7 | 19 | 2.7 | 2B06EEE4D3D346AAA0169A6D63588C22 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Fresno | CA | 93706-1302 |  | 2013-09-12 | 2013-09-12 15:15 | 2013-09-12 15:33 | CARRIER - UNK | 70 | 2.5 | Yes | Yes | 21.9 | 20.6 | 1.3 | 0C3504C8CB604F598792A896619B1535 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Bakersfield | CA | 93309-5904 |  | 2013-08-20 | 2013-08-20 17:52 | 2013-08-20 17:52 | BRYANT - 577CNWA48090NATP | 152 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | 3ECCFB38F00845FF9BF7F577AE95AF92 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4399 |  | 2013-08-06 | 2013-08-06 12:55 | 2013-08-06 13:27 | CARRIER - 38BRB042310 | 131 | 20.4 | Yes | Yes | 24.9 | 20.4 | 4.5 | BF5FB442547341EF85A9D6A721AB496F |  | R22 | Non-TXV |  | 15.57% | 0.84427 | 29.93% | [5 empty] | Non-TXV | 15.57%
Parlier | CA | 93648-9624 |  | 2013-08-19 | 2013-08-19 13:21 | 2013-08-19 14:17 | RUUD - UNK | 80 | 2.6 | Yes | Yes | 17.7 | 19.3 | -1.6 | 410AC5784B0C44DE808DC72EFD3DD28A |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Fresno | CA | 93727-6412 |  | 2013-07-30 | 2013-07-30 14:42 | 2013-07-30 16:00 | YORK - 02GA030N06406C | 80 | 4.6 | Yes | Yes | 19.8 | 20.2 | -0.4 | 431BFAC60F8C4F11A053A264A0153EA2 |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Fresno | CA | 93727-3321 |  | 2013-07-29 | 2013-07-29 17:13 | 2013-07-29 18:22 | OTHER - PGC036K060D | 71 | -5 | Yes | Yes | 18.8 | 19.9 | -1.1 | D6CBE1C215B642FCB43ED34F27E85820 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Fairfield | CA | 94533-1803 |  | 2013-07-26 | 2013-07-26 11:45 | 2013-07-26 11:46 | OTHER - CA7036UJA2 | 72 | -5.1 | Yes | Yes | 17.4 | 17.6 | -0.2 | 128A147A8D4A43BEB9E7C7AABD00FBFB |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Fresno | CA | 93726-1251 |  | 2013-10-31 | 2013-10-31 10:56 | 2013-10-31 11:22 | RUUD - RRNLB024JK06X | 79 | 4.3 | Yes | Yes | 20.6 | 18.2 | 2.4 | 81A021BBD9844A6DB9EDA6FBB319A0BB |  | R410A | Non-TXV |  | 5.443% | 0.94557 | 10.46% | [5 empty] | Non-TXV | 5.443%
Fresno | CA | 93710-3941 |  | 2013-07-24 | 2013-07-24 09:45 | 2013-07-24 10:06 | PAYNE - 597CN030C | 100 | -5.9 | Yes | Yes | 21.8 | 19.9 | 1.9 | 01D3813E42274E85AD58BA8BCB803D8B |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Fresno | CA | 93711-0889 |  | 2013-08-14 | 2013-08-14 14:13 | 2013-08-14 14:32 | PAYNE - UNK | 70 | 22.9 | Yes | Yes | 23.3 | 21.4 | 2 | B883FFD2F16D4107BE75A943CEEB4EDB |  | R22 | Non-TXV |  | 32.71% | 0.67286 | 62.87% | [5 empty] | Non-TXV | 32.71%
Fresno | CA | 93711-0889 |  | 2013-08-14 | 2013-08-14 14:35 | 2013-08-14 14:35 | PAYNE - UNK | 70 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | E12332B81833459DBED2CCE6A0D0B6B2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-0749 |  | 2013-08-02 | 2013-08-02 16:42 | 2013-08-02 16:42 | HEIL - UKN | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 77C12E1D0DFE44A885B9034C8EA58EB8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-2007 |  | 2013-07-30 | 2013-07-30 12:40 | 2013-07-30 12:40 | GOODMAN - GPG13300701BB | 77 | 17 | Yes | Yes | 27.7 | 18.5 | 9.3 | A7932E14006C48D6BB22E9048B9C898F | Add refrigerant: 17 oz | R22 | Non-TXV |  | 22.08% | 0.77922 | 42.43% | [5 empty] | Non-TXV | 22.08%
Fairfield | CA | 94533-8003 |  | 2013-08-14 | 2013-08-14 09:18 | 2013-08-14 13:54 | RUUD - UAFD-024JAS | 67 | -3.9 | Yes | Yes | 18.7 | 20.4 | -1.7 | 91B54DA1708A49BABA223A05F478F8D1 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Vacaville | CA | 95687-7811 |  | 2013-08-01 | 2013-08-01 09:50 | 2013-08-01 10:50 | TRANE - 2TTR1042A1000AA | 95 | 3.2 | Yes | Yes | 14.4 | 17.2 | -2.8 | C7555212FC1F4BEBA556B8C391B47919 |  | R22 | Non-TXV |  | 3.368% | 0.96632 | 6.473% | [5 empty] | Non-TXV | 3.368%
Fresno | CA | 93726-1242 |  | 2013-09-17 | 2013-09-17 09:28 | 2013-09-17 09:28 | GOODMAN - GPG1324045M41BA | 69 | 0 | Yes | Yes | 17 | 19.4 | -2.4 | 40F23FCC431141379AF664BDE2F84F64 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1248 |  | 2013-09-17 | 2013-09-17 10:01 | 2013-09-17 10:21 | TAPPAN - IRTA227541S | 80 | 4.7 | Yes | Yes | 18.7 | 19.9 | -1.2 | 56FA2A557E174EC7AA1CC33FE323EA19 |  | R22 | Non-TXV |  | 5.875% | 0.94125 | 11.29% | [5 empty] | Non-TXV | 5.875%
Suisun City | CA | 94585-1811 |  | 2013-08-23 | 2013-08-23 13:41 | 2013-08-23 13:41 | PAYNE - PA10JA036-C | 75 | 0 | Yes | Yes | 15.3 | 17.7 | -2.4 | B2717DF6F3D549DEA3ED451A81984289 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1509 |  | 2013-08-13 | 2013-08-13 09:23 | 2013-08-13 09:23 | DAY & NIGHT - 591AN036-A | 84 | 0 | Yes | Yes | 19.1 | 21.9 | -2.8 | 5C2DFC71B06B45FDA5308451A7690620 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4328 |  | 2013-08-01 | 2013-08-01 10:47 | 2013-08-01 12:44 | YORK - H2RC036S06G | 83 | 7.9 | Yes | Yes | 20 | 19.3 | 0.7 | F902A7B66D1542BB948CDBF8E8E9FDA2 |  | R22 | TXV |  | 9.518% | 0.90482 | 18.29% | [5 empty] | TXV | 9.518%
Fresno | CA | 93726-1251 |  | 2013-09-17 | 2013-09-17 10:25 | 2013-09-17 10:25 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 21.9 | 21.3 | 0.6 | F3C61D515687493C8950626B2D981F4A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3525 |  | 2013-09-06 | 2013-09-06 11:06 | 2013-09-06 11:24 | TRANE - YCC024F1L0BH | 65 | 1.9 | Yes | Yes | 18.6 | 18.7 | -0.1 | 84039B5DA4784FC4A2A30200AD974C6F |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Cottonwood | CA | 96022-9072 |  | 2013-09-07 | 2013-09-07 08:40 | 2013-09-07 09:24 | INTERTHERM - CKL30-15 | 83 | -6.8 | Yes | Yes | 22.5 | 19.8 | 2.7 | FEF6F682C81241C2BE2320AFF5A5A030 |  | R22 | Non-TXV |  | -8.193% | 1.0819 | 2.294% |  |  |  |  | Non-TXV |  |  | -8.193%
Suisun City | CA | 94585-1811 |  | 2013-08-01 | 2013-08-01 12:03 | 2013-08-01 12:03 | TRANE - UKN | 85 | 0 | Yes | Yes | 16.3 | 18.5 | -2.2 | F1B3B083C9F7440B9637B8FA9E3663E8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4015 |  | 2013-07-23 | 2013-07-23 15:56 | 2013-07-23 16:18 | PAYNE - 589ANW030080ABBD | 72 | 3.4 | Yes | Yes | 22.6 | 21.6 | 1.1 | EADD02A8BB4945BD961CDD5F997AFE65 |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Fresno | CA | 93726-4015 |  | 2013-07-23 | 2013-07-23 16:20 | 2013-07-23 17:00 | PAYNE - 589ANW030080ABBD | 72 | 11 | Yes | Yes | 27.1 | 21.1 | 6 | 85CE4ECA1E7349CFB522A663A9366D7E |  | R22 | Non-TXV |  | 15.28% | 0.84722 | 29.36% | [5 empty] | Non-TXV | 15.28%
Parlier | CA | 93648-9629 |  | 2013-08-20 | 2013-08-20 13:41 | 2013-08-20 14:21 | RUUD - UNK | 70 | 5.1 | Yes | Yes | 18.6 | 19.8 | -1.2 | F45989930DA34EEDB6CE0E4CB144FD06 |  | R22 | Non-TXV |  | 7.286% | 0.92714 | 14% | [5 empty] | Non-TXV | 7.286%
Bakersfield | CA | 93308-2969 |  | 2013-08-30 | 2013-08-30 17:13 | 2013-08-30 17:13 | TRANE - 4YCC3024B1064AA | 93 | 0 | Yes | Yes | 21.3 | 19.8 | 1.5 | F464A79EAFC0471DBAFCFC729B567FA1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3527 |  | 2013-09-06 | 2013-09-06 11:25 | 2013-09-06 11:47 | TRANE - YCC024F1L0BJ | 65 | 1.9 | Yes | Yes | 20 | 18.9 | 1.1 | 11078A53566942839F6C687160873111 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Fresno | CA | 93705-1642 |  | 2013-08-15 | 2013-08-15 11:11 | 2013-08-15 11:39 | LENNOX - 036X751PA | 58 | 6 | Yes | Yes | 22 | 20.2 | 1.9 | 298AE3D98FEC4134B81D1D32B96F1584 |  | R22 | Non-TXV |  | 10.34% | 0.89655 | 19.88% | [5 empty] | Non-TXV | 10.34%
Clovis | CA | 93612-2447 |  | 2013-07-30 | 2013-07-30 15:49 | 2013-07-30 15:49 | TAPPAN - CM4845C | 122 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 6A696C8A829849CFB2141EAD3785134D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1810 |  | 2013-07-25 | 2013-07-25 13:22 | 2013-07-25 15:35 | GE - | 85 | 2.5 | Yes | Yes | 14.4 | 17.2 | -2.8 | B9A9DFE8E6DA4A709EA91C4BB7633521 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93726-2645 |  | 2013-07-23 | 2013-07-23 14:43 | 2013-07-23 14:43 | CARRIER - 4855036080321 | 68 | 0 | Yes | Yes | 24.8 | 20.7 | 4.1 | DE984ABCDDCC4A9EADDE97F40546F05B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2966 |  | 2013-08-30 | 2013-08-30 15:27 | 2013-08-30 15:27 | TRANE - 4YCC3024B1064AA | 93 | 0 | Yes | Yes | 19.8 | 19.8 | 0 | 53B2E3C43B304169AFE755BECC87A5F8 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5773 |  | 2013-07-30 | 2013-07-30 17:31 | 2013-07-30 17:50 | OTHER - N2A336AKB200 | 85 | -3.3 | Yes | Yes | 13.9 | 16.3 | -2.4 | 179B44ABDA964231B8BAFAD0CCA6AF66 |  | R22 | TXV |  | -3.882% | 1.0388 | 1.087% |  |  |  |  | TXV |  |  | -3.882%
Fresno | CA | 93710-5606 |  | 2013-07-24 | 2013-07-24 10:43 | 2013-07-24 11:04 | ARCOAIRE - UNK | 70 | 10.1 | Yes | Yes | 18.7 | 20.1 | -1.4 | 5AB3616B5FC3412496B25BE5EC0815BD |  | R22 | Non-TXV |  | 14.43% | 0.85571 | 27.73% | [5 empty] | Non-TXV | 14.43%
Antioch | CA | 94509-5871 |  | 2013-08-12 | 2013-08-12 08:50 | 2013-08-12 08:54 | DAY & NIGHT - 569DB048 | 161 | 5.7 | Yes | Yes | 18.5 | 17.6 | 0.9 | DEB2A8C1DF4141D3AD250807788AD3C3 |  | R22 | Non-TXV |  | 3.54% | 0.9646 | 6.804% | [5 empty] | Non-TXV | 3.54%
Fairfield | CA | 94533-2001 |  | 2013-07-26 | 2013-07-26 11:06 | 2013-07-26 11:08 | YORK - AC024X1021A | 52 | 2.9 | Yes | Yes | 17.3 | 19.8 | -2.5 | 56F30FC35B5B4B39B79CE95223959212 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Bakersfield | CA | 93308-2972 |  | 2013-08-29 | 2013-08-29 17:00 | 2013-08-29 17:00 | ICP - PGC024K0L10A | 58 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 5C017C38A5304C408AACCAB000D58923 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7166 |  | 2013-10-08 | 2013-10-08 18:25 | 2013-10-08 18:25 | YORK - H2RC042S06HG | 109 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 5964C7047B5B45CFBBF691662DF44581 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5472 |  | 2013-07-24 | 2013-07-24 14:09 | 2013-07-24 14:39 | OTHER - FS3BC048KA | 110 | 10.9 | Yes | Yes | 21.4 | 22 | -0.6 | 0851A93A0D564ED49F7D7589909A695C |  | R22 | TXV |  | 9.909% | 0.90091 | 19.04% | [5 empty] | TXV | 9.909%
Antioch | CA | 94509-3644 |  | 2013-10-18 | 2013-10-18 10:07 | 2013-10-18 10:07 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 16.5 | 16.6 | -0.1 | AACDA803A2E74895B0E034F749CEB782 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6848 |  | 2013-07-24 | 2013-07-24 09:26 | 2013-07-24 09:47 | LENNOX - 12ACB30-5P | 101 | 6.9 | Yes | Yes | 20.9 | 20.2 | 0.7 | F5E0B6C787144C10AB1227FAA9591132 | Add refrigerant: 10.9 oz | R22 | TXV |  | 6.832% | 0.93168 | 13.13% | [5 empty] | TXV | 6.832%
Fresno | CA | 93705-4152 |  | 2013-08-23 | 2013-08-23 11:14 | 2013-08-23 11:50 | RHEEM - RRNLB024JK06X | 78 | 3 | Yes | Yes | 19.8 | 19.7 | 0.1 | 1C42202612FC411881D9F41113293150 |  | R410A | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Bakersfield | CA | 93308-5404 |  | 2013-09-04 | 2013-09-04 18:50 | 2013-09-04 18:50 | ICP - PGD3240K001C1 | 72 | 0 | Yes | Yes | 22.1 | 22.1 | 0 | F0F7C145C05B4C9BAE876812A141C210 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2217 |  | 2013-08-30 | 2013-08-30 18:47 | 2013-08-30 18:49 | OTHER - N/A | 85 | -4.8 | Yes | Yes | 25.7 | 21.9 | 3.8 | CEB75B3A92944F77945B161CB9D6F6BD |  | R22 | Non-TXV |  | -5.647% | 1.0565 | 1.581% |  |  |  |  | Non-TXV |  |  | -5.647%
Fresno | CA | 93722-2381 |  | 2013-07-17 | 2013-07-17 09:04 | 2013-07-17 09:04 | LENNOX - 12ACB42-4P | 128 | 0 | Yes | Yes | 25.2 | 19.3 | 5.9 | BF183E955D654B3495509D18944E2DDC |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2972 |  | 2013-08-29 | 2013-08-29 17:26 | 2013-08-29 17:26 | PAYNE - PY3PNA024040MB | 89 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | 7528FC7665804C2091B498C432BA6BA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2972 |  | 2013-08-29 | 2013-08-29 17:13 | 2013-08-29 17:13 | RHEEM - UKN | 60 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | FBA65D787109467380D65AB1C8194525 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2431 |  | 2013-07-25 | 2013-07-25 15:45 | 2013-07-25 20:00 | RUUD - UAMB036JAZ | 93 | 8.5 | Yes | Yes | 19.9 | 22.1 | -2.2 | 84CDED12D2FF4B75A76429CD6AE70E5E |  | R22 | TXV |  | 9.14% | 0.9086 | 17.56% | [5 empty] | TXV | 9.14%
Shafter | CA | 93263-2431 |  | 2013-07-25 | 2013-07-25 15:49 | 2013-07-25 20:28 | YORK - YCJD50541SHA | 62 | 2.3 | Yes | Yes | 19.7 | 22.1 | -2.4 | 0344E9D28DFA4833B04016C0E85E253C |  | R410A | Non-TXV |  | 3.71% | 0.9629 | 7.129% | [5 empty] | Non-TXV | 3.71%
San Jose | CA | 95148-3000 |  | 2013-10-12 | 2013-10-12 14:04 | 2013-10-12 14:41 | CARRIER - 38CK048320 | 94 | -6.6 | Yes | Yes | 23.9 | 20.3 | 3.6 | 19AB2C535B78463DA4485931D6D03B21 |  | R22 | Non-TXV |  | -7.021% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.021%
San Jose | CA | 95148-3000 |  | 2013-10-12 | 2013-10-12 14:43 | 2013-10-12 15:18 | CARRIER - 38CK036300 | 80 | -7.5 | Yes | Yes | 20.4 | 18.8 | 1.6 | 84C6FE77BC6944FFA3DECBF9FAF62816 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Fresno | CA | 93728-1534 |  | 2013-08-02 | 2013-08-02 11:09 | 2013-08-02 11:27 | - NRGF36DKB04867.815185 | 90 | 2.8 | Yes | Yes | 19.1 | 18.7 | 0.4 | E7D262CC2A2E49198798809A7AA45EB4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Reedley | CA | 93654-7043 |  | 2013-07-31 | 2013-07-31 09:07 | 2013-07-31 09:28 | GOODMAN - GSC130361FA | 83 | 2.9 | Yes | Yes | 18.2 | 17.5 | 0.7 | FF57A16FC2ED44DE8D537CBF9350FFC6 |  | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
Fresno | CA | 93720-1933 |  | 2013-10-08 | 2013-10-08 13:49 | 2013-10-08 14:35 | CARRIER - UKN | 80 | 3.4 | Yes | Yes | 22.1 | 19.9 | 2.2 | 01735CDF2A1846BDB2F50AF5E41A45E6 |  | R22 | Non-TXV |  | 4.25% | 0.9575 | 8.168% | [5 empty] | Non-TXV | 4.25%
Bakersfield | CA | 93309-1706 |  | 2013-08-01 | 2013-08-01 10:15 | 2013-08-01 10:37 | ICP - PGAD47D1K8 | 214 | 32.1 | Yes | Yes | 19.8 | 21.5 | -1.7 | 20BA004CA89B4FD9993DD19422FBFD60 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Bakersfield | CA | 93308-1122 |  | 2013-07-29 | 2013-07-29 11:38 | 2013-07-29 11:56 | CARRIER - 48GXN048090311 | 131 | 22.5 | Yes | Yes | 21.7 | 21.8 | -0.1 | A385FD05F6294CA791D88D6D75655C58 |  | R22 | Non-TXV |  | 17.18% | 0.82824 | 33.01% | [5 empty] | Non-TXV | 17.18%
Bakersfield | CA | 93307-5360 |  | 2013-07-17 | 2013-07-17 13:12 | 2013-07-17 13:29 | CONCORD - SSG13B2406LP | 104 | 11.3 | Yes | Yes | 19.2 | 20.2 | -1 | 4FD3188C94DA4E41A0135CEEE8E141EC |  | R22 | Non-TXV |  | 10.87% | 0.89135 | 20.88% | [5 empty] | Non-TXV | 10.87%
Pittsburg | CA | 94565-4227 |  | 2013-07-24 | 2013-07-24 10:56 | 2013-07-24 10:56 | DAY & NIGHT - 561AJ042-A | 88 | 0 | Yes | Yes | 16.3 | 18.9 | -2.6 | F7942D1B31FD40058D51B8D576E49D5F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4940 |  | 2013-07-30 | 2013-07-30 13:31 | 2013-07-30 13:31 | TRANE - YCP030F1M0AC | 106 | 0 | Yes | Yes | 14.1 | 17.1 | -3 | 3764D9FFB755463BAC669026A4851F2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5772 |  | 2013-07-17 | 2013-07-17 09:15 | 2013-07-17 09:33 | HEIL - 234AKA300 | 120 | 13.8 | Yes | Yes | 23.7 | 19.2 | 4.5 | 29662DFE787E4B039FBBBA3C9E648511 | Add refrigerant: 12.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 11.5% | 0.885 | 22.1% | [5 empty] | TXV | 11.5%
Bakersfield | CA | 93308-2169 |  | 2013-08-31 | 2013-08-31 18:02 | 2013-08-31 18:02 | OTHER - CTG024G7A | 60 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 264CE56A7CC54FEBB26DEF6FF4CF9E05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2167 |  | 2013-08-30 | 2013-08-30 17:20 | 2013-08-30 17:20 | OTHER - CTG024G7A | 60 | 0 | Yes | Yes | 22.1 | 21.4 | 0.7 | 0F55490D5D044AB0B46A7AB2BB76496D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Buttonwillow | CA | 93206-9720 |  | 2013-09-16 | 2013-09-16 18:39 | 2013-09-16 18:41 | COMFORT AIRE - PGC036KO60B | 71 | 2.6 | Yes | Yes | 19.7 | 19.3 | 0.4 | F10C124ACF604178A6103A83AD8F8AB1 |  | R22 | Non-TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | Non-TXV | 3.662%
Fresno | CA | 93726-1538 |  | 2013-07-23 | 2013-07-23 09:37 | 2013-07-23 09:58 | RHEEM - RRNAA036JK06K | 114 | 5.4 | Yes | Yes | 18.8 | 18.2 | 0.6 | 0281425B695F48708CFC980841F6CD48 |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Suisun City | CA | 94585-1839 |  | 2013-08-01 | 2013-08-01 13:07 | 2013-08-01 13:07 | AMANA - APG153709041AX | 112 | 0 | Yes | Yes | 16.9 | 19.5 | -2.6 | B8FFC4EE6E204579BFBA1BD377369BAC |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93723-8130 |  | 2013-07-31 | 2013-07-31 15:30 | 2013-07-31 15:30 | OTHER - UKN | 81 | 0 | Yes | Yes | 35.5 | 20.4 | 15.1 | 9AFED247350346B384908876E647EAD2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-4149 |  | 2013-07-31 | 2013-07-31 11:17 | 2013-07-31 12:07 | RHEEM - RCGA36AZAS17 | 80 | 5.5 | Yes | Yes | 17.8 | 20.7 | -2.9 | F21AE60ED87542A8B0698EBF889D8DFF |  | R22 | TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | TXV | 6.875%
Bakersfield | CA | 93308-1022 |  | 2013-07-26 | 2013-07-26 17:04 | 2013-07-26 17:04 | BRYANT - 1799E01161 | 108 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 5E333454FF5944F6932B6D30BFB78E0A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2181 |  | 2013-08-30 | 2013-08-30 14:54 | 2013-08-30 15:13 | ICP - PGAB24B1K1 | 80 | 12.7 | Yes | Yes | 21.7 | 21.5 | 0.2 | 0FD27835595E4258B4DF9C9E028DE7DE |  | R22 | Non-TXV |  | 15.88% | 0.84125 | 30.51% | [5 empty] | Non-TXV | 15.88%
Fairfield | CA | 94534-3420 |  | 2013-07-30 | 2013-07-30 10:37 | 2013-07-30 16:11 | TRANE - 2TTB0036A1000AA | 76 | 2.3 | Yes | Yes | 13.5 | 16.5 | -3 | 05CA53DE9EDC43B5BD39A6B3FF2DEEB5 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Clovis | CA | 93611-7375 |  | 2013-08-22 | 2013-08-22 11:02 | 2013-08-22 11:38 | ARCOAIRE - PGF036K060E | 70 | 4.1 | Yes | Yes | 21.8 | 21 | 0.8 | 564570FB2BE74530B9AA5DCDC6B9C9EA |  | R22 | Non-TXV |  | 5.857% | 0.94143 | 11.26% | [5 empty] | Non-TXV | 5.857%
Bakersfield | CA | 93308-2963 |  | 2013-08-29 | 2013-08-29 18:19 | 2013-08-29 18:36 | ICP - PGC030K060A | 52 | 8 | Yes | Yes | 21.8 | 21.5 | 0.3 | 2977EB9EC8634F1C845A03C44727B962 |  | R22 | Non-TXV |  | 15.38% | 0.84615 | 29.57% | [5 empty] | Non-TXV | 15.38%
San Jose | CA | 95135-1308 |  | 2013-08-08 | 2013-08-08 11:36 | 2013-08-08 12:01 | CARRIER - 38CKC024===341 | 55 | 5.1 | Yes | Yes | 15.3 | 17.1 | -1.8 | EC6DEA59B48F4689B3E2D7EA4562EA13 |  | R22 | TXV |  | 9.273% | 0.90727 | 17.82% | [5 empty] | TXV | 9.273%
Clovis | CA | 93611-4515 |  | 2013-07-30 | 2013-07-30 10:22 | 2013-07-30 11:04 | OTHER - 585A036080YAC | 60 | 4 | Yes | Yes | 26 | 20.1 | 6 | 25B77F71F0EB4ADCBC5CB8046288FE8E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Reedley | CA | 93654-3117 |  | 2013-07-18 | 2013-07-18 10:28 | 2013-07-18 10:56 | TEMPSTAR - PGAD30D1K7 | 78 | 8.1 | Yes | Yes | 21.2 | 19.6 | 1.6 | B78D59AA765B43399026DF413F379410 |  | R22 | Non-TXV |  | 10.38% | 0.89615 | 19.96% | [5 empty] | Non-TXV | 10.38%
Fresno | CA | 93726-3526 |  | 2013-09-05 | 2013-09-05 10:34 | 2013-09-05 10:52 | AMERICAN STANDARD - YCC024F1L0BJ | 56 | 3.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | E056C6FED89D4B869F20894193AA5043 |  | R22 | Non-TXV |  | 6.071% | 0.93929 | 11.67% | [5 empty] | Non-TXV | 6.071%
Shafter | CA | 93263-2322 |  | 2013-07-24 | 2013-07-24 19:50 | 2013-07-24 20:14 | GOODMAN - GG13300451AB | 77 | 3.7 | Yes | Yes | 18.8 | 21.8 | -3 | 66E48B4CE1BD4740BA6462878590AB60 |  | R22 | Non-TXV |  | 4.805% | 0.95195 | 9.235% | [5 empty] | Non-TXV | 4.805%
Shafter | CA | 93263-2322 |  | 2013-07-24 | 2013-07-24 19:58 | 2013-07-24 20:22 | GOODMAN - GPG103007C1A | 50 | 2.4 | Yes | Yes | 25.1 | 20.4 | 4.7 | 328BDC689E464D4EB5A4620855C28FEB |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Fresno | CA | 93711-2666 |  | 2013-09-07 | 2013-09-07 10:21 | 2013-09-07 10:38 | OTHER - UNK | 80 | 2.6 | Yes | Yes | 18.3 | 19.6 | -1.3 | 5E1184FC175F41ECB324DD60A62DB9F5 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Bakersfield | CA | 93309-5904 |  | 2013-08-20 | 2013-08-20 17:30 | 2013-08-20 17:30 | OTHER - UKN | 90 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | 0F9602DF9F564431BA4CE9D5F92DCBB4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2523 |  | 2013-11-07 | 2013-11-07 13:02 | 2013-11-07 13:28 | BRYANT - 561CJ018-D | 52 | 1.5 | Yes | Yes | 17.2 | 19.1 | -1.9 | B775F08F821D44D19FC0975B51F9B38C |  | R22 | Non-TXV |  | 2.885% | 0.97115 | 5.544% | [5 empty] | Non-TXV | 2.885%
Fresno | CA | 93726-3525 |  | 2013-09-05 | 2013-09-05 10:21 | 2013-09-05 10:53 | YORK - D2NP024N05606A | 100 | 3.6 | Yes | Yes | 20.8 | 18.7 | 2.1 | 0B144CE5C4FF4119B6AF8A99353AE871 |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Selma | CA | 93662-9693 |  | 2013-08-01 | 2013-08-01 15:36 | 2013-08-01 17:03 | OTHER - 24ECW060GA | 84 | 7.7 | Yes | Yes | 23.9 | 22.7 | 1.2 | 60C68FCBA75741268F27CFC06B7DE286 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Shafter | CA | 93263-2300 |  | 2013-08-12 | 2013-08-12 21:45 | 2013-08-12 21:47 | GOODMAN - PGP13300451AB | 77 | -6.3 | Yes | Yes | 18.3 | 19.4 | -1.1 | 37BBE9473DE74C489A7718F2AA803A1C |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Fairfield | CA | 94533-5027 |  | 2013-09-20 | 2013-09-20 09:57 | 2013-09-20 09:57 | OTHER - 561AJ024-B | 131 | 0 | Yes | Yes | 22.3 | 17.4 | 4.9 | 81440A92226D4107B943561C9E188C50 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2518 |  | 2013-09-04 | 2013-09-04 12:59 | 2013-09-04 13:43 | BRYANT - 561CJ024D | 58 | 6.1 | Yes | Yes | 19 | 19 | 0 | A3159B14CEDE4765AE3DDC72A9164E96 |  | R22 | Non-TXV |  | 10.52% | 0.89483 | 20.21% | [5 empty] | Non-TXV | 10.52%
Clovis | CA | 93612-2517 |  | 2013-08-09 | 2013-08-09 10:32 | 2013-08-09 10:52 | BRYANT - 561CJ018 | 56 | 19.7 | Yes | Yes | 15.1 | 17.9 | -2.8 | 6B6238CBD06C41BA8FFE184069113DD2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 35.18% | 0.64821 | 67.61% | [5 empty] | Non-TXV | 35.18%
Selma | CA | 93662-9693 |  | 2013-08-01 | 2013-08-01 14:26 | 2013-08-01 15:00 | OTHER - 24ECW060GA | 84 | 8.9 | Yes | Yes | 20.2 | 19.8 | 0.4 | 0844C9417B1044F59ACF440E805F7165 |  | R22 | Non-TXV |  | 10.6% | 0.89405 | 20.36% | [5 empty] | Non-TXV | 10.6%
Shafter | CA | 93263-2214 |  | 2013-07-23 | 2013-07-23 19:15 | 2013-07-23 19:47 | CARRIER - 48GXN0360606301 | 82 | 4.4 | Yes | Yes | 20.7 | 22.8 | -2.1 | 2B99C7554A434BB4877DF7D96719BB75 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.366% | 0.94634 | 10.31% | [5 empty] | Non-TXV | 5.366%
Bakersfield | CA | 93308-3621 |  | 2013-07-29 | 2013-07-29 04:36 | 2013-07-29 04:36 | LENNOX - GCS20H-311-75-3P | 48 | 0 | Yes | Yes | 21.7 | 21 | 0.7 | 5FDFADBEF3ED461EA967D44D59410FF0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1537 |  | 2013-07-29 | 2013-07-29 15:31 | 2013-07-29 15:56 | OTHER - TA036H1D | 101 | 11.2 | Yes | Yes | 24.2 | 20.1 | 4.1 | AFA42B8FBEA84DB1B8B287E983B82803 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.09% | 0.88911 | 21.31% | [5 empty] | Non-TXV | 11.09%
Fresno | CA | 93705-0152 |  | 2013-08-27 | 2013-08-27 13:47 | 2013-08-27 14:17 | OTHER - UKN | 71 | 4.3 | Yes | Yes | 23.5 | 21.9 | 1.6 | DE2DF59F7AF947B4A9266FF27A0D3B47 |  | R22 | TXV |  | 6.056% | 0.93944 | 11.64% | [5 empty] | TXV | 6.056%
Fresno | CA | 93710-7006 |  | 2013-07-29 | 2013-07-29 12:25 | 2013-07-29 12:25 | OTHER - TCJ0425433HA | 69 | 0 | Yes | Yes | 19.9 | 19.3 | 0.6 | 9CA63C5F4DB1413D87F1BEA51ECC36EA |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3234 |  | 2013-07-22 | 2013-07-22 15:09 | 2013-07-22 15:09 | DAY & NIGHT - 587AN2036080 | 70 | 0 | Yes | Yes | 35 | 21 | 14 | 3C206025E4F84C0F95933AB4625E36D9 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-2615 |  | 2013-09-25 | 2013-09-25 14:53 | 2013-09-25 14:57 | TRANE - TTR036C1000 | 92 | 3.5 | Yes | Yes | 18.4 | 20.9 | -2.5 | 5E8A76CC8BAD47408CAD31FE65FF4D93 |  | R22 | Non-TXV |  | 3.804% | 0.96196 | 7.311% | [5 empty] | Non-TXV | 3.804%
Bakersfield | CA | 93308-2961 |  | 2013-08-29 | 2013-08-29 17:49 | 2013-08-29 17:49 | ICP - PGC024K06A | 58 | 0 | Yes | Yes | 21.5 | 19.7 | 1.8 | 0CDCD748E2AA4C889D8A04F6308509C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-2585 |  | 2013-09-23 | 2013-09-23 11:48 | 2013-09-23 11:48 | - CK36-1A | 73 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | DCE593738AE14663843264B0273EFD98 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2991 |  | 2013-08-30 | 2013-08-30 17:30 | 2013-08-30 17:30 | LUXAIRE - 18ECW045GA | 71 | 0 | Yes | Yes | 21.3 | 20.5 | 0.8 | 9F3F7137FAB64A1DB344325D07A84D66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2006 |  | 2013-07-29 | 2013-07-29 14:03 | 2013-07-29 14:31 | HEIL - NRGF36DCR02 | 90 | 4.3 | Yes | Yes | 17.1 | 18.8 | -1.7 | 899FC75BA01B4747A5BFE5AAE3223E3F |  | R22 | Non-TXV |  | 4.778% | 0.95222 | 9.182% | [5 empty] | Non-TXV | 4.778%
Fresno | CA | 93727-2604 |  | 2013-07-29 | 2013-07-29 12:45 | 2013-07-29 13:58 | GOODMAN - PGB0361001AREVA | 57 | 3.3 | Yes | Yes | 24.5 | 21.3 | 3.2 | 03C4CA2B07364A70A012A32468E43213 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Clovis | CA | 93619-9533 |  | 2013-07-30 | 2013-07-30 11:32 | 2013-07-30 12:42 | CARRIER - 48NBF030301BB | 85 | 4.4 | Yes | Yes | 20.2 | 20.4 | -0.2 | 7FEB435820134B4FA1386AB506356676 |  | R22 | TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | TXV | 5.176%
Bakersfield | CA | 93312-5183 |  | 2013-07-30 | 2013-07-30 15:56 | 2013-07-30 16:45 | YORK - HIRA042S06A | 84 | 2.5 | Yes | Yes | 22.2 | 22.3 | -0.1 | 19F69B7734EC487BB82515BA65F9CCC0 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Fresno | CA | 93704-6131 |  | 2013-08-26 | 2013-08-26 10:34 | 2013-08-26 16:34 | TRANE - 2TTR1048A1000AA | 109 | 6.9 | Yes | Yes | 21.9 | 21.3 | 0.6 | 088B7FA544974454B72DDDFB7969D189 |  | R22 | TXV |  | 6.33% | 0.9367 | 12.17% | [5 empty] | TXV | 6.33%
Shafter | CA | 93263-2335 |  | 2013-10-24 | 2013-10-24 19:45 | 2013-10-24 19:51 | GOODMAN - GPG1360451AC | 112 | 4.6 | Yes | Yes | 24.7 | 19.5 | 5.2 | B1B06C31A35D4FA0931468288EF9497D |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Bakersfield | CA | 93307-5905 |  | 2013-07-17 | 2013-07-17 14:52 | 2013-07-17 15:32 | BRYANT - 589ANW042080ACBF | 86 | 15.9 | Yes | Yes | 21.1 | 21.4 | -0.2 | AC85662EFC3248EC826DE555787DA530 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.49% | 0.81512 | 35.53% | [5 empty] | Non-TXV | 18.49%
Bakersfield | CA | 93307-5772 |  | 2013-07-31 | 2013-07-31 13:14 | 2013-07-31 14:02 | HEIL - N2A336AKB200 | 85 | 2.5 | Yes | Yes | 15.9 | 18.5 | -2.6 | 0920E6B1412B488BB571989DD6F04AC3 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Reedley | CA | 93654-2406 |  | 2013-07-18 | 2013-07-18 11:35 | 2013-07-18 11:35 | GOODMAN - CKJ601C | 149 | 0 | Yes | Yes | 20.5 | 19 | 1.5 | B9B3D8D4A6B245BEAC98DC534B978542 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-8618 |  | 2013-07-18 | 2013-07-18 09:50 | 2013-07-18 10:12 | AMERICAN STANDARD - WCX060G100AC | 176 | 6.3 | Yes | Yes | 20.1 | 20.2 | -0.1 | FE08191F391B44C2AA6B8889CC25BB95 |  | R22 | Non-TXV |  | 3.58% | 0.9642 | 6.879% | [5 empty] | Non-TXV | 3.58%
Anderson | CA | 96007-8618 |  | 2013-07-18 | 2013-07-18 10:14 | 2013-07-18 13:15 | AMERICAN STANDARD - WCX024G100AB | 118 | 3.5 | Yes | Yes | 20.8 | 19.5 | 1.3 | 40EDF8A9DEA94FE4A89F2A3ED2436C91 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Fresno | CA | 93710-4020 |  | 2013-07-31 | 2013-07-31 10:51 | 2013-07-31 11:43 | OTHER - DAYQF036NO70C | 58 | 4.5 | Yes | Yes | 19.4 | 19.6 | -0.2 | E3952D5307A54DE08EF09E859F37061A |  | R410A | TXV |  | 7.759% | 0.92241 | 14.91% | [5 empty] | TXV | 7.759%
Fresno | CA | 93705-0166 |  | 2013-09-19 | 2013-09-19 16:42 | 2013-09-19 16:42 | AMERICAN STANDARD - UNK | 64 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | B1FC0EAB56054746A430F43B47D80E48 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2916 |  | 2013-07-22 | 2013-07-22 11:32 | 2013-07-22 11:51 | CARRIER - 38BRB036300 | 113 | 16.2 | Yes | Yes | 21.4 | 20.4 | 1 | 73C6340B8A9047BCA76AD6E49BD763CF |  | R22 | Non-TXV |  | 14.34% | 0.85664 | 27.55% | [5 empty] | Non-TXV | 14.34%
Selma | CA | 93662-2468 |  | 2013-10-14 | 2013-10-14 14:24 | 2013-10-14 14:54 | LENNOX - 13ACC03623001 | 115 | 30.1 | Yes | Yes | 21.4 | 20.7 | 0.7 | E4D3728D7C584DF6A28E9BF2EDC1F162 |  | R22 | Non-TXV |  | 26.17% | 0.73826 | 50.3% | [5 empty] | Non-TXV | 26.17%
Suisun City | CA | 94585-2166 |  | 2013-08-01 | 2013-08-01 14:07 | 2013-08-01 15:33 | DAY & NIGHT - 597BN036-A | 146 | 10.6 | Yes | Yes | 20.2 | 19.3 | 0.9 | 46081B49D280462F8CF6182E27EA2D33 |  | R22 | Non-TXV |  | 7.26% | 0.9274 | 13.95% | [5 empty] | Non-TXV | 7.26%
Fresno | CA | 93720-2448 |  | 2013-09-03 | 2013-09-03 10:21 | 2013-09-03 13:01 | TRANE - UKN | 61 | 3 | Yes | Yes | 20 | 19.9 | 0.1 | 9B461F0D78F04F3C9293432B3AC5F68E |  | R22 | TXV |  | 4.918% | 0.95082 | 9.451% | [5 empty] | TXV | 4.918%
Selma | CA | 93662-9693 |  | 2013-08-01 | 2013-08-01 15:03 | 2013-08-01 15:33 | OTHER - 24ECW060GA | 84 | 8.2 | Yes | Yes | 24 | 23.6 | 0.4 | 933C93F238DC41FB8EF1B2C0429DFD29 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.762% | 0.90238 | 18.76% | [5 empty] | Non-TXV | 9.762%
Sunnyvale | CA | 94089-1633 |  | 2013-09-27 | 2013-09-27 15:15 | 2013-09-27 15:34 | PAYNE - PA10JA036-A | 83 | -5.9 | Yes | Yes | 24.9 | 21.5 | 3.4 | 7D120B4347B943EB95CD4789E2811905 |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Fairfield | CA | 94533-5228 |  | 2013-08-13 | 2013-08-13 12:55 | 2013-08-13 13:21 | PAYNE - PA10JA048-A | 100 | 3.2 | Yes | Yes | 15.4 | 14 | 1.5 | 9DDE07BB53894C85BB450141CDB0FA50 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93704-5802 |  | 2013-07-23 | 2013-07-23 10:55 | 2013-07-23 11:12 | GOODMAN - GPG12240701A | 64 | 13.1 | Yes | Yes | 25.5 | 19.6 | 5.9 | 1C7B4DF7F50A47DFAFD1B6D769910982 |  | R22 | Non-TXV |  | 20.47% | 0.79531 | 39.34% | [5 empty] | Non-TXV | 20.47%
Fairfield | CA | 94533-1676 |  | 2013-07-30 | 2013-07-30 09:14 | 2013-07-30 09:14 | RHEEM - RAFD-036JA3 | 80 | 0 | Yes | Yes | 16.6 | 19.3 | -2.7 | D0E6EF65392944DB919E2B48F9C43B24 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3173 |  | 2013-08-27 | 2013-08-27 11:09 | 2013-08-27 11:55 | CARRIER - UKN | 80 | 3.6 | Yes | Yes | 23 | 20.9 | 2.1 | 12AFE515113A4FC7A98D2616392855F0 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Sunnyvale | CA | 94089-1633 |  | 2013-10-03 | 2013-10-03 10:46 | 2013-10-03 13:04 | ARMSTRONG - UNK | 70 | 4.4 | Yes | Yes | 20 | 21 | -1 | 29AE64F1254B47A88329E43AB8182E96 |  | R22 | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Clovis | CA | 93611-5117 |  | 2013-07-30 | 2013-07-30 13:44 | 2013-07-30 14:12 | GOODMAN - PGB0360751A | 60 | 4 | Yes | Yes | 23.4 | 20.4 | 3 | 62A59E4A3AC844D8A8FE6E42BD3788D7 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fairfield | CA | 94533-5012 |  | 2013-07-30 | 2013-07-30 09:49 | 2013-07-30 10:17 | RHEEM - | 85 | 3.5 | Yes | Yes | 15.9 | 18.8 | -2.9 | F4B669702ABD44EFAB83050DAF3255A0 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93309-6022 |  | 2013-08-04 | 2013-08-04 13:34 | 2013-08-04 13:53 | ICP - PGAD36D1K3 | 138 | 20.3 | Yes | Yes | 21.7 | 21.5 | 0.2 | C2ED6BBDA0E143F88A46BB9957BB0A1C |  | R22 | Non-TXV |  | 14.71% | 0.8529 | 28.27% | [5 empty] | Non-TXV | 14.71%
San Jose | CA | 95148-4114 |  | 2013-09-17 | 2013-09-17 10:14 | 2013-09-17 10:38 | CARRIER - 38CKC036 341 | 70 | 6 | Yes | Yes | 19.1 | 20.7 | -1.6 | A8AAF13D6BB94EC0AD9AF3895F8326D3 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Kerman | CA | 93630-1969 |  | 2013-08-07 | 2013-08-07 10:47 | 2013-08-07 12:36 | CARRIER - 48GX048090301 | 116 | 4.5 | Yes | Yes | 24.2 | 18.8 | 5.4 | 01D339C370D34B9D9F333170D12A3BC9 |  | R22 | Non-TXV |  | 3.879% | 0.96121 | 7.455% | [5 empty] | Non-TXV | 3.879%
Fresno | CA | 93701-1211 |  | 2013-09-11 | 2013-09-11 11:16 | 2013-09-11 11:16 | OTHER - UKN | 76 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | E36D93500C9C4DDD82EDFC9C5898D842 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0313 |  | 2013-07-23 | 2013-07-23 09:30 | 2013-07-23 09:48 | YORK - D1NH036N05606C | 108 | 3.5 | Yes | Yes | 16.7 | 19.2 | -2.5 | 5BC320FE0D3744FEBEE4E7BBB70ECD1A |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Sunnyvale | CA | 94089-1633 |  | 2013-09-27 | 2013-09-27 08:07 | 2013-09-27 09:09 | NORDYNE - FS3BC-042KA | 102 | 3.7 | Yes | Yes | 24.1 | 20.1 | 4 | 4709AEADA8774FD6972AC8253B2D73AC |  | R22 | TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | TXV | 3.627%
Fresno | CA | 93727-5247 |  | 2013-08-01 | 2013-08-01 14:08 | 2013-08-01 14:26 | LENNOX - 13ACC048-230-02 | 158 | 5.8 | Yes | Yes | 18.5 | 20.4 | -1.9 | 49D6EBEFC97A43B289D0C1F5FCA502C5 |  | R22 | TXV |  | 3.671% | 0.96329 | 7.055% | [5 empty] | TXV | 3.671%
Clovis | CA | 93612-2516 |  | 2013-08-09 | 2013-08-09 12:09 | 2013-08-09 13:03 | BRYANT - 561CJ024 | 57 | 1.8 | Yes | Yes | 23 | 17.3 | 5.7 | 92B1B82A4DDD4D5E9DCBE14F39D35BEE |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Bakersfield | CA | 93308-2971 |  | 2013-08-29 | 2013-08-29 16:33 | 2013-08-29 16:33 | RHEEM - RRKA-A030JK06E | 54 | 0 | Yes | Yes | 22.3 | 22.4 | -0.1 | 8686FA4645984018AA17D8DD5377B7AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1404 |  | 2013-08-26 | 2013-08-26 16:38 | 2013-08-26 16:54 | OTHER - UKN | 72 | 4.1 | Yes | Yes | 20.4 | 21.1 | -0.7 | 29F2848DAB6B467CBB8EF428178C64FA |  | R22 | TXV |  | 5.694% | 0.94306 | 10.94% | [5 empty] | TXV | 5.694%
Clovis | CA | 93612-2526 |  | 2013-09-04 | 2013-09-04 10:27 | 2013-09-04 10:45 | BRYANT - 561CJX01800ADAA | 55 | 3.4 | Yes | Yes | 20.2 | 19.4 | 0.8 | 71E0705A641E4103BC6F35BEC04CA996 |  | R22 | Non-TXV |  | 6.182% | 0.93818 | 11.88% | [5 empty] | Non-TXV | 6.182%
Fairfield | CA | 94534-1741 |  | 2013-09-13 | 2013-09-13 10:57 | 2013-09-13 10:58 | GE - NA | 66 | 2.4 | Yes | Yes | 19.1 | 17.6 | 1.5 | B681AD40B3C14680BBCC816F113FC270 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Bakersfield | CA | 93307-4718 |  | 2013-10-23 | 2013-10-23 09:45 | 2013-10-23 09:45 | CARRIER - UKN | 85 | 0 | Yes | Yes | 20 | 21 | -1 | 3551E08F824040648357602DB6577962 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2516 |  | 2013-08-09 | 2013-08-09 13:05 | 2013-08-09 13:31 | BRYANT - 561CJO18 | 57 | 2.1 | Yes | Yes | 17.1 | 17.7 | -0.6 | 05BFEA4C8746495E8B60C0B3F44E060E |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Fresno | CA | 93703-3946 |  | 2013-08-31 | 2013-08-31 10:45 | 2013-08-31 11:23 | BDP - 585CJ02450 | 72 | -6.8 | Yes | Yes | 18 | 17.3 | 0.7 | EDBA9BE5100F496EA05C9EA09CC91635 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Clovis | CA | 93612-2527 |  | 2013-08-12 | 2013-08-12 16:53 | 2013-08-12 16:53 | BRYANT - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | EDB62C5ABE1F4217B25BE7FA35631467 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2527 |  | 2013-09-04 | 2013-09-04 09:38 | 2013-09-04 09:38 | BRYANT - 561CJ024D | 58 | 0 | Yes | Yes | 19.1 | 18.8 | 0.3 | E1C0836A2F0D4E6593E0B1D348A3C535 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8006 |  | 2013-09-20 | 2013-09-20 09:26 | 2013-09-20 09:26 | RUUD - UAFD-024JAS | 85 | 0 | Yes | Yes | 22 | 17.2 | 4.8 | EE85445815EA4AFB9E0B309F4D5BC42B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2227 |  | 2013-07-23 | 2013-07-23 19:23 | 2013-07-23 19:23 | - | 85 | 0 | Yes | Yes | 35.5 | 21 | 14.5 | 53848EA66C0C4CFC95F935054DCB861F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-6372 |  | 2013-09-26 | 2013-09-26 14:48 | 2013-09-26 15:47 | RUUD - UAJC-024JAS | 72 | -3.1 | Yes | Yes | 12.7 | 15.3 | -2.6 | 589C94D896AB49D296D72E2578B192A8 |  | R22 | Non-TXV |  | -4.306% | 1.0431 | 1.206% |  |  |  |  | Non-TXV |  |  | -4.306%
Fresno | CA | 93711-2014 |  | 2013-07-18 | 2013-07-18 15:56 | 2013-07-18 16:18 | ARCOAIRE - NAC048AKA4 | 108 | 17.9 | Yes | Yes | 20.6 | 20.4 | 0.2 | 81AA31CCF13D46E3A383BA4C2845E379 |  | R22 | Non-TXV |  | 16.57% | 0.83426 | 31.85% | [5 empty] | Non-TXV | 16.57%
Fresno | CA | 93711-2014 |  | 2013-07-18 | 2013-07-18 16:47 | 2013-07-18 17:08 | OTHER - NCABA24AB0Z8678101233C454A | 42 | 14.8 | Yes | Yes | 2.7 | 20.2 | -17.5 | AB8091212BE24252BF10C0169B2F309D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 35.24% | 0.64762 | 67.72% | [5 empty] | Non-TXV | 35.24%
Woodland | CA | 95776-4939 |  | 2013-07-26 | 2013-07-26 09:54 | 2013-07-26 10:13 | GOODMAN - GSC30241FA | 77 | 6.6 | Yes | Yes | 16.5 | 16.6 | -0.1 | 793B7195C91649DEA81CA1F6E58EFF82 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Fresno | CA | 93702-2529 |  | 2013-08-01 | 2013-08-01 09:51 | 2013-08-01 10:22 | HEIL - UKN | 80 | 4.6 | Yes | Yes | 23.7 | 20.2 | 3.5 | 3084307773534892A6538BE64138C9C1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
San Jose | CA | 95135-1320 |  | 2013-10-19 | 2013-10-19 11:19 | 2013-10-19 12:07 | GE - 21TA924H1H | 42 | 1.3 | Yes | Yes | 22.5 | 19.3 | 3.2 | 0F348A3A721C4AC49C8BC4EFE9191EE9 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Selma | CA | 93662-2468 |  | 2013-07-17 | 2013-07-17 15:40 | 2013-07-17 16:05 | LENNOX - 13ACC03623001 | 115 | 5 | Yes | Yes | 22 | 21 | 1 | 511D0A5C22DC41DA8B10540873D92EA7 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Bakersfield | CA | 93313-4455 |  | 2013-07-19 | 2013-07-19 13:09 | 2013-07-19 13:37 | RUUD - UGPH-10EBRJR | 85 | 4 | Yes | Yes | 20.3 | 19.9 | 0.4 | C3704CD845834BA790ACA0CCFED7D7D8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fresno | CA | 93705-0513 |  | 2013-07-23 | 2013-07-23 08:45 | 2013-07-23 08:45 | LENNOX - 13AGX-042-230-10 | 102 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 630A3217997C4084B88673B0E4C4BEE5 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2644 |  | 2013-07-23 | 2013-07-23 11:35 | 2013-07-23 11:58 | RUUD - UNK | 66 | 4 | Yes | Yes | 25.1 | 20.2 | 4.9 | 8440C3230D5540C6B40FA0410BD7A783 |  | R22 | Non-TXV |  | 6.061% | 0.93939 | 11.65% | [5 empty] | Non-TXV | 6.061%
Pittsburg | CA | 94565-6204 |  | 2013-07-23 | 2013-07-23 12:01 | 2013-07-23 12:04 | RHEEM - NA | 72 | -5.1 | Yes | Yes | 16.4 | 17.6 | -1.2 | 597145862A2B44AF9809DEF751BE75E1 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Sunnyvale | CA | 94089-1633 |  | 2013-10-03 | 2013-10-03 10:19 | 2013-10-03 10:45 | UNITARY PRODUCTS GROUP - ERC0421BBB | 141 | 6.1 | Yes | Yes | 19 | 20.1 | -1.1 | 77112C990DCE4841BB0D72ADE11762FC |  | R22 | Non-TXV |  | 4.326% | 0.95674 | 8.314% | [5 empty] | Non-TXV | 4.326%
San Jose | CA | 95148-1724 |  | 2013-08-08 | 2013-08-08 13:35 | 2013-08-08 13:35 | TRANE - TTRO048100A1 | 81 | 0 | Yes | Yes | 18.1 | 19.8 | -1.7 | EC183D94AE5D45138658FA2176A3BA07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5707 |  | 2013-08-24 | 2013-08-24 10:40 | 2013-08-24 11:24 | AMERICAN STANDARD - YCZ060F1M0BD | 205 | 9.4 | Yes | Yes | 22.4 | 19.2 | 3.2 | 36B02B14836742D18E7CAA8226D0ACE5 |  | R22 | TXV |  | 4.585% | 0.95415 | 8.812% | [5 empty] | TXV | 4.585%
Fairfield | CA | 94533-2069 |  | 2013-08-13 | 2013-08-13 13:40 | 2013-08-13 13:40 | GUARDIAN - GCGD24S41S3A | 61 | 0 | Yes | Yes | 18.2 | 19.7 | -1.5 | 4A64AC42336E44A184D1511FD18DC8E0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1939 |  | 2013-09-30 | 2013-09-30 09:19 | 2013-09-30 09:20 | CARRIER - 38HDL036-311 | 88 | -7.2 | Yes | Yes | 17.6 | 18.2 | -0.6 | FF370AEADC1E4A01B0752E83F6034CE0 |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Fresno | CA | 93711-4059 |  | 2013-09-06 | 2013-09-06 16:18 | 2013-09-06 16:39 | GOODMAN - GSC130301AE | 117 | 28.5 | Yes | Yes | 16.1 | 19.2 | -3.1 | 2557C59E013145F5905AA76D1887B013 |  | R22 | Non-TXV |  | 24.36% | 0.75641 | 46.81% | [5 empty] | Non-TXV | 24.36%
Bakersfield | CA | 93307-5747 |  | 2013-08-05 | 2013-08-05 13:44 | 2013-08-05 14:11 | OTHER - N2A336AKB200 | 85 | 2.8 | Yes | Yes | 17.5 | 20.4 | -2.9 | 4B67FC85FE0F42969B27AE391C5FBE74 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Ukiah | CA | 95482-9414 |  | 2013-08-24 | 2013-08-24 11:05 | 2013-08-24 11:31 | COLEMAN - ILLEGIBLE | 71 | 5.4 | Yes | Yes | 24.9 | 20.2 | 4.8 | 0AD4EB2D7E4B4035969CE0BCA96B4BA9 |  | R22 | Non-TXV |  | 7.606% | 0.92394 | 14.62% | [5 empty] | Non-TXV | 7.606%
San Jose | CA | 95148-1621 |  | 2013-08-08 | 2013-08-08 14:13 | 2013-08-08 14:13 | GMC - CK42199 | 85 | 0 | Yes | Yes | 16.4 | 18.6 | -2.2 | 936021167D0F49B192CDE2E47E634C9F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-1118 |  | 2013-10-12 | 2013-10-12 09:48 | 2013-10-12 10:11 | TRANE - BTR736E100A0 | 114 | -10.7 | Yes | Yes | 24.6 | 20.9 | 3.7 | 4DFDBFEB705A4FDFBB582D16B4AB8278 |  | R22 | Non-TXV |  | -9.386% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.386%
Antioch | CA | 94509-5182 |  | 2013-07-24 | 2013-07-24 10:12 | 2013-07-24 10:47 | HEIL - CA5530VKD2 | 74 | -4.4 | Yes | Yes | 18.8 | 21.3 | -2.5 | 0327DDBF6EA44ED09C4EDF6EB851AE8D |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Fresno | CA | 93705-0411 |  | 2013-07-19 | 2013-07-19 17:26 | 2013-07-19 17:59 | CARRIER - 38TDA060300 | 190 | 20.8 | Yes | Yes | 22.1 | 19.2 | 2.9 | CD4EA94A36E04A88A0B3DB718CE829F0 |  | R22 | Non-TXV |  | 10.95% | 0.89053 | 21.04% | [5 empty] | Non-TXV | 10.95%
Pittsburg | CA | 94565-3663 |  | 2013-07-23 | 2013-07-23 10:42 | 2013-07-23 10:44 | GOODMAN - CK36-1A | 77 | 5.5 | Yes | Yes | 18 | 17.6 | 0.4 | DB81B4C267CE45D5BDA1AC6ECE4103CB |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Fresno | CA | 93711-4049 |  | 2013-09-06 | 2013-09-06 09:43 | 2013-09-06 10:36 | RHEEM - UNK | 66 | -3.9 | Yes | Yes | 20.1 | 18.6 | 1.5 | 873C141248D14AB09C8EAAC554EDCAF3 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Bakersfield | CA | 93307-2031 |  | 2013-07-17 | 2013-07-17 18:14 | 2013-07-17 18:56 | PAYNE - PY1PNB0360AAAA | 56 | 4.2 | Yes | Yes | 22.3 | 21.5 | 0.8 | ACEA35B99A94406CA5972804032DE305 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Vallejo | CA | 94591-7657 |  | 2013-08-02 | 2013-08-02 10:33 | 2013-08-02 10:33 | AMERICAN STANDARD - 2A7A02036A1000AA | 97 | 0 | Yes | Yes | 16.1 | 19.1 | -3 | ECFCC2E9F8034E93A41DFC7F0D7BD68B |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1620 |  | 2013-08-02 | 2013-08-02 12:07 | 2013-08-02 12:30 | TRANE - 2TTB3036A1000AA | 102 | 4.9 | Yes | Yes | 17.3 | 17.6 | -0.3 | D5F3E9CF3B1244A090BB9A9110663463 |  | R22 | Non-TXV |  | 4.804% | 0.95196 | 9.232% | [5 empty] | Non-TXV | 4.804%
Bakersfield | CA | 93308-2961 |  | 2013-08-29 | 2013-08-29 16:50 | 2013-08-29 16:50 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20 | 19.8 | 0.2 | 8B648CF38CCA47B5B3E6D4A179444A10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4533 |  | 2013-09-19 | 2013-09-19 14:51 | 2013-09-19 16:32 | PAYNE - PA13NA036-E | 73 | 3.7 | Yes | Yes | 15.1 | 17.7 | -2.6 | 96AFE68CF70348FE83E6D96582843859 |  | R22 | Non-TXV |  | 5.068% | 0.94932 | 9.741% | [5 empty] | Non-TXV | 5.068%
Fresno | CA | 93711-2680 |  | 2013-09-07 | 2013-09-07 11:30 | 2013-09-07 11:30 | GOODMAN - GSC130301DA | 87 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 7C0C389C2BA94B54A19C3783C22E7A4B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9503 |  | 2013-09-19 | 2013-09-19 16:36 | 2013-09-19 16:53 | ICP - PGC024K060A | 58 | 5.5 | Yes | Yes | 22.3 | 22 | 0.3 | AB9BA4BEE72C41BEACD8594A608142AF |  | R22 | Non-TXV |  | 9.483% | 0.90517 | 18.22% | [5 empty] | Non-TXV | 9.483%
Dixon | CA | 95620-2534 |  | 2013-08-16 | 2013-08-16 13:30 | 2013-08-16 16:11 | CARRIER - 38CKB048300 | 102 | 3.1 | Yes | Yes | 15.3 | 18 | -2.7 | 86C7C4B6E41C4630B939E30109E1F56F |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Fresno | CA | 93710-7207 |  | 2013-07-24 | 2013-07-24 13:36 | 2013-07-24 13:59 | TRANE - YCC024F1L0BC | 64 | 4.2 | Yes | Yes | 21 | 19.8 | 1.2 | 780110C9629640BDB8BCE68461EF8DC9 |  | R22 | Non-TXV |  | 6.562% | 0.93437 | 12.61% | [5 empty] | Non-TXV | 6.562%
San Jose | CA | 95148-2639 |  | 2013-09-17 | 2013-09-17 12:59 | 2013-09-17 13:41 | RUUD - UNK | 84 | -4.9 | Yes | Yes | 20 | 20.2 | -0.2 | B776773FCF6147C3921EF05B5F30DE30 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
San Jose | CA | 95127-4213 |  | 2013-09-24 | 2013-09-24 09:21 | 2013-09-24 09:21 | RHEEM - UNK | 80 | 0 | Yes | Yes | 9.4 | 18.9 | -9.5 | 1848F6EB10D84626B49FA267E1C76351 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9504 |  | 2013-09-19 | 2013-09-19 14:52 | 2013-09-19 14:52 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 54CA30253E1D4A61BCC80A1D323EEE7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8821 |  | 2013-07-31 | 2013-07-31 14:11 | 2013-07-31 14:56 | YORK - D1NP030N05606A | 73 | 3.5 | Yes | Yes | 18.8 | 17.9 | 0.9 | BC01A474623E44DEB09823CD59D6D5AD |  | R22 | Non-TXV |  | 4.795% | 0.95205 | 9.214% | [5 empty] | Non-TXV | 4.795%
Bakersfield | CA | 93305-2431 |  | 2013-07-23 | 2013-07-23 08:41 | 2013-07-23 10:22 | PAYNE - PY1PNB042060AAAA | 100 | 5.6 | Yes | Yes | 21.6 | 20.3 | 1.3 | 17D621AFB7E44C808421A795581A3877 |  | R22 | Non-TXV |  | 5.6% | 0.944 | 10.76% | [5 empty] | Non-TXV | 5.6%
Vacaville | CA | 95687-5822 |  | 2013-08-01 | 2013-08-01 10:22 | 2013-08-01 10:47 | GOODMAN - CLT36-1B | 140 | -4.2 | Yes | Yes | 15.2 | 17.7 | -2.5 | DFBA5AB891AB41CCAC92DE13A8B648F1 |  | R22 | Non-TXV |  | -3% | 1.03 | 0.8401% |  |  |  |  | Non-TXV |  |  | -3%
Bakersfield | CA | 93308-9511 |  | 2013-09-19 | 2013-09-19 12:33 | 2013-09-19 12:33 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 22.1 | 22.1 | 0 | 4687932937CA4BF18294E0077479E035 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-2417 |  | 2013-08-07 | 2013-08-07 11:37 | 2013-08-07 11:37 | YORK - H2RA036S06D | 58 | 0 | Yes | Yes | 17.8 | 18.7 | -0.9 | C2463347A58D4C598D15B8694C822028 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94089-1633 |  | 2013-09-27 | 2013-09-27 12:36 | 2013-09-27 13:06 | COLEMAN - BRCQ04231BB | 68 | -4 | Yes | Yes | 24.4 | 20.3 | 4.1 | 7D79F000AB0848BF8E3A0B3C6105F9EE |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93308-9504 |  | 2013-09-19 | 2013-09-19 15:45 | 2013-09-19 15:45 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.8 | 22.1 | -0.3 | 82F4F94B81154133A030A26965FCAF7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5302 |  | 2013-08-02 | 2013-08-02 11:27 | 2013-08-02 11:27 | BDP - 585B024050YACR | 51 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 5F3C1C03934E4CA8BE09FD04DF9273B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5402 |  | 2013-07-24 | 2013-07-24 13:51 | 2013-07-24 15:27 | GOODMAN - GPG1336045M41AC | 85 | 3.8 | Yes | Yes | 20.3 | 20.6 | -0.3 | 217D282E6E3F480BB10C4C15BDEA0C1B |  | R410A | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Bakersfield | CA | 93308-9504 |  | 2013-09-19 | 2013-09-19 15:15 | 2013-09-19 15:15 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 75D7CC13A12A4883A6BA82E11BD49838 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3140 |  | 2013-08-08 | 2013-08-08 22:05 | 2013-08-08 22:11 | OTHER - HBB-F048SB | 134 | 5.4 | Yes | Yes | 27.1 | 21.8 | 5.3 | 6C5CB05AF025489D94959AEFE905ADC4 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 4.03% | 0.9597 | 7.744% | [5 empty] | TXV | 4.03%
Bakersfield | CA | 93313-5102 |  | 2013-07-22 | 2013-07-22 10:45 | 2013-07-22 11:21 | RHEEM - RRGG07N435KR | 109 | -5 | Yes | Yes | 24.3 | 20.4 | 3.9 | A65C9E58B90E468DA628BB1664E97FE6 |  | R22 | TXV |  | -4.587% | 1.0459 | 1.285% |  |  |  |  | TXV |  |  | -4.587%
Bakersfield | CA | 93306-4332 |  | 2013-07-18 | 2013-07-18 09:30 | 2013-07-18 10:06 | CARRIER - N4A34AKA300 | 92 | 5.8 | Yes | Yes | 21.7 | 20.7 | 1.1 | C4152E7744EA4C99A1053B8F55A04D92 |  | R410A | TXV |  | 6.304% | 0.93696 | 12.12% | [5 empty] | TXV | 6.304%
Winters | CA | 95694-2103 |  | 2013-08-16 | 2013-08-16 12:00 | 2013-08-16 15:57 | RHEEM - | 85 | 2.8 | Yes | Yes | 13.4 | 16.1 | -2.7 | EC9926A4A1DA4E949243646DDF8F7BA1 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Bakersfield | CA | 93309-5118 |  | 2013-08-02 | 2013-08-02 08:53 | 2013-08-02 09:24 | RHEEM - RRNL-B042JK08X | 112 | 13.4 | Yes | Yes | 21.8 | 21.8 | 0 | 32FFB99BB25645DFA30F3AF36CC2E811 |  | R410A | Non-TXV |  | 11.96% | 0.88036 | 22.99% | [5 empty] | Non-TXV | 11.96%
Hayward | CA | 94544-6432 |  | 2013-07-31 | 2013-07-31 10:45 | 2013-07-31 10:45 | TRANE - 2TTR024A1000AA | 95 | 0 | Yes | Yes | 22.7 | 18.1 | 4.6 | B97B485550FA4008A97C5BB76AA90424 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5922 |  | 2013-08-09 | 2013-08-09 10:29 | 2013-08-09 10:49 | YORK - D1NH0660N09006C | 140 | 6.8 | Yes | Yes | 17.7 | 20.4 | -2.7 | 0A735EBB2B8840A8939A3E32AFF294D3 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Bakersfield | CA | 93306-2337 |  | 2013-07-22 | 2013-07-22 19:13 | 2013-07-22 19:32 | ARCOAIRE - | 85 | 3.9 | Yes | Yes | 19.8 | 22.5 | -2.7 | D3AD1C406F944091854AAEA2EC430979 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Vacaville | CA | 95688-3630 |  | 2013-08-01 | 2013-08-01 12:58 | 2013-08-01 15:27 | CARRIER - 48KH024300BE | 58 | 2.6 | Yes | Yes | 14.5 | 16.5 | -2 | A9639AA053A947ADBD51DBDE52103841 |  | R22 | Non-TXV |  | 4.483% | 0.48 | 99.93% | [5 empty] | Non-TXV | 4.483%
Pittsburg | CA | 94565-4445 |  | 2013-09-20 | 2013-09-20 11:43 | 2013-09-20 15:41 | CARRIER - 38CKC030340 | 68 | 3.2 | Yes | Yes | 14.2 | 15.2 | -1 | CED1D95EB8814945B28A9DCE677D3D68 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
San Jose | CA | 95148-3431 |  | 2013-09-17 | 2013-09-17 13:43 | 2013-09-17 14:03 | GOODMAN - CK36 1A | 156 | -9.2 | Yes | Yes | 22.6 | 20.4 | 2.2 | 1842FDE0D5454653B812BA9F0D59214F |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Bakersfield | CA | 93308-9505 |  | 2013-08-29 | 2013-08-29 18:43 | 2013-08-29 18:43 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.4 | 21.4 | -1 | 570F8FED4808451D84EE1970FF3828F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-4914 |  | 2013-10-16 | 2013-10-16 08:14 | 2013-10-16 08:41 | CARRIER - 3HDL036-311 | 88 | -8.3 | Yes | Yes | 20.3 | 20.4 | -0.1 | 300F15C7FCAA4E498F837639BEE7632A |  | R22 | Non-TXV |  | -9.432% | 1.0943 | 2.641% |  |  |  |  | Non-TXV |  |  | -9.432%
Bakersfield | CA | 93308-9502 |  | 2013-09-19 | 2013-09-19 12:26 | 2013-09-19 12:26 | ICP - PGC024K040A | 58 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | 8EC0602A7C28426187E932E1BC0D5D13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-7134 |  | 2013-10-15 | 2013-10-15 10:22 | 2013-10-15 10:23 | YORK - H1RA018S06D | 54 | -3.8 | Yes | Yes | 16.8 | 17 | -0.2 | 1A52AB4B79AC4BACBCC0506B94186FC7 |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
San Jose | CA | 95148-2844 |  | 2013-10-12 | 2013-10-12 11:30 | 2013-10-12 13:46 | TRANE - 4TTX6048B1000BA | 120 | -9.5 | Yes | Yes | 23.6 | 19.5 | 4.1 | DD2E8A7F334440BC9554580073121F25 |  | R410A | TXV |  | -7.917% | 1.0792 | 2.217% |  |  |  |  | TXV |  |  | -7.917%
Pittsburg | CA | 94565-4618 |  | 2013-07-23 | 2013-07-23 11:17 | 2013-07-23 11:18 | HEIL - CA5536VKD2 | 82 | -5.8 | Yes | Yes | 17.8 | 15.5 | 2.3 | 1A24F00D4BC24F45A476598ABDA99387 |  | R22 | Non-TXV |  | -7.073% | 1.0707 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.073%
Bakersfield | CA | 93305-4027 |  | 2013-07-25 | 2013-07-25 15:41 | 2013-07-25 16:19 | GOODMAN - GPG1336045M41DA | 70 | 2.9 | Yes | Yes | 28.4 | 22.7 | 5.7 | 3EB81351A9F94DEBB4659D5D8E5F6D25 |  | R410A | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Bakersfield | CA | 93308-9502 |  | 2013-09-19 | 2013-09-19 13:19 | 2013-09-19 13:19 | ICP - PGC024K040A | 58 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | D06A165893CD47479D5E8150211C5E71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4810 |  | 2013-07-18 | 2013-07-18 14:40 | 2013-07-18 15:05 | YORK - D1NH036N05606C | 108 | 5.4 | Yes | Yes | 23.4 | 20.4 | 3 | 4CECE1A4770145A2A5C3972B0FB44EFC |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Shafter | CA | 93263-1909 |  | 2013-07-23 | 2013-07-23 18:38 | 2013-07-23 18:57 | GOODMAN - GPG13336045M41AB | 85 | 2.5 | Yes | Yes | 18 | 18.2 | -0.2 | 98CB64C920B745F48A1828286E97DDE6 |  | R410A | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93306-7712 |  | 2013-07-18 | 2013-07-18 15:30 | 2013-07-18 16:00 | YORK - D1NHO42N060506C | 95 | 7.7 | Yes | Yes | 21.3 | 22.2 | -0.9 | 5BD960267BC64F5BB3A90C99EB75A373 |  | R22 | Non-TXV |  | 8.105% | 0.91895 | 15.58% | [5 empty] | Non-TXV | 8.105%
Bakersfield | CA | 93307-2887 |  | 2013-07-17 | 2013-07-17 12:40 | 2013-07-17 14:53 | RUUD - RRNA-B036JK06X | 83 | 3.8 | Yes | Yes | 18 | 18.7 | -0.7 | 3EF8C53C67394120A5CF3600BA6B9262 |  | R22 | Non-TXV |  | 4.578% | 0.95422 | 8.799% | [5 empty] | Non-TXV | 4.578%
Arvin | CA | 93203-1706 |  | 2013-07-22 | 2013-07-22 13:56 | 2013-07-22 14:20 | BRYANT - 574ANW060090NA | 186 | 49 | Yes | Yes | 22.5 | 22.5 | 0 | 9A4F89A668F04E4A8F28963C138888AF |  | R22 | Non-TXV |  | 26.34% | 0.73656 | 50.63% | [5 empty] | Non-TXV | 26.34%
Antioch | CA | 94531-7118 |  | 2013-07-24 | 2013-07-24 12:56 | 2013-07-24 13:17 | YORK - UKN | 85 | 2.7 | Yes | Yes | 21.6 | 21.3 | 0.3 | AC414E81277D498CBA6E5D6B49BC0845 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Antioch | CA | 94531-8125 |  | 2013-08-05 | 2013-08-05 09:19 | 2013-08-05 10:05 | CARRIER - 38EH060330 | 225 | 19 | Yes | Yes | 19.9 | 19.9 | 0 | F9C720BD988B456B9DDE4A03241736B0 |  | R22 | Non-TXV |  | 8.444% | 0.91556 | 16.23% | [5 empty] | Non-TXV | 8.444%
Bakersfield | CA | 93308-9501 |  | 2013-09-19 | 2013-09-19 11:12 | 2013-09-19 11:12 | ICP - PGC024K040A | 58 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | 5CF5CA256757435EAC6BD1BE6AC5ED33 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8598 |  | 2013-07-24 | 2013-07-24 13:40 | 2013-07-24 14:04 | CARRIER - 38CKC042----341 | 80 | -3 | Yes | Yes | 22.8 | 21 | 1.8 | 0B0EF66C08F04C6F8A48EAF4D8135260 |  | R22 | TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | TXV |  |  | -3.75%
Bakersfield | CA | 93308-9511 |  | 2013-09-19 | 2013-09-19 12:07 | 2013-09-19 12:07 | BRYANT - 582ANW0240NAAD | 53 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 9819EAB9D6CC4EA297A042D86688251D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8193 |  | 2013-07-29 | 2013-07-29 09:59 | 2013-07-29 09:59 | PAYNE - PA13NR042-H | 113 | 0 | Yes | Yes | 17.3 | 17 | 0.3 | D216F025CABB4F068A4B418DA26074A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-1955 |  | 2013-08-02 | 2013-08-02 12:27 | 2013-08-02 12:46 | RUUD - URKAA030JK06E | 54 | 3.5 | Yes | Yes | 23.6 | 21 | 2.6 | 4616681929624BC5B6DC93AB82E3D960 |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Bakersfield | CA | 93309-5009 |  | 2013-08-21 | 2013-08-21 11:21 | 2013-08-21 11:36 | CARRIER - 48N042060301 | 170 | 21.4 | Yes | Yes | 21.7 | 21.8 | -0.1 | 70C9A55B1D2547DF8563B8153F1A77FB |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Bakersfield | CA | 93308-2971 |  | 2013-08-29 | 2013-08-29 16:47 | 2013-08-29 16:47 | TRANE - 4YCC3024B1014AA | 93 | 0 | Yes | Yes | 22 | 21.8 | 0.2 | EC5B901E0BC84B6899AE1FE4E9470ED7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2740 |  | 2013-07-29 | 2013-07-29 12:29 | 2013-07-29 13:07 | CONCORD - RPG10B36D075LA8A | 58 | -5.5 | Yes | Yes | 20.3 | 14.4 | 5.9 | 90E65D2A198845EDA5D2EC149919326A |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Antioch | CA | 94509-2941 |  | 2013-07-29 | 2013-07-29 10:39 | 2013-07-29 10:39 | CARRIER - 38YCC018300 | 70 | 0 | Yes | Yes | 17.3 | 17.6 | -0.3 | 7E469AB798074292B1FD74779E71BDD3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2965 |  | 2013-08-30 | 2013-08-30 14:53 | 2013-08-30 15:09 | LUXAIRE - 1E018PCAON | 71 | 10.4 | Yes | Yes | 21 | 20.2 | 0.8 | 3ED930F0DE854AF8B10B7CBDF2980AB4 |  | R22 | Non-TXV |  | 14.65% | 0.85352 | 28.15% | [5 empty] | Non-TXV | 14.65%
Pittsburg | CA | 94565-2282 |  | 2013-07-29 | 2013-07-29 11:05 | 2013-07-29 11:07 | CARRIER - 38BRC036350 | 108 | -7.6 | Yes | Yes | 18 | 17.6 | 0.4 | C5DA21F9C2024ADE887187B5BC8F8EE0 |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Bakersfield | CA | 93308-2185 |  | 2013-09-03 | 2013-09-03 18:30 | 2013-09-03 18:30 | BRYANT - 582ANW024040AAAD | 53 | 0 | Yes | Yes | 19.7 | 20.1 | -0.4 | F979C6B5FA2A45148A7122B043FFCCD6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1911 |  | 2013-07-23 | 2013-07-23 19:24 | 2013-07-23 19:45 | GOODMAN - GPG13480701AB | 145 | 12.6 | Yes | Yes | 21.8 | 19.9 | 1.9 | 303B728E43AA45F5ADFB8C76BC871801 |  | R22 | Non-TXV |  | 8.69% | 0.9131 | 16.7% | [5 empty] | Non-TXV | 8.69%
San Jose | CA | 95116-2972 |  | 2013-10-15 | 2013-10-15 12:38 | 2013-10-15 13:15 | BRYANT - UNK | 83 | 4.9 | Yes | Yes | 18.3 | 19.9 | -1.6 | 93E7BD886905493B933E38022572056B |  | R22 | Non-TXV |  | 5.904% | 0.94096 | 11.35% | [5 empty] | Non-TXV | 5.904%
Fresno | CA | 93725-1419 |  | 2013-08-26 | 2013-08-26 17:01 | 2013-08-26 18:30 | RUUD - UNK | 70 | 4.8 | Yes | Yes | 27.3 | 23 | 4.3 | 4E4BAF49D16F42AEB3128B606B9D9EAB |  | R22 | Non-TXV |  | 6.857% | 0.93143 | 13.18% | [5 empty] | Non-TXV | 6.857%
Shafter | CA | 93263-2329 |  | 2013-07-24 | 2013-07-24 19:44 | 2013-07-24 20:03 | DAY & NIGHT - PGD336060K001C1 | 102 | -6 | Yes | Yes | 20.8 | 18.3 | 2.5 | 4B8C74E986B846F588AEEBF7E5BE8828 |  | R410A | TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | TXV |  |  | -5.882%
Bakersfield | CA | 93306-5972 |  | 2013-07-18 | 2013-07-18 16:28 | 2013-07-18 17:09 | GOODMAN - GPG13480701AC | 85 | 4.5 | Yes | Yes | 21.4 | 24.2 | -2.8 | 66078937EDF94256B147BBB044E430C6 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Bakersfield | CA | 93313-5615 |  | 2013-07-21 | 2013-07-21 10:40 | 2013-07-21 11:16 | TRANE - 2TTB3048A1000AA | 132 | 13.7 | Yes | Yes | 18.5 | 20.4 | -1.9 | 39F53F6D8F9048929B28472C4D629C6C |  | R22 | TXV |  | 10.38% | 0.89621 | 19.95% | [5 empty] | TXV | 10.38%
Bakersfield | CA | 93306-4104 |  | 2013-08-10 | 2013-08-10 19:41 | 2013-08-10 19:41 | ICP - PGA036D1K3 | 78 | 0 | Yes | Yes | 21.6 | 21.8 | -0.2 | BC774CED185640C291FD43278F7B9251 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1910 |  | 2013-08-30 | 2013-08-30 18:58 | 2013-08-30 19:00 | TRANE - YCY042G1MOAB | 85 | 2.6 | Yes | Yes | 25.2 | 20.4 | 4.8 | 893452D9711A451692ADD3C05C646BFF |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Antioch | CA | 94509-4632 |  | 2013-09-26 | 2013-09-26 09:12 | 2013-09-26 09:14 | CARRIER - 38TD048300 | 197 | -18.5 | Yes | Yes | 17.9 | 17.9 | 0 | 6BFD716D696A43A69C4E2366ACA20CCA |  | R22 | Non-TXV |  | -9.391% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.391%
Bakersfield | CA | 93306-7710 |  | 2013-07-31 | 2013-07-31 11:17 | 2013-07-31 12:09 | YORK - D1NH036N05606C | 108 | 5 | Yes | Yes | 22 | 20.4 | 1.6 | 3B203DF028704931BC603F31C649E7A3 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Sunnyvale | CA | 94089-1814 |  | 2013-09-27 | 2013-09-27 10:53 | 2013-09-27 12:04 | BRYANT - 561CJ036-D | 83 | -5.9 | Yes | Yes | 22.6 | 20.4 | 2.2 | B9F8A9FEC7164F7E902E098D698B6ED8 |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Sunnyvale | CA | 94089-1633 |  | 2013-09-27 | 2013-09-27 13:34 | 2013-09-27 14:03 | COLEMAN - BRC3042188 | 72 | -6.8 | Yes | Yes | 25.2 | 19.3 | 5.9 | 6ABC2C80A4A9482281836E86712A8D15 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Bakersfield | CA | 93306-2515 |  | 2013-07-17 | 2013-07-17 16:15 | 2013-07-17 16:31 | YORK - D1NH036N07206A | 104 | 4.3 | Yes | Yes | 23.4 | 21.1 | 2.4 | BFBBBC33728E4D67B434387618E694B0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.135% | 0.95865 | 7.946% | [5 empty] | Non-TXV | 4.135%
Fairfield | CA | 94534-3972 |  | 2013-07-30 | 2013-07-30 11:17 | 2013-07-30 16:15 | GOODMAN - CK36-1B | 76 | 2.6 | Yes | Yes | 14 | 16.5 | -2.5 | 7C8CBFEC7159402D860ED929D97EA96B |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Fairfield | CA | 94533-2710 |  | 2013-09-13 | 2013-09-13 11:32 | 2013-09-13 11:34 | CARRIER - 38TDA036300 | 184 | 8.1 | Yes | Yes | 17.3 | 17.3 | 0 | 321784F988354B15ADB6CBE844B3BC93 |  | R22 | Non-TXV |  | 4.402% | 0.95598 | 8.46% | [5 empty] | Non-TXV | 4.402%
Bakersfield | CA | 93306-2040 |  | 2013-07-17 | 2013-07-17 11:07 | 2013-07-17 11:24 | RHEEM - RRMAA042JK08F | 115 | -12.4 | Yes | Yes | 23.8 | 20.4 | 3.4 | 84175A1929414ED898033AA7BD68F127 |  | R22 | TXV |  | -10.78% | 1.1078 | 3.02% |  |  |  |  | TXV |  |  | -10.78%
Bakersfield | CA | 93312-6117 |  | 2013-07-26 | 2013-07-26 15:53 | 2013-07-26 16:40 | YORK - H2RA036506E | 85 | 5.1 | Yes | Yes | 17.8 | 19.3 | -1.5 | CDF5A55A5F0042C2AE8ED9F9CC179E06 |  | R22 | TXV |  | 6% | 0.94 | 11.53% | [5 empty] | TXV | 6%
Bakersfield | CA | 93306-4679 |  | 2013-08-08 | 2013-08-08 13:22 | 2013-08-08 14:36 | RHEEM - RRPL-B036JK06X | 85 | 3.5 | Yes | Yes | 23.6 | 21.4 | 2.2 | D8B8B241DAC741B0B8CA5ACF04CF3BB5 |  | R410A | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93306-4679 |  | 2013-08-08 | 2013-08-08 14:39 | 2013-08-08 14:57 | RHEEM - RRPL-B036JK06X | 85 | 4 | Yes | Yes | 20.6 | 20.4 | 0.2 | 3D70FE66C3A24B3CB547ED8C67CD572D |  | R410A | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Winters | CA | 95694-1818 |  | 2013-08-15 | 2013-08-15 14:37 | 2013-08-15 14:37 | COLEMAN - F036N070A | 120 | 0 | Yes | Yes | 15.1 | 17.5 | -2.3 | C4D0531ECB064E9B9EB3683B28FB7AB1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2659 |  | 2013-08-01 | 2013-08-01 14:32 | 2013-08-01 15:31 | CARRIER - 38ESG0423000 | 178 | 10.3 | Yes | Yes | 16.9 | 19.8 | -2.9 | 778BD869FBB040BB8D3FED77575A754C |  | R410A | TXV |  | 5.787% | 0.94213 | 11.12% | [5 empty] | TXV | 5.787%
Dixon | CA | 95620-3113 |  | 2013-09-16 | 2013-09-16 13:00 | 2013-09-16 13:25 | CARRIER - 24ABA336A310 | 105 | 16.1 | Yes | Yes | 23.2 | 17.2 | 6 | 15976072E7E341FA9084A52ED2788308 |  | R410A | TXV |  | 15.33% | 0.84667 | 29.47% | [5 empty] | TXV | 15.33%
Lost Hills | CA | 93249-0000 |  | 2013-09-18 | 2013-09-18 17:29 | 2013-09-18 17:32 | OTHER - JS5BD036KA | 110 | 9.3 | Yes | Yes | 25.2 | 20.4 | 4.8 | 96FA82BF76AB40F7942A39F63977AAA9 |  | R22 | TXV |  | 8.455% | 0.91545 | 16.25% | [5 empty] | TXV | 8.455%
Bakersfield | CA | 93308-1130 |  | 2013-07-29 | 2013-07-29 09:58 | 2013-07-29 09:58 | TRANE - 4TTR4042C1000AA | 112 | 0 | Yes | Yes | 21.3 | 20.6 | 0.8 | D01FB3EDAB6249B7956A0A4A69E366C7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4417 |  | 2013-08-27 | 2013-08-27 18:23 | 2013-08-27 18:23 | GOODMAN - CKL421A | 95 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 9CCD1AB9B4914D649483C35202E334D2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95409-4141 |  | 2013-09-16 | 2013-09-16 12:13 | 2013-09-16 12:16 | OTHER - BRCQ0421BD | 66 | 6.2 | Yes | Yes | 17.2 | 17.6 | -0.4 | A419DABEB8494814BCF5942B92DBD5BE |  | R22 | Non-TXV |  | 9.394% | 0.90606 | 18.05% | [5 empty] | Non-TXV | 9.394%
Wasco | CA | 93280-0000 |  | 2013-08-13 | 2013-08-13 12:45 | 2013-08-13 13:26 | GE - BGTA848R1D01 | 115 | -4.9 | Yes | Yes | 22.1 | 21 | 1.1 | DD99C7B8E91549FB94CEC66C0FBC6AA2 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -4.261% | 1.0426 | 1.193% |  |  |  |  | Non-TXV |  |  | -4.261%
Antioch | CA | 94509-1413 |  | 2013-08-05 | 2013-08-05 11:59 | 2013-08-05 11:59 | CARRIER - 38CKC036---341 | 76 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | DD20ECE632314790AB3A242FD95E1B7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4128 |  | 2013-07-25 | 2013-07-25 14:05 | 2013-07-25 14:39 | RHEEM - UKN | 109 | 5.8 | Yes | Yes | 18.1 | 19.1 | -1 | DFC99BC3C47642768A13D209DB8CF1CD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.321% | 0.94679 | 10.23% | [5 empty] | Non-TXV | 5.321%
Fairfield | CA | 94533-5158 |  | 2013-08-05 | 2013-08-05 10:43 | 2013-08-05 10:59 | CARRIER - 38BRC030320 | 100 | 12.1 | Yes | Yes | 18.2 | 17.9 | 0.3 | 36EB901358854BAB89FFF04B000EBB12 |  | R22 | Non-TXV |  | 12.1% | 0.879 | 23.25% | [5 empty] | Non-TXV | 12.1%
Antioch | CA | 94509-7318 |  | 2013-08-05 | 2013-08-05 10:37 | 2013-08-05 11:50 | CARRIER - UKN | 85 | -4 | Yes | Yes | 18.6 | 17.9 | 0.7 | 3248A8E863774131AF8BDD301E4E52A0 |  | R22 | Non-TXV |  | -4.706% | 1.0471 | 1.318% |  |  |  |  | Non-TXV |  |  | -4.706%
Hayward | CA | 94541-6536 |  | 2013-10-02 | 2013-10-02 14:21 | 2013-10-02 21:19 | CARRIER - 38HDL030-301 | 82 | 12.1 | Yes | Yes | 22.9 | 17.9 | 5 | 77C61C1C6FB240438979180F0FE9EC91 |  | R22 | Non-TXV |  | 14.76% | 0.85244 | 28.36% | [5 empty] | Non-TXV | 14.76%
Shafter | CA | 93263-3438 |  | 2013-08-06 | 2013-08-06 19:48 | 2013-08-06 19:50 | GOODMAN - GPG10300701A | 50 | 3.4 | Yes | Yes | 22.3 | 23.7 | -1.4 | E2D2773EA2874C328884AED9F3B8A0F7 |  | R22 | Non-TXV |  | 6.8% | 0.932 | 13.07% | [5 empty] | Non-TXV | 6.8%
Shafter | CA | 93263-3438 |  | 2013-08-06 | 2013-08-06 19:52 | 2013-08-06 19:57 | GOODMAN - GPG10300701A | 50 | 4.1 | Yes | Yes | 22.9 | 22.6 | 0.3 | 5CE82DBD412A4E098587BB9FDBA59367 |  | R22 | Non-TXV |  | 8.2% | 0.918 | 15.76% | [5 empty] | Non-TXV | 8.2%
Bakersfield | CA | 93307-3171 |  | 2013-09-27 | 2013-09-27 10:54 | 2013-09-27 10:54 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.7 | 20.4 | -1.7 | 56C9BFA3E81B4E93AE9E42C99701334C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3777 |  | 2013-08-05 | 2013-08-05 12:37 | 2013-08-05 12:38 | PAYNE - 598ANX036-B | 196 | 8.6 | Yes | Yes | 16.5 | 17.6 | -1.1 | 5608340BE11F4C3EB0BF541134817F87 |  | R22 | Non-TXV |  | 4.388% | 0.95612 | 8.432% | [5 empty] | Non-TXV | 4.388%
Bakersfield | CA | 93311-2241 |  | 2013-09-25 | 2013-09-25 17:37 | 2013-09-25 17:56 | RHEEM - RAMA-036JBZ | 96 | 8.8 | Yes | Yes | 21.4 | 21 | 0.4 | E49A30E3AD134843AFDB6C4A565DF969 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Fairfield | CA | 94533-7227 |  | 2013-07-30 | 2013-07-30 15:04 | 2013-07-30 15:04 | GOODMAN - GSC130481CB | 128 | 0 | Yes | Yes | 13 | 15.8 | -2.8 | 53D71B79E05A4BA1A0A6FB964A3AA185 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Willits | CA | 95490-9763 |  | 2013-08-20 | 2013-08-20 13:24 | 2013-08-20 14:21 | COLEMAN - ILLEGIBLE | 89 | 9.1 | Yes | Yes | 26.2 | 20.9 | 5.3 | 52274F57150B47D187D5B6A3D8B21908 |  | R22 | Non-TXV |  | 10.22% | 0.89775 | 19.65% | [5 empty] | Non-TXV | 10.22%
Milpitas | CA | 95035-3172 |  | 2013-09-26 | 2013-09-26 10:52 | 2013-09-26 11:25 | CARRIER - 561AJ024 B | 56 | 1.9 | Yes | Yes | 20.8 | 21.5 | -0.7 | D0707086E95D4BF9A6F1EC51107898AD |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Bakersfield | CA | 93307-4707 |  | 2013-07-18 | 2013-07-18 17:28 | 2013-07-18 17:28 | PAYNE - PA13NAO36000AEAA | 73 | 0 | Yes | Yes | 18.3 | 20.7 | -2.4 | 132D2C9609AD4ECE81FAA11E9E9C8D5A |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-2521 |  | 2013-07-29 | 2013-07-29 16:10 | 2013-07-29 17:11 | GOODMAN - CK601C | 122 | 8.6 | Yes | Yes | 22.1 | 20.4 | 1.8 | F6A3B72B3C584BE08831F4D67A8D3F2A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.049% | 0.92951 | 13.55% | [5 empty] | Non-TXV | 7.049%
Davis | CA | 95618-6026 |  | 2013-08-12 | 2013-08-12 13:19 | 2013-08-12 13:42 | CARRIER - 38CK030310 | 68 | 0 | Yes | Yes | 14.1 | 16.8 | -2.7 | 537EE82BEA5743C3A908F0609AD4F52F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-0000 |  | 2013-08-05 | 2013-08-05 11:34 | 2013-08-05 11:34 | CARRIER - 38ETG048300 | 149 | 0 | Yes | Yes | 16.7 | 17.3 | -0.6 | 4ED99B17FADD4A088BECD7C5BAD7FCD6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2509 |  | 2013-07-25 | 2013-07-25 11:46 | 2013-07-25 12:35 | GOODMAN - 10360701A | 75 | -7.1 | Yes | Yes | 16.8 | 19.3 | -2.5 | 21E79B16EFD448069A426C73EBB482DC |  | R22 | Non-TXV |  | -9.467% | 1.0947 | 2.651% |  |  |  |  | Non-TXV |  |  | -9.467%
Suisun City | CA | 94585-4142 |  | 2013-08-05 | 2013-08-05 13:03 | 2013-08-05 13:05 | OTHER - DRCS0601CD | 147 | 6.7 | Yes | Yes | 19.7 | 18.2 | 1.5 | 77A1EEE7C86049FE8841EDDD4B2B43D8 |  | R22 | Non-TXV |  | 4.558% | 0.95442 | 8.759% | [5 empty] | Non-TXV | 4.558%
Suisun City | CA | 94585-1842 |  | 2013-08-05 | 2013-08-05 12:10 | 2013-08-05 12:13 | CARRIER - 561CJ024-E | 54 | 2.2 | Yes | Yes | 16.1 | 17.1 | -1 | 04CF58DF00674645A0E5931609D9689B |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Taft | CA | 93268-3012 |  | 2013-09-23 | 2013-09-23 18:54 | 2013-09-23 18:54 | LENNOX - 13GEP42075ALP-2A | 96 | 4 | Yes | Yes | 22.3 | 20.3 | 2 | 32C8CA0689A147F6B77E56C55624FDDB | Add refrigerant: 4 oz | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Bakersfield | CA | 93308-2976 |  | 2013-08-28 | 2013-08-28 17:01 | 2013-08-28 17:01 | BRYANT - 582ANW024040AAAD | 53 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 03403F649B724D758587D87EAFDB4D17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2974 |  | 2013-08-28 | 2013-08-28 15:20 | 2013-08-28 15:37 | CARRIER - 48GS024040301 | 53 | 6.3 | Yes | Yes | 22.5 | 21.5 | 1 | 726108FABAA44D9182C7CCE0C7E36198 |  | R22 | Non-TXV |  | 11.89% | 0.88113 | 22.84% | [5 empty] | Non-TXV | 11.89%
Bakersfield | CA | 93309-6013 |  | 2013-08-02 | 2013-08-02 14:02 | 2013-08-02 14:02 | PAYNE - PY3NAA3606NA | 102 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 2EC542316B584291A47C9AC81C9E6903 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6162 |  | 2013-08-21 | 2013-08-21 19:24 | 2013-08-21 19:24 | TRANE - 4YCZ036A1075AA | 111 | 0 | Yes | Yes | 20.6 | 21 | -0.4 | 57588B2E83134AAEB4B4BF65149C010B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5018 |  | 2013-07-26 | 2013-07-26 17:35 | 2013-07-26 18:11 | RHEEM - RRMAA036JK06X | 99 | 6.2 | Yes | Yes | 19.8 | 21.1 | -1.3 | 353A79D3E8F7443CA90CCA982AF9FD3B |  | R22 | Non-TXV |  | 6.263% | 0.93737 | 12.04% | [5 empty] | Non-TXV | 6.263%
Bakersfield | CA | 93309-8543 |  | 2013-08-22 | 2013-08-22 16:00 | 2013-08-22 16:00 | ICP - PGAD48G080E | 160 | 0 | Yes | Yes | 22.3 | 21 | 1.3 | 7F3E8CF7E0CF441692FA457CF24EE027 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2984 |  | 2013-08-28 | 2013-08-28 13:12 | 2013-08-28 13:12 | ICP - PGD324040K00K1 | 72 | 0 | Yes | Yes | 19.8 | 18.2 | 1.6 | F7C86E48EB2243EA9384A25505002302 |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2994 |  | 2013-07-25 | 2013-07-25 12:39 | 2013-07-25 12:39 | - GSC130241DA | 83 | 0 | Yes | Yes | 13.5 | 15.9 | -2.4 | 52D15912A0AC40B68FD0FCFBC3673D73 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3161 |  | 2013-08-05 | 2013-08-05 19:24 | 2013-08-05 19:28 | OTHER - 24ABB348A310 | 112 | 24 | Yes | Yes | 22.3 | 20.4 | 1.9 | 04F7E3DDE5794D61BED291AC78549E5F |  | R410A | Non-TXV |  | 21.43% | 0.78571 | 41.18% | [5 empty] | Non-TXV | 21.43%
Bakersfield | CA | 93308-2167 |  | 2013-08-30 | 2013-08-30 17:08 | 2013-08-30 17:08 | PAYNE - PY3PNA024040NB | 89 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 19792FBAD31849F6879B0D6F70A7FA16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1319 |  | 2013-09-06 | 2013-09-06 13:35 | 2013-09-06 13:35 | HEIL - HAC030AKA4 | 85 | 0 | Yes | Yes | 19.5 | 16.2 | 3.3 | 679E000EA64B43B5A6C78988A6B2CC6A |  | R22 | TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2067 |  | 2013-08-19 | 2013-08-19 10:49 | 2013-08-19 11:14 | GOODMAN - C[PLE42 1B | 120 | 4 | Yes | Yes | 24 | 20.9 | 3.1 | 136EE793A27E411AB07A64D68A6084CC |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Sunnyvale | CA | 94089-5001 |  | 2013-10-04 | 2013-10-04 09:47 | 2013-10-04 10:22 | COLEMAN - ILLEGIBLE | 62 | 6.7 | Yes | Yes | 25.3 | 19.7 | 5.6 | 76CAEACBE6AB4EFBB2E72FF9CC30D43C |  | R22 | Non-TXV |  | 10.81% | 0.89194 | 20.77% | [5 empty] | Non-TXV | 10.81%
Redding | CA | 96003-0000 |  | 2013-09-05 | 2013-09-05 15:59 | 2013-09-05 16:46 | RHEEM - RQKA-A048JK | 138 | 8.5 | Yes | Yes | 26.4 | 22.6 | 3.8 | 599A679ECEF84F27A0DF14C5E3AE5023 |  | R22 | Non-TXV |  | 6.159% | 0.93841 | 11.84% | [5 empty] | Non-TXV | 6.159%
Fairfield | CA | 94533-6594 |  | 2013-09-25 | 2013-09-25 16:00 | 2013-09-25 16:27 | CARRIER - 38CKC042350 | 93 | 4.8 | Yes | Yes | 16.6 | 19.2 | -2.6 | 2A9C23914DAB4DBDBDF8B3E52C66F959 |  | R22 | Non-TXV |  | 5.161% | 0.94839 | 9.919% | [5 empty] | Non-TXV | 5.161%
Fairfield | CA | 94534-6624 |  | 2013-08-05 | 2013-08-05 13:38 | 2013-08-05 13:38 | CARRIER - 38CKC060300 | 158 | 0 | Yes | Yes | 18.4 | 19.9 | -1.5 | 0460C248B38A403BA35BD3FB197DD4F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5117 |  | 2013-08-06 | 2013-08-06 13:22 | 2013-08-06 13:40 | CARRIER - 38BRB048300 | 167 | 17.3 | Yes | Yes | 18 | 19.3 | -1.3 | 7B9AFF275B02480AA94B442C062C602A |  | R22 | Non-TXV |  | 10.36% | 0.89641 | 19.91% | [5 empty] | Non-TXV | 10.36%
Bay Point | CA | 94565-3287 |  | 2013-09-24 | 2013-09-24 11:23 | 2013-09-24 11:23 | CARRIER - 38EN024310 | 56 | 5.1 | Yes | Yes | 18.8 | 17.6 | 1.2 | 3EA251C8DE994DBBBE0FF19FCAEF2487 |  | R22 | Non-TXV |  | 9.107% | 0.90893 | 17.5% | [5 empty] | Non-TXV | 9.107%
Bakersfield | CA | 93308-2972 |  | 2013-08-29 | 2013-08-29 17:40 | 2013-08-29 18:02 | ICP - PGC024060A | 58 | 9.8 | Yes | Yes | 21.9 | 21.5 | 0.4 | 5D61821175744F579972F05D3D69EC2D |  | R22 | Non-TXV |  | 16.9% | 0.83103 | 32.47% | [5 empty] | Non-TXV | 16.9%
Sunnyvale | CA | 94089-5001 |  | 2013-10-04 | 2013-10-04 16:16 | 2013-10-04 16:46 | COLEMAN - ILLEGIBLE | 68 | -6.4 | Yes | Yes | 22.2 | 19.7 | 2.6 | 477F8FCF5BA7403BBDE2A172C6C36AC6 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Suisun City | CA | 94585-1937 |  | 2013-08-05 | 2013-08-05 11:56 | 2013-08-05 11:57 | RHEEM - RAKA-036JAS | 75 | 3.6 | Yes | Yes | 17.6 | 17.6 | 0 | 9750ECAACE574900B766229E40BDA5A4 |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Bakersfield | CA | 93306-3472 |  | 2013-10-15 | 2013-10-15 18:23 | 2013-10-15 18:23 | HEIL - NRGF42DDB04 | 90 | 0 | Yes | Yes | 20.6 | 20.8 | -0.2 | FF3A8506C6784C849F4DC0ABA92B6399 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2009 |  | 2013-10-04 | 2013-10-04 11:34 | 2013-10-04 11:34 | GUARDIAN - GCGD36S21S2A | 63 | 2.4 | Yes | Yes | 17.8 | 18.1 | -0.3 | 2B0907BE46CF465792E9994B340AD7DB |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Bay Point | CA | 94565-3340 |  | 2013-07-29 | 2013-07-29 09:07 | 2013-07-29 09:11 | OTHER - NA | 72 | -5.1 | Yes | Yes | 17.3 | 16.7 | 0.6 | 5A7B88487D5B42098FA63E014FA0888C |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Bakersfield | CA | 93308-1053 |  | 2013-07-29 | 2013-07-29 13:32 | 2013-07-29 13:32 | TRANE - YCP036F1M0AC | 109 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 4DA5BA9F6C5B438789DC873AC4E79A3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2978 |  | 2013-08-28 | 2013-08-28 17:26 | 2013-08-28 17:26 | OTHER - CTG024GYA | 60 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 28607DB3F9BE42628F615CF4C53D33A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2025 |  | 2013-10-08 | 2013-10-08 11:46 | 2013-10-08 13:27 | ICP - HAC036AKA4 | 80 | 2.7 | Yes | Yes | 20.8 | 20.9 | -0.1 | 5BE55215606D44B28DDB10B3D66FD6B3 |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Bakersfield | CA | 93311-2101 |  | 2013-09-25 | 2013-09-25 14:49 | 2013-09-25 14:49 | YORK - D1NH048N06506C | 128 | 0 | Yes | Yes | 22.4 | 21.5 | 0.9 | CBBE008D4F1F4E65970B9367B08626B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2101 |  | 2013-09-25 | 2013-09-25 14:56 | 2013-09-25 14:56 | YORK - UKN | 90 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 3990200925564A78B2C6480DA5DF3131 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2101 |  | 2013-09-25 | 2013-09-25 15:22 | 2013-09-25 15:22 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 56A9594D96074EAE9D52EC9B25218A21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2343 |  | 2013-08-07 | 2013-08-07 15:42 | 2013-08-07 16:44 | AIRE-FLO - URKA-A036JK08E | 62 | 3.1 | Yes | Yes | 14.8 | 17.7 | -2.9 | 6C42B88604994FABA97B89BF6F055F42 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Vacaville | CA | 95687-7122 |  | 2013-10-14 | 2013-10-14 11:17 | 2013-10-14 11:17 | CARRIER - 38TH036300 | 267 | 0 | Yes | Yes | 17.5 | 17.2 | 0.3 | 031664D394C14057B89BEF0672916954 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-2566 |  | 2013-08-12 | 2013-08-12 11:18 | 2013-08-12 11:18 | CARRIER - 38CK042300 | 168 | 0 | Yes | Yes | 20.2 | 15.9 | 4.3 | EF373EFA99384D5F82CB9BEFCD68FE80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2986 |  | 2013-08-28 | 2013-08-28 13:33 | 2013-08-28 13:33 | BRYANT - 588ANW030040AAD | 52 | 0 | Yes | Yes | 20.7 | 19.9 | 0.8 | 2DB9BC391DF847DBBF1E3CBCFDA64017 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Ukiah | CA | 95482-9534 |  | 2013-08-23 | 2013-08-23 09:35 | 2013-08-23 10:17 | COLEMAN - ILLEGIBLE | 78 | 4.7 | Yes | Yes | 24.7 | 21 | 3.7 | F6FB6CA360394BBFB365BC1AECC6FE46 |  | R22 | Non-TXV |  | 6.026% | 0.93974 | 11.58% | [5 empty] | Non-TXV | 6.026%
Antioch | CA | 94509-3932 |  | 2013-08-09 | 2013-08-09 11:22 | 2013-08-09 11:43 | CARRIER - 24ACR342A300 | 116 | 8.5 | Yes | Yes | 19.2 | 21.7 | -2.5 | 384C4C0306974E64A718423CB0C98EDF |  | R22 | TXV |  | 7.328% | 0.92672 | 14.08% | [5 empty] | TXV | 7.328%
Bakersfield | CA | 93308-2986 |  | 2013-08-28 | 2013-08-28 13:13 | 2013-08-28 13:13 | CARRIER - 48SDN042040301 | 120 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | 0C95CDDA061C4DD583EF10D5744ABC40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4521 |  | 2013-09-05 | 2013-09-05 11:41 | 2013-09-05 11:42 | RHEEM - RAFD-036JAS | 80 | 2.9 | Yes | Yes | 17.9 | 17.6 | 0.3 | 3A674EBF419C4A92AB09277BAB0D3AD2 |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Bakersfield | CA | 93308-2986 |  | 2013-08-28 | 2013-08-28 13:53 | 2013-08-28 14:13 | OTHER - CTG024G7A | 60 | 5.2 | Yes | Yes | 20 | 19.5 | 0.5 | 1EC6E7CA7E7D46F2870DF0C6986E740A |  | R22 | Non-TXV |  | 8.667% | 0.91333 | 16.66% | [5 empty] | Non-TXV | 8.667%
San Jose | CA | 95127-1022 |  | 2013-10-09 | 2013-10-09 14:50 | 2013-10-09 15:26 | NORDYNE - ILLEGIBLE | 91 | 5.9 | Yes | Yes | 27.1 | 21.4 | 5.7 | DA71568181F645DA82A71102A8C1B5DD |  | R22 | Non-TXV |  | 6.484% | 0.93516 | 12.46% | [5 empty] | Non-TXV | 6.484%
Antioch | CA | 94509-5873 |  | 2013-08-09 | 2013-08-09 12:19 | 2013-08-12 08:11 | DAY & NIGHT - 567C048BCU | 85 | 10.7 | Yes | Yes | 17.3 | 18.7 | -1.4 | 8C76E6340A2E4C78B607C85B7800A230 |  | R22 | Non-TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | Non-TXV | 12.59%
Bakersfield | CA | 93309-4722 |  | 2013-08-22 | 2013-08-22 15:05 | 2013-08-22 15:30 | ICP - PGC048K080A | 102 | 14 | Yes | Yes | 22.2 | 20.9 | 1.3 | A5AB454FF3DF45A5A9AB63790967B175 |  | R22 | Non-TXV |  | 13.73% | 0.86275 | 26.38% | [5 empty] | Non-TXV | 13.73%
Bakersfield | CA | 93313-6000 |  | 2013-10-21 | 2013-10-21 11:23 | 2013-10-21 11:23 | RHEEM - RAKA-042JAZ | 79 | 0 | Yes | Yes | 22 | 21 | 1 | B25F5457AB7A4D83A4BD0236A7B16008 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3850 |  | 2013-10-21 | 2013-10-21 11:15 | 2013-10-21 11:56 | CARRIER - 38CKC03600 | 80 | 3.3 | Yes | Yes | 22.3 | 22.6 | -0.3 | D806F1F3F8794AA6BB6BF7D4B940705E |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Anderson | CA | 96007-4720 |  | 2013-07-18 | 2013-07-18 08:33 | 2013-07-18 09:00 | ARMSTRONG - SCU12E36A | 88 | -6.2 | Yes | Yes | 20.8 | 19.8 | 1 | 6BDE2197D6CC4BB8954AC85C08547598 |  | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Bakersfield | CA | 93313-4362 |  | 2013-07-25 | 2013-07-25 15:23 | 2013-07-25 16:09 | CARRIER - CA9048VKC1 | 115 | 4.5 | Yes | Yes | 20 | 21 | -1 | B1369C39F2BB4C04A9DF8DB59B5777E9 |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
San Jose | CA | 95148-2508 |  | 2013-09-17 | 2013-09-17 12:02 | 2013-09-17 12:58 | ARMSTRONG - AG048GBZ | 134 | -7.9 | Yes | Yes | 19.8 | 21.5 | -1.7 | AA228622F876452E916B3E738A2A7784 |  | R22 | Non-TXV |  | -5.896% | 1.059 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.896%
Davis | CA | 95616-4822 |  | 2013-08-12 | 2013-08-12 10:04 | 2013-08-12 10:04 | GMC - CRT30-1 | 107 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | B7F4A693A6AC4DC1A27557BDBBE26322 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2329 |  | 2013-08-05 | 2013-08-05 18:57 | 2013-08-05 18:59 | DAY & NIGHT - PGF336060K01 | 148 | 5.6 | Yes | Yes | 20.6 | 21.4 | -0.8 | 01B607913E2E4F0F9570007EBB728EE0 |  | R22 | Non-TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | Non-TXV | 3.784%
Fairfield | CA | 94533-3719 |  | 2013-07-30 | 2013-07-30 14:18 | 2013-07-30 16:16 | - 593CJ048-B | 122 | 7.2 | Yes | Yes | 14.7 | 15.2 | -0.5 | 31276E578FF54EF48FAF1AD034CB8511 |  | R22 | Non-TXV |  | 5.902% | 0.94098 | 11.34% | [5 empty] | Non-TXV | 5.902%
Bakersfield | CA | 93312-5406 |  | 2013-09-26 | 2013-09-26 17:42 | 2013-09-26 17:42 | RUUD - UAMB-048JAZ | 192 | 0 | Yes | Yes | 22.1 | 21.2 | 0.9 | 8245A8F1754F4588BB4FC692849EB574 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5502 |  | 2013-09-04 | 2013-09-04 23:20 | 2013-09-04 23:40 | YORK - DAYP-F042N080A | 150 | 18.2 | Yes | Yes | 21.8 | 21.5 | 0.3 | 75553D67E8A548889EAC124844395B97 |  | R22 | Non-TXV |  | 12.13% | 0.87867 | 23.32% | [5 empty] | Non-TXV | 12.13%
Bakersfield | CA | 93304-5515 |  | 2013-09-04 | 2013-09-04 12:29 | 2013-09-04 12:29 | OTHER - DRCS0481B8 | 136 | 0 | Yes | Yes | 21.6 | 21.4 | 0.2 | 57D1CD67DD6E4573987F8B663B1F4DFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7300 |  | 2013-08-09 | 2013-08-09 13:35 | 2013-08-09 13:35 | CARRIER - 38CKC060 | 136 | 0 | Yes | Yes | 18.9 | 18.5 | 0.4 | C5DD252B411240AEB502CB01A6E7BDF9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1228 |  | 2013-08-13 | 2013-08-13 09:59 | 2013-08-13 11:22 | GOODMAN - | 85 | 2.5 | Yes | Yes | 18.3 | 18.5 | -0.2 | 997A5E97240149DEB66D84834992FE93 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Vacaville | CA | 95687-5405 |  | 2013-08-01 | 2013-08-01 14:32 | 2013-08-01 15:26 | PAYNE - PA10JA036-C | 78 | 2.5 | Yes | Yes | 16.6 | 17.7 | -1.1 | D7D71B648245423E873B5C532FB52BA0 |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Fresno | CA | 93728-1412 |  | 2013-08-15 | 2013-08-15 13:27 | 2013-08-15 14:14 | PAYNE - PY3PNA036060NB | 115 | 4 | Yes | Yes | 23.3 | 20.2 | 3.2 | 197E33761D6E47D8841B7B2FE5F132A7 |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Bakersfield | CA | 93304-3645 |  | 2013-09-25 | 2013-09-25 16:52 | 2013-09-25 17:18 | CARRIER - 48DL003 | 54 | 4.3 | Yes | Yes | 22.6 | 22.1 | 0.5 | 77D4BB3A50814195953E49391CBD5CB5 |  | R22 | Non-TXV |  | 7.963% | 0.92037 | 15.3% | [5 empty] | Non-TXV | 7.963%
Bakersfield | CA | 93308-1228 |  | 2013-07-29 | 2013-07-29 03:53 | 2013-07-29 03:53 | GOODMAN - GPG1336045M41AB | 85 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | C3005E2E09604276855FAB1C0D62B3C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-1920 |  | 2013-08-12 | 2013-08-12 12:08 | 2013-08-12 12:57 | CARRIER - 38CKC060300 | 233 | 24.8 | Yes | Yes | 20.4 | 17.4 | 3 | 64CD4F49B4CE4108A55F18A6D2A20786 |  | R22 | Non-TXV |  | 10.64% | 0.89356 | 20.45% | [5 empty] | Non-TXV | 10.64%
Lemoore | CA | 93245-2436 |  | 2013-08-28 | 2013-08-28 10:35 | 2013-08-28 11:18 | OTHER - PGAD47D1K5 | 215 | 10.8 | Yes | Yes | 23.4 | 19.3 | 4.1 | 88FC3C00FB534840ABA461E4DEDE572E |  | R22 | Non-TXV |  | 5.023% | 0.94977 | 9.654% | [5 empty] | Non-TXV | 5.023%
San Jose | CA | 95110-2827 |  | 2013-09-25 | 2013-09-25 12:07 | 2013-09-25 12:45 | BRYANT - 538ANR03600BBAA | 99 | 4.4 | Yes | Yes | 21 | 20.9 | 0.1 | D622B2D35A4A4FBF9D7729C4F336D34C |  | R410A | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
San Jose | CA | 95123-6246 |  | 2013-10-09 | 2013-10-09 14:32 | 2013-10-09 15:03 | CARRIER - 3BENE1833410 | 48 | 2.3 | Yes | Yes | 21.1 | 21 | 0.1 | 43301918131645DBB22AC833BD574C2D |  | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Bakersfield | CA | 93309-1885 |  | 2013-10-15 | 2013-10-15 18:49 | 2013-10-15 19:10 | YORK - D1NA0240560EC | 56 | 5.6 | Yes | Yes | 19.9 | 20.4 | -0.5 | E2A46A57240746BF9F73A70103FEFA96 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93306-4204 |  | 2013-07-17 | 2013-07-17 14:34 | 2013-07-17 14:56 | DAY & NIGHT - 584AWW048080AAAG | 117 | 21.2 | Yes | Yes | 23.4 | 20.2 | 3.2 | 861A80B63DFC4C1384782FB0DAEDADA7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.12% | 0.8188 | 34.82% | [5 empty] | Non-TXV | 18.12%
Bakersfield | CA | 93306-4204 |  | 2013-07-17 | 2013-07-17 15:05 | 2013-07-17 15:30 | DAY & NIGHT - 584AWW048080AAAG | 117 | 20.3 | Yes | Yes | 21.2 | 21.2 | 0.1 | 05DA990F439C44E093D1C98C5B1A4D33 |  | R22 | Non-TXV |  | 17.35% | 0.8265 | 33.34% | [5 empty] | Non-TXV | 17.35%
Shafter | CA | 93263-2202 |  | 2013-07-23 | 2013-07-23 19:20 | 2013-07-23 19:48 | AMERICAN STANDARD - 2YCC3036A106AA | 82 | 4.9 | Yes | Yes | 20.9 | 20.4 | 0.5 | 91D1F9ACBFB140899A8481ED8D9FE0CF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.976% | 0.94024 | 11.48% | [5 empty] | Non-TXV | 5.976%
Fresno | CA | 93727-8009 |  | 2013-08-07 | 2013-08-07 15:30 | 2013-08-07 16:13 | YORK - D2NP036N05606A | 108 | 6 | Yes | Yes | 26.6 | 20.9 | 5.7 | 31C9F1720D5247A597A1C6625CA9135F |  | R22 | TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | TXV | 5.556%
Davis | CA | 95618-6372 |  | 2013-08-15 | 2013-08-15 11:28 | 2013-08-15 11:28 | OTHER - 598AN036-B | 185 | 0 | Yes | Yes | 20.4 | 19.6 | 0.8 | 1C893285E1B4486AB130BB1E62A88CDE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5040 |  | 2013-07-25 | 2013-07-25 08:51 | 2013-07-25 09:10 | GOODMAN - GPG13420701AB | 107 | 7.4 | Yes | Yes | 23.3 | 19.5 | 3.8 | 30A02EECF6C04F4B83EF7C5395A3780C |  | R22 | Non-TXV |  | 6.916% | 0.93084 | 13.29% | [5 empty] | Non-TXV | 6.916%
Bakersfield | CA | 93305-4370 |  | 2013-08-19 | 2013-08-19 15:03 | 2013-08-19 15:21 | YORK - DBYP-F024N045A | 100 | 15.3 | Yes | Yes | 21.9 | 21 | 0.9 | 96AB469DD67D45DDB3076A7F3E593259 |  | R22 | Non-TXV |  | 15.3% | 0.847 | 29.4% | [5 empty] | Non-TXV | 15.3%
Arvin | CA | 93203-2060 |  | 2013-08-19 | 2013-08-19 17:12 | 2013-08-19 17:14 | GOODMAN - CPLE36-1A | 110 | 8.3 | Yes | Yes | 23.1 | 21.4 | 1.7 | D262D49FAA6845FD8ECAE4CA8279D3D9 |  | R22 | Non-TXV |  | 7.545% | 0.92455 | 14.5% | [5 empty] | Non-TXV | 7.545%
Bakersfield | CA | 93308-3850 |  | 2013-08-13 | 2013-08-13 15:20 | 2013-08-13 16:05 | BDP - 585A024055YAC | 51 | 6.8 | Yes | Yes | 22.1 | 20.4 | 1.7 | 642B5255780740059E707057FE50F63B |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Pittsburg | CA | 94565-6232 |  | 2013-09-20 | 2013-09-20 09:16 | 2013-09-20 09:43 | CARRIER - 38TXA036330 | 109 | -5 | Yes | Yes | 15.5 | 17.2 | -1.7 | 7C53AAD043564B82A8232A0958685E48 |  | R410A | Non-TXV |  | -4.587% | 1.0459 | 1.285% |  |  |  |  | Non-TXV |  |  | -4.587%
Bakersfield | CA | 93306-4677 |  | 2013-07-22 | 2013-07-22 09:59 | 2013-07-22 10:37 | RHEEM - UNK | 85 | 3.9 | Yes | Yes | 13.1 | 16.1 | -3 | AB884097705B4CB8907B7368480AE544 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93307-4379 |  | 2013-08-05 | 2013-08-05 16:16 | 2013-08-05 16:16 | NORDYNE - JT5BD-036K | 155 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | A0CDB496907E449EBE0FFCED81F5D6E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6331 |  | 2013-08-21 | 2013-08-21 13:37 | 2013-08-21 14:05 | TRANE - TTR042D100B0 | 81 | 9 | Yes | Yes | 22.7 | 18.6 | 4.1 | 0A636569EDCB4341BBC024F3014823E1 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
San Jose | CA | 95124-6057 |  | 2013-08-12 | 2013-08-12 13:06 | 2013-08-12 13:06 | BRYANT - 538ANX0480000B | 116 | 0 | Yes | Yes | 19.4 | 16.1 | 3.3 | 4B0D1447048848FBA7E8B781B4DA9ADE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1883 |  | 2013-08-22 | 2013-08-22 11:52 | 2013-08-22 12:19 | BDP - 42RCU108K | 89 | 13.6 | Yes | Yes | 21.2 | 22.1 | -0.9 | 9E0EA6D7FB764133992921CA0DC67533 |  | R22 | Non-TXV |  | 15.28% | 0.84719 | 29.37% | [5 empty] | Non-TXV | 15.28%
Pittsburg | CA | 94565-5640 |  | 2013-10-24 | 2013-10-24 09:57 | 2013-10-24 09:58 | CARRIER - 38CKC036340 | 70 | 2.8 | Yes | Yes | 18.6 | 18.2 | 0.4 | 9EE03F4876684D9C9840094A12C12F61 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93705-0161 |  | 2013-08-29 | 2013-08-29 12:34 | 2013-08-29 12:34 | AMERICAN STANDARD - CM1641T | 36 | 23.3 | Yes | Yes | 12.3 | 20.1 | -7.8 | 84B23C10827B4E0AA9430FA4865A6FA3 | Add refrigerant: 23.3 oz Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 64.72% | 0.35278 | 124.4% | [5 empty] | Non-TXV | 64.72%
Fresno | CA | 93722-4017 |  | 2013-07-24 | 2013-07-24 08:42 | 2013-07-24 08:42 | - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 6BD848EF448A484D85568EDABA681B2C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6752 |  | 2013-08-09 | 2013-08-09 09:44 | 2013-08-09 09:48 | OTHER - SCU10B36A-7 | 71 | 6.5 | Yes | Yes | 16.8 | 17.6 | -0.8 | A1933DF06F48497494B67ECB5A5DCEE1 |  | R22 | Non-TXV |  | 9.155% | 0.90845 | 17.59% | [5 empty] | Non-TXV | 9.155%
Antioch | CA | 94509-5706 |  | 2013-07-29 | 2013-07-29 11:47 | 2013-07-29 11:48 | RHEEM - NA | 72 | -4.2 | Yes | Yes | 19 | 17.6 | 1.4 | 4E352C950DC846DE949C51E4B227DD17 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93705-0158 |  | 2013-08-27 | 2013-08-27 12:52 | 2013-08-27 13:45 | OTHER - UKN | 66 | 3.8 | Yes | Yes | 22.4 | 21 | 1.4 | 0BD7B15ECDB64B028566D29AA6AD1CE2 |  | R22 | TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | TXV | 5.758%
San Jose | CA | 95148-2637 |  | 2013-10-12 | 2013-10-12 08:50 | 2013-10-12 09:23 | BDP - PA13NR036-J | 89 | 4.3 | Yes | Yes | 14.7 | 15.2 | -0.5 | 729D2151191E45ADAEE9E17E4356E6C8 |  | R22 | Non-TXV |  | 4.831% | 0.95169 | 9.285% | [5 empty] | Non-TXV | 4.831%
Fairfield | CA | 94533-3286 |  | 2013-09-19 | 2013-09-19 11:39 | 2013-09-19 11:39 | PAYNE - 541DJ018 | 83 | 0 | Yes | Yes | 16.9 | 17 | -0.1 | CCD4FCA1EC234320A262BB90BC018651 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-7127 |  | 2013-08-12 | 2013-08-12 14:19 | 2013-08-12 14:45 | CARRIER - 38CKC030330 | 68 | -4 | Yes | Yes | 13.5 | 15.2 | -1.7 | 5F61C27A9D0B4E798F2BDC3A64CB452A |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Milpitas | CA | 95035-7803 |  | 2013-09-27 | 2013-09-27 10:07 | 2013-09-27 10:29 | CARRIER - 38EH042691 | 131 | 6 | Yes | Yes | 19.6 | 20.4 | -0.8 | 90755F153E834F96A2D0FF1580009A99 |  | R22 | Non-TXV |  | 4.58% | 0.9542 | 8.802% | [5 empty] | Non-TXV | 4.58%
Milpitas | CA | 95035-7803 |  | 2013-09-27 | 2013-09-27 10:31 | 2013-09-27 10:53 | CARRIER - 38EH042320 | 131 | 4.4 | Yes | Yes | 21.9 | 21.8 | 0.1 | 744D2F3491B34A5CA752536F742191B7 |  | R22 | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
Bakersfield | CA | 93307-3377 |  | 2013-10-24 | 2013-10-24 08:57 | 2013-10-24 08:57 | YORK - DAYP-F030N045A | 73 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 496A5AABD2E84618AA47C7DE4695BF18 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3353 |  | 2013-09-10 | 2013-09-10 10:10 | 2013-09-10 10:11 | OTHER - 569CJ036 | 102 | 4.3 | Yes | Yes | 15.9 | 17.6 | -1.7 | AF8661E784B143C09483C6FA9B135020 |  | R22 | Non-TXV |  | 4.216% | 0.95784 | 8.102% | [5 empty] | Non-TXV | 4.216%
Fresno | CA | 93722-4119 |  | 2013-07-17 | 2013-07-17 11:40 | 2013-07-17 12:06 | TRANE - YCX036F1M0AB | 118 | 24.2 | Yes | Yes | 23.6 | 19.8 | 3.8 | 8E684FEC587C48CE807E6CB4F4295A0F |  | R22 | Non-TXV |  | 20.51% | 0.79492 | 39.41% | [5 empty] | Non-TXV | 20.51%
Bakersfield | CA | 93312-2847 |  | 2013-09-25 | 2013-09-25 15:23 | 2013-09-25 15:23 | YORK - D1NH060N09006C | 140 | 0 | Yes | Yes | 23.5 | 17.5 | 6 | 9692A4760EEE45B28B7E5A468758B99F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2745 |  | 2013-07-25 | 2013-07-25 16:28 | 2013-07-25 16:49 | OTHER - UNK | 54 | 2.8 | Yes | Yes | 17.6 | 20.1 | -2.5 | 3044841D5B424D629BD483E270656083 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Fresno | CA | 93711-2745 |  | 2013-07-25 | 2013-07-25 15:54 | 2013-07-25 16:23 | CARRIER - UNK | 66 | 3.3 | Yes | Yes | 19.9 | 20.2 | -0.3 | 8A2FC448D3F44C6BB533D70C44F4B1CF |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Milpitas | CA | 95035-4448 |  | 2013-09-26 | 2013-09-26 11:26 | 2013-09-26 13:08 | CARRIER - AA1CJ042 A | 80 | 5 | Yes | Yes | 19.4 | 22 | -2.6 | 5DEC2057365B43BAB9513317177B40EA |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Fairfield | CA | 94533-3283 |  | 2013-07-30 | 2013-07-30 12:51 | 2013-07-30 16:12 | PAYNE - | 85 | 3.4 | Yes | Yes | 14.7 | 14.4 | 0.3 | FDDD876682524E2BA98AE7716285C0D3 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Kerman | CA | 93630-9384 |  | 2013-09-23 | 2013-09-23 11:30 | 2013-09-23 12:12 | LENNOX - 13ACD04823002 | 204 | 7.4 | Yes | Yes | 20.9 | 19.9 | 1 | 0CABBE97395F4F6687A504A667605E72 |  | R22 | TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | TXV | 3.627%
Fresno | CA | 93705-1233 |  | 2013-07-31 | 2013-07-31 17:00 | 2013-07-31 17:47 | RUUD - UNK | 80 | -5.6 | Yes | Yes | 23.8 | 20.2 | 3.6 | 52610E149EE540AA9E6127F84EE1C4A8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Selma | CA | 93662-9023 |  | 2013-07-30 | 2013-07-30 16:19 | 2013-07-30 16:50 | CARRIER - UNK | 66 | 13.1 | Yes | Yes | 20.6 | 21.5 | -0.9 | C1A0473B76A5435BBCD2E454C06DF315 |  | R22 | Non-TXV |  | 19.85% | 0.80152 | 38.14% | [5 empty] | Non-TXV | 19.85%
Bakersfield | CA | 93301-5808 |  | 2013-09-10 | 2013-09-10 17:38 | 2013-09-10 17:38 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | 69F72ABD2BF1492EA46E6A3465A0031D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-1225 |  | 2013-08-12 | 2013-08-12 14:02 | 2013-08-12 14:02 | HEIL - H4A442GKA100 | 236 | 0 | Yes | Yes | 20.6 | 16.1 | 4.5 | 2F9CA0C7DACC4C41925B4F57C1027579 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-10 | 2013-09-10 17:09 | 2013-09-10 17:09 | CARRIER - 24ABR324A320 | 74 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | B95BD2F5918B432A85057BD56D3BA2C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9764 |  | 2013-09-17 | 2013-09-17 10:45 | 2013-09-17 11:12 | TRANE - YCC036F1M0BK | 85 | 19.8 | Yes | Yes | 19.7 | 19.9 | -0.2 | 78922A9C816643299BB245778B117E43 |  | R22 | Non-TXV |  | 23.29% | 0.76706 | 44.77% | [5 empty] | Non-TXV | 23.29%
Fresno | CA | 93725-1261 |  | 2013-08-09 | 2013-08-09 11:37 | 2013-08-09 11:37 | CARRIER - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 85A94D6A8BAD4D87B899CBB497439B6A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2013 |  | 2013-08-01 | 2013-08-01 10:54 | 2013-08-01 11:14 | DAY & NIGHT - 585B042100YACR | 89 | 2.8 | Yes | Yes | 27.9 | 22.1 | 5.8 | 4BF81B745F4A451B99F46E386B7693B8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.146% | 0.96854 | 6.046% | [5 empty] | Non-TXV | 3.146%
Hayward | CA | 94544-6301 |  | 2013-09-11 | 2013-09-11 12:13 | 2013-09-11 12:13 | COLEMAN - AC036X1021A | 63 | 0 | Yes | Yes | 19.3 | 17.4 | 1.9 | D08C0FC5B2E14C0F80E54019A1ED9E3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94089-4611 |  | 2013-10-03 | 2013-10-03 14:23 | 2013-10-03 15:23 | CARRIER - UCS36 1B | 71 | 3.4 | Yes | Yes | 20.7 | 21 | -0.3 | FACBC5F5FFD54AB09DEF54AC2C66D5E4 |  | R22 | Non-TXV |  | 4.789% | 0.95211 | 9.203% | [5 empty] | Non-TXV | 4.789%
Fresno | CA | 93704-6129 |  | 2013-07-23 | 2013-07-23 13:23 | 2013-07-23 14:04 | ICP - PGD336060K001C1 | 102 | 3.7 | Yes | Yes | 19.8 | 18.5 | 1.3 | 7DD623735DC84EA1BEFE79B1BBD82368 |  | R410A | TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | TXV | 3.627%
Bakersfield | CA | 93301-5808 |  | 2013-09-10 | 2013-09-10 18:19 | 2013-09-10 18:19 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 86CB048907154F38A5CED4A0FAC85A43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-9793 |  | 2013-09-03 | 2013-09-03 21:23 | 2013-09-03 21:26 | TEMPSTAR - POAD361K3 | 78 | -4 | Yes | Yes | 23.8 | 20.9 | 2.9 | 6CFB1AAC45084AB19F934F4D6127C95D |  | R22 | Non-TXV |  | -5.128% | 1.0513 | 1.436% |  |  |  |  | Non-TXV |  |  | -5.128%
Mc Farland | CA | 93250-9793 |  | 2013-09-03 | 2013-09-03 21:32 | 2013-09-03 21:33 | AMERICAN STANDARD - WCH036B1A | 152 | -8.4 | Yes | Yes | 26 | 22.1 | 3.9 | F6A88951A409475F91A7EC8A78570214 |  | R22 | TXV |  | -5.526% | 1.0553 | 1.548% |  |  |  |  | TXV |  |  | -5.526%
Mc Farland | CA | 93250-9793 |  | 2013-09-03 | 2013-09-03 21:38 | 2013-09-03 21:41 | RHEEM - N/A | 85 | 5.8 | Yes | Yes | 19.4 | 20.9 | -1.5 | CEE66CCB464A46C7B3269D519D1C2FE0 |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
San Jose | CA | 95125-1816 |  | 2013-08-12 | 2013-08-12 14:34 | 2013-08-15 12:03 | TRANE - TTP042D100A0 | 139 | 6.6 | Yes | Yes | 21.1 | 15.8 | 5.3 | FEE8C73450AA4A9DBF670F881319D4CC |  | R22 | Non-TXV |  | 4.748% | 0.95252 | 9.125% | [5 empty] | Non-TXV | 4.748%
Vacaville | CA | 95687-7847 |  | 2013-08-09 | 2013-08-09 09:19 | 2013-08-09 09:20 | OTHER - 563CN042-B | 132 | 4.1 | Yes | Yes | 17.5 | 17.6 | -0.1 | 9EA864AE134D446291129712DD4C833F |  | R22 | Non-TXV |  | 3.106% | 0.96894 | 5.969% | [5 empty] | Non-TXV | 3.106%
Fresno | CA | 93710-4516 |  | 2013-07-24 | 2013-07-24 14:40 | 2013-07-24 15:14 | LENNOX - 13ACD04223002 | 111 | 7.6 | Yes | Yes | 20 | 19 | 1 | C20A754980FE4331B63F873FB4030F17 |  | R22 | Non-TXV |  | 6.847% | 0.93153 | 13.16% | [5 empty] | Non-TXV | 6.847%
San Jose | CA | 95127-1555 |  | 2013-10-09 | 2013-10-09 11:49 | 2013-10-09 12:24 | BDP - 538ANX036000B | 84 | -5.9 | Yes | Yes | 21.1 | 19.5 | 1.6 | 71592EC4A6AB4410AFDB482A09764822 |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Vacaville | CA | 95687-3458 |  | 2013-08-15 | 2013-08-15 10:10 | 2013-08-15 11:11 | TRANE - 2TTR3048A1000AA | 142 | 4.8 | Yes | Yes | 11.9 | 14.7 | -2.8 | 324EC4C7EEF64367A44E1E08FCCA0249 |  | R22 | Non-TXV |  | 3.38% | 0.9662 | 6.496% | [5 empty] | Non-TXV | 3.38%
Vacaville | CA | 95687-3301 |  | 2013-08-09 | 2013-08-09 10:32 | 2013-08-09 10:34 | GE - BTN936A100B2 | 144 | -13.6 | Yes | Yes | 17 | 17.7 | -0.7 | A9D64DA134A443F582AFF04F689855F7 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Bakersfield | CA | 93301-5808 |  | 2013-09-10 | 2013-09-10 18:00 | 2013-09-10 18:00 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 1A186A69CBCE40AA9A8BF7AD342C194A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 16:41 | 2013-09-11 16:58 | CARRIER - 24AB2324A320 | 72 | 9.3 | Yes | Yes | 22.2 | 22.1 | 0.1 | 4038F83B63A24C118CC171B2EC26E430 |  | R22 | Non-TXV |  | 12.92% | 0.87083 | 24.82% | [5 empty] | Non-TXV | 12.92%
Anderson | CA | 96007-8236 |  | 2013-09-04 | 2013-09-04 10:47 | 2013-09-04 11:19 | GOODMAN - GPH1536M41AA | 181 | 8 | Yes | Yes | 20.4 | 19.8 | 0.6 | 3331EB31759F4F7A802BF6CFD3D5021F |  | R410A | Non-TXV |  | 4.42% | 0.9558 | 8.494% | [5 empty] | Non-TXV | 4.42%
Santa Rosa | CA | 95403-8961 |  | 2013-09-16 | 2013-09-16 10:52 | 2013-09-16 10:54 | CARRIER - 38TH048310 | 116 | -9.6 | Yes | Yes | 17.3 | 17.3 | 0 | 4052216311834E7D9E200EEB69E9B0BA |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Fresno | CA | 93728-3010 |  | 2013-07-22 | 2013-07-22 10:34 | 2013-07-22 10:52 | CARRIER - 48DL002-8 | 46 | 1.5 | Yes | Yes | 18.3 | 14.7 | 3.6 | C70D704865AE4E3A9D1ED77E478EF014 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Bakersfield | CA | 93306-1559 |  | 2013-10-15 | 2013-10-15 17:53 | 2013-10-15 17:53 | BDP - UKN | 90 | 0 | Yes | Yes | 19.8 | 22.7 | -2.9 | 775448948DC248C2B73D3C82E474D43F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 16:18 | 2013-09-11 16:18 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | D5441091AEAD4364B06D30F0CDE23650 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1140 |  | 2013-08-22 | 2013-08-22 13:38 | 2013-08-22 13:38 | OTHER - 80AW36406 | 112 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 6CB851E811BB47189DABE7B1509CE380 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-3366 |  | 2013-09-16 | 2013-09-16 13:49 | 2013-09-16 14:26 | CARRIER - 384G02400 | 70 | -6.6 | Yes | Yes | 18 | 20.4 | -2.4 | 02D23599B88445048D440DDB65806032 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Bakersfield | CA | 93309-5742 |  | 2013-08-23 | 2013-08-23 11:08 | 2013-08-23 11:08 | GOODMAN - GSX130361DA | 77 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 36B33187577F4F40815F740B05C2A57A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8411 |  | 2013-08-22 | 2013-08-22 09:42 | 2013-08-22 09:42 | YORK - DBYZ-F042N080A | 144 | 0 | Yes | Yes | 21.7 | 21.2 | 0.5 | 2FBB6EEDCED0430CAE29B1628CBD7646 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6302 |  | 2013-08-21 | 2013-08-21 14:10 | 2013-08-21 14:10 | RHEEM - RACA-036ABQ | 85 | 0 | Yes | Yes | 18.1 | 16.6 | 1.5 | 8E0717D7161443D49FFB40F02DDE68CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-2452 |  | 2013-09-26 | 2013-09-26 10:19 | 2013-09-26 10:50 | CARRIER - 38CKC0422300 | 88 | 6 | Yes | Yes | 18.9 | 21.1 | -2.2 | D6CD32027EBF478E96714DFBB286CC15 |  | R22 | Non-TXV |  | 6.818% | 0.93182 | 13.1% | [5 empty] | Non-TXV | 6.818%
Bakersfield | CA | 93313-3726 |  | 2013-10-14 | 2013-10-14 15:17 | 2013-10-14 15:17 | COLEMAN - 9541B901 | 57 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | C713518FA35E4465BE2E62FDCFE40BEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4616 |  | 2013-08-06 | 2013-08-06 19:44 | 2013-08-06 19:44 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 20.8 | 20.9 | -0.1 | 1C425D03450E480CBF58435298A681EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4616 |  | 2013-08-06 | 2013-08-06 19:25 | 2013-08-06 19:25 | BRYANT - 561CJX01800AEAA | 51 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | CE0C9E5D74B1426B86CAA60AAFA429FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2021 |  | 2013-07-17 | 2013-07-17 11:46 | 2013-07-17 11:59 | GOODMAN - GPG13480701AC | 145 | -13.6 | Yes | Yes | 23.3 | 19.5 | 3.8 | 5D92892153C746B1AA9A1B1DDBF84E5E |  | R22 | Non-TXV |  | -9.379% | 1.0938 | 2.627% |  |  |  |  | Non-TXV |  |  | -9.379%
Shafter | CA | 93263-2906 |  | 2013-08-05 | 2013-08-05 10:36 | 2013-08-05 19:20 | HEIL - GPCM042K080I | 85 | 17.6 | Yes | Yes | 19.8 | 20.4 | -0.6 | 1C689773EEFF432881946E58A2A3874C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.71% | 0.79294 | 39.79% | [5 empty] | Non-TXV | 20.71%
Bakersfield | CA | 93307-1797 |  | 2013-10-24 | 2013-10-24 18:13 | 2013-10-24 18:13 | GOODMAN - GPG10300701A | 50 | 0 | Yes | Yes | 20.7 | 20.7 | 0 | BA11DE2C902A49929CEAE563FAAA3D89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5102 |  | 2013-08-21 | 2013-08-21 09:44 | 2013-08-21 09:45 | RHEEM - RAJC-024JAS | 72 | -6.8 | Yes | Yes | 16.8 | 17.6 | -0.8 | 2F52A3521BCE4B9BA5050601B3E3AEF2 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Vallejo | CA | 94591-8359 |  | 2013-10-02 | 2013-10-02 11:12 | 2013-10-02 14:26 | ICP - TCA048AKA1 | 123 | 5.2 | Yes | Yes | 13 | 15.8 | -2.8 | 4B1AB186F7024CF9978451B533F1ADDB |  | R22 | Non-TXV |  | 4.228% | 0.95772 | 8.125% | [5 empty] | Non-TXV | 4.228%
Pittsburg | CA | 94565-4136 |  | 2013-08-27 | 2013-08-27 09:54 | 2013-08-27 09:55 | CARRIER - 38CKC036350 | 70 | -6.6 | Yes | Yes | 17.3 | 17.9 | -0.6 | 9DB4D516F01446AD8159BF9B248BDDB8 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Bakersfield | CA | 93307-1797 |  | 2013-10-24 | 2013-10-24 17:23 | 2013-10-24 17:23 | GOODMAN - GPG10300701A | 50 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | 7DEAC8C0738944D09663F2698C43AD08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4501 |  | 2013-08-27 | 2013-08-27 08:43 | 2013-08-27 08:45 | CARRIER - 38TR036300 | 132 | 16.1 | Yes | Yes | 16 | 16.4 | -0.4 | 0C473804C7C94094BC8E4B0506150BB5 |  | R22 | Non-TXV |  | 12.2% | 0.87803 | 23.44% | [5 empty] | Non-TXV | 12.2%
Bakersfield | CA | 93304-4835 |  | 2013-08-15 | 2013-08-15 12:17 | 2013-08-15 14:35 | RHEEM - RRNA-B036JK6X | 85 | 3.6 | Yes | Yes | 17.9 | 20.9 | -3 | 9721ECA91BF0440D97A345F9769D0B37 |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Suisun City | CA | 94585-2824 |  | 2013-08-08 | 2013-08-08 14:28 | 2013-08-08 15:18 | GOODMAN - CK24-1B | 71 | 2.2 | Yes | Yes | 15.5 | 18.3 | -2.8 | 68D7CE09CEE6482E997DD588CE7DE7FB |  | R22 | Non-TXV |  | 3.099% | 0.96901 | 5.955% | [5 empty] | Non-TXV | 3.099%
Shafter | CA | 93263-3510 |  | 2013-08-06 | 2013-08-06 19:33 | 2013-08-06 19:37 | GOODMAN - PGB0420751A | 68 | 3.5 | Yes | Yes | 21.2 | 22.1 | -0.9 | 55A1D287356E4FD9982EF2DAA9E883E8 |  | R22 | Non-TXV |  | 5.147% | 0.94853 | 9.892% | [5 empty] | Non-TXV | 5.147%
Davis | CA | 95618-7808 |  | 2013-08-14 | 2013-08-14 09:30 | 2013-08-14 09:30 | YORK - AC024X1021A | 59 | 0 | Yes | Yes | 15 | 17.9 | -2.9 | 415D7786AE454545A78A3DD28ED0E8F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-1155 |  | 2013-10-21 | 2013-10-21 17:13 | 2013-10-21 17:41 | CARRIER - 24ABB330A300 | 64 | 10.5 | Yes | Yes | 15.2 | 17.2 | -2 | 9DBA5CB910DC458398F687448DE8053D |  | R410A | TXV |  | 16.41% | 0.83594 | 31.53% | [5 empty] | TXV | 16.41%
Davis | CA | 95618-7807 |  | 2013-08-13 | 2013-08-13 11:07 | 2013-08-13 11:29 | YORK - AC024X1021A | 59 | 4.3 | Yes | Yes | 15.5 | 17.6 | -2.1 | 77ADC5C87BFE4B629B91194A6DDEAF9E |  | R22 | Non-TXV |  | 7.288% | 0.92712 | 14.01% | [5 empty] | Non-TXV | 7.288%
Napa | CA | 94559-2058 |  | 2013-09-11 | 2013-09-11 09:21 | 2013-09-11 09:24 | CARRIER - 38CKC018340 | 50 | 2.1 | Yes | Yes | 15.3 | 17.4 | -2.1 | D43A77E0AF90448C9DB04B76EE000C93 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Bakersfield | CA | 93308-2973 |  | 2013-08-28 | 2013-08-28 14:17 | 2013-08-28 14:17 | OTHER - CTG024GTA | 90 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | B6A423C87DE3488D84E61D535CA3F3F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4702 |  | 2013-08-23 | 2013-08-23 08:20 | 2013-08-23 08:49 | YORK - DAYP042N08080A | 150 | 17.9 | Yes | Yes | 22.2 | 21.5 | 0.7 | B9DC0BED45B6408F82E52EAA64418B1F |  | R22 | Non-TXV |  | 11.93% | 0.88067 | 22.93% | [5 empty] | Non-TXV | 11.93%
Bakersfield | CA | 93309-4617 |  | 2013-08-06 | 2013-08-06 16:05 | 2013-08-06 16:05 | BDP - UKN | 90 | 0 | Yes | Yes | 20.8 | 21 | -0.2 | A8F3829229D84A66AB091F034892D7E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1905 |  | 2013-08-06 | 2013-08-06 19:26 | 2013-08-06 19:29 | TEMPSTAR - PGAD36D1K3 | 78 | 8 | Yes | Yes | 23.4 | 21 | 2.4 | 1A27B80743BB48F9A7E12806FF775D8B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.26% | 0.89744 | 19.71% | [5 empty] | Non-TXV | 10.26%
Bakersfield | CA | 93309-4780 |  | 2013-08-22 | 2013-08-22 10:53 | 2013-08-22 10:53 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 063F4576B1844FBDB4E2C304ADA5110E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1186 |  | 2013-09-20 | 2013-09-20 17:59 | 2013-09-20 18:01 | OTHER - AC5030A2A1 | 69 | 2.8 | Yes | Yes | 23.7 | 21.5 | 2.2 | 6B0615BCF8454DC4B225BDA9541A847C |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Bakersfield | CA | 93309-4684 |  | 2013-08-06 | 2013-08-06 17:31 | 2013-08-06 17:31 | GOODMAN - CKL18 | 72 | 0 | Yes | Yes | 22.2 | 22.1 | 0.1 | 5D3C90A8BD8549F89BB748C4EAF1D7E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-9778 |  | 2013-09-17 | 2013-09-17 18:45 | 2013-09-17 18:45 | YORK - D1NH048N06506C | 128 | 0 | Yes | Yes | 26.8 | 20.7 | 6.1 | 26921668C5CF4AA98DB5553B48C70F8E | Add refrigerant: 9.3 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7645 |  | 2013-09-19 | 2013-09-19 09:25 | 2013-09-19 09:47 | PAYNE - 567C036RCU | 67 | 11.1 | Yes | Yes | 17.5 | 17.6 | -0.1 | A49C07C327D6451BA74E1205B5F666AE |  | R22 | Non-TXV |  | 16.57% | 0.83433 | 31.84% | [5 empty] | Non-TXV | 16.57%
San Jose | CA | 95133-2302 |  | 2013-10-21 | 2013-10-21 14:49 | 2013-10-21 15:16 | UNITARY PRODUCTS GROUP - TCGD42S21S1HA | 72 | 3.1 | Yes | Yes | 18.7 | 21.3 | -2.6 | AECBF666E9C84A18A1667894BF35E209 |  | R22 | Non-TXV |  | 4.306% | 0.95694 | 8.274% | [5 empty] | Non-TXV | 4.306%
Fairfield | CA | 94534-4315 |  | 2013-09-19 | 2013-09-19 13:08 | 2013-09-19 13:09 | TRANE - 2TTR3036A1000AA | 101 | 3.7 | Yes | Yes | 14.1 | 15.7 | -1.6 | F5FA43874C5E422CAE4F448118D3C39A |  | R22 | Non-TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | Non-TXV | 3.663%
Bakersfield | CA | 93309-5761 |  | 2013-08-20 | 2013-08-20 15:54 | 2013-08-20 15:54 | ICP - PGF036K060B | 71 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 8D977C02258B43E9B4F91D2B4EA05135 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-7828 |  | 2013-09-27 | 2013-09-27 11:36 | 2013-09-27 12:24 | GOODMAN - CK421C | 87 | 3.4 | Yes | Yes | 21.6 | 20.6 | 1 | F1C089139A334306B69AFAB5E1894154 |  | R22 | Non-TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | Non-TXV | 3.908%
Bakersfield | CA | 93301-5808 |  | 2013-09-10 | 2013-09-10 18:37 | 2013-09-10 18:37 | CARRIER - 24ABR32A320 | 72 | 0 | Yes | Yes | 22.3 | 20.9 | 1.4 | D6418E2EC5E44B4AB0989FF6A529FEA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7085 |  | 2013-09-20 | 2013-09-20 14:29 | 2013-09-20 14:29 | OTHER - UNK | 85 | 0 | Yes | Yes | 20.6 | 16.6 | 4 | C97DCC1CBF1C40A386BF6D8F5FC43B09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5379 |  | 2013-10-10 | 2013-10-10 14:57 | 2013-10-10 14:57 | ICP - UKN | 90 | 0 | Yes | Yes | 20.6 | 21.4 | -0.8 | 61DDF582A72445AEB7188E945AA142EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9812 |  | 2013-10-21 | 2013-10-21 12:06 | 2013-10-21 12:24 | YORK - H2RC042S06HG | 109 | 9.3 | Yes | Yes | 21.2 | 20.4 | 0.8 | C4C71C2E94334C12850A754D0889AEE7 |  | R22 | Non-TXV |  | 8.532% | 0.91468 | 16.4% | [5 empty] | Non-TXV | 8.532%
Bakersfield | CA | 93309-4640 |  | 2013-08-06 | 2013-08-06 18:23 | 2013-08-06 18:23 | GOODMAN - UKN | 90 | 0 | Yes | Yes | 22.1 | 20.4 | 1.7 | 67560A3C99294F8298D8F073AB79C742 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2509 |  | 2013-09-05 | 2013-09-05 12:09 | 2013-09-05 12:12 | COPELAND - ZRCF36U01E | 107 | 14.9 | Yes | Yes | 16.9 | 17.6 | -0.7 | AF06AE95EFD141A5AF00C0451AF36EB3 |  | R22 | Non-TXV |  | 13.93% | 0.86075 | 26.76% | [5 empty] | Non-TXV | 13.93%
Bakersfield | CA | 93309-4685 |  | 2013-08-06 | 2013-08-06 19:12 | 2013-08-06 19:12 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 21.9 | 21.3 | 0.6 | AA626DEACD7046A589139CF464F1880D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4684 |  | 2013-08-06 | 2013-08-06 17:52 | 2013-08-06 17:52 | BDP - 567C018RCU | 40 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | B6DD229021AF4475A1308528AEA3025A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 19:11 | 2013-09-11 19:11 | CARRIER - 24AB324A320 | 72 | 0 | Yes | Yes | 22.4 | 21.2 | 1.3 | 701EFF94B5B74D439DC04FE87570043F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7608 |  | 2013-09-20 | 2013-09-20 13:07 | 2013-09-20 15:42 | CARRIER - 38CKC042300 | 80 | 2.8 | Yes | Yes | 19.4 | 22 | -2.6 | D9DCEDF9CB8946D1A315C97510E5DDCF |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Bakersfield | CA | 93309-5790 |  | 2013-08-22 | 2013-08-22 19:49 | 2013-08-22 19:49 | ICP - PGC036K0G0B | 71 | 0 | Yes | Yes | 21.8 | 21.2 | 0.6 | 588D6EC0810E4B24933C3BC28DCBE3D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4687 |  | 2013-08-06 | 2013-08-06 17:00 | 2013-08-06 17:00 | CARRIER - UKN | 90 | 0 | Yes | Yes | 21.2 | 19.5 | 1.7 | C0702F79F10447D693D5892F794715AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-10 | 2013-09-10 19:37 | 2013-09-10 19:37 | CARRIER - 24ABR32A320 | 72 | 0 | Yes | Yes | 22.7 | 21.2 | 1.5 | 377DF3AF797C41FA87C0B22A04DE150C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4376 |  | 2013-08-21 | 2013-08-21 14:11 | 2013-08-21 14:50 | CARRIER - 38CK036330 | 74 | 3.3 | Yes | Yes | 14.4 | 17.7 | -3.3 | 5E9C8874925C43EEB13961475AA189DA |  | R22 | Non-TXV |  | 4.459% | 0.95541 | 8.57% | [5 empty] | Non-TXV | 4.459%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 18:49 | 2013-09-11 18:49 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | E7C10D068BE2460D96FD5BFF7D2E5C07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4685 |  | 2013-08-06 | 2013-08-06 18:17 | 2013-08-06 18:17 | YORK - H4DB02406A | 58 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | F92B166084C64F7EB6454B856AE6103B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4680 |  | 2013-08-05 | 2013-08-05 18:46 | 2013-08-05 18:46 | ICP - NACC24KA5 | 79 | 0 | Yes | Yes | 22.2 | 21.4 | 0.8 | 098B562DC7E14228803832E5F653282D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3349 |  | 2013-08-21 | 2013-08-21 11:06 | 2013-08-21 14:58 | GE - | 85 | -8 | Yes | Yes | 15.8 | 18.8 | -3 | B67EA67F804141508CCCF33E1FF2FFE6 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Wasco | CA | 93280-1236 |  | 2013-08-13 | 2013-08-13 17:29 | 2013-08-13 17:32 | GOODMAN - SSX140601AE | 274 | 10.2 | Yes | Yes | 22.3 | 19.9 | 2.4 | BC0EA4338FC34406BC8029347D2F0B74 |  | R22 | Non-TXV |  | 3.723% | 0.96277 | 7.154% | [5 empty] | Non-TXV | 3.723%
Shafter | CA | 93263-0000 |  | 2013-08-12 | 2013-08-12 21:14 | 2013-08-12 21:20 | GOODMAN - PGB030050-1B | 56 | 6.5 | Yes | Yes | 18.9 | 19.4 | -0.5 | 73C7B1B0B04B4AE8957822A3D78D12BB |  | R22 | Non-TXV |  | 11.61% | 0.88393 | 22.31% | [5 empty] | Non-TXV | 11.61%
Fairfield | CA | 94533-5012 |  | 2013-09-24 | 2013-09-24 10:00 | 2013-09-24 10:00 | RHEEM - | 85 | 0 | Yes | Yes | 17.6 | 20.4 | -2.8 | 74050421D5BB4BDB8A86E2386BB8017A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2813 |  | 2013-08-02 | 2013-08-02 09:54 | 2013-08-02 12:43 | ARMSTRONG - 2SHP13LB118P-1 | 85 | 3 | Yes | Yes | 12.2 | 15 | -2.8 | A8AA82BF09F94BEEACFDE692CD52CC98 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
San Jose | CA | 95111-3097 |  | 2013-08-14 | 2013-08-14 10:25 | 2013-08-14 10:26 | COLEMAN - 7842-901 | 108 | 5.9 | Yes | Yes | 17 | 17.6 | -0.6 | BDF7F890125441C8A37D7C55433921E2 |  | R22 | Non-TXV |  | 5.463% | 0.94537 | 10.5% | [5 empty] | Non-TXV | 5.463%
Bakersfield | CA | 93309-8400 |  | 2013-09-05 | 2013-09-05 19:49 | 2013-09-05 19:52 | DAY & NIGHT - N/A | 85 | -7 | Yes | Yes | 24.1 | 21 | 3.1 | 3DA19B34A1074C30A32D5C6F51124295 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 17:17 | 2013-09-11 17:34 | CARRIER - 24ABR324A320 | 72 | 8.4 | Yes | Yes | 22.1 | 21.5 | 0.6 | E190E31E60284B81B51A623FB9C1D23F |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Pittsburg | CA | 94565-6201 |  | 2013-08-27 | 2013-08-27 10:27 | 2013-08-27 10:27 | ALLEGIANCE - 2A7A1036A1000AA | 73 | 0 | Yes | Yes | 18.7 | 17 | 1.7 | A806214AADDE48FA8C15FFF5F198A43C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1330 |  | 2013-10-19 | 2013-10-19 12:11 | 2013-10-19 12:39 | ICP - CA535VKD2 | 82 | 6.4 | Yes | Yes | 24.8 | 19.1 | 5.8 | 16C2A933E67A4BFD88E6255ACC1FDCDE |  | R22 | Non-TXV |  | 7.805% | 0.92195 | 15% | [5 empty] | Non-TXV | 7.805%
Fairfield | CA | 94533-3286 |  | 2013-09-20 | 2013-09-20 13:08 | 2013-09-20 13:35 | BDP - 5410J018 | 52 | 3.4 | Yes | Yes | 23.1 | 18.5 | 4.6 | 9E60DFC0C11E4B0EA474ECF4D7546D2A |  | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 15:33 | 2013-09-11 15:33 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 21.7 | 20.9 | 0.8 | FFA4A377859846DEB3BB2437B4C2DF9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9435 |  | 2013-10-04 | 2013-10-04 18:15 | 2013-10-04 18:15 | RUUD - UAMB 042JAZ | 96 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | C1438A4F9ABC4D76BA8AEFA98FA48DD1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-7250 |  | 2013-10-23 | 2013-10-23 14:52 | 2013-10-23 16:00 | RHEEM - ILLEGIBLE | 95 | -8.9 | Yes | Yes | 20.7 | 19.3 | 1.4 | 0E81CA51013E4C199E74F132BA99D2B0 |  | R22 | Non-TXV |  | -9.368% | 1.0937 | 2.624% |  |  |  |  | Non-TXV |  |  | -9.368%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 19:51 | 2013-09-11 19:51 | CARRIER - 24ABR24A20 | 72 | 0 | Yes | Yes | 21.2 | 20.9 | 0.3 | 67ACED43BFF94D5AA277A84A6214978F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6010 |  | 2013-09-25 | 2013-09-25 12:17 | 2013-09-25 12:51 | CONCORD - RPG10B42D075CA-8A | 73 | 5.9 | Yes | Yes | 22.9 | 22.1 | 0.8 | 5E51DC87309F4FD3B6C0E36056CA7109 |  | R22 | Non-TXV |  | 8.082% | 0.91918 | 15.53% | [5 empty] | Non-TXV | 8.082%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 19:29 | 2013-09-11 19:29 | CARRIER - 24B324A320 | 72 | 0 | Yes | Yes | 21.7 | 21.8 | -0.1 | FCA8A3B9B19E4976BEA89538DF4206E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2344 |  | 2013-08-10 | 2013-08-10 14:06 | 2013-08-10 14:28 | RHEEM - RAMB-042JAZ | 96 | 13.9 | Yes | Yes | 22.1 | 21.5 | 0.6 | 2BF706FB19714BA7A0A943364522D3CB |  | R22 | Non-TXV |  | 14.48% | 0.85521 | 27.83% | [5 empty] | Non-TXV | 14.48%
Bakersfield | CA | 93306-6162 |  | 2013-08-15 | 2013-08-15 13:19 | 2013-08-15 13:19 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 74A5002BCBDA43229FD1D8044D7A23CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4447 |  | 2013-08-27 | 2013-08-27 09:35 | 2013-08-27 09:37 | CARRIER - 38CKC030340 | 68 | 2.7 | Yes | Yes | 18.4 | 17.3 | 1.1 | 581CD0D65D564327AA35D0F4E82D1EAD |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Fresno | CA | 93705-3419 |  | 2013-08-23 | 2013-08-23 09:28 | 2013-08-23 10:07 | DAY & NIGHT - UNK | 70 | 7.1 | Yes | Yes | 17.8 | 19.9 | -2.1 | 425246A577F04FD1BFBA066F0F9BEC0A |  | R22 | Non-TXV |  | 10.14% | 0.89857 | 19.49% | [5 empty] | Non-TXV | 10.14%
Fairfield | CA | 94533-4162 |  | 2013-08-02 | 2013-08-02 11:24 | 2013-08-02 11:24 | KENMORE - TCA042AKA1 | 98 | 0 | Yes | Yes | 15 | 17.7 | -2.7 | FBDF82F5195743EB8B760B1169276D86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7235 |  | 2013-08-16 | 2013-08-16 10:42 | 2013-08-16 15:16 | PAYNE - UKN | 85 | -8 | Yes | Yes | 15.7 | 17.6 | -1.9 | BE0BAA5F469E47E3885D793DB6D4D130 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Shafter | CA | 93263-3531 |  | 2013-08-06 | 2013-08-06 19:20 | 2013-08-06 19:24 | BRYANT - PGB0300501B | 56 | 2.2 | Yes | Yes | 22.5 | 19.4 | 3.1 | AFC38FBA90FB4E13AC47C977972573AA |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Pleasanton | CA | 94566-4641 |  | 2013-09-13 | 2013-09-13 08:51 | 2013-09-13 09:29 | RHEEM - RAHE-048JAS | 85 | 5.5 | Yes | Yes | 21.6 | 15.9 | 5.7 | C1D140480C5B4ECE959E5C67B70D6BF1 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Davis | CA | 95618-7812 |  | 2013-08-13 | 2013-08-13 10:38 | 2013-08-13 11:04 | YORK - AC024X1021A | 59 | 7.8 | Yes | Yes | 15.5 | 17 | -1.5 | 83BAB77EAFB044C9B9FC2C4C4AFBFE67 |  | R22 | Non-TXV |  | 13.22% | 0.8678 | 25.41% | [5 empty] | Non-TXV | 13.22%
Pittsburg | CA | 94565-4355 |  | 2013-10-02 | 2013-10-02 09:56 | 2013-10-02 09:57 | GE - NA | 72 | 2.6 | Yes | Yes | 16.2 | 15.5 | 0.7 | AF97F66302214C42900A21ADE814D349 |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Fairfield | CA | 94534-3455 |  | 2013-08-07 | 2013-08-07 08:57 | 2013-08-07 09:17 | TRANE - 4TTX4048B1000AA | 127 | 4.9 | Yes | Yes | 14.4 | 14.4 | 0 | C665660A1E944213A398E31F69D01264 |  | R22 | Non-TXV |  | 3.858% | 0.96142 | 7.415% | [5 empty] | Non-TXV | 3.858%
Lamont | CA | 93241-2225 |  | 2013-08-15 | 2013-08-15 12:37 | 2013-08-15 12:39 | DAY & NIGHT - 580ANW036060AAAF | 85 | 3.7 | Yes | Yes | 18.2 | 19.8 | -1.6 | 49BA83900AF043E9AD66BC12C77F3E85 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Fairfield | CA | 94533-3927 |  | 2013-08-09 | 2013-08-09 11:14 | 2013-08-09 11:17 | CARRIER - 38TRA036330 | 100 | -8.2 | Yes | Yes | 17.6 | 16.3 | 1.3 | 804AA061D6294608B244803DE2A8F3B7 |  | R22 | Non-TXV |  | -8.2% | 1.082 | 2.296% |  |  |  |  | Non-TXV |  |  | -8.2%
Gilroy | CA | 95020-9103 |  | 2013-09-04 | 2013-09-04 11:10 | 2013-09-04 11:10 | CARRIER - 113ANA048-E | 85 | 0 | Yes | Yes | 21.3 | 18.2 | 3.1 | F9835F6D277C404CA5140958498E8366 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 15:09 | 2013-09-11 15:09 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 3C221FC12D9148CDA1B5EC38EA19FE60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2733 |  | 2013-08-19 | 2013-08-19 09:46 | 2013-08-19 09:48 | RUUD - NA | 66 | 4.9 | Yes | Yes | 16.5 | 17.6 | -1.1 | 7EF42AF10C5E41638D4319DFD0693785 |  | R22 | Non-TXV |  | 7.424% | 0.92576 | 14.27% | [5 empty] | Non-TXV | 7.424%
Fresno | CA | 93705-3318 |  | 2013-08-23 | 2013-08-23 12:30 | 2013-08-23 12:49 | RHEEM - RRNAB024JK06X | 70 | 3.6 | Yes | Yes | 22.5 | 21.2 | 1.3 | 90AF04C8A1844FC9AEF222C45CCF9E4C |  | R22 | Non-TXV |  | 5.143% | 0.94857 | 9.883% | [5 empty] | Non-TXV | 5.143%
Willits | CA | 95490-5704 |  | 2013-08-21 | 2013-08-21 08:52 | 2013-08-21 09:47 | TRANE - TTH048D100A0 | 129 | 5.5 | Yes | Yes | 22.5 | 19.2 | 3.3 | CCC4A1025FC24D758E75FAD3D45798D1 |  | R22 | Non-TXV |  | 4.264% | 0.95736 | 8.194% | [5 empty] | Non-TXV | 4.264%
Bakersfield | CA | 93313-5281 |  | 2013-10-10 | 2013-10-10 12:46 | 2013-10-10 12:46 | YORK - H2RD048S06B | 134 | 0 | Yes | Yes | 20.8 | 22.6 | -1.8 | BF57E38F74B54FE2AFAB7A8B9C9A8239 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7601 |  | 2013-08-07 | 2013-08-07 21:55 | 2013-08-07 21:58 | YORK - D1NH042N06506G | 94 | 3.1 | Yes | Yes | 27 | 21.1 | 6 | 8ED205C8B5C24CF088821AAAC7970736 |  | R22 | Non-TXV |  | 3.298% | 0.96702 | 6.338% | [5 empty] | Non-TXV | 3.298%
Antioch | CA | 94509-4835 |  | 2013-08-12 | 2013-08-12 10:35 | 2013-08-12 10:40 | TEMPSTAR - PGD336060K001C1 | 100 | -5.9 | Yes | Yes | 16.3 | 16.4 | -0.1 | D891E58F95C74E578EF78B207CF66DF0 |  | R410A | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Bakersfield | CA | 93312-2224 |  | 2013-08-16 | 2013-08-16 11:54 | 2013-08-16 11:54 | RHEEM - RRGG05N24JKR | 42 | 0 | Yes | Yes | 22.3 | 22.6 | -0.3 | 5AB96974829143A48FAF5D7D2C8666EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2241 |  | 2013-09-18 | 2013-09-18 11:45 | 2013-09-18 11:45 | PAYNE - PY1PNB0360ABAA | 85 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | 0C6F7FAF763B4C178A99EC152C5076C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2241 |  | 2013-09-18 | 2013-09-18 11:57 | 2013-09-18 11:57 | PAYNE - PY1PNB0360ABAA | 85 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | F9B3805BB4D248C0BF541A341870E1FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2224 |  | 2013-08-16 | 2013-08-16 12:18 | 2013-08-16 12:18 | RHEEM - RRGG-05N24JKR | 85 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | 9602EDEE01704A42B01CFBD0591AA803 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1797 |  | 2013-10-24 | 2013-10-24 17:39 | 2013-10-24 17:39 | GOODMAN - GPG10300701A | 50 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | E5DFC0E70905468FA4078A125522FA27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6313 |  | 2013-08-15 | 2013-08-15 09:44 | 2013-08-15 09:44 | AMERICAN STANDARD - YCC024F1L0BE | 64 | 0 | Yes | Yes | 16.9 | 18.8 | -1.9 | 20FB905FCDCC4E4D8EB6B17DD0379B0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6313 |  | 2013-08-16 | 2013-08-16 10:04 | 2013-08-16 10:04 | CARRIER - 588ANW030080ABAD | 85 | 0 | Yes | Yes | 16.8 | 18.5 | -1.7 | D58AD42EF6CA418D82DB2D9091D33FC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3537 |  | 2013-09-19 | 2013-09-19 18:54 | 2013-09-19 18:56 | GOODMAN - GPG13300451AA | 77 | 2.3 | Yes | Yes | 26.6 | 22.6 | 4 | 393E2FB4B3D14505A9ADB22A8FEA46F3 |  | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Vacaville | CA | 95687-5126 |  | 2013-08-15 | 2013-08-15 10:32 | 2013-08-15 10:32 | YORK - | 85 | 0 | Yes | Yes | 13.3 | 15.9 | -2.6 | 0B90446FDA5346F0A6798FD421F96F49 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7330 |  | 2013-08-09 | 2013-08-09 18:13 | 2013-08-09 18:13 | RHEEM - UKN | 85 | 0 | Yes | Yes | 21.6 | 20.9 | 0.7 | FE3F96A935CB4935B8716A9D4EAC1FD3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-6912 |  | 2013-10-01 | 2013-10-01 16:49 | 2013-10-01 19:02 | PAYNE - PGAA10060 | 115 | 5.9 | Yes | Yes | 21.2 | 20.4 | 0.8 | 1855C1D9450C451291B2C9E48D4C0EA0 |  | R22 | Non-TXV |  | 5.13% | 0.9487 | 9.86% | [5 empty] | Non-TXV | 5.13%
Bakersfield | CA | 93309-3631 |  | 2013-08-22 | 2013-08-22 08:10 | 2013-08-22 08:35 | RHEEM - RRNL-- B042JK08X | 85 | 4.2 | Yes | Yes | 18 | 21 | -3 | 83C7B030DB5B470DB795189A22AF431B |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 15:37 | 2013-09-11 16:01 | CARRIER - 24ABR324A3 | 72 | 7.8 | Yes | Yes | 22.2 | 20.9 | 1.3 | 8B42A6DCA81741E6943E1E4E452BCA48 |  | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 17:51 | 2013-09-11 17:51 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 38170FA9ABDD434888707A0A74FE2D73 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 18:15 | 2013-09-11 18:15 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 22 | 21.8 | 0.2 | 9D84D6611CFC437FAF7BEE8F61444531 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2825 |  | 2013-08-11 | 2013-08-11 12:52 | 2013-08-11 13:17 | WEATHER KING - 13AJA60A01 | 191 | 25.7 | Yes | Yes | 25.4 | 20.4 | 5 | 2FD838E0BEFB4A7D826BC535B2CBCE86 |  | R22 | Non-TXV |  | 13.46% | 0.86545 | 25.86% | [5 empty] | Non-TXV | 13.46%
Livermore | CA | 94550-5202 |  | 2013-09-13 | 2013-09-13 11:49 | 2013-09-13 14:50 | AMERICAN STANDARD - 2A7A2060A1000AA | 125 | 3.9 | Yes | Yes | 14.8 | 16.8 | -2 | 2F901A30436C45BB90614FEC12623C19 |  | R22 | Non-TXV |  | 3.12% | 0.9688 | 5.996% | [5 empty] | Non-TXV | 3.12%
Bakersfield | CA | 93301-5808 |  | 2013-09-10 | 2013-09-10 18:59 | 2013-09-10 19:16 | CARRIER - 24ABR324A320 | 72 | 8.5 | Yes | Yes | 22.1 | 20.9 | 1.2 | A82422B1E4EE4A33B87456BDE03CAE1E |  | R22 | Non-TXV |  | 11.81% | 0.88194 | 22.69% | [5 empty] | Non-TXV | 11.81%
Clovis | CA | 93611-1433 |  | 2013-08-16 | 2013-08-16 09:04 | 2013-08-16 09:24 | RHEEM - RRPL-B036JK06X | 92 | -5.4 | Yes | Yes | 19.3 | 19.3 | 0 | E3D5676F0B1B406381833B2B31414E17 |  | R410A | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Pittsburg | CA | 94565-5560 |  | 2013-08-28 | 2013-08-28 09:17 | 2013-08-28 09:18 | PAYNE - 5670036RCU | 67 | 16.5 | Yes | Yes | 15.1 | 15.7 | -0.6 | B2390D31E444477DADF1F3109BEAB4ED |  | R22 | Non-TXV |  | 24.63% | 0.75373 | 47.33% | [5 empty] | Non-TXV | 24.63%
Pittsburg | CA | 94565-4455 |  | 2013-08-28 | 2013-08-28 09:47 | 2013-08-28 09:47 | TEMPSTAR - N4A336AKB200 | 83 | 0 | Yes | Yes | 17.8 | 17 | 0.8 | EF5B2DFB1F9C40B19140E3D01940457B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4260 |  | 2013-08-28 | 2013-08-28 10:24 | 2013-08-28 10:25 | OTHER - 561AJ036-C | 70 | -5.8 | Yes | Yes | 18 | 17 | 1 | 2F87E9F4727D44F58BF67D3887AF7B84 |  | R22 | Non-TXV |  | -8.286% | 1.0829 | 2.32% |  |  |  |  | Non-TXV |  |  | -8.286%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 14:40 | 2013-09-11 14:40 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | 10AEA54BFB4F48BB9096A305CBEB5F22 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5808 |  | 2013-09-11 | 2013-09-11 18:17 | 2013-09-11 18:17 | CARRIER - 24ABR324A320 | 72 | 0 | Yes | Yes | 21.5 | 20.9 | 0.6 | F1D7D509620847CBB2408AC150B1F310 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7113 |  | 2013-09-18 | 2013-09-18 12:41 | 2013-09-18 12:41 | YORK - AC042X1221A | 107 | 0 | Yes | Yes | 21.6 | 22.1 | -0.5 | 1FEBB8CB7C6A4F42ABDE836143AD7B39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5713 |  | 2013-08-20 | 2013-08-20 15:20 | 2013-08-20 15:20 | RHEEM - RRPL-B036JK08X | 92 | 0 | Yes | Yes | 21.3 | 21.8 | -0.5 | 018CF91D9FD04EC5B09E08E4BAAC304D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2523 |  | 2013-08-30 | 2013-08-30 17:50 | 2013-08-30 17:50 | RHEEM - N/A | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 64240A82A6F84FC084FEE95CC0258485 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1722 |  | 2013-08-11 | 2013-08-11 08:47 | 2013-08-11 09:18 | PAYNE - PY2PNB048090ABAA | 131 | -12.3 | Yes | Yes | 22.7 | 19.1 | 3.7 | FCD9AA95409845149F4EAE299C26F77C |  | R22 | Non-TXV |  | -9.389% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.389%
Shafter | CA | 93263-2201 |  | 2013-09-24 | 2013-09-24 19:23 | 2013-09-24 19:25 | TEMPSTAR - PGAA36C1K3 | 81 | -4.8 | Yes | Yes | 17.9 | 19.1 | -1.2 | 6753A8FB3BF04614BBD41D2A1B315CF1 |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Bakersfield | CA | 93307-5192 |  | 2013-08-07 | 2013-08-07 21:07 | 2013-08-07 21:07 | ICP - PGC036K060E | 68 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | 3959C9D3B55A489CAA2FDCC7180B2903 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1522 |  | 2013-08-12 | 2013-08-12 12:40 | 2013-08-12 14:49 | CARRIER - 38BRB030300 | 106 | 3.2 | Yes | Yes | 14.7 | 17.7 | -3 | D420D630A508447DA3540E042BC95B9A |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Bakersfield | CA | 93306-2344 |  | 2013-08-10 | 2013-08-10 14:58 | 2013-08-10 14:58 | YORK - HAMD-F048SA | 100 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 33C91F66EA9544D9B40E24DC7BF875EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4326 |  | 2013-08-12 | 2013-08-12 13:39 | 2013-08-12 14:50 | TRANE - TTR048C100A2 | 114 | 6 | Yes | Yes | 9.6 | 12.2 | -2.6 | 14333CC7B2044A9FAB08AE8B9FF93552 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Vallejo | CA | 94589-1708 |  | 2013-09-19 | 2013-09-19 11:48 | 2013-09-19 11:48 | BRYANT - 38CKC036330 | 105 | 0 | Yes | Yes | 22 | 16.9 | 5.1 | B101E136029F4A4BB5FA13F25C09D454 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1441 |  | 2013-10-17 | 2013-10-17 08:48 | 2013-10-17 09:24 | RHEEM - RRNL-B048JK08X | 161 | -15.2 | Yes | Yes | 21.4 | 20.1 | 1.3 | AC269B465A7741C4886DFAF609AE2492 |  | R410A | Non-TXV |  | -9.441% | 1.0944 | 2.644% |  |  |  |  | Non-TXV |  |  | -9.441%
Bay Point | CA | 94565-6675 |  | 2013-09-10 | 2013-09-10 10:50 | 2013-09-10 10:50 | BRYANT - 661CJ018-E | 68 | 3.7 | Yes | Yes | 18.1 | 18.2 | -0.1 | E02FA0564A094DAE9F13ACF9857C9742 |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Gilroy | CA | 95020-9630 |  | 2013-10-23 | 2013-10-23 10:56 | 2013-10-23 11:27 | CARRIER - 38CKC060370 | 134 | 10.1 | Yes | Yes | 21.2 | 21.2 | 0 | 2FAE14BDE86F4F5A941DAA00972177F2 |  | R22 | Non-TXV |  | 7.537% | 0.92463 | 14.49% | [5 empty] | Non-TXV | 7.537%
Pittsburg | CA | 94565-2640 |  | 2013-08-28 | 2013-08-28 11:21 | 2013-08-28 11:21 | RHEEM - AT-38B1 0 | 45 | 4.5 | Yes | Yes | 17.5 | 17.3 | 0.2 | F7B7CC7C969841389B351C7E46FC1898 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Davis | CA | 95616-1035 |  | 2013-08-13 | 2013-08-13 12:33 | 2013-08-13 13:22 | LENNOX - 13ACX--0240230-12 | 70 | 2.6 | Yes | Yes | 16.1 | 19 | -2.9 | 1B9922DEA2E941A99208CF94C41DA114 |  | R410A | TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | TXV | 3.714%
San Jose | CA | 95111-3097 |  | 2013-08-14 | 2013-08-14 09:50 | 2013-08-14 09:52 | SEARS - NA | 74 | -7 | Yes | Yes | 19.1 | 17.9 | 1.2 | D6237B9FA7DB493B9E22E454010AA31A |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Davis | CA | 95618-7808 |  | 2013-09-26 | 2013-09-26 13:44 | 2013-09-26 15:44 | UNITARY PRODUCTS GROUP - AC024X1021A | 59 | 2.2 | Yes | Yes | 14.4 | 16.8 | -2.4 | 55DE1CF37BA745569EE278F22B71F58E |  | R22 | Non-TXV |  | 3.729% | 0.96271 | 7.166% | [5 empty] | Non-TXV | 3.729%
Fresno | CA | 93702-1629 |  | 2013-08-08 | 2013-08-08 11:16 | 2013-08-08 12:03 | WHIRLPOOL - HWA30480K | 83 | 4.9 | Yes | Yes | 19.4 | 19.3 | 0.1 | 0C4344A0C5594940836B8D79C64EB92E |  | R22 | Non-TXV |  | 5.904% | 0.94096 | 11.35% | [5 empty] | Non-TXV | 5.904%
Fresno | CA | 93727-3669 |  | 2013-08-07 | 2013-08-07 16:58 | 2013-08-07 16:58 | LENNOX - 10GCS03675 | 58 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 3DD82A4CF0014050A90D3507CA7BB012 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-9527 |  | 2013-10-03 | 2013-10-03 13:44 | 2013-10-03 13:44 | OTHER - UNK | 70 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 42A6B691573A4FE09F686C7C3571AE86 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2662 |  | 2013-08-07 | 2013-08-07 14:05 | 2013-08-07 14:46 | PAYNE - PA10JA042-B | 85 | 3.5 | Yes | Yes | 27.7 | 22.1 | 5.6 | AEB80ECC53B84FB8A9440054C4757F71 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93309-4640 |  | 2013-08-26 | 2013-08-26 17:29 | 2013-08-26 17:47 | BDP - 567C018RCU | 65 | 9.7 | Yes | Yes | 21.9 | 21.5 | 0.4 | 4512EC9F09EE4993B6F9A7A0F5F733A5 |  | R22 | Non-TXV |  | 14.92% | 0.85077 | 28.68% | [5 empty] | Non-TXV | 14.92%
Lemoore | CA | 93245-9170 |  | 2013-08-02 | 2013-08-02 15:38 | 2013-08-02 15:38 | LENNOX - 13ACD03623002 | 85 | 0 | Yes | Yes | 21.5 | 19.8 | 1.7 | FE8026388D5B4249A9400F58B97297A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-9170 |  | 2013-08-02 | 2013-08-02 15:42 | 2013-08-02 16:13 | LENNOX - 13ACD03623002 | 111 | 12.4 | Yes | Yes | 19.9 | 18.1 | 1.8 | ED46B2FBF9B9467B8914509210CA7F79 |  | R22 | Non-TXV |  | 11.17% | 0.88829 | 21.47% | [5 empty] | Non-TXV | 11.17%
Bakersfield | CA | 93309-4640 |  | 2013-08-26 | 2013-08-26 18:15 | 2013-08-26 18:15 | BDP - 567C018RCU | 65 | 0 | Yes | Yes | 21.8 | 21.4 | 0.4 | 2011AD58FC7044FAB59DEFDB516E053F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2958 |  | 2013-09-26 | 2013-09-26 15:22 | 2013-09-26 15:42 | TRANE - 2TTX4036B1000AA | 118 | 4.5 | Yes | Yes | 14.3 | 14.4 | -0.1 | 25996D1B8A9B4605B0072022A3A9702C |  | R22 | Non-TXV |  | 3.814% | 0.96186 | 7.329% | [5 empty] | Non-TXV | 3.814%
Bakersfield | CA | 93309-4686 |  | 2013-08-26 | 2013-08-26 17:01 | 2013-08-26 17:01 | OTHER - UKN | 60 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | 1C8BB7AAEE9F44B3A56D9A6766064BE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2851 |  | 2013-10-14 | 2013-10-14 12:05 | 2013-10-14 12:19 | YORK - D4NZ0606506N | 82 | 6.3 | Yes | Yes | 22.5 | 21.5 | 1 | E392479569B245EC8F7A7241404958A0 |  | R410A | Non-TXV |  | 7.683% | 0.92317 | 14.76% | [5 empty] | Non-TXV | 7.683%
Bakersfield | CA | 93308-1091 |  | 2013-09-18 | 2013-09-18 10:16 | 2013-09-18 10:16 | AMANA - PGD36C0702E | 111 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | 8BD8522DD09040208176F1A346C772A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3437 |  | 2013-10-01 | 2013-10-01 13:49 | 2013-10-01 15:25 | COMFORT AIRE - UNK | 131 | 12.7 | Yes | Yes | 19.8 | 21 | -1.2 | 0C7FD009CEC642C99F8292A3B108B0C6 |  | R22 | Non-TXV |  | 9.695% | 0.90305 | 18.63% | [5 empty] | Non-TXV | 9.695%
Bakersfield | CA | 93309-5751 |  | 2013-08-22 | 2013-08-22 17:23 | 2013-08-22 17:23 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22.7 | 21.5 | 1.2 | 508EE27715D449708B191E20181E776F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5751 |  | 2013-08-22 | 2013-08-22 17:25 | 2013-08-22 17:25 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | 8083B03A82554826B3B2CCDBD74E476B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3398 |  | 2013-08-16 | 2013-08-16 11:50 | 2013-08-16 16:26 | - | 73 | -6.2 | Yes | Yes | 28 | 22 | 6 | BB03EDFC24C94DF89C3632F740D92854 |  | R22 | TXV |  | -8.493% | 1.0849 | 2.378% |  |  |  |  | TXV |  |  | -8.493%
Concord | CA | 94519-1514 |  | 2013-09-05 | 2013-09-05 13:34 | 2013-09-05 13:35 | LENNOX - 12GCS048X-100-4PA | 167 | 5.4 | Yes | Yes | 17 | 17.6 | -0.6 | 9F4658CEEC2E49D8BCAE01AB62210F98 |  | R22 | Non-TXV |  | 3.234% | 0.96766 | 6.214% | [5 empty] | Non-TXV | 3.234%
Bakersfield | CA | 93304-6348 |  | 2013-08-09 | 2013-08-09 15:13 | 2013-08-09 15:13 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.8 | 21.4 | 0.4 | 38544E3156B942B49BE7ACC4580D6FE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6910 |  | 2013-08-09 | 2013-08-09 11:14 | 2013-08-09 12:30 | CARRIER - 38BR036300 | 113 | 9 | Yes | Yes | 18.9 | 19.9 | -1 | 129042EC101D40C68363B2EB862334B6 |  | R22 | Non-TXV |  | 7.965% | 0.92035 | 15.31% | [5 empty] | Non-TXV | 7.965%
Fresno | CA | 93726-4510 |  | 2013-08-23 | 2013-08-23 11:31 | 2013-08-23 11:57 | AMERICAN STANDARD - YCZ036F1M0BD | 82 | 3.7 | Yes | Yes | 25.1 | 20.4 | 4.7 | 719761C78E0E4F13B341B03DE967A58C |  | R22 | Non-TXV |  | 4.512% | 0.95488 | 8.671% | [5 empty] | Non-TXV | 4.512%
Pittsburg | CA | 94565-5555 |  | 2013-09-20 | 2013-09-20 13:38 | 2013-09-20 14:07 | ICP - N4A330AKC200 | 74 | 3 | Yes | Yes | 18.7 | 17.7 | 1 | 5C79DDD1952B4056802BF138AC1334CE |  | R22 | Non-TXV |  | 4.054% | 0.95946 | 7.791% | [5 empty] | Non-TXV | 4.054%
San Jose | CA | 95121-1033 |  | 2013-09-18 | 2013-09-18 13:44 | 2013-09-18 14:11 | TRANE - TTY036B100AD | 170 | 5.8 | Yes | Yes | 19.6 | 20.1 | -0.5 | 6A50209A45DF49918C96510371962D6A |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Pittsburg | CA | 94565-5555 |  | 2013-08-28 | 2013-08-28 10:48 | 2013-08-28 10:50 | RUUD - UAKB-024JAZ | 56 | 2.7 | Yes | Yes | 17.4 | 17.6 | -0.2 | 1788650A2C6F43C783965CD3124EE5BF |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Fresno | CA | 93702-3513 |  | 2013-08-09 | 2013-08-09 10:41 | 2013-08-09 11:26 | AMERICAN STANDARD - YCC030F1M0BH | 80 | 4.1 | Yes | Yes | 19.8 | 19.3 | 0.5 | 9A57518FAD254F4190D034721A795261 |  | R22 | Non-TXV |  | 5.125% | 0.94875 | 9.849% | [5 empty] | Non-TXV | 5.125%
Bakersfield | CA | 93308-5020 |  | 2013-08-14 | 2013-08-14 10:01 | 2013-08-14 10:01 | PAYNE - 1604E05859 | 100 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 443FD11061DC4B73A3AA485CEE4BE672 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4512 |  | 2013-09-05 | 2013-09-05 21:39 | 2013-09-05 21:45 | AMERICAN STANDARD - YCX036F1M0AD | 114 | 8.9 | Yes | Yes | 22 | 21 | 1 | A4575304BE2147F3B8FF892DC8DADD97 |  | R22 | Non-TXV |  | 7.807% | 0.92193 | 15% | [5 empty] | Non-TXV | 7.807%
Fresno | CA | 93722-2916 |  | 2013-08-14 | 2013-08-14 17:41 | 2013-08-14 17:41 | OTHER - UKN | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 5F389012302D4C2495D105A7DB5A4473 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3683 |  | 2013-08-14 | 2013-08-14 17:42 | 2013-08-14 17:42 | OTHER - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | B91C99AED0614B70BB9B87FD85C7F47A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2429 |  | 2013-10-22 | 2013-10-22 23:01 | 2013-10-22 23:01 | OTHER - 4095E9409 | 80 | 0 | Yes | Yes | 14.1 | 15.1 | -1 | 77C50C925EAE423488F167E038955C9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5264 |  | 2013-10-13 | 2013-10-13 14:04 | 2013-10-13 14:07 | OTHER - H2RD048S06B | 134 | 0 | Yes | Yes | 23.4 | 20.4 | 3 | EB1533F9F8864C648F2B72FCB111B1DB |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5521 |  | 2013-08-02 | 2013-08-02 00:49 | 2013-08-02 00:49 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | BF9133AF9CD5406C97140A941CD710D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-8020 |  | 2013-10-22 | 2013-10-22 17:44 | 2013-10-22 17:44 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 23.4 | 21.5 | 1.9 | DD8F68D3ABD5407FA3A532160BFD2AFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5437 |  | 2013-08-05 | 2013-08-05 14:32 | 2013-08-05 14:32 | PAYNE - PA13NR030-H | 66 | 0 | Yes | Yes | 15 | 18 | -3 | D923CF001D3C4B13883826CEDF218139 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4542 |  | 2013-08-07 | 2013-08-07 11:51 | 2013-08-07 12:28 | OTHER - PGC036K060B | 71 | -5 | Yes | Yes | 19.5 | 19.9 | -0.3 | FCEBFB7DAD7F456C9E04E10D9EFE12BA |  | R22 | Non-TXV |  | -7.042% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.042%
Bakersfield | CA | 93312-4965 |  | 2013-09-26 | 2013-09-26 15:37 | 2013-09-26 15:37 | RHEEM - RAND-042JAZ | 136 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | BE421D4EBC084BC683C9925CEA0960A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8104 |  | 2013-09-25 | 2013-09-25 10:37 | 2013-09-25 12:08 | CARRIER - 38TH036300 | 117 | 6.1 | Yes | Yes | 20.2 | 16.5 | 3.7 | 89C310EBB59241C9BED6D8D51B37285B |  | R22 | Non-TXV |  | 5.214% | 0.94786 | 10.02% | [5 empty] | Non-TXV | 5.214%
Bakersfield | CA | 93313-4268 |  | 2013-08-09 | 2013-08-09 10:57 | 2013-08-09 11:42 | GOODMAN - PGB036050-1A REV A | 60 | 8.8 | Yes | Yes | 27 | 23.6 | 3.4 | 3FDE8739273A4248A25A2A7039FBA261 |  | R22 | Non-TXV |  | 14.67% | 0.85333 | 28.19% | [5 empty] | Non-TXV | 14.67%
Bakersfield | CA | 93313-3388 |  | 2013-10-14 | 2013-10-14 13:08 | 2013-10-14 13:08 | RUUD - UKN | 90 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 572253CFC80441C09A2BAA8C521BCA76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3146 |  | 2013-08-07 | 2013-08-07 09:57 | 2013-08-07 09:57 | TRANE - 4YCY4036B1075AA | 118 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | CEE91D6841974A6F84C1C402421FB263 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8616 |  | 2013-08-12 | 2013-08-12 10:07 | 2013-08-12 10:09 | CARRIER - 38CKC048370 | 100 | -7.1 | Yes | Yes | 16 | 16.7 | -0.6 | 2FBE830392BD4454B484E29C7516BCA3 |  | R22 | Non-TXV |  | -7.1% | 1.071 | 1.988% |  |  |  |  | Non-TXV |  |  | -7.1%
San Jose | CA | 95121-1034 |  | 2013-09-18 | 2013-09-18 12:38 | 2013-09-18 13:43 | RUUD - UNK | 88 | -6.2 | Yes | Yes | 19.6 | 21 | -1.4 | 606D41649B91419E8A6F7EB50AB91D51 |  | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Bakersfield | CA | 93312-6486 |  | 2013-10-01 | 2013-10-01 14:52 | 2013-10-01 14:52 | CARRIER - 38CK036351 | 70 | 0 | Yes | Yes | 21.2 | 21.4 | -0.2 | 5418888183F04B5E83AE040F009D01C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6340 |  | 2013-09-20 | 2013-09-20 10:02 | 2013-09-20 10:41 | RHEEM - | 85 | 5.9 | Yes | Yes | 16.5 | 19.2 | -2.7 | F7668C98C60F402DA8BC86E2BB3FD048 |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
San Jose | CA | 95111-3097 |  | 2013-08-14 | 2013-08-14 10:57 | 2013-08-14 10:59 | COLEMAN - NA | 72 | 4.5 | Yes | Yes | 18.6 | 17.6 | 1 | A2715D49BD194353A8CF7A55ACB6FA00 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Vallejo | CA | 94589-2661 |  | 2013-08-19 | 2013-08-19 09:32 | 2013-08-19 09:32 | TRANE - | 85 | 0 | Yes | Yes | 15.5 | 18.3 | -2.8 | EAF168F13A804FEC844EB661BE677528 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1063 |  | 2013-09-11 | 2013-09-11 13:43 | 2013-09-11 13:43 | TRANE - YCC036F1M0BG | 83 | 0 | Yes | Yes | 17.8 | 17.9 | -0.1 | 74B30792842B48478E686F84A4FB12CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6245 |  | 2013-08-12 | 2013-08-12 10:56 | 2013-08-12 10:59 | OTHER - 561J048-A | 102 | 10.6 | Yes | Yes | 16.1 | 16.4 | -0.3 | 151DAFB64DEB4D71808E30255ADABEB8 |  | R22 | Non-TXV |  | 10.39% | 0.89608 | 19.97% | [5 empty] | Non-TXV | 10.39%
Wasco | CA | 93280-2420 |  | 2013-08-13 | 2013-08-13 17:40 | 2013-08-13 17:42 | DAY & NIGHT - 588ANW042060AAAG | 84 | 2.9 | Yes | Yes | 23.2 | 20.4 | 2.8 | 4300ADD3705C4551993563C14B965264 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Suisun City | CA | 94585-3230 |  | 2013-08-08 | 2013-08-08 12:05 | 2013-08-08 14:20 | PAYNE - 561AJX030000AAAA | 68 | 3.5 | Yes | Yes | 14.9 | 16.5 | -1.6 | 86636C97801740F5988BA12E12BCFAB4 |  | R22 | Non-TXV |  | 5.147% | 0.94853 | 9.892% | [5 empty] | Non-TXV | 5.147%
Fresno | CA | 93727-5674 |  | 2013-08-07 | 2013-08-07 13:50 | 2013-08-07 14:10 | CARRIER - UNK | 85 | 5.3 | Yes | Yes | 20 | 19 | 1 | E2F71A6B405E4162BBD281CC77D49B60 |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Davis | CA | 95616-3601 |  | 2013-08-13 | 2013-08-13 13:24 | 2013-08-13 13:24 | LENNOX - HS26-030-4P | 75 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 62E2B70B515943B2BB2646DF6DAA631F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94089-4611 |  | 2013-10-03 | 2013-10-03 13:06 | 2013-10-03 13:26 | ARMSTRONG - UNK | 84 | 5 | Yes | Yes | 20.5 | 21 | -0.5 | 7DD380CEF47E422C900A798578AEE7B6 |  | R22 | Non-TXV |  | 5.952% | 0.94048 | 11.44% | [5 empty] | Non-TXV | 5.952%
Vallejo | CA | 94591-8357 |  | 2013-08-12 | 2013-08-12 11:30 | 2013-08-12 14:46 | CARRIER - 38CKC030340 | 68 | 3.5 | Yes | Yes | 19.9 | 19.1 | 0.8 | 094E242A2E4E4B738A80077723ACE49D |  | R22 | Non-TXV |  | 5.147% | 0.94853 | 9.892% | [5 empty] | Non-TXV | 5.147%
Fresno | CA | 93726-4521 |  | 2013-08-13 | 2013-08-13 13:18 | 2013-08-13 14:07 | YORK - DAYPF036N070A | 108 | 4.4 | Yes | Yes | 23.6 | 20.2 | 3.5 | 522BF8AEFD1A4B0FBE6550863517AD6C |  | R22 | TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | TXV | 4.074%
Vallejo | CA | 94589-1811 |  | 2013-08-12 | 2013-08-12 11:59 | 2013-08-12 14:48 | BRYANT - 561CJ042-E | 80 | -4.6 | Yes | Yes | 14.9 | 15.9 | -1 | 0C22C24CFB0640CDA19B4DF04CE85A1A |  | R22 | Non-TXV |  | -5.75% | 1.0575 | 1.61% |  |  |  |  | Non-TXV |  |  | -5.75%
Bakersfield | CA | 93309-4533 |  | 2013-08-22 | 2013-08-22 16:29 | 2013-08-22 16:29 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 21.6 | 21.8 | -0.2 | 10028847279D418798B4CC1E19A3FC35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4664 |  | 2013-08-15 | 2013-08-15 16:07 | 2013-08-15 16:07 | CARRIER - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D8EBA36752D34ED18DC5B9A3D985FC73 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4004 |  | 2013-08-20 | 2013-08-20 19:49 | 2013-08-20 19:51 | YORK - D1NP030N05606A | 73 | -3.9 | Yes | Yes | 22.2 | 20.1 | 2.1 | 79348DB9AD1144BC87A286B8EF676C4B |  | R22 | TXV |  | -5.342% | 1.0534 | 1.496% |  |  |  |  | TXV |  |  | -5.342%
Fresno | CA | 93727-6522 |  | 2013-08-07 | 2013-08-07 12:29 | 2013-08-07 12:51 | CARRIER - 585GJW48080ABAF | 86 | 5.1 | Yes | Yes | 24.3 | 20.8 | 3.5 | 25A3C83B17B54162AF2787A01481F5C8 |  | R22 | Non-TXV |  | 5.93% | 0.9407 | 11.4% | [5 empty] | Non-TXV | 5.93%
Bakersfield | CA | 93313-5277 |  | 2013-08-09 | 2013-08-09 09:23 | 2013-08-09 10:18 | YORK - H2RD042S06B | 141 | 14.8 | Yes | Yes | 19.5 | 17.7 | 1.8 | 233758F568BF45E78720E770FFF0EE8E |  | R22 | TXV |  | 10.5% | 0.89504 | 20.17% | [5 empty] | TXV | 10.5%
Bakersfield | CA | 93313-5277 |  | 2013-08-09 | 2013-08-09 09:39 | 2013-08-09 10:17 | YORK - H2RD036S06B | 96 | 12 | Yes | Yes | 22.5 | 16.7 | 5.9 | 070C10AB6F8A4FDB95105BDA13565512 |  | R22 | TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | TXV | 12.5%
Bakersfield | CA | 93306-5457 |  | 2013-08-08 | 2013-08-08 11:59 | 2013-08-08 12:37 | GOODMAN - GPG1342090M41AD | 85 | 2.5 | Yes | Yes | 24.1 | 18.3 | 5.8 | B2A6D955F7E14082851779B7AA79862D |  | R410A | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93727-5861 |  | 2013-08-07 | 2013-08-07 09:00 | 2013-08-07 09:19 | LENNOX - UNK | 111 | 13.6 | Yes | Yes | 21.5 | 19.5 | 2 | DB1FE0E523E54BB6AB962EA2A0775383 |  | R22 | Non-TXV |  | 12.25% | 0.87748 | 23.55% | [5 empty] | Non-TXV | 12.25%
Fresno | CA | 93711-2657 |  | 2013-09-06 | 2013-09-06 17:22 | 2013-09-06 18:05 | PAYNE - PA13NR030K | 66 | 2 | Yes | Yes | 19.8 | 19.3 | 0.5 | A6C1F467A13F4A68AC0C3EA71EAB5147 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Clovis | CA | 93611-8168 |  | 2013-08-08 | 2013-08-08 14:21 | 2013-08-08 14:39 | LENNOX - 12GCS060-X-100-4PA | 159 | -11.2 | Yes | Yes | 20 | 19.9 | 0.1 | 90B200DD79F843CFA212C930CEF3C22C |  | R22 | Non-TXV |  | -7.044% | 1.0704 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.044%
Clovis | CA | 93612-2471 |  | 2013-08-22 | 2013-08-22 15:00 | 2013-08-22 15:00 | OTHER - UKN | 70 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 9C75DD6ADE434562BFC52FF78BFE047C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4001 |  | 2013-09-05 | 2013-09-05 10:38 | 2013-09-05 10:39 | GOODMAN - CE36-1GB | 79 | 8.8 | Yes | Yes | 17.1 | 17.6 | -0.5 | 3F7C7D518DAE4D9B9AB57A69421D4C14 |  | R22 | Non-TXV |  | 11.14% | 0.88861 | 21.41% | [5 empty] | Non-TXV | 11.14%
Fresno | CA | 93710-6106 |  | 2013-09-06 | 2013-09-06 09:44 | 2013-09-06 10:12 | OTHER - 21SC-21 | 62 | 11.5 | Yes | Yes | 16.2 | 18.6 | -2.4 | 7F2EE1B5E6B048FC85946FB291973F32 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.55% | 0.81452 | 35.65% | [5 empty] | Non-TXV | 18.55%
Fresno | CA | 93727-6597 |  | 2013-08-07 | 2013-08-07 14:10 | 2013-08-07 14:30 | LENNOX - UNK | 111 | 4.7 | Yes | Yes | 17.8 | 17.2 | 0.6 | C094784F0BB8499CA8D033B4910BFB22 |  | R22 | TXV |  | 4.234% | 0.95766 | 8.137% | [5 empty] | TXV | 4.234%
Vallejo | CA | 94589-3841 |  | 2013-08-06 | 2013-08-06 14:45 | 2013-08-06 14:45 | RHEEM - RAFD-036JS | 80 | 0 | Yes | Yes | 15.4 | 17.7 | -2.3 | 075FFD2A8D3D449A9807DDFC0447E143 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7026 |  | 2013-09-11 | 2013-09-11 12:46 | 2013-09-11 14:14 | ICP - CA5536VKD2 | 82 | 5.7 | Yes | Yes | 14.7 | 16.5 | -1.8 | E7182162414C4D2898A5B6A50EF8A361 |  | R22 | Non-TXV |  | 6.951% | 0.93049 | 13.36% | [5 empty] | Non-TXV | 6.951%
Bakersfield | CA | 93311-9198 |  | 2013-08-10 | 2013-08-10 11:18 | 2013-08-10 11:44 | YORK - H2RD060S06D | 162 | 13.7 | Yes | Yes | 26.8 | 21 | 5.8 | 8E7C1032DF23432B8D00434C6A3B40E4 |  | R22 | Non-TXV |  | 8.457% | 0.91543 | 16.25% | [5 empty] | Non-TXV | 8.457%
Sanger | CA | 93657-3617 |  | 2013-08-22 | 2013-08-22 14:31 | 2013-08-22 14:51 | CARRIER - 48GX036090301AD | 83 | 6.1 | Yes | Yes | 20.4 | 20.4 | 0 | D34C37F00B49433B9AEE90F77FC3B7BC |  | R22 | Non-TXV |  | 7.349% | 0.92651 | 14.12% | [5 empty] | Non-TXV | 7.349%
Sanger | CA | 93657-0000 |  | 2013-09-16 | 2013-09-16 09:52 | 2013-09-16 13:56 | LENNOX - 13ACD06023001 | 214 | 6.4 | Yes | Yes | 20.5 | 19.3 | 1.2 | 41471C6DE58E47AA91A5282DC209204A |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.747% | [5 empty] | Non-TXV | 2.991%
Milpitas | CA | 95035-6636 |  | 2013-09-27 | 2013-09-27 15:12 | 2013-09-27 15:29 | UNITARY PRODUCTS GROUP - 38HDC030331 | 115 | 3.5 | Yes | Yes | 20.6 | 20.2 | 0.5 | 5323354523554CB8BA94C88C288EBAC4 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Antioch | CA | 94509-6947 |  | 2013-08-23 | 2013-08-23 09:57 | 2013-08-23 09:59 | PAYNE - 591ANX048000ABAA | 112 | 10.6 | Yes | Yes | 17.4 | 17.6 | -0.2 | B106F5D482674CEE99677594EAFFB486 |  | R22 | Non-TXV |  | 9.464% | 0.90536 | 18.19% | [5 empty] | Non-TXV | 9.464%
Benicia | CA | 94510-2253 |  | 2013-08-13 | 2013-08-13 09:10 | 2013-08-13 09:12 | PAYNE - PA10JA042-B | 88 | 4.6 | Yes | Yes | 15.9 | 17.6 | -1.7 | F5ABC8AE6B0A4FD9BF34C4A5C7C0FD07 |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Bakersfield | CA | 93306-5549 |  | 2013-08-16 | 2013-08-16 10:53 | 2013-08-16 11:44 | RHEEM - RRKA-A036JK06X | 85 | 2.7 | Yes | Yes | 15.7 | 18.7 | -3 | 5E3D0AD138794319BB3ABDB607508F20 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Selma | CA | 93662-4117 |  | 2013-08-14 | 2013-08-14 08:31 | 2013-08-14 08:50 | CARRIER - UNK | 66 | 2.1 | Yes | Yes | 23.1 | 19.3 | 3.8 | 3C73CB737D8946F9846B6D7858BB8BDE |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Clovis | CA | 93612-2236 |  | 2013-08-08 | 2013-08-08 11:24 | 2013-08-08 11:51 | PAYNE - PY1PNB036060ABAA | 68 | 9.7 | Yes | Yes | 23.2 | 20.4 | 2.8 | 5EAB57BED45F43A9875EC2E658CB3F29 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.26% | 0.85735 | 27.41% | [5 empty] | Non-TXV | 14.26%
Clovis | CA | 93611-4565 |  | 2013-10-29 | 2013-10-29 11:42 | 2013-10-29 12:02 | ARCOAIRE - PGF030K060A | 52 | 1.5 | Yes | Yes | 24.4 | 20.6 | 3.8 | 697C43AD79F84F0987EA5698C4EB0B20 |  | R22 | Non-TXV |  | 2.885% | 0.97115 | 5.544% | [5 empty] | Non-TXV | 2.885%
Sanger | CA | 93657-9441 |  | 2013-08-12 | 2013-08-12 10:16 | 2013-08-12 10:47 | TRANE - TTB048C100A0 | 115 | 5.9 | Yes | Yes | 19.8 | 19.9 | -0.1 | 8D31EFDEC56E4C22B4045B7883F9BFA4 |  | R22 | Non-TXV |  | 5.13% | 0.9487 | 9.86% | [5 empty] | Non-TXV | 5.13%
Antioch | CA | 94509-6820 |  | 2013-08-15 | 2013-08-15 09:17 | 2013-08-15 09:20 | OTHER - BRC00481BD | 103 | 19.8 | Yes | Yes | 18.4 | 18.2 | 0.2 | 9F55855595294C738995F7AE730AB0E7 |  | R22 | Non-TXV |  | 19.22% | 0.80777 | 36.94% | [5 empty] | Non-TXV | 19.22%
Antioch | CA | 94509-2056 |  | 2013-09-26 | 2013-09-26 10:33 | 2013-09-26 10:35 | TRANE - 4TTR3048D1000AB | 109 | 4 | Yes | Yes | 19.3 | 17 | 2.3 | 01DFF8154886478CAA8AB0B7E977CEBE |  | R22 | Non-TXV |  | 3.67% | 0.9633 | 7.052% | [5 empty] | Non-TXV | 3.67%
Bakersfield | CA | 93313-9813 |  | 2013-08-08 | 2013-08-08 09:02 | 2013-08-08 09:34 | YORK - H2RC048S06HG | 119 | 33.3 | Yes | Yes | 26.2 | 20.8 | 5.4 | 48567C17B1494DBEB92CE5188DBECFE7 |  | R22 | Non-TXV |  | 27.98% | 0.72017 | 53.78% | [5 empty] | Non-TXV | 27.98%
Sanger | CA | 93657-3153 |  | 2013-08-12 | 2013-08-12 14:33 | 2013-08-12 15:26 | DAY & NIGHT - UNK | 53 | 15.6 | Yes | Yes | 19.3 | 20.9 | -1.6 | 2D8F8B87CB22472A9F166565A3F11C86 |  | R22 | Non-TXV |  | 29.43% | 0.70566 | 56.57% | [5 empty] | Non-TXV | 29.43%
Clovis | CA | 93612-2561 |  | 2013-08-12 | 2013-08-12 09:30 | 2013-08-12 10:33 | DAY & NIGHT - UNK | 80 | -5.6 | Yes | Yes | 22.7 | 20.4 | 2.3 | 6B18543F74F041A795366C014E4460FB |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Bakersfield | CA | 93309-0509 |  | 2013-08-07 | 2013-08-07 22:00 | 2013-08-07 22:02 | CARRIER - N/A | 85 | 5.1 | Yes | Yes | 26.7 | 22.1 | 4.6 | DDFF6F18786B4C9C99D98E30D3D5A06C |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Bakersfield | CA | 93309-2044 |  | 2013-08-07 | 2013-08-07 22:11 | 2013-08-07 22:13 | - | 113 | -6.2 | Yes | Yes | 19.2 | 21.9 | -2.7 | 0E0CF62A6E6245C0976460B663D205A3 |  | R22 | Non-TXV |  | -5.487% | 1.0549 | 1.537% |  |  |  |  | Non-TXV |  |  | -5.487%
Bakersfield | CA | 93312-6426 |  | 2013-08-17 | 2013-08-17 16:24 | 2013-08-17 16:54 | CARRIER - 38BR-C048305 | 167 | 24.2 | Yes | Yes | 21.4 | 21.5 | -0.1 | 7C58347AAB7A4B0485FBEA41A5914C79 |  | R22 | Non-TXV |  | 14.49% | 0.85509 | 27.85% | [5 empty] | Non-TXV | 14.49%
Bakersfield | CA | 93309-6909 |  | 2013-08-22 | 2013-08-22 18:07 | 2013-08-22 18:07 | PAYNE - PY1PNB036060ABAA | 68 | 0 | Yes | Yes | 21.8 | 22.1 | -0.3 | E5907D5C1BE741178E89E3984F2285ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-08-27 | 2013-08-27 19:50 | 2013-08-27 19:53 | OTHER - JS55D-036K | 138 | 6.2 | Yes | Yes | 21.7 | 22.1 | -0.4 | 6FA3E2183A334D90A42F433D1A83CB3F |  | R22 | TXV |  | 4.493% | 0.95507 | 8.634% | [5 empty] | TXV | 4.493%
Fresno | CA | 93711-1734 |  | 2013-08-23 | 2013-08-23 16:12 | 2013-08-23 16:32 | DAY & NIGHT - UNK | 70 | 3.9 | Yes | Yes | 21.7 | 23.6 | -1.9 | 13A36F02D72343C78DBA78923E46E6A4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.571% | 0.94429 | 10.71% | [5 empty] | Non-TXV | 5.571%
Fresno | CA | 93711-1734 |  | 2013-08-23 | 2013-08-23 16:34 | 2013-08-23 16:34 | DAY & NIGHT - UNK | 70 | 0 | Yes | Yes | 35 | 21 | 14 | 78A9C2D2EBEB435EBECBD450FB42FCEA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3153 |  | 2013-08-12 | 2013-08-12 13:58 | 2013-08-12 14:30 | BRYANT - 582ANW0240NAAD | 56 | 2.6 | Yes | Yes | 18.2 | 20.4 | -2.2 | A2602F7191E548888F28C2C4A053E092 |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Martinez | CA | 94553-6848 |  | 2013-08-13 | 2013-08-13 11:11 | 2013-08-13 11:12 | DAY & NIGHT - 585HJ018040 | 61 | 2.3 | Yes | Yes | 17.4 | 17.6 | -0.2 | 2A7B0DCF9348426F8E369FE1E6B04BFA |  | R22 | Non-TXV |  | 3.77% | 0.9623 | 7.246% | [5 empty] | Non-TXV | 3.77%
Clovis | CA | 93611-4567 |  | 2013-08-07 | 2013-08-07 15:51 | 2013-08-07 16:19 | BRYANT - 583ANW042060AAAF | 121 | 11 | Yes | Yes | 21.7 | 19.9 | 1.8 | 188DF4F54EAA430AA716C90B4EE8E4E7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.091% | 0.90909 | 17.47% | [5 empty] | Non-TXV | 9.091%
Bakersfield | CA | 93304-2027 |  | 2013-08-09 | 2013-08-09 09:39 | 2013-08-09 10:22 | YORK - D1NP036N05606A | 108 | 3.2 | Yes | Yes | 15 | 17.8 | -2.8 | 30807E0F61834D0EA1B2F5855F4DBC17 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93722-0429 |  | 2013-08-14 | 2013-08-14 17:42 | 2013-08-14 17:42 | OTHER - UKN | 78 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 20B2D2D21B1F41EEBA614EC5377C3A81 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3153 |  | 2013-08-12 | 2013-08-12 13:55 | 2013-08-12 13:55 | DAY & NIGHT - UNK | 56 | 0 | Yes | Yes | 35 | 21 | 14 | C54CB5C559AB4D3EA9461CDAC0AD71BE | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95138-1517 |  | 2013-10-17 | 2013-10-17 08:59 | 2013-10-17 10:37 | TRANE - 2TTR2024A1000AA | 80 | 3 | Yes | Yes | 18.5 | 21.2 | -2.7 | 068B782063F94BEEB51EA68B08B4D62F |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Pittsburg | CA | 94565-1923 |  | 2013-08-30 | 2013-08-30 08:48 | 2013-08-30 08:50 | WEATHER KING - 13AJA42A01 | 121 | 11.2 | Yes | Yes | 17.9 | 17.6 | 0.3 | DC91318F88994452B7A8A6F09B526526 |  | R22 | Non-TXV |  | 9.256% | 0.90744 | 17.79% | [5 empty] | Non-TXV | 9.256%
Vallejo | CA | 94589-2105 |  | 2013-08-19 | 2013-08-19 10:46 | 2013-08-19 15:12 | TRANE - TTX030C100A3 | 118 | 3.7 | Yes | Yes | 16.6 | 15.9 | 0.7 | DB21722FBDAD4E4AA2C807B9699DEB19 |  | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Fresno | CA | 93728-3626 |  | 2013-08-15 | 2013-08-15 15:00 | 2013-08-15 15:39 | LENNOX - 12GCS036X753PA | 110 | 6 | Yes | Yes | 20.7 | 21.4 | -0.7 | 4AFA619343F142A288206B02FAD682FE |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Fresno | CA | 93706-8931 |  | 2013-10-08 | 2013-10-08 09:44 | 2013-10-08 09:44 | GOODMAN - GPG12360701A | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 6603890177D742878EF931562BED2ACA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1955 |  | 2013-08-07 | 2013-08-07 10:10 | 2013-08-07 10:30 | OTHER - PGC036060E | 70 | 4.7 | Yes | Yes | 21.8 | 19.9 | 1.9 | 5F57ADE7522D42549551BD9D49B5CF92 |  | R22 | Non-TXV |  | 6.714% | 0.93286 | 12.9% | [5 empty] | Non-TXV | 6.714%
Bakersfield | CA | 93312-6274 |  | 2013-08-10 | 2013-08-10 16:48 | 2013-08-10 17:38 | YORK - HRC036S06HG | 83 | 11.8 | Yes | Yes | 25.8 | 21.8 | 4 | EE825E667D7A4C69BE6900A104E45F3B |  | R22 | Non-TXV |  | 14.22% | 0.85783 | 27.32% | [5 empty] | Non-TXV | 14.22%
Fresno | CA | 93704-4503 |  | 2013-08-24 | 2013-08-24 12:15 | 2013-08-24 12:38 | ARCOAIRE - UNK | 85 | 12.8 | Yes | Yes | 23.4 | 19.5 | 3.9 | AFFD1907D84248C79B5E4EAF5A9CB7D6 |  | R22 | Non-TXV |  | 15.06% | 0.84941 | 28.94% | [5 empty] | Non-TXV | 15.06%
Bakersfield | CA | 93311-9491 |  | 2013-10-24 | 2013-10-24 11:38 | 2013-10-24 11:38 | YORK - AC042X1221A | 107 | 0 | Yes | Yes | 21.5 | 21.4 | 0.1 | BC369F18E6BD4326B6BF25B65CE37F39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9491 |  | 2013-10-24 | 2013-10-24 12:08 | 2013-10-24 12:08 | YORK - AC036X1222A | 83 | 0 | Yes | Yes | 21 | 21.4 | -0.4 | 9FE0F3911F534AE9AD6F85A2347EC103 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-5539 |  | 2013-10-22 | 2013-10-22 16:30 | 2013-10-22 16:49 | NORDYNE - JS38A-036KA | 89 | -5.2 | Yes | Yes | 24.7 | 20.8 | 3.9 | 657F75D8BC45475F8FC80E8CBB41A1BE |  | R22 | Non-TXV |  | -5.843% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.843%
Vacaville | CA | 95688-8514 |  | 2013-08-28 | 2013-08-28 09:50 | 2013-08-28 09:50 | CARRIER - 38TH048320 | 128 | 0 | Yes | Yes | 17 | 19.2 | -2.2 | BD0C9BF2ABBF409886CA193C9EB7EE09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1839 |  | 2013-08-07 | 2013-08-07 14:18 | 2013-08-07 14:45 | RHEEM - 13AJA480A1757 | 87 | 5.9 | Yes | Yes | 20.3 | 21.2 | -0.9 | 9E58C83758934C89A92B3F1E8ABACA8E |  | R22 | TXV |  | 6.782% | 0.93218 | 13.03% | [5 empty] | TXV | 6.782%
Fairfield | CA | 94533-5452 |  | 2013-08-14 | 2013-08-14 10:48 | 2013-08-14 14:02 | PAYNE - PA13NR036-N | 85 | -6 | Yes | Yes | 15.4 | 17.7 | -2.3 | 24E9DB99D84445ADBE6475D7B251D01B |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Pittsburg | CA | 94565-6049 |  | 2013-09-30 | 2013-09-30 10:34 | 2013-09-30 10:35 | COLEMAN - TCGD60S41S1C | 86 | -8.1 | Yes | Yes | 18.1 | 17.3 | 0.9 | F2627F4BCF1748B098F0D11E8F644DE5 |  | R22 | Non-TXV |  | -9.419% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.419%
Fresno | CA | 93704-1752 |  | 2013-08-07 | 2013-08-07 15:04 | 2013-08-07 15:38 | BRYANT - 574ANW042060NB | 120 | 4.5 | Yes | Yes | 16.8 | 19.7 | -2.9 | D89519257D344D899E9A1005BC1A977E |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Fresno | CA | 93722-3148 |  | 2013-08-14 | 2013-08-14 17:43 | 2013-08-14 20:23 | ARCOAIRE - 38CK024310 | 56 | 4.2 | Yes | Yes | 20.1 | 19 | 1.1 | BE1ED5466A954D0CB06F2BE39D91B61B |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Davis | CA | 95616-3024 |  | 2013-08-14 | 2013-08-14 10:02 | 2013-08-14 10:29 | CARRIER - 38EN030300 | 86 | 12 | Yes | Yes | 20.7 | 19.6 | 1.1 | 893CA247A5AD4D998378614E12E50409 |  | R22 | Non-TXV |  | 13.95% | 0.86047 | 26.82% | [5 empty] | Non-TXV | 13.95%
Fresno | CA | 93726-5517 |  | 2013-08-14 | 2013-08-14 15:32 | 2013-08-14 16:14 | GOODMAN - GPG1336070M41AC | 106 | 3.2 | Yes | Yes | 19.4 | 19.5 | -0.1 | 7AA83980E29C4FA2AEEC2AFFEE735DA2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Fresno | CA | 93726-1839 |  | 2013-08-13 | 2013-08-13 15:21 | 2013-08-13 15:58 | PAYNE - PY3PNA036060NB | 118 | 5.3 | Yes | Yes | 23.6 | 21.4 | 2.2 | 9D0FDC7DF6B64DFD801F4C2A8C4F3554 |  | R22 | Non-TXV |  | 4.492% | 0.95508 | 8.632% | [5 empty] | Non-TXV | 4.492%
Vallejo | CA | 94590-6418 |  | 2013-08-15 | 2013-08-15 14:00 | 2013-08-15 15:58 | CARRIER - 38TXA042330 | 140 | 4.9 | Yes | Yes | 16.8 | 17.2 | -0.4 | 342BC49025384F118B952C018511033C |  | R410A | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Bakersfield | CA | 93309-6479 |  | 2013-08-07 | 2013-08-07 22:16 | 2013-08-07 22:19 | GOODMAN - GPG1360090M41AD | 185 | 8.9 | Yes | Yes | 27.4 | 21.7 | 5.7 | D343007CC675404A9C14424244BD068F |  | R410A | Non-TXV |  | 4.811% | 0.95189 | 9.245% | [5 empty] | Non-TXV | 4.811%
Fresno | CA | 93728-2102 |  | 2013-09-10 | 2013-09-10 15:07 | 2013-09-10 15:55 | OTHER - UNK | 66 | 5.7 | Yes | Yes | 20.2 | 18.3 | 1.9 | CFD1E82E77DB408E892A1519CF147D1E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.636% | 0.91364 | 16.6% | [5 empty] | Non-TXV | 8.636%
Bakersfield | CA | 93306-5455 |  | 2013-08-07 | 2013-08-07 14:09 | 2013-08-07 15:23 | ICP - PGAA24B11K3 | 85 | 4.2 | Yes | Yes | 17.6 | 19.5 | -1.9 | 6B501EB5B99341879748260CE327375F |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Bakersfield | CA | 93312-6704 |  | 2013-08-12 | 2013-08-12 10:30 | 2013-08-12 11:47 | CARRIER - 38CKC042340 | 85 | -4.6 | Yes | Yes | 18.4 | 21.4 | -3 | 584E0554404744FB8C71F6446F7C1BED |  | R22 | TXV |  | -5.412% | 1.0541 | 1.516% |  |  |  |  | TXV |  |  | -5.412%
Bakersfield | CA | 93311-9157 |  | 2013-10-04 | 2013-10-04 16:20 | 2013-10-04 16:37 | LENNOX - 13ACD-042-230-01 | 111 | 12 | Yes | Yes | 22.5 | 21.5 | 1 | 6D4E213993B344BAAEB38E0389C57899 |  | R22 | Non-TXV |  | 10.81% | 0.89189 | 20.78% | [5 empty] | Non-TXV | 10.81%
Hayward | CA | 94544-6415 |  | 2013-08-21 | 2013-08-21 12:46 | 2013-08-21 12:46 | OTHER - HAC361-A | 85 | 0 | Yes | Yes | 20.8 | 16.4 | 4.4 | EF441FD366254316830360BA6EA037B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-08-28 | 2013-08-28 19:03 | 2013-08-28 19:05 | OTHER - JS3BD-036K | 114 | 4.2 | Yes | Yes | 22.5 | 22 | 0.5 | BC195AEC4D254C6D986A3A9B2C6D2EAF |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Fresno | CA | 93726-1514 |  | 2013-09-10 | 2013-09-10 13:02 | 2013-09-10 13:49 | WEATHER KING - 10AJA3601 | 80 | 4.2 | Yes | Yes | 20 | 22.6 | -2.6 | D8F6C93D2A3940A289E6C3FC8C6AF855 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | Non-TXV | 5.25%
Fresno | CA | 93711-6176 |  | 2013-09-27 | 2013-09-27 13:45 | 2013-09-27 14:02 | YORK - D2Y5024N03206A | 62 | 7.5 | Yes | Yes | 20.1 | 18.7 | 1.4 | 06D2658B50EA4C2FB1C86B5EDB572B00 |  | R22 | Non-TXV |  | 12.1% | 0.87903 | 23.25% | [5 empty] | Non-TXV | 12.1%
Fresno | CA | 93722-3155 |  | 2013-10-25 | 2013-10-25 16:41 | 2013-10-25 16:58 | CARRIER - 38CK030310 | 68 | 5.7 | Yes | Yes | 22.9 | 20.6 | 2.4 | 8A04E582D30D42D6A7A5EEAC05C390DD |  | R22 | Non-TXV |  | 8.382% | 0.91618 | 16.11% | [5 empty] | Non-TXV | 8.382%
Fresno | CA | 93722-2524 |  | 2013-08-14 | 2013-08-14 12:39 | 2013-08-14 16:05 | LENNOX - 12GCS036751PA | 87 | 4.4 | Yes | Yes | 22.9 | 20.5 | 2.4 | 0068535C48BC405AA55D5C9E2426196B |  | R22 | Non-TXV |  | 5.057% | 0.94943 | 9.719% | [5 empty] | Non-TXV | 5.057%
Hayward | CA | 94544-6343 |  | 2013-10-02 | 2013-10-02 13:50 | 2013-10-02 13:50 | OTHER - AC030M1021A | 57 | 0 | Yes | Yes | 19.2 | 16.8 | 2.4 | 9790DD848F9E453A84B185527ED43541 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6330 |  | 2013-09-05 | 2013-09-05 14:30 | 2013-09-05 14:30 | ARMSTRONG - R53-36P1-C | 85 | 0 | Yes | Yes | 18.9 | 17.9 | 1 | 00BDBF333D4A431C834044548A06A18E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1613 |  | 2013-08-14 | 2013-08-14 13:25 | 2013-08-14 13:58 | CARRIER - 38TRA060330 | 176 | 5.7 | Yes | Yes | 19.4 | 20.1 | -0.7 | BCD85B702E3D410BA54C1C301E316C51 |  | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.224% | [5 empty] | Non-TXV | 3.239%
Fresno | CA | 93704-1444 |  | 2013-08-24 | 2013-08-24 11:26 | 2013-08-24 11:55 | BRYANT - UNK | 82 | 5.5 | Yes | Yes | 25.5 | 20.6 | 4.9 | 6EDDD8A0D6E6445DA88A46E93A75EE98 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.707% | 0.93293 | 12.89% | [5 empty] | Non-TXV | 6.707%
Bakersfield | CA | 93309-2781 |  | 2013-08-24 | 2013-08-24 14:22 | 2013-08-24 14:38 | RHEEM - RAAE-060JAS | 85 | 4.2 | Yes | Yes | 18.3 | 20.7 | -2.4 | DF9B4ED05E1D4580A2784DA9CDD429A9 |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Fresno | CA | 93722-5175 |  | 2013-08-15 | 2013-08-15 12:01 | 2013-08-15 12:28 | CARRIER - 48KLA130-321BE | 85 | 8.7 | Yes | Yes | 21.4 | 17.2 | 4.2 | 1518828A94C14AACB093F280492027F9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.24% | 0.89765 | 19.67% | [5 empty] | Non-TXV | 10.24%
Fresno | CA | 93706-9124 |  | 2013-08-16 | 2013-08-16 12:51 | 2013-08-16 12:51 | GIBSON - JS4BD048KB | 62 | 0 | Yes | Yes | 20.6 | 21.4 | -0.8 | C430F5237CBB4EA08F0D22F684826709 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4519 |  | 2013-08-02 | 2013-08-02 11:32 | 2013-08-02 11:32 | DAY & NIGHT - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 1EB8DAFF5E7A4467A7E16F05CC2862D6 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95110-2949 |  | 2013-10-15 | 2013-10-15 12:19 | 2013-10-15 12:35 | CARRIER - 38HDC036 321 | 70 | 2.5 | Yes | Yes | 20.3 | 20.9 | -0.6 | 09CC508E9703458C953C9D8B027DB5D5 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Fresno | CA | 93711-6174 |  | 2013-09-27 | 2013-09-27 14:18 | 2013-09-27 14:45 | YORK - D2YS024N03206A | 62 | 3.5 | Yes | Yes | 23 | 20.1 | 2.9 | 2889041BE61E45F4B83DD65160112735 |  | R22 | Non-TXV |  | 5.645% | 0.94355 | 10.85% | [5 empty] | Non-TXV | 5.645%
Fresno | CA | 93722-6718 |  | 2013-08-15 | 2013-08-15 10:57 | 2013-08-15 11:15 | BDP - 585CJW030040 | 58 | -3.4 | Yes | Yes | 20.4 | 22.7 | -2.2 | 99FA6B2F55944C30ABE2847543176B01 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
San Jose | CA | 95138-1527 |  | 2013-09-06 | 2013-09-06 12:26 | 2013-09-06 12:26 | RUUD - UAKA042JAZ | 85 | 0 | Yes | Yes | 23.6 | 17.7 | 5.9 | 5FD405EF9DE04A9AA4DE447642736AEA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9429 |  | 2013-08-21 | 2013-08-21 09:12 | 2013-08-21 09:12 | CARRIER - 38CKC048360 | 97 | 4.7 | Yes | Yes | 17.6 | 17.6 | 0 | A29A26CACEEB406EA89B6622A9FF53DF |  | R22 | Non-TXV |  | 4.845% | 0.95155 | 9.312% | [5 empty] | Non-TXV | 4.845%
Clovis | CA | 93611-5112 |  | 2013-08-07 | 2013-08-07 10:53 | 2013-08-07 11:11 | YORK - D1NP036N5606A | 108 | 3.2 | Yes | Yes | 21.7 | 18.7 | 3 | 8B44AD4380BD48F191C8FED591022C65 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93726-1838 |  | 2013-08-28 | 2013-08-28 10:40 | 2013-08-28 11:52 | ARCOAIRE - 563CNX036000ACAA | 104 | 3.8 | Yes | Yes | 23.4 | 21.5 | 1.9 | 93FCB3C4782F47A28251E081E1E0C1E0 |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
San Jose | CA | 95112-1746 |  | 2013-10-15 | 2013-10-15 13:46 | 2013-10-15 14:12 | PAYNE - RA10JA036 A | 83 | 4.5 | Yes | Yes | 21.1 | 22.4 | -1.3 | 20FA7EDF0E2E4727AE83F4F68E35CE88 |  | R22 | Non-TXV |  | 5.422% | 0.94578 | 10.42% | [5 empty] | Non-TXV | 5.422%
Pleasanton | CA | 94588-3089 |  | 2013-09-12 | 2013-09-12 14:19 | 2013-09-12 19:21 | CARRIER - 38CKC030320 | 139 | 5.6 | Yes | Yes | 20.4 | 16.4 | 4 | 662946E3703D40F1A8CBF45188FCE07C |  | R22 | TXV |  | 4.029% | 0.95971 | 7.742% | [5 empty] | TXV | 4.029%
Fresno | CA | 93722-4129 |  | 2013-08-15 | 2013-08-15 09:46 | 2013-08-15 10:07 | CARRIER - 48GS-03606301-- | 60 | 2 | Yes | Yes | 22.7 | 20.9 | 1.8 | FC2FE77A3990447B8A02C5ECC4DD6EB3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Antioch | CA | 94531-8205 |  | 2013-10-02 | 2013-10-02 09:00 | 2013-10-02 09:01 | TRANE - TTR742A100A0 | 138 | -9.7 | Yes | Yes | 16.7 | 17 | -0.3 | C3CB681373CD47289FB980AC15D66277 |  | R22 | Non-TXV |  | -7.029% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.029%
San Jose | CA | 95148-1406 |  | 2013-10-12 | 2013-10-12 10:44 | 2013-10-12 11:10 | AMERICAN STANDARD - CM36-11 B | 88 | -8.3 | Yes | Yes | 21.9 | 20.6 | 1.4 | 8DA088A2C3EF4F6698A402C074C0C123 |  | R22 | Non-TXV |  | -9.432% | 1.0943 | 2.641% |  |  |  |  | Non-TXV |  |  | -9.432%
Bakersfield | CA | 93313-5701 |  | 2013-08-09 | 2013-08-09 14:19 | 2013-08-09 14:58 | YORK - H1RA042S06D | 84 | 12.1 | Yes | Yes | 26.4 | 20.8 | 5.6 | FCE7E9CF6E1B40118D937F59110F7F3B |  | R22 | Non-TXV |  | 14.4% | 0.85595 | 27.68% | [5 empty] | Non-TXV | 14.4%
Clovis | CA | 93612-2323 |  | 2013-10-11 | 2013-10-11 12:22 | 2013-10-11 14:07 | PAYNE - PY3PNA03606NB | 114 | 4.3 | Yes | Yes | 20.4 | 19.4 | 1 | 6ADD855CC72C4FD5987343D0CE6C9A00 |  | R22 | Non-TXV |  | 3.772% | 0.96228 | 7.249% | [5 empty] | Non-TXV | 3.772%
Fresno | CA | 93711-2650 |  | 2013-09-06 | 2013-09-06 11:18 | 2013-09-06 11:35 | CARRIER - 48K;LA124300BF | 66 | 4.9 | Yes | Yes | 19.5 | 19.3 | 0.2 | CE78D4DDB1CD4485AAD1CFA97827536B |  | R22 | Non-TXV |  | 7.424% | 0.92576 | 14.27% | [5 empty] | Non-TXV | 7.424%
Pittsburg | CA | 94565-4734 |  | 2013-09-06 | 2013-09-06 08:42 | 2013-09-06 08:43 | DAY & NIGHT - PGD330060K001C1 | 98 | 3.5 | Yes | Yes | 15.7 | 16.4 | -0.7 | 7EC3CD4B8647422787023C2415BC3286 |  | R410A | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Fresno | CA | 93711-6160 |  | 2013-09-25 | 2013-09-25 13:33 | 2013-09-25 13:59 | YORK - D2YS018N03206A | 52 | 4.3 | Yes | Yes | 23.1 | 20.4 | 2.7 | 97CB6EFE4AE04B03BF28EA860EFFF906 |  | R22 | Non-TXV |  | 8.269% | 0.91731 | 15.89% | [5 empty] | Non-TXV | 8.269%
Fresno | CA | 93711-6160 |  | 2013-09-27 | 2013-09-27 15:34 | 2013-09-27 16:11 | YORK - D2YS018N03206A | 52 | 2.9 | Yes | Yes | 20.6 | 20.1 | 0.5 | 4E9EA54856C8452DB7724899FD4DA046 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Antioch | CA | 94509-5519 |  | 2013-08-21 | 2013-08-21 11:04 | 2013-08-21 11:05 | LENNOX - HS26-042-2P | 104 | 3.6 | Yes | Yes | 18.2 | 17.6 | 0.6 | E0F9F9FE368C41E887BE1E031296C915 |  | R22 | Non-TXV |  | 3.462% | 0.96538 | 6.652% | [5 empty] | Non-TXV | 3.462%
Bakersfield | CA | 93308-9756 |  | 2013-08-08 | 2013-08-08 09:31 | 2013-08-08 09:48 | RHEEM - RRGG-05N315KR | 85 | 7.2 | Yes | Yes | 19.6 | 16.2 | 3.5 | B8483ADBABFF4C38B71B9D1785E9D28D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Fresno | CA | 93704-5309 |  | 2013-08-17 | 2013-08-17 15:31 | 2013-08-17 16:00 | RHEEM - RRKAA048JK10X | 77 | 3.9 | Yes | Yes | 19.9 | 20 | -0.1 | 062905F66A924F0D88F8222CAB2F4CF4 |  | R22 | TXV |  | 5.065% | 0.94935 | 9.734% | [5 empty] | TXV | 5.065%
Fresno | CA | 93727-6813 |  | 2013-08-07 | 2013-08-07 12:39 | 2013-08-07 14:07 | YORK - D2YS036N04506A | 92 | -5.4 | Yes | Yes | 27.4 | 21.7 | 5.7 | D9F1D2CBCBB843AAAC8BFEC2B3EE8827 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Pleasant Hill | CA | 94523-2151 |  | 2013-09-06 | 2013-09-06 11:18 | 2013-09-06 11:21 | TRANE - 4TTX3048A1000AA | 126 | 6 | Yes | Yes | 16.8 | 17.5 | -0.7 | 9A1C0D8A71FB4A2AB83B4B88181438F4 |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Pleasant Hill | CA | 94523-2151 |  | 2013-09-06 | 2013-09-06 11:23 | 2013-09-06 11:25 | TRANE - 4TTX3048A1000AA | 126 | 5.7 | Yes | Yes | 17.9 | 18.2 | -0.3 | 11A3B2141A7F41D7A22664E87842CD81 |  | R22 | Non-TXV |  | 4.524% | 0.95476 | 8.694% | [5 empty] | Non-TXV | 4.524%
Fresno | CA | 93710-6106 |  | 2013-08-07 | 2013-08-07 12:03 | 2013-08-07 12:03 | OTHER - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 320F1372074F41CE9586B51E40A25E8E | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4781 |  | 2013-08-16 | 2013-08-16 07:38 | 2013-08-16 07:56 | CARRIER - UNK | 80 | -4.7 | Yes | Yes | 21.1 | 18.5 | 2.6 | FA95410F35014A9796354E67011801BE |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Fairfield | CA | 94533-5230 |  | 2013-10-15 | 2013-10-15 10:31 | 2013-10-15 13:46 | OTHER - TCJD48S41S3A | 73 | -4.2 | Yes | Yes | 17.6 | 20.5 | -2.8 | E7EFDA705BFA4111A0DA6E710B897B34 |  | R410A | Non-TXV |  | -5.753% | 1.0575 | 1.611% |  |  |  |  | Non-TXV |  |  | -5.753%
Suisun City | CA | 94585-2334 |  | 2013-10-02 | 2013-10-02 13:30 | 2013-10-02 13:50 | BARD - 563CN060-A | 232 | 4.7 | Yes | Yes | 18.3 | 20.9 | -2.6 | 13DD1ADBE58D4DCC9A7D15DAE3386A78 |  | R22 | Non-TXV |  | 2.026% | 0.97974 | 3.893% | [5 empty] | Non-TXV | 2.026%
Bakersfield | CA | 93311-9162 |  | 2013-08-10 | 2013-08-10 10:09 | 2013-08-10 10:43 | CARRIER - 38BRC042340 | 106 | 19 | Yes | Yes | 25.3 | 19.8 | 5.5 | C140CF75DCE446FBABDCF94318F30672 |  | R22 | Non-TXV |  | 17.92% | 0.82075 | 34.45% | [5 empty] | Non-TXV | 17.92%
Morgan Hill | CA | 95037-4007 |  | 2013-10-01 | 2013-10-01 16:04 | 2013-10-01 16:49 | CARRIER - UNK | 101 | 3.3 | Yes | Yes | 18.6 | 21.5 | -2.9 | 9228EC24EE3741A5807DFA84F2241C4E |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Fresno | CA | 93727-6212 |  | 2013-08-13 | 2013-08-13 11:22 | 2013-08-13 11:48 | CARRIER - 0997E00503 | 167 | 5.2 | Yes | Yes | 17.4 | 20.4 | -3 | 1F07AE6F3D9C47D8944CA2B07B60376D |  | R22 | Non-TXV |  | 3.114% | 0.96886 | 5.984% | [5 empty] | Non-TXV | 3.114%
Fresno | CA | 93702-4416 |  | 2013-08-08 | 2013-08-08 15:37 | 2013-08-08 15:37 | CARRIER - 585HJ036060 | 102 | 0 | Yes | Yes | 22 | 19.5 | 2.5 | DF46D05CE441416C8E71FFEEB4B8B185 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-6159 |  | 2013-09-25 | 2013-09-25 14:01 | 2013-09-25 14:01 | YORK - D2YSO24N03206A | 52 | 0 | Yes | Yes | 21.7 | 19.3 | 2.4 | 9512082D6F6640E1A02A1CAFA8409019 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7076 |  | 2013-08-21 | 2013-08-21 12:19 | 2013-08-21 12:48 | GOODMAN - GPG1336701AC | 85 | 6.5 | Yes | Yes | 17.6 | 20.5 | -2.9 | CB5F9239F6AB42D688593AE4C296FD6D |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Vallejo | CA | 94591-4282 |  | 2013-08-15 | 2013-08-15 14:34 | 2013-08-15 16:00 | TRANE - 2TTX4048B1000AA | 150 | 5.2 | Yes | Yes | 16.3 | 18.7 | -2.4 | 7A90899DE9D84293AD1DB042526488B5 |  | R22 | Non-TXV |  | 3.467% | 0.96533 | 6.662% | [5 empty] | Non-TXV | 3.467%
Bakersfield | CA | 93309-5136 |  | 2013-08-27 | 2013-08-27 12:34 | 2013-08-27 13:48 | ICP - PGAA42C1KA | 70 | 3.4 | Yes | Yes | 16.1 | 17.9 | -1.8 | 83FA5CCEF3D4496C99447EE219313F01 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Clovis | CA | 93611-7418 |  | 2013-08-13 | 2013-08-13 10:00 | 2013-08-13 10:32 | CARRIER - UKN | 87 | 3.8 | Yes | Yes | 23.1 | 19.2 | 3.9 | 531B2E06D2F748A4817DD7B89DC32A0B |  | R22 | Non-TXV |  | 4.368% | 0.95632 | 8.394% | [5 empty] | Non-TXV | 4.368%
Sanger | CA | 93657-1914 |  | 2013-08-12 | 2013-08-12 15:30 | 2013-08-12 16:16 | LENNOX - 13ACD04823001 | 204 | 9.4 | Yes | Yes | 19.9 | 17.9 | 2 | 9FA09250BCA64D59AA9FBA01B0BD21C4 |  | R22 | Non-TXV |  | 4.608% | 0.95392 | 8.855% | [5 empty] | Non-TXV | 4.608%
Bakersfield | CA | 93308-7131 |  | 2013-08-20 | 2013-08-20 18:55 | 2013-08-20 19:17 | OTHER - AC060X1222A | 133 | 20.9 | Yes | Yes | 25.6 | 23.3 | 2.3 | 8568F180C00E49C78AF28FA43B2B03C7 |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Fresno | CA | 93727-3260 |  | 2013-08-15 | 2013-08-15 11:03 | 2013-08-15 11:33 | HEIL - GPCM042K080I | 86 | 19.9 | Yes | Yes | 21.7 | 20.8 | 0.9 | 789324FEC69346CB8A7DBD69CAB236C1 |  | R22 | Non-TXV |  | 23.14% | 0.7686 | 44.47% | [5 empty] | Non-TXV | 23.14%
Fresno | CA | 93703-4133 |  | 2013-08-07 | 2013-08-07 14:58 | 2013-08-07 14:58 | CARRIER - 48SX024060331AA | 62 | 0 | Yes | Yes | 16.8 | 18.3 | -1.5 | BC319F0DB42248528B378319788DF264 | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8804 |  | 2013-08-07 | 2013-08-07 11:19 | 2013-08-07 11:41 | LENNOX - 12CAB604P | 173 | 6.9 | Yes | Yes | 25.5 | 20.4 | 5.1 | 98D5216CD5484039A4070140CAEE4930 |  | R22 | Non-TXV |  | 3.988% | 0.96012 | 7.665% | [5 empty] | Non-TXV | 3.988%
Lost Hills | CA | 93249-0000 |  | 2013-08-28 | 2013-08-28 19:16 | 2013-08-28 19:18 | OTHER - JS3BD-036K | 114 | 9.1 | Yes | Yes | 21.1 | 21 | 0.1 | EB5D5D7ECA1243F8877F0E81F4B085FE |  | R22 | Non-TXV |  | 7.982% | 0.92018 | 15.34% | [5 empty] | Non-TXV | 7.982%
Lost Hills | CA | 93249-0000 |  | 2013-08-28 | 2013-08-28 19:10 | 2013-08-28 19:13 | OTHER - FS3BD-036K | 114 | 8 | Yes | Yes | 22.1 | 22.1 | 0 | CA99BB163CA841D78D25D9DB49B77A6A |  | R22 | TXV |  | 7.018% | 0.92982 | 13.49% | [5 empty] | TXV | 7.018%
Bakersfield | CA | 93308-7820 |  | 2013-08-20 | 2013-08-20 14:20 | 2013-08-20 18:47 | GOODMAN - PGB036050-1A | 85 | 11.1 | Yes | Yes | 18.6 | 21.6 | -3 | 0333087F47624F10B4380151B808C8FC |  | R22 | Non-TXV |  | 13.06% | 0.86941 | 25.1% | [5 empty] | Non-TXV | 13.06%
Kerman | CA | 93630-1937 |  | 2013-09-23 | 2013-09-23 12:49 | 2013-09-23 13:27 | BRYANT - 583ANW030060AAD | 68 | 4.4 | Yes | Yes | 22.5 | 21 | 1.5 | E2D8F92E0C7B4918AFD9F247BC3DA888 |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Bakersfield | CA | 93304-7038 |  | 2013-08-15 | 2013-08-15 11:00 | 2013-08-15 12:13 | YORK - D1NH036N056060 | 85 | 3.1 | Yes | Yes | 20.9 | 19.1 | 1.9 | 41530C8E5FD94834920FBAA8E5553BB8 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Fresno | CA | 93710-6106 |  | 2013-08-07 | 2013-08-07 12:06 | 2013-08-07 12:53 | YORK - B4HP024A06A | 85 | 4.2 | Yes | Yes | 21.2 | 18.2 | 3 | 690C109AD335431BAE5AC5C28034F515 |  | R22 | TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | TXV | 4.941%
San Ramon | CA | 94583-9214 |  | 2013-09-18 | 2013-09-18 13:31 | 2013-09-18 14:17 | YORK - H1RA042S06D | 84 | 7.4 | Yes | Yes | 20.7 | 17.4 | 3.3 | 59E0AED16D9B4E2FBE67896E1CA2C9BD |  | R22 | Non-TXV |  | 8.81% | 0.9119 | 16.93% | [5 empty] | Non-TXV | 8.81%
Martinez | CA | 94553-5342 |  | 2013-10-02 | 2013-10-02 11:47 | 2013-10-02 11:48 | TAPPAN - CM 30 4 | 71 | 3.4 | Yes | Yes | 16.7 | 17.6 | -0.9 | 36E9EC5D75214C6BBEF722631B316A38 |  | R22 | Non-TXV |  | 4.789% | 0.95211 | 9.203% | [5 empty] | Non-TXV | 4.789%
Suisun City | CA | 94585-6312 |  | 2013-10-04 | 2013-10-04 12:41 | 2013-10-04 12:42 | CARRIER - 38TD036300 | 182 | 6.5 | Yes | Yes | 17.4 | 17 | 0.4 | 5550BB7F5E584CEEA7B314DA71148D2B |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Bakersfield | CA | 93304-7030 |  | 2013-09-25 | 2013-09-25 16:10 | 2013-09-25 16:10 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | F8A52907C6914E9B8E8BBAE3AF7D8448 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2410 |  | 2013-08-15 | 2013-08-15 09:01 | 2013-08-15 09:37 | PAYNE - 588ANW036080ACAF | 69 | 8.6 | Yes | Yes | 22.3 | 20.4 | 1.9 | 719A96C15ECE468E846D3620E4061BAE |  | R22 | Non-TXV |  | 12.46% | 0.87536 | 23.95% | [5 empty] | Non-TXV | 12.46%
Bakersfield | CA | 93313-5432 |  | 2013-08-20 | 2013-08-20 19:20 | 2013-08-20 19:23 | OTHER - AC042X1021A | 84 | 3.1 | Yes | Yes | 21.1 | 22.1 | -1 | D94CA0AD30184583A92E96C22309E0F0 |  | R22 | Non-TXV |  | 3.69% | 0.9631 | 7.092% | [5 empty] | Non-TXV | 3.69%
Mc Farland | CA | 93250-1641 |  | 2013-08-22 | 2013-08-22 17:46 | 2013-08-22 17:52 | GOODMAN - PGB042075-1A | 68 | 3.6 | Yes | Yes | 18.6 | 20.7 | -2.1 | 8C74924E38684B0DABBACEDC7592D812 |  | R22 | TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | TXV | 5.294%
Clovis | CA | 93611-4032 |  | 2013-08-24 | 2013-08-24 14:35 | 2013-08-24 14:35 | BDP - 585A03680YAC | 60 | 8.8 | Yes | Yes | 29.6 | 20.2 | 9.4 | 99866B067ADE4C58AB8BCF82A996E6DE | Add refrigerant: 8.8 oz | R22 | Non-TXV |  | 14.67% | 0.85333 | 28.19% | [5 empty] | Non-TXV | 14.67%
Redding | CA | 96001-9709 |  | 2013-09-03 | 2013-09-03 12:07 | 2013-09-03 13:21 | CARRIER - 38BYC048320 | 178 | 9.4 | Yes | Yes | 24.9 | 20.7 | 4.3 | AE4255113D4B4B6BAA369D28617C7B4A |  | R22 | Non-TXV |  | 5.281% | 0.94719 | 10.15% | [5 empty] | Non-TXV | 5.281%
Willits | CA | 95490-9510 |  | 2013-08-21 | 2013-08-21 11:10 | 2013-08-21 12:29 | PAYNE - ILLEGIBLE | 89 | 6.4 | Yes | Yes | 25 | 20.9 | 4.1 | 336F18C5CEB04A54BC02D03BA59421BE |  | R22 | Non-TXV |  | 7.191% | 0.92809 | 13.82% | [5 empty] | Non-TXV | 7.191%
Bay Point | CA | 94565-6600 |  | 2013-09-11 | 2013-09-11 10:16 | 2013-09-11 14:10 | BRYANT - 661CJ018-E | 68 | -4.8 | Yes | Yes | 17.4 | 20.2 | -2.8 | 9C3E263C97924D06B0644086FA70D2B5 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Vacaville | CA | 95687-3413 |  | 2013-08-20 | 2013-08-20 09:55 | 2013-08-20 09:55 | TRANE - 2TTB0030A1000AA | 64 | 0 | Yes | Yes | 15.3 | 17.6 | -2.3 | 766E1DFC42C14F1DABCB7142FAC67C91 | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6245 |  | 2013-08-21 | 2013-08-21 18:35 | 2013-08-21 18:39 | OTHER - PGC030K060A | 52 | 5.1 | Yes | Yes | 20.6 | 18.2 | 2.4 | CF2D7092BCD24ABD9B204D3D55EF03EC |  | R22 | Non-TXV |  | 9.808% | 0.90192 | 18.85% | [5 empty] | Non-TXV | 9.808%
Kerman | CA | 93630-9744 |  | 2013-10-10 | 2013-10-10 13:07 | 2013-10-10 13:48 | YORK - D1NA024N05606A | 50 | 4.1 | Yes | Yes | 19.2 | 19.3 | -0.1 | 6C73E89ECF2049AB8E30ECB85C8BF91C |  | R22 | Non-TXV |  | 8.2% | 0.918 | 15.76% | [5 empty] | Non-TXV | 8.2%
Pittsburg | CA | 94565-2758 |  | 2013-08-29 | 2013-08-29 09:44 | 2013-08-29 09:47 | OTHER - NA | 72 | 2.4 | Yes | Yes | 18.2 | 17.6 | 0.6 | 322E1497CF604221863ADFF9B6D33F4F |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Napa | CA | 94558-5226 |  | 2013-10-04 | 2013-10-04 10:23 | 2013-10-04 10:23 | AMERICAN STANDARD - 4A7A6060B1000AA | 160 | -13.2 | Yes | Yes | 15.2 | 16.4 | -1.2 | 6A82FF3EE52643DC82AB8CB11F51CCF5 |  | R410A | Non-TXV |  | -8.25% | 1.0825 | 2.31% |  |  |  |  | Non-TXV |  |  | -8.25%
Bakersfield | CA | 93309-2051 |  | 2013-08-07 | 2013-08-07 12:13 | 2013-08-07 21:13 | - | 85 | 2.8 | Yes | Yes | 27 | 21 | 6 | 0ACFFF8182384F4CB5EF4E1290ACC0C1 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Bakersfield | CA | 93307-4882 |  | 2013-08-08 | 2013-08-08 17:41 | 2013-08-08 22:15 | OTHER - RHEEM | 85 | 3.1 | Yes | Yes | 19 | 20.4 | -1.4 | 334126ADDC784CFDB4DE0E52FF0B583E | Add refrigerant: 2.7 oz Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Bakersfield | CA | 93312-5928 |  | 2013-08-12 | 2013-08-12 09:35 | 2013-08-12 09:56 | YORK - H1RC048S06D | 122 | 3.6 | Yes | Yes | 14.1 | 16.4 | -2.3 | 82D74194FB71404E9D5DD9331477E073 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.951% | 0.97049 | 5.671% | [5 empty] | Non-TXV | 2.951%
Lost Hills | CA | 93249-0000 |  | 2013-08-27 | 2013-08-27 19:40 | 2013-08-27 19:42 | OTHER - JS5BD-036K | 138 | 5.4 | Yes | Yes | 21 | 21.3 | -0.3 | 81E2B25C31C44609A420028BFA58D8D5 |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Mountain View | CA | 94041-2442 |  | 2013-10-02 | 2013-10-02 16:37 | 2013-10-02 17:23 | CARRIER - UNK | 84 | 2.7 | Yes | Yes | 22.6 | 21.3 | 1.4 | EF4E73C2FC47497CAC0F632BFD5EC5A3 |  | R410A | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Clovis | CA | 93612-4431 |  | 2013-08-07 | 2013-08-07 08:41 | 2013-08-07 09:02 | PAYNE - UNK | 80 | 7.2 | Yes | Yes | 20.4 | 18.7 | 1.7 | 8FE42E3007B8454AAFCCDF35BFD17083 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Bakersfield | CA | 93308-2836 |  | 2013-08-07 | 2013-08-07 09:32 | 2013-08-07 09:51 | OTHER - AC-100-0H-2 | 85 | 2.5 | Yes | Yes | 24.7 | 22 | 2.7 | 421A6AC72DC94D059CD2734E8866C465 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Pittsburg | CA | 94565-6048 |  | 2013-09-20 | 2013-09-20 14:31 | 2013-09-20 14:31 | DAY & NIGHT - N2A348AKA300 | 120 | 0 | Yes | Yes | 14.9 | 17.7 | -2.8 | 0C9161A167BB4211AE2888E5CCF3AFF0 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7207 |  | 2013-08-07 | 2013-08-07 12:04 | 2013-08-07 12:04 | OTHER - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | A820AE037FF74A5CB9D6DD5760E2F47B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-6652 |  | 2013-10-25 | 2013-10-25 15:12 | 2013-10-25 15:47 | CARRIER - 48KLA1243008E | 68 | 16 | Yes | Yes | 20.9 | 20.1 | 0.8 | 334E9682EE304220AF94BC6EE80F1AD9 |  | R22 | Non-TXV |  | 23.53% | 0.76471 | 45.22% | [5 empty] | Non-TXV | 23.53%
Bakersfield | CA | 93309-1218 |  | 2013-09-05 | 2013-09-05 22:28 | 2013-09-05 22:28 | WESTINGHOUSE - IE036BAA0N | 120 | 0 | Yes | Yes | 22.4 | 21.8 | 0.6 | 8CE497E50D424F8E9A908945021668C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5465 |  | 2013-08-23 | 2013-08-23 09:57 | 2013-08-23 10:25 | ICP - PGAD47D1K6 | 215 | 29 | Yes | Yes | 22.3 | 22.1 | 0.2 | 299DD641B4AE4D21BC72E823CC0A4CD9 |  | R22 | Non-TXV |  | 13.49% | 0.86512 | 25.92% | [5 empty] | Non-TXV | 13.49%
Bakersfield | CA | 93313-0000 |  | 2013-08-16 | 2013-08-16 16:40 | 2013-08-16 16:44 | OTHER - N2A342AKA200 | 108 | 5.2 | Yes | Yes | 21.7 | 21.5 | 0.2 | 598BCF8499824C95ABAE993FA36920FC |  | R22 | TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | TXV | 4.815%
Bakersfield | CA | 93313-0000 |  | 2013-08-16 | 2013-08-16 16:44 | 2013-08-16 16:46 | OTHER - N2A342AKA200 | 108 | 4.8 | Yes | Yes | 22.8 | 21.5 | 1.3 | E190DB40960140259AB3A6F4FB18B99E |  | R22 | TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | TXV | 4.444%
Pittsburg | CA | 94565-6132 |  | 2013-08-30 | 2013-08-30 10:56 | 2013-08-30 10:57 | RHEEM - NA | 70 | -3.5 | Yes | Yes | 17.5 | 17.6 | -0.1 | A86E8CB8BB6840AF99C8C8D9AD0A0487 |  | R22 | TXV |  | -5% | 1.05 | 1.4% |  |  |  |  | TXV |  |  | -5%
Pittsburg | CA | 94565-6132 |  | 2013-08-30 | 2013-08-30 10:59 | 2013-08-30 11:06 | RHEEM - NA | 70 | -3.3 | Yes | Yes | 19.3 | 17.9 | 1.5 | A883FFFB68194B24857AA3CCE8E9E80D |  | R22 | TXV |  | -4.714% | 1.0471 | 1.32% |  |  |  |  | TXV |  |  | -4.714%
Concord | CA | 94521-2038 |  | 2013-09-05 | 2013-09-05 08:52 | 2013-09-05 08:52 | OTHER - SRV-51254A | 49 | 0 | Yes | Yes | 18.2 | 17.6 | 0.6 | CD49C6E442D24665823BBF92AD33B708 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4130 |  | 2013-08-19 | 2013-08-19 18:41 | 2013-08-19 19:00 | YORK - D1NP048N09006A | 132 | 12.7 | Yes | Yes | 17 | 19.5 | -2.5 | 8E6E98BBB67B4080B3F58B6D4ECDD382 |  | R22 | Non-TXV |  | 9.621% | 0.90379 | 18.49% | [5 empty] | Non-TXV | 9.621%
Davis | CA | 95618-1626 |  | 2013-08-13 | 2013-08-13 11:45 | 2013-08-13 12:12 | RHEEM - UAKA-037JAZ | 79 | -7.4 | Yes | Yes | 16.5 | 18.6 | -2.1 | 3F9388486F524898B682624893ACCB24 | Remove refrigerant: 4.6 oz | R22 | Non-TXV |  | -9.367% | 1.0937 | 2.623% |  |  |  |  | Non-TXV |  |  | -9.367%
Bakersfield | CA | 93304-7053 |  | 2013-09-17 | 2013-09-17 12:47 | 2013-09-18 07:21 | DAY & NIGHT - PGD336060K00111 | 85 | 16.8 | Yes | Yes | 17.1 | 20.1 | -3 | 621E89953C6B4A51BD6B7AD24BA74A85 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.76% | 0.80235 | 37.98% | [5 empty] | Non-TXV | 19.76%
Pittsburg | CA | 94565-1783 |  | 2013-08-29 | 2013-08-29 10:19 | 2013-08-29 10:21 | COPELAND - ZRCF36UO1E | 107 | 8.6 | Yes | Yes | 17.4 | 17.6 | -0.2 | C5F66F93FDB14D1282300238E390C2C2 |  | R22 | Non-TXV |  | 8.037% | 0.91963 | 15.45% | [5 empty] | Non-TXV | 8.037%
Vacaville | CA | 95688-2632 |  | 2013-08-22 | 2013-08-22 10:53 | 2013-08-22 15:55 | CARRIER - 38TKB0320 | 76 | 4.2 | Yes | Yes | 14.7 | 17.5 | -2.8 | 6AFD821D2B694DDEAC12363869C121B3 |  | R410A | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Suisun City | CA | 94585-2124 |  | 2013-10-10 | 2013-10-10 10:05 | 2013-10-10 10:05 | RUUD - UAKA-037JAZ | 85 | 0 | Yes | Yes | 19.2 | 17.2 | 2 | E11035E87F5B424F9894106FBAC07BD0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1866 |  | 2013-09-24 | 2013-09-24 19:30 | 2013-09-24 19:31 | OTHER - NAC048AKA1 | 108 | -8.9 | Yes | Yes | 23.6 | 21.5 | 2.1 | 1B7558735AB44E2AB026EA7E270FB126 |  | R22 | Non-TXV |  | -8.241% | 1.0824 | 2.308% |  |  |  |  | Non-TXV |  |  | -8.241%
Pittsburg | CA | 94565-4034 |  | 2013-08-29 | 2013-08-29 11:58 | 2013-08-29 12:00 | DAY & NIGHT - 565AJ024 | 70 | 3.9 | Yes | Yes | 16.3 | 17.6 | -1.3 | FB3E65F38F794D0683DE7AF0A2DE23E0 |  | R22 | Non-TXV |  | 5.571% | 0.94429 | 10.71% | [5 empty] | Non-TXV | 5.571%
Fresno | CA | 93706-4260 |  | 2013-09-12 | 2013-09-12 14:10 | 2013-09-12 14:29 | GOODMAN - GPJ301B | 123 | 16.2 | Yes | Yes | 19.1 | 18.7 | 0.4 | 1B97F2EB7B2A48F4A94744B80F20C945 |  | R22 | Non-TXV |  | 13.17% | 0.86829 | 25.31% | [5 empty] | Non-TXV | 13.17%
San Jose | CA | 95125-4260 |  | 2013-10-16 | 2013-10-16 10:15 | 2013-10-16 10:57 | BRYANT - 561CJX060-A | 156 | -14.7 | Yes | Yes | 19.9 | 18.7 | 1.2 | 9FB33AA6B60D42D1951CC0D4963114FB |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Fresno | CA | 93703-1566 |  | 2013-11-08 | 2013-11-08 14:32 | 2013-11-08 15:56 | CARRIER - 48KL024300BE | 50 | 1.5 | Yes | Yes | 23.6 | 19.7 | 3.9 | 884AADF1E465461D895510297312F763 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Pittsburg | CA | 94565-2723 |  | 2013-09-25 | 2013-09-25 12:30 | 2013-09-25 12:30 | OTHER - CA9036VKD3 | 85 | 0 | Yes | Yes | 19.8 | 17.3 | 2.6 | 27FFC696C47B495BA3EABA6C46D620A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5616 |  | 2013-08-15 | 2013-08-15 18:31 | 2013-08-15 18:34 | TRANE - 2TTB3048A1000AA | 132 | 11.8 | Yes | Yes | 23.6 | 23.1 | 0.5 | B8A7A74D82B44AB3AE862622FE6CF67E |  | R22 | Non-TXV |  | 8.939% | 0.91061 | 17.18% | [5 empty] | Non-TXV | 8.939%
Bakersfield | CA | 93313-3104 |  | 2013-08-20 | 2013-08-20 20:15 | 2013-08-20 20:20 | YORK - D1NH042N0606C | 94 | 5 | Yes | Yes | 25.9 | 20.8 | 5.1 | 331221EA4EB44FC5A77BD3C2AF44C668 |  | R22 | Non-TXV |  | 5.319% | 0.94681 | 10.22% | [5 empty] | Non-TXV | 5.319%
Bakersfield | CA | 93306-1129 |  | 2013-09-19 | 2013-09-19 11:35 | 2013-09-19 12:22 | DAY & NIGHT - 585H J048080 | 118 | 4.9 | Yes | Yes | 22.5 | 21.5 | 1 | 9E34B918B280409BAD198AE0BAEBAE29 |  | R22 | Non-TXV |  | 4.153% | 0.95847 | 7.98% | [5 empty] | Non-TXV | 4.153%
Vacaville | CA | 95687-6223 |  | 2013-08-28 | 2013-08-28 11:48 | 2013-08-28 15:13 | AMERICAN STANDARD - 2A6B0030A1000AA | 75 | -4.4 | Yes | Yes | 15.3 | 18 | -2.7 | F5F9C3B8C7F84E609AB04446A3B64472 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Bakersfield | CA | 93304-6727 |  | 2013-08-15 | 2013-08-15 09:56 | 2013-08-15 10:58 | TRANE - TTR736A100AC | 116 | 3.8 | Yes | Yes | 15.6 | 18.5 | -2.9 | A5E8B73632F2483EB5AB76B5854C8EA1 |  | R22 | Non-TXV |  | 3.276% | 0.96724 | 6.295% | [5 empty] | Non-TXV | 3.276%
San Jose | CA | 95111-3097 |  | 2013-10-10 | 2013-10-10 14:36 | 2013-10-10 15:36 | PAYNE - PA10JA048-D | 97 | -9.1 | Yes | Yes | 24.2 | 20.3 | 3.9 | B595B4C0AB2E4C5DAD0BE48204EB9549 |  | R22 | Non-TXV |  | -9.381% | 1.0938 | 2.627% |  |  |  |  | Non-TXV |  |  | -9.381%
Fresno | CA | 93727-6150 |  | 2013-08-14 | 2013-08-14 11:51 | 2013-08-14 12:10 | LENNOX - 13ACC-060-230-01 | 168 | 6.5 | Yes | Yes | 19.4 | 18.8 | 0.6 | B002C6DA2D484B11939499B286ED8AE2 |  | R22 | TXV |  | 3.869% | 0.96131 | 7.435% | [5 empty] | TXV | 3.869%
Fresno | CA | 93703-1251 |  | 2013-08-28 | 2013-08-28 11:55 | 2013-08-28 16:05 | RHEEM - RRNAB030JK06X | 72 | 5.5 | Yes | Yes | 22.1 | 19.3 | 2.8 | 7B6317436CAC4A08BED2C31B9A9D8505 |  | R22 | Non-TXV |  | 7.639% | 0.92361 | 14.68% | [5 empty] | Non-TXV | 7.639%
Martinez | CA | 94553-2715 |  | 2013-08-23 | 2013-08-23 08:23 | 2013-08-23 08:24 | LENNOX - 10ACC-048-230-04 | 96 | 3.7 | Yes | Yes | 17.6 | 17.1 | 0.5 | E64BA4FC78B94F389AC51BF4579169D9 |  | R22 | Non-TXV |  | 3.854% | 0.96146 | 7.407% | [5 empty] | Non-TXV | 3.854%
Fresno | CA | 93722-5470 |  | 2013-08-22 | 2013-08-22 16:20 | 2013-08-22 19:07 | OTHER - 38BR042300 | 133 | 5 | Yes | Yes | 19 | 20.2 | -1.2 | 526AFB7D06444EADA4E9B33CF2B5D33B |  | R22 | TXV |  | 3.759% | 0.96241 | 7.225% | [5 empty] | TXV | 3.759%
Fairfield | CA | 94533-7091 |  | 2013-08-14 | 2013-08-14 09:50 | 2013-08-14 13:56 | PAYNE - | 85 | -6 | Yes | Yes | 18.5 | 19.9 | -1.4 | 05DE04B84BC541EFBCAA33F2230D3874 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fresno | CA | 93711-6051 |  | 2013-08-22 | 2013-08-22 11:20 | 2013-08-22 11:37 | LENNOX - GCS20R-411-1002P | 70 | -2.7 | Yes | Yes | 20.6 | 20.4 | 0.2 | 90B78FF7DB114A2A91FE67B847B91CDF |  | R22 | TXV |  | -3.857% | 1.0386 | 1.08% |  |  |  |  | TXV |  |  | -3.857%
Fresno | CA | 93702-2710 |  | 2013-08-08 | 2013-08-08 09:36 | 2013-08-08 10:16 | TRANE - YCY060G1M0AB | 155 | 26.5 | Yes | Yes | 19.5 | 18.7 | 0.8 | 652493FFC39B488DB4E5A962A4B26EF5 |  | R22 | Non-TXV |  | 17.1% | 0.82903 | 32.86% | [5 empty] | Non-TXV | 17.1%
Fresno | CA | 93710-4528 |  | 2013-10-04 | 2013-10-04 14:37 | 2013-10-04 15:06 | CARRIER - 24ABR342A310 | 114 | 3.4 | Yes | Yes | 19.5 | 21.2 | -1.7 | 4443F37CE2FD41C9931453B8E4EC24B6 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Vallejo | CA | 94591-7944 |  | 2013-08-19 | 2013-08-19 12:40 | 2013-08-19 15:01 | ICP - HHP030AKA1 | 132 | 5 | Yes | Yes | 14.5 | 15.2 | -0.7 | CC8A419B55F647D589970AFA73E52562 |  | R22 | Non-TXV |  | 3.788% | 0.96212 | 7.279% | [5 empty] | Non-TXV | 3.788%
Pittsburg | CA | 94565-6022 |  | 2013-08-29 | 2013-08-29 08:48 | 2013-08-29 08:49 | RHEEM - AT-48B10 | 55 | -3.2 | Yes | Yes | 17.5 | 17.6 | -0.1 | 522906358F304D1998962892CA03A96B |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Shafter | CA | 93263-3534 |  | 2013-08-07 | 2013-08-07 16:26 | 2013-08-07 16:52 | GOODMAN - GPG10360701A | 75 | 2.4 | Yes | Yes | 25.4 | 20.1 | 5.3 | E83214780C0A4066A80B254EDD5E8D61 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93722-6193 |  | 2013-08-16 | 2013-08-16 15:44 | 2013-08-16 16:37 | TEMPSTAR - GPCM30K060F | 69 | 4.2 | Yes | Yes | 18.8 | 20.6 | -1.8 | A84413B5728B4E8A895E63AC475324B3 |  | R22 | Non-TXV |  | 6.087% | 0.93913 | 11.7% | [5 empty] | Non-TXV | 6.087%
Sanger | CA | 93657-8783 |  | 2013-09-17 | 2013-09-17 13:18 | 2013-09-17 13:46 | YORK - H2RD042S06B | 141 | 35.5 | Yes | Yes | 20.4 | 22.5 | -2.1 | E2DD319986CA423D9FC7698AF5A4649C |  | R22 | Non-TXV |  | 25.18% | 0.74823 | 48.39% | [5 empty] | Non-TXV | 25.18%
Bakersfield | CA | 93309-3802 |  | 2013-08-24 | 2013-08-24 11:57 | 2013-08-24 11:57 | NORDYNE - R4GD-X30K072X | 104 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | A00BD26C17DF441D9FADB20C0163CC9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-1101 |  | 2013-09-06 | 2013-09-06 09:16 | 2013-09-06 09:16 | OTHER - 597CN042-B | 141 | 0 | Yes | Yes | 21 | 18.8 | 2.2 | CE518F528EA24D4C8B8CE80E062AAF83 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-3331 |  | 2013-09-06 | 2013-09-06 08:45 | 2013-09-06 09:36 | RUUD - URGG-05N31JKR | 48 | 3.2 | Yes | Yes | 22 | 18.2 | 3.8 | BC36A0C6799E4EF0B2904D66BB6F571D |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Antioch | CA | 94531-7673 |  | 2013-09-03 | 2013-09-03 09:35 | 2013-09-03 09:37 | PAYNE - 591ANX060000AAAA | 166 | -15.6 | Yes | Yes | 16.3 | 17 | -0.7 | F7C8221D131142E299515F1EFE8F4C32 |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Fresno | CA | 93703-3324 |  | 2013-08-08 | 2013-08-08 13:18 | 2013-08-08 13:37 | YORK - D1NA036N05606C | 67 | 8.5 | Yes | Yes | 22.4 | 20.4 | 2 | CD8F5FAF98B044E6A14B644F5BD2F535 |  | R22 | Non-TXV |  | 12.69% | 0.87313 | 24.38% | [5 empty] | Non-TXV | 12.69%
Clovis | CA | 93619-7628 |  | 2013-10-22 | 2013-10-22 14:17 | 2013-10-22 14:45 | OTHER - | 85 | 28.9 | Yes | Yes | 40 | 20.9 | 19.1 | BD054A3185B24ABF8AF9018C9B6562CC | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 34% | 0.66 | 65.34% | [5 empty] | Non-TXV | 34%
Clovis | CA | 93619-7628 |  | 2013-10-24 | 2013-10-24 15:09 | 2013-10-24 15:36 | LENNOX - 13ACC04823001 | 158 | 7.2 | Yes | Yes | 22.2 | 20.3 | 1.9 | AE92DDD56FC6422C9DD49249DBA8EE00 |  | R22 | Non-TXV |  | 4.557% | 0.95443 | 8.757% | [5 empty] | Non-TXV | 4.557%
Clovis | CA | 93619-7628 |  | 2013-10-24 | 2013-10-24 15:41 | 2013-10-24 16:11 | LENNOX - 13ACC04223001 | 123 | 4.5 | Yes | Yes | 21.3 | 19.7 | 1.7 | E98CD58AE7F64EA0AAAB2E4042AB54D2 |  | R22 | Non-TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | Non-TXV | 3.659%
Bakersfield | CA | 93305-1022 |  | 2013-08-19 | 2013-08-19 12:19 | 2013-08-19 12:19 | AMERICAN STANDARD - 4A7A6060B1000AA | 160 | 0 | Yes | Yes | 22.4 | 21.8 | 0.6 | BED125250676472D94031032E55CF25C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1022 |  | 2013-08-19 | 2013-08-19 12:37 | 2013-08-19 12:37 | PAYNE - PY1PNB024040NAAA | 53 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | 8C9528D95B6C4F748902E2B5524C6F9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1022 |  | 2013-08-19 | 2013-08-19 12:58 | 2013-08-19 12:58 | AMERICAN STANDARD - PY3PNA036060NA | 167 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | A0B327BCF1054EDA9AB0FEC47533CC70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4339 |  | 2013-08-16 | 2013-08-16 13:49 | 2013-08-16 16:46 | DAY & NIGHT - UNK | 85 | -8 | Yes | Yes | 10.7 | 13.6 | -2.9 | EA031C810FA54BFC8A56EA4EF3EE1447 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93722-6148 |  | 2013-08-21 | 2013-08-21 14:00 | 2013-08-21 14:27 | OTHER - 38CK042310 | 93 | 4.5 | Yes | Yes | 21 | 20.1 | 0.9 | 40B0F9CB21A6449EB53652E9A57EF250 |  | R22 | Non-TXV |  | 4.839% | 0.95161 | 9.299% | [5 empty] | Non-TXV | 4.839%
Bakersfield | CA | 93313-3104 |  | 2013-08-20 | 2013-08-20 20:32 | 2013-08-20 20:37 | PAYNE - N/A | 85 | 0 | Yes | Yes | 28 | 22.1 | 5.9 | AF1B7B609F0340B1A710EA1E99760084 | Add refrigerant: 13 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-8686 |  | 2013-08-08 | 2013-08-08 15:32 | 2013-08-08 15:50 | GOODMAN - GPG13480901AC | 145 | 4.3 | Yes | Yes | 21.4 | 18.8 | 2.6 | 59F6B4FD69014BE9B1CC2FD609530053 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.699% | [5 empty] | Non-TXV | 2.966%
Fresno | CA | 93722-6171 |  | 2013-08-16 | 2013-08-16 15:04 | 2013-08-16 15:38 | LENNOX - PGF330060K01A1 | 154 | 5.3 | Yes | Yes | 20.3 | 20.1 | 0.2 | 0D77B1C5B991456A8C29EEEEC9BFF010 |  | R22 | Non-TXV |  | 3.442% | 0.96558 | 6.614% | [5 empty] | Non-TXV | 3.442%
Vacaville | CA | 95687-7810 |  | 2013-08-30 | 2013-08-30 09:13 | 2013-08-30 16:26 | YORK - H1DE030506B | 80 | 4 | Yes | Yes | 13.5 | 16.5 | -3 | 854B858C300449BE9C6F9C3439225403 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93703-4033 |  | 2013-08-23 | 2013-08-23 10:53 | 2013-08-23 11:28 | AMANA - PGD36C0702X | 110 | 4 | Yes | Yes | 25.6 | 20.3 | 5.3 | E4F76AE9BCC64C03B5F240C78955BD1F |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Fresno | CA | 93705-3426 |  | 2013-08-14 | 2013-08-14 10:05 | 2013-08-14 11:39 | ARCOAIRE - PGAD36D1K5 | 102 | 4.4 | Yes | Yes | 20 | 19.5 | 0.5 | C527B16C531A40FC919AFF98662E3E25 |  | R22 | Non-TXV |  | 4.314% | 0.95686 | 8.29% | [5 empty] | Non-TXV | 4.314%
Bakersfield | CA | 93308-1366 |  | 2013-08-21 | 2013-08-21 19:07 | 2013-08-21 19:07 | LENNOX - N,A | 85 | 0 | Yes | Yes | 11.1 | 20.2 | -9.1 | A48368F5C6F4416C8D49C4B848A740A0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4104 |  | 2013-08-14 | 2013-08-14 10:43 | 2013-08-14 11:12 | GOODMAN - UNK | 105 | -6.2 | Yes | Yes | 16.8 | 18.6 | -1.8 | 49B771681F174E678F8B6EF1FCAB19FD |  | R22 | Non-TXV |  | -5.905% | 1.059 | 1.654% |  |  |  |  | Non-TXV |  |  | -5.905%
Bakersfield | CA | 93313-3028 |  | 2013-08-16 | 2013-08-16 16:30 | 2013-08-16 16:30 | TEMPSTAR - PGAD47D1K3 | 220 | 0 | Yes | Yes | -0.5 | 21.3 | -21.8 | 4CED8D8721894FB3A471550B8AF18024 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2207 |  | 2013-08-11 | 2013-08-11 17:38 | 2013-08-11 17:40 | TEMPSTAR - PGF342080K01 | 184 | -10.6 | Yes | Yes | 21 | 21.5 | -0.5 | 0F6A0E49A2EE45CB86CABA18388C01E1 |  | R22 | Non-TXV |  | -5.761% | 1.0576 | 1.613% |  |  |  |  | Non-TXV |  |  | -5.761%
Sanger | CA | 93657-8757 |  | 2013-08-22 | 2013-08-22 15:14 | 2013-08-22 15:37 | LENNOX - 10ACC06023004 | 130 | -5.4 | Yes | Yes | 20.5 | 19.9 | 0.6 | DEB1D4FB17C042FDB04ABD00101EDA0E |  | R22 | Non-TXV |  | -4.154% | 1.0415 | 1.163% |  |  |  |  | Non-TXV |  |  | -4.154%
Fresno | CA | 93726-4527 |  | 2013-09-17 | 2013-09-17 11:02 | 2013-09-17 11:39 | ARCOAIRE - PGF036K060B | 55 | 4 | Yes | Yes | 22.4 | 19.9 | 2.5 | 3864ACB9CB0746AA81807C14ACBE0E73 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Fresno | CA | 93710-4028 |  | 2013-08-28 | 2013-08-28 09:00 | 2013-08-28 09:18 | BRYANT - 582ANW036060AAAF | 60 | 1.9 | Yes | Yes | 20.6 | 20.9 | -0.3 | 313A472ED4294280A3EE1965BDF8F7AA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Bakersfield | CA | 93311-3238 |  | 2013-09-12 | 2013-09-12 21:47 | 2013-09-12 22:05 | GIBSON - JS3BC-048KA | 85 | 4.1 | Yes | Yes | 17.7 | 20.6 | -2.9 | B9F84CB0938F4A4391500E53D600B835 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Fresno | CA | 93704-4107 |  | 2013-11-01 | 2013-11-01 10:48 | 2013-11-01 11:17 | RHEEM - RRKA-A036JK08X | 62 | 1.8 | Yes | Yes | 26.5 | 20.6 | 5.9 | 5D5E671797014B3EBD77950057943FCA |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Vallejo | CA | 94591-8453 |  | 2013-09-19 | 2013-09-19 11:01 | 2013-09-19 11:01 | OTHER - CA9036VKC1 | 85 | 0 | Yes | Yes | 17.9 | 17.8 | 0.1 | 4011B77307BD44B2867A31491A3A43C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5884 |  | 2013-08-15 | 2013-08-15 12:26 | 2013-08-15 12:46 | YORK - H2RD060S068 | 162 | -6.1 | Yes | Yes | 19.9 | 19.1 | 0.8 | 644B83290B9140DDB03E23FB1DFDADB6 |  | R22 | Non-TXV |  | -3.765% | 1.0377 | 1.054% |  |  |  |  | Non-TXV |  |  | -3.765%
Antioch | CA | 94509-3335 |  | 2013-08-19 | 2013-08-19 09:06 | 2013-08-19 09:07 | PAYNE - 38CK024310 | 56 | -5.3 | Yes | Yes | 16.5 | 17.6 | -1.1 | 4FFD05E13E5E4F76A8E572BC0B46B556 |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
Fresno | CA | 93701-1117 |  | 2013-08-22 | 2013-08-22 08:48 | 2013-08-22 09:27 | TRANE - 4YC3048A1075AB | 131 | -16.8 | Yes | Yes | 22.2 | 19.4 | 2.8 | EAEAB64DA4D342C7A1D56943D518CB82 |  | R410A | TXV |  | -12.82% | 1.1282 | 3.591% |  |  |  |  | TXV |  |  | -12.82%
Fresno | CA | 93711-1384 |  | 2013-08-23 | 2013-08-23 09:04 | 2013-08-23 09:04 | RHEEM - UNK | 80 | 0 | Yes | Yes | 25 | 20.4 | 4.6 | 29F8A5161D6343B983609221CBED56F9 | Final Suction Temperature must be between 20°F and 80°F. Please check entries. Final Suction pressure must be between 78 psig and 170 psig. Please check entries. Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-1919 |  | 2013-08-19 | 2013-08-19 10:34 | 2013-08-19 10:53 | YORK - H2RA060S06A | 118 | 33.8 | Yes | Yes | 25 | 21.3 | 3.8 | F6FC1EE89C334A5E86438497ADE78CD9 |  | R22 | Non-TXV |  | 28.64% | 0.71356 | 55.05% | [5 empty] | Non-TXV | 28.64%
Clovis | CA | 93612-0443 |  | 2013-08-08 | 2013-08-08 13:15 | 2013-08-08 13:15 | RHEEM - RRNL-B036JK06X | 92 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 30136DD2C6CC450DAD4A43299AA945DC | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3629 |  | 2013-08-21 | 2013-08-21 13:10 | 2013-08-21 13:58 | DAY & NIGHT - UKN | 80 | 5 | Yes | Yes | 20 | 19.4 | 0.6 | B7F016AA06D244D1BF9EED230F2690AC |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Vacaville | CA | 95687-6242 |  | 2013-08-20 | 2013-08-20 11:02 | 2013-08-20 13:50 | PAYNE - PA10JA024-C | 64 | -4 | Yes | Yes | 11.6 | 12.8 | -1.2 | 8E8A09B10C56431385B04E8121778DDD |  | R22 | Non-TXV |  | -6.25% | 1.0625 | 1.75% |  |  |  |  | Non-TXV |  |  | -6.25%
Concord | CA | 94518-2096 |  | 2013-09-05 | 2013-09-05 12:36 | 2013-09-05 12:36 | COLEMAN - BRCS036BG1 | 63 | 0 | Yes | Yes | 17.5 | 18.2 | -0.7 | 56D8FFF6852F48E4A9913805BFE8D626 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cottonwood | CA | 96022-8707 |  | 2013-09-07 | 2013-09-07 10:03 | 2013-09-07 10:45 | ICP - CA9036VKD3 | 124 | -11.7 | Yes | Yes | 20 | 19.3 | 0.7 | FBD6A8A1ADC749388105B868CD352C6B |  | R22 | Non-TXV |  | -9.435% | 1.0944 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.435%
Wasco | CA | 93280-1117 |  | 2013-08-22 | 2013-08-22 18:45 | 2013-08-22 18:48 | GOODMAN - GPG1336045M41BA | 70 | 3.3 | Yes | Yes | 23.8 | 19.9 | 3.9 | 9D43C660396743A18DAE56516AD00300 |  | R22 | TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | TXV | 4.714%
Fresno | CA | 93705-0836 |  | 2013-08-22 | 2013-08-22 11:27 | 2013-08-22 11:51 | AMERICAN STANDARD - YCC030F1M0BJ | 72 | 4.2 | Yes | Yes | 19.3 | 18.1 | 1.2 | 9AD8E4690FB64407B6A65D817224515E |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Fresno | CA | 93722-7159 |  | 2013-08-15 | 2013-08-15 13:56 | 2013-08-15 14:16 | YORK - H1RA048S06B | 85 | 2.6 | Yes | Yes | 16 | 18.8 | -2.8 | A79168F8D70047A4A116BA64415AC27C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Antioch | CA | 94509-3325 |  | 2013-08-19 | 2013-08-19 08:47 | 2013-08-19 08:47 | OTHER - AE18B10 | 72 | 0 | Yes | Yes | 16 | 17.6 | -1.6 | F11163C5532A4DD9B359CF503CA715BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-2909 |  | 2013-10-01 | 2013-10-01 09:08 | 2013-10-01 09:57 | GOODMAN - CLJ36-1A | 85 | 10.8 | Yes | Yes | 20.4 | 17.7 | 2.7 | D33531454B1048109791662B3A17125C |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
Fresno | CA | 93703-2431 |  | 2013-09-27 | 2013-09-27 09:31 | 2013-09-27 09:31 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 20.7 | 18.8 | 1.9 | 12C501AB451E4C238F53A2AD345C1146 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5617 |  | 2013-08-30 | 2013-08-30 09:39 | 2013-08-30 09:40 | PAYNE - PA10JAG48-A | 99 | 6.1 | Yes | Yes | 16.5 | 17.3 | -0.8 | 986922132A9D457FB16A10BDD9C75C22 |  | R22 | Non-TXV |  | 6.162% | 0.93838 | 11.84% | [5 empty] | Non-TXV | 6.162%
Clovis | CA | 93612-2674 |  | 2013-08-08 | 2013-08-08 09:46 | 2013-08-08 10:15 | CARRIER - 4855-036080321-- | 68 | -2.6 | Yes | Yes | 22.1 | 19.8 | 2.3 | 889B58FB9F7545C4BF2CD113A6C15229 | OK: Verified Refrigerant Charge Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -3.824% | 1.0382 | 1.071% |  |  |  |  | TXV |  |  | -3.824%
Fairfield | CA | 94533-2341 |  | 2013-08-14 | 2013-08-14 13:00 | 2013-08-14 14:05 | PAYNE - PA10JA042-D | 81 | 2.4 | Yes | Yes | 16.6 | 18.2 | -1.6 | 245C9841D4994D7BAD22CEE2474BFF55 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Bakersfield | CA | 93307-4829 |  | 2013-08-21 | 2013-08-21 09:56 | 2013-08-21 10:56 | GOODMAN - GPG133607OM41DA | 70 | 3.1 | Yes | Yes | 20.7 | 19.5 | 1.2 | 4402743411C548F3941F60970E1E62A4 |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Fairfield | CA | 94533-4270 |  | 2013-08-30 | 2013-08-30 13:26 | 2013-08-30 16:28 | PAYNE - | 85 | -3 | Yes | Yes | 12.9 | 15.9 | -3 | FDC048699B314C6281F07A207FCD9B04 |  | R22 | Non-TXV |  | -3.529% | 1.0353 | 0.9884% |  |  |  |  | Non-TXV |  |  | -3.529%
Fresno | CA | 93727-3261 |  | 2013-08-13 | 2013-08-13 13:30 | 2013-08-13 13:50 | CARRIER - 48KLA136---321BE | 85 | 9.5 | Yes | Yes | 27 | 21.2 | 5.8 | 3CCD432E675C48EC8FC8EF37DB5DC50E |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Fresno | CA | 93726-5128 |  | 2013-08-13 | 2013-08-13 14:32 | 2013-08-13 15:00 | PAYNE - 588ANW036060ADAF | 70 | 4.2 | Yes | Yes | 24.4 | 21.2 | 3.2 | C6974835514F4B5998FB571CFD4441AE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Selma | CA | 93662-9437 |  | 2013-08-13 | 2013-08-13 13:48 | 2013-08-13 13:48 | WHIRLPOOL - UNK | 96 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 1FBF2A66A3C44D44A4157039E9BEEED1 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1963 |  | 2013-08-13 | 2013-08-13 09:18 | 2013-08-13 09:18 | LUXAIRE - HARB-F030SA | 122 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 865B0FA842F04152852D5042792846B8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4024 |  | 2013-08-22 | 2013-08-22 15:02 | 2013-08-22 15:02 | RHEEM - RRPLB030JK06X | 76 | 0 | Yes | Yes | 20.1 | 19.7 | 0.4 | 8592CDABAA12404488CF8072EBC0851C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6456 |  | 2013-09-25 | 2013-09-25 13:46 | 2013-09-25 22:01 | YORK - H1R048S06D | 117 | 15.7 | Yes | Yes | 22.9 | 17.2 | 5.7 | 1FE92896F5EF4B1CAE68D7EC775B4C32 |  | R22 | Non-TXV |  | 13.42% | 0.86581 | 25.79% | [5 empty] | Non-TXV | 13.42%
Pittsburg | CA | 94565-6456 |  | 2013-09-25 | 2013-09-25 22:02 | 2013-09-25 22:37 | YORK - H1R048S06D | 117 | 10.6 | Yes | Yes | 21.4 | 17.2 | 4.2 | 05EE589A7C9542178F1AE8A33A96A64D |  | R22 | Non-TXV |  | 9.06% | 0.9094 | 17.41% | [5 empty] | Non-TXV | 9.06%
Bakersfield | CA | 93312-6418 |  | 2013-08-18 | 2013-08-18 14:40 | 2013-08-18 14:40 | RUUD - UAKA-042JAZ | 81 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 5036C5F0368E4A1284EE9445C19329EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0318 |  | 2013-08-27 | 2013-08-27 11:58 | 2013-08-27 12:50 | LENNOX - 10GCS024503PA | 52 | 4.4 | Yes | Yes | 21.3 | 19.6 | 1.7 | 3C1F753DE89942739BE256D4F7A37C86 |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
San Jose | CA | 95135-1303 |  | 2013-10-22 | 2013-10-22 10:40 | 2013-10-22 11:05 | CARRIER - 38TKB0300 | 66 | 2.6 | Yes | Yes | 20 | 22.3 | -2.3 | D89269D518544FA4A0014389ACDA135D |  | R22 | Non-TXV |  | 3.939% | 0.96061 | 7.571% | [5 empty] | Non-TXV | 3.939%
Fresno | CA | 93728-3834 |  | 2013-08-13 | 2013-08-13 12:28 | 2013-08-13 12:51 | - H2CB0365060 | 91 | 2.8 | Yes | Yes | 18.8 | 19.3 | -0.5 | BF6563FE3FF74305B54B8E5CF0899F69 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Fresno | CA | 93722-3743 |  | 2013-08-14 | 2013-08-14 11:44 | 2013-08-14 12:37 | OTHER - PA13MR036J | 87 | 4 | Yes | Yes | 20 | 19.3 | 0.7 | C54AB5B5F2204C91B5D960FF8A4C7057 |  | R22 | TXV |  | 4.598% | 0.95402 | 8.836% | [5 empty] | TXV | 4.598%
Fresno | CA | 93706-4262 |  | 2013-09-12 | 2013-09-12 12:50 | 2013-09-12 13:15 | GOODMAN - CDLJ301B | 123 | 5.1 | Yes | Yes | 21.1 | 18.6 | 2.5 | 5DE7F11A0FDC423E88E4E53A71E31DE1 |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Fresno | CA | 93711-2643 |  | 2013-09-06 | 2013-09-06 10:40 | 2013-09-06 10:59 | CARRIER - 48KLA1243008E | 66 | 2.3 | Yes | Yes | 19.5 | 19.3 | 0.2 | FE9117B7ECBB4059AD236361657FB599 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Fresno | CA | 93706-4263 |  | 2013-09-12 | 2013-09-12 13:23 | 2013-09-12 13:52 | GOODMAN - GPLJ301B | 123 | 3.7 | Yes | Yes | 20.4 | 19.3 | 1.1 | BB520951D9444D23A8836F9149BA6ED3 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.781% | [5 empty] | Non-TXV | 3.008%
Concord | CA | 94521-2120 |  | 2013-09-05 | 2013-09-05 15:17 | 2013-09-05 15:18 | FRIGIDAIRE - S3BA-036KA | 69 | 8 | Yes | Yes | 18.1 | 18.2 | -0.1 | 434960C092EA45B0AE8F3D5EAE010643 |  | R22 | Non-TXV |  | 11.59% | 0.88406 | 22.28% | [5 empty] | Non-TXV | 11.59%
Fresno | CA | 93703-2410 |  | 2013-08-15 | 2013-08-15 09:47 | 2013-08-15 10:08 | RHEEM - RRKAA036JK06X | 62 | 6.1 | Yes | Yes | 21 | 19.7 | 1.3 | 5B2628BF4F7044AF9686941BEB18FFBE |  | R22 | Non-TXV |  | 9.839% | 0.90161 | 18.91% | [5 empty] | Non-TXV | 9.839%
Bakersfield | CA | 93305-3408 |  | 2013-09-13 | 2013-09-13 11:08 | 2013-09-16 07:35 | YORK - D1NA030N05606C | 76 | 3.6 | Yes | Yes | 13.4 | 15.6 | -2.2 | CBBBEFF6672A4EC591781C44A39FB009 |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Lemoore | CA | 93245-2545 |  | 2013-08-27 | 2013-08-27 09:35 | 2013-08-27 10:15 | CARRIER - 48GP042090311 | 144 | 7.5 | Yes | Yes | 20.2 | 19.6 | 0.7 | FD858FA695464425960B05A52EA04D14 |  | R410A | Non-TXV |  | 5.208% | 0.94792 | 10.01% | [5 empty] | Non-TXV | 5.208%
Bakersfield | CA | 93306-4563 |  | 2013-10-15 | 2013-10-15 17:57 | 2013-10-15 18:00 | CLIMATEMASTER - PGC048K080A | 102 | 7.1 | Yes | Yes | 24 | 21.3 | 2.7 | 72CD2131650E4F679A2116071716B070 |  | R22 | Non-TXV |  | 6.961% | 0.93039 | 13.38% | [5 empty] | Non-TXV | 6.961%
Fairfield | CA | 94534-3414 |  | 2013-09-20 | 2013-09-20 12:34 | 2013-09-20 12:34 | OTHER - GCGD36S21SA | 63 | 0 | Yes | Yes | 15.2 | 16.4 | -1.2 | 9A0C31C3E73449169A41ECD1A7867CF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5618 |  | 2013-08-14 | 2013-08-14 13:28 | 2013-08-14 13:45 | - 563CN048-C | 167 | -9.8 | Yes | Yes | 21.8 | 20.1 | 1.7 | 95B4EB73A70B4564B25207CE50FE8A57 |  | R22 | Non-TXV |  | -5.868% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.868%
Bakersfield | CA | 93313-3448 |  | 2013-09-10 | 2013-09-10 19:48 | 2013-09-10 19:50 | BRYANT - 585CJ02450 | 72 | 2.7 | Yes | Yes | 27.1 | 21.5 | 5.6 | FD6E0AD4250A4228A784E7EECF0B2ED3 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Fresno | CA | 93706-4331 |  | 2013-08-16 | 2013-08-16 08:59 | 2013-08-16 09:26 | GOODMAN - PGB0240501REVA | 54 | 7 | Yes | Yes | 23.8 | 20.4 | 3.4 | C186F719B5154C859078C03C892B6269 |  | R22 | Non-TXV |  | 12.96% | 0.87037 | 24.91% | [5 empty] | Non-TXV | 12.96%
Fresno | CA | 93722-3718 |  | 2013-08-14 | 2013-08-14 11:31 | 2013-08-14 11:51 | CARRIER - 38BR030300 | 106 | 3.9 | Yes | Yes | 18.1 | 18.9 | -0.8 | 4A74DEA82DE64076BB86487534F9D462 |  | R22 | Non-TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | Non-TXV | 3.679%
Fresno | CA | 93703-1921 |  | 2013-08-23 | 2013-08-23 10:25 | 2013-08-23 10:51 | YORK - D1NP036N05606A | 108 | 4.3 | Yes | Yes | 24.8 | 20.1 | 4.7 | FF29C65BA9134A6384C65E762D3D2BB1 |  | R22 | Non-TXV |  | 3.981% | 0.96019 | 7.652% | [5 empty] | Non-TXV | 3.981%
Antioch | CA | 94509-3357 |  | 2013-08-21 | 2013-08-21 10:44 | 2013-08-21 10:44 | TRANE - TDDR018D100A1 | 60 | 7.5 | Yes | Yes | 18.7 | 18.2 | 0.5 | AF72D801B05C4557B11280EB43E292E6 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Antioch | CA | 94509-3320 |  | 2013-08-19 | 2013-08-19 09:28 | 2013-08-19 09:29 | LENNOX - 10ACC-024-230-02 | 57 | 2.2 | Yes | Yes | 18.3 | 17 | 1.3 | C48E5FCEFEF24F0BA5E69A5B7719AFE8 |  | R22 | Non-TXV |  | 3.86% | 0.9614 | 7.417% | [5 empty] | Non-TXV | 3.86%
Fresno | CA | 93727-3656 |  | 2013-08-13 | 2013-08-13 10:25 | 2013-08-13 10:45 | LENNOX - 10GCS036-75-1PA | 58 | 1.8 | Yes | Yes | 26 | 20.9 | 5.1 | A0224A0298DA46D89243063513FBF21D |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Fresno | CA | 93722-4146 |  | 2013-08-28 | 2013-08-28 17:17 | 2013-08-28 17:48 | AMERICAN STANDARD - YCY036G1M0AA | 93 | 5.1 | Yes | Yes | 19.5 | 19.1 | 0.4 | B5C913DB126C4058A4900972BD91E77B |  | R22 | Non-TXV |  | 5.484% | 0.94516 | 10.54% | [5 empty] | Non-TXV | 5.484%
Lemoore | CA | 93245-9741 |  | 2013-08-27 | 2013-08-27 10:32 | 2013-08-27 10:54 | BRYANT - 589ANW042080ACBF | 91 | 11.1 | Yes | Yes | 20.9 | 18.9 | 2 | 5BBC851C9AFA4D9888E1A8A05AA56E05 |  | R22 | Non-TXV |  | 12.2% | 0.87802 | 23.44% | [5 empty] | Non-TXV | 12.2%
Vallejo | CA | 94591-6650 |  | 2013-08-19 | 2013-08-19 14:24 | 2013-08-19 14:24 | CARRIER - 38TR042300 | 175 | 0 | Yes | Yes | 16.4 | 19.3 | -2.9 | 460E0D66DA774731AAF4B7B80DE960AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1525 |  | 2013-08-13 | 2013-08-13 17:51 | 2013-08-13 17:55 | RHEEM - RRRNA-B036JK08X | 83 | 5.2 | Yes | Yes | 22.3 | 22.6 | -0.3 | DA5E75C78BF548E9B043DCA588587D10 |  | R22 | Non-TXV |  | 6.265% | 0.93735 | 12.04% | [5 empty] | Non-TXV | 6.265%
Fresno | CA | 93727-3686 |  | 2013-08-14 | 2013-08-14 14:23 | 2013-08-14 14:39 | LENNOX - 12GCS042-75-3PB | 133 | 4.4 | Yes | Yes | 26.8 | 21.3 | 5.6 | CA4AFDF3011145F4806D7810F84EEB3C |  | R22 | Non-TXV |  | 3.308% | 0.96692 | 6.358% | [5 empty] | Non-TXV | 3.308%
Vacaville | CA | 95687-7397 |  | 2013-08-21 | 2013-08-21 13:06 | 2013-08-21 14:56 | CARRIER - 38CKC042300 | 80 | 4.3 | Yes | Yes | 15.6 | 18.3 | -2.7 | A4D73C798CDD4C94AEF37D7AF094399B |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Fresno | CA | 93702-2447 |  | 2013-08-09 | 2013-08-09 09:40 | 2013-08-09 10:11 | PAYNE - 585B030075YACR | 80 | 4 | Yes | Yes | 22.1 | 18.2 | 3.9 | 787685C49EF34D4AA3C1AAC2D9E81A4A |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93702-2218 |  | 2013-08-09 | 2013-08-09 14:20 | 2013-08-09 14:52 | DAY & NIGHT - 585A030080YAC | 50 | 4.2 | Yes | Yes | 23.1 | 20.2 | 2.9 | 1E1D4CC9EB1344D8A83CB2887FDACC40 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.4% | 0.916 | 16.14% | [5 empty] | Non-TXV | 8.4%
Vacaville | CA | 95688-9697 |  | 2013-09-17 | 2013-09-17 09:05 | 2013-09-17 09:52 | RHEEM - 13PJL30A01 | 101 | -4.1 | Yes | Yes | 22.5 | 24.8 | -2.3 | 665A0523A0DE4DF2A57A65AB65C09312 |  | R22 | Non-TXV |  | -4.059% | 1.0406 | 1.137% |  |  |  |  | Non-TXV |  |  | -4.059%
Fresno | CA | 93711-1400 |  | 2013-08-23 | 2013-08-23 15:12 | 2013-08-23 15:12 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 24.5 | 19.9 | 4.7 | 6A8CF412931B43D598841522EB392A79 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2328 |  | 2013-09-03 | 2013-09-03 08:41 | 2013-09-03 08:42 | CARRIER - 38TDA036300 | 184 | 7 | Yes | Yes | 17.8 | 17 | 0.8 | 9615EAC6B51A4CD2AAE56030C95AA3AA |  | R22 | Non-TXV |  | 3.804% | 0.96196 | 7.311% | [5 empty] | Non-TXV | 3.804%
Bakersfield | CA | 93306-3938 |  | 2013-10-15 | 2013-10-15 18:12 | 2013-10-15 18:17 | PAYNE - PA13NR036-C | 128 | -11.1 | Yes | Yes | 19.2 | 21 | -1.8 | A14822BBE3CD450484DCB3DCFF3527C0 |  | R22 | TXV |  | -8.672% | 1.0867 | 2.429% |  |  |  |  | TXV |  |  | -8.672%
Sanger | CA | 93657-2833 |  | 2013-08-22 | 2013-08-22 16:09 | 2013-08-22 16:09 | GOODMAN - PGJ0481001 | 84 | 0 | Yes | Yes | 21.9 | 19.6 | 2.3 | 53D0FBC42C8940F7AB34594C1014CD28 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3415 |  | 2013-08-12 | 2013-08-12 09:10 | 2013-08-12 09:41 | TRANE - YCY048F1H0AB | 177 | 19.8 | Yes | Yes | 25.4 | 20.4 | 5 | 7DB71D130B7E40DCBCEC7A31C9D15013 |  | R22 | Non-TXV |  | 11.19% | 0.88814 | 21.5% | [5 empty] | Non-TXV | 11.19%
Fresno | CA | 93702-4422 |  | 2013-08-09 | 2013-08-09 11:27 | 2013-08-09 11:27 | OTHER - UKN | 85 | 0 | Yes | Yes | 35.5 | 20.4 | 15.1 | D0C469CBEB604004873D1E22E64B54A4 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3415 |  | 2013-08-12 | 2013-08-12 11:48 | 2013-08-12 12:23 | RHEEM - RRMA042JK08X | 114 | 11.9 | Yes | Yes | 22.1 | 20.4 | 1.7 | 723E2BC8749F429AACA9E1539798A3DC |  | R22 | Non-TXV |  | 10.44% | 0.89561 | 20.06% | [5 empty] | Non-TXV | 10.44%
Sanger | CA | 93657-3415 |  | 2013-08-12 | 2013-08-12 12:30 | 2013-08-12 12:55 | LENNOX - 12GC036755PB | 110 | 7.3 | Yes | Yes | 23.1 | 19.9 | 3.2 | FAC7DE9221354992972FE8B0A1B42FDC |  | R22 | Non-TXV |  | 6.636% | 0.93364 | 12.75% | [5 empty] | Non-TXV | 6.636%
Antioch | CA | 94531-8380 |  | 2013-10-01 | 2013-10-01 10:43 | 2013-10-01 12:13 | PAYNE - 561AJ042-D | 85 | 4.3 | Yes | Yes | 20.7 | 15.5 | 5.2 | 382D3C75F004454E81697E1B5DA87C47 |  | R22 | TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | TXV | 5.059%
Pittsburg | CA | 94565-4412 |  | 2013-08-29 | 2013-08-29 10:41 | 2013-08-29 10:42 | PAYNE - 591ANX030000ABAA | 68 | -6.4 | Yes | Yes | 15.7 | 16.7 | -1 | E22CF6293F5842FBAB91D10E39663E66 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Mc Farland | CA | 93250-1371 |  | 2013-08-22 | 2013-08-22 18:08 | 2013-08-22 18:10 | TEMPSTAR - PGAA30C1K4 | 95 | 3.4 | Yes | Yes | 21.9 | 22.6 | -0.7 | B2E297F7104E4F0E9C0E59C1269C7112 |  | R22 | Non-TXV |  | 3.579% | 0.96421 | 6.878% | [5 empty] | Non-TXV | 3.579%
Fresno | CA | 93702-2438 |  | 2013-08-08 | 2013-08-08 08:44 | 2013-08-08 08:44 | - | 85 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | F0181A9FA7604446BD541F5A299EE2D1 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2592 |  | 2013-09-17 | 2013-09-17 09:22 | 2013-09-17 09:48 | GOODMAN - GPG13420701AB | 107 | -7.6 | Yes | Yes | 21.1 | 19.3 | 1.8 | 7D444783F8B94BC883B2C396036EBFCC |  | R22 | Non-TXV |  | -7.103% | 1.071 | 1.989% |  |  |  |  | Non-TXV |  |  | -7.103%
Fresno | CA | 93727-3036 |  | 2013-08-31 | 2013-08-31 12:20 | 2013-08-31 13:44 | TEMPSTAR - PGAD30D1K3 | 78 | 14.7 | Yes | Yes | 19.6 | 18.3 | 1.3 | B6BFCBC7E7784B998BBD11CD7FF376BF | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 18.85% | 0.81154 | 36.22% | [5 empty] | TXV | 18.85%
Fairfield | CA | 94533-5219 |  | 2013-08-22 | 2013-08-22 09:40 | 2013-08-22 15:53 | - 561C1036-D | 84 | 3.4 | Yes | Yes | 14.9 | 17.7 | -2.8 | DBB259089ADD45F0AD8408157EDAA089 |  | R22 | Non-TXV |  | 4.048% | 0.95952 | 7.779% | [5 empty] | Non-TXV | 4.048%
Bakersfield | CA | 93312-5452 |  | 2013-09-26 | 2013-09-26 22:54 | 2013-09-26 22:54 | GOODMAN - SSX140601AE | 268 | 0 | Yes | Yes | 22 | 22.5 | -0.5 | 297C9F5E0EEB4CD1A5CDB37E3DCA623F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3530 |  | 2013-08-15 | 2013-08-15 15:55 | 2013-08-15 15:55 | CARRIER - UNK | 84 | 0 | Yes | Yes | 24.3 | 23.1 | 1.2 | 54C6FA83A23645DBAAA4F0B2D0CC0D5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2435 |  | 2013-08-08 | 2013-08-08 14:30 | 2013-08-08 14:49 | CARRIER - UNK | 80 | 2.5 | Yes | Yes | 23.8 | 20.1 | 3.7 | DD95D481CFAA46B3B631025DD77CCEA4 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Bakersfield | CA | 93306-1901 |  | 2013-08-22 | 2013-08-22 09:40 | 2013-08-22 10:15 | NORDYNE - JS3BC-0421AA | 85 | 6.6 | Yes | Yes | 16.3 | 19.3 | -3 | DD974B5B0B5E430787AF158940804073 |  | R22 | Non-TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | Non-TXV | 7.765%
Fresno | CA | 93722-9184 |  | 2013-08-21 | 2013-08-21 09:03 | 2013-08-21 09:34 | BRYANT - 582ANW036090AAAF | 60 | 1.8 | Yes | Yes | 23.2 | 20.7 | 2.5 | 3B78BC57674F483B8AAAD951CBD4DAF7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Vallejo | CA | 94591-5658 |  | 2013-08-19 | 2013-08-19 13:53 | 2013-08-19 15:03 | SEARS - 867816730 | 37 | 7.4 | Yes | Yes | 14.5 | 17.7 | -3.2 | 39720D577C584E31B3A8DE242E2EB2C8 | Add refrigerant: 15.9 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Suisun City | CA | 94585-1851 |  | 2013-08-23 | 2013-08-23 14:14 | 2013-08-23 14:14 | TRANE - 2YCC3030A1064AA | 88 | 0 | Yes | Yes | 15.2 | 18.2 | -3 | B8D746203C744A41AE555457204457E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95128-1331 |  | 2013-08-26 | 2013-08-26 09:56 | 2013-08-26 09:56 | NORDYNE - FS5BD-048 | 85 | 0 | Yes | Yes | 22.4 | 18.3 | 4.1 | DA4F12715A16416D853BD9F71DA9E6C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2527 |  | 2013-08-21 | 2013-08-21 14:39 | 2013-08-21 15:09 | AMERICAN STANDARD - YCY0484F1H0AB | 85 | 4.5 | Yes | Yes | 26.8 | 20.9 | 5.9 | AFF93F7BA67F40CEB63603E06D2A5438 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
San Jose | CA | 95121-1786 |  | 2013-08-26 | 2013-08-26 14:10 | 2013-08-26 14:10 | OTHER - 561CJ048000-F | 109 | 0 | Yes | Yes | 23.6 | 18.5 | 5.1 | 6A5CFE5BF3C14A109F34901CAAD1AFCA |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6045 |  | 2013-08-21 | 2013-08-21 09:43 | 2013-08-21 10:13 | ICP - PGF336060K01A1 | 85 | 3.9 | Yes | Yes | 20.1 | 19.9 | 0.2 | 460FC567C5754AACAEDB1AAA020064D3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93313-2948 |  | 2013-09-03 | 2013-09-03 10:47 | 2013-09-03 11:07 | OTHER - UNK | 85 | 3.4 | Yes | Yes | 22.3 | 23 | -0.7 | A3F98E8DF9D34F23BF851AC07A5F6338 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93703-3246 |  | 2013-08-08 | 2013-08-08 12:05 | 2013-08-08 12:33 | RUUD - UNK | 66 | 11.8 | Yes | Yes | 26.1 | 22.3 | 3.8 | DDED4B2862AD4E88B73CCDBD42C5E645 |  | R22 | Non-TXV |  | 17.88% | 0.82121 | 34.36% | [5 empty] | Non-TXV | 17.88%
Selma | CA | 93662-4509 |  | 2013-08-21 | 2013-08-21 09:09 | 2013-08-21 09:34 | CARRIER - UNK | 70 | 3.6 | Yes | Yes | 19.8 | 19.4 | 0.4 | AC21766D10D140439E8EA8CD8E52EEA4 |  | R22 | Non-TXV |  | 5.143% | 0.94857 | 9.883% | [5 empty] | Non-TXV | 5.143%
Bakersfield | CA | 93313-2943 |  | 2013-08-15 | 2013-08-15 18:01 | 2013-08-15 18:01 | PAYNE - 585CJ030050 | 78 | 0 | Yes | Yes | 11.4 | 14.4 | -3 | D6BE05F16960454EA814AA4C06078A47 | Add refrigerant: 9.7 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-9323 |  | 2013-10-22 | 2013-10-22 12:48 | 2013-10-22 13:33 | CARRIER - 48GX060115311 | 130 | 4.7 | Yes | Yes | 24 | 21.7 | 2.4 | 49D0FAD09027420D8E4BABC5731A4C25 |  | R22 | Non-TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | Non-TXV | 3.615%
Pittsburg | CA | 94565-7601 |  | 2013-08-30 | 2013-08-30 11:35 | 2013-08-30 11:36 | YORK - H2RC042S06A | 107 | 16.2 | Yes | Yes | 16 | 17 | -1 | 1936A89572E544A5AADCEC7C8AA05029 |  | R22 | Non-TXV |  | 15.14% | 0.8486 | 29.1% | [5 empty] | Non-TXV | 15.14%
Coalinga | CA | 93210-2545 |  | 2013-10-02 | 2013-10-02 14:08 | 2013-10-02 14:08 | OTHER - GR6GDX36K072X | 112 | 0 | Yes | Yes | 21.6 | 19.1 | 2.6 | 91336C8B61C648D0A16845C70DD5B528 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4552 |  | 2013-08-22 | 2013-08-22 12:17 | 2013-08-22 14:59 | DAY & NIGHT - UKN | 85 | 3.3 | Yes | Yes | 25.5 | 21 | 4.5 | 6FDADC24BF6A4814AFD8B1E16C0DAA10 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Arvin | CA | 93203-1717 |  | 2013-08-20 | 2013-08-20 11:00 | 2013-08-20 11:50 | YORK - D1NH042N06506C | 115 | 4.5 | Yes | Yes | 21.7 | 19.9 | 1.9 | 3228DF7E03CE4B0BBF061E53AEB52CD0 |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Bakersfield | CA | 93307-6048 |  | 2013-10-12 | 2013-10-12 08:12 | 2013-10-12 08:29 | YORK - D1NH036N05606C | 108 | 3.7 | Yes | Yes | 21.5 | 21.5 | 0 | 280EE9C4B6734DA3A2F98013496CCAF1 |  | R22 | Non-TXV |  | 3.426% | 0.96574 | 6.584% | [5 empty] | Non-TXV | 3.426%
Fresno | CA | 93726-0336 |  | 2013-08-23 | 2013-08-23 16:25 | 2013-08-23 16:58 | RHEEM - UKN | 85 | 3.5 | Yes | Yes | 21.3 | 19.7 | 1.6 | 67FB56BE483D481AAA91AF41951684F9 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Antioch | CA | 94509-3342 |  | 2013-08-23 | 2013-08-23 09:12 | 2013-08-23 09:12 | RHEEM - RAKA-018JAZ | 46 | 2.2 | Yes | Yes | 17.3 | 17.6 | -0.3 | 25E020039B884784A44F2D4D46E1176F |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Bakersfield | CA | 93313-2930 |  | 2013-09-03 | 2013-09-03 17:01 | 2013-09-03 22:42 | PAYNE - UNK | 85 | 9.9 | Yes | Yes | 19.9 | 22.8 | -2.9 | 7E6177702A3D40CD9F0CB649EF214C97 |  | R22 | Non-TXV |  | 11.65% | 0.88353 | 22.38% | [5 empty] | Non-TXV | 11.65%
Pittsburg | CA | 94565-6479 |  | 2013-08-30 | 2013-08-30 09:17 | 2013-08-30 09:18 | PAYNE - PA13NR048000AHAA | 68 | 4.8 | Yes | Yes | 17.3 | 18.2 | -0.9 | ED53BF72C9A54352A930B07C860D4C02 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Pittsburg | CA | 94565-6479 |  | 2013-08-30 | 2013-08-30 09:19 | 2013-08-30 09:20 | PAYNE - PA13NR048000AHAA | 68 | -5.6 | Yes | Yes | 18.8 | 17.9 | 0.9 | 0F05A49D0A9C491A8C746092FE29EC46 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Antioch | CA | 94509-3355 |  | 2013-08-23 | 2013-08-23 09:31 | 2013-08-23 09:32 | TRANE - 2TTR1018A1000AA | 50 | 3.1 | Yes | Yes | 18.3 | 18.1 | 0.2 | 3D0AB79FD2F6497FBB4F8DDB1AC90630 |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Bakersfield | CA | 93313-3006 |  | 2013-09-10 | 2013-09-10 19:08 | 2013-09-10 19:08 | BRYANT - 585HJW04808ABAF | 118 | 0 | Yes | Yes | 25.6 | 22.8 | 2.8 | E7C37D3F075A438F8DD797A93ECF84B9 | Add refrigerant: 16.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5839 |  | 2013-10-31 | 2013-10-31 10:48 | 2013-10-31 11:06 | RHEEM - RRKA-A036JK06X | 62 | 1.8 | Yes | Yes | 26.9 | 20.9 | 6 | F4A586F135964F79B2541237C57FE978 |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Fairfield | CA | 94534-3012 |  | 2013-09-24 | 2013-09-24 14:45 | 2013-09-24 15:42 | GE - | 85 | -4 | Yes | Yes | 18.8 | 21.5 | -2.7 | 6B9AE66FE0A6435FA12D5F30B8A783BC |  | R22 | Non-TXV |  | -4.706% | 1.0471 | 1.318% |  |  |  |  | Non-TXV |  |  | -4.706%
Fresno | CA | 93702-1743 |  | 2013-08-26 | 2013-08-26 09:50 | 2013-08-26 10:34 | ARCOAIRE - PGF024K060E | 57 | 7.2 | Yes | Yes | 19 | 19.8 | -0.8 | DB039BB34A934E06957885B654F49137 |  | R22 | Non-TXV |  | 12.63% | 0.87368 | 24.28% | [5 empty] | Non-TXV | 12.63%
Bay Point | CA | 94565-6648 |  | 2013-09-11 | 2013-09-11 10:33 | 2013-09-11 14:12 | BRYANT - 661CJ018-E | 68 | 3.2 | Yes | Yes | 21.3 | 24.2 | -2.9 | 245FD69F532344199E779C9048DE391E |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fairfield | CA | 94533-6409 |  | 2013-08-23 | 2013-08-23 12:44 | 2013-08-23 15:25 | LENNOX - HS26-036-2P | 93 | 5.6 | Yes | Yes | 11.3 | 14.2 | -2.9 | 5A332A0515484248BE3BE1E4D96A76FD |  | R22 | Non-TXV |  | 6.022% | 0.93978 | 11.57% | [5 empty] | Non-TXV | 6.022%
Bay Point | CA | 94565-6617 |  | 2013-10-01 | 2013-10-01 09:45 | 2013-10-01 13:24 | BRYANT - 661CJ018-E | 89 | 4.1 | Yes | Yes | 17.8 | 14.4 | 3.4 | E5D63A4CA28147DB95447DB2E15E52B1 |  | R22 | TXV |  | 4.607% | 0.95393 | 8.853% | [5 empty] | TXV | 4.607%
Bay Point | CA | 94565-6619 |  | 2013-09-11 | 2013-09-11 11:38 | 2013-09-11 14:13 | BRYANT - 661CJ018-E | 68 | -4.4 | Yes | Yes | 14.2 | 15.8 | -1.6 | C106D4922DEC4A79A87A32648CBB8811 |  | R22 | Non-TXV |  | -6.471% | 1.0647 | 1.812% |  |  |  |  | Non-TXV |  |  | -6.471%
Bakersfield | CA | 93313-3761 |  | 2013-09-10 | 2013-09-10 18:56 | 2013-09-10 18:58 | OTHER - 13AJA36A01 | 108 | 3.2 | Yes | Yes | 21.5 | 20.4 | 1.1 | 9FB7AFEC700043B8AC292CC237D7AD7C |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Bakersfield | CA | 93306-6072 |  | 2013-09-20 | 2013-09-20 07:26 | 2013-09-20 07:46 | OTHER - PGME60G1152 | 215 | 11 | Yes | Yes | 20.9 | 23.9 | -3 | 8ED5255FED9F4A36A71F056BEE66EED0 |  | R22 | Non-TXV |  | 5.116% | 0.94884 | 9.832% | [5 empty] | Non-TXV | 5.116%
Clovis | CA | 93611-2071 |  | 2013-08-22 | 2013-08-22 11:39 | 2013-08-22 12:16 | HEIL - PGAA42E1K6 | 70 | 4.9 | Yes | Yes | 25.2 | 20.6 | 4.7 | 8C56DE1033A549CB920C6FB02039B2AB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fairfield | CA | 94534-6681 |  | 2013-09-20 | 2013-09-20 15:17 | 2013-09-20 15:17 | CARRIER - 38CKC036350 | 124 | 0 | Yes | Yes | 20.5 | 15.7 | 4.9 | AC7587DE27F340C5800AB38DE15C7611 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3127 |  | 2013-08-21 | 2013-08-21 14:28 | 2013-08-21 15:16 | CARRIER - UNK | 80 | 5.3 | Yes | Yes | 19.9 | 19.2 | 0.7 | 80ECFFEFFE9A483285488DB4497A5677 |  | R22 | Non-TXV |  | 6.625% | 0.93375 | 12.73% | [5 empty] | Non-TXV | 6.625%
Bakersfield | CA | 93305-2424 |  | 2013-09-12 | 2013-09-12 19:36 | 2013-09-12 19:38 | BRYANT - 57ANW048090NA-- | 193 | 7 | Yes | Yes | 22.7 | 20.2 | 2.6 | 708E056045494A51B4EDFEE8EFA094AD |  | R22 | Non-TXV |  | 3.627% | 0.96373 | 6.97% | [5 empty] | Non-TXV | 3.627%
Selma | CA | 93662-4225 |  | 2013-08-21 | 2013-08-21 10:22 | 2013-08-21 10:57 | RUUD - UNK | 70 | 16.9 | Yes | Yes | 19.7 | 19.9 | -0.2 | 85367D34E4A64E3390D2762821B284D4 |  | R22 | Non-TXV |  | 24.14% | 0.75857 | 46.4% | [5 empty] | Non-TXV | 24.14%
Fairfield | CA | 94533-3628 |  | 2013-08-27 | 2013-08-27 11:12 | 2013-08-27 13:08 | OTHER - 561AJ048-D | 112 | 4.2 | Yes | Yes | 13.3 | 16 | -2.7 | 501980FD2434455CADB398FDB8A7EB61 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Fairfield | CA | 94534-7443 |  | 2013-09-20 | 2013-09-20 13:41 | 2013-09-20 13:41 | CARRIER - 1889E87113 | 117 | 0 | Yes | Yes | 18.9 | 16.1 | 2.8 | 8CAD097573E346D88AEB00FFA56456B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5200 |  | 2013-09-10 | 2013-09-10 19:57 | 2013-09-10 20:00 | OTHER - AC060X121A | 147 | 8.6 | Yes | Yes | 21 | 20.7 | 0.3 | F28A7359E4DB4414BEF789BE39360C28 |  | R22 | Non-TXV |  | 5.85% | 0.9415 | 11.24% | [5 empty] | Non-TXV | 5.85%
Bakersfield | CA | 93312-4105 |  | 2013-09-04 | 2013-09-04 19:25 | 2013-09-04 19:26 | DAY & NIGHT - 593CJX060000AAAA | 133 | -5.6 | Yes | Yes | 20.6 | 21 | -0.4 | EF100B82B84C40C292C9B919D7A21E54 |  | R22 | TXV |  | -4.211% | 1.0421 | 1.179% |  |  |  |  | TXV |  |  | -4.211%
Antioch | CA | 94509-4419 |  | 2013-08-23 | 2013-08-23 11:07 | 2013-08-23 11:07 | RUUD - UAKA-037JAZ | 97 | 0 | Yes | Yes | 16 | 17 | -1 | 7BAA55C6FC9045A2B3466192BBE26AFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3120 |  | 2013-08-26 | 2013-08-26 11:10 | 2013-08-26 11:10 | OTHER - PGCM042K080D | 86 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 06CE9E4AF46E46F49E4203DB0A1A0DDF | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-6005 |  | 2013-08-16 | 2013-08-16 11:36 | 2013-08-16 12:07 | YORK - DBYPF060N110A | 140 | -9.9 | Yes | Yes | 23.6 | 18.8 | 4.8 | 5EE7E7F04C794E5EA32B660110BF5A0E |  | R22 | Non-TXV |  | -7.071% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.071%
Fresno | CA | 93722-4353 |  | 2013-08-16 | 2013-08-16 10:30 | 2013-08-16 11:05 | LENNOX - 12GCS036752PA | 110 | 4.2 | Yes | Yes | 21.7 | 19.3 | 2.4 | 1C789D2986064DB99593FEC0FAFD7A56 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Bakersfield | CA | 93309-4429 |  | 2013-08-20 | 2013-08-20 20:24 | 2013-08-20 20:28 | RHEEM - RRRL-C048JK10X | 169 | 6.8 | Yes | Yes | 22.5 | 19.7 | 2.8 | 86F9CF3E050B4B5CBF80479DA118F36B |  | R410A | TXV |  | 4.024% | 0.95976 | 7.733% | [5 empty] | TXV | 4.024%
Bakersfield | CA | 93312-6442 |  | 2013-08-19 | 2013-08-19 09:40 | 2013-08-19 10:31 | OTHER - 563CN042-D | 122 | -9.3 | Yes | Yes | 16.5 | 19.3 | -2.8 | 9E1DC97C9F2643B99C833BEF7A9EE852 |  | R22 | Non-TXV |  | -7.623% | 1.0762 | 2.135% |  |  |  |  | Non-TXV |  |  | -7.623%
Pittsburg | CA | 94565-2470 |  | 2013-08-29 | 2013-08-29 09:16 | 2013-08-29 09:47 | ALLEGIANCE - 7A0024A100A2 | 67 | 2.9 | Yes | Yes | 18.6 | 17.6 | 1 | B0A23B119F3A4A748BD94FE9005BC383 |  | R22 | Non-TXV |  | 4.328% | 0.95672 | 8.318% | [5 empty] | Non-TXV | 4.328%
Fairfield | CA | 94533-2313 |  | 2013-08-27 | 2013-08-27 09:45 | 2013-08-27 13:05 | GOODMAN - CK30-1A | 76 | 2.5 | Yes | Yes | 15.3 | 18.3 | -3 | CDF10499A50A4055A199C411E465AB18 |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Bakersfield | CA | 93309-4638 |  | 2013-08-26 | 2013-08-26 15:18 | 2013-08-26 15:18 | ICP - X100673008 | 64 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | D842BFF9C5B942EAB86E296447AA9DF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3042 |  | 2013-08-16 | 2013-08-16 11:52 | 2013-08-16 11:52 | DAY & NIGHT - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C7D2DE4F63E741988CA1793BCA60D6B5 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-1814 |  | 2013-08-19 | 2013-08-19 11:48 | 2013-08-19 12:14 | RUUD - UAMB-060JAZ | 85 | -8 | Yes | Yes | 16.8 | 19.8 | -3 | F8F4AF1E85BB4345A190AC56BE917CE5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93308-5167 |  | 2013-08-20 | 2013-08-20 10:11 | 2013-08-20 11:41 | OTHER - AC042X1221A | 107 | 5.6 | Yes | Yes | 24.4 | 23.4 | 1 | 3A789507EC4A4827A1CDA6B20B650396 |  | R22 | Non-TXV |  | 5.234% | 0.94766 | 10.06% | [5 empty] | Non-TXV | 5.234%
Lost Hills | CA | 93249-0000 |  | 2013-08-29 | 2013-08-29 16:18 | 2013-08-29 16:21 | OTHER - PGAA36C1K4 | 69 | 2.5 | Yes | Yes | 20.7 | 20.4 | 0.3 | 413CAFCBE5E3435C942D5454F2B5CA27 |  | R22 | Non-TXV |  | 3.623% | 0.96377 | 6.963% | [5 empty] | Non-TXV | 3.623%
Fairfield | CA | 94533-1865 |  | 2013-08-30 | 2013-08-30 14:21 | 2013-08-30 14:21 | GOODMAN - CRT36-1A | 140 | 0 | Yes | Yes | 18.8 | 20.9 | -2.1 | A05AE743DEDD4075B2C1C5576C5815F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95110-2829 |  | 2013-09-24 | 2013-09-24 13:51 | 2013-09-24 15:47 | CARRIER - 38H030 | 72 | 3 | Yes | Yes | 20 | 20.7 | -0.7 | 82A74F2CF3A8428B99741CA5F8EB5AD2 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Bakersfield | CA | 93309-4685 |  | 2013-08-26 | 2013-08-26 15:34 | 2013-08-26 15:34 | OTHER - UKN | 65 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 7182AA0B3A8C4EADA7BCB2A35DAEF45E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-8337 |  | 2013-09-04 | 2013-09-04 15:13 | 2013-09-04 16:04 | TRANE - YCC042F1M0BE | 104 | 18 | Yes | Yes | 24.9 | 20.9 | 4 | 94700DA9E4D94239BC54EED5B754D6BE |  | R22 | Non-TXV |  | 17.31% | 0.82692 | 33.26% | [5 empty] | Non-TXV | 17.31%
Bay Point | CA | 94565-6645 |  | 2013-09-11 | 2013-09-11 13:53 | 2013-09-11 14:11 | BRYANT - 661CJ018-E | 68 | -4.4 | Yes | Yes | 14.5 | 17.1 | -2.6 | 5E3AA473230942C99CC1D2085D4D98FD |  | R22 | Non-TXV |  | -6.471% | 1.0647 | 1.812% |  |  |  |  | Non-TXV |  |  | -6.471%
Bay Point | CA | 94565-6649 |  | 2013-09-11 | 2013-09-11 09:03 | 2013-09-11 14:09 | BRYANT - 661CJ91-E | 68 | -4 | Yes | Yes | 15.2 | 17.7 | -2.5 | 2113650A465D43CB84C5E99DEE490A4B |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93711-3901 |  | 2013-08-22 | 2013-08-22 10:34 | 2013-08-22 11:02 | - H2CB042506A | 108 | -6.4 | Yes | Yes | 18.5 | 20.7 | -2.2 | D371C548541F443AB96745C29A75A29F |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Fresno | CA | 93711-2739 |  | 2013-09-11 | 2013-09-11 12:24 | 2013-09-11 12:40 | BRYANT - 588ANW036080ACAF | 68 | 4.6 | Yes | Yes | 19.9 | 20.2 | -0.3 | 0D310DB8A916488B807EA9AF643BED49 |  | R22 | TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | TXV | 6.765%
Fresno | CA | 93711-2739 |  | 2013-09-11 | 2013-09-11 12:43 | 2013-09-11 12:43 | GOODMAN - GPG153609041AB | 94 | 0 | Yes | Yes | 24.8 | 21.2 | 3.6 | 1566BEBEBFB4499C86DF3DF7141B4078 |  | R410A | TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-0000 |  | 2013-09-23 | 2013-09-23 13:20 | 2013-09-23 13:38 | LENNOX - 13ACD03623002 | 111 | 3.6 | Yes | Yes | 20.3 | 19.2 | 1.2 | 1C775E69981A416B9D1DA1C660B2E1E1 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Lemoore | CA | 93245-0000 |  | 2013-09-23 | 2013-09-23 13:40 | 2013-09-23 13:40 | LENNOX - 13ACD03623002 | 111 | 0 | Yes | Yes | 20.8 | 19.6 | 1.2 | 0550258F4C4E4C63807F386561BEF0E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6444 |  | 2013-09-05 | 2013-09-05 14:48 | 2013-09-05 14:48 | CARRIER - 38CKC042300 | 85 | 0 | Yes | Yes | 21 | 17.4 | 3.6 | FB8E1E59803941D9A0448747FE2474B0 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-4105 |  | 2013-08-17 | 2013-08-17 09:55 | 2013-08-17 10:28 | YORK - H20H036S06B | 124 | -15 | Yes | Yes | 17.8 | 19.9 | -2.1 | 94D05E1CA3EE4D99AF793679DF2564FE |  | R22 | TXV |  | -12.1% | 1.121 | 3.388% |  |  |  |  | TXV |  |  | -12.1%
Pittsburg | CA | 94565-3749 |  | 2013-09-04 | 2013-09-04 09:03 | 2013-09-04 09:08 | CARRIER - 38BRC048370 | 136 | 5 | Yes | Yes | 17.2 | 17 | 0.2 | 837B5A7CDB1F4947B57C3B77F654D3F1 |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Bakersfield | CA | 93313-5443 |  | 2013-09-17 | 2013-09-17 13:01 | 2013-09-17 13:01 | GOODMAN - CLJ42-1A | 85 | 0 | Yes | Yes | 22.4 | 22.4 | 0 | 3051B38F1FD14D0582563A23F41AA9EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4647 |  | 2013-09-05 | 2013-09-05 09:35 | 2013-09-05 10:40 | CARRIER - NA | 72 | 9.4 | Yes | Yes | 16.1 | 17 | -0.9 | CA7348D2D61C4A19A623D0D6A7EC0870 |  | R22 | Non-TXV |  | 13.06% | 0.86944 | 25.09% | [5 empty] | Non-TXV | 13.06%
Lemoore | CA | 93245-4445 |  | 2013-08-28 | 2013-08-28 09:35 | 2013-08-28 09:52 | RHEEM - EAFF037JAZ | 94 | 7.6 | Yes | Yes | 19.6 | 19.3 | 0.3 | 98B58FB167874BF28804207CA2E29E7D |  | R22 | Non-TXV |  | 8.085% | 0.91915 | 15.54% | [5 empty] | Non-TXV | 8.085%
Lemoore | CA | 93245-4445 |  | 2013-08-28 | 2013-08-28 09:55 | 2013-08-28 10:24 | RHEEM - EAFF037JAZ | 94 | 5.3 | Yes | Yes | 19.5 | 17.7 | 1.9 | C37823F110B744E5A4505ABBA48AFAFB |  | R22 | Non-TXV |  | 5.638% | 0.94362 | 10.84% | [5 empty] | Non-TXV | 5.638%
San Jose | CA | 95148-3666 |  | 2013-09-18 | 2013-09-18 14:13 | 2013-09-18 15:26 | TRANE - 2TTB3024A1000AA | 82 | 4.1 | Yes | Yes | 20.3 | 20.1 | 0.3 | 86D420C6E0974358909B0EE2C8E9C6AB |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Vacaville | CA | 95687-7311 |  | 2013-08-22 | 2013-08-22 12:42 | 2013-08-22 15:58 | TRANE - 2TTB0042A1000AA | 95 | -3.7 | Yes | Yes | 13.7 | 16.2 | -2.5 | 726E8048319A4482A369B83C59B56A00 |  | R22 | Non-TXV |  | -3.895% | 1.0389 | 1.091% |  |  |  |  | Non-TXV |  |  | -3.895%
Hayward | CA | 94544-6433 |  | 2013-09-10 | 2013-09-10 13:36 | 2013-09-10 13:36 | GOODMAN - CK30-1B | 85 | 0 | Yes | Yes | 23 | 18.3 | 4.8 | 50C255265969445A8B897936D062029A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5336 |  | 2013-10-01 | 2013-10-01 08:37 | 2013-10-01 09:03 | AMERICAN STANDARD - 2A7B3030A1000AA | 88 | 2.8 | Yes | Yes | 22.3 | 17.7 | 4.6 | 5E25F9FA207843C1A5312914A8279582 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Bakersfield | CA | 93309-6461 |  | 2013-08-26 | 2013-08-26 10:54 | 2013-08-26 11:39 | RHEEM - RRNL- B036JK06X | 85 | 2.6 | Yes | Yes | 19.5 | 20.7 | -1.2 | ABF391A91ACA4CE68FD481BC93F7CFC9 |  | R410A | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93309-4685 |  | 2013-08-26 | 2013-08-26 16:17 | 2013-08-26 16:37 | ICP - CA5524VKD3 | 73 | 9.9 | Yes | Yes | 21.6 | 21 | 0.6 | 1A7C549880924C849991B224AED31E78 |  | R22 | Non-TXV |  | 13.56% | 0.86438 | 26.06% | [5 empty] | Non-TXV | 13.56%
Fresno | CA | 93722-7009 |  | 2013-08-16 | 2013-08-16 12:25 | 2013-08-16 13:08 | TEMPSTAR - NCA9036VKA1 | 140 | 11.3 | Yes | Yes | 19.6 | 19.6 | 0 | 56313A3D517D413AA126BA5FD66DDFFB |  | R22 | Non-TXV |  | 8.071% | 0.91929 | 15.51% | [5 empty] | Non-TXV | 8.071%
Bakersfield | CA | 93309-4638 |  | 2013-08-26 | 2013-08-26 15:21 | 2013-08-26 15:21 | YORK - H4DB018S061A | 62 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | A64F48ED1EFC44D38E9AB535BB51A832 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4166 |  | 2013-08-27 | 2013-08-27 12:34 | 2013-08-27 12:53 | OTHER - PGC060K100C | 136 | 5.2 | Yes | Yes | 19.6 | 20.8 | -1.2 | E455037716774C63B7946009632E8D3B |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Fresno | CA | 93706-4746 |  | 2013-08-16 | 2013-08-16 10:12 | 2013-08-16 10:34 | GOODMAN - GPG13360451AB | 112 | 8.5 | Yes | Yes | 24 | 20.1 | 3.9 | D27484B667E543CA8514579D993B5418 |  | R22 | Non-TXV |  | 7.589% | 0.92411 | 14.58% | [5 empty] | Non-TXV | 7.589%
Antioch | CA | 94531-9120 |  | 2013-08-23 | 2013-08-23 10:26 | 2013-08-23 10:26 | OTHER - CKL49-1 | 90 | 0 | Yes | Yes | 18.6 | 17 | 1.6 | 8D88AE42881B43AB8827D373197C501D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-4022 |  | 2013-08-26 | 2013-08-26 13:24 | 2013-08-26 13:51 | CARRIER - 24AB330A320 | 64 | 4.1 | Yes | Yes | 19.1 | 18.8 | 0.3 | 5DBC3999F81F4B2D9B087C3546508ADA |  | R22 | Non-TXV |  | 6.406% | 0.93594 | 12.31% | [5 empty] | Non-TXV | 6.406%
Antioch | CA | 94509-3349 |  | 2013-09-10 | 2013-09-10 09:05 | 2013-09-10 09:08 | OTHER - AC018M1021A | 49 | 2 | Yes | Yes | 16.7 | 17.1 | -0.4 | 10870FEAEA3F46FA861F855393276D1B |  | R22 | Non-TXV |  | 4.082% | 0.95918 | 7.844% | [5 empty] | Non-TXV | 4.082%
Fresno | CA | 93711-1352 |  | 2013-08-26 | 2013-08-26 16:55 | 2013-08-26 18:03 | DAY & NIGHT - UKN | 80 | 4.1 | Yes | Yes | 18.7 | 20.8 | -2.1 | B5499B25E6C542989CDE5685D86DDFAD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.125% | 0.94875 | 9.849% | [5 empty] | Non-TXV | 5.125%
Fresno | CA | 93722-7009 |  | 2013-08-16 | 2013-08-16 11:57 | 2013-08-16 12:22 | OTHER - CA9036VKA1 | 140 | 5.9 | Yes | Yes | 23.7 | 20.2 | 3.5 | 97DF824BA7214A35AB5244EB3B940AEE |  | R22 | Non-TXV |  | 4.214% | 0.95786 | 8.099% | [5 empty] | Non-TXV | 4.214%
Bakersfield | CA | 93308-1420 |  | 2013-08-20 | 2013-08-20 13:17 | 2013-08-20 14:18 | NORDYNE - D1NH036N05606C | 85 | 5.8 | Yes | Yes | 19.7 | 20.5 | -0.8 | 6071329B3C554DA49C29673E3FACEDBC |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Bakersfield | CA | 93309-8740 |  | 2013-08-23 | 2013-08-23 10:57 | 2013-08-23 11:17 | OTHER - UNK | 85 | 10.2 | Yes | Yes | 18.8 | 21.5 | -2.7 | B2B52196DB4847D2AEC2DDDC310F6167 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Antioch | CA | 94509-3369 |  | 2013-09-26 | 2013-09-26 09:43 | 2013-09-26 09:44 | OTHER - NA | 66 | 2.4 | Yes | Yes | 16.8 | 17 | -0.2 | 45CEC4CED60E4282B8382EF7A7C11E0B |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Bakersfield | CA | 93309-4679 |  | 2013-10-08 | 2013-10-08 18:34 | 2013-10-08 18:55 | GOODMAN - GSC130181AE | 89 | 6 | Yes | Yes | 22.1 | 21.5 | 0.6 | E5E78FB955CC4F6AB60B58CCDFE7D79C |  | R22 | Non-TXV |  | 6.742% | 0.93258 | 12.96% | [5 empty] | Non-TXV | 6.742%
Fairfield | CA | 94533-7051 |  | 2013-08-26 | 2013-08-26 11:23 | 2013-08-26 15:35 | OTHER - | 85 | -6 | Yes | Yes | 14.8 | 17.6 | -2.8 | 3C3CEEC475EB43969A64B369CB4F7938 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Taft | CA | 93268-4459 |  | 2013-09-23 | 2013-09-23 19:04 | 2013-09-23 19:07 | AMANA - PGA060B0902A | 151 | -8 | Yes | Yes | 24.7 | 20.8 | 4 | DA46C4BEBEBF4F0895315830874DB99A |  | R22 | TXV |  | -5.298% | 1.053 | 1.484% |  |  |  |  | TXV |  |  | -5.298%
Bakersfield | CA | 93313-5553 |  | 2013-08-22 | 2013-08-22 09:52 | 2013-08-22 10:08 | UNITARY PRODUCTS GROUP - H4DH036S06A | 95 | 7.7 | Yes | Yes | 21.6 | 20.2 | 1.4 | E7B9E485A3134ED9A443530AD740C543 |  | R22 | Non-TXV |  | 8.105% | 0.91895 | 15.58% | [5 empty] | Non-TXV | 8.105%
Bakersfield | CA | 93313-5553 |  | 2013-08-22 | 2013-08-22 10:10 | 2013-08-22 10:31 | YORK - HADOH030S06A | 103 | 3.2 | Yes | Yes | 19.6 | 20.1 | -0.5 | 07E365A090FD4A3D936D180F206150FB |  | R22 | Non-TXV |  | 3.107% | 0.96893 | 5.971% | [5 empty] | Non-TXV | 3.107%
Fresno | CA | 93722-3725 |  | 2013-08-16 | 2013-08-16 11:07 | 2013-08-16 11:55 | RHEEM - RAKA048JAZ | 103 | 4.7 | Yes | Yes | 18.8 | 20.2 | -1.4 | 5D60C4D5FA1F45D78D670A602A675B13 |  | R22 | TXV |  | 4.563% | 0.95437 | 8.769% | [5 empty] | TXV | 4.563%
Antioch | CA | 94509-3364 |  | 2013-08-23 | 2013-08-23 12:00 | 2013-08-23 12:01 | RHEEM - AT-J8B1 | 64 | 12.6 | Yes | Yes | 16.6 | 17.6 | -1 | CFA95BCF8F43472B8DACF86F43BB71D1 |  | R22 | Non-TXV |  | 19.69% | 0.80312 | 37.84% | [5 empty] | Non-TXV | 19.69%
Shafter | CA | 93263-3427 |  | 2013-09-03 | 2013-09-03 20:54 | 2013-09-03 21:02 | GOODMAN - PGB042075-1 | 68 | -3.7 | Yes | Yes | 27.2 | 21.5 | 5.7 | FEAA9D43D53F43929C048AC345B32751 |  | R22 | Non-TXV |  | -5.441% | 1.0544 | 1.524% |  |  |  |  | Non-TXV |  |  | -5.441%
Bakersfield | CA | 93309-1266 |  | 2013-09-16 | 2013-09-16 11:36 | 2013-09-16 12:25 | YORK - D1NA030N056060 | 76 | 2.4 | Yes | Yes | 22.1 | 19.5 | 2.6 | EA747C6F187E4D71A68F70245A5D1713 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Fresno | CA | 93726-5903 |  | 2013-08-30 | 2013-08-30 11:25 | 2013-08-30 12:08 | CARRIER - UKN | 106 | 4 | Yes | Yes | 24.3 | 21.5 | 2.8 | 115F1AC16161400DB71F6F19E9411F4D |  | R22 | Non-TXV |  | 3.774% | 0.96226 | 7.252% | [5 empty] | Non-TXV | 3.774%
Bakersfield | CA | 93309-6381 |  | 2013-09-04 | 2013-09-04 14:57 | 2013-09-04 14:57 | RHEEM - UKN | 120 | 0 | Yes | Yes | 21.6 | 20.8 | 0.8 | 9DC1D14CBC6C41B599CFF5C76EB9020F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3001 |  | 2013-09-05 | 2013-09-05 11:59 | 2013-09-05 12:46 | YORK - D1NH042N06506C | 94 | 9.7 | Yes | Yes | 26.2 | 20.4 | 5.8 | E874F8EFE90448F5AD6C4B202A838B1C |  | R22 | Non-TXV |  | 10.32% | 0.89681 | 19.83% | [5 empty] | Non-TXV | 10.32%
Fresno | CA | 93722-9144 |  | 2013-08-28 | 2013-08-28 16:47 | 2013-08-28 17:15 | DAY & NIGHT - UKN | 80 | 3.5 | Yes | Yes | 24.1 | 19.1 | 5 | 9854DEA88C094C9EAD57815D20DBF282 |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Antioch | CA | 94509-3359 |  | 2013-08-26 | 2013-08-26 09:15 | 2013-08-26 09:16 | OTHER - NA | 72 | 2.3 | Yes | Yes | 18.2 | 17.9 | 0.3 | E74CFD8934534FFCBB95BCE2A625444B |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Bakersfield | CA | 93313-5409 |  | 2013-10-10 | 2013-10-10 11:35 | 2013-10-10 11:51 | ICP - CA9042VKD2 | 128 | 7.9 | Yes | Yes | 20.9 | 22 | -1.1 | 5F54DED944354C4E9D3A891872BA84A6 |  | R22 | Non-TXV |  | 6.172% | 0.93828 | 11.86% | [5 empty] | Non-TXV | 6.172%
Fresno | CA | 93704-2132 |  | 2013-08-17 | 2013-08-17 16:39 | 2013-08-17 17:33 | LENNOX - 10GCS036X753PA | 58 | 1.9 | Yes | Yes | 22.7 | 19.9 | 2.8 | D49ADB6635A34F96962095C0A5D5C2CB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.276% | 0.96724 | 6.295% | [5 empty] | Non-TXV | 3.276%
Antioch | CA | 94509-3329 |  | 2013-08-30 | 2013-08-30 10:29 | 2013-08-30 10:30 | OTHER - NA | 72 | 2.2 | Yes | Yes | 16.8 | 17.6 | -0.8 | 0112D28BD95B4A0392D5611E03EE9D39 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Bakersfield | CA | 93306-1241 |  | 2013-08-22 | 2013-08-22 10:19 | 2013-08-22 11:02 | PAYNE - TZAA-348-2A757 | 85 | 3.6 | Yes | Yes | 17.2 | 20.2 | -3 | 42498560D4C84715B10C11064BA4FF54 |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Bakersfield | CA | 93313-5411 |  | 2013-08-22 | 2013-08-22 10:33 | 2013-08-22 11:31 | RUUD - UAMB 048JAZ | 129 | 5.7 | Yes | Yes | 23 | 19.5 | 3.5 | 9B51D6809811488E9B6C6CDCCFF92AB5 |  | R22 | Non-TXV |  | 4.419% | 0.95581 | 8.492% | [5 empty] | Non-TXV | 4.419%
Bakersfield | CA | 93305-2331 |  | 2013-08-27 | 2013-08-27 15:10 | 2013-08-27 15:35 | OTHER - ABBD-F036SB | 85 | -5 | Yes | Yes | 17.5 | 15.3 | 2.2 | 8CF3BE9BBE5843DB9F97D14718E9EB0B |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93723-9227 |  | 2013-08-27 | 2013-08-27 09:09 | 2013-08-27 09:27 | GOODMAN - PGJ0360751B | 72 | 2.2 | Yes | Yes | 14.2 | 17.1 | -2.9 | 7D6409FADA17433F9F86967EDC6C8B05 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Bakersfield | CA | 93306-1240 |  | 2013-08-22 | 2013-08-22 11:07 | 2013-08-22 12:20 | OTHER - HAC236AKCA | 85 | 2.5 | Yes | Yes | 18.9 | 21.8 | -2.9 | 3356E3A499824056B55E792E958655DF |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93309-6015 |  | 2013-09-24 | 2013-09-24 22:18 | 2013-09-24 22:18 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 6DEFFE5F1D554BAB8FBBA162343CB827 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-2564 |  | 2013-10-16 | 2013-10-16 12:24 | 2013-10-16 12:54 | CARRIER - 38HDL030301 | 83 | 4.6 | Yes | Yes | 24.2 | 19.9 | 4.3 | DFD8E4AB77BA4EC3B0904FD203A5F85D |  | R22 | Non-TXV |  | 5.542% | 0.94458 | 10.65% | [5 empty] | Non-TXV | 5.542%
Kerman | CA | 93630-1204 |  | 2013-09-23 | 2013-09-23 12:15 | 2013-09-23 12:48 | YORK - D1NA036N05606A | 63 | 4 | Yes | Yes | 21.6 | 20.4 | 1.2 | E862A0820936449695D39E8C9633A76C |  | R22 | TXV |  | 6.349% | 0.93651 | 12.2% | [5 empty] | TXV | 6.349%
Bakersfield | CA | 93308-3600 |  | 2013-08-20 | 2013-08-20 11:46 | 2013-08-20 12:16 | RUUD - UNK | 85 | 4 | Yes | Yes | 15.7 | 18 | -2.3 | 43046C862CD34D28B9CE31853B7C3C2A |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Bakersfield | CA | 93308-3600 |  | 2013-08-20 | 2013-08-20 12:31 | 2013-08-20 13:13 | RUUD - UNK | 85 | 2.5 | Yes | Yes | 16.5 | 19.5 | -3 | F50552F0F7F34E6AB92A0DF969FC18A2 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93722-3174 |  | 2013-08-21 | 2013-08-21 11:33 | 2013-08-21 12:15 | CARRIER - 48SX036060321AA | 84 | 4.2 | Yes | Yes | 17 | 19.3 | -2.3 | A804F0D039AE4873BC69BDF3187EBC58 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93711-1321 |  | 2013-08-22 | 2013-08-22 14:38 | 2013-08-22 14:38 | YORK - D1NH0480N09006C | 80 | 0 | Yes | Yes | 44 | 25.3 | 18.7 | 564512C59EA242D8AE31938DCA1951AB | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4668 |  | 2013-08-21 | 2013-08-21 12:38 | 2013-08-21 13:09 | DAY & NIGHT - UKN | 80 | 4.8 | Yes | Yes | 22.4 | 19.9 | 2.5 | 69BE4638458E45A39E5C8F7F68F3F017 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Anderson | CA | 96007-9481 |  | 2013-09-04 | 2013-09-04 09:45 | 2013-09-04 10:27 | ALLEGIANCE - 4A7A4048B1000AA | 127 | 14.8 | Yes | Yes | 24.1 | 19.7 | 4.4 | 662B839DBE514299B14ADC54612E6F67 |  | R410A | TXV |  | 11.65% | 0.88346 | 22.4% | [5 empty] | TXV | 11.65%
Bakersfield | CA | 93304-6105 |  | 2013-08-28 | 2013-08-28 13:56 | 2013-08-29 08:24 | OTHER - UNK | 85 | 9.1 | Yes | Yes | 20 | 22.1 | -2.1 | 2A3FC0C4435A431F8AA9F1D7C71AC1B1 |  | R22 | Non-TXV |  | 10.71% | 0.89294 | 20.57% | [5 empty] | Non-TXV | 10.71%
Lemoore | CA | 93245-2159 |  | 2013-08-29 | 2013-08-29 13:53 | 2013-08-29 14:41 | CARRIER - UKN | 80 | 4 | Yes | Yes | 21.3 | 20.7 | 0.6 | 0E621EB8F9DE4A8598EE3A4EA87AF511 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93722-4673 |  | 2013-08-21 | 2013-08-21 12:16 | 2013-08-21 12:37 | DAY & NIGHT - UKN | 80 | 4.2 | Yes | Yes | 21.1 | 19.8 | 1.3 | 6C860CC726B542A182B2A240CCCF25FC |  | R22 | Non-TXV |  | 5.25% | 0.9475 | 10.09% | [5 empty] | Non-TXV | 5.25%
Vacaville | CA | 95687-6236 |  | 2013-08-21 | 2013-08-21 09:51 | 2013-08-21 15:00 | GUARDIAN - GCGD48S41S3A | 73 | 3.4 | Yes | Yes | 13.5 | 16.5 | -3 | E9DAD251ACA74E8D8F230DAFF41584AF |  | R22 | Non-TXV |  | 4.658% | 0.95342 | 8.951% | [5 empty] | Non-TXV | 4.658%
Fresno | CA | 93722-4371 |  | 2013-08-21 | 2013-08-21 10:22 | 2013-08-21 11:30 | YORK - D1NP030N05606A | 73 | 4.2 | Yes | Yes | 20 | 19.8 | 0.2 | 58E18B7120384497A1D4931EA4C5DA6F |  | R22 | Non-TXV |  | 5.753% | 0.94247 | 11.06% | [5 empty] | Non-TXV | 5.753%
Lemoore | CA | 93245-3465 |  | 2013-09-18 | 2013-09-18 10:10 | 2013-09-18 10:35 | OTHER - PGAD36D1K5 | 102 | 3.1 | Yes | Yes | 21.6 | 19.3 | 2.3 | C157F0E6A0CD4BD3850E54E4A6B12ED5 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Fresno | CA | 93722-4370 |  | 2013-08-21 | 2013-08-21 10:54 | 2013-08-21 11:26 | GOODMAN - UNK | 80 | 2.4 | Yes | Yes | 20.3 | 19.5 | 0.8 | 1D6C3BA7A5A14228AB235DD9C88BBA95 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fairfield | CA | 94533-8978 |  | 2013-09-10 | 2013-09-10 10:24 | 2013-09-10 13:54 | CARRIER - 38CKC036350 | 75 | 8.2 | Yes | Yes | 17.7 | 18.7 | -1 | 25DAA05A9C764D239B02F1515AABE879 |  | R22 | Non-TXV |  | 10.93% | 0.89067 | 21.01% | [5 empty] | Non-TXV | 10.93%
Fresno | CA | 93704-5626 |  | 2013-08-17 | 2013-08-17 14:01 | 2013-08-17 15:28 | OTHER - PGF336060K1A1 | 176 | -12.4 | Yes | Yes | 23.2 | 24.8 | -1.6 | 79A9105B2CC8452B991023B151D65CAB |  | R22 | Non-TXV |  | -7.045% | 1.0705 | 1.973% |  |  |  |  | Non-TXV |  |  | -7.045%
Pittsburg | CA | 94565-5602 |  | 2013-10-25 | 2013-10-25 10:15 | 2013-10-25 10:16 | TRANE - 2TTR2036A1000AA | 96 | -6.8 | Yes | Yes | 18.1 | 17 | 1.1 | E86DF022668840B8A3BC2699BDE12FAD |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
San Jose | CA | 95128-4225 |  | 2013-08-26 | 2013-08-26 10:27 | 2013-08-26 10:59 | OTHER - 561CJ060-A | 233 | 12.3 | Yes | Yes | 23.6 | 17.7 | 5.9 | 4EC5B54FFB9C4D1F9DEDD842A5C8B723 |  | R22 | TXV |  | 5.279% | 0.94721 | 10.15% | [5 empty] | TXV | 5.279%
Fresno | CA | 93727-5680 |  | 2013-08-15 | 2013-08-15 13:43 | 2013-08-15 14:07 | LENNOX - HS290485P | 88 | -3.9 | Yes | Yes | 19.5 | 18.9 | 0.6 | 9FD3C17BF25149BD9BF7C89579FEF23A |  | R22 | Non-TXV |  | -4.432% | 1.0443 | 1.241% |  |  |  |  | Non-TXV |  |  | -4.432%
Lemoore | CA | 93245-2076 |  | 2013-10-11 | 2013-10-11 10:00 | 2013-10-11 10:46 | TEMPSTAR - PGA04201K3 | 180 | 6.8 | Yes | Yes | 20.7 | 18.2 | 2.5 | 2FFC67CB7BD748168F2DF934BF5CC638 |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Lemoore | CA | 93245-5289 |  | 2013-08-27 | 2013-08-27 11:25 | 2013-08-27 11:46 | YORK - H1RD042S06G | 152 | 7.6 | Yes | Yes | 20 | 20.4 | -0.4 | 2BD4CE6CBF43403CAD0622ED8B1D8C6C |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93702-3015 |  | 2013-08-26 | 2013-08-26 11:26 | 2013-08-26 12:03 | GOODMAN - PGB0240751REVA | 54 | 2.1 | Yes | Yes | 20.7 | 20.8 | -0.1 | C46C6552CDCA4F2384DF762FC5A501BD |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Fresno | CA | 93722-9102 |  | 2013-08-22 | 2013-08-22 15:35 | 2013-08-22 16:17 | DAY & NIGHT - 585EJ036075 | 82 | 3.4 | Yes | Yes | 20.2 | 18.3 | 1.9 | D7018F3FB87A498DA6A83134E455CABB |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Concord | CA | 94520-4303 |  | 2013-09-05 | 2013-09-05 11:01 | 2013-09-05 11:02 | PAYNE - PA10JA030-G | 77 | -3.7 | Yes | Yes | 15.6 | 17.1 | -1.5 | ADDC662A1F244231B41D6FF05A6116B5 |  | R22 | TXV |  | -4.805% | 1.0481 | 1.346% |  |  |  |  | TXV |  |  | -4.805%
Redding | CA | 96002-1804 |  | 2013-09-03 | 2013-09-03 13:52 | 2013-09-03 14:56 | CONCORD - RPG10B36D075LA-9B | 58 | 6.5 | Yes | Yes | 25.3 | 21 | 4.3 | 6FE774E3481744F7BD0CBB8CC1FF4BE5 |  | R22 | Non-TXV |  | 11.21% | 0.88793 | 21.54% | [5 empty] | Non-TXV | 11.21%
Fresno | CA | 93705-0908 |  | 2013-08-15 | 2013-08-15 15:40 | 2013-08-15 15:40 | OTHER - UKN | 80 | 0 | Yes | Yes | 34.5 | 20.4 | 14.1 | 5C366F3EF15440CA9DC50396B7E34EBB | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6847 |  | 2013-09-10 | 2013-09-10 10:53 | 2013-09-10 11:55 | MILLER - S3QA-060KA | 85 | 3.3 | Yes | Yes | 16.3 | 19.3 | -3 | 5314F29582784120B064E4E9FEDB18C8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Bakersfield | CA | 93309-4734 |  | 2013-08-27 | 2013-08-27 10:42 | 2013-08-27 11:00 | OTHER - UNK | 85 | -8 | Yes | Yes | 22 | 21.5 | 0.5 | F3DFA7E3A4DC4D8FAD9C91EEBCCBE9D3 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Milpitas | CA | 95035-6007 |  | 2013-09-27 | 2013-09-27 14:33 | 2013-09-27 15:10 | CARRIER - UNK | 132 | 7.2 | Yes | Yes | 18.3 | 21 | -2.7 | 0AC4D2F5527246399031EF04D0F169B5 |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Fairfield | CA | 94533-2231 |  | 2013-10-15 | 2013-10-15 11:54 | 2013-10-15 13:47 | PAYNE - PA10JA024-C | 64 | -5 | Yes | Yes | 14.9 | 17.7 | -2.8 | 8EBB05112B194E628370E8AE4F367A9D |  | R22 | Non-TXV |  | -7.812% | 1.0781 | 2.188% |  |  |  |  | Non-TXV |  |  | -7.812%
Fresno | CA | 93725-1705 |  | 2013-08-16 | 2013-08-16 14:28 | 2013-08-16 15:10 | RHEEM - UNK | 70 | 7 | Yes | Yes | 21 | 16.4 | 4.6 | 429520388F554FA89F72D191AD7C5D0B |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93725-1705 |  | 2013-08-16 | 2013-08-16 15:14 | 2013-08-16 15:33 | RHEEM - UNK | 70 | 3.2 | Yes | Yes | 28 | 23 | 5 | 6E8E06BAF0E144CDB3C7F98CA7CC520E |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Buttonwillow | CA | 93206-9746 |  | 2013-09-16 | 2013-09-16 18:27 | 2013-09-16 18:30 | CARRIER - 48GSN060090301 | 85 | -6 | Yes | Yes | 20.7 | 19.4 | 1.3 | 0F3AB04AD6644AD595C2DEAEF20AF2E1 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Campbell | CA | 95008-4618 |  | 2013-10-14 | 2013-10-14 14:07 | 2013-10-14 14:38 | BRYANT - 561CJ048-A | 102 | 5.4 | Yes | Yes | 27.1 | 21.7 | 5.4 | 3601B8F1E96D4B90BA7CD4FE7B6A47A6 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Willits | CA | 95490-9502 |  | 2013-08-20 | 2013-08-20 14:22 | 2013-08-20 14:46 | DAY & NIGHT - ILLEGIBLE | 53 | 1.9 | Yes | Yes | 25.2 | 20.4 | 4.8 | D41B50DB68794FA1BA1FB52A24D61F51 |  | R22 | Non-TXV |  | 3.585% | 0.96415 | 6.889% | [5 empty] | Non-TXV | 3.585%
Fresno | CA | 93702-2362 |  | 2013-08-30 | 2013-08-30 13:25 | 2013-08-30 13:25 | OTHER - UKN | 80 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | E37D4FC8A431405DBFF68A97FABC9392 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4455 |  | 2013-09-04 | 2013-09-04 10:39 | 2013-09-04 10:43 | DAY & NIGHT - NA | 102 | 3.6 | Yes | Yes | 18.3 | 17 | 1.3 | E0B73EA7B5E84B5CA04EAC649A275113 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fairfield | CA | 94533-2461 |  | 2013-08-27 | 2013-08-27 09:08 | 2013-08-27 13:04 | YORK - YCJF36S41S1A | 58 | 2.5 | Yes | Yes | 20.2 | 19.9 | 0.3 | FAE836A1FCD8425ABEA1638E3C564B06 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.31% | 0.9569 | 8.284% | [5 empty] | Non-TXV | 4.31%
Concord | CA | 94519-2037 |  | 2013-09-06 | 2013-09-06 12:49 | 2013-09-06 12:50 | TRANE - 4TTR2036A1000AA22633JG2F | 78 | 0 | Yes | Yes | 17.6 | 17.9 | -0.3 | 43D829225FCC4C468AD998D24F14FCAB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-08-28 | 2013-08-28 18:58 | 2013-08-28 19:01 | RHEEM - RRNA-B036JK08X | 83 | 3.1 | Yes | Yes | 20.5 | 21 | -0.5 | 9BFDDE6C5840449499F20D31185A212B |  | R22 | TXV |  | 3.735% | 0.96265 | 7.178% | [5 empty] | TXV | 3.735%
Bakersfield | CA | 93305-3219 |  | 2013-09-04 | 2013-09-04 19:38 | 2013-09-04 19:41 | BRYANT - 582ANW030040NAAD | 60 | -3.5 | Yes | Yes | 22.9 | 21.3 | 1.6 | AFA424F84DD2426B8819D0F038660A70 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93727-4523 |  | 2013-08-20 | 2013-08-20 10:47 | 2013-08-20 10:47 | OTHER - UKN | 81 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 2C37A9891BAF4237888294AF62F1F0AD | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Los Molinos | CA | 96055-9732 |  | 2013-09-08 | 2013-09-08 12:00 | 2013-09-08 12:45 | COLEMAN - BRCQ0551BEG | 86 | 2.9 | Yes | Yes | 24.1 | 20.4 | 3.7 | FDA0F742EED74C6392E90A50751AB5BB |  | R22 | Non-TXV |  | 3.372% | 0.96628 | 6.48% | [5 empty] | Non-TXV | 3.372%
Fresno | CA | 93722-6856 |  | 2013-08-16 | 2013-08-16 14:24 | 2013-08-16 15:01 | CARRIER - UKN | 85 | 5 | Yes | Yes | 20.8 | 19.7 | 1.1 | 0099EB005A634D88A9FAA4CC720DFD74 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Vacaville | CA | 95687-6742 |  | 2013-08-22 | 2013-08-22 13:35 | 2013-08-22 15:56 | TRANE - 2TTB3048A1000AA | 142 | 5.3 | Yes | Yes | 15 | 15.2 | -0.2 | 4AFE8822B0C349608641DE4A68575450 |  | R22 | Non-TXV |  | 3.732% | 0.96268 | 7.173% | [5 empty] | Non-TXV | 3.732%
Vacaville | CA | 95688-0000 |  | 2013-08-23 | 2013-08-23 09:14 | 2013-08-23 15:21 | CARRIER - 38BRC060360 | 200 | 8.7 | Yes | Yes | 12.2 | 15 | -2.8 | 3548824C8DCA485BAEA4DD185EEE77BB |  | R22 | Non-TXV |  | 4.35% | 0.9565 | 8.36% | [5 empty] | Non-TXV | 4.35%
Willits | CA | 95490-8552 |  | 2013-08-20 | 2013-08-20 10:39 | 2013-08-20 11:15 | TRANE - 2TTR2030A10000AA | 68 | 2.7 | Yes | Yes | 20.7 | 19.2 | 1.5 | B7ABA9D15D1F40D38E6B07CE6C07846B |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Lost Hills | CA | 93249-0000 |  | 2013-08-27 | 2013-08-27 19:19 | 2013-08-27 19:21 | COLEMAN - DRCS0421BEG | 109 | -7.7 | Yes | Yes | 26.7 | 21.5 | 5.2 | 1CA5667BB443427698F4EA8BCAB56D90 |  | R22 | Non-TXV |  | -7.064% | 1.0706 | 1.978% |  |  |  |  | Non-TXV |  |  | -7.064%
Concord | CA | 94521-1525 |  | 2013-09-05 | 2013-09-05 14:48 | 2013-09-05 14:49 | GOODMAN - CKT60-1B | 150 | 14.3 | Yes | Yes | 17.6 | 17.6 | 0 | 84C00336134F441B9E30464A4AAAB6EB |  | R22 | Non-TXV |  | 9.533% | 0.90467 | 18.32% | [5 empty] | Non-TXV | 9.533%
Fresno | CA | 93727-0000 |  | 2013-08-20 | 2013-08-20 10:22 | 2013-08-20 10:43 | WEATHER KING - WAJB037JAZ | 94 | 7.8 | Yes | Yes | 15.4 | 16.4 | -1 | C6FEBA560DA44DFEB73A0624849145D4 |  | R22 | Non-TXV |  | 8.298% | 0.91702 | 15.95% | [5 empty] | Non-TXV | 8.298%
Pittsburg | CA | 94565-4606 |  | 2013-09-09 | 2013-09-09 10:47 | 2013-09-09 10:48 | COMFORT AIRE - N4A348AKB200 | 112 | 6.1 | Yes | Yes | 18.3 | 17.6 | 0.7 | B74C82C508E54389A64CE1918D421DAF |  | R22 | Non-TXV |  | 5.446% | 0.94554 | 10.47% | [5 empty] | Non-TXV | 5.446%
Hayward | CA | 94544-6655 |  | 2013-09-10 | 2013-09-10 12:42 | 2013-09-10 12:42 | BRYANT - 561CJ060-A | 233 | 0 | Yes | Yes | 21.8 | 16.3 | 5.5 | AB78231344A3478EBCDDACC8C4F47633 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5218 |  | 2013-08-22 | 2013-08-22 14:55 | 2013-08-22 16:01 | CARRIER - 38CK036350 | 74 | -5 | Yes | Yes | 15.2 | 17.7 | -2.5 | D2DD4A07DD80479E9ED3151F0B7FDCA1 |  | R22 | Non-TXV |  | -6.757% | 1.0676 | 1.892% |  |  |  |  | Non-TXV |  |  | -6.757%
Concord | CA | 94519-1117 |  | 2013-09-20 | 2013-09-20 09:40 | 2013-09-20 09:41 | BRYANT - 561CJ048-G | 100 | 6.2 | Yes | Yes | 18 | 17.6 | 0.4 | F519E902771F4B158B869D10D3C8B1A6 |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Pittsburg | CA | 94565-4610 |  | 2013-09-25 | 2013-09-25 22:38 | 2013-09-25 22:38 | CARRIER - 24ACR36A300 | 106 | 0 | Yes | Yes | 21.1 | 16.1 | 5 | 95D55040E0E24F52B84C8F1F71F094F3 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7783 |  | 2013-08-30 | 2013-08-30 15:09 | 2013-08-30 16:29 | GOODMAN - CK60-1C | 122 | 3.6 | Yes | Yes | 18.8 | 20.4 | -1.6 | A0F378932AAC45C0A4159B958C540758 |  | R22 | Non-TXV |  | 2.951% | 0.97049 | 5.671% | [5 empty] | Non-TXV | 2.951%
Concord | CA | 94519-2005 |  | 2013-09-05 | 2013-09-05 13:59 | 2013-09-05 14:00 | TRANE - BTD730A100B0 | 74 | 9.4 | Yes | Yes | 17.3 | 17 | 0.3 | C6D36628393C47CCA3BEDCAEFF0094F0 |  | R22 | Non-TXV |  | 12.7% | 0.87297 | 24.41% | [5 empty] | Non-TXV | 12.7%
Hayward | CA | 94544-6441 |  | 2013-09-10 | 2013-09-10 13:21 | 2013-09-10 13:21 | PAYNE - PA10JA042-B | 130 | 0 | Yes | Yes | 21.5 | 17.5 | 4 | E2010D74D9CF40D791E1D20242EEDA5D |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3765 |  | 2013-09-13 | 2013-09-13 10:39 | 2013-09-13 10:39 | CARRIER - 48ESNA4206030TP | 97 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | 825654AD78654F5B91526BCB1808BD44 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9765 |  | 2013-08-30 | 2013-08-30 15:46 | 2013-08-30 15:46 | OTHER - UKN | 74 | 0 | Yes | Yes | 0 | N/A | N/A | 91C4043D187140A7AE1AE5188166A390 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2426 |  | 2013-09-04 | 2013-09-04 10:34 | 2013-09-04 13:20 | TRANE - BTDT36A100B0 | 88 | -8.3 | Yes | Yes | 13.6 | 16.2 | -2.6 | 1623DB49E42D4D578D7EF84386AA3937 |  | R22 | Non-TXV |  | -9.432% | 1.0943 | 2.641% |  |  |  |  | Non-TXV |  |  | -9.432%
Vacaville | CA | 95687-6770 |  | 2013-08-28 | 2013-08-28 13:08 | 2013-08-28 13:08 | DAY & NIGHT - 591ANX036000AAA | 84 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | B3F52CCA05AE4970B821596600568120 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5640 |  | 2013-08-26 | 2013-08-26 10:16 | 2013-08-26 10:51 | GOODMAN - V5X130481AN | 85 | 3.2 | Yes | Yes | 18.4 | 19.8 | -1.4 | CE655F544B304E18B7E94A5DEA548DC1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Bakersfield | CA | 93312-5083 |  | 2013-09-26 | 2013-09-26 18:34 | 2013-09-26 18:34 | PAYNE - PA12NA036-B | 100 | 0 | Yes | Yes | 22 | 21 | 1 | 7B81AAA9438B421E8B92DB0DD4D9FDA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5083 |  | 2013-09-26 | 2013-09-26 18:53 | 2013-09-26 18:53 | RUUD - UAMB030JAZ | 77 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | B4F6843890D54966A4D3ADDF1C6BF9B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9219 |  | 2013-08-22 | 2013-08-22 14:13 | 2013-08-22 16:00 | TRANE - 4TTX4036A1000AA | 85 | 2.9 | Yes | Yes | 14.5 | 17.5 | -3 | 833354F511474BFFA1CBE130C1E98533 |  | R410A | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
San Jose | CA | 95110-2828 |  | 2013-08-26 | 2013-08-26 12:12 | 2013-08-26 12:52 | BRYANT - 538ANR036000BBAA | 135 | 12.2 | Yes | Yes | 24.5 | 18.9 | 5.7 | 626C5C33ED7D4EC281AADA64B3B34060 |  | R410A | Non-TXV |  | 9.037% | 0.90963 | 17.37% | [5 empty] | Non-TXV | 9.037%
San Jose | CA | 95111-1563 |  | 2013-08-26 | 2013-08-26 11:37 | 2013-08-26 11:37 | RUUD - UAPA-049JAZ | 85 | 0 | Yes | Yes | 19.3 | 15.2 | 4.1 | CB04847F88D34DDB8DA5138C5BF7E476 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3142 |  | 2013-08-20 | 2013-08-20 10:46 | 2013-08-20 10:46 | GOODMAN - PGB0360751B | 83 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 068713B662DF41629A4FF983AF9EBEDF | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3372 |  | 2013-09-17 | 2013-09-17 11:53 | 2013-09-17 15:29 | DAY & NIGHT - 568EJ042 | 144 | -6.5 | Yes | Yes | 16.6 | 18 | -1.4 | 735B9D557E0D4EF6934BA607304C3BD5 |  | R22 | Non-TXV |  | -4.514% | 1.0451 | 1.264% |  |  |  |  | Non-TXV |  |  | -4.514%
Bakersfield | CA | 93308-3034 |  | 2013-08-30 | 2013-08-30 10:43 | 2013-08-30 11:48 | GOODMAN - GPG1336045M4CA | 85 | 7.7 | Yes | Yes | 22.2 | 19.9 | 2.3 | 37CDC381F2004A9EB225BC57F7D6CBC4 |  | R410A | Non-TXV |  | 9.059% | 0.90941 | 17.41% | [5 empty] | Non-TXV | 9.059%
Fresno | CA | 93711-6174 |  | 2013-10-28 | 2013-10-28 15:08 | 2013-10-28 17:47 | YORK - D3YS018N03206B | 53 | 3.8 | Yes | Yes | 19.9 | 19.9 | 0 | 97289FB8C5EA4C2FA7FFC05382CB3EE0 |  | R22 | Non-TXV |  | 7.17% | 0.9283 | 13.78% | [5 empty] | Non-TXV | 7.17%
Bakersfield | CA | 93309-2008 |  | 2013-08-23 | 2013-08-23 12:52 | 2013-08-24 14:14 | COLEMAN - DAYY-F036N0701A | 85 | 5.3 | Yes | Yes | 18.5 | 18.6 | -0.1 | E2F30B79636D438CA56105C660C8BD8D |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Bakersfield | CA | 93313-3650 |  | 2013-09-11 | 2013-09-11 19:15 | 2013-09-11 19:15 | OTHER - 585GJW042060ABAF | 84 | 14.6 | Yes | Yes | 33.8 | 22.5 | 11.3 | A21BC79F5D944B9EAC8169DF300B6AB8 | Add refrigerant: 14.6 oz | R22 | Non-TXV |  | 17.38% | 0.82619 | 33.4% | [5 empty] | Non-TXV | 17.38%
Bakersfield | CA | 93307-5890 |  | 2013-09-17 | 2013-09-17 11:40 | 2013-09-17 12:40 | WEATHER KING - 12AJA3601 | 85 | 3 | Yes | Yes | 16.9 | 19.9 | -3 | 05AD0CEC3C1C47DB97B8BBABB90229B8 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93309-1846 |  | 2013-08-23 | 2013-08-23 09:24 | 2013-08-23 09:24 | WESTINGHOUSE - UKN | 90 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | 63CC705D76B54C2182C36BD03B0D9B89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-4531 |  | 2013-10-02 | 2013-10-02 11:55 | 2013-10-02 12:21 | AMERICAN STANDARD - ILLEGIBLE | 157 | 6.4 | Yes | Yes | 25.8 | 20.3 | 5.5 | 9E91B92D54964C6396249DC0F873F911 |  | R22 | Non-TXV |  | 4.076% | 0.95924 | 7.834% | [5 empty] | Non-TXV | 4.076%
Bakersfield | CA | 93306-1512 |  | 2013-09-19 | 2013-09-19 22:22 | 2013-09-19 23:03 | GOODMAN - GSC130601BC | 85 | 5 | Yes | Yes | 18.9 | 21.8 | -2.9 | A730BFAD65E54B248D59E50021F18D8C |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Bakersfield | CA | 93312-5509 |  | 2013-08-16 | 2013-08-16 14:49 | 2013-08-16 14:49 | ICP - NAC236AKA5 | 65 | 0 | Yes | Yes | 22.1 | 22.1 | 0 | 17D89FEA58494ACAB9CDE2CEC0A45D96 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-9257 |  | 2013-10-08 | 2013-10-08 16:20 | 2013-10-08 16:20 | NORDYNE - F3BC048KA | 110 | 0 | Yes | Yes | 20.5 | 19.6 | 0.9 | 7C408BEB7AEF49B2A549F0628074988C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-08-27 | 2013-08-27 19:30 | 2013-08-27 19:32 | YORK - D1NA036N050606C | 67 | 4.5 | Yes | Yes | 24.4 | 19.9 | 4.5 | BA3BB57326FA450DA62A786168ECE0AB |  | R22 | Non-TXV |  | 6.716% | 0.93284 | 12.91% | [5 empty] | Non-TXV | 6.716%
Vallejo | CA | 94589-2004 |  | 2013-09-23 | 2013-09-23 10:00 | 2013-09-23 10:00 | GOODMAN - PGB036075-1A | 60 | 0 | Yes | Yes | 16 | 16.3 | -0.3 | BB9E7AE151E746C594D4AED0DE670273 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6482 |  | 2013-08-23 | 2013-08-23 09:25 | 2013-08-23 09:54 | YORK - H3RA060506B | 98 | 2.9 | Yes | Yes | 22 | 23.4 | -1.4 | 71CA34F4D90B4427BDF6A4A2EB018EAB |  | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.687% | [5 empty] | Non-TXV | 2.959%
Bakersfield | CA | 93307-7263 |  | 2013-08-22 | 2013-08-22 12:23 | 2013-08-22 12:52 | GOODMAN - PGB0 42075-1A | 107 | 12.9 | Yes | Yes | 18.1 | 21 | -2.9 | 80E6ECADC97648268B3E95CAD7AD302C |  | R22 | Non-TXV |  | 12.06% | 0.87944 | 23.17% | [5 empty] | Non-TXV | 12.06%
Fairfield | CA | 94533-9525 |  | 2013-08-27 | 2013-08-27 10:28 | 2013-08-27 10:28 | CARRIER - 38CKC036350 | 76 | 0 | Yes | Yes | 13.5 | 16.2 | -2.7 | 3AC25F0610614914860C1924436E98BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7332 |  | 2013-10-16 | 2013-10-16 13:57 | 2013-10-16 16:07 | TEMPSTAR - N4A330AKC200 | 74 | -4 | Yes | Yes | 18.1 | 21 | -2.9 | BB54EF67200F4D29A80B282765541971 |  | R410A | Non-TXV |  | -5.405% | 1.0541 | 1.514% |  |  |  |  | Non-TXV |  |  | -5.405%
Bakersfield | CA | 93304-6101 |  | 2013-08-29 | 2013-08-29 20:38 | 2013-08-29 21:00 | ICP - PGC030K060A | 52 | 2.1 | Yes | Yes | 15.3 | 18.2 | -2.9 | 564323BE68224D03AA5DF1E4091C7999 |  | R22 | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
San Jose | CA | 95111-2138 |  | 2013-09-17 | 2013-09-17 10:28 | 2013-09-17 11:11 | BRYANT - 561CJ036-E | 74 | 10.4 | Yes | Yes | 25 | 21 | 4 | 14BEE3CBE8924FA88E2A5FA6D72C427F |  | R22 | Non-TXV |  | 14.05% | 0.85946 | 27.01% | [5 empty] | Non-TXV | 14.05%
Fairfield | CA | 94533-1471 |  | 2013-10-09 | 2013-10-09 09:21 | 2013-10-09 09:21 | TRANE - BTD736A100B0 | 88 | 0 | Yes | Yes | 22.1 | 18.2 | 3.9 | 1EE3E4BBC94148A08C7EA4B065099765 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4826 |  | 2013-09-17 | 2013-09-17 10:26 | 2013-09-17 10:43 | DAY & NIGHT - PG336060K00101 | 85 | 2.7 | Yes | Yes | 20 | 18 | 2.1 | E2DD8854858A45D6BADDF67B4A21B5B6 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Pleasant Hill | CA | 94523-1207 |  | 2013-09-06 | 2013-09-06 13:15 | 2013-09-06 13:15 | OTHER - NA | 69 | 0 | Yes | Yes | 17.5 | 17.5 | 0 | 1D313CD475384EDE80F338CCD5D15A01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6848 |  | 2013-10-01 | 2013-10-01 13:27 | 2013-10-01 13:27 | LENNOX - 13ACD0302001 | 85 | 0 | Yes | Yes | 20.6 | 20.4 | 0.2 | 4178C9DF512F4FD4B2ED7C1DF4A703E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6848 |  | 2013-10-01 | 2013-10-01 13:30 | 2013-10-01 13:30 | LENNOX - 13ACD03623001 | 95 | 0 | Yes | Yes | 22.8 | 21.4 | 1.4 | C70AB09BE22D47F9B732189CCA9ADA8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1869 |  | 2013-08-26 | 2013-08-26 09:33 | 2013-08-26 09:36 | PAYNE - PA10JA030-A | 72 | 2.4 | Yes | Yes | 18.5 | 17.6 | 0.9 | AD8CA933494D4E77B3D6F9BDAA5EBB05 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Buttonwillow | CA | 93206-9709 |  | 2013-09-24 | 2013-09-24 19:39 | 2013-09-24 19:41 | OTHER - PGE10A24D050LA-2A | 50 | 2.4 | Yes | Yes | 21.3 | 18.3 | 3 | 39489FB5092D405C81BA6BA983D682BC |  | R22 | Non-TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | Non-TXV | 4.8%
Buttonwillow | CA | 93206-9757 |  | 2013-09-24 | 2013-09-24 19:48 | 2013-09-24 19:52 | OTHER - 58HJ030040 | 68 | 7.9 | Yes | Yes | 25.7 | 20.4 | 5.3 | 454F626E5D4A4BD0B86125B4C8EE6684 |  | R22 | Non-TXV |  | 11.62% | 0.88382 | 22.33% | [5 empty] | Non-TXV | 11.62%
Buttonwillow | CA | 93206-9746 |  | 2013-09-16 | 2013-09-16 18:10 | 2013-09-16 18:12 | DAY & NIGHT - N/A | 85 | 2.9 | Yes | Yes | 23.9 | 20.2 | 3.8 | 97812C5DC96A42BFAB2D30CFDBA69EFC |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Buttonwillow | CA | 93206-9757 |  | 2013-09-16 | 2013-09-16 18:15 | 2013-09-16 18:17 | CARRIER - PGC042K080A | 87 | -7.2 | Yes | Yes | 20.9 | 19.7 | 1.2 | 22CF07D894FC46DCBF0565BDB5CA423F |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Buttonwillow | CA | 93206-9701 |  | 2013-09-16 | 2013-09-16 18:18 | 2013-09-16 18:18 | RUUD - N/A | 85 | 0 | Yes | Yes | 21.3 | 21.3 | 0 | 9FD964ABD6C8476B8805646E4DF22B5B | Add refrigerant: 12.7 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1618 |  | 2013-09-07 | 2013-09-07 09:44 | 2013-09-07 09:44 | YORK - DCYZ-1036N070C | 64 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | BF2C15EF518447C38FD1D1EAE74BE788 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Taft | CA | 93268-3337 |  | 2013-09-23 | 2013-09-23 18:25 | 2013-09-23 18:28 | CARRIER - 48TLX036--301-- | 104 | 0 | Yes | Yes | 17 | 22.5 | -5.5 | 3C544B90AC184D38B87808BF2EA9BA6A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3104 |  | 2013-10-24 | 2013-10-24 10:56 | 2013-10-24 11:23 | YORK - D2NP042N06506A | 150 | 16.9 | Yes | Yes | 23.4 | 19.5 | 3.9 | B86451264D99413C8C4512A1BE1B49EC |  | R22 | Non-TXV |  | 11.27% | 0.88733 | 21.65% | [5 empty] | Non-TXV | 11.27%
Wasco | CA | 93280-1609 |  | 2013-08-22 | 2013-08-22 17:56 | 2013-08-22 17:56 | CARRIER - 48NLT060---311BE | 85 | 0 | Yes | Yes | 18.4 | 21.5 | -3.1 | D0A27AF5C7DA4DE085A4EF50395F0933 | Add refrigerant: 4.8 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3107 |  | 2013-09-24 | 2013-09-24 12:38 | 2013-09-24 12:38 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 729DE5B072E149699676E652EE45ADD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3529 |  | 2013-09-02 | 2013-09-02 20:35 | 2013-09-02 21:03 | OTHER - H2RC036S06A | 83 | 3.3 | Yes | Yes | 18.3 | 21.2 | -2.9 | 3E0A05D21DA14597832D165D421692C4 |  | R22 | Non-TXV |  | 3.976% | 0.96024 | 7.641% | [5 empty] | Non-TXV | 3.976%
Vacaville | CA | 95687-6223 |  | 2013-08-23 | 2013-08-23 10:17 | 2013-08-23 10:17 | PAYNE - 567C030RCU | 63 | 0 | Yes | Yes | 10.1 | 13 | -2.9 | 8253B70128624205959B7633B5704F56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2077 |  | 2013-09-11 | 2013-09-11 09:46 | 2013-09-11 10:04 | OTHER - BRCS0481BD | 117 | 14.3 | Yes | Yes | 18.2 | 17.2 | 1 | C41C69DF64C84FB8A8BC748479DC4B5A |  | R22 | Non-TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | Non-TXV | 12.22%
Suisun City | CA | 94585-3071 |  | 2013-10-14 | 2013-10-14 12:55 | 2013-10-14 13:30 | TRANE - BTR730E100A0 | 106 | 20.4 | Yes | Yes | 20.4 | 16.1 | 4.3 | BBF90E30F3144BB58B276918FC4F3AB6 |  | R22 | Non-TXV |  | 19.25% | 0.80755 | 36.99% | [5 empty] | Non-TXV | 19.25%
Bakersfield | CA | 93312-6826 |  | 2013-08-18 | 2013-08-18 09:15 | 2013-08-18 09:45 | GOODMAN - GSC130421A A | 143 | 22.2 | Yes | Yes | 22 | 22.1 | -0.1 | 86D3E0A3E3814EC38B54D0F4E3A5533C |  | R22 | Non-TXV |  | 15.52% | 0.84476 | 29.83% | [5 empty] | Non-TXV | 15.52%
San Jose | CA | 95110-1521 |  | 2013-09-09 | 2013-09-09 13:46 | 2013-09-09 14:27 | TRANE - TTB024C100A2 | 54 | 10 | Yes | Yes | 19.8 | 16.9 | 2.9 | CD985E63A4F045E1B56F820A219ABCDC |  | R22 | Non-TXV |  | 18.52% | 0.81481 | 35.59% | [5 empty] | Non-TXV | 18.52%
Bakersfield | CA | 93312-8219 |  | 2013-10-16 | 2013-10-16 11:17 | 2013-10-16 11:17 | LENNOX - HS290485P | 88 | 0 | Yes | Yes | 21.1 | 21.7 | -0.6 | 57B5FBF76906426CA61279EB8BE04942 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2174 |  | 2013-09-26 | 2013-09-26 11:46 | 2013-09-26 11:46 | CARRIER - 38EB030310 | 80 | 0 | Yes | Yes | 17.4 | 17.6 | -0.2 | 70253E04CF6D414CB6C07F933F1F1142 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-4620 |  | 2013-09-23 | 2013-09-23 10:41 | 2013-09-23 10:42 | HEIL - CA5530VKD2 | 74 | 2.9 | Yes | Yes | 16.6 | 16.3 | 0.3 | 4C2135B4F7A24F98984185BD643F812D |  | R22 | Non-TXV |  | 3.919% | 0.96081 | 7.531% | [5 empty] | Non-TXV | 3.919%
Vacaville | CA | 95687-6430 |  | 2013-10-16 | 2013-10-16 13:07 | 2013-10-16 16:06 | SEARS - | 57 | 4.2 | Yes | Yes | 13.8 | 16.5 | -2.7 | A70B6920FCE94F11AC5FB252AE8A4910 |  | R22 | Non-TXV |  | 7.368% | 0.92632 | 14.16% | [5 empty] | Non-TXV | 7.368%
Bakersfield | CA | 93312-3984 |  | 2013-08-17 | 2013-08-17 14:47 | 2013-08-17 14:47 | ICP - NAC236AKA5 | 114 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | 4351A6FA470D40958C7560DEA913E9A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1629 |  | 2013-08-22 | 2013-08-22 18:20 | 2013-08-22 18:20 | CARRIER - PA13NR060 | 278 | 0 | Yes | Yes | 14.8 | 20.7 | -5.9 | DBA01982E0234B4D8D7DD26FA8F4E8E1 | Add refrigerant: 14.1 oz | R22 | TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2080 |  | 2013-09-24 | 2013-09-24 09:06 | 2013-09-24 09:06 | CARRIER - 38TKB036300 | 81 | 0 | Yes | Yes | 22.7 | 17.7 | 5 | DA9BD84ACF914B48BF99C8F894598F24 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1335 |  | 2013-08-23 | 2013-08-23 12:11 | 2013-08-23 12:48 | RHEEM - D1NH042N06506C | 94 | -8.8 | Yes | Yes | 19.8 | 21.5 | -1.7 | 21E3B31F7B1F4A888ED651E16DC4D3B6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | -9.362% | 1.0936 | 2.622% |  |  |  |  | Non-TXV |  |  | -9.362%
Bakersfield | CA | 93312-6846 |  | 2013-08-18 | 2013-08-18 11:41 | 2013-08-18 11:41 | LENNOX - 13ACD-042-230-02 | 111 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 79D1FF4D7E5E48438A77E9A9F831CD1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1904 |  | 2013-08-29 | 2013-08-29 11:20 | 2013-08-29 11:48 | YORK - DMH036N05606C | 108 | 8.8 | Yes | Yes | 13.4 | 15.9 | -2.5 | 169BF9BB3D45446F819359B96DC06375 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Bakersfield | CA | 93312-6820 |  | 2013-09-06 | 2013-09-06 08:04 | 2013-09-06 08:22 | WEATHER KING - 13AJA30A01 | 85 | 2.6 | Yes | Yes | 17 | 19.3 | -2.3 | 2050C9D0241B457983F7FB81DD54E316 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93312-6820 |  | 2013-09-06 | 2013-09-06 08:26 | 2013-09-06 08:42 | WEATHER KING - 13AJA30A01 | 85 | 3.8 | Yes | Yes | 15.5 | 18.5 | -3 | 2AEA76FD59ED46B7854872CD810DD893 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Fairfield | CA | 94533-8412 |  | 2013-09-12 | 2013-09-12 10:59 | 2013-09-12 12:46 | AMERICAN STANDARD - 7 B0023B100A1 | 54 | 3.5 | Yes | Yes | 11.9 | 13 | -1.1 | 319B3D74125D44949B64109B8D11D7BA |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Vacaville | CA | 95687-6253 |  | 2013-09-17 | 2013-09-17 09:50 | 2013-09-17 11:01 | OTHER - RCU13410C36J | 90 | 3.3 | Yes | Yes | 15.7 | 17.9 | -2.2 | 36D5163D6FA347788525853D1503F54B |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Bakersfield | CA | 93312-2375 |  | 2013-09-05 | 2013-09-05 09:54 | 2013-09-05 10:59 | PAYNE - PY1PNB042090AAAA | 85 | 2.6 | Yes | Yes | 23 | 19.6 | 3.5 | CA65E72B187D440E8C05B58A4157328D |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93305-1323 |  | 2013-08-27 | 2013-08-27 14:32 | 2013-08-27 15:08 | OTHER - D1NP048N06506A | 132 | 4.6 | Yes | Yes | 19.9 | 19 | 0.9 | B34037430C3B4DD28BD7934F369022CB |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Bakersfield | CA | 93312-6577 |  | 2013-08-26 | 2013-08-26 00:06 | 2013-08-26 00:09 | RHEEM - 113RNA060-D | 170 | -10 | Yes | Yes | 20.6 | 21.5 | -0.9 | 89D84D8E39C6477A9B5E27864A317C74 |  | R22 | TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | TXV |  |  | -5.882%
Clovis | CA | 93611-6941 |  | 2013-08-24 | 2013-08-24 13:45 | 2013-08-24 14:18 | DAY & NIGHT - 59WN036-A | 187 | 7.5 | Yes | Yes | 25.1 | 21.5 | 3.7 | 07117A25E4A84AEF9517456650E3B733 |  | R22 | TXV |  | 4.011% | 0.95989 | 7.708% | [5 empty] | TXV | 4.011%
Antioch | CA | 94509-2212 |  | 2013-09-26 | 2013-09-26 11:02 | 2013-09-26 11:02 | SEARS - 29HDA-1182B | 72 | 3.3 | Yes | Yes | 18.3 | 17.6 | 0.7 | F9BAD77492C04406B2A377F1E319138B |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Bakersfield | CA | 93308-4863 |  | 2013-09-05 | 2013-09-05 21:03 | 2013-09-05 21:05 | GOODMAN - CLQ48-1B | 225 | -9 | Yes | Yes | 21.3 | 21.5 | -0.2 | 0A4E636D584140BCBBDFC6791C3CF9C1 |  | R22 | TXV |  | -4% | 1.04 | 1.12% |  |  |  |  | TXV |  |  | -4%
Bakersfield | CA | 93312-6688 |  | 2013-08-23 | 2013-08-23 18:44 | 2013-08-23 18:49 | OTHER - H2RC048S06HG | 85 | 4.6 | Yes | Yes | 21 | 21 | 0 | FF4AACC4BCEC41D782BC3E67951D1777 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Bakersfield | CA | 93313-2757 |  | 2013-09-10 | 2013-09-10 20:04 | 2013-09-10 20:06 | BRYANT - 113RNA048000BBAA | 124 | -6 | Yes | Yes | 24.1 | 21.4 | 2.7 | 696E32EBCBC041D98ED346E5682E911E |  | R22 | TXV |  | -4.839% | 1.0484 | 1.355% |  |  |  |  | TXV |  |  | -4.839%
Shafter | CA | 93263-2421 |  | 2013-08-30 | 2013-08-30 18:42 | 2013-08-30 18:45 | OTHER - PGAD3001K6 | 78 | -4.4 | Yes | Yes | 23.2 | 18.8 | 4.4 | 588A65C8E88A41E5B1B3302618CFA98F |  | R22 | Non-TXV |  | -5.641% | 1.0564 | 1.58% |  |  |  |  | Non-TXV |  |  | -5.641%
Lemoore | CA | 93245-2518 |  | 2013-10-11 | 2013-10-11 15:06 | 2013-10-11 15:29 | CARRIER - 585HJ042060 | 80 | 19.1 | Yes | Yes | 20.6 | 19.7 | 0.9 | 2B74739CDFDF4B2293794C1B2577CA0E |  | R22 | Non-TXV |  | 23.88% | 0.76125 | 45.88% | [5 empty] | Non-TXV | 23.88%
Lost Hills | CA | 93249-0000 |  | 2013-09-25 | 2013-09-25 18:42 | 2013-09-25 18:46 | YORK - D1NA036N05606C | 67 | -6.3 | Yes | Yes | 25 | 19.3 | 5.7 | B57F6573BF9E48F8AE44817C709D67FB |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Bakersfield | CA | 93312-5527 |  | 2013-09-26 | 2013-09-26 11:34 | 2013-09-26 11:34 | RHEEM - RAMB-036JBZ | 93 | 0 | Yes | Yes | 22.5 | 22 | 0.5 | 63846C64DB2A49BDBE721616E378B261 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2083 |  | 2013-09-23 | 2013-09-23 11:11 | 2013-09-23 11:11 | COLEMAN - 954000301 | 113 | 0 | Yes | Yes | 19.9 | 17.5 | 2.4 | C17B834435204A8D8F0FA97638E70959 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3443 |  | 2013-09-20 | 2013-09-20 12:04 | 2013-09-20 12:05 | CARRIER - 38ED036300 | 130 | 4.7 | Yes | Yes | 15.4 | 15.7 | -0.3 | 4A1B99FECA4B44519687E286F0B7FB6C |  | R22 | Non-TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | Non-TXV | 3.615%
Antioch | CA | 94509-5532 |  | 2013-09-03 | 2013-09-03 10:20 | 2013-09-03 10:22 | TRANE - 2TTR3048A1000AA | 142 | 15 | Yes | Yes | 16.8 | 17.6 | -0.8 | E96B894C97F3433A9C21BEA5E8A5D419 |  | R22 | Non-TXV |  | 10.56% | 0.89437 | 20.3% | [5 empty] | Non-TXV | 10.56%
Vacaville | CA | 95687-6415 |  | 2013-09-06 | 2013-09-06 10:08 | 2013-09-06 10:08 | AIRE-FLO - 4TTR2036A1000AA | 78 | 0 | Yes | Yes | 12.9 | 15 | -2.1 | 39AC44D2A8F54EA68590BCB018EF2AD2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6027 |  | 2013-09-24 | 2013-09-24 21:42 | 2013-09-24 21:42 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.7 | 22.1 | -0.4 | 5EFAA7040A55413A978CD481C5052A30 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-08-28 | 2013-08-28 18:18 | 2013-08-28 18:21 | FRIGIDAIRE - R4GD-036K072C | 100 | 5.4 | Yes | Yes | 20 | 19.9 | 0.1 | 56E0F98773A34AB8B5026E0874097DBA |  | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Fairfield | CA | 94533-2333 |  | 2013-10-09 | 2013-10-09 10:51 | 2013-10-09 11:21 | NORDYNE - FS3BA-036KA | 85 | 11.2 | Yes | Yes | 21 | 17.6 | 3.4 | E059DBA8381C4A9B8205C8A619BFD1D3 |  | R22 | Non-TXV |  | 13.18% | 0.86824 | 25.32% | [5 empty] | Non-TXV | 13.18%
Bakersfield | CA | 93312-8211 |  | 2013-09-05 | 2013-09-05 12:50 | 2013-09-06 07:38 | LENNOX - 10ACC-048-230-04 | 85 | 2.7 | Yes | Yes | 21.8 | 20.4 | 1.4 | 3F80356458694C4393A9684CF2E2A450 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Lemoore | CA | 93245-1729 |  | 2013-08-29 | 2013-08-29 12:19 | 2013-08-29 12:19 | GOODMAN - CK1491 | 109 | 0 | Yes | Yes | 19.7 | 21.4 | -1.7 | 63D3A8E1BEDD4F88A0B2D492FD182D93 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6645 |  | 2013-09-04 | 2013-09-04 08:59 | 2013-09-04 13:16 | LENNOX - HS22-411U-2P | 129 | 4.7 | Yes | Yes | 16.1 | 18.6 | -2.5 | E55C6DEE54A34684816093D1499226A4 |  | R22 | Non-TXV |  | 3.643% | 0.96357 | 7.002% | [5 empty] | Non-TXV | 3.643%
Antioch | CA | 94531-7734 |  | 2013-09-03 | 2013-09-03 09:15 | 2013-09-03 09:17 | PAYNE - 591ANX048000ACAA | 128 | 10.9 | Yes | Yes | 19.7 | 21.7 | -2 | 4E15ABDE7EBC442ABF8DEE1E3D581B37 |  | R22 | Non-TXV |  | 8.516% | 0.91484 | 16.37% | [5 empty] | Non-TXV | 8.516%
Bakersfield | CA | 93313-5410 |  | 2013-09-03 | 2013-09-03 10:09 | 2013-09-03 10:44 | OTHER - CH9048VXD2 | 85 | -8 | Yes | Yes | 17.5 | 20.5 | -3 | 3B9697337B9D4A9D8D78E87CDFDF1853 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Ukiah | CA | 95482-9533 |  | 2013-08-23 | 2013-08-23 15:29 | 2013-08-23 16:30 | AMERICAN STANDARD - YCY030F1M0AC | 148 | 12.2 | Yes | Yes | 21.8 | 21.1 | 0.7 | C6B88F6C060C45FFA66589B9E6784E77 |  | R22 | Non-TXV |  | 8.243% | 0.91757 | 15.84% | [5 empty] | Non-TXV | 8.243%
San Jose | CA | 95136-3627 |  | 2013-09-09 | 2013-09-09 13:41 | 2013-09-09 14:28 | PAYNE - PA13NAZ24-A | 146 | 5.5 | Yes | Yes | 21.7 | 17.2 | 4.5 | D707B3A03CAF4DCE89BED1A08C1DEA40 |  | R22 | TXV |  | 3.767% | 0.96233 | 7.24% | [5 empty] | TXV | 3.767%
Concord | CA | 94518-2118 |  | 2013-09-24 | 2013-09-24 09:54 | 2013-09-24 09:55 | BRYANT - 550AN048-E | 171 | 5.9 | Yes | Yes | 17.8 | 17.3 | 0.5 | 80ABE9CD225942BF8286247C5B509316 |  | R22 | Non-TXV |  | 3.45% | 0.9655 | 6.631% | [5 empty] | Non-TXV | 3.45%
Bakersfield | CA | 93308-3532 |  | 2013-08-30 | 2013-08-30 10:07 | 2013-08-30 10:41 | AMANA - APG1348901A | 85 | 3.1 | Yes | Yes | 23.6 | 18.7 | 5 | 7E1F1A68FBCC4885964C3E46C45F5D07 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Shafter | CA | 93263-3538 |  | 2013-09-03 | 2013-09-03 20:34 | 2013-09-03 20:49 | GOODMAN - GPG13420701AA | 107 | -7.6 | Yes | Yes | 24.3 | 19.2 | 5.2 | 29732C5F574341248F211B663CB38C5E |  | R22 | Non-TXV |  | -7.103% | 1.071 | 1.989% |  |  |  |  | Non-TXV |  |  | -7.103%
Hanford | CA | 93230-9534 |  | 2013-09-23 | 2013-09-23 14:52 | 2013-09-23 15:27 | GOODMAN - UNK | 68 | 20.9 | Yes | Yes | 20.5 | 18.3 | 2.3 | 42BBFC924C91424D9A0DE16A4D65038D |  | R22 | Non-TXV |  | 30.74% | 0.69265 | 59.07% | [5 empty] | Non-TXV | 30.74%
San Jose | CA | 95128-3244 |  | 2013-09-09 | 2013-09-09 11:15 | 2013-09-09 11:15 | OTHER - 563CN042-A | 166 | 0 | Yes | Yes | 19.7 | 15.7 | 4 | 0B649DE713534DBD97E27A68BAC7EFAF |  | R22 | TXV |  | 0% | 1 | 0%
Redding | CA | 96002-9733 |  | 2013-09-05 | 2013-09-05 13:32 | 2013-09-05 14:15 | GOODMAN - GPG156014041AA | 180 | 11.6 | Yes | Yes | 22.3 | 22.1 | 0.2 | 9CDDA3919E00429A9DEADEA800FAAEE4 |  | R410A | TXV |  | 6.444% | 0.93556 | 12.38% | [5 empty] | TXV | 6.444%
Pittsburg | CA | 94565-2003 |  | 2013-09-06 | 2013-09-06 09:18 | 2013-09-06 10:16 | RHEEM - RAFD-036JAS | 80 | 12.2 | Yes | Yes | 16.5 | 17.1 | -0.6 | 5364B897238640F3B09D80D114FBE3DF |  | R22 | Non-TXV |  | 15.25% | 0.8475 | 29.31% | [5 empty] | Non-TXV | 15.25%
Wasco | CA | 93280-2775 |  | 2013-08-29 | 2013-08-29 16:13 | 2013-08-29 16:15 | OTHER - TCGD3052151A | 59 | 3.3 | Yes | Yes | 21.2 | 21 | 0.2 | 8E38E334508943F8ABF1AFD21CB4372D |  | R22 | TXV |  | 5.593% | 0.94407 | 10.75% | [5 empty] | TXV | 5.593%
Pittsburg | CA | 94565-1916 |  | 2013-09-04 | 2013-09-04 10:08 | 2013-09-04 10:10 | RHEEM - RAFD-036JAS | 80 | 3.6 | Yes | Yes | 17.3 | 17.6 | -0.3 | 3883691F008B4B27860BD2530B96B044 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Hayward | CA | 94544-6441 |  | 2013-09-11 | 2013-09-11 13:37 | 2013-09-11 13:54 | OTHER - H1RA048S06D | 117 | 4.5 | Yes | Yes | 25 | 19.3 | 5.7 | BCD24186CC2047B199FB2B4AE6A3122A |  | R22 | TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | TXV | 3.846%
Antioch | CA | 94509-5219 |  | 2013-09-30 | 2013-09-30 09:56 | 2013-09-30 09:56 | LENNOX - 12ACX-048-230-11 | 120 | 8.2 | Yes | Yes | 19.1 | 18.2 | 0.9 | D5A0FF4B9F104122BBB2755FD00C796F |  | R22 | Non-TXV |  | 6.833% | 0.93167 | 13.13% | [5 empty] | Non-TXV | 6.833%
Pittsburg | CA | 94565-4877 |  | 2013-09-04 | 2013-09-04 11:03 | 2013-09-04 11:06 | OTHER - TCA042AKA5 | 98 | 7.5 | Yes | Yes | 18.7 | 21.5 | -2.8 | 3216752E77884947AA10DD1AFD2C6C62 |  | R22 | Non-TXV |  | 7.653% | 0.92347 | 14.71% | [5 empty] | Non-TXV | 7.653%
Fairfield | CA | 94533-9525 |  | 2013-08-27 | 2013-08-27 13:21 | 2013-08-27 15:33 | CARRIER - | 85 | 5.4 | Yes | Yes | 16.8 | 19.4 | -2.6 | 3613844448264CBFA40B58E8AB51E006 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Wasco | CA | 93280-9613 |  | 2013-08-29 | 2013-08-29 16:07 | 2013-08-29 16:10 | YORK - H2RD048506B | 134 | 13.4 | Yes | Yes | 20.7 | 20.4 | 0.3 | 0F258B82E896403799E5D807C3D3A1DE |  | R22 | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Fremont | CA | 94555-2080 |  | 2013-10-02 | 2013-10-02 09:05 | 2013-10-02 09:38 | BRYANT - 561CJ042-E | 85 | 11.2 | Yes | Yes | 21.9 | 17.6 | 4.3 | 6EE8D71CD29A4AB2AF2B03D91E12873A |  | R22 | TXV |  | 13.18% | 0.86824 | 25.32% | [5 empty] | TXV | 13.18%
Fremont | CA | 94555-2080 |  | 2013-09-23 | 2013-09-23 10:39 | 2013-09-23 11:07 | COLEMAN - 95A8C9015 | 88 | 5.4 | Yes | Yes | 20 | 16.4 | 3.6 | 6009DD6359F14824AECA9ABAC3B306BE |  | R22 | Non-TXV |  | 6.136% | 0.93864 | 11.79% | [5 empty] | Non-TXV | 6.136%
Fremont | CA | 94555-2082 |  | 2013-09-05 | 2013-09-05 11:16 | 2013-09-05 11:16 | OTHER - UNK | 85 | 0 | Yes | Yes | 19.8 | 17.9 | 1.9 | 098C3C0814874148894457056862C387 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6617 |  | 2013-08-30 | 2013-08-30 10:28 | 2013-08-30 16:27 | YORK - H4DH060S06A | 125 | 4.6 | Yes | Yes | 14.9 | 17.6 | -2.7 | 0D3435045D9446C7B48C67502DD9686E |  | R22 | Non-TXV |  | 3.68% | 0.9632 | 7.072% | [5 empty] | Non-TXV | 3.68%
Bakersfield | CA | 93312-3461 |  | 2013-08-25 | 2013-08-25 23:58 | 2013-08-26 00:02 | GOODMAN - PGJ048075-1 | 84 | 3.5 | Yes | Yes | 19.8 | 18.9 | 0.9 | 2CB424DAECA74D59ADCC859705F5E997 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Bakersfield | CA | 93305-1533 |  | 2013-09-04 | 2013-09-04 18:45 | 2013-09-04 18:49 | TEMPSTAR - PGAD36D1KE------ | 136 | -14.6 | Yes | Yes | 21 | 21.6 | -0.5 | A5BFFCD7A5664FC3945C8E536861AE07 |  | R22 | TXV |  | -10.74% | 1.1074 | 3.006% |  |  |  |  | TXV |  |  | -10.74%
Lemoore | CA | 93245-4946 |  | 2013-08-29 | 2013-08-29 15:27 | 2013-08-29 19:31 | GOODMAN - CK601C | 115 | 3.5 | Yes | Yes | 19.4 | 20.9 | -1.5 | 0D42741C77A842088DFD566359338A15 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Bakersfield | CA | 93309-3913 |  | 2013-09-18 | 2013-09-18 12:34 | 2013-09-19 09:26 | DAY & NIGHT - 585HJ024040 | 68 | 3.2 | Yes | Yes | 24.7 | 25.1 | -0.3 | AE3B0130064941618C83E8929D677CF7 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fairfield | CA | 94533-2635 |  | 2013-08-27 | 2013-08-27 13:47 | 2013-08-27 13:47 | TRANE - 4TTR2036A1000AA | 78 | 0 | Yes | Yes | 16.9 | 19.3 | -2.4 | BD9033B98C234C5887918934826B0F42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3962 |  | 2013-09-23 | 2013-09-23 15:21 | 2013-09-23 15:45 | PAYNE - PY30NA24040NB | 85 | 2.8 | Yes | Yes | 13.7 | 16.7 | -3 | 62F177F680F0466CA6433213725777B1 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Bakersfield | CA | 93306-1423 |  | 2013-09-19 | 2013-09-19 23:07 | 2013-09-20 07:20 | DAY & NIGHT - 585HJ048080 | 118 | 4.8 | Yes | Yes | 23 | 21.5 | 1.5 | 2DEEC1F8445147A7B3CA19D82D7D651E |  | R22 | Non-TXV |  | 4.068% | 0.95932 | 7.817% | [5 empty] | Non-TXV | 4.068%
Fairfield | CA | 94534-3401 |  | 2013-08-30 | 2013-08-30 12:20 | 2013-08-30 16:30 | GIBSON - JS3BA-048KA | 115 | 4.2 | Yes | Yes | 11.7 | 14.1 | -2.4 | 412C8C248EEC495CB3A7025294D82D8A |  | R22 | Non-TXV |  | 3.652% | 0.96348 | 7.019% | [5 empty] | Non-TXV | 3.652%
Bakersfield | CA | 93312-5652 |  | 2013-08-26 | 2013-08-26 00:12 | 2013-08-26 00:16 | CARRIER - 30CKC3040 | 69 | 4 | Yes | Yes | 20.5 | 21.5 | -1 | 629255B03DE740B2B60F6586E7047D79 |  | R22 | TXV |  | 5.797% | 0.94203 | 11.14% | [5 empty] | TXV | 5.797%
Bakersfield | CA | 93312-5652 |  | 2013-08-26 | 2013-08-26 00:19 | 2013-08-26 00:21 | CARRIER - 38CKC042---351 | 93 | 5 | Yes | Yes | 21 | 21.5 | -0.5 | BB42C6A497B44BAC8F8E4D18241DBEB7 |  | R22 | TXV |  | 5.376% | 0.94624 | 10.33% | [5 empty] | TXV | 5.376%
San Jose | CA | 95122-2650 |  | 2013-09-30 | 2013-09-30 10:46 | 2013-09-30 11:21 | BRYANT - 561CJ036-D | 85 | -8 | Yes | Yes | 14.1 | 14.7 | -0.6 | DA6FD4A7743F4948B8C19B4139B7D48C |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93309-1856 |  | 2013-09-05 | 2013-09-05 23:56 | 2013-09-05 23:56 | BRYANT - 1798E15124 | 84 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | 62B6BE6880F549CD85D9B5F14A7EADA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4032 |  | 2013-09-04 | 2013-09-04 13:35 | 2013-09-04 19:55 | PAYNE - PY3PNA042060NB | 85 | 7.6 | Yes | Yes | 21.5 | 19.4 | 2.2 | 78DEC9CF2569454DA67F4A963329AA53 |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Fremont | CA | 94536-1766 |  | 2013-09-05 | 2013-09-05 12:10 | 2013-09-05 12:33 | COLEMAN - UNK | 85 | 3.3 | Yes | Yes | 21.9 | 18.7 | 3.2 | 64A54EBC5904465787DC6CDD5704B8E6 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Fremont | CA | 94536-1767 |  | 2013-10-17 | 2013-10-17 09:25 | 2013-10-17 09:25 | RHEEM - RACB-036JAQ | 85 | 0 | Yes | Yes | 18.3 | 17.2 | 1.1 | 3FC68FC7C25348F29B927FA40D7CB42C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6153 |  | 2013-09-24 | 2013-09-24 12:04 | 2013-09-24 12:04 | YORK - AC048X1021A | 117 | 0 | Yes | Yes | 19.1 | 21 | -1.9 | BDE85D22E586485192FFED28472C7D64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1523 |  | 2013-08-22 | 2013-08-22 18:37 | 2013-08-22 18:39 | YORK - D1NPO36N05606A | 92 | -6.5 | Yes | Yes | 21.3 | 19.4 | 1.9 | AC2752B854534E678CBA7E6899807D55 |  | R22 | TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | TXV |  |  | -7.065%
Concord | CA | 94518-3011 |  | 2013-10-02 | 2013-10-02 12:25 | 2013-10-02 12:27 | CARRIER - 38CKC042350 | 93 | -8.8 | Yes | Yes | 16.8 | 17 | -0.2 | C739561C911F4BECB04C6F9BEB5B0BC4 |  | R22 | Non-TXV |  | -9.462% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.462%
Bakersfield | CA | 93312-6222 |  | 2013-09-04 | 2013-09-04 19:16 | 2013-09-04 19:21 | RUUD - UAMB-042JAZ | 96 | 5.3 | Yes | Yes | 20 | 20.4 | -0.4 | AA22120280244F1899DF672B8B99AD65 |  | R22 | TXV |  | 5.521% | 0.94479 | 10.61% | [5 empty] | TXV | 5.521%
Fremont | CA | 94536-1766 |  | 2013-09-05 | 2013-09-05 11:53 | 2013-09-05 12:06 | OTHER - BRCS0421BD | 84 | 13.4 | Yes | Yes | 22.8 | 18.1 | 4.7 | ECF727F8C49F42F38558D53FD97EC7F9 |  | R22 | Non-TXV |  | 15.95% | 0.84048 | 30.66% | [5 empty] | Non-TXV | 15.95%
Bakersfield | CA | 93308-1726 |  | 2013-09-09 | 2013-09-09 14:20 | 2013-09-10 08:01 | ICP - GPCM036K060D | 85 | 3.5 | Yes | Yes | 19.2 | 19.2 | 0 | 66C03DF2A23F4A5F80CFA1493132F6C9 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fremont | CA | 94536-1767 |  | 2013-09-10 | 2013-09-10 12:15 | 2013-09-10 12:15 | CARRIER - BRCQ0181BE | 85 | 0 | Yes | Yes | 20 | 17.2 | 2.8 | FC3535C4E8A847C1BA02E4F72A8BB0ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4419 |  | 2013-09-26 | 2013-09-26 16:29 | 2013-09-26 16:48 | CARRIER - 38TR036300 | 134 | 8.6 | Yes | Yes | 22.2 | 21 | 1.2 | D0E3613D7D66432E9A8445D34149C0C5 |  | R22 | Non-TXV |  | 6.418% | 0.93582 | 12.33% | [5 empty] | Non-TXV | 6.418%
Fremont | CA | 94539-7830 |  | 2013-09-23 | 2013-09-23 09:51 | 2013-09-23 09:51 | NORDYNE - FT3BC-024K | 85 | 0 | Yes | Yes | 19.1 | 17.1 | 2 | 511BB9681CAF43BF97F48B137167F14C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-9186 |  | 2013-09-24 | 2013-09-24 17:51 | 2013-09-24 17:51 | CARRIER - UKN | 90 | 0 | Yes | Yes | 28.9 | 23 | 5.9 | F098F797797146FDB860B7BF98056917 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-9186 |  | 2013-09-24 | 2013-09-24 17:04 | 2013-09-24 17:04 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | E3274C8A3DC14A24919F0C15297C9504 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2397 |  | 2013-09-10 | 2013-09-10 15:20 | 2013-09-10 20:47 | RUUD - UNK | 85 | 2.6 | Yes | Yes | 18 | 20.4 | -2.4 | 95980FBBFA84448394A6D628C35CF25E |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Antioch | CA | 94509-5361 |  | 2013-09-06 | 2013-09-06 10:18 | 2013-09-06 10:18 | CARRIER - 38TH036300 | 83 | 6.1 | Yes | Yes | 16.7 | 17.6 | -0.9 | 31AB727D6DA94659BDD98A276BB8BFF9 |  | R22 | Non-TXV |  | 7.349% | 0.92651 | 14.12% | [5 empty] | Non-TXV | 7.349%
Vacaville | CA | 95687-4616 |  | 2013-09-04 | 2013-09-04 09:28 | 2013-09-04 13:17 | HEIL - N4A342AKA300 | 94 | -5.7 | Yes | Yes | 15.6 | 18.5 | -2.9 | 52BC83092D81479984F2829D2E576661 |  | R22 | Non-TXV |  | -6.064% | 1.0606 | 1.698% |  |  |  |  | Non-TXV |  |  | -6.064%
Bakersfield | CA | 93312-6744 |  | 2013-10-16 | 2013-10-16 12:52 | 2013-10-16 13:08 | CARRIER - 38BRC048370 | 90 | 9.6 | Yes | Yes | 21.2 | 22.5 | -1.3 | CBE7C9876F024E85A06FA50359167E01 |  | R22 | Non-TXV |  | 10.67% | 0.89333 | 20.5% | [5 empty] | Non-TXV | 10.67%
Bakersfield | CA | 93304-1123 |  | 2013-10-15 | 2013-10-15 17:51 | 2013-10-15 17:53 | HEIL - PGC042K0805 | 87 | -8.2 | Yes | Yes | 21.2 | 19.1 | 2.1 | 20F82C4E6C48428991B34E1FA00456F1 |  | R22 | Non-TXV |  | -9.425% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.425%
Bakersfield | CA | 93312-4486 |  | 2013-09-24 | 2013-09-24 18:34 | 2013-09-24 18:34 | CARRIER - 38BR042300 | 131 | 0 | Yes | Yes | 19.3 | 19.8 | -0.5 | 46B81D4B28344D6CB97CBE50E0F02520 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4486 |  | 2013-09-24 | 2013-09-24 18:54 | 2013-09-24 18:54 | YORK - E1RA024S06B | 91 | 0 | Yes | Yes | 21.4 | 22.1 | -0.7 | 1E3022384913438289FFB97125683248 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1121 |  | 2013-09-09 | 2013-09-09 18:53 | 2013-09-09 19:01 | COMFORT AIRE - PGCO42K0805 | 87 | 3.8 | Yes | Yes | 23.8 | 21.7 | 2.1 | 934386E3441C4356986080CDF91B5605 |  | R22 | Non-TXV |  | 4.368% | 0.95632 | 8.394% | [5 empty] | Non-TXV | 4.368%
Bakersfield | CA | 93312-4095 |  | 2013-10-27 | 2013-10-27 18:38 | 2013-10-27 18:42 | RHEEM - UAMA-036-JBZ | 96 | -7.7 | Yes | Yes | 22.1 | 19.8 | 2.3 | BF531AC54A514C129B7D61D17B39ACFF |  | R22 | TXV |  | -8.021% | 1.0802 | 2.246% |  |  |  |  | TXV |  |  | -8.021%
Bakersfield | CA | 93306-2254 |  | 2013-10-15 | 2013-10-15 06:59 | 2013-10-15 08:43 | YORK - D1NH036N05606C | 108 | 5 | Yes | Yes | 18.2 | 20.1 | -1.8 | 499127BFA9214B80853D02A62E00855B |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
San Jose | CA | 95133-2058 |  | 2013-09-25 | 2013-09-25 11:28 | 2013-09-25 12:05 | FRIGIDAIRE - FS3BA-036KA | 69 | 2 | Yes | Yes | 21.7 | 19.7 | 2 | 256F44109D844246ABF7639B9294CA1C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
San Jose | CA | 95118-1917 |  | 2013-09-25 | 2013-09-25 08:36 | 2013-09-25 09:25 | TRANE - 2TTR3036A1000AA | 101 | 9.4 | Yes | Yes | 21.8 | 19.8 | 2 | 2101ED95EFCA489E9978EAAC52E831DD |  | R22 | Non-TXV |  | 9.307% | 0.90693 | 17.89% | [5 empty] | Non-TXV | 9.307%
San Jose | CA | 95111-3097 |  | 2013-09-17 | 2013-09-17 09:37 | 2013-09-17 10:26 | BRYANT - 561CJ042-F | 93 | 2.8 | Yes | Yes | 25.8 | 19.9 | 5.9 | E60CC80ACD6146B49806316D829C92AC |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Bakersfield | CA | 93309-6268 |  | 2013-09-04 | 2013-09-04 13:52 | 2013-09-04 13:52 | OTHER - TGZE-336JL08GAX | 92 | 0 | Yes | Yes | 22 | 20.9 | 1.1 | D95EC63E9EB8446AB6042608305A7C9E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5534 |  | 2013-09-03 | 2013-09-03 10:02 | 2013-09-03 10:03 | HEIL - HAC042AKA1 | 98 | 7.2 | Yes | Yes | 16.2 | 17 | -0.8 | 9F12BA94EB9B4234B56603D17CDA7AF5 |  | R22 | Non-TXV |  | 7.347% | 0.92653 | 14.12% | [5 empty] | Non-TXV | 7.347%
Los Molinos | CA | 96055-9708 |  | 2013-09-08 | 2013-09-08 08:19 | 2013-09-08 08:59 | RHEEM - RQNA-B036JK | 122 | 6 | Yes | Yes | 24.6 | 20.4 | 4.2 | E3E1B364391C469E8F9B1EEC96675E4E |  | R22 | TXV |  | 4.918% | 0.95082 | 9.451% | [5 empty] | TXV | 4.918%
Lost Hills | CA | 93249-0000 |  | 2013-08-28 | 2013-08-28 18:44 | 2013-08-28 18:50 | CARRIER - 48SX-048100341AA | 88 | 5.1 | Yes | Yes | 21.4 | 19.6 | 1.8 | D816A2C182C2442F877AC37295E644F3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.795% | 0.94205 | 11.14% | [5 empty] | Non-TXV | 5.795%
Bakersfield | CA | 93312-6609 |  | 2013-09-06 | 2013-09-06 11:41 | 2013-09-06 12:21 | TRANE - 2TTM3042A1000AA | 74 | 4.4 | Yes | Yes | 15.8 | 18.7 | -2.9 | BF6BA3AF1D3A41228B9AFF66E4C4BFEE |  | R22 | Non-TXV |  | 5.946% | 0.94054 | 11.43% | [5 empty] | Non-TXV | 5.946%
Suisun City | CA | 94585-2818 |  | 2013-09-10 | 2013-09-10 11:23 | 2013-09-10 12:14 | PAYNE - PA10JA036-A | 84 | -3.9 | Yes | Yes | 14.4 | 16.8 | -2.4 | 4CEFCF5D75B1442CAD220F43C655F8F3 |  | R22 | Non-TXV |  | -4.643% | 1.0464 | 1.3% |  |  |  |  | Non-TXV |  |  | -4.643%
Vallejo | CA | 94591-8228 |  | 2013-09-03 | 2013-09-03 12:17 | 2013-09-03 14:57 | GOODMAN - GSC130301AA | 123 | 4.2 | Yes | Yes | 21.1 | 23.7 | -2.6 | C942FAD972904105BB3F28727516A16B |  | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Bakersfield | CA | 93304-2139 |  | 2013-09-09 | 2013-09-09 18:42 | 2013-09-09 18:42 | DAY & NIGHT - N/A | 85 | 0 | Yes | Yes | 22.2 | 19.1 | 3.1 | A53A22B6E7A547FCB6E7016A764F0681 | Add refrigerant: 6.2 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-3338 |  | 2013-08-29 | 2013-08-29 14:43 | 2013-08-29 15:25 | OTHER - UKN | 69 | 3.2 | Yes | Yes | 21.1 | 20.6 | 0.5 | 53B3F23B28C34EA590C222339430F76A |  | R22 | Non-TXV |  | 4.638% | 0.95362 | 8.913% | [5 empty] | Non-TXV | 4.638%
Lost Hills | CA | 93249-0000 |  | 2013-08-28 | 2013-08-28 18:28 | 2013-08-28 18:32 | GOODMAN - GPG13360701AC | 112 | 4.4 | Yes | Yes | 27 | 21 | 6 | 9C1BDDA97FF24A50BE8AC4C94C850098 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Concord | CA | 94520-1738 |  | 2013-09-06 | 2013-09-06 12:01 | 2013-09-06 12:02 | TEMPSTAR - TCA442AKC4 | 298 | 13.1 | Yes | Yes | 18.3 | 17.2 | 1.2 | 96D3249F8A2543DE8B63C0C920467F15 |  | R22 | Non-TXV |  | 4.396% | 0.95604 | 8.448% | [5 empty] | Non-TXV | 4.396%
Bakersfield | CA | 93312-3075 |  | 2013-09-24 | 2013-09-24 15:05 | 2013-09-24 15:21 | ICP - CA5548VKD2 | 134 | 13.5 | Yes | Yes | 19.3 | 20.3 | -1 | DCE0E85B0B2F4226A906AF1EFDA7BF25 |  | R22 | Non-TXV |  | 10.07% | 0.89925 | 19.36% | [5 empty] | Non-TXV | 10.07%
Bakersfield | CA | 93312-1827 |  | 2013-09-06 | 2013-09-06 11:22 | 2013-09-06 11:38 | OTHER - AC048X1021A | 117 | 5.2 | Yes | Yes | 18.7 | 21.6 | -2.8 | B9753CB9922A4AD89F3340A8E22A11FA |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Lost Hills | CA | 93249-0000 |  | 2013-08-29 | 2013-08-29 16:24 | 2013-08-29 16:27 | RHEEM - RAND-048JAZ | 142 | -7.4 | Yes | Yes | 20.1 | 20.4 | -0.3 | 0566E0098CEB4DD7AE3967110FB1477E |  | R22 | TXV |  | -5.211% | 1.0521 | 1.459% |  |  |  |  | TXV |  |  | -5.211%
Bakersfield | CA | 93312-5400 |  | 2013-09-26 | 2013-09-26 12:07 | 2013-09-26 12:07 | CARRIER - 38BR036300 | 113 | 0 | Yes | Yes | 21.6 | 21.3 | 0.4 | 929DF6ABE93749CBAAA4810DA00FC749 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5807 |  | 2013-09-03 | 2013-09-03 10:41 | 2013-09-03 10:42 | PAYNE - PA10JA048-C | 96 | 6.2 | Yes | Yes | 18 | 17 | 1 | 304F9CCE768F40A18584B5AD4D573634 |  | R22 | Non-TXV |  | 6.458% | 0.93542 | 12.41% | [5 empty] | Non-TXV | 6.458%
Mountain View | CA | 94041-1619 |  | 2013-10-02 | 2013-10-02 14:55 | 2013-10-02 15:11 | COLEMAN - TCGD36S21S2A | 63 | 2.1 | Yes | Yes | 18.8 | 21 | -2.2 | 5C4DD3B8977148FAB57ADD77BE7EB9CD |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93312-6528 |  | 2013-10-16 | 2013-10-16 15:44 | 2013-10-16 15:44 | GOODMAN - GSX130481BA | 125 | 0 | Yes | Yes | 21 | 22.5 | -1.5 | 29E037053D844CBB954E0C245CFABCF1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-2326 |  | 2013-09-23 | 2013-09-23 13:20 | 2013-09-23 13:39 | TRANE - 2TTB3030A1000AA | 80 | 3.1 | Yes | Yes | 20.1 | 18.8 | 1.3 | 4BD797B88E924E0FAFEB89F45F697487 |  | R22 | TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | TXV | 3.875%
Bakersfield | CA | 93309-3962 |  | 2013-09-23 | 2013-09-23 15:47 | 2013-09-23 16:05 | PAYNE - UNK | 85 | 4.2 | Yes | Yes | 16 | 19 | -3 | 0BDA8DAADD7242999191AAD51857BD53 |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Bakersfield | CA | 93312-5669 |  | 2013-09-26 | 2013-09-26 13:43 | 2013-09-26 13:43 | YORK - H1RA048S06G | 117 | 0 | Yes | Yes | 21.9 | 21.3 | 0.6 | 2CD78786E5DB4024B5DEFB608C5D7220 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5411 |  | 2013-10-10 | 2013-10-10 10:32 | 2013-10-10 10:32 | ICP - CA9048VKD2 | 164 | 0 | Yes | Yes | 21.6 | 21.9 | -0.3 | 34984240E6994E4BBA73E51B0EDF1656 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-2217 |  | 2013-09-25 | 2013-09-25 08:50 | 2013-09-25 08:50 | NORDYNE - FS5BD-036K | 85 | 0 | Yes | Yes | 21.2 | 17.1 | 4.1 | DDAB03EE4EDC4CF8AA89518FED02AA14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2353 |  | 2013-09-13 | 2013-09-13 08:55 | 2013-09-13 08:55 | BRYANT - 583ANW0360AAAF | 82 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | 1E1AC0E71965494D895DA845C023DE1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5370 |  | 2013-09-24 | 2013-09-24 13:16 | 2013-09-24 13:16 | YORK - H2RC024S06HA | 71 | 0 | Yes | Yes | 18.6 | 21 | -2.4 | 06282E27D4C543ADA2075901F042646B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6722 |  | 2013-09-06 | 2013-09-06 09:04 | 2013-09-06 09:04 | PAYNE - PA10JA036-C | 78 | 0 | Yes | Yes | 14.6 | 17.6 | -3 | 4CD960CFA7184288834FBB41B0564B29 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1634 |  | 2013-09-13 | 2013-09-13 09:41 | 2013-09-13 10:09 | RHEEM - RRMA-A036JK0BE | 85 | 3.1 | Yes | Yes | 19.3 | 21 | -1.7 | 58CFC5B8BCAD4514B3E8C49C9ED02C00 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Concord | CA | 94521-4624 |  | 2013-09-06 | 2013-09-06 14:24 | 2013-09-06 14:26 | CARRIER - 38CKC036350 | 70 | 6.4 | Yes | Yes | 17.8 | 17.6 | 0.2 | B82AB5B61D4447A4948D2A0B7D57DB3D |  | R22 | Non-TXV |  | 9.143% | 0.90857 | 17.57% | [5 empty] | Non-TXV | 9.143%
Wasco | CA | 93280-2762 |  | 2013-09-17 | 2013-09-17 19:15 | 2013-09-17 19:16 | OTHER - H2RD048S06B | 134 | -7.6 | Yes | Yes | 24.2 | 20.9 | 3.3 | 07D9D0DD4CA8493381B6B52B4E267B65 |  | R22 | Non-TXV |  | -5.672% | 1.0567 | 1.588% |  |  |  |  | Non-TXV |  |  | -5.672%
Bakersfield | CA | 93312-6119 |  | 2013-09-06 | 2013-09-06 13:05 | 2013-09-06 18:59 | OTHER - AC042X1021A | 84 | -4.9 | Yes | Yes | 17.7 | 20.3 | -2.6 | 85F3AFBAE3564BF78C31DBAA5352DA1C |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Lemoore | CA | 93245-1713 |  | 2013-08-29 | 2013-08-29 11:33 | 2013-08-29 11:33 | RHEEM - EAFF031JAZ | 92 | 20.1 | Yes | Yes | 14.3 | 22.1 | -7.8 | B290B096774B4CF3960073AD0CF625AA | Add refrigerant: 20.1 oz | R22 | Non-TXV |  | 21.85% | 0.78152 | 41.99% | [5 empty] | Non-TXV | 21.85%
San Jose | CA | 95136-1337 |  | 2013-09-25 | 2013-09-25 12:40 | 2013-09-25 13:23 | COLEMAN - ILLEGIBLE | 70 | -6.6 | Yes | Yes | 25.7 | 21 | 4.7 | 0C4EC78FBB024B1E9E180FCFA3B343C0 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Bakersfield | CA | 93311-9124 |  | 2013-09-12 | 2013-09-12 10:01 | 2013-09-12 10:46 | CARRIER - 38CKC030340 | 85 | 7.4 | Yes | Yes | 17.5 | 20.4 | -2.9 | CE34DEBB9120453D82ABCD0421B149CA | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | TXV | 8.706%
Bakersfield | CA | 93311-9124 |  | 2013-09-12 | 2013-09-12 10:50 | 2013-09-12 11:59 | CARRIER - 38CKC030340 | 85 | 3.1 | Yes | Yes | 18 | 20.4 | -2.4 | 6BF89E4C7F634ECABD5F5EBC8F8E0DDF | OK: Verified Refrigerant Charge Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Bakersfield | CA | 93309-4638 |  | 2013-10-08 | 2013-10-08 15:18 | 2013-10-08 15:18 | YORK - H4DB018S06A | 62 | 0 | Yes | Yes | 22.2 | 21.3 | 1 | CABB3882C712464D80F23475DF26B1E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3025 |  | 2013-08-30 | 2013-08-30 12:46 | 2013-08-30 12:46 | AMANA - APG154811541AB | 172 | 0 | Yes | Yes | 14.7 | 17.7 | -3 | 861DBC3C0CC745A2A2B37685C382DF90 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1806 |  | 2013-09-04 | 2013-09-04 13:47 | 2013-09-04 13:47 | CARRIER - 38CK036340 | 74 | 0 | Yes | Yes | 14.9 | 17.4 | -2.5 | ECC6ED49E4A741988F63468E261F4FA6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4432 |  | 2013-08-29 | 2013-08-29 19:32 | 2013-08-29 19:32 | RHEEM - UKN | 68 | 0 | Yes | Yes | 0 | N/A | N/A | CC814E2F3AD342BB93917BED206F1766 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-1109 |  | 2013-09-25 | 2013-09-25 10:40 | 2013-09-25 10:40 | CARRIER - UNK | 80 | 0 | Yes | Yes | 21.6 | 19.9 | 1.7 | 1C5D7811E5D24B1A86F16FF29FB1C17D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Anderson | CA | 96007-9170 |  | 2013-09-06 | 2013-09-06 12:02 | 2013-09-06 12:34 | AMERICAN STANDARD - 14A34BGKA200 | 138 | 17.2 | Yes | Yes | 27 | 21 | 6 | EDB3B79A668742E197F6EAAB1BB1C140 |  | R410A | TXV |  | 12.46% | 0.87536 | 23.95% | [5 empty] | TXV | 12.46%
Bakersfield | CA | 93314-9767 |  | 2013-09-04 | 2013-09-04 09:10 | 2013-09-04 09:39 | COLEMAN - 6286-901 | 85 | 2.8 | Yes | Yes | 13.9 | 16.8 | -2.9 | 5AA4EF59B41B4AE0A3AFED7854011F57 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Anderson | CA | 96007-3529 |  | 2013-09-04 | 2013-09-04 16:23 | 2013-09-04 16:53 | PAYNE - PY3PNA048090NB | 197 | -11.6 | Yes | Yes | 21.8 | 23.5 | -1.7 | 32933206ECBE4A23A8F6CC215757315B |  | R22 | Non-TXV |  | -5.888% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.888%
Buttonwillow | CA | 93206-9725 |  | 2013-09-24 | 2013-09-24 19:58 | 2013-09-24 20:00 | OTHER - SRM-51837A | 48 | 4.8 | Yes | Yes | 20 | 18.8 | 1.2 | E0355A43799549E4BE965D7361379486 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fairfield | CA | 94533-5436 |  | 2013-10-09 | 2013-10-09 09:42 | 2013-10-09 09:42 | TRANE - 4TTB030E1000AA | 82 | 0 | Yes | Yes | 20.2 | 17.2 | 3 | 0871EA406DFA4C45A2D96E75A6A2B792 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3256 |  | 2013-09-06 | 2013-09-06 13:11 | 2013-09-06 13:43 | OTHER - 2SCU13LB136P-1 | 111 | 4.2 | Yes | Yes | 14 | 16.2 | -2.2 | 68D62295F0B54B61B9CF09AB1BCE00BE |  | R22 | Non-TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | Non-TXV | 3.784%
Bakersfield | CA | 93313-5411 |  | 2013-10-10 | 2013-10-10 09:43 | 2013-10-10 09:43 | ICP - CA9042VKD2 | 128 | 0 | Yes | Yes | 21.9 | 20.8 | 1.1 | 3139677D433E46ADA085D55DFDBA95D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4963 |  | 2013-09-04 | 2013-09-04 10:07 | 2013-09-04 10:57 | OTHER - 563AN042-A | 85 | 2.6 | Yes | Yes | 26.1 | 20.6 | 5.5 | EF7A12B1937D48C4948FC5F9690391C8 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
San Jose | CA | 95135-1323 |  | 2013-09-30 | 2013-09-30 10:07 | 2013-09-30 11:14 | CARRIER - 38CKC030330 | 66 | 3.4 | Yes | Yes | 20.8 | 21.9 | -1.1 | A96F079B06C942B7825E6F0605646464 |  | R22 | Non-TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | Non-TXV | 5.152%
Bakersfield | CA | 93313-5466 |  | 2013-09-17 | 2013-09-17 13:34 | 2013-09-17 13:55 | NORDYNE - FS3BC-048KA | 110 | 9.4 | Yes | Yes | 21.8 | 21.5 | 0.3 | 4079CE97621547BFAEF014D804547EE9 |  | R22 | Non-TXV |  | 8.545% | 0.91455 | 16.42% | [5 empty] | Non-TXV | 8.545%
Bakersfield | CA | 93304-5039 |  | 2013-09-09 | 2013-09-09 19:21 | 2013-09-09 19:24 | DAY & NIGHT - 591ANX048000ABAA | 85 | 3.5 | Yes | Yes | 24.2 | 22.6 | 1.6 | 072F70D52A55492DAF7DE8B02829766D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93312-9458 |  | 2013-09-04 | 2013-09-04 18:55 | 2013-09-04 18:57 | DAY & NIGHT - N/A | 85 | 3.2 | Yes | Yes | 26.6 | 22.4 | 4.2 | 9D0EF7C21C504E26B5ADDC6A686855C5 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Bakersfield | CA | 93312-9458 |  | 2013-09-04 | 2013-09-04 19:02 | 2013-09-04 19:02 | DAY & NIGHT - N/A | 85 | 0 | Yes | Yes | 34.9 | 20.4 | 14.5 | 2C48D08C22F3451599B7C83627BA08E3 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-9458 |  | 2013-09-04 | 2013-09-04 19:10 | 2013-09-04 19:12 | TEMPSTAR - PGAB30CLK1 | 74 | 5.1 | Yes | Yes | 25.3 | 21 | 4.3 | 811D4372E97F4776B9998436C1B12996 |  | R22 | Non-TXV |  | 6.892% | 0.93108 | 13.24% | [5 empty] | Non-TXV | 6.892%
Bakersfield | CA | 93313-9812 |  | 2013-09-11 | 2013-09-11 19:04 | 2013-09-11 19:06 | OTHER - H2R048S06HG | 119 | -6.6 | Yes | Yes | 20.2 | 19.4 | 0.8 | 831431AFE69D4417825C65B4725CB550 |  | R22 | TXV |  | -5.546% | 1.0555 | 1.553% |  |  |  |  | TXV |  |  | -5.546%
Bakersfield | CA | 93311-1800 |  | 2013-09-19 | 2013-09-19 09:32 | 2013-09-19 09:48 | RHEEM - UNK | 85 | 6.3 | Yes | Yes | 16.6 | 19.4 | -2.8 | 4CAEAD4FC40A47A0B205D5BFE50668D4 |  | R22 | Non-TXV |  | 7.412% | 0.92588 | 14.24% | [5 empty] | Non-TXV | 7.412%
Bakersfield | CA | 93312-5433 |  | 2013-09-11 | 2013-09-11 11:41 | 2013-09-11 12:14 | GOODMAN - CK1-36-1D | 85 | 2.9 | Yes | Yes | 11.5 | 14.3 | -2.8 | 19EF60A3B00845A58924C0DEBF91B140 |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Fairfield | CA | 94533-7329 |  | 2013-09-13 | 2013-09-13 09:08 | 2013-09-13 09:09 | GOODMAN - GSH130241BA | 122 | -8.6 | Yes | Yes | 16.7 | 17.6 | -0.9 | 90C48827EC56442FA49C348346462127 |  | R22 | Non-TXV |  | -7.049% | 1.0705 | 1.974% |  |  |  |  | Non-TXV |  |  | -7.049%
Bakersfield | CA | 93307-7289 |  | 2013-10-12 | 2013-10-12 08:32 | 2013-10-12 09:03 | WEATHER KING - 12AJB36A01 | 85 | 5 | Yes | Yes | 19.5 | 22.5 | -3 | 8F4D7697FC134DF08F53175B7B2D6E8C |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Byron | CA | 94505-9463 |  | 2013-10-03 | 2013-10-03 09:51 | 2013-10-03 09:53 | OTHER - NA | 72 | 2.8 | Yes | Yes | 17.5 | 17 | 0.5 | 6AE8FD9DF7B144758777BE57D82F46DE |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Bakersfield | CA | 93309-1160 |  | 2013-09-11 | 2013-09-11 19:46 | 2013-09-11 19:46 | RHEEM - URKA-A024J06Z | 85 | -6 | Yes | Yes | 23.4 | 20.3 | 3.1 | 275FD2893BED409B89D52010C99449AB | Remove refrigerant: 6 oz | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93313-5538 |  | 2013-09-10 | 2013-09-10 19:52 | 2013-09-10 19:54 | RHEEM - RAMC-060JB2 | 192 | 7.9 | Yes | Yes | 21.5 | 21.5 | 0 | D75EC28298834F00AA847E14442B50AA |  | R22 | TXV |  | 4.115% | 0.95885 | 7.907% | [5 empty] | TXV | 4.115%
Mountain View | CA | 94041-1619 |  | 2013-10-02 | 2013-10-02 15:13 | 2013-10-02 16:05 | UNITARY PRODUCTS GROUP - BRQ0181BE | 32 | 2.7 | Yes | Yes | 20.2 | 21 | -0.8 | 25EBF5633E524731A1385CBB9BD6D129 |  | R22 | Non-TXV |  | 8.438% | 0.91563 | 16.22% | [5 empty] | Non-TXV | 8.438%
Bakersfield | CA | 93308-1725 |  | 2013-09-26 | 2013-09-26 16:30 | 2013-09-26 16:30 | WESTINGHOUSE - 1E030BAA0N | 86 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | B0766CC5C00C4F119AB552D5E15A7A54 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2435 |  | 2013-09-18 | 2013-09-18 11:56 | 2013-09-18 12:29 | YORK - D1NP060N09006A | 140 | 11.5 | Yes | Yes | 17.5 | 20.4 | -2.9 | 6D4315EA000F434880ED41F10852080D |  | R22 | Non-TXV |  | 8.214% | 0.91786 | 15.79% | [5 empty] | Non-TXV | 8.214%
Bakersfield | CA | 93311-2733 |  | 2013-09-12 | 2013-09-12 12:01 | 2013-09-12 12:44 | ARCOAIRE - UNK | 85 | 2.8 | Yes | Yes | 16.5 | 19.3 | -2.8 | 4E32661A76054151BE542718B064693A |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Milpitas | CA | 95035-5921 |  | 2013-09-26 | 2013-09-26 13:43 | 2013-09-26 17:52 | GOODMAN - CK30 1A | 76 | 4.4 | Yes | Yes | 21.3 | 21 | 0.3 | 522F7B43179A4BAAA3A6908564C013D8 |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Anderson | CA | 96007-8336 |  | 2013-09-04 | 2013-09-04 14:24 | 2013-09-04 14:59 | ARMSTRONG - RPHP13A60P-1 | 150 | 18.9 | Yes | Yes | 24 | 22 | 2.1 | C1023EDEDD804D4788CA62F72F329509 |  | R410A | TXV |  | 12.6% | 0.874 | 24.21% | [5 empty] | TXV | 12.6%
Bakersfield | CA | 93304-1325 |  | 2013-09-09 | 2013-09-09 18:26 | 2013-09-09 18:26 | OTHER - 8UAW25 | 62 | 0 | Yes | Yes | 11.7 | 17.1 | -5.4 | 693F7E55C36C41A8B63FD1A7618B02AD | Add refrigerant: 8.9 oz Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5809 |  | 2013-09-16 | 2013-09-16 10:41 | 2013-09-16 11:33 | BRYANT - 582ANW036060NBAF | 85 | 2.6 | Yes | Yes | 17.2 | 19.5 | -2.3 | C6462194BFA34706BFADC526066E10C5 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93309-4636 |  | 2013-10-08 | 2013-10-08 19:35 | 2013-10-08 19:35 | BDP - 567C018RCU | 37 | 0 | Yes | Yes | 22 | 22.1 | -0.1 | 5A896ADBF4F14DDF87A8264B41B1221B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8003 |  | 2013-09-04 | 2013-09-04 10:14 | 2013-09-04 13:19 | RUUD - UAFD-024JAS | 67 | 4.1 | Yes | Yes | 11.5 | 12.8 | -1.3 | 9F46E94D339F4C8CB08F264309E181FB |  | R22 | Non-TXV |  | 6.119% | 0.93881 | 11.76% | [5 empty] | Non-TXV | 6.119%
Bakersfield | CA | 93305-3144 |  | 2013-10-15 | 2013-10-15 14:20 | 2013-10-15 14:20 | YORK - DCYZ-F036N070C | 64 | 0 | Yes | Yes | 20.4 | 20.2 | 0.3 | A291B920FDB54E099C288DB2392FD4AC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5356 |  | 2013-09-06 | 2013-09-06 12:24 | 2013-09-06 13:03 | YORK - H1RC048S06B | 122 | 4 | Yes | Yes | 18.8 | 21.8 | -3 | 3701BDB8FF634F0D9DD177AAF9C74151 |  | R22 | Non-TXV |  | 3.279% | 0.96721 | 6.301% | [5 empty] | Non-TXV | 3.279%
San Jose | CA | 95116-3088 |  | 2013-09-23 | 2013-09-23 18:38 | 2013-09-23 18:38 | GOODMAN - CK36-1B | 76 | 0 | Yes | Yes | 5.7 | 22.1 | -16.4 | 2AB30F896C754C7694265DCB82A0BEF6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3969 |  | 2013-08-30 | 2013-08-30 11:52 | 2013-08-30 12:21 | BRYANT - 563CN060-E | 85 | 2.6 | Yes | Yes | 12.6 | 15.4 | -2.8 | F5BCA02D505A4FC4BF196554D1570CFA |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Vacaville | CA | 95687-6407 |  | 2013-09-06 | 2013-09-06 16:06 | 2013-09-06 16:06 | CARRIER - 38TKB036300 | 81 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | F5BEE6844E6441CDB6BD6A8D579A4C1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-1917 |  | 2013-09-04 | 2013-09-04 13:14 | 2013-09-04 13:32 | OTHER - 38CK036320 | 85 | 4 | Yes | Yes | 26.1 | 20.2 | 6 | 6BC1F46A276D40B1BC16E10CF2E6ECB2 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Bakersfield | CA | 93306-6022 |  | 2013-09-10 | 2013-09-10 09:56 | 2013-09-10 10:52 | ICP - PGAD47D1K7 | 215 | 9.9 | Yes | Yes | 20.3 | 20.1 | 0.2 | 962941C28C4145599314B096683DA68B |  | R22 | Non-TXV |  | 4.605% | 0.95395 | 8.849% | [5 empty] | Non-TXV | 4.605%
Bakersfield | CA | 93312-2029 |  | 2013-09-04 | 2013-09-04 11:00 | 2013-09-04 13:09 | RHEEM - UNK | 85 | 5.3 | Yes | Yes | 20.6 | 23.4 | -2.8 | 7B0358744DDB4DD998CB63FBC577A3B8 |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
San Jose | CA | 95111-3814 |  | 2013-09-17 | 2013-09-17 13:57 | 2013-09-17 14:45 | TRANE - TTB036C100A1 | 90 | 4 | Yes | Yes | 24.6 | 19.4 | 5.2 | 639FF3D7ED1E48D7A90723BC33EF8552 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Bakersfield | CA | 93308-2205 |  | 2013-09-18 | 2013-09-18 10:52 | 2013-09-18 11:17 | TRANE - YCZ036F1M0BD | 160 | 11.3 | Yes | Yes | 22 | 20.9 | 1.1 | 544B6DA9E3A24AEA92D87812549BA97A |  | R22 | Non-TXV |  | 7.062% | 0.92937 | 13.57% | [5 empty] | Non-TXV | 7.062%
Fairfield | CA | 94533-4920 |  | 2013-09-12 | 2013-09-12 13:00 | 2013-09-12 13:00 | CARRIER - 48SS-036080321AA | 67 | -6.3 | Yes | Yes | 14.1 | 18.5 | -4.4 | E7FEAFF7258E435D9AC3B8172212AA33 | Remove refrigerant: 6.3 oz | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
San Jose | CA | 95135-1335 |  | 2013-10-02 | 2013-10-02 14:32 | 2013-10-02 15:07 | GE - 21TA924H1F | 49 | -4 | Yes | Yes | 22.8 | 18.2 | 4.6 | 58FB1D1FFEFA449C94399135D960F4F0 |  | R22 | Non-TXV |  | -8.163% | 1.0816 | 2.286% |  |  |  |  | Non-TXV |  |  | -8.163%
San Jose | CA | 95110-3502 |  | 2013-09-24 | 2013-09-24 10:06 | 2013-09-24 10:32 | WEATHER KING - 13AJA36A01 | 108 | 3.7 | Yes | Yes | 18.1 | 20.4 | -2.3 | 7481C99296C8484AB9D11FF8393B1DDD |  | R22 | Non-TXV |  | 3.426% | 0.96574 | 6.584% | [5 empty] | Non-TXV | 3.426%
Bakersfield | CA | 93309-6003 |  | 2013-09-16 | 2013-09-16 09:37 | 2013-09-16 10:37 | ICP - PGC042K0B0E | 85 | 2.7 | Yes | Yes | 17 | 19.9 | -2.9 | 25897467F9A64A83B247FF80137554C2 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Vacaville | CA | 95687-5152 |  | 2013-09-06 | 2013-09-06 09:35 | 2013-09-06 09:35 | GUARDIAN - GCGD30S41S3A | 58 | 0 | Yes | Yes | 16.2 | 18.8 | -2.6 | 5423692C5CC14F99A027221094A99E61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3913 |  | 2013-09-23 | 2013-09-23 16:08 | 2013-09-23 16:25 | DAY & NIGHT - 585HJ20024040ABAE | 68 | 3.6 | Yes | Yes | 17.8 | 20.7 | -2.9 | A0156CCE7BDA41FDA88E4AE30595B4B7 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Bakersfield | CA | 93308-2359 |  | 2013-09-05 | 2013-09-05 21:07 | 2013-09-05 21:15 | LENNOX - LB-34802BB | 85 | 10.1 | Yes | Yes | 12.5 | 19 | -6.5 | BCC2C6B06D6B438AB77FC7AF8F13B234 | Add refrigerant: 5.7 oz | R22 | TXV |  | 11.88% | 0.88118 | 22.84% | [5 empty] | TXV | 11.88%
Bakersfield | CA | 93312-5103 |  | 2013-09-06 | 2013-09-06 07:44 | 2013-09-06 08:01 | AIRE-FLO - EAFF-049812697 | 85 | 4.4 | Yes | Yes | 17.4 | 20.4 | -3 | 932EFC8690A44BDAB179D8FC5EF61523 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
San Jose | CA | 95123-4547 |  | 2013-09-19 | 2013-09-19 10:48 | 2013-09-19 11:04 | TRANE - 2TTR3048A1OOOAA | 142 | 4.7 | Yes | Yes | 18.4 | 21 | -2.6 | C6A1A57E84BF427FA9C0582923A3E7A2 |  | R22 | Non-TXV |  | 3.31% | 0.9669 | 6.361% | [5 empty] | Non-TXV | 3.31%
San Jose | CA | 95135-1310 |  | 2013-09-30 | 2013-09-30 15:26 | 2013-09-30 16:00 | GE - 21TA924H1H | 42 | 9.3 | Yes | Yes | 25.5 | 19.9 | 5.6 | 31AE96BA00324BAEB258C89C38143B8C |  | R22 | Non-TXV |  | 22.14% | 0.77857 | 42.55% | [5 empty] | Non-TXV | 22.14%
Anderson | CA | 96007-8210 |  | 2013-09-06 | 2013-09-06 10:45 | 2013-09-06 11:33 | BDP - 542EJX036000AAAE | 132 | 4.6 | Yes | Yes | 23.6 | 20.8 | 2.8 | 8EC4DA1F35A74509924D02BBAAF47BC3 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Bakersfield | CA | 93305-1824 |  | 2013-09-13 | 2013-09-13 10:12 | 2013-09-13 11:04 | GOODMAN - SRM-5120A | 85 | 2.5 | Yes | Yes | 14.8 | 17.7 | -2.9 | DCD2EA2B20D049F0ADB14D378D4C1F32 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93312-6850 |  | 2013-09-20 | 2013-09-20 18:07 | 2013-09-20 18:09 | LENNOX - 13ACD-36-230-02 | 111 | 4.2 | Yes | Yes | 24.3 | 21.5 | 2.8 | E2664CA209E840A5BCD1FA0393D8A976 |  | R22 | TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | TXV | 3.784%
Bakersfield | CA | 93312-6850 |  | 2013-09-20 | 2013-09-20 18:15 | 2013-09-20 18:19 | LENNOX - N/A | 111 | 6.7 | Yes | Yes | 23.5 | 21.5 | 2 | A73A0AA0E1544AB8BA86493AAE5809D2 |  | R22 | TXV |  | 6.036% | 0.93964 | 11.6% | [5 empty] | TXV | 6.036%
Bakersfield | CA | 93311-9119 |  | 2013-09-12 | 2013-09-12 22:13 | 2013-09-12 22:32 | OTHER - 38BRC048370 | 85 | 2.6 | Yes | Yes | 17.6 | 20.6 | -3 | 760B1C308220499EA1E37726424AB997 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93304-4214 |  | 2013-10-16 | 2013-10-16 05:35 | 2013-10-16 06:30 | ICP - PGAA.30C1K3 | 75 | 9 | Yes | Yes | 23.5 | 23.4 | 0.1 | AC83CCAD1868460B8288D4E7CA6A6A96 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Lemoore | CA | 93245-1785 |  | 2013-09-18 | 2013-09-18 09:34 | 2013-09-18 09:52 | HEIL - FBA242GGA1 | 103 | 3.4 | Yes | Yes | 18.4 | 18.7 | -0.3 | 340B7B3B0B244EC08C3C0025A91B04C4 |  | R22 | Non-TXV |  | 3.301% | 0.96699 | 6.344% | [5 empty] | Non-TXV | 3.301%
Fremont | CA | 94538-1926 |  | 2013-09-23 | 2013-09-23 09:03 | 2013-09-23 09:03 | RUUD - UANB-036JAZ | 85 | 0 | Yes | Yes | 17.3 | 15.9 | 1.4 | 93A08EF98E22456382F7556A7873A9BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2553 |  | 2013-09-18 | 2013-09-18 13:36 | 2013-09-18 14:02 | CARRIER - UNK | 128 | 4.7 | Yes | Yes | 20 | 19.3 | 0.7 | F5CAB2C9ADDC44E4806FF57A6A8AF9B7 |  | R22 | Non-TXV |  | 3.672% | 0.96328 | 7.057% | [5 empty] | Non-TXV | 3.672%
Bakersfield | CA | 93308-5630 |  | 2013-09-12 | 2013-09-12 19:22 | 2013-09-12 19:24 | GOODMAN - GPG13360451AC | 112 | 15 | Yes | Yes | 24.2 | 19.2 | 5 | A1082243D6634442BA958ECA2D8848D7 |  | R22 | Non-TXV |  | 13.39% | 0.86607 | 25.74% | [5 empty] | Non-TXV | 13.39%
Bakersfield | CA | 93304-2047 |  | 2013-09-09 | 2013-09-09 18:35 | 2013-09-09 18:39 | AMERICAN STANDARD - YCY048F1HOAA | 177 | -7.7 | Yes | Yes | 23.4 | 19.8 | 3.6 | 12C540394B8340D5BEDBDC5736E8C379 |  | R22 | TXV |  | -4.35% | 1.0435 | 1.218% |  |  |  |  | TXV |  |  | -4.35%
San Jose | CA | 95135-1306 |  | 2013-09-30 | 2013-09-30 14:36 | 2013-09-30 14:59 | GE - TA924H1F | 48 | 1.6 | Yes | Yes | 21.7 | 18.6 | 3.1 | B8E4C6208A1644AA976E2B576745C8B7 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93308-2929 |  | 2013-09-12 | 2013-09-12 19:43 | 2013-09-12 19:45 | PAYNE - PA12NA048B | 156 | -6.2 | Yes | Yes | 22.1 | 20.9 | 1.2 | 7B560A64167441768B3EFB5B96E02B5B |  | R22 | TXV |  | -3.974% | 1.0397 | 1.113% |  |  |  |  | TXV |  |  | -3.974%
San Jose | CA | 95131-2979 |  | 2013-09-25 | 2013-09-25 10:13 | 2013-09-25 10:13 | RHEEM - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | E18CB21FEE5A440FA4585AC0BA78FE2A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4914 |  | 2013-09-06 | 2013-09-06 10:42 | 2013-09-06 11:07 | COMFORT AIRE - CAC036AKA4 | 85 | 2.8 | Yes | Yes | 18.5 | 21.5 | -3 | 9E33D9C3A03C45C396C511DD4C46D73E |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
San Jose | CA | 95135-1431 |  | 2013-10-02 | 2013-10-02 16:10 | 2013-10-02 16:32 | BDP - 588ANW036060ACBF | 67 | 4.7 | Yes | Yes | 25.6 | 20.4 | 5.2 | 3C8CF6A31E0344E7BA6F825F7A7011A2 |  | R22 | Non-TXV |  | 7.015% | 0.92985 | 13.48% | [5 empty] | Non-TXV | 7.015%
Cottonwood | CA | 96022-7621 |  | 2013-09-07 | 2013-09-07 15:26 | 2013-09-07 15:51 | ARMSTRONG - SCU10G42A-1 | 87 | 3.2 | Yes | Yes | 27.7 | 23.3 | 4.5 | 668BE8E58397409CA203F990D70EC383 |  | R22 | Non-TXV |  | 3.678% | 0.96322 | 7.069% | [5 empty] | Non-TXV | 3.678%
Bakersfield | CA | 93313-2645 |  | 2013-10-14 | 2013-10-14 15:58 | 2013-10-14 15:58 | PAYNE - PY3GNAA48090NA | 100 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | ACBD53B2A0C74D9DADFA4395BA2C11DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5317 |  | 2013-10-27 | 2013-10-27 18:28 | 2013-10-27 18:31 | OTHER - H2RD036S06B | 96 | 17.8 | Yes | Yes | 20.5 | 20.3 | 0.2 | 6DEF64F10E904FC980A9E238D0EA0565 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.54% | 0.81458 | 35.63% | [5 empty] | Non-TXV | 18.54%
Wasco | CA | 93280-2107 |  | 2013-09-08 | 2013-09-08 19:52 | 2013-09-08 19:54 | ARCOAIRE - PGAA47D1K4 | 113 | 6.9 | Yes | Yes | 25.4 | 21.3 | 4.2 | 93A63467B72F42B5BAE74AB0A4348CB6 |  | R22 | Non-TXV |  | 6.106% | 0.93894 | 11.73% | [5 empty] | Non-TXV | 6.106%
Wasco | CA | 93280-2775 |  | 2013-09-08 | 2013-09-08 19:58 | 2013-09-08 20:01 | OTHER - TCGD30S21A | 59 | 6.9 | Yes | Yes | 21.9 | 20.4 | 1.5 | 622F72F0B977419EAFE99A2B3B2C84EB |  | R22 | TXV |  | 11.69% | 0.88305 | 22.48% | [5 empty] | TXV | 11.69%
Bakersfield | CA | 93309-6825 |  | 2013-09-16 | 2013-09-16 12:28 | 2013-09-16 14:13 | - | 85 | 3.3 | Yes | Yes | 19.5 | 20.7 | -1.2 | AF2AD1F2F8A744228C261DE9E1DFAF06 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Bakersfield | CA | 93305-1235 |  | 2013-09-13 | 2013-09-13 09:07 | 2013-09-13 09:37 | OTHER - 56CJ036-D | 85 | 4.5 | Yes | Yes | 16 | 18.8 | -2.8 | 28980A0551924882B73AAC266A6279D2 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Bakersfield | CA | 93312-2843 |  | 2013-10-27 | 2013-10-27 19:32 | 2013-10-27 19:35 | ARCOAIRE - PGMD36G0752 | 81 | 5 | Yes | Yes | 20.3 | 20.2 | 0.1 | 1FD692E005EE44D1B37232AB3914B8FA |  | R22 | Non-TXV |  | 6.173% | 0.93827 | 11.86% | [5 empty] | Non-TXV | 6.173%
Bakersfield | CA | 93312-2843 |  | 2013-10-27 | 2013-10-27 19:38 | 2013-10-27 19:40 | YORK - D1NH036N05606C | 108 | 3.2 | Yes | Yes | 24.6 | 20.1 | 4.5 | 0F77A08346144258960D6166799EBC59 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Bakersfield | CA | 93312-2843 |  | 2013-10-27 | 2013-10-27 19:44 | 2013-10-27 19:46 | YORK - B1HH02406B | 85 | -5 | Yes | Yes | 22.8 | 20.4 | 2.4 | 202052DF570D4042BEEECD4DA1CC3D22 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
San Jose | CA | 95111-1816 |  | 2013-09-17 | 2013-09-17 11:28 | 2013-09-17 12:38 | TRANE - 4TTX5042A1000AA | 112 | 13.4 | Yes | Yes | 21.5 | 17.6 | 3.9 | 1BB109D0C6EC4E8EA8BD16976DFAE6BD |  | R410A | TXV |  | 11.96% | 0.88036 | 22.99% | [5 empty] | TXV | 11.96%
Bakersfield | CA | 93312-6861 |  | 2013-09-08 | 2013-09-08 20:19 | 2013-09-08 20:21 | OTHER - 13ACD-048-230 | 204 | -7.4 | Yes | Yes | 22.6 | 21 | 1.6 | 140FB8F24B2F4BA8BFF931B0962C4D71 |  | R22 | Non-TXV |  | -3.627% | 1.0363 | 1.016% |  |  |  |  | Non-TXV |  |  | -3.627%
Lost Hills | CA | 93249-0000 |  | 2013-09-18 | 2013-09-18 17:35 | 2013-09-18 17:38 | RUUD - N/A | 85 | 0 | Yes | Yes | 18.6 | 19.8 | -1.2 | 76AA21B25AEA4B26B922219BF8923D95 | Add refrigerant: 14.6 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5805 |  | 2013-09-11 | 2013-09-11 12:19 | 2013-09-11 13:26 | PAYNE - PA12NA036-B | 85 | 3.4 | Yes | Yes | 16.5 | 19.5 | -3 | D06C2AAEF9624F1384D47A0010AE2C4E |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93727-1926 |  | 2013-09-13 | 2013-09-13 11:38 | 2013-09-13 12:10 | BRYANT - 574ANW042090NA | 168 | 5 | Yes | Yes | 20.3 | 19.7 | 0.6 | FD14AFFA588E4534A2CEA4186B920402 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Bakersfield | CA | 93308-1720 |  | 2013-09-09 | 2013-09-09 13:04 | 2013-09-09 13:28 | YORK - D1NH036N05606C | 108 | 11.6 | Yes | Yes | 16.8 | 19.8 | -3 | EE27A9D926E5437693597CEC3E813C6F |  | R22 | Non-TXV |  | 10.74% | 0.89259 | 20.64% | [5 empty] | Non-TXV | 10.74%
Bakersfield | CA | 93312-4414 |  | 2013-09-11 | 2013-09-11 11:09 | 2013-09-11 11:39 | RUUD - UNK | 85 | 5.5 | Yes | Yes | 17.5 | 20.4 | -2.9 | 15D00D2B51BF4AD0A2669737204A19EC |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Lemoore | CA | 93245-9560 |  | 2013-09-20 | 2013-09-20 14:22 | 2013-09-20 15:01 | RHEEM - RRNAA036JK06X | 114 | 16.9 | Yes | Yes | 20.6 | 19.3 | 1.3 | F448C6ABC2ED4F31A5950EA0F76404D9 |  | R22 | Non-TXV |  | 14.82% | 0.85175 | 28.49% | [5 empty] | Non-TXV | 14.82%
Lemoore | CA | 93245-9560 |  | 2013-09-20 | 2013-09-20 15:07 | 2013-09-20 15:29 | RHEEM - UNK | 70 | 14.3 | Yes | Yes | 23.5 | 20.4 | 3.1 | DA3F96DA3F0649419B80144D2EC4D300 |  | R22 | Non-TXV |  | 20.43% | 0.79571 | 39.26% | [5 empty] | Non-TXV | 20.43%
Bakersfield | CA | 93309-5940 |  | 2013-09-18 | 2013-09-18 11:07 | 2013-09-18 11:54 | ICP - PGF342080K01A1 | 85 | 2.7 | Yes | Yes | 16.4 | 19.2 | -2.8 | A49D65FC45EB4499BCE21343011F3CEB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93308-7152 |  | 2013-09-09 | 2013-09-09 11:14 | 2013-09-09 13:02 | YORK - H2RC042S06HG | 109 | 3.5 | Yes | Yes | 19.6 | 22.6 | -3 | CEA838A4638D4D9AAC67BE2029E4C2D5 |  | R22 | Non-TXV |  | 3.211% | 0.96789 | 6.171% | [5 empty] | Non-TXV | 3.211%
Sanger | CA | 93657-3606 |  | 2013-09-30 | 2013-09-30 10:35 | 2013-09-30 11:05 | RHEEM - RRMAA042JKO8X | 114 | 6.3 | Yes | Yes | 21.7 | 19.7 | 2 | 1EBEAC6D4C604374AF37E2377EC9CA46 |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Bakersfield | CA | 93306-4711 |  | 2013-09-16 | 2013-09-16 17:58 | 2013-09-16 18:23 | PAYNE - PY3PNA036C6CNB | 114 | 14.6 | Yes | Yes | 22.2 | 22.1 | 0.1 | 3FC65A662D7F4248B379878E3B4CA87E |  | R22 | Non-TXV |  | 12.81% | 0.87193 | 24.61% | [5 empty] | Non-TXV | 12.81%
Bakersfield | CA | 93308-5678 |  | 2013-09-09 | 2013-09-09 09:51 | 2013-09-09 11:10 | YORK - D1NA036N0560606B | 63 | 5.4 | Yes | Yes | 20 | 20.9 | -0.9 | ADD3D8AEEF5449C4A9993C4BB2332CED |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Bakersfield | CA | 93308-2412 |  | 2013-10-23 | 2013-10-23 15:07 | 2013-10-23 15:24 | BDP - 588ANW036060AAAF | 67 | 5.4 | Yes | Yes | 18.8 | 19.8 | -1 | EC1E36485A074343B205E1AFBFA5E7CF |  | R22 | Non-TXV |  | 8.06% | 0.9194 | 15.49% | [5 empty] | Non-TXV | 8.06%
Fremont | CA | 94536-1726 |  | 2013-09-11 | 2013-09-11 09:00 | 2013-09-11 09:00 | TRANE - 2AC13B42P-1A | 85 | 0 | Yes | Yes | 21.9 | 18.4 | 3.5 | 42D082472AA04E388956C0A8DBF0ABF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-1902 |  | 2013-09-18 | 2013-09-18 14:18 | 2013-09-18 14:41 | YORK - DBYPF042N080A | 150 | 11.2 | Yes | Yes | 25 | 20.8 | 4.2 | 706A27D67356482DA31959935FC2060E |  | R22 | Non-TXV |  | 7.467% | 0.92533 | 14.35% | [5 empty] | Non-TXV | 7.467%
Bakersfield | CA | 93313-4267 |  | 2013-09-17 | 2013-09-17 15:12 | 2013-09-17 15:12 | GOODMAN - GPG13480701AC | 143 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | D533CA1C94224761B27204F34B7CB012 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2037 |  | 2013-09-18 | 2013-09-18 11:50 | 2013-09-18 12:26 | RUUD - UNK | 70 | 14 | Yes | Yes | 25.3 | 20.8 | 4.5 | 16C8BA0D44204162AAB5790E756F3E7C |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Lemoore | CA | 93245-2037 |  | 2013-09-18 | 2013-09-18 12:33 | 2013-09-18 12:57 | RHEEM - RRMAA030JK06X | 80 | 10.4 | Yes | Yes | 20.5 | 19.5 | 1 | DC5DFBB0BC424B508E83693444C1C362 |  | R22 | Non-TXV |  | 13% | 0.87 | 24.98% | [5 empty] | Non-TXV | 13%
San Jose | CA | 95128-3441 |  | 2013-10-01 | 2013-10-01 08:58 | 2013-10-01 09:40 | BDP - 561CJ048 A | 102 | 4.8 | Yes | Yes | 19.6 | 21.7 | -2.1 | F8914CF2AC994022A47A7F29E48D9763 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Fresno | CA | 93704-1708 |  | 2013-09-25 | 2013-09-25 13:42 | 2013-09-25 14:00 | DAY & NIGHT - 24/60YAC106TC | 64 | 2.4 | Yes | Yes | 22.9 | 20.2 | 2.8 | 7F034F1E7C9B4FD0A5537DAC34A884C2 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Bakersfield | CA | 93313-4287 |  | 2013-09-17 | 2013-09-17 15:46 | 2013-09-17 15:46 | GOODMAN - PGB042075-1 | 68 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | 056D2B746FE94626AB7C7775DE2F69A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-4818 |  | 2013-09-25 | 2013-09-25 11:18 | 2013-09-25 11:18 | AMANA - PGD36C0702E | 110 | 0 | Yes | Yes | 20.6 | 18.3 | 2.3 | 32EE3841238A4097A35B4DF422D559D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3656 |  | 2013-10-21 | 2013-10-21 11:17 | 2013-10-21 11:17 | LENNOX - 10GCS036X751PA | 58 | 0 | Yes | Yes | 25.1 | 21.4 | 3.7 | 7622E1F517574207AE26FB112DD4AECB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4915 |  | 2013-09-25 | 2013-09-25 13:29 | 2013-09-25 13:29 | RHEEM - RRMA-A036JK06E | 99 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 194416863701401D88C9395198EF15ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6577 |  | 2013-09-11 | 2013-09-11 14:50 | 2013-09-12 07:28 | OTHER - 113RNA060 | 85 | -8 | Yes | Yes | 19 | 20.7 | -1.7 | E6705C8955E0465EBA54D7F2431E156F |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93722-7106 |  | 2013-09-13 | 2013-09-13 12:21 | 2013-09-13 12:45 | CARRIER - 48NLX030301BE | 69 | 16.7 | Yes | Yes | 19.6 | 18.8 | 0.8 | 200EAC3E6DD046EB8EA2698A3909B5D4 |  | R22 | Non-TXV |  | 24.2% | 0.75797 | 46.51% | [5 empty] | Non-TXV | 24.2%
Bakersfield | CA | 93313-4277 |  | 2013-09-17 | 2013-09-17 16:22 | 2013-09-17 16:22 | GOODMAN - PGB042075-1 | 68 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | AE8B29DE0D6C46E79EC21E2308161F08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6724 |  | 2013-10-27 | 2013-10-27 18:48 | 2013-10-27 18:50 | WEATHER KING - 12AG60A01 | 248 | 12 | Yes | Yes | 23.2 | 20.1 | 3.1 | 691FF6BE242A4CEC882F21503F88E853 |  | R22 | TXV |  | 4.839% | 0.95161 | 9.299% | [5 empty] | TXV | 4.839%
Fresno | CA | 93702-4719 |  | 2013-09-20 | 2013-09-20 13:57 | 2013-09-20 16:20 | AMANA - PGA36B0702C | 112 | 9.6 | Yes | Yes | 21.1 | 21 | 0.1 | 8B490608ED52440A9E9F47A388D37295 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Bakersfield | CA | 93312-5998 |  | 2013-09-06 | 2013-09-06 09:59 | 2013-09-06 10:37 | YORK - H2RC036S0HG | 83 | 4.5 | Yes | Yes | 19.3 | 20.4 | -1.1 | 0267BE876E2E4159B10813CBA09445B5 |  | R22 | Non-TXV |  | 5.422% | 0.94578 | 10.42% | [5 empty] | Non-TXV | 5.422%
Bakersfield | CA | 93308-5639 |  | 2013-09-12 | 2013-09-12 19:03 | 2013-09-12 19:03 | RHEEM - N/A | 85 | -8 | Yes | Yes | 24.1 | 20.4 | 3.7 | 7DB3AE25CF9B4D85AEB64AC5C232444B | Remove refrigerant: 8 oz | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93701-1214 |  | 2013-09-11 | 2013-09-11 10:12 | 2013-09-11 10:12 | YORK - DCYZF024N045A | 58 | 4.4 | Yes | Yes | 17.2 | 20.1 | -2.9 | D9D14FEEC1FA49BC9D0AD7E4C9780D0F | Add refrigerant: 4.4 oz | R410A | Non-TXV |  | 7.586% | 0.92414 | 14.58% | [5 empty] | Non-TXV | 7.586%
Bakersfield | CA | 93313-5419 |  | 2013-10-10 | 2013-10-10 16:13 | 2013-10-10 16:13 | BRYANT - 582ANW042060AAAG | 100 | 0 | Yes | Yes | 22.1 | 21.3 | 0.9 | 470AAB0FAD8D4189BD4A1B101C9F8CDD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5266 |  | 2013-10-21 | 2013-10-21 15:00 | 2013-10-21 15:00 | YORK - H2RD048S06B | 134 | 0 | Yes | Yes | 21.3 | 21 | 0.3 | E4E8BD99F37B432F9D2A65E9D5F41085 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5834 |  | 2013-10-01 | 2013-10-01 13:30 | 2013-10-01 13:49 | TRANE - YCY036G1M0AD | 130 | 13.4 | Yes | Yes | 22.3 | 22.1 | 0.2 | F16E468645A448F889D06496A8C91B1D |  | R22 | Non-TXV |  | 10.31% | 0.89692 | 19.81% | [5 empty] | Non-TXV | 10.31%
San Jose | CA | 95123-3607 |  | 2013-09-25 | 2013-09-25 14:32 | 2013-09-25 15:08 | PAYNE - PA10JA036-A | 83 | 5.8 | Yes | Yes | 24.7 | 20.1 | 4.6 | D21E3EF10540406F8EBB5F373903A57A |  | R22 | Non-TXV |  | 6.988% | 0.93012 | 13.43% | [5 empty] | Non-TXV | 6.988%
Bakersfield | CA | 93312-8651 |  | 2013-09-21 | 2013-09-21 16:05 | 2013-09-21 16:33 | OTHER - PA13NR048-J | 85 | 19.8 | Yes | Yes | 17 | 19.9 | -2.9 | 3217CE07ECA74064B72F1A9FDF4D7AEC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 23.29% | 0.76706 | 44.77% | [5 empty] | Non-TXV | 23.29%
San Jose | CA | 95121-1648 |  | 2013-09-18 | 2013-09-18 11:49 | 2013-09-18 12:37 | PAYNE - PA10A048 | 99 | -7 | Yes | Yes | 21.9 | 21.2 | 0.7 | CDD3C9A3F7CC4D039BF5DF1E6BCCAE29 |  | R22 | Non-TXV |  | -7.071% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.071%
Clovis | CA | 93611-2071 |  | 2013-09-16 | 2013-09-16 15:34 | 2013-09-16 16:08 | ICP - PGF348080K01A1 | 214 | 6.4 | Yes | Yes | 25 | 19.9 | 5.1 | 27F39F6ED3C74D44AD22FA36CA63C861 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.747% | [5 empty] | Non-TXV | 2.991%
Milpitas | CA | 95035-2703 |  | 2013-09-26 | 2013-09-26 18:12 | 2013-09-26 18:27 | AMANA - RCB24ABA2A | 84 | 12.8 | Yes | Yes | 19 | 21.7 | -2.7 | 762D29D2B22A4A67926621F6BFAB926D |  | R22 | Non-TXV |  | 15.24% | 0.84762 | 29.28% | [5 empty] | Non-TXV | 15.24%
Bakersfield | CA | 93312-5659 |  | 2013-09-08 | 2013-09-08 20:04 | 2013-09-08 20:07 | OTHER - H2RC036S06G | 83 | 6.7 | Yes | Yes | 22.8 | 20.7 | 2.1 | 1AAA987B93FD477B8D5DDAF33C9F60CB |  | R22 | TXV |  | 8.072% | 0.91928 | 15.51% | [5 empty] | TXV | 8.072%
Bakersfield | CA | 93312-5659 |  | 2013-09-08 | 2013-09-08 20:11 | 2013-09-08 20:13 | OTHER - H2RC036S06G | 83 | 6.5 | Yes | Yes | 20.7 | 20.4 | 0.3 | 01218BBD44714876A89BAEA6AA91F76F |  | R22 | TXV |  | 7.831% | 0.92169 | 15.05% | [5 empty] | TXV | 7.831%
Bakersfield | CA | 93309-4617 |  | 2013-10-08 | 2013-10-08 14:09 | 2013-10-08 14:09 | BDP - UKN | 45 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | E9EE694245264A0DA871D24E2F21BE2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1803 |  | 2013-10-09 | 2013-10-09 11:25 | 2013-10-09 12:42 | PAYNE - 561CJ036-A | 127 | 4.9 | Yes | Yes | 20.9 | 16.8 | 4.1 | F108BA182F92415D83DA642942F9412F |  | R22 | TXV |  | 3.858% | 0.96142 | 7.415% | [5 empty] | TXV | 3.858%
Bakersfield | CA | 93313-5465 |  | 2013-09-17 | 2013-09-17 11:07 | 2013-09-17 11:24 | ICP - GPCM042K0800 | 84 | 4.5 | Yes | Yes | 21.1 | 21.3 | -0.1 | 9EA580D3B91342FD9C6D428181AD0FF5 |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Bakersfield | CA | 93309-4686 |  | 2013-10-08 | 2013-10-08 14:34 | 2013-10-08 14:34 | DAY & NIGHT - B588E16944 | 48 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | D2C891FE869F4B96A608673E86D9602C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2098 |  | 2013-09-12 | 2013-09-12 14:17 | 2013-09-12 15:37 | YORK - H1RA018S060 | 54 | 2 | Yes | Yes | 18.6 | 21.3 | -2.7 | 0E3F69F408074681998961A9CD55E68B |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Sanger | CA | 93657-8782 |  | 2013-09-17 | 2013-09-17 12:35 | 2013-09-17 13:15 | YORK - H2RD036306B | 96 | 10.6 | Yes | Yes | 19.8 | 19.9 | -0.1 | 3425A22BBD164023BD0F0A957BF3F66D |  | R22 | Non-TXV |  | 11.04% | 0.88958 | 21.22% | [5 empty] | Non-TXV | 11.04%
Bakersfield | CA | 93304-2720 |  | 2013-09-25 | 2013-09-25 12:02 | 2013-09-25 12:02 | ICP - PGC036K080B | 71 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | 6DF26E3177AF43949A2E06F79E9702F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4692 |  | 2013-10-08 | 2013-10-08 15:57 | 2013-10-08 16:15 | GOODMAN - GSC13024 | 89 | 7.9 | Yes | Yes | 21.4 | 20.4 | 1 | 04FFD5FF2C054ACA9E5640BBB2B2D44A |  | R22 | Non-TXV |  | 8.876% | 0.91124 | 17.06% | [5 empty] | Non-TXV | 8.876%
Fresno | CA | 93722-7107 |  | 2013-09-13 | 2013-09-13 13:05 | 2013-09-13 13:28 | CARRIER - UNK | 69 | 2.6 | Yes | Yes | 24.1 | 22.1 | 2 | FD28F2F2A1704644A8258997778F6471 |  | R22 | Non-TXV |  | 3.768% | 0.96232 | 7.241% | [5 empty] | Non-TXV | 3.768%
Kingsburg | CA | 93631-2429 |  | 2013-09-20 | 2013-09-20 09:58 | 2013-09-20 10:24 | ARMSTRONG - PGE10B36D075A3A | 70 | 3.1 | Yes | Yes | 23.4 | 19.5 | 3.9 | 2F7C1C8C276745A883A03686694463B8 |  | R22 | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Sanger | CA | 93657-2585 |  | 2013-09-11 | 2013-09-11 09:22 | 2013-09-11 09:47 | LENNOX - 10GCS036753PB | 58 | 2.9 | Yes | Yes | 23.9 | 19.8 | 4.1 | B0CA84ED65B3457187208B4775812F7B |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Kingsburg | CA | 93631-2450 |  | 2013-09-23 | 2013-09-23 09:41 | 2013-09-23 10:00 | CARRIER - UNK | 70 | 3.5 | Yes | Yes | 20 | 18.2 | 1.8 | C368066F9CCD4FEE848BFF7BB04A47C1 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
San Jose | CA | 95135-1406 |  | 2013-09-30 | 2013-09-30 12:32 | 2013-09-30 13:09 | CARRIER - 48GSN048090301 | 82 | 2.6 | Yes | Yes | 21.6 | 18.7 | 2.9 | 5D3CCA97B12448A997D2D2E6274E3EB5 |  | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Bakersfield | CA | 93308-2985 |  | 2013-10-13 | 2013-10-13 13:37 | 2013-10-13 13:37 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.8 | 21 | -0.2 | AFC56830782748B6B8E20C2A28A9597F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-4244 |  | 2013-09-11 | 2013-09-11 12:43 | 2013-09-11 13:03 | GOODMAN - CK601C | 115 | 4.4 | Yes | Yes | 19.3 | 18.6 | 0.7 | A09C66A8FC7A495D80DD765546A90B2A |  | R22 | Non-TXV |  | 3.826% | 0.96174 | 7.353% | [5 empty] | Non-TXV | 3.826%
Fresno | CA | 93702-4242 |  | 2013-09-11 | 2013-09-11 11:17 | 2013-09-11 12:22 | ARCOAIRE - GPEM30K060E | 51 | 4.3 | Yes | Yes | 23.4 | 20.9 | 2.5 | BAC48580AEC64F82BC0E816ACFB7368E |  | R22 | Non-TXV |  | 8.431% | 0.91569 | 16.2% | [5 empty] | Non-TXV | 8.431%
Bakersfield | CA | 93308-2701 |  | 2013-09-12 | 2013-09-12 19:17 | 2013-09-12 19:20 | GOODMAN - PGJ048075-1 | 84 | 3.3 | Yes | Yes | 20 | 19.9 | 0.1 | 61736EF5328E42CD966679705AA75499 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Fresno | CA | 93705-2840 |  | 2013-10-04 | 2013-10-04 12:31 | 2013-10-04 12:31 | CARRIER - 48SS03608P321 | 68 | 0 | Yes | Yes | 20.5 | 18.8 | 1.7 | E04E171EBDBA460C825E25296D5EA772 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3571 |  | 2013-09-11 | 2013-09-11 13:30 | 2013-09-11 14:00 | YORK - H2RC030S06G | 88 | 2.7 | Yes | Yes | 19.6 | 18.6 | 1 | 47110B49D970467FB5A5318B0655829A |  | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Bakersfield | CA | 93308-2977 |  | 2013-10-13 | 2013-10-13 14:55 | 2013-10-13 15:14 | ICP - PGC030 K060A | 63 | 4.5 | Yes | Yes | 20.5 | 20.4 | 0.1 | 14C73432DDC34B41A4D3A1ACF0AA6B39 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Fresno | CA | 93704-1709 |  | 2013-09-25 | 2013-09-25 13:09 | 2013-09-25 13:29 | DAY & NIGHT - UNK | 64 | 2.8 | Yes | Yes | 22.2 | 20.1 | 2.1 | 9B5A38A7B3634C448D180A8BABCF3CFA |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Clovis | CA | 93619-9158 |  | 2013-09-16 | 2013-09-16 14:51 | 2013-09-16 15:31 | RUUD - UKN | 99 | 4.5 | Yes | Yes | 24.7 | 20.4 | 4.4 | 1B0BE30B38554E8B8A523AE2EBB82461 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93705-1316 |  | 2013-09-19 | 2013-09-19 14:11 | 2013-09-19 14:30 | RHEEM - UNK | 70 | 4.9 | Yes | Yes | 23.6 | 20.2 | 3.4 | 184E7AECA953428AAAE18C4E92350434 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Bakersfield | CA | 93312-6421 |  | 2013-09-20 | 2013-09-20 18:23 | 2013-09-20 18:27 | RHEEM - FADC-042JAS | 90 | 3.3 | Yes | Yes | 23.5 | 21.5 | 2 | 10415579FABD42729972F53B68B3C726 |  | R22 | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Bakersfield | CA | 93312-3342 |  | 2013-09-26 | 2013-09-26 19:36 | 2013-09-26 19:36 | BDP - 561AJ030-B | 68 | 0 | Yes | Yes | 21.7 | 20.2 | 1.6 | 0B10BDDE6D8E414998422CD0205916AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7759 |  | 2013-10-09 | 2013-10-09 13:19 | 2013-10-09 20:07 | YORK - HLRA042SQ6A | 84 | 13.9 | Yes | Yes | 21.8 | 16.6 | 5.2 | AEAC2657E6C9492FB159CE79F9DD027D |  | R22 | Non-TXV |  | 16.55% | 0.83452 | 31.8% | [5 empty] | Non-TXV | 16.55%
Bakersfield | CA | 93308-7834 |  | 2013-09-10 | 2013-09-10 08:04 | 2013-09-10 08:24 | GOODMAN - PG5030050-1 | 85 | 8.2 | Yes | Yes | 14 | 16.8 | -2.8 | E8AD099AF8754D8D8B60A0DB9CDE8B68 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Fresno | CA | 93702-4212 |  | 2013-09-30 | 2013-09-30 08:40 | 2013-09-30 09:14 | YORK - 440-122B | 85 | 3.7 | Yes | Yes | 21.3 | 21 | 0.3 | 6346A0C04F36428398F600C4B3A7A982 |  | R22 | TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | TXV | 4.353%
Lemoore | CA | 93245-9755 |  | 2013-10-11 | 2013-10-11 14:14 | 2013-10-11 14:49 | RHEEM - UNK | 84 | 2.7 | Yes | Yes | 23.7 | 19.5 | 4.2 | B1C6D55353AE43708FBE2DF80F32E4DC |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Kingsburg | CA | 93631-2434 |  | 2013-09-20 | 2013-09-20 10:38 | 2013-09-20 10:59 | CARRIER - 48NLT030300 | 88 | 16.3 | Yes | Yes | 20.3 | 19.9 | 0.4 | B05F97D19ADB42C8BDEE96E68F218918 |  | R22 | Non-TXV |  | 18.52% | 0.81477 | 35.6% | [5 empty] | Non-TXV | 18.52%
Bakersfield | CA | 93308-2987 |  | 2013-10-13 | 2013-10-13 14:14 | 2013-10-13 14:14 | ICP - PGC030K060A | 63 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | 190F3F57536047B2B79A9A1CEACDB215 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5474 |  | 2013-09-13 | 2013-09-13 13:52 | 2013-09-13 14:16 | CARRIER - 38CK036310 | 78 | 5.6 | Yes | Yes | 19.7 | 19.9 | -0.2 | AA11CFD222004BE8B38BCB2B7DED7C20 |  | R22 | Non-TXV |  | 7.179% | 0.92821 | 13.8% | [5 empty] | Non-TXV | 7.179%
Clovis | CA | 93611-6227 |  | 2013-10-29 | 2013-10-29 11:04 | 2013-10-29 11:21 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 22.6 | 20.4 | 2.2 | BB6157197FA94058BF1525206668303E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93702-3006 |  | 2013-09-11 | 2013-09-11 13:41 | 2013-09-11 14:12 | OTHER - DARHF024N06A | 132 | 4 | Yes | Yes | 21.4 | 20.7 | 0.7 | 3972BE12AD8E4D7396A25CB541A20A04 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Fresno | CA | 93722-9110 |  | 2013-09-16 | 2013-09-16 11:46 | 2013-09-16 11:46 | YORK - DBYZF024N045A | 72 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 42372A23C5BA4477996CC299F45F0EA4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4004 |  | 2013-09-13 | 2013-09-13 14:32 | 2013-09-13 14:54 | YORK - D1NH036N05606C | 108 | 26.1 | Yes | Yes | 24.4 | 20.8 | 3.6 | 746352D656F540949410F5BF5390577A |  | R22 | Non-TXV |  | 24.17% | 0.75833 | 46.44% | [5 empty] | Non-TXV | 24.17%
Clovis | CA | 93611-6767 |  | 2013-09-16 | 2013-09-16 16:52 | 2013-09-16 19:39 | BRYANT - 563CNX048000AFAA | 164 | 6 | Yes | Yes | 21.3 | 21.1 | 0.2 | 19AD1C314F7642EE9D473602C9DF01C3 |  | R22 | TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | TXV | 3.659%
Bakersfield | CA | 93306-1361 |  | 2013-09-16 | 2013-09-16 08:24 | 2013-09-16 08:24 | ICP - PGAA30C1K6 | 79 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | C248C9AA7A104C77B61AF3734FA16F92 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6259 |  | 2013-09-12 | 2013-09-12 07:31 | 2013-09-12 07:48 | GIBSON - UNK | 85 | 2.7 | Yes | Yes | 17.6 | 20.6 | -3 | 22D0A9F48D254054ACCF9222E71BA87A |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93312-6259 |  | 2013-09-12 | 2013-09-12 07:48 | 2013-09-12 08:15 | GIBSON - UNK | 85 | 2.9 | Yes | Yes | 19 | 19.8 | -0.8 | 44FB49823A5A471BAEA3DD34ABA3FEC2 |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
San Jose | CA | 95135-1318 |  | 2013-09-30 | 2013-09-30 13:38 | 2013-09-30 14:34 | GE - BGTA924H1L | 42 | -4.4 | Yes | Yes | 17.3 | 19.2 | -1.9 | C14BD976FA8047C89E3984B92567A77B |  | R22 | Non-TXV |  | -10.48% | 1.1048 | 2.934% |  |  |  |  | Non-TXV |  |  | -10.48%
Sanger | CA | 93657-3565 |  | 2013-09-11 | 2013-09-11 10:18 | 2013-09-11 10:53 | LENNOX - 10ACC03023003 | 58 | 4.3 | Yes | Yes | 19.3 | 18.6 | 0.7 | 55D2111FB8F648DD85FA7C543AE97BC6 |  | R22 | Non-TXV |  | 7.414% | 0.92586 | 14.25% | [5 empty] | Non-TXV | 7.414%
Bakersfield | CA | 93308-9504 |  | 2013-09-19 | 2013-09-19 14:07 | 2013-09-19 14:25 | ICP - PGC024K060A | 58 | 5.7 | Yes | Yes | 21.7 | 21.8 | -0.1 | 787401D7067247A5A3615E7DC9CD15DA |  | R22 | Non-TXV |  | 9.828% | 0.90172 | 18.89% | [5 empty] | Non-TXV | 9.828%
Bakersfield | CA | 93312-6405 |  | 2013-09-11 | 2013-09-11 13:28 | 2013-09-11 13:58 | COMFORT AIRE - FADC-060JAS | 85 | 2.6 | Yes | Yes | 16.4 | 19.3 | -2.9 | 8C7488ED91FC4D5EA918B8F72E0505BE |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Wasco | CA | 93280-2686 |  | 2013-09-08 | 2013-09-08 19:44 | 2013-09-08 19:46 | OTHER - N/A | 85 | 3.2 | Yes | Yes | 23.2 | 21.5 | 1.7 | 057DA6993D9D4E20AD971A5695D13BA2 |  | R22 | TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | TXV | 3.765%
Fresno | CA | 93704-1761 |  | 2013-09-26 | 2013-09-26 11:23 | 2013-09-26 12:04 | RUUD - RRNLB030JKO6X | 77 | 3.5 | Yes | Yes | 22.5 | 18.2 | 4.3 | 02BBDE6461B04982B0DDCFB85D63CDF7 |  | R410A | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Bakersfield | CA | 93308-2963 |  | 2013-10-13 | 2013-10-13 12:16 | 2013-10-13 12:16 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.1 | 20.4 | -0.3 | A0B5DFFA78894E1EACC0778B4753CED9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1709 |  | 2013-09-25 | 2013-09-25 11:47 | 2013-09-25 12:27 | RUUD - RRNLB024JK06X | 78 | 4.6 | Yes | Yes | 26.1 | 22.6 | 3.5 | AA748B5AAFA1453D8CC0CB6C73905AA5 |  | R410A | Non-TXV |  | 5.897% | 0.94103 | 11.33% | [5 empty] | Non-TXV | 5.897%
Fresno | CA | 93725-1714 |  | 2013-09-12 | 2013-09-12 11:08 | 2013-09-12 11:38 | DAY & NIGHT - 585A030080YAC | 86 | 4 | Yes | Yes | 20.1 | 19.2 | 0.9 | 2AE8C8C34E8C444CA4EF691C87C94990 |  | R22 | Non-TXV |  | 4.651% | 0.95349 | 8.939% | [5 empty] | Non-TXV | 4.651%
Lamont | CA | 93241-1005 |  | 2013-09-11 | 2013-09-11 10:47 | 2013-09-11 11:11 | ICP - T4A436GKD200 | 105 | -6.2 | Yes | Yes | 21 | 18.8 | 2.2 | 038352D264AF48DE8964F37793591F85 |  | R410A | Non-TXV |  | -5.905% | 1.059 | 1.654% |  |  |  |  | Non-TXV |  |  | -5.905%
Sanger | CA | 93657-3567 |  | 2013-09-11 | 2013-09-11 10:57 | 2013-09-11 11:18 | YORK - H2RC030S06G | 88 | 2.6 | Yes | Yes | 19.8 | 19.2 | 0.6 | 614783D83D7346E58D81E68A7B6A08A4 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Fresno | CA | 93704-1708 |  | 2013-09-26 | 2013-09-26 10:49 | 2013-09-26 11:20 | OTHER - UNK | 74 | 3 | Yes | Yes | 22.9 | 19.8 | 3.1 | 70A93D8FF4E948E1BCE0503FA1C8FE17 |  | R22 | Non-TXV |  | 4.054% | 0.95946 | 7.791% | [5 empty] | Non-TXV | 4.054%
Fresno | CA | 93722-9171 |  | 2013-09-16 | 2013-09-16 17:16 | 2013-09-16 17:38 | YORK - D1NH036N05606C | 108 | 5.4 | Yes | Yes | 27.1 | 21.8 | 5.3 | 0DDA7E507DB146DEB34F9B0FDCE4C3AC |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93722-4041 |  | 2013-09-16 | 2013-09-16 16:36 | 2013-09-16 17:02 | YORK - DAYAF036N070C | 67 | 4.8 | Yes | Yes | 24.9 | 20.4 | 4.5 | 41C7A402E80349A0B8B1085DE9474C54 |  | R22 | Non-TXV |  | 7.164% | 0.92836 | 13.77% | [5 empty] | Non-TXV | 7.164%
Bakersfield | CA | 93308-2550 |  | 2013-09-13 | 2013-09-13 09:20 | 2013-09-13 09:46 | PAYNE - PY3GNAA48090NA | 100 | 7.1 | Yes | Yes | 19.4 | 19.4 | 0 | A97AA76FA5E942D2AF9F8B3F0BC76F44 |  | R22 | Non-TXV |  | 7.1% | 0.929 | 13.64% | [5 empty] | Non-TXV | 7.1%
Fresno | CA | 93704-1708 |  | 2013-10-18 | 2013-10-18 14:28 | 2013-10-18 14:48 | DAY & NIGHT - 2460YAC108T | 54 | 5.1 | Yes | Yes | 21.7 | 20.2 | 1.6 | C936482E11AC4A01A49CF4051AA5F229 |  | R22 | Non-TXV |  | 9.444% | 0.90556 | 18.15% | [5 empty] | Non-TXV | 9.444%
Fresno | CA | 93725-1143 |  | 2013-09-12 | 2013-09-12 13:48 | 2013-09-12 14:39 | DAY & NIGHT - UKN | 80 | 5.6 | Yes | Yes | 20.6 | 19.5 | 1.1 | BBAA8D84B31747A1B9F4C55D7A3E69A2 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93722-3757 |  | 2013-09-13 | 2013-09-13 09:57 | 2013-09-13 10:25 | LENNOX - 12GCS036X753PA | 110 | 3.9 | Yes | Yes | 22.4 | 18.7 | 3.7 | 2E69C768B166498398243911FD48E370 |  | R22 | Non-TXV |  | 3.545% | 0.96455 | 6.814% | [5 empty] | Non-TXV | 3.545%
Fresno | CA | 93722-7311 |  | 2013-09-16 | 2013-09-16 11:27 | 2013-09-16 11:43 | GOODMAN - GSC130301EA | 82 | 4 | Yes | Yes | 22 | 19.9 | 2.1 | EB243F15A3E644BF8CE8D006B8922801 |  | R22 | TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | TXV | 4.878%
Fresno | CA | 93722-8725 |  | 2013-09-13 | 2013-09-13 11:09 | 2013-09-13 11:38 | CARRIER - 24ABA348A300 | 127 | 13 | Yes | Yes | 20.5 | 18.8 | 1.7 | 41800E1B4F304B4E944C139361CD314E |  | R410A | Non-TXV |  | 10.24% | 0.89764 | 19.67% | [5 empty] | Non-TXV | 10.24%
Bakersfield | CA | 93309-5546 |  | 2013-09-27 | 2013-09-27 15:39 | 2013-09-27 15:39 | BDP - 585036080YACB | 61 | 0 | Yes | Yes | 22.5 | 20.9 | 1.6 | 812CA06034A948F6918E07BABE9D38A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1305 |  | 2013-10-03 | 2013-10-03 18:45 | 2013-10-03 21:25 | CARRIER - UNK | 84 | 2.6 | Yes | Yes | 18.5 | 21 | -2.5 | 491E68B530E14B68802838E0033BBF66 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Fresno | CA | 93725-1108 |  | 2013-09-12 | 2013-09-12 11:41 | 2013-09-12 12:14 | GOODMAN - PGB0481251 | 86 | 4.5 | Yes | Yes | 20 | 19.3 | 0.7 | 91C8B2E7B8D14595BCA2C3FB2E8828C3 |  | R22 | Non-TXV |  | 5.233% | 0.94767 | 10.06% | [5 empty] | Non-TXV | 5.233%
Fresno | CA | 93727-7823 |  | 2013-09-20 | 2013-09-20 10:15 | 2013-09-20 11:45 | ARCOAIRE - DRCS0361BE | 83 | 4 | Yes | Yes | 21.8 | 21.5 | 0.3 | 7A769A89C98B4342ABBB296522928B65 |  | R22 | TXV |  | 4.819% | 0.95181 | 9.262% | [5 empty] | TXV | 4.819%
Fresno | CA | 93703-1922 |  | 2013-09-19 | 2013-09-19 14:42 | 2013-09-19 21:41 | DAY & NIGHT - UKN | 80 | 4 | Yes | Yes | 21.7 | 21.5 | 0.2 | BA363A32C0EF4F5A8DD1BBA97FAABBC0 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fairfield | CA | 94533-2856 |  | 2013-10-08 | 2013-10-08 11:45 | 2013-10-08 16:22 | YORK - HIDE036S06B | 84 | 3.9 | Yes | Yes | 17.5 | 20 | -2.5 | F0284E239FE74E7288C73833685508F5 |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Wasco | CA | 93280-1122 |  | 2013-09-17 | 2013-09-17 19:00 | 2013-09-17 19:02 | OTHER - N2A336AKB200 | 84 | 3.2 | Yes | Yes | 22.5 | 20.4 | 2.1 | 87204E726EE14D4594C61986033FDDE5 |  | R22 | TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | TXV | 3.81%
Lamont | CA | 93241-2218 |  | 2013-09-11 | 2013-09-11 11:15 | 2013-09-11 11:50 | RHEEM - RRPL B042JKO8X | 112 | 4 | Yes | Yes | 22.4 | 18.8 | 3.6 | 60768E9037AC456DA22130074BE96F33 |  | R410A | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Lamont | CA | 93241-2363 |  | 2013-09-11 | 2013-09-11 13:31 | 2013-09-11 14:03 | PAYNE - PY3PNA036090NA | 167 | 5.8 | Yes | Yes | 21.4 | 19.5 | 1.9 | 8E516A4845244485BDF86504CA4C6EE9 |  | R22 | Non-TXV |  | 3.473% | 0.96527 | 6.674% | [5 empty] | Non-TXV | 3.473%
Fresno | CA | 93722-9771 |  | 2013-09-13 | 2013-09-13 09:16 | 2013-09-13 09:40 | YORK - D1NQ060N0906NXA | 95 | 3.3 | Yes | Yes | 20.6 | 18.5 | 2.1 | 8FF0F278092E44E7ABD140F081B97903 |  | R410A | Non-TXV |  | 3.474% | 0.96526 | 6.676% | [5 empty] | Non-TXV | 3.474%
Fresno | CA | 93704-1709 |  | 2013-10-18 | 2013-10-18 13:40 | 2013-10-18 13:56 | DAY & NIGHT - 2460YAC108T | 54 | 4.1 | Yes | Yes | 21.3 | 19.3 | 2 | 6F976F4A27914E918E540DBFDC89E6B4 |  | R22 | Non-TXV |  | 7.593% | 0.92407 | 14.59% | [5 empty] | Non-TXV | 7.593%
Wasco | CA | 93280-2595 |  | 2013-10-29 | 2013-10-29 19:10 | 2013-10-29 19:12 | OTHER - CCU12A30A | 90 | 5.1 | Yes | Yes | 25.1 | 19.5 | 5.6 | 8BB7DB73C3B2464AB05DECD153566C25 |  | R22 | TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | TXV | 5.667%
Wasco | CA | 93280-2555 |  | 2013-09-17 | 2013-09-17 19:07 | 2013-09-17 19:10 | HEIL - PGC036K060B | 71 | 2.5 | Yes | Yes | 22.2 | 19.9 | 2.3 | 09107A010A51491681470A9337E77FE7 |  | R22 | Non-TXV |  | 3.521% | 0.96479 | 6.767% | [5 empty] | Non-TXV | 3.521%
San Jose | CA | 95132-3025 |  | 2013-09-24 | 2013-09-24 14:36 | 2013-09-24 17:09 | BRYANT - 561CJ048-A | 106 | 3.2 | Yes | Yes | 17.2 | 18.7 | -1.5 | E82A2C6BC53942F289505CEE98047C8A |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Fresno | CA | 93702-3230 |  | 2013-09-11 | 2013-09-11 14:14 | 2013-09-11 14:14 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 826D3E003AAF4A6390E6BCBD6216E1C1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1945 |  | 2013-09-13 | 2013-09-13 10:56 | 2013-09-13 11:33 | OTHER - GPCM048K08OD | 100 | 3.9 | Yes | Yes | 20.4 | 18.4 | 2.1 | 49B0B8C1E88842B09DC28B14DC03C7E6 |  | R22 | Non-TXV |  | 3.9% | 0.961 | 7.495% | [5 empty] | Non-TXV | 3.9%
Fresno | CA | 93706-1735 |  | 2013-09-12 | 2013-09-12 10:11 | 2013-09-12 10:37 | GOODMAN - GPG10360701A | 75 | -4.4 | Yes | Yes | 20.7 | 18.7 | 2 | B4AA8CBBF0004DE28F5F0AB246953ABC |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Reedley | CA | 93654-2711 |  | 2013-10-11 | 2013-10-11 09:49 | 2013-10-11 10:11 | CARRIER - 48SX-042080321AA | 85 | -5 | Yes | Yes | 30 | 19.9 | 10.1 | A6316942AE7B4AB894DD490A1456ED01 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93704-1708 |  | 2013-09-25 | 2013-09-25 14:05 | 2013-09-25 14:30 | DAY & NIGHT - 24/60YAC108TC | 64 | 12.5 | Yes | Yes | 22.6 | 20.6 | 2 | 75D033C240C3431AA3BACC2A69F292F4 |  | R22 | Non-TXV |  | 19.53% | 0.80469 | 37.53% | [5 empty] | Non-TXV | 19.53%
Fresno | CA | 93704-1710 |  | 2013-10-18 | 2013-10-18 14:50 | 2013-10-18 19:47 | DAY & NIGHT - 3080YAC106T | 65 | 4.9 | Yes | Yes | 23.9 | 20.7 | 3.2 | D8F2402D88C649C795BCF51BB15941D0 |  | R22 | Non-TXV |  | 7.538% | 0.92462 | 14.49% | [5 empty] | Non-TXV | 7.538%
Fresno | CA | 93722-3261 |  | 2013-09-16 | 2013-09-16 12:28 | 2013-09-16 13:44 | YORK - H1RA036506A | 69 | 8.3 | Yes | Yes | 21.4 | 19.9 | 1.5 | 69C5F8EDB19348F39CEB4843223B3B36 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.03% | 0.87971 | 23.12% | [5 empty] | Non-TXV | 12.03%
Fresno | CA | 93704-1710 |  | 2013-10-18 | 2013-10-18 13:59 | 2013-10-18 13:59 | RHEEM - RRNLB030JK06X | 76 | 0 | Yes | Yes | 20.1 | 20.2 | 0 | D8F0F12942B941BDBA22ED5EDD4C4482 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3322 |  | 2013-10-22 | 2013-10-22 18:48 | 2013-10-22 18:48 | - | 85 | 0 | Yes | Yes | 35 | 23.6 | 11.4 | 2E182BA3231F42FA98EB69AC94633DB3 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1216 |  | 2013-10-18 | 2013-10-18 12:10 | 2013-10-18 13:32 | AMERICAN STANDARD - YCC042F1M0BH | 104 | 4.7 | Yes | Yes | 20.6 | 19.3 | 1.3 | 3D9B99C9DB404B719CFD70C261AA4600 |  | R22 | Non-TXV |  | 4.519% | 0.95481 | 8.685% | [5 empty] | Non-TXV | 4.519%
Pittsburg | CA | 94565-5114 |  | 2013-10-24 | 2013-10-24 12:58 | 2013-10-24 12:59 | BDP - 56900036 | 102 | 6.5 | Yes | Yes | 15.5 | 17.6 | -2.1 | C7772F41893747A4B7DA0A5C38BA9399 |  | R22 | Non-TXV |  | 6.373% | 0.93627 | 12.25% | [5 empty] | Non-TXV | 6.373%
Fresno | CA | 93703-4802 |  | 2013-10-12 | 2013-10-12 14:13 | 2013-10-12 14:48 | DAY & NIGHT - 585GJW02440ABAE | 85 | 3.2 | Yes | Yes | 22.6 | 20.1 | 2.6 | 230579992FD7437C8D7212511161172E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Clovis | CA | 93611-5330 |  | 2013-09-16 | 2013-09-16 16:09 | 2013-09-16 16:49 | OTHER - TTP036C100A3 | 132 | 4.8 | Yes | Yes | 21.1 | 20.6 | 0.5 | 697AF745DCD74AA685D8AA52342501E2 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Sanger | CA | 93657-3569 |  | 2013-09-11 | 2013-09-11 11:48 | 2013-09-11 12:11 | YORK - H2RC030S06G | 88 | 3.9 | Yes | Yes | 19.6 | 19.3 | 0.3 | B85275960E62409CA2BCB2FF85D8BDDA |  | R22 | Non-TXV |  | 4.432% | 0.95568 | 8.517% | [5 empty] | Non-TXV | 4.432%
Fresno | CA | 93722-6794 |  | 2013-09-16 | 2013-09-16 15:32 | 2013-09-16 15:56 | YORK - 02GA036N04806C | 84 | 8 | Yes | Yes | 21.8 | 19.9 | 1.9 | EDDC0C9D477846D4913E023C6DD8FB0F |  | R22 | Non-TXV |  | 9.524% | 0.90476 | 18.3% | [5 empty] | Non-TXV | 9.524%
Bakersfield | CA | 93311-2179 |  | 2013-10-02 | 2013-10-02 10:33 | 2013-10-02 10:33 | LENNOX - 13ACD-048-230-02 | 206 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | AF73AF27DC064DF28DAFC917EF2839D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3926 |  | 2013-09-20 | 2013-09-20 13:07 | 2013-09-20 13:55 | WESTINGHOUSE - UKN | 80 | 13.9 | Yes | Yes | 22.2 | 20.6 | 1.6 | 5B213AA1F7D04BE7AD67AC272465C7C7 |  | R22 | Non-TXV |  | 17.38% | 0.82625 | 33.39% | [5 empty] | Non-TXV | 17.38%
Bakersfield | CA | 93313-5469 |  | 2013-09-17 | 2013-09-17 14:26 | 2013-09-17 14:26 | NORDYNE - FS3B6-036KA | 82 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | 8AA34C06A3314A559F065EB88E90172B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1710 |  | 2013-09-25 | 2013-09-25 12:32 | 2013-09-25 13:03 | DAY & NIGHT - 30/80YAC106T | 64 | -3.8 | Yes | Yes | 25.5 | 21 | 4.5 | 4138DC50844E4ECAA5276191DEAEEF13 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Fresno | CA | 93727-6509 |  | 2013-09-13 | 2013-09-13 15:33 | 2013-09-13 15:33 | OTHER - UKN | 70 | 0 | Yes | Yes | 35 | 20.2 | 14.9 | 996EE69417BA4F0BB8A4F249F52168FE | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4895 |  | 2013-10-08 | 2013-10-08 15:27 | 2013-10-08 23:41 | GOODMAN - CKL30IL | 74 | 3.6 | Yes | Yes | 20.4 | 19.4 | 1 | 22D9A6DED10A465FABB75DB45FAB6DFD |  | R22 | Non-TXV |  | 4.865% | 0.95135 | 9.349% | [5 empty] | Non-TXV | 4.865%
Fresno | CA | 93727-4895 |  | 2013-09-24 | 2013-09-24 11:23 | 2013-09-24 11:41 | GOODMAN - CKL301L | 74 | 4.1 | Yes | Yes | 22.1 | 20.4 | 1.7 | 9AE16281451C4F70A4DA802D9DF242E0 |  | R22 | TXV |  | 5.541% | 0.94459 | 10.65% | [5 empty] | TXV | 5.541%
Bakersfield | CA | 93304-2821 |  | 2013-09-25 | 2013-09-25 14:15 | 2013-09-25 14:47 | YORK - D1NP030N05606A | 73 | 7.2 | Yes | Yes | 22.1 | 21.5 | 0.6 | D8AF78625E0B48829F9A9AACF98348B4 |  | R22 | Non-TXV |  | 9.863% | 0.90137 | 18.95% | [5 empty] | Non-TXV | 9.863%
Bakersfield | CA | 93311-9131 |  | 2013-10-02 | 2013-10-02 16:29 | 2013-10-02 16:29 | CARRIER - 38BRC048370 | 112 | 0 | Yes | Yes | 22.2 | 20.9 | 1.3 | 87C3CA2164BF4CCC82D2FB24A482A6E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4895 |  | 2013-09-24 | 2013-09-24 11:43 | 2013-09-24 12:13 | GOODMAN - CKL301L | 74 | 4.3 | Yes | Yes | 22.3 | 20.7 | 1.6 | EF8BC02ACB3F4E54B0DE88622CECDF74 |  | R22 | Non-TXV |  | 5.811% | 0.94189 | 11.17% | [5 empty] | Non-TXV | 5.811%
Fresno | CA | 93727-4895 |  | 2013-10-03 | 2013-10-03 11:49 | 2013-10-03 12:17 | GOODMAN - CKL24L1 | 76 | 3.6 | Yes | Yes | 23.2 | 20.2 | 3.1 | 230D090A18E94E12A092A5EA41701B2E |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Fresno | CA | 93727-4895 |  | 2013-09-24 | 2013-09-24 08:49 | 2013-09-24 09:08 | GOODMAN - UNK | 70 | -5.8 | Yes | Yes | 22 | 19.9 | 2.1 | F5F9AF2574C6492FBEDFD84B2BCDB212 |  | R22 | Non-TXV |  | -8.286% | 1.0829 | 2.32% |  |  |  |  | Non-TXV |  |  | -8.286%
Lemoore | CA | 93245-1909 |  | 2013-09-18 | 2013-09-18 10:58 | 2013-09-18 11:22 | OTHER - PGC036K060B | 71 | 3.2 | Yes | Yes | 20.9 | 19.5 | 1.4 | F19DE92401F04601ABCD3E041F42D3FE |  | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
Bakersfield | CA | 93312-6728 |  | 2013-09-24 | 2013-09-24 13:57 | 2013-09-24 14:15 | RHEEM - 12AJB42A01 | 115 | 11 | Yes | Yes | 20.4 | 20.5 | -0.1 | 5094A976C8854D46A14A0088264AED3E |  | R22 | Non-TXV |  | 9.565% | 0.90435 | 18.38% | [5 empty] | Non-TXV | 9.565%
Fresno | CA | 93725-0928 |  | 2013-10-02 | 2013-10-02 12:48 | 2013-10-02 13:11 | YORK - 24ABA336A310 | 84 | 4.5 | Yes | Yes | 20.5 | 20.6 | -0.1 | B3EE97010E3A412A93F854BA3371BD07 |  | R410A | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Fresno | CA | 93727-3429 |  | 2013-09-13 | 2013-09-13 13:51 | 2013-09-13 14:24 | HEIL - PGAA42C1K3 | 82 | 4.2 | Yes | Yes | 21.8 | 20.1 | 1.7 | 1805CABE010C47E6863F68460643355C |  | R22 | Non-TXV |  | 5.122% | 0.94878 | 9.843% | [5 empty] | Non-TXV | 5.122%
Fresno | CA | 93727-4895 |  | 2013-10-03 | 2013-10-03 11:31 | 2013-10-03 11:48 | GOODMAN - CKL301L | 52 | 3.6 | Yes | Yes | 20.5 | 19.9 | 0.6 | 3CEA2D1A02BD408CA3665716A7850ECD |  | R22 | TXV |  | 6.923% | 0.93077 | 13.3% | [5 empty] | TXV | 6.923%
Parlier | CA | 93648-9633 |  | 2013-11-01 | 2013-11-01 12:04 | 2013-11-01 12:23 | RUUD - UAMA024JAZ | 85 | -5 | Yes | Yes | 21.9 | 19.1 | 2.9 | 649510CE914C4BE9821CA196776CF317 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Arvin | CA | 93203-1516 |  | 2013-10-02 | 2013-10-02 07:44 | 2013-10-02 08:03 | YORK - D1NH0448N06506C | 85 | 10.3 | Yes | Yes | 19.5 | 16.8 | 2.8 | 3E8EA30ACF2E48AF83EF1D2F13613142 |  | R22 | Non-TXV |  | 12.12% | 0.87882 | 23.29% | [5 empty] | Non-TXV | 12.12%
Fresno | CA | 93727-4891 |  | 2013-09-24 | 2013-09-24 10:00 | 2013-09-24 10:00 | GOODMAN - UNK | 74 | 0 | Yes | Yes | 20.9 | 18.7 | 2.2 | FC993B8E71DB4FA493CB0C3EE5427925 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4891 |  | 2013-09-25 | 2013-09-25 11:36 | 2013-09-25 11:57 | GOODMAN - CKL241L | 85 | 3.3 | Yes | Yes | 23.5 | 20.4 | 3.1 | 696D2822FFE54E91822DE319B1DD7286 |  | R22 | TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | TXV | 3.882%
Fresno | CA | 93727-4891 |  | 2013-09-24 | 2013-09-24 11:36 | 2013-09-24 11:54 | GOODMAN - CKL301L | 74 | 2.6 | Yes | Yes | 20.2 | 19.3 | 0.9 | 0E25C6967EF74D6FB10B66B57D46FD52 |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Parlier | CA | 93648-2848 |  | 2013-09-11 | 2013-09-11 17:26 | 2013-09-11 18:04 | LENNOX - 10GCS030755PA | 51 | 3.4 | Yes | Yes | 24.1 | 20.4 | 3.7 | FF2B0CC2738D4C8EAA0E3A69561BDFAA |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93727-4892 |  | 2013-09-24 | 2013-09-24 10:45 | 2013-09-24 11:21 | GOODMAN - CKL301L | 74 | 4.5 | Yes | Yes | 18.1 | 20.1 | -2 | 7C7E9627C124431485271B7147CD9A60 |  | R22 | TXV |  | 6.081% | 0.93919 | 11.69% | [5 empty] | TXV | 6.081%
Fresno | CA | 93727-4892 |  | 2013-09-25 | 2013-09-25 10:44 | 2013-09-25 11:02 | GOODMAN - UNK | 74 | -4.4 | Yes | Yes | 22.7 | 19.1 | 3.6 | 45BB82F40FFA494EBF2B26A406DBF65A |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Fresno | CA | 93727-4891 |  | 2013-09-24 | 2013-09-24 11:04 | 2013-09-24 11:32 | GOODMAN - CKL0301L | 74 | -4.4 | Yes | Yes | 21.3 | 18.7 | 2.6 | E13BD8393A114284995E6B31B5C0E907 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Fresno | CA | 93727-4895 |  | 2013-10-03 | 2013-10-03 14:19 | 2013-10-03 15:00 | GOODMAN - CKL30-1L | 74 | 2.2 | Yes | Yes | 23.1 | 20.3 | 2.8 | 0DC3CD1EF37F48A38BA5FA9F8A89719A |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Clovis | CA | 93612-2372 |  | 2013-09-17 | 2013-09-17 16:14 | 2013-09-17 19:59 | DAY & NIGHT - UKN | 80 | 4 | Yes | Yes | 24.1 | 20.5 | 3.6 | 3E61B5C4783B49AF8185794D411E0DF8 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93727-0000 |  | 2013-09-24 | 2013-09-24 16:48 | 2013-09-24 17:06 | GOODMAN - CKL241L | 74 | 3.7 | Yes | Yes | 20.7 | 20.4 | 0.3 | 0D59025B53DC4F0E84651793F40BC2D3 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93727-4895 |  | 2013-09-24 | 2013-09-24 12:15 | 2013-09-24 12:43 | GOODMAN - CKL24H | 74 | 3.8 | Yes | Yes | 23.9 | 21.7 | 2.2 | 2973B104037A47CEA0364FF051556870 |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Bakersfield | CA | 93312-3352 |  | 2013-09-26 | 2013-09-26 14:26 | 2013-09-26 14:47 | YORK - H2RC042S06HG | 109 | 7.1 | Yes | Yes | 22 | 21 | 1 | C21599A4217A4E3B8F1AA80E745FCD5B |  | R22 | Non-TXV |  | 6.514% | 0.93486 | 12.52% | [5 empty] | Non-TXV | 6.514%
Buttonwillow | CA | 93206-9759 |  | 2013-09-16 | 2013-09-16 18:32 | 2013-09-16 18:34 | RHEEM - N/A | 85 | 3.4 | Yes | Yes | 25.1 | 19.3 | 5.8 | 8CE1549AABAF428DB3AB7EA8981D3325 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93727-4892 |  | 2013-09-24 | 2013-09-24 13:28 | 2013-09-24 16:46 | GOODMAN - CKL301L | 74 | 4.5 | Yes | Yes | 22.4 | 21.2 | 1.3 | 74AAFA61A48D4F6D984E3BDE299E5050 |  | R22 | TXV |  | 6.081% | 0.93919 | 11.69% | [5 empty] | TXV | 6.081%
Bakersfield | CA | 93305-1641 |  | 2013-10-15 | 2013-10-15 13:29 | 2013-10-15 13:46 | LENNOX - GCS2R0RX-511-100-2P | 115 | 8.5 | Yes | Yes | 20.4 | 20.4 | 0 | FEB1A476C29D4E9E95DB55929F9B10A2 |  | R22 | Non-TXV |  | 7.391% | 0.92609 | 14.2% | [5 empty] | Non-TXV | 7.391%
Fresno | CA | 93727-4891 |  | 2013-10-03 | 2013-10-03 13:37 | 2013-10-03 22:04 | GOODMAN - CKL301L | 74 | 3.5 | Yes | Yes | 20.7 | 18.2 | 2.5 | 84D945468532456396D0FD6628BAB3FD |  | R22 | Non-TXV |  | 4.73% | 0.9527 | 9.09% | [5 empty] | Non-TXV | 4.73%
San Jose | CA | 95111-2585 |  | 2013-09-17 | 2013-09-17 08:34 | 2013-09-17 09:25 | TRANE - TTY024B100A0 | 107 | 13.3 | Yes | Yes | 17.6 | 16.2 | 1.5 | FC62EC8D89534319B4BFB6BC4E8A3997 |  | R22 | TXV |  | 12.43% | 0.8757 | 23.89% | [5 empty] | TXV | 12.43%
Bakersfield | CA | 93312-6829 |  | 2013-10-16 | 2013-10-16 14:05 | 2013-10-16 14:05 | CARRIER - UKN | 90 | 0 | Yes | Yes | 26.5 | 22.4 | 4.1 | 91723CEB86564B0D8124DDAAD045560B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6829 |  | 2013-10-16 | 2013-10-16 14:19 | 2013-10-16 14:19 | - | 85 | 0 | Yes | Yes | 21.8 | 22.7 | -0.9 | 669EF0A5A6DE4AC882EA218BD2BDA78A |  |  |  |  | 0% | 1 | 0%
San Jose | CA | 95132-1237 |  | 2013-09-25 | 2013-09-25 12:46 | 2013-09-25 14:03 | CARRIER - UNK | 86 | 3.9 | Yes | Yes | 20.5 | 22 | -1.5 | 67C4DAC5149740CAAD3AA8C89DEC5092 |  | R22 | Non-TXV |  | 4.535% | 0.95465 | 8.715% | [5 empty] | Non-TXV | 4.535%
Arvin | CA | 93203-2430 |  | 2013-10-02 | 2013-10-02 08:29 | 2013-10-02 08:45 | PAYNE - UNK | 85 | 3.7 | Yes | Yes | 18.5 | 18.5 | 0 | 6030A609C9134F2F9770CACBB4676553 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Fresno | CA | 93727-4895 |  | 2013-10-03 | 2013-10-03 12:33 | 2013-10-03 13:00 | GOODMAN - CKL24-1L | 76 | -4.5 | Yes | Yes | 23.5 | 19.5 | 4 | D372FF30750F45A494B7A3B850410B39 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Bakersfield | CA | 93311-1293 |  | 2013-10-02 | 2013-10-02 09:50 | 2013-10-02 09:50 | ICP - PGAD47D1K6 | 215 | 0 | Yes | Yes | 22.1 | 22.1 | 0 | E590AC450CCD4F258A78870C714608C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4895 |  | 2013-10-03 | 2013-10-03 12:19 | 2013-10-03 12:55 | GOODMAN - CKL301L | 74 | 3.8 | Yes | Yes | 23.5 | 20.2 | 3.4 | 2737B386FE1C4AF3A3E9431D9AAF8274 |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Fresno | CA | 93727-3689 |  | 2013-09-13 | 2013-09-13 12:15 | 2013-09-13 13:50 | LENNOX - 12GCS042X755PB | 85 | 4.2 | Yes | Yes | 21.2 | 19.7 | 1.5 | C97291EB6AFD4958A12333480458186C |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Fresno | CA | 93727-4891 |  | 2013-09-24 | 2013-09-24 10:38 | 2013-09-24 10:56 | GOODMAN - UNK | 74 | -4.4 | Yes | Yes | 20.4 | 18.8 | 1.6 | 1C71EF7BBA15476686945377EF629AF6 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Fresno | CA | 93727-3340 |  | 2013-09-19 | 2013-09-19 12:53 | 2013-09-19 12:53 | CARRIER - UKN | 80 | 0 | Yes | Yes | 20.6 | 21.4 | -0.8 | A9FDA9B56B6744C6B0C18071D224E4F2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3267 |  | 2013-10-03 | 2013-10-03 12:12 | 2013-10-03 12:31 | LENNOX - 12GC030753PB | 85 | 10.4 | Yes | Yes | 24.5 | 19.8 | 4.7 | 30DAB77C285447F2B4576BD2341C3020 |  | R22 | Non-TXV |  | 12.24% | 0.87765 | 23.51% | [5 empty] | Non-TXV | 12.24%
Bakersfield | CA | 93312-5605 |  | 2013-09-26 | 2013-09-26 12:52 | 2013-09-26 12:52 | ICP - CA9048VK | 164 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 0213A88AF30048A9AC14F8BC4C89D351 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4892 |  | 2013-10-03 | 2013-10-03 12:57 | 2013-10-03 13:13 | GOODMAN - CKL301L | 74 | 3.3 | Yes | Yes | 22.8 | 19.9 | 2.9 | 2D08C28E74D642B993DC2C94FC9009A7 |  | R22 | TXV |  | 4.459% | 0.95541 | 8.57% | [5 empty] | TXV | 4.459%
Fresno | CA | 93727-4892 |  | 2013-09-25 | 2013-09-25 11:59 | 2013-09-25 13:06 | GOODMAN - CKL301L | 74 | 3.2 | Yes | Yes | 20.1 | 20.2 | 0 | 50BDA91366224048B6816F9A42004F5E |  | R22 | TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | TXV | 4.324%
Bakersfield | CA | 93309-6061 |  | 2013-10-15 | 2013-10-15 15:47 | 2013-10-15 15:47 | PAYNE - PY1PNB024040AAAA | 56 | 0 | Yes | Yes | 20.7 | 20.7 | 0 | 2802C6DBE1EB4AB4A2747F9CFB5ECCC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5989 |  | 2013-09-26 | 2013-09-26 09:19 | 2013-09-26 09:19 | YORK - H3RC060S06HA | 147 | 0 | Yes | Yes | 17.3 | 19.3 | -2 | 45AC1E94EF464464BF76FC5C66E7CB2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3657 |  | 2013-10-01 | 2013-10-01 10:29 | 2013-10-01 10:53 | COLEMAN - DRCS048B | 106 | 3.9 | Yes | Yes | 21.1 | 18.8 | 2.3 | 7A3FD9512B4C4BFB887E28B1AC51B24B |  | R22 | Non-TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | Non-TXV | 3.679%
Fresno | CA | 93726-5625 |  | 2013-09-27 | 2013-09-27 09:58 | 2013-09-27 09:58 | RHEEM - RRNLB042JK08X | 112 | 0 | Yes | Yes | 20 | 18.7 | 1.3 | 852C8937DA7A4B6480A67B7F676959C9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5462 |  | 2013-09-17 | 2013-09-17 11:57 | 2013-09-17 11:57 | ICP - PGC042080E | 84 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | F7ABB1DBBEBA4C92B96C015C1A612873 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4895 |  | 2013-10-03 | 2013-10-03 13:02 | 2013-10-03 13:27 | GOODMAN - CKL30-1L | 74 | -4.4 | Yes | Yes | 21.5 | 19.1 | 2.4 | 4DA34ABBC95E466593B081DFEEC79700 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Fresno | CA | 93705-4955 |  | 2013-09-16 | 2013-09-16 14:20 | 2013-09-16 14:56 | YORK - D2NP036N05606A | 108 | 4.3 | Yes | Yes | 25 | 21.3 | 3.7 | 1A8BF859A34B4617A8A6FEE717D9C09A |  | R22 | Non-TXV |  | 3.981% | 0.96019 | 7.652% | [5 empty] | Non-TXV | 3.981%
Fresno | CA | 93727-4895 |  | 2013-09-24 | 2013-09-24 17:08 | 2013-09-24 17:08 | GOODMAN - CKL301L | 74 | 4.7 | Yes | Yes | 17.8 | 20.5 | -2.7 | 9DE383D369314B89911B415CAD565AA8 | Add refrigerant: 4.7 oz | R22 | Non-TXV |  | 6.351% | 0.93649 | 12.21% | [5 empty] | Non-TXV | 6.351%
Fresno | CA | 93727-4895 |  | 2013-09-24 | 2013-09-24 12:37 | 2013-09-24 13:20 | GOODMAN - CKL301L | 74 | 3.2 | Yes | Yes | 21.6 | 19.5 | 2.1 | F6B523A861AC4A6ABE7E1883DBA10E3E |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
Lemoore | CA | 93245-2510 |  | 2013-10-11 | 2013-10-11 13:29 | 2013-10-11 13:47 | GOODMAN - GPG134207M41AC | 105 | 3.3 | Yes | Yes | 22 | 18.5 | 3.6 | 990EC71013C4462CB8BC2AC8ADCADE17 |  | R410A | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Fresno | CA | 93727-3640 |  | 2013-09-13 | 2013-09-13 15:36 | 2013-09-14 11:39 | LENNOX - 10GCS042X753PA | 73 | 7.6 | Yes | Yes | 22.5 | 20.6 | 1.9 | 399C437CE0A84B98A6993B990B02BD88 |  | R22 | Non-TXV |  | 10.41% | 0.89589 | 20.01% | [5 empty] | Non-TXV | 10.41%
Fresno | CA | 93705-1107 |  | 2013-10-09 | 2013-10-09 08:48 | 2013-10-09 09:16 | PAYNE - PY3GNAA30060NA | 99 | -5.8 | Yes | Yes | 22.3 | 18.7 | 3.6 | 0197A5BA351C49E4B213D7CB8DC32970 |  | R410A | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Fresno | CA | 93727-2435 |  | 2013-09-13 | 2013-09-13 14:27 | 2013-09-13 15:32 | HEIL - PGC030K060 | 52 | 3.5 | Yes | Yes | 20.3 | 21.3 | -1 | 9A20A9E9F6BD410B96EA47E0AD4C914A |  | R22 | Non-TXV |  | 6.731% | 0.93269 | 12.94% | [5 empty] | Non-TXV | 6.731%
Fresno | CA | 93727-4891 |  | 2013-09-24 | 2013-09-24 11:58 | 2013-09-24 12:33 | GOODMAN - CKL301L | 74 | 7 | Yes | Yes | 19.8 | 18.2 | 1.6 | CAB68D03ED0E46D2B59DED6408D58862 |  | R22 | Non-TXV |  | 9.459% | 0.90541 | 18.18% | [5 empty] | Non-TXV | 9.459%
Reedley | CA | 93654-3656 |  | 2013-10-11 | 2013-10-11 09:15 | 2013-10-11 09:15 | OTHER - PGAD36D1K7 | 104 | 0 | Yes | Yes | 30 | 17.7 | 12.3 | 81E6FA6C981A49C5B6CECE3B53FA7417 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3563 |  | 2013-10-25 | 2013-10-25 13:05 | 2013-10-25 13:06 | OTHER - NA | 72 | 2.2 | Yes | Yes | 15.9 | 17 | -1.1 | 49C37AF8BD184FBABC30421BFE6EE2C3 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Bakersfield | CA | 93312-4300 |  | 2013-09-24 | 2013-09-24 16:18 | 2013-09-24 16:18 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 20.8 | 21.2 | -0.4 | C66A749FEF8D4826B777BC48AC62D0AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4895 |  | 2013-09-24 | 2013-09-24 09:18 | 2013-09-24 09:36 | GOODMAN - UNK | 70 | 6.4 | Yes | Yes | 20.3 | 19.3 | 1 | 14612A693BDF4575801CE16AEC4B6BD7 |  | R22 | Non-TXV |  | 9.143% | 0.90857 | 17.57% | [5 empty] | Non-TXV | 9.143%
Kingsburg | CA | 93631-9617 |  | 2013-09-20 | 2013-09-20 09:08 | 2013-09-20 09:47 | CARRIER - UNK | 70 | 3.4 | Yes | Yes | 20.6 | 18.7 | 1.9 | 3AD287624D43405781D12229B5646392 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Sunnyvale | CA | 94087-4251 |  | 2013-09-27 | 2013-09-27 10:47 | 2013-09-27 10:47 | CARRIER - 24APA548A300 | 187 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 2E93D151B1724F6BA9BC75EA217B1C7C | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1797 |  | 2013-10-24 | 2013-10-24 17:53 | 2013-10-24 17:53 | GOODMAN - GPG10300701A | 50 | 0 | Yes | Yes | 19.5 | 20.7 | -1.2 | 63B56AAD29AD4B3CBDFC41AB9263F4B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4892 |  | 2013-09-24 | 2013-09-24 13:01 | 2013-09-24 13:26 | GOODMAN - CKL301L | 74 | 3.4 | Yes | Yes | 24.7 | 20.9 | 3.8 | 2F9496F6CFB84F2E8A463CDCAA502266 |  | R22 | Non-TXV |  | 4.595% | 0.95405 | 8.83% | [5 empty] | Non-TXV | 4.595%
Reedley | CA | 93654-3660 |  | 2013-10-03 | 2013-10-03 11:03 | 2013-10-03 11:33 | COLEMAN - UNK | 122 | 12.7 | Yes | Yes | 20 | 19.5 | 0.5 | F99A1FA5DD5E4CC483CD2D46AB9EB93B |  | R22 | Non-TXV |  | 10.41% | 0.8959 | 20.01% | [5 empty] | Non-TXV | 10.41%
Bakersfield | CA | 93308-1360 |  | 2013-09-18 | 2013-09-18 13:40 | 2013-09-18 13:59 | ICP - PGME42G0907 | 180 | 12.6 | Yes | Yes | 22.5 | 21.4 | 1.1 | 37393D80B05545D9995C40271E5BAF37 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93727-4892 |  | 2013-10-03 | 2013-10-03 13:15 | 2013-10-03 13:35 | GOODMAN - CKL241L | 74 | 3.2 | Yes | Yes | 23 | 19.1 | 4 | 7F48439AD1FE40328D8C2F6F6537964C |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
Bakersfield | CA | 93312-6851 |  | 2013-10-16 | 2013-10-16 10:00 | 2013-10-16 10:00 | LENNOX - 13ACD04823002 | 220 | 0 | Yes | Yes | 21 | 20.9 | 0.1 | 3D4BB1CE70014B988C4DA02884033AB7 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4892 |  | 2013-10-03 | 2013-10-03 13:28 | 2013-10-03 13:53 | GOODMAN - CKL24-1L | 76 | 2.3 | Yes | Yes | 21 | 20.9 | 0.1 | 4F61FA42DFFC408388AE650B1BF43032 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Arvin | CA | 93203-2735 |  | 2013-10-01 | 2013-10-01 08:03 | 2013-10-01 08:21 | ICP - PGF030K060A | 52 | 3.5 | Yes | Yes | 19.5 | 20.7 | -1.2 | 20CF6D0E2EDE4545B9097E09698C2D37 |  | R22 | Non-TXV |  | 6.731% | 0.93269 | 12.94% | [5 empty] | Non-TXV | 6.731%
Sanger | CA | 93657-9739 |  | 2013-09-17 | 2013-09-17 11:46 | 2013-09-17 12:10 | COLEMAN - BRCQ048B | 82 | 5.4 | Yes | Yes | 19.1 | 20.4 | -1.3 | 0BA195C281474B0B889D358CC8B82F7A |  | R22 | Non-TXV |  | 6.585% | 0.93415 | 12.66% | [5 empty] | Non-TXV | 6.585%
Reedley | CA | 93654-3661 |  | 2013-10-03 | 2013-10-03 10:21 | 2013-10-03 10:56 | COLEMAN - ERCS0481CA | 227 | 6.8 | Yes | Yes | 22.4 | 19.5 | 2.9 | C13A2BB0BA854EE596D894A63C7BF967 |  | R22 | Non-TXV |  | 2.996% | 0.97004 | 5.757% | [5 empty] | Non-TXV | 2.996%
Arvin | CA | 93203-0000 |  | 2013-10-02 | 2013-10-02 08:48 | 2013-10-02 09:05 | OTHER - GSC130481AC | 85 | -7 | Yes | Yes | 15.8 | 18.6 | -2.8 | A5DF427D48C146B7B7C41D693ED96AF7 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Bakersfield | CA | 93308-7148 |  | 2013-10-08 | 2013-10-08 13:41 | 2013-10-08 13:41 | YORK - AC036X1222A | 83 | 0 | Yes | Yes | 21.1 | 19.3 | 1.8 | 1BE2E0ECE5314F98AB45739BF4819F8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3661 |  | 2013-10-03 | 2013-10-03 09:41 | 2013-10-03 10:17 | COLEMAN - UNK | 90 | -8.5 | Yes | Yes | 24.2 | 20 | 4.3 | CF9206E5199146858B0A9D83A4A86934 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Bakersfield | CA | 93308-4041 |  | 2013-10-08 | 2013-10-08 17:21 | 2013-10-08 17:21 | GOODMAN - PGJ0360751 | 81 | 0 | Yes | Yes | 22.1 | 19.3 | 2.8 | 8AB1155101284927AFAC72A4903FCB71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2965 |  | 2013-10-13 | 2013-10-13 11:56 | 2013-10-13 11:56 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.4 | 21 | -0.6 | C25B72CF8CBB4F478673974AFDA38563 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4895 |  | 2013-11-09 | 2013-11-09 14:18 | 2013-11-09 14:54 | GOODMAN - CKL301L | 74 | 4.5 | Yes | Yes | 20.5 | 18.2 | 2.3 | EB2716215EB24B8180F166CE9E7F5111 |  | R22 | Non-TXV |  | 6.081% | 0.93919 | 11.69% | [5 empty] | Non-TXV | 6.081%
Bakersfield | CA | 93308-2968 |  | 2013-10-13 | 2013-10-13 11:30 | 2013-10-13 11:30 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 19.5 | 20.7 | -1.2 | 2CC9E057077645438DC40BDD629EB63E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-1122 |  | 2013-09-18 | 2013-09-18 14:07 | 2013-09-18 14:42 | DAY & NIGHT - UKN | 80 | 4 | Yes | Yes | 21 | 20.8 | 0.2 | 3BE654121C58431FBBB3B9E0A5837A2E |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Clovis | CA | 93612-4494 |  | 2013-09-16 | 2013-09-16 13:47 | 2013-09-16 14:50 | CARRIER - 582ANW036090NBAF | 68 | 4.8 | Yes | Yes | 21.4 | 20.6 | 0.8 | 057E36B1A2984FE493A134C64A7315F4 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Reedley | CA | 93654-3657 |  | 2013-10-01 | 2013-10-01 09:34 | 2013-10-01 10:05 | COLEMAN - DRCS0481BE | 119 | 3.8 | Yes | Yes | 20.2 | 17.7 | 2.5 | 965B7ECE4B104C179B1012499A44D557 |  | R22 | Non-TXV |  | 3.193% | 0.96807 | 6.137% | [5 empty] | Non-TXV | 3.193%
Bakersfield | CA | 93308-9501 |  | 2013-09-19 | 2013-09-19 12:03 | 2013-09-19 12:03 | ICP - PGC024K040A | 58 | 0 | Yes | Yes | 22.1 | 22.1 | 0 | C5255FD891134774B52D7446B3DDE4AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5355 |  | 2013-09-27 | 2013-09-27 13:42 | 2013-09-27 13:42 | ICP - PGAD60E1K7 | 214 | 0 | Yes | Yes | 21.8 | 21.2 | 0.6 | 834C907829E748BC97AF7A50CD8FF14E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5526 |  | 2013-09-19 | 2013-09-19 12:08 | 2013-09-19 12:51 | LENNOX - 10GCS042X1002PA | 80 | 3.4 | Yes | Yes | 20.8 | 21 | -0.2 | 791A616DA3AF4D4787AF25EA8ED15494 |  | R22 | Non-TXV |  | 4.25% | 0.9575 | 8.168% | [5 empty] | Non-TXV | 4.25%
Arvin | CA | 93203-0000 |  | 2013-10-02 | 2013-10-02 08:06 | 2013-10-02 08:26 | GOODMAN - GPG1330045AA | 85 | 8.1 | Yes | Yes | 20.5 | 19.1 | 1.4 | 126AE8E29DD84B36B2441C36C2C639AF |  | R22 | Non-TXV |  | 9.529% | 0.90471 | 18.31% | [5 empty] | Non-TXV | 9.529%
Wasco | CA | 93280-1632 |  | 2013-10-31 | 2013-10-31 17:32 | 2013-10-31 17:32 | OTHER - GR8D-036K072C | 61 | 0 | Yes | Yes | 15.7 | 19.9 | -4.2 | BCBE1FD6C3FF437DB8A3211F937ADDA6 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-3799 |  | 2013-10-24 | 2013-10-24 17:16 | 2013-10-24 18:29 | BRYANT - 563CN030C | 102 | 3.4 | Yes | Yes | 21.5 | 20.3 | 1.2 | BC61B268F29243E89DE9059404E0D06B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93308-2963 |  | 2013-10-13 | 2013-10-13 12:34 | 2013-10-13 12:34 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.3 | 21 | -0.7 | 287FD00C000D4D9F9EAFF24D4ED2FE33 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2962 |  | 2013-10-13 | 2013-10-13 13:05 | 2013-10-13 13:05 | TRANE - 4YCC03024B1064AA | 58 | 0 | Yes | Yes | 20.3 | 20.7 | -0.4 | EB67EE659DBD40C0A869A301E2F66207 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1310 |  | 2013-09-23 | 2013-09-23 14:00 | 2013-09-23 14:33 | CARRIER - 38CKC024340 | 57 | 8.5 | Yes | Yes | 24.5 | 21.5 | 3 | 6186551DB5B2480189346B4E16AE1A48 |  | R22 | Non-TXV |  | 14.91% | 0.85088 | 28.66% | [5 empty] | Non-TXV | 14.91%
Bakersfield | CA | 93308-2963 |  | 2013-10-13 | 2013-10-13 12:50 | 2013-10-13 12:50 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 19.6 | 21 | -1.4 | D76FC76F0A7D4A97985A4F7B3932504D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-0000 |  | 2013-09-25 | 2013-09-25 10:17 | 2013-09-25 10:17 | NORDYNE - FS5BD048 | 147 | 0 | Yes | Yes | 23.2 | 20.2 | 3.1 | F3BC9B6675794310B1BBF2DE79326CEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6228 |  | 2013-09-19 | 2013-09-19 10:38 | 2013-09-19 12:05 | DAY & NIGHT - UKN | 80 | 3.7 | Yes | Yes | 22.2 | 21 | 1.2 | 3C85676732124CFC98BA4A66501000FF |  | R22 | TXV |  | 4.625% | 0.95375 | 8.888% | [5 empty] | TXV | 4.625%
Lemoore | CA | 93245-3315 |  | 2013-10-11 | 2013-10-11 10:57 | 2013-10-11 11:15 | TEMPSTAR - CA5030VKB1 | 79 | 2.5 | Yes | Yes | 20.2 | 18.7 | 1.5 | A6CB3F2C48E14094AC17159A8EDD5AE2 |  | R22 | Non-TXV |  | 3.165% | 0.96835 | 6.082% | [5 empty] | Non-TXV | 3.165%
Bakersfield | CA | 93308-2978 |  | 2013-10-13 | 2013-10-13 15:30 | 2013-10-13 15:30 | OTHER - UKN | 60 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 516627C8427C45BF93AA89F7E0FCCC8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0428 |  | 2013-09-19 | 2013-09-19 13:15 | 2013-09-19 13:39 | OTHER - DDYZF060N110A | 82 | 10.7 | Yes | Yes | 25.1 | 19.8 | 5.3 | 884D1C408926496B8AD3219B876C5197 |  | R410A | Non-TXV |  | 13.05% | 0.86951 | 25.08% | [5 empty] | Non-TXV | 13.05%
Bakersfield | CA | 93309-6102 |  | 2013-09-27 | 2013-09-27 09:18 | 2013-09-27 09:18 | OTHER - NRGR420D0B4 | 81 | 0 | Yes | Yes | 22.8 | 20 | 2.9 | F9FF076C47154610A5AFEF50AAB633E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2811 |  | 2013-10-01 | 2013-10-01 08:27 | 2013-10-01 08:45 | CARRIER - 48GS-04206301 | 85 | -7 | Yes | Yes | 17.6 | 20.4 | -2.8 | C8D56D104EE44F89A91173B1385341BC |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Bakersfield | CA | 93309-4678 |  | 2013-10-08 | 2013-10-08 19:13 | 2013-10-08 19:13 | BDP - 567C018RC0 | 37 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 255A34CD44764C4CA1C0D2FDF30C33BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1104 |  | 2013-09-19 | 2013-09-19 14:54 | 2013-09-19 15:19 | OTHER - GPCM36K060K | 89 | 12.2 | Yes | Yes | 21.1 | 21.5 | -0.4 | 84AF57B8E7354012BC5ED0AD03277BFE |  | R22 | Non-TXV |  | 13.71% | 0.86292 | 26.34% | [5 empty] | Non-TXV | 13.71%
Fresno | CA | 93702-2349 |  | 2013-09-19 | 2013-09-19 12:12 | 2013-09-19 12:31 | PAYNE - PY1PNB042060AAAA | 102 | 5.1 | Yes | Yes | 23.9 | 20.9 | 3 | D73F270B0DFB48E698BC806C22EBFBDC |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93309-3661 |  | 2013-09-27 | 2013-09-27 10:34 | 2013-09-27 10:34 | GOODMAN - GPG13600901BA | 164 | 0 | Yes | Yes | 20.1 | 20.2 | -0.1 | C96A10EE756142C3B33905875B7F5DBB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3697 |  | 2013-09-26 | 2013-09-26 14:59 | 2013-09-26 14:59 | GOODMAN - GPG1348090M41AD | 125 | 0 | Yes | Yes | 17.7 | 19 | -1.3 | BA4C17D28B1A42E2A0F5F409D6698446 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-09-18 | 2013-09-18 17:53 | 2013-09-18 17:53 | HEIL - PGC030K060A | 52 | 7.6 | Yes | Yes | 23.3 | 21.5 | 1.8 | 192B6442FDC14A16BC9CCCBB9C19D97D | Add refrigerant: 7.6 oz | R22 | Non-TXV |  | 14.62% | 0.85385 | 28.09% | [5 empty] | Non-TXV | 14.62%
Fresno | CA | 93722-5743 |  | 2013-09-18 | 2013-09-18 11:52 | 2013-09-18 11:52 | PAYNE - PY3GNAA36090NA | 80 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | FDCC5B97950A42E98F30F8D6A05CC90F |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-4265 |  | 2013-09-24 | 2013-09-24 10:33 | 2013-09-24 11:00 | BRYANT - 561CJ042 B | 81 | 3.4 | Yes | Yes | 20.7 | 21.3 | -0.5 | D9B26B97569D4B32AB6A91E53F894322 |  | R22 | Non-TXV |  | 4.198% | 0.95802 | 8.067% | [5 empty] | Non-TXV | 4.198%
Lost Hills | CA | 93249-0000 |  | 2013-09-25 | 2013-09-25 18:35 | 2013-09-25 18:38 | YORK - PGC030K060A | 52 | 2 | Yes | Yes | 24.1 | 19.8 | 4.3 | B359A029C5BB49D281760AE6FF2DFAC9 |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Fresno | CA | 93728-3626 |  | 2013-09-18 | 2013-09-18 12:53 | 2013-09-18 12:53 | GOODMAN - GPG1342070M4AD | 105 | 0 | Yes | Yes | 22.3 | 20.4 | 1.9 | 03892BA75D7E4C3C84D0CF0B9A9531B7 |  | R410A | TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-09-18 | 2013-09-18 18:01 | 2013-09-18 18:03 | HEIL - PGC030K060A | 52 | 2.6 | Yes | Yes | 24 | 21 | 3 | DF0D513F1B5044FBACB897920E1B46B4 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Lost Hills | CA | 93249-0000 |  | 2013-09-25 | 2013-09-25 18:53 | 2013-09-25 18:53 | TEMPSTAR - PGAA36C1K4 | 69 | 0 | Yes | Yes | 0 | 23.2 | -23.2 | AED50C71D12549F5AE340F998FB1AA8D | Add refrigerant: 9 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5043 |  | 2013-09-17 | 2013-09-17 15:43 | 2013-09-17 16:12 | DAY & NIGHT - UKN | 80 | 4.9 | Yes | Yes | 22.7 | 21.2 | 1.5 | B908F15A2F224731B69BADF7A60940E5 |  | R22 | Non-TXV |  | 6.125% | 0.93875 | 11.77% | [5 empty] | Non-TXV | 6.125%
Wasco | CA | 93280-2678 |  | 2013-10-29 | 2013-10-29 18:26 | 2013-10-29 18:27 | RHEEM - N/A | 85 | 4.8 | Yes | Yes | 25.4 | 20.7 | 4.7 | 894CAD4C288D47A1A44D67AC39112798 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Bakersfield | CA | 93309-4637 |  | 2013-10-08 | 2013-10-08 18:03 | 2013-10-08 18:19 | GOODMAN - GSC103081B1A | 81 | 7.1 | Yes | Yes | 22.1 | 21.8 | 0.3 | 6517F2AA154E40A1BA93F75871181886 |  | R22 | Non-TXV |  | 8.765% | 0.91235 | 16.85% | [5 empty] | Non-TXV | 8.765%
Wasco | CA | 93280-1354 |  | 2013-09-26 | 2013-09-26 18:42 | 2013-09-26 18:47 | OTHER - DBYP-F060N110A | 130 | 8.1 | Yes | Yes | 25.9 | 20.1 | 5.8 | DDD8C8BE07C4405F8F8EBC626F90C661 |  | R22 | TXV |  | 6.231% | 0.93769 | 11.97% | [5 empty] | TXV | 6.231%
Wasco | CA | 93280-1613 |  | 2013-09-26 | 2013-09-26 18:54 | 2013-09-26 18:56 | PAYNE - PA13NR060000AHAA | 167 | 10.8 | Yes | Yes | 23.2 | 20.2 | 3 | 068C8B2BCB8944C298098A3C772E40E0 |  | R22 | TXV |  | 6.467% | 0.93533 | 12.43% | [5 empty] | TXV | 6.467%
Buttonwillow | CA | 93206-9768 |  | 2013-09-24 | 2013-09-24 20:06 | 2013-09-24 20:08 | TEMPSTAR - PGAA42C1K1 | 82 | 2.5 | Yes | Yes | 22 | 18.8 | 3.2 | 3566AE2463BC4F5297B6DAA65E147A7C |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Buttonwillow | CA | 93206-9768 |  | 2013-09-24 | 2013-09-24 20:12 | 2013-09-24 20:12 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 18.3 | 16.9 | 1.4 | B54072BC6E5746C28154F73B2FC32864 | Add refrigerant: 14.9 oz | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95138-1931 |  | 2013-10-17 | 2013-10-17 11:26 | 2013-10-17 11:44 | CARRIER - 38CKC018300 | 85 | 3.7 | Yes | Yes | 19.5 | 20.9 | -1.4 | F35A6756DDDC46D6BE30BB364042114D |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Bakersfield | CA | 93313-4268 |  | 2013-10-10 | 2013-10-10 18:05 | 2013-10-10 18:07 | OTHER - PGBO48075-1 REVA | 86 | 6.3 | Yes | Yes | 20.3 | 18.7 | 1.6 | 1DA0864A3E664518BAA3A2A3C013C41B |  | R22 | Non-TXV |  | 7.326% | 0.92674 | 14.08% | [5 empty] | Non-TXV | 7.326%
Bakersfield | CA | 93309-4637 |  | 2013-10-08 | 2013-10-08 17:48 | 2013-10-08 17:48 | BDP - 5C7C024RCU | 60 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 8572F9AE7A8D4C999425135C80283210 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1311 |  | 2013-09-27 | 2013-09-27 09:00 | 2013-09-27 09:29 | GOODMAN - PGB0480751 | 86 | 3.8 | Yes | Yes | 20 | 18.8 | 1.2 | FCB9098C2C63486D90A8565DD53D7AD8 |  | R22 | Non-TXV |  | 4.419% | 0.95581 | 8.492% | [5 empty] | Non-TXV | 4.419%
Fresno | CA | 93703-5209 |  | 2013-09-19 | 2013-09-19 14:05 | 2013-09-19 14:27 | GOODMAN - GPG12360701A | 85 | 4.3 | Yes | Yes | 22.8 | 19 | 3.8 | F758BA3FCB284EF4BF1FFF016F7C2072 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Bakersfield | CA | 93309-4734 |  | 2013-09-27 | 2013-09-27 09:52 | 2013-09-27 09:52 | YORK - D1NH024N06506C | 94 | 0 | Yes | Yes | 21.8 | 20.6 | 1.3 | F5B573A9219A4269AC9C7FC9E37DAB8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6161 |  | 2013-09-18 | 2013-09-18 10:30 | 2013-09-18 10:30 | DAY & NIGHT - 585GJ0304 | 58 | 0 | Yes | Yes | 20.1 | 18.2 | 1.9 | 1E252BAD1F0B491F9001791CA9664AD7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1909 |  | 2013-09-19 | 2013-09-19 13:37 | 2013-09-20 09:51 | CARRIER - UNK | 83 | 2.8 | Yes | Yes | 22 | 20.9 | 1.1 | 6CA13DEF6E1B421EA889C3A184A5400B |  | R22 | Non-TXV |  | 3.373% | 0.96627 | 6.483% | [5 empty] | Non-TXV | 3.373%
Shafter | CA | 93263-1910 |  | 2013-10-08 | 2013-10-08 17:44 | 2013-10-08 17:44 | OTHER - PGF036K060A | 71 | 0 | Yes | Yes | 18 | 18.8 | -0.8 | B67ACD68749E4B14ABA8BBEF12DEC299 | Add refrigerant: 13.1 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4422 |  | 2013-09-19 | 2013-09-19 16:47 | 2013-09-19 16:47 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 89D84410A5754962ADCED06A7B2BDBEA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4680 |  | 2013-10-08 | 2013-10-08 17:00 | 2013-10-08 17:00 | BDP - UKN | 60 | 0 | Yes | Yes | 22.6 | 22.1 | 0.5 | CBB4ED98B1C141B38F0F87FE124A34D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2592 |  | 2013-09-26 | 2013-09-26 19:13 | 2013-09-26 19:15 | OTHER - CCU12A36A-1 | 94 | -5.3 | Yes | Yes | 24.7 | 20.4 | 4.3 | 003512A468A54C14BF204ACF6DD06759 |  | R22 | TXV |  | -5.638% | 1.0564 | 1.579% |  |  |  |  | TXV |  |  | -5.638%
Wasco | CA | 93280-2592 |  | 2013-10-31 | 2013-10-31 18:24 | 2013-10-31 18:29 | OTHER - CCU12A36A-1 | 94 | 4.4 | Yes | Yes | 21.1 | 20.1 | 1 | D0DA6542B6304DF5BCB171AD1431A51B | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 4.681% | 0.95319 | 8.996% | [5 empty] | Non-TXV | 4.681%
Wasco | CA | 93280-2592 |  | 2013-09-26 | 2013-09-26 19:03 | 2013-09-26 19:09 | OTHER - CCU12A30A-1 | 90 | -3.5 | Yes | Yes | 24.8 | 20.4 | 4.4 | 39E244DF1E5E4FA58AB0AC80514DDAEB |  | R22 | TXV |  | -3.889% | 1.0389 | 1.089% |  |  |  |  | TXV |  |  | -3.889%
Shafter | CA | 93263-2429 |  | 2013-09-19 | 2013-09-19 18:31 | 2013-09-19 18:33 | CARRIER - 48GXN048115301-- | 114 | 5.4 | Yes | Yes | 24.4 | 18.7 | 5.7 | E065B772F0D9415BB8B6F374BC467151 |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Fresno | CA | 93722-6150 |  | 2013-09-18 | 2013-09-18 09:52 | 2013-09-18 10:27 | LENNOX - 12GCS030753PA | 85 | 3.8 | Yes | Yes | 19 | 19.5 | -0.5 | EA091B5BE4E54003BA71EB62399D6B46 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Bakersfield | CA | 93313-5473 |  | 2013-10-10 | 2013-10-10 16:52 | 2013-10-10 17:08 | WESTINGHOUSE - UKN | 90 | 8.2 | Yes | Yes | 21.5 | 22 | -0.5 | BAD651EBE72D467D9503CA19F5D1B8F1 |  | R22 | Non-TXV |  | 9.111% | 0.90889 | 17.51% | [5 empty] | Non-TXV | 9.111%
Shafter | CA | 93263-2908 |  | 2013-09-19 | 2013-09-19 18:41 | 2013-09-19 18:44 | RHEEM - N/A | 85 | -6 | Yes | Yes | 25.5 | 20.4 | 5.1 | 7D0CF2BCB23C49D8BEE67F5814421CCE |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Shafter | CA | 93263-2908 |  | 2013-09-19 | 2013-09-19 18:46 | 2013-09-19 18:47 | RHEEM - N/A | 85 | -8 | Yes | Yes | 26.4 | 20.4 | 6 | 7A9459D469114C1E81F325E1647C297C |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93308-7624 |  | 2013-10-10 | 2013-10-10 16:41 | 2013-10-10 17:00 | BDP - 561CJ030-A | 56 | 3.9 | Yes | Yes | 20 | 20.4 | -0.4 | 6742911DEE844BA89DBF6B3738BE80AF |  | R22 | Non-TXV |  | 6.964% | 0.93036 | 13.38% | [5 empty] | Non-TXV | 6.964%
Shafter | CA | 93263-2206 |  | 2013-09-19 | 2013-09-19 18:49 | 2013-09-19 18:51 | OTHER - R4GDX36K100X | 85 | -5 | Yes | Yes | 20.1 | 22.3 | -2.2 | 4B05ADD1A88A4124B65D89F5B0E01D1E |  | R22 | TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | TXV |  |  | -5.882%
Bakersfield | CA | 93308-7625 |  | 2013-10-07 | 2013-10-07 19:36 | 2013-10-07 19:36 | GOODMAN - GSC130301EA | 82 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | 0B665673AC5D4BD0905B26322936FB30 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7625 |  | 2013-10-07 | 2013-10-07 19:46 | 2013-10-07 19:46 | BDP - 561CJ018B | 49 | 0 | Yes | Yes | 21 | 20.7 | 0.3 | 8E568A7C8F404173AA0AE18E50931503 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7628 |  | 2013-10-09 | 2013-10-09 10:31 | 2013-10-09 10:31 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 19.8 | 19.9 | -0.1 | B022AD8CBA0A4C33869BB644725B81AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9156 |  | 2013-09-18 | 2013-09-18 11:09 | 2013-09-18 11:09 | YORK - DCYZF036N070B | 64 | 0 | Yes | Yes | 18 | 20.1 | -2.1 | 8F32C7D7138F4623B1DCBDBFA50D8917 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6151 |  | 2013-10-10 | 2013-10-10 12:13 | 2013-10-10 12:13 | BRYANT - 582ANW024000AAAD | 56 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | 96341EF45A934FD5831ACD2C3561CF61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7627 |  | 2013-10-09 | 2013-10-09 10:50 | 2013-10-09 10:50 | BDP - 561CJ024-A | 61 | 0 | Yes | Yes | 20.1 | 20.4 | -0.3 | AC0BB0F5CD2C46EE853FF49797A01A27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6061 |  | 2013-10-15 | 2013-10-15 17:01 | 2013-10-15 17:01 | PAYNE - PY1PNB024040AAAA | 56 | 0 | Yes | Yes | 20.8 | 21 | -0.2 | C5135FDF703C4F0792559C7D4FA1869E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7628 |  | 2013-10-10 | 2013-10-10 18:10 | 2013-10-10 18:10 | BDP - 561J030A | 56 | 0 | Yes | Yes | 20.8 | 21 | -0.2 | BD41B0A24C914CE8BD5BE3697E27F6EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-6234 |  | 2013-09-19 | 2013-09-19 10:10 | 2013-09-19 10:27 | CARRIER - 38FN036300 | 81 | 4.3 | Yes | Yes | 20.9 | 20.7 | 0.2 | 138E5747FEC34FCE986A72F124B0461E | Add refrigerant: 2.9 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 5.309% | 0.94691 | 10.2% | [5 empty] | Non-TXV | 5.309%
Bakersfield | CA | 93308-7627 |  | 2013-10-09 | 2013-10-09 11:54 | 2013-10-09 11:54 | BDP - 561CJ024-A | 61 | 0 | Yes | Yes | 22 | 21.8 | 0.2 | 66043CFA834B4956A94A49BA0C52839B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Buttonwillow | CA | 93206-9606 |  | 2013-10-15 | 2013-10-15 17:25 | 2013-10-15 17:28 | COLEMAN - PGE10A24D0504A-3A | 52 | 3.1 | Yes | Yes | 23.1 | 20.9 | 2.2 | 2F9F1A63C95E4175AF999FC8E2A728EB |  | R22 | Non-TXV |  | 5.962% | 0.94038 | 11.46% | [5 empty] | Non-TXV | 5.962%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 18:33 | 2013-10-07 18:33 | BDP - 561CJ030-A | 65 | 0 | Yes | Yes | 21.5 | 20.9 | 0.6 | 0D200CB910754E6E828CB7B5DF0DE4DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6152 |  | 2013-10-10 | 2013-10-10 12:36 | 2013-10-10 12:36 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 19.8 | 20.7 | -0.9 | C5A8BC30C35F4E0CAFD98B6A3B061371 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7628 |  | 2013-10-10 | 2013-10-10 17:20 | 2013-10-10 17:20 | BRYANT - 561J030A | 56 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 697DD8B94EC04FE6832C58F4E684198E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2409 |  | 2013-10-14 | 2013-10-14 14:47 | 2013-10-14 14:47 | RHEEM - UKN | 58 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 4BB7BA884D8246D9841C22CC9B696C73 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4451 |  | 2013-09-27 | 2013-09-27 10:33 | 2013-09-27 22:40 | GOODMAN - PGB0360751A | 60 | 3.9 | Yes | Yes | 19.9 | 18.8 | 1.1 | 295BF1F71873483CA41B9673E1738492 |  | R22 | Non-TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | Non-TXV | 6.5%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 13:10 | 2013-10-09 13:10 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | B001B22764DD4F0989928E386500450E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-09-25 | 2013-09-25 19:03 | 2013-09-25 19:03 | OTHER - JS5BD-36K | 137 | 0 | Yes | Yes | 26.5 | 21.2 | 5.3 | 1F67466D66B142629ECAD0D733BC0A95 | Add refrigerant: 16.1 oz | R22 | TXV |  | 0% | 1 | 0%
Buttonwillow | CA | 93206-0000 |  | 2013-10-15 | 2013-10-15 17:30 | 2013-10-15 17:33 | YORK - D2NZ042N0606NXA | 144 | -7.6 | Yes | Yes | 18.8 | 19.1 | -0.3 | D463F72B2CFB466881DF8CAE23C24791 |  | R410A | TXV |  | -5.278% | 1.0528 | 1.478% |  |  |  |  | TXV |  |  | -5.278%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 17:45 | 2013-10-07 17:45 | BDP - 561CJ030-A | 65 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 1D7B925ECCE245C0A189999737A6F014 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lost Hills | CA | 93249-0000 |  | 2013-09-25 | 2013-09-25 19:10 | 2013-09-25 19:12 | OTHER - ERCQ0361BBA | 83 | 4.8 | Yes | Yes | 26.4 | 20.7 | 5.7 | A1C4BF04F2A0421285FA44BFE1696389 |  | R22 | TXV |  | 5.783% | 0.94217 | 11.11% | [5 empty] | TXV | 5.783%
Bakersfield | CA | 93311-9053 |  | 2013-10-02 | 2013-10-02 18:49 | 2013-10-02 18:49 | YORK - H2RC042S06G | 109 | 0 | Yes | Yes | 21.7 | 21 | 0.7 | 144FE62151E5486E84EEA92564CD8C07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7627 |  | 2013-10-09 | 2013-10-09 12:08 | 2013-10-09 12:08 | BDP - 561CJ030-B | 71 | 0 | Yes | Yes | 21.7 | 21.3 | 0.5 | 506F97B61542441D9F50D83DEAFE20E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5460 |  | 2013-10-10 | 2013-10-10 18:21 | 2013-10-10 18:21 | ICP - PGC042K080E | 84 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | A2796EC9A2D2464E9E9B661B33FE15EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 18:47 | 2013-10-07 18:47 | BDP - 561CJ030-A | 65 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 03247AF5EDC6435297E7E25CEE79D4F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-9554 |  | 2013-09-25 | 2013-09-25 12:10 | 2013-09-25 12:10 | GOODMAN - GSC130481AF | 152 | 0 | Yes | Yes | 23.3 | 18.8 | 4.5 | 8BEB317AD092483F91DA86BD98C82DA4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 12:53 | 2013-10-09 12:53 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 4B65D2C0850641CAB14CA65E56134417 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6061 |  | 2013-10-15 | 2013-10-15 17:34 | 2013-10-15 17:34 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.8 | 20.4 | 0.4 | 7F4CB92E43A04577BA02DC000022BD8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6061 |  | 2013-10-15 | 2013-10-15 16:05 | 2013-10-15 16:05 | ICP - PGC024K040E | 54 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | 1F913FB90DF2484DA22B72090379ACA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6156 |  | 2013-10-10 | 2013-10-10 14:03 | 2013-10-10 14:20 | BRYANT - 882ANW024060AAAD | 56 | 4.4 | Yes | Yes | 19.8 | 20.4 | -0.6 | 9A93E9D5339A4A4EAE0549B64023187F |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Bakersfield | CA | 93314-9103 |  | 2013-10-10 | 2013-10-10 18:45 | 2013-10-10 18:50 | YORK - D1NH042N0656C | 94 | 6.2 | Yes | Yes | 25.5 | 21.9 | 3.6 | 4EF0947C2124445EB8CFDC5DA86D134D |  | R22 | Non-TXV |  | 6.596% | 0.93404 | 12.68% | [5 empty] | Non-TXV | 6.596%
Bakersfield | CA | 93309-6061 |  | 2013-10-15 | 2013-10-15 16:35 | 2013-10-15 16:35 | PAYNE - PY1NNB024040AAAA | 56 | 0 | Yes | Yes | 20.3 | 21 | -0.7 | 9057681275AC4153B83F4F84786F37D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5003 |  | 2013-09-17 | 2013-09-17 11:41 | 2013-09-17 15:41 | DAY & NIGHT - UKN | 68 | 3.6 | Yes | Yes | 23.1 | 21 | 2.1 | 6FF7DD432A86451B8A440B5BB7462ECD |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Selma | CA | 93662-4818 |  | 2013-10-07 | 2013-10-07 16:42 | 2013-10-07 17:02 | LENNOX - UNK | 110 | 4.2 | Yes | Yes | 20.9 | 21.5 | -0.6 | AD858975E3C54CCC8FFE1BB4B0D32027 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Bakersfield | CA | 93309-6156 |  | 2013-10-10 | 2013-10-10 13:49 | 2013-10-10 13:49 | BRYANT - 582ANW024060AAAD | 53 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | 5935609BDC004F979E399C1A296C67C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6156 |  | 2013-10-10 | 2013-10-10 14:35 | 2013-10-10 14:35 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 20.8 | 20.4 | 0.4 | F95F5F562A394C0E993BA89A928D15BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6152 |  | 2013-10-10 | 2013-10-10 13:12 | 2013-10-10 13:12 | PAYNE - 582ANW024060AAAD | 53 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | 16C240D6E5764D6A8ACEF5DAF4BF108C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-4274 |  | 2013-10-10 | 2013-10-10 18:26 | 2013-10-10 18:28 | YORK - H2RC036S06G | 83 | 6 | Yes | Yes | 26.9 | 22 | 4.9 | 1782791F0309491395BC9018F63D3758 |  | R22 | TXV |  | 7.229% | 0.92771 | 13.89% | [5 empty] | TXV | 7.229%
Bakersfield | CA | 93314-4274 |  | 2013-10-10 | 2013-10-10 18:33 | 2013-10-10 18:39 | OTHER - AC030X1222G | 88 | -6 | Yes | Yes | 20.7 | 20.4 | 0.3 | C31CC37374D54F7087A9541085593438 |  | R22 | TXV |  | -6.818% | 1.0682 | 1.909% |  |  |  |  | TXV |  |  | -6.818%
Bakersfield | CA | 93309-4680 |  | 2013-10-08 | 2013-10-08 17:23 | 2013-10-08 17:23 | GOODMAN - GSC130308181DA | 75 | 0 | Yes | Yes | 22.8 | 20.9 | 1.9 | D97FF915D6CB470B9CFFAD53721B87D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2859 |  | 2013-09-19 | 2013-09-19 18:23 | 2013-09-19 18:23 | HEIL - PGAA60D1K1 | 122 | 0 | Yes | Yes | 20.5 | 19.8 | 0.7 | 156E8DE5459E423889FCFD95F1EE4573 | Add refrigerant: 17.3 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4692 |  | 2013-10-08 | 2013-10-08 16:37 | 2013-10-08 16:37 | GOODMAN - GSC130241FA | 77 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | CA8EB1FA14CE4BF0B5652EA29F557461 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6157 |  | 2013-10-10 | 2013-10-10 14:47 | 2013-10-10 14:47 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 20.8 | 21 | -0.2 | F9A5DF969FC048AF85950DD6692112F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-1353 |  | 2013-09-30 | 2013-09-30 15:53 | 2013-09-30 16:17 | UNITARY PRODUCTS GROUP - BRCQ10301BA | 48 | 1.7 | Yes | Yes | 21 | 21.5 | -0.5 | F3086D10F1B745F6A569669FF193F38C |  | R22 | Non-TXV |  | 3.542% | 0.96458 | 6.806% | [5 empty] | Non-TXV | 3.542%
Bakersfield | CA | 93311-9113 |  | 2013-10-04 | 2013-10-04 13:00 | 2013-10-04 13:00 | CARRIER - 38CK036350 | 70 | 0 | Yes | Yes | 22.5 | 21.2 | 1.3 | 2C17BFF178DB4C6892CE8B27C86CC427 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9113 |  | 2013-10-04 | 2013-10-04 13:06 | 2013-10-04 13:06 | CARRIER - 38CK036350 | 70 | 0 | Yes | Yes | 22.9 | 21 | 1.9 | 43D14D3FDC034435995FDF8F012C3DB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9110 |  | 2013-10-02 | 2013-10-02 15:31 | 2013-10-02 15:31 | CARRIER - 38BRC036340 | 95 | 0 | Yes | Yes | 21.9 | 21.8 | 0.1 | FE8E10637A4C476B8B0CFBE008956308 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9110 |  | 2013-10-02 | 2013-10-02 15:33 | 2013-10-02 15:33 | CARRIER - 38BRC036340 | 101 | 0 | Yes | Yes | 21.7 | 21.2 | 0.5 | 3C00AFCFB0A54E7D94C83C10B29D7725 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9144 |  | 2013-10-02 | 2013-10-02 14:46 | 2013-10-02 15:05 | CARRIER - 38CK060370 | 131 | 10.6 | Yes | Yes | 22.3 | 22.1 | 0.2 | D1E4AC007DFF411E8DE77FBC0C93C268 |  | R22 | Non-TXV |  | 8.092% | 0.91908 | 15.55% | [5 empty] | Non-TXV | 8.092%
Bakersfield | CA | 93308-1121 |  | 2013-10-22 | 2013-10-22 15:17 | 2013-10-22 15:17 | GOODMAN - GPG13420701AB | 107 | 0 | Yes | Yes | 19 | 22 | -3 | BB3F2DECFE9F46AD865E0C3CFB60A985 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5802 |  | 2013-10-07 | 2013-10-07 15:17 | 2013-10-07 15:46 | PAYNE - PA12NA042-B | 85 | 6.6 | Yes | Yes | 18.2 | 21.2 | -3 | 8CF8DBF1D1A14E03A750D9EAEBE7DA7D |  | R22 | TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | TXV | 7.765%
Vacaville | CA | 95688-9211 |  | 2013-10-08 | 2013-10-08 11:46 | 2013-10-08 12:17 | PAYNE - PA10JA042-D | 90 | 4.4 | Yes | Yes | 21 | 15.5 | 5.5 | 0D5F16C2E4684E52A396B7719F6B2806 |  | R22 | TXV |  | 4.889% | 0.95111 | 9.395% | [5 empty] | TXV | 4.889%
Bakersfield | CA | 93309-6158 |  | 2013-10-10 | 2013-10-10 15:36 | 2013-10-10 15:36 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 19.9 | 21 | -1.1 | F1BB438D8F0C49919B9B953E3B671A78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2734 |  | 2013-09-25 | 2013-09-25 16:51 | 2013-09-25 16:51 | DAY & NIGHT - 591AN042-B | 112 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | FF50EAF7836A4E818F4F0BFD99DED76A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-3730 |  | 2013-10-07 | 2013-10-07 16:25 | 2013-10-07 18:35 | COLEMAN - DAYP-F048N080A | 132 | 15.1 | Yes | Yes | 19.3 | 20.8 | -1.5 | 686EE4ADD16D4499B760C26E5C8D424A |  | R22 | Non-TXV |  | 11.44% | 0.88561 | 21.98% | [5 empty] | Non-TXV | 11.44%
Bakersfield | CA | 93311-2832 |  | 2013-10-04 | 2013-10-04 11:54 | 2013-10-04 11:54 | YORK - H2RC030506G | 87 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | 38F8E90401684072BE2EBEDD68749790 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2832 |  | 2013-10-04 | 2013-10-04 12:03 | 2013-10-04 12:03 | YORK - H2RC036506G | 87 | 0 | Yes | Yes | 20.1 | 21 | -0.9 | 885927E72F6246BFA8EEBEBA7B8EA73D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1431 |  | 2013-09-23 | 2013-09-23 12:29 | 2013-09-23 13:59 | NORDYNE - ILLEGIBLE | 89 | 4 | Yes | Yes | 25.9 | 20.8 | 5.1 | 598858BDDFCF40D78F687330BD534739 |  | R22 | Non-TXV |  | 4.494% | 0.95506 | 8.637% | [5 empty] | Non-TXV | 4.494%
San Jose | CA | 95135-1418 |  | 2013-10-22 | 2013-10-22 11:37 | 2013-10-22 13:33 | CARRIER - 48ESN030060311 | 98 | -6.9 | Yes | Yes | 18.6 | 20.4 | -1.8 | 80C6668D8357418A836C8522B3CD22D2 |  | R410A | Non-TXV |  | -7.041% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.041%
San Jose | CA | 95122-3363 |  | 2013-10-03 | 2013-10-03 16:01 | 2013-10-03 18:44 | CARRIER - 38YG018310 | 72 | 3 | Yes | Yes | 21.5 | 21 | 0.5 | 9FE30FE970B145238BB70F735D0F9FF0 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Bakersfield | CA | 93308-1426 |  | 2013-09-26 | 2013-09-26 15:36 | 2013-09-26 15:36 | BDP - 588ANW042060ADAG | 82 | 0 | Yes | Yes | 18.7 | 18.9 | -0.2 | 738A8E88BD5941CDB0604A54F82A0B2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6155 |  | 2013-10-10 | 2013-10-10 13:28 | 2013-10-10 13:28 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 21.5 | 21 | 0.5 | 5DFB073632424DC9A046EFC046005EB3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1822 |  | 2013-10-11 | 2013-10-11 04:20 | 2013-10-11 04:37 | ICP - PGME48G0904 | 215 | 12.9 | Yes | Yes | 21.3 | 21.8 | -0.5 | 722994463C704E22910014C57FC52A65 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Bakersfield | CA | 93308-7628 |  | 2013-10-07 | 2013-10-07 18:01 | 2013-10-07 18:01 | BDP - 561CJ030-A | 60 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 4E46CA8F2769428E9716A6CD18431238 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2888 |  | 2013-10-02 | 2013-10-02 17:01 | 2013-10-02 17:01 | ICP - ACS042A2C1 | 90 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | DA74FDFA7A974986BA7A6045308C8B48 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7626 |  | 2013-10-08 | 2013-10-08 11:29 | 2013-10-08 11:29 | BDP - 561CJ024B | 56 | 0 | Yes | Yes | 20.7 | 20.8 | -0.1 | 99E39CDE8AB14E648425358C79C24E53 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7626 |  | 2013-10-09 | 2013-10-09 16:06 | 2013-10-09 16:06 | BDP - 561CJ03024-B | 61 | 0 | Yes | Yes | 21.5 | 21 | 0.5 | A141C3E43698473489EAA973DF425390 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 17:12 | 2013-10-07 17:12 | BDP - 561CJ030-A | 65 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | B2458B76ACD24C1A9A94EEE3A695E83A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 17:26 | 2013-10-07 17:26 | BDP - 561CJ018-B | 65 | 0 | Yes | Yes | 21.2 | 21.4 | -0.2 | 1E48274718F54056AC67A6B157E309DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 16:54 | 2013-10-07 16:54 | BDP - 561CJ024-A | 61 | 0 | Yes | Yes | 21.4 | 20.9 | 0.5 | B50FB6559E304E38833DE1E63E7C6C6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7629 |  | 2013-10-09 | 2013-10-09 16:25 | 2013-10-09 16:25 | BDP - 561CJ024-B | 61 | 0 | Yes | Yes | 21.7 | 20.7 | 1 | AE41A8095E014DAABCA04A27F92BABF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9030 |  | 2013-10-04 | 2013-10-04 10:05 | 2013-10-04 10:05 | YORK - H2RC0425069 | 109 | 0 | Yes | Yes | 19.6 | 19.9 | -0.3 | D60162E157004D82A7050268C85CD8F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 15:23 | 2013-10-09 15:23 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 21.7 | 21 | 0.7 | 6A7A07C64ABE46F8A17BC6D6CFBD2BDA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2829 |  | 2013-10-02 | 2013-10-02 11:26 | 2013-10-02 11:26 | YORK - G2RC042S06HA | 109 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | B0EC3350AC9F4C9C9D3468C06EA1AE25 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2829 |  | 2013-10-02 | 2013-10-02 11:32 | 2013-10-02 11:32 | YORK - G2RC042S06HA | 109 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | A385B1E3759F44A48DFB3D7AAE2664DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3261 |  | 2013-09-27 | 2013-09-27 17:06 | 2013-09-27 17:06 | TRANE - 2A6H030B1D000AA | 305 | 0 | Yes | Yes | 21.6 | 22 | -0.4 | 460F677EFF9D439EB6F5D5EDC9DB0858 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1961 |  | 2013-09-26 | 2013-09-26 14:13 | 2013-09-26 14:13 | ICP - CA9060VKC1 | 160 | 0 | Yes | Yes | 22 | 18.7 | 3.3 | A85728BBDEFC4553B3519245A8DE3405 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 10:53 | 2013-10-09 10:53 | BDP - 561CJ024-A | 61 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | 828BD058A5364F7A8CE6B4E773FFD014 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9361 |  | 2013-10-04 | 2013-10-04 15:42 | 2013-10-04 15:42 | YORK - H2RC048S06G | 119 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 424CF4CFD4B9498E8CC34B3A83A83388 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2594 |  | 2013-10-31 | 2013-10-31 17:44 | 2013-10-31 17:46 | OTHER - CCU12A39A-1 | 90 | 3.2 | Yes | Yes | 21.8 | 19.8 | 2 | 298AC509FCBC4EEDAD7871F2598A819F |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Wasco | CA | 93280-2594 |  | 2013-11-07 | 2013-11-07 19:05 | 2013-11-07 19:07 | OTHER - CCU12A30A-1 | 90 | -3.4 | Yes | Yes | 24.2 | 20.9 | 3.3 | 449FC88AA29A46FD9AD8F65CC57E26EB |  | R22 | TXV |  | -3.778% | 1.0378 | 1.058% |  |  |  |  | TXV |  |  | -3.778%
Bakersfield | CA | 93308-7626 |  | 2013-10-09 | 2013-10-09 14:41 | 2013-10-09 14:41 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 0BBC91B24F86439084F0D44D22A75496 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 14:12 | 2013-10-09 14:12 | BDP - 561CJ030-B | 71 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 7E06AF27FD7F423183E3DD8E1A9468F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2593 |  | 2013-11-07 | 2013-11-07 19:09 | 2013-11-07 19:09 | OTHER - CCU12AB0A-1 | 90 | 0 | Yes | Yes | 15.4 | 21 | -5.6 | C5E4A4EFDC674D608AA0ACC4BF2CC7B3 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7625 |  | 2013-10-08 | 2013-10-08 11:51 | 2013-10-08 11:51 | GOODMAN - GSC130301EB | 66 | 0 | Yes | Yes | 21.1 | 22.5 | -1.4 | 16619509050144A499AA6A5EBE268349 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9110 |  | 2013-10-04 | 2013-10-04 14:42 | 2013-10-04 15:00 | CARRIER - 3BCKC060370 | 132 | 13.8 | Yes | Yes | 22.1 | 21 | 1.1 | 8702C1A5D1184748B1097B4809EFEEDC |  | R22 | Non-TXV |  | 10.45% | 0.89545 | 20.09% | [5 empty] | Non-TXV | 10.45%
Bakersfield | CA | 93311-2811 |  | 2013-10-02 | 2013-10-02 09:07 | 2013-10-02 09:07 | NORDYNE - JS5BD-060K | 232 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | FE43E88DD749479F97400751C9D8E630 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6854 |  | 2013-10-04 | 2013-10-04 13:56 | 2013-10-04 14:15 | CARRIER - UNK | 100 | 5.7 | Yes | Yes | 25 | 21.3 | 3.7 | FA37F1C608DF495390B0B243813D72BC |  | R22 | Non-TXV |  | 5.7% | 0.943 | 10.95% | [5 empty] | Non-TXV | 5.7%
Fresno | CA | 93728-2920 |  | 2013-10-08 | 2013-10-08 10:20 | 2013-10-08 11:00 | CARRIER - 48VLNA3609030 | 152 | 5.4 | Yes | Yes | 22.5 | 19.9 | 2.6 | DCA31379964D4252AE044E85A6376980 |  | R410A | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Fresno | CA | 93703-1106 |  | 2013-10-16 | 2013-10-16 11:01 | 2013-10-16 11:33 | CARRIER - 48GS030040301 | 55 | 3.5 | Yes | Yes | 19.3 | 19.3 | 0 | A4D004A9A70C413F818DCC7BF34F1FF1 |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Bakersfield | CA | 93309-6149 |  | 2013-10-10 | 2013-10-10 11:32 | 2013-10-10 11:32 | BRYANT - 582ANW024000AAAD | 60 | 0 | Yes | Yes | 20.6 | 20.7 | -0.1 | 92F8CB6F42C045008B5CB4F7CB6A4332 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2095 |  | 2013-10-09 | 2013-10-09 12:11 | 2013-10-09 12:11 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.1 | 21 | -2.9 | 6824A30976994117B423B8370418F1B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2593 |  | 2013-11-11 | 2013-11-11 16:21 | 2013-11-11 16:23 | OTHER - CCU12A30A-1 | 90 | -5.3 | Yes | Yes | 23.1 | 21 | 2.1 | 324FC3DE47D448B1B2A90B098AA2720E |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Bakersfield | CA | 93308-7625 |  | 2013-10-08 | 2013-10-08 09:35 | 2013-10-08 09:35 | BDP - 561CJ024B | 56 | 0 | Yes | Yes | 21.8 | 18.8 | 3 | DA98726C53EA4D33A072571024259A45 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3589 |  | 2013-10-24 | 2013-10-24 10:49 | 2013-10-24 10:49 | OTHER - FAFF-043JAZ | 99 | 0 | Yes | Yes | 22.1 | 19.7 | 2.4 | 391A0ACFF94D4DB0948E9019377B430F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-4207 |  | 2013-10-07 | 2013-10-07 10:12 | 2013-10-07 10:44 | TEMPSTAR - PGF030K060A | 52 | 6.2 | Yes | Yes | 21.9 | 19.1 | 2.8 | 94415F634DD7406499E5F076B4FEA791 |  | R22 | Non-TXV |  | 11.92% | 0.88077 | 22.91% | [5 empty] | Non-TXV | 11.92%
Buttonwillow | CA | 93206-9705 |  | 2013-10-15 | 2013-10-15 17:13 | 2013-10-15 17:16 | CARRIER - 48G2N048090301-- | 81 | 4.3 | Yes | Yes | 22.5 | 20.9 | 1.6 | D7B002B417784FCFA13F268A9286C177 |  | R22 | Non-TXV |  | 5.309% | 0.94691 | 10.2% | [5 empty] | Non-TXV | 5.309%
Bakersfield | CA | 93308-1138 |  | 2013-09-26 | 2013-09-26 09:57 | 2013-09-26 09:57 | RHEEM - RRKAA036JK06X | 62 | 0 | Yes | Yes | 21 | 18.8 | 2.2 | 0CC703DF7E204947B1343801C53C63C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7625 |  | 2013-10-07 | 2013-10-07 19:54 | 2013-10-07 19:54 | BDP - 561CJ024B | 52 | 0 | Yes | Yes | 21 | 21.8 | -0.8 | C20E5FD68C1A43C0AC5DDE2F791415AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9109 |  | 2013-10-13 | 2013-10-13 13:24 | 2013-10-13 13:29 | OTHER - 38BRC060360 | 206 | -4.5 | Yes | Yes | 26.5 | 21.3 | 5.3 | 4FC54DBDB69447C797AC0897FF77F687 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | -2.184% | 1.0218 | 0.6118% |  |  |  |  | Non-TXV |  |  | -2.184%
Bakersfield | CA | 93308-7629 |  | 2013-10-08 | 2013-10-08 10:22 | 2013-10-08 10:22 | BDP - 561CJ024B | 56 | 0 | Yes | Yes | 21.1 | 19.1 | 2 | 35C19906333D4F97A7F58293EBB456E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5630 |  | 2013-10-08 | 2013-10-08 12:53 | 2013-10-08 12:53 | RHEEM - RRNAB036JK06X | 83 | 0 | Yes | Yes | 19.6 | 22 | -2.4 | 4B9B26A7844E4164A2E3B316984B01F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7626 |  | 2013-10-10 | 2013-10-10 17:49 | 2013-10-10 17:49 | BDP - 561CJ024-B | 56 | 0 | Yes | Yes | 19.4 | 19.9 | -0.5 | B532CFF15D294F5999951DECBB76A2F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7626 |  | 2013-10-08 | 2013-10-08 10:40 | 2013-10-08 10:40 | BDP - 561CJ030B | 85 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | F1424F74D2D444B885189A03FC182D6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7626 |  | 2013-10-08 | 2013-10-08 12:50 | 2013-10-08 12:50 | BDP - 561CJ018B | 52 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | C3ADCDB72BB741A1B1E19E66AEE65A0F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1122 |  | 2013-10-22 | 2013-10-22 14:49 | 2013-10-22 14:49 | PAYNE - UKN | 90 | 0 | Yes | Yes | 23.2 | 22 | 1.2 | 8FDAC5A615CE4AD6B5135FE11BF913F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3202 |  | 2013-10-13 | 2013-10-13 13:41 | 2013-10-13 13:46 | OTHER - AC042X1021A | 100 | 5.5 | Yes | Yes | 22.8 | 20.8 | 2 | 227DD92AD61641F68D673782EB3EF796 |  | R22 | TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | TXV | 5.5%
Bakersfield | CA | 93308-7625 |  | 2013-10-07 | 2013-10-07 18:52 | 2013-10-07 18:52 | BDP - 561CJ024B | 56 | 0 | Yes | Yes | 19.5 | 19.9 | -0.4 | 4423F7F36EC24B389D355316277AE938 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7625 |  | 2013-10-07 | 2013-10-07 19:13 | 2013-10-07 19:13 | GOODMAN - GSC130301EA | 82 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | 92210EC7717E481FBE6A4D89A6256934 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7625 |  | 2013-10-07 | 2013-10-07 19:27 | 2013-10-07 19:27 | BDP - 561CJ018B | 52 | 0 | Yes | Yes | 20.8 | 19.8 | 1 | D76ED0674393464CB30D5A9FF810C79B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1803 |  | 2013-09-26 | 2013-09-26 19:18 | 2013-09-26 19:20 | OTHER - 597BN048-A | 220 | -10.6 | Yes | Yes | 25.1 | 19.4 | 5.8 | FCCE88444E1D4C8595CB49F01F90F8C2 |  | R22 | TXV |  | -4.818% | 1.0482 | 1.349% |  |  |  |  | TXV |  |  | -4.818%
Bakersfield | CA | 93308-7629 |  | 2013-10-08 | 2013-10-08 09:50 | 2013-10-08 10:07 | BDP - 561CJ024B | 56 | 3 | Yes | Yes | 21.5 | 19.4 | 2.1 | CEDB7CCACB4843E083EC65533FE3325E |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Vallejo | CA | 94589-2769 |  | 2013-10-10 | 2013-10-10 15:09 | 2013-10-10 15:09 | YORK - GCGD24S41S3A | 61 | 0 | Yes | Yes | 21.7 | 15.8 | 5.9 | 43885968CBFE4C5DAD32D10FFFC2B1F0 |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6309 |  | 2013-10-25 | 2013-10-25 10:41 | 2013-10-25 10:42 | AMERICAN STANDARD - 7A0048100A1 | 97 | -6.8 | Yes | Yes | 16.8 | 17.5 | -0.7 | 23839283660944F4B8AB9ECE9FF4D337 |  | R22 | Non-TXV |  | -7.01% | 1.0701 | 1.963% |  |  |  |  | Non-TXV |  |  | -7.01%
Bakersfield | CA | 93313-5128 |  | 2013-10-13 | 2013-10-13 14:13 | 2013-10-13 14:13 | OTHER - H1RD042S06G | 150 | 0 | Yes | Yes | 23.6 | 21 | 2.6 | 048666E9E4E34DF1AECABE4BD0433A4F | Actual Subcooling cannot be negative. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1102 |  | 2013-10-01 | 2013-10-01 11:38 | 2013-10-01 12:15 | JANITROL - UNK | 84 | -5.9 | Yes | Yes | 21.1 | 20.7 | 0.4 | 6BC23AEBBCE24836A74A2602C4C5D766 |  | R410A | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Fresno | CA | 93727-1943 |  | 2013-10-21 | 2013-10-21 14:29 | 2013-10-21 14:29 | RHEEM - RRPLB042JK08X | 112 | 0 | Yes | Yes | 21.7 | 20.2 | 1.6 | 390C65A840604EC2A0D8C0838EDDEE82 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5372 |  | 2013-10-10 | 2013-10-10 18:21 | 2013-10-10 18:23 | LENNOX - 13ACD-042-230-02 | 111 | 6.5 | Yes | Yes | 22.1 | 21.2 | 0.9 | E0DCBC0E91744FB28ECDC95DE535378F |  | R22 | TXV |  | 5.856% | 0.94144 | 11.25% | [5 empty] | TXV | 5.856%
San Jose | CA | 95124-2505 |  | 2013-09-26 | 2013-09-26 14:13 | 2013-09-26 14:34 | GUARDIAN - UNK | 80 | 16.6 | Yes | Yes | 22 | 20.4 | 1.6 | 09AB4FE0F17F4AA397BDACA93513DF8B |  | R22 | Non-TXV |  | 20.75% | 0.7925 | 39.88% | [5 empty] | Non-TXV | 20.75%
Wasco | CA | 93280-2596 |  | 2013-10-31 | 2013-10-31 18:08 | 2013-10-31 18:10 | OTHER - WCA3362GKR1 | 85 | 4.5 | Yes | Yes | 24.5 | 20.4 | 4.1 | 70A79CE0AA4740C4B916BE314C341C82 |  | R22 | TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | TXV | 5.294%
Clovis | CA | 93612-4485 |  | 2013-10-11 | 2013-10-11 11:45 | 2013-10-11 11:45 | RHEEM - RRNAB036JK06X | 83 | 0 | Yes | Yes | 21.9 | 19.3 | 2.6 | E357459C45E14AB8A333403EFA17CFBF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2595 |  | 2013-11-11 | 2013-11-11 16:14 | 2013-11-11 16:18 | OTHER - CCU12A30A-1 | 90 | -4.3 | Yes | Yes | 23.7 | 20.7 | 3.1 | D28B52AAAC244880A3928EA0F8BB88C4 |  | R22 | Non-TXV |  | -4.778% | 1.0478 | 1.338% |  |  |  |  | Non-TXV |  |  | -4.778%
Bakersfield | CA | 93311-2871 |  | 2013-10-02 | 2013-10-02 13:41 | 2013-10-02 13:59 | GOODMAN - GSC1300601CB | 131 | 9.6 | Yes | Yes | 22.6 | 22.4 | 0.3 | B26F0F006F0C49C2970CE0FE34534063 |  | R22 | Non-TXV |  | 7.328% | 0.92672 | 14.08% | [5 empty] | Non-TXV | 7.328%
Bakersfield | CA | 93313-5058 |  | 2013-10-09 | 2013-10-09 07:13 | 2013-10-09 07:56 | BRYANT - 113ANA048-E | 85 | 4.1 | Yes | Yes | 18.8 | 21.8 | -3 | 90DA9B49CD12488AA37E5636AB12E201 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Wasco | CA | 93280-2595 |  | 2013-11-11 | 2013-11-11 16:50 | 2013-11-11 16:52 | OTHER - CCU12A30A-1 | 90 | 0 | Yes | Yes | 17 | 21.5 | -4.5 | 6277C750606A4C0B8F91A95501404871 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2596 |  | 2013-11-04 | 2013-11-04 15:40 | 2013-11-04 15:42 | OTHER - CCUA12A30A-1 | 90 | 4.1 | Yes | Yes | 21.6 | 19.7 | 1.9 | DDC79C274AB8483599EF458185F76124 |  | R22 | Non-TXV |  | 4.556% | 0.95444 | 8.755% | [5 empty] | Non-TXV | 4.556%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 11:36 | 2013-10-09 11:36 | BDP - 561CJ024-A | 61 | 0 | Yes | Yes | 22.3 | 22 | 0.3 | 28BD337CF7F442308177598B4D183F39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 11:19 | 2013-10-09 11:19 | BDP - 561CJ024-A | 61 | 0 | Yes | Yes | 21.3 | 21.6 | -0.3 | 866EC8807ED44FF3835431559EC13E7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 16:20 | 2013-10-07 16:20 | BDP - 561CJ024-A | 65 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | D099EA2F841E41ECAED46FFE9054FA20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7627 |  | 2013-10-09 | 2013-10-09 13:26 | 2013-10-09 13:26 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 21.4 | 20.9 | 0.5 | EFF2F45964724C5CA05A38E08BCD7745 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3214 |  | 2013-10-02 | 2013-10-02 17:40 | 2013-10-02 17:40 | YORK - AC042X021A | 84 | 0 | Yes | Yes | 21.7 | 20.9 | 0.8 | 1C73DC71EC124CAD9A2693F88E73776A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7628 |  | 2013-10-07 | 2013-10-07 16:38 | 2013-10-07 16:38 | BDP - 561CJ024-A | 58 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 2A01346908694545AB361FB3ABC9901C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7629 |  | 2013-10-07 | 2013-10-07 18:10 | 2013-10-07 18:10 | BDP - 561CJ030B | 68 | 0 | Yes | Yes | 20.7 | 19.3 | 1.4 | EFD08F93A98749D3BFA04EC3BE1075C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7624 |  | 2013-10-07 | 2013-10-07 16:04 | 2013-10-07 16:04 | BDP - 2485E13140 | 65 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | E40356DD1F164719ACD250941A301CFE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7627 |  | 2013-10-09 | 2013-10-09 11:04 | 2013-10-09 11:04 | BDP - 561CJ024-A | 61 | 0 | Yes | Yes | 20.4 | 21.5 | -1.1 | 9B22D4BA6AC145F688AFFE4E1A16B38B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7629 |  | 2013-10-07 | 2013-10-07 18:27 | 2013-10-07 18:27 | BDP - 561CJ130B | 68 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | 714B5C0C045F4EEAA2165A61A910C2F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 12:40 | 2013-10-09 12:40 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | 1226C216DCDF4CBF8F18274D86253196 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1336 |  | 2013-10-15 | 2013-10-15 18:35 | 2013-10-15 18:37 | RHEEM - URMA-A042JK08E | 114 | 13.3 | Yes | Yes | 25 | 20.4 | 4.6 | 8C252BA6F69749CFB4EC0B240DADB7F0 |  | R22 | TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | TXV | 11.67%
Bakersfield | CA | 93308-7626 |  | 2013-10-09 | 2013-10-09 15:42 | 2013-10-09 15:42 | BDP - 561CJ030A | 68 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 786B9216EAC14DA4B1573A3564B87965 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7627 |  | 2013-10-09 | 2013-10-09 13:51 | 2013-10-09 13:51 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 20.3 | 21.3 | -1 | ABEC9BD62CC547558882489FAABAAD26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2595 |  | 2013-11-04 | 2013-11-04 15:44 | 2013-11-04 15:46 | OTHER - CCU12A-1 | 90 | 9.4 | Yes | Yes | 21.9 | 20.2 | 1.7 | DBD8B7C079064BFCB9A1C3BF29333529 |  | R22 | Non-TXV |  | 10.44% | 0.89556 | 20.07% | [5 empty] | Non-TXV | 10.44%
Fresno | CA | 93722-1121 |  | 2013-10-04 | 2013-10-04 16:18 | 2013-10-04 16:35 | CARRIER - UNK | 74 | 4.7 | Yes | Yes | 25.5 | 21.3 | 4.2 | 7B8A88774E57429384CDD83F81699C0F |  | R22 | Non-TXV |  | 6.351% | 0.93649 | 12.21% | [5 empty] | Non-TXV | 6.351%
Sanger | CA | 93657-2717 |  | 2013-10-07 | 2013-10-07 15:12 | 2013-10-07 15:54 | BRYANT - 588ANW048100AFAG | 104 | 8.5 | Yes | Yes | 25 | 22.2 | 2.8 | E2707000F5944CE2A7EFAFC629ABFFCC |  | R22 | Non-TXV |  | 8.173% | 0.91827 | 15.71% | [5 empty] | Non-TXV | 8.173%
San Jose | CA | 95111-2650 |  | 2013-10-04 | 2013-10-04 12:03 | 2013-10-04 12:34 | TRANE - TTR036D100A0 | 79 | -6.5 | Yes | Yes | 22.6 | 19.8 | 2.8 | D6EC15D43249442AAF7824ECF4F72D52 |  | R22 | Non-TXV |  | -8.228% | 1.0823 | 2.304% |  |  |  |  | Non-TXV |  |  | -8.228%
Fresno | CA | 93705-4509 |  | 2013-10-04 | 2013-10-04 13:14 | 2013-10-04 14:04 | GOODMAN - PGB0240501 | 54 | 4.3 | Yes | Yes | 21.2 | 20.1 | 1.2 | 755C4AEBD7B74D029F039F5162D18C80 |  | R22 | Non-TXV |  | 7.963% | 0.92037 | 15.3% | [5 empty] | Non-TXV | 7.963%
San Jose | CA | 95135-1419 |  | 2013-10-22 | 2013-10-22 11:06 | 2013-10-22 11:35 | CARRIER - 48SND048090311 | 85 | 4.3 | Yes | Yes | 19.4 | 21.5 | -2.1 | 703F7001E3A84B9CAC77380C0DE51256 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Fresno | CA | 93703-2742 |  | 2013-10-31 | 2013-10-31 12:26 | 2013-10-31 12:51 | OTHER - UNK | 74 | 3.4 | Yes | Yes | 20.7 | 18.2 | 2.5 | 27F49A2025564A7B8A2B0519F0A5DC71 |  | R22 | Non-TXV |  | 4.595% | 0.95405 | 8.83% | [5 empty] | Non-TXV | 4.595%
San Jose | CA | 95124-2555 |  | 2013-10-01 | 2013-10-01 10:58 | 2013-10-01 11:34 | CARRIER - 38CKC030300 | 73 | 3.1 | Yes | Yes | 20 | 21.4 | -1.4 | 929ABEC4E4F54D59AFBE9F22A5549F79 |  | R22 | Non-TXV |  | 4.247% | 0.95753 | 8.161% | [5 empty] | Non-TXV | 4.247%
Fresno | CA | 93702-2158 |  | 2013-10-12 | 2013-10-12 10:15 | 2013-10-12 10:42 | OTHER - PGF336060K01A1 | 176 | -16.6 | Yes | Yes | 25.5 | 19.5 | 6 | B62A10ED724E4B15A0EB6B01871E9E43 |  | R22 | Non-TXV |  | -9.432% | 1.0943 | 2.641% |  |  |  |  | Non-TXV |  |  | -9.432%
Clovis | CA | 93611-6089 |  | 2013-10-07 | 2013-10-07 18:11 | 2013-10-07 18:29 | COLEMAN - ERCS0361BA | 145 | 6.4 | Yes | Yes | 21.2 | 21.2 | 0 | FA2515370DEE42E4BF727F03C09074B2 |  | R22 | Non-TXV |  | 4.414% | 0.95586 | 8.482% | [5 empty] | Non-TXV | 4.414%
Clovis | CA | 93611-6089 |  | 2013-10-07 | 2013-10-07 18:32 | 2013-10-07 20:52 | COLEMAN - ERCS0481CAG | 227 | 6.7 | Yes | Yes | 22.6 | 21.5 | 1.1 | 88E2C57D4AF344A2883C9B33EBF3E526 |  | R22 | Non-TXV |  | 2.952% | 0.97048 | 5.672% | [5 empty] | Non-TXV | 2.952%
Bakersfield | CA | 93311-2723 |  | 2013-10-24 | 2013-10-24 13:00 | 2013-10-24 13:00 | PAYNE - PYPNA048090NB | 196 | 0 | Yes | Yes | 19.5 | 20.9 | -1.4 | 87013E9FB6904E209A63B017F0A44990 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2596 |  | 2013-11-11 | 2013-11-11 16:43 | 2013-11-11 16:46 | OTHER - CCU12A36A-1 | 90 | 5.5 | Yes | Yes | 25.5 | 19.7 | 5.8 | 8AF6C95F9330462AAECD936B5D60647E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Pittsburg | CA | 94565-5723 |  | 2013-10-25 | 2013-10-25 11:50 | 2013-10-25 11:52 | TEMPSTAR - N2A342AKA300 | 104 | -9.8 | Yes | Yes | 17 | 17 | 0 | EDE0700BC4CA4052A791468EA1302649 |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Vacaville | CA | 95687-7228 |  | 2013-10-08 | 2013-10-08 12:25 | 2013-10-08 12:51 | RUUD - UAKA-048JAZ | 85 | 3.5 | Yes | Yes | 20.8 | 15.5 | 5.3 | 7C8BF704BE114621B60D97984ABC0481 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Wasco | CA | 93280-2596 |  | 2013-11-04 | 2013-11-04 15:34 | 2013-11-04 15:37 | OTHER - CCU12A36A-1 | 94 | -6.6 | Yes | Yes | 22.2 | 19.7 | 2.5 | A1765FE60DCC42CC9BB9D0FA37884AAB |  | R22 | Non-TXV |  | -7.021% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.021%
Fresno | CA | 93703-4303 |  | 2013-10-21 | 2013-10-21 16:49 | 2013-10-21 16:49 | - | 85 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 41712C3E9D4E4CDFA97008550CF8063B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-3002 |  | 2013-10-21 | 2013-10-21 13:15 | 2013-10-21 13:31 | RHEEM - RAKA 042JAZ | 79 | 4 | Yes | Yes | 23 | 21.3 | 1.7 | AE5E6958C19649B19EC2BCAAF5B2DBE5 |  | R22 | Non-TXV |  | 5.063% | 0.94937 | 9.731% | [5 empty] | Non-TXV | 5.063%
Wasco | CA | 93280-2592 |  | 2013-10-31 | 2013-10-31 18:38 | 2013-10-31 18:40 | OTHER - CCU12A30A-1 | 90 | -10.4 | Yes | Yes | 21.1 | 19.5 | 1.6 | 0C70194CCD5541E58F58046645D5520F |  | R22 | TXV |  | -11.56% | 1.1156 | 3.236% |  |  |  |  | TXV |  |  | -11.56%
Fresno | CA | 93703-2748 |  | 2013-10-31 | 2013-10-31 13:22 | 2013-10-31 13:41 | LENNOX - 13GCSXA36068X2301A | 125 | 5 | Yes | Yes | 21.3 | 18.7 | 2.6 | 496FDC983A484FF8AC0A19B45EA00BBF |  | R410A | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93722-6878 |  | 2013-10-04 | 2013-10-04 14:31 | 2013-10-04 14:55 | LENNOX - 12ACB424P | 125 | 7 | Yes | Yes | 24.4 | 21.2 | 3.2 | BDCC5AA9B70F457BAFDD8F81DE96AEEB |  | R22 | Non-TXV |  | 5.6% | 0.944 | 10.76% | [5 empty] | Non-TXV | 5.6%
San Jose | CA | 95127-1455 |  | 2013-10-07 | 2013-10-07 14:49 | 2013-10-07 15:14 | YORK - H1RA048S06D | 117 | 6.1 | Yes | Yes | 26.1 | 20.3 | 5.8 | C6397DFC1CD64FD3B983F35B2AE4C656 |  | R22 | Non-TXV |  | 5.214% | 0.94786 | 10.02% | [5 empty] | Non-TXV | 5.214%
Bakersfield | CA | 93313-3397 |  | 2013-10-08 | 2013-10-08 23:49 | 2013-10-09 00:06 | RHEEM - UNK | 85 | 5.8 | Yes | Yes | 16.5 | 19.5 | -3 | FE21F2DB0A8044BABA7E46F48B76CB72 |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Bakersfield | CA | 93311-9121 |  | 2013-10-04 | 2013-10-04 10:46 | 2013-10-04 10:46 | CARRIER - 38BRC030320 | 100 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | EB5C54E8D4594A94B1D38E20D9127270 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9121 |  | 2013-10-04 | 2013-10-04 10:53 | 2013-10-04 10:53 | CARRIER - 38BRC030320 | 100 | 0 | Yes | Yes | 20.1 | 21 | -0.9 | D27C95DDBF2B4DC888D297F05C0AE692 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2715 |  | 2013-10-04 | 2013-10-04 17:11 | 2013-10-04 17:28 | AMANA - APG133360701AC | 112 | 10.3 | Yes | Yes | 21.9 | 22.1 | -0.2 | BA1CEF76FA5240F09111F60E80EA184D |  | R22 | Non-TXV |  | 9.196% | 0.90804 | 17.67% | [5 empty] | Non-TXV | 9.196%
Fresno | CA | 93727-7944 |  | 2013-10-17 | 2013-10-17 15:28 | 2013-10-17 16:14 | LENNOX - 13ACD06023002 | 214 | 9.1 | Yes | Yes | 23.9 | 21.2 | 2.7 | EBC0AAA6920148C095C7D83A28E48050 |  | R22 | TXV |  | 4.252% | 0.95748 | 8.172% | [5 empty] | TXV | 4.252%
Fresno | CA | 93722-9136 |  | 2013-10-09 | 2013-10-09 16:05 | 2013-10-09 16:25 | BDP - 585EJ036075 | 82 | 2.5 | Yes | Yes | 26.6 | 20.6 | 6 | 0BEB931BEE0F4C19BE2394810FB455BE |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Fresno | CA | 93705-4121 |  | 2013-10-09 | 2013-10-09 12:43 | 2013-10-09 13:05 | YORK - DBPYF036N070A | 108 | 4.5 | Yes | Yes | 22.6 | 19.1 | 3.5 | FCF430F4BE644FECA1F14EDD98315A32 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Bakersfield | CA | 93309-1372 |  | 2013-09-27 | 2013-09-27 11:53 | 2013-09-27 12:30 | ICP - PGF042K080E | 86 | 8.5 | Yes | Yes | 18.7 | 20.6 | -1.9 | 59C1EA03646B4E759FDA5447060D236D |  | R22 | Non-TXV |  | 9.884% | 0.90116 | 18.99% | [5 empty] | Non-TXV | 9.884%
Fresno | CA | 93722-7700 |  | 2013-10-09 | 2013-10-09 14:05 | 2013-10-09 14:22 | LENNOX - GCS26X-042-75-2PA | 133 | 4 | Yes | Yes | 24.5 | 19.9 | 4.6 | C851A5F67B4546AC84E8933F026AADF1 |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Wasco | CA | 93280-2592 |  | 2013-10-31 | 2013-10-31 18:47 | 2013-10-31 18:49 | OTHER - CCU12A30A-1 | 90 | -4.3 | Yes | Yes | 22.7 | 20.2 | 2.5 | EB3F734E76FF4BF1A2A724C4CE6F7A91 |  | R22 | TXV |  | -4.778% | 1.0478 | 1.338% |  |  |  |  | TXV |  |  | -4.778%
Fresno | CA | 93726-6516 |  | 2013-10-04 | 2013-10-04 09:58 | 2013-10-04 09:58 | DAY & NIGHT - 585A036090YAC | 76 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 171E43722264456D8877A2A95637959A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2232 |  | 2013-10-09 | 2013-10-09 10:17 | 2013-10-09 10:17 | TEMPSTAR - CA5524VKD3 | 85 | 0 | Yes | Yes | 20.2 | 17 | 3.2 | 116362B9247E4983B93EE86E45D22273 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2748 |  | 2013-10-31 | 2013-10-31 14:10 | 2013-10-31 14:29 | YORK - DCYZF024N045C | 58 | 4.4 | Yes | Yes | 21.3 | 18.2 | 3.1 | 0ED3674B71AE4033BC24EFAFCC3CED22 |  | R410A | Non-TXV |  | 7.586% | 0.92414 | 14.58% | [5 empty] | Non-TXV | 7.586%
Coalinga | CA | 93210-2203 |  | 2013-10-15 | 2013-10-15 16:03 | 2013-10-15 16:03 | GOODMAN - CPLJ361 | 129 | 0 | Yes | Yes | 22.7 | 19.6 | 3.1 | 592261E3157149CB81669F479E0741EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-0518 |  | 2013-10-21 | 2013-10-21 10:18 | 2013-10-21 10:19 | WEATHER KING - 13AJA24A01 | 77 | 5.2 | Yes | Yes | 17 | 17 | 0 | 20E1A0C7510445D289565C78CBD03F78 |  | R22 | Non-TXV |  | 6.753% | 0.93247 | 12.98% | [5 empty] | Non-TXV | 6.753%
Sanger | CA | 93657-8715 |  | 2013-10-18 | 2013-10-18 17:37 | 2013-10-18 17:37 | - | 85 | 0 | Yes | Yes | 35.5 | 21 | 14.5 | 7980684C2910404290BCCEBFE057482F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2855 |  | 2013-10-02 | 2013-10-02 12:35 | 2013-10-02 12:35 | YORK - H2RCO36S06G | 93 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 5C2FFFB1E9574973A7534D19FB6587EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2855 |  | 2013-10-02 | 2013-10-02 12:53 | 2013-10-02 12:53 | YORK - H2RCO360S06G | 88 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 8786CA24926B46398AF0D014B7E4D912 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kingsburg | CA | 93631-9214 |  | 2013-10-14 | 2013-10-14 12:08 | 2013-10-14 12:31 | OTHER - UNK | 90 | 2.6 | Yes | Yes | 20.7 | 18.2 | 2.5 | 42BFE425EAE64D719D35C4033EF41D3F |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Fresno | CA | 93705-2768 |  | 2013-10-09 | 2013-10-09 10:29 | 2013-10-09 11:22 | OTHER - N2A324AKA200 | 74 | 5.6 | Yes | Yes | 19.8 | 18.8 | 1 | E3BE7C49A4EF409D9BD9DAFF7C80C6FE |  | R22 | Non-TXV |  | 7.568% | 0.92432 | 14.54% | [5 empty] | Non-TXV | 7.568%
Fairfield | CA | 94534-7987 |  | 2013-10-08 | 2013-10-08 13:03 | 2013-10-08 16:24 | GOODMAN - CK24-10 | 65 | -3.1 | Yes | Yes | 12.5 | 14.7 | -2.2 | 3ABAF9B0F5354144882E2E2A9ED4652F |  | R22 | Non-TXV |  | -4.769% | 1.0477 | 1.336% |  |  |  |  | Non-TXV |  |  | -4.769%
Pittsburg | CA | 94565-4729 |  | 2013-10-18 | 2013-10-18 12:29 | 2013-10-18 12:30 | CARRIER - 38CKC036340 | 70 | 2.7 | Yes | Yes | 14.4 | 16.5 | -2.1 | 56F7CC4224E84BC4ADF9692AA8517467 |  | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
Bakersfield | CA | 93309-3058 |  | 2013-10-22 | 2013-10-22 16:46 | 2013-10-22 16:46 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | CABDC7A95D1A4C3E9CE1DCEDE06854AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3058 |  | 2013-10-22 | 2013-10-22 17:00 | 2013-10-22 17:00 | RUUD - UKN | 90 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 30F3F35CF83F4EB8AC1A2B1ED17E7792 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-5407 |  | 2013-10-07 | 2013-10-07 12:45 | 2013-10-07 13:05 | GOODMAN - SSX140601AE | 268 | 7.9 | Yes | Yes | 22.4 | 19.3 | 3.1 | 692D1F36ED24438F982EA13177328AF9 |  | R410A | Non-TXV |  | 2.948% | 0.97052 | 5.665% | [5 empty] | Non-TXV | 2.948%
Clovis | CA | 93612-2471 |  | 2013-10-11 | 2013-10-11 16:04 | 2013-10-11 20:59 | YORK - H2RA036S06E | 63 | 4.3 | Yes | Yes | 21.8 | 21 | 0.8 | 8BAED517357E427C93299E4704F1A096 |  | R22 | Non-TXV |  | 6.825% | 0.93175 | 13.12% | [5 empty] | Non-TXV | 6.825%
Fresno | CA | 93726-1502 |  | 2013-10-04 | 2013-10-04 09:15 | 2013-10-04 09:33 | GOODMAN - CKL36-1H | 71 | -4.2 | Yes | Yes | 18 | 19.7 | -1.7 | 5E07C48EAC884D758A74AC4BE1DEE6C2 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Kerman | CA | 93630-1934 |  | 2013-10-09 | 2013-10-09 09:48 | 2013-10-09 10:34 | BRYANT - 583ANW030040AAD | 69 | 3.4 | Yes | Yes | 20.7 | 19.8 | 0.9 | F91C21E1EC6F41C0A7E5C1646A79BF93 |  | R22 | Non-TXV |  | 4.928% | 0.95072 | 9.47% | [5 empty] | Non-TXV | 4.928%
Bakersfield | CA | 93312-5378 |  | 2013-10-07 | 2013-10-07 15:52 | 2013-10-07 16:20 | YORK - HIRC036S06D | 98 | 19.7 | Yes | Yes | 20.2 | 23.1 | -2.9 | 914AE60EE89E471F994698A40E7204FC |  | R22 | Non-TXV |  | 20.1% | 0.79898 | 38.63% | [5 empty] | Non-TXV | 20.1%
Fresno | CA | 93720-2541 |  | 2013-10-18 | 2013-10-18 15:15 | 2013-10-18 16:22 | ICP - PFC060K100D | 136 | 4 | Yes | Yes | 18.8 | 21.7 | -2.9 | 0DC22C49E948414AAA4725E66ACF07CF |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bay Point | CA | 94565-3419 |  | 2013-10-22 | 2013-10-22 13:29 | 2013-10-22 13:29 | - 563CN036-D | 104 | 0 | Yes | Yes | 14.3 | 17.1 | -2.8 | 2AD781A728584678AA1AC1447DE3CE18 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3308 |  | 2013-10-08 | 2013-10-08 13:35 | 2013-10-08 14:08 | PAYNE - PA13NR048-E | 184 | 6.1 | Yes | Yes | 20.6 | 23.6 | -3 | 5DA74352E727401DBE4D55CCF098B14E |  | R22 | Non-TXV |  | 3.315% | 0.96685 | 6.371% | [5 empty] | Non-TXV | 3.315%
Pittsburg | CA | 94565-6080 |  | 2013-10-18 | 2013-10-18 11:02 | 2013-10-18 11:05 | OTHER - 13ACD-048-230 | 120 | -8.5 | Yes | Yes | 16.2 | 17.3 | -1.1 | 75EFF8201A78466E83974082D91CF986 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Fairfield | CA | 94533-4266 |  | 2013-10-08 | 2013-10-08 16:24 | 2013-10-08 16:24 | PAYNE - | 85 | 0 | Yes | Yes | 16.5 | 18.7 | -2.2 | A3868DE667114DBCBCC1B3616A534EA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5793 |  | 2013-10-13 | 2013-10-13 13:56 | 2013-10-13 13:58 | GIBSON - JS3BA-036KA | 69 | 4.3 | Yes | Yes | 25 | 20.4 | 4.6 | 81C6BD48C6CA4E82993A89D431E1E93B |  | R22 | TXV |  | 6.232% | 0.93768 | 11.98% | [5 empty] | TXV | 6.232%
San Jose | CA | 95118-1731 |  | 2013-10-09 | 2013-10-09 13:54 | 2013-10-09 14:31 | ICP - HACO48AKC4 | 122 | 3.9 | Yes | Yes | 18.5 | 21.2 | -2.7 | E8A94AFD95254739A984E2589AE03CCB |  | R22 | Non-TXV |  | 3.197% | 0.96803 | 6.143% | [5 empty] | Non-TXV | 3.197%
Shafter | CA | 93263-3424 |  | 2013-10-22 | 2013-10-22 17:57 | 2013-10-22 17:59 | GOODMAN - PGB042075-1 | 68 | 5 | Yes | Yes | 24.5 | 19.7 | 4.8 | F8C735762BA24225A3742F412D01540F |  | R22 | Non-TXV |  | 7.353% | 0.92647 | 14.13% | [5 empty] | Non-TXV | 7.353%
Bakersfield | CA | 93309-3077 |  | 2013-10-24 | 2013-10-24 15:39 | 2013-10-24 15:56 | ICP - PGF324040K01 | 64 | 4.9 | Yes | Yes | 21.2 | 21.5 | -0.3 | 2C3819AA8FD84BD2B6D7050198C6D98E |  | R22 | Non-TXV |  | 7.656% | 0.92344 | 14.71% | [5 empty] | Non-TXV | 7.656%
San Jose | CA | 95130-1508 |  | 2013-10-14 | 2013-10-14 09:04 | 2013-10-14 10:05 | CARRIER - 24ACB436A300 | 111 | 9.7 | Yes | Yes | 24 | 18.9 | 5.1 | 1D636DD4F9004335A0F95E58F4E965E1 |  | R410A | TXV |  | 8.739% | 0.91261 | 16.79% | [5 empty] | TXV | 8.739%
Fresno | CA | 93727-6320 |  | 2013-10-05 | 2013-10-05 14:23 | 2013-10-05 14:40 | DAY & NIGHT - 24/60YAC1081 | 54 | 7.8 | Yes | Yes | 19 | 21.2 | -2.2 | D4B056DB046F41CE86B7024F891C561E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.44% | 0.85556 | 27.76% | [5 empty] | Non-TXV | 14.44%
Fresno | CA | 93727-6320 |  | 2013-10-05 | 2013-10-05 14:50 | 2013-10-05 15:07 | DAY & NIGHT - 24/60YAC1081 | 54 | -2.9 | Yes | Yes | 21.7 | 22.8 | -1.1 | B5E4D77654D541CE863C451E02E55EA3 |  | R22 | Non-TXV |  | -5.37% | 1.0537 | 1.504% |  |  |  |  | Non-TXV |  |  | -5.37%
Clovis | CA | 93611-8573 |  | 2013-10-07 | 2013-10-07 16:49 | 2013-10-07 17:08 | GOODMAN - UKN | 120 | 5 | Yes | Yes | 23.7 | 21.5 | 2.2 | 6FFF8D6FCA754111B5F436BFD6A8CB1C |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Clovis | CA | 93611-8573 |  | 2013-10-07 | 2013-10-07 17:11 | 2013-10-07 18:09 | GOODMAN - CKL421A | 95 | 4.7 | Yes | Yes | 23.2 | 21.8 | 1.5 | 794D48F1B8CA44CEA691FC7F3A52355D |  | R22 | TXV |  | 4.947% | 0.95053 | 9.508% | [5 empty] | TXV | 4.947%
Bakersfield | CA | 93305-3446 |  | 2013-10-16 | 2013-10-16 17:44 | 2013-10-16 17:44 | ICP - PGME24G040 | 73 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | 7318892348614881AB59F95724990F46 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6320 |  | 2013-10-05 | 2013-10-05 15:32 | 2013-10-05 15:32 | RHEEM - RRNL-B030JK06X | 76 | 0 | Yes | Yes | 20.8 | 20.8 | 0 | D93F99EFFFB248B7942BB805663B047D |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3448 |  | 2013-10-16 | 2013-10-16 16:52 | 2013-10-16 17:19 | GOODMAN - GPG13300451BB | 77 | 6.8 | Yes | Yes | 21.7 | 21 | 0.7 | A3CD5478F1604454B5A059E54691B25C |  | R22 | Non-TXV |  | 8.831% | 0.91169 | 16.97% | [5 empty] | Non-TXV | 8.831%
Wasco | CA | 93280-1647 |  | 2013-10-07 | 2013-10-07 16:15 | 2013-10-07 16:18 | CARRIER - 48KHA042---321BF | 80 | 4 | Yes | Yes | 25.6 | 19.7 | 5.9 | F728B76C328D43DB9F6A18558FF36D5B |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Union City | CA | 94587-4105 |  | 2013-10-11 | 2013-10-11 13:23 | 2013-10-11 13:23 | YORK - H2RA036S06D | 63 | 0 | Yes | Yes | 21.3 | 17.5 | 3.8 | 5217D82AF6534456978BABFE37C5F910 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2716 |  | 2013-10-24 | 2013-10-24 19:38 | 2013-10-24 19:41 | TRANE - YCY060G1M0AD | 151 | 6.4 | Yes | Yes | 25.3 | 20.1 | 5.2 | 11636819824346789E66B33827E43292 |  | R22 | TXV |  | 4.238% | 0.95762 | 8.145% | [5 empty] | TXV | 4.238%
Wasco | CA | 93280-2316 |  | 2013-10-29 | 2013-10-29 19:19 | 2013-10-29 19:21 | CARRIER - N/A | 85 | -8 | Yes | Yes | 21.1 | 20.2 | 1 | 4517D04FB9D1477AA1F9F8A7C981BC76 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93727-7211 |  | 2013-10-08 | 2013-10-08 14:37 | 2013-10-08 14:37 | OTHER - UKN | 80 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 55E7C45F05FA4C56BE46A20F83EAD4A9 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3446 |  | 2013-10-16 | 2013-10-16 17:31 | 2013-10-16 17:31 | OTHER - 5SAW24106 | 72 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 743D4CD336D2478C94151E200C8D99D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-2242 |  | 2013-11-01 | 2013-11-01 12:48 | 2013-11-01 13:11 | DAY & NIGHT - UNK | 74 | 3.7 | Yes | Yes | 20.8 | 19.1 | 1.7 | DD33058EC2B547459A9E55C57F2FDED4 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Shafter | CA | 93263-1703 |  | 2013-10-08 | 2013-10-08 17:31 | 2013-10-08 17:36 | YORK - D3NZ03N03606NXA | 64 | -3.8 | Yes | Yes | 25.7 | 20.6 | 5.1 | 6B88BF5FAB164C788871E002CC961AA0 |  | R410A | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Gilroy | CA | 95020-3312 |  | 2013-10-22 | 2013-10-22 14:24 | 2013-10-22 14:58 | CARRIER - 38CKC060370 | 133 | 22.5 | Yes | Yes | 24.4 | 19.6 | 4.8 | 340976084649407983745AD836380526 |  | R22 | Non-TXV |  | 16.92% | 0.83083 | 32.51% | [5 empty] | Non-TXV | 16.92%
Gilroy | CA | 95020-3312 |  | 2013-10-22 | 2013-10-22 15:00 | 2013-10-22 15:36 | CARRIER - ILLEGIBLE | 95 | 3.1 | Yes | Yes | 25.5 | 21.3 | 4.2 | 0454E6FEC30540BBA3B7AE5FA210091B |  | R22 | Non-TXV |  | 3.263% | 0.96737 | 6.271% | [5 empty] | Non-TXV | 3.263%
Clovis | CA | 93611-4510 |  | 2013-10-07 | 2013-10-07 15:53 | 2013-10-07 15:53 | GOODMAN - PGB0360751A | 60 | 0 | Yes | Yes | 22.5 | 21.9 | 0.6 | 7C12AE09A46F495F91976DFD915B1537 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5209 |  | 2013-10-10 | 2013-10-10 18:14 | 2013-10-10 18:16 | YORK - H1RC0360S060 | 98 | 4.3 | Yes | Yes | 24 | 20.9 | 3.1 | 58A126E6EC7144B382AB89D5C3185C84 |  | R22 | TXV |  | 4.388% | 0.95612 | 8.432% | [5 empty] | TXV | 4.388%
Bakersfield | CA | 93309-3076 |  | 2013-10-24 | 2013-10-24 16:11 | 2013-10-24 16:11 | ICP - PGC024K040E | 54 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 621D4DB826834DE7A2C89ED4BB3817F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1337 |  | 2013-10-08 | 2013-10-08 10:25 | 2013-10-08 11:06 | UNITARY PRODUCTS GROUP - AC036X1021A | 63 | 4.1 | Yes | Yes | 21.1 | 21.4 | -0.3 | 08C7A8F282324CF998B249B63C819157 |  | R22 | Non-TXV |  | 6.508% | 0.93492 | 12.51% | [5 empty] | Non-TXV | 6.508%
San Jose | CA | 95136-1337 |  | 2013-10-07 | 2013-10-07 10:43 | 2013-10-07 11:06 | PAYNE - PA10JA042 C | 78 | 4.6 | Yes | Yes | 20.8 | 21.5 | -0.7 | 5C93E617333A49069F718206732E090B |  | R22 | Non-TXV |  | 5.897% | 0.94103 | 11.33% | [5 empty] | Non-TXV | 5.897%
Fresno | CA | 93703-2748 |  | 2013-10-31 | 2013-10-31 13:47 | 2013-10-31 14:06 | PAYNE - PY3NAA24040NA | 79 | -3.9 | Yes | Yes | 20.5 | 18 | 2.6 | E384E6DA680946D28918ACA0C27E5CC0 |  | R410A | Non-TXV |  | -4.937% | 1.0494 | 1.383% |  |  |  |  | Non-TXV |  |  | -4.937%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 14:23 | 2013-10-09 14:23 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | BA0FDE606A394C028E52FC7514C3E0D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7915 |  | 2013-10-04 | 2013-10-04 09:39 | 2013-10-04 09:58 | LENNOX - 10GCS036X753PA | 58 | 2.7 | Yes | Yes | 25.2 | 19.7 | 5.5 | E4D5682E043849FA8801B1A12466F0C1 |  | R22 | Non-TXV |  | 4.655% | 0.95345 | 8.946% | [5 empty] | Non-TXV | 4.655%
Bakersfield | CA | 93308-6470 |  | 2013-10-09 | 2013-10-09 10:55 | 2013-10-09 10:55 | RHEEM - RRNAB048JK10X | 153 | 0 | Yes | Yes | 19.7 | 19 | 0.7 | EF6FEA479A1E4C31A01AD2E857BBF1A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2765 |  | 2013-10-10 | 2013-10-10 11:00 | 2013-10-10 11:23 | OTHER - AC024X1321A | 88 | 5.5 | Yes | Yes | 18 | 17.7 | 0.3 | 8E068BF0018540858FEADC0F11DD6503 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Bakersfield | CA | 93304-4846 |  | 2013-10-15 | 2013-10-15 18:29 | 2013-10-15 18:31 | TRANE - 4YCC3024A1064AA | 93 | 3.9 | Yes | Yes | 25.3 | 20.1 | 5.2 | 6B1218210CFD4F9DA84BB60759FE5562 |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Wasco | CA | 93280-2682 |  | 2013-10-21 | 2013-10-21 19:02 | 2013-10-21 19:04 | OTHER - AC13B36P-1A | 139 | 10 | Yes | Yes | 22.7 | 19.8 | 2.9 | 8D0300520B7141698BDBCA63827449A3 |  | R22 | TXV |  | 7.194% | 0.92806 | 13.83% | [5 empty] | TXV | 7.194%
Fresno | CA | 93710-3834 |  | 2013-10-24 | 2013-10-24 12:04 | 2013-10-24 12:22 | PAYNE - UNK | 76 | 7 | Yes | Yes | 20.5 | 19.1 | 1.4 | 09BC099911284FC892378FC206E4335D |  | R22 | Non-TXV |  | 9.211% | 0.90789 | 17.7% | [5 empty] | Non-TXV | 9.211%
Fresno | CA | 93722-3146 |  | 2013-10-04 | 2013-10-04 10:58 | 2013-10-04 11:18 | CARRIER - 38CK024310 | 62 | 2.7 | Yes | Yes | 21.6 | 19.5 | 2.1 | E200C254459E47F897728828182FAF0D |  | R22 | Non-TXV |  | 4.355% | 0.95645 | 8.369% | [5 empty] | Non-TXV | 4.355%
Fresno | CA | 93705-2768 |  | 2013-10-09 | 2013-10-09 11:26 | 2013-10-09 12:40 | OTHER - AC024X1322B | 88 | 3.9 | Yes | Yes | 19.8 | 18.8 | 1 | F5411F0E4F1648438409D6AEB61B3E3E |  | R22 | Non-TXV |  | 4.432% | 0.95568 | 8.517% | [5 empty] | Non-TXV | 4.432%
Bakersfield | CA | 93308-2763 |  | 2013-10-09 | 2013-10-09 13:57 | 2013-10-09 13:57 | RHEEM - RRNLB060JK10X | 172 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | D67AE36D06A346859F0490564CFDC15C |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5146 |  | 2013-10-21 | 2013-10-21 10:05 | 2013-10-21 10:05 | YORK - H2RD048S06B | 134 | 0 | Yes | Yes | 21.5 | 19.9 | 1.6 | 1160820DDB274862A6BAB68E04C6EF1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1419 |  | 2013-10-17 | 2013-10-17 10:40 | 2013-10-17 11:38 | CARRIER - 48SDN048090311 | 196 | -13.8 | Yes | Yes | 21.8 | 20.8 | 1 | D8EFF03251FA47FDA28D8AAEC4EB4D8F |  | R22 | Non-TXV |  | -7.041% | 1.0704 | 1.972% |  |  |  |  | Non-TXV |  |  | -7.041%
Bakersfield | CA | 93308-7630 |  | 2013-10-09 | 2013-10-09 15:04 | 2013-10-09 15:04 | BDP - 561CJ030-A | 68 | 0 | Yes | Yes | 20.6 | 20.4 | 0.2 | 5217078ECB524D8B8574F0EED56C7AA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5515 |  | 2013-10-22 | 2013-10-22 09:56 | 2013-10-22 09:57 | AMERICAN STANDARD - 2A7A1036A1000AA | 73 | 2.7 | Yes | Yes | 17.6 | 17.6 | 0 | CAD46C650411411A89C90AF8DEAEEDEE |  | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Fairfield | CA | 94533-4267 |  | 2013-10-08 | 2013-10-08 14:36 | 2013-10-08 16:27 | PAYNE - 591ANX018000AAAA | 48 | -4.5 | Yes | Yes | 16.2 | 18.6 | -2.4 | B44F3A942BBD4F1F97DCFB5355E43997 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Fresno | CA | 93727-7106 |  | 2013-10-05 | 2013-10-05 11:39 | 2013-10-05 11:39 | RHEEM - RRKA-A060JK10X | 114 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | FBC485C80E2F43609E279A15E7A7682D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2040 |  | 2013-10-07 | 2013-10-07 11:06 | 2013-10-07 11:26 | DAY & NIGHT - 58CJ042075 | 104 | 19.4 | Yes | Yes | 26.2 | 20.3 | 6 | 5B1006EE98954797A8702E00EA349F4F |  | R22 | Non-TXV |  | 18.65% | 0.81346 | 35.85% | [5 empty] | Non-TXV | 18.65%
Hayward | CA | 94544-6715 |  | 2013-10-11 | 2013-10-11 10:49 | 2013-10-11 10:49 | RUUD - UAMB-060JAZ | 85 | 0 | Yes | Yes | 21.3 | 17 | 4.3 | 40B393EA77F74E3A8BD6AE13C888679F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5129 |  | 2013-10-07 | 2013-10-07 08:58 | 2013-10-07 09:25 | LENNOX - GCS26X-042-75-2PA | 133 | 3.9 | Yes | Yes | 21.8 | 20.1 | 1.7 | A21A7F5C47FF4435A5375FF54474F1F0 |  | R22 | Non-TXV |  | 2.932% | 0.97068 | 5.635% | [5 empty] | Non-TXV | 2.932%
Gilroy | CA | 95020-8300 |  | 2013-10-24 | 2013-10-24 10:40 | 2013-10-24 11:07 | BRYANT - 561CJ036-E | 72 | -6.8 | Yes | Yes | 19.9 | 20.8 | -0.9 | 278281C3636342A8AA99967F9DF4818C |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Gilroy | CA | 95020-8300 |  | 2013-10-24 | 2013-10-24 11:08 | 2013-10-24 11:48 | BRYANT - 561CJ036-E | 72 | 9.2 | Yes | Yes | 24 | 20.9 | 3.1 | 937451CED8AB4D41B504B287EAA6BEC7 |  | R22 | Non-TXV |  | 12.78% | 0.87222 | 24.56% | [5 empty] | Non-TXV | 12.78%
Fresno | CA | 93727-1836 |  | 2013-10-04 | 2013-10-04 15:34 | 2013-10-04 16:15 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 18.4 | 20.6 | -2.1 | 090478C3555242E685FAD351E7076113 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
San Jose | CA | 95123-0000 |  | 2013-10-10 | 2013-10-10 15:38 | 2013-10-10 16:05 | ICP - ILLEGIBLE | 72 | 2.8 | Yes | Yes | 21.9 | 20.8 | 1.2 | 050CD29C23C244B48053EF7D9AA2137A |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Wasco | CA | 93280-3600 |  | 2013-10-29 | 2013-10-29 18:39 | 2013-10-29 18:41 | GOODMAN - GPG10600901A | 100 | 6.6 | Yes | Yes | 25.7 | 20.4 | 5.3 | 3C3FA480529145F3B48F665A11DD3559 |  | R22 | Non-TXV |  | 6.6% | 0.934 | 12.68% | [5 empty] | Non-TXV | 6.6%
Lemoore | CA | 93245-2311 |  | 2013-10-11 | 2013-10-11 12:27 | 2013-10-11 12:46 | DAY & NIGHT - UNK | 92 | 19.1 | Yes | Yes | 21.2 | 19.1 | 2.1 | 5491A0E068B44E669C68E4A6168C9906 |  | R22 | Non-TXV |  | 20.76% | 0.79239 | 39.9% | [5 empty] | Non-TXV | 20.76%
Shafter | CA | 93263-0000 |  | 2013-10-08 | 2013-10-08 18:09 | 2013-10-08 18:11 | DAY & NIGHT - PGD33606K001C1 | 100 | 4.6 | Yes | Yes | 23.3 | 19.3 | 4 | 11DDE93E4AFB42DFAA810C0F273B2AAD |  | R410A | TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | TXV | 4.6%
Fairfield | CA | 94534-1030 |  | 2013-10-11 | 2013-10-11 13:34 | 2013-10-11 14:00 | PAYNE - 591ANX036000AAAA | 84 | -5.9 | Yes | Yes | 15.8 | 18.3 | -2.5 | E62CFFC37D98447BB7966708CBC6FFEB |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Fresno | CA | 93727-3652 |  | 2013-10-21 | 2013-10-21 15:00 | 2013-10-21 16:07 | LENNOX - 10GCS042751PA | 73 | 4.5 | Yes | Yes | 25.7 | 20.4 | 5.3 | 05FD9F823F444D0FA09B6FC03C7A525B |  | R22 | Non-TXV |  | 6.164% | 0.93836 | 11.85% | [5 empty] | Non-TXV | 6.164%
Sanger | CA | 93657-3431 |  | 2013-10-07 | 2013-10-07 13:46 | 2013-10-07 13:46 | OTHER - PGF33003060K01A1 | 157 | 0 | Yes | Yes | 0.2 | 22.4 | -22.2 | 4C20BF4C2D5E468BAB48DE0DDACF495D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-5310 |  | 2013-10-11 | 2013-10-11 11:46 | 2013-10-11 12:23 | LENNOX - UNK | 90 | -5.3 | Yes | Yes | 21.4 | 19.1 | 2.3 | A8B5D0AFA7D14054879F99FE201635B4 |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Sanger | CA | 93657-8878 |  | 2013-10-07 | 2013-10-07 17:07 | 2013-10-07 17:07 | CARRIER - 480L045 | 82 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 8F12DD8A1A6B4C928A83D904956FFEB1 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9336 |  | 2013-10-13 | 2013-10-13 13:49 | 2013-10-13 13:52 | TRANE - 2TTR2030A1000AA | 68 | 4.5 | Yes | Yes | 23.6 | 20.3 | 3.3 | 51581D009F464E50A0FFE410C8A5BBCA |  | R22 | TXV |  | 6.618% | 0.93382 | 12.72% | [5 empty] | TXV | 6.618%
San Jose | CA | 95136-1337 |  | 2013-10-07 | 2013-10-07 10:05 | 2013-10-07 10:41 | BARD - HYAC421 A | 88 | 4.3 | Yes | Yes | 25.3 | 21.5 | 3.8 | 7D8B0E75BBCE452292A51C7FC08DB3C0 |  | R22 | Non-TXV |  | 4.886% | 0.95114 | 9.391% | [5 empty] | Non-TXV | 4.886%
Fresno | CA | 93722-1101 |  | 2013-10-04 | 2013-10-04 13:12 | 2013-10-04 13:37 | OTHER - UNK | 68 | 6.2 | Yes | Yes | 21.3 | 19.5 | 1.8 | B5FD946256D0498B853578712B9FC448 |  | R22 | Non-TXV |  | 9.118% | 0.90882 | 17.52% | [5 empty] | Non-TXV | 9.118%
Fresno | CA | 93702-2345 |  | 2013-10-08 | 2013-10-08 12:20 | 2013-10-08 12:57 | YORK - D1NP036N05606A | 108 | 3.5 | Yes | Yes | 21.1 | 20.6 | 0.5 | 4D4DCCFECD5147EC985A579D3573BBD2 |  | R22 | Non-TXV |  | 3.241% | 0.96759 | 6.228% | [5 empty] | Non-TXV | 3.241%
Fresno | CA | 93705-2765 |  | 2013-10-29 | 2013-10-29 14:40 | 2013-10-29 15:12 | OTHER - AC024X131A | 86 | 5.4 | Yes | Yes | 21.8 | 19.3 | 2.5 | DF3CA33AD7F1409C88D67608A11754FE |  | R22 | Non-TXV |  | 6.279% | 0.93721 | 12.07% | [5 empty] | Non-TXV | 6.279%
Fresno | CA | 93701-1722 |  | 2013-10-08 | 2013-10-08 11:36 | 2013-10-08 12:07 | TEMPSTAR - PGD336060K001C1 | 102 | 3.7 | Yes | Yes | 21.4 | 19.6 | 1.9 | C7452E1234C04E22BEF3C28061BBB294 |  | R410A | Non-TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | Non-TXV | 3.627%
Vallejo | CA | 94589-2625 |  | 2013-10-10 | 2013-10-10 13:00 | 2013-10-10 13:00 | OTHER - CA55536VKD2 | 85 | 0 | Yes | Yes | 20.1 | 17.5 | 2.6 | 32E17006EB314B5CAA42DC0B7739058D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-2374 |  | 2013-10-18 | 2013-10-18 14:53 | 2013-10-18 14:53 | - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | CA9458FFBEBD4E89841DFBADCE28132D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3637 |  | 2013-10-07 | 2013-10-07 09:52 | 2013-10-07 10:39 | CARRIER - UNK | 80 | -4.7 | Yes | Yes | 30 | 20.1 | 9.9 | F6301480A624441F9AE8ED0A9F5150F3 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Clovis | CA | 93611-5150 |  | 2013-10-11 | 2013-10-11 14:41 | 2013-10-11 16:02 | DAY & NIGHT - 585EJ024050 | 54 | 3.8 | Yes | Yes | 21.2 | 20.7 | 0.5 | 57D30E4BB3554583962FCAACB4CC691B |  | R22 | Non-TXV |  | 7.037% | 0.92963 | 13.52% | [5 empty] | Non-TXV | 7.037%
Bakersfield | CA | 93311-8974 |  | 2013-10-13 | 2013-10-13 13:36 | 2013-10-13 13:38 | RHEEM - 13AJA42A01 | 121 | 7.3 | Yes | Yes | 23.1 | 20.9 | 2.2 | 817CDABF805F4AE3ACC0CB74F96C9B5B |  | R22 | TXV |  | 6.033% | 0.93967 | 11.59% | [5 empty] | TXV | 6.033%
Fresno | CA | 93705-2768 |  | 2013-10-10 | 2013-10-10 10:04 | 2013-10-10 10:53 | YORK - N2A324AKA200 | 72 | 2.8 | Yes | Yes | 20.9 | 19.1 | 1.9 | 642E41F8FCBD405C8E697BF5585CBFD1 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Wasco | CA | 93280-1712 |  | 2013-10-07 | 2013-10-07 16:08 | 2013-10-07 16:11 | WESTINGHOUSE - 36AW08OGD | 57 | 7.8 | Yes | Yes | 22.9 | 19.5 | 3.4 | EC195946AC814A3B8765186685057899 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.68% | 0.86316 | 26.3% | [5 empty] | Non-TXV | 13.68%
Wasco | CA | 93280-2593 |  | 2013-10-31 | 2013-10-31 17:55 | 2013-10-31 17:55 | OTHER - WCA3302GKR1 | 75 | 14.8 | Yes | Yes | -11.6 | 20.2 | -31.8 | 7D4E283F4585466F938339AF4379C1F9 | Add refrigerant: 14.8 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 19.73% | 0.80267 | 37.92% | [5 empty] | TXV | 19.73%
Fresno | CA | 93722-3624 |  | 2013-10-07 | 2013-10-07 14:21 | 2013-10-07 15:27 | CARRIER - UNK | 80 | 2.4 | Yes | Yes | 20.1 | 21.3 | -1.2 | 8F82E47C814D4CABB99CE8BC1950F161 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93308-2104 |  | 2013-10-09 | 2013-10-09 13:27 | 2013-10-09 13:27 | BRYANT - 583ANW036060AAAF | 82 | 0 | Yes | Yes | 20.4 | 20.7 | -0.3 | 6BE24DB72E994BA2A561A2A51AC7990A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1865 |  | 2013-10-10 | 2013-10-10 10:32 | 2013-10-10 10:33 | TRANE - BTD730A100A0 | 74 | 2.3 | Yes | Yes | 18.7 | 17.6 | 1.1 | DA03F551F5CB45CDAF62F3638BBE5D13 |  | R22 | Non-TXV |  | 3.108% | 0.96892 | 5.973% | [5 empty] | Non-TXV | 3.108%
Fresno | CA | 93706-3865 |  | 2013-10-14 | 2013-10-14 13:53 | 2013-10-14 13:53 | ICP - GPFM30K060E | 52 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 323A932FAC4F415081DA0515B741C9CA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3077 |  | 2013-10-24 | 2013-10-24 16:26 | 2013-10-24 16:26 | PAYNE - PY1PNB030040AAAA | 90 | 0 | Yes | Yes | 21 | 21.8 | -0.8 | AC38AD737B414C00AA4BCCCD1649C50C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4211 |  | 2013-10-14 | 2013-10-14 12:33 | 2013-10-14 16:45 | YORK - N2CB036506A | 91 | 3.9 | Yes | Yes | 20.4 | 19.9 | 0.5 | E9A9035D60374D2AA25451CB4121896D |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Fairfield | CA | 94533-2516 |  | 2013-10-10 | 2013-10-10 13:11 | 2013-10-10 13:12 | CARRIER - 38TKB030300 | 72 | -6.8 | Yes | Yes | 15.6 | 17 | -1.4 | 0ED34AF2CF7B4D2DACE147FE49E3DED4 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Wasco | CA | 93280-0000 |  | 2013-10-21 | 2013-10-21 18:57 | 2013-10-21 18:59 | OTHER - 2AC13B42P-1A | 146 | 9.4 | Yes | Yes | 23 | 19.8 | 3.2 | 2B3770B38F934417B4D4E929641211A6 |  | R22 | TXV |  | 6.438% | 0.93562 | 12.37% | [5 empty] | TXV | 6.438%
Wasco | CA | 93280-2683 |  | 2013-10-29 | 2013-10-29 18:30 | 2013-10-29 18:32 | OTHER - 2AC13B36P-1A | 139 | -14.2 | Yes | Yes | 23.1 | 20.2 | 2.9 | 8AF6BB5DDBE74CA3BBFF2A68DE96C021 |  | R22 | TXV |  | -10.22% | 1.1022 | 2.861% |  |  |  |  | TXV |  |  | -10.22%
Shafter | CA | 93263-2444 |  | 2013-10-24 | 2013-10-24 20:06 | 2013-10-24 20:08 | OTHER - CA55600KD1 | 150 | -23.3 | Yes | Yes | 22.4 | 19.3 | 3.1 | DC198C1BFEA14A80A0F9C6ACD1085736 |  | R22 | TXV |  | -15.53% | 1.1553 | 4.35% |  |  |  |  | TXV |  |  | -15.53%
Wasco | CA | 93280-2682 |  | 2013-10-29 | 2013-10-29 18:57 | 2013-10-29 18:59 | OTHER - 2AC13B36P-1A | 139 | 5.4 | Yes | Yes | 25.8 | 19.9 | 5.9 | 87F912B91BDB4F099ED72132879082ED |  | R22 | TXV |  | 3.885% | 0.96115 | 7.466% | [5 empty] | TXV | 3.885%
Clovis | CA | 93612-5809 |  | 2013-10-11 | 2013-10-11 11:13 | 2013-10-11 11:41 | DAY & NIGHT - 585HJ036060 | 102 | 3.1 | Yes | Yes | 20.9 | 19.3 | 1.6 | 93136EC0BC954B528EC9D68A511A486A |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Wasco | CA | 93280-0000 |  | 2013-10-07 | 2013-10-07 15:38 | 2013-10-07 15:43 | OTHER - 2AC13B36P-A1 | 139 | -6.9 | Yes | Yes | 20.6 | 20.8 | -0.2 | 4CB6FEE741C243D292571106FB0DEF00 |  | R22 | TXV |  | -4.964% | 1.0496 | 1.39% |  |  |  |  | TXV |  |  | -4.964%
Vacaville | CA | 95687-6906 |  | 2013-10-09 | 2013-10-09 10:20 | 2013-10-09 10:21 | CARRIER - 38CKC036340 | 70 | -5.8 | Yes | Yes | 16.6 | 17.5 | -0.9 | C75BD25EE4ED433FA29BA5765F00B684 |  | R22 | Non-TXV |  | -8.286% | 1.0829 | 2.32% |  |  |  |  | Non-TXV |  |  | -8.286%
Clovis | CA | 93612-0443 |  | 2013-10-11 | 2013-10-11 14:09 | 2013-10-11 14:39 | DAY & NIGHT - 585HJ030040 | 68 | 5.4 | Yes | Yes | 18.7 | 20.8 | -2.1 | 01B73DB1D36B49F8AAA5F117E2948019 |  | R22 | Non-TXV |  | 7.941% | 0.92059 | 15.26% | [5 empty] | Non-TXV | 7.941%
Sunnyvale | CA | 94086-5917 |  | 2013-10-07 | 2013-10-07 09:40 | 2013-10-07 10:07 | CARRIER - 38CKC036 | 84 | -5.9 | Yes | Yes | 21.1 | 19.9 | 1.2 | 4228BB0A1E234E7A8EF84A6F64CC05F6 |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Fresno | CA | 93722-2916 |  | 2013-10-07 | 2013-10-07 11:41 | 2013-10-07 12:13 | CARRIER - 48KLA136---300BE | 102 | 3 | Yes | Yes | 24.3 | 20.6 | 3.7 | 896F383D3F8245D78DB2D673561C73C2 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
San Jose | CA | 95135-1419 |  | 2013-10-22 | 2013-10-22 14:11 | 2013-10-22 14:36 | BDP - 588ANW030040AAAD | 52 | 2.7 | Yes | Yes | 22.2 | 21.5 | 0.7 | 794500944C5B41D69796BABD78373B20 |  | R22 | Non-TXV |  | 5.192% | 0.94808 | 9.978% | [5 empty] | Non-TXV | 5.192%
Union City | CA | 94587-2360 |  | 2013-10-11 | 2013-10-11 14:03 | 2013-10-11 14:03 | DAY & NIGHT - N2A336AKA200 | 160 | 0 | Yes | Yes | 20.1 | 16.8 | 3.4 | 03DD8DD793F8439E937A748F38E3A713 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3341 |  | 2013-10-21 | 2013-10-21 13:18 | 2013-10-21 13:19 | YORK - H2RD048S06B | 134 | -9.5 | Yes | Yes | 15.6 | 17 | -1.4 | DB9842BCCFB645B19589C384CE55D071 |  | R22 | Non-TXV |  | -7.09% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.09%
Fresno | CA | 93727-1941 |  | 2013-10-04 | 2013-10-04 14:06 | 2013-10-04 14:49 | OTHER - UKN | 80 | 10.8 | Yes | Yes | 20.3 | 20.4 | -0.1 | 06EBE90B82E3428A9FD16124809BD295 |  | R22 | Non-TXV |  | 13.5% | 0.865 | 25.94% | [5 empty] | Non-TXV | 13.5%
Fairfield | CA | 94533-1680 |  | 2013-10-16 | 2013-10-16 10:00 | 2013-10-16 13:08 | RHEEM - RAFD-042JBS | 79 | 2.7 | Yes | Yes | 16.4 | 19.3 | -2.9 | 1145363A9BEF45DBABDFE4A44F6FA4BD |  | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Shafter | CA | 93263-1763 |  | 2013-10-08 | 2013-10-08 17:39 | 2013-10-08 17:41 | OTHER - 561CJ036-D | 84 | -3.2 | Yes | Yes | 20.8 | 20.3 | 0.5 | BB31E47D782E4732AFD27EF1B3B71CFC |  | R22 | TXV |  | -3.81% | 1.0381 | 1.067% |  |  |  |  | TXV |  |  | -3.81%
Bakersfield | CA | 93306-2113 |  | 2013-10-11 | 2013-10-11 04:43 | 2013-10-11 05:01 | RHEEM - UNK | 85 | 3.7 | Yes | Yes | 16.6 | 19.6 | -3 | 7EEA185D92684CD4A2D08CA4F97B61A5 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Kerman | CA | 93630-1850 |  | 2013-10-09 | 2013-10-09 12:13 | 2013-10-09 14:46 | LENNOX - 13ACC02423002 | 81 | 3.1 | Yes | Yes | 18.5 | 19.3 | -0.8 | 456CE0BE15BC427489C6131A8978E9F5 |  | R22 | TXV |  | 3.827% | 0.96173 | 7.355% | [5 empty] | TXV | 3.827%
Fresno | CA | 93722-5604 |  | 2013-10-10 | 2013-10-10 14:56 | 2013-10-10 15:26 | OTHER - UNK | 80 | 2.4 | Yes | Yes | 24.7 | 19.9 | 4.8 | 1DCE34114BEB44BE96D5FD88BB2D8C55 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Wasco | CA | 93280-1218 |  | 2013-10-20 | 2013-10-20 17:39 | 2013-10-20 17:42 | YORK - D1NP036N05606NXA | 108 | 4.5 | Yes | Yes | 26.3 | 20.7 | 5.6 | 629ED7FA0A25499DB4D6240A40E86299 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Fresno | CA | 93727-1941 |  | 2013-10-04 | 2013-10-04 14:52 | 2013-10-04 15:57 | GOODMAN - GPG13420701AB | 107 | 5 | Yes | Yes | 24 | 20.2 | 3.9 | D10D5C2244A74923BE9E00936108888E |  | R22 | Non-TXV |  | 4.673% | 0.95327 | 8.98% | [5 empty] | Non-TXV | 4.673%
Shafter | CA | 93263-2441 |  | 2013-10-24 | 2013-10-24 20:13 | 2013-10-24 20:16 | OTHER - DBYP-FO42N080A | 150 | 6.2 | Yes | Yes | 24.9 | 20.4 | 4.5 | 1A2C9D3B61A04F1981B35063FD992F16 |  | R22 | Non-TXV |  | 4.133% | 0.95867 | 7.943% | [5 empty] | Non-TXV | 4.133%
Fresno | CA | 93722-4006 |  | 2013-10-04 | 2013-10-04 12:00 | 2013-10-04 12:33 | YORK - D3YS036N0456C | 78 | 4 | Yes | Yes | 21.2 | 19.1 | 2.1 | D9814274E64D474C99CB078A69D9116D |  | R22 | Non-TXV |  | 5.128% | 0.94872 | 9.855% | [5 empty] | Non-TXV | 5.128%
Fresno | CA | 93710-7004 |  | 2013-10-16 | 2013-10-16 10:53 | 2013-10-16 11:12 | GOODMAN - GPG1336045M41AB | 85 | 2.5 | Yes | Yes | 20 | 19.9 | 0.1 | 4B054A3C93F64214B8A8B7F0587CD360 |  | R410A | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Clovis | CA | 93611-6254 |  | 2013-10-22 | 2013-10-22 18:41 | 2013-10-22 18:57 | YORK - DAYPF042N080A | 150 | 13.9 | Yes | Yes | 23.7 | 19.1 | 4.6 | 19D576F9A54A4FA39877C7B4DEBDA5A7 |  | R22 | Non-TXV |  | 9.267% | 0.90733 | 17.81% | [5 empty] | Non-TXV | 9.267%
Wasco | CA | 93280-2595 |  | 2013-10-31 | 2013-10-31 18:31 | 2013-10-31 18:34 | OTHER - CCU12A30A-1 | 90 | -5.3 | Yes | Yes | 20.6 | 19.9 | 0.7 | 775621F4F7334D6D936632F24D670508 |  | R22 | TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | TXV |  |  | -5.889%
Clovis | CA | 93611-3140 |  | 2013-10-07 | 2013-10-07 09:35 | 2013-10-07 10:11 | GOODMAN - PGP0360751A | 60 | 3.5 | Yes | Yes | 20 | 19.7 | 0.3 | 882DEE3C0B494371916485621664F948 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Fresno | CA | 93727-1960 |  | 2013-10-04 | 2013-10-04 15:59 | 2013-10-04 19:33 | PAYNE - 594CN024A | 70 | 5.5 | Yes | Yes | 21.3 | 21 | 0.3 | E1B08F66221D471ABD4CC440DD666CBC |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Kerman | CA | 93630-1360 |  | 2013-10-10 | 2013-10-10 13:50 | 2013-10-10 14:55 | GOODMAN - GPG10240451A | 50 | 3.1 | Yes | Yes | 23.3 | 20.2 | 3.2 | 95B1A76AC1E348E9852E518772EF044E |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Shafter | CA | 93263-2434 |  | 2013-10-08 | 2013-10-08 18:16 | 2013-10-08 18:19 | CARRIER - 48SX-030060331AA | 69 | 5.6 | Yes | Yes | 19.8 | 19.3 | 0.5 | C110FF9D829F4ED8B43C3BFE7BEA4846 |  | R22 | TXV |  | 8.116% | 0.91884 | 15.6% | [5 empty] | TXV | 8.116%
Shafter | CA | 93263-2434 |  | 2013-10-08 | 2013-10-08 18:22 | 2013-10-08 18:22 | CARRIER - 48SX-42080321AA | 92 | 0 | Yes | Yes | 22.6 | 20.7 | 2 | 48D96FDE8136494DAA6C4579584A5963 | Add refrigerant: 12.4 oz Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2687 |  | 2013-10-20 | 2013-10-20 18:06 | 2013-10-20 18:13 | OTHER - 2AC13B36P-1A | 134 | 3.8 | Yes | Yes | 20.2 | 20.2 | 0 | AABA312DD6894109800CF5E91A9FDFC4 |  | R22 | TXV |  | 2.836% | 0.97164 | 5.45% | [5 empty] | TXV | 2.836%
Wasco | CA | 93280-2687 |  | 2013-10-20 | 2013-10-20 18:18 | 2013-10-20 18:19 | OTHER - 2HP13B24P-1A | 130 | 0 | Yes | Yes | 24.2 | 21.4 | 2.8 | 3199766F0A994A8780D529AD889498D7 | Remove refrigerant: 6.6 oz | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7721 |  | 2013-10-15 | 2013-10-15 18:03 | 2013-10-15 18:05 | YORK - D1NH036N05606C | 108 | 5.3 | Yes | Yes | 19 | 22 | -3 | F674501ED2A64855B4AAFB34DE1154E9 |  | R22 | Non-TXV |  | 4.907% | 0.95093 | 9.431% | [5 empty] | Non-TXV | 4.907%
Clovis | CA | 93612-0457 |  | 2013-10-07 | 2013-10-07 10:13 | 2013-10-07 15:47 | UNK - UNK | 85 | 4 | Yes | Yes | 20.3 | 19.8 | 0.5 | DE3A0FEB01E6479CBA55027FE7DD8E7D |  |  |  |  | 4.706% | 0.95294 | 9.044% | [5 empty] | 0 | 4.706%
Fresno | CA | 93727-1824 |  | 2013-10-14 | 2013-10-14 11:45 | 2013-10-14 12:31 | YORK - DAYAF036N070C | 67 | 0 | Yes | Yes | 16.2 | 20.1 | -3.9 | D729DA79A95048DE95FB31B3A84CB6D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3625 |  | 2013-10-07 | 2013-10-07 15:29 | 2013-10-07 15:29 | CARRIER - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 9617E7AFA4B242509E8C9CCE7E5D18AF | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2687 |  | 2013-10-07 | 2013-10-07 15:26 | 2013-10-07 15:28 | OTHER - 2AC13B48P-A | 203 | -7.4 | Yes | Yes | 24.2 | 21.5 | 2.7 | 0146096C56FF47FFAD63FD5EDC1516E6 |  | R22 | TXV |  | -3.645% | 1.0365 | 1.021% |  |  |  |  | TXV |  |  | -3.645%
Wasco | CA | 93280-2687 |  | 2013-10-07 | 2013-10-07 15:52 | 2013-10-07 16:01 | LENNOX - 13HP-018-230-01 | 102 | 8.3 | Yes | Yes | 24.7 | 22.6 | 2.1 | EF773DCB15E142ADA522F43146195068 |  | R22 | TXV |  | 8.137% | 0.91863 | 15.64% | [5 empty] | TXV | 8.137%
Fresno | CA | 93727-1931 |  | 2013-10-04 | 2013-10-04 16:17 | 2013-10-04 16:17 | OTHER - HAC036AKA1 | 80 | 9 | Yes | Yes | 28.3 | 20.4 | 7.9 | 3FC32902D8CC4E809132B34DF28F2130 | Add refrigerant: 9 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Kerman | CA | 93630-1965 |  | 2013-10-22 | 2013-10-22 14:27 | 2013-10-22 14:27 | CARRIER - 48GX030040301 | 71 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 4BB4C49442EE4D6DB0AA6AD28482D8A4 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3742 |  | 2013-10-09 | 2013-10-09 09:27 | 2013-10-09 09:45 | CARRIER - 48SX042080311AA | 91 | 3.2 | Yes | Yes | 24.4 | 19.1 | 5.3 | 6D06EE6104454F2EA9A9CB99F01FA0A9 |  | R22 | Non-TXV |  | 3.516% | 0.96484 | 6.758% | [5 empty] | Non-TXV | 3.516%
Wasco | CA | 93280-2596 |  | 2013-11-04 | 2013-11-04 15:26 | 2013-11-04 15:28 | OTHER - CCU12A30A-1 | 90 | 4.7 | Yes | Yes | 20.6 | 19.5 | 1.1 | 31ED5FCC5C5A4EC2A2315555E38EA36C |  | R22 | Non-TXV |  | 5.222% | 0.94778 | 10.04% | [5 empty] | Non-TXV | 5.222%
Kerman | CA | 93630-1850 |  | 2013-10-09 | 2013-10-09 11:48 | 2013-10-09 12:11 | LENNOX - 13ACC02423002 | 81 | 3.5 | Yes | Yes | 20.6 | 19.1 | 1.5 | E0FE355E41B74E339568393126ABB66E |  | R22 | TXV |  | 4.321% | 0.95679 | 8.304% | [5 empty] | TXV | 4.321%
Wasco | CA | 93280-2595 |  | 2013-11-04 | 2013-11-04 15:15 | 2013-11-04 15:19 | OTHER - CCU12A30A-1 | 90 | 3.4 | Yes | Yes | 17.1 | 19.7 | -2.6 | EF9677B639C647CFA6D758C5C7D1B816 |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Sanger | CA | 93657-2064 |  | 2013-10-21 | 2013-10-21 13:59 | 2013-10-21 14:24 | YORK - H1RA048596G | 117 | 12 | Yes | Yes | 20.5 | 19.9 | 0.6 | 1E86CC3F776A4A46A63C358B2BAED569 |  | R22 | Non-TXV |  | 10.26% | 0.89744 | 19.71% | [5 empty] | Non-TXV | 10.26%
Kerman | CA | 93630-1227 |  | 2013-10-10 | 2013-10-10 12:20 | 2013-10-10 12:20 | RHEEM - RRNLB030JK06X | 76 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | A36FF36963C2418FBE3FC26C0CC6BFB0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6430 |  | 2013-10-05 | 2013-10-05 12:50 | 2013-10-05 13:19 | CARRIER - 38BRB042300 | 131 | 35.8 | Yes | Yes | 29 | 21.2 | 7.8 | 0FF32211FFDD434CA0FA5230B85B992A | Add refrigerant: 29.9 oz | R22 | Non-TXV |  | 27.33% | 0.72672 | 52.52% | [5 empty] | Non-TXV | 27.33%
Bakersfield | CA | 93312-6845 |  | 2013-10-09 | 2013-10-09 17:31 | 2013-10-09 17:33 | LENNOX - 13ACD-048-230-02 | 204 | 11 | Yes | Yes | 25.8 | 21.4 | 4.4 | 11413338BE4048D9969B13290DEFD13D |  | R22 | TXV |  | 5.392% | 0.94608 | 10.36% | [5 empty] | TXV | 5.392%
Fairfield | CA | 94533-7772 |  | 2013-10-17 | 2013-10-17 11:32 | 2013-10-17 11:33 | RUUD - UAKA-037JAZ | 79 | 3.5 | Yes | Yes | 17.1 | 17.6 | -0.5 | 2F1AA360A0B9457781A094ABF25F2B99 |  | R22 | Non-TXV |  | 4.43% | 0.9557 | 8.514% | [5 empty] | Non-TXV | 4.43%
Fairfield | CA | 94533-7772 |  | 2013-10-17 | 2013-10-17 11:34 | 2013-10-17 11:34 | RUUD - UAKA-037JAZ | 79 | -5.6 | Yes | Yes | 17.4 | 17.6 | -0.2 | E5F6C139AEAB40AF98C5236CD15540A1 |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Pittsburg | CA | 94565-6029 |  | 2013-10-22 | 2013-10-22 11:03 | 2013-10-22 11:04 | CARRIER - 38TXA048330 | 173 | 7.1 | Yes | Yes | 15.9 | 17.3 | -1.4 | 43222840269F4BEC97A3801F12F254EC |  | R22 | Non-TXV |  | 4.104% | 0.95896 | 7.887% | [5 empty] | Non-TXV | 4.104%
Bakersfield | CA | 93309-6151 |  | 2013-10-10 | 2013-10-10 11:49 | 2013-10-10 11:49 | BRYANT - 582ANW0240600AAAD | 56 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 95AC92616EE44B3D9573E22531AD8BA2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1227 |  | 2013-10-09 | 2013-10-09 10:36 | 2013-10-09 10:36 | DAY & NIGHT - UKN | 76 | 0 | Yes | Yes | 21.5 | 19.1 | 2.4 | F53B74266332491FA88530B9DA1CF583 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Coalinga | CA | 93210-3223 |  | 2013-11-08 | 2013-11-08 18:15 | 2013-11-08 18:15 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F2FFFC7A649E4033A9EE77813D98BCA0 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6158 |  | 2013-10-10 | 2013-10-10 15:18 | 2013-10-10 15:18 | BRYANT - 582ANW024060AAAD | 56 | 0 | Yes | Yes | 21 | 21 | 0 | C6719376B4444781B0598371DFFF1F73 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3441 |  | 2013-10-14 | 2013-10-14 10:33 | 2013-10-14 11:11 | OTHER - UKN | 80 | 3 | Yes | Yes | 20.7 | 21.4 | -0.7 | A482E011D51645B29975085E0221FDE1 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Clovis | CA | 93612-3561 |  | 2013-10-22 | 2013-10-22 11:17 | 2013-10-22 11:46 | DUCANE - AC10B24 | 60 | -3.5 | Yes | Yes | 21.7 | 20.9 | 0.8 | 0BD2CE4A78AC4C29816F8859668F4500 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Kerman | CA | 93630-1850 |  | 2013-10-09 | 2013-10-09 11:22 | 2013-10-09 11:46 | LENNOX - 13ACC02423002 | 81 | 4 | Yes | Yes | 19.9 | 18.5 | 1.4 | AA655C6A29AA4EC8818B4CEBD055BF34 |  | R22 | TXV |  | 4.938% | 0.95062 | 9.49% | [5 empty] | TXV | 4.938%
Rio Vista | CA | 94571-2122 |  | 2013-10-21 | 2013-10-21 13:25 | 2013-10-21 15:03 | YORK - H2RC036S06A | 83 | -4.8 | Yes | Yes | 12.5 | 15.2 | -2.7 | 946897AAAC6F4909A1399BE950581854 |  | R22 | Non-TXV |  | -5.783% | 1.0578 | 1.62% |  |  |  |  | Non-TXV |  |  | -5.783%
Fresno | CA | 93701-1153 |  | 2013-10-08 | 2013-10-08 18:35 | 2013-10-08 18:35 | YORK - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | ACB992A20D07431692F3E44289832C77 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5508 |  | 2013-10-22 | 2013-10-22 10:37 | 2013-10-22 10:37 | PAYNE - PA13NA036-C | 70 | 0 | Yes | Yes | 17.1 | 17 | 0.1 | 15FA540CBE6B4C3B8B52B2241EC3B00F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-2101 |  | 2013-10-21 | 2013-10-21 13:43 | 2013-10-21 15:05 | YORK - H15C030S060 | 76 | 2.7 | Yes | Yes | 14 | 14.4 | -0.4 | C93BA989F7DC43049A03851247D6CCC5 |  | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Pittsburg | CA | 94565-2344 |  | 2013-10-22 | 2013-10-22 10:17 | 2013-10-22 10:17 | - 598ANX036000ABAA | 196 | 14.9 | Yes | Yes | 13.1 | 15.6 | -2.5 | 38F663871B744B5BBFDA739FA7FB0C00 | Add refrigerant: 14.9 oz | R22 | Non-TXV |  | 7.602% | 0.92398 | 14.61% | [5 empty] | Non-TXV | 7.602%
Fresno | CA | 93722-3077 |  | 2013-10-25 | 2013-10-25 12:00 | 2013-10-25 12:54 | RHEEM - FADC048JAS | 113 | 3.5 | Yes | Yes | 20.6 | 18.2 | 2.4 | C71D8600D91940A080F0EB96C6D6CF1E |  | R22 | Non-TXV |  | 3.097% | 0.96903 | 5.952% | [5 empty] | Non-TXV | 3.097%
Fresno | CA | 93704-4028 |  | 2013-10-24 | 2013-10-24 15:43 | 2013-10-24 16:02 | AMERICAN STANDARD - YCC036F1M0BJ | 85 | 2.5 | Yes | Yes | 20.9 | 19.1 | 1.8 | C9F456957D8C461686D8A8979B7FD2C1 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Rio Vista | CA | 94571-2118 |  | 2013-10-21 | 2013-10-21 14:12 | 2013-10-21 15:05 | YORK - H1RC030S06D | 76 | 3.3 | Yes | Yes | 13.9 | 16.9 | -3 | D25772D2E42F4C318A776FC61113DA34 |  | R22 | Non-TXV |  | 4.342% | 0.95658 | 8.345% | [5 empty] | Non-TXV | 4.342%
Fresno | CA | 93706-9044 |  | 2013-10-08 | 2013-10-08 10:24 | 2013-10-08 10:53 | OTHER - DBYA-F0360N0110D | 84 | 22.5 | Yes | Yes | 22.2 | 20.4 | 1.8 | 8FD1997C830A412EBF5180A34CD48571 |  | R22 | Non-TXV |  | 26.79% | 0.73214 | 51.48% | [5 empty] | Non-TXV | 26.79%
Clovis | CA | 93611-6913 |  | 2013-10-17 | 2013-10-17 10:06 | 2013-10-17 10:27 | YORK - H1DH036506B | 127 | 16.5 | Yes | Yes | 25.1 | 20.7 | 4.4 | AC096CB462BC4DA3AFAB947127050764 |  | R22 | Non-TXV |  | 12.99% | 0.87008 | 24.97% | [5 empty] | Non-TXV | 12.99%
Fresno | CA | 93703-3485 |  | 2013-10-14 | 2013-10-14 11:13 | 2013-10-14 11:13 | OTHER - GS2TPB1 | 60 | 0 | Yes | Yes | 21.7 | 20.6 | 1.2 | A6597901BBE84398AFE23643C1FDB2E5 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2879 |  | 2013-10-24 | 2013-10-24 19:14 | 2013-10-24 19:16 | RHEEM - RRGG-05N31JKR | 48 | 5.4 | Yes | Yes | 23.8 | 20.9 | 2.9 | 1598AEF7484E41CC8D13A2736C7FCAC5 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Lemoore | CA | 93245-3481 |  | 2013-11-08 | 2013-11-08 12:51 | 2013-11-08 14:00 | GOODMAN - UNK | 74 | 4.1 | Yes | Yes | 22.6 | 19.3 | 3.3 | EFC59D347BFF41348BA92DDD849DA8D8 |  | R22 | Non-TXV |  | 5.541% | 0.94459 | 10.65% | [5 empty] | Non-TXV | 5.541%
Shafter | CA | 93263-2906 |  | 2013-10-08 | 2013-10-08 17:55 | 2013-10-08 17:57 | COMFORT AIRE - PGF342080K01A1 | 184 | 8.7 | Yes | Yes | 25.2 | 21.2 | 4 | A6379DEC2D0245E184520C6B73780E2C |  | R22 | TXV |  | 4.728% | 0.95272 | 9.087% | [5 empty] | TXV | 4.728%
Shafter | CA | 93263-2906 |  | 2013-10-08 | 2013-10-08 18:02 | 2013-10-08 18:05 | COMFORT AIRE - PGF342080K01A1 | 184 | -7.4 | Yes | Yes | 26.1 | 20.4 | 5.7 | ACB5D32064324043BCB937F67283C8D6 |  | R22 | TXV |  | -4.022% | 1.0402 | 1.126% |  |  |  |  | TXV |  |  | -4.022%
Fresno | CA | 93725-1276 |  | 2013-10-08 | 2013-10-08 12:30 | 2013-10-08 13:02 | AMERICAN STANDARD - YCC036F1M0BJ | 83 | 7.2 | Yes | Yes | 23.2 | 20.2 | 3.1 | 40283AAA3CC04F41A9E339A365D7DCD5 |  | R22 | Non-TXV |  | 8.675% | 0.91325 | 16.67% | [5 empty] | Non-TXV | 8.675%
Fresno | CA | 93722-3069 |  | 2013-11-07 | 2013-11-07 22:39 | 2013-11-08 12:29 | WEATHER KING - 10AJA3001 | 70 | 4 | Yes | Yes | 21.8 | 20.2 | 1.7 | 03EF5AD1431A43FEAAC67733FD5BB9A7 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Fresno | CA | 93705-2768 |  | 2013-10-09 | 2013-10-09 13:41 | 2013-10-09 13:59 | YORK - AC024X1322B | 88 | 2.9 | Yes | Yes | 20.3 | 18.8 | 1.5 | D90D3B5D45C24E1184E8E57D2BDFA5B5 |  | R22 | Non-TXV |  | 3.295% | 0.96705 | 6.333% | [5 empty] | Non-TXV | 3.295%
Fresno | CA | 93727-5269 |  | 2013-10-05 | 2013-10-05 13:59 | 2013-10-05 14:20 | CARRIER - 24ABA360A300 | 151 | 8.8 | Yes | Yes | 24.5 | 18.9 | 5.6 | 77868E2C7FF54A458BF60F8F403AB2E0 |  | R410A | Non-TXV |  | 5.828% | 0.94172 | 11.2% | [5 empty] | Non-TXV | 5.828%
Fresno | CA | 93722-3070 |  | 2013-10-22 | 2013-10-22 12:55 | 2013-10-22 13:19 | WEATHER KING - 10AJ4801 | 90 | 2.7 | Yes | Yes | 16.6 | 19.5 | -2.9 | BA3BE5153EC7423F97DCB43764894E08 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Kingsburg | CA | 93631-9229 |  | 2013-10-14 | 2013-10-14 12:47 | 2013-10-14 13:12 | CARRIER - UNK | 76 | 7.2 | Yes | Yes | 19.6 | 18.8 | 0.8 | 8B04C89EAFE04B7F97F344932ADA42F0 |  | R22 | Non-TXV |  | 9.474% | 0.90526 | 18.21% | [5 empty] | Non-TXV | 9.474%
Fresno | CA | 93722-4378 |  | 2013-10-04 | 2013-10-04 15:21 | 2013-10-04 15:51 | RHEEM - RRNLB036JK06X | 93 | 4.2 | Yes | Yes | 21.6 | 22.6 | -1 | BDF60303AA5B48E29ECAAE593D292E6D |  | R410A | Non-TXV |  | 4.516% | 0.95484 | 8.679% | [5 empty] | Non-TXV | 4.516%
Fresno | CA | 93710-6350 |  | 2013-10-16 | 2013-10-16 10:00 | 2013-10-16 10:24 | RUUD - UNK | 80 | 2.4 | Yes | Yes | 21.7 | 20.1 | 1.6 | A73A79DD5C884FC9894E2A1CF3D27DDC |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93706-5527 |  | 2013-10-14 | 2013-10-14 15:46 | 2013-10-14 20:32 | RHEEM - RRMA-A042JK08X | 114 | 3.4 | Yes | Yes | 21 | 21.1 | -0.1 | 4A4B99799DE442EFB6073DDA1558CC85 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Fresno | CA | 93727-6498 |  | 2013-10-05 | 2013-10-05 10:09 | 2013-10-05 10:29 | LENNOX - 12ACB365P | 103 | 5.3 | Yes | Yes | 19.5 | 20 | -0.5 | AF0E494331FD448E9B75FD2B1F089A18 |  | R22 | TXV |  | 5.146% | 0.94854 | 9.889% | [5 empty] | TXV | 5.146%
Bakersfield | CA | 93305-1713 |  | 2013-10-09 | 2013-10-09 16:49 | 2013-10-09 16:52 | TEMPSTAR - PGAD3D1K6 | 102 | 9.7 | Yes | Yes | 23 | 20.6 | 2.4 | 562025A74DEA49C1A8F10ED4C2324340 |  | R22 | TXV |  | 9.51% | 0.9049 | 18.28% | [5 empty] | TXV | 9.51%
Fresno | CA | 93705-2765 |  | 2013-11-08 | 2013-11-08 15:57 | 2013-11-08 15:57 | OTHER - AC024X1322B | 88 | 4.9 | Yes | Yes | 17 | 19.3 | -2.3 | 5E541E5D06934227BE3A8AA98787D16C | Add refrigerant: 4.9 oz | R22 | Non-TXV |  | 5.568% | 0.94432 | 10.7% | [5 empty] | Non-TXV | 5.568%
Sanger | CA | 93657-2360 |  | 2013-10-21 | 2013-10-21 15:22 | 2013-10-21 15:43 | PAYNE - PA13NA042B | 97 | 5.5 | Yes | Yes | 21.9 | 19.3 | 2.6 | 673ABC73332348FC9DE71D3AA99293B2 |  | R410A | Non-TXV |  | 5.67% | 0.9433 | 10.9% | [5 empty] | Non-TXV | 5.67%
Clovis | CA | 93611-3033 |  | 2013-10-07 | 2013-10-07 08:58 | 2013-10-07 09:33 | YORK - D1NH036N07206C | 108 | 3.4 | Yes | Yes | 22.1 | 20.8 | 1.3 | 8085D2ADB2A741FEAFEEF4C918DF0912 |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Fresno | CA | 93727-3638 |  | 2013-10-17 | 2013-10-17 14:10 | 2013-10-17 15:24 | HEIL - 10GCS042X753PA | 73 | 4.3 | Yes | Yes | 22.9 | 21.5 | 1.4 | 93F46438A1094B5DADE662B410EB7247 |  | R22 | Non-TXV |  | 5.89% | 0.9411 | 11.32% | [5 empty] | Non-TXV | 5.89%
Kerman | CA | 93630-1951 |  | 2013-10-22 | 2013-10-22 14:42 | 2013-10-22 14:42 | CARRIER - 48GX036060301 | 82 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | AF5CAE4982E84EB88291CE13ADDB6101 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1730 |  | 2013-10-09 | 2013-10-09 16:55 | 2013-10-09 16:58 | RHEEM - RRMA-A036JK06E | 99 | 9.9 | Yes | Yes | 23.2 | 21.2 | 2 | DA3EC68592D94DAC89F400DA2D294E67 |  | R22 | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Fairfield | CA | 94533-2521 |  | 2013-10-17 | 2013-10-17 10:08 | 2013-10-17 10:09 | AMERICAN STANDARD - 4A7A5036E1000AA | 116 | 5.6 | Yes | Yes | 16.6 | 17.3 | -0.7 | 3EC998F30CBF49C8A74C5917ECA021A8 |  | R410A | Non-TXV |  | 4.828% | 0.95172 | 9.278% | [5 empty] | Non-TXV | 4.828%
Kerman | CA | 93630-1848 |  | 2013-10-22 | 2013-10-22 11:07 | 2013-10-22 11:52 | CARRIER - UKN | 90 | 16.5 | Yes | Yes | 22.5 | 21 | 1.5 | 3EE49EC448084AFEA48014E83DDDF9FC |  | R22 | Non-TXV |  | 18.33% | 0.81667 | 35.23% | [5 empty] | Non-TXV | 18.33%
Clovis | CA | 93612-3535 |  | 2013-10-17 | 2013-10-17 10:11 | 2013-10-17 10:28 | YORK - D1NP036N05606A | 108 | 3.8 | Yes | Yes | 20.6 | 18.2 | 2.4 | 774902CB50E84C368294DECF3F9E118B |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Pittsburg | CA | 94565-2249 |  | 2013-10-23 | 2013-10-23 10:08 | 2013-10-23 10:09 | TEMPSTAR - AC8042A2A1 | 97 | -6.8 | Yes | Yes | 17.2 | 16.6 | 0.7 | 1884E387709A4FD3858EBE0FF6C808C4 |  | R22 | Non-TXV |  | -7.01% | 1.0701 | 1.963% |  |  |  |  | Non-TXV |  |  | -7.01%
Selma | CA | 93662-4534 |  | 2013-10-14 | 2013-10-14 11:18 | 2013-10-14 11:55 | WEATHER KING - 12AJB60A01 | 248 | -9 | Yes | Yes | 23.1 | 18.7 | 4.4 | BD18C73EC4614BE0BC5908A91E4C2650 |  | R22 | Non-TXV |  | -3.629% | 1.0363 | 1.016% |  |  |  |  | Non-TXV |  |  | -3.629%
Fresno | CA | 93727-5526 |  | 2013-10-17 | 2013-10-17 13:30 | 2013-10-17 14:08 | GOODMAN - CKJ301A | 92 | 6.9 | Yes | Yes | 22.1 | 20.7 | 1.4 | 96253A77E498423DAAD82A3D4C2E6668 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Fresno | CA | 93727-9333 |  | 2013-10-17 | 2013-10-17 15:26 | 2013-10-17 15:26 | OTHER - PGF042K080B | 87 | 0 | Yes | Yes | 35.5 | 20.4 | 15.1 | 78F822C722264EA2AF179D69798DC914 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2019 |  | 2013-10-16 | 2013-10-16 11:35 | 2013-10-16 12:02 | GOODMAN - CK361B | 76 | 4.3 | Yes | Yes | 20.2 | 19.8 | 0.5 | A87A7DA04F1B4843A37D152BCBE2076F |  | R22 | Non-TXV |  | 5.658% | 0.94342 | 10.87% | [5 empty] | Non-TXV | 5.658%
Fresno | CA | 93726-3418 |  | 2013-10-23 | 2013-10-23 11:25 | 2013-10-23 11:47 | CARRIER - UNK | 76 | 4.2 | Yes | Yes | 20.2 | 17.7 | 2.5 | E70313EDEBAB4AA283ABCCAF2BC7E8A3 |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Selma | CA | 93662-4427 |  | 2013-11-11 | 2013-11-11 16:04 | 2013-11-11 16:04 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | E4B4A8FE20E04190B70B077C9DC98065 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5717 |  | 2013-10-16 | 2013-10-16 11:40 | 2013-10-16 12:11 | RHEEM - RRPLB036JK06X | 93 | 7.5 | Yes | Yes | 23.2 | 19.1 | 4.1 | 5FCEFD91E78140ABB440C4CE2EC821D7 |  | R410A | Non-TXV |  | 8.065% | 0.91935 | 15.5% | [5 empty] | Non-TXV | 8.065%
Fresno | CA | 93727-9318 |  | 2013-11-07 | 2013-11-07 13:17 | 2013-11-07 13:53 | TEMPSTAR - PGF042K080E | 87 | 4.4 | Yes | Yes | 20.7 | 19.5 | 1.2 | 1CB3AB3582384FA19D4870D1D9AA3E58 |  | R22 | Non-TXV |  | 5.057% | 0.94943 | 9.719% | [5 empty] | Non-TXV | 5.057%
Wasco | CA | 93280-2594 |  | 2013-11-11 | 2013-11-11 16:35 | 2013-11-11 16:37 | OTHER - CCU12A30A-1 | 90 | 5.2 | Yes | Yes | 25.2 | 20.9 | 4.3 | 5CCDB1EFF26340BC8C4F206A7465DF8B |  | R22 | Non-TXV |  | 5.778% | 0.94222 | 11.1% | [5 empty] | Non-TXV | 5.778%
Dixon | CA | 95620-3753 |  | 2013-10-21 | 2013-10-21 11:45 | 2013-10-21 15:01 | CARRIER - 38TKB036300 | 80 | 2.6 | Yes | Yes | 17.7 | 20.4 | -2.7 | A492BE58DB2A47E4ACACC1FC92AE8C97 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Bakersfield | CA | 93304-3925 |  | 2013-10-16 | 2013-10-16 15:38 | 2013-10-16 15:38 | GOODMAN - PGB01001843 | 60 | 0 | Yes | Yes | 22.8 | 21.5 | 1.3 | C61A5A6A04C64E0FAA955ACE37E926A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-9322 |  | 2013-10-21 | 2013-10-21 13:40 | 2013-10-21 14:26 | TEMPSTAR - PGF042K080B | 87 | 4.9 | Yes | Yes | 19.7 | 19.9 | -0.2 | 31B33FF915804FE08651C08616C93842 |  | R22 | Non-TXV |  | 5.632% | 0.94368 | 10.82% | [5 empty] | Non-TXV | 5.632%
Winters | CA | 95694-2010 |  | 2013-10-21 | 2013-10-21 11:53 | 2013-10-21 11:53 | DAY & NIGHT - NA | 72 | 6.9 | Yes | Yes | 16.4 | 17.6 | -1.2 | A10597391E374F2EBA6B38510C28E40A |  | R22 | Non-TXV |  | 9.583% | 0.90417 | 18.42% | [5 empty] | Non-TXV | 9.583%
Parlier | CA | 93648-9671 |  | 2013-11-01 | 2013-11-01 14:26 | 2013-11-01 14:57 | LENNOX - 13ACD04223002 | 111 | 7.8 | Yes | Yes | 23.9 | 20.4 | 3.5 | 08F0799F12B444EBB4BF4721F5C795F0 |  | R22 | Non-TXV |  | 7.027% | 0.92973 | 13.5% | [5 empty] | Non-TXV | 7.027%
Clovis | CA | 93612-2559 |  | 2013-10-17 | 2013-10-17 12:20 | 2013-10-17 12:50 | OTHER - DYCZ-F030N070A | 64 | 1.9 | Yes | Yes | 23 | 19.7 | 3.3 | BCC2E1CDE348409EAC488E63B4E833F4 |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Bakersfield | CA | 93304-6170 |  | 2013-10-16 | 2013-10-16 19:59 | 2013-10-16 19:59 | ICP - PGC024K040 | 56 | 0 | Yes | Yes | 21.7 | 21.8 | -0.1 | 7E9DCA0085A9465B8163A52CEC21EF84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Parlier | CA | 93648-9671 |  | 2013-11-01 | 2013-11-01 13:41 | 2013-11-01 14:21 | LENNOX - 13GCSA36068X2301A | 101 | 17.6 | Yes | Yes | 19.9 | 18.7 | 1.2 | 74129980E62E4F7F985319B97394CA00 |  | R22 | Non-TXV |  | 17.43% | 0.82574 | 33.49% | [5 empty] | Non-TXV | 17.43%
Fresno | CA | 93702-3343 |  | 2013-10-08 | 2013-10-08 13:00 | 2013-10-08 13:47 | DAY & NIGHT - 585A030060YACR | 50 | 4.4 | Yes | Yes | 21.7 | 20.2 | 1.5 | 618928C6FA1D40D7AE5E8CF3E843610C |  | R22 | Non-TXV |  | 8.8% | 0.912 | 16.91% | [5 empty] | Non-TXV | 8.8%
Bakersfield | CA | 93313-5573 |  | 2013-10-21 | 2013-10-21 14:10 | 2013-10-21 14:10 | BRYANT - 563CNO-6 | 201 | 0 | Yes | Yes | 22 | 21 | 1 | EFF56C9CAF254733B09734091A62BDC0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-2018 |  | 2013-10-17 | 2013-10-17 15:09 | 2013-10-17 20:59 | CARRIER - 24ABA348A00300 | 121 | 3.7 | Yes | Yes | 19.8 | 22.1 | -2.3 | 1A9F66FAD3D644599E8CC866725C0B0F |  | R410A | Non-TXV |  | 3.058% | 0.96942 | 5.877% | [5 empty] | Non-TXV | 3.058%
Bakersfield | CA | 93304-6170 |  | 2013-10-16 | 2013-10-16 19:20 | 2013-10-16 19:20 | PAYNE - PY3GNA24040NA | 74 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 7967B0E5ACEB4CF88C041966D86859F4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2592 |  | 2013-10-31 | 2013-10-31 17:48 | 2013-10-31 17:49 | OTHER - CCU12A30A-1 | 90 | 4.6 | Yes | Yes | 22.5 | 20.8 | 1.7 | A3BDD2ECA8CC46239D0FE5356718FCBE |  | R22 | Non-TXV |  | 5.111% | 0.94889 | 9.822% | [5 empty] | Non-TXV | 5.111%
Fresno | CA | 93727-3684 |  | 2013-11-07 | 2013-11-07 14:56 | 2013-11-07 22:36 | LENNOX - UKN | 87 | 4.2 | Yes | Yes | 20.6 | 20.2 | 0.4 | F4ED547385264AD0B025FEF11C7AA095 |  | R22 | Non-TXV |  | 4.828% | 0.95172 | 9.278% | [5 empty] | Non-TXV | 4.828%
Fresno | CA | 93722-2626 |  | 2013-10-25 | 2013-10-25 14:03 | 2013-10-25 15:04 | CARRIER - 38CKB036321 | 73 | 3.9 | Yes | Yes | 19.2 | 19.9 | -0.7 | FAD0BD83BAE644589233E228825FEDEC |  | R22 | TXV |  | 5.342% | 0.94658 | 10.27% | [5 empty] | TXV | 5.342%
Bakersfield | CA | 93304-6171 |  | 2013-10-16 | 2013-10-16 18:44 | 2013-10-16 18:44 | PAYNE - PY3GNAA24040NA | 76 | 0 | Yes | Yes | 22 | 22.1 | -0.1 | 74025C10FF944513A86095FF76DE379C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9394 |  | 2013-10-29 | 2013-10-29 13:58 | 2013-10-29 14:17 | YORK - H4RC060S06HG | 143 | 5.2 | Yes | Yes | 21.2 | 19.5 | 1.7 | 4EEB277919E642C8B267A127B3AC6400 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Shafter | CA | 93263-2941 |  | 2013-10-22 | 2013-10-22 18:02 | 2013-10-22 18:10 | RHEEM - RRNA-B030JK06X | 65 | 4 | Yes | Yes | 20 | 19.3 | 0.7 | 62B5279BF39342589BBED8405077B27F |  | R22 | TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | TXV | 6.154%
Bakersfield | CA | 93304-6171 |  | 2013-10-16 | 2013-10-16 18:58 | 2013-10-16 18:58 | TRANE - 4YCC3024B1064AA | 109 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | A1DD51E91FE2428288053C08B12CD5A5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4934 |  | 2013-10-09 | 2013-10-09 17:12 | 2013-10-09 17:23 | RHEEM - RRNA-B036JK06X | 83 | 5.7 | Yes | Yes | 24.1 | 20.6 | 3.5 | E199FBEEB0A6406D988B55DD4A7D07CB |  | R22 | TXV |  | 6.867% | 0.93133 | 13.2% | [5 empty] | TXV | 6.867%
Bakersfield | CA | 93311-2782 |  | 2013-10-24 | 2013-10-24 16:30 | 2013-10-24 16:30 | YORK - H1RC048J06B | 122 | 0 | Yes | Yes | 21.7 | 22 | -0.3 | 83585FD9373D437BBFD4DAF81C8EE70F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2782 |  | 2013-10-24 | 2013-10-24 16:40 | 2013-10-24 16:40 | YORK - H1RC048J06B | 122 | 0 | Yes | Yes | 20.3 | 21.5 | -1.2 | F0E85CEE63F54036BE35E4260ABC3541 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2815 |  | 2013-10-22 | 2013-10-22 12:14 | 2013-10-22 12:14 | CARRIER - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 145A1BCEA8434034AFE7449E16779854 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6506 |  | 2013-10-17 | 2013-10-17 18:29 | 2013-10-17 18:29 | GOODMAN - PGB024050-1 | 54 | 0 | Yes | Yes | 22 | 21.3 | 0.8 | 71F82923A40342B3A0E3E087FA6ACAC4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-9504 |  | 2013-10-18 | 2013-10-18 17:38 | 2013-10-18 17:38 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | BF610EADF2F24DD6A51883E6DD158F0A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6506 |  | 2013-10-17 | 2013-10-17 18:55 | 2013-10-17 18:55 | YORK - D2P024N03606A | 100 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 4129331339234F14875F1F599F4FAFA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6517 |  | 2013-10-17 | 2013-10-17 16:49 | 2013-10-17 16:49 | YORK - D2NP024N03606A | 100 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | C3221227E7734BCAADF11CF12D94B535 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2210 |  | 2013-10-17 | 2013-10-17 12:54 | 2013-10-17 12:54 | TRANE - 2TTB0036A1000AA | 76 | 3.8 | Yes | Yes | 16.5 | 17.5 | -1 | 2D5DDD21FB414E4C8FBA02427D66D7EA |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93304-6518 |  | 2013-10-17 | 2013-10-17 16:35 | 2013-10-17 16:35 | GOODMAN - GPG13224045M4KA | 68 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | FA380E45A7F748C18F886D8CE19FF16E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4113 |  | 2013-11-11 | 2013-11-11 12:45 | 2013-11-11 12:45 | CARRIER - UNK | 74 | 0 | Yes | Yes | 40 | 20.9 | 19.1 | B195F5F6043945788F51C93DF475D366 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3456 |  | 2013-10-17 | 2013-10-17 11:02 | 2013-10-17 11:34 | COLEMAN - CJ421C | 84 | 2.9 | Yes | Yes | 21.2 | 19.5 | 1.7 | EA6E9455D7BE43D4B4C94868CA900FA4 |  | R22 | Non-TXV |  | 3.452% | 0.96548 | 6.635% | [5 empty] | Non-TXV | 3.452%
Bakersfield | CA | 93304-6523 |  | 2013-10-17 | 2013-10-17 15:34 | 2013-10-17 15:34 | DAY & NIGHT - UKN | 60 | 0 | Yes | Yes | 21.9 | 21.2 | 0.7 | D6C1049358EC4A19A2709913FBE04FA0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6524 |  | 2013-10-17 | 2013-10-17 14:43 | 2013-10-17 15:03 | DAY & NIGHT - UKN | 60 | 4.8 | Yes | Yes | 22.5 | 21 | 1.5 | 8E3F2DE7EA1642C88E7071E37844CD9D |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Dixon | CA | 95620-3815 |  | 2013-10-21 | 2013-10-21 10:53 | 2013-10-21 10:53 | GOODMAN - GSC130421AB | 143 | 0 | Yes | Yes | 18.1 | 20.1 | -2 | EE03303BCF9F44E2B3B4E2244B6A73E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1449 |  | 2013-10-22 | 2013-10-22 14:37 | 2013-10-22 14:55 | BRYANT - 582ANW036090ABAF | 68 | 2.4 | Yes | Yes | 21.2 | 21 | 0.2 | 8E8A93805DF34EE092E884C93972BD61 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Clovis | CA | 93612-4830 |  | 2013-10-22 | 2013-10-22 11:50 | 2013-10-22 12:16 | RUUD - RRNLB030JK06X | 77 | 2.4 | Yes | Yes | 18.5 | 19 | -0.5 | 793C0F6D8ED9429EB0D892063F06BC7B |  | R410A | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Fresno | CA | 93722-3206 |  | 2013-10-16 | 2013-10-16 10:13 | 2013-10-16 11:36 | RHEEM - RRNAB036JK06X | 83 | 3.6 | Yes | Yes | 20.7 | 18.7 | 2 | 813D041CF38F4114B2A30E914E0EE85F |  | R22 | Non-TXV |  | 4.337% | 0.95663 | 8.335% | [5 empty] | Non-TXV | 4.337%
Fremont | CA | 94555-1953 |  | 2013-10-17 | 2013-10-17 10:12 | 2013-10-17 10:12 | YORK - H2RD036S06B | 85 | 0 | Yes | Yes | 20.9 | 16.3 | 4.6 | 8E3E2BBF79BD4402B377373C65775635 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2133 |  | 2013-10-21 | 2013-10-21 11:20 | 2013-10-21 11:51 | GOODMAN - CK49-1B | 97 | 13.4 | Yes | Yes | 22.1 | 16.5 | 5.6 | EBBCEBC5FC5F482FAA9CE60910345074 |  | R22 | Non-TXV |  | 13.81% | 0.86186 | 26.55% | [5 empty] | Non-TXV | 13.81%
Bakersfield | CA | 93304-6522 |  | 2013-10-17 | 2013-10-17 16:00 | 2013-10-17 16:00 | ICP - GPFM24K040E | 54 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 8E2542BEE047415B8FAE386B8914306B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6523 |  | 2013-10-17 | 2013-10-17 15:48 | 2013-10-17 15:48 | GOODMAN - PGB024050-1 | 84 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | C9FE6402783F4FFFA7CC9B49C7D565FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7917 |  | 2013-10-18 | 2013-10-18 11:30 | 2013-10-18 12:15 | LENNOX - 12ACB425P | 125 | 5.3 | Yes | Yes | 21.4 | 20.4 | 1.1 | FD84421FA9774FC88DF949BE984A4C57 |  | R22 | TXV |  | 4.24% | 0.9576 | 8.148% | [5 empty] | TXV | 4.24%
Clovis | CA | 93611-2008 |  | 2013-10-18 | 2013-10-18 12:17 | 2013-10-18 13:00 | OTHER - PGD348090K001C1 | 102 | 3.7 | Yes | Yes | 24 | 20.1 | 3.9 | 7C51012E21694F348BD5BACBE77BDC7C |  | R410A | TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | TXV | 3.627%
Bakersfield | CA | 93304-6509 |  | 2013-10-17 | 2013-10-17 17:58 | 2013-10-17 17:58 | GOODMAN - PGB024050-1 | 54 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 106091305F7D4BF597FFF635C08DDDD6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6512 |  | 2013-10-17 | 2013-10-17 17:39 | 2013-10-17 17:39 | ICP - GPCM024K040D | 54 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 437F8ED4D9764990A1AAADB9D89E483C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-0446 |  | 2013-10-17 | 2013-10-17 12:32 | 2013-10-17 12:50 | GOODMAN - GPG1336070M41BA | 70 | 3.4 | Yes | Yes | 22.4 | 19.5 | 2.9 | D7182F9A6ED54FAB814C5E6C717E9A73 |  | R410A | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Fresno | CA | 93722-9788 |  | 2013-10-24 | 2013-10-24 11:32 | 2013-10-24 11:48 | BDP - 585GJ036060 | 82 | 15.9 | Yes | Yes | 22.6 | 19.5 | 3.1 | D25E6B26C01542C7B992355D2488BB43 |  | R22 | Non-TXV |  | 19.39% | 0.8061 | 37.26% | [5 empty] | Non-TXV | 19.39%
Clovis | CA | 93612-4831 |  | 2013-10-17 | 2013-10-17 11:37 | 2013-10-17 12:28 | DAY & NIGHT - UNK | 74 | 5.1 | Yes | Yes | 20.7 | 18.9 | 1.8 | F653A52D767C42059DC38B16A9483637 |  | R22 | Non-TXV |  | 6.892% | 0.93108 | 13.24% | [5 empty] | Non-TXV | 6.892%
Fresno | CA | 93705-3638 |  | 2013-10-31 | 2013-10-31 12:48 | 2013-10-31 13:49 | DAY & NIGHT - 585A024055YAC | 51 | 8.3 | Yes | Yes | 21.1 | 19.3 | 1.8 | 843FCC46671441949777933CBDB8E612 |  | R22 | Non-TXV |  | 16.27% | 0.83725 | 31.28% | [5 empty] | Non-TXV | 16.27%
Bakersfield | CA | 93304-6170 |  | 2013-10-16 | 2013-10-16 19:46 | 2013-10-16 19:46 | PAYNE - PY3GNAA24040NA | 74 | 0 | Yes | Yes | 22.6 | 21.4 | 1.2 | 864CC1602BAF4BE19D528188BBA2B76A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3266 |  | 2013-10-23 | 2013-10-23 12:27 | 2013-10-23 12:28 | PAYNE - PA13NA036 | 70 | 2.1 | Yes | Yes | 16.7 | 18.2 | -1.5 | 51A52BF03BB0400EAA7325C00078A9BF |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93313-5766 |  | 2013-10-21 | 2013-10-21 09:12 | 2013-10-21 09:29 | RHEEM - RAND 060JAZ | 152 | 10.6 | Yes | Yes | 18 | 20.9 | -2.9 | 146334F9B42147DE9759C635601023A6 |  | R22 | Non-TXV |  | 6.974% | 0.93026 | 13.4% | [5 empty] | Non-TXV | 6.974%
Vacaville | CA | 95687-3223 |  | 2013-10-21 | 2013-10-21 12:24 | 2013-10-21 12:25 | OTHER - BRCQ0361BD | 52 | -3.7 | Yes | Yes | 16.7 | 16.3 | 0.4 | 7B95E6C746F444F8BBF81B625509D973 |  | R22 | Non-TXV |  | -7.115% | 1.0712 | 1.993% |  |  |  |  | Non-TXV |  |  | -7.115%
Clovis | CA | 93612-4806 |  | 2013-10-23 | 2013-10-23 11:25 | 2013-10-23 12:02 | BDP - 588ANW030040ACAD | 56 | 1.6 | Yes | Yes | 19.6 | 19.1 | 0.5 | 4699AAA256B8443D932E4E83AD64FEE0 |  | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Clovis | CA | 93612-4242 |  | 2013-10-17 | 2013-10-17 13:28 | 2013-10-17 13:48 | CARRIER - 48DC004 | 92 | 9.3 | Yes | Yes | 24.1 | 20.4 | 3.7 | 03156A363E95475EADC1A83F48301B2A |  | R22 | Non-TXV |  | 10.11% | 0.89891 | 19.43% | [5 empty] | Non-TXV | 10.11%
Bay Point | CA | 94565-3293 |  | 2013-10-23 | 2013-10-23 11:58 | 2013-10-23 11:59 | CARRIER - 38EN024310 | 56 | 1.7 | Yes | Yes | 18.1 | 18.2 | -0.1 | 5A4DE4A526294EF696EFEBA30EA2223B |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Fairfield | CA | 94533-4251 |  | 2013-10-17 | 2013-10-17 10:39 | 2013-10-17 10:40 | GE - NA | 68 | 3.7 | Yes | Yes | 18.9 | 17.5 | 1.4 | 8FEB498586C247149447320242E4CB85 |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Kerman | CA | 93630-1950 |  | 2013-10-22 | 2013-10-22 11:56 | 2013-10-22 11:56 | CARRIER - 48GX042060301 | 119 | 0 | Yes | Yes | 21.2 | 20.4 | 0.9 | F65293B13C6347F9846217F2E3EE9F8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-1402 |  | 2013-10-25 | 2013-10-25 12:04 | 2013-10-25 13:07 | PAYNE - 589ANW036080ABBF | 84 | 4.7 | Yes | Yes | 20.9 | 19.8 | 1.1 | 8E85839D8DE846E28B392A88885A86B1 |  | R22 | TXV |  | 5.595% | 0.94405 | 10.75% | [5 empty] | TXV | 5.595%
San Jose | CA | 95136-1337 |  | 2013-10-21 | 2013-10-21 10:11 | 2013-10-21 10:43 | COLEMAN - BRC421BD | 84 | -7.9 | Yes | Yes | 22.7 | 20.6 | 2.1 | D1552E2E48C54E1294D0F4059E05B984 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Fresno | CA | 93703-1654 |  | 2013-10-16 | 2013-10-16 12:33 | 2013-10-16 13:08 | CARRIER - 48SDN036060311 | 134 | 4.1 | Yes | Yes | 20.2 | 20.1 | 0.2 | A92883BC912348379C0AD84108AE702B |  | R22 | Non-TXV |  | 3.06% | 0.9694 | 5.88% | [5 empty] | Non-TXV | 3.06%
Wasco | CA | 93280-1348 |  | 2013-10-20 | 2013-10-20 17:24 | 2013-10-20 17:28 | PAYNE - PY2PNB042060AAAA | 120 | 5.5 | Yes | Yes | 26.5 | 20.9 | 5.6 | F0EC345D83374BDA9EE459C1C93CEA6C |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Clovis | CA | 93612-4809 |  | 2013-10-17 | 2013-10-17 14:10 | 2013-10-17 14:29 | YORK - D1NP030N05606A | 73 | 6.4 | Yes | Yes | 23.7 | 21.3 | 2.5 | 0757919C740344DBAAD09913CCB9AF83 |  | R22 | Non-TXV |  | 8.767% | 0.91233 | 16.85% | [5 empty] | Non-TXV | 8.767%
Bakersfield | CA | 93307-2974 |  | 2013-10-24 | 2013-10-24 08:19 | 2013-10-24 08:19 | BDP - 5856J030050 | 63 | 0 | Yes | Yes | 21.6 | 19.7 | 1.9 | 9E5656F49FFF43D1AD4B79EE9A7000AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2594 |  | 2013-11-04 | 2013-11-04 15:22 | 2013-11-04 15:24 | OTHER - CCU12A30A-1 | 90 | 4.2 | Yes | Yes | 19.4 | 20.1 | -0.7 | 9496AAC394774C0485AD3EFD8DF0B718 |  | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Pittsburg | CA | 94565-1790 |  | 2013-10-25 | 2013-10-25 12:49 | 2013-10-25 12:50 | HEIL - CA5060UKA2 | 183 | 22.5 | Yes | Yes | 14.3 | 17.1 | -2.8 | 0B155D67951146D9A6E2DE14B8D26064 |  | R22 | Non-TXV |  | 12.3% | 0.87705 | 23.63% | [5 empty] | Non-TXV | 12.3%
Kerman | CA | 93630-2105 |  | 2013-10-24 | 2013-10-24 11:52 | 2013-10-24 12:34 | LENNOX - GCS29X030751PA | 51 | 4.1 | Yes | Yes | 22.3 | 20.4 | 1.9 | CF897BF619514E978B1E8BE4BEF8C95C |  | R22 | Non-TXV |  | 8.039% | 0.91961 | 15.45% | [5 empty] | Non-TXV | 8.039%
Fresno | CA | 93727-9309 |  | 2013-10-21 | 2013-10-21 12:54 | 2013-10-21 13:36 | TEMPSTAR - PGF042K080B | 87 | 5.1 | Yes | Yes | 18.4 | 20.3 | -1.9 | 42A96F80A45841ABBFE3B808019A244F |  | R22 | Non-TXV |  | 5.862% | 0.94138 | 11.27% | [5 empty] | Non-TXV | 5.862%
Kerman | CA | 93630-1423 |  | 2013-10-24 | 2013-10-24 12:37 | 2013-10-24 13:26 | TEMPSTAR - PGF036K060E | 68 | 4.1 | Yes | Yes | 23.6 | 19.9 | 3.7 | F37F1BE966E145AD8CC74FBB5A10C0C8 |  | R22 | Non-TXV |  | 6.029% | 0.93971 | 11.59% | [5 empty] | Non-TXV | 6.029%
Shafter | CA | 93263-2523 |  | 2013-10-22 | 2013-10-22 17:25 | 2013-10-22 17:27 | RHEEM - N/A | 85 | 5.7 | Yes | Yes | 22 | 18.7 | 3.3 | 540D7B5A0BC340B2A9AE143092D58A90 |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Kerman | CA | 93630-9357 |  | 2013-10-22 | 2013-10-22 12:44 | 2013-10-22 14:25 | CARRIER - 48GX042060301 | 118 | 12.2 | Yes | Yes | 18.9 | 20.6 | -1.7 | A3C097943DF7404388D43EC65A3B3094 |  | R22 | Non-TXV |  | 10.34% | 0.89661 | 19.87% | [5 empty] | Non-TXV | 10.34%
Clovis | CA | 93612-2521 |  | 2013-10-23 | 2013-10-23 12:51 | 2013-10-23 13:08 | BRYANT - 561CJ018-D | 52 | 1.5 | Yes | Yes | 16.2 | 19.1 | -2.9 | B8E531AE9F36413F9501C95CC347DC38 |  | R22 | Non-TXV |  | 2.885% | 0.97115 | 5.544% | [5 empty] | Non-TXV | 2.885%
Bakersfield | CA | 93304-6505 |  | 2013-10-17 | 2013-10-17 13:11 | 2013-10-17 13:11 | ICP - PGF024K040E | 56 | 0 | Yes | Yes | 21.1 | 21 | 0.1 | B2BD4CA05C4C4C4C9E0210BB51459A0A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2533 |  | 2013-10-30 | 2013-10-30 10:52 | 2013-10-30 11:15 | BRYANT - 561CJ024-D | 58 | -3.4 | Yes | Yes | 26.1 | 20.1 | 6 | 0675ED6DFB5A4AE1AB27E4D55148832A |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
San Jose | CA | 95116-1215 |  | 2013-10-16 | 2013-10-16 16:19 | 2013-10-16 18:54 | PAYNE - PA13NR030 | 69 | 3 | Yes | Yes | 20.8 | 21 | -0.2 | 40715B3ABF684A68A2CED4C3A32804A6 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Fresno | CA | 93726-1105 |  | 2013-10-17 | 2013-10-17 12:21 | 2013-10-17 13:28 | HEIL - PGC036K060A | 71 | 3.2 | Yes | Yes | 19.9 | 19.9 | 0 | 5F28BDC4C980465BBDFCE4AD328B9DC9 |  | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
Fresno | CA | 93710-5438 |  | 2013-10-23 | 2013-10-23 10:35 | 2013-10-23 10:58 | CARRIER - 38TXA036320 | 110 | 21.4 | Yes | Yes | 20.9 | 18.7 | 2.2 | 0AB6652D88C84567B823EBC0A0685DDD |  | R410A | Non-TXV |  | 19.45% | 0.80545 | 37.39% | [5 empty] | Non-TXV | 19.45%
Clovis | CA | 93612-2522 |  | 2013-10-24 | 2013-10-24 16:30 | 2013-10-24 17:13 | BRYANT - 561CJ024D | 58 | 3.2 | Yes | Yes | 21.4 | 20.4 | 1 | 5AC2B588D2034271B2E42E4729E86D40 |  | R22 | Non-TXV |  | 5.517% | 0.94483 | 10.6% | [5 empty] | Non-TXV | 5.517%
Fresno | CA | 93711-2323 |  | 2013-10-16 | 2013-10-16 14:07 | 2013-10-16 15:13 | PAYNE - 597CN060B | 176 | 43.1 | Yes | Yes | 20.7 | 22 | -1.3 | 24C9A3064ACC4126992E2788F6D83E3D |  | R22 | Non-TXV |  | 24.49% | 0.75511 | 47.06% | [5 empty] | Non-TXV | 24.49%
Clovis | CA | 93612-2523 |  | 2013-10-23 | 2013-10-23 13:34 | 2013-10-23 13:53 | BRYANT - 2299E10544 | 52 | -3.1 | Yes | Yes | 20.5 | 19.4 | 1.1 | A8836CAA845843379509D1451D1332A3 |  | R22 | Non-TXV |  | -5.962% | 1.0596 | 1.67% |  |  |  |  | Non-TXV |  |  | -5.962%
Wasco | CA | 93280-2593 |  | 2013-11-11 | 2013-11-11 16:31 | 2013-11-11 16:33 | OTHER - CCU12A30A-1 | 90 | -3.3 | Yes | Yes | 24.6 | 20.9 | 3.7 | 6325CF82437540399DE765BAE93C0F05 |  | R22 | Non-TXV |  | -3.667% | 1.0367 | 1.027% |  |  |  |  | Non-TXV |  |  | -3.667%
Bakersfield | CA | 93304-6524 |  | 2013-10-17 | 2013-10-17 15:20 | 2013-10-17 15:20 | GOODMAN - PGB024050-1 | 54 | 0 | Yes | Yes | 21.5 | 21 | 0.5 | 6C23C0EE976C4F1587FF34620246F5E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6530 |  | 2013-10-17 | 2013-10-17 14:05 | 2013-10-17 14:05 | ICP - GPFM24K040E | 56 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 9B0B99A0F78445A1A1BB25C57D059490 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4725 |  | 2013-10-28 | 2013-10-28 13:24 | 2013-10-28 13:50 | RHEEM - EADB031JAS | 75 | -5.3 | Yes | Yes | 18.7 | 18.7 | 0 | 5676F4A186274F69BDD065BED338562A |  | R22 | Non-TXV |  | -7.067% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.067%
Clovis | CA | 93612-2512 |  | 2013-10-29 | 2013-10-29 15:41 | 2013-10-29 16:04 | BRYANT - 561CJ018-D | 52 | -3.1 | Yes | Yes | 16.7 | 19.7 | -3 | F7F8754D091E456FBF511EB0A1B60608 |  | R22 | Non-TXV |  | -5.962% | 1.0596 | 1.67% |  |  |  |  | Non-TXV |  |  | -5.962%
Bakersfield | CA | 93304-6508 |  | 2013-10-17 | 2013-10-17 18:15 | 2013-10-17 18:15 | ICP - GPFM24K040E | 54 | 0 | Yes | Yes | 22.1 | 21.2 | 0.9 | 0B10CB9B86214C0780615BA0B84F7628 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7117 |  | 2013-10-16 | 2013-10-16 11:46 | 2013-10-16 12:16 | GOODMAN - CLT36-1C | 140 | 4.2 | Yes | Yes | 18 | 19.5 | -1.5 | 757DE62B988D48A4B30D1F626CF86C00 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93312-6748 |  | 2013-10-16 | 2013-10-16 09:02 | 2013-10-16 09:02 | CARRIER - UKN | 90 | 0 | Yes | Yes | 20.9 | 19.9 | 1 | DA19BAEFCF404EB6868F9867307DB92D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6748 |  | 2013-10-16 | 2013-10-16 09:22 | 2013-10-16 09:22 | CARRIER - UKN | 90 | 0 | Yes | Yes | 21 | 19.7 | 1.3 | 9FAF647DE6834F8EB7A18667C4C48C7F | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6512 |  | 2013-10-17 | 2013-10-17 17:20 | 2013-10-17 17:20 | ICP - PGB024050-1 | 54 | 0 | Yes | Yes | 21.4 | 21.3 | 0.2 | A6E409FF2EC741ABB7DEA6C835F8B68C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2162 |  | 2013-10-24 | 2013-10-24 15:45 | 2013-10-24 15:45 | LENNOX - 13ACD-036-230-02 | 111 | 0 | Yes | Yes | 21.9 | 21.8 | 0.1 | 56CAD26FFED84610BD7284394406E817 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2162 |  | 2013-10-24 | 2013-10-24 15:48 | 2013-10-24 15:48 | LENNOX - 13ACD-036-230-02 | 111 | 0 | Yes | Yes | 20.9 | 21.5 | -0.6 | A2CE3AC855BD4BC2AB53AF46754A9B19 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6516 |  | 2013-10-17 | 2013-10-17 17:06 | 2013-10-17 17:06 | OTHER - UKN | 60 | 0 | Yes | Yes | 21.5 | 20.7 | 0.8 | DF65945EDBD04BBBA50D946F443810F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6170 |  | 2013-10-16 | 2013-10-16 19:21 | 2013-10-16 19:21 | ICP - PGC024K040E | 54 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | 3D64E845C6634B718068D72931340D85 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-9739 |  | 2013-10-16 | 2013-10-16 19:05 | 2013-10-16 19:08 | OTHER - DRCS0481BE | 119 | -8.4 | Yes | Yes | 22.8 | 20.6 | 2.2 | 81FFC3CC465D4CDB848147A2485FEF83 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93304-6531 |  | 2013-10-17 | 2013-10-17 13:48 | 2013-10-17 13:48 | GOODMAN - GPG1324051BA | 77 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 3824EA64750D42EA88B2F918DBF2FC49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6522 |  | 2013-10-17 | 2013-10-17 16:22 | 2013-10-17 16:22 | ICP - GPFM24K040E | 54 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 1C773B9BF1744C34884DE44C614E82FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4262 |  | 2013-11-11 | 2013-11-11 15:21 | 2013-11-11 15:43 | GOODMAN - CPL830 | 51 | 3.1 | Yes | Yes | 22.6 | 20.3 | 2.3 | 41AFCE3CAA9A4F05ABFF92B135D337F6 |  | R22 | Non-TXV |  | 6.078% | 0.93922 | 11.68% | [5 empty] | Non-TXV | 6.078%
Fairfield | CA | 94533-8014 |  | 2013-10-17 | 2013-10-17 13:16 | 2013-10-17 13:16 | GOODMAN - CM18-1EB | 49 | 3.3 | Yes | Yes | 15.9 | 17 | -1.1 | 3E0852EA8E3D49CAA25300CEA27A5DB9 |  | R22 | Non-TXV |  | 6.735% | 0.93265 | 12.94% | [5 empty] | Non-TXV | 6.735%
Kerman | CA | 93630-1450 |  | 2013-10-22 | 2013-10-22 10:28 | 2013-10-22 10:28 | CARRIER - 48SX036060331 | 84 | 0 | Yes | Yes | 21.1 | 19.9 | 1.2 | D5BF4DFCDEFF4E47A60AAF323AA09617 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1248 |  | 2013-10-16 | 2013-10-16 15:21 | 2013-10-16 15:46 | PAYNE - 563AN060A | 207 | 6.1 | Yes | Yes | 20.9 | 20 | 0.9 | E1A3F1C33D6E494F90158520CCD158FC |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.663% | [5 empty] | Non-TXV | 2.947%
Fresno | CA | 93711-1248 |  | 2013-10-16 | 2013-10-16 15:51 | 2013-10-16 16:35 | PAYNE - 563AN036A | 113 | 3.5 | Yes | Yes | 22.7 | 21 | 1.7 | 7F1E5B2EB3574518B1B5F2C1FB8960F1 |  | R22 | Non-TXV |  | 3.097% | 0.96903 | 5.952% | [5 empty] | Non-TXV | 3.097%
Fresno | CA | 93726-0419 |  | 2013-10-17 | 2013-10-17 11:39 | 2013-10-17 12:19 | YORK - DAYPF042N080A | 150 | 5.6 | Yes | Yes | 20.9 | 20.2 | 0.7 | 5DDDD8A473BE445186AA24575A629DC7 |  | R22 | Non-TXV |  | 3.733% | 0.96267 | 7.175% | [5 empty] | Non-TXV | 3.733%
Fresno | CA | 93720-2505 |  | 2013-10-16 | 2013-10-16 09:06 | 2013-10-16 09:29 | RHEEM - RRMA-A048JK10X | 115 | 3.4 | Yes | Yes | 26 | 20.7 | 5.3 | 872AFF3DFFCD427BBB31479228A6BEA7 |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Fresno | CA | 93703-1453 |  | 2013-10-21 | 2013-10-21 09:50 | 2013-10-21 10:26 | RUUD - UNK | 74 | 3.7 | Yes | Yes | 20.3 | 18.5 | 1.9 | 8FEE2CAD735548C2B1410853030BA118 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93727-7970 |  | 2013-11-08 | 2013-11-08 16:15 | 2013-11-09 00:41 | GOODMAN - GPG13420901AB | 107 | 3.8 | Yes | Yes | 21.7 | 19.6 | 2.2 | E458EE7F8AE940F29A9BCCBC09CBAED3 |  | R22 | Non-TXV |  | 3.551% | 0.96449 | 6.825% | [5 empty] | Non-TXV | 3.551%
Clovis | CA | 93611-4594 |  | 2013-10-17 | 2013-10-17 11:28 | 2013-10-17 11:51 | BDP - 585HJW036060ABAF | 134 | 4 | Yes | Yes | 24.7 | 20.7 | 4 | 55E57EB434594A1F89BCF23CB1F72060 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Fresno | CA | 93722-3651 |  | 2013-10-22 | 2013-10-22 14:34 | 2013-10-22 14:53 | LENNOX - 10GCS042X-75-2PA | 73 | 2.2 | Yes | Yes | 24.3 | 21.9 | 2.4 | 34AB2BCBF5BE4525A5F1348663ACB487 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Clovis | CA | 93611-5140 |  | 2013-11-07 | 2013-11-07 14:27 | 2013-11-07 14:56 | BDP - 588ANW036060ACAF | 68 | 2 | Yes | Yes | 20.2 | 20.6 | -0.4 | 42356041D3CB4491AA34776BF4CCE889 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Sanger | CA | 93657-8779 |  | 2013-10-21 | 2013-10-21 16:05 | 2013-10-21 16:47 | YORK - H2RD042S068 | 141 | 9.6 | Yes | Yes | 22.6 | 22.9 | -0.3 | 4E28759E1DF04A12AC4FDD972C14994C |  | R22 | TXV |  | 6.809% | 0.93191 | 13.08% | [5 empty] | TXV | 6.809%
Clovis | CA | 93611-5140 |  | 2013-10-25 | 2013-10-25 11:36 | 2013-10-25 11:36 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C74BAEFCBF254064B9C90F72BBE61F50 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2325 |  | 2013-10-24 | 2013-10-24 13:54 | 2013-10-24 15:04 | OTHER - WPG3364060LKG1 | 102 | -5.2 | Yes | Yes | 23.6 | 19.3 | 4.3 | EB3C69938D7B4D9C874C6367E95D2AF0 |  | R410A | Non-TXV |  | -5.098% | 1.051 | 1.428% |  |  |  |  | Non-TXV |  |  | -5.098%
Wasco | CA | 93280-2592 |  | 2013-10-31 | 2013-10-31 17:51 | 2013-10-31 17:53 | OTHER - CCU12A30A-1 | 90 | 4.4 | Yes | Yes | 19.8 | 19.6 | 0.2 | FD1B5EA2955C42F29571B0CA53D98987 |  | R22 | TXV |  | 4.889% | 0.95111 | 9.395% | [5 empty] | TXV | 4.889%
San Jose | CA | 95136-1337 |  | 2013-10-21 | 2013-10-21 13:25 | 2013-10-21 14:08 | COLEMAN - BRCQ042C | 57 | -4 | Yes | Yes | 23.2 | 19.7 | 3.5 | 0CC51F7509274A69B4EC169CE6C1B6D1 |  | R22 | Non-TXV |  | -7.018% | 1.0702 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.018%
Pittsburg | CA | 94565-4473 |  | 2013-10-22 | 2013-10-22 11:22 | 2013-10-22 11:22 | GOODMAN - | 85 | 0 | Yes | Yes | 18.2 | 21 | -2.8 | E4F1FAE6CA3445D3A7E9E976C809EBB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-0421 |  | 2013-10-24 | 2013-10-24 13:00 | 2013-10-24 13:29 | TRANE - YCY042G1M0AC | 149 | 6.7 | Yes | Yes | 22.7 | 21 | 1.7 | 5A19B00150D54E05BD01BA6A0DEF344B |  | R22 | Non-TXV |  | 4.497% | 0.95503 | 8.642% | [5 empty] | Non-TXV | 4.497%
Clovis | CA | 93611-3132 |  | 2013-10-18 | 2013-10-18 13:31 | 2013-10-18 13:50 | ICP - PGC036K060E | 85 | 2.5 | Yes | Yes | 21.8 | 20.1 | 1.7 | 1DCD189B5AEE47B599B8F545B9F6F3BD |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Wasco | CA | 93280-2595 |  | 2013-11-07 | 2013-11-07 18:50 | 2013-11-07 18:52 | OTHER - CCU12AB030A-1 | 90 | 4.6 | Yes | Yes | 25.6 | 21.2 | 4.5 | 3F8E4EAB180D4D9186B755271D8CDB62 |  | R22 | TXV |  | 5.111% | 0.94889 | 9.822% | [5 empty] | TXV | 5.111%
Fresno | CA | 93711-0885 |  | 2013-10-23 | 2013-10-23 13:03 | 2013-10-23 13:31 | PAYNE - UNK | 76 | 3.2 | Yes | Yes | 23 | 19.5 | 3.5 | A6813AE4ABC0400CBB57B5913B7E6FF0 |  | R22 | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Bakersfield | CA | 93304-6170 |  | 2013-10-16 | 2013-10-16 19:39 | 2013-10-16 19:39 | RHEEM - UKN | 60 | 0 | Yes | Yes | 21.5 | 20.7 | 0.8 | 1617AD1469CF403E952B288E93E8A021 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1580 |  | 2013-10-25 | 2013-10-25 10:58 | 2013-10-25 11:35 | PAYNE - 585GJ018040 | 55 | 4.1 | Yes | Yes | 20.8 | 19.8 | 1 | D13A4271DECD44F4B7E37C44EAB58D03 |  | R22 | Non-TXV |  | 7.455% | 0.92545 | 14.33% | [5 empty] | Non-TXV | 7.455%
San Jose | CA | 95122-4006 |  | 2013-10-16 | 2013-10-16 10:47 | 2013-10-16 11:14 | UNITARY PRODUCTS GROUP - NCAFB830 | 72 | 2.4 | Yes | Yes | 17.4 | 20.3 | -2.9 | F2C952BA197C4AC6BD83BFF2736378FC |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93703-1817 |  | 2013-10-16 | 2013-10-16 13:11 | 2013-10-16 17:20 | DAY & NIGHT - 585HJW30040ABAF | 68 | 4.3 | Yes | Yes | 19.5 | 19.8 | -0.3 | 9E42A179C26C4EB29B1F64904BF7B161 |  | R22 | Non-TXV |  | 6.324% | 0.93676 | 12.15% | [5 empty] | Non-TXV | 6.324%
Fresno | CA | 93727-7916 |  | 2013-10-25 | 2013-10-25 15:07 | 2013-10-25 17:48 | YORK - D5YS030N04506A | 64 | 4.9 | Yes | Yes | 20.6 | 19.9 | 0.7 | 637DE27304A04410A821590CD11FEF6D |  | R22 | Non-TXV |  | 7.656% | 0.92344 | 14.71% | [5 empty] | Non-TXV | 7.656%
San Jose | CA | 95122-4024 |  | 2013-10-16 | 2013-10-16 10:25 | 2013-10-16 10:45 | LENNOX - BID736A10004 | 84 | 6.6 | Yes | Yes | 21 | 21.5 | -0.5 | D4E0476113FE443089BDEC61AF5A5E93 |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Fresno | CA | 93703-1271 |  | 2013-10-21 | 2013-10-21 10:31 | 2013-10-21 10:52 | YORK - DE1NH036N05606C | 108 | 4.3 | Yes | Yes | 21.3 | 18.7 | 2.6 | 8C7661117FF3471B855E12CD604A661B |  | R22 | Non-TXV |  | 3.981% | 0.96019 | 7.652% | [5 empty] | Non-TXV | 3.981%
Fresno | CA | 93722-3117 |  | 2013-10-18 | 2013-10-18 10:46 | 2013-10-18 11:26 | CARRIER - UKN | 85 | 4.2 | Yes | Yes | 22.8 | 19.3 | 3.5 | 3BBCA76DA14D405A8CDFC80CCF98CF6D |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Livermore | CA | 94551-1675 |  | 2013-10-24 | 2013-10-24 11:20 | 2013-10-24 16:05 | AMANA - | 85 | 4.5 | Yes | Yes | 14 | 16.4 | -2.4 | 694E38402B1B47E2A4499C9D500C8D07 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Fresno | CA | 93710-5818 |  | 2013-10-18 | 2013-10-18 11:04 | 2013-10-18 11:32 | AMANA - PGA36B0702C | 112 | 3.3 | Yes | Yes | 22.7 | 20.4 | 2.3 | 8A2E23B9DF234C24844C656600917ADB |  | R22 | Non-TXV |  | 2.946% | 0.97054 | 5.662% | [5 empty] | Non-TXV | 2.946%
Fresno | CA | 93722-2306 |  | 2013-10-18 | 2013-10-18 12:21 | 2013-10-18 13:37 | CARRIER - 48SS042060331 | 84 | 4.8 | Yes | Yes | 23.3 | 20 | 3.3 | CFD46E20818445498CAB6160C3762454 |  | R22 | TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | TXV | 5.714%
Mc Farland | CA | 93250-1380 |  | 2013-10-16 | 2013-10-16 19:33 | 2013-10-16 19:36 | GOODMAN - CKL36-1D | 72 | -4.2 | Yes | Yes | 23 | 20.6 | 2.4 | 78A4CB6B621847B1AE88006F5CE774B4 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Mc Farland | CA | 93250-1505 |  | 2013-10-16 | 2013-10-16 19:17 | 2013-10-16 19:19 | AMERICAN STANDARD - YCY030G1M0AD | 85 | 4.9 | Yes | Yes | 26.7 | 22.9 | 3.8 | 881142A5DC3C4614A3FCCE1FF0596C63 |  | R410A | TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | TXV | 5.765%
Fresno | CA | 93727-3541 |  | 2013-10-21 | 2013-10-21 12:04 | 2013-10-21 12:34 | BRYANT - 582ANW04206AAG | 100 | 4.6 | Yes | Yes | 22.6 | 20.4 | 2.2 | 6EADDD454C8C4E95B1F06E2B427E9A96 |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Wasco | CA | 93280-2621 |  | 2013-10-20 | 2013-10-20 17:49 | 2013-10-20 17:52 | ARCOAIRE - PGF342080K01A1 | 188 | 7.4 | Yes | Yes | 20.8 | 20.9 | -0.1 | E1A1B2EC155A44EDB063EF0CE8303AC6 |  | R22 | Non-TXV |  | 3.936% | 0.96064 | 7.564% | [5 empty] | Non-TXV | 3.936%
Fresno | CA | 93727-3245 |  | 2013-10-17 | 2013-10-17 16:21 | 2013-10-17 17:28 | OTHER - UKN | 85 | -5.1 | Yes | Yes | 21.1 | 20.2 | 1 | 1B4D2E3671E640B9A811856BFC529222 |  | R22 | TXV |  | -6% | 1.06 | 1.68% |  |  |  |  | TXV |  |  | -6%
Bakersfield | CA | 93308-1823 |  | 2013-10-23 | 2013-10-23 14:20 | 2013-10-23 14:20 | YORK - D3NZ036N05606NXB | 64 | 0 | Yes | Yes | 19.1 | 20.6 | -1.5 | D04BF490D46B4746AD08238CF9D3953A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1380 |  | 2013-10-16 | 2013-10-16 19:27 | 2013-10-16 19:27 | OTHER - 38BRC42320 | 108 | 0 | Yes | Yes | 20.9 | 21.4 | -0.5 | CF3999787F6A404E9726C7881C1A2B08 | Add refrigerant: 23.8 oz Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4609 |  | 2013-10-23 | 2013-10-23 15:34 | 2013-10-23 15:34 | RUUD - URGH07E36JKR | 81 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | F12A5EE658D447D5914DBF39EF134F34 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2767 |  | 2013-10-21 | 2013-10-21 13:06 | 2013-10-21 13:06 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.4 | 21.2 | 0.2 | 686B8576518747EBBF5B818C588CFE2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1149 |  | 2013-10-16 | 2013-10-16 12:04 | 2013-10-16 12:04 | GOODMAN - GPG1342070M41BA | 81 | 0 | Yes | Yes | 21.1 | 20.6 | 0.5 | 1BD19CC962F341888FDB8F760AA35089 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-1038 |  | 2013-10-16 | 2013-10-16 10:03 | 2013-10-16 10:23 | GOODMAN - UNK | 70 | 3.1 | Yes | Yes | 18.9 | 20.4 | -1.5 | B35C0210D67041A6A00953CB04ADC6A3 |  | R410A | Non-TXV |  | 4.429% | 0.95571 | 8.511% | [5 empty] | Non-TXV | 4.429%
Fresno | CA | 93711-1517 |  | 2013-10-18 | 2013-10-18 13:45 | 2013-10-18 14:07 | YORK - DBYPF030N070A | 72 | 4.8 | Yes | Yes | 25.2 | 22.6 | 2.6 | C13701E3D62C470EB62F46E386C0ADD4 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Bakersfield | CA | 93308-1120 |  | 2013-10-22 | 2013-10-22 13:17 | 2013-10-22 13:17 | CARRIER - 48SS036060321 | 67 | 0 | Yes | Yes | 24.1 | 23.2 | 0.9 | 67470B43E08B4B7CA67B6B98AAE69D4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-9648 |  | 2013-10-16 | 2013-10-16 19:22 | 2013-10-16 19:24 | YORK - D3NZ042N06506NX | 78 | 4.3 | Yes | Yes | 22.2 | 20.6 | 1.6 | 4CCE1DD2EB8446E9896C7FA6E0853D62 |  | R410A | TXV |  | 5.513% | 0.94487 | 10.59% | [5 empty] | TXV | 5.513%
Clovis | CA | 93611-3008 |  | 2013-10-17 | 2013-10-17 10:52 | 2013-10-17 10:52 | ARCOAIRE - PGMD36G0601 | 81 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 7FC6EA15D4CF40E59D6B66553D7D2A44 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-4104 |  | 2013-10-21 | 2013-10-21 09:18 | 2013-10-21 09:53 | BRYANT - 561CJ048-A | 104 | -11 | Yes | Yes | 23.5 | 19.3 | 4.2 | 05D1AA165D874745933630D1638B8845 |  | R22 | Non-TXV |  | -10.58% | 1.1058 | 2.962% |  |  |  |  | Non-TXV |  |  | -10.58%
Kerman | CA | 93630-1931 |  | 2013-10-29 | 2013-10-29 11:30 | 2013-10-29 12:00 | LENNOX - 10GCS030X751PA | 51 | 4 | Yes | Yes | 21.1 | 18.2 | 2.9 | A4F5055294134FB79E9E2F7E47680FB6 |  | R22 | Non-TXV |  | 7.843% | 0.92157 | 15.07% | [5 empty] | Non-TXV | 7.843%
Fresno | CA | 93726-3431 |  | 2013-10-17 | 2013-10-17 11:06 | 2013-10-17 11:35 | YORK - D1NP042N06506A | 150 | 4.6 | Yes | Yes | 20.6 | 19.9 | 0.7 | B564AEA6BE4D43F1ABBFC872332906AB |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Pittsburg | CA | 94565-0000 |  | 2013-10-22 | 2013-10-22 12:52 | 2013-10-22 13:45 | WEATHER KING - 13AJA36A01 | 108 | 3.9 | Yes | Yes | 14.5 | 16.3 | -1.8 | 1A0743B80EFB4135A9946E2448BD3B5F |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Fresno | CA | 93722-3692 |  | 2013-10-23 | 2013-10-23 13:52 | 2013-10-23 14:11 | CARRIER - UNK | 76 | 10.8 | Yes | Yes | 20.1 | 19.3 | 0.8 | 6CC84D02414847F887FFF9E97DA3B3DE |  | R22 | Non-TXV |  | 14.21% | 0.85789 | 27.31% | [5 empty] | Non-TXV | 14.21%
Kerman | CA | 93630-9363 |  | 2013-10-24 | 2013-10-24 14:45 | 2013-10-24 21:54 | CARRIER - 48GX036060301 | 82 | 4.1 | Yes | Yes | 21.5 | 20.3 | 1.2 | 58291235E0DB439385D864893EA4B985 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Wasco | CA | 93280-2101 |  | 2013-10-31 | 2013-10-31 18:20 | 2013-10-31 18:22 | OTHER - N/A | 85 | -6 | Yes | Yes | 23.1 | 21.7 | 1.5 | 2531263E514243B49920A71FF71C1179 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93308-4800 |  | 2013-10-23 | 2013-10-23 18:32 | 2013-10-23 18:32 | GOODMAN - GPG1324045M41BA | 68 | 0 | Yes | Yes | 21.3 | 21.3 | 0.1 | B69616408E03470AA9DFE411D9F197D9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1717 |  | 2013-10-21 | 2013-10-21 18:28 | 2013-10-21 18:30 | CARRIER - 48SX-03680321AA | 84 | 4.2 | Yes | Yes | 23.9 | 19.1 | 4.8 | 3BB90073F2C44D27BBD004B207D9E667 |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Fresno | CA | 93722-4752 |  | 2013-10-16 | 2013-10-16 12:37 | 2013-10-16 13:05 | AMANA - PGD36C0702E | 110 | 16.6 | Yes | Yes | 23.6 | 19.9 | 3.7 | 3246816D01354C8A9B9D0FD23F30F62C |  | R22 | Non-TXV |  | 15.09% | 0.84909 | 29% | [5 empty] | Non-TXV | 15.09%
Sanger | CA | 93657-2728 |  | 2013-10-18 | 2013-10-18 09:29 | 2013-10-18 10:16 | TEMPSTAR - PGD336060K001C1 | 102 | -6 | Yes | Yes | 24.4 | 19.5 | 4.9 | 9BB7171C662A4C7AAFDAB27EF1000387 |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93725-1827 |  | 2013-10-18 | 2013-10-18 11:17 | 2013-10-18 11:37 | CARRIER - 48GP03606060311 | 110 | 5.2 | Yes | Yes | 20.3 | 18.2 | 2.1 | DD4B98ED32D3448A9ADA6E00E9F4F612 |  | R410A | Non-TXV |  | 4.727% | 0.95273 | 9.085% | [5 empty] | Non-TXV | 4.727%
Fresno | CA | 93710-4345 |  | 2013-10-16 | 2013-10-16 12:55 | 2013-10-16 13:28 | YORK - D1NH036N05606C | 108 | 3.2 | Yes | Yes | 19.5 | 20.3 | -0.8 | AF03CD42958E407C881F9FAD84B217B8 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Wasco | CA | 93280-3206 |  | 2013-10-20 | 2013-10-20 17:18 | 2013-10-20 17:20 | TEMPSTAR - PGSD30D1K4 | 78 | -2.9 | Yes | Yes | 25.8 | 20.9 | 4.9 | 68F82E0E13C44D8FB2E31960E004AD34 |  | R22 | TXV |  | -3.718% | 1.0372 | 1.041% |  |  |  |  | TXV |  |  | -3.718%
Vacaville | CA | 95687-6657 |  | 2013-10-25 | 2013-10-25 13:09 | 2013-10-25 13:09 | GIBSON - JS5BD-048KA | 126 | 0 | Yes | Yes | 16.1 | 18.9 | -2.8 | C4880711B8424287BD0DAEA06DA37DF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1445 |  | 2013-10-22 | 2013-10-22 14:56 | 2013-10-22 15:29 | AMERICAN STANDARD - YCC048F1MOBH | 100 | 4.4 | Yes | Yes | 20.2 | 21 | -0.8 | FD157B693E77401A865D66FDB7403B74 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Wasco | CA | 93280-2725 |  | 2013-10-20 | 2013-10-20 17:59 | 2013-10-20 18:04 | HEIL - PGAD36D1K7----- | 100 | 5 | Yes | Yes | 27.2 | 24 | 3.2 | 474DA57FB3A64F82B8012E19F4EF3D7A |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Wasco | CA | 93280-2228 |  | 2013-10-21 | 2013-10-21 19:08 | 2013-10-21 19:11 | TEMPSTAR - PGD44209OK001C1 | 140 | 10.5 | Yes | Yes | 21.5 | 19.3 | 2.2 | C121AF9C6E754B8CA81CEFDF007CC1DF |  | R410A | TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | TXV | 7.5%
Shafter | CA | 93263-1770 |  | 2013-10-24 | 2013-10-24 20:19 | 2013-10-24 20:22 | WEATHER KING - 13AJA48A01 | 124 | -7.3 | Yes | Yes | 22.1 | 19.8 | 2.3 | 75430839A0464715A1325FAD08A99AC3 |  | R22 | TXV |  | -5.887% | 1.0589 | 1.649% |  |  |  |  | TXV |  |  | -5.887%
Shafter | CA | 93263-3535 |  | 2013-10-22 | 2013-10-22 17:15 | 2013-10-22 17:17 | GOODMAN - GPG10300701A | 50 | 6 | Yes | Yes | 21.7 | 19.8 | 1.9 | E107C5C0792040BCB3E4E7DB82125385 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Shafter | CA | 93263-3535 |  | 2013-10-22 | 2013-10-22 17:11 | 2013-10-22 17:14 | GOODMAN - GPG10300701A | 50 | 8 | Yes | Yes | 21 | 20.1 | 0.9 | B032371D71CD4B4CA2983C9FB2018434 |  | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Wasco | CA | 93280-9776 |  | 2013-10-31 | 2013-10-31 17:40 | 2013-10-31 17:42 | DUCANE - SG10B36075 | 82 | 4.2 | Yes | Yes | 20.9 | 19.7 | 1.2 | 89E76F89BD714152B81934CBA7DF1EAE |  | R22 | Non-TXV |  | 5.122% | 0.94878 | 9.843% | [5 empty] | Non-TXV | 5.122%
Bakersfield | CA | 93304-6540 |  | 2013-10-17 | 2013-10-17 13:28 | 2013-10-17 13:28 | RHEEM - RRKA-A024JK06E | 69 | 0 | Yes | Yes | 21.8 | 21.3 | 0.6 | 374E5A48607749EB8519474F8EE5CB56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3405 |  | 2013-10-23 | 2013-10-23 12:46 | 2013-10-23 12:47 | WHIRLPOOL - 36T0944167G | 57 | -4 | Yes | Yes | 16.9 | 17.6 | -0.7 | FA9C2A468406445DAC9909CFE142FC0B |  | R22 | Non-TXV |  | -7.018% | 1.0702 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.018%
Wasco | CA | 93280-2596 |  | 2013-11-04 | 2013-11-04 15:30 | 2013-11-04 15:32 | OTHER - CCU12A30A-1 | 90 | 4.1 | Yes | Yes | 22.3 | 20.6 | 1.7 | 771EC6D5A6D14E32B1A7D8C38E82BA5E |  | R22 | Non-TXV |  | 4.556% | 0.95444 | 8.755% | [5 empty] | Non-TXV | 4.556%
Wasco | CA | 93280-1812 |  | 2013-10-21 | 2013-10-21 18:20 | 2013-10-21 18:23 | RHEEM - N/A | 85 | 9.8 | Yes | Yes | 20.8 | 19.5 | 1.3 | 04455214B6B642D1B798AED2F722A86F |  | R22 | Non-TXV |  | 11.53% | 0.88471 | 22.16% | [5 empty] | Non-TXV | 11.53%
Wasco | CA | 93280-2221 |  | 2013-10-17 | 2013-10-17 21:14 | 2013-10-18 07:51 | AMERICAN STANDARD - YCY042G1MAD | 147 | 4.9 | Yes | Yes | 20.1 | 20.7 | -0.5 | 010F72A6959E4A30A743612F987A5D64 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93304-6526 |  | 2013-10-17 | 2013-10-17 14:24 | 2013-10-17 14:24 | GOODMAN - GPG1324045M41AA | 90 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 5A6637E018964F9D99D43E2E20DA9BA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2765 |  | 2013-10-29 | 2013-10-29 15:14 | 2013-10-29 15:33 | OTHER - AC024X1321A | 88 | 3.6 | Yes | Yes | 22 | 19.7 | 2.4 | 4D698A28542D48AE98C5608EF1575529 |  | R22 | TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | TXV | 4.091%
San Jose | CA | 95135-1305 |  | 2013-10-22 | 2013-10-22 13:35 | 2013-10-22 14:09 | GE - TA9224H1H1 | 70 | 7.9 | Yes | Yes | 19 | 21.9 | -2.9 | 712A5CE0230C4451A499AFECC0C6FE38 |  | R22 | Non-TXV |  | 11.29% | 0.88714 | 21.69% | [5 empty] | Non-TXV | 11.29%
Shafter | CA | 93263-1770 |  | 2013-10-22 | 2013-10-22 18:15 | 2013-10-22 18:18 | OTHER - G2C130361FA | 83 | 8.6 | Yes | Yes | 19.5 | 19.8 | -0.3 | 46A40ED14A7A474EB387CF78829928A0 |  | R22 | TXV |  | 10.36% | 0.89639 | 19.91% | [5 empty] | TXV | 10.36%
Santa Rosa | CA | 95409-3454 |  | 2013-10-22 | 2013-10-22 11:24 | 2013-10-22 11:24 | BRYANT - 561C036-F | 124 | 0 | Yes | Yes | 19.4 | 16.2 | 3.2 | 90FA34100FC245E7AA8845EE1D6187E1 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2768 |  | 2013-10-29 | 2013-10-29 13:43 | 2013-10-29 14:38 | OTHER - N2A324AKA200 | 70 | 3 | Yes | Yes | 20.6 | 19.4 | 1.2 | 0FF6056DFA24402899C11D1694495883 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Shafter | CA | 93263-2309 |  | 2013-10-27 | 2013-10-27 19:03 | 2013-10-27 19:08 | HEIL - PG360K01A1 | 176 | 5.8 | Yes | Yes | 24.6 | 20.9 | 3.7 | 7B69ADA8FA2349CFB7279527C01A294B |  | R22 | Non-TXV |  | 3.295% | 0.96705 | 6.333% | [5 empty] | Non-TXV | 3.295%
Pittsburg | CA | 94565-7715 |  | 2013-10-24 | 2013-10-24 11:14 | 2013-10-24 11:15 | GOODMAN - CKL18-1C | 72 | 4 | Yes | Yes | 17 | 17.9 | -0.9 | 72F9D920D5AB41089BC5D125DC3F2B2E |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Wasco | CA | 93280-3118 |  | 2013-10-24 | 2013-10-24 18:51 | 2013-10-24 18:56 | COMFORT AIRE - PGC036K060E---- | 70 | 16.2 | Yes | Yes | 21.8 | 21.1 | 0.7 | 03D417EADEC143ADB8B3F41937643C56 |  | R22 | Non-TXV |  | 23.14% | 0.76857 | 44.48% | [5 empty] | Non-TXV | 23.14%
Pittsburg | CA | 94565-7714 |  | 2013-10-24 | 2013-10-24 11:07 | 2013-10-24 11:08 | GOODMAN - CKL18-1G | 72 | -5.1 | Yes | Yes | 16 | 17.5 | -1.5 | 240A0010307D4B6B8449FCA8228A43CC |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Bakersfield | CA | 93308-2069 |  | 2013-10-23 | 2013-10-23 18:03 | 2013-10-23 18:03 | COLEMAN - D4NZ060N06506NXA | 82 | 0 | Yes | Yes | 17.4 | 19.9 | -2.5 | D9A14046A8F54E46A4C1F4BB0F1CEB8A |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4800 |  | 2013-10-23 | 2013-10-23 18:45 | 2013-10-23 18:45 | BDP - 588ANW024040AAAE | 39 | 0 | Yes | Yes | 19.1 | 21.5 | -2.4 | A3E1F3F5344348D292E968FC71C51608 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4800 |  | 2013-10-23 | 2013-10-23 18:58 | 2013-10-23 18:58 | GOODMAN - GPG1324045M41BA | 68 | 0 | Yes | Yes | 20.2 | 21 | -0.8 | A1E705444ADE4DD9ACF65814E2E2AF46 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4800 |  | 2013-10-23 | 2013-10-23 19:15 | 2013-10-23 19:15 | ICP - WPG324040LKC1 | 85 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 788273CA30AC45B79C343EB3043EA0EB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2563 |  | 2013-10-29 | 2013-10-29 18:17 | 2013-10-29 18:19 | GOODMAN - GPG13480701AB | 145 | 8.6 | Yes | Yes | 25.3 | 20.6 | 4.7 | 38FBA3B0A32946F9BB2BA57BEF4A1C87 |  | R22 | Non-TXV |  | 5.931% | 0.94069 | 11.4% | [5 empty] | Non-TXV | 5.931%
Shafter | CA | 93263-2209 |  | 2013-10-24 | 2013-10-24 19:27 | 2013-10-24 19:30 | CLIMATEMASTER - PGC036K0B | 71 | -6.7 | Yes | Yes | 24.4 | 20.1 | 4.3 | 2E03EBC38B6D4AB3ACAC9FF4778CC4F4 |  | R22 | Non-TXV |  | -9.437% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.437%
Wasco | CA | 93280-2638 |  | 2013-10-29 | 2013-10-29 19:15 | 2013-10-29 19:17 | TEMPSTAR - PGF024K040F---- | 54 | 3.7 | Yes | Yes | 23.9 | 20.4 | 3.5 | FC7F6B45B36C471B9BBEB74E2698AA3E |  | R22 | Non-TXV |  | 6.852% | 0.93148 | 13.17% | [5 empty] | Non-TXV | 6.852%
Fresno | CA | 93727-7940 |  | 2013-10-28 | 2013-10-28 12:19 | 2013-10-28 12:50 | ARCOAIRE - PGF036K060D | 71 | 2.9 | Yes | Yes | 21.7 | 19.1 | 2.6 | 0ABD4DF98204429EB7E8EA8F67B1B6A6 |  | R22 | Non-TXV |  | 4.085% | 0.95915 | 7.85% | [5 empty] | Non-TXV | 4.085%
Wasco | CA | 93280-3119 |  | 2013-11-07 | 2013-11-07 18:40 | 2013-11-07 18:42 | GOODMAN - PGB030075-1B | 56 | 4.9 | Yes | Yes | 28 | 22.4 | 5.6 | 1FE9AB02F0E74A8A92CED62EAEF915A0 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Wasco | CA | 93280-3417 |  | 2013-10-24 | 2013-10-24 18:42 | 2013-10-24 18:45 | GOODMAN - PGB036050-1A | 60 | 2.5 | Yes | Yes | 24.5 | 20.8 | 3.7 | 680F2F1D540F4AA5A7355FD72AEDA859 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Wasco | CA | 93280-2132 |  | 2013-10-29 | 2013-10-29 18:21 | 2013-10-29 18:23 | TRANE - YCY036G1M0AD | 130 | 7.5 | Yes | Yes | 24.3 | 20.6 | 3.7 | EC8023CD01004FAF9808DE0385760BB9 |  | R22 | TXV |  | 5.769% | 0.94231 | 11.09% | [5 empty] | TXV | 5.769%
Wasco | CA | 93280-0000 |  | 2013-10-29 | 2013-10-29 18:51 | 2013-10-29 18:54 | GOODMAN - GPG1342070AA | 107 | 8.1 | Yes | Yes | 26.3 | 20.7 | 5.6 | D36F6F5A1BCE41EFA5DC14328CC102C7 |  | R22 | Non-TXV |  | 7.57% | 0.9243 | 14.55% | [5 empty] | Non-TXV | 7.57%
Shafter | CA | 93263-3160 |  | 2013-10-24 | 2013-10-24 19:08 | 2013-10-24 19:11 | OTHER - TCGD42S2151A | 88 | 6.8 | Yes | Yes | 22.2 | 20.9 | 1.3 | 15FB10BB7AD14961A20A79B68A9F621F |  | R22 | TXV |  | 7.727% | 0.92273 | 14.85% | [5 empty] | TXV | 7.727%
Shafter | CA | 93263-2210 |  | 2013-10-24 | 2013-10-24 19:20 | 2013-10-24 19:22 | CLIMATEMASTER - PGC36K060E----- | 68 | 4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 6812496EE9E34722AE0DEF56DD454A64 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Fresno | CA | 93702-4551 |  | 2013-11-09 | 2013-11-09 12:39 | 2013-11-09 13:06 | RHEEM - UNK | 64 | 4.1 | Yes | Yes | 22.6 | 20.4 | 2.2 | BF84877DED404C8B9F8981DACDE9596C |  | R22 | Non-TXV |  | 6.406% | 0.93594 | 12.31% | [5 empty] | Non-TXV | 6.406%
Fresno | CA | 93702-4593 |  | 2013-11-09 | 2013-11-09 13:09 | 2013-11-09 13:35 | RHEEM - UNK | 64 | 7.1 | Yes | Yes | 24.4 | 21 | 3.4 | 540AD61DAF284AC39138015AEC1F5468 |  | R22 | Non-TXV |  | 11.09% | 0.88906 | 21.32% | [5 empty] | Non-TXV | 11.09%
Shafter | CA | 93263-3520 |  | 2013-10-24 | 2013-10-24 19:02 | 2013-10-24 19:04 | GOODMAN - PGB036050-1A | 60 | 3.5 | Yes | Yes | 20 | 20.2 | -0.2 | E730A0842FE04E43B2723E28D619B1F0 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Fresno | CA | 93722-8408 |  | 2013-10-31 | 2013-10-31 15:00 | 2013-10-31 15:41 | YORK - H1RA036S06A | 69 | 6.5 | Yes | Yes | 20.7 | 19.3 | 1.4 | 07349E1826564B8DAE4F3CD12089C6E8 |  | R22 | Non-TXV |  | 9.42% | 0.9058 | 18.1% | [5 empty] | Non-TXV | 9.42%
Fresno | CA | 93702-4578 |  | 2013-11-09 | 2013-11-09 13:38 | 2013-11-09 14:15 | RHEEM - UNK | 64 | 3.2 | Yes | Yes | 22 | 19.5 | 2.5 | 090A30A957AF4D7C9645E1896794758A |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93704-4828 |  | 2013-10-30 | 2013-10-30 11:39 | 2013-10-30 12:11 | AMERICAN STANDARD - YCY042G1M0AC | 147 | 4.9 | Yes | Yes | 20.5 | 19.9 | 0.6 | E71A0644C0CB4971B741D1FD377372F1 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Kerman | CA | 93630-1747 |  | 2013-10-29 | 2013-10-29 10:41 | 2013-10-29 11:26 | RUUD - UNK | 74 | 3.1 | Yes | Yes | 21.7 | 19.1 | 2.6 | 7619FFA26EAC477789205615B33B1281 |  | R22 | Non-TXV |  | 4.189% | 0.95811 | 8.051% | [5 empty] | Non-TXV | 4.189%
Shafter | CA | 93263-2435 |  | 2013-10-27 | 2013-10-27 19:12 | 2013-10-27 19:18 | GOODMAN - GP134807M41AD | 125 | 4.5 | Yes | Yes | 21.6 | 19.7 | 1.9 | 843929B115B44C2D9B02644C3DE42DB7 |  | R410A | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Fresno | CA | 93711-6173 |  | 2013-11-07 | 2013-11-07 13:45 | 2013-11-07 14:07 | YORK - D3YS018N03206B | 52 | 2.3 | Yes | Yes | 21.3 | 18.7 | 2.6 | F33EEEBB1A2842F2A46BD55068C62D56 |  | R22 | Non-TXV |  | 4.423% | 0.95577 | 8.5% | [5 empty] | Non-TXV | 4.423%
Shafter | CA | 93263-2906 |  | 2013-10-27 | 2013-10-27 18:56 | 2013-10-27 18:59 | DAY & NIGHT - N/A | 85 | 3.3 | Yes | Yes | 24.3 | 18.7 | 5.6 | F21A2B8E6E2049AFA546FA9CE83E24B0 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Fresno | CA | 93711-6160 |  | 2013-11-07 | 2013-11-07 12:36 | 2013-11-07 12:54 | YORK - D2YS024N03206A | 62 | 3.7 | Yes | Yes | 21.5 | 18.7 | 2.8 | ABEA7973D9164160A8A071372BFFDD25 |  | R22 | Non-TXV |  | 5.968% | 0.94032 | 11.47% | [5 empty] | Non-TXV | 5.968%
Fresno | CA | 93701-1882 |  | 2013-11-09 | 2013-11-09 15:05 | 2013-11-09 15:44 | RHEEM - UNK | 64 | 3.9 | Yes | Yes | 21.6 | 19.9 | 1.7 | 462EBF9EFA4A4E8CA573098628B8E333 |  | R22 | Non-TXV |  | 6.094% | 0.93906 | 11.71% | [5 empty] | Non-TXV | 6.094%
Fresno | CA | 93722-2400 |  | 2013-10-29 | 2013-10-29 12:51 | 2013-10-29 13:41 | CARRIER - UKN | 84 | 4 | Yes | Yes | 19.9 | 19.1 | 0.8 | 23CBF8A86C2E4CE1B6E30E9DA420CF91 |  | R22 | Non-TXV |  | 4.762% | 0.95238 | 9.151% | [5 empty] | Non-TXV | 4.762%
Clovis | CA | 93611-5436 |  | 2013-10-29 | 2013-10-29 10:37 | 2013-10-29 10:37 | RUUD - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 2984034281CE487A981577CBCE593BC6 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2527 |  | 2013-11-07 | 2013-11-07 13:41 | 2013-11-07 14:05 | PAYNE - PA13NR024-H | 65 | -2.4 | Yes | Yes | 20.4 | 20.1 | 0.3 | AC9EF91FDB1841109CFE1AB1FD22372E |  | R22 | TXV |  | -3.692% | 1.0369 | 1.034% |  |  |  |  | TXV |  |  | -3.692%
Clovis | CA | 93612-2518 |  | 2013-10-30 | 2013-10-30 16:43 | 2013-10-30 17:51 | BRYANT - 561CJ024-D | 58 | 1.7 | Yes | Yes | 18.8 | 19.9 | -1.1 | A8B7A242ADCE40E88B154F58DD6874FA |  | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Fresno | CA | 93710-4823 |  | 2013-11-01 | 2013-11-01 13:39 | 2013-11-01 13:39 | DAY & NIGHT - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D443B4BAF4CF438E88CD58B69685D66A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5842 |  | 2013-10-30 | 2013-10-30 13:45 | 2013-10-30 14:08 | AMERICAN STANDARD - YCC030F1M0BJ | 72 | 3.2 | Yes | Yes | 21.7 | 19.5 | 2.2 | 051BE18B37884D5FA3741D7577E831BE |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Fresno | CA | 93722-7163 |  | 2013-10-29 | 2013-10-29 11:56 | 2013-10-29 12:49 | GIBSON - JS3BC036KA | 82 | 4 | Yes | Yes | 21.4 | 20 | 1.4 | 3DA6E59EBAD142E4B2665B5A3AF53B21 |  | R22 | Non-TXV |  | 4.878% | 0.95122 | 9.375% | [5 empty] | Non-TXV | 4.878%
Fresno | CA | 93705-2926 |  | 2013-10-30 | 2013-10-30 12:13 | 2013-10-30 13:10 | DAY & NIGHT - UKN | 67 | 3.4 | Yes | Yes | 20.6 | 19.3 | 1.3 | 21EC9572E1894E518B0B14BB6F40A354 |  | R22 | Non-TXV |  | 5.075% | 0.94925 | 9.752% | [5 empty] | Non-TXV | 5.075%
Fresno | CA | 93710-6223 |  | 2013-10-31 | 2013-10-31 10:04 | 2013-10-31 10:26 | TRANE - 4YCC3048A1096AB | 131 | -7.7 | Yes | Yes | 21.3 | 17.7 | 3.6 | AF676E8E3C634E65A9E4B30588C67C7E |  | R410A | Non-TXV |  | -5.878% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.878%
Fresno | CA | 93726-7413 |  | 2013-10-28 | 2013-10-28 14:21 | 2013-10-28 14:47 | CARRIER - UNK | 76 | 2.4 | Yes | Yes | 21.1 | 18.7 | 2.4 | BA7D61056F4A48878D25FEF6612E5F1A |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Fresno | CA | 93720-1840 |  | 2013-10-30 | 2013-10-30 11:36 | 2013-10-30 12:23 | - NCA036AKA4 | 87 | 3.3 | Yes | Yes | 21.8 | 19.3 | 2.5 | E6B49A31DB064FAD8167114F5C5E1C19 |  | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Clovis | CA | 93612-2528 |  | 2013-10-29 | 2013-10-29 14:24 | 2013-10-29 14:51 | BRYANT - 561CJ018-D | 52 | -3.1 | Yes | Yes | 21.5 | 20.1 | 1.4 | 995BBAA776B64A169094A6CE16B3D2DE |  | R22 | Non-TXV |  | -5.962% | 1.0596 | 1.67% |  |  |  |  | Non-TXV |  |  | -5.962%
Fresno | CA | 93726-4205 |  | 2013-10-28 | 2013-10-28 14:58 | 2013-10-28 15:29 | GOODMAN - GPG13300451AC | 77 | 4.6 | Yes | Yes | 22.1 | 19.1 | 3 | 379B98B3BFF54F2381F9A9175611B5D2 |  | R22 | Non-TXV |  | 5.974% | 0.94026 | 11.48% | [5 empty] | Non-TXV | 5.974%
Fresno | CA | 93726-4205 |  | 2013-10-28 | 2013-10-28 15:36 | 2013-10-28 16:17 | LENNOX - 12GCS024502PA | 72 | 2.3 | Yes | Yes | 21.3 | 19.1 | 2.2 | 3ACA84C627B94003A97886149727B3A0 |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Fresno | CA | 93705-3316 |  | 2013-10-30 | 2013-10-30 13:13 | 2013-10-30 13:49 | CARRIER - UKN | 89 | 8.4 | Yes | Yes | 19.7 | 19.4 | 0.3 | 2120ADF2D2514109A9327DF560192625 |  | R22 | Non-TXV |  | 9.438% | 0.90562 | 18.14% | [5 empty] | Non-TXV | 9.438%
Bakersfield | CA | 93313-4107 |  | 2014-05-03 | 2014-05-03 14:47 | 2014-05-03 14:47 | - | 85 | 0 | Yes | Yes | 19.5 | 20.3 | -0.8 | A3F0C42286064BE5B19A3C45C5221B6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-1820 |  | 2014-10-30 | 2014-10-30 16:14 | 2014-10-30 16:33 | RHEEM - RRKA-A036JK06X | 85 | 6.8 | Yes | Yes | 16.6 | 19.6 | -3 | CF457A3849E04E7E9A1240114D089243 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Bakersfield | CA | 93304-5173 |  | 2014-10-15 | 2014-10-15 14:09 | 2014-10-15 14:09 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 21 | 21.5 | -0.5 | D3638FF2CED240308A74F4C15E819626 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6434 |  | 2014-05-29 | 2014-05-29 12:19 | 2014-05-29 12:55 | RHEEM - RAFD-048JBS | 101 | 21.7 | Yes | Yes | 17.5 | 19.9 | -2.4 | BC2A542518AB42B1A4D911EBF9AE05FA |  | R22 | Non-TXV |  | 21.49% | 0.78515 | 41.29% | [5 empty] | Non-TXV | 21.49%
Bakersfield | CA | 93304-5173 |  | 2014-10-15 | 2014-10-15 14:29 | 2014-10-15 14:29 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 21.5 | 22 | -0.5 | 73CFADEC61E94D96B6CB7AED73CBB2EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5119 |  | 2014-05-22 | 2014-05-22 08:29 | 2014-05-22 13:21 | CARRIER - 38CKC036350 | 73 | 6.7 | Yes | Yes | 12.5 | 15.3 | -2.8 | 57BF782119014388A1C222D9193BFCE0 |  | R22 | Non-TXV |  | 9.178% | 0.90822 | 17.64% | [5 empty] | Non-TXV | 9.178%
Suisun City | CA | 94585-3789 |  | 2014-05-09 | 2014-05-09 13:00 | 2014-05-09 13:00 | CARRIER - 24ABA342A310 | 92 | 0 | Yes | Yes | 15 | 17.5 | -2.5 | DBC03C5E7D65402E97A1CDE553256B96 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5174 |  | 2014-10-15 | 2014-10-15 15:08 | 2014-10-15 15:08 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 22.5 | 23.1 | -0.6 | 2C06A4552B2B47CEA9EFF9E27D7DDFAB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-7830 |  | 2014-05-21 | 2014-05-21 15:49 | 2014-05-21 15:49 | BDP - 541CD024 | 94 | 0 | Yes | Yes | 25.5 | 20.4 | 5.1 | DA8CE72AE3EA40B0BEB6CE50E368443C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6305 |  | 2014-05-09 | 2014-05-09 09:32 | 2014-05-09 16:02 | OTHER - CKH30 1B | 90 | 4.9 | Yes | Yes | 11.8 | 13.4 | -1.6 | 3B2C5061E69E452D84AFBEE8A46890C0 |  | R22 | Non-TXV |  | 5.444% | 0.94556 | 10.46% | [5 empty] | Non-TXV | 5.444%
Bakersfield | CA | 93308-7008 |  | 2014-09-14 | 2014-09-14 14:31 | 2014-09-14 14:31 | GOODMAN - GSH130301CB | 130 | 0 | Yes | Yes | 21 | 22.3 | -1.3 | 70422C1367B141E3A4EDC96A60FC7ECF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2070 |  | 2014-05-07 | 2014-05-07 12:40 | 2014-05-07 12:40 | - GCGD24S41S | 61 | 0 | Yes | Yes | 21 | 19.3 | 1.7 | F6FFF8039353471E8608F74E45BE88BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-7904 |  | 2014-05-22 | 2014-05-22 12:28 | 2014-05-22 12:51 | RUUD - UAKA060JAZ | 112 | -9.2 | Yes | Yes | 21.9 | 19.4 | 2.5 | 7918A3B14FF342F5902182690C71AF61 |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Vacaville | CA | 95688-8773 |  | 2014-05-05 | 2014-05-05 09:38 | 2014-05-05 14:36 | CARRIER - 38CKC036350 | 73 | 3.3 | Yes | Yes | 15.7 | 17.2 | -1.5 | BAB432C1A7814F5591F10BCFC764AFC4 |  | R22 | Non-TXV |  | 4.521% | 0.95479 | 8.687% | [5 empty] | Non-TXV | 4.521%
Fairfield | CA | 94533-4267 |  | 2014-07-28 | 2014-07-28 12:55 | 2014-07-28 16:15 | - | 85 | -8 | Yes | Yes | 15.3 | 18.2 | -2.9 | 05541149B7804D62AB526A08EAD947A2 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
W Sacramento | CA | 95691-5166 |  | 2014-05-07 | 2014-05-07 12:17 | 2014-05-07 15:37 | GOODMAN - CK49-1A | 90 | -5.4 | Yes | Yes | 14.6 | 16.9 | -2.3 | 33A5EE62BF2944C2A7EE1D60C49520DE |  | R22 | Non-TXV |  | -6% | 1.06 | 1.68% |  |  |  |  | Non-TXV |  |  | -6%
Antioch | CA | 94531-9363 |  | 2014-10-06 | 2014-10-06 10:37 | 2014-10-06 10:57 | YORK - H3RA060S06A | 106 | 27.7 | Yes | Yes | 19.1 | 21.3 | -2.1 | BE8A694570184969A7EA06C8AA8F7C4C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 26.13% | 0.73868 | 50.22% | [5 empty] | Non-TXV | 26.13%
Cupertino | CA | 95014-3467 |  | 2014-05-16 | 2014-05-16 15:19 | 2014-05-16 15:35 | YORK - E1RA024S06 | 80 | -10.4 | Yes | Yes | 22.1 | 18.7 | 3.4 | BE7AC05E11AF4BD889880E1281E9949F |  | R22 | Non-TXV |  | -13% | 1.13 | 3.641% |  |  |  |  | Non-TXV |  |  | -13%
American Canyon | CA | 94503-4601 |  | 2014-05-14 | 2014-05-14 13:26 | 2014-05-14 15:40 | CARRIER - 38BRCO36330 | 104 | -5.8 | Yes | Yes | 15.6 | 16.9 | -1.3 | 6FD7EA771A4548D5B28FB0AD5313CE03 |  | R22 | Non-TXV |  | -5.577% | 1.0558 | 1.562% |  |  |  |  | Non-TXV |  |  | -5.577%
Fairfield | CA | 94533-7200 |  | 2014-05-09 | 2014-05-09 08:16 | 2014-05-09 16:05 | YORK - | 85 | 3.1 | Yes | Yes | 19.4 | 19.2 | 0.2 | 8C50C3FC51A64671BD54EC1E97438AEA |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
W Sacramento | CA | 95691-5173 |  | 2014-05-07 | 2014-05-07 13:37 | 2014-05-07 13:37 | GOODMAN - CKL49-1 | 90 | 0 | Yes | Yes | 14.9 | 16.8 | -1.9 | F830D8EE29D14C70B73DA31DA9B0D3A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-0517 |  | 2014-05-20 | 2014-05-20 14:15 | 2014-05-20 14:15 | OTHER - | 85 | 0 | Yes | Yes | 17.6 | 18.3 | -0.7 | 07458CC39DA748ACBCCF0030E335551B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2068 |  | 2014-05-08 | 2014-05-08 09:45 | 2014-05-08 10:41 | DAY & NIGHT - 565A0024 | 70 | -2.6 | Yes | Yes | 19.5 | 22.2 | -2.7 | 7E8207E1107C43009ACA6C1467B5C0CE |  | R22 | Non-TXV |  | -3.714% | 1.0371 | 1.04% |  |  |  |  | Non-TXV |  |  | -3.714%
San Jose | CA | 95120-3804 |  | 2014-05-06 | 2014-05-06 09:29 | 2014-05-06 09:53 | PAYNE - PA13NA04800ACAA | 116 | -10.9 | Yes | Yes | 21.4 | 16.3 | 5.1 | AF8D885E2D32497796575BEA3D586C7D |  | R22 | Non-TXV |  | -9.397% | 1.094 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.397%
Bakersfield | CA | 93308-7011 |  | 2014-09-14 | 2014-09-14 19:47 | 2014-09-14 19:47 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 21.5 | 22.1 | -0.6 | 37673FF627494F1E8D4C3EDF783A58E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7003 |  | 2014-09-14 | 2014-09-14 14:41 | 2014-09-14 14:41 | GOODMAN - GSH130241BB | 127 | 0 | Yes | Yes | 22.6 | 22.6 | 0 | 950EFD2CAC664462B9BA5D6C9E0C69E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5524 |  | 2014-09-26 | 2014-09-26 10:01 | 2014-09-26 10:26 | CARRIER - PA13NR030-H | 75 | 2.7 | Yes | Yes | 18.2 | 19.9 | -1.7 | 300E35369EFA40DD8AAA26EF05F43B14 |  | R22 | TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | TXV | 3.6%
Suisun City | CA | 94585-2115 |  | 2014-05-08 | 2014-05-08 11:16 | 2014-05-08 11:16 | AMANA - RCE30C2C | 125 | 0 | Yes | Yes | 18.9 | 21.5 | -2.6 | 6303BE5BB87F4A55A358D2C2C678BC7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1762 |  | 2014-07-31 | 2014-07-31 13:44 | 2014-07-31 20:55 | CARRIER - 38EH036300 | 71 | -5.8 | Yes | Yes | 14.9 | 17.8 | -2.9 | D92AD40B86C6442D9409A06AC084EABE |  | R22 | Non-TXV |  | -8.169% | 1.0817 | 2.288% |  |  |  |  | Non-TXV |  |  | -8.169%
Antioch | CA | 94509-4761 |  | 2014-10-01 | 2014-10-01 09:14 | 2014-10-01 09:14 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 17.8 | 19.3 | -1.5 | 0BB3897CF6BE48E5B35F976A3B557C51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1728 |  | 2014-05-07 | 2014-05-07 08:46 | 2014-05-07 09:00 | BRYANT - 561CJ030 | 68 | -10.4 | Yes | Yes | 20.5 | 14.7 | 5.8 | B3864135527E4984B0561C2A25DD81D9 |  | R22 | Non-TXV |  | -15.29% | 1.1529 | 4.283% |  |  |  |  | Non-TXV |  |  | -15.29%
San Jose | CA | 95148-2537 |  | 2014-05-06 | 2014-05-06 08:27 | 2014-05-06 08:53 | AMANA - RCB42BA | 85 | 4.7 | Yes | Yes | 14.1 | 16.8 | -2.7 | B50D6F6DD94941F4B63EBFB6D114C057 |  | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Gilroy | CA | 95020-9582 |  | 2014-05-22 | 2014-05-22 09:10 | 2014-05-22 09:10 | RUUD - URKA-A030JK06 | 85 | 0 | Yes | Yes | 17.3 | 18.8 | -1.5 | 752399C40A3B477DB7A08D0B8788FA37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2509 |  | 2014-06-02 | 2014-06-02 13:34 | 2014-06-02 13:34 | UNITARY PRODUCTS GROUP - TCGD24S21S2HA | 51 | 0 | Yes | Yes | 16.4 | 17.7 | -1.3 | 1A1F841AD1264C2CB0841A2A3A12616F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1242 |  | 2014-05-12 | 2014-05-12 09:58 | 2014-05-12 09:58 | CARRIER - 38TDB048300 | 189 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 901C053607B8400787FFC59B778EE273 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95126-3186 |  | 2014-05-12 | 2014-05-12 13:44 | 2014-05-12 14:11 | BRYANT - 538ABA04800 | 121 | 4.8 | Yes | Yes | 14.3 | 17.3 | -3 | E4B494D6EB0E400DBACDD13A64CBBC9B |  | R22 | Non-TXV |  | 3.967% | 0.96033 | 7.624% | [5 empty] | Non-TXV | 3.967%
Vacaville | CA | 95688-4449 |  | 2014-05-05 | 2014-05-05 10:18 | 2014-05-05 14:26 | DAY & NIGHT - 588ANW024060ADAD | 38 | 2.9 | Yes | Yes | 13.9 | 15.7 | -1.8 | 2E09F02421F04E7A95A4A621B18C6E66 |  | R22 | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
Vacaville | CA | 95687-5665 |  | 2014-05-05 | 2014-05-05 10:54 | 2014-05-05 10:54 | BRYANT - 113RNA036-C | 92 | 0 | Yes | Yes | 13.9 | 16.4 | -2.5 | F573BD446EF94945A2292D8992E7464B | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7003 |  | 2014-09-14 | 2014-09-14 19:31 | 2014-09-14 19:31 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 22.5 | 22.6 | -0.1 | D2317196C9624266A7B9FE2DA2FC33F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7010 |  | 2014-09-14 | 2014-09-14 13:37 | 2014-09-14 13:37 | PAYNE - PH10JA030C | 86 | 0 | Yes | Yes | 20.5 | 22.1 | -1.6 | B627D55E8F8F46E0814DB7B9DDAAEB4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7012 |  | 2014-09-14 | 2014-09-14 19:58 | 2014-09-14 19:58 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 21.8 | 21.3 | 0.5 | D8F66A904AE3485FA955ABAB7263CCCF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7012 |  | 2014-09-14 | 2014-09-14 19:55 | 2014-09-14 19:55 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 23.6 | 21.5 | 2.1 | E623BC11EA3745D3BADC51BC7ACF8F0A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-4529 |  | 2014-06-17 | 2014-06-17 13:27 | 2014-06-17 13:27 | ICP - CA5542VKD2 | 98 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 40415C832BC14BBE89C263363E8F99DF | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6152 |  | 2014-06-20 | 2014-06-20 11:03 | 2014-06-20 11:03 | UNITARY PRODUCTS GROUP - D3NP02403606NXB | 100 | 0 | Yes | Yes | 20.9 | 23.2 | -2.3 | 050C0C7A0AE24AA19F472B808DE9EA9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6127 |  | 2014-06-05 | 2014-06-05 14:21 | 2014-06-05 14:21 | UNITARY PRODUCTS GROUP - D1NH042N06506C | 94 | 0 | Yes | Yes | 25.7 | 21 | 4.7 | C8A8ADC7CDCE46D78E1E9D2F7847A05F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2551 |  | 2014-05-28 | 2014-05-28 14:28 | 2014-05-29 08:17 | CARRIER - 24ABA342A310 | 100 | 3.1 | Yes | Yes | 18.8 | 18.8 | 0 | FE023878CA7D48388E740A95DB38E5F1 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Bakersfield | CA | 93301-2270 |  | 2014-05-10 | 2014-05-10 15:40 | 2014-05-10 15:40 | BDP - 585EJW030050ABAF | 58 | 0 | Yes | Yes | 23.2 | 20.2 | 3 | AF0754D18A0A47BCB1C1967ABCE4D05D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7006 |  | 2014-09-14 | 2014-09-14 19:33 | 2014-09-14 19:33 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 20.6 | 21.5 | -0.9 | 4C4035B749264C0190FF1EB7AF55B7E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7006 |  | 2014-09-14 | 2014-09-14 19:42 | 2014-09-14 19:42 | GOODMAN - GSH130241BA | 122 | 0 | Yes | Yes | 19.7 | 21 | -1.3 | 82F8533D256A4E0992D49BB30B96925C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7005 |  | 2014-09-14 | 2014-09-14 14:21 | 2014-09-14 14:21 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 21.3 | 21 | 0.3 | F9489B8E5E03412B9C98C2A6EF965031 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7008 |  | 2014-09-14 | 2014-09-14 14:02 | 2014-09-14 14:02 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 20.3 | 21.5 | -1.2 | 9FB3A6F89A7744D2BC3A5CAB99CBF4D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7000 |  | 2014-09-14 | 2014-09-14 13:16 | 2014-09-14 13:16 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 21.4 | 21.8 | -0.4 | 3E35ACE7658B4E1FAA4D3D82CDBB9129 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7000 |  | 2014-09-14 | 2014-09-14 14:15 | 2014-09-14 14:15 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 20.2 | 21.8 | -1.6 | 479CB4A6BEFD43B6914F02EB0B3F7D5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7009 |  | 2014-09-14 | 2014-09-14 19:21 | 2014-09-14 19:21 | GOODMAN - GSH130241BB | 122 | 0 | Yes | Yes | 21.9 | 22 | -0.1 | 0265825405F64D8D9664E01A70324B81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7008 |  | 2014-09-14 | 2014-09-14 13:44 | 2014-09-14 13:44 | GOODMAN - GSH130241BB | 122 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | CECE1BFFA9874429802442AC6A7900EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2644 |  | 2014-05-09 | 2014-05-09 12:52 | 2014-05-09 13:15 | CARRIER - 38CKC042 | 85 | -8 | Yes | Yes | 23.1 | 17.5 | 5.7 | 4D6A97FB0B3B4CFB81DDE8528290932B |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Vallejo | CA | 94590-4384 |  | 2014-05-14 | 2014-05-14 12:34 | 2014-05-14 15:44 | CARRIER - 38CKC048300 | 105 | -4.4 | Yes | Yes | 16.3 | 16.8 | -0.5 | D1ACFFD32C8E48F18F9CE461E1F07BD2 |  | R22 | Non-TXV |  | -4.19% | 1.0419 | 1.174% |  |  |  |  | Non-TXV |  |  | -4.19%
San Jose | CA | 95128-5217 |  | 2014-05-13 | 2014-05-13 09:41 | 2014-05-13 10:00 | PAYNE - PA100A036 | 87 | 6.4 | Yes | Yes | 16.1 | 15.8 | 0.3 | 53FB4FF9405743E1973145A56121BEAE |  | R22 | Non-TXV |  | 7.356% | 0.92644 | 14.14% | [5 empty] | Non-TXV | 7.356%
Wasco | CA | 93280-1532 |  | 2014-08-17 | 2014-08-17 17:48 | 2014-08-17 17:51 | CARRIER - 48SX-048080331AA | 94 | 21 | Yes | Yes | 27.3 | 22.5 | 4.8 | B89DD5D4FB5A436D91C08968ECA0C837 |  | R22 | Non-TXV |  | 22.34% | 0.7766 | 42.93% | [5 empty] | Non-TXV | 22.34%
Wasco | CA | 93280-2315 |  | 2014-07-28 | 2014-07-28 14:30 | 2014-07-28 14:32 | OTHER - PGAA36C1K4 | 69 | 8 | Yes | Yes | 21.7 | 20.4 | 1.3 | CCCBD3A2E4BB41E4816B459976A18CB6 |  | R22 | Non-TXV |  | 11.59% | 0.88406 | 22.28% | [5 empty] | Non-TXV | 11.59%
Arvin | CA | 93203-2203 |  | 2014-11-04 | 2014-11-04 16:20 | 2014-11-04 16:36 | OTHER - UNK | 85 | 11.7 | Yes | Yes | 25.6 | 24.5 | 1.1 | 1A45EE313D3F4D1B9E6FF39834F4BF02 |  | R22 | Non-TXV |  | 13.76% | 0.86235 | 26.45% | [5 empty] | Non-TXV | 13.76%
Arvin | CA | 93203-9451 |  | 2014-11-07 | 2014-11-07 13:27 | 2014-11-07 13:52 | GOODMAN - UNK | 118 | 9.9 | Yes | Yes | 17.8 | 20.7 | -2.9 | 91CB681F4A7A4EA6BBDD582F2ECC3DB5 |  | R22 | Non-TXV |  | 8.39% | 0.9161 | 16.12% | [5 empty] | Non-TXV | 8.39%
Davis | CA | 95618-7218 |  | 2014-05-28 | 2014-05-28 08:29 | 2014-05-28 08:58 | TRANE - BRCS3618D | 63 | -4.4 | Yes | Yes | 15.6 | 18.5 | -2.9 | E9C0F08358AE430894E778A2D5390C8E |  | R22 | Non-TXV |  | -6.984% | 1.0698 | 1.956% |  |  |  |  | Non-TXV |  |  | -6.984%
Santa Rosa | CA | 95405-7551 |  | 2014-05-20 | 2014-05-20 11:12 | 2014-05-20 11:37 | GOODMAN - CA-24-13 | 69 | -6.5 | Yes | Yes | 21.7 | 16.8 | 4.9 | 62FF2ABAA6894C87A2941DDE1C42D822 |  | R22 | Non-TXV |  | -9.42% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.42%
American Canyon | CA | 94503-1247 |  | 2014-05-15 | 2014-05-15 09:19 | 2014-05-15 09:19 | COMFORT AIRE - AD042GD | 141 | 0 | Yes | Yes | 12.7 | 15.2 | -2.5 | 31E832C120604E5586A63B2FF2A24432 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7125 |  | 2014-11-11 | 2014-11-11 10:48 | 2014-11-11 10:48 | TRANE - B1D7484100B0 | 128 | 0 | Yes | Yes | 24.6 | 18.7 | 5.9 | 4C11571BF5C548FFA6A24430AA137CC3 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5175 |  | 2014-10-15 | 2014-10-15 13:52 | 2014-10-15 13:52 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 21.7 | 22 | -0.3 | 73701612309440219C5B0AE7FA41BADA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4747 |  | 2014-09-15 | 2014-09-15 14:54 | 2014-09-15 15:19 | AMANA - ASC130481AD | 152 | 5.5 | Yes | Yes | 22.3 | 19.8 | 2.5 | 466F1F3423E4449DA88E85FA82A835D0 |  | R22 | Non-TXV |  | 3.618% | 0.96382 | 6.954% | [5 empty] | Non-TXV | 3.618%
Fairfield | CA | 94533-6565 |  | 2014-05-08 | 2014-05-08 10:38 | 2014-05-08 10:38 | - | 85 | 0 | Yes | Yes | 20.8 | 23.6 | -2.8 | C7C59F9393DC4053AF4BEB4CE6E3EB36 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7013 |  | 2014-09-14 | 2014-09-14 14:05 | 2014-09-14 14:05 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 20.6 | 23.1 | -2.5 | 4092E3D12250496FA163ED29A1E53F55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1776 |  | 2014-06-03 | 2014-06-03 13:23 | 2014-06-03 14:02 | AIRE-FLO - 591ANX030000ABAA | 68 | -4.6 | Yes | Yes | 20.7 | 17.6 | 3.1 | 736647DA650646E58BEC73DDEDE055B4 |  | R22 | Non-TXV |  | -6.765% | 1.0676 | 1.894% |  |  |  |  | Non-TXV |  |  | -6.765%
Davis | CA | 95616-0625 |  | 2014-05-28 | 2014-05-28 09:33 | 2014-05-28 14:30 | - | 34 | -6 | Yes | Yes | 16.7 | 17.9 | -1.2 | 74A5C3D40D6542DE9EC171A669895556 |  | R22 | Non-TXV |  | -17.65% | 1.1765 | 4.942% |  |  |  |  | Non-TXV |  |  | -17.65%
Fairfield | CA | 94533-2197 |  | 2014-05-07 | 2014-05-07 09:24 | 2014-05-07 09:24 | - | 85 | 0 | Yes | Yes | 10.5 | 12.6 | -2.1 | 6F131BAB11DC4B8E849248261B84FE64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1267 |  | 2014-04-30 | 2014-04-30 11:00 | 2014-04-30 11:00 | BDP - 585HJ024640 | 68 | 0 | Yes | Yes | 19.2 | 22.2 | -3 | 8580DEFE229446D480A4404E5E872078 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7012 |  | 2014-09-14 | 2014-09-14 13:40 | 2014-09-14 13:40 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 21.1 | 22 | -0.9 | 11CD37F6FB1940CF83DB7DDBCE6993AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2071 |  | 2014-05-08 | 2014-05-08 09:16 | 2014-05-08 10:40 | GUARDIAN - GCGD24S21S2A | 77 | 2.6 | Yes | Yes | 14.7 | 17.3 | -2.6 | 917027060132472482D06B06FAE66B24 |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Bakersfield | CA | 93306-2654 |  | 2014-08-26 | 2014-08-26 09:06 | 2014-08-26 09:06 | UNITARY PRODUCTS GROUP - D1NA036N05 | 67 | 0 | Yes | Yes | 21 | 22.4 | -1.4 | D796C499CEBD42A9B202A24109B3943C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1916 |  | 2014-05-07 | 2014-05-07 10:14 | 2014-05-07 10:49 | CARRIER - 38CKC036350 | 73 | 5.8 | Yes | Yes | 13.7 | 16.6 | -2.9 | E8C6836181FE49F7BB93CD9F40F9996B |  | R22 | Non-TXV |  | 7.945% | 0.92055 | 15.27% | [5 empty] | Non-TXV | 7.945%
San Jose | CA | 95121-1787 |  | 2014-05-06 | 2014-05-06 13:50 | 2014-05-06 14:11 | BRYANT - 567C048RLD | 76 | 10.6 | Yes | Yes | 14.7 | 17.5 | -2.8 | 2033D7C45F854E5A92D970B27B1FA07A |  | R22 | Non-TXV |  | 13.95% | 0.86053 | 26.8% | [5 empty] | Non-TXV | 13.95%
Bakersfield | CA | 93306-2654 |  | 2014-05-22 | 2014-05-22 11:55 | 2014-05-22 11:55 | UNITARY PRODUCTS GROUP - DBYP-F036N070A | 108 | 0 | Yes | Yes | 26.4 | 20.6 | 5.9 | 19B4490F7EAD471584F98B760522369A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3326 |  | 2014-05-05 | 2014-05-05 12:04 | 2014-05-05 12:04 | GE - BTB936A100A3 | 70 | 0 | Yes | Yes | 13.9 | 16.8 | -2.9 | CCE089A3AD1840958FBA9F79964936BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7006 |  | 2014-09-14 | 2014-09-14 19:26 | 2014-09-14 19:26 | YORK - ERHS0241BAA | 102 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | 3364B6BDA16E4F3EAA59C4B3E4D4D4C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2919 |  | 2014-05-23 | 2014-05-23 08:23 | 2014-05-23 15:54 | GOODMAN - GSC140361AE | 149 | 5.3 | Yes | Yes | 16.8 | 19.3 | -2.5 | 7294294A254843219E12A8C700B237FA |  | R22 | Non-TXV |  | 3.557% | 0.96443 | 6.836% | [5 empty] | Non-TXV | 3.557%
Bakersfield | CA | 93308-7004 |  | 2014-09-14 | 2014-09-14 13:22 | 2014-09-14 13:22 | GOODMAN - GSH130301CB | 130 | 0 | Yes | Yes | 20.5 | 22.1 | -1.6 | 30FB4E2E35A0464C82A3080D1C3A6B97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2804 |  | 2014-05-16 | 2014-05-16 17:37 | 2014-05-16 17:37 | OTHER - UKN | 90 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | 6E840EC39BEF4DB4A437125F361D7D21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2014-05-23 | 2014-05-23 16:31 | 2014-05-23 16:31 | ICP - C4A624GKD200E091901206 | 200 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | 6A1E767E999540CE8F7ADA2A8548D7A9 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 18:06 | 2014-05-22 18:06 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.4 | 22.6 | -2.2 | 60F9143F1E954F49ADF02FA2B52CA286 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 17:30 | 2014-05-23 17:46 | ICP - C4A624GKD200 | 200 | 21.6 | Yes | Yes | 20.8 | 21.3 | -0.5 | 03FFB6C4CEAA45CDA2B0284B1F00122E |  | R410A | TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | TXV | 10.8%
Bakersfield | CA | 93308-7005 |  | 2014-09-14 | 2014-09-14 14:36 | 2014-09-14 14:36 | YORK - ERHS0241BAA | 121 | 0 | Yes | Yes | 22.5 | 22 | 0.5 | 0EE9295C17CC49DBB78FE11C42F93536 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 17:12 | 2014-05-23 17:12 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | 18EAA880A0464F5B9490188C08B867D3 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2014-05-23 | 2014-05-23 16:52 | 2014-05-23 16:52 | ICP - C4A624GK200 | 200 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 2A74C8E8061C4EC095F0B86EF5F79D8D |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-1543 |  | 2014-05-06 | 2014-05-06 10:55 | 2014-05-06 11:41 | RHEEM - AT38B10 | 45 | -4.2 | Yes | Yes | 24.1 | 19.3 | 4.8 | 18FD6CE0FD344E10B49377B84BED3567 |  | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 16:49 | 2014-05-23 16:49 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | 7D642FA41F7F4D89BED1D651809BD480 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-3086 |  | 2014-05-13 | 2014-05-13 07:12 | 2014-05-13 07:12 | - | 85 | 0 | Yes | Yes | 20.3 | 23.2 | -2.9 | 13B9EF2400BB435C9328E824E5AD00DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6413 |  | 2014-05-05 | 2014-05-05 12:41 | 2014-05-05 12:53 | GE - BTB936A100C1297 | 83 | -4.9 | Yes | Yes | 14.7 | 16.7 | -2 | 595C287C44704DA6A213DA9FC6A4BBF3 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Fairfield | CA | 94534-6603 |  | 2014-05-06 | 2014-05-06 09:55 | 2014-05-06 13:51 | CARRIER - 38TKB036300 | 80 | -3.6 | Yes | Yes | 12.1 | 14.6 | -2.5 | 006DC3F452FF40989E374B7E94486A87 |  | R22 | Non-TXV |  | -4.5% | 1.045 | 1.26% |  |  |  |  | Non-TXV |  |  | -4.5%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 17:48 | 2014-05-23 17:48 | ICP - C4A62GKD200 | 200 | 0 | Yes | Yes | 21.5 | 20.7 | 0.8 | B8313B6FE83149FBB81D942C7D20057A |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2014-05-23 | 2014-05-23 17:09 | 2014-05-23 17:09 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.3 | 21.4 | -0.1 | 7C11C7DFE1AE466C8C8ABCD2E481CE87 |  | R410A | TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3117 |  | 2014-05-12 | 2014-05-12 08:15 | 2014-05-13 07:09 | - 8RCS0301SB | 70 | 2.7 | Yes | Yes | 17.9 | 20.8 | -2.9 | 01278B1F3BC34AC6A6112B2C093ABA62 |  | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
San Jose | CA | 95136-4844 |  | 2014-05-06 | 2014-05-06 12:06 | 2014-05-06 12:27 | CARRIER - 38HDL030 | 84 | -9.9 | Yes | Yes | 21 | 18.8 | 2.2 | E2A8FCDC147C4CEE94DB504D3F40360E |  | R22 | Non-TXV |  | -11.79% | 1.1179 | 3.301% |  |  |  |  | Non-TXV |  |  | -11.79%
San Jose | CA | 95111-1805 |  | 2014-05-09 | 2014-05-09 14:09 | 2014-05-09 14:09 | AMERICAN STANDARD - 4A7A-4200A100 | 85 | 0 | Yes | Yes | 10.9 | 13.2 | -2.3 | 4710FF6912EF49629E18AFC042810E5E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-9641 |  | 2014-05-19 | 2014-05-19 10:22 | 2014-05-19 10:40 | YORK - GCDG60S41S3 | 86 | 4.7 | Yes | Yes | 14.3 | 16.8 | -2.5 | 6F23F71594754DC7B3FE54C90DF33195 |  | R410A | Non-TXV |  | 5.465% | 0.94535 | 10.5% | [5 empty] | Non-TXV | 5.465%
Sunnyvale | CA | 94085-2358 |  | 2014-05-16 | 2014-05-16 10:31 | 2014-05-16 13:38 | AMANA - RCB024C24 | 90 | 12 | Yes | Yes | 15.1 | 17.9 | -2.8 | E4AA34F24CD04106BE711B55E72DB927 |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
San Jose | CA | 95123-5002 |  | 2014-05-09 | 2014-05-09 09:12 | 2014-05-09 09:20 | AIRE-FLO - CKL30-16 | 74 | -7 | Yes | Yes | 21.3 | 16.8 | 4.5 | 6F6CF1B7A3C7435BA57BDF58FA252015 |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Napa | CA | 94558-1977 |  | 2014-06-24 | 2014-06-24 10:30 | 2014-06-24 10:50 | COLEMAN - BRCS048B | 110 | 7.2 | Yes | Yes | 18.1 | 19.3 | -1.2 | D2CAD2481E7148A5A3CAE31AE006E590 |  | R22 | Non-TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | Non-TXV | 6.545%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 18:52 | 2014-05-23 18:52 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | 4D5095AB73D045088DC8A4552F5A7175 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4348 |  | 2014-05-13 | 2014-05-13 13:45 | 2014-05-13 16:30 | DAY & NIGHT - 591ANX036000AAAA | 84 | -5.4 | Yes | Yes | 20 | 22.6 | -2.6 | A871DE94B46041F9B85D48CFCED1CD5E |  | R22 | Non-TXV |  | -6.429% | 1.0643 | 1.8% |  |  |  |  | Non-TXV |  |  | -6.429%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 18:34 | 2014-05-23 18:34 | ICP - C4A624GK200 | 200 | 0 | Yes | Yes | 20.5 | 22.1 | -1.6 | 56780C7FC0E54FE7B49DA32FF4E64ACA |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7325 |  | 2014-07-25 | 2014-07-25 13:36 | 2014-07-25 15:56 | GOODMAN - GSH130241BA | 85 | 3.4 | Yes | Yes | 15.3 | 17.9 | -2.6 | 6739C8CC6D99483BB2965248DB9F6687 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93304-5185 |  | 2014-10-29 | 2014-10-29 12:27 | 2014-10-29 12:27 | BDP - 585EJ024050 | 54 | 0 | Yes | Yes | 25.5 | 21.5 | 4 | AB21975731A74873ACF3D9E8F0BE7A14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4562 |  | 2014-08-25 | 2014-08-25 09:16 | 2014-08-25 09:16 | UNITARY PRODUCTS GROUP - 73D1NA024N03606C | 50 | 0 | Yes | Yes | 25.9 | 23.4 | 2.6 | 67FF05C94D3B43DF81C72B16937B8655 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2072 |  | 2014-06-27 | 2014-06-27 10:55 | 2014-06-27 11:32 | BRYANT - 24ABA318A30010 | 74 | 6.4 | Yes | Yes | 13.5 | 16.4 | -2.9 | C82C0E1E8D3A461E8110B01E9D282363 |  | R410A | Non-TXV |  | 8.649% | 0.91351 | 16.62% | [5 empty] | Non-TXV | 8.649%
Bakersfield | CA | 93304-5185 |  | 2014-10-29 | 2014-10-29 12:33 | 2014-10-29 12:33 | BDP - 585EJ024050 | 54 | 0 | Yes | Yes | 24.7 | 20.4 | 4.3 | 74EFF5786E1243B3988B865A48594DFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1625 |  | 2014-05-06 | 2014-05-06 10:30 | 2014-05-06 13:52 | PAYNE - PA10JA036000ACAA | 74 | -3.2 | Yes | Yes | 12 | 15 | -3 | 5BC196815F9E45EFA0EA407E4031D43D |  | R22 | Non-TXV |  | -4.324% | 1.0432 | 1.211% |  |  |  |  | Non-TXV |  |  | -4.324%
Antioch | CA | 94531-8011 |  | 2014-05-21 | 2014-05-21 13:57 | 2014-05-21 13:57 | CARRIER - 38CKC048300 | 106 | 0 | Yes | Yes | 23.1 | 19.9 | 3.2 | 4FE6B279084D4863ADFB3D073C0E2F22 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 14:57 | 2014-05-21 15:14 | ICP - C4A624GKD200 | 200 | 12.2 | Yes | Yes | 19.5 | 19.9 | -0.4 | 124820F0F810473EA7B6271AE2EAEA81 |  | R22 | TXV |  | 6.1% | 0.939 | 11.72% | [5 empty] | TXV | 6.1%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 15:51 | 2014-05-21 15:51 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.1 | 22.1 | -1 | 5EF03487033C4C38A151E047BA2621F8 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5182 |  | 2014-10-29 | 2014-10-29 12:08 | 2014-10-29 12:08 | BRYANT - 583ANW024040NBAD | 57 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | EE1F3886C9104ABEA180EED56E470011 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 17:07 | 2014-05-22 17:34 | ICP - C4A624GKD200 | 200 | 22.4 | Yes | Yes | 22.6 | 23.7 | -1.1 | BAB3F1B60AC54670802C94A4F52F4091 |  | R410A | TXV |  | 11.2% | 0.888 | 21.52% | [5 empty] | TXV | 11.2%
Vallejo | CA | 94589-3724 |  | 2014-08-13 | 2014-08-13 16:16 | 2014-08-13 18:30 | CARRIER - | 67 | 4.4 | Yes | Yes | 22.9 | 20.4 | 2.5 | 75B11924C9D94FF0B981E041225DAE24 |  | R22 | Non-TXV |  | 6.567% | 0.93433 | 12.62% | [5 empty] | Non-TXV | 6.567%
Bakersfield | CA | 93312-6682 |  | 2014-09-26 | 2014-09-26 12:55 | 2014-09-26 12:55 | GOODMAN - GSC130421BB | 95 | 0 | Yes | Yes | 20.5 | 22.4 | -1.9 | 132332C39BD846118C850FF7195504B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6682 |  | 2014-09-26 | 2014-09-26 13:15 | 2014-09-26 13:15 | YORK - H1RD030S06G | 121 | 0 | Yes | Yes | 22.2 | 23.2 | -1 | C5ADE0924F0E4A999F7A9F5D129C8E14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2508 |  | 2014-11-05 | 2014-11-05 18:08 | 2014-11-05 18:24 | BRYANT - UNK | 85 | 4.8 | Yes | Yes | 22.2 | 21.8 | 0.5 | 3B20BB9BCDE24290BB3613809EB1C13A |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Wasco | CA | 93280-2307 |  | 2014-11-05 | 2014-11-05 10:10 | 2014-11-05 10:10 | GIBSON - JS5BD030KA | 99 | 0 | Yes | Yes | 19.3 | 18 | 1.4 | 8395D17D6DF34E678EE6CB38A15F68D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5688 |  | 2014-09-16 | 2014-09-16 11:31 | 2014-09-16 11:31 | LENNOX - GCS81E31180 | 100 | 0 | Yes | Yes | 22.5 | 21.8 | 0.7 | 8A4A33E25BC443FCAB8E05989836680B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 11:31 | 2014-10-16 11:31 | ICP - PGC030K060A | 56 | 0 | Yes | Yes | 23.4 | 20.9 | 2.5 | 01A8C7C89D30471E87168FB52C041248 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1401 |  | 2014-06-27 | 2014-06-27 11:12 | 2014-06-27 11:12 | LENNOX - GCS16R-651-125-5P | 112 | 0 | Yes | Yes | 26.6 | 20.7 | 5.9 | 6A01F03BC08B4A7EA92550C77804533C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5184 |  | 2014-10-29 | 2014-10-29 12:52 | 2014-10-29 12:52 | BRYANT - PY3GNAA24040NA | 77 | 0 | Yes | Yes | 22 | 20.1 | 1.9 | 42274F9578EF42A4B998EFF7F4457D76 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5425 |  | 2014-06-26 | 2014-06-26 10:48 | 2014-06-26 10:48 | BDP - 585CJ036075 | 90 | 0 | Yes | Yes | 21.8 | 20.8 | 1 | 94108462AF7A4868B3721CA9359339C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5425 |  | 2014-06-26 | 2014-06-26 10:51 | 2014-06-26 10:51 | BDP - 585CJ030075 | 90 | 0 | Yes | Yes | 25.5 | 20.7 | 4.9 | 4B1D76EE7EA5495A85B98E02EBAD07B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1475 |  | 2014-08-14 | 2014-08-14 09:42 | 2014-08-14 09:42 | OTHER - UKN | 90 | 0 | Yes | Yes | 19 | 17.3 | 1.8 | 1797D13AD92349A3B6D6E42096B2AD8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 18:24 | 2014-05-22 18:24 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | 556B10DA7ECB4CA9A943F1DFA695B551 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8107 |  | 2014-05-15 | 2014-05-15 13:33 | 2014-05-15 16:18 | CARRIER - 38EH030340 | 119 | 6.5 | Yes | Yes | 22 | 23.2 | -1.2 | 866F291574A740498C71D3C8065C2A26 |  | R22 | Non-TXV |  | 5.462% | 0.94538 | 10.5% | [5 empty] | Non-TXV | 5.462%
Bakersfield | CA | 93306-4353 |  | 2014-05-02 | 2014-05-02 11:57 | 2014-05-02 11:57 | BRYANT - 574ANW024040NA | 120 | 0 | Yes | Yes | 19.8 | 22.7 | -2.9 | 9142D6BCA6344B0B9A8ABF955AD7A8F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2934 |  | 2014-07-07 | 2014-07-07 11:28 | 2014-07-07 11:28 | UNITARY PRODUCTS GROUP - D1NH024N03606C | 70 | 0 | Yes | Yes | 20 | 21.7 | -1.7 | BF83B7A2D2CE47A09BD157D3FDFAF156 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3676 |  | 2014-09-23 | 2014-09-23 14:51 | 2014-09-23 14:51 | HEIL - UKN | 90 | 0 | Yes | Yes | 21 | 22.1 | -1.1 | 7ACB298E848D462CA88713E6FFA1B009 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3397 |  | 2014-05-09 | 2014-05-09 10:19 | 2014-05-09 10:19 | ICP - PGP342080K01A1 | 184 | 0 | Yes | Yes | 21.7 | 19.5 | 2.2 | EA778E58FC11401FA410C3691CF658F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 16:12 | 2014-05-23 16:12 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19 | 21.2 | -2.2 | 7F471582A97B4738A1008270EFB42F58 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5184 |  | 2014-10-29 | 2014-10-29 13:28 | 2014-10-29 13:28 | BRYANT - 582ANW024040AAAD | 56 | 0 | Yes | Yes | 24.2 | 20.2 | 4.1 | BC8B3B66984E4D85AE6A4C3106312019 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5971 |  | 2014-09-30 | 2014-09-30 09:42 | 2014-09-30 09:42 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | 5E1F2CDA926649DC8C71D9BDB74C206A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 19:12 | 2014-05-23 19:12 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.8 | 21.5 | -1.7 | 263DCFB0B7B3404C806051677B9D23A3 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 16:23 | 2014-05-21 16:23 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.6 | 19.6 | 2.1 | 5D3F2A6C2B6749C18B38EED887328144 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5973 |  | 2014-08-25 | 2014-08-25 10:40 | 2014-08-25 10:40 | OTHER - UKN | 90 | 0 | Yes | Yes | 22.7 | 19.4 | 3.3 | E4F68644A5AF4F2EA132AA81304091F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 16:56 | 2014-05-21 16:56 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.3 | 21.8 | -2.5 | 9B8E3AB026A64331AB582A4BB1642059 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 14:42 | 2014-05-21 14:42 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.1 | 19.8 | 1.3 | 9E4604A145484B0C9B592DE28AAADB87 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8961 |  | 2014-05-15 | 2014-05-15 15:27 | 2014-05-15 15:27 | OTHER - PGE12B36D075A-2A | 110 | 0 | Yes | Yes | 23.6 | 21 | 2.6 | 65AA79F3A5C541AE9C190A0EF88365A6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5970 |  | 2014-08-25 | 2014-08-25 10:35 | 2014-08-25 10:35 | PAYNE - PNAOZ4040NB | 95 | 0 | Yes | Yes | 19.5 | 22.2 | -2.7 | 0295C8E82A934525A246889A51DBD4CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3408 |  | 2014-11-06 | 2014-11-06 10:19 | 2014-11-06 10:19 | GOODMAN - PCB0360501AREVA | 60 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 7A27801D529E4B36AB613001226363A7 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-0000 |  | 2014-05-28 | 2014-05-28 10:30 | 2014-05-28 14:34 | CARRIER - | 85 | -4 | Yes | Yes | 16.8 | 18.2 | -1.4 | 9B62F091C5D34E0186A0F88145B3C948 |  | R22 | Non-TXV |  | -4.706% | 1.0471 | 1.318% |  |  |  |  | Non-TXV |  |  | -4.706%
Woodland | CA | 95695-4606 |  | 2014-05-19 | 2014-05-19 13:02 | 2014-05-19 16:30 | AMERICAN STANDARD - 4YCC3030B1075AA | 106 | -4.5 | Yes | Yes | 12.8 | 15.5 | -2.7 | 9B4F5973AAED4A04B36D55548E0B1FDF |  | R22 | Non-TXV |  | -4.245% | 1.0425 | 1.189% |  |  |  |  | Non-TXV |  |  | -4.245%
Bakersfield | CA | 93305-5032 |  | 2014-05-17 | 2014-05-17 19:29 | 2014-05-17 19:29 | ICP - PGME60G1157 | 211 | 0 | Yes | Yes | 23.9 | 25.3 | -1.4 | CAB4794772B246E0AAA09514E50A8A7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 18:49 | 2014-05-23 18:49 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | AB2526DB94A942A7A6CB62DB0CF828CC |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4104 |  | 2014-05-03 | 2014-05-03 13:33 | 2014-05-03 13:33 | CARRIER - 580AN030040 | 88 | 0 | Yes | Yes | 19.2 | 19.7 | -0.5 | 96C36AAD930F4021AC2B277B73F2835D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1752 |  | 2014-05-13 | 2014-05-13 13:47 | 2014-05-13 14:27 | TRANE - TTN030C100 | 87 | -8.2 | Yes | Yes | 22.6 | 16.8 | 5.8 | 66D958573BC74C708D7FD33919B94A59 |  | R22 | Non-TXV |  | -9.425% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.425%
Bakersfield | CA | 93307-0000 |  | 2014-05-23 | 2014-05-23 16:17 | 2014-05-23 16:34 | ICP - C4A624GKD200 | 200 | 21.4 | Yes | Yes | 20.3 | 21.9 | -1.6 | A4E60EFCC3AC40D6A5634F676972097D |  | R410A | TXV |  | 10.7% | 0.893 | 20.56% | [5 empty] | TXV | 10.7%
Bakersfield | CA | 93304-5174 |  | 2014-10-15 | 2014-10-15 14:56 | 2014-10-15 14:56 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 22.1 | 22.5 | -0.4 | B48CF229E83A45EDAE6581B8C6A4C5D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 18:11 | 2014-05-23 18:11 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 18.9 | 21 | -2.1 | 7181A36CF9DB4F3AB504E63F78D85FA1 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7003 |  | 2014-09-14 | 2014-09-14 19:39 | 2014-09-14 19:39 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | 2AE67E9FF95C4AFCBC9195C9EC3C932E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2014-05-23 | 2014-05-23 19:32 | 2014-05-23 19:32 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | FF492A24493E4745AF5DEC1F17C41C47 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7005 |  | 2014-09-14 | 2014-09-14 13:52 | 2014-09-14 13:52 | GOODMAN - GSH130301CA | 130 | 0 | Yes | Yes | 21.1 | 21 | 0.1 | 4D34500868E84AAA81BA2E8C8B8AA43B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 15:16 | 2014-05-21 15:16 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.2 | 21.5 | -0.3 | 2A4864CFBE32412CB943CE2415227838 |  | R410A | TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2809 |  | 2014-07-30 | 2014-07-30 12:25 | 2014-07-30 12:53 | RUUD - UACB036JAS | 48 | 2.6 | Yes | Yes | 18.8 | 18.5 | 0.3 | F5808FE9DD164E8F8F73B60AFF9BC3F1 |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Bakersfield | CA | 93308-7014 |  | 2014-09-14 | 2014-09-14 19:57 | 2014-09-14 19:57 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 22 | 23.4 | -1.4 | 1C615ED826324C6A9069C2679BE922F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-3219 |  | 2014-05-09 | 2014-05-09 08:46 | 2014-05-09 08:46 | TRANE - 4TTR042A1000 | 85 | 0 | Yes | Yes | 15.8 | 15.7 | 0.1 | E2C8CC0E2DEC4B06A708BDCE08CFC59C |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5196 |  | 2014-05-07 | 2014-05-07 10:48 | 2014-05-07 10:48 | GOODMAN - CKL49-1 | 109 | 0 | Yes | Yes | 16.2 | 18.5 | -2.3 | 6D71E8E27ADA4C93A6132F4BCDED322B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 17:27 | 2014-05-23 17:27 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.5 | 19.9 | -0.4 | 2902D1508D50444EBC3959F4878FC8F0 |  | R410A | TXV |  | 0% | 1 | 0%
Newark | CA | 94560-5600 |  | 2014-06-24 | 2014-06-24 10:43 | 2014-06-24 11:13 | YORK - H2RA036 | 63 | 2.8 | Yes | Yes | 24.7 | 20.2 | 4.6 | 280B733C22C443BA93C9188198DB37B9 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Bakersfield | CA | 93304-5183 |  | 2014-10-29 | 2014-10-29 12:19 | 2014-10-29 12:19 | BDP - 585EJ024050 | 54 | 0 | Yes | Yes | 25.2 | 21 | 4.2 | AC280D4252594C5394BEE571D985C555 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 18:04 | 2014-05-23 18:04 | ICP - C4A62GKD200 | 200 | 0 | Yes | Yes | 20.7 | 21.3 | -0.5 | 6DD62CE0171E42E08EA9337E8982D022 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3421 |  | 2014-06-30 | 2014-06-30 15:30 | 2014-06-30 15:30 | UNITARY PRODUCTS GROUP - DCYZ-F024N045A | 58 | 0 | Yes | Yes | 20.4 | 23.2 | -2.8 | A3173E7DA8D3414D99156C2536562B35 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 14:49 | 2014-05-22 14:49 | ICP - C4A62GKD200 | 200 | 0 | Yes | Yes | 19.6 | 21.5 | -1.9 | 48C2CBD9C15B4537B8E3858E9F14F107 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 17:44 | 2014-05-22 17:44 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.9 | 21.8 | -0.9 | 6E71E44D54044FF5999350C4CB347E09 |  | R410A | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3746 |  | 2014-05-07 | 2014-05-07 09:32 | 2014-05-07 09:56 | HEIL - NC5060VK2 | 183 | -21.5 | Yes | Yes | 18.6 | 15 | 3.6 | 54BFA2714DDE47A082CD07ADD9D9768E |  | R22 | Non-TXV |  | -11.75% | 1.1175 | 3.29% |  |  |  |  | Non-TXV |  |  | -11.75%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 19:14 | 2014-05-23 19:14 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.7 | 21.5 | -0.8 | 209BAA6C705A49F29E70AB20336496F3 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1441 |  | 2014-05-22 | 2014-05-22 18:08 | 2014-05-22 18:08 | ICP - UKN | 228 | 0 | Yes | Yes | 18.9 | 21 | -2.1 | 1A28CC1DB0C94D4EBB194E45074EFC37 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-6606 |  | 2014-05-06 | 2014-05-06 12:18 | 2014-05-06 13:54 | GOODMAN - CK49-1B | 97 | -6.1 | Yes | Yes | 12 | 15 | -3 | B8377E38C0E0475C9508C5E25F47BE02 |  | R22 | Non-TXV |  | -6.289% | 1.0629 | 1.761% |  |  |  |  | Non-TXV |  |  | -6.289%
Bakersfield | CA | 93306-3325 |  | 2014-05-05 | 2014-05-05 08:45 | 2014-05-05 09:17 | YORK - D1NA018N03606C | 46 | 2.2 | Yes | Yes | 19.5 | 21.4 | -1.9 | 93A2CA14B9154EF5802BBD8E050A7F51 |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
San Jose | CA | 95132-1661 |  | 2014-06-09 | 2014-06-09 10:07 | 2014-06-09 10:36 | BDP - 56988048 | 117 | 25 | Yes | Yes | 18.8 | 21 | -2.2 | AF3C0145AE834DCE9299C2D81E8BA9C9 |  | R22 | Non-TXV |  | 21.37% | 0.78632 | 41.06% | [5 empty] | Non-TXV | 21.37%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 19:37 | 2014-05-23 19:37 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | 5E59CE164B2C446582C572B067236F21 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-4447 |  | 2014-05-15 | 2014-05-15 09:26 | 2014-05-15 09:41 | YORK - H22RD036S06 | 96 | -9 | Yes | Yes | 20.8 | 17.2 | 3.7 | CCEA9ADE91114B6F99652ACBB2D286DF |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
San Jose | CA | 95127-2553 |  | 2014-05-08 | 2014-05-08 08:54 | 2014-05-08 09:26 | RHEEM - BRCS0601BD | 118 | -14.6 | Yes | Yes | 18.2 | 17 | 1.2 | E0BA4802F01E4A7998FBC9DAE8521FCF |  | R22 | Non-TXV |  | -12.37% | 1.1237 | 3.465% |  |  |  |  | Non-TXV |  |  | -12.37%
Dixon | CA | 95620-4501 |  | 2014-05-21 | 2014-05-21 13:32 | 2014-05-21 17:03 | AMERICAN STANDARD - 2A7A3042A1000AA | 109 | -5.7 | Yes | Yes | 14 | 15.6 | -1.6 | 00926862F7F94DAB95A9707563811F8D |  | R22 | Non-TXV |  | -5.229% | 1.0523 | 1.464% |  |  |  |  | Non-TXV |  |  | -5.229%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 14:40 | 2014-05-21 14:56 | ICP - C4A624GKD200 | 200 | 23.8 | Yes | Yes | 19 | 21 | -2 | 3D45A530FC0240F1A2402865C13DDFA0 |  | R410A | TXV |  | 11.9% | 0.881 | 22.87% | [5 empty] | TXV | 11.9%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 13:38 | 2014-08-19 13:38 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 20.6 | 19.9 | 0.7 | 395536365C694E79BA762F32F8293F5C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-5623 |  | 2014-05-12 | 2014-05-12 08:34 | 2014-05-12 08:49 | CARRIER - 24ABB3422AA300 | 93 | -8.8 | Yes | Yes | 17.8 | 13.7 | 4.1 | C52F3FD6EF5B4F89BDBA158DC22C180F |  | R22 | Non-TXV |  | -9.462% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.462%
Vallejo | CA | 94589-2198 |  | 2014-05-13 | 2014-05-13 14:28 | 2014-05-13 16:31 | DAY & NIGHT - 565BJ036-D | 76 | -4.3 | Yes | Yes | 11.3 | 14.2 | -2.9 | AEAC1D4BF2F4433F9D9B9911938E7132 |  | R22 | Non-TXV |  | -5.658% | 1.0566 | 1.584% |  |  |  |  | Non-TXV |  |  | -5.658%
Davis | CA | 95618-0516 |  | 2014-05-23 | 2014-05-23 09:10 | 2014-05-23 15:56 | OTHER - | 85 | 3.4 | Yes | Yes | 16.4 | 16.4 | 0 | 6412647F28DE4C409CBC3BA82C719334 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 13:16 | 2014-08-20 13:16 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 19.6 | 20.4 | -0.8 | 027D7973613A47CAB41B1121BC5BA5DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-3859 |  | 2014-05-15 | 2014-05-15 12:04 | 2014-05-15 16:13 | RHEEM - RAK,A-024JAZ | 47 | -4.4 | Yes | Yes | 17.3 | 19.5 | -2.2 | 2F50CE5A4DD0465BBC3D1ED522D471EF |  | R22 | Non-TXV |  | -9.362% | 1.0936 | 2.622% |  |  |  |  | Non-TXV |  |  | -9.362%
Fairfield | CA | 94534-7968 |  | 2014-05-09 | 2014-05-09 13:49 | 2014-05-09 15:58 | BRYANT - 591ANX060000AAAA | 162 | -5.4 | Yes | Yes | 17.2 | 20.1 | -2.9 | 14D36D2D3E9F452E91F6D30476167812 |  | R22 | Non-TXV |  | -3.333% | 1.0333 | 0.9335% |  |  |  |  | Non-TXV |  |  | -3.333%
Bakersfield | CA | 93309-8855 |  | 2014-08-25 | 2014-08-25 09:40 | 2014-08-25 09:40 | BDP - 5853J03J050 | 58 | 0 | Yes | Yes | 21.2 | 23.7 | -2.5 | 60FE500415BE46728A9A30F4B6CDA60F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-3923 |  | 2014-07-14 | 2014-07-14 14:08 | 2014-07-14 14:41 | CARRIER - 38HDC0300 | 91 | 9.2 | Yes | Yes | 23.2 | 21.4 | 1.8 | A083DEA5166E49D7B49F7763ABCE8542 |  | R22 | Non-TXV |  | 10.11% | 0.8989 | 19.43% | [5 empty] | Non-TXV | 10.11%
Bakersfield | CA | 93301-5928 |  | 2014-05-09 | 2014-05-09 15:24 | 2014-05-09 15:24 | OTHER - UKN | 85 | 0 | Yes | Yes | 25 | 23.1 | 1.9 | 2C7B9AD2833549E384BC0CD9AF796E9F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7002 |  | 2014-09-14 | 2014-09-14 19:28 | 2014-09-14 19:28 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 22.6 | 21 | 1.6 | 779B910FC49342498D9CDDEDE0DE3EF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 17:06 | 2014-05-21 17:06 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.7 | 22.5 | -2.8 | 370B1FA5175F49C488AD3D23E936C7D0 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 15:28 | 2014-05-22 15:52 | ICP - C4A624GKD200 | 200 | 24.5 | Yes | Yes | 20.7 | 22.1 | -1.4 | 070C4B7ED5CF4BF2BC9F1A4BF379FD37 |  | R410A | TXV |  | 12.25% | 0.8775 | 23.54% | [5 empty] | TXV | 12.25%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 17:03 | 2014-05-21 17:03 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.1 | 21 | -0.9 | E44B3D52566C4947B911878FE0D65D08 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 17:11 | 2014-05-21 17:28 | ICP - C4A624GKD200 | 200 | 13.4 | Yes | Yes | 19.6 | 21.3 | -1.7 | B69CE898BA534A60802FD58146CD017F |  | R410A | TXV |  | 6.7% | 0.933 | 12.88% | [5 empty] | TXV | 6.7%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 16:52 | 2014-05-21 16:52 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.7 | 20.9 | -0.2 | 88FADF9330674DEEAD37721AAD709D25 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 15:55 | 2014-05-21 16:11 | ICP - C4A624GKD200 | 200 | 22.1 | Yes | Yes | 19.1 | 20.4 | -1.3 | 61BA533D0F8741678035EC5A03AB4639 |  | R410A | TXV |  | 11.05% | 0.8895 | 21.24% | [5 empty] | TXV | 11.05%
Gilroy | CA | 95020-6739 |  | 2014-05-22 | 2014-05-22 10:35 | 2014-05-22 10:55 | AMANA - RCB30A2C | 79 | 7 | Yes | Yes | 14.9 | 17.7 | -2.8 | A009C3A3E33D48A2AF2C8B9BD19155F1 |  | R22 | Non-TXV |  | 8.861% | 0.91139 | 17.03% | [5 empty] | Non-TXV | 8.861%
Gilroy | CA | 95020-6739 |  | 2014-05-22 | 2014-05-22 10:51 | 2014-05-22 11:10 | AMANA - RCB030A2C | 79 | 4.1 | Yes | Yes | 19.7 | 18.2 | 1.5 | BC1D8498990A426EB1EAA38BC2FA8EB1 |  | R22 | Non-TXV |  | 5.19% | 0.9481 | 9.974% | [5 empty] | Non-TXV | 5.19%
Woodland | CA | 95776-4249 |  | 2014-05-29 | 2014-05-29 08:23 | 2014-05-29 10:11 | PAYNE - PA10JA042-D | 90 | -8.5 | Yes | Yes | 16.8 | 15.4 | 1.4 | E7B71BD909794A539B2339453C1FE2EC |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
San Jose | CA | 95112-5912 |  | 2014-05-08 | 2014-05-08 09:32 | 2014-05-08 09:53 | FRIGIDAIRE - TCA036AKC | 96 | -9 | Yes | Yes | 19.2 | 17.7 | 1.5 | 5E4F4CEE11574444A885EBE90552E6C4 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93312-6707 |  | 2014-10-02 | 2014-10-02 11:01 | 2014-10-02 11:01 | CARRIER - 3BBRC042330 | 108 | 0 | Yes | Yes | 23 | 21 | 2 | 5B27B1E7BE8F4AA893E6782DF5CBD323 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2667 |  | 2014-05-27 | 2014-05-27 09:10 | 2014-05-27 09:10 | DAY & NIGHT - 594ANX036000 | 120 | 0 | Yes | Yes | 18.3 | 18.2 | 0.1 | 6CA26B30F2334B1CA928C8C25FE0CEF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8058 |  | 2014-05-16 | 2014-05-16 09:49 | 2014-05-16 13:59 | CARRIER - 38CKCO48300 | 107 | -6.8 | Yes | Yes | 14.8 | 17.8 | -3 | 8DAD57F61DB247198286CF7761E1579B |  | R22 | Non-TXV |  | -6.355% | 1.0636 | 1.78% |  |  |  |  | Non-TXV |  |  | -6.355%
San Jose | CA | 95121-2775 |  | 2014-05-08 | 2014-05-08 11:47 | 2014-05-08 12:14 | HEIL - CA55336VLC | 74 | 7.2 | Yes | Yes | 14.5 | 17.5 | -3 | DB78213C6B3B4062BEBD88DA7C6AB989 |  | R22 | Non-TXV |  | 9.73% | 0.9027 | 18.7% | [5 empty] | Non-TXV | 9.73%
Bakersfield | CA | 93306-2725 |  | 2014-08-26 | 2014-08-26 09:29 | 2014-08-26 09:29 | ICP - PGAD36DIK2 | 78 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | D9B2653922A6475581D73E2248509AEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1129 |  | 2014-10-28 | 2014-10-28 12:02 | 2014-10-28 12:02 | GOODMAN - GPG1324045M41DA | 75 | 0 | Yes | Yes | 19.9 | 19.1 | 0.8 | D10419C5C6874E89967A697AF4D08A1E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4810 |  | 2014-05-16 | 2014-05-16 18:57 | 2014-05-16 18:57 | GOODMAN - GSC130361DE | 119 | 0 | Yes | Yes | 26.5 | 22.9 | 3.7 | 2FE25FA8CE424BB89743F87E442651A6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-2245 |  | 2014-05-09 | 2014-05-09 10:50 | 2014-05-09 10:50 | YORK - H2CB036S08 | 85 | 0 | Yes | Yes | 11.1 | 13.6 | -2.5 | 0ACCFC50A2464E02B716FB616FB31366 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6981 |  | 2014-07-31 | 2014-07-31 13:39 | 2014-07-31 13:39 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | EC1C23CF325045B8BC4E984A54B8DC5B |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-2147 |  | 2014-05-12 | 2014-05-12 13:14 | 2014-05-12 13:39 | CARRIER - 48GN036 | 70 | 3 | Yes | Yes | 17.1 | 16.1 | 1 | 840B574BE38E43E6ADDFE5FF802E1421 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
San Jose | CA | 95120-3601 |  | 2014-05-08 | 2014-05-08 10:32 | 2014-05-08 10:32 | BRYANT - 13RNA04800 | 120 | 0 | Yes | Yes | 21.4 | 17.1 | 4.3 | 30F9189733F74CD2B7A4D823673E3850 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1411 |  | 2014-05-13 | 2014-05-13 13:01 | 2014-05-13 13:24 | TRANE - TTP042C100 | 140 | 5.6 | Yes | Yes | 18 | 17.9 | 0.1 | B4A4FE82EBF7428591A6A2327F29335E |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Sunnyvale | CA | 94087-4678 |  | 2014-05-30 | 2014-05-30 09:15 | 2014-05-30 09:42 | ICP - CA55560VKD1 | 150 | -14.1 | Yes | Yes | 22 | 19.3 | 2.7 | 8F94D85A940E4579B51D4BB986D07FDB |  | R22 | Non-TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.4%
Sunnyvale | CA | 94087-4678 |  | 2014-05-30 | 2014-05-30 09:26 | 2014-05-30 09:43 | TRANE - 4TTB3042D1000 | 106 | -6.2 | Yes | Yes | 22.6 | 19.9 | 2.7 | DA506D1D1D6248C2B8A06550594BFF8E |  | R410A | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
San Jose | CA | 95148-2509 |  | 2014-05-12 | 2014-05-12 10:24 | 2014-05-12 10:50 | GOODMAN - CKK0601C | 122 | 6.5 | Yes | Yes | 14.5 | 16.4 | -1.9 | 2A092B0DF6A04AC2818BB8A57C9AA7A7 |  | R22 | Non-TXV |  | 5.328% | 0.94672 | 10.24% | [5 empty] | Non-TXV | 5.328%
Sunnyvale | CA | 94089-0000 |  | 2014-05-16 | 2014-05-16 14:09 | 2014-05-16 14:33 | YORK - H2RD036S06B | 96 | -9 | Yes | Yes | 20 | 18.1 | 1.9 | 6DB18B32ABC541029204E38FF9C75983 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93307-1213 |  | 2014-07-24 | 2014-07-24 11:51 | 2014-07-24 11:51 | CARRIER - 48SS-024040321 | 44 | 0 | Yes | Yes | 21.3 | 24.2 | -2.9 | 6FE6BDB782FC4A119C3DCF9A90518887 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2545 |  | 2014-09-20 | 2014-09-20 17:17 | 2014-09-20 17:18 | OTHER - WPG32440LKC1 | 72 | -4.2 | Yes | Yes | 21.5 | 20.9 | 0.6 | 8350B49B430646D8829767E785F8A92D |  | R410A | TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | TXV |  |  | -5.833%
Bakersfield | CA | 93308-7002 |  | 2014-09-14 | 2014-09-14 19:44 | 2014-09-14 19:44 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 21 | 22.5 | -1.5 | A5DC9934F33D4FA692C9CB55375E16BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Union City | CA | 94587-4237 |  | 2014-05-22 | 2014-05-22 11:38 | 2014-05-22 11:58 | SEARS - BRCQ0301BE | 41 | 5.6 | Yes | Yes | 19.8 | 18.6 | 1.3 | 599DB30F8D464C78866756B30ECED04A |  | R22 | Non-TXV |  | 13.66% | 0.86341 | 26.25% | [5 empty] | Non-TXV | 13.66%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 15:56 | 2014-08-19 15:56 | CARRIER - 3BYCC018340 | 85 | 0 | Yes | Yes | 20.1 | 22.3 | -2.2 | 6BA424567378447CBCB37875A6E0EC40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-4208 |  | 2014-05-09 | 2014-05-09 10:11 | 2014-05-09 10:37 | AMERICAN STANDARD - 4A7A2030 | 66 | 2.8 | Yes | Yes | 16.1 | 15.5 | 0.6 | D9828D41F66E45C6949313D39A8710B0 |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 13:27 | 2014-08-19 13:27 | CARRIER - 3BYCC01834 | 66 | 0 | Yes | Yes | 18.7 | 20.1 | -1.4 | 74ADA64A9E904F2191D908D8203ADE4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 14:18 | 2014-08-20 14:18 | CARRIER - 3B YCC018340 | 66 | 0 | Yes | Yes | 19.4 | 21.9 | -2.5 | A7263201469A43C6B2DC137FF4E1E0E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1917 |  | 2014-09-10 | 2014-09-10 15:24 | 2014-09-10 15:24 | DAY & NIGHT - 588ANW036080ACAF | 70 | 0 | Yes | Yes | 27.4 | 21.7 | 5.7 | AA5B05083E374C3293518A06A35C85BA | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:57 | 2014-10-10 15:57 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | 075E468C0F6248518D06F2339D6C28E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 12:50 | 2014-08-19 12:50 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 21.2 | 16.8 | 4.4 | 0BBD98D1BC0947E5974A1DCCF3F5323F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5228 |  | 2014-05-15 | 2014-05-15 13:17 | 2014-05-15 13:17 | GOODMAN - GPG13240451CB | 74 | 0 | Yes | Yes | 20.2 | 21 | -0.8 | 24FFA2EC0C144BE1B1A2B66034AF8CC6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2812 |  | 2014-11-01 | 2014-11-01 09:32 | 2014-11-01 09:51 | BRYANT - GCGDA48821S11A | 75 | 6.9 | Yes | Yes | 18.3 | 21.2 | -2.9 | 02BCE5ADDED446C0BDB3C2587D460FFD |  | R22 | Non-TXV |  | 9.2% | 0.908 | 17.68% | [5 empty] | Non-TXV | 9.2%
San Jose | CA | 95110-2897 |  | 2014-05-27 | 2014-05-27 09:57 | 2014-05-27 10:15 | BRYANT - 538ANR024 | 104 | 11.4 | Yes | Yes | 19 | 21 | -2 | 3E2662BD6D5B4C1EB26482DA8D61D92B |  | R410A | TXV |  | 10.96% | 0.89038 | 21.07% | [5 empty] | TXV | 10.96%
Bakersfield | CA | 93301-2270 |  | 2014-08-26 | 2014-08-26 16:00 | 2014-08-26 16:00 | BDP - 585EJ030050 | 49.6 | 0 | Yes | Yes | 26.9 | 21 | 5.9 | D90F0DA301F9465DB28961D89943AF42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5646 |  | 2014-05-28 | 2014-05-28 14:12 | 2014-05-28 14:12 | CARRIER - 24ABB336W310 | 86 | 0 | Yes | Yes | 22.5 | 19.4 | 3.1 | 10163196AFF54FC49B4E16F4B4B4FE09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1129 |  | 2014-10-28 | 2014-10-28 09:27 | 2014-10-28 09:27 | GOODMAN - GPG1324045M41CA | 68 | 0 | Yes | Yes | 24 | 20.1 | 3.9 | 22B98681F56A4EF0A7FC7FE36778DAB4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-1533 |  | 2014-10-30 | 2014-10-30 16:19 | 2014-10-30 16:36 | OTHER - UNK | 85 | 6.4 | Yes | Yes | 17.8 | 20.7 | -2.9 | B108914DFC624BF581F1A1785630AAE2 |  | R22 | Non-TXV |  | 7.529% | 0.92471 | 14.47% | [5 empty] | Non-TXV | 7.529%
Fremont | CA | 94536-4063 |  | 2014-06-24 | 2014-06-24 10:01 | 2014-06-24 10:30 | YORK - H2RA036S06 | 63 | 10.3 | Yes | Yes | 19.1 | 20.3 | -1.2 | 475799EF6DA64303A6CFFFF3D7D651BC |  | R22 | Non-TXV |  | 16.35% | 0.83651 | 31.42% | [5 empty] | Non-TXV | 16.35%
Napa | CA | 94558-1724 |  | 2014-06-24 | 2014-06-24 12:25 | 2014-06-24 13:33 | AMERICAN STANDARD - 7A0036100A1 | 89 | 9.8 | Yes | Yes | 14.7 | 17.4 | -2.7 | B0D564939C604449B2585F081D0BA9E8 |  | R22 | Non-TXV |  | 11.01% | 0.88989 | 21.16% | [5 empty] | Non-TXV | 11.01%
Napa | CA | 94559-1044 |  | 2014-05-15 | 2014-05-15 11:45 | 2014-05-15 11:45 | RHEEM - | 74 | 0 | Yes | Yes | 15.5 | 17.5 | -2 | 6FD5CCF3E8C74F2BBC6D30BFCC727809 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3835 |  | 2014-06-30 | 2014-06-30 12:49 | 2014-06-30 12:49 | OTHER - UKN | 90 | 0 | Yes | Yes | 15.6 | 17.6 | -2 | AFBE75E0F6FC433391078DAA4D901204 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3420 |  | 2014-05-06 | 2014-05-06 12:57 | 2014-05-06 12:57 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 13.3 | 15.7 | -2.4 | 8D3728CC5D1F409385C58B53B0D87B05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1557 |  | 2014-05-14 | 2014-05-14 11:31 | 2014-05-14 11:31 | TRANE - TCJD36S41S3A | 73 | 0 | Yes | Yes | 16.4 | 19.1 | -2.7 | 293AA7FEF3F54B619B92A2C3658DC01F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2325 |  | 2014-07-07 | 2014-07-07 13:44 | 2014-07-07 13:44 | RHEEM - RRRL-C024JK06X | 97 | 0 | Yes | Yes | 20.1 | 21.8 | -1.7 | 67E94FBC0863401FB2A7ABC2890B1AD2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Cupertino | CA | 95014-2924 |  | 2014-05-16 | 2014-05-16 09:38 | 2014-05-16 10:21 | GOODMAN - G6X130481B | 125 | -11.8 | Yes | Yes | 20.8 | 16.1 | 4.7 | 15BD8977DC2546189AE29E5119310FA1 |  | R410A | Non-TXV |  | -9.44% | 1.0944 | 2.644% |  |  |  |  | Non-TXV |  |  | -9.44%
Bakersfield | CA | 93308-4852 |  | 2014-05-10 | 2014-05-10 14:46 | 2014-05-10 14:46 | OTHER - UKN | 60 | 0 | Yes | Yes | 24.3 | 23.1 | 1.2 | 23851EA158E24E0B8A92324389F6C324 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 15:18 | 2014-08-19 15:18 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 19 | 21.1 | -2.1 | 1F59FAB0574A45949C0BA9E36B230392 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2015 |  | 2014-05-13 | 2014-05-13 07:09 | 2014-05-13 07:09 | AMERICAN STANDARD - 2A7B3042A1000AA | 109 | 0 | Yes | Yes | 13.9 | 16.6 | -2.7 | 5DBF39333CEB4F8CBD26FADE922C3399 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1928 |  | 2014-09-10 | 2014-09-10 17:40 | 2014-09-10 17:40 | ICP - PGAA42C1K3 | 82 | 0 | Yes | Yes | 21.7 | 20.8 | 0.9 | AF5B3B75B62E4F57A0A9E5EEFB24A973 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1724 |  | 2014-06-05 | 2014-06-05 11:01 | 2014-06-05 11:01 | BDP - 565042RLCU | 104 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | 2965EDF623884B87B35F66F0BB19D801 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5165 |  | 2014-08-26 | 2014-08-26 15:22 | 2014-08-26 16:19 | GOODMAN - CK49-1 | 97 | 0 | Yes | Yes | 22.6 | 20.2 | 2.5 | C1A1907F7E02428799E128CDAF5B78DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-4226 |  | 2014-05-23 | 2014-05-23 09:00 | 2014-05-23 09:00 | TRANE - 2TTR4030A1000AA | 105 | 0 | Yes | Yes | 17.8 | 18.8 | -1 | 44F8400A6A0C48C98643516A62CD3352 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1127 |  | 2014-10-21 | 2014-10-21 18:19 | 2014-10-21 18:19 | ICP - PGC024K04001 | 54 | 0 | Yes | Yes | 19.1 | 20.9 | -1.8 | 78606D5ED7774EE09438F3065AAFEA1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 16:15 | 2014-08-19 16:15 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 22.4 | 21.9 | 0.5 | E5698D547C764439B5712A8500E9DD95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4085 |  | 2014-09-13 | 2014-09-13 16:04 | 2014-09-13 16:04 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 20.3 | 22 | -1.7 | 014F68E7511146859DE3879E17F48CB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7920 |  | 2014-05-22 | 2014-05-22 10:41 | 2014-05-22 10:41 | UNITARY PRODUCTS GROUP - AC036X1222A | 83 | 0 | Yes | Yes | 22.3 | 19.3 | 3 | 35E1CE7C1A384553818BFBDA46B4EABD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4632 |  | 2014-09-09 | 2014-09-09 08:54 | 2014-09-09 08:54 | OTHER - UNK | 60 | 0 | Yes | Yes | 29 | 19.9 | 9.1 | 22AE89870937465BAB9B935ED813ED19 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2303 |  | 2014-05-21 | 2014-05-21 14:12 | 2014-05-21 17:02 | PAYNE - PA13NR024-A | 83 | 6 | Yes | Yes | 15.2 | 15.5 | -0.3 | 4505E1FB9763447591E469CCCBC56FE0 |  | R22 | Non-TXV |  | 7.229% | 0.92771 | 13.89% | [5 empty] | Non-TXV | 7.229%
Bakersfield | CA | 93301-1132 |  | 2014-10-24 | 2014-10-24 13:10 | 2014-10-24 13:10 | RHEEM - RRNAB024JK06X | 70 | 0 | Yes | Yes | 23 | 21.5 | 1.5 | DCBFB6068687411DBD0BBCD2DCBC8779 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3369 |  | 2014-05-14 | 2014-05-14 18:52 | 2014-05-14 18:52 | - N4A336AKB200 | 85 | 0 | Yes | Yes | 20 | 22.8 | -2.8 | 7F996500093543FD970ACCA39B557A80 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1116 |  | 2014-07-19 | 2014-07-19 17:28 | 2014-07-19 17:31 | GOODMAN - GPG1336070M41AC | 85 | -5 | Yes | Yes | 21 | 19.4 | 1.7 | 5FF546F99527479895CAE8B1ACE75224 |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Vallejo | CA | 94589-1802 |  | 2014-05-14 | 2014-05-14 14:53 | 2014-05-14 15:38 | GOODMAN - | 85 | -4 | Yes | Yes | 16 | 13.9 | 2.1 | 893FF7837CB2467AAC68E94A257BA5E9 |  | R22 | Non-TXV |  | -4.706% | 1.0471 | 1.318% |  |  |  |  | Non-TXV |  |  | -4.706%
San Jose | CA | 95120-2139 |  | 2014-05-08 | 2014-05-08 14:19 | 2014-05-08 14:31 | LENNOX - HS2636 | 87 | 7.4 | Yes | Yes | 13.8 | 16.1 | -2.3 | 4831FE0AC3DA495EA8AC5CF222E1B2D7 |  | R22 | Non-TXV |  | 8.506% | 0.91494 | 16.35% | [5 empty] | Non-TXV | 8.506%
San Jose | CA | 95136-1605 |  | 2014-05-09 | 2014-05-09 13:37 | 2014-05-09 14:00 | CARRIER - 38CKC042 | 80 | -8.5 | Yes | Yes | 21.8 | 16.8 | 5 | 08D9BC47E6764958B5C0D81ABA3D798C |  | R22 | Non-TXV |  | -10.62% | 1.1062 | 2.975% |  |  |  |  | Non-TXV |  |  | -10.62%
Bakersfield | CA | 93306-2047 |  | 2014-05-01 | 2014-05-01 08:06 | 2014-05-01 08:06 | YORK - D1NA042N05606B | 72 | 0 | Yes | Yes | 21.2 | 21.3 | -0.1 | 0D6CEAAD3BB74303880336ED2B08E3AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1001 |  | 2014-05-16 | 2014-05-16 10:56 | 2014-05-16 10:56 | YORK - D2NP042N06506 | 150 | 0 | Yes | Yes | 17.2 | 19.8 | -2.6 | EE504A3CB1104D64B373447EFE48630C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-2210 |  | 2014-05-27 | 2014-05-27 15:03 | 2014-05-27 15:16 | BRYANT - S3BA042K | 85 | -8 | Yes | Yes | 21.1 | 20.4 | 0.7 | D2972A245A1246E3907107AE70135945 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
San Jose | CA | 95112-2210 |  | 2014-05-27 | 2014-05-27 15:14 | 2014-05-27 16:49 | TRANE - 2TTB0030A10000 | 85 | -8 | Yes | Yes | 25.2 | 19.9 | 5.3 | 9572EEB93E1C4F5AA3CC24D9E1EA9225 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Gilroy | CA | 95020-7449 |  | 2014-05-28 | 2014-05-28 10:06 | 2014-05-28 10:37 | PAYNE - 5656J36 | 80 | 7.5 | Yes | Yes | 20.3 | 19.9 | 0.4 | 7EC3A0F873464D6A9C0B77FE5C25BF44 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 13:09 | 2014-08-19 13:09 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 22.4 | 19.7 | 2.7 | 1F071E4007BD4450A14882E6380F0F4A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 13:55 | 2014-08-20 13:55 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 20.2 | 20.5 | -0.3 | E13236C48D5E429696A9A2B68BF67FC7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3227 |  | 2014-05-12 | 2014-05-12 14:14 | 2014-05-12 14:14 | UNITARY PRODUCTS GROUP - DAYA-F030N045C | 76 | 0 | Yes | Yes | 18.4 | 21 | -2.6 | 2F8E2E36D816415DAF001A215509B925 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4120 |  | 2014-05-08 | 2014-05-08 08:49 | 2014-05-08 08:49 | ICP - PGC048K080E | 100 | 0 | Yes | Yes | 20 | 22.9 | -2.9 | 3FEEA35875C14CD68C647462FCBD7988 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4120 |  | 2014-05-08 | 2014-05-08 08:52 | 2014-05-08 08:52 | ICP - PGC048K080E | 100 | 0 | Yes | Yes | 19.9 | 22.9 | -3 | 9125344D898540FB9D8B43D52EB906E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 14:07 | 2014-08-19 14:07 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 18.4 | 19.1 | -0.7 | CFD3633E2FA44E1BBF96A15361DBCF87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2208 |  | 2014-05-23 | 2014-05-23 09:53 | 2014-05-23 15:58 | RHEEM - RAKA--037JAZ | 85 | -5 | Yes | Yes | 14.2 | 17.2 | -3 | DD1994C1B0EE4F429DA5596D413855FB |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
San Jose | CA | 95116-4010 |  | 2014-07-22 | 2014-07-22 09:35 | 2014-07-22 10:06 | RHEEM - RAKA048JAZ | 103 | 5.6 | Yes | Yes | 19.3 | 21.4 | -2.1 | 5561054B107346F9BFF08DBDEB99CDCF |  | R22 | Non-TXV |  | 5.437% | 0.94563 | 10.45% | [5 empty] | Non-TXV | 5.437%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 18:42 | 2014-05-21 18:42 | ICP - C4A624KD200 | 200 | 0 | Yes | Yes | 19 | 21.8 | -2.8 | D521479294B74ADEA10867DE369DB186 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 17:54 | 2014-05-21 18:21 | ICP - C4A624GKD200 | 200 | 23.1 | Yes | Yes | 22.2 | 22.3 | -0.1 | 85D8DBBE46D0454D91E19804C9F7EEBE |  | R410A | TXV |  | 11.55% | 0.8845 | 22.2% | [5 empty] | TXV | 11.55%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 16:39 | 2014-05-21 16:39 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.3 | 21.5 | -1.2 | 495B5F2E5EC44F56A89577E4B94DA4D0 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2014-05-22 | 2014-05-22 16:45 | 2014-05-22 16:45 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | E117BE8668434732A73B67480070ACB6 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 15:23 | 2014-08-19 15:23 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 22.6 | 21 | 1.6 | 9EB5060C5D794F6BBA0BE941CB9CA2FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 17:51 | 2014-05-21 17:51 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.4 | 22 | -2.6 | A3E0D00DB3584E0394DE90FDB7C3A1E2 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 17:31 | 2014-05-21 17:31 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 18.9 | 20.2 | -1.3 | 49DABDED4F7A4519AF7BEFB2B72F1ECD |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4101 |  | 2014-05-16 | 2014-05-16 10:35 | 2014-05-16 10:58 | ICP - CA536VK02 | 85 | -9.5 | Yes | Yes | 12.5 | 15 | -2.5 | BBD4492D7B1C43D089E4C19200DE5826 |  | R22 | Non-TXV |  | -11.18% | 1.1118 | 3.13% |  |  |  |  | Non-TXV |  |  | -11.18%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 17:37 | 2014-05-21 17:37 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.2 | 22.4 | -2.2 | 3DD522C9A29A493C854D69961D2D5636 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2014-05-21 | 2014-05-21 14:21 | 2014-05-21 14:21 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.3 | 22.5 | -2.2 | 6398D3056589422C882D77112848B416 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 18:13 | 2014-05-21 18:13 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | 9F9D15389D1847F48E56ED5AAFD95B5F |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 18:38 | 2014-05-21 18:55 | ICP - C4A624GKD200 | 200 | 23.1 | Yes | Yes | 20.7 | 21.8 | -1.1 | FAB564A9D39940F3BC875573DB7F1015 |  | R410A | TXV |  | 11.55% | 0.8845 | 22.2% | [5 empty] | TXV | 11.55%
Bakersfield | CA | 93308-7003 |  | 2014-09-14 | 2014-09-14 14:53 | 2014-09-14 14:53 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 22.4 | 19.9 | 2.5 | 4B316F71A6AA4A20897D266E3960C813 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 19:04 | 2014-05-21 19:04 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.3 | 21.5 | -2.2 | A8DEE2981BBA46E48553990F5575356C |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 15:40 | 2014-08-19 15:40 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 20 | 21.8 | -1.8 | E66673F0A973474DBE9C7387F8BFCD0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 18:57 | 2014-05-21 18:57 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19 | 21.8 | -2.8 | 21F18B619CEB4F6DB6C4F80C21E94939 |  | R410A | TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3718 |  | 2014-06-05 | 2014-06-05 10:04 | 2014-06-05 17:55 | HEIL - | 85 | -5 | Yes | Yes | 19.7 | 19.9 | -0.2 | F823E6B4FB354C398FF458653B465E0C |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 16:08 | 2014-05-21 16:08 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | B5DD6918AEE743C6B0422D918A62AF32 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 16:33 | 2014-05-21 16:49 | ICP - C4A624GKD200 | 200 | 24.9 | Yes | Yes | 21.5 | 21 | 0.5 | D80DD2F82F534CE9827EC9A80059930F |  | R410A | TXV |  | 12.45% | 0.8755 | 23.93% | [5 empty] | TXV | 12.45%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 16:25 | 2014-05-22 16:25 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 18.7 | 20.4 | -1.7 | 7C5E9060BD5449B7A64C21823DB5899B |  | R410A | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2729 |  | 2014-05-12 | 2014-05-12 14:45 | 2014-05-13 07:11 | AMANA - RCC48C2C | 115 | 4.5 | Yes | Yes | 11.9 | 14.3 | -2.4 | C87193F1BC4D4273A6CFD28F99848D10 |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 15:28 | 2014-08-19 15:28 | CARRIER - 3BYCC018340600 | 66 | 0 | Yes | Yes | 23 | 20.6 | 2.4 | DF3072D4DF054DA18290B3EED4076B69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1957 |  | 2014-05-28 | 2014-05-28 18:56 | 2014-05-28 18:56 | PAYNE - PY3GNAA30040NAT | 98 | 0 | Yes | Yes | 23.5 | 20.4 | 3.1 | 3CE52EEEC7E54102B1B4C455D4F18ECC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-7416 |  | 2014-05-23 | 2014-05-23 13:59 | 2014-05-23 13:59 | AMANA - 591ANX048000 | 112 | 0 | Yes | Yes | 24.2 | 18.7 | 5.5 | C1100183810847A6BD3EFA9950DE9C73 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 16:19 | 2014-08-19 16:19 | CARRIER - RBYCC018340 | 66 | 0 | Yes | Yes | 20.2 | 20.5 | -0.3 | 9BF047A38ED8415097D67C658ABAEC4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4953 |  | 2014-07-31 | 2014-07-31 09:24 | 2014-07-31 09:24 | CARRIER - 48SS-224040311 | 39 | 0 | Yes | Yes | 16.6 | 18.3 | -1.7 | 1B9C558C4F474A7FA5C1FAB4DD90E170 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3740 |  | 2014-05-14 | 2014-05-14 14:00 | 2014-05-14 14:38 | LENNOX - HS1042V1P | 90 | 3.9 | Yes | Yes | 12.5 | 15 | -2.5 | 998A64309F8F4BB9B24D5DE5067A9882 |  | R22 | Non-TXV |  | 4.333% | 0.95667 | 8.328% | [5 empty] | Non-TXV | 4.333%
Bakersfield | CA | 93313-4533 |  | 2014-05-08 | 2014-05-08 11:26 | 2014-05-08 11:26 | OTHER - UNK | 90 | 0 | Yes | Yes | 17.7 | 20.6 | -2.9 | D0F3D655A73B44F3A1C2563D8E5BADA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7258 |  | 2014-10-02 | 2014-10-02 19:21 | 2014-10-02 19:42 | INTERTHERM - TTR060D100A0 | 134 | 4.2 | Yes | Yes | 20.8 | 20.4 | 0.4 | D1868748BD7444C5817CEAC61A2F931D |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Bakersfield | CA | 93306-3723 |  | 2014-06-30 | 2014-06-30 14:54 | 2014-06-30 14:54 | BDP - 568EJ048 | 180 | 0 | Yes | Yes | 16.3 | 15.2 | 1.1 | 07A0E5D2FEC44F10B591AC97EDD8218B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4801 |  | 2014-05-22 | 2014-05-22 09:41 | 2014-05-22 13:22 | - | 85 | 3.9 | Yes | Yes | 13.1 | 15.7 | -2.6 | B3C4A1C2579E483ABB4E0FABA7CDE301 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93304-2305 |  | 2014-05-12 | 2014-05-12 19:21 | 2014-05-12 19:21 | OTHER - UKN | 85 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 60BF9E0676BC42A3B47FF67EF9C92833 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2933 |  | 2014-05-05 | 2014-05-05 10:59 | 2014-05-05 10:59 | PAYNE - P43PNA036060NB | 85 | 0 | Yes | Yes | 21.7 | 20.5 | 1.2 | AA5DFA369328469886A3E530F8A2C8CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3819 |  | 2014-05-21 | 2014-05-21 15:24 | 2014-05-21 17:01 | CARRIER - | 85 | -5 | Yes | Yes | 17.5 | 20.4 | -2.9 | 4452B5A74B95419683E530A84C971F6B |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93305-3628 |  | 2014-08-05 | 2014-08-05 09:35 | 2014-08-05 09:35 | OTHER - UKN | 90 | 0 | Yes | Yes | 18.7 | 12.7 | 6 | 7D124A55DAD34B0092159D321BE8B38C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 16:24 | 2014-10-10 16:24 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | 1573BEFAF3354127BBF646D376521E6E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-5116 |  | 2014-08-21 | 2014-08-21 12:28 | 2014-08-21 12:47 | LENNOX - 3ACD-024-230-01 | 72 | 3.9 | Yes | Yes | 23 | 20.4 | 2.6 | 09D8E9DD2A0E40DD888AD56FDF4793CE |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 13:41 | 2014-08-20 13:41 | - 3BYCC018340 | 66 | 0 | Yes | Yes | 20.4 | 21 | -0.6 | A105E04DA4A247C1963DAEA92B5589E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 14:02 | 2014-08-20 14:02 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 23.3 | 21.5 | 1.9 | 6EDEE98D96C540598D0285D0AAF54B6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7911 |  | 2014-05-03 | 2014-05-03 13:45 | 2014-05-03 13:45 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 27.7 | 21.8 | 6 | 076B834800254F4CB4A55A569FDFA74B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4153 |  | 2014-05-07 | 2014-05-07 08:29 | 2014-05-07 08:29 | RUUD - URKA-A024JK06X | 60 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | 542E5FF4AF86435D811CE0CA2712322E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4153 |  | 2014-05-07 | 2014-05-07 08:32 | 2014-05-07 08:32 | OTHER - UKN | 90 | 0 | Yes | Yes | 20.2 | 21.2 | -1 | 503E15FDD6C043AE9FCAA7E05944AEBE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1556 |  | 2014-08-25 | 2014-08-25 19:14 | 2014-08-25 19:14 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 21.2 | 21.5 | -0.3 | EE54077820274A56B79CF058270783DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1557 |  | 2014-08-25 | 2014-08-25 19:43 | 2014-08-25 19:43 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | BC97641117D445BD9EFF27D60ECDE3A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1427 |  | 2014-05-14 | 2014-05-14 10:30 | 2014-05-14 11:57 | RUUD - | 85 | -3 | Yes | Yes | 11.7 | 14.7 | -3 | 6149049375E44DCFA320C53403C432AC |  | R22 | Non-TXV |  | -3.529% | 1.0353 | 0.9884% |  |  |  |  | Non-TXV |  |  | -3.529%
Bakersfield | CA | 93304-1560 |  | 2014-09-03 | 2014-09-03 18:30 | 2014-09-03 18:30 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 22.4 | 22.6 | -0.2 | 962CEC98C7DF400797E4E70285827A79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-2424 |  | 2014-05-27 | 2014-05-27 10:41 | 2014-05-27 11:10 | TRANE - TTP036D10000A0 | 133 | 5.8 | Yes | Yes | 21.2 | 20.4 | 0.8 | 9DC72F4E6770421B8544164954461A72 |  | R22 | Non-TXV |  | 4.361% | 0.95639 | 8.381% | [5 empty] | Non-TXV | 4.361%
W Sacramento | CA | 95691-4256 |  | 2014-05-07 | 2014-05-07 15:34 | 2014-05-07 15:34 | GIBSON - | 160 | 0 | Yes | Yes | 15.4 | 17.4 | -2 | 1ABEC46111EE4E528AA4B97BFD23CA85 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1560 |  | 2014-08-28 | 2014-08-28 19:36 | 2014-08-28 19:36 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.1 | 21 | 0.1 | F5DC61C85D134662A2DE6C5DD8321D09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5130 |  | 2014-05-21 | 2014-05-21 15:16 | 2014-05-21 15:41 | YORK - YCJF48S41S1A | 73 | 9.9 | Yes | Yes | 21.5 | 20.1 | 1.5 | 98ED07B5B3FC414289D6D9B709A3524C | Add refrigerant: 7.2 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | TXV |  | 13.56% | 0.86438 | 26.06% | [5 empty] | TXV | 13.56%
Bakersfield | CA | 93307-4882 |  | 2014-06-18 | 2014-06-18 10:10 | 2014-06-18 10:10 | UNITARY PRODUCTS GROUP - DCYZ-F036N070C | 64 | 0 | Yes | Yes | 26.3 | 21.5 | 4.9 | 6CDAEDFD979D4A8D8D062B55D47952EB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1573 |  | 2014-09-03 | 2014-09-03 19:28 | 2014-09-03 19:28 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.8 | 22.6 | -1.8 | 7CD7D32706394FB9A34EFE57B0B5168C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8303 |  | 2014-05-14 | 2014-05-14 09:02 | 2014-05-14 09:25 | TRANE - TTB036C100A2 | 90 | -4.5 | Yes | Yes | 17 | 18.8 | -1.8 | E2D4B51282E748E5A528EE68117C5776 |  | R22 | Non-TXV |  | -5% | 1.05 | 1.4% |  |  |  |  | Non-TXV |  |  | -5%
Fairfield | CA | 94534-4077 |  | 2014-05-07 | 2014-05-07 11:24 | 2014-05-07 12:10 | CARRIER - 38BRB042300 | 133 | 4.9 | Yes | Yes | 17 | 19.9 | -2.9 | 9A368DD6329D47EFABA40FDD176C2C63 |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Bakersfield | CA | 93304-1559 |  | 2014-08-25 | 2014-08-25 19:38 | 2014-08-25 19:38 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 21.9 | 22 | -0.1 | 66EBF40A2A664F039307FC389257183F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 14:29 | 2014-08-20 14:29 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 20.1 | 22.5 | -2.4 | E14F15FFC89146518D247F5EBFA2F417 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-7002 |  | 2014-05-27 | 2014-05-27 14:32 | 2014-05-27 14:51 | YORK - TCGD36D02 | 85 | 4.4 | Yes | Yes | 20.8 | 20.2 | 0.6 | 96B2F22B36AE4B89A1EB9A7C1F6BD355 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Dixon | CA | 95620-2207 |  | 2014-06-05 | 2014-06-05 09:06 | 2014-06-05 18:22 | FRIGIDKING - 38CKC036340 | 74 | -7 | Yes | Yes | 16.4 | 18.8 | -2.4 | A19884E754154335B733E7EA398ADB5B |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Bakersfield | CA | 93313-4107 |  | 2014-05-15 | 2014-05-15 15:10 | 2014-05-15 15:10 | RHEEM - RAPL-036JA2 | 141 | 0 | Yes | Yes | 19.6 | 20.4 | -0.8 | 6293E3E6AFFD4FCE9C99066FF414EA65 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4159 |  | 2014-05-05 | 2014-05-05 17:39 | 2014-05-05 17:39 | YORK - D1NH036N05606C | 104 | 0 | Yes | Yes | 26.3 | 22.9 | 3.5 | 85CD56F1C70A4623BCE13B09BCC86ECD |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5425 |  | 2014-05-12 | 2014-05-12 09:02 | 2014-05-13 07:10 | PAYNE - 561AJ048-F | 106 | 3.9 | Yes | Yes | 15.4 | 18.3 | -2.9 | 3C4B13EA03334E0A9D288778F97F3DD1 |  | R22 | Non-TXV |  | 3.679% | 0.96321 | 7.071% | [5 empty] | Non-TXV | 3.679%
Bakersfield | CA | 93305-4020 |  | 2014-05-30 | 2014-05-30 10:05 | 2014-05-30 10:22 | CARRIER - 48DL036BB | 90 | 8.4 | Yes | Yes | 19.4 | 22.1 | -2.7 | 0A775FCB3D36406F8684325FAED1B2B1 |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Davis | CA | 95616-3091 |  | 2014-05-20 | 2014-05-20 15:13 | 2014-05-20 15:13 | - | 85 | 0 | Yes | Yes | 20.5 | 18.7 | 1.8 | 73497465B4B54FA196D4905112CD6B62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5661 |  | 2014-05-03 | 2014-05-03 13:38 | 2014-05-03 13:38 | ICP - GPCM042K080I | 84 | 0 | Yes | Yes | 23.7 | 21.7 | 2 | 4B8968C2B42240F2A453C1B26C43CCF9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1565 |  | 2014-08-20 | 2014-08-20 14:41 | 2014-08-20 14:41 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 26.3 | 22.1 | 4.2 | 188A1CD96D20493E9F6108A761934094 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3506 |  | 2014-05-09 | 2014-05-09 10:19 | 2014-05-09 16:00 | YORK - | 90 | 3.3 | Yes | Yes | 13.9 | 15.8 | -1.9 | 586A0295988041E9939F658433746317 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Bakersfield | CA | 93304-3217 |  | 2014-05-13 | 2014-05-13 08:41 | 2014-05-13 08:41 | BDP - 588ANW048080AEAG | 104 | 0 | Yes | Yes | 19.7 | 22.6 | -2.9 | 6C8011906E524244A7F7EABD9FEFAB0F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4085 |  | 2014-09-13 | 2014-09-13 15:45 | 2014-09-13 15:45 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | 753595FB6B064CD08258D638E2FAC5DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1577 |  | 2014-08-26 | 2014-08-26 18:26 | 2014-08-26 18:26 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.4 | 21.8 | -0.3 | 6B71F7AB59F04B5EA83C04D14FEB0F90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 13:52 | 2014-08-19 13:52 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 18.3 | 19.3 | -1 | BB29C0DBDFB548308B1632374E48E980 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6442 |  | 2014-06-25 | 2014-06-25 09:10 | 2014-06-25 09:36 | LENNOX - 10ACB048 | 102 | 3.2 | Yes | Yes | 21.2 | 19.1 | 2.1 | F3EC0EB863674BE09A2FDBF1331B0471 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Bakersfield | CA | 93306-2443 |  | 2014-04-30 | 2014-04-30 13:49 | 2014-04-30 13:49 | ICP - PGF048K080A | 102 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | EC37D4FCFD3A48E4A8B28AFDC085CAA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6345 |  | 2014-05-12 | 2014-05-12 10:32 | 2014-05-12 10:32 | RUUD - UKN | 90 | 0 | Yes | Yes | 24.8 | 21.5 | 3.3 | C877C9D4F4DF4392BF960540974D8B06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 14:17 | 2014-08-19 14:17 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 19.4 | 20.1 | -0.7 | 83BB1A205E4749BD81FC4477ED859BCF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 14:31 | 2014-08-19 14:31 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 19.9 | 20.6 | -0.7 | 2B73983BACBB4E69811213C8E18E0C51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 13:42 | 2014-08-19 13:42 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 21.1 | 21.2 | -0.1 | 7574C1202B2F4714A681E7027123FBCB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 14:22 | 2014-08-20 14:22 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 22.3 | 20.4 | 2 | D80DB0D046524EAA8AC17D8E0078ECC9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 14:49 | 2014-10-10 14:49 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | E61AD0AEAFDD4BCBB7DAA43400B35099 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 14:25 | 2014-08-20 14:25 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 20.3 | 22.1 | -1.8 | DF1F8FEE8CC048FB893A66DF0A87B7AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1567 |  | 2014-08-25 | 2014-08-25 19:25 | 2014-08-25 19:25 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 20.5 | 20.7 | -0.2 | 3CDB25F4F0914A0EB0355FD6B2B08C74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 14:45 | 2014-10-10 14:45 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.4 | 21.5 | -1.1 | A9EA27782EC042708489FB822EF3A089 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 14:07 | 2014-08-20 14:07 | - | 66 | 0 | Yes | Yes | 18 | 20.8 | -2.8 | 85EF74C098F6407DBF0F7CE6A50E4035 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1534 |  | 2014-09-03 | 2014-09-03 19:22 | 2014-09-03 19:22 | CARRIER - 38YCC018341 | 85 | 0 | Yes | Yes | 19.3 | 21.5 | -2.2 | FC26F9A5705D4462BBF424A05E37CACF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 13:58 | 2014-08-19 13:58 | CARRIER - 3BYCC018340 | 66 | 29.1 | Yes | Yes | 19.7 | 20.3 | -0.5 | 797A2BCAF5454CA9A72EB0CB79884AAF | Add refrigerant: 29.1 oz | R22 | Non-TXV |  | 44.09% | 0.55909 | 84.73% | [5 empty] | Non-TXV | 44.09%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 13:23 | 2014-08-19 13:23 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 18.6 | 21.3 | -2.7 | 8D7A24175A234F06B2B8DE6080BAEDB4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 13:35 | 2014-08-20 13:35 | CARRIER - 3BYCC01834C | 66 | 0 | Yes | Yes | 22.1 | 20.9 | 1.2 | 23BFA20199974B4F86F654084D87C6CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 13:47 | 2014-08-20 13:47 | CARRIER - 3BYCC018340 | 85 | 0 | Yes | Yes | 22.2 | 19.9 | 2.3 | 7A73E348DBAB4DC4A450E7E51C3084E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 16:06 | 2014-08-19 16:06 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 21.1 | 19.9 | 1.2 | 154C8B92B9974BBFA0F0D6703B6136BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-20 | 2014-08-20 13:25 | 2014-08-20 13:25 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 22 | 20.8 | 1.2 | 78CF9760B54146BC9A04AD01220932BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-08-19 | 2014-08-19 14:40 | 2014-08-19 14:40 | CARRIER - 3BYC40C0183 | 66 | 0 | Yes | Yes | 19.9 | 22 | -2.1 | B7BD175DC5FA45549730AC4417717DE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 14:21 | 2014-09-13 14:21 | NORDYNE - CTT3BA024KA | 70 | 0 | Yes | Yes | 20.9 | 21.5 | -0.6 | 82B09D185041462691C60F40FD322612 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3701 |  | 2014-05-16 | 2014-05-16 14:00 | 2014-05-16 14:00 | RHEEM - UKN | 90 | 0 | Yes | Yes | 19.3 | 21.7 | -2.4 | 7DCFDDA4C41A42428D8ED6AFA5744237 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 16:01 | 2014-09-13 16:01 | GOODMAN - GSH130181CB | 127 | 0 | Yes | Yes | 21.1 | 22 | -0.9 | F9699860390C46F4966789DA81957AE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7310 |  | 2014-05-19 | 2014-05-19 15:22 | 2014-05-19 15:22 | HEIL - N4A30OAKC200 | 74 | 0 | Yes | Yes | 15.5 | 17.8 | -2.3 | 0B829C5B9F0A4937904AAC70D15F26BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4126 |  | 2014-05-06 | 2014-05-06 18:24 | 2014-05-06 18:24 | GOODMAN - GPG13240451CB | 74 | 0 | Yes | Yes | 19.7 | 22.6 | -2.9 | 6D1C35BAD1424BD3A55443A1B07D53C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1569 |  | 2014-08-20 | 2014-08-20 15:11 | 2014-08-20 15:11 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 21.5 | 21.7 | -0.2 | 7E49ADD4CC9443BAA7D895DF7EE4EC37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4801 |  | 2014-07-17 | 2014-07-17 08:59 | 2014-07-17 09:20 | YORK - | 74 | 3.5 | Yes | Yes | 11.9 | 14.7 | -2.8 | 4062374A4AA34B699B55D89F6355129C |  | R22 | Non-TXV |  | 4.73% | 0.9527 | 9.09% | [5 empty] | Non-TXV | 4.73%
Bakersfield | CA | 93304-1569 |  | 2014-08-20 | 2014-08-20 14:49 | 2014-08-20 14:49 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 19.9 | 22.5 | -2.6 | 4F06EEB0A9384D7CB5575B5AEB740C38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 14:23 | 2014-09-13 14:23 | BDP - 661CJ024B | 72 | 0 | Yes | Yes | 21.9 | 22.9 | -0.9 | 69654AFCC14D4BFA8363D9CFA6F58496 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4101 |  | 2014-06-18 | 2014-06-18 12:12 | 2014-06-18 14:05 | BDP - 561CJ060-A | 85 | -8 | Yes | Yes | 21.8 | 19.6 | 2.2 | 7E8AE2B718EB46738E2C4BE0148BD532 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93305-4926 |  | 2014-08-13 | 2014-08-13 12:08 | 2014-08-13 12:08 | UNITARY PRODUCTS GROUP - DCYZ-F024N045A | 108 | 0 | Yes | Yes | 17.9 | 20.5 | -2.6 | A75357D2C7AC415192170543D17CD728 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4926 |  | 2014-08-13 | 2014-08-13 12:34 | 2014-08-13 12:34 | UNITARY PRODUCTS GROUP - DAYH-F036N07GC | 108 | 0 | Yes | Yes | 19.1 | 19.8 | -0.7 | AFF2C8A0087D45EEABD8A76A24A83A2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1568 |  | 2014-08-28 | 2014-08-28 19:53 | 2014-08-28 19:53 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.3 | 21.5 | -1.2 | C4892DA407E8466DA49E9DC3FD55EAA0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-3261 |  | 2014-05-12 | 2014-05-12 14:42 | 2014-05-12 14:42 | COMFORT AIRE - NA | 83 | 0 | Yes | Yes | 21.8 | 18.7 | 3.1 | CBDD4513425D4901931E16876F9A6CE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3039 |  | 2014-05-22 | 2014-05-22 13:26 | 2014-05-22 10:31 | - | 85 | 0 | Yes | Yes | 22.8 | 23 | -0.2 | A5910181AC3F42FD8FFA5B458F9A36A3 | Remove refrigerant: 8 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1575 |  | 2014-08-25 | 2014-08-25 18:45 | 2014-08-25 19:08 | CARRIER - 38YCC018340 | 85 | 8.8 | Yes | Yes | 20 | 21 | -1 | CA2138F5877346E9BB8DDF39AF86E8E1 |  | R22 | Non-TXV |  | 10.35% | 0.89647 | 19.9% | [5 empty] | Non-TXV | 10.35%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 14:33 | 2014-09-13 14:33 | GOODMAN - CPLE241B | 110 | 0 | Yes | Yes | 21.4 | 22 | -0.6 | 4141BF0D0825401E875396654FBC959B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4513 |  | 2014-05-23 | 2014-05-23 11:05 | 2014-05-23 16:00 | GOODMAN - CKJ48-1B | 85 | -5.5 | Yes | Yes | 15.5 | 17.5 | -2 | 2184C0B60D2C4F5296D0011344932705 |  | R22 | Non-TXV |  | -6.471% | 1.0647 | 1.812% |  |  |  |  | Non-TXV |  |  | -6.471%
Woodland | CA | 95695-2897 |  | 2014-05-29 | 2014-05-29 09:08 | 2014-05-29 10:13 | TEMPSTAR - CA9630VKA1 | 141 | -8.3 | Yes | Yes | 18 | 17.5 | 0.5 | 0F45903CAD004AEFA6AD9BBF06B9D47B |  | R22 | Non-TXV |  | -5.887% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.887%
San Jose | CA | 95122-1113 |  | 2014-05-08 | 2014-05-08 15:26 | 2014-05-08 15:49 | AMANA - BRC365C | 70 | 3.3 | Yes | Yes | 15 | 16.8 | -1.8 | 0F56E2A0AD58441A814106B050EC84C2 |  | R22 | Non-TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | Non-TXV | 4.714%
Bakersfield | CA | 93313-4573 |  | 2014-08-29 | 2014-08-29 10:50 | 2014-08-29 10:50 | OTHER - FAFF-049JAZ | 163 | 0 | Yes | Yes | 20.5 | 23 | -2.5 | 0C954C84792B4E4DA9FC57155222DC18 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2121 |  | 2014-05-02 | 2014-05-02 10:22 | 2014-05-02 10:22 | YORK - DAYHF060N110C | 140 | 0 | Yes | Yes | 29.5 | 25.1 | 4.4 | 0E8E4A0FF2414E768A352B34B8DCC372 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4354 |  | 2014-10-01 | 2014-10-01 11:45 | 2014-10-01 12:04 | LENNOX - 13ACX-036 | 89 | 7.4 | Yes | Yes | 22.3 | 20.2 | 2.1 | AB176813C5E14B568F9045741692274F |  | R410A | Non-TXV |  | 8.315% | 0.91685 | 15.98% | [5 empty] | Non-TXV | 8.315%
Vacaville | CA | 95688-2035 |  | 2014-05-05 | 2014-05-05 13:31 | 2014-05-05 14:19 | ARMSTRONG - SCU12E36A | 99 | -7 | Yes | Yes | 23.4 | 20.4 | 3 | 6814AECB940A49E18612C9E84C46490A |  | R22 | Non-TXV |  | -7.071% | 1.0707 | 1.98% |  |  |  |  | Non-TXV |  |  | -7.071%
Bakersfield | CA | 93311-2274 |  | 2014-05-15 | 2014-05-15 10:40 | 2014-05-15 10:40 | RHEEM - RAMA-042JB2 | 95 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | 7E702B850E8D4AF794B38BAA1C66A0B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cupertino | CA | 95014-1657 |  | 2014-05-16 | 2014-05-16 14:43 | 2014-05-16 15:07 | GOODMAN - 088048RCUHL | 125 | 16.8 | Yes | Yes | 14.1 | 16.9 | -2.8 | 171B9FA1B1224B2991255549F93EBF00 |  | R22 | Non-TXV |  | 13.44% | 0.8656 | 25.83% | [5 empty] | Non-TXV | 13.44%
Bakersfield | CA | 93308-8013 |  | 2014-05-19 | 2014-05-19 09:30 | 2014-05-19 09:30 | WESTINGHOUSE - 1E024AAA0N | 52 | 0 | Yes | Yes | 19.4 | 21.5 | -2.1 | 6A3A560720594BFDB2CC4D0AAF262715 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-9352 |  | 2014-09-03 | 2014-09-03 09:37 | 2014-09-03 09:37 | UNITARY PRODUCTS GROUP - BRCS80481BD | 117 | 0 | Yes | Yes | 18.7 | 21.7 | -3 | 16F79BB418B74B2CABDA47F08F7723B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-1166 |  | 2014-05-09 | 2014-05-09 14:46 | 2014-05-09 14:46 | CARRIER - 24ABB330W310 | 68 | 0 | Yes | Yes | 22.1 | 19.3 | 2.8 | 551BB17CC1D74801BB5FD336274F1ADF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 15:08 | 2014-05-22 15:26 | ICP - C4A624GKD200 | 200 | 24.2 | Yes | Yes | 20.2 | 22.6 | -2.4 | 47AAB343CE654C13BB0CABF3B52B7EDB |  | R410A | TXV |  | 12.1% | 0.879 | 23.25% | [5 empty] | TXV | 12.1%
Woodland | CA | 95776-5713 |  | 2014-05-19 | 2014-05-19 10:10 | 2014-05-19 16:28 | AMANA - A8X140361CA | 98 | 4.2 | Yes | Yes | 16.1 | 18.8 | -2.7 | B7D5AC899E7247FF846E4BE7615E5AD8 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Bakersfield | CA | 93304-5183 |  | 2014-10-29 | 2014-10-29 12:11 | 2014-10-29 12:11 | BDP - 585EJ024050 | 54 | 0 | Yes | Yes | 26.6 | 22.3 | 4.3 | F16749FB1BCA49FFB721DAE0926C846B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 14:31 | 2014-05-22 14:31 | ICP - C4A624D200 | 200 | 0 | Yes | Yes | 19.4 | 22.4 | -3 | 661ED9DD145D42028483EB2913438F34 |  | R410A | TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-7722 |  | 2014-05-15 | 2014-05-15 10:07 | 2014-05-15 10:31 | CARRIER - 38CKC048300 | 104 | -11.6 | Yes | Yes | 21.9 | 16.3 | 5.6 | E246417A19F14C38B0B6A0988E5D31BE |  | R22 | Non-TXV |  | -11.15% | 1.1115 | 3.124% |  |  |  |  | Non-TXV |  |  | -11.15%
Woodland | CA | 95695-4350 |  | 2014-05-19 | 2014-05-19 12:19 | 2014-05-19 16:30 | PAYNE - PA13NR030-E | 86 | -5.1 | Yes | Yes | 15.7 | 18.5 | -2.8 | 39556CDA34C84278A8186F7049FACB59 |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Bakersfield | CA | 93304-5184 |  | 2014-10-29 | 2014-10-29 12:34 | 2014-10-29 12:34 | BDP - 585EJ024050 | 54 | 0 | Yes | Yes | 25.8 | 21 | 4.8 | 413E58EEC962481D8FBC76DBA248997E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-23 | 2014-05-23 18:28 | 2014-05-23 18:28 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 18.9 | 21.5 | -2.6 | 96E2E32ED3A04832B4054718160C90F9 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-2666 |  | 2014-07-21 | 2014-07-21 09:26 | 2014-07-21 09:26 | OTHER - UKN | 85 | 0 | Yes | Yes | 17.4 | 19.5 | -2.1 | 0A2248D30613463CAC1066FB4606CC75 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2394 |  | 2014-05-01 | 2014-05-01 19:08 | 2014-05-01 19:08 | YORK - D1NP042N06506A | 150 | 0 | Yes | Yes | 26.5 | 24.7 | 1.8 | 3160B0CED3694B9A84BA5832036BCABE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9473 |  | 2014-05-10 | 2014-05-10 14:07 | 2014-05-10 14:07 | UNITARY PRODUCTS GROUP - AC042X1221A | 107 | 0 | Yes | Yes | 18 | 20.9 | -2.9 | 44384C2C01044F35B8E96EC23DA2246C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2417 |  | 2014-07-25 | 2014-07-25 12:51 | 2014-07-25 12:51 | UNITARY PRODUCTS GROUP - DAYP-F042N080A | 150 | 0 | Yes | Yes | 22.8 | 20.2 | 2.6 | F8E269C844D448158502BEF64FB917B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-8125 |  | 2014-05-19 | 2014-05-19 12:37 | 2014-05-19 13:07 | BRYANT - 561CJX036 | 70 | -7 | Yes | Yes | 20 | 17.7 | 2.4 | A8217A2C798F4795915997CE4C2587FC |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Gilroy | CA | 95020-8125 |  | 2014-05-19 | 2014-05-19 12:43 | 2014-05-19 13:08 | - | 85 | 10.3 | Yes | Yes | 18 | 18.6 | -0.6 | F138488897E247109BBD70CC819EAB0A |  |  |  |  | 12.12% | 0.87882 | 23.29% | [5 empty] | 0 | 12.12%
Antioch | CA | 94531-9106 |  | 2014-05-23 | 2014-05-23 11:53 | 2014-05-23 11:53 | OTHER - 38CKC048360 | 125 | 0 | Yes | Yes | 21.3 | 18.5 | 2.8 | BB96167BC4E94EF1B468DD06804FAF62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 15:33 | 2014-05-21 15:33 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 21 | 21.8 | -0.8 | 9B21D42CD7D243DFB2A7FA120FFD4F8E |  | R410A | TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-4002 |  | 2014-05-19 | 2014-05-19 10:46 | 2014-05-19 10:46 | INTERTHERM - HAC036AKA443 | 80 | 0 | Yes | Yes | 21.5 | 19.3 | 2.2 | F79993902C654D9A96E40C3DF2589CA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 15:35 | 2014-05-21 15:35 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19 | 21 | -2 | E88EB026271F4D03BD58E7D83910A8C5 |  | R410A | TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5173 |  | 2014-05-13 | 2014-05-13 08:22 | 2014-05-13 16:24 | GOODMAN - CKL36-1D | 72 | -3.1 | Yes | Yes | 16.8 | 19.6 | -2.8 | 3FC371B0735442C8BD64C30F552AC5E8 |  | R22 | Non-TXV |  | -4.306% | 1.0431 | 1.206% |  |  |  |  | Non-TXV |  |  | -4.306%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 14:15 | 2014-05-21 14:15 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 18.1 | 20.3 | -2.2 | 45E39648F9B14F7EBF2643E77F257BA8 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4506 |  | 2014-05-28 | 2014-05-28 09:32 | 2014-05-28 09:32 | ARCOAIRE - PGF030K060A | 52 | 0 | Yes | Yes | 27.3 | 22.2 | 5.1 | 929058D9D97D4423B207868D5018E9DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-4012 |  | 2014-05-13 | 2014-05-13 08:29 | 2014-05-13 08:59 | CARRIER - T4A342CLA1 | 121 | 6.8 | Yes | Yes | 17.5 | 19 | -1.5 | 0E02292525934B5A9844CB5D6E8437B8 |  | R22 | Non-TXV |  | 5.62% | 0.9438 | 10.8% | [5 empty] | Non-TXV | 5.62%
Bakersfield | CA | 93306-3340 |  | 2014-07-22 | 2014-07-22 14:17 | 2014-07-22 14:17 | RUUD - UKN | 90 | 0 | Yes | Yes | 23.8 | 18.1 | 5.7 | 9498EAC30A8F4A4F87085ADF959FAF1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6016 |  | 2014-09-02 | 2014-09-02 09:53 | 2014-09-02 09:53 | RUUD - RRNA-B036JK6X | 83.2 | 3.3 | Yes | Yes | 26 | 22 | 4 | FB79794FFF5F47B9B864028C8D11EB04 | Add refrigerant: 3.3 oz | R22 | Non-TXV |  | 3.966% | 0.96034 | 7.622% | [5 empty] | Non-TXV | 3.966%
San Jose | CA | 95116-2967 |  | 2014-05-13 | 2014-05-13 09:14 | 2014-05-13 09:31 | CARRIER - 38CKC042 | 85 | -8 | Yes | Yes | 24.2 | 18.5 | 5.7 | 50A956F60800411499B3FC0529D48FED |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 15:54 | 2014-05-22 15:54 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 18.9 | 20.7 | -1.8 | D0BEEED8EC3E4C73B5F18E563960AE0A |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4376 |  | 2014-05-22 | 2014-05-22 09:53 | 2014-05-22 09:53 | CARRIER - 48GP-030040311 | 88 | 0 | Yes | Yes | 18.7 | 21.7 | -3 | 1285B706827C4E0E8B7E33D51D691B3F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6326 |  | 2014-05-22 | 2014-05-22 13:08 | 2014-05-22 13:08 | COLEMAN - BRCS04218DG | 84 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 4DF0C50AF25144578EE904B0E0B872E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1575 |  | 2014-08-28 | 2014-08-28 18:55 | 2014-08-28 18:55 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.9 | 19.9 | 2 | 59FDC59CB40A49B3B0787D16B1FE5F52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1576 |  | 2014-08-28 | 2014-08-28 19:07 | 2014-08-28 19:07 | CARRIER - 38YCC018 | 66 | 0 | Yes | Yes | 20.6 | 21.5 | -0.9 | F4B6886DE1F14FB29CF4613FAC20F75E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-21 | 2014-05-21 18:25 | 2014-05-21 18:25 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 19.2 | 20.4 | -1.2 | 9D7FBD005F29470B8578B44CCDAA0F92 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4205 |  | 2014-05-22 | 2014-05-22 16:23 | 2014-05-22 16:23 | ICP - C4A624GKD200 | 200 | 0 | Yes | Yes | 20.9 | 22.9 | -2 | B2623ED4176D4F9B91D8CD7F70EB1625 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95128-1256 |  | 2014-05-15 | 2014-05-15 15:09 | 2014-05-15 15:41 | AMANA - ZRCF036 | 107 | 7.7 | Yes | Yes | 13.7 | 16.4 | -2.7 | A9A12B40CD614674AA89477609020DFB |  | R22 | Non-TXV |  | 7.196% | 0.92804 | 13.83% | [5 empty] | Non-TXV | 7.196%
Fremont | CA | 94538-4145 |  | 2014-08-06 | 2014-08-06 10:03 | 2014-08-06 10:27 | CARRIER - 38CKB036320 | 85 | -6.7 | Yes | Yes | 17.3 | 18.2 | -0.9 | 7C4EDFCFE6754DDAAA7B462F2DE3E85D |  | R22 | TXV |  | -7.882% | 1.0788 | 2.207% |  |  |  |  | TXV |  |  | -7.882%
Shafter | CA | 93263-2420 |  | 2014-10-05 | 2014-10-05 18:45 | 2014-10-05 18:52 | OTHER - PGAD42D1K1 | 180 | 5.4 | Yes | Yes | 15.8 | 18.2 | -2.4 | 50F5D08C457D49C8941C7804A7455AC3 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fremont | CA | 94536-5560 |  | 2014-05-29 | 2014-05-29 09:30 | 2014-05-29 10:12 | AMANA - RCB030B2A | 77 | -7.2 | Yes | Yes | 23 | 19.9 | 3.1 | 19BEB8DC1A0C47F4B7C7069E9BC3AD70 |  | R22 | Non-TXV |  | -9.351% | 1.0935 | 2.619% |  |  |  |  | Non-TXV |  |  | -9.351%
Bakersfield | CA | 93304-4555 |  | 2014-06-17 | 2014-06-17 11:33 | 2014-06-17 11:33 | BRYANT - 582ANW036060AAAF | 60 | 0 | Yes | Yes | 23.4 | 22.4 | 1.1 | BB872C2FE2C84E93907BD7DEF8297BBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 14:02 | 2014-09-13 14:18 | BDP - 661CJ018B | 68 | 7 | Yes | Yes | 25.6 | 23 | 2.6 | 2A40529DFD2C49BF99737B77B80292ED |  | R22 | Non-TXV |  | 10.29% | 0.89706 | 19.78% | [5 empty] | Non-TXV | 10.29%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 16:07 | 2014-09-13 16:07 | GOODMAN - GSH130181BB | 127 | 0 | Yes | Yes | 21.2 | 21.8 | -0.5 | 4245A2BFF88F432D82691A0BC0E4969F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2727 |  | 2014-06-30 | 2014-06-30 11:16 | 2014-06-30 11:54 | RHEEM - RRKA-A048JK10X | 75 | 0 | Yes | Yes | 18.4 | 21.2 | -2.8 | C2F4E39E516F46F0B428982F70A24442 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4319 |  | 2014-05-20 | 2014-05-20 08:26 | 2014-05-20 08:26 | AMANA - PGC30B0702A | 81 | 0 | Yes | Yes | 19.2 | 21.5 | -2.3 | 1D6A38B49C1F44CFA209176EFD3E8583 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 15:13 | 2014-09-13 15:13 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 21.2 | 21.4 | -0.2 | 8A372F1963824B76BEDB9029F9188565 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2308 |  | 2014-08-30 | 2014-08-30 17:48 | 2014-08-30 17:48 | OTHER - DRCS0361BE | 83 | 0 | Yes | Yes | 23.7 | 20.4 | 3.3 | 7E866F26E2DE46F49B6850C1F7AD5481 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2517 |  | 2014-07-18 | 2014-07-18 17:20 | 2014-07-18 19:41 | RHEEM - RRMA-A036JK08X | 99 | -8.2 | Yes | Yes | 14.5 | 17.4 | -2.9 | 2EEDD3289F5D48DBBBA753FC33370822 |  | R22 | Non-TXV |  | -8.283% | 1.0828 | 2.32% |  |  |  |  | Non-TXV |  |  | -8.283%
San Jose | CA | 95126-4814 |  | 2014-09-05 | 2014-09-05 10:55 | 2014-09-05 10:57 | OTHER - 565BJ030 | 150 | 4.4 | Yes | Yes | 19 | 18.8 | 0.2 | 515AA90847D8405EA03F2E0644F44684 |  | R22 | Non-TXV |  | 2.933% | 0.97067 | 5.637% | [5 empty] | Non-TXV | 2.933%
Bakersfield | CA | 93301-1121 |  | 2014-10-21 | 2014-10-21 16:10 | 2014-10-21 16:10 | RHEEM - RRNAB024JK06X | 70 | 0 | Yes | Yes | 21.8 | 22.3 | -0.5 | C9143A3217DC4FF082D492DD96FFF9E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5111 |  | 2014-07-02 | 2014-07-02 08:51 | 2014-07-02 21:36 | PAYNE - PY1PNB036060AAAA | 56 | -5.3 | Yes | Yes | 14 | 15.9 | -1.9 | 2640E0CAC8D344338DE67770B29D10B1 |  | R22 | Non-TXV |  | -9.464% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.464%
Wasco | CA | 93280-2226 |  | 2014-07-22 | 2014-07-22 17:49 | 2014-07-22 17:52 | OTHER - N/A | 85 | 3.3 | Yes | Yes | 20.4 | 21.2 | -0.8 | 0F07FFE8D6114D3382947D9031BAF133 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Fairfield | CA | 94533-2067 |  | 2014-06-09 | 2014-06-09 13:42 | 2014-06-09 15:16 | AMERICAN STANDARD - | 85 | 5.4 | Yes | Yes | 20.6 | 16.5 | 4.1 | 42A40E2289854642BCDE83A65D0481C0 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
San Jose | CA | 95128-2128 |  | 2014-05-14 | 2014-05-14 09:08 | 2014-05-14 09:27 | YORK - H2RA036S06 | 63 | 8.1 | Yes | Yes | 15.5 | 16.1 | -0.6 | D7D6454284F44998BAD21163AB0457DC |  | R22 | Non-TXV |  | 12.86% | 0.87143 | 24.71% | [5 empty] | Non-TXV | 12.86%
W Sacramento | CA | 95691-4448 |  | 2014-08-26 | 2014-08-26 11:44 | 2014-08-26 12:27 | CARRIER - 38K036300 | 117 | 5.4 | Yes | Yes | 23.5 | 21.4 | 2.1 | 5086540AF0BE4143B11611F79CE6AEBD |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Morgan Hill | CA | 95037-4431 |  | 2014-05-28 | 2014-05-28 09:27 | 2014-05-28 09:27 | AMANA - RCB60A2A | 195 | 0 | Yes | Yes | 18.2 | 19.4 | -1.2 | 60C8C644A12D45C5937E7CCAF4021632 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-0000 |  | 2014-08-23 | 2014-08-23 19:12 | 2014-08-23 19:16 | COLEMAN - ERCQ0481B1BBA | 124 | -5.8 | Yes | Yes | 21.1 | 20.8 | 0.3 | BD4BF93093994449A91C415B141F9073 |  | R22 | TXV |  | -4.677% | 1.0468 | 1.31% |  |  |  |  | TXV |  |  | -4.677%
Morgan Hill | CA | 95037-6070 |  | 2014-05-23 | 2014-05-23 11:28 | 2014-05-23 11:56 | NORDYNE - FS3BA-030KA | 68 | 14 | Yes | Yes | 15.5 | 18.4 | -2.9 | 2DB6ACDA9E094B208C54F1D8F2FA5A6B |  | R22 | Non-TXV |  | 20.59% | 0.79412 | 39.57% | [5 empty] | Non-TXV | 20.59%
W Sacramento | CA | 95691-4216 |  | 2014-05-20 | 2014-05-20 09:02 | 2014-05-20 09:28 | GOODMAN - GSH130361AD | 188 | 3.1 | Yes | Yes | 13 | 15.8 | -2.8 | 0422E873E11844D0AC7D96A03908506E |  | R22 | Non-TXV |  | 1.649% | 0.98351 | 3.169% | [5 empty] | Non-TXV | 1.649%
Vallejo | CA | 94589-4369 |  | 2014-08-07 | 2014-08-07 11:16 | 2014-08-07 22:11 | CARRIER - 591ANX030000ABAA | 85 | 6.9 | Yes | Yes | 16.5 | 18.8 | -2.3 | 932F3C4D42E64E65BB31B5A714237BE7 |  | R22 | Non-TXV |  | 8.118% | 0.91882 | 15.6% | [5 empty] | Non-TXV | 8.118%
W Sacramento | CA | 95691-5926 |  | 2014-05-20 | 2014-05-20 09:52 | 2014-05-20 16:55 | CARRIER - 38CKC036350 | 70 | -3.9 | Yes | Yes | 21.3 | 23.5 | -2.2 | 58BED01116A44B9CB7F80CFD8B6F8A00 |  | R22 | Non-TXV |  | -5.571% | 1.0557 | 1.56% |  |  |  |  | Non-TXV |  |  | -5.571%
San Jose | CA | 95127-1927 |  | 2014-05-27 | 2014-05-27 11:17 | 2014-05-27 11:41 | TEMPSTAR - TZZA3362A737 | 100 | -9.4 | Yes | Yes | 22.6 | 18.1 | 4.5 | 0AA19C78222E4B00AD53EE1355F6AE0D |  | R22 | Non-TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.4%
Gilroy | CA | 95020-6717 |  | 2014-05-19 | 2014-05-19 11:12 | 2014-05-19 11:31 | AMANA - RCB36A2B | 94 | -8.8 | Yes | Yes | 21.2 | 17.5 | 3.7 | C38217AC1C2F42478993CC1F283FD39B |  | R22 | Non-TXV |  | -9.362% | 1.0936 | 2.622% |  |  |  |  | Non-TXV |  |  | -9.362%
W Sacramento | CA | 95691-5145 |  | 2014-05-20 | 2014-05-20 10:28 | 2014-05-20 10:28 | GE - BGTA742B1B | 85 | 0 | Yes | Yes | 19.7 | 19.3 | 0.4 | D5EA7796609A40AEBD40C7490ADB3863 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9387 |  | 2014-05-29 | 2014-05-29 10:22 | 2014-05-29 10:51 | GOODMAN - CRJ30-16 | 85 | -6 | Yes | Yes | 19.1 | 17.5 | 1.6 | D487A3B7D4F14B45A487596C56AB9681 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Vacaville | CA | 95687-3402 |  | 2014-05-13 | 2014-05-13 11:14 | 2014-05-13 16:28 | - | 85 | -5 | Yes | Yes | 13.9 | 16.9 | -3 | 623AC363B377469BAFB71CBE04F21671 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93306-9545 |  | 2014-07-30 | 2014-07-30 14:14 | 2014-07-30 14:14 | RHEEM - RQPL-B024JK | 97 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | 58229290791048C790F832943E434FCB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-3929 |  | 2014-06-25 | 2014-06-25 11:09 | 2014-06-25 12:18 | ALLEGIANCE - 2A7A036B1000AAA | 118 | -8.3 | Yes | Yes | 21.6 | 19.3 | 2.3 | 5BA87F73362A4233BC02EE4C899C5AAB |  | R22 | Non-TXV |  | -7.034% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.034%
Suisun City | CA | 94585-4136 |  | 2014-07-31 | 2014-07-31 15:01 | 2014-07-31 20:53 | PAYNE - PA13NR036-J | 84 | -6.9 | Yes | Yes | 15.2 | 18.1 | -2.9 | D21AFE5012904918AA50CDE754BA39AA |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Dixon | CA | 95620-4276 |  | 2014-05-23 | 2014-05-23 10:36 | 2014-05-23 15:59 | CARRIER - 38TDA036300 | 85 | -6 | Yes | Yes | 17.4 | 17.1 | 0.4 | 195F2ED97FD44B86AFD64550923172BE |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Vacaville | CA | 95687-4937 |  | 2014-05-13 | 2014-05-13 10:43 | 2014-05-13 16:27 | - | 85 | -4 | Yes | Yes | 12.2 | 14.7 | -2.5 | 69460B28F0FD43469DA141997B90C050 |  | R22 | Non-TXV |  | -4.706% | 1.0471 | 1.318% |  |  |  |  | Non-TXV |  |  | -4.706%
Vacaville | CA | 95687-6337 |  | 2014-05-13 | 2014-05-13 10:07 | 2014-05-13 16:25 | DAY & NIGHT - 5658J024 | 70 | -4.9 | Yes | Yes | 13.9 | 16.4 | -2.5 | 8F9CD979EC4B4CDB914F4689DF3C5C6A |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Bakersfield | CA | 93311-2464 |  | 2014-05-15 | 2014-05-15 11:59 | 2014-05-15 11:59 | LENNOX - 14ACX-048-230-10 | 160 | 0 | Yes | Yes | 17.8 | 19.8 | -2 | 7003EFB0E7C94A00B38D7ADF84D28E9B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2333 |  | 2014-08-30 | 2014-08-30 10:24 | 2014-08-30 11:07 | DAY & NIGHT - PGF336060K00 | 146 | -8 | Yes | Yes | 17.4 | 11.7 | 5.7 | 9511203E1F0240F891D6EDAE4C4B0FF8 |  | R22 | Non-TXV |  | -5.479% | 1.0548 | 1.535% |  |  |  |  | Non-TXV |  |  | -5.479%
Santa Rosa | CA | 95403-1386 |  | 2014-05-20 | 2014-05-20 12:51 | 2014-05-20 13:24 | HEIL - CA5530VKD2 | 74 | -6.1 | Yes | Yes | 20.5 | 19.1 | 1.4 | AEFFFB3C2D2145B98569FB6AAAB3D63E |  | R22 | Non-TXV |  | -8.243% | 1.0824 | 2.308% |  |  |  |  | Non-TXV |  |  | -8.243%
Dixon | CA | 95620-2304 |  | 2014-05-22 | 2014-05-22 11:27 | 2014-05-22 13:24 | CARRIER - 38CKC030330 | 68 | -6.4 | Yes | Yes | 14.8 | 17.2 | -2.4 | 4F64F158D1F6413AB3F8432F790D81CC |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93305-2147 |  | 2014-05-16 | 2014-05-16 12:16 | 2014-05-16 12:16 | BDP - 585B036075 | 60 | 0 | Yes | Yes | 22.1 | 19.6 | 2.6 | 58122B9CA7E5450D89B286E52B727DEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4640 |  | 2014-07-22 | 2014-07-22 13:41 | 2014-07-22 13:41 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 16.8 | 17.9 | -1.1 | FFFFCC5F58574986B29F93825F0FB094 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5971 |  | 2014-05-12 | 2014-05-12 13:06 | 2014-05-12 13:06 | OTHER - UKN | 90 | 0 | Yes | Yes | 22.1 | 21 | 1.1 | 05A8167D26C84E0FBF754973F75EE36B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 15:00 | 2014-09-13 15:00 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 481084D240074B2DAFA2B775C443C4EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1120 |  | 2014-10-24 | 2014-10-24 11:47 | 2014-10-24 11:47 | RHEEM - UKN | 90 | 0 | Yes | Yes | 23.3 | 21.4 | 1.9 | 3457073A6E2848ADBCE386AF2D007AB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1575 |  | 2014-08-25 | 2014-08-25 19:18 | 2014-08-25 19:18 | CARRIER - 38YCC01840 | 85 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | EFF00074297E453892CEEC978FAAD6C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 15:54 | 2014-09-13 15:54 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 21.1 | 22.6 | -1.5 | 8901E09C2062463CB1E318FE846DBBCF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-6007 |  | 2014-05-22 | 2014-05-22 13:22 | 2014-05-22 13:39 | CARRIER - 24ABB336W310 | 85 | 9.4 | Yes | Yes | 21.6 | 19.9 | 1.7 | 84486E55BB0B4ED0B807B0FD3F0E9CE7 |  | R22 | TXV |  | 11.06% | 0.88941 | 21.25% | [5 empty] | TXV | 11.06%
San Jose | CA | 95122-3378 |  | 2014-05-27 | 2014-05-27 13:40 | 2014-05-27 14:12 | YORK - H1RA048S06 | 117 | 24.4 | Yes | Yes | 19.3 | 20.4 | -1.1 | 7780F6B828E84B81972DA8386998BB07 |  | R22 | Non-TXV |  | 20.85% | 0.79145 | 40.08% | [5 empty] | Non-TXV | 20.85%
Dixon | CA | 95620-3103 |  | 2014-05-22 | 2014-05-22 12:40 | 2014-05-22 13:24 | GE - | 85 | -6 | Yes | Yes | 12.7 | 15.7 | -3 | 055DDDCAFB1E438194889CA3F9FC53CF |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 14:48 | 2014-09-13 14:48 | BDP - UKN | 68 | 0 | Yes | Yes | 21 | 21.5 | -0.5 | DC9DE0F469C44A0498ADD978917C7F0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5188 |  | 2014-06-26 | 2014-06-26 08:49 | 2014-06-26 09:19 | CARRIER - 38CKC036350 | 71 | 3 | Yes | Yes | 19.3 | 20.4 | -1.1 | 7AA88D7E2F1A4F87AE82E92A6730CF5B |  | R22 | Non-TXV |  | 4.225% | 0.95775 | 8.12% | [5 empty] | Non-TXV | 4.225%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 13:59 | 2014-09-13 13:59 | GOODMAN - GSH130181CB | 127 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | 34CDEE1921D04FCC8AC0C6E937CACCC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4927 |  | 2014-05-22 | 2014-05-22 14:01 | 2014-05-22 14:01 | OTHER - EAFF-043JAZ | 99 | 0 | Yes | Yes | 17.9 | 20.9 | -3 | 203B1F6F37034BC99D181870CACAA4F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2176 |  | 2014-06-24 | 2014-06-24 09:16 | 2014-06-24 09:40 | YORK - H4DB024S06A | 58 | -4.8 | Yes | Yes | 12.3 | 14.7 | -2.4 | 2E1B53395B514AF88BA97ECB10B3ACC9 |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Bakersfield | CA | 93311-8904 |  | 2014-05-15 | 2014-05-15 09:30 | 2014-05-15 09:30 | WEATHER KING - 13AJA60A01 | 191 | 0 | Yes | Yes | 25.4 | 21.5 | 3.9 | 45F01D0B68DD46C19FDDDFAF2C401E74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2941 |  | 2014-11-06 | 2014-11-06 11:00 | 2014-11-06 11:00 | OTHER - GR8GD036K072C | 59 | 0 | Yes | Yes | 21.1 | 19.1 | 2 | B1B94991D0C747CAA19F59F7852C81DB |  | R410A | TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3741 |  | 2014-05-20 | 2014-05-20 13:03 | 2014-05-20 16:56 | CARRIER - PGE0B24D0LA1602M14455 | 59 | -4.9 | Yes | Yes | 17.8 | 19.1 | -1.3 | 2B0149CE87AD49D6AF9DC7155C9439EF |  | R22 | Non-TXV |  | -8.305% | 1.0831 | 2.326% |  |  |  |  | Non-TXV |  |  | -8.305%
Bakersfield | CA | 93306-4837 |  | 2014-06-25 | 2014-06-25 11:20 | 2014-06-25 11:20 | ICP - PGAA42C1K3 | 82 | 0 | Yes | Yes | 20.2 | 20.2 | 0 | B5E15A8AC4D2473FA5E2AFF0F24CAAD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-8013 |  | 2014-05-19 | 2014-05-19 09:43 | 2014-05-19 09:43 | WESTINGHOUSE - 1E024AAA0N | 52 | 0 | Yes | Yes | 15.6 | 18.5 | -2.9 | 82FCA59750884737B2CADAB1645DB00F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2103 |  | 2014-06-12 | 2014-06-12 10:53 | 2014-06-12 11:21 | PAYNE - PA10JA030-B | 80 | 3 | Yes | Yes | 22.3 | 20.4 | 1.9 | AA4F0515CE44447191CDFDA5C0F63770 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
San Jose | CA | 95116-3626 |  | 2014-05-15 | 2014-05-15 14:29 | 2014-05-15 14:50 | YORK - AC048X102A | 117 | 9.9 | Yes | Yes | 16.2 | 17.9 | -1.7 | B546F11A2C2F40129B7FCB02344C1F41 |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Davis | CA | 95618-4349 |  | 2014-06-18 | 2014-06-18 08:20 | 2014-06-18 08:20 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 23.8 | 18.1 | 5.7 | 29CF9C9CB650405492A0449B9F3C0A85 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1459 |  | 2014-06-09 | 2014-06-09 12:59 | 2014-06-09 15:15 | RHEEM - | 85 | 7 | Yes | Yes | 19.7 | 15.4 | 4.3 | 8E519592C9D0434C8DE873D2A6841889 |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Morgan Hill | CA | 95037-7810 |  | 2014-05-22 | 2014-05-22 14:30 | 2014-05-22 15:34 | CARRIER - 561CJX0300 | 68 | -6.4 | Yes | Yes | 22.6 | 19.4 | 3.2 | B5CA76B57D2A48CA935B1CE3DEF6E286 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
San Jose | CA | 95138-1322 |  | 2014-05-14 | 2014-05-14 12:41 | 2014-05-14 12:57 | CARRIER - 39CKC03633- | 84 | 10.5 | Yes | Yes | 15.2 | 17.8 | -2.6 | 64FC43B768A64D50B1A0CC099A5D2E03 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Vacaville | CA | 95687-5197 |  | 2014-05-28 | 2014-05-28 11:08 | 2014-05-28 14:37 | GOODMAN - GSX130481BA | 128 | 4.9 | Yes | Yes | 16.9 | 16.4 | 0.5 | 9A777F94D26549E0B8094CBEBA8428D9 |  | R22 | Non-TXV |  | 3.828% | 0.96172 | 7.357% | [5 empty] | Non-TXV | 3.828%
Bakersfield | CA | 93304-5519 |  | 2014-07-10 | 2014-07-10 12:33 | 2014-07-10 12:33 | CARRIER - 48SS-042060331 | 83 | 0 | Yes | Yes | 19.9 | 21.3 | -1.4 | 8FA62C3E2EBF438095AC7D6A02C191B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2903 |  | 2014-08-10 | 2014-08-10 20:30 | 2014-08-10 20:34 | DAY & NIGHT - N/A | 85 | 5.5 | Yes | Yes | 26.7 | 21.5 | 5.2 | 6AED8301C8594E85AA1DB3B398358BAB |  | R22 | Non-TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | Non-TXV | 6.471%
Davis | CA | 95618-4443 |  | 2014-05-19 | 2014-05-19 14:10 | 2014-05-19 16:31 | LENNOX - 13ACD-024-230-11 | 67 | -4.3 | Yes | Yes | 10.4 | 13 | -2.6 | C3C888FF20FE4ABBBC1AFEAB8B8058EB |  | R22 | Non-TXV |  | -6.418% | 1.0642 | 1.797% |  |  |  |  | Non-TXV |  |  | -6.418%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 15:25 | 2014-09-13 15:25 | GOODMAN - G8H130241CB | 122 | 0 | Yes | Yes | 20.5 | 22.6 | -2.1 | 2EAD787725F242B7B8258031EFB5699F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1560 |  | 2014-09-03 | 2014-09-03 18:43 | 2014-09-03 19:06 | PAYNE - PH13NR018H | 83 | 12.9 | Yes | Yes | 21.1 | 22 | -0.9 | 87B6FD1C44A34F0B9EC05493C75B5761 |  | R22 | Non-TXV |  | 15.54% | 0.84458 | 29.87% | [5 empty] | Non-TXV | 15.54%
Bakersfield | CA | 93304-1560 |  | 2014-08-25 | 2014-08-25 19:53 | 2014-08-25 19:53 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 18.6 | 21.5 | -2.9 | B2197F95B2EE4D588FAE532A440993E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1534 |  | 2014-08-28 | 2014-08-28 19:56 | 2014-08-28 19:56 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.3 | 22.3 | -2 | F07378CF3029449389B9FB18112ACEAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1559 |  | 2014-08-25 | 2014-08-25 18:48 | 2014-08-25 19:10 | CARRIER - 38YCC018340 | 85 | 10.6 | Yes | Yes | 18.9 | 20.8 | -1.9 | AE46F499379C435E922263F6B6B4A00A |  | R22 | Non-TXV |  | 12.47% | 0.87529 | 23.97% | [5 empty] | Non-TXV | 12.47%
Bakersfield | CA | 93304-1534 |  | 2014-08-28 | 2014-08-28 20:00 | 2014-08-28 20:00 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.5 | 22 | -1.5 | 7E6BDBC64ECB4DB68CFD0DE19D6F4A38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5763 |  | 2014-06-03 | 2014-06-03 10:27 | 2014-06-03 10:27 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.9 | 21 | 0.9 | 33B31BFCC6CA4A108CDE4D0F0DBAA385 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1569 |  | 2014-09-03 | 2014-09-03 19:41 | 2014-09-03 19:41 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | DDC61C08FFA64C69BD70969925CC0419 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1559 |  | 2014-08-28 | 2014-08-28 18:47 | 2014-08-28 18:47 | PAYNE - PH13NR018H | 70 | 0 | Yes | Yes | 22.5 | 22 | 0.5 | C8C85E89F8C74955BD1D1AFA9727C937 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1556 |  | 2014-08-25 | 2014-08-25 18:37 | 2014-08-25 18:37 | CARRIER - 38YCC018340 | 87 | 0 | Yes | Yes | 19.2 | 20.7 | -1.5 | E2D4C58EB9C24EB68C566C9380ACE87A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1556 |  | 2014-08-20 | 2014-08-20 15:41 | 2014-08-20 15:41 | CARRIER - 3BYCC018340 | 66 | 0 | Yes | Yes | 19.9 | 22.4 | -2.5 | 5BEF9774CB7643289A972BFB28F234F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1557 |  | 2014-08-25 | 2014-08-25 19:28 | 2014-08-25 19:28 | CARRIER - 38YCC018340 | 85 | 0 | Yes | Yes | 19.4 | 21.2 | -1.8 | B05B64669D0F4B3081340CD9D5BDB949 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1551 |  | 2014-08-25 | 2014-08-25 19:47 | 2014-08-25 19:47 | - | 85 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | CD93823CEB6A464B8C195874420A4361 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1551 |  | 2014-08-28 | 2014-08-28 20:05 | 2014-08-28 20:05 | CARRIER - 38YCC024341 | 66 | 0 | Yes | Yes | 20.9 | 21.8 | -0.9 | D58EC851509F4C249EDC6FA0B3C867A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1569 |  | 2014-08-20 | 2014-08-20 16:07 | 2014-08-20 16:07 | CARRIER - 3YBCC018340 | 66 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | 18A27B1F1D4E47C1BE14CDEECBE4161B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1569 |  | 2014-09-03 | 2014-09-03 19:44 | 2014-09-03 19:44 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.6 | 19.9 | 0.7 | F37B76CDFBD3484482E8D44BCF06F9DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1561 |  | 2014-09-03 | 2014-09-03 19:48 | 2014-09-03 19:48 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.7 | 21.5 | -0.8 | CE2DDF864C754965A00D85C0E13B76D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2509 |  | 2014-08-30 | 2014-08-30 17:15 | 2014-08-30 17:36 | GOODMAN - GPG13360451AC | 112 | 6.1 | Yes | Yes | 23.7 | 20.4 | 3.3 | FCF33CB6F1E241939629B96507EA3CC1 |  | R22 | Non-TXV |  | 5.446% | 0.94554 | 10.47% | [5 empty] | Non-TXV | 5.446%
Gilroy | CA | 95020-8925 |  | 2014-05-19 | 2014-05-19 13:22 | 2014-05-19 14:14 | TRANE - TTR042D100B0 | 81 | 4.1 | Yes | Yes | 19.5 | 18.7 | 0.8 | 487579A24E2846E1B66B6A501752563D |  | R22 | Non-TXV |  | 5.062% | 0.94938 | 9.728% | [5 empty] | Non-TXV | 5.062%
Suisun City | CA | 94585-4130 |  | 2014-05-12 | 2014-05-12 15:20 | 2014-05-12 15:20 | PAYNE - 598AN036-B | 188 | 0 | Yes | Yes | 18.1 | 20.1 | -2 | 503E3B34942E470ABB8BF09D47A27DE2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-7249 |  | 2014-05-28 | 2014-05-28 12:37 | 2014-05-28 12:53 | RUUD - UAKA037JAZ | 79 | 14.8 | Yes | Yes | 18 | 19.9 | -1.9 | ACDA5A4DEBB942FAB342C17177C3D557 |  | R22 | Non-TXV |  | 18.73% | 0.81266 | 36% | [5 empty] | Non-TXV | 18.73%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 15:22 | 2014-09-13 15:22 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 20.7 | 22.6 | -1.9 | EFFA4E40C78F48FDB3054DD2D553A089 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2322 |  | 2014-10-05 | 2014-10-05 18:31 | 2014-10-05 18:35 | GOODMAN - GPG13300451AB | 77 | 5.9 | Yes | Yes | 20.6 | 21 | -0.4 | 783FC6F2C46E47A78286C5809C03C327 |  | R22 | Non-TXV |  | 7.662% | 0.92338 | 14.73% | [5 empty] | Non-TXV | 7.662%
Woodland | CA | 95776-4205 |  | 2014-06-11 | 2014-06-11 08:46 | 2014-06-11 09:24 | TRANE - 4TTX4024A1000AA | 82 | 2.7 | Yes | Yes | 19.2 | 18 | 1.3 | 5575C4B913B7493ABAB25C6AC601CB9B |  | R22 | Non-TXV |  | 3.293% | 0.96707 | 6.328% | [5 empty] | Non-TXV | 3.293%
Bakersfield | CA | 93306-3857 |  | 2014-06-24 | 2014-06-24 14:35 | 2014-06-24 14:35 | HEIL - UKN | 90 | 0 | Yes | Yes | 20.6 | 21.4 | -0.8 | 745BA6EF03FB4C8699ECF5EE7307EE22 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2626 |  | 2014-08-02 | 2014-08-02 18:28 | 2014-08-02 18:35 | GIBSON - JS5BD-030KA | 99 | 6.3 | Yes | Yes | 20.7 | 20.4 | 0.3 | 5BE132C924F24EDCB5FC0D5F70C6510C |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Vallejo | CA | 94591-6310 |  | 2014-05-16 | 2014-05-16 09:06 | 2014-05-16 14:01 | GOODMAN - CK36-1A | 73 | 2.4 | Yes | Yes | 13.8 | 16.4 | -2.6 | 23FBA11BC436414585D60B316BD718B5 |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Morgan Hill | CA | 95037-5729 |  | 2014-08-08 | 2014-08-08 12:02 | 2014-08-08 12:02 | GOODMAN - CKL36-1D | 72 | 0 | Yes | Yes | -3 | 20.9 | -23.9 | 075F56CB63F6470A8AE5ADFA047B7242 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Livermore | CA | 94550-5725 |  | 2014-05-22 | 2014-05-22 09:53 | 2014-05-22 09:53 | RHEEM - KACA-868JAS | 112 | 0 | Yes | Yes | 19.6 | 19.6 | 0 | 48FB797481934E898910FEA71A54BF2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95118-2626 |  | 2014-05-14 | 2014-05-14 10:20 | 2014-05-14 10:52 | WESTINGHOUSE - FS5BD036K | 116 | -10.9 | Yes | Yes | 20.2 | 17 | 3.2 | DE0C8756ABDC4BB5B8D016DD1B5DF023 |  | R22 | Non-TXV |  | -9.397% | 1.094 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.397%
Morgan Hill | CA | 95037-3022 |  | 2014-05-22 | 2014-05-22 13:59 | 2014-05-22 14:15 | CARRIER - 38TK048300 | 187 | -13.2 | Yes | Yes | 17.8 | 18.8 | -1 | 2D71B8C6AA4E438FB0FA2471268951C6 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Vacaville | CA | 95687-8215 |  | 2014-05-13 | 2014-05-13 12:51 | 2014-05-13 12:51 | CARRIER - 24ABA342A310 | 93 | 0 | Yes | Yes | 12.5 | 15.2 | -2.7 | FD41FEC9CA064E4B8A9C391673D785DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4432 |  | 2014-11-11 | 2014-11-11 13:26 | 2014-11-11 13:43 | DAY & NIGHT - N4A330AKC200 | 66 | 4 | Yes | Yes | 19.6 | 20.4 | -0.8 | 1D92BE2BF4A74D91B6EBD88B2EC14B52 |  | R410A | Non-TXV |  | 6.061% | 0.93939 | 11.65% | [5 empty] | Non-TXV | 6.061%
Winters | CA | 95694-1669 |  | 2014-09-30 | 2014-09-30 09:57 | 2014-09-30 10:23 | BRYANT - 38CKC042300 | 80 | 5.9 | Yes | Yes | 20 | 19.9 | 0.1 | 24AB405F0DB241F0B02C0D961E6546F2 |  | R22 | Non-TXV |  | 7.375% | 0.92625 | 14.17% | [5 empty] | Non-TXV | 7.375%
Gilroy | CA | 95020-8227 |  | 2014-05-28 | 2014-05-28 13:26 | 2014-05-28 14:17 | CARRIER - 38CKC048300 | 106 | -7.2 | Yes | Yes | 22.4 | 20.4 | 2 | 714BB5F4D7024973892E1B7AAE6E1803 |  | R22 | TXV |  | -6.792% | 1.0679 | 1.902% |  |  |  |  | TXV |  |  | -6.792%
Bakersfield | CA | 93306-6436 |  | 2014-06-24 | 2014-06-24 12:49 | 2014-06-24 12:49 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 23.7 | 20.1 | 3.6 | CBBBF23EB94D4300825E7E8E90607E8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6741 |  | 2014-06-11 | 2014-06-11 09:09 | 2014-06-11 10:56 | CARRIER - 38TH036300 | 83 | -4.8 | Yes | Yes | 19.9 | 17.5 | 2.5 | E155671D044B4F769697EA3DBAEA2895 |  | R22 | Non-TXV |  | -5.783% | 1.0578 | 1.62% |  |  |  |  | Non-TXV |  |  | -5.783%
Bakersfield | CA | 93307-4284 |  | 2014-06-18 | 2014-06-18 12:26 | 2014-06-18 12:26 | ICP - PGD330060K001C1 | 98 | 0 | Yes | Yes | 24.3 | 20.4 | 3.9 | 92847EB360EA4B5A82A6A94C50F1EB86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-3811 |  | 2014-06-25 | 2014-06-25 13:06 | 2014-06-25 13:26 | AMANA - CCU10A48 | 98 | 9.8 | Yes | Yes | 21.3 | 20.3 | 1 | 5F8221B839224A9E979E4914E98D0336 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
San Jose | CA | 95116-2414 |  | 2014-05-14 | 2014-05-14 09:45 | 2014-05-14 09:45 | AMERICAN STANDARD - 3BSA030 | 76 | 0 | Yes | Yes | 17 | 16.6 | 0.4 | CD4F66453C14423289F91076A7C377DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1131 |  | 2014-10-24 | 2014-10-24 12:33 | 2014-10-24 12:33 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.6 | 21.5 | -0.9 | 75C13DA7D0F145E597441235767A79F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2721 |  | 2014-08-03 | 2014-08-03 18:25 | 2014-08-03 18:29 | FRIGIDAIRE - N/A | 85 | 7.4 | Yes | Yes | 20.1 | 22.5 | -2.4 | 7F9D8C0DB31E4CFEAFF799563C8735B6 |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Wasco | CA | 93280-2761 |  | 2014-08-09 | 2014-08-09 17:27 | 2014-08-09 17:29 | YORK - H2RD042S06B | 141 | 6.2 | Yes | Yes | 20.4 | 21 | -0.6 | 922FDEF3EBD448098D297C92529C1352 |  | R22 | Non-TXV |  | 4.397% | 0.95603 | 8.45% | [5 empty] | Non-TXV | 4.397%
Wasco | CA | 93280-2699 |  | 2014-08-03 | 2014-08-03 18:57 | 2014-08-03 19:00 | YORK - H2RD036S06B | 96 | 6.9 | Yes | Yes | 22.3 | 22.3 | 0 | FDC9A8E9910D4AC786CA0BEB128DE5FB |  | R22 | TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | TXV | 7.187%
Bakersfield | CA | 93305-2852 |  | 2014-05-19 | 2014-05-19 10:52 | 2014-05-19 10:52 | RHEEM - RRNL-B024JK06X | 77 | 0 | Yes | Yes | 24 | 21.6 | 2.4 | AEEFC472039E4E298C22F85A3E85032B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-0000 |  | 2014-08-09 | 2014-08-09 16:50 | 2014-08-09 16:52 | OTHER - 2AC13B36P-1A | 139 | 5.8 | Yes | Yes | 19.7 | 19.8 | -0.1 | 09491D5AB8B14D8B9D5FBFB7FDCCE184 |  | R22 | Non-TXV |  | 4.173% | 0.95827 | 8.019% | [5 empty] | Non-TXV | 4.173%
Bakersfield | CA | 93301-1122 |  | 2014-10-21 | 2014-10-21 17:06 | 2014-10-21 17:06 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22.2 | 22.6 | -0.4 | BFFE77741F3349DA85DEEE794C114BDA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3439 |  | 2014-09-20 | 2014-09-20 17:36 | 2014-09-20 17:39 | GOODMAN - GPG1360451AA | 112 | 5.5 | Yes | Yes | 23.6 | 22 | 1.6 | 9DC38A87FB404272B3D64001FD87720E |  | R22 | Non-TXV |  | 4.911% | 0.95089 | 9.437% | [5 empty] | Non-TXV | 4.911%
Shafter | CA | 93263-2218 |  | 2014-08-24 | 2014-08-24 19:57 | 2014-08-24 19:59 | PAYNE - PY3PNA048090NB | 196 | 6.1 | Yes | Yes | 22.9 | 22.3 | 0.6 | AF4FCE445D034092BD0D5351562D49CC |  | R22 | Non-TXV |  | 3.112% | 0.96888 | 5.981% | [5 empty] | Non-TXV | 3.112%
Bakersfield | CA | 93311-2834 |  | 2014-09-26 | 2014-09-26 13:00 | 2014-09-26 13:22 | UNITARY PRODUCTS GROUP - H2RC036S06G | 83 | 0 | Yes | Yes | 19.7 | 20.3 | -0.6 | 4E7AF3A921E24E90BC61A53EB8B6FEF3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2834 |  | 2014-09-26 | 2014-09-26 12:49 | 2014-09-26 12:49 | UNITARY PRODUCTS GROUP - H2RC030506G | 88 | 0 | Yes | Yes | 19.5 | 22 | -2.5 | 72718F2D3BCA491FACA038B61BB95C55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6322 |  | 2014-06-13 | 2014-06-13 11:05 | 2014-06-13 17:52 | GOODMAN - | 89 | 4.8 | Yes | Yes | 15.3 | 15.7 | -0.4 | BD4EFD3B2F474FDD9324BE8DDEC281D0 |  | R22 | Non-TXV |  | 5.393% | 0.94607 | 10.36% | [5 empty] | Non-TXV | 5.393%
San Jose | CA | 95118-3021 |  | 2014-06-12 | 2014-06-12 09:22 | 2014-06-12 09:40 | BRYANT - 561CJ036 | 72 | -4.2 | Yes | Yes | 22.3 | 21.3 | 1 | 7AB2F6EB4B4140729F47C4A633639CD9 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Gilroy | CA | 95020-7473 |  | 2014-05-22 | 2014-05-22 09:53 | 2014-05-22 09:53 | BRYANT - 561CJ0602000 | 157 | -24.4 | Yes | Yes | 11.7 | 18.8 | -7.1 | 332255A9009D4C93928383FEDE2B07DB | Remove refrigerant: 24.4 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -15.54% | 1.1554 | 4.352% |  |  |  |  | TXV |  |  | -15.54%
San Jose | CA | 95131-3519 |  | 2014-05-27 | 2014-05-27 11:45 | 2014-05-27 11:45 | RUUD - UAKA-037JAZ | 79 | 0 | Yes | Yes | 18.7 | 19.1 | -0.3 | 78A0FF32A4FC4BE3BA72C1949F27D3DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4616 |  | 2014-10-02 | 2014-10-02 11:15 | 2014-10-02 11:15 | RHEEM - RAMA036JAZ | 96 | 0 | Yes | Yes | 19.1 | 18.6 | 0.5 | 911C426D1E6745F291144A2A15EEE759 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1257 |  | 2014-07-22 | 2014-07-22 14:44 | 2014-07-22 15:21 | PAYNE - 561CJ042 | 80 | 2.8 | Yes | Yes | 22.8 | 19.7 | 3.2 | D6A276049629415F874A653AE0689FE6 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Woodland | CA | 95695-6648 |  | 2014-06-04 | 2014-06-04 15:28 | 2014-06-04 16:35 | GOODMAN - PGBO30075-1REUA | 55 | 3.1 | Yes | Yes | 14.5 | 16.9 | -2.4 | 07E672A2505D4995BE1BA46A87E81C62 |  | R22 | Non-TXV |  | 5.636% | 0.94364 | 10.83% | [5 empty] | Non-TXV | 5.636%
San Jose | CA | 95123-4344 |  | 2014-06-02 | 2014-06-02 11:02 | 2014-06-02 12:10 | GOODMAN - GSC130481AF | 152 | -14.3 | Yes | Yes | 23 | 18.8 | 4.2 | FAE23DC405DE4379AB0AA418D43FAFD4 |  | R22 | Non-TXV |  | -9.408% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.408%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 15:50 | 2014-09-13 15:50 | OTHER - DRHS0241BD | 103 | 0 | Yes | Yes | 20.3 | 22 | -1.7 | CBF8813DA30E4890B4F3302F4119DDDE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-0000 |  | 2014-07-19 | 2014-07-19 17:19 | 2014-07-19 17:21 | YORK - H2D042S06B | 141 | 11.1 | Yes | Yes | 23.8 | 21 | 2.8 | 6A8A8F2600C1482CAE5E6AF8C64DD253 |  | R22 | TXV |  | 7.872% | 0.92128 | 15.13% | [5 empty] | TXV | 7.872%
Bakersfield | CA | 93307-4284 |  | 2014-06-20 | 2014-06-20 14:14 | 2014-06-20 14:14 | ICP - PGME60G100E | 228 | 0 | Yes | Yes | 23.5 | 22 | 1.5 | EE2FA50D207D47BD82FF9514EC777072 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4828 |  | 2014-09-18 | 2014-09-18 15:42 | 2014-09-18 16:05 | RUUD - UNK | 85 | 10.8 | Yes | Yes | 22.8 | 20.4 | 2.4 | C8F8A3F6449E4FB393C17356117EC29E |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 15:32 | 2014-09-13 15:32 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 21.4 | 22 | -0.6 | FD28B657562442D9816986D50576672A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2343 |  | 2014-07-28 | 2014-07-28 14:16 | 2014-07-28 14:20 | ARCOAIRE - PGF330060K01A1-- | 152 | 0 | Yes | Yes | 17.4 | 19.9 | -2.5 | 0956721295564531B7BC3CA947D8C48B |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6581 |  | 2014-06-05 | 2014-06-05 13:41 | 2014-06-05 13:41 | CARRIER - 38CKC042---341 | 80 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | 639F021B54764926B4311EDAAD29ABA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 15:42 | 2014-09-13 15:42 | ICP - WCH3182GKA1 | 83 | 0 | Yes | Yes | 21.2 | 21.5 | -0.3 | 7E56A6211CE2487A9F5A58B52290D2CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-3107 |  | 2014-09-18 | 2014-09-18 11:13 | 2014-09-18 11:32 | TRANE - TTR036D100AD | 79 | 3.1 | Yes | Yes | 19.1 | 19.9 | -0.8 | 109F453CD2794090A21544CAE90A1426 |  | R22 | Non-TXV |  | 3.924% | 0.96076 | 7.541% | [5 empty] | Non-TXV | 3.924%
San Jose | CA | 95116-2057 |  | 2014-06-18 | 2014-06-18 09:41 | 2014-06-18 09:41 | YORK - AC030M1021CA | 57 | 0 | Yes | Yes | 23.4 | 19.9 | 3.5 | 0466285885E545CAA671FC5ABC0F55CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2629 |  | 2014-06-23 | 2014-06-23 11:39 | 2014-06-23 12:11 | - CJ30-1FB | 110 | 10.7 | Yes | Yes | 13.7 | 16.4 | -2.7 | 455ADD282FFF48F4BB5C11A819BC26AA |  | R22 | Non-TXV |  | 9.727% | 0.90273 | 18.69% | [5 empty] | Non-TXV | 9.727%
Pleasanton | CA | 94588-4337 |  | 2014-06-25 | 2014-06-25 13:36 | 2014-06-25 13:57 | CARRIER - 38TXA042330 | 140 | 10.7 | Yes | Yes | 23 | 19.7 | 3.3 | 43577777AA474AD0827CBABB2A0C1EC5 |  | R410A | TXV |  | 7.643% | 0.92357 | 14.69% | [5 empty] | TXV | 7.643%
Mc Farland | CA | 93250-1803 |  | 2014-09-02 | 2014-09-02 14:45 | 2014-09-02 18:36 | GOODMAN - GPG12420701 | 105 | 11.8 | Yes | Yes | 23.4 | 20.4 | 3 | E1006984D6F04371BF1DE36AEA0A1A5C |  | R22 | Non-TXV |  | 11.24% | 0.88762 | 21.6% | [5 empty] | Non-TXV | 11.24%
Milpitas | CA | 95035-2449 |  | 2014-06-18 | 2014-06-18 13:28 | 2014-06-18 13:44 | AMANA - RCB36B2D | 85 | -5 | Yes | Yes | 21.9 | 20.3 | 1.6 | 463A127A4745440DB86D5440DBC80E68 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Vallejo | CA | 94590-3552 |  | 2014-05-16 | 2014-05-16 14:08 | 2014-05-16 14:27 | GE - | 85 | 3.1 | Yes | Yes | 15.4 | 17.4 | -2 | AC546735766845ABB6386AFD11CA7DFC |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
San Jose | CA | 95120-1528 |  | 2014-06-02 | 2014-06-02 13:05 | 2014-06-02 13:46 | FRIGIDKING - CM4845T | 122 | -10 | Yes | Yes | 20.1 | 18.8 | 1.3 | 8838C63DE4604D458675D1D0382D26F2 |  | R22 | Non-TXV |  | -8.197% | 1.082 | 2.295% |  |  |  |  | Non-TXV |  |  | -8.197%
W Sacramento | CA | 95691-5172 |  | 2014-06-26 | 2014-06-26 09:40 | 2014-06-26 10:04 | GOODMAN - CK49-18 | 91 | 4.5 | Yes | Yes | 15.6 | 16.6 | -1 | FD05567F65FE4A52AE4795402613CB9E |  | R22 | Non-TXV |  | 4.945% | 0.95055 | 9.503% | [5 empty] | Non-TXV | 4.945%
Benicia | CA | 94510-3615 |  | 2014-09-17 | 2014-09-17 09:08 | 2014-09-22 08:46 | GE - | 85 | 13 | Yes | Yes | 16.1 | 17.2 | -1.1 | 109E22C24B544DACBCEDE9143CBDB81D |  | R22 | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
Milpitas | CA | 95035-4462 |  | 2014-06-18 | 2014-06-18 13:51 | 2014-06-18 14:10 | CARRIER - 38CKC363300 | 84 | 3.9 | Yes | Yes | 22.6 | 20.9 | 1.7 | 14289170F75F487390E084994524AEAD |  | R22 | Non-TXV |  | 4.643% | 0.95357 | 8.923% | [5 empty] | Non-TXV | 4.643%
Lamont | CA | 93241-2051 |  | 2014-11-01 | 2014-11-01 09:28 | 2014-11-01 09:44 | OTHER - UNK | 85 | 8 | Yes | Yes | 18 | 20.9 | -2.9 | 2E85D8A0DD324E0F8AF10E0E7EC7F03B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Bakersfield | CA | 93306-1418 |  | 2014-05-27 | 2014-05-27 16:11 | 2014-05-27 16:11 | ICP - PGAD47D1K8 | 212 | 0 | Yes | Yes | 20.2 | 21 | -0.8 | 4717F8EC90F04DC88CDD8D43E628DAAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4931 |  | 2014-06-03 | 2014-06-03 18:45 | 2014-06-03 18:45 | OTHER - H1RC036S06D | 98 | 0 | Yes | Yes | 21.1 | 20.2 | 1 | 0D47846817814E9D81677B6FCF48AE8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7102 |  | 2014-06-05 | 2014-06-05 12:40 | 2014-06-05 18:09 | TRANE - BTD730A100A0 | 74 | 10 | Yes | Yes | 16 | 18.8 | -2.8 | C7258A6409B04982B5E5F8755E48CCCB |  | R22 | Non-TXV |  | 13.51% | 0.86486 | 25.97% | [5 empty] | Non-TXV | 13.51%
Mc Farland | CA | 93250-0000 |  | 2014-10-27 | 2014-10-27 16:48 | 2014-10-27 16:48 | RHEEM - UNK | 116 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F738BCFDE50E42528F2E8E8351F253B8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-1227 |  | 2014-10-30 | 2014-10-30 16:56 | 2014-10-30 17:12 | RHEEM - RR71-6X367WP1 | 118 | 8.7 | Yes | Yes | 21.1 | 20.4 | 0.7 | ABAE19589180420BA0F4D3BAA9DD5AEF |  | R22 | Non-TXV |  | 7.373% | 0.92627 | 14.17% | [5 empty] | Non-TXV | 7.373%
Winters | CA | 95694-1833 |  | 2014-09-30 | 2014-09-30 11:39 | 2014-09-30 12:03 | PAYNE - PA10JA036-G | 70 | 2.8 | Yes | Yes | 18 | 20.4 | -2.4 | AC961C604337485786FDBB482A9028AC |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93311-2834 |  | 2014-10-02 | 2014-10-02 10:12 | 2014-10-02 10:35 | YORK - H2RC036S06G | 83 | 6.9 | Yes | Yes | 20.7 | 21.8 | -1.1 | 07D00A780C534137A32C7DECE072B06F |  | R22 | Non-TXV |  | 8.313% | 0.91687 | 15.98% | [5 empty] | Non-TXV | 8.313%
Bakersfield | CA | 93311-2834 |  | 2014-10-02 | 2014-10-02 10:54 | 2014-10-02 10:54 | YORK - H2RC030S06G | 88 | 0 | Yes | Yes | 21.1 | 20.7 | 0.4 | A831AA556CE54203867C89D75B3921C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6821 |  | 2014-05-28 | 2014-05-28 12:03 | 2014-05-28 12:03 | RUUD - | 85 | 0 | Yes | Yes | 17.5 | 17.7 | -0.2 | 8140CD890ED84501829908858B5B523C |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5119 |  | 2014-07-29 | 2014-07-29 08:43 | 2014-07-29 09:01 | RHEEM - RRNA-BO48JK08X | 153 | 4.9 | Yes | Yes | 17.8 | 20.4 | -2.6 | 8D1CE678F6A94D64973EC33BE535D6E3 |  | R22 | Non-TXV |  | 3.203% | 0.96797 | 6.155% | [5 empty] | Non-TXV | 3.203%
Woodland | CA | 95695-2530 |  | 2014-08-07 | 2014-08-07 12:31 | 2014-08-07 12:56 | BRYANT - 5030060AAHD83ANW | 68 | 4.2 | Yes | Yes | 17.9 | 19.7 | -1.8 | 5E83E851176047FEA063E2CB0213B178 |  | R22 | Non-TXV |  | 6.176% | 0.93824 | 11.87% | [5 empty] | Non-TXV | 6.176%
Woodland | CA | 95776-6758 |  | 2014-08-06 | 2014-08-06 14:25 | 2014-08-06 14:55 | GOODMAN - CM36-1EB | 82 | 6.1 | Yes | Yes | 22.2 | 20.2 | 2.1 | 2DA73680901941FA87410C93100964C4 |  | R22 | Non-TXV |  | 7.439% | 0.92561 | 14.3% | [5 empty] | Non-TXV | 7.439%
Fairfield | CA | 94533-3111 |  | 2014-10-09 | 2014-10-09 09:19 | 2014-10-10 08:35 | YORK - | 85 | 4.8 | Yes | Yes | 16.4 | 16.5 | -0.1 | 66C96164B50045C0856E7C39107EE811 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Bakersfield | CA | 93306-5477 |  | 2014-05-30 | 2014-05-30 13:49 | 2014-05-30 13:49 | GOODMAN - GPG1342070M41DA | 99 | 0 | Yes | Yes | 27.9 | 22.1 | 5.8 | DD005F6D3E6342ACA47E7E943F46058B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3041 |  | 2014-09-10 | 2014-09-10 11:12 | 2014-09-10 11:12 | HEIL - PGC024K060A | 58 | 0 | Yes | Yes | 19.5 | 21.3 | -1.8 | 8D341209D96F4B8FA05B7322F3301B13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-9538 |  | 2014-10-27 | 2014-10-27 09:50 | 2014-10-27 09:50 | DAY & NIGHT - PGF336060K01 | 146 | 0 | Yes | Yes | 25.3 | 20.4 | 4.9 | 2FA252F00B144E43B938C03F1F6513CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1220 |  | 2014-06-02 | 2014-06-02 13:51 | 2014-06-02 14:21 | CARRIER - 38TH042310 | 112 | -7.9 | Yes | Yes | 21.4 | 19.9 | 1.5 | EFAE6603F8C648229F48862D4A882963 |  | R22 | Non-TXV |  | -7.054% | 1.0705 | 1.975% |  |  |  |  | Non-TXV |  |  | -7.054%
Bakersfield | CA | 93306-1504 |  | 2014-05-27 | 2014-05-27 14:11 | 2014-05-27 14:11 | AMANA - RCE36A2A | 90 | 0 | Yes | Yes | 19.7 | 22.6 | -2.9 | 401C8BD0098E494D84695DA6CB97C524 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3708 |  | 2014-06-02 | 2014-06-02 14:32 | 2014-06-02 14:32 | RHEEM - RAKA048JAZ | 103 | 0 | Yes | Yes | 21.6 | 19.9 | 1.7 | E8949AA9A4D448FF8A646D41A1B127CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2217 |  | 2014-06-24 | 2014-06-24 11:43 | 2014-06-24 11:43 | OTHER - UKN | 90 | 0 | Yes | Yes | 19.9 | 22.9 | -3 | 73EC1D0B7150488BB13FB90BE63364AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-4445 |  | 2014-06-12 | 2014-06-12 13:15 | 2014-06-12 13:45 | TRANE - 4TTM3030TA1000 | 66 | 9.5 | Yes | Yes | 21.4 | 19.3 | 2.1 | 58DDD60B312046BBA44CA7F6871A0C34 |  | R22 | Non-TXV |  | 14.39% | 0.85606 | 27.66% | [5 empty] | Non-TXV | 14.39%
Dixon | CA | 95620-2106 |  | 2014-07-22 | 2014-07-22 12:53 | 2014-07-22 13:43 | PAYNE - PA18NR036-J | 83 | 5 | Yes | Yes | 19.1 | 19.8 | -0.7 | 6DAD5A0EBD424A688DAB0F12277FF275 |  | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Suisun City | CA | 94585-2140 |  | 2014-06-12 | 2014-06-12 13:01 | 2014-06-12 17:40 | OTHER - | 59 | -6.2 | Yes | Yes | 17.5 | 19.9 | -2.4 | ED60265C4EF2432B803E226EDB1FCDC3 |  | R22 | Non-TXV |  | -10.51% | 1.1051 | 2.943% |  |  |  |  | Non-TXV |  |  | -10.51%
Vacaville | CA | 95687-6222 |  | 2014-06-04 | 2014-06-04 11:48 | 2014-06-04 18:23 | BDP - 5859300757ASR | 50 | 5.2 | Yes | Yes | 15.7 | 18.1 | -2.4 | 086B15A904BC489EADF0047D301D2FF8 |  | R22 | Non-TXV |  | 10.4% | 0.896 | 19.99% | [5 empty] | Non-TXV | 10.4%
Vacaville | CA | 95687-6534 |  | 2014-06-20 | 2014-06-20 09:10 | 2014-06-20 10:38 | AMANA - RCF36U01D | 112 | 5.4 | Yes | Yes | 16.4 | 19.3 | -2.9 | AC1890838A274D2DA3CEC81C07863CC5 |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Fairfield | CA | 94534-3970 |  | 2014-06-05 | 2014-06-05 15:47 | 2014-06-05 16:28 | BRYANT - CK36-1T | 76 | 7.6 | Yes | Yes | 16.8 | 19.5 | -2.7 | EAF3E30D3ADB438BBC137BED07331197 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fairfield | CA | 94534-1830 |  | 2014-07-30 | 2014-07-30 11:09 | 2014-07-30 21:17 | PAYNE - PA13NR036-E | 85 | 2.6 | Yes | Yes | 14.5 | 17.3 | -2.8 | 7DF5C1038C0D46F7AC1E95BA5AB5C521 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fairfield | CA | 94533-4237 |  | 2014-06-09 | 2014-06-09 10:23 | 2014-06-09 15:08 | GE - | 85 | -6 | Yes | Yes | 21.4 | 16.7 | 4.8 | 2D52CB5BB9444C698D81E28029E9ECBA |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Suisun City | CA | 94585-2229 |  | 2014-05-30 | 2014-05-30 12:22 | 2014-05-30 13:57 | DAY & NIGHT - | 85 | -8 | Yes | Yes | 21.1 | 16.9 | 4.2 | CF846D07DFE24844A6B64F631795F8C2 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93313-4527 |  | 2014-06-03 | 2014-06-03 18:03 | 2014-06-03 18:03 | GOODMAN - CLJ361A | 109 | 0 | Yes | Yes | 19.2 | 21.5 | -2.3 | DD409A565A9B4C97A406514D6B1350E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4385 |  | 2014-06-03 | 2014-06-03 10:01 | 2014-06-03 10:01 | HEIL - CA5530VKA1 | 77 | 0 | Yes | Yes | 25.2 | 20.1 | 5.1 | CF7E7C65F7AC4BB286AA11D067B11F00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7738 |  | 2014-06-25 | 2014-06-25 16:48 | 2014-06-25 16:48 | UNITARY PRODUCTS GROUP - H2RD036S06B | 96 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | BE2335C68559470AAED23C484F63168F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7646 |  | 2014-06-17 | 2014-06-17 19:52 | 2014-06-17 19:52 | OTHER - UKN | 85 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | 62531EB34E5D495D84F1E9F3F4CF334A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hayward | CA | 94544-6591 |  | 2014-06-24 | 2014-06-24 11:44 | 2014-06-24 12:03 | CARRIER - 38VE0043 | 133 | 31.8 | Yes | Yes | 20.6 | 19.9 | 0.7 | 19E1A9CA4C82463DA6FBE44FFC8056CF |  | R22 | Non-TXV |  | 23.91% | 0.7609 | 45.95% | [5 empty] | Non-TXV | 23.91%
Suisun City | CA | 94585-2914 |  | 2014-06-12 | 2014-06-12 14:02 | 2014-06-12 16:22 | AIRE-FLO - 38CKC036340 | 72 | 5.2 | Yes | Yes | 15.8 | 18.8 | -3 | 9FB97602729B4DB1A4741F99EDF29C31 |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Bakersfield | CA | 93301-1127 |  | 2014-10-21 | 2014-10-21 18:14 | 2014-10-21 18:14 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.4 | 22.5 | -1.1 | CF62941A280F461E83626743B8476BB0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-0000 |  | 2014-07-21 | 2014-07-21 14:44 | 2014-07-21 14:44 | CARRIER - | 108 | 0 | Yes | Yes | 9.2 | 12.1 | -2.9 | BD6DF046BDD344659B02493B12270FBC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1515 |  | 2014-08-21 | 2014-08-21 12:00 | 2014-08-21 12:20 | GUARDIAN - GCGD36S41S3A | 73 | 3.7 | Yes | Yes | 19.8 | 19.7 | 0.1 | 760307B8853D424090605E5F048ACC4F |  | R22 | Non-TXV |  | 5.068% | 0.94932 | 9.741% | [5 empty] | Non-TXV | 5.068%
W Sacramento | CA | 95691-5897 |  | 2014-07-17 | 2014-07-17 10:03 | 2014-07-17 10:03 | PAYNE - | 89 | 5.7 | Yes | Yes | 16.2 | 17.6 | -1.4 | 286CDA15A6AF4008B2AF0F55CA82C776 | Add refrigerant: 5.7 oz | R22 | Non-TXV |  | 6.404% | 0.93596 | 12.31% | [5 empty] | Non-TXV | 6.404%
Bakersfield | CA | 93313-4516 |  | 2014-08-29 | 2014-08-29 10:32 | 2014-08-29 10:32 | YORK - H2DH036S068 | 124 | 0 | Yes | Yes | 23 | 19.9 | 3.1 | 87EA944E06ED4AEDBF74CC444D5F289F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2622 |  | 2014-07-30 | 2014-07-30 13:18 | 2014-07-30 18:36 | TRANE - 4TTX403031000AA | 79 | 7.9 | Yes | Yes | 18.5 | 20.7 | -2.2 | B3F27C018D3346D1993BF78D39847EB2 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93306-4527 |  | 2014-06-30 | 2014-06-30 09:33 | 2014-06-30 09:33 | BRYANT - 583ANW060090NAAG | 129 | 0 | Yes | Yes | 28.2 | 22.3 | 6 | AE6206CE045E4F4A9A60878DB62E40E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4234 |  | 2014-07-07 | 2014-07-07 12:47 | 2014-07-07 19:28 | GOODMAN - CJ36-1GB | 106 | 3.2 | Yes | Yes | 17.9 | 18.3 | -0.4 | 736E1F1CB9964BF69A9F8B01E185F4BB |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
W Sacramento | CA | 95691-5867 |  | 2014-06-26 | 2014-06-26 10:26 | 2014-06-26 10:46 | GOODMAN - CKT26-1AB | 104 | 7.2 | Yes | Yes | 19.1 | 18.8 | 0.3 | 2AE819FFE78E41F6BC66E238A3221E87 |  | R22 | Non-TXV |  | 6.923% | 0.93077 | 13.3% | [5 empty] | Non-TXV | 6.923%
Dixon | CA | 95620-9313 |  | 2014-06-23 | 2014-06-23 13:15 | 2014-06-23 13:46 | RUUD - MFD | 61 | 4.4 | Yes | Yes | 16.2 | 18.2 | -2 | 0C84BA58E1924BA1A31223B309D33467 |  | R22 | Non-TXV |  | 7.213% | 0.92787 | 13.86% | [5 empty] | Non-TXV | 7.213%
Napa | CA | 94558-2851 |  | 2014-09-18 | 2014-09-18 10:41 | 2014-09-18 10:59 | AIRE-FLO - 113ANA042-B | 83 | 3.9 | Yes | Yes | 21 | 20.4 | 0.6 | 239211D395DA478FAC7DFF0A53CC1DA9 |  | R22 | TXV |  | 4.699% | 0.95301 | 9.03% | [5 empty] | TXV | 4.699%
Mc Farland | CA | 93250-1082 |  | 2014-11-18 | 2014-11-18 11:11 | 2014-11-18 11:11 | GOODMAN - GPG13360451AB | 112 | 0 | Yes | Yes | 29.3 | 19.1 | 10.2 | 5AEBE188FDA849D68B5135A01E98366C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Winters | CA | 95694-1647 |  | 2014-07-07 | 2014-07-07 08:40 | 2014-07-07 19:29 | TRANE - TTB036C100A1 | 97 | 3 | Yes | Yes | 15 | 17.7 | -2.7 | 81450FA59C95480FA14AB77ACB29CA5C |  | R22 | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Suisun City | CA | 94585-3712 |  | 2014-06-13 | 2014-06-13 13:17 | 2014-06-13 13:34 | RUUD - UALB-036JAZ5351 | 74 | 5.7 | Yes | Yes | 18 | 20.2 | -2.2 | CBCB9D186E4A4B94B926C5B445CE29F7 |  | R22 | Non-TXV |  | 7.703% | 0.92297 | 14.8% | [5 empty] | Non-TXV | 7.703%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 14:38 | 2014-09-13 14:38 | RHEEM - RPKB024JAZ | 73 | 0 | Yes | Yes | 19.9 | 22.4 | -2.5 | 2781AFC84F6D4E2B9780B5F09394F5E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1156 |  | 2014-10-21 | 2014-10-21 15:19 | 2014-10-21 15:19 | GOODMAN - GPG13240451BA | 77 | 0 | Yes | Yes | 22.8 | 21.3 | 1.5 | 867342231DD44227AD72F7609E53D2B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 14:16 | 2014-09-13 14:16 | GOODMAN - GSH130241CB | 122 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | 53EE7BCAA62A4F3E80919A1B1AC63727 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1347 |  | 2014-10-28 | 2014-10-28 13:41 | 2014-10-28 13:41 | GOODMAN - GPG1330045M41AC | 80 | 0 | Yes | Yes | 20.6 | 19.1 | 1.5 | 63B417CF0C084DB09A3C6144629243B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5823 |  | 2014-07-01 | 2014-07-01 13:32 | 2014-07-01 21:51 | YORK - H4DE030S06A | 82 | -4.8 | Yes | Yes | 15 | 17.9 | -2.9 | 45CEF29CCC454206AA2681E8E7089E99 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Bakersfield | CA | 93305-4773 |  | 2014-08-13 | 2014-08-13 12:03 | 2014-08-13 12:03 | RHEEM - UKN | 72 | 0 | Yes | Yes | 18.9 | 20.8 | -1.9 | 85420CA168F8412188CFBDA34E2B3093 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4709 |  | 2014-06-24 | 2014-06-24 13:13 | 2014-06-24 13:13 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 26.1 | 21.3 | 4.8 | AE74F9DDC7A343979603047332162090 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5238 |  | 2014-07-21 | 2014-07-21 10:06 | 2014-07-21 12:25 | BRYANT - 2406E17810 | 81 | 3.1 | Yes | Yes | 12.7 | 14.7 | -2 | C13054FA2E054D4A91224C5E79D32762 |  | R22 | Non-TXV |  | 3.827% | 0.96173 | 7.355% | [5 empty] | Non-TXV | 3.827%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 15:10 | 2014-09-13 15:10 | OTHER - WCH3242GKA1 | 70 | 0 | Yes | Yes | 21.6 | 22.1 | -0.5 | C65A9100EFCB4BE89E649C90B131CE45 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2550 |  | 2014-07-09 | 2014-07-09 09:47 | 2014-07-09 09:47 | CARRIER - 48SX-030060331AA | 72 | 0 | Yes | Yes | 25.1 | 21.5 | 3.6 | 328850DE53A24014852E9DF09533E308 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1671 |  | 2014-08-29 | 2014-08-29 18:31 | 2014-08-29 19:38 | WEATHER KING - 13AJA30A01 | 98 | -20.4 | Yes | Yes | 14.8 | 17.8 | -3 | 3232DF3C49D349999C1F01D556556836 |  | R22 | TXV |  | -20.82% | 1.2082 | 5.83% |  |  |  |  | TXV |  |  | -20.82%
Vallejo | CA | 94590-4729 |  | 2014-08-01 | 2014-08-01 10:13 | 2014-08-01 15:08 | CARRIER - 11RA024S06D | 59 | 4.6 | Yes | Yes | 14.8 | 16.5 | -1.7 | 52807D87F437464EB7229639F39638DB |  | R22 | Non-TXV |  | 7.797% | 0.92203 | 14.98% | [5 empty] | Non-TXV | 7.797%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 14:31 | 2014-09-13 14:49 | GOODMAN - GSH130181BB | 127 | 14.2 | Yes | Yes | 23.9 | 21.9 | 2 | E45F44D742294519A46DFF6494F74487 |  | R22 | Non-TXV |  | 11.18% | 0.88819 | 21.49% | [5 empty] | Non-TXV | 11.18%
Los Gatos | CA | 95032-5646 |  | 2014-09-30 | 2014-09-30 08:23 | 2014-09-30 08:30 | DAY & NIGHT - 561AJ048-F | 155 | -5.7 | Yes | Yes | 20.1 | 18.2 | 1.9 | FEA48C7390894696A8DDFFD27E9FF547 |  | R22 | Non-TXV |  | -3.677% | 1.0368 | 1.03% |  |  |  |  | Non-TXV |  |  | -3.677%
San Jose | CA | 95127-2343 |  | 2014-06-02 | 2014-06-02 15:39 | 2014-06-02 15:39 | RUUD - UAKA048JAZ | 103 | 0 | Yes | Yes | 28.7 | 19.9 | 8.8 | 1776FCC3810848E3B3EABE264F645E51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 15:19 | 2014-09-13 15:19 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 21 | 20.9 | 0.1 | 44AFA2AB673F4E459ADD2E23F4A0A0DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 14:08 | 2014-09-13 14:25 | GOODMAN - GSH130181CB | 127 | 14.1 | Yes | Yes | 23.8 | 22.7 | 1.1 | 7844FD284C1B4FE98933FDEB9B73A657 |  | R22 | Non-TXV |  | 11.1% | 0.88898 | 21.34% | [5 empty] | Non-TXV | 11.1%
Morgan Hill | CA | 95037-2522 |  | 2014-07-31 | 2014-07-31 12:09 | 2014-07-31 12:40 | CARRIER - 38EZG060310 | 156 | 23.3 | Yes | Yes | 23.1 | 22.1 | 1 | 722F0BD86B1441BB9EC6FAC6728D4141 |  | R410A | TXV |  | 14.94% | 0.85064 | 28.7% | [5 empty] | TXV | 14.94%
San Jose | CA | 95118-5226 |  | 2014-06-12 | 2014-06-12 09:55 | 2014-06-12 10:15 | GIBSON - JS5BD18KA | 78 | 13.3 | Yes | Yes | 19.6 | 22.4 | -2.8 | B41D229D9AD54AE5900B261A043060C0 |  | R22 | Non-TXV |  | 17.05% | 0.82949 | 32.77% | [5 empty] | Non-TXV | 17.05%
San Jose | CA | 95118-5226 |  | 2014-06-12 | 2014-06-12 10:04 | 2014-06-12 10:34 | GIBSON - JS5BD18KA | 78 | -4.6 | Yes | Yes | 23.3 | 19.9 | 3.4 | B71AA609513249889EA0D1FD61F060BE |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Bakersfield | CA | 93313-5419 |  | 2014-06-03 | 2014-06-03 11:53 | 2014-06-03 11:53 | PAYNE - PY1PNB042060AAAA | 100 | 0 | Yes | Yes | 24.8 | 19.9 | 4.9 | A045E6C0FC804A17989F5349E185F0BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2724 |  | 2014-11-05 | 2014-11-05 17:51 | 2014-11-05 18:14 | OTHER - UNK | 85 | 7 | Yes | Yes | 21 | 20.4 | 0.6 | C1B260F67E134668B9530A5B8A57DDCF |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Bakersfield | CA | 93308-4084 |  | 2014-09-13 | 2014-09-13 14:28 | 2014-09-13 14:45 | BDP - 661CJ024B | 72 | 8.2 | Yes | Yes | 22.9 | 20.8 | 2.1 | 1A54C1939F054A54A19EBDC2A6527437 |  | R22 | Non-TXV |  | 11.39% | 0.88611 | 21.89% | [5 empty] | Non-TXV | 11.39%
San Jose | CA | 95128-4050 |  | 2014-06-13 | 2014-06-13 08:54 | 2014-06-13 09:14 | CARRIER - 38CKC048360 | 100 | -6.4 | Yes | Yes | 25.8 | 21.5 | 4.4 | A4BFC4DE8CE14761A94EF55EAC8C1C64 |  | R22 | TXV |  | -6.4% | 1.064 | 1.792% |  |  |  |  | TXV |  |  | -6.4%
Mc Farland | CA | 93250-1657 |  | 2014-09-03 | 2014-09-03 16:10 | 2014-09-03 16:10 | GOODMAN - UNK | 113 | 0 | Yes | Yes | 24.6 | 20.2 | 4.4 | 5153D5DCEA1A415B9628349A4AC5869B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 15:28 | 2014-09-13 15:28 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 20.5 | 22.6 | -2.1 | 7A9BFE60ADC342D983B65D6B02533B8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3304 |  | 2014-06-26 | 2014-06-26 11:40 | 2014-06-26 12:12 | CARRIER - 48DL002 | 51 | 2.7 | Yes | Yes | 14.9 | 16.8 | -1.9 | 0C1A4F0233EC4B479CD296A7E19E6475 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Bakersfield | CA | 93301-1121 |  | 2014-10-21 | 2014-10-21 16:33 | 2014-10-21 16:33 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.7 | 21.4 | -0.7 | 5EF8984E78A4469DA1BE99ADF706572E |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1353 |  | 2014-06-23 | 2014-06-23 12:57 | 2014-06-23 13:17 | PAYNE - PA10JA036 | 74 | 4 | Yes | Yes | 20.7 | 19.7 | 1.1 | 55D9769BA14E464CA2642E7B6957D33C |  | R22 | Non-TXV |  | 5.405% | 0.94595 | 10.39% | [5 empty] | Non-TXV | 5.405%
Wasco | CA | 93280-1156 |  | 2014-07-19 | 2014-07-19 17:48 | 2014-07-19 17:51 | GOODMAN - GPG13360451AB | 112 | 3.7 | Yes | Yes | 27.4 | 21.5 | 5.9 | E3C37BFF5E2144AF9422881DFD92BC48 |  | R22 | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
San Jose | CA | 95127-1023 |  | 2014-06-03 | 2014-06-03 08:35 | 2014-06-03 08:55 | GOODMAN - CL0481A | 225 | -23.8 | Yes | Yes | 21.9 | 18.2 | 3.7 | F6C4BD78F57747938EBDBCC14F48C6F8 |  | R22 | Non-TXV |  | -10.58% | 1.1058 | 2.962% |  |  |  |  | Non-TXV |  |  | -10.58%
Bakersfield | CA | 93308-4346 |  | 2014-06-05 | 2014-06-05 19:06 | 2014-06-05 19:06 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22.8 | 22.6 | 0.2 | 2624F3A9A4194D44B69CEC5D2FA3F7C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3081 |  | 2014-06-19 | 2014-06-19 08:50 | 2014-06-19 09:23 | BRYANT - 561CJ0363000 | 74 | -7 | Yes | Yes | 26.5 | 21.2 | 5.3 | C654949577694B129CFB5607277BECD8 |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Shafter | CA | 93263-3528 |  | 2014-11-18 | 2014-11-18 13:27 | 2014-11-18 13:27 | GOODMAN - UNK | 50 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | BC57142FB0FE4433AE9F1FFC812200A1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3528 |  | 2014-11-18 | 2014-11-18 14:00 | 2014-11-18 14:00 | GOODMAN - GPG10300701A | 55 | 0 | Yes | Yes | 20.6 | 20.1 | 0.5 | BBA4081BD5CB418DB37792C173C7D750 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2414 |  | 2014-10-29 | 2014-10-29 12:10 | 2014-10-29 12:10 | ARCOAIRE - PGF330060K01A1 | 152 | 0 | Yes | Yes | 15.4 | 16.5 | -1.1 | 645B13CFC22D4A9FB23603A13A6DFC97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6762 |  | 2014-05-28 | 2014-05-28 13:32 | 2014-05-28 13:32 | YORK - | 85 | 0 | Yes | Yes | 15.7 | 18.1 | -2.4 | 07DCBAA092C142E8A361EA05AB785039 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2106 |  | 2014-06-23 | 2014-06-23 14:12 | 2014-06-23 16:56 | ARCOAIRE - UAKA-037JAZ | 78 | 3.3 | Yes | Yes | 15 | 17.5 | -2.5 | 124A0B8861BB4F129E4FF33ADC317821 |  | R22 | Non-TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | Non-TXV | 4.231%
Bakersfield | CA | 93301-1123 |  | 2014-10-21 | 2014-10-21 17:39 | 2014-10-21 17:39 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | 6A1D9B65766C498AA015230FEE38872A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1557 |  | 2014-08-28 | 2014-08-28 18:50 | 2014-08-28 18:50 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | D7EF8BA940F54823A9D4A6BD3D7E981D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4325 |  | 2014-06-05 | 2014-06-05 16:35 | 2014-06-05 16:35 | UNITARY PRODUCTS GROUP - DAYA-F024N045C | 54 | 0 | Yes | Yes | 18.2 | 19.2 | -1 | 75FA4AE209CF4DC6845286E0366900FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1122 |  | 2014-10-21 | 2014-10-21 16:35 | 2014-10-21 16:35 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.5 | 21.4 | 0.1 | E6AEC77D98274606A2D8A04418174EE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-0000 |  | 2014-07-19 | 2014-07-19 16:41 | 2014-07-19 16:48 | PAYNE - PY13NR060000ACAA | 276 | -53.9 | Yes | Yes | 18.5 | 19.9 | -1.4 | 008DDBA72C40402B8259FB7C5273D214 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | -19.53% | 1.1953 | 5.469% |  |  |  |  | TXV |  |  | -19.53%
W Sacramento | CA | 95691-5157 |  | 2014-06-26 | 2014-06-26 11:59 | 2014-06-26 12:21 | GOODMAN - CKT36-1AB | 112 | -6.6 | Yes | Yes | 19.2 | 20.4 | -1.2 | 3E29F197E07645639341F63C55CBFFC4 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Bakersfield | CA | 93309-1154 |  | 2014-06-27 | 2014-06-27 09:52 | 2014-06-27 09:52 | BRYANT - 582ANW030040NAAD | 58 | 0 | Yes | Yes | 24.2 | 21.5 | 2.7 | CC7243E0AFA049AFADE8C28D67DCEBDA |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-3117 |  | 2014-06-03 | 2014-06-03 09:04 | 2014-06-03 09:30 | PAYNE - PA10J042 | 83 | -4.9 | Yes | Yes | 21.6 | 19.1 | 2.6 | EA51B8A6EC35431D838FEF29DD594B92 |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Vacaville | CA | 95687-6163 |  | 2014-06-16 | 2014-06-16 13:46 | 2014-06-16 14:13 | GE - | 55 | -5.2 | Yes | Yes | 11.5 | 13.2 | -1.7 | 7175D3A7492942EF9D79C1A593E70329 |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Bakersfield | CA | 93314-9676 |  | 2014-09-03 | 2014-09-03 14:57 | 2014-09-03 14:57 | COLEMAN - 7830-901 | 50 | 0 | Yes | Yes | 24 | 21.5 | 2.5 | DF789A036FFB4AEAAC0A4CEFCB9C6E9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5738 |  | 2014-05-28 | 2014-05-28 09:17 | 2014-05-28 14:40 | GE - 18DNR-108K | 34 | -7 | Yes | Yes | 15.6 | 16.1 | -0.5 | F3C0A5CCD0FE4A2EA24A66C93D094D4E |  | R22 | Non-TXV |  | -20.59% | 1.2059 | 5.766% |  |  |  |  | Non-TXV |  |  | -20.59%
W Sacramento | CA | 95691-5454 |  | 2014-08-06 | 2014-08-06 08:42 | 2014-08-06 09:34 | CARRIER - 2504E32742 | 118 | 6.7 | Yes | Yes | 18.2 | 19.4 | -1.2 | 8F65A43175814944A9AB4BDAE04AD83F |  | R22 | Non-TXV |  | 5.678% | 0.94322 | 10.91% | [5 empty] | Non-TXV | 5.678%
Fairfield | CA | 94533-2522 |  | 2014-06-13 | 2014-06-13 09:16 | 2014-06-13 09:16 | AIRE-FLO - 2TTB0030A1000AA | 64 | 0 | Yes | Yes | 17.9 | 20.1 | -2.2 | 693C9B8D174443EC959DA520DA3E0206 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4131 |  | 2014-06-04 | 2014-06-04 10:11 | 2014-06-04 18:35 | AIRE-FLO - 4A7A4036A1000AB | 91 | 5.8 | Yes | Yes | 16.8 | 19.3 | -2.5 | CB816A5311F3434A9FA096989A6AF928 |  | R410A | Non-TXV |  | 6.374% | 0.93626 | 12.25% | [5 empty] | Non-TXV | 6.374%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 15:56 | 2014-09-13 15:56 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 21.2 | 22.3 | -1.1 | 4C517C7CACE74743ACE0E01C3476DA6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2831 |  | 2014-11-07 | 2014-11-07 13:36 | 2014-11-07 13:55 | OTHER - UNK | 85 | 7.4 | Yes | Yes | 19.5 | 22.3 | -2.8 | 73F0E6C0329040D7A72EC4E2712DC213 |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Suisun City | CA | 94585-6313 |  | 2014-06-17 | 2014-06-17 08:42 | 2014-06-17 15:30 | RUUD - AC1BN036-A | 97 | 5.6 | Yes | Yes | 30.2 | 25.1 | 5.2 | C5DE321E3BE1418FBEC4B645CD502FDE |  | R22 | Non-TXV |  | 5.773% | 0.94227 | 11.09% | [5 empty] | Non-TXV | 5.773%
Fairfield | CA | 94533-6525 |  | 2014-06-06 | 2014-06-06 14:28 | 2014-06-06 14:46 | TRANE - 2TTR1048A1000AA | 109 | 4 | Yes | Yes | 20 | 17.6 | 2.4 | 2339CCC57ECD42D58131229E109F5447 |  | R22 | Non-TXV |  | 3.67% | 0.9633 | 7.052% | [5 empty] | Non-TXV | 3.67%
Bakersfield | CA | 93308-3638 |  | 2014-07-30 | 2014-07-30 11:02 | 2014-07-30 11:02 | UNITARY PRODUCTS GROUP - D1NP048N09006A | 132 | 0 | Yes | Yes | 17.1 | 18.8 | -1.7 | ECD28748297D4D12955939CACAC6D335 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4559 |  | 2014-05-28 | 2014-05-28 15:36 | 2014-05-28 15:36 | ARCOAIRE - PGF030K060A | 52 | 0 | Yes | Yes | 21.1 | 20.9 | 0.2 | C7BEE9AB712E4C1D923F2C7492F3E4AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-0525 |  | 2014-06-18 | 2014-06-18 08:54 | 2014-06-18 10:12 | GOODMAN - CRT24-IA | 112 | 0 | Yes | Yes | 21.7 | 17.9 | 3.8 | 0D49D2AE51CD4068A9A0F744B37ACCF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1911 |  | 2014-11-18 | 2014-11-18 15:20 | 2014-11-18 15:20 | GOODMAN - GPG13360701AB | 112 | 0 | Yes | Yes | 31.7 | 19.7 | 12 | 2D7BC1FBB93443AEBE354E15B26BA1B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6724 |  | 2014-05-29 | 2014-05-29 11:44 | 2014-05-29 12:06 | CARRIER - 38EH024320 | 96 | -7 | Yes | Yes | 20.1 | 17.7 | 2.5 | C973128C769D4A12B1CF0BE18E23B523 |  | R22 | Non-TXV |  | -7.292% | 1.0729 | 2.042% |  |  |  |  | Non-TXV |  |  | -7.292%
San Jose | CA | 95127-5007 |  | 2014-06-12 | 2014-06-12 14:01 | 2014-06-12 14:01 | LENNOX - HS294112P | 80 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | 6C79ED28B7C143DAA62EB52D4789D526 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-5007 |  | 2014-06-12 | 2014-06-12 14:08 | 2014-06-12 15:01 | LENNOX - HS294112P | 80 | 10.7 | Yes | Yes | 19.3 | 21.1 | -1.8 | F7D607E1DE044992A12FD45DB2FDB24D |  | R22 | Non-TXV |  | 13.38% | 0.86625 | 25.7% | [5 empty] | Non-TXV | 13.38%
Winters | CA | 95694-2203 |  | 2014-09-30 | 2014-09-30 10:41 | 2014-09-30 11:24 | CARRIER - 38E024320 | 81 | 6.4 | Yes | Yes | 20.5 | 20.4 | 0.1 | EE24901FEF374D99A55D8E740F0EC77E |  | R22 | Non-TXV |  | 7.901% | 0.92099 | 15.18% | [5 empty] | Non-TXV | 7.901%
Suisun City | CA | 94585-6312 |  | 2014-06-03 | 2014-06-03 10:38 | 2014-06-03 13:58 | CARRIER - 38TD036300 | 182 | -5.7 | Yes | Yes | 18.2 | 17.5 | 0.7 | 5A473BE719FA4EACB3AFCF3680AFB6CA |  | R22 | Non-TXV |  | -3.132% | 1.0313 | 0.8771% |  |  |  |  | Non-TXV |  |  | -3.132%
Suisun City | CA | 94585-2330 |  | 2014-05-30 | 2014-05-30 10:26 | 2014-05-30 13:49 | DAY & NIGHT - | 85 | 4.5 | Yes | Yes | 20.9 | 16.6 | 4.3 | CA946425C83B48C6BCACFFEC09FD3CB8 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Fairfield | CA | 94533-2244 |  | 2014-06-24 | 2014-06-24 08:39 | 2014-06-24 08:39 | AMERICAN STANDARD - 4A7B3036D1000AA | 106 | 0 | Yes | Yes | 11.2 | 13 | -1.8 | 44E590042DDA484989CCBE1DE8ADB270 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2405 |  | 2014-07-31 | 2014-07-31 19:57 | 2014-07-31 19:57 | ALLEGIANCE - | 53 | 0 | Yes | Yes | 21.2 | 21.4 | -0.2 | FC4877859E8743A98C04343ABC74E4ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1928 |  | 2014-07-27 | 2014-07-27 19:55 | 2014-07-27 19:58 | GOODMAN - GPC13240451CB | 74 | -5.2 | Yes | Yes | 23.4 | 19.1 | 4.3 | 57EED3A6042F420496143E3648BDC96F |  | R22 | Non-TXV |  | -7.027% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.027%
Vacaville | CA | 95687-5433 |  | 2014-06-04 | 2014-06-04 10:50 | 2014-06-04 18:44 | PAYNE - PA1JA03D-C | 77 | -4.5 | Yes | Yes | 18.4 | 21.3 | -2.9 | EFB703F004634B25A2DAA6BAC5D26EBB |  | R22 | Non-TXV |  | -5.844% | 1.0584 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.844%
Arvin | CA | 93203-2214 |  | 2014-11-05 | 2014-11-05 18:35 | 2014-11-05 18:51 | RHEEM - RRGG-07N43JKR | 85 | 5.4 | Yes | Yes | 12.5 | 14.5 | -2 | 03BC1E818B8D4838A7EC1D67D0E1B433 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Bakersfield | CA | 93311-1244 |  | 2014-09-24 | 2014-09-24 09:44 | 2014-09-24 09:44 | ICP - GPCM030K060D | 53 | 0 | Yes | Yes | 19.5 | 22.4 | -2.9 | C97EC34E9A4D41A99AF2AEE553B5BC67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4019 |  | 2014-06-03 | 2014-06-03 15:06 | 2014-06-03 15:06 | OTHER - UKN | 90 | 0 | Yes | Yes | 25.8 | 23.3 | 2.5 | E95A02B45E304E70879C4B543D5425A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4282 |  | 2014-06-18 | 2014-06-18 12:01 | 2014-06-18 12:01 | ICP - GPCM042K080F | 87 | 0 | Yes | Yes | 24.3 | 22.6 | 1.7 | DF6C5F5BE2CA4FD39F11A5FD11EC4E06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-4766 |  | 2014-06-04 | 2014-06-04 12:40 | 2014-06-04 12:57 | INTERTHERM - N/A | 80 | 3.3 | Yes | Yes | 21.6 | 19.9 | 1.7 | 27C60BFB67CE43E19E916A7ECDBE5FDD |  | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Shafter | CA | 93263-1858 |  | 2014-10-05 | 2014-10-05 19:26 | 2014-10-05 19:28 | ARCOAIRE - PGA047D1K5 | 215 | 8.9 | Yes | Yes | 22.3 | 20.4 | 1.9 | 4B60FE854BCD4D66A07901E550BB5A22 |  | R22 | Non-TXV |  | 4.14% | 0.9586 | 7.955% | [5 empty] | Non-TXV | 4.14%
San Jose | CA | 95132-3013 |  | 2014-06-05 | 2014-06-05 10:02 | 2014-06-05 10:38 | DAY & NIGHT - N2A336AKB300 | 88 | 10.3 | Yes | Yes | 16 | 18.2 | -2.2 | E9974AD6EE5D45BBB969E6532161FEDC |  | R22 | Non-TXV |  | 11.7% | 0.88295 | 22.49% | [5 empty] | Non-TXV | 11.7%
Antioch | CA | 94509-4355 |  | 2014-11-11 | 2014-11-11 12:20 | 2014-11-11 12:20 | YORK - DGUC-F036N100A | 96 | 0 | Yes | Yes | 19.7 | 18.7 | 1 | EDC3E568F83D4220B523522C5D08309A | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-3369 |  | 2014-06-05 | 2014-06-05 09:00 | 2014-06-05 09:47 | CARRIER - 38BBAC048B370 | 140 | -8.2 | Yes | Yes | 23.6 | 18.8 | 4.8 | CD87F2A6E80243C081138BAAF9DE4601 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Bakersfield | CA | 93305-4963 |  | 2014-10-06 | 2014-10-06 10:19 | 2014-10-06 10:19 | OTHER - UNK | 90 | 0 | Yes | Yes | 19.3 | 22 | -2.7 | 2E4D09E58F344C828BC3F131F0E220D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6327 |  | 2014-05-30 | 2014-05-30 11:01 | 2014-05-30 13:53 | GOODMAN - CLJ60 1C | 85 | -6 | Yes | Yes | 14.5 | 16.6 | -2.1 | C46A4768D35C44CBAF92E9002F9B92B9 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
San Jose | CA | 95121-2509 |  | 2014-06-03 | 2014-06-03 12:43 | 2014-06-03 13:56 | PAYNE - GCDB48SA13 | 73 | 2.7 | Yes | Yes | 17.4 | 18.6 | -1.2 | 529172553FB841CFA9D0D7BDAA1935E6 |  | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Fairfield | CA | 94533-2559 |  | 2014-06-09 | 2014-06-09 10:50 | 2014-06-09 15:03 | HEIL - NACO36AKA1 | 89 | -6.4 | Yes | Yes | 26.3 | 21.7 | 4.6 | 7E4EDDEFC6F545228FF6DFA98BC63662 |  | R22 | Non-TXV |  | -7.191% | 1.0719 | 2.014% |  |  |  |  | Non-TXV |  |  | -7.191%
Arvin | CA | 93203-1614 |  | 2014-10-30 | 2014-10-30 04:43 | 2014-10-30 05:07 | WESTINGHOUSE - UNK | 85 | 4.2 | Yes | Yes | 16.3 | 18.6 | -2.3 | 9C63C43A2A6742B4918ECA56E77EAD09 |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Dixon | CA | 95620-2705 |  | 2014-07-30 | 2014-07-30 16:07 | 2014-07-30 18:34 | AIRE-FLO - PA13N042-C | 178 | 5.9 | Yes | Yes | 18.5 | 20.4 | -1.9 | 0191160FAFCC4FBFAA397C01A38B6441 |  | R22 | Non-TXV |  | 3.315% | 0.96685 | 6.37% | [5 empty] | Non-TXV | 3.315%
Fairfield | CA | 94534-6644 |  | 2014-06-17 | 2014-06-17 12:25 | 2014-06-17 15:26 | AMERICAN STANDARD - | 98 | 5.4 | Yes | Yes | 19 | 20.3 | -1.3 | C3F421887EA14C51985167A43C2BEDB5 |  | R22 | Non-TXV |  | 5.51% | 0.9449 | 10.59% | [5 empty] | Non-TXV | 5.51%
Fairfield | CA | 94533-5464 |  | 2014-06-06 | 2014-06-06 08:37 | 2014-06-06 14:13 | PAYNE - PA12NA036-A | 100 | 3.7 | Yes | Yes | 20.2 | 17.5 | 2.7 | CB3CFD65A0374CD6AACCD1A4F67D26B4 |  | R22 | Non-TXV |  | 3.7% | 0.963 | 7.111% | [5 empty] | Non-TXV | 3.7%
Suisun City | CA | 94585-3767 |  | 2014-06-13 | 2014-06-13 10:00 | 2014-06-13 10:00 | TRANE - 2TTR3036A1000AA | 101 | 0 | Yes | Yes | 12.1 | 14.3 | -2.2 | 02C7A8C5A92D499AB5D84ED85B47331A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4249 |  | 2014-06-06 | 2014-06-06 09:13 | 2014-06-06 09:13 | ICP - PGME24G0408 | 73 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 55610095EAA14F26AAB11FBD8E27539E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2737 |  | 2014-07-03 | 2014-07-03 09:35 | 2014-07-03 09:35 | CARRIER - 48SS-036080311 | 67 | 0 | Yes | Yes | 22.2 | 17.5 | 4.7 | 8C90A8ACE7E64F2EA561A53D82AC2FC2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dublin | CA | 94568-3480 |  | 2014-06-26 | 2014-06-26 10:40 | 2014-06-26 11:03 | PAYNE - 55BJB024 | 70 | 2.7 | Yes | Yes | 23.9 | 20.2 | 3.8 | 7C4CF14636AD49A39992016B47042D36 |  | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
Dublin | CA | 94568-4573 |  | 2014-06-25 | 2014-06-25 12:27 | 2014-06-25 12:45 | CARRIER - 38CKC030340 | 68 | 10.4 | Yes | Yes | 18.5 | 20.8 | -2.3 | 87B67805D04C4453906FEE94AF4EF0C4 |  | R22 | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
San Jose | CA | 95127-2389 |  | 2014-06-03 | 2014-06-03 13:21 | 2014-06-03 13:21 | PAYNE - 525A2403 | 75 | 0 | Yes | Yes | 18.9 | 19.1 | -0.2 | 37850C16650D4757A5FEAB5CD85E76E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1839 |  | 2014-07-22 | 2014-07-22 11:06 | 2014-07-22 11:06 | UNITARY PRODUCTS GROUP - D1NP060N9006A | 140 | 0 | Yes | Yes | 21.6 | 20.1 | 1.5 | 56E51049564A4AC2BF62EB3C29115C6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1805 |  | 2014-06-06 | 2014-06-06 08:35 | 2014-06-06 09:01 | CARRIER - 561AJX00360000AAA | 76 | -5.4 | Yes | Yes | 22.4 | 20.4 | 2 | C179D2EB86B94F7090C5A79791BEBFF1 |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
San Jose | CA | 95127-1106 |  | 2014-06-02 | 2014-06-02 10:24 | 2014-06-02 10:58 | CARRIER - 38CKC0360 | 74 | 9.8 | Yes | Yes | 19.4 | 19.9 | -0.5 | D474989368FB484AAE78723C3B1CFC29 |  | R22 | TXV |  | 13.24% | 0.86757 | 25.45% | [5 empty] | TXV | 13.24%
Mc Farland | CA | 93250-1671 |  | 2014-09-03 | 2014-09-03 15:40 | 2014-09-03 15:40 | WEATHER KING - 13AJA30A01 | 98 | 0 | Yes | Yes | 18.8 | 20.9 | -2.1 | 57AC4CE85EF24C2390DACC4AE6C5FDE5 |  | R22 | TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-2601 |  | 2014-06-04 | 2014-06-04 13:22 | 2014-06-04 14:15 | CARRIER - 24ABB330W310 | 74 | -4.4 | Yes | Yes | 22.5 | 21 | 1.5 | 139B10B9347749669FE428DCF5AB8632 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Bakersfield | CA | 93306-2731 |  | 2014-06-30 | 2014-06-30 10:52 | 2014-06-30 10:52 | ICP - PGAD47D1K6 | 85 | 0 | Yes | Yes | 20.8 | 20.4 | 0.4 | 7C07DA2DD23B49B1AAC2FEF95692AC7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7006 |  | 2014-09-14 | 2014-09-14 14:55 | 2014-09-14 14:55 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 19.3 | 21 | -1.7 | E3B9F98A60F54F699416BDB47278175F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1243 |  | 2014-06-19 | 2014-06-19 11:29 | 2014-06-19 11:29 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 21.8 | 22.6 | -0.8 | FE0E949A35AA467495303D71E835D6E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3925 |  | 2014-08-22 | 2014-08-22 09:27 | 2014-08-22 09:27 | RHEEM - UKN | 90 | 0 | Yes | Yes | 19.6 | 22.3 | -2.7 | 01F1CB19946D41E79A8590E258BB0F97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3420 |  | 2014-06-12 | 2014-06-12 13:22 | 2014-06-12 17:32 | AIRE-FLO - | 95 | -5.6 | Yes | Yes | 17.5 | 19.7 | -2.2 | 39280AA2547C47F4B736D1F130AA9A98 |  | R22 | Non-TXV |  | -5.895% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Fairfield | CA | 94534-4330 |  | 2014-06-06 | 2014-06-06 12:30 | 2014-06-06 14:20 | PAYNE - 562AJ030-A | 96 | 3.6 | Yes | Yes | 18.3 | 17.1 | 1.2 | 2D5FD5AE003A4034B6964F559382B46E |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Suisun City | CA | 94585-2002 |  | 2014-06-17 | 2014-06-17 15:35 | 2014-06-17 15:59 | CARRIER - | 76 | 4.2 | Yes | Yes | 17 | 19 | -2 | B84832B4451C4E4D8BD705CD55992B36 |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Wasco | CA | 93280-2314 |  | 2014-07-28 | 2014-07-28 14:02 | 2014-07-28 14:04 | GOODMAN - GPG13240701BA | 77 | -7.2 | Yes | Yes | 20 | 19 | 1 | 54F9C3B81B3F4066A92035A0D7CA31F5 |  | R22 | Non-TXV |  | -9.351% | 1.0935 | 2.619% |  |  |  |  | Non-TXV |  |  | -9.351%
Bakersfield | CA | 93304-1171 |  | 2014-06-17 | 2014-06-17 15:42 | 2014-06-17 15:42 | ICP - PGAD47D1K6 | 215 | 0 | Yes | Yes | 28 | 22.4 | 5.6 | 5F46FEB1A38549DAA1E18DACAB6B34B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3358 |  | 2014-08-19 | 2014-08-19 13:14 | 2014-08-19 20:09 | CARRIER - 38HDL036301 | 66 | 5.4 | Yes | Yes | 16.8 | 13.8 | 3 | 02462685BDD84490BE5E04EEAB3A736F |  | R22 | Non-TXV |  | 8.182% | 0.91818 | 15.72% | [5 empty] | Non-TXV | 8.182%
Wasco | CA | 93280-2235 |  | 2014-07-22 | 2014-07-22 17:41 | 2014-07-22 17:45 | PAYNE - PY3PNA030090NB-- | 96 | 16 | Yes | Yes | 21.7 | 20.1 | 1.6 | ACB6AF09B5524B9FB1CC346A62815059 |  | R22 | Non-TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | Non-TXV | 16.67%
Bakersfield | CA | 93308-4306 |  | 2014-06-06 | 2014-06-06 11:09 | 2014-06-06 11:09 | BRYANT - 582ANW030040AAAD | 60 | 0 | Yes | Yes | 23.3 | 19.8 | 3.5 | 26B8DE7C91784584B49AA0CF1EBE647E |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-3803 |  | 2014-06-03 | 2014-06-03 14:41 | 2014-06-03 15:12 | LENNOX - HS294112P | 80 | -7.5 | Yes | Yes | 24.9 | 20.7 | 4.2 | 2D766041A34E4EC6A6358F7DE5AE9DA1 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
San Jose | CA | 95127-4301 |  | 2014-06-06 | 2014-06-06 09:05 | 2014-06-06 09:05 | PAYNE - PA13NA060 | 136 | 0 | Yes | Yes | 29.5 | 20.4 | 9.1 | FFEDEEB10EC74E618FAEFF7A7DB590A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2570 |  | 2014-06-26 | 2014-06-26 18:14 | 2014-06-26 18:31 | AIRE-FLO - H1RA048SD6G | 119 | 4.9 | Yes | Yes | 14.2 | 17 | -2.8 | 7ADF1917735141BCAA44877FEC34B295 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Wasco | CA | 93280-2236 |  | 2014-07-28 | 2014-07-28 14:41 | 2014-07-28 14:44 | YORK - DCYZ-F035N070A | 64 | -6 | Yes | Yes | 26 | 21 | 5 | 9B57027F8B99417FB5F63DBEC7CDC20D |  | R410A | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Lamont | CA | 93241-2036 |  | 2014-11-01 | 2014-11-01 09:48 | 2014-11-01 10:05 | GOODMAN - GPG133645M41AB | 85 | 12.2 | Yes | Yes | 23.3 | 24.2 | -0.9 | 5AE4BD1713B94E0EB362A37F24BDA0E3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | Non-TXV | 14.35%
Wasco | CA | 93280-3310 |  | 2014-11-05 | 2014-11-05 12:28 | 2014-11-05 12:28 | OTHER - GR8GD042K072C | 71 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | 6189861C17214C74A06B35A4F79CF2D4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2783 |  | 2014-09-06 | 2014-09-06 19:17 | 2014-09-06 19:20 | GOODMAN - PGB030050-1 | 56 | 2.7 | Yes | Yes | 25.2 | 20.7 | 4.5 | 3D7B6E9599FD4C80ACD5A3D48E97CBE1 |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Bakersfield | CA | 93304-1557 |  | 2014-08-28 | 2014-08-28 19:02 | 2014-08-28 19:02 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21 | 22 | -1 | AC321B47FD16478A9BCDF5AA8F427AB9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1558 |  | 2014-08-28 | 2014-08-28 19:40 | 2014-08-28 19:40 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.7 | 21.8 | -2.1 | 54766EB4443445C0931A6C28CA9BBB84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1563 |  | 2014-08-26 | 2014-08-26 18:50 | 2014-08-26 18:50 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | F4878AB2A24B444B8A85867794973AE6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1563 |  | 2014-08-26 | 2014-08-26 19:26 | 2014-08-26 19:26 | GOODMAN - GSH13018CB | 127 | 0 | Yes | Yes | 20.5 | 22.1 | -1.6 | 01E1994B77CA4CCAACFDCDC62B94C419 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1568 |  | 2014-09-03 | 2014-09-03 18:26 | 2014-09-03 18:26 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.1 | 22 | -0.9 | 00E9F753530C44688CA8F3C28696C2A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1566 |  | 2014-08-26 | 2014-08-26 19:13 | 2014-08-26 19:13 | CARRIER - 38YC018341 | 66 | 0 | Yes | Yes | 18.1 | 20.4 | -2.3 | AC813CD07DEC4B53B2206DD8CD5BEC64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1578 |  | 2014-08-26 | 2014-08-26 18:33 | 2014-08-26 18:33 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.3 | 21.3 | -2 | E868842696394B578DD3AF7D363F8C96 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1562 |  | 2014-09-03 | 2014-09-03 17:44 | 2014-09-03 17:44 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.2 | 21.2 | -2 | D856A27F5CC149B3948E9F7D50EF0F9B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3206 |  | 2014-06-11 | 2014-06-11 10:53 | 2014-06-11 10:53 | AMERICAN STANDARD - 2YCX3030A1075AA | 89 | 0 | Yes | Yes | 22.9 | 17.9 | 5 | EF6CB7436B564C58B7123DF5BE767E78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1562 |  | 2014-08-26 | 2014-08-26 18:22 | 2014-08-26 18:22 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | 05A7B091C8F448599815D5ABB8207C88 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1566 |  | 2014-08-26 | 2014-08-26 18:42 | 2014-08-26 18:42 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | 7C63310DEC9640049702C604751FDF94 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1562 |  | 2014-09-03 | 2014-09-03 17:36 | 2014-09-03 17:36 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.9 | 22.6 | -1.7 | EEA34DDC5B9B436C920CB9691C7C5A7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1557 |  | 2014-08-28 | 2014-08-28 19:14 | 2014-08-28 19:14 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.8 | 20.9 | 0.9 | 0C5828ACE47344BE871201C96191EC7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1577 |  | 2014-08-26 | 2014-08-26 19:29 | 2014-08-26 19:29 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.6 | 20.4 | -0.8 | 5988FEBCDD56471A84ED76804BFA40A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1563 |  | 2014-08-26 | 2014-08-26 18:29 | 2014-08-26 18:29 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.2 | 20.7 | -1.5 | 632641207BC743F68E9A10DAB45F5636 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1574 |  | 2014-09-03 | 2014-09-03 17:47 | 2014-09-03 17:47 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21 | 22.1 | -1.1 | 42C92DB8FE3A43B08AB7AE33869C6AEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1574 |  | 2014-09-03 | 2014-09-03 18:03 | 2014-09-03 18:03 | CARRIER - 38YCC024341 | 70 | 0 | Yes | Yes | 20.4 | 21 | -0.6 | 5C01BCF89E864308A1419A6BE1726B5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1575 |  | 2014-09-03 | 2014-09-03 18:16 | 2014-09-03 18:16 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.3 | 23.1 | -1.8 | 756CD486CF85424C8DC68A1435F767F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1563 |  | 2014-08-26 | 2014-08-26 19:43 | 2014-08-26 19:43 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.8 | 22.1 | -1.3 | 3E9777CEC3E54892AE669556C3260837 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1575 |  | 2014-08-28 | 2014-08-28 18:43 | 2014-08-28 18:43 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.6 | 22 | -1.4 | 0F7CDB92EDC940C0AA436DE4D39CA640 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1576 |  | 2014-08-28 | 2014-08-28 19:34 | 2014-08-28 19:34 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.6 | 22.3 | -1.7 | DC498190A9144AA58F7D39C793DB859F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1574 |  | 2014-08-26 | 2014-08-26 19:50 | 2014-08-26 19:50 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20 | 22.5 | -2.5 | EE11F86DD1944DB8A89B91905D95B200 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2014-08-26 | 2014-08-26 19:41 | 2014-08-26 19:41 | ICP - WCH3184GKA1 | 64 | 0 | Yes | Yes | 20.3 | 21.5 | -1.2 | 0F21EEFE1F74408F90BAB33DE47805EA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2014-08-26 | 2014-08-26 19:52 | 2014-08-26 19:52 | CARRIER - 38YC018341 | 66 | 0 | Yes | Yes | 21 | 22.8 | -1.8 | 7323E2AF14D443968905E29E5CF5CAC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1560 |  | 2014-08-28 | 2014-08-28 19:50 | 2014-08-28 19:50 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.2 | 22 | -0.8 | FF9055DC05FF474EB5FFFDD23D272C11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2014-08-26 | 2014-08-26 19:23 | 2014-08-26 19:23 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 23.6 | 20.4 | 3.2 | 5FFCEB32F45944579F31AAEA5CE0EBE2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1576 |  | 2014-08-28 | 2014-08-28 19:17 | 2014-08-28 19:17 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.2 | 22.1 | -2.9 | 37943FECCE9F481A82F48B528F87D2CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1568 |  | 2014-08-28 | 2014-08-28 19:58 | 2014-08-28 19:58 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.3 | 22.3 | -2 | 61F3A4F4716745288F40501994246511 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1568 |  | 2014-08-28 | 2014-08-28 19:46 | 2014-08-28 19:46 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.6 | 21.5 | -1.9 | 21445F3C6FCA41E08EC9F3A19AF2C6CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2014-08-26 | 2014-08-26 19:45 | 2014-08-26 19:45 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.1 | 21 | -1.9 | B704C79342334C0D9FA92E6CE2E61BF3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5252 |  | 2014-07-24 | 2014-07-24 10:01 | 2014-07-24 10:01 | ICP - GPCM30K060F | 71 | 0 | Yes | Yes | 22.9 | 19.2 | 3.7 | 7FEDA8AF0DB74EEBB553B69E23D35E13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-2561 |  | 2014-06-09 | 2014-06-09 10:47 | 2014-06-09 11:04 | NORDYNE - GS3BA036KA | 69 | 11.4 | Yes | Yes | 20.3 | 21.7 | -1.4 | 5C22FA395414406781D6BD34384EE20C |  | R22 | Non-TXV |  | 16.52% | 0.83478 | 31.75% | [5 empty] | Non-TXV | 16.52%
Pleasanton | CA | 94588-4312 |  | 2014-06-25 | 2014-06-25 13:51 | 2014-06-25 15:07 | BRYANT - 561CJ036F | 74 | 12.7 | Yes | Yes | 18 | 20.7 | -2.7 | F2D7FE094DA94D19BE97FB44F852E968 |  | R22 | Non-TXV |  | 17.16% | 0.82838 | 32.98% | [5 empty] | Non-TXV | 17.16%
Pleasanton | CA | 94588-4312 |  | 2014-06-25 | 2014-06-25 14:00 | 2014-06-25 15:06 | BRYANT - PA10JA03030 | 67 | -3.6 | Yes | Yes | 24.4 | 21 | 3.4 | CC77EC9DE4AA417AB0EDAF11ABFAF18F |  | R22 | TXV |  | -5.373% | 1.0537 | 1.505% |  |  |  |  | TXV |  |  | -5.373%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 15:39 | 2014-09-13 15:39 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 20.7 | 22.1 | -1.4 | DD0F8CC1804446A8AA4AFA16C8B67542 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3227 |  | 2014-07-03 | 2014-07-03 09:03 | 2014-07-03 14:58 | RHEEM - RAKA-030JAZ | 62 | -4.4 | Yes | Yes | 19.3 | 18.3 | 1 | A9580DA4238A4579B9114F124485E40B |  | R22 | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Vacaville | CA | 95688-4621 |  | 2014-06-02 | 2014-06-02 11:09 | 2014-06-02 15:14 | TRANE - YCC036F1M0BF | 83 | -5.8 | Yes | Yes | 20.7 | 17.7 | 3 | C5D7B0583FFA4D67AF2C89AF13AC91D4 |  | R22 | Non-TXV |  | -6.988% | 1.0699 | 1.957% |  |  |  |  | Non-TXV |  |  | -6.988%
Davis | CA | 95616-3946 |  | 2014-10-17 | 2014-10-17 10:30 | 2014-10-17 10:49 | TRANE - 4YCYC4030A1075AB | 97 | 4.4 | Yes | Yes | 17.5 | 20.4 | -2.9 | 4F3AB06C546E4E549A91EBE40991627F |  | R410A | Non-TXV |  | 4.536% | 0.95464 | 8.717% | [5 empty] | Non-TXV | 4.536%
Dixon | CA | 95620-4236 |  | 2014-06-23 | 2014-06-23 14:41 | 2014-06-23 16:25 | ARCOAIRE - CJ30-1FB | 100 | 4.1 | Yes | Yes | 15.1 | 17.7 | -2.6 | 6A289613CA4D4A24B4B711A155C5A1B8 |  | R22 | Non-TXV |  | 4.1% | 0.959 | 7.879% | [5 empty] | Non-TXV | 4.1%
Shafter | CA | 93263-2720 |  | 2014-11-06 | 2014-11-06 13:05 | 2014-11-06 13:05 | RHEEM - UNK | 111 | 0 | Yes | Yes | 16.1 | 19 | -2.9 | A3E051C2D90B4730A38D364574B58172 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2828 |  | 2014-08-10 | 2014-08-10 19:11 | 2014-08-10 19:14 | BRYANT - 588ANW036060ADAF | 67 | 4.6 | Yes | Yes | 25 | 21.8 | 3.2 | 518A27555FE3425E92FAF2E0BF6025F4 |  | R22 | Non-TXV |  | 6.866% | 0.93134 | 13.19% | [5 empty] | Non-TXV | 6.866%
San Jose | CA | 95123-3250 |  | 2014-06-06 | 2014-06-06 09:45 | 2014-06-06 10:06 | AMANA - ARCF36U01D | 112 | 15.8 | Yes | Yes | 16.8 | 19.3 | -2.5 | 390A828AACE746E89BAB078926069663 |  | R22 | Non-TXV |  | 14.11% | 0.85893 | 27.11% | [5 empty] | Non-TXV | 14.11%
Bakersfield | CA | 93311-9773 |  | 2014-06-03 | 2014-06-03 16:23 | 2014-06-03 16:23 | COLEMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 25 | 19.9 | 5.1 | 652EBA1B1F844E0182B6197BE6BBE6D6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-1627 |  | 2014-07-14 | 2014-07-14 12:22 | 2014-07-14 13:37 | PAYNE - PA10JA036000ACAA | 76 | 3.3 | Yes | Yes | 19.6 | 17.1 | 2.5 | 4BA6786FA4F241C7AAF4E80E9DA3D3DB |  | R22 | Non-TXV |  | 4.342% | 0.95658 | 8.345% | [5 empty] | Non-TXV | 4.342%
Shafter | CA | 93263-2440 |  | 2014-08-30 | 2014-08-30 12:42 | 2014-08-30 13:33 | RUUD - RRNAB036JK06X | 81 | 11.8 | Yes | Yes | 27 | 22.5 | 4.5 | 13D92F5C78344A2299453C3C0C352303 |  | R22 | Non-TXV |  | 14.57% | 0.85432 | 28% | [5 empty] | Non-TXV | 14.57%
Shafter | CA | 93263-2442 |  | 2014-11-06 | 2014-11-06 12:07 | 2014-11-06 12:07 | CARRIER - 48GS042060301 | 100 | 0 | Yes | Yes | 22.7 | 20.5 | 2.2 | E614FD79411F4CC2BAE113D0EFCF560C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1805 |  | 2014-07-21 | 2014-07-21 10:57 | 2014-07-21 10:57 | ARCOAIRE - AH036GA1 | 124 | 0 | Yes | Yes | 18.9 | 18 | 0.9 | 642D144FEFEC4A7BB9D2020EDF2888EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4683 |  | 2014-09-26 | 2014-09-26 10:56 | 2014-09-26 11:22 | YORK - DRCSO421BEG | 109 | 8 | Yes | Yes | 20.7 | 23.1 | -2.4 | 8B2FE66D5E014497A094D1662440F1E2 |  | R22 | Non-TXV |  | 7.339% | 0.92661 | 14.1% | [5 empty] | Non-TXV | 7.339%
Hayward | CA | 94544-4413 |  | 2014-06-24 | 2014-06-24 12:26 | 2014-06-24 12:26 | CARRIER - 36100YAC1080 | 63 | 0 | Yes | Yes | 24.5 | 20.3 | 4.2 | F6427609D1F441CEBDF4311D92403F96 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6378 |  | 2014-06-20 | 2014-06-20 10:29 | 2014-06-20 10:29 | RUUD - UKN | 90 | 0 | Yes | Yes | 20.3 | 22.9 | -2.6 | 61BDB62065FC47F082E9C15C4E315F23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4519 |  | 2014-07-17 | 2014-07-17 15:20 | 2014-07-17 20:19 | LENNOX - HPXA15-036-03 | 170 | 5.2 | Yes | Yes | 17.5 | 18.7 | -1.2 | 7044891CA56C4FAD84AECA69DE9B4393 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Wasco | CA | 93280-1639 |  | 2014-07-27 | 2014-07-27 20:43 | 2014-07-27 20:46 | YORK - DBYPF024N045A | 100 | 4.9 | Yes | Yes | 26.3 | 22.8 | 3.5 | 11200BEDB8DC450FADCCF77135FD673A |  | R22 | TXV |  | 4.9% | 0.951 | 9.417% | [5 empty] | TXV | 4.9%
Vallejo | CA | 94589-2039 |  | 2014-08-04 | 2014-08-04 15:18 | 2014-08-04 16:40 | TRANE - 2TTB0036A1000AA | 76 | 4.9 | Yes | Yes | 23.8 | 20.4 | 3.4 | C01709BB88C142C29BD464BFDDD253BD |  | R22 | Non-TXV |  | 6.447% | 0.93553 | 12.39% | [5 empty] | Non-TXV | 6.447%
Gilroy | CA | 95020-3029 |  | 2014-06-19 | 2014-06-19 11:32 | 2014-06-19 11:56 | BRYANT - 561CJ036 | 74 | 2.7 | Yes | Yes | 21.2 | 20.2 | 1.1 | BF8CE1B9E48D455E96B3B716E5AF9E12 |  | R22 | Non-TXV |  | 3.649% | 0.96351 | 7.012% | [5 empty] | Non-TXV | 3.649%
Gilroy | CA | 95020-3029 |  | 2014-06-19 | 2014-06-19 11:38 | 2014-06-19 11:56 | BRYANT - 561CK036000AA | 74 | 3.8 | Yes | Yes | 22.1 | 20.4 | 1.7 | 62F1B103EBCB43CA97BA262481A5FA7C |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Shafter | CA | 93263-2241 |  | 2014-08-24 | 2014-08-24 19:45 | 2014-08-24 19:48 | OTHER - DCVC-F048N075E | 88 | 6.1 | Yes | Yes | 17.7 | 20.4 | -2.7 | AF9717C7FBBF46B982E90E01D24C48E2 |  | R22 | Non-TXV |  | 6.932% | 0.93068 | 13.32% | [5 empty] | Non-TXV | 6.932%
Dixon | CA | 95620-2005 |  | 2014-06-25 | 2014-06-25 11:22 | 2014-06-25 11:46 | CARRIER - | 74 | 4 | Yes | Yes | 14.1 | 15.7 | -1.6 | 07D224E3FDAC4C61ADB33CB2759EE398 |  | R22 | Non-TXV |  | 5.405% | 0.94595 | 10.39% | [5 empty] | Non-TXV | 5.405%
San Jose | CA | 95118-1242 |  | 2014-06-09 | 2014-06-09 08:40 | 2014-06-09 09:04 | BRYANT - 561CJ042 | 84 | -7.9 | Yes | Yes | 21.1 | 19.4 | 1.7 | F8F004FF1617448EBC85D011613BFCAC |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Davis | CA | 95618-1308 |  | 2014-06-18 | 2014-06-18 11:21 | 2014-06-18 13:59 | AMANA - 587BNZ0360B0AAAF | 104 | 0 | Yes | Yes | 20.8 | 18.8 | 2 | BAE9F7B8E2BF47ACBB4E63E8464EFD7D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6629 |  | 2014-07-24 | 2014-07-24 10:26 | 2014-07-24 10:26 | ICP - NACS042A2B1 | 90 | 0 | Yes | Yes | 25.9 | 20.4 | 5.5 | 122E59AD02BE46708575DC566B2C9575 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-6226 |  | 2014-06-19 | 2014-06-19 09:25 | 2014-06-19 09:45 | YORK - TCGF60S41S1A | 89 | -6.3 | Yes | Yes | 17.7 | 20.1 | -2.4 | D6A3DB467E1944EC82AAA2C1F570E545 |  | R410A | Non-TXV |  | -7.079% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.079%
Morgan Hill | CA | 95037-6226 |  | 2014-06-19 | 2014-06-19 09:31 | 2014-06-19 09:49 | YORK - TCGF48S41S1 | 73 | 2.5 | Yes | Yes | 19.4 | 20.2 | -0.8 | 2FF1CF9B078145829F6243C63F752A7D |  | R22 | Non-TXV |  | 3.425% | 0.96575 | 6.581% | [5 empty] | Non-TXV | 3.425%
San Jose | CA | 95128-4011 |  | 2014-07-17 | 2014-07-17 09:25 | 2014-07-17 10:17 | CARRIER - 113ANA036 | 83 | 4.1 | Yes | Yes | 21.2 | 19.3 | 1.9 | 5DD1B70CE7824FD493B49AECA27412FD |  | R22 | Non-TXV |  | 4.94% | 0.9506 | 9.493% | [5 empty] | Non-TXV | 4.94%
Dixon | CA | 95620-4252 |  | 2014-07-30 | 2014-07-30 16:49 | 2014-07-30 18:31 | GOODMAN - CJ36-1GB | 106 | 6.8 | Yes | Yes | 22.4 | 19.3 | 3.1 | 0FD95FCB02044A3E89D1ACABC07C2431 |  | R22 | Non-TXV |  | 6.415% | 0.93585 | 12.33% | [5 empty] | Non-TXV | 6.415%
San Jose | CA | 95127-1434 |  | 2014-06-11 | 2014-06-11 15:11 | 2014-06-11 15:11 | LENNOX - HS29-3112P | 66 | 0 | Yes | Yes | 21.2 | 21.4 | -0.2 | F7CBE7C57D2E4461A2720E7BF8BA0D09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2217 |  | 2014-08-09 | 2014-08-09 17:13 | 2014-08-09 17:17 | GOODMAN - GPG13300451BB | 77 | 2.4 | Yes | Yes | 21.3 | 18.5 | 2.8 | D43AEEC707CC40A7A6B94A14B0A6F30C |  | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Rio Vista | CA | 94571-5133 |  | 2014-09-03 | 2014-09-03 11:16 | 2014-09-03 11:42 | LENNOX - 13ACD-042-230-02 | 111 | 5.7 | Yes | Yes | 19.9 | 20.4 | -0.5 | 3DA5DB0D008A4E3587EAB89FFCD96212 |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Rio Vista | CA | 94571-2176 |  | 2014-08-21 | 2014-08-21 10:59 | 2014-08-21 11:17 | YORK - H2RCO24SO6HG | 71 | 4.6 | Yes | Yes | 20.9 | 20.2 | 0.8 | DC040474939B4283AA8DF5A4B540B81B |  | R22 | Non-TXV |  | 6.479% | 0.93521 | 12.45% | [5 empty] | Non-TXV | 6.479%
Bakersfield | CA | 93313-0000 |  | 2014-06-03 | 2014-06-03 12:01 | 2014-06-03 12:01 | GOODMAN - GSC130481AF | 152 | 0 | Yes | Yes | 22.4 | 22.4 | 0 | 7172D606BF124528B43FF0989908826F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6625 |  | 2014-05-30 | 2014-05-30 10:25 | 2014-05-30 10:25 | ICP - PGF060K100E | 136 | 0 | Yes | Yes | 23.8 | 20.4 | 3.4 | 2F6339478792416D9399A42419B55123 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6625 |  | 2014-05-30 | 2014-05-30 10:08 | 2014-05-30 10:08 | DAY & NIGHT - UKN | 85 | 0 | Yes | Yes | 25.6 | 21.2 | 4.4 | 1F1C11F6EF8A4CC08D39F2D7760B015C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-7402 |  | 2014-11-04 | 2014-11-04 16:59 | 2014-11-04 16:59 | OTHER - UNK | 183 | 0 | Yes | Yes | 20.2 | 18.8 | 1.4 | 431FFEC44C0941B4B7BBB840EFACB5C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-1679 |  | 2014-10-30 | 2014-10-30 16:25 | 2014-10-30 16:43 | GOODMAN - GSX1301BA | 85 | 8.7 | Yes | Yes | 13.9 | 16.5 | -2.6 | 5A123AD2F1BF47A3AA44D3CB82B17A1F |  | R22 | Non-TXV |  | 10.24% | 0.89765 | 19.67% | [5 empty] | Non-TXV | 10.24%
Wasco | CA | 93280-1944 |  | 2014-07-28 | 2014-07-28 13:55 | 2014-07-28 13:58 | DAY & NIGHT - 584BNW030040B | 85 | 4.9 | Yes | Yes | 26.5 | 24.2 | 2.3 | C4375688565C400E830FE0CBCE3A1355 |  | R22 | Non-TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | Non-TXV | 5.765%
Vacaville | CA | 95688-5349 |  | 2014-10-22 | 2014-10-22 14:55 | 2014-10-22 15:15 | BDP - 561AJ024-B | 62 | 16.2 | Yes | Yes | 21.1 | 19.1 | 2 | DED4983FCFA64D8EB238A21D5FA83AF8 |  | R22 | Non-TXV |  | 26.13% | 0.73871 | 50.21% | [5 empty] | Non-TXV | 26.13%
Dixon | CA | 95620-3241 |  | 2014-06-23 | 2014-06-23 09:47 | 2014-06-23 10:55 | HEIL - CA5048UKA1 | 196 | 6.3 | Yes | Yes | 12.5 | 15 | -2.5 | 056BA4A897FA4973A827C78EFC1D46C8 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Morgan Hill | CA | 95037-7233 |  | 2014-08-04 | 2014-08-04 10:21 | 2014-08-04 10:50 | CARRIER - 38HDL060301 | 135 | 32.3 | Yes | Yes | 20.2 | 20.4 | -0.2 | 54C5653CD3F74C0F8399C4F1B08AD8AF |  | R22 | Non-TXV |  | 23.93% | 0.76074 | 45.98% | [5 empty] | Non-TXV | 23.93%
Dixon | CA | 95620-4252 |  | 2014-06-23 | 2014-06-23 12:18 | 2014-06-23 13:48 | CARRIER - | 108 | 4 | Yes | Yes | 17.4 | 19.9 | -2.5 | F881D707631F445DBDCDAE89DDFFB482 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Wasco | CA | 93280-2566 |  | 2014-08-03 | 2014-08-03 19:12 | 2014-08-03 19:13 | HEIL - PGAD36D1K2 | 78 | 5.6 | Yes | Yes | 23.9 | 21 | 2.9 | 1953C68FB29F4FDF91580FC2DBE5BDD7 |  | R22 | Non-TXV |  | 7.179% | 0.92821 | 13.8% | [5 empty] | Non-TXV | 7.179%
Davis | CA | 95618-2542 |  | 2014-06-18 | 2014-06-18 09:39 | 2014-06-18 10:10 | LENNOX - GCS29-036-75-2PA | 58 | -5.5 | Yes | Yes | 21.5 | 17.2 | 4.3 | C94CB62C879249BCB061A187E1C9D037 |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Wasco | CA | 93280-0000 |  | 2014-11-07 | 2014-11-07 18:56 | 2014-11-07 18:56 | GOODMAN - GPG1036070 | 75 | 0 | Yes | Yes | 25.9 | 17.9 | 8 | 907340DEB7CC4B4BA234896463DF6D7D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-4698 |  | 2014-06-19 | 2014-06-19 10:14 | 2014-06-19 10:30 | CARRIER - 24ABA348A310 | 127 | 5.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | 8400EB9C5DBD4D0D8687A75EA433BD9A |  | R22 | Non-TXV |  | 4.646% | 0.95354 | 8.928% | [5 empty] | Non-TXV | 4.646%
W Sacramento | CA | 95605-2115 |  | 2014-06-27 | 2014-06-27 08:12 | 2014-06-27 09:26 | ARCOAIRE - 3C648A | 68 | 6.6 | Yes | Yes | 16.5 | 19.1 | -2.6 | 84F493068D86478CB9F1678B8B026A15 |  | R22 | Non-TXV |  | 9.706% | 0.90294 | 18.65% | [5 empty] | Non-TXV | 9.706%
Fairfield | CA | 94533-1413 |  | 2014-06-06 | 2014-06-06 09:19 | 2014-06-06 09:19 | RHEEM - RAKA-037JAAZ | 79 | 0 | Yes | Yes | 16.6 | 17.1 | -0.5 | CD9B8F9A056B49379AAD0499865B04BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3131 |  | 2014-11-05 | 2014-11-05 15:44 | 2014-11-05 15:44 | GOODMAN - GSC130601B | 175 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 893CD8A8CE904B90889534FFF50DEB43 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2648 |  | 2014-06-24 | 2014-06-24 11:40 | 2014-06-24 11:40 | AMERICAN STANDARD - 2A7A2048A1000AA | 120 | 0 | Yes | Yes | 17.7 | 17.4 | 0.3 | EAAF29851F8D4231911A211FE7E70D20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5812 |  | 2014-06-02 | 2014-06-02 11:31 | 2014-06-02 15:16 | GE - | 85 | -6 | Yes | Yes | 20.2 | 17.2 | 3 | CDE3BD8148064CB1824C0EADCA70C00A |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Vallejo | CA | 94591-4239 |  | 2014-08-06 | 2014-08-06 11:09 | 2014-08-06 22:14 | AMERICAN STANDARD - 7A0048A100A0 | 85 | 4.7 | Yes | Yes | 15.6 | 18.2 | -2.6 | 84C779445E2648858608D84EA0C98895 |  | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Morgan Hill | CA | 95037-4649 |  | 2014-07-31 | 2014-07-31 13:56 | 2014-07-31 14:17 | RUUD - 36 | 75 | 13.3 | Yes | Yes | 22.2 | 18.2 | 4 | 65A3956CBFC74F9EB2516361B3460F42 |  | R22 | Non-TXV |  | 17.73% | 0.82267 | 34.08% | [5 empty] | Non-TXV | 17.73%
Davis | CA | 95616-0419 |  | 2014-10-09 | 2014-10-09 21:54 | 2014-10-09 22:20 | LENNOX - GDS20RV-411-100-1P | 106 | 3.6 | Yes | Yes | 21.3 | 20.4 | 0.9 | 869AE54262D94D8C9B5139D6F4EB82C9 |  | R22 | Non-TXV |  | 3.396% | 0.96604 | 6.527% | [5 empty] | Non-TXV | 3.396%
Bakersfield | CA | 93311-9652 |  | 2014-06-03 | 2014-06-03 15:55 | 2014-06-03 15:55 | UNITARY PRODUCTS GROUP - H2RD048S06B | 85 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | 6FEA625EA7C44D5894C509EAC09D1C0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1854 |  | 2014-06-17 | 2014-06-17 13:16 | 2014-06-17 15:21 | GMC - CL4810B | 130 | 5.5 | Yes | Yes | 19.1 | 20.2 | -1.1 | A3EE7E039B764F24BA38F887A4C80BAD |  | R22 | Non-TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | Non-TXV | 4.231%
Fairfield | CA | 94533-6141 |  | 2014-06-06 | 2014-06-06 10:25 | 2014-06-06 14:21 | GIBSON - | 85 | 4.1 | Yes | Yes | 19.4 | 17 | 2.4 | 7570C5C1B4D04344BB81FCED3C237C75 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Suisun City | CA | 94585-6314 |  | 2014-06-12 | 2014-06-12 11:48 | 2014-06-12 17:35 | OTHER - AC1BNO36-A | 96 | 5.4 | Yes | Yes | 18.1 | 19.3 | -1.2 | 5E0DCD44784C463FA525ECFEC43C156D |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Vacaville | CA | 95687-0000 |  | 2014-10-14 | 2014-10-14 13:33 | 2014-10-14 17:10 | CARRIER - 24ABA342A310 | 85 | 4.4 | Yes | Yes | 22.6 | 20.7 | 1.9 | 00A6345483A2424F961F43D38E2BCBB3 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Bakersfield | CA | 93306-4815 |  | 2014-07-21 | 2014-07-21 10:13 | 2014-07-21 10:13 | UNITARY PRODUCTS GROUP - D1NH042N06506C | 94 | 0 | Yes | Yes | 24.5 | 19.3 | 5.2 | CE8661CA0E3647859665F4B57D54542F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3422 |  | 2014-09-20 | 2014-09-20 17:32 | 2014-09-20 17:33 | GOODMAN - PGB030050-1 | 56 | 2.9 | Yes | Yes | 21.5 | 20.2 | 1.3 | 52D70E330DCF4DBDA1CAADB6F16BF584 |  | R22 | Non-TXV |  | 5.179% | 0.94821 | 9.952% | [5 empty] | Non-TXV | 5.179%
Davis | CA | 95616-3213 |  | 2014-06-23 | 2014-06-23 08:38 | 2014-06-23 09:25 | LENNOX - HS16-461U-P | 106 | -10 | Yes | Yes | 19.5 | 16.1 | 3.4 | 2075E768AF694E79B8D065C015A76F7C |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
W Sacramento | CA | 95691-5455 |  | 2014-07-30 | 2014-07-30 10:06 | 2014-07-30 10:54 | CARRIER - 38CKC042850 | 77 | 4.7 | Yes | Yes | 17.1 | 20.1 | -3 | 43EE43EFD1804F3E907849F3D287A6D1 |  | R22 | Non-TXV |  | 6.104% | 0.93896 | 11.73% | [5 empty] | Non-TXV | 6.104%
Wasco | CA | 93280-2932 |  | 2014-08-16 | 2014-08-16 17:04 | 2014-08-16 17:06 | LENNOX - 13ACD-036-230-02 | 127 | -24.7 | Yes | Yes | 21.2 | 20.4 | 0.8 | A8C7F3DFFA684AB7B6BA95E5651A9F03 |  | R22 | TXV |  | -19.45% | 1.1945 | 5.447% |  |  |  |  | TXV |  |  | -19.45%
Winters | CA | 95694-1835 |  | 2014-07-07 | 2014-07-07 09:40 | 2014-07-07 19:16 | PAYNE - | 85 | -8 | Yes | Yes | 15.5 | 18.3 | -2.8 | 085551B6841B47DF8BC16658199A7454 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Vallejo | CA | 94591-7810 |  | 2014-08-04 | 2014-08-04 12:57 | 2014-08-04 13:26 | DAY & NIGHT - 5658J048 | 125 | 6.3 | Yes | Yes | 20.1 | 19.4 | 0.7 | EAAF2F88BEB048CAA78377031DE605C8 |  | R22 | Non-TXV |  | 5.04% | 0.9496 | 9.686% | [5 empty] | Non-TXV | 5.04%
Napa | CA | 94558-5830 |  | 2014-06-24 | 2014-06-24 14:42 | 2014-06-24 17:36 | TRANE - | 104 | 3.4 | Yes | Yes | 19 | 20.4 | -1.4 | 67B10E5F12BB4AD8856D209788AAB38C |  | R22 | Non-TXV |  | 3.269% | 0.96731 | 6.283% | [5 empty] | Non-TXV | 3.269%
Campbell | CA | 95008-4104 |  | 2014-05-30 | 2014-05-30 10:55 | 2014-05-30 12:48 | COLEMAN - 3836-901 | 74 | 4.6 | Yes | Yes | 20.5 | 19.9 | 0.6 | 58F9751291974BED9A5517E3B060D41E |  | R22 | Non-TXV |  | 6.216% | 0.93784 | 11.95% | [5 empty] | Non-TXV | 6.216%
Fairfield | CA | 94533-5920 |  | 2014-06-06 | 2014-06-06 11:50 | 2014-06-06 14:21 | UNK - UNK | 85 | 2.8 | Yes | Yes | 20.7 | 17.7 | 3 | 8F62ACB46BB54A93B36A6C611F623861 |  |  |  |  | 3.294% | 0.96706 | 6.331% | [5 empty] | 0 | 3.294%
San Jose | CA | 95125-4560 |  | 2014-06-13 | 2014-06-13 13:44 | 2014-06-13 14:09 | TEMPSTAR - CA5536VDK1 | 82 | 3 | Yes | Yes | 21.7 | 20.4 | 1.3 | 9AE7B15472744775B2A00C49F0012DDF |  | R22 | Non-TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | Non-TXV | 3.659%
W Sacramento | CA | 95691-5897 |  | 2014-06-27 | 2014-06-27 08:26 | 2014-06-30 08:23 | YORK - | 85 | -6 | Yes | Yes | 18.1 | 14.7 | 3.4 | 5522ECD7F5AD4169AEB67039D9E8ADBD |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93311-1841 |  | 2014-07-23 | 2014-07-23 12:17 | 2014-07-23 12:17 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | A0119A65C9BB4F168F4B66FE3C14184A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2101 |  | 2014-07-22 | 2014-07-22 17:22 | 2014-07-22 17:26 | YORK - D1NP036N05606A | 92 | 5 | Yes | Yes | 18.9 | 20.4 | -1.5 | DAE701F8D8124C49B746271576A7E153 |  | R22 | TXV |  | 5.435% | 0.94565 | 10.44% | [5 empty] | TXV | 5.435%
San Jose | CA | 95124-2302 |  | 2014-06-20 | 2014-06-20 10:41 | 2014-06-20 12:42 | CARRIER - 38HDC036-321 | 84 | 4.7 | Yes | Yes | 22.4 | 20.3 | 2.1 | 8D6ABEE3145B41B899242720E1ABA3D8 |  | R22 | Non-TXV |  | 5.595% | 0.94405 | 10.75% | [5 empty] | Non-TXV | 5.595%
Vacaville | CA | 95687-7403 |  | 2014-06-20 | 2014-06-20 09:51 | 2014-06-20 09:51 | AIRE-FLO - 5676038RG08 | 56 | 0 | Yes | Yes | 12.7 | 14.1 | -1.4 | 7E649D447607431FBD1F63451DA9FADC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4085 |  | 2014-09-13 | 2014-09-13 15:59 | 2014-09-13 15:59 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | AA3DC00CFBCD4977ABB8A4665C336AF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5839 |  | 2014-05-29 | 2014-05-29 11:28 | 2014-05-29 11:28 | GE - BTX724A100A0 | 90 | 0 | Yes | Yes | 19.4 | 17.9 | 1.5 | 95CC642D662F4738A87FD0A103C967EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5419 |  | 2014-07-22 | 2014-07-22 10:02 | 2014-07-22 10:02 | ICP - PGAD36D1K5 | 150 | 0 | Yes | Yes | 24.7 | 20.6 | 4.1 | 02246732C40B45E0BF4D38DB368C6DFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2690 |  | 2014-06-09 | 2014-06-09 09:16 | 2014-06-09 09:35 | COLEMAN - N/A | 83 | 17.6 | Yes | Yes | 19.9 | 20.2 | -0.3 | 756E460574444F578CDC9C35E4EE69D1 |  | R22 | Non-TXV |  | 21.2% | 0.78795 | 40.75% | [5 empty] | Non-TXV | 21.2%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 15:04 | 2014-09-13 15:04 | BDP - 661CJ018 | 68 | 0 | Yes | Yes | 19.5 | 21.5 | -2 | 978C09E3714741B19FFBB71064A282E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3521 |  | 2014-06-25 | 2014-06-25 10:11 | 2014-06-25 11:47 | CARRIER - 38TKB024300 | 68 | 5.2 | Yes | Yes | 17.3 | 20.1 | -2.8 | FC0B3624E6F94003A7D6FD730D65F20C |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Bakersfield | CA | 93308-4085 |  | 2014-09-13 | 2014-09-13 16:10 | 2014-09-13 16:10 | GOODMAN - GSH13018B1CB | 127 | 0 | Yes | Yes | 21.6 | 22.5 | -0.9 | 22387551196B4DB2A570C5F5CC789403 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9566 |  | 2014-06-03 | 2014-06-03 09:33 | 2014-06-03 09:33 | GOODMAN - GSX130481BB | 104 | 0 | Yes | Yes | 24.4 | 20.7 | 3.8 | 282CFE471FA344BE8C7A14C8D08D4D8C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6736 |  | 2014-05-29 | 2014-05-29 12:39 | 2014-05-29 13:05 | CARRIER - 38TH036300 | 85 | 2.7 | Yes | Yes | 20.9 | 17 | 3.9 | 70F65C8B7A0C4B97AEAA6381AB498625 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Suisun City | CA | 94585-3516 |  | 2014-06-13 | 2014-06-13 11:42 | 2014-06-13 17:54 | PAYNE - 591ANX030000AAAA | 76 | 4.1 | Yes | Yes | 18 | 20.4 | -2.4 | 27205047F72A44E1A1A1100F67006274 |  | R22 | Non-TXV |  | 5.395% | 0.94605 | 10.37% | [5 empty] | Non-TXV | 5.395%
Fairfield | CA | 94534-6632 |  | 2014-06-09 | 2014-06-09 09:30 | 2014-06-09 15:04 | CARRIER - 38CKC042300 | 80 | -5.6 | Yes | Yes | 20.8 | 17.1 | 3.7 | 639B0634696B485180FD563AF6F61AC9 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
San Jose | CA | 95111-1530 |  | 2014-06-13 | 2014-06-13 12:56 | 2014-06-13 12:56 | FRIGIDAIRE - FS3BA048KA | 102 | 0 | Yes | Yes | 23.3 | 20.4 | 2.9 | F82C04EDA7C0470783C2E302DAA5C8AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4820 |  | 2014-06-16 | 2014-06-16 13:28 | 2014-06-16 14:12 | TRANE - TTRO25C100A4`` | 62 | -5.8 | Yes | Yes | 20.6 | 18.2 | 2.4 | 3213932A81CC4AB5BDC2073C1031AD64 |  | R22 | Non-TXV |  | -9.355% | 1.0935 | 2.62% |  |  |  |  | Non-TXV |  |  | -9.355%
Wasco | CA | 93280-3303 |  | 2014-11-04 | 2014-11-04 11:25 | 2014-11-04 11:25 | BRYANT - 588ANW036060ADAF | 67 | 0 | Yes | Yes | 22.2 | 19.5 | 2.7 | 9B3420BEECFD48AEA11269ADCF6EF070 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5353 |  | 2014-06-03 | 2014-06-03 13:45 | 2014-06-03 13:45 | GOODMAN - GSC130421AC | 102 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | D32AFEC8D721444D96D43C047D145824 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-1962 |  | 2014-07-18 | 2014-07-18 12:54 | 2014-07-18 15:52 | GOODMAN - CE30-1HB | 72 | 6.4 | Yes | Yes | 8.8 | 11.2 | -2.4 | A1D6A5B1C78D459B8FBBABF7968241CB |  | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Wasco | CA | 93280-2900 |  | 2014-08-10 | 2014-08-10 19:16 | 2014-08-10 19:31 | GOODMAN - GPG1336070M41AB | 85 | -5 | Yes | Yes | 21.1 | 20.4 | 0.7 | A63736781D804A7C9F20775F4EF74E9A |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93307-4220 |  | 2014-06-18 | 2014-06-18 12:58 | 2014-06-18 12:58 | ICP - D5NZ060N06506NXA | 82 | 0 | Yes | Yes | 25.9 | 21.1 | 4.8 | F8B7F7FBEB2E44C09F9DAE5196D01BC7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2603 |  | 2014-08-27 | 2014-08-27 10:34 | 2014-08-27 10:50 | LENNOX - HS29-03-1P | 68 | 2.5 | Yes | Yes | 16.4 | 16.6 | -0.2 | B022C9038C964D5B9BE6BA8896BB931C |  | R22 | Non-TXV |  | 3.676% | 0.96324 | 7.065% | [5 empty] | Non-TXV | 3.676%
Fairfield | CA | 94533-2213 |  | 2014-06-27 | 2014-06-27 11:50 | 2014-06-27 12:08 | RHEEM - RAMB-030JBZ | 80 | -5.6 | Yes | Yes | 9.5 | 12.3 | -2.8 | E12C579B3DFB411F94B406A53DFE5072 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Bakersfield | CA | 93307-5230 |  | 2014-06-18 | 2014-06-18 15:05 | 2014-06-18 15:05 | RHEEM - UKN | 90 | 0 | Yes | Yes | 25.1 | 21.8 | 3.3 | E03033214A554362B1B369EA09DD7FA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95138-1398 |  | 2014-06-03 | 2014-06-03 14:07 | 2014-06-03 14:32 | CARRIER - 24ABA460300 | 217 | 8.4 | Yes | Yes | 21 | 19.9 | 1.1 | DE921A302A374021B0066E80BE11CE50 |  | R410A | TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | TXV | 3.871%
Davis | CA | 95616-0938 |  | 2014-10-16 | 2014-10-16 12:57 | 2014-10-16 13:19 | TRANE - TTR025C100A1 | 83 | 3.7 | Yes | Yes | 20.3 | 20.4 | -0.1 | 4D2E879AEB2B4A49B37069B4FFF6BE1D |  | R22 | Non-TXV |  | 4.458% | 0.95542 | 8.567% | [5 empty] | Non-TXV | 4.458%
San Jose | CA | 95123-4476 |  | 2014-07-22 | 2014-07-22 13:08 | 2014-07-22 14:12 | RUUD - UAKA060JAZ | 112 | 15.9 | Yes | Yes | 20.8 | 20.4 | 0.4 | C48F6F4D9B964A13A812E4BC0C369C26 |  | R22 | Non-TXV |  | 14.2% | 0.85804 | 27.28% | [5 empty] | Non-TXV | 14.2%
Bakersfield | CA | 93313-5353 |  | 2014-06-03 | 2014-06-03 12:58 | 2014-06-03 12:58 | GOODMAN - GSC130481AF | 102 | 0 | Yes | Yes | 21.2 | 22.4 | -1.2 | E14EF3D12014492180A7AC5A0E6CD0B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-7517 |  | 2014-06-05 | 2014-06-05 11:25 | 2014-06-05 11:50 | BRYANT - 38CKB036330 | 76 | 8.1 | Yes | Yes | 17.1 | 19.3 | -2.2 | 9F585D55BBF14C5C8DB5A0B26620AB5C |  | R22 | Non-TXV |  | 10.66% | 0.89342 | 20.48% | [5 empty] | Non-TXV | 10.66%
Bakersfield | CA | 93307-5111 |  | 2014-06-09 | 2014-06-09 11:26 | 2014-06-09 11:26 | - | 85 | 0 | Yes | Yes | 19.6 | 21.3 | -1.7 | ED0B2722ED744504A3AC43D305D8103C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-4418 |  | 2014-06-23 | 2014-06-23 13:24 | 2014-06-23 13:44 | LENNOX - 14ACX03623011 | 107 | 8.6 | Yes | Yes | 17.7 | 19.6 | -1.9 | D2C4F200FD5E4DC39125EF1E8D47EA1B |  | R22 | Non-TXV |  | 8.037% | 0.91963 | 15.45% | [5 empty] | Non-TXV | 8.037%
Vacaville | CA | 95687-3482 |  | 2014-07-29 | 2014-07-29 09:00 | 2014-07-29 14:53 | CARRIER - 38CKC030340 | 85 | -8 | Yes | Yes | 14.9 | 17.5 | -2.6 | 9358BF3CBA004B598C44B8F09B90FE73 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Vallejo | CA | 94591-6328 |  | 2014-08-04 | 2014-08-04 11:29 | 2014-08-04 12:03 | CARRIER - 38CKC060---301 | 146 | 8.3 | Yes | Yes | 18 | 20.4 | -2.4 | F60D72A0AACE4E77A3E82D8E1FA203E5 |  | R22 | Non-TXV |  | 5.685% | 0.94315 | 10.93% | [5 empty] | Non-TXV | 5.685%
Wasco | CA | 93280-1559 |  | 2014-11-04 | 2014-11-04 10:49 | 2014-11-04 10:49 | GOODMAN - GPG13300451AC | 77 | 0 | Yes | Yes | 18.8 | 19.9 | -1.1 | 8F11B00705A64BF48D63AB97F4D64A81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8398 |  | 2014-08-04 | 2014-08-04 12:20 | 2014-08-04 12:44 | TRANE - 2TTB00481000A | 109 | 6.3 | Yes | Yes | 25.2 | 19.6 | 5.6 | 35F2CEEE827F48019BF0044E456E4C8B |  | R22 | Non-TXV |  | 5.78% | 0.9422 | 11.11% | [5 empty] | Non-TXV | 5.78%
Bakersfield | CA | 93309-6130 |  | 2014-10-15 | 2014-10-15 10:47 | 2014-10-15 10:47 | ICP - GPCM30K060F | 70 | 0 | Yes | Yes | 24.8 | 19.9 | 4.9 | 98E09963EC97483F8777230B6EDCBE8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3002 |  | 2014-10-30 | 2014-10-30 15:01 | 2014-10-30 15:01 | RHEEM - RRNAB030JK06X | 72 | 0 | Yes | Yes | 25.9 | 20.4 | 5.5 | B11A7B4130424D4C80E7DCE8A1BF3F3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1505 |  | 2014-08-17 | 2014-08-17 17:56 | 2014-08-17 18:00 | CARRIER - WPG36049090LKC1 | 160 | -6.4 | Yes | Yes | 24.3 | 22.1 | 2.2 | 25F174ACD78843A1A687775FBFA23031 |  | R410A | TXV |  | -4% | 1.04 | 1.12% |  |  |  |  | TXV |  |  | -4%
Bakersfield | CA | 93309-6246 |  | 2014-08-25 | 2014-08-25 12:25 | 2014-08-25 12:25 | PAYNE - PX3GNA24040NATP | 78 | 0 | Yes | Yes | 17.5 | 19.9 | -2.4 | 175A7630159F42E59D461249709B0334 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6727 |  | 2014-07-24 | 2014-07-24 09:39 | 2014-07-24 10:12 | GIBSON - JS3BD042K | 131 | 4.4 | Yes | Yes | 20 | 19.3 | 0.7 | 330916DCF3E849D0B58FAD42E611E055 |  | R22 | Non-TXV |  | 3.359% | 0.96641 | 6.455% | [5 empty] | Non-TXV | 3.359%
San Jose | CA | 95123-3012 |  | 2014-06-23 | 2014-06-23 14:08 | 2014-06-23 15:29 | PAYNE - PA13NA036 | 74 | 3.2 | Yes | Yes | 20.4 | 19.4 | 1 | 189EF8DFFB0D4B729FC78E7E32D163FB |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
San Jose | CA | 95124-4940 |  | 2014-06-06 | 2014-06-06 12:57 | 2014-06-06 13:18 | FRIGIDAIRE - 363L414 | 68 | 3.5 | Yes | Yes | 18.4 | 19.3 | -0.9 | 22FE230242AE468EB4D72274032F8451 |  | R22 | Non-TXV |  | 5.147% | 0.94853 | 9.892% | [5 empty] | Non-TXV | 5.147%
San Jose | CA | 95132-2432 |  | 2014-07-16 | 2014-07-16 14:12 | 2014-07-16 21:04 | AMANA - RCC36A2B | 114 | 7.5 | Yes | Yes | 19.8 | 20.3 | -0.5 | 86B2EB4B38F5488A912FCB325904FC3A |  | R22 | Non-TXV |  | 6.579% | 0.93421 | 12.64% | [5 empty] | Non-TXV | 6.579%
Concord | CA | 94519-2133 |  | 2014-08-19 | 2014-08-19 20:06 | 2014-08-19 20:06 | OTHER - | 85 | 0 | Yes | Yes | 26.8 | 21.5 | 5.3 | CF1BA7CC14DC40B488693E1D16D7F93C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4450 |  | 2014-06-05 | 2014-06-05 15:36 | 2014-06-05 15:36 | ICP - PGF036K060B | 71 | 0 | Yes | Yes | 18.4 | 19.9 | -1.5 | 8749EBED5E5A442AA74F0FEB3B57C9FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-1625 |  | 2014-06-09 | 2014-06-09 12:48 | 2014-06-09 13:24 | TEMPSTAR - TCA230AKA5 | 80 | 5.6 | Yes | Yes | 20.1 | 19.9 | 0.2 | B3CDE9BD240D4811BDC482886E167FDF |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Vallejo | CA | 94591-4872 |  | 2014-07-31 | 2014-07-31 10:23 | 2014-07-31 10:43 | CARRIER - 38CKB060300 | 153 | 5.6 | Yes | Yes | 20.6 | 19.8 | 0.8 | F1826A69AAEF4AEDBBD0BF9D1D3BECDF |  | R22 | Non-TXV |  | 3.66% | 0.9634 | 7.034% | [5 empty] | Non-TXV | 3.66%
Shafter | CA | 93263-2421 |  | 2014-09-20 | 2014-09-20 17:21 | 2014-09-20 17:23 | OTHER - 704896 | 69 | 2.6 | Yes | Yes | 19.7 | 21.4 | -1.7 | 41228A3609E1497094A347F37851787B |  | R22 | Non-TXV |  | 3.768% | 0.96232 | 7.241% | [5 empty] | Non-TXV | 3.768%
Morgan Hill | CA | 95037-7717 |  | 2014-06-19 | 2014-06-19 10:37 | 2014-06-19 10:37 | BRYANT - 561CJ420000AAA | 80 | 0 | Yes | Yes | 24 | 19.9 | 4.1 | 3D74E124A5B149529FBB5B57720F5A59 |  | R22 | TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2970 |  | 2014-06-04 | 2014-06-04 15:11 | 2014-06-05 08:07 | RHEEM - RAKA037JAZ | 79 | 15.6 | Yes | Yes | 20.4 | 20.4 | 0 | 1440AB8B22EB41DBB70F4917C1AC9D62 |  | R22 | Non-TXV |  | 19.75% | 0.80253 | 37.95% | [5 empty] | Non-TXV | 19.75%
Davis | CA | 95616-0938 |  | 2014-06-11 | 2014-06-11 12:18 | 2014-06-11 13:33 | LENNOX - 13ACD-030-230-11 | 77 | -7.2 | Yes | Yes | 20.6 | 17.4 | 3.2 | E35B84A23A0C4391A2FCABCC9A8D4F08 |  | R22 | Non-TXV |  | -9.351% | 1.0935 | 2.619% |  |  |  |  | Non-TXV |  |  | -9.351%
Bakersfield | CA | 93306-8316 |  | 2014-08-26 | 2014-08-26 12:15 | 2014-08-26 12:15 | BRYANT - 5616J060-A | 158 | 0 | Yes | Yes | 22.7 | 20.8 | 1.9 | 43CD8FA01C36474392C6700829D983F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2745 |  | 2014-09-10 | 2014-09-10 11:17 | 2014-09-10 11:45 | OTHER - 38ETC060300 | 85 | 9.6 | Yes | Yes | 18.2 | 19.7 | -1.5 | 793604702C704422A092CD8EEE7EB1D8 |  | R410A | TXV |  | 11.29% | 0.88706 | 21.7% | [5 empty] | TXV | 11.29%
San Jose | CA | 95111-3264 |  | 2014-06-09 | 2014-06-09 13:35 | 2014-06-09 14:04 | TRANE - TTR18C1000 | 51 | 5.7 | Yes | Yes | 21.1 | 20.4 | 0.7 | 006F78EDFAA44081B1591887F67C87C0 |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Morgan Hill | CA | 95037-4641 |  | 2014-08-08 | 2014-08-08 10:59 | 2014-08-08 11:22 | AMANA - RCC36A2B | 114 | 8.7 | Yes | Yes | 21 | 17.7 | 3.3 | 96B2D16F01874F0FAC3167CA332363F3 |  | R22 | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
San Jose | CA | 95124-2642 |  | 2014-06-09 | 2014-06-09 14:15 | 2014-06-09 14:50 | PAYNE - 561ANX0004800 | 116 | 4 | Yes | Yes | 21.2 | 20.4 | 0.8 | A5807FE66CCF4B219B27B370AD858925 |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Vacaville | CA | 95687-6406 |  | 2014-07-09 | 2014-07-09 11:05 | 2014-07-09 17:13 | RHEEM - | 85 | 3.4 | Yes | Yes | 15.2 | 18 | -2.8 | 0CADC7858EDD4F26A9D30DB30E047488 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 13:56 | 2014-09-13 14:13 | GOODMAN - GSH130181CC | 127 | 20.1 | Yes | Yes | 22.7 | 23.1 | -0.4 | D9E24E4A03754B4784EB7492D023E43F |  | R22 | Non-TXV |  | 15.83% | 0.84173 | 30.42% | [5 empty] | Non-TXV | 15.83%
San Jose | CA | 95116-3453 |  | 2014-06-20 | 2014-06-20 08:38 | 2014-06-20 08:38 | CARRIER - 38CKC036340 | 71 | 0 | Yes | Yes | 20 | 20.6 | -0.6 | B3B97C86A1FF4B0EA2F0F4CC46E9501A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1940 |  | 2014-06-10 | 2014-06-10 14:49 | 2014-06-10 14:49 | NORDYNE - JS4BD036KB | 80 | 0 | Yes | Yes | 23.6 | 21.5 | 2.1 | 0AD4504D8F8B4387A807AF53E4636E9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1351 |  | 2014-06-18 | 2014-06-18 09:23 | 2014-06-18 09:23 | YORK - D3NZ030N03606NXA | 64 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | A1848DF196194E2AABE8965F5A613DFB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1223 |  | 2014-05-27 | 2014-05-27 15:06 | 2014-05-27 15:06 | CARRIER - 38EN048320 | 121 | 0 | Yes | Yes | 25 | 22.6 | 2.4 | 96EB64358AE9434C962A153687326C02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-3229 |  | 2014-06-17 | 2014-06-17 08:36 | 2014-06-17 09:13 | GOODMAN - CK601C | 122 | -7.2 | Yes | Yes | 21.7 | 19.8 | 1.9 | B90BC0E987FE4D02BC903D17B0D744EB |  | R22 | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Bakersfield | CA | 93309-3049 |  | 2014-06-05 | 2014-06-05 10:17 | 2014-06-05 10:17 | ICP - PGD324040K001C1 | 77 | 0 | Yes | Yes | 23 | 21 | 2 | 88DB179289DA4E4295B808860DF91314 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3349 |  | 2014-06-04 | 2014-06-04 14:31 | 2014-06-04 16:45 | PAYNE - PA13N03600GAJAA | 93 | 6.4 | Yes | Yes | 14.6 | 17.4 | -2.8 | BB0E2D8DD7C64E1895E7902B77650116 |  | R22 | Non-TXV |  | 6.882% | 0.93118 | 13.23% | [5 empty] | Non-TXV | 6.882%
Mc Farland | CA | 93250-1083 |  | 2014-09-02 | 2014-09-02 10:54 | 2014-09-02 10:54 | YORK - DNP036N05606NXA | 109 | 0 | Yes | Yes | 21.1 | 18.7 | 2.4 | 8E9A0A4BC13E4E7DBA3B716380E1C717 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4040 |  | 2014-07-21 | 2014-07-21 08:43 | 2014-07-21 09:16 | TRANE - YCX036F1MOAC | 114 | 5.5 | Yes | Yes | 18 | 18.8 | -0.8 | 8F5BDD07477E47A8AA2E991F94B45BAA |  | R22 | Non-TXV |  | 4.825% | 0.95175 | 9.272% | [5 empty] | Non-TXV | 4.825%
Fairfield | CA | 94533-4009 |  | 2014-06-09 | 2014-06-09 08:45 | 2014-06-09 15:04 | PHILCO - RAKA-037JAZ | 79 | -4.5 | Yes | Yes | 20.2 | 18.5 | 1.7 | 6CCF8C9C42214C638117ACA46881A5B7 |  | R22 | Non-TXV |  | -5.696% | 1.057 | 1.595% |  |  |  |  | Non-TXV |  |  | -5.696%
Bakersfield | CA | 93301-1195 |  | 2014-10-28 | 2014-10-28 17:29 | 2014-10-28 17:29 | OTHER - UKN | 90 | 0 | Yes | Yes | 23.7 | 19.8 | 3.9 | 41BFAFA6EB2A4057B80ECF88F7EF140C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-1845 |  | 2014-05-30 | 2014-05-30 10:12 | 2014-05-30 10:12 | INTERTHERM - 16A049K | 89 | 0 | Yes | Yes | 18.7 | 18.8 | -0.1 | F2D55C5FEF9D49579917EF07257AC2E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3203 |  | 2014-06-03 | 2014-06-03 13:46 | 2014-06-03 14:03 | DAY & NIGHT - 565BJ036-D | 76 | -5.4 | Yes | Yes | 17 | 16.4 | 0.6 | 0477F2EF96384C3EAACC47877461DE67 |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Bakersfield | CA | 93305-2154 |  | 2014-10-24 | 2014-10-24 16:17 | 2014-10-24 16:17 | YORK - D1NA024N05606C | 54 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 32EB97EAA3D34A7FA35D9B21F4B122A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5123 |  | 2014-08-07 | 2014-08-07 11:31 | 2014-08-07 11:48 | CARRIER - 38CKC06370 | 131 | 5.5 | Yes | Yes | 22.9 | 20.4 | 2.5 | 44E3CF28AAA94FB5AE7803EC5E7ECB63 |  | R22 | Non-TXV |  | 4.198% | 0.95802 | 8.069% | [5 empty] | Non-TXV | 4.198%
Suisun City | CA | 94585-2632 |  | 2014-06-16 | 2014-06-16 09:44 | 2014-06-16 14:09 | TRANE - | 83 | -5.8 | Yes | Yes | 22.9 | 17.4 | 5.5 | 7658204DFADA48C2BF436ACBFECF125E |  | R22 | Non-TXV |  | -6.988% | 1.0699 | 1.957% |  |  |  |  | Non-TXV |  |  | -6.988%
Fairfield | CA | 94534-7443 |  | 2014-06-09 | 2014-06-09 12:18 | 2014-06-09 15:14 | BRYANT - | 85 | 3.6 | Yes | Yes | 22.6 | 17.5 | 5.1 | 85198FA269EA4FFA9F923400CA16D129 |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Suisun City | CA | 94585-1856 |  | 2014-06-03 | 2014-06-03 09:54 | 2014-06-03 09:54 | AMERICAN STANDARD - YCC036F1M0BK | 83 | 0 | Yes | Yes | 18.2 | 16.4 | 1.8 | F9F54A71D2EE4EAA8554705FC46D4089 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2154 |  | 2014-10-24 | 2014-10-24 16:40 | 2014-10-24 16:40 | YORK - D1NA024N03606C | 54 | 0 | Yes | Yes | 20.4 | 22 | -1.6 | 075434ACA023469DB6D689FFEF519C80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2154 |  | 2014-10-24 | 2014-10-24 16:47 | 2014-10-24 16:47 | YORK - D1NA024N05606C | 54 | 0 | Yes | Yes | 19.2 | 22 | -2.8 | 380EF1A636F6472C90641DB2E7514222 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2046 |  | 2014-05-30 | 2014-05-30 13:44 | 2014-05-30 13:44 | CARRIER - 48SS036060301 | 68 | 0 | Yes | Yes | 28.6 | 24.2 | 4.4 | 481AFB385D75460B9920EE152620CC88 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4294 |  | 2014-06-23 | 2014-06-23 10:39 | 2014-06-23 10:59 | CARRIER - 38TDA036300 | 178 | 5.4 | Yes | Yes | 13.4 | 16.1 | -2.7 | 7F90E489AE114454BEF71903EF50D9F4 |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.83% | [5 empty] | Non-TXV | 3.034%
Suisun City | CA | 94585-2817 |  | 2014-08-01 | 2014-08-01 13:15 | 2014-08-01 13:15 | - | 85 | 0 | Yes | Yes | 17.5 | 18.6 | -1.1 | 15E2148B5EDD49DEB50C1B722F0F86A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-5338 |  | 2014-06-09 | 2014-06-09 15:19 | 2014-06-09 16:02 | CARRIER - 36EN018300 | 55 | 11.5 | Yes | Yes | 18.7 | 21 | -2.3 | 90AE788579484C57817CF6BD0FDBE24E |  | R22 | Non-TXV |  | 20.91% | 0.79091 | 40.18% | [5 empty] | Non-TXV | 20.91%
Bakersfield | CA | 93313-5223 |  | 2014-10-16 | 2014-10-16 16:07 | 2014-10-16 16:07 | ICP - N2A342AKA100 | 114 | 0 | Yes | Yes | 22.8 | 21 | 1.8 | 1E66AF268311446C92E78C75A5E893B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1237 |  | 2014-07-22 | 2014-07-22 17:05 | 2014-07-22 17:07 | GOODMAN - GPG1336045M41BA | 85 | 7.8 | Yes | Yes | 24.1 | 19.1 | 5 | 44F823209C5345EAAA58DFBE0984C8B7 |  | R410A | Non-TXV |  | 9.176% | 0.90824 | 17.64% | [5 empty] | Non-TXV | 9.176%
Suisun City | CA | 94585-2634 |  | 2014-06-16 | 2014-06-16 10:21 | 2014-06-16 14:11 | TRANE - | 85 | 5.8 | Yes | Yes | 17.3 | 17.2 | 0.1 | CEF480AF73AE495CA483867181F34BFD |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Davis | CA | 95618-6737 |  | 2014-06-11 | 2014-06-11 12:41 | 2014-06-11 13:33 | GOODMAN - CK30-1T | 76 | -6.2 | Yes | Yes | 20.5 | 17 | 3.5 | 075B8BE9EAEE4311964C6457FF6BED6F |  | R22 | Non-TXV |  | -8.158% | 1.0816 | 2.285% |  |  |  |  | Non-TXV |  |  | -8.158%
Bakersfield | CA | 93313-5285 |  | 2014-09-26 | 2014-09-26 15:58 | 2014-09-26 15:58 | AIRE-FLO - 2AC13B30P-1A | 129 | 0 | Yes | Yes | 23.5 | 21.8 | 1.7 | 7240C5DCCE5048F69985B2B09E2E824E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5285 |  | 2014-09-26 | 2014-09-26 16:02 | 2014-09-26 16:02 | AIRE-FLO - 2AC13B30P-1A | 129 | 0 | Yes | Yes | 18.6 | 21.5 | -2.9 | 0E51F300209D40368CB17BAD41BBAE47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3349 |  | 2014-06-06 | 2014-06-06 09:44 | 2014-06-06 09:44 | UNITARY PRODUCTS GROUP - D3NP02N03606NXA | 100 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 208B34F189474A0C8449002B4B8490BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6946 |  | 2014-07-24 | 2014-07-24 14:36 | 2014-07-24 14:36 | UNITARY PRODUCTS GROUP - H1RA048S06G | 117 | 0 | Yes | Yes | 19.5 | 22.1 | -2.6 | 49F54986675D4A9584E342E5BF883031 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5231 |  | 2014-08-27 | 2014-08-27 09:45 | 2014-08-27 09:45 | ICP - N2A362AKA200 | 148 | -12.2 | Yes | Yes | 17.3 | 19.9 | -2.6 | 0F8507A88AE0436EBF4473BDF3D8852A | Remove refrigerant: 12.2 oz | R22 | Non-TXV |  | -8.243% | 1.0824 | 2.308% |  |  |  |  | Non-TXV |  |  | -8.243%
Bakersfield | CA | 93307-4565 |  | 2014-07-24 | 2014-07-24 10:58 | 2014-07-24 10:58 | ICP - PGAD30D1K7 | 78 | 0 | Yes | Yes | 19.4 | 20.1 | -0.6 | 4D0277F75BB34826A5D55740D12E9E51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3511 |  | 2014-06-03 | 2014-06-03 11:38 | 2014-06-03 11:38 | CARRIER - 38EN030340 | 109 | 0 | Yes | Yes | 20.4 | 17.9 | 2.5 | 886BAA0B10D84EE5BE026AE297E93B12 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2154 |  | 2014-10-24 | 2014-10-24 14:24 | 2014-10-24 14:24 | UNITARY PRODUCTS GROUP - D1NA024N03606C | 54 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | 72D45CC072BC4752B6150430B1B93F90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-1420 |  | 2014-06-10 | 2014-06-10 13:42 | 2014-06-10 14:11 | BRYANT - 113ANA042C | 92 | 8 | Yes | Yes | 18.6 | 21.4 | -2.8 | DA016041E1CB45AB8AD8FA55CC57D0D7 |  | R410A | Non-TXV |  | 8.696% | 0.91304 | 16.71% | [5 empty] | Non-TXV | 8.696%
San Jose | CA | 95128-5211 |  | 2014-06-20 | 2014-06-20 09:56 | 2014-06-20 10:16 | LENNOX - XC14-042-230 | 138 | 10.8 | Yes | Yes | 17.9 | 19.3 | -1.4 | B5FE65BA4B70417296D7F9072E7738B9 |  | R22 | Non-TXV |  | 7.826% | 0.92174 | 15.04% | [5 empty] | Non-TXV | 7.826%
Morgan Hill | CA | 95037-3764 |  | 2014-08-04 | 2014-08-04 11:15 | 2014-08-04 11:15 | HEIL - CA5548VKA1 | 139 | 0 | Yes | Yes | 21.1 | 19.9 | 1.2 | 299862E48A7D4A33A0C1AC245BCA6558 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2110 |  | 2014-07-22 | 2014-07-22 17:35 | 2014-07-22 17:37 | YORK - DAYPF042N0801A | 150 | -12.7 | Yes | Yes | 19.2 | 19.7 | -0.5 | 85EE0D1D5385443DA172F75DC677EA22 |  | R22 | Non-TXV |  | -8.467% | 1.0847 | 2.371% |  |  |  |  | Non-TXV |  |  | -8.467%
Vallejo | CA | 94590-3346 |  | 2014-08-07 | 2014-08-07 13:24 | 2014-08-07 22:14 | - GPC024K060D | 85 | 3.8 | Yes | Yes | 16 | 18.1 | -2.1 | A99ADF30A43744B581F4B8F50E0BC1FA |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Napa | CA | 94558-2817 |  | 2014-06-24 | 2014-06-24 13:56 | 2014-06-24 14:36 | NORDYNE - GS3BA-036KA | 70 | 4.6 | Yes | Yes | 10.1 | 12 | -1.9 | 22889F419B2D4C99A6E18B6AACA35ABE |  | R22 | Non-TXV |  | 6.571% | 0.93429 | 12.63% | [5 empty] | Non-TXV | 6.571%
Bakersfield | CA | 93306-7020 |  | 2014-09-02 | 2014-09-02 10:33 | 2014-09-02 10:33 | GOODMAN - GPG13300451BB | 77 | 0 | Yes | Yes | 28 | 22.3 | 5.7 | 93A6EF2AE77C42B9896C3B78649928FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-7580 |  | 2014-06-04 | 2014-06-04 14:19 | 2014-06-04 14:49 | RHEEM - RAND036JAZ | 116 | 27.5 | Yes | Yes | 18.8 | 21.5 | -2.7 | 06B913DF85FF4A2BA10754A527B1F831 |  | R22 | Non-TXV |  | 23.71% | 0.76293 | 45.56% | [5 empty] | Non-TXV | 23.71%
Wasco | CA | 93280-2682 |  | 2014-08-03 | 2014-08-03 18:47 | 2014-08-03 18:53 | AIRE-FLO - 2AC13B36P-1A | 85 | -5.3 | Yes | Yes | 21.7 | 21.5 | 0.2 | 7283809BEDFF447C89BE8EB485997FEA |  | R22 | Non-TXV |  | -6.235% | 1.0624 | 1.746% |  |  |  |  | Non-TXV |  |  | -6.235%
Bakersfield | CA | 93306-7020 |  | 2014-05-30 | 2014-05-30 13:08 | 2014-05-30 13:08 | UNITARY PRODUCTS GROUP - DAYP-F030N070A | 73 | 0 | Yes | Yes | 19.9 | 21.9 | -2 | A91CCD0221C9436188470B37A52C1089 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-2544 |  | 2014-08-21 | 2014-08-21 09:21 | 2014-08-21 10:43 | LENNOX - HS26-030-2P | 78 | 5.6 | Yes | Yes | 17.5 | 19.6 | -2.1 | 1637C98942394D259575785FB7777C2C |  | R22 | Non-TXV |  | 7.179% | 0.92821 | 13.8% | [5 empty] | Non-TXV | 7.179%
Winters | CA | 95694-1713 |  | 2014-07-07 | 2014-07-07 10:30 | 2014-07-07 19:24 | TRANE - TTX036C100A0 | 152 | 5.8 | Yes | Yes | 14.6 | 17.4 | -2.8 | 73A50FCFCEF04D9ABA53553C1B0E9607 |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Rio Vista | CA | 94571-1914 |  | 2014-09-23 | 2014-09-23 10:13 | 2014-09-23 10:31 | CARRIER - 38CKC018340 | 51 | 2.5 | Yes | Yes | 21.5 | 19.9 | 1.6 | 04EF2A477DCB40E89E70C73210ECD4CD |  | R22 | Non-TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | Non-TXV | 4.902%
Bakersfield | CA | 93313-5286 |  | 2014-10-01 | 2014-10-01 11:39 | 2014-10-01 11:39 | GOODMAN - GSC130421AC | 187 | 0 | Yes | Yes | 20.5 | 22 | -1.5 | EEC5A1CD47CB44358A312F1CDCD17185 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-0854 |  | 2014-10-16 | 2014-10-16 10:10 | 2014-10-16 12:26 | GE - 573KLP-03001-02 | 104 | 4.6 | Yes | Yes | 19.4 | 19.4 | 0 | 40CE48E373034767BAA623E6278257FD |  | R22 | Non-TXV |  | 4.423% | 0.95577 | 8.5% | [5 empty] | Non-TXV | 4.423%
Wasco | CA | 93280-2743 |  | 2014-08-16 | 2014-08-16 16:51 | 2014-08-16 16:53 | TEMPSTAR - N/A | 85 | 9.2 | Yes | Yes | 23.7 | 21.5 | 2.2 | 52F2F7EE3B884359AB890597FD888D86 |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
San Jose | CA | 95125-5059 |  | 2014-06-10 | 2014-06-10 10:19 | 2014-06-10 10:49 | GOODMAN - GSX130481BB | 104 | -6.1 | Yes | Yes | 23 | 20.4 | 2.6 | EE01286CEF5849A3AF55D9594E4E640A |  | R22 | Non-TXV |  | -5.865% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.865%
W Sacramento | CA | 95605-1953 |  | 2014-07-01 | 2014-07-01 12:57 | 2014-07-01 12:57 | - | 85 | 0 | Yes | Yes | 23.8 | 19.3 | 4.5 | 64BC93A643FE48038832101ACDB87B3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-6697 |  | 2014-07-30 | 2014-07-30 15:16 | 2014-07-30 15:16 | CARRIER - 2902E16276 | 85 | 0 | Yes | Yes | 15 | 15.8 | -0.8 | D6F0ECB658F447478908716D3C623A06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-3419 |  | 2014-06-10 | 2014-06-10 10:57 | 2014-06-10 13:20 | YORK - H5DB048S06A | 104 | -6.1 | Yes | Yes | 22.4 | 21.3 | 1.1 | B3923E08CBB041C397EDB1B02763E054 |  | R22 | Non-TXV |  | -5.865% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.865%
Campbell | CA | 95008-6400 |  | 2014-05-30 | 2014-05-30 13:41 | 2014-05-30 14:15 | TRANE - TTR36D100A0 | 79 | -7.4 | Yes | Yes | 19.6 | 19.4 | 0.2 | 4F743ACBB29046D998B20F064DD7132B |  | R22 | Non-TXV |  | -9.367% | 1.0937 | 2.623% |  |  |  |  | Non-TXV |  |  | -9.367%
Fairfield | CA | 94533-4531 |  | 2014-06-27 | 2014-06-27 13:30 | 2014-06-27 13:30 | TRANE - | 101 | 0 | Yes | Yes | 12.7 | 15.5 | -2.8 | 8FE2586ECFB24B399C4F421BD5021E6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95117-1134 |  | 2014-07-25 | 2014-07-25 10:13 | 2014-07-25 10:49 | BRYANT - 58ANR036 | 136 | 6.2 | Yes | Yes | 23.8 | 19.7 | 4.2 | 3F0D81F610DE45378B3ADB6310D4D708 |  | R22 | Non-TXV |  | 4.559% | 0.95441 | 8.761% | [5 empty] | Non-TXV | 4.559%
Woodland | CA | 95776-5143 |  | 2014-08-14 | 2014-08-14 12:43 | 2014-08-14 13:06 | FRIGIDAIRE - FS3BA-06KA3 | 69 | 4.5 | Yes | Yes | 19.6 | 20.4 | -0.8 | 99AD206F41844A5C8E885BC9C4CBFB82 |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Suisun City | CA | 94585-1916 |  | 2014-07-31 | 2014-07-31 14:11 | 2014-07-31 20:56 | LENNOX - | 85 | 2.5 | Yes | Yes | 15.3 | 18.2 | -2.9 | 670C3F165F7246508E1AFD61CCD0B48F |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
W Sacramento | CA | 95691-2556 |  | 2014-08-11 | 2014-08-11 14:45 | 2014-08-11 15:44 | BDP - 589ANW024040ACBD | 57 | 6.6 | Yes | Yes | 20.2 | 19.3 | 0.9 | 6670FF7CFBD24B64B725129FDF8F3D14 |  | R22 | Non-TXV |  | 11.58% | 0.88421 | 22.25% | [5 empty] | Non-TXV | 11.58%
San Jose | CA | 95118-2405 |  | 2014-06-10 | 2014-06-10 14:18 | 2014-06-10 14:44 | GOODMAN - CK481B | 97 | -5.7 | Yes | Yes | 23.6 | 21 | 2.6 | E97D223580B24BF392C07833D4492AB8 |  | R22 | Non-TXV |  | -5.876% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.876%
Pleasanton | CA | 94566-6813 |  | 2014-06-26 | 2014-06-26 09:09 | 2014-06-26 09:39 | PAYNE - 565AJ024 | 70 | 8.6 | Yes | Yes | 17.3 | 20.2 | -2.9 | 8B8E75F6BF334923A2C5510390D4EF33 |  | R22 | Non-TXV |  | 12.29% | 0.87714 | 23.61% | [5 empty] | Non-TXV | 12.29%
Napa | CA | 94558-2403 |  | 2014-07-15 | 2014-07-15 09:51 | 2014-07-15 10:54 | YORK - YCJD42S41S1HA | 68 | 10.4 | Yes | Yes | 21.1 | 20.7 | 0.4 | F62FDA24C7324B84B2FE9F12708AACB0 |  | R410A | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
Woodland | CA | 95776-9386 |  | 2014-06-18 | 2014-06-18 13:52 | 2014-06-18 14:15 | GOODMAN - CKJ48-1B | 110 | -7.8 | Yes | Yes | 17.6 | 17.4 | 0.2 | A2C82D12F048452EB408FF840C4FD5B9 |  | R22 | Non-TXV |  | -7.091% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.091%
Bakersfield | CA | 93301-5904 |  | 2014-10-28 | 2014-10-28 19:24 | 2014-10-28 19:24 | OTHER - UKN | 90 | 0 | Yes | Yes | 24 | 20.7 | 3.3 | 6C02B91F24424ED4B8C19D4EADE569C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5614 |  | 2014-07-24 | 2014-07-24 12:22 | 2014-07-24 12:50 | - 561CJ036-C | 74 | 3.4 | Yes | Yes | 12.9 | 15.3 | -2.4 | 5E002B7B2B1745A4846C586E27FB2F9F |  | R22 | Non-TXV |  | 4.595% | 0.95405 | 8.83% | [5 empty] | Non-TXV | 4.595%
Bakersfield | CA | 93311-1829 |  | 2014-06-05 | 2014-06-05 09:30 | 2014-06-05 09:30 | RHEEM - UKN | 85 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 2DF86D2676824853AF5D3CF739845C9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5905 |  | 2014-10-28 | 2014-10-28 19:42 | 2014-10-28 19:42 | OTHER - UKN | 90 | 0 | Yes | Yes | 22.1 | 20.1 | 2 | 0F915AC28D184E6E8AF23DAE6FEFC127 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2665 |  | 2014-08-02 | 2014-08-02 19:04 | 2014-08-02 19:06 | TEMPSTAR - PGAD361K3 | 78 | 4.4 | Yes | Yes | 22 | 20.4 | 1.6 | AA1197DBEEE74E1FB73F73264B3B7874 |  | R22 | Non-TXV |  | 5.641% | 0.94359 | 10.84% | [5 empty] | Non-TXV | 5.641%
Vallejo | CA | 94591-6307 |  | 2014-08-13 | 2014-08-13 10:01 | 2014-08-13 10:18 | CARRIER - 38CKC048300 | 102 | 5.3 | Yes | Yes | 25.8 | 20.4 | 5.4 | 8E3F1FD1DF3146C78EB6D90FEA7CAE3F |  | R22 | Non-TXV |  | 5.196% | 0.94804 | 9.986% | [5 empty] | Non-TXV | 5.196%
Bakersfield | CA | 93301-5904 |  | 2014-10-28 | 2014-10-28 19:25 | 2014-10-28 19:25 | OTHER - UKN | 90 | 0 | Yes | Yes | 23.9 | 19 | 4.9 | 4B3F8B210D794F68988578BEDF337C79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6794 |  | 2014-06-02 | 2014-06-02 12:08 | 2014-06-02 12:08 | UNK - UNK | 85 | 0 | Yes | Yes | 19.3 | 17.7 | 1.6 | 55C3B0A8FC0748D9BDDF774716F53E05 |  |  |  |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5902 |  | 2014-10-28 | 2014-10-28 18:23 | 2014-10-28 18:23 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.8 | 19.3 | 2.5 | 8107B11524E9493D91032C1B0DC341A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-7313 |  | 2014-05-30 | 2014-05-30 13:11 | 2014-05-30 13:30 | - | 85 | -7 | Yes | Yes | 20.9 | 19.4 | 1.5 | C56E89AEAB8A430EAC967519635E446C |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Bakersfield | CA | 93308-2116 |  | 2014-07-28 | 2014-07-28 09:33 | 2014-07-28 09:33 | HEIL - PGAA36C1K4 | 69 | 0 | Yes | Yes | 17.3 | 19.2 | -1.9 | 771B04B7726649F78626FD082BD4AB3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2779 |  | 2014-08-10 | 2014-08-10 20:23 | 2014-08-10 20:25 | OTHER - N2348AKA200 | 124 | 11.2 | Yes | Yes | 23.3 | 22.1 | 1.2 | 71AFA5A1804A4A62B6FC9F5AB8148985 |  | R22 | TXV |  | 9.032% | 0.90968 | 17.36% | [5 empty] | TXV | 9.032%
Hayward | CA | 94544-6669 |  | 2014-06-25 | 2014-06-25 10:03 | 2014-06-25 10:31 | TRANE - 2TTR1036A10000AA | 73 | -6.9 | Yes | Yes | 24.5 | 18.8 | 5.7 | AC09555266D74BFE83D5F989BE1DFDD6 |  | R22 | Non-TXV |  | -9.452% | 1.0945 | 2.647% |  |  |  |  | Non-TXV |  |  | -9.452%
Hayward | CA | 94544-6669 |  | 2014-06-25 | 2014-06-25 10:15 | 2014-06-25 10:33 | TRANE - 2TTR1036A1000AAA | 73 | 2.2 | Yes | Yes | 22.1 | 19.8 | 2.3 | 641E422EC6C649E79633A7B2158A6A0F |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Shafter | CA | 93263-2335 |  | 2014-09-21 | 2014-09-21 19:05 | 2014-09-21 19:06 | DAY & NIGHT - PGF336060K01 | 146 | 6.9 | Yes | Yes | 20.9 | 21 | -0.1 | B04E257D953A453CAF677B6653DD2B91 |  | R22 | TXV |  | 4.726% | 0.95274 | 9.082% | [5 empty] | TXV | 4.726%
Vacaville | CA | 95687-4919 |  | 2014-07-03 | 2014-07-03 12:34 | 2014-07-03 12:34 | PAYNE - PA14NA042-A | 138 | 0 | Yes | Yes | 19.4 | 19.4 | 0 | BDC50E3E6D374D969F5D8C2AFD91F8BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1438 |  | 2014-11-03 | 2014-11-03 15:22 | 2014-11-03 15:22 | RHEEM - UKN | 75 | 0 | Yes | Yes | 24.8 | 20.2 | 4.7 | C1AE583F9B014918BCF21FD8B046AEC2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2633 |  | 2014-06-16 | 2014-06-16 10:09 | 2014-06-16 10:09 | - | 85 | 0 | Yes | Yes | 19.9 | 17.4 | 2.5 | 22658C1F23E04321A7BDCC7E021AC77F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-1821 |  | 2014-07-11 | 2014-07-11 09:02 | 2014-07-11 09:22 | PAYNE - PA110JA060 | 121 | 5.9 | Yes | Yes | 19.3 | 19.9 | -0.6 | 47CD25108B2C423DBB0E2216E8871EE9 |  | R22 | Non-TXV |  | 4.876% | 0.95124 | 9.371% | [5 empty] | Non-TXV | 4.876%
San Jose | CA | 95116-2424 |  | 2014-06-11 | 2014-06-11 09:10 | 2014-06-11 09:29 | PAYNE - PA13NR036 | 128 | -7.5 | Yes | Yes | 22.2 | 20.7 | 1.6 | C0C828E3299844DBB504443BF3DECD61 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
San Jose | CA | 95125-5837 |  | 2014-09-05 | 2014-09-05 09:47 | 2014-09-05 10:11 | RUUD - UAKA-037JAZ | 79 | -7.4 | Yes | Yes | 19 | 17.1 | 1.9 | 9CB2932080474BE4BFD39B6535B71FA3 |  | R22 | Non-TXV |  | -9.367% | 1.0937 | 2.623% |  |  |  |  | Non-TXV |  |  | -9.367%
Bakersfield | CA | 93306-4540 |  | 2014-08-26 | 2014-08-26 13:38 | 2014-08-26 13:38 | GOODMAN - GPG1330045M1AB | 80 | 0 | Yes | Yes | 27 | 22.4 | 4.7 | 2188DED3DB104857A8BF0FFEF644B235 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2132 |  | 2014-11-24 | 2014-11-24 10:27 | 2014-11-24 10:27 | RHEEM - UNK | 85 | 0 | Yes | Yes | 21.9 | 16.4 | 5.5 | B551DA5E190B44DBB5B57542D8ECFDAD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2624 |  | 2014-08-21 | 2014-08-21 09:08 | 2014-08-21 09:08 | - | 85 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | 6BF019A71C9A4833BA5F651F657B83C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3341 |  | 2014-10-02 | 2014-10-02 11:21 | 2014-10-02 11:37 | CARRIER - H2RDO48S06B | 136 | 4.5 | Yes | Yes | 19.7 | 20.4 | -0.7 | 26710F1DA56440338AAEA68B561F35FB |  | R22 | Non-TXV |  | 3.309% | 0.96691 | 6.359% | [5 empty] | Non-TXV | 3.309%
San Jose | CA | 95148-1407 |  | 2014-07-23 | 2014-07-23 14:14 | 2014-07-23 14:33 | CARRIER - 38HDL048 | 114 | 12.6 | Yes | Yes | 20.3 | 20.3 | 0 | A687D784EE5642BB96665548D56921F4 |  | R22 | Non-TXV |  | 11.05% | 0.88947 | 21.24% | [5 empty] | Non-TXV | 11.05%
Bakersfield | CA | 93308-4083 |  | 2014-09-13 | 2014-09-13 14:52 | 2014-09-13 14:52 | BDP - 661CJ018B | 68 | 0 | Yes | Yes | 18.7 | 19.9 | -1.2 | B2B190B055DB44E488AB6C0DA4B0AF6E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3737 |  | 2014-06-06 | 2014-06-06 10:23 | 2014-06-06 10:23 | BDP - 585GJ036060 | 82 | 0 | Yes | Yes | 23.3 | 20.8 | 2.5 | 5F9780CE3FAE48F080A8C6DD8DC6FD40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3737 |  | 2014-06-06 | 2014-06-06 10:27 | 2014-06-06 10:27 | BDP - 585GJ024040 | 54 | 0 | Yes | Yes | 23.7 | 19.7 | 4.1 | EBF6C30E5F78416993DF97003A1DACA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1611 |  | 2014-06-10 | 2014-06-10 09:10 | 2014-06-10 09:55 | GOODMAN - CK24-1D | 66 | -5.4 | Yes | Yes | 19.4 | 20.4 | -1 | 5CC8599008C04F2D9AA7DAEF15F47E93 |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Bakersfield | CA | 93307-4329 |  | 2014-06-18 | 2014-06-18 13:29 | 2014-06-18 13:29 | UNITARY PRODUCTS GROUP - DRCS0421BE | 109 | 0 | Yes | Yes | 18.7 | 19.8 | -1.1 | 8D094F0178DE48E89AAFFEA69827EC6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4868 |  | 2014-06-25 | 2014-06-25 11:02 | 2014-06-25 11:02 | COLEMAN - BRCQ048B | 93 | 0 | Yes | Yes | 27.3 | 22.1 | 5.2 | 193F6EA37CA6400BB757016A4F009685 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2619 |  | 2014-07-17 | 2014-07-17 12:28 | 2014-07-17 13:40 | AMERICAN STANDARD - 2YCX3030A1064AA | 81 | 3.5 | Yes | Yes | 17.4 | 18.8 | -1.4 | 7865B1B6CEE542D3B947AE6F9C9B7479 |  | R22 | Non-TXV |  | 4.321% | 0.95679 | 8.304% | [5 empty] | Non-TXV | 4.321%
Rio Vista | CA | 94571-1533 |  | 2014-08-21 | 2014-08-21 13:19 | 2014-08-21 13:34 | FRESCHI - | 40 | 7.1 | Yes | Yes | 17.7 | 18.2 | -0.5 | 8599D34244E04C2481693B3AD13C8171 |  | R22 | Non-TXV |  | 17.75% | 0.8225 | 34.11% | [5 empty] | Non-TXV | 17.75%
Bakersfield | CA | 93309-3437 |  | 2014-05-28 | 2014-05-28 11:09 | 2014-05-28 11:09 | OTHER - UKN | 90 | 0 | Yes | Yes | 28.4 | 22.5 | 5.9 | 8ED64A977DC246E3B7FB632CEDBDA110 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-9162 |  | 2014-06-05 | 2014-06-05 15:09 | 2014-06-06 07:59 | NORDYNE - FS3BA060KA | 122 | 19 | Yes | Yes | 20.7 | 21.3 | -0.5 | BE02302EAB9944B6BD7F5531AD8861F4 |  | R22 | Non-TXV |  | 15.57% | 0.84426 | 29.93% | [5 empty] | Non-TXV | 15.57%
Bakersfield | CA | 93304-1563 |  | 2014-08-26 | 2014-08-26 18:37 | 2014-08-26 18:37 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 18.9 | 20.9 | -2 | C9124B414F78484F8971C7DEFFFE75E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1886 |  | 2014-09-16 | 2014-09-16 08:42 | 2014-09-16 08:42 | BDP - 585B024050YACR | 51 | 0 | Yes | Yes | 22.7 | 19.8 | 2.9 | 89153E2AEAC7496A9E521BC9A720B123 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1577 |  | 2014-08-26 | 2014-08-26 19:18 | 2014-08-26 19:18 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.1 | 22.9 | -2.8 | E974100335E8418590842D0E99810E1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1551 |  | 2014-08-28 | 2014-08-28 19:54 | 2014-08-28 19:54 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.3 | 20.3 | -1 | 0F00282F2FC240D385E744313BC0D8A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1569 |  | 2014-09-03 | 2014-09-03 19:32 | 2014-09-03 19:32 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | 464966FAAD284A7CAA3C84C0C9038B84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2011 |  | 2014-05-28 | 2014-05-28 12:54 | 2014-05-28 12:54 | BRYANT - UKN | 168 | 0 | Yes | Yes | 28.7 | 25.1 | 3.6 | BF91456A4B784C7981EBB79E55F99B67 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Winters | CA | 95694-9646 |  | 2014-09-30 | 2014-09-30 12:59 | 2014-09-30 19:18 | AMERICAN STANDARD - 34GTB030-473ATG-01 | 80 | 4.6 | Yes | Yes | 20 | 19.3 | 0.7 | D520CE9C3554485C8AE8A65FE98CB025 |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Bakersfield | CA | 93305-2332 |  | 2014-06-17 | 2014-06-17 13:41 | 2014-06-17 13:41 | ICP - PGF042K080D | 87 | 0 | Yes | Yes | 23.4 | 20.9 | 2.5 | 846184150EFE4DF68A32F39878E467C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3653 |  | 2014-06-03 | 2014-06-03 09:02 | 2014-06-03 09:02 | UNITARY PRODUCTS GROUP - BRCQ01BD36 | 52 | 0 | Yes | Yes | 23.5 | 20.6 | 2.9 | 76AB7DD563F4421A8B1E4BCE26D6C400 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5746 |  | 2014-09-19 | 2014-09-19 09:39 | 2014-09-19 09:39 | PAYNE - UKN | 90 | 0 | Yes | Yes | 18.5 | 20.6 | -2.1 | D7B3AE1110EB44139B449EA458C72273 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-3130 |  | 2014-07-23 | 2014-07-23 14:43 | 2014-07-23 14:43 | CARRIER - 561CJX036 | 86 | 0 | Yes | Yes | 24.2 | 20.4 | 3.8 | 9756FBB21A5840EBA4731A5E989FAE65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4639 |  | 2014-05-30 | 2014-05-30 12:27 | 2014-05-30 12:27 | CARRIER - 48DG004 | 87 | 0 | Yes | Yes | 18.9 | 21 | -2.1 | CCB3B1BBCEA44F34A981A9D5ED7BCA89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5902 |  | 2014-10-28 | 2014-10-28 18:04 | 2014-10-28 18:04 | OTHER - UKN | 85 | 0 | Yes | Yes | 25.1 | 19.6 | 5.5 | C6642F73CE30464F99AB8ADB4AE6ADEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6728 |  | 2014-05-30 | 2014-05-30 11:45 | 2014-05-30 11:45 | CARRIER - UKN | 90 | 0 | Yes | Yes | 23.2 | 22.1 | 1.1 | 891A697460734F948D735B1452FB8817 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1730 |  | 2014-06-27 | 2014-06-27 12:27 | 2014-06-27 12:27 | TRANE - | 106 | 0 | Yes | Yes | 11.8 | 14.7 | -2.9 | 90026E1968944683961ADE6C64D557D6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2788 |  | 2014-07-09 | 2014-07-09 15:16 | 2014-07-09 15:16 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 19.6 | 22.6 | -3 | A91A974291B54324885AA8162FD8D09D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5905 |  | 2014-10-28 | 2014-10-28 19:44 | 2014-10-28 19:44 | OTHER - UKN | 90 | 0 | Yes | Yes | 23.3 | 21 | 2.3 | 6C45A439798A47DAB4E6C1A2D43D2E4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1564 |  | 2014-08-26 | 2014-08-26 19:04 | 2014-08-26 19:04 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.7 | 21.3 | -0.5 | 05EA88A905CD4D0B9CEB93F798DCC5A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3922 |  | 2014-06-04 | 2014-06-04 16:09 | 2014-06-04 16:30 | AMERICAN STANDARD - 2YC3048A1096AA | 144 | 4.3 | Yes | Yes | 18.3 | 20.8 | -2.5 | FE090307176B4E34B77FFD373D65C5D6 |  | R22 | Non-TXV |  | 2.986% | 0.97014 | 5.739% | [5 empty] | Non-TXV | 2.986%
Bakersfield | CA | 93301-1195 |  | 2014-10-28 | 2014-10-28 16:39 | 2014-10-28 16:39 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.9 | 19.5 | 2.4 | BCD92417373E4F5790EC72A7CC6124F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1890 |  | 2014-09-10 | 2014-09-10 12:42 | 2014-09-10 12:42 | GOODMAN - GPG1330045M41AB | 80 | 0 | Yes | Yes | 25.1 | 19.9 | 5.2 | A50C12334AF0406286E20A1C53A573B4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2790 |  | 2014-10-01 | 2014-10-01 10:50 | 2014-10-01 10:50 | NORDYNE - FS5B060KA | 180 | 0 | Yes | Yes | 21.4 | 21.4 | 0 | F1DA2A363D95498880FA2F613F9ADA1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6562 |  | 2014-06-03 | 2014-06-03 13:56 | 2014-06-03 13:56 | UNITARY PRODUCTS GROUP - H2RD048S06B | 134 | 0 | Yes | Yes | 18.2 | 21.2 | -3 | 17EC06E646D04E5CB8468B287967046F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-3243 |  | 2014-06-11 | 2014-06-11 09:44 | 2014-06-11 10:06 | ICP - N4A336AKB200 | 85 | -5 | Yes | Yes | 20.1 | 18.8 | 1.3 | 3DA711A3D2914C1094B5D42FD8E7FB3E |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93309-1929 |  | 2014-05-28 | 2014-05-28 11:46 | 2014-05-28 11:46 | PAYNE - PY1PJB048090AAAA | 97 | 0 | Yes | Yes | 22.8 | 20.9 | 1.9 | DA5B87854CDC4E8CB1A6FF1B10624200 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1024 |  | 2014-06-11 | 2014-06-11 10:13 | 2014-06-11 10:41 | TRANE - 2TTR3048A1000AA | 142 | 6.1 | Yes | Yes | 21.6 | 20.4 | 1.2 | A5AB4A8137694807987FC0EFC89A393F |  | R22 | Non-TXV |  | 4.296% | 0.95704 | 8.256% | [5 empty] | Non-TXV | 4.296%
Bakersfield | CA | 93305-4034 |  | 2014-06-24 | 2014-06-24 14:37 | 2014-06-24 14:37 | UNITARY PRODUCTS GROUP - DBYP-F030N070A | 73 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 8EB29C737AEF401095E995B2B2A27F9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-3471 |  | 2014-09-03 | 2014-09-03 10:44 | 2014-09-03 11:03 | CARRIER - 38QR030C-321 | 32 | 29.6 | Yes | Yes | 17.7 | 18.3 | -0.6 | CA191E7A076F403D976EDE9561EF0202 |  | R22 | Non-TXV |  | 92.5% | 0.075 | 177.8% | [5 empty] | Non-TXV | 92.5%
Vallejo | CA | 94591-3803 |  | 2014-08-06 | 2014-08-06 12:00 | 2014-08-06 22:14 | - | 85 | -6 | Yes | Yes | 13.8 | 16 | -2.2 | FC5AF29E07CB4854813116B8746258F9 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Vacaville | CA | 95687-3207 |  | 2014-06-12 | 2014-06-12 08:52 | 2014-06-12 09:10 | CLIMATEMASTER - 7830-901 | 44 | 1.5 | Yes | Yes | 19.2 | 17 | 2.2 | D5C5683293034F7C84989E32D28A09D0 |  | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Arvin | CA | 93203-1717 |  | 2014-11-04 | 2014-11-04 15:29 | 2014-11-04 16:02 | YORK - D2NZ036N05606NXA | 85 | 16 | Yes | Yes | 17.8 | 20.7 | -2.9 | 35A579BBCCB34FC5B23A224EA2D5FEFF |  | R410A | Non-TXV |  | 18.82% | 0.81176 | 36.17% | [5 empty] | Non-TXV | 18.82%
San Jose | CA | 95136-2325 |  | 2014-06-11 | 2014-06-11 13:32 | 2014-06-11 13:51 | TRANE - TTR048D1000A1 | 86 | 6.4 | Yes | Yes | 20.1 | 19.8 | 0.3 | D48F1139E4904400AEC98ADB76081B29 |  | R22 | Non-TXV |  | 7.442% | 0.92558 | 14.3% | [5 empty] | Non-TXV | 7.442%
Arvin | CA | 93203-2775 |  | 2014-11-06 | 2014-11-06 12:18 | 2014-11-06 12:36 | GOODMAN - PGB036075-1B | 85 | 5.3 | Yes | Yes | 18.2 | 21.1 | -2.9 | 9EED84080D4C48EE8547C04BEB7167C2 |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Fairfield | CA | 94533-1212 |  | 2014-06-10 | 2014-06-10 10:43 | 2014-06-10 11:10 | AIRE-FLO - 597CN036-B | 75 | 3.3 | Yes | Yes | 16.6 | 17.2 | -0.6 | 75555B2738D6415DBB1D93A211F5A643 |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
Fairfield | CA | 94534-4345 |  | 2014-06-10 | 2014-06-10 12:43 | 2014-06-10 13:34 | TRANE - | 82 | 4.9 | Yes | Yes | 20.4 | 20.2 | 0.3 | 8290336F0066425AA59474F36BE12529 |  | R22 | Non-TXV |  | 5.976% | 0.94024 | 11.48% | [5 empty] | Non-TXV | 5.976%
Bakersfield | CA | 93308-1847 |  | 2014-07-28 | 2014-07-28 14:56 | 2014-07-28 14:56 | UNITARY PRODUCTS GROUP - D1H042N06506C | 90 | 0 | Yes | Yes | 26.4 | 20.9 | 5.5 | 119DAD772329418A8E407FECF646C9F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2360 |  | 2014-08-26 | 2014-08-26 10:09 | 2014-08-26 10:09 | OTHER - UKN | 90 | 0 | Yes | Yes | 20.1 | 20.6 | -0.5 | 75E32C6CFD4741C389F57A6CF4065B5C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1265 |  | 2014-05-30 | 2014-05-30 10:59 | 2014-05-30 10:59 | ICP - GPCM024K040D | 54 | 0 | Yes | Yes | 20.2 | 22.1 | -1.9 | F27A23926B33478F8DD2695E8E8D84D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-4706 |  | 2014-06-12 | 2014-06-12 08:40 | 2014-06-12 09:11 | CARRIER - 38EYG24300 | 74 | 2.5 | Yes | Yes | 23.3 | 20.9 | 2.4 | 00FD9D9FF601493DB15687A3E2B92248 |  | R410A | Non-TXV |  | 3.378% | 0.96622 | 6.492% | [5 empty] | Non-TXV | 3.378%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:38 | 2014-10-10 15:38 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.4 | 22.3 | -2.8 | ABEA986E11FA405DA4E14472E6516DCA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:35 | 2014-10-10 15:35 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.8 | 22 | -1.2 | B485A50931D74D3FAE0F0EEDE1673362 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 16:26 | 2014-10-10 16:26 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.8 | 22 | -0.2 | 23702B6190614B4A9BAA692FB2285898 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:06 | 2014-10-10 15:06 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.3 | 22.6 | -1.3 | C9C2E09571C24100857C7DA227AC6788 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:04 | 2014-10-10 15:04 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | F6E0CF086CA7490AA2803BA22665B913 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 14:26 | 2014-10-10 14:26 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 18.1 | 20.4 | -2.3 | 9DA81F139ACD4E6D824AD20E5245C493 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 14:29 | 2014-10-10 14:29 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | EB228CFC19FE41BCBB5383519657B32B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 14:31 | 2014-10-10 14:31 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.2 | 22 | -0.8 | 0836B3BD270A4FF4AC087AC10D5E6E87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 14:47 | 2014-10-10 14:47 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.7 | 22.5 | -0.8 | 1772AD20E7E34CF694F72BA5C267AAF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:30 | 2014-10-10 15:30 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21.3 | 22 | -0.7 | E33E27F738A64CCFA5AA67D99F50A1D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:55 | 2014-10-10 15:55 | CARRIER - 38YCC024341 | 70 | 0 | Yes | Yes | 21 | 22 | -1 | 3F9F5FBE2310413FA9AA80E45D2F6B7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 16:00 | 2014-10-10 16:00 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | 9071AF018403434F8B78D8E061FD998D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5884 |  | 2014-07-31 | 2014-07-31 12:19 | 2014-07-31 12:19 | WEATHER KING - 12AJA3621 | 90 | 0 | Yes | Yes | 20.3 | 14.8 | 5.6 | 2CDEFB6C7A71404AB2AFCECBA672E46D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3271 |  | 2014-06-24 | 2014-06-24 11:00 | 2014-06-24 11:00 | DAY & NIGHT - 565BB060 | 128 | 0 | Yes | Yes | 23.7 | 22 | 1.7 | 7EC481D43ED24D8CB5321B87727565AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-3751 |  | 2014-06-13 | 2014-06-13 09:57 | 2014-06-13 11:52 | CARRIER - 38CKC048300 | 104 | -7.3 | Yes | Yes | 24.6 | 20.6 | 4 | 41C8743968CB4EE8BD0DCF4991B6062A |  | R22 | Non-TXV |  | -7.019% | 1.0702 | 1.966% |  |  |  |  | Non-TXV |  |  | -7.019%
Bakersfield | CA | 93308-3004 |  | 2014-07-25 | 2014-07-25 14:19 | 2014-07-25 14:19 | CARRIER - 48SDN030040301 | 130 | 0 | Yes | Yes | 27.2 | 21.3 | 5.9 | 0B9B3D9EE252480F951181CF1DF89D8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95131-3430 |  | 2014-06-18 | 2014-06-18 08:49 | 2014-06-18 09:15 | CARRIER - 38CKC042350 | 83 | 7.5 | Yes | Yes | 16.9 | 19.7 | -2.8 | 90DC2F1D9E73486CADE4F10266558D48 |  | R22 | TXV |  | 9.036% | 0.90964 | 17.37% | [5 empty] | TXV | 9.036%
San Jose | CA | 95136-2123 |  | 2014-06-11 | 2014-06-11 13:10 | 2014-06-11 13:27 | LENNOX - HS26048 | 117 | 8 | Yes | Yes | 24.1 | 21.3 | 2.8 | 1B8C7A987D3D4E699E6C3E2C7B24BB13 |  | R22 | Non-TXV |  | 6.838% | 0.93162 | 13.14% | [5 empty] | Non-TXV | 6.838%
San Jose | CA | 95118-1320 |  | 2014-06-11 | 2014-06-11 14:06 | 2014-06-11 15:06 | TRANE - 2TTR2042A1000AA | 95 | 3.4 | Yes | Yes | 22.3 | 20.3 | 2 | 8C232FFE938A469F87045D49A96B14DB |  | R22 | Non-TXV |  | 3.579% | 0.96421 | 6.878% | [5 empty] | Non-TXV | 3.579%
Bakersfield | CA | 93308-1857 |  | 2014-07-28 | 2014-07-28 13:58 | 2014-07-28 13:58 | TRANE - 4YCY4036B1075AA | 118 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | 9314B23A5C364185AF12B68C2E30974F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1857 |  | 2014-07-28 | 2014-07-28 14:07 | 2014-07-28 14:07 | PAYNE - PH3PNA036000AA | 169 | 0 | Yes | Yes | 22.9 | 16.9 | 6 | B7BECB8A39F045BFAC79BE9379C65BCF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1265 |  | 2014-05-27 | 2014-05-27 13:20 | 2014-05-27 13:20 | RHEEM - RRKA-A024JK06X | 50 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | 3810E87B1AE04B4F8026332B36E1EDDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1539 |  | 2014-07-25 | 2014-07-25 10:19 | 2014-07-25 10:19 | RHEEM - RRPL-B036JK06X | 85 | 0 | Yes | Yes | 17.3 | 19.7 | -2.4 | 842144991F8E4996985601CE203F970D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7656 |  | 2014-07-23 | 2014-07-23 09:02 | 2014-07-23 09:20 | GOODMAN - GSC130421AC | 137 | 5.4 | Yes | Yes | 27.1 | 21.5 | 5.6 | 099E249366DE4648969D90702FB01080 |  | R22 | Non-TXV |  | 3.942% | 0.96058 | 7.575% | [5 empty] | Non-TXV | 3.942%
Bakersfield | CA | 93306-0000 |  | 2014-07-21 | 2014-07-21 13:54 | 2014-07-21 13:54 | CARRIER - 24ABB360W310 | 147 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | 4F1EB936BD1C447D97716D45242E0567 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1704 |  | 2014-07-25 | 2014-07-25 13:26 | 2014-07-25 13:26 | TRANE - 2YCC3042A1064AA | 131 | 0 | Yes | Yes | 18.6 | 18.1 | 0.5 | 6516332FB76645148109C754441DE088 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-9710 |  | 2014-07-30 | 2014-07-30 10:00 | 2014-07-30 10:00 | TRANE - 4WCC3036A1000AB | 116 | 0 | Yes | Yes | 23.3 | 18.6 | 4.7 | BDE9B4921FEF43D5A9CD6A38C290C2A5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-3732 |  | 2014-06-26 | 2014-06-26 12:41 | 2014-06-26 13:24 | GMC - VSX13036 | 89 | -6.3 | Yes | Yes | 19.8 | 20.3 | -0.5 | F53D96EA27854CB985C1A3B46863E151 |  | R410A | Non-TXV |  | -7.079% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.079%
Bakersfield | CA | 93308-4085 |  | 2014-09-13 | 2014-09-13 15:34 | 2014-09-13 15:34 | BDP - UKN | 68 | 0 | Yes | Yes | 21.1 | 21 | 0.1 | F8562ECC4E5D4E62B2A20C03F30DE3E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-0739 |  | 2014-07-29 | 2014-07-29 12:32 | 2014-07-29 12:55 | GIBSON - JS5BD048K | 147 | -8.6 | Yes | Yes | 24.8 | 20.3 | 4.5 | 04518968D8F5441F8394BDC9C6B5B877 |  | R22 | Non-TXV |  | -5.85% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.85%
Sunnyvale | CA | 94089-4611 |  | 2014-07-21 | 2014-07-21 13:02 | 2014-07-21 13:35 | - UCS3615 | 66 | 8.3 | Yes | Yes | 20.9 | 19.9 | 1 | 88739E96BCFA42DDAF6BC72E5C1B4FFF |  | R22 | Non-TXV |  | 12.58% | 0.87424 | 24.17% | [5 empty] | Non-TXV | 12.58%
Milpitas | CA | 95035-3617 |  | 2014-06-23 | 2014-06-23 09:04 | 2014-06-23 09:35 | DAY & NIGHT - S3BA036K | 98 | 6.4 | Yes | Yes | 17 | 19.8 | -2.8 | 6037B31BD33B48A8BF4F05330FF1C6B2 |  | R22 | Non-TXV |  | 6.531% | 0.93469 | 12.55% | [5 empty] | Non-TXV | 6.531%
Bakersfield | CA | 93308-4702 |  | 2014-06-13 | 2014-06-13 10:32 | 2014-06-13 10:32 | YORK - SA36G080N-6A | 99 | 0 | Yes | Yes | 18.6 | 21.3 | -2.7 | 17C98822C9C5456AA73D1C07F1F20B15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5187 |  | 2014-08-27 | 2014-08-27 14:54 | 2014-08-27 14:54 | UNITARY PRODUCTS GROUP - H2RA036S06D | 63 | 0 | Yes | Yes | 20.5 | 22.2 | -1.7 | 5F5391AA63244922932E3455F74E8B9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1163 |  | 2014-06-13 | 2014-06-13 09:45 | 2014-06-13 09:45 | GOODMAN - GPG1336045M41AB | 85 | 0 | Yes | Yes | 26.9 | 23.1 | 3.8 | 702967E77AE840A1B0DEE82F70A489FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4711 |  | 2014-06-19 | 2014-06-19 08:42 | 2014-06-19 08:42 | AIRE-FLO - PGE13B24JO6 | 78 | 0 | Yes | Yes | 15.3 | 17.6 | -2.3 | DD8ABC479CC647A296F3ADB2E9AB32B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5640 |  | 2014-07-23 | 2014-07-23 14:09 | 2014-07-23 14:09 | UNITARY PRODUCTS GROUP - D1NP036N05606A | 108 | 0 | Yes | Yes | 17.8 | 15.4 | 2.4 | 6FD8899893C94A0DA944D42CF0ACA2A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6627 |  | 2014-07-03 | 2014-07-03 13:22 | 2014-07-03 14:57 | LENNOX - | 85 | 3.9 | Yes | Yes | 18.4 | 18.8 | -0.4 | 4A54AA9ACDF0485A85A5A5D0E79C06FA |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
San Jose | CA | 95127-3202 |  | 2014-06-16 | 2014-06-16 13:07 | 2014-06-16 13:45 | DAY & NIGHT - 591ANX036000AAA | 82 | -4.8 | Yes | Yes | 22.6 | 19.3 | 3.3 | 3E6CC4B0A0444050917B57143B14FC05 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Bakersfield | CA | 93307-7143 |  | 2014-06-20 | 2014-06-20 09:51 | 2014-06-20 09:51 | RUUD - EADB-042JAS | 79 | 0 | Yes | Yes | 22.4 | 20.6 | 1.9 | F2BF6D8FDB784161939E12B5BF5377B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-4740 |  | 2014-06-16 | 2014-06-16 13:51 | 2014-06-16 13:51 | CARRIER - 38TXA060350 | 184 | 0 | Yes | Yes | 16.8 | 19.4 | -2.6 | 6DA687B3D37D43119A7983B00778D617 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4907 |  | 2014-07-03 | 2014-07-03 10:56 | 2014-07-03 11:15 | YORK - YCJD60S41S1C | 86 | 3 | Yes | Yes | 23.1 | 19.9 | 3.2 | 7CEEB11BF64C44AAA611452AD79CC132 |  | R22 | Non-TXV |  | 3.488% | 0.96512 | 6.704% | [5 empty] | Non-TXV | 3.488%
Fairfield | CA | 94534-3314 |  | 2014-08-18 | 2014-08-18 11:48 | 2014-08-18 12:11 | PAYNE - 591ANX018OOOAAA | 48 | 4.2 | Yes | Yes | 20.8 | 19.7 | 1.2 | 2C383D05F481494E94D55E1DCCD2B057 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Dixon | CA | 95620-9310 |  | 2014-07-29 | 2014-07-29 11:16 | 2014-07-29 11:33 | UNK - UNK | 85 | 7.2 | Yes | Yes | 19.2 | 19.9 | -0.7 | 758475E4F33D4002828A9C7F4067087C |  |  |  |  | 8.471% | 0.91529 | 16.28% | [5 empty] | 0 | 8.471%
Davis | CA | 95616-2294 |  | 2014-06-18 | 2014-06-18 09:51 | 2014-06-18 10:08 | LENNOX - HS29-024-2P | 62 | 2.6 | Yes | Yes | 22.3 | 17.7 | 4.7 | 88969C6E27B44C06B53F4A22275C884F |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
San Jose | CA | 95121-2346 |  | 2014-07-23 | 2014-07-23 15:07 | 2014-07-24 08:29 | ICP - NCA5536VKD2 | 82 | 5.7 | Yes | Yes | 24.4 | 19.9 | 4.5 | B512C2F9D2494B6AB9E32EF6B8F2C0FF |  | R22 | Non-TXV |  | 6.951% | 0.93049 | 13.36% | [5 empty] | Non-TXV | 6.951%
Bakersfield | CA | 93312-4994 |  | 2014-09-18 | 2014-09-18 15:05 | 2014-09-18 15:05 | ICP - AG036GB2 | 82 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | F14452494BD1430E8D18FC89309D654C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5112 |  | 2014-08-05 | 2014-08-05 13:12 | 2014-08-05 13:12 | OTHER - UKN | 90 | 0 | Yes | Yes | 19.2 | 20.4 | -1.2 | A02D095727F748B8B7A84A3D91B5E07F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5230 |  | 2014-08-29 | 2014-08-29 11:36 | 2014-08-29 11:36 | CARRIER - 24ABB342W300 | 93 | 0 | Yes | Yes | 22.8 | 19.4 | 3.5 | C82C31EC5CBB4BB5B13C647D6354CCD9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4818 |  | 2014-07-25 | 2014-07-25 19:26 | 2014-07-25 19:55 | GOODMAN - CK30-1E | 100 | 4.6 | Yes | Yes | 13 | 15.3 | -2.3 | 440B1684DF124E4393C6D7CD330437DD |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Rio Vista | CA | 94571-2229 |  | 2014-10-15 | 2014-10-15 10:51 | 2014-10-15 11:29 | YORK - H2RC024S6A | 91 | 5.1 | Yes | Yes | 21.3 | 20.4 | 0.9 | F9A7D1B4AA0C4ACB965EAF9572A3CA51 |  | R22 | Non-TXV |  | 5.604% | 0.94396 | 10.77% | [5 empty] | Non-TXV | 5.604%
Suisun City | CA | 94585-2111 |  | 2014-06-13 | 2014-06-13 15:40 | 2014-06-13 17:58 | CARRIER - 24ABA336A300 | 88 | 5.7 | Yes | Yes | 11.7 | 14.7 | -3 | 108C2BED4B834DF6AC292548B0146CF8 |  | R410A | Non-TXV |  | 6.477% | 0.93523 | 12.45% | [5 empty] | Non-TXV | 6.477%
W Sacramento | CA | 95691-5179 |  | 2014-07-02 | 2014-07-02 09:58 | 2014-07-02 21:34 | GOODMAN - CKF36-1AB | 85 | 3.2 | Yes | Yes | 22 | 19.3 | 2.7 | B3E2F82E3700423CAD45F2C1E301B527 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Bakersfield | CA | 93304-3926 |  | 2014-06-17 | 2014-06-17 12:13 | 2014-06-17 12:13 | TRANE - YCP030F1L0AB | 106 | 0 | Yes | Yes | 18.5 | 21.5 | -3 | A1D71938829447C88FD8E84E73786D26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5228 |  | 2014-08-29 | 2014-08-29 12:39 | 2014-08-29 12:39 | AIRE-FLO - 2AC13B60P-1A | 225 | 0 | Yes | Yes | 20.6 | 23.1 | -2.5 | 8ED028504B8549459B99925E8C264AF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3939 |  | 2014-06-27 | 2014-06-27 09:59 | 2014-06-30 08:22 | UNITARY PRODUCTS GROUP - PGN330060K01A1-- | 96 | -5.6 | Yes | Yes | 22.9 | 16.9 | 6 | 683DE89B633644D685AE90B18BA29B5B |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
San Jose | CA | 95136-2739 |  | 2014-06-16 | 2014-06-16 14:27 | 2014-06-16 21:43 | YORK - BRC0301BE | 41 | 6.2 | Yes | Yes | 23.1 | 19.3 | 3.8 | 7B3606BE926B4D4696FFB3FFF44CC0D0 |  | R22 | Non-TXV |  | 15.12% | 0.84878 | 29.06% | [5 empty] | Non-TXV | 15.12%
San Jose | CA | 95117-2513 |  | 2014-09-15 | 2014-09-15 10:42 | 2014-09-15 11:09 | ALLEGIANCE - 7A0036A100A1 | 86 | 5.2 | Yes | Yes | 20 | 18.8 | 1.2 | FB5693B3C999407A9607991BFFECC757 |  | R22 | Non-TXV |  | 6.047% | 0.93953 | 11.62% | [5 empty] | Non-TXV | 6.047%
W Sacramento | CA | 95691-3942 |  | 2014-06-27 | 2014-06-27 10:31 | 2014-06-30 08:21 | RHEEM - RAND-024JAZ | 85 | -8 | Yes | Yes | 21.6 | 15.7 | 5.9 | 55ADFC68A78D41AEA73AA0EB8CFABEDE |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93313-5229 |  | 2014-09-23 | 2014-09-23 10:12 | 2014-09-23 10:12 | ICP - N2A342AKA100 | 116 | 0 | Yes | Yes | 19.5 | 20.9 | -1.4 | 530BFA8F13E54279B6F347A6AB31B23F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2359 |  | 2014-08-26 | 2014-08-26 15:28 | 2014-08-26 15:28 | OTHER - 80D25BC23 | 35 | 0 | Yes | Yes | 19.6 | 21.2 | -1.6 | FA17E7DAE014421182731D818BB0735F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4976 |  | 2014-08-06 | 2014-08-06 12:59 | 2014-08-06 12:59 | ICP - PGME36G0907 | 100 | 0 | Yes | Yes | 21.5 | 15.6 | 6 | 4A58746AD2FF43D4921B5B243C847F90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-6328 |  | 2014-07-16 | 2014-07-16 13:13 | 2014-07-16 13:37 | CARRIER - 38CKC036350 | 70 | 7.1 | Yes | Yes | 21.8 | 19 | 2.8 | 3188A75AACBB4916A6E92E83F4D4B3A9 |  | R22 | Non-TXV |  | 10.14% | 0.89857 | 19.49% | [5 empty] | Non-TXV | 10.14%
Woodland | CA | 95695-2922 |  | 2014-07-23 | 2014-07-23 10:03 | 2014-07-23 10:48 | CARRIER - 38CKCGD-- | 112 | 4.8 | Yes | Yes | 18.5 | 17.7 | 0.8 | DBBE0A2D1DA740FC89F66DB3979B1E04 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Dixon | CA | 95620-4242 |  | 2014-07-03 | 2014-07-03 10:06 | 2014-07-03 14:56 | GOODMAN - CJ36-1GB | 106 | -10 | Yes | Yes | 22.5 | 18.4 | 4.2 | C8816C5A79ED482A9126B7EC7F3EE744 |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Woodland | CA | 95695-3323 |  | 2014-06-18 | 2014-06-18 13:24 | 2014-06-18 14:00 | - | 85 | -5 | Yes | Yes | 21.6 | 17.4 | 4.2 | 1AF5BD666A5640568458AFBECD3CDFF5 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
San Jose | CA | 95124-1761 |  | 2014-06-20 | 2014-06-20 09:22 | 2014-06-20 09:45 | LENNOX - HS293113P | 69 | 3 | Yes | Yes | 21.8 | 19.3 | 2.5 | 6A06F9AABB304723BAF1E9C057F6F061 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
San Jose | CA | 95111-3909 |  | 2014-06-17 | 2014-06-17 10:35 | 2014-06-17 13:09 | PAYNE - PA13NA060 | 140 | 13.2 | Yes | Yes | 18 | 19.9 | -1.9 | 7B1C32234FE74B6DBD99538820A3E86A |  | R22 | Non-TXV |  | 9.429% | 0.90571 | 18.12% | [5 empty] | Non-TXV | 9.429%
Morgan Hill | CA | 95037-3117 |  | 2014-08-08 | 2014-08-08 14:34 | 2014-08-08 14:52 | COPELAND - UNK | 131 | 6.2 | Yes | Yes | 16.6 | 17.5 | -0.9 | 72A288ADC7694DC2A34ADC58BA1BE654 |  | R22 | Non-TXV |  | 4.733% | 0.95267 | 9.095% | [5 empty] | Non-TXV | 4.733%
W Sacramento | CA | 95691-4511 |  | 2014-06-27 | 2014-06-27 13:38 | 2014-06-27 14:27 | - | 85 | -8 | Yes | Yes | 21.7 | 16.4 | 5.3 | F41D44112FB249DEAF1E04D8401443CC |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93301-5903 |  | 2014-10-28 | 2014-10-28 19:12 | 2014-10-28 19:12 | OTHER - UKN | 90 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | 9BFE32CF007D462CA1DC249DEB99A1E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3938 |  | 2014-07-22 | 2014-07-22 10:19 | 2014-07-22 11:05 | RHEEM - HO-60-36-210 | 49 | 4.8 | Yes | Yes | 19.5 | 18.2 | 1.3 | B7489398635A47ACACADDE3A57019177 |  | R22 | Non-TXV |  | 9.796% | 0.90204 | 18.83% | [5 empty] | Non-TXV | 9.796%
Vallejo | CA | 94591-6834 |  | 2014-10-02 | 2014-10-02 19:15 | 2014-10-02 19:43 | CARRIER - 2TTR3048A10000AA | 142 | 4.8 | Yes | Yes | 21.7 | 20.4 | 1.3 | 4D667FFB1DD347F4A07A2CEBA1CA4292 |  | R22 | Non-TXV |  | 3.38% | 0.9662 | 6.496% | [5 empty] | Non-TXV | 3.38%
Bakersfield | CA | 93307-1807 |  | 2014-06-20 | 2014-06-20 13:15 | 2014-06-20 13:15 | AMERICAN STANDARD - YCZ036F1M0BD | 160 | 0 | Yes | Yes | 23.9 | 22.1 | 1.8 | 2E3C96B804E14DD49C71F868394440B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5901 |  | 2014-10-28 | 2014-10-28 17:33 | 2014-10-28 17:33 | OTHER - UKN | 90 | 0 | Yes | Yes | 18.7 | 20.4 | -1.7 | F5A7E037C7CA4B758B368A0A679DB638 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5816 |  | 2014-06-17 | 2014-06-17 10:51 | 2014-06-17 10:51 | ICP - PGC036K080E | 71 | 0 | Yes | Yes | 24.1 | 24.2 | -0.1 | D3C81CE0D79C471DBF1CF047D8EC9230 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-9450 |  | 2014-11-07 | 2014-11-07 13:43 | 2014-11-07 14:01 | OTHER - GSC130481AA | 85 | 13.6 | Yes | Yes | 21.5 | 22.6 | -1.1 | CC434C765BD5495C9CA5B24D5274F7F4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Bakersfield | CA | 93312-4446 |  | 2014-08-15 | 2014-08-15 10:27 | 2014-08-15 10:27 | RUUD - UKN | 90 | 0 | Yes | Yes | 19.3 | 21.7 | -2.4 | 3051F94BA08C4AB2B6DEA5E81B32F508 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2742 |  | 2014-06-17 | 2014-06-17 09:55 | 2014-06-17 15:25 | TRANE - TT506C100C1 | 86 | 6.2 | Yes | Yes | 17.2 | 19.3 | -2.1 | 5B83659144B94AD1BBFEBE3CAEA4A8DB | Add refrigerant: 2.6 oz | R22 | Non-TXV |  | 7.209% | 0.92791 | 13.85% | [5 empty] | Non-TXV | 7.209%
Vacaville | CA | 95687-4611 |  | 2014-07-03 | 2014-07-03 11:19 | 2014-07-03 11:36 | ALLEGIANCE - 2A7A3036A1000AA | 101 | 3.9 | Yes | Yes | 22.2 | 20.3 | 1.9 | 6EEA3243A1904D0EADE7F9DCC0F53E8A |  | R22 | Non-TXV |  | 3.861% | 0.96139 | 7.421% | [5 empty] | Non-TXV | 3.861%
Bakersfield | CA | 93301-1129 |  | 2014-10-24 | 2014-10-24 12:11 | 2014-10-24 12:11 | GOODMAN - GPG1324045M41AC | 80 | 0 | Yes | Yes | 22.3 | 21 | 1.3 | 67288F7B4D2345F3ADBD80AE98BD99BC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3248 |  | 2014-06-25 | 2014-06-25 09:51 | 2014-06-25 09:51 | RHEEM - URMAA036JK08X | 99 | 0 | Yes | Yes | 21.6 | 20.7 | 0.9 | FE8B132DD550478DA92B41BB818B90C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3248 |  | 2014-06-25 | 2014-06-25 10:00 | 2014-06-25 10:00 | RHEEM - URMAA036JK06X | 99 | 0 | Yes | Yes | 21.6 | 22.6 | -1 | F5C9FF242E60421AA1EF306DC1945548 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2584 |  | 2014-07-25 | 2014-07-25 12:07 | 2014-07-25 12:07 | AIRE-FLO - GCGD60S21S2A | 84 | 0 | Yes | Yes | 14.4 | 17.1 | -2.7 | 7259BE978BAE4D9E8B0D4D253E0CF1D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5917 |  | 2014-09-19 | 2014-09-19 14:48 | 2014-09-19 14:48 | ICP - PGAA42C1K3 | 82 | 0 | Yes | Yes | 21 | 19.1 | 1.9 | C2D1AD92CEE040FA85809D701C8B1B6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2178 |  | 2014-09-02 | 2014-09-02 14:03 | 2014-09-02 14:03 | RHEEM - UKN | 90 | 0 | Yes | Yes | 19.9 | 22.3 | -2.4 | C7C5730620B048A2A974E9E4ED9A59E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2203 |  | 2014-06-24 | 2014-06-24 15:17 | 2014-06-24 17:24 | TRANE - TTB038C100A1 | 90 | 8.7 | Yes | Yes | 10.8 | 13.7 | -2.9 | E9572832EB1645E3912FB7A29A697B2B |  | R22 | Non-TXV |  | 9.667% | 0.90333 | 18.58% | [5 empty] | Non-TXV | 9.667%
Bakersfield | CA | 93306-5112 |  | 2014-08-06 | 2014-08-06 09:53 | 2014-08-06 09:53 | ICP - GPCM024K040D800 | 109 | 0 | Yes | Yes | 24.5 | 18.5 | 6 | 9DA74C5ACA88484F9D42BFB582F5F176 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3316 |  | 2014-11-04 | 2014-11-04 12:56 | 2014-11-04 12:56 | TEMPSTAR - PGF036K060B | 71 | 0 | Yes | Yes | 17.5 | 19.1 | -1.6 | 3706575A57194E2AA750BE142AC40397 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1192 |  | 2014-10-28 | 2014-10-28 16:18 | 2014-10-28 16:18 | OTHER - UKN | 90 | 0 | Yes | Yes | 23 | 20.4 | 2.6 | 439871098D0D4287826C525BA7B5D9FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9214 |  | 2014-09-26 | 2014-09-26 09:21 | 2014-09-26 09:21 | GOODMAN - GBC130301AE | 117 | 0 | Yes | Yes | 18.8 | 21.5 | -2.7 | 4A9816DFE18F499882C992FDB8E38E32 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9214 |  | 2014-09-26 | 2014-09-26 09:23 | 2014-09-26 09:23 | GOODMAN - GSC130301AE | 117 | 0 | Yes | Yes | 19.9 | 21.5 | -1.6 | A387253A504E461BAB839D2F34EF35AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-2133 |  | 2014-06-13 | 2014-06-13 13:17 | 2014-06-13 13:17 | BRYANT - 113ANA030 | 67 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | EA19A201AEA642EA89532088A4E9783D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-3703 |  | 2014-10-02 | 2014-10-02 13:47 | 2014-10-02 13:47 | WESTINGHOUSE - UNK | 90 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | 8DDB87E6AB264EF8B468D7B9961C0668 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-1839 |  | 2014-09-04 | 2014-09-04 08:42 | 2014-09-04 08:59 | OTHER - UKN | 82 | 0 | Yes | Yes | 20.2 | 18.2 | 2 | C3ADC8EC805D4F62AF1A81D4B4BB39FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-3014 |  | 2014-06-20 | 2014-06-20 14:00 | 2014-06-20 14:33 | CARRIER - 38HDL036 | 88 | 5.5 | Yes | Yes | 23.3 | 21.4 | 1.9 | 972F4A6C5368493481B38831589424F0 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Bakersfield | CA | 93309-7644 |  | 2014-10-28 | 2014-10-28 15:35 | 2014-10-28 15:35 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 25.4 | 21 | 4.4 | 72D15F8AD1574EEB9712CE66EDD04A8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-6461 |  | 2014-08-07 | 2014-08-07 14:32 | 2014-08-07 14:32 | - | 85 | 0 | Yes | Yes | 15.3 | 17.4 | -2.1 | CD3A7AE0F27F493DA32DC0CDB0BC80CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-1020 |  | 2014-06-13 | 2014-06-13 14:20 | 2014-06-13 14:41 | CARRIER - 38HDC036321 | 88 | 3.6 | Yes | Yes | 22.6 | 20.9 | 1.7 | 33499709808941BBB8947821F662C226 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Napa | CA | 94559-3564 |  | 2014-07-15 | 2014-07-15 15:19 | 2014-07-15 15:57 | TRANE - TTRO36C100A2 | 108 | 3.7 | Yes | Yes | 14 | 16.3 | -2.3 | F7787BA384A54DFA8CC27EE740339CE3 |  | R22 | Non-TXV |  | 3.426% | 0.96574 | 6.584% | [5 empty] | Non-TXV | 3.426%
Vacaville | CA | 95688-9300 |  | 2014-07-29 | 2014-07-29 12:40 | 2014-07-29 14:57 | TRANE - 2TTZ9048A1000AB | 85 | 3.9 | Yes | Yes | 16.8 | 17.3 | -0.5 | CB04516EA1F143C792797914035BF53D |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93301-1131 |  | 2014-10-24 | 2014-10-24 12:51 | 2014-10-24 12:51 | RHEEM - RRNAB024JK06X | 70 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | FBD7E01C42B84E40B4737E265921C5EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6215 |  | 2014-07-10 | 2014-07-10 12:22 | 2014-07-10 12:37 | AMANA - RCC48A28 | 85 | 5 | Yes | Yes | 21.5 | 18.8 | 2.7 | 9AF20F334A5B49DC939DB3DCB88A9085 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Vacaville | CA | 95688-5320 |  | 2014-07-01 | 2014-07-01 10:10 | 2014-07-01 11:34 | AMERICAN STANDARD - 2A7B0030A100 | 66 | 3.4 | Yes | Yes | 18 | 19.3 | -1.3 | 647F0061092F4E8E886032536D0B7CD8 |  | R22 | Non-TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | Non-TXV | 5.152%
Bakersfield | CA | 93306-0000 |  | 2014-06-24 | 2014-06-24 12:11 | 2014-06-24 12:11 | UNITARY PRODUCTS GROUP - D2NP030N05606A | 73 | 0 | Yes | Yes | 22.6 | 23.1 | -0.5 | D786E63BCCEE4FD7A7B0C75616579CC9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2639 |  | 2014-08-02 | 2014-08-02 18:48 | 2014-08-02 18:52 | GOODMAN - GPG13300451AB | 77 | 4.1 | Yes | Yes | 27.1 | 22.3 | 4.8 | 43D604E421F74AB899687ECF735A5847 |  | R22 | Non-TXV |  | 5.325% | 0.94675 | 10.23% | [5 empty] | Non-TXV | 5.325%
Shafter | CA | 93263-2440 |  | 2014-11-06 | 2014-11-06 13:41 | 2014-11-06 13:41 | GE - PGMD36G0604 | 69 | 0 | Yes | Yes | 20.9 | 21 | -0.1 | A145F22047EE4B84995CD3AE1BA66E94 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3779 |  | 2014-06-27 | 2014-06-27 12:14 | 2014-06-27 12:32 | CARRIER - | 87 | 2.7 | Yes | Yes | 19.6 | 17.6 | 2 | 52CB99676F8F4B6E9B0BB794F192D4A7 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Suisun City | CA | 94585-1309 |  | 2014-06-17 | 2014-06-17 11:34 | 2014-06-17 15:23 | GIBSON - JT5BD-018K | 93 | 3.2 | Yes | Yes | 18.8 | 15.8 | 3 | E48424FF286C4CB080F9EA1172FBDAC1 |  | R22 | Non-TXV |  | 3.441% | 0.96559 | 6.613% | [5 empty] | Non-TXV | 3.441%
Dixon | CA | 95620-2610 |  | 2014-10-09 | 2014-10-09 11:36 | 2014-10-09 21:55 | BRYANT - 578E0307342A1000 | 100 | 4.5 | Yes | Yes | 21.5 | 20.4 | 1.1 | 7466E2AF26B94E5C80AEE92F4FA63989 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Dixon | CA | 95620-4259 |  | 2014-07-30 | 2014-07-30 11:55 | 2014-07-30 11:55 | AIRE-FLO - CGCD36S21S1A | 65 | 0 | Yes | Yes | 11.4 | 13.7 | -2.3 | 587D5659032F4F258C2F3E5D8BCC8C4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-6154 |  | 2014-07-15 | 2014-07-15 13:26 | 2014-07-15 13:53 | COPELAND - GSC140421AE | 100 | -5.9 | Yes | Yes | 21.9 | 19.8 | 2.1 | C9CC03AE7B734C458D0673FCC648400E |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Bakersfield | CA | 93312-1878 |  | 2014-10-20 | 2014-10-20 12:50 | 2014-10-20 12:50 | UNITARY PRODUCTS GROUP - H2RC030506HG | 109 | 0 | Yes | Yes | 24.2 | 21.5 | 2.7 | 9375733DDE7248D5925C0D5BD6B630D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-1878 |  | 2014-10-20 | 2014-10-20 12:52 | 2014-10-20 12:52 | UNITARY PRODUCTS GROUP - H2RC030506HG | 88 | 0 | Yes | Yes | 25 | 21.5 | 3.5 | 3A618DB3ECF145DB808B46858DE3E151 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6948 |  | 2014-07-31 | 2014-07-31 08:23 | 2014-07-31 20:51 | RHEEM - RRKA-A024-JK06X | 85 | -6 | Yes | Yes | 16.7 | 18.2 | -1.5 | 2A9780C1F9D641B185CB1293EB9D0A63 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93306-4240 |  | 2014-06-24 | 2014-06-24 09:43 | 2014-06-24 09:43 | OTHER - UKN | 90 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | 57E4C7FA76BA40909F846002A8A0E84A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1215 |  | 2014-06-17 | 2014-06-17 09:19 | 2014-06-17 09:40 | HEIL - HAC024AKA5 | 69 | -6.5 | Yes | Yes | 25.1 | 20 | 5.2 | DAEBBF659B4743B78A8C1BEA5EE78E30 |  | R22 | Non-TXV |  | -9.42% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.42%
Vacaville | CA | 95687-6215 |  | 2014-06-25 | 2014-06-25 13:32 | 2014-06-25 14:52 | CARRIER - 38TKB036300 | 93 | 3.7 | Yes | Yes | 24.6 | 22.4 | 2.2 | 15EB21B2A61B4982BE6D103DE2A8045E |  | R22 | Non-TXV |  | 3.978% | 0.96022 | 7.646% | [5 empty] | Non-TXV | 3.978%
Shafter | CA | 93263-2906 |  | 2014-09-07 | 2014-09-07 18:03 | 2014-09-15 00:19 | GOODMAN - GPG1336045M41BA | 70 | 6.7 | Yes | Yes | 25 | 19.3 | 5.7 | FB6480FDDE714385A592592AFB5B06BA |  | R410A | Non-TXV |  | 9.571% | 0.90429 | 18.39% | [5 empty] | Non-TXV | 9.571%
Vacaville | CA | 95687-6440 |  | 2014-06-19 | 2014-06-19 15:37 | 2014-06-19 17:25 | GMC - BTD7364100A0 | 88 | 4.2 | Yes | Yes | 17.6 | 19.7 | -2.1 | C8BACB34AE6045E9BFE930C7EBEE1D3A |  | R22 | Non-TXV |  | 4.773% | 0.95227 | 9.172% | [5 empty] | Non-TXV | 4.773%
Dixon | CA | 95620-4809 |  | 2014-07-14 | 2014-07-14 15:32 | 2014-07-14 22:08 | PAYNE - PA12NA060-B | 184 | 8.7 | Yes | Yes | 19.6 | 17.4 | 2.2 | 64472AB524DC4C3A941EE8F82FEB0D18 |  | R22 | Non-TXV |  | 4.728% | 0.95272 | 9.087% | [5 empty] | Non-TXV | 4.728%
Bakersfield | CA | 93304-5174 |  | 2014-10-15 | 2014-10-15 14:42 | 2014-10-15 14:42 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 21.9 | 22 | -0.1 | 15E5BA070C5643739B781EEF5F891417 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2617 |  | 2014-06-19 | 2014-06-19 09:33 | 2014-06-19 09:52 | AIRE-FLO - VSX130361EF | 69 | 4.7 | Yes | Yes | 14.3 | 13.9 | 0.4 | 20F0A0884CCB4EF68E00F54453752DC1 |  | R410A | Non-TXV |  | 6.812% | 0.93188 | 13.09% | [5 empty] | Non-TXV | 6.812%
Milpitas | CA | 95035-4349 |  | 2014-06-20 | 2014-06-20 13:04 | 2014-06-20 13:25 | NORDYNE - JS5BD036KB | 69 | 12.5 | Yes | Yes | 19.9 | 20.1 | -0.2 | AE21B5E5CF264DA68E7DE2E7E799926B |  | R22 | Non-TXV |  | 18.12% | 0.81884 | 34.81% | [5 empty] | Non-TXV | 18.12%
Wasco | CA | 93280-1628 |  | 2014-07-27 | 2014-07-27 20:03 | 2014-07-27 20:10 | OTHER - HBBDF036SB | 96 | 22.3 | Yes | Yes | 22.8 | 22.1 | 0.7 | A6A8D20BD2334ADCA3F5B210323645E3 |  | R22 | TXV |  | 23.23% | 0.76771 | 44.64% | [5 empty] | TXV | 23.23%
Wasco | CA | 93280-1628 |  | 2014-07-27 | 2014-07-27 20:13 | 2014-07-27 20:16 | YORK - DBYPF024N045A | 100 | 4.8 | Yes | Yes | 22 | 23.2 | -1.2 | AFF0029B514B484DBE3AC48A9937F75E |  | R22 | TXV |  | 4.8% | 0.952 | 9.225% | [5 empty] | TXV | 4.8%
Bakersfield | CA | 93304-5174 |  | 2014-10-15 | 2014-10-15 14:51 | 2014-10-15 14:51 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 22.2 | 21.8 | 0.4 | 34F2CCEA4ACA4CDCA552E2F42C72E781 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4536 |  | 2014-08-15 | 2014-08-15 13:18 | 2014-08-15 20:58 | CARRIER - 48GS-030060301 | 85 | 3.2 | Yes | Yes | 16.3 | 18.8 | -2.5 | 0011C89AC7E54B509836C435C13AF300 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Wasco | CA | 93280-2639 |  | 2014-08-02 | 2014-08-02 18:55 | 2014-08-02 19:02 | GOODMAN - PGP13300451AB | 77 | 3.2 | Yes | Yes | 27.8 | 22.3 | 5.5 | 7B6DB080EF174C25817316096F6646EC |  | R22 | Non-TXV |  | 4.156% | 0.95844 | 7.987% | [5 empty] | Non-TXV | 4.156%
Bakersfield | CA | 93304-5173 |  | 2014-10-15 | 2014-10-15 14:36 | 2014-10-15 14:36 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 21.5 | 22.6 | -1.1 | 3BF22E08405549638704B222DD08378B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6433 |  | 2014-06-27 | 2014-06-27 09:37 | 2014-06-27 09:37 | CARRIER - 38CKC036340 | 60 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 512B3DB9EE914C7FB1DC7137710A1C2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3784 |  | 2014-08-25 | 2014-08-25 14:51 | 2014-08-25 14:51 | CARRIER - 48NLT024300 | 80 | 0 | Yes | Yes | 21 | 22.4 | -1.4 | DCFEFE190E1E4720AE5E7B05794EB679 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5229 |  | 2014-08-27 | 2014-08-27 09:57 | 2014-08-27 09:57 | ICP - N2A360AKA200 | 148 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 6160F079F52A479AB225EDDDD3055B3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-4619 |  | 2014-06-23 | 2014-06-23 10:11 | 2014-06-23 10:42 | KENMORE - TCA036AAAA | 80 | 8.3 | Yes | Yes | 18.2 | 18.2 | 0 | 57D7886CE4F140E599F2280D5BDDDDEF |  | R22 | Non-TXV |  | 10.38% | 0.89625 | 19.94% | [5 empty] | Non-TXV | 10.38%
San Jose | CA | 95121-1558 |  | 2014-06-17 | 2014-06-17 14:31 | 2014-06-17 14:55 | GOODMAN - CE361B | 79 | 3.2 | Yes | Yes | 25 | 20.7 | 4.4 | DCCD2B955A234745B2F59404B2D8C9E9 |  | R22 | Non-TXV |  | 4.051% | 0.95949 | 7.784% | [5 empty] | Non-TXV | 4.051%
Vacaville | CA | 95688-2306 |  | 2014-06-19 | 2014-06-19 15:10 | 2014-06-19 17:32 | TRANE - | 117 | 4.3 | Yes | Yes | 14.2 | 16.6 | -2.4 | FB539EFC170542C586A7D1A02A589E45 |  | R410A | Non-TXV |  | 3.675% | 0.96325 | 7.063% | [5 empty] | Non-TXV | 3.675%
Bakersfield | CA | 93306-3925 |  | 2014-09-10 | 2014-09-10 08:55 | 2014-09-10 08:55 | OTHER - PA13NR042 | 115 | -10.8 | Yes | Yes | 19.3 | 20.4 | -1.1 | 80748677B0354D68A87120C8712395D7 | Remove refrigerant: 10.8 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | -9.391% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.391%
Bakersfield | CA | 93306-1537 |  | 2014-06-30 | 2014-06-30 10:18 | 2014-06-30 10:18 | RUUD - UAPC-060JAZ | 150 | 0 | Yes | Yes | 17.2 | 20.2 | -3 | 6CB57D5852494A609AEFCAC3902BF9C8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2785 |  | 2014-09-23 | 2014-09-23 13:24 | 2014-09-23 13:24 | BRYANT - 113ANA048-E | 112 | 0 | Yes | Yes | 23 | 21.5 | 1.5 | E17AFAFB1D2442518729744C536706CE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7981 |  | 2014-06-19 | 2014-06-19 11:45 | 2014-06-19 18:03 | GOODMAN - | 54 | 6 | Yes | Yes | 13.3 | 15.5 | -2.2 | 55EA965AA1D449789187DBB61564A76E |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Bakersfield | CA | 93304-6735 |  | 2014-06-20 | 2014-06-20 09:17 | 2014-06-20 09:17 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | BF8D64E2377E4081921B6A4F1DC07269 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6809 |  | 2014-07-09 | 2014-07-09 09:31 | 2014-07-09 17:21 | CARRIER - 38CK036310 | 75 | 2.5 | Yes | Yes | 20.1 | 18.1 | 2 | 63A2F73A47104B16BD232F03E8B2990E |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Vacaville | CA | 95687-5160 |  | 2014-10-14 | 2014-10-14 13:13 | 2014-10-14 19:19 | AIRE-FLO - 2A7A2030A10000AA | 66 | 3.8 | Yes | Yes | 21.3 | 20.4 | 0.9 | B4F04885640441D9968DB287AFDCD5DA |  | R22 | Non-TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | Non-TXV | 5.758%
Bakersfield | CA | 93308-1517 |  | 2014-06-13 | 2014-06-13 15:44 | 2014-06-13 15:44 | UNITARY PRODUCTS GROUP - D1NP048N06506A | 132 | 0 | Yes | Yes | 25.7 | 19.9 | 5.8 | AEC912110F1F486C8CEBD354463CB294 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5903 |  | 2014-10-28 | 2014-10-28 18:36 | 2014-10-28 18:36 | OTHER - UKN | 90 | 0 | Yes | Yes | 26.1 | 21 | 5.1 | 62993CC81E714BF5AC08B84EC2230A40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-3222 |  | 2014-06-20 | 2014-06-20 13:30 | 2014-06-20 13:53 | AMANA - RCC36AA2A | 180 | 20.1 | Yes | Yes | 19.8 | 21.2 | -1.4 | AB7A84331EB34331B97902591D1C8098 |  | R22 | Non-TXV |  | 11.17% | 0.88833 | 21.46% | [5 empty] | Non-TXV | 11.17%
San Jose | CA | 95111-1150 |  | 2014-06-17 | 2014-06-17 15:00 | 2014-06-17 20:22 | YORK - N/A | 69 | 7 | Yes | Yes | 18.2 | 20.3 | -2.1 | BADA563E96144749B98BBADB126D4795 |  | R22 | Non-TXV |  | 10.14% | 0.89855 | 19.5% | [5 empty] | Non-TXV | 10.14%
Sunnyvale | CA | 94089-2614 |  | 2014-07-24 | 2014-07-24 09:16 | 2014-07-24 09:55 | BRYANT - 215BNA030 | 112 | -10.5 | Yes | Yes | 23.1 | 19.1 | 4 | E825B811C19A44C8967C7A93AB419C02 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Concord | CA | 94520-5451 |  | 2014-09-08 | 2014-09-08 09:04 | 2014-09-08 09:04 | CARRIER - 38CKC024330 | 56 | 0 | Yes | Yes | 23 | 17.1 | 5.9 | 809D3350DAEB4900BD3F365947F66C76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95118-1107 |  | 2014-07-11 | 2014-07-11 13:43 | 2014-07-11 14:04 | RUUD - UAKA048JAZ | 103 | -6.1 | Yes | Yes | 21.3 | 19.9 | 1.4 | 219E7F96A7204C9D85893B158A2A02E2 |  | R22 | Non-TXV |  | -5.922% | 1.0592 | 1.659% |  |  |  |  | Non-TXV |  |  | -5.922%
Vacaville | CA | 95687-6243 |  | 2014-06-30 | 2014-06-30 13:09 | 2014-06-30 15:09 | TRANE - 2TTBOO36A100AA | 76 | 4.5 | Yes | Yes | 10.3 | 12.2 | -1.9 | C87F9C49B2B04F97A9462B824F4650A3 |  | R22 | Non-TXV |  | 5.921% | 0.94079 | 11.38% | [5 empty] | Non-TXV | 5.921%
Wasco | CA | 93280-2554 |  | 2014-11-05 | 2014-11-05 10:57 | 2014-11-05 10:57 | HEIL - PGC042K080B | 87 | 0 | Yes | Yes | 16.4 | 19.4 | -3 | 29DDB7B082054C36BF75CDC26F09E276 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1519 |  | 2014-06-27 | 2014-06-27 09:56 | 2014-06-27 10:15 | CARRIER - 38CMB0483000 | 136 | -9.6 | Yes | Yes | 24 | 19.9 | 4.1 | EE4758C8A8924007B457185F067AB244 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Livermore | CA | 94551-4247 |  | 2014-06-26 | 2014-06-26 09:53 | 2014-06-26 10:26 | DUCANE - A12B36 | 83 | 10.7 | Yes | Yes | 16.7 | 19.3 | -2.6 | 89A9BC74592C45A0B2B6CE28DA574296 |  | R22 | Non-TXV |  | 12.89% | 0.87108 | 24.77% | [5 empty] | Non-TXV | 12.89%
Davis | CA | 95616-3407 |  | 2014-10-10 | 2014-10-10 11:46 | 2014-10-10 12:05 | LENNOX - HS29-036-2P | 72 | 5 | Yes | Yes | 19.6 | 20.4 | -0.8 | 314EB78788A84558A6989467D5E5BD2A |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Livermore | CA | 94551-5603 |  | 2014-08-12 | 2014-08-12 12:54 | 2014-08-12 13:22 | YORK - H2RA036S06G | 63 | 9 | Yes | Yes | 15.6 | 18.6 | -3 | 3DA262C5B74D41E1BCEA6237DA44B29B |  | R22 | Non-TXV |  | 14.29% | 0.85714 | 27.45% | [5 empty] | Non-TXV | 14.29%
Morgan Hill | CA | 95037-3763 |  | 2014-07-31 | 2014-07-31 14:30 | 2014-08-01 07:45 | HEIL - CA5036VKB1 | 86 | 3.3 | Yes | Yes | 19.3 | 20.3 | -1 | 02E7913B891E4993BC997C6B4BA629DA |  | R22 | Non-TXV |  | 3.837% | 0.96163 | 7.374% | [5 empty] | Non-TXV | 3.837%
San Jose | CA | 95125-3981 |  | 2014-06-27 | 2014-06-27 10:33 | 2014-06-27 12:58 | TRANE - TTR060F100AD | 131 | 5.8 | Yes | Yes | 21.8 | 19.7 | 2.2 | 5BD9BA2C15D54C45BDDCBB0D59BCC769 |  | R22 | Non-TXV |  | 4.427% | 0.95573 | 8.509% | [5 empty] | Non-TXV | 4.427%
Bakersfield | CA | 93308-7002 |  | 2014-09-14 | 2014-09-14 19:36 | 2014-09-14 19:36 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 22.7 | 20.9 | 1.8 | 1FD0CB1ED4A4499696070147BA0FD689 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-2204 |  | 2014-09-16 | 2014-09-16 08:34 | 2014-09-16 08:41 | NORDYNE - UKN | 85 | 0 | Yes | Yes | 22 | 18.7 | 3.3 | FAFB7A91F27648C0893216825E200704 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9197 |  | 2014-09-24 | 2014-09-24 15:35 | 2014-09-24 15:35 | YORK - H3RCO60S06A | 144 | 0 | Yes | Yes | 20 | 22.5 | -2.5 | 735A4F64D5854AABBFBB5078510A2DD6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3135 |  | 2014-08-08 | 2014-08-08 13:06 | 2014-08-08 13:31 | GOODMAN - CK60-1C | 122 | 6.2 | Yes | Yes | 16.9 | 18.8 | -1.9 | C42519011F6640BFB8528DCC9D35EB81 |  | R22 | Non-TXV |  | 5.082% | 0.94918 | 9.766% | [5 empty] | Non-TXV | 5.082%
San Jose | CA | 95125-2018 |  | 2014-06-27 | 2014-06-27 08:47 | 2014-06-27 09:13 | COLEMAN - ERCS10181BBB | 73 | -5.2 | Yes | Yes | 18.5 | 19.9 | -1.4 | 1CE34D8A119E4E888DF3F0210A3AEC44 |  | R22 | Non-TXV |  | -7.123% | 1.0712 | 1.995% |  |  |  |  | Non-TXV |  |  | -7.123%
Esparto | CA | 95627-2059 |  | 2014-08-08 | 2014-08-08 11:26 | 2014-08-08 11:51 | GOODMAN - CKL36-1F | 71 | 4.3 | Yes | Yes | 22 | 19.3 | 2.7 | A6ADCC802F8F45429C95788D945E61C1 |  | R22 | Non-TXV |  | 6.056% | 0.93944 | 11.64% | [5 empty] | Non-TXV | 6.056%
Bakersfield | CA | 93306-3413 |  | 2014-06-25 | 2014-06-25 15:03 | 2014-06-25 15:03 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 22.9 | 19.4 | 3.5 | 1840DD4B333541B3B7671DC956FECE83 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-2407 |  | 2014-06-30 | 2014-06-30 10:10 | 2014-06-30 13:01 | DAY & NIGHT - 56X90036A000 | 84 | 8.1 | Yes | Yes | 20.4 | 19 | 1.4 | 62D225F001B849B0B2F168C58A84551A |  | R22 | Non-TXV |  | 9.643% | 0.90357 | 18.53% | [5 empty] | Non-TXV | 9.643%
Milpitas | CA | 95035-6508 |  | 2014-07-17 | 2014-07-17 10:47 | 2014-07-17 11:10 | RHEEM - 13AJA42A01 | 121 | -7.1 | Yes | Yes | 26.4 | 20.8 | 5.6 | 720296BCDF954D4581858517587A9801 |  | R22 | Non-TXV |  | -5.868% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.868%
Woodland | CA | 95695-5231 |  | 2014-07-15 | 2014-07-15 11:33 | 2014-07-15 22:21 | CARRIER - 48GS-048090311- | 35 | -8 | Yes | Yes | 14.5 | 17.3 | -2.8 | EAE8B2DDC9514DD2B40363F4C17025B5 |  | R22 | Non-TXV |  | -22.86% | 1.2286 | 6.401% |  |  |  |  | Non-TXV |  |  | -22.86%
Vallejo | CA | 94590-3548 |  | 2014-10-06 | 2014-10-06 14:23 | 2014-10-07 07:35 | - | 85 | 4.2 | Yes | Yes | 15.8 | 16.3 | -0.5 | 5ACB77E7C14C40CB9786E1D1EB069C4F |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Woodland | CA | 95695-5826 |  | 2014-07-10 | 2014-07-10 13:55 | 2014-07-10 18:42 | GE - BTX724A100A0 | 90 | 4.7 | Yes | Yes | 16.1 | 18.1 | -2 | A2A61AF51F244506B8B0B22FD88E0311 |  | R22 | Non-TXV |  | 5.222% | 0.94778 | 10.04% | [5 empty] | Non-TXV | 5.222%
Vacaville | CA | 95687-3410 |  | 2014-06-30 | 2014-06-30 12:04 | 2014-06-30 12:56 | AIRE-FLO - GCGD30S41S3A | 62 | 6.1 | Yes | Yes | 8.6 | 11.2 | -2.6 | 77FF4129D44847FD8A5133675500B20F |  | R410A | Non-TXV |  | 9.839% | 0.90161 | 18.91% | [5 empty] | Non-TXV | 9.839%
San Jose | CA | 95121-2904 |  | 2014-06-27 | 2014-06-27 14:54 | 2014-06-27 15:28 | TRANE - IWB724B1000 | 76 | 14 | Yes | Yes | 19.5 | 20.9 | -1.4 | 8A808DC8BFFD48ADB2340DF18DE4B863 |  | R22 | Non-TXV |  | 18.42% | 0.81579 | 35.4% | [5 empty] | Non-TXV | 18.42%
Suisun City | CA | 94585-6319 |  | 2014-09-12 | 2014-09-12 14:28 | 2014-09-12 14:47 | TRANE - 2TTM3060A1000AA | 74 | 3.9 | Yes | Yes | 20.9 | 21.5 | -0.6 | 6EDBE577201A43D49512B4D374A4F69F |  | R22 | Non-TXV |  | 5.27% | 0.9473 | 10.13% | [5 empty] | Non-TXV | 5.27%
Wasco | CA | 93280-3002 |  | 2014-08-16 | 2014-08-16 17:08 | 2014-08-16 17:10 | RHEEM - RRNAB024JK06X | 70 | -4 | Yes | Yes | 23.4 | 20.9 | 2.5 | E87BFB6502844EBB9028190A9C6BDDAE |  | R22 | TXV |  | -5.714% | 1.0571 | 1.6% |  |  |  |  | TXV |  |  | -5.714%
Bakersfield | CA | 93304-3716 |  | 2014-06-25 | 2014-06-25 11:45 | 2014-06-25 11:45 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 22 | 19.3 | 2.7 | CE4B55AF754B4C2E83BAAEF07B39E82F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4648 |  | 2014-10-28 | 2014-10-28 10:12 | 2014-10-28 10:12 | HEIL - PGC030K060A | 85 | 0 | Yes | Yes | 27 | 21 | 6 | AD57652086BE4A14B8F0BD545663CC09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-3647 |  | 2014-07-23 | 2014-07-23 09:03 | 2014-07-23 09:44 | PAYNE - PA10JA42 | 83 | 5.2 | Yes | Yes | 19 | 19.3 | -0.3 | ED72203517CC48319DE0C401030043E3 |  | R22 | Non-TXV |  | 6.265% | 0.93735 | 12.04% | [5 empty] | Non-TXV | 6.265%
Vallejo | CA | 94591-4312 |  | 2014-07-31 | 2014-07-31 11:02 | 2014-07-31 11:52 | TRANE - 11NO24C100A0 | 102 | 4.7 | Yes | Yes | 20.6 | 18.8 | 1.8 | E44081333BF64D0C9088BB19C3180DA7 |  | R22 | Non-TXV |  | 4.608% | 0.95392 | 8.855% | [5 empty] | Non-TXV | 4.608%
Woodland | CA | 95695-4310 |  | 2014-09-09 | 2014-09-09 11:23 | 2014-09-09 11:38 | CARRIER - 38TR036300 | 132 | 4 | Yes | Yes | 17.5 | 19.9 | -2.4 | 022B870BA03F4FD4A2AA21F024D19E36 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Bakersfield | CA | 93309-5613 |  | 2014-07-23 | 2014-07-23 09:58 | 2014-07-23 09:58 | WESTINGHOUSE - JE030BAA0N | 86 | 0 | Yes | Yes | 18.1 | 20.4 | -2.3 | 7FCF6150FD1349FAB82BBA615ABF9BB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2662 |  | 2014-09-06 | 2014-09-06 18:51 | 2014-09-06 18:53 | OTHER - N/A | 83 | 2.7 | Yes | Yes | 24.2 | 20.4 | 3.8 | 95004A0B23934BA2ADFE0DB451713A84 |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Suisun City | CA | 94585-2631 |  | 2014-08-01 | 2014-08-01 10:24 | 2014-08-01 13:55 | TRANE - TTB030C100A1 | 70 | -6.6 | Yes | Yes | 16 | 17.8 | -1.8 | 9F943E9B6CE04A61873792D8C5D9CF9A |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Bakersfield | CA | 93304-6429 |  | 2014-07-10 | 2014-07-10 14:56 | 2014-07-10 14:56 | ICP - PGC036K060B | 71 | 0 | Yes | Yes | 24.9 | 22.6 | 2.4 | 0AD047A26D36487EB2D07B92B9605891 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2631 |  | 2014-08-01 | 2014-08-01 12:36 | 2014-08-01 13:55 | TRANE - TTB030C100A1 | 70 | 5.4 | Yes | Yes | 15.8 | 18.2 | -2.4 | E5ACDEF0C5CC4A95B255795ABEF7171E |  | R22 | Non-TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | Non-TXV | 7.714%
Woodland | CA | 95695-5240 |  | 2014-07-09 | 2014-07-09 13:24 | 2014-07-09 16:03 | PAYNE - PA13NA036-C | 70 | 7.5 | Yes | Yes | 9.6 | 11.7 | -2.1 | BA8D2F799C2546CE9DDE4A2F119592F5 |  | R410A | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Vacaville | CA | 95688-8578 |  | 2014-10-22 | 2014-10-22 12:29 | 2014-10-22 12:54 | CARRIER - CK0370301200 | 85 | 3.8 | Yes | Yes | 19 | 20.4 | -1.4 | D4719CA97F81421AB59EF6B77B1B1E07 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Bakersfield | CA | 93309-7662 |  | 2014-07-23 | 2014-07-23 10:11 | 2014-07-23 10:31 | OTHER - 2.5D6012 | 100 | 7.5 | Yes | Yes | 20.8 | 23.4 | -2.6 | EBCC50E2AF374193B4F036C83BBF981B |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Bakersfield | CA | 93309-1213 |  | 2014-09-10 | 2014-09-10 13:36 | 2014-09-10 13:36 | BDP - 588ANW060080AAAG | 112 | 0 | Yes | Yes | 20.4 | 20.1 | 0.3 | BC26EA981BC44474B1051AE408966CC6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4237 |  | 2014-07-02 | 2014-07-02 09:36 | 2014-07-02 21:33 | - 6661AJ024-B | 93 | -8.8 | Yes | Yes | 20.9 | 19 | 1.9 | 79991BE321E948E494D5F5CD23ACF24E |  | R22 | Non-TXV |  | -9.462% | 1.0946 | 2.65% |  |  |  |  | Non-TXV |  |  | -9.462%
Bakersfield | CA | 93304-6330 |  | 2014-07-10 | 2014-07-10 10:02 | 2014-07-10 10:02 | TRANE - YCX042G1M0AB | 128 | 0 | Yes | Yes | 20.1 | 20.2 | -0.1 | 535FEB6C88F747FF8ECE3F92882467F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3652 |  | 2014-10-23 | 2014-10-23 13:26 | 2014-10-23 13:26 | BDP - 585GJW030040ABAF | 58 | 0 | Yes | Yes | 17.7 | 18.1 | -0.4 | 3A6F8A483F8149909A52AE84BC213BF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3741 |  | 2014-09-16 | 2014-09-16 09:58 | 2014-09-16 10:00 | RUUD - UAKA-060JAZ | 112 | -6.6 | Yes | Yes | 20.2 | 19.9 | 0.3 | 068AFDD270144763959FA96CF6917FC7 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Arvin | CA | 93203-9751 |  | 2014-11-07 | 2014-11-07 13:32 | 2014-11-07 13:54 | YORK - D1WA030N05606B | 72 | 3.4 | Yes | Yes | 18.7 | 20.6 | -1.8 | EA49EB82B670487FB92EA14C9D3B17BF |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
Vacaville | CA | 95688-4517 |  | 2014-07-10 | 2014-07-10 10:06 | 2014-07-10 10:35 | BRYANT - 561CJ060-A | 151 | -8.9 | Yes | Yes | 14.9 | 16.8 | -1.9 | D942535BEC5C49CE8A2B21D532BD4564 |  | R22 | Non-TXV |  | -5.894% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.894%
Pittsburg | CA | 94565-2120 |  | 2014-09-10 | 2014-09-10 14:16 | 2014-09-10 14:37 | CARRIER - 38CM048300 | 137 | -9.5 | Yes | Yes | 27.2 | 21.9 | 5.3 | C0E112E0816A4823B5FF82E198CC4331 |  | R22 | TXV |  | -6.934% | 1.0693 | 1.942% |  |  |  |  | TXV |  |  | -6.934%
Bakersfield | CA | 93304-1558 |  | 2014-08-28 | 2014-08-28 19:48 | 2014-08-28 19:48 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 19.3 | 21 | -1.7 | 7DB4CA1DAD464E0180B724386DB11A70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1621 |  | 2014-08-17 | 2014-08-17 18:24 | 2014-08-17 18:26 | HEIL - PGME36G0907 | 100 | 6.3 | Yes | Yes | 23.4 | 22 | 1.4 | 1B627B1B61D9457EB30F044F52D0A08E |  | R22 | Non-TXV |  | 6.3% | 0.937 | 12.11% | [5 empty] | Non-TXV | 6.3%
Vacaville | CA | 95688-2603 |  | 2014-07-11 | 2014-07-11 09:06 | 2014-07-11 09:41 | HEIL - TTR030C100A2 | 90 | 4 | Yes | Yes | 14.5 | 17.4 | -2.9 | 2B54F995AC6741AABFDD1337A7ADAA48 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Bakersfield | CA | 93304-1560 |  | 2014-08-28 | 2014-08-28 19:43 | 2014-08-28 19:43 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 21 | 22 | -1 | B190E7E6997A486EA5DE34BFEAB10A6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2621 |  | 2014-06-30 | 2014-06-30 11:36 | 2014-06-30 11:36 | - HASE-F036SA | 85 | 0 | Yes | Yes | 19.9 | 16.8 | 3.1 | 7BDBF72CF0EF4AB7B40708411569D3FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4645 |  | 2014-10-27 | 2014-10-27 09:45 | 2014-10-27 09:45 | CARRIER - 48GSN036060301 | 62 | 0 | Yes | Yes | 26.1 | 21 | 5.1 | 1F97D1912A0E4AE5AEF4F519427E8B60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1537 |  | 2014-11-07 | 2014-11-07 11:10 | 2014-11-07 11:10 | OTHER - UNK | 93 | 0 | Yes | Yes | 21.2 | 23.7 | -2.5 | 5506509D7EE34B90A3F4CF38461CBBFC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5111 |  | 2014-07-18 | 2014-07-18 08:50 | 2014-07-18 08:50 | NORDYNE - FS3BA-030KA | 68 | 0 | Yes | Yes | 20.7 | 18.8 | 1.9 | 54ED41F0F58649E6B7217B7A9AE62DB8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dublin | CA | 94568-1547 |  | 2014-06-26 | 2014-06-26 12:11 | 2014-06-26 12:32 | TRANE - BTD48A1000 | 152 | -14.3 | Yes | Yes | 25.5 | 20.3 | 5.2 | CBC4BD9E6B70484E8CEFC4B2D6ED6E90 |  | R22 | Non-TXV |  | -9.408% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.408%
Fairfield | CA | 94533-1409 |  | 2014-10-09 | 2014-10-09 10:08 | 2014-10-10 08:36 | PAYNE - 597ANX036000AAAA | 135 | 5.5 | Yes | Yes | 13.2 | 16.1 | -2.9 | CCA4451E53BC43F5811F59C61809807D |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Woodland | CA | 95695-0000 |  | 2014-07-15 | 2014-07-15 09:11 | 2014-07-15 22:18 | CARRIER - 50YQ024300 | 84 | -7.9 | Yes | Yes | 15.4 | 18.1 | -2.7 | 73DE09DC5DB740399124340CF493DAD1 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Vacaville | CA | 95687-3416 |  | 2014-07-03 | 2014-07-03 13:15 | 2014-07-03 15:04 | LENNOX - HS20261 | 57 | -3.4 | Yes | Yes | 22.9 | 19.4 | 3.5 | FD920FBA08E347F2AE0959CBFAABB369 |  | R22 | Non-TXV |  | -5.965% | 1.0596 | 1.67% |  |  |  |  | Non-TXV |  |  | -5.965%
Bakersfield | CA | 93308-2239 |  | 2014-07-28 | 2014-07-28 09:15 | 2014-07-28 09:15 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 25 | 22.1 | 3 | E6A82D8698FB481BBDE88A2F6C8145BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1567 |  | 2014-08-26 | 2014-08-26 18:35 | 2014-08-26 18:51 | CARRIER - 38YCC018341 | 66 | 8.3 | Yes | Yes | 21.2 | 21.5 | -0.3 | C4119C10CB94442784D5A6CDAD1718D3 |  | R22 | Non-TXV |  | 12.58% | 0.87424 | 24.17% | [5 empty] | Non-TXV | 12.58%
Wasco | CA | 93280-1530 |  | 2014-08-17 | 2014-08-17 17:41 | 2014-08-17 17:44 | TEMPSTAR - PGAD42D1K5 | 180 | -16.9 | Yes | Yes | 20.6 | 19.8 | 0.8 | D1EF9412B6644B479AC958E17D5DF44D |  | R22 | Non-TXV |  | -9.389% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.389%
San Jose | CA | 95135-1223 |  | 2014-09-16 | 2014-09-16 09:07 | 2014-09-16 09:12 | BRYANT - 561CJ036-E | 95 | 3.8 | Yes | Yes | 19.2 | 18.5 | 0.7 | D8E029B7658C4CFB99AA27328BA8B711 |  | R22 | TXV |  | 4% | 0.96 | 7.687% | [5 empty] | TXV | 4%
Bakersfield | CA | 93309-6385 |  | 2014-06-27 | 2014-06-27 12:05 | 2014-06-27 12:05 | GOODMAN - GPG13360451AC | 112 | 0 | Yes | Yes | 24.1 | 18.2 | 5.9 | 37FB9AE123C0442091746C439134259B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2624 |  | 2014-08-18 | 2014-08-18 16:05 | 2014-08-18 17:43 | GE - BTB836A100C0 | 76 | 4.4 | Yes | Yes | 21.4 | 19.6 | 1.8 | 3A2D08A8364B40ACA41EBC3B21C5FE8C |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Bakersfield | CA | 93306-4038 |  | 2014-06-25 | 2014-06-25 12:52 | 2014-06-25 12:52 | CARRIER - 48GXN048090311 | 131 | 0 | Yes | Yes | 27.9 | 22.1 | 5.8 | 35254609F34E41E3A9368510020BE8F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4717 |  | 2014-07-07 | 2014-07-07 09:45 | 2014-07-07 09:45 | BRYANT - 563CN036-C | 104 | 0 | Yes | Yes | 23 | 21 | 2 | 1A2318B69B2B4E63A7615CBA76D81A93 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95118-1043 |  | 2014-06-27 | 2014-06-27 13:25 | 2014-06-27 14:02 | ARMSTRONG - SCU10E36 | 80 | -4.7 | Yes | Yes | 25.8 | 20.2 | 5.7 | 799F3C9FC8C94C57A53F2186F487AC64 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Lamont | CA | 93241-1101 |  | 2014-10-30 | 2014-10-30 17:02 | 2014-10-30 17:19 | YORK - XY874268HN9O | 85 | 10 | Yes | Yes | 17.8 | 20.4 | -2.6 | 7EFC609F3642493293474DB947CCD7A1 |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
San Jose | CA | 95117-2145 |  | 2014-09-16 | 2014-09-16 11:08 | 2014-09-16 11:32 | WESTINGHOUSE - UKN | 85 | 2.5 | Yes | Yes | 19.1 | 18.3 | 0.8 | 2987B8571960436FBCB8268C7051C5FC |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Woodland | CA | 95695-5825 |  | 2014-07-09 | 2014-07-09 10:55 | 2014-07-09 12:24 | TRANE - B1X730A100A0 | 106 | -10 | Yes | Yes | 13.7 | 16.6 | -2.9 | 438ABF56BD1246F9BF17B5D781E4E0BC |  | R22 | Non-TXV |  | -9.434% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.434%
Davis | CA | 95618-7132 |  | 2014-07-14 | 2014-07-14 09:50 | 2014-07-14 22:09 | CARRIER - 38BRC036300 | 122 | 5.3 | Yes | Yes | 22.4 | 17.1 | 5.3 | F94AD9F7775149DBB14261433EEFBC4D |  | R22 | Non-TXV |  | 4.344% | 0.95656 | 8.349% | [5 empty] | Non-TXV | 4.344%
San Jose | CA | 95125-4461 |  | 2014-07-14 | 2014-07-14 10:19 | 2014-07-14 11:03 | TRANE - 2TTB00060A10000AAA | 126 | 6.7 | Yes | Yes | 19.2 | 19.8 | -0.6 | 6829B119536445A783BDFE8C4A4E6365 |  | R22 | Non-TXV |  | 5.317% | 0.94683 | 10.22% | [5 empty] | Non-TXV | 5.317%
San Jose | CA | 95125-4461 |  | 2014-07-14 | 2014-07-14 10:27 | 2014-07-14 11:02 | TRANE - 2TTB0060A10000AA | 126 | -7.4 | Yes | Yes | 23.4 | 20.4 | 3 | 39FF3A51629E4EEA9E0C1A3177F7161D |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Bakersfield | CA | 93307-3041 |  | 2014-09-29 | 2014-09-29 11:53 | 2014-09-29 11:53 | PAYNE - PY1PNBO42060AAAA | 102 | 0 | Yes | Yes | 18.8 | 21.5 | -2.7 | A577F97D559048909ECC861C71365941 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5868 |  | 2014-07-01 | 2014-07-01 09:12 | 2014-07-01 13:33 | BRYANT - 561CJ060-A | 134 | -12.6 | Yes | Yes | 22.4 | 17.7 | 4.7 | 1A48031AE9F040578A934E96920E3912 |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Bakersfield | CA | 93304-5752 |  | 2014-07-15 | 2014-07-15 13:08 | 2014-07-15 13:08 | NORDYNE - GR8GD-03 | 85 | 0 | Yes | Yes | 21.8 | 17.1 | 4.7 | 79778F8C4154492CB4ABB16C028D6D3A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1511 |  | 2014-07-17 | 2014-07-17 11:25 | 2014-07-17 22:15 | CARRIER - 38CK030330 | 68 | 2.3 | Yes | Yes | 15.2 | 18.2 | -3 | 9EA0B873A5154DE2A2B5E041A48B4156 |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
San Jose | CA | 95120-2811 |  | 2014-06-30 | 2014-06-30 13:05 | 2014-06-30 13:21 | CARRIER - 38CKC04830 | 100 | 5.3 | Yes | Yes | 26.8 | 21.5 | 5.3 | 5CB506CFE21C43E0B0D03F5AB2F39C4D |  | R22 | TXV |  | 5.3% | 0.947 | 10.19% | [5 empty] | TXV | 5.3%
Davis | CA | 95616-1337 |  | 2014-07-11 | 2014-07-11 09:24 | 2014-07-11 19:50 | BRYANT - 113ANA030-E | 74 | -8.7 | Yes | Yes | 16.7 | 19.3 | -2.6 | A6B53496A7534CEBAE1A5362717A1CC9 |  | R22 | Non-TXV |  | -11.76% | 1.1176 | 3.292% |  |  |  |  | Non-TXV |  |  | -11.76%
Vacaville | CA | 95687-5702 |  | 2014-08-05 | 2014-08-05 12:02 | 2014-08-05 12:02 | TRANE - 4TTX4030B1000AA | 79 | 0 | Yes | Yes | 17.7 | 17.9 | -0.2 | 26DFE6AC24F041D4A35E48E9ADEA92D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-9586 |  | 2014-08-04 | 2014-08-04 10:09 | 2014-08-04 10:37 | OTHER - CA30420KA1 | 84 | -5.9 | Yes | Yes | 20.4 | 19.1 | 1.3 | F3414FCA8DBC42D9876C075541FD8761 |  | R22 | Non-TXV |  | -7.024% | 1.0702 | 1.967% |  |  |  |  | Non-TXV |  |  | -7.024%
Bakersfield | CA | 93306-7910 |  | 2014-07-22 | 2014-07-22 09:53 | 2014-07-22 09:53 | WEATHER KING - 13AJA42AD1 | 121 | 0 | Yes | Yes | 20 | 16.4 | 3.6 | 77918E076E244430B81CCA104E3B39EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3521 |  | 2014-07-31 | 2014-07-31 10:09 | 2014-07-31 20:54 | UNITARY PRODUCTS GROUP - BRCS0421BD | 84 | 3.2 | Yes | Yes | 15.1 | 17.6 | -2.5 | 171B664E097143699433574B8E5F12CD |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
San Jose | CA | 95123-4938 |  | 2014-07-01 | 2014-07-01 08:51 | 2014-07-01 09:21 | TRANE - 4TTB3036D1000 | 105 | 5.7 | Yes | Yes | 21.9 | 19.7 | 2.3 | 0E688AC924A24B98AE527DBD2A8B7DBB |  | R410A | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Dixon | CA | 95620-2021 |  | 2014-07-29 | 2014-07-29 11:52 | 2014-07-29 12:09 | CARRIER - 38TH042330 | 96 | 4.5 | Yes | Yes | 20.1 | 19.9 | 0.2 | 24DD94C288FA43F880D094A80DBF5C1F |  | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Lemoore | CA | 93245-1714 |  | 2014-08-04 | 2014-08-04 17:07 | 2014-08-04 22:16 | RHEEM - RARL060JEZ | 220 | 11.2 | Yes | Yes | 21 | 20.4 | 0.6 | B002A148086F4AB6B8C8375267EC433C |  | R410A | Non-TXV |  | 5.091% | 0.94909 | 9.784% | [5 empty] | Non-TXV | 5.091%
Bakersfield | CA | 93306-6731 |  | 2014-08-05 | 2014-08-05 10:33 | 2014-08-05 10:33 | RHEEM - RRNL-B036JK06X | 189 | 0 | Yes | Yes | 24.1 | 18.3 | 5.8 | ADFA1FAD70D843228309BD4CF29C7925 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-5526 |  | 2014-06-30 | 2014-06-30 14:03 | 2014-06-30 14:29 | CARRIER - 561AJ048 | 110 | 28.5 | Yes | Yes | 19 | 21.5 | -2.5 | B414D0DFDBAE4E1BAB416DDCD3484AD9 |  | R22 | Non-TXV |  | 25.91% | 0.74091 | 49.79% | [5 empty] | Non-TXV | 25.91%
Rio Vista | CA | 94571-9787 |  | 2014-08-21 | 2014-08-21 13:56 | 2014-08-21 16:14 | CARRIER - H2RC024S06A | 71 | 4 | Yes | Yes | 21.3 | 20.4 | 0.9 | A78E0EA90139412CA62058405C9AAFCE |  | R22 | Non-TXV |  | 5.634% | 0.94366 | 10.83% | [5 empty] | Non-TXV | 5.634%
Davis | CA | 95618-7120 |  | 2014-08-26 | 2014-08-26 10:45 | 2014-08-26 10:45 | GMC - | 91 | 0 | Yes | Yes | 23.3 | 21.8 | 1.6 | 295C9D5A24304B1EB1F3A418EA22FC38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2126 |  | 2014-07-30 | 2014-07-30 11:39 | 2014-07-30 11:58 | CARRIER - 48GX036090301AD | 83 | 4.2 | Yes | Yes | 23.5 | 20.1 | 3.4 | FE2BFE6FD6CD4914AEF3C0970D5A1D24 |  | R22 | Non-TXV |  | 5.06% | 0.9494 | 9.725% | [5 empty] | Non-TXV | 5.06%
San Jose | CA | 95123-6405 |  | 2014-06-30 | 2014-06-30 14:33 | 2014-06-30 14:59 | GIBSON - GS3BA036KA | 69 | 2.8 | Yes | Yes | 23.8 | 20.2 | 3.7 | 9D06821B69DE4D589164F5A66AFA15C8 |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Bakersfield | CA | 93307-4355 |  | 2014-07-24 | 2014-07-24 14:04 | 2014-07-24 14:04 | ICP - GPCM030K060D | 53 | 0 | Yes | Yes | 18.2 | 19.8 | -1.6 | C8156DA48BBD4C22A51DA32B5B201B97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3405 |  | 2014-08-26 | 2014-08-26 14:51 | 2014-08-26 14:51 | CARRIER - 485X-042060321AA | 91.2 | 0 | Yes | Yes | 19.5 | 21.8 | -2.3 | 6213AA31C25F4CEE8F28BE1DFE43DF06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6577 |  | 2014-06-27 | 2014-06-27 14:45 | 2014-06-27 14:45 | OTHER - UKN | 90 | 0 | Yes | Yes | 23.1 | 20.6 | 2.5 | E753DCA7C4C04752BDAA69F135DEB4F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4431 |  | 2014-07-29 | 2014-07-29 13:09 | 2014-07-29 14:58 | PAYNE - PA13NR030-A | 87 | -6.1 | Yes | Yes | 19.8 | 16.9 | 2.9 | E78C867EA9FD4AB782140941E7861C7E |  | R22 | Non-TXV |  | -7.011% | 1.0701 | 1.964% |  |  |  |  | Non-TXV |  |  | -7.011%
Rio Vista | CA | 94571-2147 |  | 2014-08-25 | 2014-08-25 10:38 | 2014-08-25 11:50 | YORK - H2RCO24S06A | 71 | 3.7 | Yes | Yes | 18.9 | 18.5 | 0.4 | 79C90214C3FF48149014AA2A1A5C45F8 |  | R22 | Non-TXV |  | 5.211% | 0.94789 | 10.01% | [5 empty] | Non-TXV | 5.211%
Arvin | CA | 93203-2507 |  | 2014-11-05 | 2014-11-05 17:58 | 2014-11-05 18:02 | GOODMAN - GPG133000451AA | 85 | 3.2 | Yes | Yes | 19.5 | 22.3 | -2.8 | 5129E9746E54409BA40C48D5F72990A7 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Arvin | CA | 93203-2507 |  | 2014-11-05 | 2014-11-05 18:03 | 2014-11-05 18:20 | GOODMAN - GPG133000451AA | 85 | 3.7 | Yes | Yes | 20 | 22.4 | -2.4 | 6C8BC74CA3104AA2A39DA842A5FC3F55 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Bakersfield | CA | 93306-4508 |  | 2014-09-10 | 2014-09-10 12:42 | 2014-09-10 12:42 | DAY & NIGHT - PGD32404K001C1 | 72 | 0 | Yes | Yes | 24.2 | 20.2 | 4.1 | B89842027F1D47AF81C9555E38BAC716 |  | R410A | TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3746 |  | 2014-08-04 | 2014-08-04 12:48 | 2014-08-04 13:14 | RHEEM - RACB-042JAQ | 37 | 3.9 | Yes | Yes | 15.8 | 18.6 | -2.8 | 4B45F097D7DC4E41B0CA33687ADCE9E8 |  | R22 | Non-TXV |  | 10.54% | 0.89459 | 20.26% | [5 empty] | Non-TXV | 10.54%
San Jose | CA | 95135-2211 |  | 2014-07-14 | 2014-07-14 13:33 | 2014-07-14 14:03 | CARRIER - 38CKC043300 | 80 | 10.2 | Yes | Yes | 18.8 | 20.7 | -1.8 | 93C5B606B9A4413784FCF9B315D75320 |  | R22 | Non-TXV |  | 12.75% | 0.8725 | 24.5% | [5 empty] | Non-TXV | 12.75%
Vallejo | CA | 94589-2177 |  | 2014-08-07 | 2014-08-07 12:13 | 2014-08-07 22:10 | BDP - | 85 | 3 | Yes | Yes | 14.2 | 17.2 | -3 | EBC58E0BDC104B2EB5965CEAC89B9423 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Wasco | CA | 93280-1618 |  | 2014-07-28 | 2014-07-28 14:07 | 2014-07-28 14:12 | GOODMAN - GPG1360090M41CA | 91 | 3.3 | Yes | Yes | 22.2 | 20.4 | 1.8 | 88D46FB2F4974B6EA1189127A48E44BA |  | R410A | Non-TXV |  | 3.626% | 0.96374 | 6.969% | [5 empty] | Non-TXV | 3.626%
Suisun City | CA | 94585-3733 |  | 2014-08-01 | 2014-08-01 13:14 | 2014-08-01 13:14 | - | 85 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | 2AAFA9BFA24046568A418ED148B2EA78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2601 |  | 2014-07-17 | 2014-07-17 12:47 | 2014-07-17 13:37 | RHEEM - RRNA-B030JK00X | 72 | 6.3 | Yes | Yes | 11.2 | 13.6 | -2.4 | A2B52371AC99418D8CAE04BFD5F57698 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Wasco | CA | 93280-2507 |  | 2014-11-05 | 2014-11-05 13:15 | 2014-11-05 13:15 | GOODMAN - PGB0360751A | 60 | 0 | Yes | Yes | 22.7 | 19.5 | 3.2 | 4DF8336DA1F7430391E01B000A8C00BB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2557 |  | 2014-08-02 | 2014-08-02 18:42 | 2014-08-02 18:45 | YORK - H2RA036S060 | 63 | 4.3 | Yes | Yes | 23.1 | 22 | 1.1 | 8D800AAE82C24E81B89E2D4B604ABC9B |  | R22 | Non-TXV |  | 6.825% | 0.93175 | 13.12% | [5 empty] | Non-TXV | 6.825%
Bakersfield | CA | 93307-1418 |  | 2014-08-11 | 2014-08-11 12:58 | 2014-08-11 12:58 | UNITARY PRODUCTS GROUP - DBYP-030N070A | 73 | 0 | Yes | Yes | 24.6 | 18.8 | 5.8 | 02B88D4BC3DE46E8B095B3915847C998 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-6633 |  | 2014-07-30 | 2014-07-30 09:01 | 2014-07-30 09:33 | CARRIER - 38CKC042 | 85 | -6 | Yes | Yes | 22.1 | 19.3 | 2.8 | 31C9258A4EDE4770839EB7342FF131A8 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
San Jose | CA | 95132-2605 |  | 2014-09-15 | 2014-09-15 10:08 | 2014-09-15 10:30 | FRIGIDAIRE - FS3BA-036KA | 69 | 2.1 | Yes | Yes | 20.3 | 18.2 | 2.1 | 6646A57BA114498D8730DD1F2F50A8DB |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Lemoore | CA | 93245-3478 |  | 2014-07-31 | 2014-07-31 09:06 | 2014-07-31 09:37 | YORK - TCGD24S21S2A | 76 | 4 | Yes | Yes | 23.2 | 21.4 | 1.8 | D16621E1B6CE47BA87EA83380D9DB691 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Woodland | CA | 95776-4261 |  | 2014-07-09 | 2014-07-09 12:48 | 2014-07-09 13:31 | GE - BTB930A100A0 | 55 | 5.7 | Yes | Yes | 14.5 | 17.2 | -2.7 | 6D389B6FCEB9427797719F5886FC3DE4 |  | R22 | Non-TXV |  | 10.36% | 0.89636 | 19.92% | [5 empty] | Non-TXV | 10.36%
Bakersfield | CA | 93311-1875 |  | 2014-08-14 | 2014-08-14 10:47 | 2014-08-14 10:47 | UNITARY PRODUCTS GROUP - AC036X1222A | 83 | 0 | Yes | Yes | 22.9 | 19 | 3.9 | A24FFC55167642798A4DF5DF0BF7EE34 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-3045 |  | 2014-07-01 | 2014-07-01 12:10 | 2014-07-01 12:31 | GOODMAN - CRT361A | 140 | 9.4 | Yes | Yes | 21.9 | 19.4 | 2.5 | 0F2DCD491E134A78913296DEC6F14CB5 |  | R22 | Non-TXV |  | 6.714% | 0.93286 | 12.9% | [5 empty] | Non-TXV | 6.714%
Bakersfield | CA | 93313-4572 |  | 2014-08-29 | 2014-08-29 11:00 | 2014-08-29 11:00 | UNITARY PRODUCTS GROUP - ACO42X1221A | 107 | 0 | Yes | Yes | 18 | 20.2 | -2.2 | A5E5361BA42F43ADBA9F7765DCE048E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2013 |  | 2014-10-30 | 2014-10-30 04:55 | 2014-10-30 05:13 | ICP - PGAD48D1KE | 85 | 18.6 | Yes | Yes | 17.2 | 20.1 | -2.9 | 23B9D26F79CB48D0B4D8925401FF3D11 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 36°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.88% | 0.78118 | 42.05% | [5 empty] | Non-TXV | 21.88%
Bakersfield | CA | 93312-5964 |  | 2014-08-15 | 2014-08-15 12:48 | 2014-08-15 12:48 | UNITARY PRODUCTS GROUP - AC042X1221A | 107 | 0 | Yes | Yes | 19.4 | 18.4 | 1 | AD31CC8232CE4303BDF0EA2BE1DA635D |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-1723 |  | 2014-07-17 | 2014-07-17 16:07 | 2014-07-17 17:28 | AMANA - APG1330070M41AA | 81 | 6.5 | Yes | Yes | 18.3 | 19.9 | -1.6 | 6F4A7288055E49CA96A02F98D65734EA |  | R22 | Non-TXV |  | 8.025% | 0.91975 | 15.42% | [5 empty] | Non-TXV | 8.025%
Bakersfield | CA | 93306-2368 |  | 2014-06-30 | 2014-06-30 14:17 | 2014-06-30 14:17 | RUUD - UKN | 90 | 0 | Yes | Yes | 23.9 | 21.5 | 2.4 | BFFC39D7861340F1A955A3553E4A22DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6117 |  | 2014-08-13 | 2014-08-13 15:02 | 2014-08-13 20:49 | AMERICAN STANDARD - 4A7B3036D1000AA | 105 | -8.6 | Yes | Yes | 17.2 | 17.7 | -0.5 | F29664813F054979A0BD9BBA1D66517D |  | R410A | Non-TXV |  | -8.19% | 1.0819 | 2.294% |  |  |  |  | Non-TXV |  |  | -8.19%
Bakersfield | CA | 93314-4261 |  | 2014-09-03 | 2014-09-03 12:38 | 2014-09-03 12:38 | OTHER - PA13NR048 | 142 | 0 | Yes | Yes | 20 | 21 | -1 | BA2D7EA94BEB427B8D53347A32D9E30F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-2819 |  | 2014-09-17 | 2014-09-17 09:21 | 2014-09-17 09:36 | CARRIER - 4ABB336W310 | 83 | 10.8 | Yes | Yes | 18.9 | 17.7 | 1.2 | 2CD72061DEF246268A9F73F9521B2BE1 |  | R410A | Non-TXV |  | 13.01% | 0.86988 | 25.01% | [5 empty] | Non-TXV | 13.01%
San Jose | CA | 95124-4820 |  | 2014-07-23 | 2014-07-23 13:01 | 2014-07-23 13:35 | CARRIER - 38CKC024 | 57 | 4.5 | Yes | Yes | 21.3 | 19.4 | 1.9 | 21C6DA3F8C8C4606B4577EDB4E310D0E |  | R22 | Non-TXV |  | 7.895% | 0.92105 | 15.17% | [5 empty] | Non-TXV | 7.895%
W Sacramento | CA | 95691-3942 |  | 2014-07-29 | 2014-07-29 22:18 | 2014-07-29 22:35 | PAYNE - | 98 | 6 | Yes | Yes | 16.3 | 18.7 | -2.4 | B4295DD7CA7D438CB572ED9355DB64B4 |  | R22 | Non-TXV |  | 6.122% | 0.93878 | 11.77% | [5 empty] | Non-TXV | 6.122%
Bakersfield | CA | 93304-4113 |  | 2014-07-10 | 2014-07-10 13:25 | 2014-07-10 13:25 | ICP - PGF336060K01A1 | 85 | 0 | Yes | Yes | 18.7 | 21.7 | -3 | 3BEEB48EB9A540FFAF9FF0D79B6C3536 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7116 |  | 2014-07-23 | 2014-07-23 16:21 | 2014-07-23 16:21 | PAYNE - PYPJB048090AAAA | 91 | 0 | Yes | Yes | 21.7 | 20.6 | 1.2 | 5577EA21D30E403C94E94395EF14BF20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7116 |  | 2014-07-24 | 2014-07-24 15:23 | 2014-07-24 15:23 | ICP - PGN348090K00A1 | 196 | 0 | Yes | Yes | 19.7 | 21.4 | -1.7 | 6DDBD9B1607340E284ED9CEFEA9D2ABF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1758 |  | 2014-09-17 | 2014-09-17 08:43 | 2014-09-17 08:43 | BRYANT - 561CJ036-F | 70 | 0 | Yes | Yes | 19.7 | 17.7 | 2 | 026BF48A21544CBFAE167284DBB6EA04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9193 |  | 2014-07-23 | 2014-07-23 12:59 | 2014-07-23 12:59 | YORK - AC048X1222G | 119 | 0 | Yes | Yes | 18.1 | 20.7 | -2.6 | 572D4398AAC949C29F36AB8692BAF431 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9193 |  | 2014-07-23 | 2014-07-23 13:15 | 2014-07-23 13:37 | YORK - AC036X1222A | 83 | 5.6 | Yes | Yes | 21 | 21.4 | -0.4 | 36842060A2FB4BF9A19A8706EF0CE892 |  | R22 | Non-TXV |  | 6.747% | 0.93253 | 12.97% | [5 empty] | Non-TXV | 6.747%
San Jose | CA | 95148-2224 |  | 2014-07-23 | 2014-07-23 13:41 | 2014-07-23 14:01 | NORDYNE - FS3BA042KA | 87 | 14.1 | Yes | Yes | 21.4 | 21 | 0.4 | 1D7A0788C4DE446E8C72B190BF44C0FA |  | R22 | Non-TXV |  | 16.21% | 0.83793 | 31.15% | [5 empty] | Non-TXV | 16.21%
San Jose | CA | 95124-4751 |  | 2014-07-08 | 2014-07-08 14:23 | 2014-07-08 14:23 | CARRIER - 38CKC036030 | 74 | 0 | Yes | Yes | 24.9 | 21.8 | 3.2 | CD31EBABDAC44045BB88676598AD991D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8504 |  | 2014-10-06 | 2014-10-06 13:29 | 2014-10-07 07:32 | KENMORE - CA5548VKC1 | 85 | 9.5 | Yes | Yes | 14.9 | 16.3 | -1.4 | ED9365C87EBA46DE8B4AABAFB0720CE6 |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
San Jose | CA | 95124-3156 |  | 2014-07-01 | 2014-07-01 09:32 | 2014-07-01 12:00 | ALLEGIANCE - 7A2042Z1000 | 134 | 5.6 | Yes | Yes | 19.9 | 19.1 | 0.8 | A6451D82D3C648E4BF862CA8D26FE939 |  | R22 | Non-TXV |  | 4.179% | 0.95821 | 8.031% | [5 empty] | Non-TXV | 4.179%
Fairfield | CA | 94533-6180 |  | 2014-07-18 | 2014-07-18 09:27 | 2014-07-18 09:27 | - | 85 | 0 | Yes | Yes | 19.1 | 17.6 | 1.5 | 18F97729BA3E48A78C146533B96B83C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-4018 |  | 2014-08-07 | 2014-08-07 12:53 | 2014-08-07 22:12 | RUUD - UAKA-024JAZ | 85 | -6 | Yes | Yes | 17 | 18.1 | -1.1 | 1EB89A62138C4337B62A1AB688AF02CB |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Fairfield | CA | 94533-2526 |  | 2014-07-18 | 2014-07-18 11:06 | 2014-07-18 11:06 | PAYNE - 561CJ024-B | 85 | 0 | Yes | Yes | 17.9 | 17.4 | 0.5 | BAF98E9FCCA448649B0084E6A74398A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4902 |  | 2014-07-09 | 2014-07-09 11:44 | 2014-07-09 12:17 | AMANA - | 140 | 5.4 | Yes | Yes | 11.4 | 14.4 | -3 | B934A2291197424694D4A0CE04A0D373 |  | R22 | Non-TXV |  | 3.857% | 0.96143 | 7.413% | [5 empty] | Non-TXV | 3.857%
Vallejo | CA | 94591-5710 |  | 2014-08-25 | 2014-08-25 12:19 | 2014-08-25 12:53 | - TTN030C100C2 | 95 | 4.5 | Yes | Yes | 22.5 | 19.7 | 2.9 | 62A2C7E6C30C4B59BB626CCB00379A7E |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
San Jose | CA | 95123-6250 |  | 2014-07-01 | 2014-07-01 14:14 | 2014-07-01 22:04 | CARRIER - 38CN024310 | 59 | 1.9 | Yes | Yes | 21.5 | 20.3 | 1.2 | 06C9CC73D2424295B37D30BE756637E2 |  | R22 | Non-TXV |  | 3.22% | 0.9678 | 6.189% | [5 empty] | Non-TXV | 3.22%
Fairfield | CA | 94533-2422 |  | 2014-07-17 | 2014-07-17 13:47 | 2014-07-17 22:09 | OTHER - 2A7A2036A1000AA | 96 | 4.6 | Yes | Yes | 14.4 | 17.2 | -2.8 | C8423EF7001F4B0D8FC701BB4E797563 |  | R22 | Non-TXV |  | 4.792% | 0.95208 | 9.209% | [5 empty] | Non-TXV | 4.792%
Bakersfield | CA | 93307-5074 |  | 2014-08-11 | 2014-08-11 11:30 | 2014-08-11 11:30 | HEIL - NRGE24SAK02 | 53 | 0 | Yes | Yes | 17.5 | 17 | 0.5 | C5F8DF48CEF941E59F967FC22698A962 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1077 |  | 2014-09-26 | 2014-09-26 16:55 | 2014-09-26 17:27 | OTHER - HAC2336AKA4 | 113 | -10.6 | Yes | Yes | 22.7 | 17.7 | 5 | B933959ABA2B4868A2A8953DDAD33574 |  | R22 | Non-TXV |  | -9.381% | 1.0938 | 2.627% |  |  |  |  | Non-TXV |  |  | -9.381%
Fairfield | CA | 94533-1148 |  | 2014-08-07 | 2014-08-07 08:42 | 2014-08-07 22:08 | DAY & NIGHT - 597AN036-A | 134 | -12.6 | Yes | Yes | 15.1 | 18.1 | -3 | 44F3F9E92D084630A9037ED895165053 |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Bakersfield | CA | 93304-1565 |  | 2014-08-28 | 2014-08-28 20:02 | 2014-08-28 20:02 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | AF46B785FBCD4B88B56B73A4C9EE32A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5904 |  | 2014-07-18 | 2014-07-18 13:41 | 2014-07-18 14:46 | BRYANT - 1002E18170 | 109 | 5.2 | Yes | Yes | 15.2 | 17.1 | -1.9 | 4271CE8295BC4BFA9450B767BD76A70B |  | R22 | Non-TXV |  | 4.771% | 0.95229 | 9.168% | [5 empty] | Non-TXV | 4.771%
Vallejo | CA | 94591-4858 |  | 2014-07-31 | 2014-07-31 15:08 | 2014-07-31 15:33 | RHEEM - RAKA-030JAZ | 66 | 5 | Yes | Yes | 14.2 | 14.7 | -0.5 | 15ECD4EE5D3A4B5980DAA2CB1A8F0B99 |  | R410A | Non-TXV |  | 7.576% | 0.92424 | 14.56% | [5 empty] | Non-TXV | 7.576%
Bakersfield | CA | 93304-1488 |  | 2014-10-10 | 2014-10-10 15:01 | 2014-10-10 15:01 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.4 | 21.3 | -0.8 | F6B1464BD9D04A72B194675F6314931A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1559 |  | 2014-08-28 | 2014-08-28 18:59 | 2014-08-28 18:59 | CARRIER - 38YCC018341 | 66 | 0 | Yes | Yes | 20.1 | 21.5 | -1.4 | BE83B2B525514334834CAEA9039509BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-7218 |  | 2014-07-10 | 2014-07-10 09:10 | 2014-07-10 09:49 | AMANA - BRCS0361BD | 63 | 5.2 | Yes | Yes | 14.6 | 17.4 | -2.8 | EBD4E7579E814D86A2569E8DE297F834 |  | R22 | Non-TXV |  | 8.254% | 0.91746 | 15.86% | [5 empty] | Non-TXV | 8.254%
Bakersfield | CA | 93309-2541 |  | 2014-10-12 | 2014-10-12 16:26 | 2014-10-12 16:31 | YORK - D1NH036N03606C | 109 | 3.8 | Yes | Yes | 21 | 20 | 1.1 | E49B003F20C6468FABC8DD0AD1C3CCB3 |  | R22 | Non-TXV |  | 3.486% | 0.96514 | 6.7% | [5 empty] | Non-TXV | 3.486%
Vacaville | CA | 95688-4529 |  | 2014-07-31 | 2014-07-31 11:55 | 2014-07-31 20:54 | CARRIER - 48GSN036060301 | 85 | 7.1 | Yes | Yes | 15.4 | 18.2 | -2.8 | F0C3A62DB16944428D9ED844B0883E48 |  | R22 | Non-TXV |  | 8.353% | 0.91647 | 16.05% | [5 empty] | Non-TXV | 8.353%
Woodland | CA | 95695-2648 |  | 2014-08-12 | 2014-08-12 14:00 | 2014-08-12 15:23 | LENNOX - HS29-030-1P | 68 | 5.6 | Yes | Yes | 24.7 | 19 | 5.7 | ADDC35B4DE3B417FBE5D91A8AB4F3A6C |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Bakersfield | CA | 93307-7290 |  | 2014-10-21 | 2014-10-21 15:29 | 2014-10-21 15:29 | RHEEM - 12AJA3001 | 96 | 0 | Yes | Yes | 21.5 | 20.7 | 0.8 | 63323EFE8022401FBFD9BB0219810228 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-8403 |  | 2014-08-05 | 2014-08-05 11:23 | 2014-08-05 11:23 | CARRIER - 24ABB336W0031010 | 85 | 0 | Yes | Yes | 21.9 | 18.5 | 3.4 | 2360FE790F774614876AFE56BDF960D3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2954 |  | 2014-07-29 | 2014-07-29 16:36 | 2014-07-29 22:12 | GMC - | 83 | 6.3 | Yes | Yes | 17.2 | 18.7 | -1.5 | C695DF502EF4437191FFE8D91F92AE91 |  | R22 | Non-TXV |  | 7.59% | 0.9241 | 14.59% | [5 empty] | Non-TXV | 7.59%
Antioch | CA | 94531-8124 |  | 2014-10-02 | 2014-10-02 12:09 | 2014-10-02 12:38 | CARRIER - 38TH048320 | 128 | 20.6 | Yes | Yes | 21.7 | 20.4 | 1.3 | 3E33E96ECA7B4778852B9F4DED2670E1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.09% | 0.83906 | 30.93% | [5 empty] | Non-TXV | 16.09%
Suisun City | CA | 94585-2630 |  | 2014-09-16 | 2014-09-16 13:59 | 2014-09-16 14:32 | GOODMAN - CL4B-1C1 | 104 | 3.5 | Yes | Yes | 21.6 | 20.4 | 1.2 | E7B5AA215EB2432FAAA6345DA5DB17F6 |  | R22 | Non-TXV |  | 3.365% | 0.96635 | 6.468% | [5 empty] | Non-TXV | 3.365%
Bakersfield | CA | 93305-3332 |  | 2014-08-05 | 2014-08-05 09:54 | 2014-08-05 09:54 | TRANE - YCC024F1L0BJ | 65 | 0 | Yes | Yes | 18 | 12.8 | 5.2 | 90D6741236D14134914085200BC730EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4378 |  | 2014-10-28 | 2014-10-28 14:32 | 2014-10-28 14:32 | NORDYNE - JT5BD-030KA | 144 | 0 | Yes | Yes | 20.1 | 19.2 | 0.9 | 857F3A91340F4EDAAB78670B5B8624A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1617 |  | 2014-11-07 | 2014-11-07 18:26 | 2014-11-07 18:26 | CARRIER - UNK | 131 | 0 | Yes | Yes | 21.3 | 20.9 | 0.4 | DC0C706A8E8E49079B49839503F7E87A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1617 |  | 2014-11-07 | 2014-11-07 18:32 | 2014-11-07 18:32 | OTHER - CAC448AKC3 | 208 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 22A7964C2742426786C19E75D3017528 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4119 |  | 2014-08-18 | 2014-08-18 09:06 | 2014-08-18 10:09 | YORK - H2RD036S06B | 96 | 3.7 | Yes | Yes | 23.2 | 20.7 | 2.5 | 11BA862383824BD8B17715A57D0D468A | Add refrigerant: 3.2 oz | R22 | Non-TXV |  | 3.854% | 0.96146 | 7.407% | [5 empty] | Non-TXV | 3.854%
San Jose | CA | 95120-1541 |  | 2014-07-02 | 2014-07-02 09:00 | 2014-07-02 09:25 | NORDYNE - FS5BD030K | 116 | 11.6 | Yes | Yes | 22.6 | 19.3 | 3.3 | B686AFB2743C44E9862D0E027C9C9AC0 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93309-2224 |  | 2014-09-19 | 2014-09-19 10:36 | 2014-09-19 10:36 | PAYNE - PAYPAB042060ABAA1600 | 118 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 0856B18509384799B0430E2313490A52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2224 |  | 2014-09-19 | 2014-09-19 10:42 | 2014-09-19 10:42 | ICP - PGAD36D1K6 | 80 | 0 | Yes | Yes | 20 | 21 | -1 | 53240FEE610945A39988512B2BBA370E |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5855 |  | 2014-07-01 | 2014-07-01 22:14 | 2014-07-01 22:14 | UNK - UNK | 85 | 0 | Yes | Yes | 16.7 | 15.5 | 1.2 | D277168DA67B40CF9167D6EAD35E482A |  |  |  |  | 0% | 1 | 0%
Bay Point | CA | 94565-6741 |  | 2014-09-09 | 2014-09-09 12:56 | 2014-09-09 12:56 | CARRIER - 24ABC648A310 | 208 | 0 | Yes | Yes | 16.9 | 16.7 | 0.2 | F229F93C58DB41DD9E637A44685115BC |  | R410A | TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-9586 |  | 2014-08-04 | 2014-08-04 10:40 | 2014-08-04 10:40 | RHEEM - RRPLB048JK1 | 161 | 0 | Yes | Yes | 20.4 | 18.3 | 2.1 | 3B0D3F7DB4194784A94ABA571C88113C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4813 |  | 2014-07-09 | 2014-07-09 13:57 | 2014-07-09 16:05 | GOODMAN - PG042100-1AB | 85 | 6.4 | Yes | Yes | 15.6 | 17.9 | -2.3 | CE87B5C5478B420488105AEC124B8DED |  | R22 | Non-TXV |  | 7.529% | 0.92471 | 14.47% | [5 empty] | Non-TXV | 7.529%
Lemoore | CA | 93245-9586 |  | 2014-08-04 | 2014-08-04 11:22 | 2014-08-04 11:47 | RHEEM - RAKA042JAZ | 79 | 2.6 | Yes | Yes | 20.7 | 16.6 | 4.1 | B704B8E7BCE148369F05FE1C5293496C |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Dixon | CA | 95620-2533 |  | 2014-07-29 | 2014-07-29 13:08 | 2014-07-29 13:45 | RUUD - UAKA-048JAZ | 103 | 7.6 | Yes | Yes | 17.5 | 20.1 | -2.6 | 48ACE9FC63074C65A83556A7BB54D432 |  | R22 | Non-TXV |  | 7.379% | 0.92621 | 14.18% | [5 empty] | Non-TXV | 7.379%
San Jose | CA | 95123-5623 |  | 2014-07-24 | 2014-07-24 10:02 | 2014-07-24 10:24 | GOODMAN - CKJ36IA8 | 97 | 13.4 | Yes | Yes | 17.5 | 19.4 | -1.9 | 96E4BF351CE5432DBB2428B2F63FEEE3 |  | R22 | Non-TXV |  | 13.81% | 0.86186 | 26.55% | [5 empty] | Non-TXV | 13.81%
San Jose | CA | 95124-5653 |  | 2014-07-24 | 2014-07-24 10:29 | 2014-07-24 11:05 | PAYNE - PA10JA036 | 86 | -5.1 | Yes | Yes | 21.7 | 19.1 | 2.6 | 68FF61E45ABC4981AA037F534AE8D9BA |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Bakersfield | CA | 93306-6783 |  | 2014-07-22 | 2014-07-22 09:13 | 2014-07-22 09:58 | BDP - 585HJW030040 | 68 | 3 | Yes | Yes | 20.6 | 14.7 | 5.9 | 43ECCD14E96B4944BF1ED5840864FFAE |  | R22 | Non-TXV |  | 4.412% | 0.95588 | 8.478% | [5 empty] | Non-TXV | 4.412%
Vacaville | CA | 95688-2510 |  | 2014-07-03 | 2014-07-03 12:35 | 2014-07-03 12:35 | ICP - PGX4481000K01 | 232 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | CFD45387064A4975B3ABA58728FC14F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-4925 |  | 2014-07-02 | 2014-07-02 09:35 | 2014-07-02 09:59 | TRANE - 4TTX3036A1000AAA | 78 | 10.4 | Yes | Yes | 23 | 20.4 | 2.6 | CCE1A3B9C829432EAB1F87CC482562F9 |  | R410A | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Bakersfield | CA | 93308-7014 |  | 2014-09-14 | 2014-09-14 20:01 | 2014-09-14 20:01 | GOODMAN - GSH130301CD | 130 | 0 | Yes | Yes | 20.9 | 21.5 | -0.6 | 4B190C86F9F340B8BBC869B75CA5C3AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-1635 |  | 2014-07-08 | 2014-07-08 09:46 | 2014-07-08 10:08 | BRYANT - 561CJ048 | 100 | -8.2 | Yes | Yes | 24.8 | 19.9 | 4.9 | 1734F7146A0D4C118F267884F367B885 |  | R22 | Non-TXV |  | -8.2% | 1.082 | 2.296% |  |  |  |  | Non-TXV |  |  | -8.2%
San Jose | CA | 95120-1635 |  | 2014-07-08 | 2014-07-08 09:51 | 2014-07-08 10:09 | BRYANT - 561CJ030 | 72 | -5.1 | Yes | Yes | 20.9 | 19.4 | 1.5 | 53E6C325D813410585D1AB17A36C1ABE |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Bakersfield | CA | 93308-7009 |  | 2014-09-14 | 2014-09-14 14:50 | 2014-09-14 14:50 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 20.4 | 22 | -1.6 | 4FDB8941B9CA49DC95B318AA7A16C237 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-4398 |  | 2014-07-24 | 2014-07-24 11:21 | 2014-07-24 11:21 | TRANE - 2TTR3036A1000 | 101 | 0 | Yes | Yes | 22.7 | 20.4 | 2.3 | F6DB2FA10F3D4A179CDF390BA62DE536 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-4398 |  | 2014-07-24 | 2014-07-24 11:31 | 2014-07-24 12:45 | TRANE - 2TTR3036A1000 | 101 | -5.9 | Yes | Yes | 24.3 | 20.2 | 4.2 | A0F6287366EA499B9A1DAF203333F809 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Bakersfield | CA | 93306-3070 |  | 2014-11-10 | 2014-11-10 12:47 | 2014-11-10 12:47 | OTHER - 2AC13B30P2B | 97 | 27.8 | Yes | Yes | -11.1 | 17.7 | -28.8 | CCFBA0E934AA4FD19FC55637E498B164 | Add refrigerant: 27.8 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 28.66% | 0.7134 | 55.08% | [5 empty] | Non-TXV | 28.66%
San Jose | CA | 95123-2475 |  | 2014-07-02 | 2014-07-02 10:07 | 2014-07-02 10:40 | PAYNE - PH13NR018H | 85 | -5 | Yes | Yes | 25.8 | 19.9 | 5.9 | A29BFE0AA15C49158DC8B39A3233DE44 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93306-1375 |  | 2014-10-01 | 2014-10-01 12:43 | 2014-10-01 12:43 | DAY & NIGHT - 24/60YAC-10EC | 53 | 0 | Yes | Yes | 19.1 | 21 | -1.9 | 32B30A8EAFED4A5FBADE27E3D25EB742 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4040 |  | 2014-09-09 | 2014-09-09 12:05 | 2014-09-09 12:05 | AIRE-FLO - SCU12E48A-1A | 130 | 0 | Yes | Yes | 19.5 | 19.6 | -0.1 | CF5C561511DB4ABA85A15E4A5FE24AF0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7010 |  | 2014-09-14 | 2014-09-14 14:18 | 2014-09-14 14:18 | CARRIER - 38YC0B030301 | 86 | 0 | Yes | Yes | 22.2 | 22.1 | 0.1 | A2FA85B5731342CBA890E1ABB9788768 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4157 |  | 2014-08-22 | 2014-08-22 14:41 | 2014-08-22 14:41 | TRANE - 4YCZ6048A1096BA | 136 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | 43F947D9BABA4C118ED3665551E70C43 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-1957 |  | 2014-07-01 | 2014-07-01 12:00 | 2014-07-01 21:04 | COLEMAN - | 85 | -6 | Yes | Yes | 19.7 | 16.1 | 3.6 | 6E3792529A544C559120EB8E0DD9593D |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Lemoore | CA | 93245-9415 |  | 2014-07-31 | 2014-07-31 14:26 | 2014-07-31 15:27 | GOODMAN - PGJ0480751REVA | 84 | 4.8 | Yes | Yes | 20.6 | 20.4 | 0.3 | 86467BBBE5FB43C4B59CD93249A4E8E9 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Vallejo | CA | 94591-5534 |  | 2014-08-25 | 2014-08-25 13:44 | 2014-08-25 14:04 | PAYNE - PA14NA03000AAAA | 122 | 5.3 | Yes | Yes | 22.6 | 20.7 | 1.9 | 6D1785320A07433BA42020A3A2099017 |  | R410A | Non-TXV |  | 4.344% | 0.95656 | 8.349% | [5 empty] | Non-TXV | 4.344%
Woodland | CA | 95695-5844 |  | 2014-09-29 | 2014-09-29 11:21 | 2014-09-29 11:43 | GOODMAN - G8X130361A | 78 | 2.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | 22482EFAEAAE43038B726BE47387575B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
San Jose | CA | 95120-1005 |  | 2014-07-02 | 2014-07-02 14:07 | 2014-07-02 14:07 | YORK - E2F060S06A | 149 | 0 | Yes | Yes | 14.4 | 20.4 | -6 | 3C504385E39547F6A719A46CD2547BC5 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-1005 |  | 2014-07-02 | 2014-07-02 14:15 | 2014-07-02 14:15 | DAY & NIGHT - 54B028SDP | 90 | 0 | Yes | Yes | 8.2 | 21.1 | -12.9 | 477DB0A0EC7544C7848EA5B9AA358D3D | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-1005 |  | 2014-07-02 | 2014-07-02 14:37 | 2014-07-02 14:56 | OTHER - US24ACRN | 52 | 4.1 | Yes | Yes | 20.5 | 19.7 | 0.9 | EF8FEA343D894032AEB1F31F1E55110F |  | R22 | Non-TXV |  | 7.885% | 0.92115 | 15.15% | [5 empty] | Non-TXV | 7.885%
Bakersfield | CA | 93308-7000 |  | 2014-09-14 | 2014-09-14 13:34 | 2014-09-14 13:34 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 21.5 | 22 | -0.5 | 74C566513A444CFCBB36528E83EEE0BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4539 |  | 2014-11-03 | 2014-11-03 09:49 | 2014-11-03 09:49 | OTHER - UKN | 90 | 0 | Yes | Yes | 24.2 | 20.4 | 3.8 | 91C60A0C41484D44BEFF03D77BD806F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6449 |  | 2014-06-27 | 2014-06-27 15:24 | 2014-06-27 15:24 | BDP - 585EJW048100AAAF | 86 | 0 | Yes | Yes | 21.4 | 18.6 | 2.8 | 344AF1E837114F798236FD4D72D52D65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6831 |  | 2014-06-27 | 2014-06-27 14:18 | 2014-06-27 14:18 | RUUD - URMA-A036JK08E | 99 | 0 | Yes | Yes | 22.6 | 20.4 | 2.2 | 397CC2FABC2245A78B0F87165E486AC0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1244 |  | 2014-07-22 | 2014-07-22 17:16 | 2014-07-22 17:18 | GOODMAN - GPG1330045M41BA | 78 | -6.4 | Yes | Yes | 18.2 | 18.6 | -0.3 | 0A5D13F032794984B5BCECE247C0EF76 |  | R410A | Non-TXV |  | -8.205% | 1.0821 | 2.298% |  |  |  |  | Non-TXV |  |  | -8.205%
Bakersfield | CA | 93309-5144 |  | 2014-06-26 | 2014-06-26 09:22 | 2014-06-26 09:22 | ICP - PGC036K0608 | 71 | 0 | Yes | Yes | 19.2 | 19.9 | -0.7 | 040B56C7E1AA4A55BDAA8529D5DCAFA6 |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7524 |  | 2014-08-25 | 2014-08-25 14:17 | 2014-08-25 15:51 | PAYNE - PA13NR3300908X75810 | 87 | 6.2 | Yes | Yes | 20.4 | 20.4 | 0 | 1474C158056440C082F7784F2CBD331B |  | R22 | Non-TXV |  | 7.126% | 0.92874 | 13.7% | [5 empty] | Non-TXV | 7.126%
Davis | CA | 95616-5711 |  | 2014-08-19 | 2014-08-19 12:52 | 2014-08-19 13:54 | RHEEM - ACC-03607 | 55 | 6.4 | Yes | Yes | 22.6 | 20.4 | 2.2 | BD4930A2DE0D488B81B27EB72224AE8D |  | R22 | Non-TXV |  | 11.64% | 0.88364 | 22.36% | [5 empty] | Non-TXV | 11.64%
Bakersfield | CA | 93308-7002 |  | 2014-09-14 | 2014-09-14 13:48 | 2014-09-14 14:06 | CARRIER - 38YCB030301 | 86 | 8.8 | Yes | Yes | 22.6 | 22.2 | 0.4 | 55B6972C24AB45C7B7EB6BE7587BC666 |  | R22 | Non-TXV |  | 10.23% | 0.89767 | 19.66% | [5 empty] | Non-TXV | 10.23%
Bakersfield | CA | 93312-2708 |  | 2014-09-18 | 2014-09-18 09:05 | 2014-09-18 09:05 | ICP - PGF336060K01A2 | 147 | 0 | Yes | Yes | 24.7 | 18.7 | 6 | 6E8176683C49427BA4C72150B17B074B |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2688 |  | 2014-08-05 | 2014-08-05 10:59 | 2014-08-05 10:59 | GOODMAN - GSC140601AE | 279 | 0 | Yes | Yes | 23.7 | 19.6 | 4.1 | 31AB8805F5B142FA83B93AFB4F28ADAE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-6808 |  | 2014-07-18 | 2014-07-18 10:14 | 2014-07-18 11:12 | RHEEM - | 80 | 4 | Yes | Yes | 19.9 | 20.4 | -0.5 | 1ECFFEC545394024A92B219AD7FDF401 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fairfield | CA | 94533-2234 |  | 2014-07-17 | 2014-07-17 14:55 | 2014-07-17 22:08 | - PA13NR024-J | 66 | -6.2 | Yes | Yes | 15.8 | 17.4 | -1.6 | 2BA155A0211A45259015D50E90DD68BA |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
Fairfield | CA | 94534-6676 |  | 2014-07-17 | 2014-07-17 15:36 | 2014-07-17 15:36 | CARRIER - 38CKC048360 | 98 | 0 | Yes | Yes | 19.7 | 16.5 | 3.2 | 0C951365BC4046A0AF497CC844C17D2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2749 |  | 2014-07-09 | 2014-07-09 10:16 | 2014-07-09 10:16 | CARRIER - 38TZA030320 | 82 | 0 | Yes | Yes | 16.8 | 18.8 | -2 | EB76624329BE4EFD9BB5D657B9585204 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3354 |  | 2014-10-02 | 2014-10-02 10:06 | 2014-10-02 10:06 | PAYNE - PQ10JA024-C | 64 | 0 | Yes | Yes | 23 | 19.9 | 3.1 | 53195FE6D60243F8B6CF48E9A9A32C81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6834 |  | 2014-08-06 | 2014-08-06 11:19 | 2014-08-06 11:19 | COLEMAN - UKN | 90 | 0 | Yes | Yes | 26.4 | 21 | 5.4 | B2D88651E2DD4845ADC1E3C5CA5E24D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2300 |  | 2014-08-24 | 2014-08-24 20:02 | 2014-08-24 20:04 | GOODMAN - GPG13420701AA | 107 | -8.8 | Yes | Yes | 28.9 | 23 | 5.9 | CC84CC670FDA4640B99545927D6382FD |  | R22 | Non-TXV |  | -8.224% | 1.0822 | 2.303% |  |  |  |  | Non-TXV |  |  | -8.224%
Wasco | CA | 93280-2565 |  | 2014-08-02 | 2014-08-02 18:20 | 2014-08-02 18:24 | RHEEM - RRGH07N36JKR | 81 | 5.5 | Yes | Yes | 19 | 20.4 | -1.4 | 8ACAC3BBD1CD49C894ECD526E82F1E2F |  | R22 | Non-TXV |  | 6.79% | 0.9321 | 13.05% | [5 empty] | Non-TXV | 6.79%
Rio Vista | CA | 94571-0000 |  | 2014-09-03 | 2014-09-03 12:59 | 2014-09-03 12:59 | LENNOX - 14ACX-030-230-111910H13405 | 107 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | AD89160AFA0C432FA2DD288D0809B0AE |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-4134 |  | 2014-07-02 | 2014-07-02 10:49 | 2014-07-02 11:15 | FRIGIDAIRE - S3BA036 | 90 | 17.4 | Yes | Yes | 19.4 | 19.9 | -0.5 | 5D639614DB5D43448DA519C12977887B |  | R22 | Non-TXV |  | 19.33% | 0.80667 | 37.15% | [5 empty] | Non-TXV | 19.33%
San Jose | CA | 95148-4134 |  | 2014-07-02 | 2014-07-02 10:55 | 2014-07-02 11:15 | FRIGIDAIRE - S3BA036K | 90 | 18.7 | Yes | Yes | 23.2 | 22 | 1.2 | C7D44C90A46E434686A15C79339FD3AF |  | R22 | Non-TXV |  | 20.78% | 0.79222 | 39.93% | [5 empty] | Non-TXV | 20.78%
Wasco | CA | 93280-3302 |  | 2014-08-16 | 2014-08-16 16:39 | 2014-08-16 16:41 | YORK - D1NA036N05606C | 67 | -6.3 | Yes | Yes | 23.8 | 20.9 | 2.9 | 6FEF460A195F45BBB68D062E0E0E1B8A |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
San Jose | CA | 95124-4916 |  | 2014-07-02 | 2014-07-02 15:24 | 2014-07-02 15:50 | YORK - H2RS036D06E | 63 | 9.5 | Yes | Yes | 20.8 | 20.3 | 0.5 | 38F1257B6E454859B809A3667E32D6FB |  | R22 | Non-TXV |  | 15.08% | 0.84921 | 28.98% | [5 empty] | Non-TXV | 15.08%
Vacaville | CA | 95688-8514 |  | 2014-07-03 | 2014-07-03 10:24 | 2014-07-03 10:49 | CARRIER - 38TH048320 | 128 | -7.5 | Yes | Yes | 22.1 | 19.7 | 2.5 | 64CA88EB251A41129A6CE44BF35D4B85 |  | R22 | Non-TXV |  | -5.859% | 1.0586 | 1.641% |  |  |  |  | Non-TXV |  |  | -5.859%
Vacaville | CA | 95687-5730 |  | 2014-07-01 | 2014-07-01 11:25 | 2014-07-01 12:51 | TRANE - TTR036C100A2 | 92 | 3.5 | Yes | Yes | 19.3 | 22.1 | -2.8 | A1294825E8AA4FE184C3A4294B705DA9 |  | R22 | Non-TXV |  | 3.804% | 0.96196 | 7.311% | [5 empty] | Non-TXV | 3.804%
Shafter | CA | 93263-3162 |  | 2014-09-07 | 2014-09-07 18:25 | 2014-09-07 18:28 | YORK - H2RD060S06B | 162 | -8.2 | Yes | Yes | 20.2 | 19.6 | 0.6 | 7C353BE3A6224687900852192F0156BA |  | R22 | TXV |  | -5.062% | 1.0506 | 1.418% |  |  |  |  | TXV |  |  | -5.062%
Rio Vista | CA | 94571-1341 |  | 2014-09-03 | 2014-09-03 12:23 | 2014-09-03 12:51 | AIRE-FLO - PY3GNAA30060NA | 85 | 4.4 | Yes | Yes | 20.3 | 19.9 | 0.4 | A3E3D8019BE749EDBD66090E03299D74 |  | R410A | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Lemoore | CA | 93245-3708 |  | 2014-07-31 | 2014-07-31 11:18 | 2014-07-31 11:41 | DUCANE - SG10B42075 | 88 | 4.8 | Yes | Yes | 21 | 20.4 | 0.6 | 5F5807B5E60E4D4F8C3F49A4C39D339D |  | R22 | Non-TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | Non-TXV | 5.455%
Fairfield | CA | 94533-4152 |  | 2014-07-22 | 2014-07-22 09:40 | 2014-07-22 10:40 | CARRIER - 591ANX024000AAAA | 53 | 3 | Yes | Yes | 15.2 | 17.7 | -2.5 | 51C41EBCA19C4FA9B973703E2ABA7144 |  | R22 | Non-TXV |  | 5.66% | 0.9434 | 10.88% | [5 empty] | Non-TXV | 5.66%
Bakersfield | CA | 93309-6490 |  | 2014-10-23 | 2014-10-23 12:45 | 2014-10-23 12:45 | RHEEM - UKN | 60 | 0 | Yes | Yes | 23.4 | 18.8 | 4.7 | 0B87EE6E86D943C1AE1B82A49C976495 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-3316 |  | 2014-08-01 | 2014-08-01 14:22 | 2014-08-01 14:42 | PAYNE - 591AN036A | 82 | 5.1 | Yes | Yes | 18.6 | 20.8 | -2.2 | DB3CCA06687249F28F2B65118EEE0EBF |  | R22 | Non-TXV |  | 6.22% | 0.9378 | 11.95% | [5 empty] | Non-TXV | 6.22%
Shafter | CA | 93263-1932 |  | 2014-08-23 | 2014-08-23 19:48 | 2014-08-23 19:54 | HEIL - PGX336100K01A1 | 162 | 0 | Yes | Yes | 23.9 | 22.1 | 1.8 | BECFD29979CE4137B87D3415A4D3804C | Remove refrigerant: 10.7 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-6532 |  | 2014-07-16 | 2014-07-16 09:19 | 2014-07-16 09:58 | RUUD - UAKA030JAZ | 66 | 9.6 | Yes | Yes | 18.3 | 19.6 | -1.3 | 50794AE5BC704C3C8DC1375AB56B4D63 |  | R22 | Non-TXV |  | 14.55% | 0.85455 | 27.95% | [5 empty] | Non-TXV | 14.55%
San Jose | CA | 95125-2618 |  | 2014-07-24 | 2014-07-24 14:57 | 2014-07-25 08:26 | BRYANT - 113ANA060 | 130 | 5.7 | Yes | Yes | 21.2 | 20.4 | 0.8 | 53E146E6A77B4FBE9201617378AB6E25 |  | R22 | Non-TXV |  | 4.385% | 0.95615 | 8.426% | [5 empty] | Non-TXV | 4.385%
Bakersfield | CA | 93307-5752 |  | 2014-07-18 | 2014-07-18 10:45 | 2014-07-18 10:45 | UNITARY PRODUCTS GROUP - 24A66348W0031010 | 85 | 0 | Yes | Yes | 20.4 | 20.8 | -0.4 | 0884EB61FFCD44E1B89BB639CAF6C05D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2132 |  | 2014-07-31 | 2014-07-31 09:00 | 2014-07-31 20:52 | TRANE - TTR036C100A3 | 80 | 4 | Yes | Yes | 14.6 | 17.2 | -2.6 | 977EA932E0244148AA0B398F822CC928 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
W Sacramento | CA | 95605-2134 |  | 2014-07-02 | 2014-07-02 08:09 | 2014-07-02 21:35 | TRANE - YCY030F1MOAA | 148 | 7.8 | Yes | Yes | 20.4 | 15.2 | 5.2 | 6E5B63D1BA5E4F609C9C6261B722630C |  | R22 | Non-TXV |  | 5.27% | 0.9473 | 10.13% | [5 empty] | Non-TXV | 5.27%
San Jose | CA | 95127-1956 |  | 2014-07-25 | 2014-07-25 09:40 | 2014-07-25 10:06 | -36 | 83 | 6.4 | Yes | Yes | 20.9 | 19.9 | 1 | 8BAA55FDF6D840EFA505A451B1FB2671 |  | R22 | Non-TXV |  | 7.711% | 0.92289 | 14.82% | [5 empty] | Non-TXV | 7.711%
Bakersfield | CA | 93309-6022 |  | 2014-06-27 | 2014-06-27 13:49 | 2014-06-27 13:49 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 20.8 | 19.9 | 1 | 32CEADD441D7461FA32BC958420A6596 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2133 |  | 2014-08-18 | 2014-08-18 14:25 | 2014-08-18 15:20 | - GCGD24S41S3A | 61 | 4.9 | Yes | Yes | 16.1 | 18.8 | -2.7 | 42B094284161422BA215B4FA6D1F0255 |  | R22 | Non-TXV |  | 8.033% | 0.91967 | 15.44% | [5 empty] | Non-TXV | 8.033%
Bakersfield | CA | 93307-5074 |  | 2014-09-09 | 2014-09-09 11:11 | 2014-09-09 11:11 | OTHER - NRCE24SAK02 | 49 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | 2EA90C53E5804B0EB17AF1FD5BDB275E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5782 |  | 2014-06-26 | 2014-06-26 14:31 | 2014-06-26 14:31 | GOODMAN - GPG1342070M41CA | 81 | 0 | Yes | Yes | 24.9 | 19.9 | 5 | BC17A34B90894A4EBB50418FC71173A8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5650 |  | 2014-10-14 | 2014-10-14 11:13 | 2014-10-14 11:43 | PAYNE - 591ANNO36-A | 90 | 4.3 | Yes | Yes | 20.6 | 20.4 | 0.2 | 40198E2C5C4E4DD5BCDDFAEF3296E72B |  | R22 | Non-TXV |  | 4.778% | 0.95222 | 9.182% | [5 empty] | Non-TXV | 4.778%
San Jose | CA | 95132-3540 |  | 2014-07-07 | 2014-07-07 09:01 | 2014-07-07 09:28 | TRANE - 2TTB0042A1000AAA | 95 | 6.8 | Yes | Yes | 18.9 | 19.9 | -1 | 466A1CA49354403B950CB1716603D7A0 |  | R22 | Non-TXV |  | 7.158% | 0.92842 | 13.76% | [5 empty] | Non-TXV | 7.158%
San Jose | CA | 95123-3258 |  | 2014-07-07 | 2014-07-07 09:34 | 2014-07-07 09:59 | BRYANT - 363CN0036 | 104 | -6.1 | Yes | Yes | 23.9 | 19.9 | 4 | DB6ACB8CFC984343914BBCC5F89CB333 |  | R22 | Non-TXV |  | -5.865% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.865%
Davis | CA | 95618-4898 |  | 2014-07-11 | 2014-07-11 10:22 | 2014-07-11 19:56 | GE - | 85 | 5.4 | Yes | Yes | 16.4 | 18.1 | -1.7 | 9EAB9B95F68F4C43946650B5D5DFD200 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Fairfield | CA | 94533-4043 |  | 2014-07-18 | 2014-07-18 12:39 | 2014-07-18 17:15 | PAYNE - PA10JA036-C | 77 | 2.6 | Yes | Yes | 17.7 | 20.4 | -2.7 | F7DB085605AC4B0783C081BE1DF58B6E |  | R22 | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Suisun City | CA | 94585-1822 |  | 2014-09-12 | 2014-09-12 14:34 | 2014-09-12 15:02 | GMC - BGTA730B1301 | 61 | 4.8 | Yes | Yes | 14.9 | 17 | -2.1 | 7EB1ADC6620B48EF80B66EECD016E741 |  | R22 | Non-TXV |  | 7.869% | 0.92131 | 15.12% | [5 empty] | Non-TXV | 7.869%
San Jose | CA | 95122-3823 |  | 2014-07-25 | 2014-07-25 11:00 | 2014-07-25 11:34 | LENNOX - HS10411V3P | 90 | 21.6 | Yes | Yes | 20.1 | 20.9 | -0.8 | 801A661149CA4C10878BF320E732BCBE |  | R22 | Non-TXV |  | 24% | 0.76 | 46.12% | [5 empty] | Non-TXV | 24%
Bakersfield | CA | 93304-7102 |  | 2014-07-11 | 2014-07-11 14:51 | 2014-07-11 14:51 | UNITARY PRODUCTS GROUP - D1NH042N06506C | 94 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 552CA49AF7BE4D7794668EB7622670E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4155 |  | 2014-07-18 | 2014-07-18 09:34 | 2014-07-18 16:02 | TRANE - BTD736A100B0 | 83 | 3.5 | Yes | Yes | 15.9 | 18.7 | -2.8 | E7E8845BCB1C483BBAFD300C8C4DC5AD |  | R22 | Non-TXV |  | 4.217% | 0.95783 | 8.104% | [5 empty] | Non-TXV | 4.217%
San Jose | CA | 95110-3105 |  | 2014-07-29 | 2014-07-29 10:32 | 2014-07-29 10:32 | BRYANT - 538ANR024 | 104 | 0 | Yes | Yes | 21.9 | 19.6 | 2.3 | 976614F5A75642C5867159D408F04642 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-4151 |  | 2014-07-07 | 2014-07-07 13:50 | 2014-07-07 15:34 | TRANE - TTD736B1000 | 80 | 2.7 | Yes | Yes | 22.6 | 19.4 | 3.3 | B07543FC8A7E4CAC8166CA2DA536A33D |  | R22 | Non-TXV |  | 3.375% | 0.96625 | 6.486% | [5 empty] | Non-TXV | 3.375%
Bakersfield | CA | 93307-5318 |  | 2014-07-24 | 2014-07-24 13:39 | 2014-07-24 13:39 | GOODMAN - PGB036075-1B | 50 | 0 | Yes | Yes | 23.2 | 19.9 | 3.3 | F11780D698144B419F7BF62ABD5B7B44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4427 |  | 2014-08-05 | 2014-08-05 09:15 | 2014-08-05 09:15 | ICP - PGAA24B1K4 | 66 | 0 | Yes | Yes | 21.3 | 17 | 4.3 | C6239E32E2214FA49A457DBE4CDC0A57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7031 |  | 2014-07-31 | 2014-07-31 11:37 | 2014-07-31 11:37 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.5 | 19.5 | -1 | 2C6B2536260F435DA7CC1586BE75A17C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7060 |  | 2014-07-10 | 2014-07-10 10:46 | 2014-07-10 10:46 | TEMPSTAR - N2A348AKA300 | 121 | 0 | Yes | Yes | 28.6 | 23 | 5.6 | 5F89E9467E2547B098BC54EAF159D37A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7036 |  | 2014-08-13 | 2014-08-13 10:20 | 2014-08-13 10:20 | BDP - 585CJ036075 | 84 | 0 | Yes | Yes | 20.7 | 20.6 | 0.1 | D0F97B1573094D1498B13BA5520A9F08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6926 |  | 2014-07-01 | 2014-07-01 09:05 | 2014-07-01 09:29 | SEARS - 2A7B0030A1000AA | 64 | 0 | Yes | Yes | 15.8 | 18.7 | -2.9 | 7405CA85CD4B422F9F6216C7E134AB89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5804 |  | 2014-07-16 | 2014-07-16 09:28 | 2014-07-16 09:43 | YORK - H2RC042S06A | 107 | 3.3 | Yes | Yes | 14.9 | 17.5 | -2.6 | 8CCDAB94E75B4CF1A05868863229053F |  | R22 | Non-TXV |  | 3.084% | 0.96916 | 5.927% | [5 empty] | Non-TXV | 3.084%
Bakersfield | CA | 93304-7007 |  | 2014-07-11 | 2014-07-11 11:18 | 2014-07-11 11:18 | SEARS - 769 812240 | 101 | 0 | Yes | Yes | 20.3 | 18.8 | 1.5 | C2AFC9D20DF04C78ABDC2D1273D6C1C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95131-3137 |  | 2014-07-07 | 2014-07-07 10:03 | 2014-07-07 12:43 | CARRIER - 38HDL036311 | 92 | -6.5 | Yes | Yes | 24.4 | 19.9 | 4.5 | E7116B6449DC4087834BB3449EA1D385 |  | R22 | Non-TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.065%
San Jose | CA | 95121-1034 |  | 2014-07-07 | 2014-07-07 13:09 | 2014-07-07 13:43 | CARRIER - 24ACA436A000 | 117 | 5.4 | Yes | Yes | 25.5 | 19.9 | 5.6 | 34F949E752B64D8B9DB49E25C53AD1B3 |  | R410A | TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | TXV | 4.615%
Vallejo | CA | 94591-6878 |  | 2014-08-01 | 2014-08-01 11:43 | 2014-08-01 12:04 | GE - BGTA73B1BO1 | 57 | 5.3 | Yes | Yes | 19.1 | 20.4 | -1.3 | FEFC28F1E4AD44CD965E4F0F6DDCD926 |  | R22 | Non-TXV |  | 9.298% | 0.90702 | 17.87% | [5 empty] | Non-TXV | 9.298%
San Jose | CA | 95136-2152 |  | 2014-08-22 | 2014-08-22 13:14 | 2014-08-22 13:14 | ARMSTRONG - SCU10E48A-2A | 98 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | EE4B75103CAE4039A94C21EF3E2EAACF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2680 |  | 2014-07-11 | 2014-07-11 10:09 | 2014-07-11 13:23 | BRYANT - 561CK048 | 103 | 17 | Yes | Yes | 18.6 | 20.3 | -1.7 | B7087B892147408A948DC4CC9F69F859 |  | R22 | Non-TXV |  | 16.5% | 0.83495 | 31.72% | [5 empty] | Non-TXV | 16.5%
Antioch | CA | 94509-1932 |  | 2014-11-11 | 2014-11-11 14:35 | 2014-11-11 18:17 | RHEEM - | 106 | 4.1 | Yes | Yes | 20.5 | 20.4 | 0.1 | 8D18EF37BA634DFF9AEAA96EA2E51B3E |  | R22 | Non-TXV |  | 3.868% | 0.96132 | 7.433% | [5 empty] | Non-TXV | 3.868%
Bay Point | CA | 94565-3163 |  | 2014-09-12 | 2014-09-12 12:41 | 2014-09-12 12:41 | BRYANT - 561CJX036-F | 73 | 0 | Yes | Yes | 23.3 | 22.1 | 1.2 | 3C15BAD1F48945DA9338452D125C3D74 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2301 |  | 2014-09-18 | 2014-09-18 08:40 | 2014-09-18 09:18 | OTHER - AC030M1021A | 57 | 8.7 | Yes | Yes | 17.3 | 16.1 | 1.2 | 633B0819B95B45A9B584136AC65B442E |  | R22 | Non-TXV |  | 15.26% | 0.84737 | 29.33% | [5 empty] | Non-TXV | 15.26%
Bakersfield | CA | 93304-7230 |  | 2014-07-11 | 2014-07-11 11:34 | 2014-07-11 11:34 | PAYNE - PY3GNAA30040NA | 98 | 0 | Yes | Yes | 22.9 | 20.8 | 2.1 | E89307A03BB24665802F1102EF5A3668 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-4061 |  | 2014-07-18 | 2014-07-18 10:30 | 2014-07-18 17:10 | DAY & NIGHT - NXA636GKA100 | 106 | -6.2 | Yes | Yes | 18.8 | 19.1 | -0.3 | B657123C43B943F59AA31DBB5FF2F769 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Union City | CA | 94587-2546 |  | 2014-08-21 | 2014-08-21 11:21 | 2014-08-21 11:43 | CARRIER - 24ABA318A0030010 | 74 | 7.5 | Yes | Yes | 19 | 18.8 | 0.2 | FAAB0C0C29624C04A24443E1CBA48BBC |  | R410A | TXV |  | 10.14% | 0.89865 | 19.48% | [5 empty] | TXV | 10.14%
Bakersfield | CA | 93306-2239 |  | 2014-07-21 | 2014-07-21 14:29 | 2014-07-21 14:29 | UNITARY PRODUCTS GROUP - CMA04211A | 120 | 0 | Yes | Yes | 19.3 | 21.5 | -2.2 | 8FD4DB85787543099E25CFCB5113A166 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6711 |  | 2014-07-21 | 2014-07-21 08:37 | 2014-07-21 19:17 | OTHER - 591ANX036000AAAA | 90 | 2.7 | Yes | Yes | 15.3 | 18.2 | -2.9 | 21A338BA3E6D4C8B87102B334661D82B |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Suisun City | CA | 94585-3032 |  | 2014-08-01 | 2014-08-01 14:07 | 2014-08-01 14:07 | - | 85 | 0 | Yes | Yes | 15.3 | 17.8 | -2.5 | 3555C8E18D704325864D77E69A4131A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-3213 |  | 2014-07-08 | 2014-07-08 08:33 | 2014-07-08 09:05 | BRYANT - 561CJX0360000AEAA | 72 | 3.4 | Yes | Yes | 17.2 | 19.6 | -2.4 | D0F80191860147A9876CB94641E8FC7C |  | R22 | Non-TXV |  | 4.722% | 0.95278 | 9.075% | [5 empty] | Non-TXV | 4.722%
San Jose | CA | 95121-3213 |  | 2014-07-08 | 2014-07-08 08:37 | 2014-07-08 09:05 | BRYANT - 561CJX042 | 80 | -5.6 | Yes | Yes | 22 | 18.8 | 3.2 | 28EE4604321F407893A79239BFB423D6 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Bakersfield | CA | 93309-3762 |  | 2014-09-16 | 2014-09-16 09:11 | 2014-09-16 09:11 | ICP - PGAA30C1K4 | 79 | 0 | Yes | Yes | 26.9 | 20.9 | 6 | 790F3A405CED4136A0B156ADF920C002 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3917 |  | 2014-07-22 | 2014-07-22 08:29 | 2014-07-22 10:40 | BDP - 591AN042-D | 91 | -6.4 | Yes | Yes | 16.8 | 18.8 | -2 | 05F451FCFEE64253A79721053EE319CF |  | R22 | Non-TXV |  | -7.033% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.033%
Bakersfield | CA | 93304-5723 |  | 2014-07-07 | 2014-07-07 10:45 | 2014-07-07 10:45 | RHEEM - HC-100-42-21C | 72 | 0 | Yes | Yes | 19.4 | 21.5 | -2.1 | B0131720D40147A58F8FED61074171C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cupertino | CA | 95014-1180 |  | 2014-08-14 | 2014-08-14 09:10 | 2014-08-14 09:31 | CARRIER - 38CK036330 | 127 | 6.9 | Yes | Yes | 18.3 | 18.2 | 0.1 | 585F23309D1444DCBF93D8E6B0EF4908 |  | R22 | TXV |  | 5.433% | 0.94567 | 10.44% | [5 empty] | TXV | 5.433%
Rio Vista | CA | 94571-1637 |  | 2014-09-23 | 2014-09-23 12:43 | 2014-09-23 14:19 | SEARS - | 78 | 5.1 | Yes | Yes | 21 | 20.4 | 0.6 | B2F06D9AD4A2472B87208906AA8B84AA |  | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Vallejo | CA | 94589-4379 |  | 2014-10-07 | 2014-10-07 10:36 | 2014-10-07 10:57 | CARRIER - 4194E05980 | 78 | 3.1 | Yes | Yes | 20.5 | 20.4 | 0.1 | 8B5D0C575F9B46D893BFF1C351099750 |  | R22 | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
Woodland | CA | 95776-5399 |  | 2014-07-07 | 2014-07-07 14:32 | 2014-07-07 14:32 | CARRIER - 24ABA324A310 | 74 | 0 | Yes | Yes | 19.7 | 19.8 | -0.1 | E70E30253FCB410E9920971B0A18E3C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5402 |  | 2014-07-24 | 2014-07-24 13:22 | 2014-07-24 13:48 | CARRIER - 24ABA324A310 | 74 | 5.3 | Yes | Yes | 24.2 | 20.4 | 3.8 | B814D29B0F82434BAD4C071A4DD86141 |  | R22 | Non-TXV |  | 7.162% | 0.92838 | 13.76% | [5 empty] | Non-TXV | 7.162%
Woodland | CA | 95695-2896 |  | 2014-08-14 | 2014-08-14 13:41 | 2014-08-14 13:59 | TAPPAN - CA9630UKA1 | 141 | 10.1 | Yes | Yes | 21 | 19.3 | 1.7 | 68335F87133342D3B69D39CF5AD5753E |  | R22 | Non-TXV |  | 7.163% | 0.92837 | 13.77% | [5 empty] | Non-TXV | 7.163%
Vallejo | CA | 94590-3370 |  | 2014-09-17 | 2014-09-17 18:05 | 2014-09-17 18:23 | BRYANT - CTC0240P34-A1000 | 72 | 4 | Yes | Yes | 19.2 | 20.4 | -1.2 | 496BFB42A74747B68CEB5724FE221CAB |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Woodland | CA | 95776-5401 |  | 2014-09-15 | 2014-09-15 10:26 | 2014-09-15 10:43 | CARRIER - 24ABA324A310 | 74 | 5.6 | Yes | Yes | 18.6 | 21.5 | -2.9 | 7BF09CCCB0A54F17B83F55B596E65D6F |  | R410A | Non-TXV |  | 7.568% | 0.92432 | 14.54% | [5 empty] | Non-TXV | 7.568%
San Jose | CA | 95138-1816 |  | 2014-07-28 | 2014-07-28 14:14 | 2014-07-29 08:43 | TRANE - TTR048C1000 | 114 | 15.1 | Yes | Yes | 22.6 | 20.2 | 2.5 | C750B65427C641B891253DA6DD0005D3 |  | R22 | Non-TXV |  | 13.25% | 0.86754 | 25.46% | [5 empty] | Non-TXV | 13.25%
Woodland | CA | 95776-5400 |  | 2014-07-07 | 2014-07-07 14:46 | 2014-07-07 14:46 | CARRIER - 24ABA324A310 | 74 | 0 | Yes | Yes | 17.5 | 18.5 | -1 | 176C80992EF04C79B4A3DE09667A52FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3419 |  | 2014-08-16 | 2014-08-16 16:44 | 2014-08-16 16:47 | ARCOAIRE - PGAD47D1K8------ | 211 | 17.2 | Yes | Yes | 22.5 | 21.5 | 1 | 8D5A648B0E2A4B388EFBBBAE0A3CF7AF |  | R22 | Non-TXV |  | 8.152% | 0.91848 | 15.67% | [5 empty] | Non-TXV | 8.152%
Bakersfield | CA | 93304-3035 |  | 2014-06-25 | 2014-06-25 12:45 | 2014-06-25 12:45 | GOODMAN - PGB048075-1 | 86 | 0 | Yes | Yes | 24 | 19.9 | 4.1 | 9643C59025074B2D958675BCD410B58D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2507 |  | 2014-11-05 | 2014-11-05 13:35 | 2014-11-05 13:35 | GOODMAN - UNK | 100 | 0 | Yes | Yes | 21.5 | 19.9 | 1.6 | 33985EE26F114890ADD44A4526D4C809 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2523 |  | 2014-07-09 | 2014-07-09 10:12 | 2014-07-09 10:12 | BDP - 589ANW030060ADBD | 72 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | 5531D15C0FB24F5796A4F0AE851622C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2523 |  | 2014-07-09 | 2014-07-09 10:20 | 2014-07-09 10:20 | BDP - 589ANW030060ADBD | 72 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | DC2ED2EE282D4E6D97E93586941E5F60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1592 |  | 2014-08-04 | 2014-08-04 12:37 | 2014-08-04 12:37 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | BC52EC905DC64E7FBB6E701DD3690C1F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6833 |  | 2014-08-25 | 2014-08-25 10:03 | 2014-08-25 10:03 | CARRIER - 38BRC042300 | 134 | 0 | Yes | Yes | 24 | 22 | 2 | 1EB7C3630A0940AEBAC4E1BD2F67EC47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5634 |  | 2014-07-18 | 2014-07-18 16:01 | 2014-07-18 16:01 | TRANE - TTR025C100A3 | 62 | 0 | Yes | Yes | 17.8 | 17.8 | 0 | C0A51C49E9604867AF0E0F17E9C409ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94087-5221 |  | 2014-07-30 | 2014-07-30 13:51 | 2014-07-30 21:12 | LENNOX - XC13036 | 118 | -8.3 | Yes | Yes | 22.1 | 20.4 | 1.7 | E4270636AC804421A2616164424B4822 |  | R22 | Non-TXV |  | -7.034% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.034%
Bakersfield | CA | 93312-3488 |  | 2014-08-21 | 2014-08-21 09:45 | 2014-08-21 09:45 | GOODMAN - PGX048075-1BB | 80 | 0 | Yes | Yes | 23.1 | 19 | 4.1 | E023408D8DE5427F87324520D5628ED0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-0532 |  | 2014-07-17 | 2014-07-17 09:40 | 2014-07-17 09:40 | - | 85 | 0 | Yes | Yes | 16.3 | 17.7 | -1.4 | 3D501D3B7BA842E7962C1802E2D14743 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1903 |  | 2014-11-12 | 2014-11-12 11:29 | 2014-11-12 11:59 | CARRIER - 1590E10 | 80 | -4.7 | Yes | Yes | 20.3 | 20.4 | -0.1 | 02FCFEDF10364CA89962DFFCF8527864 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Bakersfield | CA | 93313-5314 |  | 2014-08-27 | 2014-08-27 11:11 | 2014-08-27 11:11 | RHEEM - 43AJA48A01 | 123 | 0 | Yes | Yes | 21 | 20.3 | 0.7 | 90E1B3D8EA9C4F0BA74430301D150B4A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-0000 |  | 2014-08-29 | 2014-08-29 11:19 | 2014-08-29 11:19 | BRYANT - 116BNA030-A | 108 | 0 | Yes | Yes | 22.7 | 21.5 | 1.2 | 99C8D0235A1F4DE6BEA59A1E18793C18 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6109 |  | 2014-09-30 | 2014-09-30 09:22 | 2014-09-30 09:22 | AMANA - APG13480901AB | 145 | 0 | Yes | Yes | 23.5 | 19.9 | 3.6 | 7F9085BDE8284A87ACA584A20F8E632F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6575 |  | 2014-10-23 | 2014-10-23 09:41 | 2014-10-23 09:41 | BRYANT - 113RNA048-B | 124 | 0 | Yes | Yes | 22.4 | 20.4 | 2 | C3F2A67A78924790A37BA89E762C9241 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2131 |  | 2014-08-21 | 2014-08-21 10:15 | 2014-08-21 10:15 | YORK - D1NA030N05606C | 72 | 0 | Yes | Yes | 22.9 | 23 | -0.1 | 7156F662C0094C209AF47C694D658434 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7009 |  | 2014-09-14 | 2014-09-14 15:01 | 2014-09-14 15:01 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 21.7 | 22 | -0.3 | 26A1F4E547BC4AE4B7888D0905C2A87E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6405 |  | 2014-07-11 | 2014-07-11 10:14 | 2014-07-11 10:14 | UNITARY PRODUCTS GROUP - DAYH-F042N080C | 94 | 0 | Yes | Yes | 28 | 23.3 | 4.7 | 64F19B294626484188594F8071647C1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6422 |  | 2014-10-15 | 2014-10-15 11:11 | 2014-10-15 11:11 | ICP - PGAD47D1K5 | 215 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 0D4015D1F2894F659BED5B23B6C19229 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95117-2332 |  | 2014-07-09 | 2014-07-09 09:58 | 2014-07-09 10:15 | STREAMLINE - 538ANX036000B | 86 | -5.1 | Yes | Yes | 24.3 | 20.1 | 4.2 | A4BF7021458047A69BE58A84B464355C |  | R22 | Non-TXV |  | -5.93% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.93%
Esparto | CA | 95627-2079 |  | 2014-08-08 | 2014-08-08 12:23 | 2014-08-08 13:37 | AMERICAN STANDARD - YCX036G1M0AD | 108 | 5.2 | Yes | Yes | 17.7 | 19 | -1.3 | 82250FF3F1814B9B9B29E97B1F48DB05 |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Bakersfield | CA | 93311-9514 |  | 2014-07-23 | 2014-07-23 15:29 | 2014-07-23 15:29 | WESTINGHOUSE - 13ACD06023002 | 214 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 1AD2A1AD9E844BB6B4EC28CF848CD156 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6625 |  | 2014-07-11 | 2014-07-11 10:40 | 2014-07-11 10:40 | UNITARY PRODUCTS GROUP - DAYP-F030N070A | 73 | 0 | Yes | Yes | 24.6 | 18.6 | 6 | B7FAAD7F863A4C2AA95CC359BA2C58B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94087-2837 |  | 2014-07-21 | 2014-07-21 13:45 | 2014-07-21 13:45 | RHEEM - RAKA048JAZ | 103 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | 827054A348A448638D34C5313B8019E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1533 |  | 2014-08-29 | 2014-08-29 09:14 | 2014-08-29 12:32 | - | 85 | 2.8 | Yes | Yes | 16.2 | 17.4 | -1.2 | 7F7652732DEB4481BE6E6B31E246417F |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Vallejo | CA | 94591-6391 |  | 2014-09-16 | 2014-09-16 12:52 | 2014-09-16 13:24 | CARRIER - 38CKC042340 | 80 | 5 | Yes | Yes | 22.6 | 20.4 | 2.2 | F70054FCB5B54F9EB2E9F5EFE131581C |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Bakersfield | CA | 93309-3637 |  | 2014-06-26 | 2014-06-26 12:42 | 2014-06-26 12:42 | BDP - 589ANW048080ADBG | 92 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | DDD6FB9CA8E045529FD8418AABC15805 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94087-4141 |  | 2014-08-04 | 2014-08-04 09:01 | 2014-08-04 10:10 | TRANE - 2TTR4048A1000AA | 150 | 6.6 | Yes | Yes | 19.4 | 20.4 | -1 | 425ED8251C4040DD88E418216417363E |  | R22 | Non-TXV |  | 4.4% | 0.956 | 8.456% | [5 empty] | Non-TXV | 4.4%
San Jose | CA | 95125-4743 |  | 2014-07-08 | 2014-07-08 13:56 | 2014-07-08 14:14 | COLEMAN - 7036-811 | 87 | 3.3 | Yes | Yes | 24.2 | 21.5 | 2.7 | F117CFBB4CD445588FEB643729E05926 |  | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Bakersfield | CA | 93308-7014 |  | 2014-09-14 | 2014-09-14 19:50 | 2014-09-14 19:50 | GOODMAN - GSH130241CB | 122 | 0 | Yes | Yes | 22.3 | 22 | 0.3 | 88982243A6124B8A8A338B4DFEC844BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7010 |  | 2014-09-14 | 2014-09-14 19:52 | 2014-09-14 19:52 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 20.8 | 21.8 | -1 | BD32FA42FBDD49E7AD10E5DC28DA2838 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1435 |  | 2014-10-16 | 2014-10-16 14:17 | 2014-10-16 14:17 | ICP - GPCM036K060D | 71 | 0 | Yes | Yes | 19.3 | 22.1 | -2.8 | D4E7C265449145F19D0E4DAFEE97A24B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-2851 |  | 2014-07-29 | 2014-07-29 11:42 | 2014-07-29 11:42 | AMANA - ASX13036 | 89 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 047A1523EC4E4E0999C4F289291F9344 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2107 |  | 2014-07-08 | 2014-07-08 10:29 | 2014-07-08 12:37 | ICP - HC436AKA4 | 194 | -11.4 | Yes | Yes | 20.8 | 19.4 | 1.4 | 3316B91C01A54DB89A528D9613D83DF0 |  | R22 | Non-TXV |  | -5.876% | 1.0588 | 1.646% |  |  |  |  | Non-TXV |  |  | -5.876%
Campbell | CA | 95008-5831 |  | 2014-07-21 | 2014-07-21 10:42 | 2014-07-21 11:34 | PAYNE - 565BJ048 | 125 | -7.4 | Yes | Yes | 21.5 | 19.8 | 1.7 | 650573A19CD04806A10F8C40ADBB4393 |  | R22 | Non-TXV |  | -5.92% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.92%
Fairfield | CA | 94534-8631 |  | 2014-07-18 | 2014-07-18 16:02 | 2014-07-18 17:17 | CARRIER - | 85 | 7.6 | Yes | Yes | 14.9 | 17.6 | -2.7 | FE60F3EFAADC49ABB4FB26997CC19073 |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Fairfield | CA | 94534-8631 |  | 2014-07-18 | 2014-07-18 16:03 | 2014-07-18 17:18 | CARRIER - | 85 | 4.4 | Yes | Yes | 15.5 | 16.7 | -1.2 | 46A7C2829EA84D80A4B7E40D227BE0D1 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Vacaville | CA | 95687-4938 |  | 2014-07-01 | 2014-07-01 10:41 | 2014-07-01 11:36 | PAYNE - PA10JA036-C | 72 | -5.1 | Yes | Yes | 15.3 | 16.9 | -1.6 | C52BE2CB61B74800A674B5F8F768FA67 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Fairfield | CA | 94533-1105 |  | 2014-07-18 | 2014-07-18 13:39 | 2014-07-18 17:15 | AIRE-FLO - | 85 | -7 | Yes | Yes | 15 | 17.2 | -2.2 | F434ADA8CE2C419EBFB7FF94EB7D7239 |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Bakersfield | CA | 93308-7010 |  | 2014-09-14 | 2014-09-14 14:34 | 2014-09-14 14:34 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 20.8 | 20.4 | 0.4 | 9E39B077710C4FFD81B5EBC86C8F11AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2329 |  | 2014-07-23 | 2014-07-23 12:19 | 2014-07-23 12:19 | ICP - PGF330060K01A1 | 152 | 0 | Yes | Yes | 24.2 | 20.9 | 3.4 | 14B06AC49B3A44FB89AE768892E4B2F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7850 |  | 2014-08-25 | 2014-08-25 12:03 | 2014-08-25 12:03 | PAYNE - PA10JA042-C | 81 | 0 | Yes | Yes | 19 | 20.7 | -1.7 | 3A1833F9DC2F42BE88CF59C0EBC15ADC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7036 |  | 2014-08-18 | 2014-08-18 14:58 | 2014-08-18 15:26 | YORK - H1RA042S06D | 85 | 4.8 | Yes | Yes | 17.1 | 19.9 | -2.8 | 3FA35C53BD5E49F986B02276B00DC277 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Pleasanton | CA | 94566-5470 |  | 2014-08-28 | 2014-08-28 09:04 | 2014-08-28 09:04 | AMERICAN STANDARD - 4A7A4048B1000AA | 240 | 0 | Yes | Yes | 22.5 | 18.8 | 3.7 | 77CB52999BB44B39A37CCB57181E8425 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-2417 |  | 2014-07-08 | 2014-07-08 13:19 | 2014-07-08 13:53 | PAYNE - PA10AJ036 | 76 | 2.9 | Yes | Yes | 23.7 | 20.3 | 3.4 | A973FA8EBF7E49D2822A01645B7FCEA0 |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Woodland | CA | 95776-6420 |  | 2014-07-28 | 2014-07-28 11:16 | 2014-07-28 11:16 | TRANE - 4TTX3030A1000AA | 66 | 0 | Yes | Yes | 12.3 | 15 | -2.7 | D86896C354E44549A6C9BA36E6C5DA8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7320 |  | 2014-07-15 | 2014-07-15 12:11 | 2014-07-15 12:11 | YORK - D1NP042N06506A | 150 | 0 | Yes | Yes | 22.6 | 17.9 | 4.7 | 3BA7DD63B78B42E2AFE13A8C530D959C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-2408 |  | 2014-07-08 | 2014-07-08 12:51 | 2014-07-08 13:08 | HEIL - HAC042 | 98 | -9.2 | Yes | Yes | 20.3 | 19.9 | 0.4 | B9A50110BB1447CE8FC7699CAF9C769F |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Shafter | CA | 93263-2506 |  | 2014-10-05 | 2014-10-05 19:15 | 2014-10-05 19:19 | GOODMAN - GPG1336045M11AB | 85 | 4.5 | Yes | Yes | 19.8 | 20.4 | -0.6 | A67221118D024894BA26520D5E64C8F9 |  | R410A | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Bakersfield | CA | 93301-1121 |  | 2014-10-21 | 2014-10-21 15:41 | 2014-10-21 15:41 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.8 | 22 | -1.2 | 31232F03FAA447F7AEEAC5AEA39503F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1536 |  | 2014-07-27 | 2014-07-27 20:22 | 2014-07-27 20:26 | OTHER - GR6GDX60K096C | 184 | -9.7 | Yes | Yes | 26.7 | 21.2 | 5.5 | 5787A54F01B24715B6071D5CA1E5B285 |  | R22 | TXV |  | -5.272% | 1.0527 | 1.476% |  |  |  |  | TXV |  |  | -5.272%
Woodland | CA | 95776-5396 |  | 2014-08-14 | 2014-08-14 09:37 | 2014-08-14 10:48 | CARRIER - 24ABA324A310 | 74 | 6.2 | Yes | Yes | 24.9 | 19.4 | 5.5 | 8FC1D4038DAD4DC8B3046CEBC41B1524 |  | R22 | Non-TXV |  | 8.378% | 0.91622 | 16.1% | [5 empty] | Non-TXV | 8.378%
Esparto | CA | 95627-2059 |  | 2014-08-08 | 2014-08-08 09:47 | 2014-08-08 10:54 | RUUD - UAHE-023JAS | 64 | 7.9 | Yes | Yes | 23.6 | 19.9 | 3.7 | 6FDC4E0EA2CA405E9D4C74C439AF1A18 |  | R22 | Non-TXV |  | 12.34% | 0.87656 | 23.72% | [5 empty] | Non-TXV | 12.34%
Bakersfield | CA | 93309-3274 |  | 2014-09-30 | 2014-09-30 11:13 | 2014-09-30 11:13 | UNITARY PRODUCTS GROUP - D1NP036N05606A | 108 | 0 | Yes | Yes | 20.2 | 18.8 | 1.4 | 363274A3C61E4D5794543A6382805727 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1103 |  | 2014-09-03 | 2014-09-03 08:48 | 2014-09-03 09:09 | LENNOX - GCS20RX5111002P | 115 | 4.9 | Yes | Yes | 20.8 | 20.4 | 0.4 | E9F44859476F4DF9B0C580CA26CB6E33 |  | R22 | Non-TXV |  | 4.261% | 0.95739 | 8.188% | [5 empty] | Non-TXV | 4.261%
Bakersfield | CA | 93306-3442 |  | 2014-06-30 | 2014-06-30 13:37 | 2014-06-30 13:37 | GOODMAN - GPG1336045M41A | 85 | 0 | Yes | Yes | 18.5 | 19.3 | -0.8 | E625ED79A6E44912A3D98EA27A447938 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2930 |  | 2014-09-07 | 2014-09-07 18:19 | 2014-09-07 18:21 | HEIL - PGC042K080F | 84 | 9.3 | Yes | Yes | 18.6 | 21.5 | -2.9 | 104E1F4F45584DAF9C2927F6F28D6E59 |  | R22 | Non-TXV |  | 11.07% | 0.88929 | 21.28% | [5 empty] | Non-TXV | 11.07%
Bakersfield | CA | 93304-3004 |  | 2014-06-25 | 2014-06-25 13:12 | 2014-06-25 13:12 | GOODMAN - GPG13240451BA | 77 | 0 | Yes | Yes | 16.8 | 17.5 | -0.7 | A869CF321F2047E19C4BF5A9C6B08BFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9334 |  | 2014-07-10 | 2014-07-10 11:00 | 2014-07-10 18:38 | TRANE - 4TTX4030B1000AA | 79 | 2.7 | Yes | Yes | 15.4 | 17.3 | -1.9 | E63098E8026B4ACFBF82C937BC043F24 |  | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Wasco | CA | 93280-2816 |  | 2014-08-10 | 2014-08-10 19:03 | 2014-08-10 19:08 | OTHER - N/A | 85 | 4.7 | Yes | Yes | 22.8 | 21.5 | 1.3 | A9AE737DDC924E26AE6345EBE99D3D5A |  | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Bakersfield | CA | 93309-6395 |  | 2014-10-15 | 2014-10-15 12:54 | 2014-10-15 12:54 | RHEEM - RRPL-B030JK06X | 76 | 0 | Yes | Yes | 23.4 | 19.3 | 4.1 | D7C1EC8B3467424F983115835A9F4CB3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6228 |  | 2014-07-10 | 2014-07-10 09:34 | 2014-07-10 09:34 | RHEEM - RRKA-A030JK06E | 75 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | C98101BFB8DA40A1A47B0BF4240AE112 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4854 |  | 2014-09-19 | 2014-09-19 13:35 | 2014-09-19 13:35 | GOODMAN - GPG13300451BB | 77 | 0 | Yes | Yes | 22.2 | 24.8 | -2.6 | A9D2F14CF7C742D188590FA67DB5469D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6214 |  | 2014-07-16 | 2014-07-16 10:22 | 2014-07-16 17:13 | YORK - D3NNZ030N03606NXC | 64 | 4.4 | Yes | Yes | 16.9 | 18 | -1.1 | E2096CF04E07405DAF6A8D63199185C7 |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Bakersfield | CA | 93307-5935 |  | 2014-09-09 | 2014-09-09 14:58 | 2014-09-09 14:58 | ICP - PGAA42C1K4 | 70 | 0 | Yes | Yes | 23 | 17.7 | 5.3 | D668A52CE4B943F3B00F2CC72CF03D2D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3317 |  | 2014-08-06 | 2014-08-06 11:36 | 2014-08-06 12:36 | STREAMLINE - 7B0042C100A0 | 78 | 6.9 | Yes | Yes | 17.9 | 18.8 | -0.9 | 369F231FC7B542DD8FCF52D16C6415AD |  | R22 | Non-TXV |  | 8.846% | 0.91154 | 17% | [5 empty] | Non-TXV | 8.846%
Shafter | CA | 93263-2667 |  | 2014-10-05 | 2014-10-05 18:56 | 2014-10-05 18:59 | RUUD - UAMB-036JAZ | 85 | 3.6 | Yes | Yes | 21.9 | 19.9 | 2 | 2FD73D5FDF7C4D2487F4AB67CC54A684 |  | R22 | Non-TXV |  | 4.235% | 0.95765 | 8.139% | [5 empty] | Non-TXV | 4.235%
Shafter | CA | 93263-2540 |  | 2014-09-20 | 2014-09-20 17:10 | 2014-09-20 17:13 | DAY & NIGHT - DAYP-F036N070A | 108 | 5.7 | Yes | Yes | 22.1 | 22 | 0.1 | 1C225A5B63F14A5086D51F5BD59DD0A1 |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Fairfield | CA | 94533-4423 |  | 2014-10-10 | 2014-10-10 08:37 | 2014-10-10 08:37 | - | 85 | 0 | Yes | Yes | 12 | 13.7 | -1.7 | 281538D47C79468E9CEA53D95748D673 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4774 |  | 2014-08-13 | 2014-08-13 11:20 | 2014-08-13 11:20 | RHEEM - RRNA-B030JK06X | 72 | 0 | Yes | Yes | 23.5 | 23.4 | 0.1 | C194001D4388428D8E29C4333F714F74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7827 |  | 2014-08-25 | 2014-08-25 11:26 | 2014-08-25 11:26 | YORK - H2DB036506A | 73 | 0 | Yes | Yes | 21.8 | 21.9 | -0.1 | 037C08282932498681C5082FC9EEC365 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4774 |  | 2014-08-13 | 2014-08-13 11:25 | 2014-08-13 11:25 | UNITARY PRODUCTS GROUP - DCYZ-F024N045A | 58 | 0 | Yes | Yes | 20.1 | 22.6 | -2.5 | 69C18E3E131B4A31B30B4657556C65CE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2749 |  | 2014-07-09 | 2014-07-09 14:19 | 2014-07-09 15:06 | OTHER - ACS048A2A1 | 101 | 11.1 | Yes | Yes | 20.6 | 23.1 | -2.5 | 53228ED743A84BD695E86B6AF7454F68 |  | R22 | Non-TXV |  | 10.99% | 0.8901 | 21.12% | [5 empty] | Non-TXV | 10.99%
San Jose | CA | 95125-5641 |  | 2014-07-09 | 2014-07-09 13:48 | 2014-07-09 14:10 | RUUD - RAKA048JAZ | 95 | -5.6 | Yes | Yes | 21.5 | 20.6 | 0.9 | 0EB616267DA7452180AFB74679987F4F |  | R22 | Non-TXV |  | -5.895% | 1.0589 | 1.651% |  |  |  |  | Non-TXV |  |  | -5.895%
Fremont | CA | 94538-3318 |  | 2014-08-26 | 2014-08-26 11:11 | 2014-08-26 11:34 | RHEEM - UKN | 96 | 12.2 | Yes | Yes | 24.8 | 19.1 | 5.8 | 3137CD9DC6374A9BA423CB62D56F1FB1 |  | R22 | Non-TXV |  | 12.71% | 0.87292 | 24.42% | [5 empty] | Non-TXV | 12.71%
Pittsburg | CA | 94565-6834 |  | 2014-09-10 | 2014-09-10 13:13 | 2014-09-10 13:13 | PAYNE - 5858J024 | 70 | 0 | Yes | Yes | 23.4 | 19.7 | 3.7 | 15FB776127864E9EB537A1F6468FD7D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3582 |  | 2014-09-23 | 2014-09-23 13:54 | 2014-09-23 13:54 | BDP - 585HJ030040 | 68 | 0 | Yes | Yes | 15.5 | 18 | -2.5 | 6ECEA1A021B544F9A73FACA4E6D68E1D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-4460 |  | 2014-08-26 | 2014-08-26 12:06 | 2014-08-26 12:26 | CARRIER - 38HDC060321 | 214 | 6.4 | Yes | Yes | 22.4 | 18.8 | 3.6 | 1ABD36ABD1B7485B9BDB8C5E46330297 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.747% | [5 empty] | Non-TXV | 2.991%
Bakersfield | CA | 93304-7013 |  | 2014-07-10 | 2014-07-10 11:12 | 2014-07-10 11:12 | LUXAIRE - TCJD36S41S3A | 73 | 0 | Yes | Yes | 23.9 | 20.4 | 3.5 | AE3D2A4C7F85453692E32C94D248F17D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8204 |  | 2014-09-17 | 2014-09-17 12:30 | 2014-09-17 13:08 | GE - | 91 | 4.2 | Yes | Yes | 19.7 | 19.9 | -0.2 | E2EAE87815F44FEAB242C5F7E885A012 |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Fremont | CA | 94539-6049 |  | 2014-08-27 | 2014-08-27 09:50 | 2014-08-27 10:07 | GOODMAN - CLJ60-1C | 141 | 5.2 | Yes | Yes | 19 | 18 | 1.1 | 2BE567C767AA472F9A47252D74B00B66 |  | R22 | Non-TXV |  | 3.688% | 0.96312 | 7.087% | [5 empty] | Non-TXV | 3.688%
Bakersfield | CA | 93308-7001 |  | 2014-09-14 | 2014-09-14 14:38 | 2014-09-14 14:38 | GOODMAN - GSH130241BB | 122 | 0 | Yes | Yes | 20.9 | 21 | -0.1 | 8D71A75152474CEEB6E7B034C9E0BB95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5398 |  | 2014-07-09 | 2014-07-09 13:24 | 2014-07-09 17:06 | CARRIER - 24ABA324A310 | 74 | -7 | Yes | Yes | 15.7 | 15.5 | 0.2 | C457D4F1D5B04323BD56BA14074994DE |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Woodland | CA | 95776-5401 |  | 2014-09-15 | 2014-09-15 10:52 | 2014-09-15 12:26 | CARRIER - 24ABA324A310 | 58 | 5.8 | Yes | Yes | 13.5 | 14.7 | -1.2 | 9B673E1F0637421BB1DF577F990F69CF |  | R410A | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Fremont | CA | 94539-8113 |  | 2014-08-06 | 2014-08-06 12:50 | 2014-08-06 13:26 | AMANA - ASX140241AD | 129 | 7.1 | Yes | Yes | 19.6 | 17.8 | 1.8 | A29E54F4B92243A091C009A0D182955D |  | R22 | Non-TXV |  | 5.504% | 0.94496 | 10.58% | [5 empty] | Non-TXV | 5.504%
Union City | CA | 94587-6007 |  | 2014-08-21 | 2014-08-21 12:11 | 2014-08-21 12:27 | CARRIER - 38CKB030320 | 71 | -7 | Yes | Yes | 18.6 | 16.8 | 1.8 | 1E99C207F5824C1A8E8220361E9A7C4B |  | R22 | TXV |  | -9.859% | 1.0986 | 2.761% |  |  |  |  | TXV |  |  | -9.859%
Davis | CA | 95616-7332 |  | 2014-08-19 | 2014-08-19 11:43 | 2014-08-19 12:16 | BARD - 563CN036-C | 101 | 4.5 | Yes | Yes | 19.4 | 18.8 | 0.6 | E58CF87343B9474C8183DD2CD9BAB9A1 |  | R22 | Non-TXV |  | 4.455% | 0.95545 | 8.562% | [5 empty] | Non-TXV | 4.455%
Davis | CA | 95616-7332 |  | 2014-08-19 | 2014-08-19 12:24 | 2014-08-19 13:14 | BARD - 563CNX036000A | 101 | 5.6 | Yes | Yes | 20.1 | 20.2 | 0 | BC90A7F7F7C24F35A1593ECD84F29B34 |  | R22 | Non-TXV |  | 5.545% | 0.94455 | 10.66% | [5 empty] | Non-TXV | 5.545%
Fremont | CA | 94538-3906 |  | 2014-08-06 | 2014-08-06 11:04 | 2014-08-06 12:32 | TRANE - 4TTR4030C1000AA | 106 | 0 | Yes | Yes | 17.8 | 19.9 | -2.1 | E11CA9106FC941CA9030097B75FF4F4D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4702 |  | 2014-07-11 | 2014-07-11 14:00 | 2014-07-11 14:22 | FRESCHI - FT29528 | 66 | 5.2 | Yes | Yes | 14.3 | 17.3 | -3 | A84267AD8A524BDFBD05C607D76AB278 |  | R22 | Non-TXV |  | 7.879% | 0.92121 | 15.14% | [5 empty] | Non-TXV | 7.879%
Fremont | CA | 94539-6086 |  | 2014-08-27 | 2014-08-27 10:26 | 2014-08-27 10:26 | CARRIER - 38CKC036330 | 82 | 0 | Yes | Yes | 20.3 | 18.7 | 1.6 | CD0A0D877EC64878BB83D59A14D0D7B7 |  | R22 | TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-6086 |  | 2014-08-27 | 2014-08-27 10:31 | 2014-08-27 10:51 | CARRIER - 38CKC036330 | 82 | 5 | Yes | Yes | 19 | 18.2 | 0.8 | C5F3F071CC5D4E5A834734743119F944 |  | R22 | TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | TXV | 6.098%
Mc Farland | CA | 93250-1340 |  | 2014-10-28 | 2014-10-28 11:26 | 2014-10-28 11:26 | GOODMAN - GPG1330045 | 77 | 0 | Yes | Yes | 26.9 | 20.9 | 6 | 414357E706CA470B843C1FAD82448C36 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-2830 |  | 2014-08-06 | 2014-08-06 10:41 | 2014-08-06 10:41 | YORK - H3DH036S06A | 95 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 6D3048801C0F415BB4113FDF9B6AEAF4 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2147 |  | 2014-07-16 | 2014-07-16 11:09 | 2014-07-16 15:22 | AMANA - YCX036F1OAC | 98 | 6.7 | Yes | Yes | 17.4 | 19 | -1.6 | A972E8A9C5024E029074A0EF2D025BE4 |  | R22 | Non-TXV |  | 6.837% | 0.93163 | 13.14% | [5 empty] | Non-TXV | 6.837%
Mc Farland | CA | 93250-1666 |  | 2014-10-28 | 2014-10-28 13:13 | 2014-10-28 13:13 | RHEEM - 13AJA36A01 | 108 | 0 | Yes | Yes | 22.5 | 19.3 | 3.2 | 538DEA67FD104F3882601488A8364EB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2760 |  | 2014-08-20 | 2014-08-20 11:09 | 2014-08-20 12:08 | COLEMAN - TCJD36S41S3A | 73 | 3.6 | Yes | Yes | 22.8 | 20.4 | 2.4 | 513129CD53D949089338791067EBEA6A |  | R410A | Non-TXV |  | 4.932% | 0.95068 | 9.477% | [5 empty] | Non-TXV | 4.932%
Pleasanton | CA | 94566-6384 |  | 2014-08-28 | 2014-08-28 10:01 | 2014-08-28 10:01 | OTHER - LSR-42-1 | 92 | 0 | Yes | Yes | 20.5 | 19.3 | 1.2 | C54CA6C29B2545CC9E68452717CC5A2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3953 |  | 2014-08-13 | 2014-08-13 09:29 | 2014-08-13 09:29 | RHEEM - 1RMAN036JK06X | 99 | 0 | Yes | Yes | 19 | 21 | -2 | 5553A6BD975E4B30B06787D62668B329 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5525 |  | 2014-10-07 | 2014-10-07 11:07 | 2014-10-07 11:44 | CARRIER - PETE0300-6894E- | 83 | 3.7 | Yes | Yes | 20.4 | 20.4 | 0 | B759B8DD66A3416498E35A2F44D24D67 |  | R22 | Non-TXV |  | 4.458% | 0.95542 | 8.567% | [5 empty] | Non-TXV | 4.458%
Fairfield | CA | 94533-2615 |  | 2014-07-21 | 2014-07-21 09:36 | 2014-07-21 19:20 | - | 85 | 3 | Yes | Yes | 15.9 | 18.8 | -2.9 | BE94255958964087B90DDF690DA05B5F |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93307-4282 |  | 2014-07-18 | 2014-07-18 13:30 | 2014-07-18 13:30 | UNITARY PRODUCTS GROUP - DBYP-F036N070A | 108 | 0 | Yes | Yes | 21.6 | 18.1 | 3.5 | CE742AFDE5CB44F192924FCA67A4EA4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-2467 |  | 2014-08-07 | 2014-08-07 12:55 | 2014-08-07 13:13 | CARRIER - R060 | 192 | 8.6 | Yes | Yes | 21.7 | 17.1 | 4.6 | 47C9A9AEBED1409D92C9952C487BD9FC |  | R410A | TXV |  | 4.479% | 0.95521 | 8.608% | [5 empty] | TXV | 4.479%
Woodland | CA | 95695-3874 |  | 2014-07-28 | 2014-07-28 12:07 | 2014-07-28 12:07 | CARRIER - 584BNH018010AA85 | 131 | 4.9 | Yes | Yes | 19.2 | 21.2 | -2 | 655FACC9529E441CB66BCE04425B76A8 | Add refrigerant: 4.9 oz | R22 | Non-TXV |  | 3.74% | 0.9626 | 7.188% | [5 empty] | Non-TXV | 3.74%
San Jose | CA | 95129-5100 |  | 2014-07-18 | 2014-07-18 13:57 | 2014-07-18 13:57 | BRYANT - 538ANX06000 | 216 | 0 | Yes | Yes | 24.8 | 20.3 | 4.5 | 9808E9BD4FF5415F93E9AA71BECBF8AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2527 |  | 2014-07-21 | 2014-07-21 09:49 | 2014-07-21 19:21 | YORK - H2CB024S06B | 65 | -4.6 | Yes | Yes | 13.3 | 16.1 | -2.8 | 08224991B2C14797AEFE11AB20524490 |  | R22 | Non-TXV |  | -7.077% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.077%
Fremont | CA | 94538-1842 |  | 2014-08-07 | 2014-08-07 14:09 | 2014-08-07 14:28 | TRANE - 2TTR3036A1000AA | 101 | -4.4 | Yes | Yes | 17.7 | 17.5 | 0.2 | 050135EE00254FF89F69C0168697DDA3 |  | R22 | TXV |  | -4.356% | 1.0436 | 1.22% |  |  |  |  | TXV |  |  | -4.356%
Wasco | CA | 93280-1639 |  | 2014-11-04 | 2014-11-04 13:42 | 2014-11-04 13:42 | OTHER - PGX336060K01A1 | 162 | 0 | Yes | Yes | 17.1 | 20.1 | -3 | 8631747514954E1689E9C829BB6C96FE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-1005 |  | 2014-08-12 | 2014-08-12 10:08 | 2014-08-12 10:32 | AMERICAN STANDARD - 2A7A2042B1000AA | 85 | 2.6 | Yes | Yes | 18.9 | 18.7 | 0.2 | 86CF95AD918143AEB29B6046FB999B7E |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93308-5669 |  | 2014-11-26 | 2014-11-26 15:27 | 2014-11-26 15:27 | BDP - 561CJ024C | 69 | 0 | Yes | Yes | 22.2 | 19.8 | 2.4 | C6780B52E3E04E90A397EA03DC5D6421 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3712 |  | 2014-08-01 | 2014-08-01 12:09 | 2014-08-01 15:07 | CARRIER - 38TXA048320 | 174 | 6.8 | Yes | Yes | 18.4 | 20.4 | -2 | DA81D3B683F64700B21C21A4C1046198 |  | R410A | Non-TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | Non-TXV | 3.908%
Fremont | CA | 94539-3721 |  | 2014-08-12 | 2014-08-12 11:24 | 2014-08-12 11:45 | CARRIER - 38CKC048360 | 109 | 11.7 | Yes | Yes | 21 | 18.7 | 2.3 | EA4C2BB8C906410BBF0815EA394669EE |  | R22 | TXV |  | 10.73% | 0.89266 | 20.63% | [5 empty] | TXV | 10.73%
Bakersfield | CA | 93313-4587 |  | 2014-08-22 | 2014-08-22 09:00 | 2014-08-22 09:00 | OTHER - EAFF-049JAZ | 163 | 0 | Yes | Yes | 19.9 | 22.5 | -2.6 | 261228BC52EB48CFA15082FFE35B44AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5140 |  | 2014-09-12 | 2014-09-12 09:48 | 2014-09-12 10:09 | DAY & NIGHT - 541D1024 | 118 | -8.3 | Yes | Yes | 17.6 | 20.1 | -2.5 | DD8FD11C968541428DF74979BEDB322C |  | R22 | Non-TXV |  | -7.034% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.034%
Bakersfield | CA | 93309-4992 |  | 2014-09-19 | 2014-09-19 09:21 | 2014-09-19 09:21 | ICP - PGF324040K01 | 65 | 0 | Yes | Yes | 24.9 | 19.1 | 5.8 | 9927E73B633B43E5BC4EAC3D4AD0BA82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4903 |  | 2014-09-19 | 2014-09-19 15:24 | 2014-09-19 15:24 | CARRIER - 48K1024300BE | 50 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | D8AA6DDEFC8D4D41B2CA68A9DBFB6ECD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6631 |  | 2014-07-16 | 2014-07-16 08:29 | 2014-07-16 17:11 | CARRIER - 38TRA036330 | 85 | -6 | Yes | Yes | 14.8 | 17.7 | -2.9 | 664490AEB8024B3D95A02990015D48EF |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93304-7111 |  | 2014-07-31 | 2014-07-31 12:49 | 2014-07-31 12:49 | CARRIER - 585A030080YACR | 50 | 0 | Yes | Yes | 25.6 | 19.9 | 5.7 | 23DC00D9060A4C36B7D582DDC89FBC68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5937 |  | 2014-09-12 | 2014-09-12 13:47 | 2014-09-12 13:47 | HEIL - PGAA42C1K1 | 82 | 0 | Yes | Yes | 19.5 | 21.5 | -2 | DF829658275D4527BE155BF6A5027207 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4714 |  | 2014-08-06 | 2014-08-06 11:52 | 2014-08-06 11:52 | GOODMAN - GPG153609041AB | 102 | 0 | Yes | Yes | 27.2 | 21.5 | 5.7 | 6263947201BB46639C193936C30ED2C1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6518 |  | 2014-07-24 | 2014-07-24 09:07 | 2014-07-24 09:07 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | F0AA8ED6078D40D38C2F9D230E82C37C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-8853 |  | 2014-09-25 | 2014-09-25 12:39 | 2014-09-25 12:39 | TRANE - 4YCC3042B1096AA | 120 | 0 | Yes | Yes | 20.9 | 18.7 | 2.2 | 944E3CD11709477D9FF57207B62A9CE0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5037 |  | 2014-09-19 | 2014-09-19 11:31 | 2014-09-19 11:31 | CONCORD - R9PG10B24D050BA | 52 | 0 | Yes | Yes | 20 | 22.6 | -2.6 | 0FBC3E8A874542888681C4B2703E1196 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5329 |  | 2014-07-15 | 2014-07-15 10:19 | 2014-07-15 22:19 | CARRIER - 24ABA436A300 | 116 | 4.2 | Yes | Yes | 17.2 | 19.3 | -2.1 | 99A9C3E42F0949F0A066451A749C71AD |  | R22 | Non-TXV |  | 3.621% | 0.96379 | 6.958% | [5 empty] | Non-TXV | 3.621%
San Jose | CA | 95110-2816 |  | 2014-10-01 | 2014-10-01 10:45 | 2014-10-01 10:45 | CARRIER - 38HDC030-331 | 115 | 0 | Yes | Yes | 19.8 | 19.9 | -0.1 | EEE85851C5364234ABA22782C2D6E2C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1198 |  | 2014-09-02 | 2014-09-02 16:22 | 2014-09-02 16:22 | BDP - 585HJ03004 | 68 | 0 | Yes | Yes | 21.8 | 21.9 | -0.1 | 19D739BD2E2F4B7DA91688038F79E026 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5404 |  | 2014-07-10 | 2014-07-10 10:11 | 2014-07-10 18:44 | CARRIER - 24ABA31BA310 | 74 | -7 | Yes | Yes | 14.7 | 17.5 | -2.8 | 7CEE92454DA74A4E8AA27C34DD495537 |  | R410A | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Bakersfield | CA | 93304-7278 |  | 2014-07-15 | 2014-07-15 14:35 | 2014-07-15 14:35 | GOODMAN - GPG1360090M41DA | 85 | 0 | Yes | Yes | 24.1 | 19.3 | 4.8 | 91A87E80C6CC406C97F0AF0058DDA6B2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1139 |  | 2014-07-19 | 2014-07-19 17:40 | 2014-07-19 17:44 | GOODMAN - GPG133045M41AC | 80 | 3.1 | Yes | Yes | 24.2 | 20.2 | 4 | C7358E9957924BE3A42EE4CF028A5A54 |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Bakersfield | CA | 93309-5073 |  | 2014-09-30 | 2014-09-30 15:53 | 2014-09-30 15:53 | CONCORD - RPG10B36D050LA-9B | 58 | 0 | Yes | Yes | 26.1 | 21.5 | 4.6 | 6F23DD0CD7314336BB0F073F71D4BAD3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5038 |  | 2014-09-19 | 2014-09-19 11:43 | 2014-09-19 11:43 | CONCORD - RPG12B24D050A | 72 | 0 | Yes | Yes | 18.9 | 21.3 | -2.4 | D9EE0DEE7B79471383213B959E6D40CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7602 |  | 2014-07-31 | 2014-07-31 13:24 | 2014-07-31 13:24 | GOODMAN - GSC130301ER | 90 | 0 | Yes | Yes | 16.9 | 18.8 | -1.9 | 9890F6B30E8E40838761E964EE4F90F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-5218 |  | 2014-08-12 | 2014-08-12 09:16 | 2014-08-12 09:32 | HEIL - CA3042VKA1 | 99 | 4 | Yes | Yes | 18.8 | 18.5 | 0.3 | 1C9EB74A47EB49949E392CF1B75CB2EF |  | R22 | Non-TXV |  | 4.04% | 0.9596 | 7.765% | [5 empty] | Non-TXV | 4.04%
Bakersfield | CA | 93304-7127 |  | 2014-07-15 | 2014-07-15 11:39 | 2014-07-15 11:39 | PAYNE - PY3GNAA48090NA | 100 | 0 | Yes | Yes | 23.8 | 19.3 | 4.5 | 91D39E6F5D254F438AA4409BE5344E8D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5167 |  | 2014-09-15 | 2014-09-15 08:29 | 2014-09-15 08:54 | GOODMAN - CPLE24-1A | 106 | 5.4 | Yes | Yes | 16.4 | 17.8 | -1.4 | 5D039E4D51BF472BA2B94669712278F1 |  | R22 | Non-TXV |  | 5.094% | 0.94906 | 9.79% | [5 empty] | Non-TXV | 5.094%
Woodland | CA | 95695-3741 |  | 2014-07-10 | 2014-07-10 13:16 | 2014-07-10 18:37 | GOODMAN - CKL18-1M | 85 | 7.1 | Yes | Yes | 14.7 | 17 | -2.3 | 722D6231BEB3487CA338CF1F2D1B6558 |  | R22 | Non-TXV |  | 8.353% | 0.91647 | 16.05% | [5 empty] | Non-TXV | 8.353%
Bakersfield | CA | 93304-7181 |  | 2014-07-15 | 2014-07-15 11:19 | 2014-07-15 11:19 | BDP - 585EJ042075 | 84 | 0 | Yes | Yes | 23.7 | 19.6 | 4.2 | 0E30A3E218EA4447B6F314D92D1AABB4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3741 |  | 2014-07-10 | 2014-07-10 13:34 | 2014-07-10 18:36 | GOODMAN - CKL18-1M | 72 | 2.3 | Yes | Yes | 16 | 17.7 | -1.7 | 837A8D710AFB46C8A05D8D7E03D1BE74 |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Antioch | CA | 94509-7343 |  | 2014-11-11 | 2014-11-11 13:09 | 2014-11-11 13:09 | PAYNE - PA10JA036-C | 70 | 0 | Yes | Yes | 22.8 | 19 | 3.8 | 2C05DE0A4411486E857F0D89D8EA962E |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3741 |  | 2014-07-09 | 2014-07-09 14:52 | 2014-07-09 16:18 | GOODMAN - CKL18-1M | 91 | 5.4 | Yes | Yes | 17.7 | 20.4 | -2.7 | F095F0EB261749A296DD5034B1DD355C |  | R22 | Non-TXV |  | 5.934% | 0.94066 | 11.4% | [5 empty] | Non-TXV | 5.934%
Napa | CA | 94558-7303 |  | 2014-09-08 | 2014-09-08 15:34 | 2014-09-08 18:32 | AIRE-FLO - HAC036AKA1 | 80 | 4.6 | Yes | Yes | 18.6 | 19.9 | -1.3 | B33A38C9350646F0908FE6E51C84A804 |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Woodland | CA | 95776-5397 |  | 2014-07-10 | 2014-07-10 14:35 | 2014-07-10 15:00 | CARRIER - 24ABA324A300 | 74 | 7.7 | Yes | Yes | 10.1 | 11.7 | -1.6 | EFA0291826FC4A819D7893E8E6D4DF04 |  | R410A | Non-TXV |  | 10.41% | 0.89595 | 20% | [5 empty] | Non-TXV | 10.41%
W Sacramento | CA | 95691-3761 |  | 2014-07-14 | 2014-07-14 15:18 | 2014-07-14 18:01 | RUUD - RRNL-B036JK06X | 89 | 3.4 | Yes | Yes | 12.3 | 13.7 | -1.4 | B8CEF74ACA9D408C84992C6D347C9E13 |  | R22 | Non-TXV |  | 3.82% | 0.9618 | 7.342% | [5 empty] | Non-TXV | 3.82%
Bakersfield | CA | 93309-5924 |  | 2014-07-23 | 2014-07-23 09:15 | 2014-07-23 09:15 | RHEEM - RRNA-B042JK08X | 104 | 0 | Yes | Yes | 25.1 | 20.1 | 5 | B001A78EC5F24F26A12484D51AF3732D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8613 |  | 2014-09-19 | 2014-09-19 12:10 | 2014-09-19 12:10 | CARRIER - | 73 | 0 | Yes | Yes | 20.8 | 18.8 | 2 | 4E8FE86F4FE5436FAFD42F6DA0621C27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3547 |  | 2014-09-15 | 2014-09-15 11:37 | 2014-09-15 11:37 | OTHER - HAMC-F036AA | 85 | 0 | Yes | Yes | 20.5 | 19.8 | 0.7 | ADC86BD8C4F24564982E2936993ED2DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6360 |  | 2014-07-11 | 2014-07-11 13:59 | 2014-07-11 13:59 | BRYANT - 574ANW048090NA | 193 | 0 | Yes | Yes | 20.7 | 19.9 | 0.8 | F46E501AF9514444A9BAE472888A4D40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-3448 |  | 2014-08-28 | 2014-08-28 10:46 | 2014-08-28 10:46 | TAPPAN - UNK | 85 | 0 | Yes | Yes | 19.9 | 16.4 | 3.5 | 9F4E09ED456049C7A2F045CCE24A002C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6610 |  | 2014-07-11 | 2014-07-11 11:01 | 2014-07-11 11:01 | UNITARY PRODUCTS GROUP - D2NP03030N63606NXA | 73 | 0 | Yes | Yes | 21.7 | 20.5 | 1.2 | D30DA93D758743FEA734C16FC08B5714 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95134-1571 |  | 2014-07-10 | 2014-07-10 14:18 | 2014-07-10 14:42 | BRYANT - 661CJ018 | 72 | 6.9 | Yes | Yes | 20.3 | 19.9 | 0.4 | 94D1C36AA00747CB8D6594A5E5D64C8D |  | R22 | Non-TXV |  | 9.583% | 0.90417 | 18.42% | [5 empty] | Non-TXV | 9.583%
Bakersfield | CA | 93307-4590 |  | 2014-07-24 | 2014-07-24 16:03 | 2014-07-24 16:03 | ICP - GPFM30K060E | 51 | 0 | Yes | Yes | 18.9 | 21.3 | -2.4 | AA706171D4174B26BD8D50A587F7C64C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-5938 |  | 2014-08-07 | 2014-08-07 15:05 | 2014-08-07 15:30 | TRANE - TTR042C100A2 | 110 | 7.2 | Yes | Yes | 14.6 | 16.9 | -2.3 | 31AD8CDF499942D18332CDEAAB318D62 |  | R22 | Non-TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | Non-TXV | 6.545%
Shafter | CA | 93263-2877 |  | 2014-09-07 | 2014-09-07 17:53 | 2014-09-07 17:55 | RHEEM - RRGG-05N31JKR | 48 | 3.8 | Yes | Yes | 21.6 | 19.7 | 1.9 | 6EFAEB87B5054B4F90D12E951F00A0A8 |  | R22 | Non-TXV |  | 7.917% | 0.92083 | 15.21% | [5 empty] | Non-TXV | 7.917%
Fairfield | CA | 94534-3946 |  | 2014-07-21 | 2014-07-21 11:26 | 2014-07-21 19:21 | - 561AJ048-0 | 85 | 18 | Yes | Yes | 16.6 | 16.6 | 0 | AED7F0E89E184DA0801693DAA430A5F5 |  | R22 | Non-TXV |  | 21.18% | 0.78824 | 40.7% | [5 empty] | Non-TXV | 21.18%
Davis | CA | 95616-2866 |  | 2014-07-11 | 2014-07-11 11:22 | 2014-07-11 19:55 | LENNOX - HS29-211-2P | 58 | 3.3 | Yes | Yes | 15.8 | 18.2 | -2.4 | 981551524A1949D0A6532171E8B13B83 |  | R22 | Non-TXV |  | 5.69% | 0.9431 | 10.93% | [5 empty] | Non-TXV | 5.69%
Antioch | CA | 94509-1233 |  | 2014-11-12 | 2014-11-12 11:28 | 2014-11-12 11:53 | CARRIER - 38CKC042-341 | 80 | 9 | Yes | Yes | 21.9 | 18.2 | 3.7 | E2CF4DB3698F48E6966943A1834729BD |  | R22 | TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | TXV | 11.25%
San Jose | CA | 95148-3145 |  | 2014-07-10 | 2014-07-10 13:16 | 2014-07-10 13:16 | AMANA - SSX160481AB | 242 | 0 | Yes | Yes | 19.6 | 21.3 | -1.7 | 07E40FA8B8604371ACAE3A2A92DAA465 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3161 |  | 2014-09-07 | 2014-09-07 18:11 | 2014-09-07 18:11 | OTHER - GCGD42S21S1A | 72 | 0 | Yes | Yes | 16.2 | 20.8 | -4.6 | 3AB03983A34548CABAD79FB637895832 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5949 |  | 2014-07-31 | 2014-07-31 11:06 | 2014-07-31 11:06 | AMERICAN STANDARD - 2YCC3042A1064AA | 131 | 0 | Yes | Yes | 17 | 16.8 | 0.2 | 144153806DE9498EBA55B136D754919B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5185 |  | 2014-10-29 | 2014-10-29 12:24 | 2014-10-29 12:24 | BDP - 585EJ024050 | 54 | 0 | Yes | Yes | 26.7 | 20.7 | 6 | 68582CBE52BA46849FE5E915F2103BD1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2445 |  | 2014-11-05 | 2014-11-05 18:18 | 2014-11-05 18:37 | YORK - D2GH030032320CK | 85 | 2.7 | Yes | Yes | 13.5 | 16.4 | -2.9 | 33615CCA35884AB6A9E9EE3A1C09EF49 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Wasco | CA | 93280-2250 |  | 2014-07-28 | 2014-07-28 14:35 | 2014-07-28 14:37 | HEIL - HAC042AKA4 | 98 | 20 | Yes | Yes | 22.1 | 20.4 | 1.7 | C94A4DC893A440329D910C0FE134B988 |  | R22 | Non-TXV |  | 20.41% | 0.79592 | 39.22% | [5 empty] | Non-TXV | 20.41%
Bakersfield | CA | 93307-4450 |  | 2014-07-24 | 2014-07-24 11:21 | 2014-07-24 11:21 | OTHER - UKN | 90 | 0 | Yes | Yes | 20.2 | 19.1 | 1.1 | A489A76F25184AC38F39D5460DE407E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4519 |  | 2014-07-18 | 2014-07-18 15:29 | 2014-07-18 15:53 | LENNOX - 13HPD-030-230-01 | 132 | 4.4 | Yes | Yes | 19.8 | 19.9 | -0.1 | E3E77A399C7E47AF873545F60F054794 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Rio Vista | CA | 94571-2115 |  | 2014-08-29 | 2014-08-29 10:28 | 2014-08-29 12:32 | YORK - H1RC030S06D | 76 | 5.8 | Yes | Yes | 15.1 | 17.2 | -2.1 | 361323CAD70241F69D1098D1DD46F75F |  | R22 | Non-TXV |  | 7.632% | 0.92368 | 14.67% | [5 empty] | Non-TXV | 7.632%
Davis | CA | 95616-2863 |  | 2014-07-11 | 2014-07-11 11:39 | 2014-07-11 19:54 | RHEEM - | 85 | -8 | Yes | Yes | 16.6 | 18.2 | -1.6 | 7476CF3E75724DBB98EFFB0AAE7B7923 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Shafter | CA | 93263-3541 |  | 2014-09-21 | 2014-09-21 18:35 | 2014-09-21 18:37 | OTHER - N2A348AKA200 | 121 | 18.6 | Yes | Yes | 24 | 22.6 | 1.4 | 1F62C504A8C846DF9ED3306AF0CE1B7B |  | R22 | Non-TXV |  | 15.37% | 0.84628 | 29.54% | [5 empty] | Non-TXV | 15.37%
Rio Vista | CA | 94571-2113 |  | 2014-10-15 | 2014-10-15 11:27 | 2014-10-15 12:05 | CARRIER - 38BRC03010 | 87 | 4.2 | Yes | Yes | 18 | 20.4 | -2.4 | 786B14E5153445DF93AE662CC0F3D23A |  | R22 | Non-TXV |  | 4.828% | 0.95172 | 9.278% | [5 empty] | Non-TXV | 4.828%
Woodland | CA | 95695-5087 |  | 2014-07-23 | 2014-07-23 11:30 | 2014-07-23 12:43 | BRYANT - 48SD-042090301 | 168 | 7 | Yes | Yes | 15 | 17.4 | -2.4 | 012C9AC0F3A54E1DB55673F9E81046A3 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Davis | CA | 95616-2830 |  | 2014-07-11 | 2014-07-11 12:35 | 2014-07-11 19:53 | AIRE-FLO - HS29-018-3P | 60 | -5.6 | Yes | Yes | 17.9 | 17.4 | 0.5 | 78ABD4B5733B4D7DBA52AA1169EA8816 |  | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Davis | CA | 95616-2831 |  | 2014-07-11 | 2014-07-11 19:53 | 2014-07-11 19:53 | - | 85 | 0 | Yes | Yes | 18.9 | 17.2 | 1.7 | 86AE921EC4594A2DB34D9358B9F12877 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2048 |  | 2014-07-22 | 2014-07-22 08:43 | 2014-07-22 08:43 | BDP - 541DJ024 | 118 | 0 | Yes | Yes | 13.9 | 16.8 | -2.9 | C014AC3C00774F5CB585CA022F6935BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2830 |  | 2014-07-14 | 2014-07-14 18:02 | 2014-07-14 18:41 | BRYANT - | 68 | 2.7 | Yes | Yes | 19.1 | 19.9 | -0.8 | 57CE2FDE187547E5941203A86ADB627E |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Vallejo | CA | 94591-8493 |  | 2014-08-04 | 2014-08-04 10:53 | 2014-08-04 12:02 | BDP - 541DJ181 | 93 | 5.1 | Yes | Yes | 18 | 18.8 | -0.8 | DBC99598DC524270949E834FB71D438E |  | R22 | Non-TXV |  | 5.484% | 0.94516 | 10.54% | [5 empty] | Non-TXV | 5.484%
Davis | CA | 95616-2801 |  | 2014-08-19 | 2014-08-19 14:31 | 2014-08-19 15:19 | AIRE-FLO - | 40 | 2.9 | Yes | Yes | 19.7 | 20.9 | -1.2 | 4B4F70383BE0412C8DB5917CC31B2538 |  | R22 | Non-TXV |  | 7.25% | 0.9275 | 13.93% | [5 empty] | Non-TXV | 7.25%
Bakersfield | CA | 93313-3473 |  | 2014-07-09 | 2014-07-09 15:46 | 2014-07-09 15:46 | UNITARY PRODUCTS GROUP - D1NH048N06506C | 72 | 0 | Yes | Yes | 25.8 | 21 | 4.8 | 71F3582E95634FC5B9E9EC346E75529A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3432 |  | 2014-10-23 | 2014-10-23 12:58 | 2014-10-23 12:58 | LENNOX - 13GEP42075ALP-4A | 90 | 0 | Yes | Yes | 22.7 | 18.8 | 3.9 | 159DBFC6062E400EBB6CBC5FB1ADFE97 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2335 |  | 2014-09-06 | 2014-09-06 19:11 | 2014-09-06 19:13 | GOODMAN - GPG133660461AC | 112 | 12.6 | Yes | Yes | 20.5 | 19 | 1.5 | 40A782BA44A14271895B1DE1ECAD12B2 |  | R22 | Non-TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | Non-TXV | 11.25%
Bakersfield | CA | 93304-2525 |  | 2014-07-11 | 2014-07-11 15:40 | 2014-07-11 15:40 | UNITARY PRODUCTS GROUP - D1NH036N07206A | 104 | 0 | Yes | Yes | 26.4 | 20.7 | 5.7 | 19501993C5CC475E999D0114E15141B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-9131 |  | 2014-09-18 | 2014-09-18 16:34 | 2014-09-18 16:34 | RHEEM - RRMA-A048JK10X | 115 | 0 | Yes | Yes | 28.9 | 23.1 | 5.8 | EF67E388E8304A979AAB937B0C0D150E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-9285 |  | 2014-09-03 | 2014-09-03 10:59 | 2014-09-03 10:59 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.6 | 19.2 | -0.6 | 1CC93614EF5545FCBAA7948AF0697632 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3426 |  | 2014-09-26 | 2014-09-26 14:30 | 2014-09-26 14:30 | ICP - CA9048VUKA1 | 206 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 602A1C00B82F42A39CCFCC3C82F01570 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8615 |  | 2014-08-25 | 2014-08-25 15:12 | 2014-08-25 15:12 | OTHER - 584AN030040 | 216 | 0 | Yes | Yes | 21 | 20.7 | 0.4 | 7B9CFC2DE9464208ABE4B8799B4BCE2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2652 |  | 2014-09-23 | 2014-09-23 16:21 | 2014-09-23 17:27 | - | 85 | 20.1 | Yes | Yes | 18.1 | 20.2 | -2.1 | C06EEA6F95964DA28F87289227D3D0BB |  | R22 | Non-TXV |  | 23.65% | 0.76353 | 45.44% | [5 empty] | Non-TXV | 23.65%
Bakersfield | CA | 93304-5953 |  | 2014-07-31 | 2014-07-31 10:43 | 2014-07-31 10:43 | GOODMAN - GSX130481BA | 40 | 0 | Yes | Yes | 23.6 | 21 | 2.6 | 0D99288DD69A4A85A8189D72D9FF9A0A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3475 |  | 2014-10-16 | 2014-10-16 12:13 | 2014-10-16 12:13 | ICP - PGME36G0907 | 103 | 0 | Yes | Yes | 24.9 | 19.9 | 5 | F7EF8BCE8EFA4FBD989D7721A3872E86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2619 |  | 2014-08-14 | 2014-08-14 11:13 | 2014-08-14 11:13 | OTHER - AA1CJX30-C | 71 | 0 | Yes | Yes | 20.8 | 21.9 | -1.1 | 9B7B9E65F7C24CC088F98BFDCB9CD5D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5355 |  | 2014-08-29 | 2014-08-29 10:00 | 2014-08-29 10:00 | GOODMAN - GSD130601BC | 169 | 0 | Yes | Yes | 22.5 | 21.8 | 0.7 | E00A20689766410B9D38C318C8B1814E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5653 |  | 2014-08-27 | 2014-08-27 11:41 | 2014-08-27 11:41 | CARRIER - 24ABB342W300 | 93 | 0 | Yes | Yes | 18.5 | 21.3 | -2.8 | 18330A6256A845E29B6356BAC7FA3230 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-5913 |  | 2014-08-18 | 2014-08-18 11:27 | 2014-08-18 11:45 | RHEEM - UNK | 85 | 3 | Yes | Yes | 15.8 | 17.9 | -2.1 | CD42CD096D4C4F2B865A336B1F0ABBB2 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Pittsburg | CA | 94565-4480 |  | 2014-09-15 | 2014-09-15 13:43 | 2014-09-15 13:43 | ICP - N4A336AKB300 | 89 | 0 | Yes | Yes | 16.9 | 19.3 | -2.4 | 4C648F51A301495BAFE82404814E135B |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4147 |  | 2014-07-23 | 2014-07-23 10:17 | 2014-07-23 10:17 | ARCOAIRE - | 80 | 0 | Yes | Yes | 14 | 17 | -3 | 33EBEAD68DCA420E8F0D83324EE1B3FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6465 |  | 2014-07-23 | 2014-07-23 11:02 | 2014-07-23 11:02 | YORK - D1NH042N06506C | 94 | 0 | Yes | Yes | 23.4 | 17.9 | 5.5 | 10A954B946C449549A4D4A91F40AD545 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4287 |  | 2014-08-29 | 2014-08-29 09:15 | 2014-08-29 09:15 | GOODMAN - PGB042075-1 | 68 | 0 | Yes | Yes | 13.5 | 19.4 | -5.9 | C3BDC9C9D97C432A9B3EB5EB6AC3CC14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4992 |  | 2014-09-19 | 2014-09-19 09:17 | 2014-09-19 09:17 | CARRIER - 48KL-024-31BE | 114 | 0 | Yes | Yes | 26.3 | 21 | 5.3 | 9CE4B52C467C47F89C7B96DF2B0B77AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2330 |  | 2014-09-20 | 2014-09-20 17:03 | 2014-09-20 17:06 | OTHER - PGF336060K01 | 146 | 5.1 | Yes | Yes | 22.2 | 22 | 0.2 | A247961E1A4B4D7689AC42EB0A66F172 |  | R22 | Non-TXV |  | 3.493% | 0.96507 | 6.713% | [5 empty] | Non-TXV | 3.493%
Bakersfield | CA | 93311-2646 |  | 2014-08-14 | 2014-08-14 11:33 | 2014-08-14 12:07 | ICP - CA9048VKD2 | 163 | 11.4 | Yes | Yes | 19.7 | 21 | -1.3 | 589BAEA882284F0BB2F746B97DE1FB65 |  | R22 | Non-TXV |  | 6.994% | 0.43 | 109.5% | [5 empty] | Non-TXV | 6.994%
San Jose | CA | 95136-1418 |  | 2014-07-10 | 2014-07-10 09:53 | 2014-07-10 10:10 | BRYANT - 561CJ036 | 72 | 6.5 | Yes | Yes | 18.4 | 20.2 | -1.8 | 604D1F76345D4F83905C50DBB8AF7337 |  | R22 | Non-TXV |  | 9.028% | 0.90972 | 17.35% | [5 empty] | Non-TXV | 9.028%
Fresno | CA | 93704-5753 |  | 2014-07-15 | 2014-07-15 14:01 | 2014-07-15 14:01 | RHEEM - RRPL-B030JK06X | 76 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | 6A8D9DE0454A40BE8EAB05A580834D8B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5363 |  | 2014-08-27 | 2014-08-27 13:15 | 2014-08-27 13:15 | GOODMAN - GSC130361DE | 119 | 0 | Yes | Yes | 18 | 22.9 | -4.9 | D1F2907CC85B4F7EB3D60693E2C2433B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5363 |  | 2014-08-27 | 2014-08-27 13:14 | 2014-08-27 13:14 | GOODMAN - GSC130361DE | 119 | 0 | Yes | Yes | 20 | 21.4 | -1.4 | 181D1BE4B1CF4E3C8A3030CC1803E8EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1257 |  | 2014-10-15 | 2014-10-15 15:36 | 2014-10-15 15:36 | - | 85 | 0 | Yes | Yes | 24.6 | 22.5 | 2.1 | 5ADE09CCF88C4B8AB9FEAE2F688B611A |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5807 |  | 2014-07-14 | 2014-07-14 16:20 | 2014-07-14 16:58 | GE - H2RA036S06E | 64 | 9.3 | Yes | Yes | 11.1 | 14 | -2.9 | C01C4577E857420CACFBB86D62013ACB |  | R22 | Non-TXV |  | 14.53% | 0.85469 | 27.93% | [5 empty] | Non-TXV | 14.53%
Shafter | CA | 93263-9733 |  | 2014-09-21 | 2014-09-21 18:51 | 2014-09-21 18:52 | HEIL - PGF336060K1A1 | 176 | 9.2 | Yes | Yes | 21.4 | 22.1 | -0.7 | 30719AC0556D4EAC8F0336A9B66C23FF |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Shafter | CA | 93263-9733 |  | 2014-09-21 | 2014-09-21 18:55 | 2014-09-21 18:57 | HEIL - PGF336060K1A1 | 176 | 5.5 | Yes | Yes | 24.1 | 21.7 | 2.4 | FBFBAC1CD06241FFABE403C43C91E040 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Winters | CA | 95694-2012 |  | 2014-09-30 | 2014-09-30 12:55 | 2014-09-30 19:19 | AMERICAN STANDARD - YCC030F1MOBH | 88 | 6.1 | Yes | Yes | 18.6 | 20.4 | -1.8 | 5F1BEE32C468455CB07164B4392F4E81 |  | R22 | Non-TXV |  | 6.932% | 0.93068 | 13.32% | [5 empty] | Non-TXV | 6.932%
Bakersfield | CA | 93313-2749 |  | 2014-08-29 | 2014-08-29 14:51 | 2014-08-29 14:51 | ICP - ACS0S6A2A1 | 87 | 0 | Yes | Yes | 21 | 22.3 | -1.3 | A2105A084DB44BA080B90FA7E10B1437 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8630 |  | 2014-09-22 | 2014-09-22 12:17 | 2014-09-22 13:08 | TRANE - 2TWR1018A1000AB | 69 | 3 | Yes | Yes | 21.7 | 20.4 | 1.3 | 8D7D6BB174C643848EBA2C47842508F3 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Antioch | CA | 94531-6673 |  | 2014-10-08 | 2014-10-08 08:33 | 2014-10-08 08:33 | YORK - UNK | 85 | 0 | Yes | Yes | 21.6 | 18.3 | 3.3 | 4447B17DCFE04258A80F7E28F58A8748 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4415 |  | 2014-08-15 | 2014-08-15 09:20 | 2014-08-15 09:20 | RUUD - UKN | 90 | 0 | Yes | Yes | 15.5 | 17.1 | -1.6 | 9E40183E78C24538A0945D985B66BA35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4128 |  | 2014-09-17 | 2014-09-17 11:35 | 2014-09-17 11:35 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20 | 20.8 | -0.8 | 2AD3D31E3D7B4F56AA0DEE7360A21F5A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5501 |  | 2014-07-24 | 2014-07-24 14:11 | 2014-07-24 16:28 | TEMPSTAR - PGC30K060E | 55 | -4.5 | Yes | Yes | 19 | 16.1 | 2.9 | 973DE071CC09412A8B0934C4C5DC0723 |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Bakersfield | CA | 93305-5408 |  | 2014-11-03 | 2014-11-03 15:48 | 2014-11-03 15:48 | BDP - 585EJ024050 | 54 | 0 | Yes | Yes | 25.5 | 20.4 | 5.1 | 1062E9615F91425AA569B1D3C2F80FBE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4105 |  | 2014-07-29 | 2014-07-29 14:09 | 2014-07-29 14:45 | CARRIER - 2997E16182 | 136 | 5.7 | Yes | Yes | 12.3 | 14.8 | -2.5 | A2100B4C8EEB41CA8500CC89CD168DC6 |  | R22 | Non-TXV |  | 4.191% | 0.95809 | 8.055% | [5 empty] | Non-TXV | 4.191%
Dixon | CA | 95620-2744 |  | 2014-07-29 | 2014-07-29 16:08 | 2014-07-29 16:34 | TRANE - YCY036G1MOAC | 136 | 4.6 | Yes | Yes | 17.8 | 19.9 | -2.1 | CCB0C031E33F49CD8A3817A48260AA3A |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Davis | CA | 95618-6007 |  | 2014-07-14 | 2014-07-14 11:48 | 2014-07-14 13:28 | TRANE - DAD718A90B0 | 87 | -8.2 | Yes | Yes | 10.7 | 13.6 | -2.9 | EF31F075AC674831980747B5CE452204 |  | R22 | Non-TXV |  | -9.425% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.425%
Fresno | CA | 93727-7922 |  | 2014-07-18 | 2014-07-18 12:48 | 2014-07-18 13:04 | BRYANT - 582ANW030060AAAD | 59 | 6 | Yes | Yes | 18.9 | 18.3 | 0.6 | 8E1030799836442BBCF7DB98D4430542 |  | R22 | Non-TXV |  | 10.17% | 0.89831 | 19.54% | [5 empty] | Non-TXV | 10.17%
Bakersfield | CA | 93307-4460 |  | 2014-07-18 | 2014-07-18 10:16 | 2014-07-18 10:16 | DAY & NIGHT - 594AN036060 | 102 | 0 | Yes | Yes | 23.6 | 20.2 | 3.4 | F1F309A324AD41F694FA2F812DCE7710 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4112 |  | 2014-07-18 | 2014-07-18 13:47 | 2014-07-18 13:47 | UNITARY PRODUCTS GROUP - DAYP-FO36NO70A | 108 | 0 | Yes | Yes | 19.2 | 13.5 | 5.8 | 892C438DF5384E3FB10090D6EF4012FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5165 |  | 2014-07-24 | 2014-07-24 11:10 | 2014-07-24 12:07 | CARRIER - 36CKC042356 | 93 | 3.5 | Yes | Yes | 16.6 | 15.8 | 0.8 | F75B745A6B2C4534A12BCED55CC31EF6 |  | R22 | Non-TXV |  | 3.763% | 0.96237 | 7.233% | [5 empty] | Non-TXV | 3.763%
San Jose | CA | 95123-1622 |  | 2014-07-11 | 2014-07-11 14:07 | 2014-07-11 14:35 | - RCB030A2C | 79 | -4.6 | Yes | Yes | 25.1 | 20.3 | 4.8 | F2F2B5B4BF264A8C953F9E06D52B6C15 |  | R22 | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Pittsburg | CA | 94565-4775 |  | 2014-09-16 | 2014-09-16 15:28 | 2014-09-16 15:28 | CONCORD - 2AC13L48P-1A | 203 | 0 | Yes | Yes | 21.2 | 20.8 | 0.4 | 3D73CCB3FF854619A991E36525F49D9F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4230 |  | 2014-07-28 | 2014-07-28 13:30 | 2014-07-28 13:30 | AMERICAN STANDARD - YCC024F1L0BJ | 65 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 013B99629FFC44769FA05AC397C8CC5A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4232 |  | 2014-07-29 | 2014-07-29 15:46 | 2014-07-29 16:06 | GOODMAN - GPG12240451A | 64 | 4.3 | Yes | Yes | 25 | 20.4 | 4.6 | 648388906CC749A8B54EF3DE3DB2BA37 |  | R22 | Non-TXV |  | 6.719% | 0.93281 | 12.91% | [5 empty] | Non-TXV | 6.719%
Bakersfield | CA | 93305-4152 |  | 2014-08-06 | 2014-08-06 10:21 | 2014-08-06 10:21 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 25.3 | 20.4 | 4.9 | 8B85D429682B4615B763ECE4AE122C2D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2758 |  | 2014-08-09 | 2014-08-09 17:22 | 2014-08-09 17:24 | YORK - H2RD042S06B | 141 | 6.8 | Yes | Yes | 19.6 | 20.4 | -0.8 | CA23D3564AD24F25871B67B7500EB017 |  | R22 | Non-TXV |  | 4.823% | 0.95177 | 9.268% | [5 empty] | Non-TXV | 4.823%
Vacaville | CA | 95688-2627 |  | 2014-10-13 | 2014-10-13 11:16 | 2014-10-13 11:41 | PAYNE - PA10JA042-C | 91 | 5.9 | Yes | Yes | 18 | 20.4 | -2.4 | 6EBB4B61F1EA4141A0D223E0E7B8A217 |  | R22 | Non-TXV |  | 6.484% | 0.93516 | 12.46% | [5 empty] | Non-TXV | 6.484%
Davis | CA | 95616-2809 |  | 2014-07-17 | 2014-07-17 08:49 | 2014-07-17 22:06 | HEIL - CA3018VKA1 | 68 | 2.7 | Yes | Yes | 15.3 | 18.2 | -2.9 | F1D02312BE8B42C09FC568F4263E9DD4 |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Vallejo | CA | 94590-3012 |  | 2014-09-17 | 2014-09-17 12:57 | 2014-09-17 18:24 | CARRIER - CTCG458-945-0001 | 72 | 3.9 | Yes | Yes | 18.2 | 20.4 | -2.2 | FBB4F3F2F4B64A1DA6149EC060EDF51C |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Bay Point | CA | 94565-6756 |  | 2014-09-09 | 2014-09-09 10:20 | 2014-09-09 10:44 | OTHER - TCGD48S21S2A | 69 | 6.7 | Yes | Yes | 31.7 | 20.9 | 10.8 | D4C8CBD192C440B3969ABC472C0EB850 |  | R22 | TXV |  | 9.71% | 0.9029 | 18.66% | [5 empty] | TXV | 9.71%
Bakersfield | CA | 93313-2206 |  | 2014-08-27 | 2014-08-27 13:35 | 2014-08-27 13:35 | YORK - D1NP036W05606A | 108 | 0 | Yes | Yes | 21 | 21.4 | -0.4 | 3342F3F87B6B4ED3B5FF3AFB39977371 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3638 |  | 2014-07-14 | 2014-07-14 15:40 | 2014-07-14 17:58 | TRANE - TTD742B100A0 | 98 | 6.6 | Yes | Yes | 10.5 | 13.3 | -2.8 | 00CA4AC4D2B442D384E30ABD2CFEC62F |  | R22 | Non-TXV |  | 6.735% | 0.93265 | 12.94% | [5 empty] | Non-TXV | 6.735%
Fresno | CA | 93705-2148 |  | 2014-07-28 | 2014-07-28 14:04 | 2014-07-28 14:37 | OTHER - UNK | 67 | 8.9 | Yes | Yes | 25 | 23.1 | 1.9 | F6FC29A9C6714A2ABD8CD9717FDA93A1 |  | R22 | Non-TXV |  | 13.28% | 0.86716 | 25.53% | [5 empty] | Non-TXV | 13.28%
Shafter | CA | 93263-2672 |  | 2014-09-06 | 2014-09-06 19:03 | 2014-09-06 19:07 | YORK - H2RD042S06B | 141 | 40.3 | Yes | Yes | 22.7 | 20.9 | 1.8 | 10D8A817C59C4D35BC2DB3BEAD53CD9F |  | R22 | TXV |  | 28.58% | 0.71418 | 54.93% | [5 empty] | TXV | 28.58%
Fairfield | CA | 94533-1863 |  | 2014-07-21 | 2014-07-21 12:29 | 2014-07-21 19:23 | - | 85 | 2.5 | Yes | Yes | 18 | 17.7 | 0.3 | EE9708EE0E964662A2122938BA7253E7 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Davis | CA | 95618-4887 |  | 2014-07-11 | 2014-07-11 15:24 | 2014-07-11 18:52 | COLEMAN - N | 93 | -6.6 | Yes | Yes | 10.8 | 13.3 | -2.5 | 1C1A297659624232BBA3E05A2BA7F7D7 |  | R22 | Non-TXV |  | -7.097% | 1.071 | 1.987% |  |  |  |  | Non-TXV |  |  | -7.097%
Suisun City | CA | 94585-3736 |  | 2014-08-05 | 2014-08-05 13:16 | 2014-08-05 14:18 | HEIL - NAC048AKA1 | 108 | -7.6 | Yes | Yes | 16.7 | 18.5 | -1.8 | 9D176A7C82D3441E87C5FCA748E550BC |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Shafter | CA | 93263-2613 |  | 2014-09-06 | 2014-09-06 18:41 | 2014-09-06 18:45 | OTHER - NRGC30HAK02 | 55 | 16 | Yes | Yes | 17.7 | 19.9 | -2.2 | 85F6194B2EE84A4DA8AC4A9AE7807D12 |  | R22 | Non-TXV |  | 29.09% | 0.70909 | 55.91% | [5 empty] | Non-TXV | 29.09%
Bakersfield | CA | 93311-8900 |  | 2014-08-14 | 2014-08-14 16:04 | 2014-08-14 16:04 | WEATHER KING - 13AJA60A01 | 191 | 0 | Yes | Yes | 20.5 | 20.8 | -0.3 | 95A611CFAA054CB99405D885655E34A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2861 |  | 2014-08-19 | 2014-08-19 14:19 | 2014-08-19 15:20 | RHEEM - | 53 | 5.2 | Yes | Yes | 23.8 | 19.9 | 3.9 | F985342FCBF341BEB72CA57C3F7F6740 |  | R22 | Non-TXV |  | 9.811% | 0.90189 | 18.86% | [5 empty] | Non-TXV | 9.811%
Bakersfield | CA | 93307-7062 |  | 2014-07-24 | 2014-07-24 13:13 | 2014-07-24 13:13 | ICP - PGAA30C1K6 | 79 | 0 | Yes | Yes | 18.2 | 20.4 | -2.2 | 45F703C321E0475BB5CCC6C219CD8A05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4705 |  | 2014-09-29 | 2014-09-29 09:11 | 2014-09-29 09:11 | CARRIER - 48XP-048115311 | 85 | 0 | Yes | Yes | 24.1 | 18.8 | 5.3 | 45DB3C2FDA1C45E1A0FCDB69F50AE5EB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1000 |  | 2014-08-26 | 2014-08-26 10:32 | 2014-08-26 10:32 | UNITARY PRODUCTS GROUP - D1NA024N03606C | 54 | 0 | Yes | Yes | 21 | 21.7 | -0.7 | 7709868B57594CF0BBCCD41B683BAE57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2342 |  | 2014-07-25 | 2014-07-25 10:40 | 2014-07-25 11:02 | DAY & NIGHT - PGN348090K01A1 | 197 | 7.5 | Yes | Yes | 24.2 | 19.9 | 4.3 | B79D281D4832420C8F0D46357D7BA9FE |  | R22 | Non-TXV |  | 3.807% | 0.96193 | 7.316% | [5 empty] | Non-TXV | 3.807%
Bakersfield | CA | 93311-9524 |  | 2014-10-19 | 2014-10-19 17:30 | 2014-10-19 17:32 | LENNOX - 13ACD-0420320-02 | 111 | 8.8 | Yes | Yes | 21.6 | 20.4 | 1.2 | 09003B2D8A4B440B85D6AEC5C4A89128 |  | R22 | Non-TXV |  | 7.928% | 0.92072 | 15.24% | [5 empty] | Non-TXV | 7.928%
Concord | CA | 94518-3705 |  | 2014-08-20 | 2014-08-20 11:15 | 2014-08-20 11:15 | AIRE-FLO - AM018M1021G | 49 | 0 | Yes | Yes | 16 | 17.4 | -1.4 | 0F0E5C766E3F474DA1C9750A1CFD2ECB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4330 |  | 2014-07-23 | 2014-07-23 09:12 | 2014-07-23 09:41 | DAY & NIGHT - 585A030080YAC | 50 | 3.3 | Yes | Yes | 23.1 | 18.5 | 4.7 | E35B2D9B33D64EC787F872D783CA65CD |  | R22 | Non-TXV |  | 6.6% | 0.934 | 12.68% | [5 empty] | Non-TXV | 6.6%
San Jose | CA | 95123-5938 |  | 2014-07-11 | 2014-07-11 09:31 | 2014-07-11 09:57 | - 9541-801 | 52 | 3.7 | Yes | Yes | 20.7 | 20.3 | 0.4 | 0E9B42E8756049878A149D784F5927B8 |  | R22 | Non-TXV |  | 7.115% | 0.92885 | 13.67% | [5 empty] | Non-TXV | 7.115%
Bakersfield | CA | 93307-6207 |  | 2014-10-28 | 2014-10-28 16:19 | 2014-10-28 16:19 | RHEEM - RRNA042JK08X | 104 | 0 | Yes | Yes | 20.5 | 22.3 | -1.8 | 4A6D1F74B2B14BA6B74E91AD711837EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1204 |  | 2014-08-29 | 2014-08-29 11:08 | 2014-08-29 11:08 | - | 85 | 0 | Yes | Yes | 18.5 | 18.8 | -0.3 | D8458420E8B24E7D904E2D109B46CEA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7121 |  | 2014-09-19 | 2014-09-19 17:44 | 2014-09-19 18:10 | AMANA - EP2-030AHY001 | 78 | 5.1 | Yes | Yes | 22.8 | 20.4 | 2.4 | 1A279A68D4E5490EBFF607516090C8F1 |  | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Bakersfield | CA | 93306-6364 |  | 2014-09-17 | 2014-09-17 09:45 | 2014-09-17 09:45 | ICP - PGF324040K01A1 | 126 | 0 | Yes | Yes | 20.1 | 18.7 | 1.4 | 64C5B6B691BD49EC9171565BAEA3950D |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95134-1592 |  | 2014-07-17 | 2014-07-17 10:11 | 2014-07-17 10:41 | BRYANT - 691CJ24A | 76 | 7.6 | Yes | Yes | 20.1 | 19.9 | 0.2 | 0B47004A72F747EB86488F040C1F0C68 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93728-3834 |  | 2014-07-15 | 2014-07-15 11:37 | 2014-07-15 12:07 | GOODMAN - VSX130421AC | 90 | -4.6 | Yes | Yes | 27.9 | 22 | 5.9 | 0A97C5CE30574846B48996DA66CF8930 |  | R410A | Non-TXV |  | -5.111% | 1.0511 | 1.431% |  |  |  |  | Non-TXV |  |  | -5.111%
Vallejo | CA | 94591-5655 |  | 2014-10-07 | 2014-10-07 11:43 | 2014-10-07 13:36 | BDP - ETR24018345-3 | 74 | 3.7 | Yes | Yes | 23 | 20.4 | 2.6 | EAAE52EEB8B240B78EA018ABA5B335DD |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fremont | CA | 94555-1280 |  | 2014-08-20 | 2014-08-20 10:17 | 2014-08-20 10:47 | OTHER - UKN | 85 | 6.8 | Yes | Yes | 17.3 | 17.7 | -0.4 | C904BEFCE6134682B1FB2EB7D0578316 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Vacaville | CA | 95688-3819 |  | 2014-08-06 | 2014-08-06 09:57 | 2014-08-06 22:12 | - | 85 | -8 | Yes | Yes | 17.6 | 18.2 | -0.6 | AC98A9B2C4B44F74A7D9DE156F786B11 |  | R410A | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93309-8003 |  | 2014-08-25 | 2014-08-25 15:54 | 2014-08-25 15:54 | ICP - PGD348090K00K1 | 103 | 0 | Yes | Yes | 20.4 | 23.2 | -2.8 | B088BE9C981A4723A8052670EED87270 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4546 |  | 2014-08-22 | 2014-08-22 14:22 | 2014-08-22 14:22 | CARRIER - 38CKB030320 | 76 | 0 | Yes | Yes | 23.3 | 21.2 | 2.2 | 1E0757DA6F034D06B2072BE631135449 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4393 |  | 2014-09-18 | 2014-09-18 14:21 | 2014-09-18 14:21 | ICP - PGF024K040E | 57 | 0 | Yes | Yes | 19.1 | 19.8 | -0.7 | B2AE37FD8ADC44D1AF0031D916C576E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3103 |  | 2014-08-10 | 2014-08-10 20:48 | 2014-08-10 20:50 | HEIL - PGC042K080D | 87 | 6.7 | Yes | Yes | 23.8 | 22.1 | 1.7 | 5A02BB9AE11F468285732FBE97039DE7 |  | R22 | Non-TXV |  | 7.701% | 0.92299 | 14.8% | [5 empty] | Non-TXV | 7.701%
Bakersfield | CA | 93306-6016 |  | 2014-07-30 | 2014-07-30 14:51 | 2014-07-30 14:51 | ICP - PGD336090K001C1 | 100 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 6FD3D62CEDE34F93B4279EBC656A8FCA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4304 |  | 2014-07-28 | 2014-07-28 12:31 | 2014-07-28 12:31 | RHEEM - UKN | 90 | 0 | Yes | Yes | 28.2 | 22.8 | 5.4 | B5713A14FC774C5EB2EA68E32EB7E225 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1483 |  | 2014-08-11 | 2014-08-11 12:40 | 2014-08-11 12:40 | UNITARY PRODUCTS GROUP - F030N070A | 73 | 0 | Yes | Yes | 20 | 22.5 | -2.5 | AC4137643CD34B9D99D3F51BDCA2E521 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4419 |  | 2014-10-29 | 2014-10-29 10:38 | 2014-10-29 10:56 | YORK - H1RA042S06G | 84 | 30.1 | Yes | Yes | 22.7 | 20.8 | 1.9 | 2B2D09A0F0C7409BA0ACBF36C9BC9511 |  | R22 | Non-TXV |  | 35.83% | 0.64167 | 68.86% | [5 empty] | Non-TXV | 35.83%
Fresno | CA | 93705-3748 |  | 2014-07-22 | 2014-07-22 13:52 | 2014-07-22 14:16 | DAY & NIGHT - 585B024050YACR | 51 | 1.7 | Yes | Yes | 20.7 | 18.8 | 1.9 | 978E8A24059640CD9A5D64DFF7F96768 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93704-3829 |  | 2014-07-15 | 2014-07-15 12:40 | 2014-07-15 13:01 | RUUD - CA5536VKD1 | 82 | 8.8 | Yes | Yes | 20 | 21.3 | -1.3 | 5D464F8831314073A096CC0AF856A82B |  | R22 | Non-TXV |  | 10.73% | 0.89268 | 20.62% | [5 empty] | Non-TXV | 10.73%
Fairfield | CA | 94533-8919 |  | 2014-08-20 | 2014-08-20 13:21 | 2014-08-20 13:51 | CARRIER - 38CKC042---351 | 93 | 4.6 | Yes | Yes | 22 | 18.8 | 3.2 | B267EB8A7BE04D21B01AF6CBD7711123 |  | R22 | Non-TXV |  | 4.946% | 0.95054 | 9.506% | [5 empty] | Non-TXV | 4.946%
Bakersfield | CA | 93309-5785 |  | 2014-09-19 | 2014-09-19 13:51 | 2014-09-19 13:51 | UNITARY PRODUCTS GROUP - DRCS0361BE | 83 | 0 | Yes | Yes | 22.9 | 20.4 | 2.5 | 92B8D148D4BD4F13AB8CD1D8E0E0C2CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3448 |  | 2014-07-18 | 2014-07-18 14:51 | 2014-07-18 16:04 | - | 85 | 2.7 | Yes | Yes | 15.7 | 18.3 | -2.6 | 0835C97CFD804175BB03797FEA0E392F |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93304-5873 |  | 2014-08-13 | 2014-08-13 09:17 | 2014-08-13 09:17 | BDP - 585EJ030050 | 58 | 0 | Yes | Yes | 15.9 | 17.4 | -1.5 | E3EF55F7E49C496896464B7ACB98062F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-3742 |  | 2014-07-15 | 2014-07-15 12:17 | 2014-07-15 12:40 | TRANE - 2TTR1042A100AA | 91 | 5.8 | Yes | Yes | 15 | 16.1 | -1.1 | EEE5EDA45197404D80AB7492946C6C81 |  | R22 | Non-TXV |  | 6.374% | 0.93626 | 12.25% | [5 empty] | Non-TXV | 6.374%
Bakersfield | CA | 93313-0000 |  | 2014-08-29 | 2014-08-29 14:03 | 2014-08-29 14:03 | ICP - N2A348AKA200 | 123 | 4.2 | Yes | Yes | 23 | 20.3 | 2.7 | 551C3AF367204E07866D3B625FAF3697 | Add refrigerant: 4.2 oz | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Fresno | CA | 93702-2815 |  | 2014-07-17 | 2014-07-17 11:57 | 2014-07-17 11:57 | RHEEM - RRPL13030JK06X | 76 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | DC0C7C64D0DC4B4781DF370D47BCA334 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4854 |  | 2014-09-16 | 2014-09-16 11:06 | 2014-09-16 11:06 | ICP - PGC024K040D | 58 | 0 | Yes | Yes | 19.5 | 19.4 | 0.1 | 1B5F12794D3843A6955F0A17C50F5ADC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6200 |  | 2014-07-21 | 2014-07-21 12:54 | 2014-07-21 12:54 | GOODMAN - GPG13420701AA | 107 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 95D7B5E4A6ED434B8989CCF4599072CA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3709 |  | 2014-07-22 | 2014-07-22 10:58 | 2014-07-22 11:37 | ARCOAIRE - PGF042080E | 84 | 4.2 | Yes | Yes | 21 | 20.6 | 0.4 | 2B35EF77AB7848C6B7107468687966E9 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Pittsburg | CA | 94565-5603 |  | 2014-09-16 | 2014-09-16 09:47 | 2014-09-16 09:47 | RHEEM - RAFD-036JAS | 80 | 0 | Yes | Yes | 21.1 | 21 | 0.1 | BD690100BEA44C009AC0DBD7D08BE124 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-0000 |  | 2014-07-18 | 2014-07-18 09:50 | 2014-07-18 10:14 | OTHER - PA13NR030-F | 85 | 8.9 | Yes | Yes | 17.8 | 18.1 | -0.3 | 13435957E14044F5A1EF17EA89ACDA61 |  | R22 | TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | TXV | 10.47%
Arvin | CA | 93203-2307 |  | 2014-11-06 | 2014-11-06 12:33 | 2014-11-06 12:49 | RHEEM - RR851-3619X | 85 | 4.5 | Yes | Yes | 20 | 21.3 | -1.3 | 45E714B60B234645BD6FF07D42E58097 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Clovis | CA | 93612-3701 |  | 2014-07-21 | 2014-07-21 13:34 | 2014-07-21 14:12 | RHEEM - RRKAA036JK06X | 62 | 5.1 | Yes | Yes | 21.2 | 20.5 | 0.8 | 55BA14BED45D4774A8316DCCF48AF607 |  | R22 | Non-TXV |  | 8.226% | 0.91774 | 15.81% | [5 empty] | Non-TXV | 8.226%
Clovis | CA | 93611-0311 |  | 2014-07-24 | 2014-07-24 15:12 | 2014-07-24 15:33 | LENNOX - HS146519P | 209 | 15.4 | Yes | Yes | 24.6 | 19.5 | 5.1 | F42CB89C5C124367ACF932E514F4C6D8 |  | R22 | Non-TXV |  | 7.368% | 0.92632 | 14.16% | [5 empty] | Non-TXV | 7.368%
Martinez | CA | 94553-3463 |  | 2014-08-18 | 2014-08-18 09:22 | 2014-08-18 22:27 | TRANE - BTD736A100B0 | 86 | 3.1 | Yes | Yes | 16.2 | 17.4 | -1.2 | 6578A2B91E5D4BCFB7B8358FECF98A65 |  | R22 | Non-TXV |  | 3.605% | 0.96395 | 6.927% | [5 empty] | Non-TXV | 3.605%
Bakersfield | CA | 93304-6155 |  | 2014-09-22 | 2014-09-22 14:50 | 2014-09-22 14:50 | UNITARY PRODUCTS GROUP - PCGD4851SAB | 73 | 0 | Yes | Yes | 18.1 | 20.7 | -2.6 | 3C8FD37F797C45899459C689A0DF2A3D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7023 |  | 2014-07-21 | 2014-07-21 14:23 | 2014-07-21 14:23 | - 38EN036320 | 85 | 0 | Yes | Yes | 15.8 | 18.1 | -2.3 | 9B9FB986B7A947E0B3DD8193C88CDFC6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95134-1596 |  | 2014-07-14 | 2014-07-14 14:51 | 2014-07-14 19:18 | BRYANT - 561CJ01800 | 70 | 15.2 | Yes | Yes | 21.9 | 20.4 | 1.5 | 031168E0F52747D4A591242DA5134CCD |  | R22 | Non-TXV |  | 21.71% | 0.78286 | 41.73% | [5 empty] | Non-TXV | 21.71%
Davis | CA | 95616-1827 |  | 2014-07-14 | 2014-07-14 10:42 | 2014-07-14 11:22 | CARRIER - 38CKC024330 | 59 | 6.3 | Yes | Yes | 16.8 | 18.8 | -2 | 238F6D3E58FD4EA89F406117E355E287 |  | R22 | Non-TXV |  | 10.68% | 0.89322 | 20.52% | [5 empty] | Non-TXV | 10.68%
Fresno | CA | 93726-7105 |  | 2014-07-16 | 2014-07-16 11:35 | 2014-07-16 12:02 | CARRIER - 48GS042060301 | 100 | 5.6 | Yes | Yes | 24.3 | 18.6 | 5.7 | DDE2111071634F42B459FA618AB529D0 |  | R22 | Non-TXV |  | 5.6% | 0.944 | 10.76% | [5 empty] | Non-TXV | 5.6%
Wasco | CA | 93280-2346 |  | 2014-10-29 | 2014-10-29 09:55 | 2014-10-29 09:55 | GOODMAN - GPG13300451AB | 77 | 0 | Yes | Yes | 25.6 | 20.4 | 5.2 | E07157DC3BB84287889FCD028B9F714C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6804 |  | 2014-07-22 | 2014-07-22 10:00 | 2014-07-22 10:28 | CARRIER - UNK | 52 | 3 | Yes | Yes | 20.1 | 19.7 | 0.4 | 46361CC89EBA480F9F7CBBFF6FA6FB72 |  | R22 | Non-TXV |  | 5.769% | 0.94231 | 11.09% | [5 empty] | Non-TXV | 5.769%
San Jose | CA | 95129-2307 |  | 2014-07-15 | 2014-07-15 08:58 | 2014-07-15 09:16 | PAYNE - PA13NA060 | 133 | 19.2 | Yes | Yes | 18.1 | 19.3 | -1.2 | 9CAA549748A94D54BE61C258D249B35F |  | R410A | Non-TXV |  | 14.44% | 0.85564 | 27.74% | [5 empty] | Non-TXV | 14.44%
Fresno | CA | 93726-3404 |  | 2014-07-28 | 2014-07-28 09:39 | 2014-07-28 10:32 | RHEEM - RRPLB042JK08X | 112 | 3.7 | Yes | Yes | 21.5 | 21.2 | 0.3 | 5308D319587D4AE6A4978B4210A06762 |  | R410A | Non-TXV |  | 3.304% | 0.96696 | 6.349% | [5 empty] | Non-TXV | 3.304%
San Jose | CA | 95134-1587 |  | 2014-07-14 | 2014-07-14 11:05 | 2014-07-14 13:26 | BRYANT - 661CJ018 | 73 | 10.1 | Yes | Yes | 18.1 | 20.6 | -2.5 | 722F77C5280A4FD293D82926136EB691 |  | R22 | Non-TXV |  | 13.84% | 0.86164 | 26.59% | [5 empty] | Non-TXV | 13.84%
Bakersfield | CA | 93304-5038 |  | 2014-08-21 | 2014-08-21 14:40 | 2014-08-21 14:40 | GOODMAN - GPG15448111541AA | 172 | 0 | Yes | Yes | 23.7 | 21.9 | 1.8 | 28EE317B7EEF4F3DB1F5459459901F03 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2346 |  | 2014-10-29 | 2014-10-29 10:05 | 2014-10-29 10:05 | GOODMAN - GPG13300451AB | 77 | 0 | Yes | Yes | 21.8 | 19.9 | 1.9 | 0CF2912A375A4DDDB31CB74B3C640E98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94555-2307 |  | 2014-08-19 | 2014-08-19 13:56 | 2014-08-19 13:56 | CARRIER - 563CN030-A | 140 | 0 | Yes | Yes | 18.5 | 18.5 | 0 | 690439E725C34709B43C60CE993E70F6 |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3857 |  | 2014-09-08 | 2014-09-08 12:48 | 2014-09-08 12:48 | BRYANT - 561CJ024-E | 57 | 0 | Yes | Yes | 18.4 | 18.5 | -0.1 | F5CDFEE47BBC4368BD8ADDE74FEE3A3B |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4036 |  | 2014-07-11 | 2014-07-11 09:52 | 2014-07-11 09:52 | ICP - PGAD36D1K7 | 100 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | A36F3683039B4C78A5B508E6DC65E3AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5180 |  | 2014-07-24 | 2014-07-24 13:48 | 2014-07-24 14:13 | GOODMAN - RRNLC060JK10E | 173 | 7.6 | Yes | Yes | 23.6 | 20.8 | 2.8 | 740461C41B5A46819325B374FCD3D1F2 |  | R410A | Non-TXV |  | 4.393% | 0.95607 | 8.443% | [5 empty] | Non-TXV | 4.393%
W Sacramento | CA | 95605-2228 |  | 2014-07-14 | 2014-07-14 13:54 | 2014-07-14 13:54 | DAY & NIGHT - DAY-F048N080A | 152 | 0 | Yes | Yes | 17.5 | 18.6 | -1.1 | E0950314F606471E92843FC91AD416C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2684 |  | 2014-10-31 | 2014-10-31 09:46 | 2014-10-31 09:46 | OTHER - C36ACD1V | 87 | 0 | Yes | Yes | 22.8 | 20.1 | 2.7 | FCDD4354F22F465E9D42A478038E23AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-9534 |  | 2014-09-03 | 2014-09-03 13:23 | 2014-09-03 13:23 | DUCANE - 2AC13P36P-2B | 128 | 0 | Yes | Yes | 19.5 | 21.9 | -2.4 | 51801BDEF3254DDFAD05D3319F7F17F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4863 |  | 2014-09-02 | 2014-09-02 13:24 | 2014-09-02 13:24 | GOODMAN - CC048-16 | 225 | 0 | Yes | Yes | 20 | 22.3 | -2.3 | 0528E0118D9D4D21B383CFDE6CACC727 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1731 |  | 2014-07-22 | 2014-07-22 17:10 | 2014-07-22 17:13 | RHEEM - N/A | 50 | -3.5 | Yes | Yes | 19.6 | 21 | -1.4 | 2E5EDED1CB3F4E36A4DCDACA5F127FB5 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93703-3844 |  | 2014-07-17 | 2014-07-17 13:33 | 2014-07-17 13:33 | MAYTAG - PPG1G030K072X | 83 | 0 | Yes | Yes | 20.3 | 20.2 | 0.1 | FBE74B1BDD73479EA486B1CE1AEAF65C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1923 |  | 2014-07-21 | 2014-07-21 15:01 | 2014-07-21 15:01 | OTHER - GSC130301DA | 87 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | DAC676528F564CD98A0C88E07CF01FF3 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3307 |  | 2014-07-17 | 2014-07-17 15:55 | 2014-07-17 16:14 | RUUD - SRM51843A | 49 | 5.2 | Yes | Yes | 26.9 | 21.7 | 5.2 | 40526E43D1F1426BB6C3FE6C4EF55687 |  | R22 | Non-TXV |  | 10.61% | 0.89388 | 20.39% | [5 empty] | Non-TXV | 10.61%
Fresno | CA | 93722-2653 |  | 2014-07-15 | 2014-07-15 15:53 | 2014-07-15 16:38 | LENNOX - M/N 13ACC-036-230-01 | 115 | 14.4 | Yes | Yes | 24.8 | 20.6 | 4.2 | 7C5CD0B5B3F54471A4955DFA5E1425F1 |  | R22 | Non-TXV |  | 12.52% | 0.87478 | 24.06% | [5 empty] | Non-TXV | 12.52%
Fresno | CA | 93722-2653 |  | 2014-07-15 | 2014-07-15 17:40 | 2014-07-15 17:57 | LENNOX - M/N 13ACC-036-230-01 | 115 | -8.1 | Yes | Yes | 20.4 | 19.9 | 0.5 | EEABDA5C197A42888DA39EDAFB01D912 |  | R22 | TXV |  | -7.043% | 1.0704 | 1.973% |  |  |  |  | TXV |  |  | -7.043%
Fresno | CA | 93703-2419 |  | 2014-07-17 | 2014-07-17 08:48 | 2014-07-17 09:06 | PAYNE - PY3PNA030040NA-- | 131 | 3.9 | Yes | Yes | 26.1 | 20.2 | 5.9 | 1161ADE0C6534A5D8339FF9397D47ADE |  | R22 | Non-TXV |  | 2.977% | 0.97023 | 5.721% | [5 empty] | Non-TXV | 2.977%
Arvin | CA | 93203-2214 |  | 2014-11-05 | 2014-11-05 18:12 | 2014-11-05 18:28 | DAY & NIGHT - NXA660GKA10C | 85 | 3.9 | Yes | Yes | 19 | 21.8 | -2.8 | 1035086B9DCC48FDAB9184AD654B5ACE |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Clovis | CA | 93612-4976 |  | 2014-07-28 | 2014-07-28 10:41 | 2014-07-28 10:41 | RHEEM - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F775B915F3F8459AB79CC7B9BB2DF0B9 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2020 |  | 2014-07-22 | 2014-07-22 11:16 | 2014-07-22 11:45 | CARRIER - 3298E10380 | 93 | -5.5 | Yes | Yes | 11.9 | 13.7 | -1.8 | 491DDF5214E44538BCFCCB64AE41F078 |  | R22 | Non-TXV |  | -5.914% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.914%
Martinez | CA | 94553-4964 |  | 2014-08-19 | 2014-08-19 09:11 | 2014-08-19 19:58 | AMERICAN STANDARD - 2A7B0030A1000AA | 64 | 5 | Yes | Yes | 15.9 | 16.8 | -0.9 | 8A33CFCFDD3C4F2D9947CC3BE4F86DDE |  | R22 | Non-TXV |  | 7.812% | 0.92188 | 15.01% | [5 empty] | Non-TXV | 7.812%
Fresno | CA | 93710-6410 |  | 2014-07-16 | 2014-07-16 12:53 | 2014-07-16 12:53 | RHEEM - BAFD042JBS | 79 | 0 | Yes | Yes | 17.9 | 19.9 | -2 | 8E523E2940434B2D8696BDA19B9BA4AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-2941 |  | 2014-07-15 | 2014-07-15 09:52 | 2014-07-15 10:22 | BDP - 588ANW036080ACAF | 67 | 4.4 | Yes | Yes | 25.2 | 23.1 | 2.1 | D751F11FBA034E71B69D24365CDEF808 |  | R22 | Non-TXV |  | 6.567% | 0.93433 | 12.62% | [5 empty] | Non-TXV | 6.567%
Bakersfield | CA | 93313-4359 |  | 2014-09-26 | 2014-09-26 14:24 | 2014-09-26 14:24 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 23.5 | 19.2 | 4.3 | 6E435D54CD1D477D8AA442D546825E52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4949 |  | 2014-08-22 | 2014-08-22 09:43 | 2014-08-22 09:43 | UNITARY PRODUCTS GROUP - H2RA036506E | 63 | 0 | Yes | Yes | 22.2 | 18.7 | 3.5 | A0B9E2426AE44217B8C9B6421902F4AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4432 |  | 2014-08-04 | 2014-08-04 16:23 | 2014-08-04 16:38 | OTHER - EAFF237JAZ | 94 | 4.5 | Yes | Yes | 21.9 | 18.8 | 3.1 | 94FDA28D9F0B4E9A8C011A9691DAE4E0 |  | R22 | Non-TXV |  | 4.787% | 0.95213 | 9.2% | [5 empty] | Non-TXV | 4.787%
Fresno | CA | 93704-4132 |  | 2014-07-16 | 2014-07-16 14:13 | 2014-07-16 14:43 | PAYNE - 585EJ030050 | 58 | 2.4 | Yes | Yes | 21.6 | 18.8 | 2.8 | A2588618C4E84324A9D31940532F63AF |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Fresno | CA | 93704-4132 |  | 2014-07-16 | 2014-07-16 14:46 | 2014-07-16 15:16 | OTHER - PA10JA03030-C | 68 | 18.9 | Yes | Yes | 17.3 | 19.7 | -2.4 | 9AE78A1F35644AD9A9666F251D508466 |  | R22 | Non-TXV |  | 27.79% | 0.72206 | 53.41% | [5 empty] | Non-TXV | 27.79%
W Sacramento | CA | 95691-2534 |  | 2014-07-14 | 2014-07-14 14:29 | 2014-07-14 22:07 | YORK - | 85 | 2.6 | Yes | Yes | 16.6 | 17.9 | -1.3 | 73918E7840994180AF3AC6FE457D6776 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Shafter | CA | 93263-2542 |  | 2014-09-06 | 2014-09-06 18:35 | 2014-09-06 18:37 | RHEEM - N/A | 57 | 4.8 | Yes | Yes | 22.8 | 20.4 | 2.4 | 0C9BD7A78C01487094EA201E195589B7 |  | R22 | Non-TXV |  | 8.421% | 0.91579 | 16.18% | [5 empty] | Non-TXV | 8.421%
Pittsburg | CA | 94565-5162 |  | 2014-09-17 | 2014-09-17 14:52 | 2014-09-17 15:16 | GOODMAN - CPKE24-1AB | 106 | -8.7 | Yes | Yes | 19.8 | 20.2 | -0.4 | 607483B22B7C451C8E1C11E7AE38129D |  | R22 | Non-TXV |  | -8.208% | 1.0821 | 2.298% |  |  |  |  | Non-TXV |  |  | -8.208%
Shafter | CA | 93263-2209 |  | 2014-10-05 | 2014-10-05 19:06 | 2014-10-05 19:09 | YORK - D1NH060N06506C | 136 | 8.3 | Yes | Yes | 20.3 | 21 | -0.7 | CAC96E7C95354DB4962E37656C48AF03 |  | R22 | Non-TXV |  | 6.103% | 0.93897 | 11.73% | [5 empty] | Non-TXV | 6.103%
Fresno | CA | 93703-4424 |  | 2014-07-17 | 2014-07-17 09:50 | 2014-07-17 10:08 | PAYNE - PY1PNB030060AAAA | 59 | -3.5 | Yes | Yes | 24.8 | 21.5 | 3.3 | 112484A8272942748DEC7934F9B0891D |  | R22 | Non-TXV |  | -5.932% | 1.0593 | 1.661% |  |  |  |  | Non-TXV |  |  | -5.932%
Bakersfield | CA | 93307-3319 |  | 2014-07-14 | 2014-07-14 11:04 | 2014-07-14 11:04 | ICP - PGAD60E1K7 | 214 | 0 | Yes | Yes | 29.3 | 23.6 | 5.7 | D89DC0AAB4FF4A37AB8754B335D40042 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4187 |  | 2014-08-18 | 2014-08-18 10:38 | 2014-08-18 22:27 | PAYNE - PA13NR024-H | 85 | 4.8 | Yes | Yes | 19.7 | 17.6 | 2.2 | 12517CEA9F94495095419311A3C76586 |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Pittsburg | CA | 94565-4816 |  | 2014-09-17 | 2014-09-17 11:14 | 2014-09-17 11:14 | RHEEM - RAND-036JBZ | 122 | 0 | Yes | Yes | 16.4 | 18.5 | -2.1 | ADFD4E84862E4537B41A5A57CDE407E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7002 |  | 2014-09-14 | 2014-09-14 14:08 | 2014-09-14 14:08 | CARRIER - 38YC0B030301 | 86 | 0 | Yes | Yes | 21.1 | 22.6 | -1.5 | 6B292772052C4BB685ADE6A2990EBE41 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95118-3462 |  | 2014-07-15 | 2014-07-15 09:44 | 2014-07-15 10:16 | WESTINGHOUSE - FS3BC036KA | 89 | 7.5 | Yes | Yes | 21.7 | 19.7 | 2.1 | 9FF57AE1937F484AB97A94614F425BAE |  | R22 | Non-TXV |  | 8.427% | 0.91573 | 16.19% | [5 empty] | Non-TXV | 8.427%
Bakersfield | CA | 93308-7013 |  | 2014-09-14 | 2014-09-14 14:44 | 2014-09-14 14:44 | GOODMAN - GSH130241CB | 122 | 0 | Yes | Yes | 22.7 | 22.1 | 0.6 | 6D97AD66D2A64F8C86E29FD8968AA088 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7010 |  | 2014-09-14 | 2014-09-14 13:20 | 2014-09-14 13:20 | CARRIER - 38YCB030301 | 86 | 0 | Yes | Yes | 20.9 | 21.5 | -0.6 | 107DF14CF0204001B31F216E01B731B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5583 |  | 2014-08-21 | 2014-08-21 13:57 | 2014-08-21 13:57 | YORK - H1RA024S06D | 59 | 0 | Yes | Yes | 19.7 | 21.6 | -1.9 | A2E2123B070E417087F25408650F5C64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4082 |  | 2014-09-13 | 2014-09-13 14:56 | 2014-09-13 14:56 | GOODMAN - GSH13018B1CB | 127 | 0 | Yes | Yes | 20.8 | 23.1 | -2.3 | 0F9E6D9EFF094F728A40C7E1FC954399 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2638 |  | 2014-08-14 | 2014-08-14 14:09 | 2014-08-14 14:09 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.1 | 20.9 | -0.8 | 9ED6666B25104908BEBFF78657C17734 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9381 |  | 2014-07-21 | 2014-07-21 13:20 | 2014-07-21 13:42 | GOODMAN - CK30-18J | 92 | 7.7 | Yes | Yes | 20.2 | 17.1 | 3.1 | 9D24881F1BBB45FBB0A8DB94DC536D8A |  | R22 | Non-TXV |  | 8.37% | 0.9163 | 16.08% | [5 empty] | Non-TXV | 8.37%
Bakersfield | CA | 93311-2632 |  | 2014-09-26 | 2014-09-26 11:33 | 2014-09-26 11:33 | ICP - CAC030AKC4 | 73 | 0 | Yes | Yes | 24.5 | 22.1 | 2.4 | 3A13DA1B6EF6494AA1E114EC0E648C4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4703 |  | 2014-08-18 | 2014-08-18 12:22 | 2014-08-18 22:28 | CARRIER - 48GSN036060311 | 68 | 3.6 | Yes | Yes | 18.5 | 17.7 | 0.9 | DC57EA48C1FB4D178E53E155EFBBCEB5 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Vacaville | CA | 95687-3129 |  | 2014-08-04 | 2014-08-04 09:59 | 2014-08-04 09:59 | YORK - H4DE030S06S | 82 | 0 | Yes | Yes | 17.7 | 17.9 | -0.2 | A52A4770FC334FE7819B6511ABDC5195 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-0000 |  | 2014-08-23 | 2014-08-23 19:23 | 2014-08-23 19:24 | DAY & NIGHT - PGF34808K00A1-- | 208 | -7.8 | Yes | Yes | 20.9 | 20.4 | 0.5 | F25133D9BD9D4382956ACB2DB4E1F411 |  | R22 | Non-TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | Non-TXV |  |  | -3.75%
Fairfield | CA | 94533-2728 |  | 2014-07-21 | 2014-07-21 13:28 | 2014-07-21 19:24 | CARRIER - 38BRB042300 | 85 | 3.9 | Yes | Yes | 16.6 | 16.4 | 0.2 | 4E3DE5D8A60F416BA80243B162C4D49D |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93309-5801 |  | 2014-07-24 | 2014-07-24 16:46 | 2014-07-24 16:46 | GOODMAN - GPG13360701AC | 112 | 0 | Yes | Yes | 20.6 | 21.5 | -0.9 | 929FE924D07C4714A5B6D368BA380467 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2428 |  | 2014-09-26 | 2014-09-26 11:09 | 2014-09-26 11:09 | PAYNE - PY1PNB060090AAAA | 122 | 0 | Yes | Yes | 22.8 | 19.4 | 3.4 | FB757BFA7A504C53B8EDC211377A04E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94539-4559 |  | 2014-08-26 | 2014-08-26 10:41 | 2014-08-26 11:04 | GOODMAN - CK49-1B | 85 | 2.6 | Yes | Yes | 21.8 | 19.9 | 1.9 | 4209F78C64A04098A595832076F093A9 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Woodland | CA | 95695-3741 |  | 2014-07-10 | 2014-07-10 15:48 | 2014-07-10 17:02 | GOODMAN - CKL18-1M | 72 | 7.7 | Yes | Yes | 17.2 | 18.7 | -1.5 | 0151376750624D17B971F4D4D092495B |  | R22 | Non-TXV |  | 10.69% | 0.89306 | 20.55% | [5 empty] | Non-TXV | 10.69%
Wasco | CA | 93280-0000 |  | 2014-07-19 | 2014-07-19 17:00 | 2014-07-19 17:03 | YORK - H2D042S06B | 141 | 10.6 | Yes | Yes | 24 | 21.5 | 2.5 | 28F967DD893640B2A515BF68F0E07AA3 |  | R22 | TXV |  | 7.518% | 0.92482 | 14.45% | [5 empty] | TXV | 7.518%
Bakersfield | CA | 93306-5423 |  | 2014-07-21 | 2014-07-21 09:53 | 2014-07-21 09:53 | RHEEM - RRNA-BO042JK08X | 104 | 0 | Yes | Yes | 22.9 | 21.3 | 1.7 | F697F5A89356404AB7CB47B5758A9A7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8882 |  | 2014-10-07 | 2014-10-07 11:33 | 2014-10-07 11:33 | ARCOAIRE - PGME24G0401 | 73 | 0 | Yes | Yes | 19.8 | 19.7 | 0.1 | B28CF1B31C264A95AAAA1AE695A88203 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2510 |  | 2014-08-22 | 2014-08-22 11:21 | 2014-08-22 11:45 | LENNOX - | 72 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | A5A88626759C42B4BC96656738187ACD |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4431 |  | 2014-07-17 | 2014-07-17 09:33 | 2014-07-17 09:33 | TRANE - BWD724A100A2 | 98 | 0 | Yes | Yes | 20.6 | 18.2 | 2.4 | 1B9B5A837A7F4FF4A4DB14582970026B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3309 |  | 2014-11-04 | 2014-11-04 10:17 | 2014-11-04 10:17 | OTHER - PGF036K0608 | 71 | 0 | Yes | Yes | 24.5 | 20.6 | 3.9 | 8614239DFD2B4340B3499C0BCF397602 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-9765 |  | 2014-11-06 | 2014-11-06 15:02 | 2014-11-06 15:57 | BRYANT - 574DNWA6009NATP | 160 | -6.4 | Yes | Yes | 20.2 | 17.7 | 2.5 | BD41F216B7D649B18D5522E86AB46C22 |  | R410A | TXV |  | -4% | 1.04 | 1.12% |  |  |  |  | TXV |  |  | -4%
Vallejo | CA | 94589-2321 |  | 2014-08-04 | 2014-08-04 14:01 | 2014-08-04 14:22 | AIRE-FLO - GCGD36S41S3A | 73 | 7.2 | Yes | Yes | 20.6 | 18.6 | 2 | AEF610DCFD704BAD8E50C089E7810DE3 |  | R410A | Non-TXV |  | 9.863% | 0.90137 | 18.95% | [5 empty] | Non-TXV | 9.863%
Bakersfield | CA | 93308-2168 |  | 2014-09-18 | 2014-09-18 13:44 | 2014-09-18 13:44 | HEIL - GPCM24K040F | 57 | 0 | Yes | Yes | 22.6 | 19.7 | 2.9 | 7DA5783089AD47EEB87600F7D0F61D34 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-5041 |  | 2014-08-18 | 2014-08-18 13:06 | 2014-08-18 13:06 | - | 85 | 0 | Yes | Yes | 16.4 | 17.2 | -0.8 | 7F1B262FDA1E40D7A980DD4AADBC9554 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4270 |  | 2014-07-28 | 2014-07-28 14:02 | 2014-07-28 16:15 | AIRE-FLO - | 85 | 3 | Yes | Yes | 15.8 | 18.2 | -2.4 | 9C47AD5523DE451181066D75F9BD2771 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Pittsburg | CA | 94565-4637 |  | 2014-09-18 | 2014-09-18 09:12 | 2014-09-18 09:12 | DAY & NIGHT - 585AU36 | 83 | 0 | Yes | Yes | 20 | 19.3 | 0.7 | CB19566E00AE41819C3B6F16D989AB24 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-7011 |  | 2014-09-14 | 2014-09-14 19:24 | 2014-09-14 19:24 | CARRIER - 38YCB024311 | 72 | 0 | Yes | Yes | 23.1 | 22.3 | 0.9 | 9840CF61F30A43D3A6D4DE5C86212F4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-3940 |  | 2014-07-15 | 2014-07-15 10:24 | 2014-07-15 10:41 | AMANA - 565BJ042 | 94 | -5.5 | Yes | Yes | 23.2 | 19.8 | 3.4 | FB792C63AC4E44B593432C8ECBD9240D |  | R22 | Non-TXV |  | -5.851% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.851%
Antioch | CA | 94509-1419 |  | 2014-10-08 | 2014-10-08 09:31 | 2014-10-08 09:53 | CARRIER - 38TXA036340 | 110 | 13.8 | Yes | Yes | 24.4 | 19.2 | 5.2 | 730C2B52FA4C4A43814D548E10DF13B9 |  | R410A | TXV |  | 12.55% | 0.87455 | 24.11% | [5 empty] | TXV | 12.55%
Bakersfield | CA | 93307-6107 |  | 2014-07-18 | 2014-07-18 09:38 | 2014-07-18 09:38 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20.4 | 22.8 | -2.4 | D78F9D40D0BC452494A7AD98555D593E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1902 |  | 2014-08-04 | 2014-08-04 10:44 | 2014-08-04 10:44 | TRANE - 4YCC3030A1075AA | 97 | 0 | Yes | Yes | 21.3 | 18 | 3.3 | 3D2D4597B55F4A1EB71A304CE3944473 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-2926 |  | 2014-07-15 | 2014-07-15 10:54 | 2014-07-15 21:23 | COLEMAN - CPR42-132 | 77 | 2.4 | Yes | Yes | 20.6 | 19.7 | 1 | B3BE4EAC7FE84E23966A12ABAD36ADEF |  | R22 | Non-TXV |  | 3.117% | 0.96883 | 5.99% | [5 empty] | Non-TXV | 3.117%
Woodland | CA | 95776-4268 |  | 2014-07-10 | 2014-07-10 15:12 | 2014-07-10 17:07 | GOODMAN - GSC130241AA | 93 | 6.8 | Yes | Yes | 16.3 | 19.3 | -3 | C35A44AC6C694CA7BC09F8828D4072D9 |  | R22 | Non-TXV |  | 7.312% | 0.92688 | 14.05% | [5 empty] | Non-TXV | 7.312%
Lemoore | CA | 93245-2309 |  | 2014-08-01 | 2014-08-01 11:34 | 2014-08-01 11:57 | OTHER - PGC036K060D | 71 | 3.8 | Yes | Yes | 26.6 | 21.5 | 5.1 | 5D37E2B2FB3748A68F967958AD2D1648 |  | R22 | Non-TXV |  | 5.352% | 0.94648 | 10.29% | [5 empty] | Non-TXV | 5.352%
Suisun City | CA | 94585-1711 |  | 2014-08-08 | 2014-08-08 12:57 | 2014-08-08 17:18 | ALLEGIANCE - 7A0030A100A1 | 85 | 9.8 | Yes | Yes | 19 | 17.6 | 1.4 | BA39E65B69EC4A15BD90A4E34BB06234 |  | R22 | Non-TXV |  | 11.53% | 0.88471 | 22.16% | [5 empty] | Non-TXV | 11.53%
Wasco | CA | 93280-2715 |  | 2014-08-03 | 2014-08-03 19:16 | 2014-08-03 19:18 | GOODMAN - GPG1336045M41DA | 70 | 8.4 | Yes | Yes | 22.1 | 18.7 | 3.4 | 7FEFEEC747A2441A961F03BB07C28188 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Fairfield | CA | 94533-3620 |  | 2014-07-28 | 2014-07-28 11:22 | 2014-07-28 16:12 | TRANE - TTB748A1C0A0 | 85 | -8 | Yes | Yes | 18.3 | 19.6 | -1.3 | 558C996C0B554FEFB6F5F2B264C298A7 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Wasco | CA | 93280-2757 |  | 2014-10-30 | 2014-10-30 17:13 | 2014-10-30 17:13 | OTHER - H2RD036S06B | 96 | 0 | Yes | Yes | 18.2 | 19 | -0.8 | 4EB62C08367D474BAC9F4CB0429A85D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-0000 |  | 2014-07-19 | 2014-07-19 17:09 | 2014-07-19 17:13 | YORK - H2RD048S065 | 134 | 8.4 | Yes | Yes | 21.7 | 21 | 0.7 | 5C6D40881D5A4482B8D094B7EFBC5512 |  | R22 | Non-TXV |  | 6.269% | 0.93731 | 12.05% | [5 empty] | Non-TXV | 6.269%
Wasco | CA | 93280-2757 |  | 2014-11-07 | 2014-11-07 19:19 | 2014-11-07 19:19 | OTHER - H2RD042S06B | 131 | 0 | Yes | Yes | 23 | 18.2 | 4.8 | 44E84E67B6B94B8F80D690114C1071BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6715 |  | 2014-08-21 | 2014-08-21 11:43 | 2014-08-21 11:43 | CARRIER - 38BRC036340 | 104 | 0 | Yes | Yes | 23.1 | 19.5 | 3.6 | AA4C47F330AC49E1A18E0FA66B5F69AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4940 |  | 2014-08-20 | 2014-08-20 14:08 | 2014-08-20 14:55 | PAYNE - | 72 | 4.5 | Yes | Yes | 19.6 | 19.6 | 0 | 0D0E189CA114486DBA18B629838621A9 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
W Sacramento | CA | 95605-2126 |  | 2014-08-26 | 2014-08-26 12:31 | 2014-08-26 13:26 | GOODMAN - GPG1336070M41AB | 85 | 0 | Yes | Yes | 21.1 | 20.2 | 1 | 81F52DD90E67423D99257D99F25EEFBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1906 |  | 2014-08-06 | 2014-08-06 08:38 | 2014-08-06 22:11 | - | 85 | 2.8 | Yes | Yes | 14.9 | 17.5 | -2.6 | D590793ADC684AE2BA3DD837E6D7B84E |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Woodland | CA | 95695-2748 |  | 2014-10-17 | 2014-10-17 12:15 | 2014-10-17 12:40 | BDP - 588ANW030060AAAD | 52 | 4.6 | Yes | Yes | 19.5 | 20.4 | -0.9 | 2776C308F42C4B7A92578E90C9C25E8E |  | R22 | Non-TXV |  | 8.846% | 0.91154 | 17% | [5 empty] | Non-TXV | 8.846%
Bakersfield | CA | 93307-2769 |  | 2014-07-18 | 2014-07-18 12:58 | 2014-07-18 12:58 | RHEEM - RRNA-B042JK08X | 104 | 0 | Yes | Yes | 18.9 | 20.4 | -1.5 | 33B052DB52AE4F4DBF6E90A4A6500236 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5158 |  | 2014-09-18 | 2014-09-18 12:10 | 2014-09-18 12:29 | GOODMAN - D5H130241AC | 106 | 11.3 | Yes | Yes | 20.5 | 20.4 | 0.1 | 6798A93D6499427DAA542E17AD05650B |  | R22 | Non-TXV |  | 10.66% | 0.8934 | 20.49% | [5 empty] | Non-TXV | 10.66%
Pittsburg | CA | 94565-5156 |  | 2014-09-18 | 2014-09-18 10:22 | 2014-09-18 10:22 | GOODMAN - GSH1302410A | 122 | 0 | Yes | Yes | 20.6 | 19.9 | 0.7 | F790C3A0CB114C0D9462C41A00FAD5AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95129-3239 |  | 2014-07-16 | 2014-07-16 10:06 | 2014-07-16 10:24 | YORK - H1RA024S06D | 59 | 4.1 | Yes | Yes | 19.7 | 20.4 | -0.7 | C78502E44EEB42FDA4E9961A0AA3E7E6 |  | R22 | Non-TXV |  | 6.949% | 0.93051 | 13.35% | [5 empty] | Non-TXV | 6.949%
Bakersfield | CA | 93305-4220 |  | 2014-07-31 | 2014-07-31 09:45 | 2014-07-31 09:45 | GOODMAN - GPG1336045M41AC | 85 | 0 | Yes | Yes | 21.7 | 18.1 | 3.6 | EB911BE701AD422482A0D0D033D3305F |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2230 |  | 2014-07-16 | 2014-07-16 16:27 | 2014-07-16 18:30 | AMANA - RRMA-A24JK06X | 55 | 6.2 | Yes | Yes | 22.5 | 16.8 | 5.7 | E5BA553ED07E4C2E9607E1883B46A37D |  | R22 | Non-TXV |  | 11.27% | 0.88727 | 21.66% | [5 empty] | Non-TXV | 11.27%
Bakersfield | CA | 93312-3159 |  | 2014-08-21 | 2014-08-21 13:24 | 2014-08-21 13:24 | BDP - UKN | 90 | 0 | Yes | Yes | 21.3 | 19.6 | 1.7 | C08F84975FB64028B421141C306CA32A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-9538 |  | 2014-10-27 | 2014-10-27 11:03 | 2014-10-27 11:03 | DAY & NIGHT - PGF336060K01 | 146 | 0 | Yes | Yes | 16.5 | 19.5 | -3 | 4BBA1365BB2A4FFF803AC98188B4B880 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7351 |  | 2014-08-20 | 2014-08-20 14:51 | 2014-08-20 17:48 | CARRIER - 38EZGO18---301 | 71 | 5.5 | Yes | Yes | 19.3 | 18.8 | 0.5 | CE04A69E1B434F7097833840C9B4722C |  | R410A | Non-TXV |  | 7.746% | 0.92254 | 14.89% | [5 empty] | Non-TXV | 7.746%
Davis | CA | 95616-2863 |  | 2014-07-11 | 2014-07-11 14:41 | 2014-07-11 15:11 | - BSC130241AD | 108 | -7.6 | Yes | Yes | 11.5 | 14.3 | -2.8 | 33CDEFCA6B2F44759FEA591640A3E0F5 |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
W Sacramento | CA | 95691-0000 |  | 2014-07-25 | 2014-07-25 13:30 | 2014-07-25 14:27 | LENNOX - 13ACD-024 | 72 | 4.6 | Yes | Yes | 14.6 | 17.5 | -2.9 | CED88DDE8E1042A1A73D39A0EB2EC55B |  | R22 | Non-TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | Non-TXV | 6.389%
W Sacramento | CA | 95605-2602 |  | 2014-07-16 | 2014-07-16 15:08 | 2014-07-16 16:22 | RUUD - RRNL-BO36JK06X | 97 | 5.9 | Yes | Yes | 12.8 | 13.9 | -1.1 | B8BF3957E83C4A3F97F94D69E4A9FD0C |  | R410A | Non-TXV |  | 6.082% | 0.93918 | 11.69% | [5 empty] | Non-TXV | 6.082%
Bakersfield | CA | 93308-5667 |  | 2014-11-26 | 2014-11-26 15:06 | 2014-11-26 15:06 | GOODMAN - GSC130361GB | 77 | 0 | Yes | Yes | 22.7 | 21 | 1.7 | 7FD757AF6EFA4675BAA3F05C227600F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2243 |  | 2014-07-16 | 2014-07-16 10:27 | 2014-07-16 12:48 | CARRIER - | 100 | 4.6 | Yes | Yes | 18.2 | 19.9 | -1.7 | 8B094F8D9A5F4AE98DA6CA5BEBC56E39 |  | R22 | Non-TXV |  | 4.6% | 0.954 | 8.84% | [5 empty] | Non-TXV | 4.6%
Fairfield | CA | 94533-8821 |  | 2014-08-22 | 2014-08-22 12:45 | 2014-08-22 17:32 | CARRIER - H2RA036SO6E | 63 | 5.6 | Yes | Yes | 19.2 | 19.7 | -0.4 | FC58B945B3564522BA01386EB82513E1 |  | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Bakersfield | CA | 93308-5672 |  | 2014-11-26 | 2014-11-26 15:19 | 2014-11-26 15:19 | BDP - 561CJ030C | 69 | 0 | Yes | Yes | 23 | 20.8 | 2.2 | 81F66B64BF54406A96F042ED691BCA59 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7115 |  | 2014-07-11 | 2014-07-11 10:01 | 2014-07-11 10:28 | CARRIER - 38TH0483310 | 117 | 4.7 | Yes | Yes | 14.9 | 16.1 | -1.2 | D8707CB26AC64FA2BC61E542564D018B |  | R22 | Non-TXV |  | 4.017% | 0.95983 | 7.72% | [5 empty] | Non-TXV | 4.017%
Bakersfield | CA | 93311-2633 |  | 2014-07-23 | 2014-07-23 14:44 | 2014-07-23 14:44 | CARRIER - 38BRC060360 | 200 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | DB59EBE0A80A44A4A6724157D25BB030 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4661 |  | 2014-09-17 | 2014-09-17 12:37 | 2014-09-17 12:37 | GOODMAN - GPG1324045M41AD | 80 | 0 | Yes | Yes | 20 | 22.3 | -2.3 | 6E347A894A144F21AF69E3E57F54D66F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3688 |  | 2014-08-27 | 2014-08-27 10:44 | 2014-08-27 10:44 | HEIL - UKN | 90 | 0 | Yes | Yes | 17 | 19.5 | -2.5 | 954594D897B24C1D81DA8C637B4B1654 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2416 |  | 2014-07-25 | 2014-07-25 13:05 | 2014-07-25 13:05 | ICP - PGAD42D1K7 | 179 | 0 | Yes | Yes | 19.8 | 18.7 | 1.1 | A7383A11A53A4F599969760FF74A52E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7524 |  | 2014-08-07 | 2014-08-07 14:31 | 2014-08-07 22:15 | - | 85 | 2.7 | Yes | Yes | 15.7 | 18.2 | -2.5 | AC2A7D17E32A42B996CE677754D8642E |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Wasco | CA | 93280-2564 |  | 2014-08-02 | 2014-08-02 18:11 | 2014-08-02 18:16 | RHEEM - DARH-F036N060B | 112 | 10.8 | Yes | Yes | 23 | 20.8 | 2.2 | ABEF97CC730247F790F2A403DE30A1F7 |  | R22 | Non-TXV |  | 9.643% | 0.90357 | 18.53% | [5 empty] | Non-TXV | 9.643%
Bakersfield | CA | 93313-3688 |  | 2014-08-29 | 2014-08-29 09:36 | 2014-08-29 09:36 | RHEEM - RRNL-B030JK06X | 76.8 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | D99E0B97C6544986BDE01352BA4386EC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5358 |  | 2014-10-08 | 2014-10-08 10:30 | 2014-10-08 10:51 | TRANE - 2TTR1030A1000AA | 64 | 5.5 | Yes | Yes | 17.5 | 18.4 | -0.9 | 10A240F1325246DBAF9B6F30C8BDD489 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.594% | 0.91406 | 16.52% | [5 empty] | Non-TXV | 8.594%
Vacaville | CA | 95688-2709 |  | 2014-08-13 | 2014-08-13 12:52 | 2014-08-13 20:48 | TRANE - 4TTX4030A1000AB | 79 | 2.7 | Yes | Yes | 17 | 16.9 | 0.1 | 29690A8B7E9E458AB58DC31C061F023B |  | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Mc Farland | CA | 93250-1688 |  | 2014-09-02 | 2014-09-02 08:36 | 2014-09-02 08:36 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 9.2 | 19.3 | -10.1 | C8BE41D3A1B84FC0B803475ABA9147A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1066 |  | 2014-10-27 | 2014-10-27 14:08 | 2014-10-27 14:08 | YORK - D1NP060N09006A | 140 | 0 | Yes | Yes | 25.8 | 19.9 | 5.9 | FF104EFA6575499B9C51A30935975933 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-9789 |  | 2014-08-29 | 2014-08-29 09:55 | 2014-08-29 09:55 | CARRIER - 38BBRC030310 | 100 | 0 | Yes | Yes | 15.1 | 17.9 | -2.8 | 973D177C49D1479CA4FDC09E213FEA5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5653 |  | 2014-09-18 | 2014-09-18 17:08 | 2014-09-18 17:08 | CARRIER - UKN | 133 | 0 | Yes | Yes | 23.1 | 21.3 | 1.8 | FF680C547EEB4EDF945A7A4A75DF4617 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5229 |  | 2014-08-27 | 2014-08-27 10:23 | 2014-08-27 10:23 | ICP - N2A336AKA200 | 92 | 0 | Yes | Yes | 23 | 20.3 | 2.7 | D02497CDB98046FA9B968064D76DFFC3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5229 |  | 2014-08-27 | 2014-08-27 10:26 | 2014-08-27 10:26 | ICP - N2A33AOKA200 | 84 | 0 | Yes | Yes | 20.5 | 22 | -1.5 | 9D5AF66BF71A4428B03C3EDF7CE133E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5182 |  | 2014-10-29 | 2014-10-29 11:58 | 2014-10-29 11:58 | BDP - 585EJW024050ABAF | 54 | 0 | Yes | Yes | 24.2 | 18.5 | 5.7 | 43A564FF3E04409EAE232672860F60C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4394 |  | 2014-08-29 | 2014-08-29 13:40 | 2014-08-29 13:40 | CARRIER - 38BR030300 | 106 | 0 | Yes | Yes | 19.6 | 20 | -0.4 | 196B519FC8DC401282F0D343530B9AE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4394 |  | 2014-08-29 | 2014-08-29 13:31 | 2014-08-29 13:31 | CARRIER - 3BR036310 | 113 | 0 | Yes | Yes | 21.5 | 19.5 | 2 | 4CFFF41D2F2A4C888494DAD371D29ECE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-0000 |  | 2014-09-03 | 2014-09-03 11:48 | 2014-09-03 11:48 | GOODMAN - GPG1360090M41CA | 91 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 0719159DB6A94F809CC2596DFE89B2CE | Actual Subcooling cannot be negative. Please check entries. | R410A | TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-9536 |  | 2014-10-27 | 2014-10-27 10:33 | 2014-10-27 10:33 | DAY & NIGHT - PGF330060K01A2 | 89 | 0 | Yes | Yes | 25.3 | 20.6 | 4.7 | 45E413049E7C4CC19E98A45508CE6105 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1560 |  | 2014-09-11 | 2014-09-11 09:10 | 2014-09-11 09:40 | DAY & NIGHT - 585BJO24 | 70 | -9.9 | Yes | Yes | 18.6 | 17.2 | 1.4 | 39B41ECB2B4140078A4FD29B73D7D873 |  | R22 | Non-TXV |  | -14.14% | 1.1414 | 3.961% |  |  |  |  | Non-TXV |  |  | -14.14%
Mc Farland | CA | 93250-0000 |  | 2014-11-18 | 2014-11-18 10:37 | 2014-11-18 10:37 | WEATHER KING - 13AJA30A01 | 98 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 98534F97CB2C4767AD07AE1DE472C3B7 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8118 |  | 2014-09-19 | 2014-09-19 10:30 | 2014-09-19 10:58 | TRANE - 2TTB3042A1000AA | 100 | 4.9 | Yes | Yes | 19.5 | 19.4 | 0.1 | DF143CD22AE44F1BBCD5DA5E0EFE2AD6 |  | R410A | TXV |  | 4.9% | 0.951 | 9.417% | [5 empty] | TXV | 4.9%
Bakersfield | CA | 93313-3688 |  | 2014-10-23 | 2014-10-23 10:43 | 2014-10-23 10:43 | HEIL - UKN | 90 | 0 | Yes | Yes | 24.7 | 19.9 | 4.8 | 4E1A89956DBE456E9402A767A197017C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3570 |  | 2014-11-06 | 2014-11-06 09:47 | 2014-11-06 09:47 | CARRIER - 24BB348W310 | 112 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D78E835485DF42F88E9CF598173E179A | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-9613 |  | 2014-08-16 | 2014-08-16 16:57 | 2014-08-16 17:00 | YORK - H2RD048S06B | 134 | 64.9 | Yes | Yes | 24.3 | 20.9 | 3.4 | 64CADFF641804AA8A1A94F1FA72B1696 |  | R22 | Non-TXV |  | 48.43% | 0.51567 | 93.08% | [5 empty] | Non-TXV | 48.43%
Antioch | CA | 94509-6237 |  | 2014-10-09 | 2014-10-09 11:37 | 2014-10-09 11:37 | RHEEM - RACA056ABQ | 69 | 0 | Yes | Yes | 26 | 21.4 | 4.6 | 9B5C416D31D244F4BFF03889E1AF7C95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-9512 |  | 2014-09-21 | 2014-09-21 19:00 | 2014-09-21 19:02 | GOODMAN - GSX130361BA | 89 | 3.6 | Yes | Yes | 24.1 | 22.1 | 2 | 81169749852849EA8D5985FCCA218836 |  | R22 | Non-TXV |  | 4.045% | 0.95955 | 7.773% | [5 empty] | Non-TXV | 4.045%
Dixon | CA | 95620-4538 |  | 2014-07-30 | 2014-07-30 11:14 | 2014-07-30 11:36 | COLEMAN - 8ROS048190 | 87 | -7.2 | Yes | Yes | 19.7 | 17.9 | 1.8 | 6CAD66CC5B5741A6914D82057F548577 |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Bakersfield | CA | 93307-3364 |  | 2014-07-15 | 2014-07-15 15:18 | 2014-07-15 15:18 | UNITARY PRODUCTS GROUP - DAYP-F048N080A | 132 | 0 | Yes | Yes | 24 | 18 | 6 | CACF91E86D8342D38A4AEEAD104C67D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2878 |  | 2014-07-23 | 2014-07-23 15:18 | 2014-07-23 15:18 | UNITARY PRODUCTS GROUP - DYP-F042N080 | 150 | 0 | Yes | Yes | 18 | 16 | 2 | 0B38EE5F1D5847F8BE3AE5B4313ECB08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5689 |  | 2014-10-24 | 2014-10-24 08:59 | 2014-10-24 08:59 | LENNOX - CCS81E31180 | 100 | 0 | Yes | Yes | 24.3 | 20.4 | 3.9 | C2325EC670464511B665D3B7E2E338B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3346 |  | 2014-07-28 | 2014-07-28 11:14 | 2014-07-28 11:14 | GOODMAN - GPG1324045M41BA | 68 | 0 | Yes | Yes | 28 | 22 | 6 | E5826280C3BF4335B599383BBA4392CD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6387 |  | 2014-08-04 | 2014-08-04 14:34 | 2014-08-04 16:41 | CARRIER - H1RA042S06D | 84 | 5.9 | Yes | Yes | 17.8 | 18.5 | -0.7 | 5208E50EA6DD4391B5BBB717670085B7 |  | R22 | Non-TXV |  | 7.024% | 0.92976 | 13.5% | [5 empty] | Non-TXV | 7.024%
Fairfield | CA | 94533-2560 |  | 2014-07-22 | 2014-07-22 09:13 | 2014-07-22 09:13 | - | 85 | 0 | Yes | Yes | 18.5 | 16.8 | 1.7 | 71A85C4EC61A4C4D83E6BB82163E4751 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4752 |  | 2014-09-18 | 2014-09-18 10:19 | 2014-09-18 11:02 | CARRIER - 9AC11241BD | 70 | 3.7 | Yes | Yes | 23.1 | 20.4 | 2.7 | D4CAA9AE47E14CE2B70716749E2F5448 |  | R22 | Non-TXV |  | 5.286% | 0.94714 | 10.16% | [5 empty] | Non-TXV | 5.286%
Vallejo | CA | 94589-3741 |  | 2014-08-05 | 2014-08-05 10:24 | 2014-08-05 10:24 | PAYNE - | 70 | 0 | Yes | Yes | 24.2 | 19.9 | 4.3 | 5CCBB3285297434F81643AF726B42578 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3013 |  | 2014-08-10 | 2014-08-10 20:43 | 2014-08-10 20:45 | PAYNE - PA12NA042A | 104 | -6.2 | Yes | Yes | 21.3 | 20.4 | 0.9 | DAF997390F23438DAAC4CCE178931CC8 |  | R22 | TXV |  | -5.962% | 1.0596 | 1.67% |  |  |  |  | TXV |  |  | -5.962%
Bakersfield | CA | 93308-2925 |  | 2014-07-25 | 2014-07-25 12:23 | 2014-07-25 12:23 | BDP - 589ANW048080ADBG | 88 | 0 | Yes | Yes | 20.5 | 18.3 | 2.2 | ECB6143CDDB346D7872CE70CB043189A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1482 |  | 2014-08-25 | 2014-08-25 14:28 | 2014-08-25 14:28 | ICP - LPCM24K040F | 54 | 0 | Yes | Yes | 20 | 22.5 | -2.5 | BE5A218EC9A64104A2A23AAB67F84E0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3677 |  | 2014-10-13 | 2014-10-13 13:01 | 2014-10-13 13:01 | RHEEM - RAMA048JAS | 172 | 0 | Yes | Yes | 18.8 | 19.6 | -0.8 | 17F94DE490EF48728E63F159E099035A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3677 |  | 2014-10-13 | 2014-10-13 13:21 | 2014-10-13 13:21 | RHEEM - UNK | 103 | 0 | Yes | Yes | 17.5 | 19.2 | -1.7 | 8A64CC0929C941EF9B3FC78E7C55BB63 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4933 |  | 2014-08-26 | 2014-08-26 12:35 | 2014-08-26 12:35 | RHEEM - RRGG-05N31JKR | 48 | 0 | Yes | Yes | 20.2 | 19.9 | 0.3 | 56074EE087DB4AC4BA7F9599D06FD6A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6287 |  | 2014-10-14 | 2014-10-14 14:28 | 2014-10-14 14:28 | OTHER - H2RA036S06G | 63 | 0 | Yes | Yes | 19.2 | 19.7 | -0.5 | F5BAAD07081B421CBDFE0DC6E8254079 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6287 |  | 2014-10-14 | 2014-10-14 14:33 | 2014-10-14 14:33 | OTHER - H1RA042S06G | 84 | 0 | Yes | Yes | 17.4 | 20.1 | -2.7 | 6EE48732F76242C399C9986D3182E8A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5657 |  | 2014-10-14 | 2014-10-14 11:21 | 2014-10-14 11:21 | YORK - H2RD036S06A | 96 | 0 | Yes | Yes | 26.8 | 21.5 | 5.3 | 2988E2B1E53F4C70AF04846746D77ECF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5657 |  | 2014-10-14 | 2014-10-14 11:28 | 2014-10-14 11:28 | YORK - H1RD036S06G | 145 | 0 | Yes | Yes | 25.9 | 22.8 | 3.1 | C71E0A79108946C4AE26CB147C703915 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2857 |  | 2014-08-01 | 2014-08-01 12:24 | 2014-08-01 12:48 | TEMPSTAR - PGF024K040A | 58 | 4.1 | Yes | Yes | 17 | 19.8 | -2.8 | 4682F1BF662D4FED890006B9D6254F87 |  | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Concord | CA | 94519-2516 |  | 2014-08-29 | 2014-08-29 13:20 | 2014-08-29 13:20 | LENNOX - HS22-311U-2P | 129 | 0 | Yes | Yes | 19.4 | 19.3 | 0.1 | 815792D4BD5D46CA81F570E225216839 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6498 |  | 2014-07-23 | 2014-07-23 11:06 | 2014-07-23 11:06 | TRANE - 4YCZ6048A1120AA | 136 | 0 | Yes | Yes | 20.9 | 21.5 | -0.6 | 9EF7926130F14B1F83D4D29BF1656C0A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4764 |  | 2014-08-13 | 2014-08-13 13:18 | 2014-08-13 13:18 | BRYANT - 582ANW030040AAAD | 55 | 0 | Yes | Yes | 23.5 | 19.8 | 3.7 | DE405F9CC73140EEB053661A069BDFC2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1640 |  | 2014-07-22 | 2014-07-22 10:24 | 2014-07-22 10:47 | FRIGIDAIRE - NA | 80 | -5.6 | Yes | Yes | 25.3 | 20.4 | 4.9 | 00AAD4C3743346009A65BC7A3E20AF2E |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Vallejo | CA | 94590-3948 |  | 2014-08-05 | 2014-08-05 11:31 | 2014-08-05 11:31 | CARRIER - 38TK042300 | 165 | 5.6 | Yes | Yes | 19.4 | 20.4 | -1 | B447237C6185471EB4C6B43AD6AF700C | Add refrigerant: 5.6 oz | R22 | Non-TXV |  | 3.394% | 0.96606 | 6.522% | [5 empty] | Non-TXV | 3.394%
Vacaville | CA | 95687-3312 |  | 2014-07-11 | 2014-07-11 10:46 | 2014-07-11 11:20 | TRANE - TTR025C100A1 | 66 | -4.7 | Yes | Yes | 24.5 | 20.4 | 4.1 | 65FB55582D6C41E6955211E5F07BB001 |  | R22 | Non-TXV |  | -7.121% | 1.0712 | 1.994% |  |  |  |  | Non-TXV |  |  | -7.121%
Bakersfield | CA | 93309-5317 |  | 2014-10-07 | 2014-10-07 09:42 | 2014-10-07 09:42 | YORK - D1NA042N05606C | 76 | 0 | Yes | Yes | 23.6 | 19.5 | 4.1 | 7FC990E84D324095984E51A8EA5B8C27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2527 |  | 2014-07-25 | 2014-07-25 09:52 | 2014-07-25 09:52 | NORDYNE - R4GD-024K072X | 90 | 0 | Yes | Yes | 20.9 | 20.7 | 0.2 | DC19F35BBB2D47E782DECAC1BD059B9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2527 |  | 2014-07-25 | 2014-07-25 10:03 | 2014-07-25 10:03 | ICP - PGC024K040E | 54 | 0 | Yes | Yes | 22 | 21.3 | 0.7 | 18F11673D90E414D85A3774A1D9D58DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2506 |  | 2014-07-17 | 2014-07-17 10:27 | 2014-07-17 10:53 | RHEEM - RRMA-A024JK06X | 76 | 6.2 | Yes | Yes | 25.8 | 20.4 | 5.4 | 3C8DDC540BB046E6BD2736BB0EA33130 |  | R22 | Non-TXV |  | 8.158% | 0.91842 | 15.68% | [5 empty] | Non-TXV | 8.158%
Bakersfield | CA | 93308-4603 |  | 2014-10-10 | 2014-10-10 15:22 | 2014-10-10 15:40 | ICP - PGAD36D11K7 | 85 | 8.4 | Yes | Yes | 19.8 | 21.4 | -1.6 | E49F797F4C864EF991FB79D03854E955 |  | R22 | Non-TXV |  | 9.882% | 0.90118 | 18.99% | [5 empty] | Non-TXV | 9.882%
Fresno | CA | 93705-1232 |  | 2014-07-22 | 2014-07-22 13:04 | 2014-07-22 13:25 | OTHER - 80AW30106 | 99 | 4.7 | Yes | Yes | 24.5 | 20.2 | 4.4 | 7924A403FDF54CEBBDA8F0866EBD461E |  | R22 | Non-TXV |  | 4.747% | 0.95253 | 9.124% | [5 empty] | Non-TXV | 4.747%
Woodland | CA | 95776-5146 |  | 2014-07-21 | 2014-07-21 11:58 | 2014-07-21 12:24 | CARRIER - 5003E11493 | 134 | 5 | Yes | Yes | 9.3 | 11.7 | -2.4 | 8EEDA3B3A53142E9B2430F80F9B59FE9 |  | R22 | Non-TXV |  | 3.731% | 0.96269 | 7.171% | [5 empty] | Non-TXV | 3.731%
Vacaville | CA | 95687-6152 |  | 2014-07-16 | 2014-07-16 11:06 | 2014-07-16 17:18 | CARRIER - 38CK024330 | 58 | 3.9 | Yes | Yes | 15.8 | 17.5 | -1.7 | 6FE70BA6CA4F4AFDA74B7004A702C06C |  | R22 | Non-TXV |  | 6.724% | 0.93276 | 12.92% | [5 empty] | Non-TXV | 6.724%
Antioch | CA | 94509-4755 |  | 2014-10-09 | 2014-10-09 09:34 | 2014-10-09 09:34 | RHEEM - UNK | 85 | 0 | Yes | Yes | 20.3 | 18.8 | 1.5 | 41817C5B67CD47E2B2E0F348AD3BA302 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-6852 |  | 2014-07-21 | 2014-07-21 11:38 | 2014-07-21 12:08 | LENNOX - HS16511V8P | 138 | 6.3 | Yes | Yes | 21 | 20.3 | 0.7 | 8DC31D25752C456BBC1AA96EEE57CE26 |  | R22 | Non-TXV |  | 4.565% | 0.95435 | 8.773% | [5 empty] | Non-TXV | 4.565%
Esparto | CA | 95627-2050 |  | 2014-08-08 | 2014-08-08 14:12 | 2014-08-08 16:24 | COLEMAN - BR20Q481D | 85 | 4.3 | Yes | Yes | 20.6 | 18.5 | 2.2 | 0973F9447A864CD4946D5402A040AE1D |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Wasco | CA | 93280-2531 |  | 2014-10-30 | 2014-10-30 14:04 | 2014-10-30 14:04 | OTHER - UNK | 81 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C3C58F6D05A146969345461D709DE086 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2510 |  | 2014-07-30 | 2014-07-30 14:08 | 2014-07-30 14:42 | DAY & NIGHT - R4A336AKB100 | 76 | 3.2 | Yes | Yes | 20.7 | 20.7 | 0 | B3BAE8550D444846AAF8EDE69F9F70E2 |  | R410A | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Lemoore | CA | 93245-2510 |  | 2014-07-30 | 2014-07-30 15:29 | 2014-07-30 15:29 | RHEEM - SE421000 | 61 | 0 | Yes | Yes | 35 | 21.2 | 13.8 | B73C45B939214F2895BA6462FF9436A1 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2432 |  | 2014-09-19 | 2014-09-19 17:39 | 2014-09-19 18:11 | CARRIER - | 74 | 2.4 | Yes | Yes | 22 | 20.4 | 1.6 | F2AEDA7C1A894C808DBFD052BFA38896 |  | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Bakersfield | CA | 93308-2333 |  | 2014-09-26 | 2014-09-26 16:34 | 2014-09-26 16:34 | OTHER - PGC042K080B | 87 | 0 | Yes | Yes | 18.1 | 18.7 | -0.6 | F35690160BDC4B10BD63839C273B7566 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4606 |  | 2014-08-04 | 2014-08-04 14:54 | 2014-08-04 15:23 | WEATHER KING - WRMAA030JK06E | 80 | 6 | Yes | Yes | 21 | 21.5 | -0.5 | 3930BC32A1EB467C8CA0BAF17DED2B8C |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Bakersfield | CA | 93309-4853 |  | 2014-09-16 | 2014-09-16 18:39 | 2014-09-16 18:39 | GOODMAN - PGP1330045M41BA | 78 | 0 | Yes | Yes | 19 | 18.8 | 0.2 | F9C82F93C3B34B6AA92BA1C7C8886764 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2508 |  | 2014-07-16 | 2014-07-16 11:43 | 2014-07-16 14:24 | PAYNE - RRMA-A024JK06X | 62 | 5.7 | Yes | Yes | 13.7 | 14.6 | -0.8 | 8D93A04E83EE48AEB13E2CDB9D9F00AF |  | R22 | Non-TXV |  | 9.194% | 0.90806 | 17.67% | [5 empty] | Non-TXV | 9.194%
Bakersfield | CA | 93313-4339 |  | 2014-10-07 | 2014-10-07 16:25 | 2014-10-07 16:43 | OTHER - FAFF-049JAZ | 85 | 4.7 | Yes | Yes | 24.7 | 23.7 | 1 | 2AFC9C86C6C14228B78D080A8D1890DB |  | R22 | TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | TXV | 5.529%
Lemoore | CA | 93245-2503 |  | 2014-07-30 | 2014-07-30 13:22 | 2014-07-30 13:22 | GOODMAN - GPG1348070M41AD | 125 | 0 | Yes | Yes | 24.3 | 20.4 | 3.9 | 152B5584A7ED4625B74B86D84BAD0283 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3908 |  | 2014-08-21 | 2014-08-21 10:39 | 2014-08-21 10:39 | AMERICAN STANDARD - | 85 | 0 | Yes | Yes | 24.8 | 20.7 | 4.2 | F1DCEBC531984F58BE846F98B8CDA99A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94089-2440 |  | 2014-09-15 | 2014-09-15 08:39 | 2014-09-15 08:58 | OTHER - UKN | 85 | 3.2 | Yes | Yes | 20.1 | 16.9 | 3.2 | 3BE65D0E677F45C89254F7123287080B |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Bakersfield | CA | 93307-0000 |  | 2014-09-10 | 2014-09-10 19:07 | 2014-09-10 19:09 | WEATHER KING - 13AJ36A01 | 108 | 5 | Yes | Yes | 20.5 | 18.2 | 2.3 | C21E2DAA206F4617AF6E6471EBFEECC3 |  | R22 | TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | TXV | 4.63%
Wasco | CA | 93280-2903 |  | 2014-08-10 | 2014-08-10 20:38 | 2014-08-10 20:40 | RHEEM - RRNA-B036JK06X | 83 | 4.1 | Yes | Yes | 22.5 | 22.6 | -0.1 | 1F1CF40D72824CD188CA9B41BB02F3C1 |  | R22 | TXV |  | 4.94% | 0.9506 | 9.493% | [5 empty] | TXV | 4.94%
Fairfield | CA | 94534-7950 |  | 2014-10-01 | 2014-10-01 12:39 | 2014-10-03 07:59 | ARMSTRONG - SCU10E60A-2 | 131 | 6.2 | Yes | Yes | 14.3 | 17.2 | -2.9 | BD4263A5709B417EA9AC68A6E5476843 |  | R22 | Non-TXV |  | 4.733% | 0.95267 | 9.095% | [5 empty] | Non-TXV | 4.733%
Bakersfield | CA | 93313-4320 |  | 2014-10-04 | 2014-10-04 17:27 | 2014-10-04 17:55 | RHEEM - 13A548AD1 | 85 | 7.7 | Yes | Yes | 25.7 | 22 | 3.7 | C992FA8F5BC441D2A3C582AE97A7EC37 |  | R410A | TXV |  | 9.059% | 0.90941 | 17.41% | [5 empty] | TXV | 9.059%
Vacaville | CA | 95688-3044 |  | 2014-07-17 | 2014-07-17 10:41 | 2014-07-17 22:17 | ALLEGIANCE - 2A7A1018A1000AA | 50 | 1.6 | Yes | Yes | 16 | 18.5 | -2.5 | 711C4A30D49247829FC13A0F2D0E95B3 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Concord | CA | 94518-1129 |  | 2014-08-26 | 2014-08-26 12:17 | 2014-08-26 12:17 | LENNOX - PGE10B36D075LA | 58 | 0 | Yes | Yes | 18.4 | 17.7 | 0.7 | C9471742A6344C68B7941BD50332EDB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-0000 |  | 2014-11-04 | 2014-11-04 15:37 | 2014-11-04 16:14 | GOODMAN - GS430601BG | 85 | 4.3 | Yes | Yes | 21.5 | 20.6 | 1 | FD1EC6C1C36643E99138E8234C49A138 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Concord | CA | 94521-4310 |  | 2014-08-21 | 2014-08-21 12:50 | 2014-08-21 13:17 | ICP - N2A336AKB300 | 84 | 14.9 | Yes | Yes | 23 | 17.6 | 5.4 | B98FA2B767744738A182B1A8154CAFC2 |  | R22 | Non-TXV |  | 17.74% | 0.82262 | 34.09% | [5 empty] | Non-TXV | 17.74%
Woodland | CA | 95776-5117 |  | 2014-08-07 | 2014-08-07 13:33 | 2014-08-07 16:23 | CARRIER - 38CKC0244340 | 62 | 4.4 | Yes | Yes | 12.9 | 15.8 | -2.9 | 39DBBDD84D4E429F8B0685B551600364 |  | R22 | Non-TXV |  | 7.097% | 0.92903 | 13.64% | [5 empty] | Non-TXV | 7.097%
Bakersfield | CA | 93313-4556 |  | 2014-10-19 | 2014-10-19 18:07 | 2014-10-19 18:10 | OTHER - 38CK030---321 | 76 | 4.6 | Yes | Yes | 22.1 | 21 | 1.1 | B556F4AFC9894DF8ADFBC21C895F6983 |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
San Jose | CA | 95134-1579 |  | 2014-08-22 | 2014-08-22 11:37 | 2014-08-22 11:40 | BRYANT - 661CJ024 | 135 | 6 | Yes | Yes | 20.1 | 19.1 | 1.1 | 68B9F069834A4E8FA620367372353158 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Lemoore | CA | 93245-4606 |  | 2014-08-04 | 2014-08-04 12:14 | 2014-08-04 12:40 | WEATHER KING - WRMAA030JK06E | 80 | 3.9 | Yes | Yes | 20.7 | 19.7 | 1 | C52266768AAA4119BE7D5238816A6C26 |  | R22 | Non-TXV |  | 4.875% | 0.95125 | 9.369% | [5 empty] | Non-TXV | 4.875%
Arvin | CA | 93203-2783 |  | 2014-11-06 | 2014-11-06 12:00 | 2014-11-06 12:21 | OTHER - UNK | 85 | 4.4 | Yes | Yes | 20.3 | 21.8 | -1.5 | 31C5183DB53344FEAB8DB4ED3F80AD2E |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Bakersfield | CA | 93307-3139 |  | 2014-09-10 | 2014-09-10 19:19 | 2014-09-10 19:21 | OTHER - 588ANW0240ACAD | 38 | 11 | Yes | Yes | 19.8 | 20.2 | -0.4 | A7748E172EA2497FB112D26E8FFEAA9D |  | R22 | Non-TXV |  | 28.95% | 0.71053 | 55.63% | [5 empty] | Non-TXV | 28.95%
Bakersfield | CA | 93308-7859 |  | 2014-10-01 | 2014-10-01 12:21 | 2014-10-01 12:21 | YORK - D1NHA036N05606C | 67 | 0 | Yes | Yes | 13.3 | 17.9 | -4.6 | 4AE70E3CAF1F4C3990EBD6578F94385C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4786 |  | 2014-09-26 | 2014-09-26 16:42 | 2014-09-26 16:42 | RHEEM - RRPIBO48JK08K | 161 | 0 | Yes | Yes | 17.1 | 20.1 | -3 | A5CED649AE87416299C29D78DAFC4547 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1633 |  | 2014-07-27 | 2014-07-27 20:32 | 2014-07-27 20:37 | YORK - D1NH036N05606C | 108 | 5.6 | Yes | Yes | 22.9 | 20.4 | 2.5 | 36E77916A7B44608B4490EADC7A81116 |  | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Lemoore | CA | 93245-2860 |  | 2014-07-31 | 2014-07-31 10:14 | 2014-07-31 10:34 | RHEEM - URKAA042JK06E | 69 | 3.6 | Yes | Yes | 19.7 | 19.3 | 0.4 | 5260923A4E7D4CB5AC2971CFC936797B |  | R22 | Non-TXV |  | 5.217% | 0.94783 | 10.03% | [5 empty] | Non-TXV | 5.217%
Wasco | CA | 93280-1241 |  | 2014-08-17 | 2014-08-17 18:17 | 2014-08-17 18:20 | YORK - N2A336GKA200 | 92 | 6.2 | Yes | Yes | 23 | 22.6 | 0.4 | C660B564BC7340E2A9A00583DF55CB02 |  | R22 | Non-TXV |  | 6.739% | 0.93261 | 12.95% | [5 empty] | Non-TXV | 6.739%
Dixon | CA | 95620-2543 |  | 2014-07-22 | 2014-07-22 11:53 | 2014-07-22 12:35 | CARRIER - 38BRCO42330 | 103 | 3.7 | Yes | Yes | 22.3 | 18.7 | 3.6 | A14076FDFF444EE9B17FFC9101E1A532 |  | R22 | Non-TXV |  | 3.592% | 0.96408 | 6.903% | [5 empty] | Non-TXV | 3.592%
Lemoore | CA | 93245-4605 |  | 2014-08-01 | 2014-08-01 10:38 | 2014-08-01 11:03 | RHEEM - WRKAA030JK06E | 54 | 5.2 | Yes | Yes | 21.6 | 20.4 | 1.2 | 4380404674DD4B3EAF1BB44AF6C133A9 |  | R22 | Non-TXV |  | 9.63% | 0.9037 | 18.51% | [5 empty] | Non-TXV | 9.63%
Vacaville | CA | 95687-3456 |  | 2014-07-16 | 2014-07-16 11:56 | 2014-07-16 17:19 | GIBSON - JT5BD-024K | 126 | -8.9 | Yes | Yes | 15 | 17.9 | -2.9 | 28DC91B3E725430CB4B6EA56A91802BA |  | R22 | Non-TXV |  | -7.063% | 1.0706 | 1.978% |  |  |  |  | Non-TXV |  |  | -7.063%
Bakersfield | CA | 93308-9696 |  | 2014-10-01 | 2014-10-01 11:38 | 2014-10-01 11:38 | OTHER - UNK | 100 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 173BC63D738E4AB5B656CF1883D30FA1 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3605 |  | 2014-09-09 | 2014-09-09 16:14 | 2014-09-09 16:14 | OTHER - 585A030080YAC | 50 | 0 | Yes | Yes | 20.9 | 18.5 | 2.4 | 5717857BC8AF4879B40404E45EE58F49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-5648 |  | 2014-10-24 | 2014-10-24 08:41 | 2014-10-24 08:41 | RHEEM - URGG05E36JKR | 75 | 0 | Yes | Yes | 16.7 | 20.9 | -4.2 | 107E323C6D384438846204F33939BF40 | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-6814 |  | 2014-10-03 | 2014-10-03 10:02 | 2014-10-03 11:40 | AMANA - RCC60C2C | 150 | 6.7 | Yes | Yes | 22.8 | 20.4 | 2.4 | 8444365B58AF413CBD8BB9937788BE1C |  | R22 | Non-TXV |  | 4.467% | 0.95533 | 8.584% | [5 empty] | Non-TXV | 4.467%
Bakersfield | CA | 93308-7882 |  | 2014-10-01 | 2014-10-01 11:28 | 2014-10-01 11:28 | GOODMAN - GPG1036076 | 75 | 0 | Yes | Yes | 25.4 | 20.4 | 5 | 4554DA83A91D4C9CB0EBE912A49B8759 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5618 |  | 2014-09-22 | 2014-09-22 12:52 | 2014-09-22 13:08 | AMERICAN STANDARD - YCY048F1H0AD | 177 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | A44DE19C54E14FAC84304EBEF7872C43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2428 |  | 2014-09-04 | 2014-09-04 14:26 | 2014-09-04 14:26 | YORK - DAYAFO36N0902 | 85 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 7545FDC0AE94408BBF793F038640DCCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3940 |  | 2014-07-18 | 2014-07-18 16:18 | 2014-07-18 19:41 | AMANA - RCE30A2D | 151 | 5.7 | Yes | Yes | 23.1 | 18 | 5.2 | F729C7CD46A0417583468DBCF894D50E |  | R22 | Non-TXV |  | 3.775% | 0.96225 | 7.254% | [5 empty] | Non-TXV | 3.775%
Wasco | CA | 93280-2560 |  | 2014-08-03 | 2014-08-03 19:03 | 2014-08-03 19:07 | RHEEM - DARH-F036N060B | 112 | 8.2 | Yes | Yes | 23.6 | 21 | 2.6 | 7EDD35E8FCFC4ADAAC47C72CFDACC50D |  | R22 | Non-TXV |  | 7.321% | 0.92679 | 14.07% | [5 empty] | Non-TXV | 7.321%
Bakersfield | CA | 93308-7135 |  | 2014-10-01 | 2014-10-01 14:24 | 2014-10-01 15:25 | YORK - UNK | 129 | 6.5 | Yes | Yes | 22.7 | 20.4 | 2.3 | E1BAEC29866742E6A3256A351F28CBB3 |  | R22 | Non-TXV |  | 5.039% | 0.94961 | 9.683% | [5 empty] | Non-TXV | 5.039%
Bakersfield | CA | 93309-2934 |  | 2014-09-13 | 2014-09-13 10:59 | 2014-09-13 10:59 | OTHER - PGCM036K060D | 68 | 0 | Yes | Yes | 14.5 | 19.9 | -5.4 | 8C980B5C189E4374A8B4F12954492466 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2328 |  | 2014-09-04 | 2014-09-04 08:56 | 2014-09-04 08:56 | YORK - D1NH042N06506C | 84 | 0 | Yes | Yes | 20.7 | 20.1 | 0.7 | 8EF5284ABBEA4A77BB621622D0BC78DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2328 |  | 2014-09-04 | 2014-09-04 10:41 | 2014-09-04 10:41 | OTHER - UNK | 80 | 0 | Yes | Yes | 0.8 | 17.9 | -17.1 | F06E043443D84A13B245933A775DF0CF | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2330 |  | 2014-09-04 | 2014-09-04 13:12 | 2014-09-04 17:05 | DAY & NIGHT - 584ANW060080 | 96 | 11.5 | Yes | Yes | 26.8 | 21.5 | 5.3 | B755938551E743B499476F0D51DB46FC |  | R22 | Non-TXV |  | 11.98% | 0.88021 | 23.02% | [5 empty] | Non-TXV | 11.98%
Fairfield | CA | 94533-5124 |  | 2014-07-25 | 2014-07-25 12:44 | 2014-07-25 15:57 | TRANE - YCC024F1L0BJ | 65 | 3.7 | Yes | Yes | 18.5 | 18.2 | 0.3 | 9C4374B691BC46AD93E107B300923B82 |  | R22 | Non-TXV |  | 5.692% | 0.94308 | 10.94% | [5 empty] | Non-TXV | 5.692%
Davis | CA | 95618-1643 |  | 2014-08-19 | 2014-08-19 09:40 | 2014-08-19 10:22 | - CKL30--1G | 75 | -6.2 | Yes | Yes | 18.5 | 18.7 | -0.2 | F6BAF63B53B84EDC905022055FB0E405 |  | R22 | Non-TXV |  | -8.267% | 1.0827 | 2.315% |  |  |  |  | Non-TXV |  |  | -8.267%
Bakersfield | CA | 93311-2666 |  | 2014-09-24 | 2014-09-24 11:49 | 2014-09-24 11:49 | OTHER - P3HUA12NO4801A | 76 | 0 | Yes | Yes | 17.7 | 19.5 | -1.8 | 2E54E8081E7D44EEA2808D8BB0BB2150 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-3037 |  | 2014-07-17 | 2014-07-17 13:35 | 2014-07-17 14:10 | RHEEM - RACA-036AAQ | 36 | 3.3 | Yes | Yes | 25.5 | 19.9 | 5.6 | 4ADFA971806E43729D735199D15A55E5 |  | R22 | Non-TXV |  | 9.167% | 0.90833 | 17.62% | [5 empty] | Non-TXV | 9.167%
Bakersfield | CA | 93307-7187 |  | 2014-09-12 | 2014-09-12 20:53 | 2014-09-12 20:56 | GOODMAN - GPG1360090M91AD | 185 | 8.1 | Yes | Yes | 24.6 | 19.7 | 4.9 | EBECDE32C19E4E11A5B6EE70336CDE5B |  | R410A | Non-TXV |  | 4.378% | 0.95622 | 8.414% | [5 empty] | Non-TXV | 4.378%
Bakersfield | CA | 93312-2704 |  | 2014-09-19 | 2014-09-19 12:04 | 2014-09-19 12:04 | GOODMAN - GSC130361FA | 83 | 0 | Yes | Yes | 24.2 | 21.5 | 2.7 | 415A7932F0EA49EB8D3E1D221CD63154 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2704 |  | 2014-09-19 | 2014-09-19 12:07 | 2014-09-19 12:07 | GOODMAN - GSC130361FA | 83 | 0 | Yes | Yes | 24.8 | 20.8 | 4 | 02CF3005900C471E9E5101764283D2B3 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5151 |  | 2014-07-23 | 2014-07-23 11:02 | 2014-07-23 11:40 | SEARS - 811231 | 38 | 4.5 | Yes | Yes | 17.6 | 18.7 | -1.1 | F52E3024FEE24D3499482678E093254D |  | R22 | Non-TXV |  | 11.84% | 0.88158 | 22.76% | [5 empty] | Non-TXV | 11.84%
Antioch | CA | 94509-5044 |  | 2014-10-08 | 2014-10-08 12:07 | 2014-10-08 12:07 | PAYNE - PA13NR060-J | 168 | 0 | Yes | Yes | 20 | 18.7 | 1.3 | 90B7214930C84CF1B8C808E491DC1128 |  | R22 | TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2682 |  | 2014-11-05 | 2014-11-05 14:35 | 2014-11-05 14:35 | AIRE-FLO - 2AC13B36P1A | 139 | 0 | Yes | Yes | 15.4 | 18.2 | -2.8 | B2B21DE4836042509464276F6DDA54D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5103 |  | 2014-10-10 | 2014-10-10 08:31 | 2014-10-10 08:59 | CARRIER - 24ABA336A310 | 84 | 13.8 | Yes | Yes | 16 | 18 | -2 | F1D441416F0B4EF1ADBEEC4507991A19 |  | R410A | TXV |  | 16.43% | 0.83571 | 31.57% | [5 empty] | TXV | 16.43%
Fairfield | CA | 94533-4262 |  | 2014-07-25 | 2014-07-25 15:53 | 2014-07-25 15:53 | - | 85 | 0 | Yes | Yes | 15.3 | 17.5 | -2.2 | E83BA016F51C457E9D1763887D1453B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-9740 |  | 2014-07-31 | 2014-07-31 13:23 | 2014-07-31 13:42 | AMANA - PGD48C0902E | 139 | 12.2 | Yes | Yes | 21.5 | 17.7 | 3.8 | F5EC58CA281A480082A70348670A2ABB |  | R22 | Non-TXV |  | 8.777% | 0.91223 | 16.87% | [5 empty] | Non-TXV | 8.777%
Bakersfield | CA | 93301-1025 |  | 2014-10-24 | 2014-10-24 14:22 | 2014-10-24 14:22 | WESTINGHOUSE - UNK | 79 | 5.4 | Yes | Yes | 7 | 21.3 | -14.3 | CFB5584798A848D688181C4E73F98855 | Add refrigerant: 5.4 oz | R22 | Non-TXV |  | 6.835% | 0.93165 | 13.14% | [5 empty] | Non-TXV | 6.835%
Woodland | CA | 95695-4451 |  | 2014-07-23 | 2014-07-23 12:07 | 2014-07-23 12:07 | PAYNE - PY3060GNAA36060NA | 110 | 0 | Yes | Yes | 14.3 | 16.9 | -2.6 | 0210B4E0CAC542959614CE184A76952C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1025 |  | 2014-10-24 | 2014-10-24 15:33 | 2014-10-24 15:33 | OTHER - UNK | 93 | 0 | Yes | Yes | 15.4 | 18 | -2.6 | 89C30990FD184194B2F0878ECB8EAB34 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1025 |  | 2014-10-24 | 2014-10-24 15:15 | 2014-10-24 15:15 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 20 | 20.1 | -0.1 | 122A71E0E88D4C558975DE358592BA6F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-2568 |  | 2014-09-08 | 2014-09-08 19:54 | 2014-09-08 19:56 | COMFORT AIRE - PGC024K040D | 58 | 3.9 | Yes | Yes | 20.4 | 23.1 | -2.7 | 60ADB5C3AA7C4FFB9C4A5A0E9EFE8933 |  | R22 | Non-TXV |  | 6.724% | 0.93276 | 12.92% | [5 empty] | Non-TXV | 6.724%
Bakersfield | CA | 93308-2644 |  | 2014-09-26 | 2014-09-26 16:46 | 2014-09-26 16:46 | WESTINGHOUSE - UNK | 104 | 0 | Yes | Yes | 21.4 | 19.4 | 2 | 4064D6AC0F2A4B2F8DB2EBFFA121A279 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7704 |  | 2014-10-09 | 2014-10-09 08:14 | 2014-10-09 08:14 | RHEEM - RAFD048JB3 | 101 | 0 | Yes | Yes | 18.2 | 20.4 | -2.2 | BFD5B912BE03443EAFEAD2CACC87367B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7239 |  | 2014-09-12 | 2014-09-12 20:33 | 2014-09-12 20:37 | OTHER - DC42F030N07 | 64 | 4.7 | Yes | Yes | 26.8 | 21.3 | 5.5 | E4B6D3C899E44729AB49788D5BD9A008 |  | R410A | TXV |  | 7.344% | 0.92656 | 14.11% | [5 empty] | TXV | 7.344%
Dixon | CA | 95620-3145 |  | 2014-07-22 | 2014-07-22 12:29 | 2014-07-22 13:44 | DAY & NIGHT - 2294E11843 | 86 | 5.3 | Yes | Yes | 16.9 | 18.1 | -1.2 | F67252381837400D9E7C9C440235D53F |  | R22 | Non-TXV |  | 6.163% | 0.93837 | 11.84% | [5 empty] | Non-TXV | 6.163%
Antioch | CA | 94509-3344 |  | 2014-11-11 | 2014-11-11 13:36 | 2014-11-11 13:36 | PAYNE - PA10JA018000AAAA | 60 | 0 | Yes | Yes | 25.1 | 19.3 | 5.8 | 84699B21FA084530AE150013E7872C0E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2430 |  | 2014-08-22 | 2014-08-22 13:26 | 2014-08-22 17:29 | CARRIER - 38TKB030---311 | 79 | 6.8 | Yes | Yes | 21.6 | 20.4 | 1.2 | F61EE35AAD4C40B59D03E4EC4C6552FA |  | R22 | Non-TXV |  | 8.608% | 0.91392 | 16.54% | [5 empty] | Non-TXV | 8.608%
San Jose | CA | 95135-1352 |  | 2014-07-22 | 2014-07-22 13:50 | 2014-07-22 14:12 | BRYANT - 561CJX048 | 109 | 3.6 | Yes | Yes | 20.5 | 20.4 | 0.1 | AC0E6D944537444B80640C3BEE8C118E |  | R22 | Non-TXV |  | 3.303% | 0.96697 | 6.347% | [5 empty] | Non-TXV | 3.303%
Bakersfield | CA | 93313-5365 |  | 2014-10-07 | 2014-10-07 15:37 | 2014-10-07 15:56 | GOODMAN - GSC130481AF | 85 | 9.5 | Yes | Yes | 19 | 22 | -3 | 6971079846DF4B338D49E468B8CF234A |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Bakersfield | CA | 93313-5365 |  | 2014-10-07 | 2014-10-07 15:59 | 2014-10-07 16:18 | GOODMAN - GSC130481AF | 85 | 16.2 | Yes | Yes | 20.5 | 21.8 | -1.3 | C4B4D2903E754E06ACB83D43803BB261 |  | R22 | Non-TXV |  | 19.06% | 0.80941 | 36.63% | [5 empty] | Non-TXV | 19.06%
Antioch | CA | 94531-7133 |  | 2014-11-11 | 2014-11-11 14:40 | 2014-11-11 15:01 | TRANE - BTD736A100B0 | 88 | 11.5 | Yes | Yes | 19.8 | 19.3 | 0.5 | 2F3260F11B6F4623BE97BDE413E5361A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 35°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.07% | 0.86932 | 25.11% | [5 empty] | Non-TXV | 13.07%
Bakersfield | CA | 93306-4405 |  | 2014-09-08 | 2014-09-08 09:33 | 2014-09-08 18:08 | OTHER - PGC030K060E | 51 | 5.9 | Yes | Yes | 24.2 | 22 | 2.2 | 56AD4E3A677742C48678654B374D4FEC |  | R22 | TXV |  | 11.57% | 0.88431 | 22.23% | [5 empty] | TXV | 11.57%
Bakersfield | CA | 93309-1730 |  | 2014-10-08 | 2014-10-08 10:19 | 2014-10-08 11:06 | DAY & NIGHT - UNK | 85 | -8 | Yes | Yes | 17.2 | 20.2 | -3 | 08CB182AD7A14B8BB2C869277CC89413 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Milpitas | CA | 95035-6207 |  | 2014-09-22 | 2014-09-22 10:04 | 2014-09-22 10:18 | LENNOX - 13ACD-048-230-04 | 119 | 4.1 | Yes | Yes | 20.2 | 17.2 | 3 | 0300256DE05040A98C529448FA0E32A0 |  | R22 | Non-TXV |  | 3.445% | 0.96555 | 6.621% | [5 empty] | Non-TXV | 3.445%
Rio Vista | CA | 94571-2226 |  | 2014-09-03 | 2014-09-03 09:38 | 2014-09-03 10:18 | YORK - H2RRCO24S0GHG | 71 | 3 | Yes | Yes | 20.6 | 21 | -0.4 | 0326E26FC5D94C5E8E5A4F9AFDB049E5 |  | R22 | Non-TXV |  | 4.225% | 0.95775 | 8.12% | [5 empty] | Non-TXV | 4.225%
Woodland | CA | 95776-4200 |  | 2014-07-23 | 2014-07-23 14:18 | 2014-07-23 14:21 | GOODMAN - | 125 | 5.4 | Yes | Yes | 17.4 | 20.1 | -2.7 | 8E4C1428B2384425A249080427D879D2 |  | R22 | Non-TXV |  | 4.32% | 0.9568 | 8.302% | [5 empty] | Non-TXV | 4.32%
Woodland | CA | 95776-6727 |  | 2014-07-23 | 2014-07-23 14:56 | 2014-07-23 15:18 | CARRIER - 24ACR348A300 | 147 | 6.8 | Yes | Yes | 26 | 20.4 | 5.6 | F8A0EA34BF9A4964A8F95A7C90C0A507 |  | R22 | Non-TXV |  | 4.626% | 0.95374 | 8.89% | [5 empty] | Non-TXV | 4.626%
Bakersfield | CA | 93308-4612 |  | 2014-10-10 | 2014-10-10 15:16 | 2014-10-10 15:33 | OTHER - TZAA-336-2A757 | 84 | 2.5 | Yes | Yes | 17 | 18.3 | -1.3 | 8913AAF14BB44A70B7177D64A7B3BAC6 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Bakersfield | CA | 93313-0000 |  | 2014-09-15 | 2014-09-15 15:05 | 2014-09-15 15:05 | GOODMAN - OSC130481AF | 152 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 9E5C2AF40602423BABE80ACBD56C5266 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3362 |  | 2014-09-12 | 2014-09-12 20:45 | 2014-09-12 20:46 | COLEMAN - DAYP-F036N070A | 108 | 7.2 | Yes | Yes | 25.8 | 22.1 | 3.7 | 8B8325BD616B4CB8A9E1B319A027E0B9 | Add refrigerant: 7.2 oz | R22 | TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | TXV | 6.667%
Bakersfield | CA | 93313-4323 |  | 2014-10-04 | 2014-10-04 18:07 | 2014-10-04 18:25 | BRYANT - 582ANW036060AAAF | 85 | 9.3 | Yes | Yes | 17.5 | 20.3 | -2.8 | A2E3A015A39444319EB98BC8644DACFE |  | R22 | Non-TXV |  | 10.94% | 0.89059 | 21.03% | [5 empty] | Non-TXV | 10.94%
Bakersfield | CA | 93307-6910 |  | 2014-09-15 | 2014-09-15 11:57 | 2014-09-15 11:57 | OTHER - UNK | 106 | 0 | Yes | Yes | 20.6 | 19.5 | 1.1 | 1A5EF018EFD946B4B83648DE80D5E884 | Liquid Temperature cannot be less than outdoor air temperature. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4254 |  | 2014-07-21 | 2014-07-21 12:48 | 2014-07-21 14:19 | TRANE - 4TTX6048A1000AA | 116 | 5.2 | Yes | Yes | 17.8 | 18.5 | -0.7 | 2D88B3D1F70E403CAF43A7C978F9BF30 |  | R22 | Non-TXV |  | 4.483% | 0.95517 | 8.615% | [5 empty] | Non-TXV | 4.483%
Bakersfield | CA | 93309-5843 |  | 2014-11-19 | 2014-11-19 12:22 | 2014-11-19 12:22 | GOODMAN - PGP13360701A | 112 | 0 | Yes | Yes | 26 | 19.9 | 6.1 | 21F8B29F460D4BED97E1C4AA5683225D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3208 |  | 2014-08-26 | 2014-08-26 10:20 | 2014-08-26 10:20 | CARRIER - 38TH024300 | 56 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | 8D1DAE1302034F028BDE65226EA413F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1901 |  | 2014-10-13 | 2014-10-13 10:35 | 2014-10-16 07:49 | CARRIER - 38TKB042330 | 88 | 3.8 | Yes | Yes | 13.5 | 13.5 | 0.1 | 31E8E417481444F99DF128D1A6B40A47 |  | R22 | Non-TXV |  | 4.318% | 0.95682 | 8.299% | [5 empty] | Non-TXV | 4.318%
Bakersfield | CA | 93309-5843 |  | 2014-11-19 | 2014-11-19 11:49 | 2014-11-19 11:49 | OTHER - UNK | 71 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 081F489E76794FB5AC750D40A87F5C2B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1143 |  | 2014-08-25 | 2014-08-25 12:49 | 2014-08-25 12:49 | - | 85 | 0 | Yes | Yes | 20.5 | 18.8 | 1.7 | 39ADB991338D4DF09057151DDDD73323 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-3167 |  | 2014-10-17 | 2014-10-17 09:34 | 2014-10-17 09:50 | CARRIER - 38TH036300 | 84 | 4.1 | Yes | Yes | 20.7 | 20.4 | 0.3 | 2A86C82F8B4146518C59AF2DC37DD40D |  | R22 | Non-TXV |  | 4.881% | 0.95119 | 9.38% | [5 empty] | Non-TXV | 4.881%
Fresno | CA | 93722-4761 |  | 2014-07-18 | 2014-07-18 11:34 | 2014-07-18 12:09 | CARRIER - UNK | 57 | -6 | Yes | Yes | 21.2 | 19.3 | 1.9 | 2CEB54087ECD4A2DB270B2209FB3764F |  | R22 | Non-TXV |  | -10.53% | 1.1053 | 2.948% |  |  |  |  | Non-TXV |  |  | -10.53%
Napa | CA | 94558-4740 |  | 2014-09-18 | 2014-09-18 11:55 | 2014-09-18 14:22 | RHEEM - | 78 | 3.9 | Yes | Yes | 20.5 | 19.9 | 0.6 | 69E6F39D97FF4D6181DC579AE46034D5 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Woodland | CA | 95776-5104 |  | 2014-08-06 | 2014-08-06 15:07 | 2014-08-06 16:05 | GOODMAN - CK36-1A | 73 | 4.5 | Yes | Yes | 15.7 | 18.8 | -3.1 | ACCEEAA6C17140B6BE8654C36137495D | Add refrigerant: 3 oz | R22 | Non-TXV |  | 6.164% | 0.93836 | 11.85% | [5 empty] | Non-TXV | 6.164%
Bakersfield | CA | 93307-6001 |  | 2014-09-11 | 2014-09-11 17:45 | 2014-09-11 17:48 | BRYANT - 583NW030040AAAD | 70 | 2.8 | Yes | Yes | 22 | 20.9 | 1.1 | B470536746B64400A0B089BAC01194E3 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93309-2529 |  | 2014-09-05 | 2014-09-05 20:10 | 2014-09-05 20:10 | COMFORT AIRE - PGC036K060D | 98 | 0 | Yes | Yes | 22.1 | 21.2 | 0.9 | 8151D02241954A358AEA7EEBC98865A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1315 |  | 2014-10-01 | 2014-10-01 13:46 | 2014-10-03 08:00 | PAYNE - 591ANX036000AAAA | 84 | 3.4 | Yes | Yes | 12.6 | 14.9 | -2.3 | A66631B31E0E4B6AA20E168AC0A523B2 |  | R22 | Non-TXV |  | 4.048% | 0.95952 | 7.779% | [5 empty] | Non-TXV | 4.048%
Bakersfield | CA | 93309-2952 |  | 2014-09-13 | 2014-09-13 13:46 | 2014-09-13 13:46 | AMERICAN STANDARD - YCY036G1M0AD | 130 | 0 | Yes | Yes | 20.5 | 19.3 | 1.3 | 6F2AE23D9DE44A03A494F356826CB579 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5922 |  | 2014-07-16 | 2014-07-16 13:50 | 2014-07-18 13:05 | AMANA - PGD36C0702E | 104 | 7.9 | Yes | Yes | 13.2 | 16 | -2.8 | F0F4E419E488406E961448F0739B237B |  | R22 | Non-TXV |  | 7.596% | 0.92404 | 14.6% | [5 empty] | Non-TXV | 7.596%
Antioch | CA | 94509-3214 |  | 2014-10-10 | 2014-10-10 09:35 | 2014-10-10 09:35 | KENMORE - CA3036VKA1 | 94 | 0 | Yes | Yes | 19.9 | 19.9 | 0 | 8ED76B511AD340A5AA81D0F261D3CF69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1515 |  | 2014-11-04 | 2014-11-04 15:58 | 2014-11-04 16:16 | OTHER - DARA-F03N060C | 85 | 4.2 | Yes | Yes | 13.3 | 16.2 | -2.9 | 802CA55F174742F4B3910C1FA16A7B6A |  | R22 | Non-TXV |  | 4.941% | 0.95059 | 9.496% | [5 empty] | Non-TXV | 4.941%
Concord | CA | 94519-1315 |  | 2014-08-25 | 2014-08-25 13:22 | 2014-08-25 13:22 | YORK - CZB03611A | 111 | 0 | Yes | Yes | 14.6 | 10.6 | 4 | BCCFFE41C2224062B515FF0AD39C69ED |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4705 |  | 2014-10-19 | 2014-10-19 18:27 | 2014-10-19 18:30 | OTHER - DBYP-F036N070A | 108 | 5 | Yes | Yes | 21.6 | 19.7 | 1.9 | 6F957615896E42C3AB71A9974C9885DE |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
W Sacramento | CA | 95691-6214 |  | 2014-08-07 | 2014-08-07 08:38 | 2014-08-07 09:17 | CARRIER - 38CKC036---3551 | 70 | 5.1 | Yes | Yes | 20.7 | 21 | -0.3 | 9B7EA262DB004120A602831F75EA584C |  | R22 | Non-TXV |  | 7.286% | 0.92714 | 14% | [5 empty] | Non-TXV | 7.286%
Bakersfield | CA | 93311-9493 |  | 2014-10-19 | 2014-10-19 17:46 | 2014-10-19 17:48 | RHEEM - FAFF-037AZ | 96 | 11.6 | Yes | Yes | 23.4 | 21.5 | 1.9 | B72A018B66F34CB088EB2C577500F40A |  | R22 | Non-TXV |  | 12.08% | 0.87917 | 23.22% | [5 empty] | Non-TXV | 12.08%
Bakersfield | CA | 93311-9493 |  | 2014-10-19 | 2014-10-19 17:51 | 2014-10-19 17:52 | - | 85 | -5 | Yes | Yes | 22 | 19.7 | 2.4 | E3FCF45E41864DE98AA2893DE7B8BC44 |  |  |  |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | 0 |  |  | -5.882%
Pittsburg | CA | 94565-4834 |  | 2014-09-19 | 2014-09-19 09:34 | 2014-09-19 09:34 | TRANE - 2TTB0042A1000AA | 85 | 0 | Yes | Yes | 27 | 21.3 | 5.8 | 58C99D9DF1284D209840C301218969C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1113 |  | 2014-11-25 | 2014-11-25 11:05 | 2014-11-25 11:31 | PAYNE - PA14NA036 | 75 | 8.7 | Yes | Yes | 16.2 | 16.4 | -0.2 | 7113B47F94FF416C88A74DA08F9FD0A1 |  | R410A | TXV |  | 11.6% | 0.884 | 22.29% | [5 empty] | TXV | 11.6%
Bakersfield | CA | 93313-5531 |  | 2014-11-11 | 2014-11-11 09:55 | 2014-11-11 09:55 | RHEEM - RAMB060JBZ | 192 | 0 | Yes | Yes | 20.2 | 17.6 | 2.6 | AD0D267BDFEF4B01B935D9BE5F4B6C6E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1923 |  | 2014-10-30 | 2014-10-30 05:18 | 2014-10-30 05:34 | ICP - PGAD36D1K7 | 85 | 5.6 | Yes | Yes | 17.9 | 17.9 | 0 | 2528BB1DBFFE41139CD8BAB83D93A871 |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Clovis | CA | 93612-2286 |  | 2014-07-21 | 2014-07-21 17:17 | 2014-07-21 17:17 | CARRIER - 4855-036060331-- | 68 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | BA712837B6384837BEBFA23192BCAC5B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-2907 |  | 2014-07-17 | 2014-07-17 14:22 | 2014-07-17 15:03 | BRYANT - 561CJX0360 | 74 | 4.3 | Yes | Yes | 18 | 19.3 | -1.3 | 650B84E14EDA49CBBAA9397F2FCDF7D7 |  | R22 | Non-TXV |  | 5.811% | 0.94189 | 11.17% | [5 empty] | Non-TXV | 5.811%
Fresno | CA | 93722-4240 |  | 2014-07-18 | 2014-07-18 13:03 | 2014-07-18 13:24 | GOODMAN - GPG13420701AB | 105 | -8.6 | Yes | Yes | 22.8 | 19.7 | 3.1 | 151B2F592DD54B048B4B057F0D48DC49 |  | R22 | Non-TXV |  | -8.19% | 1.0819 | 2.294% |  |  |  |  | Non-TXV |  |  | -8.19%
Antioch | CA | 94509-5314 |  | 2014-10-17 | 2014-10-17 09:22 | 2014-10-17 09:22 | CARRIER - UNK | 85 | 0 | Yes | Yes | 28 | 22.4 | 5.6 | 53FAEC63822249A284920B586B3191FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95134-1577 |  | 2014-07-17 | 2014-07-17 15:17 | 2014-07-17 15:36 | BRYANT - 661CJ024 | 76 | 4.6 | Yes | Yes | 22.8 | 20.1 | 2.7 | 33932E3B593B433FB56BEC742A0F811C |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
Fresno | CA | 93722-1103 |  | 2014-07-18 | 2014-07-18 09:16 | 2014-07-18 09:40 | YORK - D3NZ030N05606NXA | 64 | 3 | Yes | Yes | 20.7 | 17.1 | 3.6 | EBEC06FF0040401B959EF69ED079637E |  | R410A | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Bakersfield | CA | 93309-4441 |  | 2014-11-19 | 2014-11-19 10:29 | 2014-11-19 10:29 | PAYNE - PY3GNAA30060NA | 98 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 0BFFFDE3AC74446EB835480376409C15 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1110 |  | 2014-11-24 | 2014-11-24 14:01 | 2014-11-24 14:01 | AMANA - RCB48B2A | 112 | 0 | Yes | Yes | 19.4 | 14.3 | 5.1 | 43C4236305C2440F9559BBE773317BBE |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1035 |  | 2014-07-28 | 2014-07-28 11:41 | 2014-07-28 12:14 | COLEMAN - UNK | 118 | 5.8 | Yes | Yes | 11 | 17.4 | -6.4 | F1F90EB4C4D74ABD9243B590B014265B |  | R22 | Non-TXV |  | 4.915% | 0.95085 | 9.446% | [5 empty] | Non-TXV | 4.915%
Bakersfield | CA | 93307-7142 |  | 2014-09-14 | 2014-09-14 23:51 | 2014-09-14 23:53 | GOODMAN - GSC130361GC | 85 | 5.7 | Yes | Yes | 22.6 | 19.8 | 2.8 | A0B033D58CDE4E57A58D039391A6BBE5 |  | R22 | Non-TXV |  | 6.706% | 0.93294 | 12.89% | [5 empty] | Non-TXV | 6.706%
Bakersfield | CA | 93306-4730 |  | 2014-09-08 | 2014-09-08 18:41 | 2014-09-08 18:41 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 19.8 | 21.5 | -1.7 | F9F7C596F99C40A99061C97C811330AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-4603 |  | 2014-08-01 | 2014-08-01 09:39 | 2014-08-01 10:05 | RHEEM - WRKAA030JK06E | 54 | 5.4 | Yes | Yes | 20.7 | 20.2 | 0.5 | BE20A2E8E5BD46968413E440AE15ACF6 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93307-3733 |  | 2014-09-14 | 2014-09-14 23:09 | 2014-09-14 23:12 | RHEEM - RRKA-A036JK06E | 62 | 5.1 | Yes | Yes | 21.4 | 19.7 | 1.7 | 0FCA98CD37B94CAD8D2A75D59A87A6C9 |  | R22 | Non-TXV |  | 8.226% | 0.91774 | 15.81% | [5 empty] | Non-TXV | 8.226%
Antioch | CA | 94509-6236 |  | 2014-10-13 | 2014-10-13 08:35 | 2014-10-13 08:35 | BRYANT - 561CJ048-G | 101 | 0 | Yes | Yes | 15.9 | 18 | -2.1 | 73E6461FDBF54E52A2E09BBB85574816 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4806 |  | 2014-09-10 | 2014-09-10 16:35 | 2014-09-10 16:35 | AMANA - PGD36C0702E | 110 | 0 | Yes | Yes | 29.1 | 21.3 | 7.9 | 9D294ECBC57F44BC9C36C5BED8D0EF89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2897 |  | 2014-07-23 | 2014-07-23 08:58 | 2014-07-23 10:16 | GOODMAN - GSC140361AE | 146 | 5.4 | Yes | Yes | 9.4 | 12.2 | -2.8 | 094A3BE718864520BBF58A03FB8FF0AA |  | R22 | Non-TXV |  | 3.699% | 0.96301 | 7.108% | [5 empty] | Non-TXV | 3.699%
Bakersfield | CA | 93306-5547 |  | 2014-09-12 | 2014-09-12 08:57 | 2014-09-12 08:57 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 22.9 | 20 | 2.9 | 58E2269B70904146A6CC0EFF47F1DAE6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4768 |  | 2014-09-11 | 2014-09-11 10:31 | 2014-09-11 10:31 | OTHER - PGAD42D1K7 | 179 | 0 | Yes | Yes | 19.7 | 20.1 | -0.4 | F5FF2FBAB3F6477CA6F48340BEE5ADA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2148 |  | 2014-08-26 | 2014-08-26 11:38 | 2014-08-26 11:38 | CARRIER - 24ABB336A310 | 83 | 0 | Yes | Yes | 24.8 | 19 | 5.8 | F8566F0C89C14F49B1CD97284E24C35C |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8514 |  | 2014-10-20 | 2014-10-20 09:42 | 2014-10-20 10:03 | CARRIER - 38CKC048360 | 109 | 11.7 | Yes | Yes | 20.4 | 22.9 | -2.5 | CF01E8022D6948FABD2C02B863F12985 |  | R22 | TXV |  | 10.73% | 0.89266 | 20.63% | [5 empty] | TXV | 10.73%
Woodland | CA | 95776-4918 |  | 2014-08-07 | 2014-08-07 10:30 | 2014-08-07 11:48 | GOODMAN - CKJ42-1AB | 106 | 6.9 | Yes | Yes | 25.2 | 19.4 | 5.8 | 7E203C2C475C4362950A206A69A78327 |  | R22 | Non-TXV |  | 6.509% | 0.93491 | 12.51% | [5 empty] | Non-TXV | 6.509%
Bakersfield | CA | 93311-9152 |  | 2014-10-03 | 2014-10-03 12:41 | 2014-10-03 12:41 | OTHER - 38CK036350 | 70 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | FE6700DC44514F3EB33B822A49FE3B3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5888 |  | 2014-08-27 | 2014-08-27 09:30 | 2014-08-27 11:07 | AMERICAN STANDARD - 2A7A3036A1000AA | 101 | 7.3 | Yes | Yes | 15.6 | 17.5 | -1.9 | D32671818C11439DB91B49C50EA52196 |  | R22 | Non-TXV |  | 7.228% | 0.92772 | 13.89% | [5 empty] | Non-TXV | 7.228%
Bakersfield | CA | 93311-9439 |  | 2014-11-13 | 2014-11-13 14:15 | 2014-11-13 14:15 | RHEEM - FAFF031JAZ | 96 | 0 | Yes | Yes | 16.6 | 18.2 | -1.6 | CEBC6A4C65C444829BE6FC702D3FAB12 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9439 |  | 2014-11-13 | 2014-11-13 14:23 | 2014-11-13 14:23 | RHEEM - FAFF037JAZ | 94 | 0 | Yes | Yes | 17.3 | 20.1 | -2.8 | 4EE9B6D396A64B368906574D9D5D3B8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4577 |  | 2014-07-22 | 2014-07-22 08:59 | 2014-07-22 09:25 | OTHER - PG030K060A | 52 | 2.1 | Yes | Yes | 24 | 19.1 | 4.9 | AAFE926FE799489D9BC46F4DD952235A |  | R22 | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
Arvin | CA | 93203-2453 |  | 2014-11-06 | 2014-11-06 12:14 | 2014-11-06 12:38 | ARCOAIRE - WC3422GKR2A | 85 | 7.4 | Yes | Yes | 17.5 | 14.9 | 2.7 | 066F77037ABD4BF092BF7EA7CAE63923 |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Bakersfield | CA | 93307-7313 |  | 2014-10-20 | 2014-10-20 15:47 | 2014-10-20 15:47 | RHEEM - URMAA036JK08X | 99 | 0 | Yes | Yes | 20.9 | 19.1 | 1.8 | 949D785C8AA84A3CA6BE748D42271A0B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1294 |  | 2014-07-18 | 2014-07-18 14:34 | 2014-07-18 14:34 | CARRIER - 48GS-024040301 | 56 | 0 | Yes | Yes | 19.6 | 19.5 | 0.1 | 5DD81101144045598EB7C7EE2C24DB8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1937 |  | 2014-09-08 | 2014-09-08 13:19 | 2014-09-08 13:19 | OTHER - 585HJ036060 | 102 | 0 | Yes | Yes | 26.7 | 25.3 | 1.4 | 8168954CAAF94FB58D2878F696CAA91A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1937 |  | 2014-09-08 | 2014-09-08 17:50 | 2014-09-08 17:50 | OTHER - 585HJ036060 | 102 | 0 | Yes | Yes | 24.3 | 23.2 | 1.2 | E391B802814F4EDB9D4B5186D5B897FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3477 |  | 2014-10-13 | 2014-10-13 10:17 | 2014-10-13 11:42 | CARRIER - 38CKC036350 | 70 | 3.8 | Yes | Yes | 21.1 | 20.4 | 0.7 | 92C2D4BBEF204F4EA05836E2F1D514A1 |  | R22 | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Fresno | CA | 93726-1517 |  | 2014-07-21 | 2014-07-21 10:22 | 2014-07-21 10:56 | OTHER - CA48K15 | 115 | 3.9 | Yes | Yes | 22.3 | 20.2 | 2.1 | F500126F2D0D4D4B8185BCD18EF177D3 |  | R22 | Non-TXV |  | 3.391% | 0.96609 | 6.517% | [5 empty] | Non-TXV | 3.391%
Bakersfield | CA | 93307-5932 |  | 2014-09-12 | 2014-09-12 20:39 | 2014-09-12 20:42 | GOODMAN - GPG1330045MA1AC | 80 | 4.4 | Yes | Yes | 27 | 21.7 | 5.3 | 7C82726AA0E04F648C0B0F612770521F |  | R410A | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Fresno | CA | 93722-9772 |  | 2014-07-23 | 2014-07-23 14:56 | 2014-07-23 15:27 | GOODMAN - GPG12360701A | 85 | 3.1 | Yes | Yes | 20.1 | 16.8 | 3.3 | A5DD7D3843D74E9E83AAE40B26A0CEBB |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Bakersfield | CA | 93312-4077 |  | 2014-10-13 | 2014-10-13 14:41 | 2014-10-13 15:06 | GOODMAN - PA0JAG42000ADAAA | 90 | 7 | Yes | Yes | 18.9 | 21.7 | -2.8 | C3849DDEA22B4DCBA9089A18EF5EBDDE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Lemoore | CA | 93245-2430 |  | 2014-07-30 | 2014-07-30 10:44 | 2014-07-30 11:06 | GOODMAN - GPG313420701AA | 107 | 4.9 | Yes | Yes | 22.1 | 19.3 | 2.8 | C878CDCD0ACB4E5CB9CF45D63B8CF83D |  | R22 | Non-TXV |  | 4.579% | 0.95421 | 8.801% | [5 empty] | Non-TXV | 4.579%
Arvin | CA | 93203-2815 |  | 2014-11-06 | 2014-11-06 12:08 | 2014-11-06 12:25 | TRANE - UNK | 132 | 7.1 | Yes | Yes | 19.2 | 21.5 | -2.3 | 5B2A499BF29F4BF0A507207B5F893D78 |  | R22 | Non-TXV |  | 5.379% | 0.94621 | 10.34% | [5 empty] | Non-TXV | 5.379%
Bakersfield | CA | 93312-6166 |  | 2014-10-14 | 2014-10-14 16:03 | 2014-10-14 16:22 | OTHER - AC036X1021A | 63 | 2.8 | Yes | Yes | 14.4 | 17.3 | -2.9 | 7D050F297E2B47DA9D3B9DD471C4D4B3 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Woodland | CA | 95695-4376 |  | 2014-09-04 | 2014-09-04 14:08 | 2014-09-04 14:08 | UNK - UNK | 85 | 0 | Yes | Yes | 19.3 | 19.6 | -0.3 | 28F2F666BF8642E7AA35DA812F109233 |  |  |  |  | 0% | 1 | 0%
San Jose | CA | 95123-1114 |  | 2014-07-18 | 2014-07-18 10:59 | 2014-07-18 10:59 | GOODMAN - GPH1324M21AB | 108 | 0 | Yes | Yes | 23.6 | 19.9 | 3.7 | 2FF85F44012C455DAFFA254FC01760D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4404 |  | 2014-07-25 | 2014-07-25 16:20 | 2014-07-25 16:57 | CARRIER - 567C024RCU | 60 | 3.8 | Yes | Yes | 20.2 | 19.5 | 0.7 | AD696C412DB0431E847DBD539D1CDFD5 |  | R22 | Non-TXV |  | 6.333% | 0.93667 | 12.17% | [5 empty] | Non-TXV | 6.333%
Arvin | CA | 93203-2803 |  | 2014-11-06 | 2014-11-06 13:17 | 2014-11-06 13:33 | OTHER - UNK | 85 | 5.6 | Yes | Yes | 17.6 | 20.4 | -2.8 | F4B170ABE67040B3AF8A137A8EC74A8C |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Bakersfield | CA | 93306-1375 |  | 2014-11-10 | 2014-11-10 10:57 | 2014-11-10 10:57 | BRYANT - 583ANW036060AAAF | 82 | 0 | Yes | Yes | 11 | 16.5 | -5.5 | 3DBC81A293E84A21A52F8C8CE6E74EA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4747 |  | 2014-09-10 | 2014-09-10 13:58 | 2014-09-10 13:58 | COLEMAN - F030N070A | 73 | 0 | Yes | Yes | 22.6 | 22.3 | 0.3 | 0B3C54CF7653499F9BC42BD9EFBE02CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4746 |  | 2014-11-25 | 2014-11-25 12:11 | 2014-11-25 12:11 | GOODMAN - SSX140241BB | 88 | 0 | Yes | Yes | 17.3 | 18.8 | -1.5 | 85C17C381DBB4D72AE14D9445E723A3E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0440 |  | 2014-07-18 | 2014-07-18 10:38 | 2014-07-18 10:59 | WEATHER KING - 14AJA42A01 | 237 | 8.6 | Yes | Yes | 20.6 | 19.9 | 0.7 | D0FA165D28A44944A0EED310B64C23BF |  | R22 | Non-TXV |  | 3.629% | 0.96371 | 6.974% | [5 empty] | Non-TXV | 3.629%
Arvin | CA | 93203-1217 |  | 2014-11-04 | 2014-11-04 16:33 | 2014-11-04 16:49 | AIRE-FLO - PGC036K060B | 71 | 5.3 | Yes | Yes | 19.5 | 21.3 | -1.8 | 8DA44E1380AC4792990D6E7AF4CC941B |  | R22 | Non-TXV |  | 7.465% | 0.92535 | 14.35% | [5 empty] | Non-TXV | 7.465%
Bakersfield | CA | 93307-5910 |  | 2014-09-11 | 2014-09-11 17:40 | 2014-09-11 17:42 | PAYNE - PY3GNA36060NATP | 100 | 4.7 | Yes | Yes | 22.1 | 20.8 | 1.3 | 65AC2A53B574461A8742D0CD4A4ED764 |  | R410A | TXV |  | 4.7% | 0.953 | 9.032% | [5 empty] | TXV | 4.7%
Bakersfield | CA | 93306-4754 |  | 2014-09-11 | 2014-09-11 09:50 | 2014-09-11 09:50 | YORK - F036N070C | 67 | 0 | Yes | Yes | 23 | 21.5 | 1.5 | 84D4F633BC604774AB5484B8C1FB35B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2505 |  | 2014-11-05 | 2014-11-05 18:31 | 2014-11-05 18:47 | OTHER - UNK | 85 | 5.6 | Yes | Yes | 19.5 | 22.5 | -3 | 481D0ED3D3F74112B2106C14B7F2257E |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Clovis | CA | 93611-0641 |  | 2014-07-24 | 2014-07-24 10:03 | 2014-07-24 10:27 | CARRIER - 48KLA1303008E | 68 | 15.1 | Yes | Yes | 20.3 | 17.4 | 2.9 | EFA5FDD8AD8C4031A29E7417ED4D0AD4 |  | R22 | Non-TXV |  | 22.21% | 0.77794 | 42.67% | [5 empty] | Non-TXV | 22.21%
Clovis | CA | 93611-0641 |  | 2014-07-24 | 2014-07-24 10:59 | 2014-07-24 11:19 | YORK - D1P036N05606A | 108 | 7.2 | Yes | Yes | 20.3 | 16.3 | 4 | D78922B9D8E241708B642D840084A4D8 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Concord | CA | 94519-1941 |  | 2014-08-28 | 2014-08-28 09:30 | 2014-08-28 09:55 | CARRIER - 38EH036300 | 116 | 12.2 | Yes | Yes | 25.6 | 20.3 | 5.3 | 304BEC3FEC9249479D3997AE8B4F4194 |  | R22 | Non-TXV |  | 10.52% | 0.89483 | 20.21% | [5 empty] | Non-TXV | 10.52%
Vallejo | CA | 94591-4707 |  | 2014-08-07 | 2014-08-07 10:05 | 2014-08-07 22:09 | BDP - 561CJX030000ACAA | 85 | 8.5 | Yes | Yes | 16.5 | 19.4 | -2.9 | 18C78ACFD0904C94960B64D036A0DFEE |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Bakersfield | CA | 93312-5339 |  | 2014-10-17 | 2014-10-17 23:45 | 2014-10-18 00:02 | RHEEM - UNK | 85 | 8.2 | Yes | Yes | 23.4 | 19.7 | 3.7 | 16904891316540D186F6F87CDEA98BFA |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Pittsburg | CA | 94565-5139 |  | 2014-09-22 | 2014-09-22 09:29 | 2014-09-22 09:29 | ECONAIR - CPKE18-1B | 79 | 0 | Yes | Yes | 18.1 | 17.9 | 0.2 | 23A178DD498D4518ADC1040600775C8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-9316 |  | 2014-08-07 | 2014-08-07 14:42 | 2014-08-07 16:17 | GE - | 86 | 5.5 | Yes | Yes | 22.7 | 18.6 | 4.1 | D73BB0D1B90A467D9ADB0E0574AA5D33 |  | R22 | Non-TXV |  | 6.395% | 0.93605 | 12.29% | [5 empty] | Non-TXV | 6.395%
Fresno | CA | 93727-4163 |  | 2014-07-25 | 2014-07-25 13:03 | 2014-07-25 13:23 | PAYNE - 585GJ024040 | 54 | 2.9 | Yes | Yes | 24.8 | 21 | 3.8 | 49AF4DF26E4A4827A35245FF8A862406 |  | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Clovis | CA | 93612-4807 |  | 2014-07-28 | 2014-07-28 14:01 | 2014-07-28 14:01 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 221CF3C62FDC4DC29272FF74731A294E | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4730 |  | 2014-09-10 | 2014-09-10 15:31 | 2014-09-10 15:31 | MAYTAG - PPG1GDX30K072X | 102 | 0 | Yes | Yes | 16.8 | 20.9 | -4.1 | 5B5CEE9DA4964807B2BEA646D81DE392 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7916 |  | 2014-07-25 | 2014-07-25 13:58 | 2014-07-25 13:58 | - | 85 | 0 | Yes | Yes | 17.5 | 17.6 | 0 | BBC693E3BE184721BFB06E48A90AEA9B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4163 |  | 2014-07-25 | 2014-07-25 11:56 | 2014-07-25 12:49 | CARRIER - 585GJ024040ABAF | 54 | 3.2 | Yes | Yes | 21.9 | 20.6 | 1.3 | 0E2EDD068EEF4C5FBB86D03B2178FB80 |  | R22 | Non-TXV |  | 5.926% | 0.94074 | 11.39% | [5 empty] | Non-TXV | 5.926%
Bakersfield | CA | 93312-5411 |  | 2014-10-14 | 2014-10-14 15:56 | 2014-10-14 16:14 | OTHER - EADB-031JAS | 85 | 9.1 | Yes | Yes | 16.5 | 19.4 | -2.9 | 9B3F1F6B61A646C6B4104296068632D7 |  | R22 | Non-TXV |  | 10.71% | 0.89294 | 20.57% | [5 empty] | Non-TXV | 10.71%
Bakersfield | CA | 93306-4701 |  | 2014-09-10 | 2014-09-10 11:38 | 2014-09-10 11:38 | AMERICAN STANDARD - YCY036G10AC | 129 | 0 | Yes | Yes | 24 | 22.6 | 1.4 | 2297039A8C474A8DB193166B56EA842D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2529 |  | 2014-10-04 | 2014-10-04 20:14 | 2014-10-04 20:16 | RHEEM - RRNL-B036JK08X | 92 | 4.1 | Yes | Yes | 21.7 | 22.6 | -0.9 | 42B8659408144C85920BA18A54A8CE9E |  | R410A | TXV |  | 4.457% | 0.95543 | 8.564% | [5 empty] | TXV | 4.457%
Fresno | CA | 93704-1552 |  | 2014-07-17 | 2014-07-17 10:56 | 2014-07-17 11:18 | GOODMAN - GPG13480701A | 145 | 26.4 | Yes | Yes | 21.2 | 18.7 | 2.5 | F466AB01944F4C90BC4F34A02577F41B |  | R22 | Non-TXV |  | 18.21% | 0.81793 | 34.99% | [5 empty] | Non-TXV | 18.21%
Fresno | CA | 93704-1552 |  | 2014-07-17 | 2014-07-17 11:32 | 2014-07-17 11:59 | GOODMAN - GPG13480702A | 145 | 5.5 | Yes | Yes | 18.7 | 18.8 | -0.1 | 7611689505954D1891562AA8BEAF798E |  | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Esparto | CA | 95627-2060 |  | 2014-08-08 | 2014-08-08 10:27 | 2014-08-08 10:53 | HEIL - E052838118 | 97 | 6.6 | Yes | Yes | 23.2 | 20.7 | 2.5 | 5AA56B7D0B054AB5A9BD06A898F03D90 |  | R22 | Non-TXV |  | 6.804% | 0.93196 | 13.08% | [5 empty] | Non-TXV | 6.804%
Fresno | CA | 93727-3682 |  | 2014-07-18 | 2014-07-18 11:19 | 2014-07-18 11:41 | LENNOX - 10GCS036-75-3PB | 58 | -5.5 | Yes | Yes | 23.1 | 19.5 | 3.6 | 95C74440199847918C95328C7964998D |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Fresno | CA | 93702-4418 |  | 2014-07-17 | 2014-07-17 14:39 | 2014-07-17 14:39 | OTHER - 100WR36G1NA | 120 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | AE67C94D3A794D60BA17AA5983635E11 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3138 |  | 2014-11-25 | 2014-11-25 12:52 | 2014-11-25 12:52 | PAYNE - 591ANX042-D | 89 | 0 | Yes | Yes | 18 | 18.3 | -0.3 | DA2D5316D0AE45C68F09F887068A5D54 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3012 |  | 2014-07-23 | 2014-07-23 11:59 | 2014-07-23 12:22 | RHEEM - RRNLB030JK06X | 77 | 2.6 | Yes | Yes | 21.4 | 19.6 | 1.9 | AE447B650CD2416C8CCC790EA768557F |  | R410A | Non-TXV |  | 3.377% | 0.96623 | 6.489% | [5 empty] | Non-TXV | 3.377%
Fresno | CA | 93727-7139 |  | 2014-07-25 | 2014-07-25 15:03 | 2014-07-25 15:29 | OTHER - PGAD36D1K5 | 102 | 18.7 | Yes | Yes | 23.7 | 23 | 0.7 | 7274DC2382BA4862B7B90D639408829E |  | R22 | Non-TXV |  | 18.33% | 0.81667 | 35.23% | [5 empty] | Non-TXV | 18.33%
Woodland | CA | 95695-3942 |  | 2014-09-29 | 2014-09-29 11:59 | 2014-09-29 12:18 | LENNOX - AC13-048-230-001 | 120 | 5.3 | Yes | Yes | 20.6 | 20.4 | 0.2 | 0ADB32AEFEF14F1AA07B154D65DA54D8 |  | R22 | Non-TXV |  | 4.417% | 0.95583 | 8.488% | [5 empty] | Non-TXV | 4.417%
Bakersfield | CA | 93306-2659 |  | 2014-11-10 | 2014-11-10 13:36 | 2014-11-10 13:36 | RHEEM - UNK | 137 | 0 | Yes | Yes | 19 | 18.3 | 0.7 | 062E593BDB514141BD1F58E2D7DE5BDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5643 |  | 2014-07-29 | 2014-07-29 09:46 | 2014-07-29 10:15 | CARRIER - 585EJ036075 | 82 | 3.8 | Yes | Yes | 25.3 | 22.1 | 3.2 | 12750A8A5FD848F08F2F04F818F5A892 |  | R22 | Non-TXV |  | 4.634% | 0.95366 | 8.906% | [5 empty] | Non-TXV | 4.634%
Suisun City | CA | 94585-1923 |  | 2014-08-05 | 2014-08-05 13:52 | 2014-08-05 14:17 | DAY & NIGHT - | 85 | 8.9 | Yes | Yes | 16.3 | 18.5 | -2.2 | D0CD96F81050419495E13B009EDAD781 |  | R22 | Non-TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | Non-TXV | 10.47%
Clovis | CA | 93612-4531 |  | 2014-07-24 | 2014-07-24 12:09 | 2014-07-24 12:31 | GOODMAN - G8Y130361BA | 89 | 5.2 | Yes | Yes | 21 | 19.1 | 1.9 | B7EBD67AD5B8448E887379088AAA04A4 |  | R410A | Non-TXV |  | 5.843% | 0.94157 | 11.23% | [5 empty] | Non-TXV | 5.843%
Clovis | CA | 93612-4531 |  | 2014-07-24 | 2014-07-24 12:35 | 2014-07-24 13:00 | GOODMAN - CK4918 | 97 | 3.3 | Yes | Yes | 21.5 | 18.8 | 2.7 | 4A79E311D45E4925BE7B2EFF415F72DE |  | R22 | Non-TXV |  | 3.402% | 0.96598 | 6.538% | [5 empty] | Non-TXV | 3.402%
Bakersfield | CA | 93306-4711 |  | 2014-11-10 | 2014-11-10 11:48 | 2014-11-10 11:48 | CARRIER - 48SX048080331AA | 88 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | F19F52230FA04017B006406B785627DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3024 |  | 2014-07-23 | 2014-07-23 12:48 | 2014-07-23 13:12 | YORK - D1NP030N05606A | 69 | 4.1 | Yes | Yes | 24.4 | 19.3 | 5.1 | 3F691567B1B44BE8AB8807F8CBE5CA2C |  | R22 | Non-TXV |  | 5.942% | 0.94058 | 11.42% | [5 empty] | Non-TXV | 5.942%
Clovis | CA | 93612-5085 |  | 2014-07-28 | 2014-07-28 11:30 | 2014-07-28 11:30 | DAY & NIGHT - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 3B40B37F240A4841925D26C2122765CA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2416 |  | 2014-07-23 | 2014-07-23 11:04 | 2014-07-23 11:04 | YORK - DCYZF036N070C | 64 | 0 | Yes | Yes | 24.6 | 19.4 | 5.2 | 34C5B7C9B36F4454A7DE3F352B74E07B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Lamont | CA | 93241-2367 |  | 2014-11-01 | 2014-11-01 09:19 | 2014-11-01 09:36 | DAY & NIGHT - UNK | 85 | 7.5 | Yes | Yes | 17.7 | 20.6 | -2.8 | 6DC6ED76B83749DEA761C3418BC6ED74 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Woodland | CA | 95776-6749 |  | 2014-08-12 | 2014-08-12 13:01 | 2014-08-12 13:31 | PAYNE - PA1A0938 | 57 | 5 | Yes | Yes | 20.1 | 20.4 | -0.3 | 5CBE526720DE4254BFE69EFD45637151 |  | R22 | Non-TXV |  | 8.772% | 0.91228 | 16.86% | [5 empty] | Non-TXV | 8.772%
Fresno | CA | 93722-9134 |  | 2014-07-23 | 2014-07-23 13:50 | 2014-07-23 14:20 | CARRIER - 585EJ036075 | 82 | 14.6 | Yes | Yes | 25.1 | 20.6 | 4.5 | FFD4A5FAEC284823A021AF00D6477A9D |  | R22 | Non-TXV |  | 17.8% | 0.82195 | 34.22% | [5 empty] | Non-TXV | 17.8%
Vallejo | CA | 94591-8628 |  | 2014-08-06 | 2014-08-06 12:39 | 2014-08-06 22:12 | TRANE - 2TWR1018A1000AB | 69 | 2.7 | Yes | Yes | 16.6 | 17 | -0.4 | D329CCBD2D2E4FEC9636C54C930C7B94 |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Fairfield | CA | 94533-4270 |  | 2014-08-27 | 2014-08-27 11:07 | 2014-08-27 11:07 | - | 85 | 0 | Yes | Yes | 15.9 | 18.2 | -2.3 | 51F99925798F4BF3A925859792FD0DCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2625 |  | 2014-07-17 | 2014-07-17 12:30 | 2014-07-17 12:30 | BDP - 588ANW024060ADAD | 44 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 2E715D69902B44AAB817571015F14BF2 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2625 |  | 2014-07-17 | 2014-07-17 12:33 | 2014-07-17 13:00 | OTHER - UNK | 80 | 2.4 | Yes | Yes | 20.3 | 21 | -0.6 | 0EF6CEC98F1248BFB2C2AE1FB47527AD |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93311-9530 |  | 2014-11-13 | 2014-11-13 11:32 | 2014-11-13 11:32 | LENNOX - 13ACD03623002 | 111 | 0 | Yes | Yes | 17.7 | 18.2 | -0.5 | C9391B6E650B41199534C657E3C18EB8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9530 |  | 2014-11-13 | 2014-11-13 11:46 | 2014-11-13 11:46 | LENNOX - 13ACD04223002 | 111 | 0 | Yes | Yes | 15 | 18.7 | -3.7 | 42A669D7643746E295EB811D93D0CC2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2137 |  | 2014-07-28 | 2014-07-28 15:06 | 2014-07-28 15:54 | CARRIER - 38TH048320 | 120 | 5.3 | Yes | Yes | 20.8 | 21.5 | -0.7 | A2F72D7D1FEF4A668E2F8041A85F54AA |  | R22 | Non-TXV |  | 4.417% | 0.95583 | 8.488% | [5 empty] | Non-TXV | 4.417%
Antioch | CA | 94509-2052 |  | 2014-10-10 | 2014-10-10 10:11 | 2014-10-10 10:11 | GUARDIAN - GCGD48S43A | 73 | 0 | Yes | Yes | 20.2 | 20.2 | 0.1 | 87DF2055B5F94749B2F38251F6A1FB81 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3808 |  | 2014-09-09 | 2014-09-09 12:56 | 2014-09-09 12:56 | HEIL - PGF330060K01A1 | 152 | 0 | Yes | Yes | 13.8 | 19.9 | -6.1 | 7C91B9F80C2441D9ACC3E94F1626B0E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9486 |  | 2014-10-28 | 2014-10-28 20:44 | 2014-10-28 21:01 | OTHER - AC048X1222A | 119 | -11.2 | Yes | Yes | 17.4 | 19 | -1.6 | A3EADC940EE949578D280C69B8C4FE22 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93312-4402 |  | 2014-10-13 | 2014-10-13 15:03 | 2014-10-13 15:19 | OTHER - UNK | 85 | 6.6 | Yes | Yes | 18.6 | 21.5 | -2.9 | 3B647E48B19B42B19842305D501935AC |  | R22 | Non-TXV |  | 7.765% | 0.92235 | 14.92% | [5 empty] | Non-TXV | 7.765%
Bakersfield | CA | 93306-4000 |  | 2014-09-08 | 2014-09-08 16:03 | 2014-09-08 18:29 | OTHER - UNK | 98 | 7.4 | Yes | Yes | 20.4 | 20.1 | 0.3 | F935789FE5B647E38CCA9D461B40BB5C |  | R22 | Non-TXV |  | 7.551% | 0.92449 | 14.51% | [5 empty] | Non-TXV | 7.551%
Bakersfield | CA | 93312-4496 |  | 2014-10-11 | 2014-10-11 16:06 | 2014-10-11 16:22 | OTHER - EADB-037JAS | 85 | 8.2 | Yes | Yes | 25.8 | 22.1 | 3.8 | E22F1C084EAB452AA77E179725FC91B8 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Bakersfield | CA | 93313-2213 |  | 2014-10-17 | 2014-10-17 11:40 | 2014-10-17 11:40 | YORK - D1NP048N06506A | 132 | 0 | Yes | Yes | 18.1 | 19.1 | -1 | 34FB8DF139A14BCF850F97EB1C1D81D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4142 |  | 2014-10-11 | 2014-10-11 16:12 | 2014-10-11 16:28 | CARRIER - UNK | 85 | 4.6 | Yes | Yes | 18.3 | 19.4 | -1.1 | 9811EC8568C64B29A6342FD1ED555994 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Mc Farland | CA | 93250-0000 |  | 2014-09-02 | 2014-09-02 18:25 | 2014-09-02 18:25 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 23.4 | 20.4 | 3 | 964F204EFF584DA695F75DF768EAFEDD |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4126 |  | 2014-08-07 | 2014-08-07 10:53 | 2014-08-07 11:22 | BRYANT - 563CN036-D | 101 | 4.8 | Yes | Yes | 17.6 | 20.4 | -2.8 | B6B06DE51EFE407F95A3D0632614C5D9 |  | R22 | Non-TXV |  | 4.752% | 0.95248 | 9.133% | [5 empty] | Non-TXV | 4.752%
Antioch | CA | 94509-8981 |  | 2014-10-13 | 2014-10-13 12:15 | 2014-10-13 12:15 | GOODMAN - CKJ68-C | 149 | 0 | Yes | Yes | 23.8 | 20.7 | 3.1 | E43FC73BD6794CA6AE114BF193B2689B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2266 |  | 2014-10-15 | 2014-10-15 14:42 | 2014-10-15 14:42 | OTHER - PGF030K60E | 51 | 0 | Yes | Yes | 22.8 | 20.1 | 2.8 | 5D0D428136E64D43A7D8B3952D2EE826 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-0321 |  | 2014-07-21 | 2014-07-21 13:50 | 2014-07-21 14:12 | OTHER - CAG236AKA4 | 113 | 4.6 | Yes | Yes | 25 | 19.7 | 5.3 | 327E9558506648858B7C84D85399D153 |  | R22 | Non-TXV |  | 4.071% | 0.95929 | 7.823% | [5 empty] | Non-TXV | 4.071%
Bakersfield | CA | 93306-6846 |  | 2014-10-12 | 2014-10-12 15:37 | 2014-10-12 15:40 | OTHER - AA5JH0E02001V5610163 | 127 | 5.5 | Yes | Yes | 22.7 | 22 | 0.7 | 4322382AE932404B824A525290D704A1 |  | R22 | Non-TXV |  | 4.331% | 0.95669 | 8.323% | [5 empty] | Non-TXV | 4.331%
Bakersfield | CA | 93307-3952 |  | 2014-10-19 | 2014-10-19 18:34 | 2014-10-19 18:38 | OTHER - DBYP-F036N070A | 108 | 7 | Yes | Yes | 22.9 | 19.5 | 3.4 | F718858EA6AA42B2BC627551E103C4CD |  | R22 | Non-TXV |  | 6.481% | 0.93519 | 12.46% | [5 empty] | Non-TXV | 6.481%
Clovis | CA | 93612-3537 |  | 2014-07-21 | 2014-07-21 15:06 | 2014-07-21 15:43 | DUCANE - AC10B24 | 60 | -4.2 | Yes | Yes | 20.4 | 19 | 1.4 | 3701FEB84989424CA6BFD73D2FDBD2C4 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Suisun City | CA | 94585-2220 |  | 2014-08-12 | 2014-08-12 09:48 | 2014-08-12 20:34 | CARRIER - 24ACB448A0030010 | 176 | 6 | Yes | Yes | 15.6 | 17 | -1.4 | FD59DB0837E64329885AFE1B7732929E |  | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Bakersfield | CA | 93306-6840 |  | 2014-09-18 | 2014-09-18 14:42 | 2014-09-18 14:42 | OTHER - BRCQ036B | 67 | 0 | Yes | Yes | 23.2 | 19.9 | 3.3 | 935E0DB7BC9948DD80BD9824C05F4F90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2733 |  | 2014-10-19 | 2014-10-19 18:00 | 2014-10-19 18:03 | OTHER - W1G3921236 | 64 | -6 | Yes | Yes | 22.8 | 19.8 | 3 | 79FFFD90FA3A4EE0AFB41E9DB7C3CBFC |  | R410A | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93301-6101 |  | 2014-10-15 | 2014-10-15 10:51 | 2014-10-15 10:51 | RHEEM - UNK | 103 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 6C7F85F300B54ADF8C695C1DAC568B64 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4070 |  | 2014-07-25 | 2014-07-25 13:48 | 2014-07-25 14:16 | PAYNE - 588ANW048080ADAG | 102 | 3.3 | Yes | Yes | 26.4 | 21.3 | 5.1 | 9D70426E79F2400082F469D641C8E4C0 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Fresno | CA | 93711-1384 |  | 2014-07-22 | 2014-07-22 12:06 | 2014-07-22 12:25 | RHEEM - UNK | 58 | -3.4 | Yes | Yes | 22.6 | 19.9 | 2.7 | 49A655450E0D42D7B677B41D55AA39C5 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Clovis | CA | 93611-4512 |  | 2014-07-21 | 2014-07-21 09:32 | 2014-07-21 09:55 | YORK - D2NP036N05606A | 108 | 4.2 | Yes | Yes | 22.4 | 18.7 | 3.7 | 9D15C0C53F46402DA28659CF9E96168A |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Bakersfield | CA | 93307-3744 |  | 2014-09-14 | 2014-09-14 23:25 | 2014-09-14 23:27 | GOODMAN - PGME36G0907 | 102 | 6 | Yes | Yes | 24.8 | 22.3 | 2.5 | BE314DD88AB143A3804169045EDBEFD5 |  | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Fairfield | CA | 94533-7700 |  | 2014-07-25 | 2014-07-25 09:11 | 2014-07-25 15:47 | CARRIER - 568EJX048000ACAA | 85 | 4 | Yes | Yes | 15.1 | 18.1 | -3 | 2BFAFD9726C54BFA8285BCEB5E92EE4B |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
San Jose | CA | 95124-1917 |  | 2014-07-18 | 2014-07-18 09:37 | 2014-07-18 10:11 | HEIL - CK3048CKA | 145 | -13.6 | Yes | Yes | 24.4 | 19.7 | 4.8 | 1F90BD8764AD4178B29C03CEC771A4A9 |  | R22 | Non-TXV |  | -9.379% | 1.0938 | 2.627% |  |  |  |  | Non-TXV |  |  | -9.379%
San Jose | CA | 95127-2457 |  | 2014-07-18 | 2014-07-18 10:17 | 2014-07-18 10:43 | DUCANE - 2AC13L48 | 201 | -11.8 | Yes | Yes | 24.1 | 20.4 | 3.7 | 160884CCF46E4B599DF42B215A460CAE |  | R22 | Non-TXV |  | -5.871% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.871%
Fresno | CA | 93728-3324 |  | 2014-07-28 | 2014-07-28 10:36 | 2014-07-28 11:07 | CARRIER - 48DL004 | 81 | 14.5 | Yes | Yes | 21.8 | 20.9 | 0.9 | 7CB74E73810D43849C5102D20E72F7AA |  | R22 | Non-TXV |  | 17.9% | 0.82099 | 34.4% | [5 empty] | Non-TXV | 17.9%
Clovis | CA | 93612-1223 |  | 2014-07-28 | 2014-07-28 12:52 | 2014-07-28 12:52 | YORK - D3N2036N05606NXA | 64 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D23A441BBE7349C2A90424C9B8C01165 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6218 |  | 2014-09-19 | 2014-09-19 12:27 | 2014-09-19 12:27 | OTHER - CA5530VKD2 | 74 | 0 | Yes | Yes | 20.5 | 21.7 | -1.2 | 59A42E35F8F746DAB44AE105FBBDC7DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1260 |  | 2014-10-28 | 2014-10-28 10:15 | 2014-10-28 10:15 | OTHER - 113ANA030E | 74 | 0 | Yes | Yes | 18.2 | 19.3 | -1.1 | 5BD6F2D187B240E0A3B712522399E05D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2118 |  | 2014-07-22 | 2014-07-22 17:54 | 2014-07-22 17:56 | RHEEM - N/A | 85 | -7 | Yes | Yes | 21.5 | 19.5 | 2 | FA4EF1A72CAB474CA849DABF6DD2AEEF |  | R22 | Non-TXV |  | -8.235% | 1.0824 | 2.306% |  |  |  |  | Non-TXV |  |  | -8.235%
Fresno | CA | 93704-5730 |  | 2014-07-17 | 2014-07-17 13:46 | 2014-07-17 13:46 | BRYANT - 574DNWA36060NA-- | 102 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 17AA3C722B204C3ABCA8690995DBDA7F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2246 |  | 2014-11-04 | 2014-11-04 14:20 | 2014-11-04 14:20 | DAY & NIGHT - UNK | 105 | 0 | Yes | Yes | 13.6 | 18.7 | -5.1 | 4AC86640B6394D36B79F010082CED6C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7745 |  | 2014-07-18 | 2014-07-18 16:23 | 2014-07-18 17:04 | LENNOX - 12ACB485P | 171 | 7.2 | Yes | Yes | 19.5 | 15.4 | 4.1 | C89397B0FB3E456EAF938853FD0B6ACD |  | R22 | Non-TXV |  | 4.211% | 0.95789 | 8.092% | [5 empty] | Non-TXV | 4.211%
Lamont | CA | 93241-2701 |  | 2014-11-01 | 2014-11-01 09:23 | 2014-11-01 09:40 | GOODMAN - PGJ030050-1 | 85 | -8 | Yes | Yes | 16.4 | 19.3 | -2.9 | 373FD309EED6415DA2CADC170FE048E0 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Clovis | CA | 93611-5343 |  | 2014-07-21 | 2014-07-21 11:52 | 2014-07-21 12:13 | OTHER - 567G3036 | 80 | -5.6 | Yes | Yes | 26.4 | 20.4 | 6 | 8BA4DD87F3C14B1F865528E1970E97F4 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Mc Farland | CA | 93250-1827 |  | 2014-10-27 | 2014-10-27 13:20 | 2014-10-27 13:20 | TEMPSTAR - PGF030K060A | 52 | 0 | Yes | Yes | 16.2 | 18 | -1.8 | C4439239B0FD482CBE9CA437187843C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1327 |  | 2014-08-17 | 2014-08-17 18:04 | 2014-08-17 18:08 | OTHER - 1D036M1A | 112 | 28.7 | Yes | Yes | 20.5 | 23.2 | -2.7 | 480CE07A8C9B4E84B9DD480AE1620513 |  | R22 | Non-TXV |  | 25.62% | 0.74375 | 49.25% | [5 empty] | Non-TXV | 25.62%
Wasco | CA | 93280-1327 |  | 2014-08-17 | 2014-08-17 18:11 | 2014-08-17 18:14 | OTHER - | 85 | -5 | Yes | Yes | 20.9 | 23.1 | -2.2 | A5631E27332E44308D15C4A383F35CB1 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Bakersfield | CA | 93309-2872 |  | 2014-09-13 | 2014-09-13 11:46 | 2014-09-13 11:46 | PAYNE - 591ANX030000ABAA | 65 | 0 | Yes | Yes | 3.2 | 19.7 | -16.5 | 95E81C5B7DEB4C01AD7DDFC7B72F74EB | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9335 |  | 2014-11-13 | 2014-11-13 13:50 | 2014-11-13 14:34 | CARRIER - | 127 | 4.3 | Yes | Yes | 18 | 20.4 | -2.4 | DEC306AF9A7249C2A149C98414F995F1 |  | R22 | Non-TXV |  | 3.386% | 0.96614 | 6.507% | [5 empty] | Non-TXV | 3.386%
Bakersfield | CA | 93306-4374 |  | 2014-09-10 | 2014-09-10 14:45 | 2014-09-10 14:45 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 24.7 | 22.3 | 2.4 | 2842A76621E84EE680FA81856E9382F9 |  | R410A | TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1671 |  | 2014-11-18 | 2014-11-18 12:16 | 2014-11-18 12:16 | WEATHER KING - 13AJA30A01 | 98 | 0 | Yes | Yes | 21.7 | 19.9 | 1.8 | FD21C6B6E555436293C615B89271B340 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1671 |  | 2014-09-02 | 2014-09-02 12:42 | 2014-09-02 18:53 | OTHER - 13AJA30A01 | 98 | 0 | Yes | Yes | 19.7 | 19.6 | 0.1 | 829C56C2A00F42E1A196A436D4E7B8CB |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5882 |  | 2014-07-29 | 2014-07-29 14:34 | 2014-07-29 15:00 | CARRIER - 48NLX036302BE | 73 | 3.6 | Yes | Yes | 23.6 | 21.2 | 2.4 | 9944113EC76745F1BFD6ACCC92874AFE |  | R22 | Non-TXV |  | 4.932% | 0.95068 | 9.477% | [5 empty] | Non-TXV | 4.932%
Bakersfield | CA | 93306-1553 |  | 2014-11-10 | 2014-11-10 10:21 | 2014-11-10 10:21 | DAY & NIGHT - 568EJX036000AGAA | 131 | 0 | Yes | Yes | 19.5 | 19.7 | -0.2 | 36572C5998F34C02B3D02711A1A1FE08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4342 |  | 2014-09-08 | 2014-09-08 10:38 | 2014-09-08 10:38 | YORK - F048N080A | 132 | 0 | Yes | Yes | 25.9 | 21.4 | 4.5 | E5F3F23EEC8445CFAD829F345D329B06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3066 |  | 2014-09-11 | 2014-09-11 15:03 | 2014-09-11 15:03 | DAY & NIGHT - 591ANX048000A | 117 | 0 | Yes | Yes | 16.9 | 19.8 | -2.9 | 2DF489740A9F465F94C6DEBC11A8EF77 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2936 |  | 2014-10-13 | 2014-10-13 14:27 | 2014-10-13 14:27 | GOODMAN - GSC130481BA | 102 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | AE13CAA59AED472AAD1966F128B59007 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4610 |  | 2014-11-19 | 2014-11-19 15:52 | 2014-11-19 15:52 | OTHER - PGC036K060D | 71 | 0 | Yes | Yes | 14.6 | 20.1 | -5.5 | 72AB246E1C734D8598336627F9C8AB83 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-3006 |  | 2014-11-05 | 2014-11-05 11:52 | 2014-11-05 11:52 | OTHER - UNK | 147 | 0 | Yes | Yes | 24.5 | 19.1 | 5.4 | 2B8BECC18D32454888242BCFC9DE88A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1116 |  | 2014-10-24 | 2014-10-24 11:31 | 2014-10-24 11:31 | LENNOX - GCS20R411751P | 70 | 0 | Yes | Yes | 18.4 | 18.2 | 0.2 | 710B0AA163B84A798ECDFEC76F338132 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-8359 |  | 2014-10-11 | 2014-10-11 10:30 | 2014-10-11 10:30 | WEATHER KING - 13AJA42A01 | 121 | 0 | Yes | Yes | 25.6 | 20.3 | 5.3 | 815AE368172C439DA5B2EFD4FC0519AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2630 |  | 2014-07-17 | 2014-07-17 09:20 | 2014-07-17 09:40 | NORDYNE - JS4BD048KA | 127 | 14.8 | Yes | Yes | 24.2 | 21 | 3.2 | F24DF5B56D6A4A88A74C0328C83F14D6 |  | R410A | Non-TXV |  | 11.65% | 0.88346 | 22.4% | [5 empty] | Non-TXV | 11.65%
Fresno | CA | 93722-7138 |  | 2014-07-18 | 2014-07-18 15:17 | 2014-07-18 15:17 | LENNOX - HS253111P | 129 | 0 | Yes | Yes | 20.3 | 18.5 | 1.8 | D0DE3499989148F08A17CC378211DC95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Campbell | CA | 95008-5914 |  | 2014-07-21 | 2014-07-21 11:58 | 2014-07-21 12:36 | TRANE - 2TTR2042A1000 | 95 | 7.9 | Yes | Yes | 20.2 | 19.9 | 0.3 | A61C29D2FF2B41B990CDC75C2059E8D3 |  | R22 | Non-TXV |  | 8.316% | 0.91684 | 15.98% | [5 empty] | Non-TXV | 8.316%
San Jose | CA | 95119-1722 |  | 2014-07-18 | 2014-07-18 14:35 | 2014-07-18 15:01 | LENNOX - HS295112P | 99 | 5.2 | Yes | Yes | 21.4 | 20.3 | 1.1 | 00669DB782B84C14B35AD8F18840DE55 |  | R22 | Non-TXV |  | 5.253% | 0.94747 | 10.09% | [5 empty] | Non-TXV | 5.253%
Bakersfield | CA | 93306-6021 |  | 2014-09-11 | 2014-09-11 15:07 | 2014-09-11 15:07 | FRIGIDAIRE - R4GD036K072C | 100 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 7730FE8FF98542D980670306F018FD04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4154 |  | 2014-10-12 | 2014-10-12 16:08 | 2014-10-12 16:12 | DAY & NIGHT - 589ANW042060ADBF | 89 | 20.8 | Yes | Yes | 23.8 | 22 | 1.8 | D70502CBF9A843398785207E1FFAACBB |  | R22 | Non-TXV |  | 23.37% | 0.76629 | 44.91% | [5 empty] | Non-TXV | 23.37%
Fresno | CA | 93710-5639 |  | 2014-07-21 | 2014-07-21 12:25 | 2014-07-21 12:46 | PAYNE - UNK | 52 | 7 | Yes | Yes | 17.9 | 19.8 | -1.9 | 65F4E9F6C4314613AABDC753FB4E8173 |  | R22 | Non-TXV |  | 13.46% | 0.86538 | 25.87% | [5 empty] | Non-TXV | 13.46%
Clovis | CA | 93611-5111 |  | 2014-07-21 | 2014-07-21 10:26 | 2014-07-21 10:53 | OTHER - UNK | 80 | -6.6 | Yes | Yes | 19.8 | 18.6 | 1.2 | 7BBBD8B1431B4F39BE343CF1855FFF80 |  | R22 | Non-TXV |  | -8.25% | 1.0825 | 2.31% |  |  |  |  | Non-TXV |  |  | -8.25%
Vacaville | CA | 95687-3416 |  | 2014-07-16 | 2014-07-16 13:12 | 2014-07-16 17:17 | MAYTAG - DS3BD-024K | 102 | 0 | Yes | Yes | 15.4 | 17.4 | -2 | 42DC4D4DC8A6463498685F34059BF1EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3219 |  | 2014-09-16 | 2014-09-16 12:04 | 2014-09-16 12:04 | DAY & NIGHT - PGD436060K001C1 | 149 | 0 | Yes | Yes | 22.2 | 19.1 | 3.1 | AE9B14D014FF483D8FF35588B3581AB7 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1543 |  | 2014-07-22 | 2014-07-22 16:04 | 2014-07-22 16:55 | CARRIER - 48ENA3004030 | 99 | -3.8 | Yes | Yes | 21.9 | 19.3 | 2.6 | AAC6F332B4124129B700FCA721D12AFF |  | R410A | Non-TXV |  | -3.838% | 1.0384 | 1.075% |  |  |  |  | Non-TXV |  |  | -3.838%
Fresno | CA | 93728-1035 |  | 2014-07-28 | 2014-07-28 12:19 | 2014-07-28 12:45 | CARRIER - 38GS048310 | 89 | 19.5 | Yes | Yes | 24 | 22.5 | 1.5 | 8A1679E82DE94D5A98B62F2692D25007 |  | R22 | Non-TXV |  | 21.91% | 0.7809 | 42.11% | [5 empty] | Non-TXV | 21.91%
Fresno | CA | 93728-1035 |  | 2014-07-22 | 2014-07-22 15:02 | 2014-07-22 15:34 | RUUD - 048JBS | 101 | 7.5 | Yes | Yes | 23 | 17.6 | 5.4 | 34D1FACCECDD41E5B8E95C5FBD6DB2FC |  | R22 | Non-TXV |  | 7.426% | 0.92574 | 14.27% | [5 empty] | Non-TXV | 7.426%
Clovis | CA | 93611-5130 |  | 2014-07-28 | 2014-07-28 14:59 | 2014-07-28 15:30 | YORK - D2NP036N05606A | 108 | 8 | Yes | Yes | 25.2 | 19.9 | 5.3 | A26E08AACE3941A283BFA1A64912A5AF |  | R22 | Non-TXV |  | 7.407% | 0.92593 | 14.24% | [5 empty] | Non-TXV | 7.407%
Mc Farland | CA | 93250-9537 |  | 2014-09-03 | 2014-09-03 12:28 | 2014-09-03 12:28 | DAY & NIGHT - PGF336060KOO | 146 | 0 | Yes | Yes | 16.7 | 19.3 | -2.6 | FC07C19CAC8340EAABF9BA036CFBDF44 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-9705 |  | 2014-07-18 | 2014-07-18 15:54 | 2014-07-18 16:19 | CARRIER - UNK | 80 | 13.4 | Yes | Yes | 18.2 | 19.1 | -0.9 | BE326CA48CF445FB9F10088D5C34A1FC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 16.75% | 0.8325 | 32.19% | [5 empty] | Non-TXV | 16.75%
Fresno | CA | 93722-6707 |  | 2014-07-18 | 2014-07-18 14:10 | 2014-07-18 14:38 | CARRIER - 585GJ030040 | 58 | 3.5 | Yes | Yes | 17.2 | 19.9 | -2.7 | FAA040667D4B44319603221DF60F29A8 |  | R22 | Non-TXV |  | 6.034% | 0.93966 | 11.6% | [5 empty] | Non-TXV | 6.034%
Bakersfield | CA | 93307-3849 |  | 2014-09-09 | 2014-09-09 11:26 | 2014-09-09 11:45 | YORK - D2NP030N05606A | 73 | 15.1 | Yes | Yes | 24 | 20.3 | 3.7 | 4AA35EF53CBC454898DE3AF239243D38 |  | R22 | Non-TXV |  | 20.68% | 0.79315 | 39.75% | [5 empty] | Non-TXV | 20.68%
Woodland | CA | 95776-4238 |  | 2014-08-28 | 2014-08-28 11:15 | 2014-08-28 11:15 | CARRIER - 38TXA036340 | 104 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 4489ACEE85D743CC91FFE6EE02E7F939 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2209 |  | 2014-07-25 | 2014-07-25 14:18 | 2014-07-25 19:22 | CARRIER - 195E17369 | 83 | 4.2 | Yes | Yes | 23.3 | 20.4 | 2.9 | 3A365F7B78DB45789BB9411C498DD199 |  | R22 | Non-TXV |  | 5.06% | 0.9494 | 9.725% | [5 empty] | Non-TXV | 5.06%
Fresno | CA | 93706-3963 |  | 2014-07-23 | 2014-07-23 10:14 | 2014-07-23 10:32 | OTHER - N2A330AKC100 | 68 | 10.2 | Yes | Yes | 19.5 | 19.2 | 0.3 | 64B5B97DFAE54E18A503C1840DB77E93 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Bakersfield | CA | 93307-3738 |  | 2014-09-14 | 2014-09-14 23:38 | 2014-09-14 23:41 | OTHER - N2A342AKA100 | 114 | 9.3 | Yes | Yes | 22.5 | 20.9 | 1.6 | C48F21EE4D9748F1ADDE43E8C57A16C8 |  | R22 | Non-TXV |  | 8.158% | 0.91842 | 15.68% | [5 empty] | Non-TXV | 8.158%
Bakersfield | CA | 93307-3738 |  | 2014-09-14 | 2014-09-14 23:43 | 2014-09-14 23:45 | OTHER - N2A342AKA100 | 114 | 7.8 | Yes | Yes | 22.9 | 20.9 | 2 | 452395FD6219474F8AF1B3334C9A54C3 |  | R22 | TXV |  | 6.842% | 0.93158 | 13.15% | [5 empty] | TXV | 6.842%
Fairfield | CA | 94533-4250 |  | 2014-07-30 | 2014-07-30 08:34 | 2014-07-30 21:14 | GE - | 85 | 3.2 | Yes | Yes | 16.8 | 19.7 | -2.9 | 1A0B8F493A384DD788CDAF6804AA2669 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Bakersfield | CA | 93313-5242 |  | 2014-10-17 | 2014-10-17 14:47 | 2014-10-17 14:47 | BRYANT - CNVRT4221ACAAAAA | 127 | 0 | Yes | Yes | 19.3 | 19.9 | -0.6 | 550EAADC7C9C4AA389157578BCB5339C |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7439 |  | 2014-07-28 | 2014-07-28 10:43 | 2014-07-28 10:43 | CARRIER - 38EH036300 | 85 | 0 | Yes | Yes | 16.2 | 18.3 | -2.1 | 02330083B25F488196B52F99345DFB78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-0000 |  | 2014-10-27 | 2014-10-27 12:04 | 2014-10-27 12:04 | NORDYNE - FS5BD048KA | 126 | 0 | Yes | Yes | 18.5 | 21.2 | -2.7 | 623B6F68804141A48198522ACE22C975 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3477 |  | 2014-10-21 | 2014-10-21 13:59 | 2014-10-21 13:59 | RUUD - URGG07E49JKR | 136 | 0 | Yes | Yes | 23.2 | 20.3 | 2.9 | 4F4D15E7CA944CBD85AEE2D5EF356E6E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4916 |  | 2014-07-21 | 2014-07-21 11:35 | 2014-07-21 12:06 | GOODMAN - GPG10360701A | 75 | -4.4 | Yes | Yes | 25.9 | 21.2 | 4.7 | 386316E9AFAE4098A999E004F60C110E |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Bakersfield | CA | 93313-3719 |  | 2014-10-07 | 2014-10-07 17:35 | 2014-10-07 17:53 | ICP - PGC036K060E | 85 | 8.4 | Yes | Yes | 17.7 | 20.7 | -3 | 83FFC175E4774E11AB13680A4046A600 |  | R22 | Non-TXV |  | 9.882% | 0.90118 | 18.99% | [5 empty] | Non-TXV | 9.882%
Bakersfield | CA | 93309-2946 |  | 2014-09-13 | 2014-09-13 09:03 | 2014-09-13 09:03 | OTHER - PGAD42D1K3 | 180 | 0 | Yes | Yes | 16.7 | 18.8 | -2.1 | 00FAC9E2F0CE4AB1B5D8E61F03D3088A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2089 |  | 2014-08-08 | 2014-08-08 13:17 | 2014-08-08 13:38 | PAYNE - 588ANW024060ACAD | 45 | 4.2 | Yes | Yes | 15.4 | 18.6 | -3.2 | 281DEBF48A374D5286EA3B404DAE8E37 | Add refrigerant: 1.4 oz | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Mc Farland | CA | 93250-1646 |  | 2014-08-29 | 2014-08-29 16:46 | 2014-08-29 17:34 | GOODMAN - PGB0601001 | 82 | -4.8 | Yes | Yes | 25.7 | 19.7 | 6 | B1A8BC62457843ECB95B5843A0A56330 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Concord | CA | 94519-1148 |  | 2014-08-28 | 2014-08-28 13:02 | 2014-08-28 13:02 | PAYNE - 561CJ036-C | 78 | 0 | Yes | Yes | 24.5 | 20.4 | 4.1 | 835CB0CB193540369AC029BC3969AF33 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2809 |  | 2014-09-05 | 2014-09-05 20:00 | 2014-09-05 20:00 | YORK - D1NH042N06506A | 90 | 0 | Yes | Yes | 23.1 | 22.1 | 1 | 3C359840F81549E6AFA50C02A260C29A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-6720 |  | 2014-10-13 | 2014-10-13 12:42 | 2014-10-13 13:00 | PAYNE - PA13NR024 | 64 | 4.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | 69F88C58112E42A99EF69FF4FD47CB37 |  | R22 | TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | TXV | 7.187%
Bakersfield | CA | 93309-2946 |  | 2014-09-13 | 2014-09-13 09:48 | 2014-09-13 09:48 | OTHER - UNK | 34 | 0 | Yes | Yes | 16.6 | 18.2 | -1.6 | 2CFB8667181D4DCDA74E89C4172D2CA7 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2147 |  | 2014-07-17 | 2014-07-17 10:32 | 2014-07-17 10:56 | YORK - DCYZF024N045A | 58 | 6 | Yes | Yes | 20.3 | 18.8 | 1.5 | 632629BFF28F4A2ABAF0E94A2494F974 |  | R410A | Non-TXV |  | 10.34% | 0.89655 | 19.88% | [5 empty] | Non-TXV | 10.34%
Bakersfield | CA | 93312-3134 |  | 2014-09-19 | 2014-09-19 14:51 | 2014-09-19 14:51 | GOODMAN - PGJ036075-1REV A | 81 | 0 | Yes | Yes | 13.3 | 18.9 | -5.6 | 35DBF4E358324AAB886AAC6D03745145 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2373 |  | 2014-09-19 | 2014-09-19 13:15 | 2014-09-19 13:48 | BRYANT - 583ANW048090AAAF | 85 | 12.2 | Yes | Yes | 15.9 | 17.9 | -2 | 496C223E6D0C48E3A95944ADA958792D |  | R22 | Non-TXV |  | 14.35% | 0.85647 | 27.58% | [5 empty] | Non-TXV | 14.35%
Vallejo | CA | 94591-8287 |  | 2014-08-05 | 2014-08-05 11:00 | 2014-08-05 11:19 | CARRIER - 38CKC036340 | 70 | 5 | Yes | Yes | 17.9 | 19.9 | -2 | E794F822C9DB47D685B72A1865B93513 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Bakersfield | CA | 93306-6660 |  | 2014-09-18 | 2014-09-18 13:10 | 2014-09-18 13:10 | DAY & NIGHT - 585GJW030040ABAF | 58 | 0 | Yes | Yes | 19.7 | 19.1 | 0.6 | C04FF1D64DDF46F4A2E6C8ACBBA1124B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5093 |  | 2014-10-13 | 2014-10-13 14:53 | 2014-10-13 15:09 | OTHER - FAFF-043JAZ | 85 | 4 | Yes | Yes | 15.9 | 18.8 | -2.9 | EFA3760413D54A3FA46E690F9AE353DC |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Vacaville | CA | 95688-4323 |  | 2014-07-16 | 2014-07-16 13:55 | 2014-07-16 17:15 | BRYANT - 561CJ036-F | 74 | 2.6 | Yes | Yes | 15.8 | 18.6 | -2.8 | 5601F17B3C014050855A04DE0B32BE32 |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Bakersfield | CA | 93309-1928 |  | 2014-09-05 | 2014-09-05 13:55 | 2014-09-05 13:55 | CARRIER - 48SX0S0100321AA | 101 | 9 | Yes | Yes | 22.6 | 21.2 | 1.4 | D1EC0C3FDF5843C8A301C25C31402CBC | Add refrigerant: 9 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.911% | 0.91089 | 17.12% | [5 empty] | Non-TXV | 8.911%
Bakersfield | CA | 93311-1423 |  | 2014-09-27 | 2014-09-27 14:48 | 2014-09-27 15:35 | CARRIER - 48KL142311BE | 78 | 10.1 | Yes | Yes | 22.9 | 18.8 | 4.1 | D170AD7569434940B34BEC17F9B247FC |  | R22 | Non-TXV |  | 12.95% | 0.87051 | 24.88% | [5 empty] | Non-TXV | 12.95%
Vacaville | CA | 95687-3420 |  | 2014-10-14 | 2014-10-14 10:35 | 2014-10-14 11:04 | GUARDIAN - CKL24-1L | 78 | 3.7 | Yes | Yes | 20.5 | 19.9 | 0.6 | 491BCF8969024AA3985279764CD7015F |  | R22 | Non-TXV |  | 4.744% | 0.95256 | 9.116% | [5 empty] | Non-TXV | 4.744%
Vallejo | CA | 94591-6837 |  | 2014-09-22 | 2014-09-22 15:27 | 2014-09-22 15:43 | AMANA - DTG48-030T0001A | 89 | 3.6 | Yes | Yes | 21.7 | 20.4 | 1.3 | CA6013A8CC894A91B65278F0C0300945 |  | R22 | Non-TXV |  | 4.045% | 0.95955 | 7.773% | [5 empty] | Non-TXV | 4.045%
Bakersfield | CA | 93312-6460 |  | 2014-10-14 | 2014-10-14 13:09 | 2014-10-14 13:09 | OTHER - 38CKC030340 | 66 | 0 | Yes | Yes | 22.8 | 22.6 | 0.2 | A7580BA25BC94B08A1E610B718241FA6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5724 |  | 2014-10-14 | 2014-10-14 09:03 | 2014-10-14 09:22 | RHEEM - RACA-030AB0 | 35 | -8 | Yes | Yes | 18.4 | 20.4 | -2 | 81B7A29E00184E23B0E5BB582D463EB0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 36°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -22.86% | 1.2286 | 6.401% |  |  |  |  | Non-TXV |  |  | -22.86%
Bakersfield | CA | 93309-6229 |  | 2014-09-17 | 2014-09-17 15:46 | 2014-09-17 15:46 | OTHER - 585A036080YACR | 60 | 0 | Yes | Yes | 20.4 | 18.6 | 1.8 | 9FD7DE6DB8EA4CC3A87785D1161D73DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8201 |  | 2014-11-12 | 2014-11-12 14:07 | 2014-11-12 14:26 | CARRIER - 38TH048320 | 128 | 12.8 | Yes | Yes | 21.1 | 16.6 | 4.5 | 1DFA56FE889844618633DDBDB654FDB4 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Woodland | CA | 95695-2811 |  | 2014-07-24 | 2014-07-24 10:36 | 2014-07-24 10:57 | HEIL - | 117 | 3.9 | Yes | Yes | 18.3 | 19.3 | -1 | F05A8C1F08F54328A3534B24A353E855 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93307-5931 |  | 2014-09-11 | 2014-09-11 18:06 | 2014-09-11 18:08 | OTHER - 361801AC-108 | 66 | 6.8 | Yes | Yes | 26.7 | 23.1 | 3.6 | 2174DDC47DD24F3EAD8F7AE8DA2228C9 |  | R22 | Non-TXV |  | 10.3% | 0.89697 | 19.8% | [5 empty] | Non-TXV | 10.3%
Vacaville | CA | 95687-5471 |  | 2014-07-16 | 2014-07-16 12:39 | 2014-07-16 17:20 | CARRIER - 38BRB048320 | 85 | 3.5 | Yes | Yes | 16.7 | 19.3 | -2.6 | C1EE8D29FB4C4787AD4F4371CFDC2D08 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Woodland | CA | 95695-4759 |  | 2014-07-21 | 2014-07-21 14:17 | 2014-07-21 15:49 | GE - | 78 | 4 | Yes | Yes | 16.5 | 17.9 | -1.4 | 3CD391E4655F4DDDBE17FBF2C2D00B3F |  | R22 | Non-TXV |  | 5.128% | 0.94872 | 9.855% | [5 empty] | Non-TXV | 5.128%
Bakersfield | CA | 93307-1054 |  | 2014-09-10 | 2014-09-10 19:13 | 2014-09-10 19:16 | BRYANT - 574BNW02404NB-- | 117 | 5 | Yes | Yes | 28.1 | 23.1 | 5 | 343F8E78A5E54286AE3EEFCED914518B |  | R410A | TXV |  | 4.274% | 0.95726 | 8.213% | [5 empty] | TXV | 4.274%
Bakersfield | CA | 93306-8375 |  | 2014-10-12 | 2014-10-12 15:51 | 2014-10-12 15:54 | OTHER - 4204E41245 | 140 | 7.8 | Yes | Yes | 18.4 | 19.9 | -1.5 | CD4F3D01736F43C492C69A8E3DE4A0FA |  | R22 | Non-TXV |  | 5.571% | 0.94429 | 10.71% | [5 empty] | Non-TXV | 5.571%
Bakersfield | CA | 93307-6099 |  | 2014-09-15 | 2014-09-15 10:54 | 2014-09-15 10:54 | GOODMAN - GSX130421BB | 90 | 0 | Yes | Yes | 19.2 | 19.4 | -0.2 | 3668F2928B254201AEFD20E48699FEB4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6155 |  | 2014-09-11 | 2014-09-11 13:15 | 2014-09-11 13:15 | AMERICAN STANDARD - 4YCY4030A1075AA | 97 | 0 | Yes | Yes | 29.4 | 23.1 | 6.3 | 9974DD264E0A431680A16D1E014095F6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8035 |  | 2014-10-14 | 2014-10-14 12:41 | 2014-10-14 13:02 | YORK - H3RE060S06B | 261 | 36.8 | Yes | Yes | 22.4 | 21.4 | 1 | 61ECEECAB7674632AF30A20FDDBE3B3F |  | R22 | Non-TXV |  | 14.1% | 0.859 | 27.1% | [5 empty] | Non-TXV | 14.1%
Bakersfield | CA | 93307-3424 |  | 2014-08-11 | 2014-08-11 09:23 | 2014-08-11 09:23 | UNITARY PRODUCTS GROUP - D1NA030N05606B | 72 | 0 | Yes | Yes | 23.3 | 20.9 | 2.4 | BEEF2C0E622047B29002173082C30F6A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-0000 |  | 2014-08-27 | 2014-08-27 13:51 | 2014-08-27 13:51 | UNITARY PRODUCTS GROUP - D1NP036W05606A | 104 | 0 | Yes | Yes | 24.5 | 20.7 | 3.9 | D34D4B8E729F4C01A4A9A4CD798CBC0A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6466 |  | 2014-10-02 | 2014-10-02 12:42 | 2014-10-02 12:42 | PAYNE - PA12NA060-B | 184 | 0 | Yes | Yes | 19.8 | 22.3 | -2.5 | 8DFA361096C342A2BCCDE03010E8A9D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95119-1846 |  | 2014-07-30 | 2014-07-30 09:38 | 2014-07-30 10:22 | - 593CJ024A | 60 | 6.9 | Yes | Yes | 19.5 | 19.9 | -0.4 | A5D5D2EFB44246CB99252A8FC631D3D9 |  | R22 | Non-TXV |  | 11.5% | 0.885 | 22.1% | [5 empty] | Non-TXV | 11.5%
Concord | CA | 94519-2317 |  | 2014-08-28 | 2014-08-28 08:44 | 2014-08-28 08:44 | CARRIER - 38GR003310 | 85 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | 4598320B37B2445BA44BE8D99325DA9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3012 |  | 2014-09-03 | 2014-09-03 08:27 | 2014-09-03 08:27 | ICP - AC8030A2C1 | 71 | 0 | Yes | Yes | 20.7 | 17.7 | 3 | F55435E6BE2340FC97F352D15AD752AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2226 |  | 2014-08-22 | 2014-08-22 10:36 | 2014-08-22 10:36 | RHEEM - RRNA-C048JK10X | 97.6 | 0 | Yes | Yes | 22.5 | 22 | 0.5 | 7004D22D2EC745D192643756243E851B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8042 |  | 2014-11-12 | 2014-11-12 16:05 | 2014-11-12 16:27 | PAYNE - PA10J060-C | 118 | 11 | Yes | Yes | 19.5 | 13.6 | 5.9 | BECA5C79C4E147C38DA45DA8D2A96ABA |  | R22 | TXV |  | 9.322% | 0.90678 | 17.91% | [5 empty] | TXV | 9.322%
Fremont | CA | 94538-5931 |  | 2014-08-19 | 2014-08-19 10:20 | 2014-08-19 10:43 | - BRCQ0481BD | 103 | -8.5 | Yes | Yes | 21.1 | 19.1 | 2 | 4F6BA7849B3D4DFDA016BC8DED98CFE9 |  | R22 | Non-TXV |  | -8.252% | 1.0825 | 2.311% |  |  |  |  | Non-TXV |  |  | -8.252%
Bakersfield | CA | 93306-5958 |  | 2014-10-09 | 2014-10-09 13:21 | 2014-10-09 13:40 | RHEEM - RRNA-B036JK06X | 85 | 4.3 | Yes | Yes | 20.7 | 20.4 | 0.3 | 83927A3A3F15493CB58A033F8C9FF105 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Fairfield | CA | 94533-4704 |  | 2014-07-25 | 2014-07-25 08:28 | 2014-07-25 09:12 | YORK - TCGD36S21S2HA | 85 | 4.1 | Yes | Yes | 15 | 17.9 | -2.9 | 1431B0D1A980417698D5DC274D54BE23 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Bakersfield | CA | 93312-0000 |  | 2014-08-15 | 2014-08-15 11:38 | 2014-08-15 11:38 | NORDYNE - JS3BC-030KA | 66 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | F50A7ADFAD804A4EB0BBB20A39607FFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6084 |  | 2014-09-11 | 2014-09-11 18:00 | 2014-09-11 18:02 | OTHER - 561CJ042-F | 83 | -3.7 | Yes | Yes | 21.4 | 19.8 | 1.6 | 77B08061E108460D92F59CEE8F75233A |  | R22 | TXV |  | -4.458% | 1.0446 | 1.248% |  |  |  |  | TXV |  |  | -4.458%
W Sacramento | CA | 95691-5894 |  | 2014-08-26 | 2014-08-26 14:42 | 2014-08-26 15:01 | CARRIER - 38CKCC501340 | 68 | -4.8 | Yes | Yes | 20.4 | 19.3 | 1.1 | 85F55CDFD57D4CD4BE26565FAA7AF23B |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93313-5249 |  | 2014-09-23 | 2014-09-23 11:27 | 2014-09-23 11:27 | UNITARY PRODUCTS GROUP - H2RD048S06A | 134 | 0 | Yes | Yes | 22 | 21.5 | 0.6 | 1E7A378654524448BA9953351FEB7E2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3346 |  | 2014-09-10 | 2014-09-10 19:33 | 2014-09-10 19:35 | BRYANT - 589ANW042060ADBF | 92 | -6.5 | Yes | Yes | 27.8 | 22.8 | 5 | FC2353ACC27D4E54AFAEAF9D6BFD00A5 |  | R22 | Non-TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.065%
Bakersfield | CA | 93309-1806 |  | 2014-09-10 | 2014-09-10 12:17 | 2014-09-10 12:17 | BDP - 585EJW048100ABAF | 86 | 0 | Yes | Yes | 19.8 | 19.3 | 0.5 | ABFE285CD98A440DBDA959A7BBF1ED1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3055 |  | 2014-07-25 | 2014-07-25 13:59 | 2014-07-25 13:59 | ICP - PGC030K060E | 51 | 0 | Yes | Yes | 23 | 21.9 | 1.1 | 1737147D026D47CB88D01655E5917171 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4694 |  | 2014-10-23 | 2014-10-23 11:41 | 2014-10-23 11:41 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 22.8 | 19.6 | 3.2 | 87236F8CEABB47F39CE1431829E40646 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6056 |  | 2014-09-18 | 2014-09-18 15:48 | 2014-09-18 15:48 | DAY & NIGHT - 586GJW02404040ABAE | 54 | 0 | Yes | Yes | 21.1 | 21.9 | -0.8 | C1A7D74655974D4E946C24F27CBCEBA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6802 |  | 2014-09-12 | 2014-09-12 13:47 | 2014-09-12 13:47 | OTHER - NAC242AKC3 | 127 | 0 | Yes | Yes | 27.4 | 22.1 | 5.3 | 3AD7EE95F6994145A18E86F8B8C40FE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4108 |  | 2014-09-19 | 2014-09-19 13:24 | 2014-09-19 13:24 | TRANE - 2TTR3024A1000AA | 82 | 0 | Yes | Yes | 24.4 | 21.5 | 3 | 66CE1CD7D72842E6B0A0B333A35EBEA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6205 |  | 2014-09-19 | 2014-09-19 10:22 | 2014-09-19 10:22 | PAYNE - PA10JA036-C | 78 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | AA62E311CBAF41D7A3999E0AA6368157 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5667 |  | 2014-09-18 | 2014-09-18 11:19 | 2014-09-18 11:19 | CARRIER - 38CKC042350 | 82 | 0 | Yes | Yes | 22.3 | 21.1 | 1.2 | 2DB73B71D1594C7D975286D2B75C1457 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3630 |  | 2014-09-09 | 2014-09-09 15:20 | 2014-09-09 15:20 | PAYNE - PY3GNAA36060NA | 121 | 0 | Yes | Yes | 21.7 | 20.2 | 1.5 | 2002D4EB251E48CF86576975B0D47D11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4425 |  | 2014-07-24 | 2014-07-24 15:33 | 2014-07-24 15:59 | AMERICAN STANDARD - 2A7A1042A1000AA | 81 | 5 | Yes | Yes | 16.6 | 18.6 | -2 | C62CE6792E484C92925F6DB9B6EFB7D2 |  | R22 | Non-TXV |  | 6.173% | 0.93827 | 11.86% | [5 empty] | Non-TXV | 6.173%
Wasco | CA | 93280-1649 |  | 2014-07-27 | 2014-07-27 20:51 | 2014-07-27 20:54 | HEIL - PGAD30D1K6 | 78 | 5.8 | Yes | Yes | 24.6 | 22.8 | 1.8 | BF663A3BA9D844249304214BA3FA1066 |  | R22 | Non-TXV |  | 7.436% | 0.92564 | 14.29% | [5 empty] | Non-TXV | 7.436%
Napa | CA | 94558-4644 |  | 2014-09-08 | 2014-09-08 10:33 | 2014-09-08 11:01 | RUUD - URKA-A036JKO8X | 62 | 3.4 | Yes | Yes | 21.3 | 19.9 | 1.4 | C04FF9133C094E84805A7F6A7F26C0FD |  | R22 | Non-TXV |  | 5.484% | 0.94516 | 10.54% | [5 empty] | Non-TXV | 5.484%
Bakersfield | CA | 93306-6847 |  | 2014-10-09 | 2014-10-09 12:58 | 2014-10-09 13:15 | GOODMAN - UNK | 85 | 6 | Yes | Yes | 20.3 | 20.2 | 0.1 | 7B658B1D71D248E4B8C31F7DA933BC17 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Vallejo | CA | 94591-5616 |  | 2014-08-05 | 2014-08-05 12:37 | 2014-08-05 13:01 | YORK - D1NA024N05606C | 54 | 4.1 | Yes | Yes | 21.8 | 20.2 | 1.7 | F36E9CDDF2A04646B22ACDD435EA0DFC |  | R22 | Non-TXV |  | 7.593% | 0.92407 | 14.59% | [5 empty] | Non-TXV | 7.593%
Bakersfield | CA | 93307-3747 |  | 2014-09-14 | 2014-09-14 22:58 | 2014-09-14 23:04 | YORK - D1NA030N5606C | 76 | 4.4 | Yes | Yes | 19.4 | 18.7 | 0.7 | E90D69CAB7684BF1B5CA07EB1A2BF001 |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Concord | CA | 94521-1951 |  | 2014-08-29 | 2014-08-29 10:39 | 2014-08-29 10:39 | PAYNE - PA10J1042-C | 82 | 0 | Yes | Yes | 23.1 | 18.8 | 4.3 | BF9CB78A8C594AA3A1000BA5E98B4EBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-1722 |  | 2014-07-30 | 2014-07-30 10:01 | 2014-07-30 10:20 | OTHER - NAC248AKA1 | 130 | 5.9 | Yes | Yes | 20.6 | 19.2 | 1.4 | F50C615C512F4440ABA7AC866DFE4670 |  | R22 | Non-TXV |  | 4.538% | 0.95462 | 8.722% | [5 empty] | Non-TXV | 4.538%
Antioch | CA | 94531-8106 |  | 2014-10-14 | 2014-10-14 11:10 | 2014-10-14 11:30 | CARRIER - 38TH036300 | 84 | 13.1 | Yes | Yes | 19.6 | 19.9 | -0.3 | 2B81078AE19545158BCEF9BF9872349F |  | R22 | Non-TXV |  | 15.6% | 0.84405 | 29.97% | [5 empty] | Non-TXV | 15.6%
San Jose | CA | 95148-2929 |  | 2014-07-28 | 2014-07-28 13:21 | 2014-07-28 14:02 | HEIL - CA5536VKD2 | 82 | 11 | Yes | Yes | 19.9 | 21 | -1.1 | 096A5E45D85749DB9BE085667830A623 |  | R22 | Non-TXV |  | 13.41% | 0.86585 | 25.78% | [5 empty] | Non-TXV | 13.41%
Bakersfield | CA | 93306-6836 |  | 2014-09-18 | 2014-09-18 14:05 | 2014-09-18 14:38 | OTHER - TZAA3362A757 | 85 | 5.5 | Yes | Yes | 21.3 | 21.9 | -0.6 | 0F622018B440493385644003B4151228 |  | R22 | TXV |  | 6.471% | 0.93529 | 12.44% | [5 empty] | TXV | 6.471%
Dixon | CA | 95620-2214 |  | 2014-07-25 | 2014-07-25 10:30 | 2014-07-25 11:05 | TRANE - 4TTX4036B1000AA | 83 | 3.3 | Yes | Yes | 17.6 | 19.4 | -1.8 | 0B811327484E4B4D927C3CDDF412AAC5 |  | R22 | Non-TXV |  | 3.976% | 0.96024 | 7.641% | [5 empty] | Non-TXV | 3.976%
Bakersfield | CA | 93306-6802 |  | 2014-10-11 | 2014-10-11 14:31 | 2014-10-11 14:31 | RHEEM - UNK | 85 | 0 | Yes | Yes | 23.7 | 19.6 | 4.1 | 0493B252710B4E2EA887B3B9D9E208A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2231 |  | 2014-08-29 | 2014-08-29 11:34 | 2014-08-29 11:57 | PAYNE - PA13NR036-H | 101 | 6.9 | Yes | Yes | 22.7 | 20.4 | 2.3 | D6697C5BB23C4C0DB8F1B4694423CBA1 |  | R22 | TXV |  | 6.832% | 0.93168 | 13.13% | [5 empty] | TXV | 6.832%
Bakersfield | CA | 93309-6003 |  | 2014-09-30 | 2014-09-30 10:34 | 2014-09-30 10:34 | BRYANT - 56CN042-C | 108 | 0 | Yes | Yes | 20 | 17.7 | 2.3 | 152199F3C47040BDA419B70FFB10D337 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6258 |  | 2014-09-11 | 2014-09-11 11:56 | 2014-09-11 11:56 | DUCANE - SG10B30050 | 62 | 0 | Yes | Yes | 21.4 | 20.6 | 0.8 | 58DB46235A5C48F08AD1F36D2A8B2374 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1311 |  | 2014-10-31 | 2014-10-31 11:27 | 2014-10-31 11:27 | OTHER - UNK | 87 | 0 | Yes | Yes | 22.7 | 19.9 | 2.8 | 237E8AADE5FF4F74A7B6B1BFD4011157 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4759 |  | 2014-08-06 | 2014-08-06 10:39 | 2014-08-06 11:08 | TRANE - 2TTB0036A1000AA | 76 | 9.6 | Yes | Yes | 20.5 | 19.9 | 0.6 | EA7ED9C8AB174D5A8CB183B8D98E4B64 |  | R22 | Non-TXV |  | 12.63% | 0.87368 | 24.28% | [5 empty] | Non-TXV | 12.63%
San Jose | CA | 95123-5363 |  | 2014-10-01 | 2014-10-01 08:03 | 2014-10-01 08:06 | YORK - H2DA036S06A | 92 | 3 | Yes | Yes | 20.2 | 17.7 | 2.5 | 93D949CB3B2748A5B9AED37CD17ED6D4 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Antioch | CA | 94531-8176 |  | 2014-10-14 | 2014-10-14 11:55 | 2014-10-14 12:16 | CARRIER - 563AN048-A | 166 | 15.2 | Yes | Yes | 23.9 | 21 | 2.9 | 1D84DA7BDC324937A8CBA358B3452D32 |  | R22 | TXV |  | 9.157% | 0.90843 | 17.6% | [5 empty] | TXV | 9.157%
Bakersfield | CA | 93313-4388 |  | 2014-08-22 | 2014-08-22 12:18 | 2014-08-22 12:18 | PAYNE - PA13NR060-J | 168 | 0 | Yes | Yes | 20.4 | 21.6 | -1.2 | F05696B9F0E54CDBBDCCFF9D97E18207 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1309 |  | 2014-08-08 | 2014-08-08 09:27 | 2014-08-08 17:19 | NORDYNE - JT5BD-024KA | 96 | -5.6 | Yes | Yes | 13.1 | 15.8 | -2.7 | FFAE00B9EC524AB1BDA7B1834EF084BB |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Suisun City | CA | 94585-2329 |  | 2014-10-13 | 2014-10-13 10:36 | 2014-10-16 07:47 | - | 85 | 7.4 | Yes | Yes | 14 | 15.9 | -1.9 | 51C1337277DE4C3F9736C0101E6DCA2E |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Bakersfield | CA | 93314-9654 |  | 2014-09-03 | 2014-09-03 15:21 | 2014-09-03 15:21 | OTHER - UKN | 90 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 1316F3DA4F284A658F570B46E9ED024F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sunnyvale | CA | 94086-9058 |  | 2014-07-31 | 2014-07-31 10:24 | 2014-07-31 10:47 | LENNOX - HS26-036-2P | 90 | 4.4 | Yes | Yes | 23.2 | 18.3 | 4.9 | 183A0075C724426CA16033ED05B16231 | Remove refrigerant: 6.4 oz | R22 | Non-TXV |  | 4.889% | 0.95111 | 9.395% | [5 empty] | Non-TXV | 4.889%
Pittsburg | CA | 94565-5659 |  | 2014-09-22 | 2014-09-22 11:35 | 2014-09-22 11:35 | RHEEM - UNK | 85 | 0 | Yes | Yes | 17.1 | 19.9 | -2.8 | 92C5378EF833463D816187694C34E6B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-7072 |  | 2014-09-22 | 2014-09-22 11:14 | 2014-09-22 11:42 | RHEEM - RAMB-036JBZ | 114 | 4 | Yes | Yes | 19.9 | 20.4 | -0.5 | 7B02635968E948D3820790347F66775D |  | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Bakersfield | CA | 93308-5163 |  | 2014-10-23 | 2014-10-23 14:57 | 2014-10-23 14:57 | UNITARY PRODUCTS GROUP - AC042X1221A | 107 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 425700A99F624E9880620C5ED5DD65DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6818 |  | 2014-09-22 | 2014-09-22 13:24 | 2014-09-22 13:52 | PAYNE - 565BJ024 | 70 | 10.9 | Yes | Yes | 19.8 | 19 | 0.8 | 31D4B979A52A4BCC8DCAD9DA6EDF46B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.57% | 0.84429 | 29.92% | [5 empty] | Non-TXV | 15.57%
W Sacramento | CA | 95691-5199 |  | 2014-07-25 | 2014-07-25 12:50 | 2014-07-25 13:32 | GOODMAN - CKL49-1 | 87 | 4.9 | Yes | Yes | 15.9 | 17.2 | -1.3 | 30EC725C36DE4260B7F49F09F1958D77 |  | R22 | Non-TXV |  | 5.632% | 0.94368 | 10.82% | [5 empty] | Non-TXV | 5.632%
Fairfield | CA | 94533-2231 |  | 2014-07-25 | 2014-07-25 13:56 | 2014-07-25 15:49 | ALLEGIANCE - 7A0018A100A2 | 61 | -4.3 | Yes | Yes | 19.3 | 17.2 | 2.1 | CB8B704538C943E893141A5E54C16BB0 |  | R22 | Non-TXV |  | -7.049% | 1.0705 | 1.974% |  |  |  |  | Non-TXV |  |  | -7.049%
Fresno | CA | 93706-2202 |  | 2014-07-31 | 2014-07-31 11:51 | 2014-07-31 11:51 | GOODMAN - GPH1342M41AC | 180 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 81A4024E485443B98D5CEA4E31483857 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2202 |  | 2014-07-31 | 2014-07-31 11:53 | 2014-07-31 11:53 | LENNOX - 12CHP036-3PA | 176 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 257B87F56AD14CB4A3701F216BFB0063 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5408 |  | 2014-10-12 | 2014-10-12 15:23 | 2014-10-12 15:25 | GOODMAN - GPG1324045M41BA | 60 | 3 | Yes | Yes | 27.6 | 22.4 | 5.3 | 14B78E4993A14C1C96A15D49A02C0104 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93308-5162 |  | 2014-07-28 | 2014-07-28 10:03 | 2014-07-28 10:03 | UNITARY PRODUCTS GROUP - AC042X1221A | 107 | 0 | Yes | Yes | 20.1 | 18.5 | 1.6 | B387143CCAF140708B564155EEB01E9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-4486 |  | 2014-07-29 | 2014-07-29 11:08 | 2014-07-29 13:28 | LENNOX - 12ACB485P | 171 | 14.5 | Yes | Yes | 21.2 | 21.5 | -0.3 | 547301B76649471FB4D6128D7613EE47 |  | R22 | Non-TXV |  | 8.48% | 0.9152 | 16.3% | [5 empty] | Non-TXV | 8.48%
Fremont | CA | 94536-1765 |  | 2014-08-06 | 2014-08-06 13:59 | 2014-08-06 14:39 | YORK - YCJF48S41D1A | 73 | 17.7 | Yes | Yes | 17.8 | 20.2 | -2.4 | EEE06064678B4F56AEAB1B955E597CE4 |  | R410A | Non-TXV |  | 24.25% | 0.75753 | 46.6% | [5 empty] | Non-TXV | 24.25%
Fresno | CA | 93702-1350 |  | 2014-07-29 | 2014-07-29 15:58 | 2014-07-29 15:58 | OTHER - UNK | 80 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C6DD6270761E406AAD630B69B39D522E | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7903 |  | 2014-09-16 | 2014-09-16 09:42 | 2014-09-16 09:42 | BDP - 585EJ036075 | 82 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 97416D320AE141BA849F4F597158476A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-3783 |  | 2014-09-03 | 2014-09-03 09:22 | 2014-09-03 09:22 | RHEEM - UKN | 90 | 0 | Yes | Yes | 17.7 | 19.2 | -1.5 | D3EA7B1601FF4B5EBD255ABBFFD17C1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2479 |  | 2014-09-23 | 2014-09-23 12:36 | 2014-09-23 13:04 | YORK - H1RA048S06D | 117 | 7 | Yes | Yes | 23.5 | 17.5 | 6 | 70BCABF5E2CB450E9CEFD896B8F73DB4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.983% | 0.94017 | 11.5% | [5 empty] | Non-TXV | 5.983%
Bakersfield | CA | 93311-3222 |  | 2014-09-26 | 2014-09-26 10:01 | 2014-09-26 10:01 | UNITARY PRODUCTS GROUP - AC042X1021A | 84 | 0 | Yes | Yes | 24.6 | 22.1 | 2.5 | 1AD196450EE647319420F4BDC18E7E5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3657 |  | 2014-08-29 | 2014-08-29 14:28 | 2014-08-29 14:49 | AMANA - RCB30A2B | 104 | -9.8 | Yes | Yes | 22.7 | 18.6 | 4.2 | A3F27F6167AA4686A202C6B7B61FE797 |  | R22 | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Martinez | CA | 94553-9717 |  | 2014-08-20 | 2014-08-20 13:01 | 2014-08-20 13:01 | - | 85 | 0 | Yes | Yes | 17 | 17.4 | -0.4 | 4203670454404EAFB0DF61F8B00A2D32 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-0000 |  | 2014-08-22 | 2014-08-22 11:38 | 2014-08-22 11:38 | YORK - H2RD048S06A | 134 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | 033E73ED863640A18FD19B55C4FB7BD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1619 |  | 2014-08-05 | 2014-08-05 12:31 | 2014-08-05 12:31 | UNITARY PRODUCTS GROUP - DBYP-F048N080A | 132 | 0 | Yes | Yes | 24.2 | 18.7 | 5.6 | 496109290CDE4EE2BC64180521CAF584 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6801 |  | 2014-09-18 | 2014-09-18 15:24 | 2014-09-18 15:24 | COLEMAN - DRCS0361BEG | 83 | 0 | Yes | Yes | 20.3 | 19.9 | 0.4 | 1264289FEF1D47189818979E8BD1AE04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-8233 |  | 2014-08-21 | 2014-08-21 11:09 | 2014-08-21 11:09 | LENNOX - 13ACD-042-230-01 | 111 | 0 | Yes | Yes | 19.7 | 21.8 | -2.1 | B365631EA05D4D8F89EA2DF5CED70044 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5828 |  | 2014-10-11 | 2014-10-11 18:54 | 2014-10-11 18:54 | OTHER - UNK | 107 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C8172AC5BD7D48358A40FAFB3BA80B0B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5803 |  | 2014-09-12 | 2014-09-12 10:57 | 2014-09-12 10:57 | HEIL - PGF336060K01A1 | 176 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | D7B457C5D77340C6ADD8853ABF04EAC9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-6672 |  | 2014-07-30 | 2014-07-30 10:44 | 2014-07-30 10:44 | ICP - ACS060A2B3 | 122 | 0 | Yes | Yes | 17 | 19.7 | -2.7 | B814CFEA840B44E7996889FFF8E26A4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1524 |  | 2014-09-23 | 2014-09-23 12:05 | 2014-09-23 19:06 | GOODMAN - CRT36-1A | 138 | 4.6 | Yes | Yes | 19.4 | 20.1 | -0.7 | 267129E296474AF19D83AA4E57C7D0C0 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Bakersfield | CA | 93311-2401 |  | 2014-08-14 | 2014-08-14 13:58 | 2014-08-14 13:58 | TRANE - 516TCP048F1H0FK | 166 | 0 | Yes | Yes | 26.5 | 20.9 | 5.6 | 8909F9B83B56467894DC50BE47DAE56F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-8722 |  | 2014-09-18 | 2014-09-18 10:03 | 2014-09-18 10:03 | UNITARY PRODUCTS GROUP - BRCQ0481BDG | 103 | 0 | Yes | Yes | 23.8 | 19.3 | 4.5 | EB7B466BA14E44D18617B745A2EE2C5A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5258 |  | 2014-08-27 | 2014-08-27 12:51 | 2014-08-27 12:51 | YORK - H2RD048S66B | 134 | 0 | Yes | Yes | 23.2 | 22.5 | 0.7 | 0D4372F795D8479B872D22D4AFE63A0B |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-3518 |  | 2014-08-11 | 2014-08-11 12:08 | 2014-08-11 12:32 | PAYNE - PA10JA036-C | 72 | 2.7 | Yes | Yes | 20.5 | 18.8 | 1.7 | 785578895993437C80B85F271F2B7E86 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Fremont | CA | 94536-1692 |  | 2014-08-19 | 2014-08-19 11:40 | 2014-08-19 12:02 | YORK - CZB04811A | 140 | 12.8 | Yes | Yes | 26.8 | 19.5 | 7.3 | ACF24167A8BB4B2EB22BF794538E9C3D |  | R410A | TXV |  | 9.143% | 0.90857 | 17.57% | [5 empty] | TXV | 9.143%
Bakersfield | CA | 93311-3228 |  | 2014-10-02 | 2014-10-02 09:37 | 2014-10-02 09:37 | YORK - AC048X1021A | 117 | 0 | Yes | Yes | 23.6 | 20.4 | 3.2 | 6AC122EA5C1E4EEC8D8C23A316351E95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6729 |  | 2014-08-21 | 2014-08-21 10:32 | 2014-08-21 10:32 | WEATHER KING - 12AJB30A01 | 96 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | 87E8A1B72479418089DBC75BE9E9E017 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6729 |  | 2014-08-21 | 2014-08-21 10:38 | 2014-08-21 10:38 | WEATHER KING - 12AJB36A01 | 117 | 0 | Yes | Yes | 27.2 | 21.4 | 5.8 | 3F8220BD9E84415B93B5DC422E99347D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1952 |  | 2014-08-11 | 2014-08-11 11:20 | 2014-08-11 11:38 | CARRIER - 38CK048320 | 104 | 5.9 | Yes | Yes | 22.9 | 18.8 | 4.1 | 93B733BB83D24014B311AE7BA14C44C7 |  | R22 | Non-TXV |  | 5.673% | 0.94327 | 10.9% | [5 empty] | Non-TXV | 5.673%
Bakersfield | CA | 93308-1086 |  | 2014-07-30 | 2014-07-30 12:45 | 2014-07-30 12:45 | UNITARY PRODUCTS GROUP - H2RC048S06A | 119 | 0 | Yes | Yes | 21.4 | 16.6 | 4.8 | 1343F96188364A0B933AF8A7631B5863 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4110 |  | 2014-07-30 | 2014-07-30 12:20 | 2014-07-30 12:53 | TRANE - 2TTB3024A1000AA | 82 | 5.5 | Yes | Yes | 19.5 | 19.6 | -0.1 | 310B2C45F1B6450589C8444691A000E6 |  | R22 | Non-TXV |  | 6.707% | 0.93293 | 12.89% | [5 empty] | Non-TXV | 6.707%
Bakersfield | CA | 93305-5905 |  | 2014-07-31 | 2014-07-31 15:13 | 2014-07-31 15:13 | RUUD - UKN | 90 | 0 | Yes | Yes | 19.8 | 18.5 | 1.3 | F168470E365F4DC7B72DE343730683D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6991 |  | 2014-09-22 | 2014-09-22 11:39 | 2014-09-22 11:39 | RHEEM - FA4C-030J00 | 70 | 0 | Yes | Yes | 20.4 | 21 | -0.6 | 9C86438D48BD46308DE318690A2712D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-1909 |  | 2014-08-15 | 2014-08-15 15:00 | 2014-08-15 15:00 | GOODMAN - GSC13060KB | 90 | 0 | Yes | Yes | 18.8 | 21.6 | -2.8 | C9CC5A1668334488A75F276524305102 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-8333 |  | 2014-09-03 | 2014-09-03 11:22 | 2014-09-03 11:22 | UNITARY PRODUCTS GROUP - AC060X1221A | 147 | 0 | Yes | Yes | 24 | 20.9 | 3.1 | EFDECEC2E913413DBC9C534D410C5A42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3410 |  | 2014-09-30 | 2014-09-30 16:56 | 2014-09-30 16:56 | UNITARY PRODUCTS GROUP - DAYP-F042N080A | 150 | 0 | Yes | Yes | 24 | 20.6 | 3.4 | 55C86E7109734356A8FED16FEBE18749 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3808 |  | 2014-08-21 | 2014-08-21 09:37 | 2014-08-21 09:37 | GOODMAN - GPG1336045M41AC | 85 | 0 | Yes | Yes | 20.5 | 21.8 | -1.3 | 856AC9A8199B4E3DA348136261B68C7F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1647 |  | 2014-07-25 | 2014-07-25 09:43 | 2014-07-25 10:01 | GOODMAN - PC03618REVE | 63 | 8.4 | Yes | Yes | 20.8 | 19.4 | 1.4 | 04FCD9EA8F9A48C483D98DAB0EE3090B |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Bakersfield | CA | 93304-5172 |  | 2014-10-15 | 2014-10-15 13:32 | 2014-10-15 13:32 | DUCANE - SG10B24075 | 58 | 0 | Yes | Yes | 22.9 | 21.5 | 1.4 | 274A668C29904823A09A1B3109B901AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2314 |  | 2014-07-25 | 2014-07-25 11:03 | 2014-07-25 12:10 | - | 85 | 5.1 | Yes | Yes | 14.2 | 15.7 | -1.5 | 51D8EC4F284046C69576554C0EDF57D3 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Vacaville | CA | 95687-6404 |  | 2014-07-29 | 2014-07-29 08:25 | 2014-07-29 14:52 | UNITARY PRODUCTS GROUP - H2RC042S04G | 109 | 10.8 | Yes | Yes | 17.9 | 20.9 | -3 | C553B0C151F1470EAF79B7AAFCDEB33A |  | R22 | Non-TXV |  | 9.908% | 0.90092 | 19.04% | [5 empty] | Non-TXV | 9.908%
Fairfield | CA | 94533-4252 |  | 2014-08-15 | 2014-08-15 12:44 | 2014-08-15 20:57 | - | 85 | -8 | Yes | Yes | 15.4 | 18.2 | -2.8 | 5BC1673127CE43C7B8A3FCE0B4920CA0 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93305-2306 |  | 2014-08-13 | 2014-08-13 14:33 | 2014-08-13 14:33 | ICP - PGAD36D1K4 | 131 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | 4D585A51DDB0440287D53C99CA51D74B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3837 |  | 2014-08-13 | 2014-08-13 11:50 | 2014-08-13 11:50 | ICP - PGC018KA040 | 58 | 0 | Yes | Yes | 26.1 | 23.9 | 2.2 | D62FA726A6124525BE87AC742DADF4D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-6286 |  | 2014-08-27 | 2014-08-27 11:58 | 2014-08-27 12:30 | CARRIER - 24ABB336A310 | 85 | 5.9 | Yes | Yes | 21.2 | 20.4 | 0.8 | 5A640C62A3EE43C1B6C13F16C9E251F9 |  | R22 | Non-TXV |  | 6.941% | 0.93059 | 13.34% | [5 empty] | Non-TXV | 6.941%
Bakersfield | CA | 93306-4808 |  | 2014-10-12 | 2014-10-12 15:42 | 2014-10-12 15:46 | OTHER - HAC036AKA4 | 80 | 3.1 | Yes | Yes | 20.7 | 20.4 | 0.3 | 33839CC82B0C49A6B007FF85AD9D183E |  | R22 | Non-TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | Non-TXV | 3.875%
Bakersfield | CA | 93306-4604 |  | 2014-09-10 | 2014-09-10 13:10 | 2014-09-10 13:10 | OTHER - 585EJW030050 | 58 | 0 | Yes | Yes | 25.9 | 22.6 | 3.3 | C10498DBB56D44ED8F3E61F11D20B3FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5978 |  | 2014-08-25 | 2014-08-25 13:14 | 2014-08-25 13:14 | BDP - 585G1024040 | 56 | 0 | Yes | Yes | 19.5 | 21.6 | -2.1 | ED4E4CD2926F4B2990A1B93D522E9CF1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3918 |  | 2014-09-08 | 2014-09-08 15:09 | 2014-09-08 22:02 | AIRE-FLO - AFAIR10B30-A | 75 | -7.9 | Yes | Yes | 14.7 | 16.4 | -1.7 | E8BD769A431540CFA0E6074D6C866186 |  | R22 | Non-TXV |  | -10.53% | 1.1053 | 2.95% |  |  |  |  | Non-TXV |  |  | -10.53%
Bakersfield | CA | 93306-4768 |  | 2014-10-01 | 2014-10-01 12:05 | 2014-10-01 12:05 | UNITARY PRODUCTS GROUP - DAYH-F030N045A | 69 | 0 | Yes | Yes | 28.5 | 22.9 | 5.6 | 3689E0476D974C4A86BF569E7321843C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-3729 |  | 2014-09-03 | 2014-09-03 10:09 | 2014-09-03 10:09 | TRANE - 4YCY4048A1096AA | 131 | 0 | Yes | Yes | 19.5 | 21.5 | -2 | C4376C731B9E40CF89EEDD03A0380505 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5164 |  | 2014-07-28 | 2014-07-28 16:09 | 2014-07-28 16:09 | - | 85 | 0 | Yes | Yes | 13.6 | 16.5 | -2.9 | 6937C8481E4B48128975BCB8585BB481 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8411 |  | 2014-10-15 | 2014-10-15 12:56 | 2014-10-15 12:56 | BRYANT - BRCS0601BD | 112 | 0 | Yes | Yes | 21 | 20.7 | 0.3 | 5044499F28FD4B7B9B84A617CC3A14D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1660 |  | 2014-09-02 | 2014-09-02 09:28 | 2014-09-02 09:54 | TRANE - TTR030C100A4 | 66 | 2.1 | Yes | Yes | 21.6 | 18 | 3.7 | 214F4111FFFD42148D07FD9A772E0144 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Wasco | CA | 93280-2683 |  | 2014-10-30 | 2014-10-30 12:37 | 2014-10-30 12:37 | OTHER - 2AC13B36P1A | 139 | 0 | Yes | Yes | 19.5 | 18.7 | 0.8 | 587834446F4B4772AF7553A12E242426 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6431 |  | 2014-09-18 | 2014-09-18 16:49 | 2014-09-18 16:49 | CARRIER - 48XPN048090311 | 179 | 0 | Yes | Yes | 17.5 | 18.8 | -1.3 | C78BC6D91F5C4966800864F3C8F60884 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4831 |  | 2014-07-28 | 2014-07-28 16:17 | 2014-07-28 16:17 | - | 85 | 0 | Yes | Yes | 15.1 | 17.7 | -2.6 | 4D86D330FEA24BA48F7842B268B6E659 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-4237 |  | 2014-07-29 | 2014-07-29 09:29 | 2014-07-29 09:29 | DAY & NIGHT - 565030 | 72 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | B4FA8C7ACD3F41E48E6F8BF11C3E77C8 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-4237 |  | 2014-07-29 | 2014-07-29 09:39 | 2014-07-29 10:44 | DAY & NIGHT - 565BJ030 | 72 | 5.2 | Yes | Yes | 22.1 | 21 | 1.1 | 3197A56F815642B0A8CE0460C1B8E1B1 |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Wasco | CA | 93280-2692 |  | 2014-08-03 | 2014-08-03 18:41 | 2014-08-03 18:44 | GOODMAN - GSX130301BB | 69 | 2.8 | Yes | Yes | 21.4 | 21.3 | 0.1 | 1F197752FEC848CAB63100B8337AD061 |  | R410A | TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | TXV | 4.058%
Bakersfield | CA | 93314-4759 |  | 2014-09-26 | 2014-09-26 08:53 | 2014-09-26 08:53 | YORK - H2RC030S06G | 88 | 0 | Yes | Yes | 21.9 | 21.8 | 0.1 | 5FE6CFE84205490A8BE68147AD56C0B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-4759 |  | 2014-09-26 | 2014-09-26 09:08 | 2014-09-26 09:08 | YORK - H2RC036S06G | 83 | 0 | Yes | Yes | 23 | 21.2 | 1.9 | A3D0917060FD492E88F9E4C21073DA22 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3314 |  | 2014-09-10 | 2014-09-10 19:27 | 2014-09-10 19:29 | OTHER - PGD436060K001C1 | 149 | 9.3 | Yes | Yes | 25.6 | 22.5 | 3.1 | C6B9CDC62E5447C39525328F9DACA555 |  | R410A | TXV |  | 6.242% | 0.93758 | 12% | [5 empty] | TXV | 6.242%
Wasco | CA | 93280-2779 |  | 2014-11-07 | 2014-11-07 18:36 | 2014-11-07 18:36 | OTHER - UNK | 120 | 0 | Yes | Yes | 21.8 | 18.5 | 3.3 | EF483F40A35D4F0BB2B7264C1CF641F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-5305 |  | 2014-07-28 | 2014-07-28 15:10 | 2014-07-28 15:10 | TRANE - 2TTB3048 | 140 | 0 | Yes | Yes | 24.5 | 20.4 | 4.1 | E84F1DCECF074A57BF87524A4281230A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4414 |  | 2014-09-25 | 2014-09-25 15:58 | 2014-09-25 15:58 | GOODMAN - GPG1336070M41AA | 85 | 0 | Yes | Yes | 24.9 | 19 | 5.9 | 6B24A1FD380C4E5693153DBC52E3792C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2435 |  | 2014-09-03 | 2014-09-03 09:40 | 2014-09-03 10:03 | RHEEM - UNK | 85 | -8 | Yes | Yes | 17.3 | 18.8 | -1.5 | 5C8DD26DBAE44931AE68B33A7EE6EF63 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93314-3866 |  | 2014-09-18 | 2014-09-18 13:05 | 2014-09-18 13:05 | ICP - PGAD42D1K6 | 180 | 0 | Yes | Yes | 24.5 | 21.3 | 3.2 | 916ECC92B11C4E57B76D3112780F476C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3815 |  | 2014-07-31 | 2014-07-31 14:27 | 2014-07-31 14:27 | GOODMAN - GPG13360457AC | 112 | 0 | Yes | Yes | 22.3 | 17.2 | 5.1 | 365E6706B1624023A2A7F2B9FFEFF31F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5871 |  | 2014-10-16 | 2014-10-16 15:56 | 2014-10-16 15:56 | GOODMAN - VSX130361EB | 85 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | CD1AC25241D749EEAFB651D8932D770F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5167 |  | 2014-08-22 | 2014-08-22 11:21 | 2014-08-22 11:21 | PAYNE - PA13NR042 | 191 | 0 | Yes | Yes | 21.4 | 23.1 | -1.7 | 2ACC5713746247BCA09A381D468423A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1533 |  | 2014-07-27 | 2014-07-27 19:32 | 2014-07-27 19:36 | TEMPSTAR - PGAD42D1K3 | 180 | 10.6 | Yes | Yes | 24.7 | 19.9 | 4.8 | F08E36E591AD46A7B6E3559DB70851E8 |  | R22 | Non-TXV |  | 5.889% | 0.94111 | 11.32% | [5 empty] | Non-TXV | 5.889%
Wasco | CA | 93280-1533 |  | 2014-07-27 | 2014-07-27 19:41 | 2014-07-27 19:45 | TEMPSTAR - PGAD42D1K3 | 180 | 6.8 | Yes | Yes | 24.7 | 19.6 | 5.2 | B8C51451B5AB48DD898E1DB8B88126B1 |  | R22 | Non-TXV |  | 3.778% | 0.96222 | 7.26% | [5 empty] | Non-TXV | 3.778%
Martinez | CA | 94553-3347 |  | 2014-08-19 | 2014-08-19 10:22 | 2014-08-19 20:06 | GOODMAN - CKL 24-1L | 76 | 4.6 | Yes | Yes | 17.1 | 17.4 | -0.3 | 34FB4BECD33644E1886394EB15ABEDB0 |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
Wasco | CA | 93280-0000 |  | 2014-10-29 | 2014-10-29 11:36 | 2014-10-29 11:36 | GOODMAN - GSX130301DB | 76 | 0 | Yes | Yes | 18.3 | 20.3 | -2 | EC080A9E78E14496902DFB13AD119B61 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2910 |  | 2014-08-10 | 2014-08-10 18:58 | 2014-08-10 19:00 | PAYNE - PY3GNAA4209NA | 97 | -7.2 | Yes | Yes | 20.9 | 19.3 | 1.6 | 15570BBD37C4492CBAFD8B579562A09F |  | R22 | Non-TXV |  | -7.423% | 1.0742 | 2.079% |  |  |  |  | Non-TXV |  |  | -7.423%
Fairfield | CA | 94533-3517 |  | 2014-09-15 | 2014-09-15 12:33 | 2014-09-17 07:46 | - | 85 | 2.7 | Yes | Yes | 16.4 | 19 | -2.6 | EB2D1864D0DE43D8B3CE134D240385E7 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93309-7693 |  | 2014-10-15 | 2014-10-15 12:23 | 2014-10-15 12:23 | RHEEM - UKN | 90 | 0 | Yes | Yes | 26.2 | 20.4 | 5.8 | 16A5E3F7A2B14443902570A2E2828D77 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2648 |  | 2014-08-14 | 2014-08-14 15:35 | 2014-08-14 15:35 | ICP - CA9042VKD2 | 50 | 0 | Yes | Yes | 19.9 | 22.3 | -2.4 | 58797190822E4179A66D24C2486705C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9469 |  | 2014-09-24 | 2014-09-24 14:19 | 2014-09-24 14:19 | RUUD - EADC-042JAS | 90 | 0 | Yes | Yes | 19.7 | 21.5 | -1.8 | 3EB538685A024C9A9E3E7FEDDD4E457A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-1700 |  | 2014-08-19 | 2014-08-19 13:22 | 2014-08-19 13:36 | OTHER - SRM-51382A | 74 | 7.2 | Yes | Yes | 16.8 | 17.1 | -0.3 | 8589A87A4C4241D28F48AA31EA89241A |  | R22 | Non-TXV |  | 9.73% | 0.9027 | 18.7% | [5 empty] | Non-TXV | 9.73%
Vacaville | CA | 95688-2723 |  | 2014-07-29 | 2014-07-29 10:44 | 2014-07-29 14:57 | TRANE - 588ANW030060ADAD | 85 | 7 | Yes | Yes | 16.6 | 19.5 | -2.9 | D5AF7E7F90E342F48A50816B0B59D303 |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 13:58 | 2014-10-16 13:58 | ICP - PGC030K060A | 52 | 0 | Yes | Yes | 22.2 | 19.8 | 2.4 | 4DEEF808CD6944598C977E8E51B6F487 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1532 |  | 2014-08-29 | 2014-08-29 11:05 | 2014-08-29 12:32 | CARRIER - 38TRA042330 | 112 | 8.8 | Yes | Yes | 17.4 | 17.8 | -0.3 | 1166F7EEFD32483793F8E5128657DA89 |  | R22 | Non-TXV |  | 7.857% | 0.92143 | 15.1% | [5 empty] | Non-TXV | 7.857%
Bakersfield | CA | 93312-2828 |  | 2014-09-18 | 2014-09-18 16:02 | 2014-09-18 16:02 | UNITARY PRODUCTS GROUP - D6NZ030N05606NXA | 64 | 0 | Yes | Yes | 28 | 22.1 | 5.9 | 36E0D6A91AB64D8AB9419142A7E28D05 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4448 |  | 2014-08-25 | 2014-08-25 12:45 | 2014-08-25 12:45 | PAYNE - PY3GNAA0040NA | 102 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 62C7AAF06762453E9308821E5DD6A82F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3335 |  | 2014-08-13 | 2014-08-13 14:21 | 2014-08-13 20:50 | RUUD - | 85 | 2.6 | Yes | Yes | 15.7 | 17.8 | -2.1 | 97C5AD95B0694D539C3A908DB3B3E8A1 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 12:22 | 2014-10-16 12:22 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.6 | 19.3 | 2.3 | D5BDDA0006B24EAB975588668D87FA47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95117-1631 |  | 2014-07-31 | 2014-07-31 09:32 | 2014-07-31 10:04 | CARRIER - 561CJ036-D | 84 | -4.3 | Yes | Yes | 18.2 | 17.5 | 0.7 | 8F724FA93B2F4670AE127300EE29C3F6 |  | R22 | TXV |  | -5.119% | 1.0512 | 1.434% |  |  |  |  | TXV |  |  | -5.119%
Bakersfield | CA | 93312-5973 |  | 2014-08-15 | 2014-08-15 12:31 | 2014-08-15 12:31 | UNITARY PRODUCTS GROUP - AC036X1222A | 83 | 0 | Yes | Yes | 23.6 | 21.3 | 2.3 | F9A258984C75498A8B52D5B76DEAA480 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95117-1612 |  | 2014-07-30 | 2014-07-30 10:34 | 2014-07-30 10:34 | YORK - H1DB048S06A | 100 | 0 | Yes | Yes | 23.9 | 19.3 | 4.6 | F3E2AA90FF914D1E8394CA8CABA2C7A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-0224 |  | 2014-10-16 | 2014-10-16 10:30 | 2014-10-16 12:25 | LENNOX - HS26-036-4P | 87 | 3.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | 6A0C76CA0A8E4C4ABCC5333B5E013F06 |  | R22 | TXV |  | 3.908% | 0.96092 | 7.51% | [5 empty] | TXV | 3.908%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 10:22 | 2014-10-16 10:22 | ICP - PGF330060K01A2 | 94 | 0 | Yes | Yes | 20.9 | 18.6 | 2.3 | 56BE7A923930487780C8B35253382078 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1545 |  | 2014-08-06 | 2014-08-06 10:31 | 2014-08-06 10:52 | GOODMAN - PGB0420751B | 80 | 9.6 | Yes | Yes | 21.1 | 19.7 | 1.4 | 189FD850F67F467EA35660D452BAA836 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Dixon | CA | 95620-4242 |  | 2014-07-29 | 2014-07-29 10:22 | 2014-07-29 10:40 | GOODMAN - CJ30-1FB | 109 | 4.4 | Yes | Yes | 19.4 | 19.3 | 0.1 | 9E9BC00D615C4B23B232ADFAE1E9A863 |  | R22 | Non-TXV |  | 4.037% | 0.95963 | 7.758% | [5 empty] | Non-TXV | 4.037%
Bakersfield | CA | 93304-5978 |  | 2014-08-25 | 2014-08-25 13:42 | 2014-08-25 13:42 | YORK - D3NZ\024N03606NXC | 58 | 0 | Yes | Yes | 25 | 20.9 | 4.1 | A7C46D7845AE4D4896F523A63AA30C01 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-2553 |  | 2014-07-29 | 2014-07-29 10:29 | 2014-07-29 10:29 | YORK - D2NP024N03606NXA | 108 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 7472BFD600624D00B9F8FD3085A788AA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-9704 |  | 2014-07-31 | 2014-07-31 12:17 | 2014-07-31 12:40 | YORK - D2NA060N09006C | 89 | 5.3 | Yes | Yes | 29.3 | 24.2 | 5.1 | A2DE118FBBAA4EA9B23A0C21FA72332F |  | R22 | Non-TXV |  | 5.955% | 0.94045 | 11.44% | [5 empty] | Non-TXV | 5.955%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 11:58 | 2014-10-16 11:58 | ICP - PGC030K060E | 53 | 0 | Yes | Yes | 25.3 | 21.3 | 4.1 | 6808722125C341FDA17B071D8071A1D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5965 |  | 2014-09-12 | 2014-09-12 10:15 | 2014-09-12 10:15 | GOODMAN - GPG1342070M41DA | 85 | 0 | Yes | Yes | 29.9 | 20.4 | 9.5 | 9C25DE5108674652B6D01361058D9DDA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2444 |  | 2014-08-14 | 2014-08-14 10:14 | 2014-08-14 10:14 | OTHER - N2A360AKA300 | 146 | 0 | Yes | Yes | 19.5 | 20.9 | -1.4 | 4FDCAF6F4D544448A3F302AC7DE98571 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3309 |  | 2014-07-29 | 2014-07-29 09:49 | 2014-07-29 14:55 | LENNOX - 14ACX-030-230-11 | 85 | 2.7 | Yes | Yes | 14.6 | 17.6 | -3 | AD7209FEEA194E739A3652B918E494B1 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Bakersfield | CA | 93308-4817 |  | 2014-09-02 | 2014-09-02 16:14 | 2014-09-02 16:14 | UNITARY PRODUCTS GROUP - D2NPO24N03606A | 100 | 0 | Yes | Yes | 20.9 | 20.1 | 0.9 | ACCD2233583F49BC8F70E2A97ED113F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-3138 |  | 2014-09-08 | 2014-09-08 14:38 | 2014-09-08 14:58 | TRANE - TTRO36D100A0 | 79 | 7.1 | Yes | Yes | 20 | 19.3 | 0.7 | A8D934EBEDFD4AE283C427ADCA9072FC |  | R22 | Non-TXV |  | 8.987% | 0.91013 | 17.27% | [5 empty] | Non-TXV | 8.987%
Pittsburg | CA | 94565-4460 |  | 2014-09-25 | 2014-09-25 10:12 | 2014-09-25 10:12 | GE - BTB930A100A3 | 53 | 0 | Yes | Yes | 19.6 | 18.8 | 0.8 | 0113C59A0C5C4C20B27BB1C9BB004627 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1327 |  | 2014-09-16 | 2014-09-16 11:50 | 2014-09-16 11:50 | ICP - PGAA36C1K2 | 81 | 0 | Yes | Yes | 20 | 22.8 | -2.8 | A8D5CB218B9F4A278F381101B91B38E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3423 |  | 2014-09-15 | 2014-09-15 10:27 | 2014-09-17 07:45 | - | 85 | 2.8 | Yes | Yes | 18.3 | 21 | -2.7 | 1D25F9EAF2CA4F34A1E39136E4BA35CF |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Antioch | CA | 94531-8107 |  | 2014-10-16 | 2014-10-16 08:23 | 2014-10-16 08:41 | CARRIER - 38THO48320 | 128 | 8.4 | Yes | Yes | 21.9 | 19.9 | 2 | 8B84B674150743E78D9FD8B8C4695EAA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 6.562% | 0.93437 | 12.61% | [5 empty] | Non-TXV | 6.562%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 13:34 | 2014-10-16 13:34 | RHEEM - UKN | 90 | 0 | Yes | Yes | 22.9 | 21 | 1.9 | A35E6C29C7D14D74B7BBAE08E110320D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5992 |  | 2014-08-21 | 2014-08-21 12:15 | 2014-08-21 12:15 | UNITARY PRODUCTS GROUP - H2RC042506HG | 109 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | E00311EBA23D4D549EF5E03D162B6B40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1089 |  | 2014-07-25 | 2014-07-25 11:07 | 2014-07-25 11:07 | CARRIER - 48GXN024040301 | 52 | 0 | Yes | Yes | 23.1 | 17.6 | 5.5 | 6D2F344B065B486F8D956AA288DD0BBC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1089 |  | 2014-07-25 | 2014-07-25 14:57 | 2014-07-25 14:57 | CARRIER - UKN | 90 | 0 | Yes | Yes | 19.8 | 17.9 | 1.9 | EA86870C605442E68B917C5A17CD3BED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0728 |  | 2014-07-28 | 2014-07-28 17:36 | 2014-07-28 18:29 | YORK - D1NP036N05606A | 108 | 3.7 | Yes | Yes | 20.2 | 19.5 | 0.7 | CF654B5B96934D0E8F6F3CF5609925C3 |  | R22 | Non-TXV |  | 3.426% | 0.96574 | 6.584% | [5 empty] | Non-TXV | 3.426%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 11:11 | 2014-10-16 11:11 | ICP - PGF3008190080K01 | 158 | 0 | Yes | Yes | 24.9 | 20.4 | 4.5 | A4914BAC880442148E5283FC45356C16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3626 |  | 2014-07-25 | 2014-07-25 12:03 | 2014-07-25 12:03 | RUUD - URMA-A042JK08X | 114 | 0 | Yes | Yes | 20.9 | 16.6 | 4.3 | 4B073597685B4AE0AE9E838E39736669 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7851 |  | 2014-08-14 | 2014-08-14 08:37 | 2014-08-14 14:47 | - | 85 | -8 | Yes | Yes | 14.1 | 16.8 | -2.7 | 90D648CE350943D0822DFEE0164A1723 |  | R410A | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93311-3237 |  | 2014-09-26 | 2014-09-26 10:24 | 2014-09-26 10:24 | NORDYNE - JS3BC-060KA | 155 | 0 | Yes | Yes | 21.5 | 22.9 | -1.4 | 547CA236A8AE4A729DB914D6BCDDD53E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3328 |  | 2014-10-29 | 2014-10-29 09:54 | 2014-10-29 09:54 | BDP - 585EJW024050ABAE | 54 | 0 | Yes | Yes | 27 | 21 | 6 | 4838EA236C35489EABACE41013B881E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3855 |  | 2014-08-04 | 2014-08-04 11:57 | 2014-08-04 11:57 | ICP - WPG3244040LKC1 | 72 | 0 | Yes | Yes | 23.3 | 20.5 | 2.8 | F790E50B3D6A46BE90C051391C47278D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2146 |  | 2014-08-08 | 2014-08-08 10:52 | 2014-08-08 17:18 | GE - | 85 | 10.1 | Yes | Yes | 18.4 | 18.2 | 0.2 | DEF8776FA8394F77AD1EE3D2284F9584 |  | R22 | Non-TXV |  | 11.88% | 0.88118 | 22.84% | [5 empty] | Non-TXV | 11.88%
Bakersfield | CA | 93309-7693 |  | 2014-10-16 | 2014-10-16 12:39 | 2014-10-16 12:39 | UNITARY PRODUCTS GROUP - D2NP030N03606 | 73 | 0 | Yes | Yes | 24.8 | 19.9 | 4.9 | 41994E96E3AA47D183740CFFC66B8D29 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3001 |  | 2014-08-21 | 2014-08-21 12:40 | 2014-08-21 12:40 | TRANE - YCZ036F1M0BC | 160 | 0 | Yes | Yes | 19.8 | 19.5 | 0.3 | 17F1F52EC0944478ADA612F6E8835E90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5482 |  | 2014-09-10 | 2014-09-10 10:07 | 2014-09-10 10:07 | HEIL - CA5542VKD2 | 98 | 0 | Yes | Yes | 19.7 | 18.1 | 1.6 | 10EEFE88DBA4492EA7691569D59D3ADD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8806 |  | 2014-10-17 | 2014-10-17 08:25 | 2014-10-17 08:25 | RHEEM - RAHE042JAS | 101 | 0 | Yes | Yes | 22 | 19.6 | 2.4 | C9C44CB93A1D445985FCA021C6C18D6A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6170 |  | 2014-09-22 | 2014-09-22 14:37 | 2014-09-22 14:37 | ICP - PGCO24KG40E | 54 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | 6818CCAADAA14212B354D3C30250B38F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6171 |  | 2014-09-22 | 2014-09-22 14:33 | 2014-09-22 14:33 | OTHER - AYCC3024B1064AA | 95 | 0 | Yes | Yes | 24 | 19.9 | 4.1 | ECCF18A21963462E9417C065B315731C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5766 |  | 2014-08-15 | 2014-08-15 13:45 | 2014-08-15 13:45 | UNITARY PRODUCTS GROUP - AC060X1223A | 144 | 0 | Yes | Yes | 19.1 | 21 | -1.9 | 187BA432E7234027BA7113009E79502D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2915 |  | 2014-11-07 | 2014-11-07 19:13 | 2014-11-07 19:13 | OTHER - UNK | 102 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 9C00C655D5D947DC9E808F9889F4C9AC | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6781 |  | 2014-09-18 | 2014-09-18 11:42 | 2014-09-18 11:42 | YORK - H3RA060S06B | 98 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | B212988A0B3B411CB3ED311B2ECB5B65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4352 |  | 2014-08-20 | 2014-08-20 13:45 | 2014-08-20 13:45 | DAY & NIGHT - 565BJ030 | 85 | 0 | Yes | Yes | 15.4 | 16.8 | -1.4 | EB334BFD8A0546159DB891DA58A19E54 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-5359 |  | 2014-08-27 | 2014-08-27 16:26 | 2014-08-27 16:52 | AMANA - GSX130601BA | 111 | -6.9 | Yes | Yes | 25.2 | 20.4 | 4.8 | ED0AEDFF39E644A89FCA5B2C61EA9859 |  | R410A | TXV |  | -6.216% | 1.0622 | 1.741% |  |  |  |  | TXV |  |  | -6.216%
Bakersfield | CA | 93309-6232 |  | 2014-09-17 | 2014-09-17 12:09 | 2014-09-17 12:09 | OTHER - 589ANW030040AABD | 69 | 0 | Yes | Yes | 16.4 | 18.7 | -2.3 | 3DFCCDA96DBC472EAF6BFC1CF25DEF02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-2071 |  | 2014-08-01 | 2014-08-01 09:52 | 2014-08-01 10:28 | CARRIER - 38CKC036630 | 79 | -4.6 | Yes | Yes | 18.1 | 19.3 | -1.2 | 05CA565516114D09B452D429C38E4565 |  | R22 | Non-TXV |  | -5.823% | 1.0582 | 1.631% |  |  |  |  | Non-TXV |  |  | -5.823%
Bakersfield | CA | 93311-3229 |  | 2014-09-24 | 2014-09-24 15:01 | 2014-09-24 15:01 | UNITARY PRODUCTS GROUP - AC060X1022B | 98 | 0 | Yes | Yes | 24.7 | 20.4 | 4.3 | D251D8EE59984629846373E844C19989 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4106 |  | 2014-09-22 | 2014-09-22 12:36 | 2014-09-22 12:36 | HEIL - CA5536VKA1 | 80 | 0 | Yes | Yes | 23.7 | 20.4 | 3.3 | A52C52B23B344D0BA0CFDDD3CF65779E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1330 |  | 2014-08-05 | 2014-08-05 18:36 | 2014-08-05 18:36 | RUUD - UNK | 60 | 0 | Yes | Yes | 35 | 21.4 | 13.6 | C44459602F284211A45CD68367D8056B | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4215 |  | 2014-08-06 | 2014-08-06 13:58 | 2014-08-06 16:09 | AMERICAN STANDARD - | 54 | 6.1 | Yes | Yes | 14.9 | 17.6 | -2.7 | B7782EC8786D4927A1AFB062DEA2088B |  | R22 | Non-TXV |  | 11.3% | 0.88704 | 21.71% | [5 empty] | Non-TXV | 11.3%
Fresno | CA | 93702-4213 |  | 2014-08-28 | 2014-08-28 09:35 | 2014-08-28 10:10 | RHEEM - RRKAA036JK08X | 60 | 3.5 | Yes | Yes | 24.2 | 21.5 | 2.7 | 939DB68C67534247B7CC5447DFC160EB |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Fresno | CA | 93702-4631 |  | 2014-08-05 | 2014-08-05 09:21 | 2014-08-05 09:48 | YORK - D1NP036N05606A | 108 | 21.9 | Yes | Yes | 23.5 | 19.3 | 4.2 | C6D974F375BE4F11A4104F4428A90DC8 |  | R22 | Non-TXV |  | 20.28% | 0.79722 | 38.97% | [5 empty] | Non-TXV | 20.28%
Bakersfield | CA | 93306-5443 |  | 2014-09-02 | 2014-09-02 11:40 | 2014-09-02 11:40 | ICP - PGNN36C1K6 | 77 | 0 | Yes | Yes | 23.8 | 22.1 | 1.8 | 1D99A76E286F43C684BBF039F549E305 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5894 |  | 2014-08-13 | 2014-08-13 15:14 | 2014-08-13 15:14 | OTHER - UKN | 90 | 0 | Yes | Yes | 21.5 | 18.3 | 3.2 | 27657AFBE4524CD996650D4B64497C29 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4978 |  | 2014-10-04 | 2014-10-04 16:32 | 2014-10-04 16:57 | AIRE-FLO - AC042X1021A | 84 | 3.7 | Yes | Yes | 18.2 | 21 | -2.8 | E1E7B243F5294FE6AB8B98E87BC99B4D |  | R22 | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Fresno | CA | 93722-5593 |  | 2014-08-08 | 2014-08-08 14:30 | 2014-08-08 14:53 | RUUD - URKAA036JK06E | 62 | 6.2 | Yes | Yes | 23.4 | 21.3 | 2.1 | 78C5ED2C4B274ECA8C0CA95B81688FA1 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Clovis | CA | 93611-8183 |  | 2014-08-20 | 2014-08-20 16:38 | 2014-08-20 16:57 | LENNOX - 13ACC06023001 | 168 | 15.7 | Yes | Yes | 20.7 | 23 | -2.3 | A28633C6E63046E8A1ECCF00BCD95A6A |  | R22 | Non-TXV |  | 9.345% | 0.90655 | 17.96% | [5 empty] | Non-TXV | 9.345%
Bakersfield | CA | 93305-3912 |  | 2014-08-05 | 2014-08-05 12:10 | 2014-08-05 12:10 | ICP - PGF348080K01A1 | 208 | 0 | Yes | Yes | 24.7 | 23.9 | 0.9 | 248D9F23657F43ACAFADDB7E7B5C2FD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1712 |  | 2014-08-14 | 2014-08-14 09:59 | 2014-08-14 20:43 | AMERICAN STANDARD - 4A7B3048D1000AA | 85 | 2.6 | Yes | Yes | 15.1 | 17.3 | -2.2 | 94F30F40F72A48AD980317F3F67F996A |  | R410A | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Bakersfield | CA | 93307-2621 |  | 2014-10-16 | 2014-10-16 10:13 | 2014-10-16 10:13 | YORK - D6NZ036N05606NXA | 64 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | 80DDBFDA7E1F481291C2AEC9C846B2B2 |  | R410A | TXV |  | 0% | 1 | 0%
Lemoore | CA | 93245-2826 |  | 2014-08-01 | 2014-08-01 13:15 | 2014-08-01 13:37 | GOODMAN - GPG1330O451BB | 77 | 3.1 | Yes | Yes | 18.2 | 18.2 | 0 | 0EDD4E04E4DE40FC8D4D04BE71C0E497 |  | R22 | Non-TXV |  | 4.026% | 0.95974 | 7.737% | [5 empty] | Non-TXV | 4.026%
Lemoore | CA | 93245-2826 |  | 2014-08-04 | 2014-08-04 14:06 | 2014-08-04 14:50 | DAY & NIGHT - UNK | 58 | 4.6 | Yes | Yes | 20.2 | 19.1 | 1.2 | A977FB2BA6414476A9DEE159E1B5044D |  | R22 | Non-TXV |  | 7.931% | 0.92069 | 15.24% | [5 empty] | Non-TXV | 7.931%
Fresno | CA | 93705-1858 |  | 2014-08-12 | 2014-08-12 09:54 | 2014-08-12 10:14 | YORK - DCYZF030N070B | 64 | 1.9 | Yes | Yes | 22 | 19.3 | 2.7 | 8AA2441AB8894B78A2BECE7E88448918 |  | R410A | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Napa | CA | 94558-1416 |  | 2014-09-08 | 2014-09-08 12:17 | 2014-09-08 12:17 | CARRIER - 38TXA060350 | 181 | 0 | Yes | Yes | 18.5 | 15.8 | 2.7 | DBC7AC003E5E42B4B9EF3839AEFDBF5E |  | R410A | TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3052 |  | 2014-08-26 | 2014-08-26 09:59 | 2014-08-26 10:44 | CARRIER - | 87 | 3.6 | Yes | Yes | 22.3 | 20.4 | 1.9 | 2CEC7D4262104CE9B78DABF1F4CB1A89 |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Fresno | CA | 93722-1113 |  | 2014-08-07 | 2014-08-07 16:16 | 2014-08-07 16:43 | CARRIER - 48KLA136921BE | 102 | 3.8 | Yes | Yes | 22.1 | 19.3 | 2.8 | FC12C3CBC47744C78F21B0FD87DCFFB0 |  | R22 | Non-TXV |  | 3.725% | 0.96275 | 7.16% | [5 empty] | Non-TXV | 3.725%
Bakersfield | CA | 93311-9397 |  | 2014-08-14 | 2014-08-14 15:20 | 2014-08-14 15:20 | UNITARY PRODUCTS GROUP - A2RC036S06G | 83 | 0 | Yes | Yes | 20.6 | 20.1 | 0.5 | D6BDE776719A41F1B20D9F5867CA576C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3518 |  | 2014-08-06 | 2014-08-06 13:42 | 2014-08-06 14:06 | CARRIER - 48GX042090301AD | 121 | 5.5 | Yes | Yes | 21.8 | 19 | 2.8 | 4FB859A8CA7341F68BC39A66B1576223 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Bakersfield | CA | 93307-4716 |  | 2014-10-20 | 2014-10-20 13:17 | 2014-10-20 13:17 | OTHER - PGF342080K01A1 | 184 | 0 | Yes | Yes | 17.6 | 18.1 | -0.5 | B013DD1BC2D64FAD8777F7F322B8225E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-2500 |  | 2014-08-26 | 2014-08-26 09:40 | 2014-08-26 10:07 | YORK - DCYZF030N070B | 64 | -4.5 | Yes | Yes | 26.4 | 20.4 | 6 | A76B7D15F59B4C6B8DB6D873AC85D6E1 |  | R410A | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Concord | CA | 94521-3936 |  | 2014-09-02 | 2014-09-02 11:36 | 2014-09-02 12:02 | GOODMAN - GSC130241EA | 77 | 7.7 | Yes | Yes | 17.1 | 18.8 | -1.7 | 8415A20B021C4512BFD18BD6726030C7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Vacaville | CA | 95687-4817 |  | 2014-08-12 | 2014-08-12 10:47 | 2014-08-12 20:34 | - | 85 | -8 | Yes | Yes | 15.4 | 17.1 | -1.7 | B2A9FF5CFB194234A700B38F768CA2E8 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93306-6314 |  | 2014-09-12 | 2014-09-12 15:03 | 2014-09-12 15:03 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 0 | 20.4 | -20.4 | E7D1282E27364EDEAB9BA8E927F1F03C | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2125 |  | 2014-10-12 | 2014-10-12 16:02 | 2014-10-12 16:04 | AMERICAN STANDARD - YCP036F1MOAB | 109 | 4.8 | Yes | Yes | 24.2 | 20.4 | 3.8 | C39EC297719E48649CBC6DDD98999ABA |  | R22 | Non-TXV |  | 4.404% | 0.95596 | 8.463% | [5 empty] | Non-TXV | 4.404%
Pittsburg | CA | 94565-5662 |  | 2014-09-23 | 2014-09-23 08:22 | 2014-09-23 08:22 | RHEEM - UNK | 85 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | 766DEE3B832C4C4CA6E96EBEC358E11C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5339 |  | 2014-11-17 | 2014-11-17 09:59 | 2014-11-17 09:59 | DAY & NIGHT - UNK | 120 | 0 | Yes | Yes | 28.1 | 20.1 | 8 | 53C592582C8247B0AFDA79FD3F40A790 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5339 |  | 2014-11-17 | 2014-11-17 10:18 | 2014-11-17 10:18 | YORK - D1NP024N03606A | 74 | 0 | Yes | Yes | 34.5 | 20.2 | 14.4 | B4BA6485110545BBBE539DAA3418FA28 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4961 |  | 2014-08-06 | 2014-08-06 09:33 | 2014-08-06 09:33 | PAYNE - PY3PNA030060NB | 98 | 0 | Yes | Yes | 18.3 | 19.4 | -1.1 | BF124F89A31F4170A323B2E97807EC27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6230 |  | 2014-10-16 | 2014-10-16 09:12 | 2014-10-16 09:12 | SEARS - 36TD948670 | 85 | 0 | Yes | Yes | 16.4 | 19.1 | -2.7 | FC57D33BE1F64C4ABFFA8899DEF79992 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2813 |  | 2014-09-18 | 2014-09-18 12:21 | 2014-09-18 12:21 | UNITARY PRODUCTS GROUP - DAYP-F042N080A | 150 | 0 | Yes | Yes | 27.7 | 22.2 | 5.5 | 5BB6856A178E4F7E8AE21ADE1D1CDE02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5737 |  | 2014-08-27 | 2014-08-27 11:08 | 2014-08-27 11:33 | LENNOX - 12GCS060X1002PA | 159 | 6.5 | Yes | Yes | 24.1 | 20.4 | 3.7 | 6DFD21C77F4F4578A19B5C28F0F2EC84 |  | R22 | Non-TXV |  | 4.088% | 0.95912 | 7.856% | [5 empty] | Non-TXV | 4.088%
Bakersfield | CA | 93312-5627 |  | 2014-10-20 | 2014-10-20 11:27 | 2014-10-20 11:27 | UNITARY PRODUCTS GROUP - HIRA042506D | 84 | 0 | Yes | Yes | 19 | 22 | -3 | 6AFA1C284437488F95AF4588754BE0E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3533 |  | 2014-09-09 | 2014-09-09 17:54 | 2014-09-09 17:56 | WESTINGHOUSE - FS3BC-060KA | 155 | 41.1 | Yes | Yes | 28.4 | 22.6 | 5.8 | D4D3616829BA4CF1BB8F6147CD3EA188 |  | R22 | Non-TXV |  | 26.52% | 0.73484 | 50.96% | [5 empty] | Non-TXV | 26.52%
Fresno | CA | 93702-4113 |  | 2014-08-28 | 2014-08-28 10:37 | 2014-08-28 11:12 | TRANE - YCC036F1MOBF | 85 | 3.2 | Yes | Yes | 19.4 | 22.1 | -2.7 | 9D056306B7CF4507A69D472DE279941D |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Bakersfield | CA | 93311-3029 |  | 2014-11-13 | 2014-11-13 17:37 | 2014-11-13 22:16 | RHEEM - EADB048JAS | 110 | 3.4 | Yes | Yes | 19.7 | 20.4 | -0.7 | 7660C473F7D040C780780A39520F8A4B |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Bakersfield | CA | 93313-2860 |  | 2014-08-22 | 2014-08-22 15:27 | 2014-08-22 15:27 | ICP - PGF342080K01 | 189 | 0 | Yes | Yes | 21.3 | 24.2 | -2.9 | AE0BAB22534E4B77B6A02E7B9F9282E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5623 |  | 2014-08-15 | 2014-08-15 16:24 | 2014-08-15 16:24 | ICP - CA9048VKD2 | 50 | 0 | Yes | Yes | 22.3 | 21.7 | 0.6 | 06BCB92DD2C544B481702B359CA2B770 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4118 |  | 2014-08-15 | 2014-08-15 08:57 | 2014-08-15 09:17 | RHEEM - RRPLB036JK06K | 93 | 3.1 | Yes | Yes | 20.9 | 19.9 | 1 | 84B9C671D69E466DA0AED0CDF974A9C6 |  | R410A | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93726-3018 |  | 2014-08-11 | 2014-08-11 11:15 | 2014-08-11 11:45 | ARCOAIRE - PGAD36D1K6 | 102 | 5.1 | Yes | Yes | 20 | 19.9 | 0.1 | 6312DFE9EA224A1191C07A74BC83285E |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Clovis | CA | 93611-4560 |  | 2014-08-20 | 2014-08-20 10:43 | 2014-08-20 11:09 | GOODMAN - GPG1336045M41AC | 85 | -5 | Yes | Yes | 26.4 | 21.3 | 5.1 | F6CBC5648C6C4585B6BBA330239D5B5B |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
W Sacramento | CA | 95691-2543 |  | 2014-08-11 | 2014-08-11 16:58 | 2014-08-11 18:37 | GOODMAN - GPG1330070M41BA | 78 | 6 | Yes | Yes | 18.9 | 19.4 | -0.5 | E330A1370287467390E802DFBFB97382 |  | R22 | Non-TXV |  | 7.692% | 0.92308 | 14.78% | [5 empty] | Non-TXV | 7.692%
Bakersfield | CA | 93312-3351 |  | 2014-09-18 | 2014-09-18 17:41 | 2014-09-18 17:41 | UNITARY PRODUCTS GROUP - H2RD036S06A | 96 | 0 | Yes | Yes | 25 | 20.9 | 4.1 | 46C7878340C64D83884C41E077017199 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3351 |  | 2014-09-18 | 2014-09-18 17:43 | 2014-09-18 17:43 | UNITARY PRODUCTS GROUP - H2RD036S06A | 96 | 0 | Yes | Yes | 21.2 | 21.4 | -0.2 | CE109E87A0E64F16952758C30ED2A5FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1435 |  | 2014-09-02 | 2014-09-02 13:15 | 2014-09-02 13:15 | CARRIER - 38CK036350 | 70 | 0 | Yes | Yes | 21.4 | 19.2 | 2.2 | D80B889022B24D39BEE6E96252C9FA07 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-2990 |  | 2014-08-01 | 2014-08-01 12:16 | 2014-08-01 12:16 | CARRIER - 38CKC042310 | 93 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 3DA09935CB1A45C6BB75A44B7FED002C | Actual Subcooling cannot be negative. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5108 |  | 2014-08-14 | 2014-08-14 10:34 | 2014-08-14 20:43 | TRANE - 4TTM3036A1000AA | 69 | 5.3 | Yes | Yes | 17.8 | 18.2 | -0.4 | 0CA59DFF39BC44458710F1D527341967 |  | R410A | Non-TXV |  | 7.681% | 0.92319 | 14.76% | [5 empty] | Non-TXV | 7.681%
Bakersfield | CA | 93304-5905 |  | 2014-08-21 | 2014-08-21 11:00 | 2014-08-21 11:00 | ICP - PGAA42C1K4 | 70 | 0 | Yes | Yes | 25.1 | 22.8 | 2.3 | 831A30F061CB41F88AF560ACED99DE4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-4125 |  | 2014-08-19 | 2014-08-19 14:01 | 2014-08-19 14:27 | ARCOAIRE - PGF030K060A | 52 | 2.1 | Yes | Yes | 23.4 | 21.3 | 2.1 | B990E8517262453785B5FEB0E2067FC6 |  | R22 | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
Fresno | CA | 93701-1025 |  | 2014-08-19 | 2014-08-19 10:19 | 2014-08-19 10:40 | YORK - DAYAF036NO70C | 67 | -3.9 | Yes | Yes | 24.3 | 18.8 | 5.5 | 5B3680AB547A4817945C000512B49035 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Fresno | CA | 93726-1715 |  | 2014-08-27 | 2014-08-27 10:10 | 2014-08-27 10:40 | GOODMAN - CK3010 | 70 | -5.8 | Yes | Yes | 21.2 | 19.1 | 2.2 | 80802836508A4B51AEC6F06C31837C1E |  | R22 | Non-TXV |  | -8.286% | 1.0829 | 2.32% |  |  |  |  | Non-TXV |  |  | -8.286%
Pittsburg | CA | 94565-7903 |  | 2014-09-23 | 2014-09-23 09:12 | 2014-09-23 09:35 | CARRIER - 24ABA336A300 | 84 | 14.5 | Yes | Yes | 17.4 | 17.3 | 0.1 | 4F0E01923C5F474FA0AF3E91A3352474 |  | R410A | TXV |  | 17.26% | 0.82738 | 33.17% | [5 empty] | TXV | 17.26%
Bakersfield | CA | 93307-3589 |  | 2014-10-20 | 2014-10-20 14:04 | 2014-10-20 14:04 | YORK - D2NZ036N05606NXA | 112 | 0 | Yes | Yes | 19 | 19.1 | -0.1 | 92030CC52D964064AE00E8E4240811AD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-0000 |  | 2014-10-27 | 2014-10-27 12:42 | 2014-10-27 12:42 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 17.3 | 19.1 | -1.8 | AC79D46CB50844BBAC49C98CF16782BC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0343 |  | 2014-08-12 | 2014-08-12 13:20 | 2014-08-12 13:20 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 19.4 | 19.6 | -0.2 | 82DE8137D1FE48E3BD0C036A7981FA52 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7047 |  | 2014-09-18 | 2014-09-18 12:06 | 2014-09-18 12:06 | GOODMAN - GPG1336045M41AB | 85 | 0 | Yes | Yes | 22.7 | 19.3 | 3.4 | EAB2D274E27D4FB58F615131DAA55117 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2955 |  | 2014-09-19 | 2014-09-19 17:38 | 2014-09-19 17:38 | OTHER - H1RC036S06B | 98 | 0 | Yes | Yes | 33.9 | 21.3 | 12.6 | 521026511C4C45198DB54CFABC808EB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3221 |  | 2014-10-17 | 2014-10-17 12:55 | 2014-10-17 12:55 | LENNOX - ACT3-036 | 111 | 0 | Yes | Yes | 24.8 | 21.4 | 3.4 | BB2D8E97946942059272E9964430CD0D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3589 |  | 2014-09-14 | 2014-09-14 23:30 | 2014-09-14 23:34 | YORK - D2NZ036W05606NXA | 114 | 9.5 | Yes | Yes | 22.5 | 19.2 | 3.3 | 256D06D3841242A0BBF7355432ADAF9F |  | R410A | TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | TXV | 8.333%
Bakersfield | CA | 93306-6270 |  | 2014-09-12 | 2014-09-12 11:39 | 2014-09-12 11:39 | WEATHER KING - 13AJA30A01 | 98 | 0 | Yes | Yes | 14.8 | 18.5 | -3.7 | E6C9F8F3714443BA8B53509771245B10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4193 |  | 2014-09-16 | 2014-09-16 09:54 | 2014-09-16 09:54 | GOODMAN - PGP1360090M41DA | 91 | 0 | Yes | Yes | 22.6 | 19.1 | 3.5 | 4B3CC257DCBF4A54A9E82906E3C7AFCC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1414 |  | 2014-10-08 | 2014-10-08 23:21 | 2014-10-08 23:39 | OTHER - UNK | 24 | 4.6 | Yes | Yes | 17.5 | 19.9 | -2.4 | 30594EA6F1FB4334B6377DF50E336979 |  | R22 | Non-TXV |  | 19.17% | 0.80833 | 36.83% | [5 empty] | Non-TXV | 19.17%
Fresno | CA | 93703-4005 |  | 2014-08-19 | 2014-08-19 13:21 | 2014-08-19 13:42 | YORK - D5YS024N04506A | 70 | 3.2 | Yes | Yes | 25.3 | 19.5 | 5.8 | 7DB127EC77EC4EA28173BDD91DAE6B45 |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Suisun City | CA | 94585-1738 |  | 2014-09-30 | 2014-09-30 08:53 | 2014-09-30 08:53 | - | 85 | 0 | Yes | Yes | 12.7 | 15.2 | -2.5 | F618C1C6AFB94A0987B80CBC6E98A459 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3847 |  | 2014-08-28 | 2014-08-28 14:58 | 2014-08-28 15:35 | GOODMAN - CL1361C | 40 | 1.3 | Yes | Yes | 20.9 | 20.6 | 0.3 | 6B5A07B58B444970A9A13F26A9EBD7AA |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
San Jose | CA | 95120-4033 |  | 2014-08-05 | 2014-08-05 10:02 | 2014-08-05 10:23 | OTHER - TTR060D100A0 | 131 | 11.3 | Yes | Yes | 23.1 | 18 | 5.1 | C87CF6A46E0D49E4A43FAE11C2E1A2FB |  | R22 | Non-TXV |  | 8.626% | 0.91374 | 16.58% | [5 empty] | Non-TXV | 8.626%
Fresno | CA | 93722-5361 |  | 2014-08-08 | 2014-08-08 16:52 | 2014-08-08 17:13 | CARRIER - 48SS030040321 | 56 | 2.3 | Yes | Yes | 25.9 | 21.5 | 4.4 | 6BAAA1EEAA87449EBD2C03B4AC4943FD |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Suisun City | CA | 94585-1816 |  | 2014-10-01 | 2014-10-01 10:11 | 2014-10-03 07:58 | BRYANT - GCGD36S41S3A | 73 | -6.9 | Yes | Yes | 18 | 16.3 | 1.7 | 378B6333CFA04700B9FDD4F27EF4CFD0 |  | R22 | Non-TXV |  | -9.452% | 1.0945 | 2.647% |  |  |  |  | Non-TXV |  |  | -9.452%
Bakersfield | CA | 93304-4717 |  | 2014-08-04 | 2014-08-04 10:14 | 2014-08-04 10:14 | UNITARY PRODUCTS GROUP - D1NP048NO6506A | 132 | 0 | Yes | Yes | 18 | 20.8 | -2.8 | 6409A8CBB775484BB4128205A940F4CE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2796 |  | 2014-10-07 | 2014-10-07 15:00 | 2014-10-07 15:00 | RHEEM - RAHE060JAS | 176 | 0 | Yes | Yes | 24.1 | 19.8 | 4.3 | 72FCE1DDAD5F4EDDA88D1E0C4F416712 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2796 |  | 2014-10-07 | 2014-10-07 15:23 | 2014-10-07 15:23 | RHEEM - RAHE060JAS | 176 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 8D7DEB3229DA4099B5BC89C1ED870092 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2404 |  | 2014-08-07 | 2014-08-07 13:34 | 2014-08-07 13:34 | RHEEM - RRNLB036JK06X | 93 | 0 | Yes | Yes | 20.7 | 16.6 | 4.1 | 8354F67BCED2418C95D09C044EC0C9DE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2611 |  | 2014-08-22 | 2014-08-22 13:14 | 2014-08-22 13:34 | LENNOX - 12GCS036X75GPB | 110 | 4.2 | Yes | Yes | 23.9 | 21.7 | 2.2 | 945E14A4ED7946E9A1F74DDA6E119014 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Fairfield | CA | 94533-4200 |  | 2014-08-05 | 2014-08-05 12:04 | 2014-08-05 14:19 | - | 85 | 3 | Yes | Yes | 16.9 | 18.7 | -1.8 | 1C89E3EB42FE44A99408B208575B4584 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93312-5599 |  | 2014-10-20 | 2014-10-20 14:38 | 2014-10-20 14:38 | GOODMAN - CK42-1A | 86 | 0 | Yes | Yes | 21 | 21 | 0 | F64481AACCC54FA7A83E8706D032D2A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4857 |  | 2014-08-06 | 2014-08-06 13:07 | 2014-08-06 22:13 | TRANE - 2TTR2036A1000AA | 96 | -9 | Yes | Yes | 15.2 | 18.1 | -2.9 | 7AC37D2D93ED43E9A340DA2D3C6F4618 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Suisun City | CA | 94585-3724 |  | 2014-08-08 | 2014-08-08 14:30 | 2014-08-08 14:30 | PAYNE - 591ANX04800ACAA | 128 | 0 | Yes | Yes | 17 | 18.4 | -1.4 | 8C57ECD8EB3C49328275D2DF71AD0598 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0403 |  | 2014-08-22 | 2014-08-22 10:00 | 2014-08-22 10:28 | TRANE - YCY024F1L0BD | 72 | 3.3 | Yes | Yes | 20.8 | 19.8 | 1 | 069A3DBE1B664073B58D675E801DA5F2 |  | R22 | Non-TXV |  | 4.583% | 0.95417 | 8.808% | [5 empty] | Non-TXV | 4.583%
Fresno | CA | 93711-0403 |  | 2014-08-22 | 2014-08-22 10:31 | 2014-08-22 11:07 | TRANE - YCX036F1M0BC | 118 | 12.8 | Yes | Yes | 21.6 | 20.4 | 1.2 | 374ABE1E7777463FAAFC7DC194D6FF60 |  | R22 | Non-TXV |  | 10.85% | 0.89153 | 20.85% | [5 empty] | Non-TXV | 10.85%
Dixon | CA | 95620-3112 |  | 2014-08-15 | 2014-08-15 13:16 | 2014-08-15 13:54 | RHEEM - RAMB-042JAZ | 97 | 6 | Yes | Yes | 23.8 | 20.4 | 3.4 | 537A98B4FCE14CE081F4A4C6EF3F2E50 |  | R22 | Non-TXV |  | 6.186% | 0.93814 | 11.89% | [5 empty] | Non-TXV | 6.186%
Bakersfield | CA | 93304-2408 |  | 2014-08-04 | 2014-08-04 11:14 | 2014-08-04 11:14 | PAYNE - PY3GNAA30040NA | 98 | 0 | Yes | Yes | 25.1 | 21.4 | 3.7 | 7E4A26F6AAB44A20B8F58EC1C98CADCF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2413 |  | 2014-08-21 | 2014-08-21 14:05 | 2014-08-21 14:30 | GOODMAN - GPG13300701BB | 77 | 2.8 | Yes | Yes | 17.6 | 19.9 | -2.3 | 2E27A529B6314FA58DCC78A33230A7FA |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Fresno | CA | 93702-4629 |  | 2014-08-05 | 2014-08-05 10:20 | 2014-08-05 10:39 | OTHER - WPG3364060LKC1 | 102 | 4.1 | Yes | Yes | 22.4 | 18.7 | 3.7 | 066DF6B9B49B4EDFAB4AABD3BA24DFF8 |  | R410A | Non-TXV |  | 4.02% | 0.9598 | 7.725% | [5 empty] | Non-TXV | 4.02%
Bakersfield | CA | 93306-2637 |  | 2014-09-09 | 2014-09-09 17:50 | 2014-09-09 17:51 | TRANE - YCY036G1M0AC | 129 | 6.5 | Yes | Yes | 27.8 | 23.1 | 4.7 | C7C59A45C3A8444E818064EA8C7A55B4 |  | R22 | TXV |  | 5.039% | 0.94961 | 9.683% | [5 empty] | TXV | 5.039%
Bakersfield | CA | 93307-5174 |  | 2014-09-11 | 2014-09-11 17:51 | 2014-09-11 17:54 | BRYANT - 585FJW030050A6F | 58 | 5.9 | Yes | Yes | 24.3 | 20.9 | 3.4 | 317C1F455BD14DA6BED6677106EB2255 |  | R22 | Non-TXV |  | 10.17% | 0.89828 | 19.55% | [5 empty] | Non-TXV | 10.17%
Fresno | CA | 93728-2013 |  | 2014-08-21 | 2014-08-21 08:57 | 2014-08-21 09:32 | HEIL - PGME36080E | 140 | 5.6 | Yes | Yes | 21.6 | 19.3 | 2.3 | 1E8CA165B0A443EDA6A2495D87657821 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
San Jose | CA | 95133-2034 |  | 2014-08-01 | 2014-08-01 13:53 | 2014-08-01 14:36 | TRANE - TTR048C1000 | 114 | 3.4 | Yes | Yes | 19.2 | 15.2 | 4 | DC6E42FF2D3D4EA4A7D7A2F62890F3F6 |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Fresno | CA | 93705-3221 |  | 2014-08-22 | 2014-08-22 17:24 | 2014-08-22 18:51 | DAY & NIGHT - 588ANW036060ADAF | 70 | 3.4 | Yes | Yes | 20.6 | 20.9 | -0.3 | EBD6260EDAC34C869F36F7F732BB0C61 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Fresno | CA | 93726-3304 |  | 2014-08-11 | 2014-08-11 14:23 | 2014-08-11 14:59 | OTHER - HAC248AKA1 | 148 | 6.4 | Yes | Yes | 21.5 | 20.4 | 1.1 | 4DCB907B477E48CC8DA6AD574F998D2F |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
W Sacramento | CA | 95691-2325 |  | 2014-09-04 | 2014-09-04 09:28 | 2014-09-04 09:56 | YORK - D1NA030N05606A | 72 | 4.4 | Yes | Yes | 17.1 | 19.6 | -2.5 | F7668AC504EE4CDDB512FB741656EE4B |  | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Suisun City | CA | 94585-2749 |  | 2014-10-01 | 2014-10-01 10:41 | 2014-10-03 07:58 | CARRIER - 38CKC030300 | 85 | 7.5 | Yes | Yes | 12 | 14.3 | -2.3 | 2BBED6009D19454EB922BA71E9CFBF12 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Bakersfield | CA | 93312-4426 |  | 2014-08-15 | 2014-08-15 12:01 | 2014-08-15 12:01 | RHEEM - UKN | 90 | 0 | Yes | Yes | 23.5 | 18.6 | 5 | 757C603442A146AA8F544702AF903708 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6423 |  | 2014-10-17 | 2014-10-17 11:34 | 2014-10-17 11:54 | CARRIER - 24ANB736A310 | 148 | 25.1 | Yes | Yes | 23.6 | 21.5 | 2.1 | F53995D5A4824F18A02548C592ABC053 |  | R410A | TXV |  | 16.96% | 0.83041 | 32.59% | [5 empty] | TXV | 16.96%
Bakersfield | CA | 93312-2217 |  | 2014-08-15 | 2014-08-15 14:04 | 2014-08-15 14:04 | UNITARY PRODUCTS GROUP - H1RC036S06D | 98 | 0 | Yes | Yes | 19.2 | 21.9 | -2.7 | 28B679D3A24F41C088C94D99A5841BF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5815 |  | 2014-08-15 | 2014-08-15 11:11 | 2014-08-15 11:11 | OTHER - FS5D-036KA | 110 | 0 | Yes | Yes | 21.3 | 21.8 | -0.5 | 70B411AC2E004A7097F42CBE391EFF85 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4613 |  | 2014-08-13 | 2014-08-13 14:26 | 2014-08-13 14:26 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 26.4 | 20.4 | 6 | 36BA3BAA805B4728A3355B9B6ACCB32A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3429 |  | 2014-08-12 | 2014-08-12 09:09 | 2014-08-12 09:29 | CARRIER - 585HJ030040 | 68 | 3.1 | Yes | Yes | 23.5 | 19.9 | 3.7 | 35D3B7A97C644F9ABCBECD34F57A455F |  | R22 | Non-TXV |  | 4.559% | 0.95441 | 8.761% | [5 empty] | Non-TXV | 4.559%
Antioch | CA | 94509-5526 |  | 2014-10-16 | 2014-10-16 12:17 | 2014-10-16 12:17 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 22.5 | 20.7 | 1.8 | 646FE9B4F5404561AA9EF65D6A91A085 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1408 |  | 2014-08-12 | 2014-08-12 14:07 | 2014-08-12 14:27 | PAYNE - 563CN036B | 114 | 7.6 | Yes | Yes | 20.9 | 20.6 | 0.3 | 8A1E325D3A4141278F4ECCB14856D3F3 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Fresno | CA | 93710-7020 |  | 2014-08-13 | 2014-08-13 10:31 | 2014-08-13 10:54 | DAY & NIGHT - UNK | 76 | 5.7 | Yes | Yes | 25.4 | 21 | 4.5 | C11B62B629B9496690CE8A7F927B7439 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Bakersfield | CA | 93313-2221 |  | 2014-10-04 | 2014-10-04 19:43 | 2014-10-04 19:45 | RHEEM - RRA-C048JK10X | 97 | 11.2 | Yes | Yes | 21.8 | 20.4 | 1.4 | E2D4E9FC8EBF42BB88A4632E96B62268 |  | R22 | TXV |  | 11.55% | 0.88454 | 22.19% | [5 empty] | TXV | 11.55%
Antioch | CA | 94509-5435 |  | 2014-11-13 | 2014-11-13 12:14 | 2014-11-13 12:34 | RHEEM - RAKA-048JAZ | 103 | 4.1 | Yes | Yes | 18.1 | 20.4 | -2.3 | EB233572E2A54A72AC278145AFE6D7A5 |  | R22 | Non-TXV |  | 3.981% | 0.96019 | 7.65% | [5 empty] | Non-TXV | 3.981%
Concord | CA | 94520-4702 |  | 2014-09-02 | 2014-09-02 14:48 | 2014-09-02 14:48 | GOODMAN - CPLE48-1 | 143 | 0 | Yes | Yes | 19 | 21 | -2 | 8BDEF076995D42A19D2F4AC720BF6BDD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2223 |  | 2014-11-11 | 2014-11-11 13:06 | 2014-11-11 13:06 | RHEEM - RRNAC048JK10X | 97 | 0 | Yes | Yes | 24.2 | 20.4 | 3.8 | C932C878832E4484BCCBB9F9777A8CBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3667 |  | 2014-09-15 | 2014-09-15 09:17 | 2014-09-15 09:36 | GIBSON - 55AW24106 | 85 | 3.7 | Yes | Yes | 22 | 19.9 | 2.1 | 72577D4A10C44D80A10EA039C64D6906 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Bakersfield | CA | 93313-5027 |  | 2014-08-29 | 2014-08-29 11:46 | 2014-08-29 11:46 | AIRE-FLO - 2AC13B60P-1A | 225.6 | 0 | Yes | Yes | 19 | 21.8 | -2.8 | F2453E602735437997077209E9C781F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5030 |  | 2014-09-23 | 2014-09-23 09:04 | 2014-09-23 09:04 | UNITARY PRODUCTS GROUP - AC060X1223A | 147 | 0 | Yes | Yes | 19.2 | 21.7 | -2.5 | 0B869223D4374DEF9A8EC0304EB56E9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9396 |  | 2014-08-14 | 2014-08-14 09:13 | 2014-08-14 09:30 | YORK - H1DE042506B | 99 | 3.6 | Yes | Yes | 21 | 19.7 | 1.4 | 0572A1E97303446190688877F6A34B24 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Antioch | CA | 94531-8151 |  | 2014-10-20 | 2014-10-20 10:57 | 2014-10-20 10:57 | OTHER - 561AJ048-C | 108 | 0 | Yes | Yes | 20.8 | 18.8 | 2 | A8AEC5C9F1EA41DBB7CF747D922F6FD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4967 |  | 2014-08-26 | 2014-08-26 11:04 | 2014-08-26 11:28 | CARRIER - 3405E288000 | 54 | 3 | Yes | Yes | 17.3 | 19.9 | -2.6 | 340A69AE8D994AFEA0E823299D5E4EE7 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Bakersfield | CA | 93307-9322 |  | 2014-10-20 | 2014-10-20 10:38 | 2014-10-20 10:38 | CARRIER - UNK | 123 | 0 | Yes | Yes | 15.2 | 18.2 | -3 | F609816FD1114E05BA7C40C9C5FD2D5B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4038 |  | 2014-09-24 | 2014-09-24 11:57 | 2014-09-24 11:57 | NORDYNE - DS3BA-030KA | 68 | 0 | Yes | Yes | 18.3 | 21.3 | -3 | B123C40F32DA45138FC5E8B100E4C6EE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6772 |  | 2014-09-11 | 2014-09-11 13:43 | 2014-09-11 13:43 | CARRIER - 24ACR336A300 | 106 | 0 | Yes | Yes | 13.8 | 16.4 | -2.6 | CEC47E0FDA924BD3B83775B8687C91AB |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8350 |  | 2014-10-28 | 2014-10-28 09:44 | 2014-10-28 10:11 | CARRIER - 38CKB048300 | 105 | 13.3 | Yes | Yes | 17 | 19.1 | -2.1 | 185DAF8F2CB748C99F63364FAB10BBDA |  | R22 | TXV |  | 12.67% | 0.87333 | 24.34% | [5 empty] | TXV | 12.67%
Bakersfield | CA | 93309-4529 |  | 2014-10-01 | 2014-10-01 15:53 | 2014-10-01 16:48 | OTHER - UNK | 136 | 18.9 | Yes | Yes | 25.9 | 20.8 | 5.1 | 17C8B0C1AD8343B593210D8127975200 |  | R22 | Non-TXV |  | 13.9% | 0.86103 | 26.71% | [5 empty] | Non-TXV | 13.9%
Bakersfield | CA | 93309-5565 |  | 2014-11-19 | 2014-11-19 13:19 | 2014-11-19 13:19 | OTHER - 4YCC3024A1064AA | 93 | 0 | Yes | Yes | 20.6 | 19.3 | 1.3 | D6866A41F99D4B9899F7B67D9F7921A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4217 |  | 2014-08-12 | 2014-08-12 11:19 | 2014-08-12 20:35 | RHEEM - RAMB-048JBZ | 162 | 6.7 | Yes | Yes | 17 | 17.9 | -0.9 | AA0CAD2DD4C24E12A9A260FD92A10001 |  | R22 | Non-TXV |  | 4.136% | 0.95864 | 7.948% | [5 empty] | Non-TXV | 4.136%
Fresno | CA | 93726-3534 |  | 2014-08-11 | 2014-08-11 15:05 | 2014-08-11 15:36 | CARRIER - 585CJ042100 | 104 | 4.1 | Yes | Yes | 25.8 | 21 | 4.8 | DF9668BABFA442A0933A9470794F7D51 |  | R22 | Non-TXV |  | 3.942% | 0.96058 | 7.576% | [5 empty] | Non-TXV | 3.942%
Bakersfield | CA | 93312-4961 |  | 2014-10-13 | 2014-10-13 15:26 | 2014-10-13 15:26 | CARRIER - 38CKB036330 | 82 | 0 | Yes | Yes | 22.9 | 20.8 | 2.1 | DE74DE3EDA7E40648A6FF03B09184215 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3152 |  | 2014-08-04 | 2014-08-04 12:05 | 2014-08-04 12:05 | CARRIER - 38CKC036350 | 70 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 90A5E48BCC104681BB44469655AA77BB | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0253 |  | 2014-08-22 | 2014-08-22 14:09 | 2014-08-22 14:28 | PAYNE - 585AJ036A | 92 | 16.6 | Yes | Yes | 21.6 | 22.3 | -0.7 | E70F19E1506C4A4F81CFE93C40366328 |  | R22 | Non-TXV |  | 18.04% | 0.81957 | 34.68% | [5 empty] | Non-TXV | 18.04%
Dixon | CA | 95620-9725 |  | 2014-08-15 | 2014-08-15 14:19 | 2014-08-15 14:58 | FRESCHI - RRGG-05N25JKR | 39 | 8.4 | Yes | Yes | 20.8 | 19.3 | 1.5 | B1C9DA97B789430DA60FA582C8C1789E |  | R22 | Non-TXV |  | 21.54% | 0.78462 | 41.39% | [5 empty] | Non-TXV | 21.54%
Martinez | CA | 94553-2742 |  | 2014-08-27 | 2014-08-27 15:24 | 2014-08-27 15:24 | AMANA - G8C130361DF | 120 | 0 | Yes | Yes | 23.3 | 20.1 | 3.2 | DA2889FE176D4FFEB4572E5B60A3F546 |  | R22 | TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-9761 |  | 2014-09-21 | 2014-09-21 18:42 | 2014-09-21 18:44 | TEMPSTAR - PGAA29C1K1 | 74 | 0 | Yes | Yes | 27.3 | 19.9 | 7.4 | 08EC046DBE5C4A38A9957C55DE191AB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4573 |  | 2014-09-17 | 2014-09-17 09:32 | 2014-09-17 09:32 | GOODMAN - GPG1348070M41EA | 99 | 0 | Yes | Yes | 25.8 | 20.1 | 5.7 | 1B426CDFD3F04B079604F33F1557F9A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-2603 |  | 2014-09-10 | 2014-09-10 08:58 | 2014-09-10 09:15 | TRANE - TTR048D100A1 | 82 | -7.7 | Yes | Yes | 16.4 | 17.7 | -1.3 | 1B81EC5B45274CDBA9830A2C406C5B4B |  | R22 | Non-TXV |  | -9.39% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.39%
Concord | CA | 94520-4336 |  | 2014-09-02 | 2014-09-02 15:58 | 2014-09-02 16:22 | OTHER - 561AJX030000ABAA | 68 | 7.6 | Yes | Yes | 19.1 | 20.4 | -1.3 | CD5A2EB32EDE4D97ABA68166B1CE31D7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Vacaville | CA | 95687-3916 |  | 2014-09-10 | 2014-09-10 14:03 | 2014-09-10 14:32 | CARRIER - 38CKC018340 | 51 | 3.1 | Yes | Yes | 24.3 | 20.4 | 3.9 | 564F32281A2649E4BA08FCCA040C63FE |  | R22 | Non-TXV |  | 6.078% | 0.93922 | 11.68% | [5 empty] | Non-TXV | 6.078%
Bakersfield | CA | 93306-5921 |  | 2014-09-12 | 2014-09-12 12:40 | 2014-09-12 12:40 | RHEEM - RRAB08E48JR | 106 | 0 | Yes | Yes | 24.9 | 23.5 | 1.4 | 220FB91DC8AF4BE4BC0EA6BCE0C6AA6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5921 |  | 2014-09-12 | 2014-09-12 13:04 | 2014-09-12 13:04 | RHEEM - UNK | 82 | 0 | Yes | Yes | 16.4 | 15 | 1.4 | DDD86A5BE38C45519B783B6097330E67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4100 |  | 2014-09-09 | 2014-09-09 09:50 | 2014-09-09 10:28 | YORK - F024N045A | 100 | -9.4 | Yes | Yes | 25 | 19.7 | 5.3 | 49AEBD1F09224565BE6AC9151B7E7FBB |  | R22 | Non-TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.4%
Bakersfield | CA | 93306-7930 |  | 2014-10-12 | 2014-10-12 15:33 | 2014-10-12 15:34 | WEATHER KING - 13AJA42A01 | 121 | 5.9 | Yes | Yes | 19.3 | 20.3 | -1 | 6A6B3F70671E43E4A1D272E67D19B903 |  | R22 | Non-TXV |  | 4.876% | 0.95124 | 9.371% | [5 empty] | Non-TXV | 4.876%
Fremont | CA | 94536-3582 |  | 2014-08-20 | 2014-08-20 09:32 | 2014-08-20 09:52 | CARRIER - 38CKB036320 | 141 | -7.6 | Yes | Yes | 18.2 | 17.5 | 0.7 | 8C537A3CD46845F9841D21FC6333E49A |  | R22 | TXV |  | -5.39% | 1.0539 | 1.509% |  |  |  |  | TXV |  |  | -5.39%
Antioch | CA | 94509-3602 |  | 2014-10-27 | 2014-10-27 09:37 | 2014-10-27 09:37 | PAYNE - PA16NA036 | 109 | 0 | Yes | Yes | 19.2 | 19.1 | 0.1 | 5243ADCCD22F4AD1A3D9583EF7FA7223 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4131 |  | 2014-08-05 | 2014-08-05 11:07 | 2014-08-05 11:33 | LENNOX - 12C036X753PA | 110 | 4.2 | Yes | Yes | 25.1 | 20.4 | 4.7 | 2D1E4516361F49A7A69A3C499E8AE715 |  | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Antioch | CA | 94509-4423 |  | 2014-11-13 | 2014-11-13 13:00 | 2014-11-13 13:40 | RHEEM - UAKA-037JAZ | 78 | 3.9 | Yes | Yes | 17.5 | 20.4 | -2.9 | C75BE35A8F404AC6B7F3AB50DFEBCBEF |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93307-7194 |  | 2014-09-12 | 2014-09-12 20:59 | 2014-09-12 21:02 | DUCANE - SG12B300050 | 87 | 10.1 | Yes | Yes | 18.8 | 21.5 | -2.7 | 02E109D1FC844EAE90484E9E8FD23B74 |  | R22 | TXV |  | 11.61% | 0.88391 | 22.31% | [5 empty] | TXV | 11.61%
Antioch | CA | 94509-5937 |  | 2014-10-29 | 2014-10-29 09:28 | 2014-10-29 09:48 | RHEEM - 13AW36A01 | 90 | -9 | Yes | Yes | 23.6 | 20.3 | 3.3 | B90E4CF3767B4356BEB673A86B2530EA |  | R410A | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Antioch | CA | 94509-2960 |  | 2014-11-13 | 2014-11-13 18:07 | 2014-11-13 18:28 | PAYNE - PH13NR024-K | 70 | 3.7 | Yes | Yes | 17.6 | 20.2 | -2.5 | 43AFEC40A2BF4007B38F72D5010DABFE |  | R22 | Non-TXV |  | 5.286% | 0.94714 | 10.16% | [5 empty] | Non-TXV | 5.286%
Bakersfield | CA | 93307-7194 |  | 2014-10-20 | 2014-10-20 09:50 | 2014-10-20 09:50 | OTHER - SG12B30050 | 87 | 0 | Yes | Yes | 24 | 19.5 | 4.5 | D78A44F01153479DA291EA2EC3D4064A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9771 |  | 2014-10-16 | 2014-10-16 17:03 | 2014-10-16 17:03 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 23.9 | 20.4 | 3.5 | DD5805F42D4F45C38416A2FCF97FF771 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5429 |  | 2014-08-13 | 2014-08-13 16:17 | 2014-08-13 16:17 | DAY & NIGHT - 588ANW036060ADAF | 68 | 0 | Yes | Yes | 20.5 | 20.7 | -0.2 | E38192BB2E9C46F2AE8A7B20251DE74A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-8596 |  | 2014-08-20 | 2014-08-20 15:39 | 2014-08-20 15:57 | GOODMAN - CKL361D | 72 | 12.9 | Yes | Yes | 21.3 | 21.9 | -0.6 | 8127EBE94BC44E4BBD0CB6448B51A6E9 |  | R22 | Non-TXV |  | 17.92% | 0.82083 | 34.43% | [5 empty] | Non-TXV | 17.92%
Clovis | CA | 93611-8596 |  | 2014-08-20 | 2014-08-20 16:01 | 2014-08-20 16:01 | GOODMAN - CKLL601 | 115 | 0 | Yes | Yes | 20.5 | 21.8 | -1.3 | 65FB405104D04D79A49919204080301E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4302 |  | 2014-08-25 | 2014-08-25 14:18 | 2014-08-25 14:18 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 25 | 19.2 | 5.8 | 9475AD2B8D1B48FC9D14BB3D939176F7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1145 |  | 2014-08-27 | 2014-08-27 09:18 | 2014-08-27 09:18 | RHEEM - RRNLB024JK06X | 78 | 0 | Yes | Yes | 20.4 | 18.9 | 1.5 | 8FDBB7660DE843CAADF34C3EA9E07E72 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9650 |  | 2014-08-12 | 2014-08-12 12:50 | 2014-08-12 20:36 | YORK - D2EG060N079066D | 85 | 2.8 | Yes | Yes | 15.3 | 16.8 | -1.5 | 76414AF205F84C5691266607F6DA6883 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Clovis | CA | 93612-4302 |  | 2014-08-25 | 2014-08-25 15:01 | 2014-08-25 15:42 | RHEEM - RRKAA042JK08X | 69 | 2.8 | Yes | Yes | 21.2 | 22.1 | -0.9 | 1A7052D314C14A05814599CE654D53C4 |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Bakersfield | CA | 93312-5462 |  | 2014-10-14 | 2014-10-14 16:18 | 2014-10-14 16:36 | OTHER - 366KC0848 | 85 | -6 | Yes | Yes | 18 | 20.8 | -2.8 | 36DFD76DC4DB4A80AC7D170CA963D38E |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Bakersfield | CA | 93307-3515 |  | 2014-09-09 | 2014-09-09 14:07 | 2014-09-09 14:07 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 17.8 | 21.5 | -3.7 | 14A82BB040A349A59974695EBFE1F6D1 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7529 |  | 2014-08-14 | 2014-08-14 10:41 | 2014-08-14 11:04 | PAYNE - 588ANW036080ABAF | 70 | 15.9 | Yes | Yes | 22.4 | 21.4 | 1 | BCB95B6E01BB45EAAA40E3F05F55DF0A |  | R22 | Non-TXV |  | 22.71% | 0.77286 | 43.65% | [5 empty] | Non-TXV | 22.71%
Clovis | CA | 93612-4302 |  | 2014-08-25 | 2014-08-25 15:47 | 2014-08-25 16:21 | GOODMAN - GPG1336070M41AB | 85 | 24.8 | Yes | Yes | 24.1 | 21.4 | 2.7 | 12F60723DCB149B299CA454466C19C63 |  | R410A | Non-TXV |  | 29.18% | 0.70824 | 56.07% | [5 empty] | Non-TXV | 29.18%
Bakersfield | CA | 93304-7097 |  | 2014-08-04 | 2014-08-04 09:41 | 2014-08-04 09:41 | BDP - 585CJ036075 | 84 | 0 | Yes | Yes | 19.4 | 19 | 0.4 | E755FCD07EDE4D33953AA5DFBB1D2F7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3908 |  | 2014-08-19 | 2014-08-19 12:30 | 2014-08-19 12:59 | TEMPSTAR - PGA030D1KA | 78 | 9.9 | Yes | Yes | 25.1 | 21.8 | 3.4 | 2FFEBC055D7C47AE8C0D566173CB48BC |  | R22 | Non-TXV |  | 12.69% | 0.87308 | 24.39% | [5 empty] | Non-TXV | 12.69%
Shafter | CA | 93263-3537 |  | 2014-09-21 | 2014-09-21 18:25 | 2014-09-21 18:28 | GOODMAN - GPG10420701A | 88 | 15.5 | Yes | Yes | 22.1 | 21.5 | 0.6 | D0655E64481F4B8CA09EDEFF9FE38C1A |  | R22 | Non-TXV |  | 17.61% | 0.82386 | 33.85% | [5 empty] | Non-TXV | 17.61%
Bakersfield | CA | 93312-5108 |  | 2014-08-21 | 2014-08-21 14:51 | 2014-08-21 14:51 | RUUD - URGG-10E61JKR | 136 | 0 | Yes | Yes | 27.4 | 21.6 | 5.8 | BB04ECD771A64122B8400ACD5F49C435 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6435 |  | 2014-08-15 | 2014-08-15 10:03 | 2014-08-15 10:03 | RHEEM - 13AJA48A01757 | 90 | 0 | Yes | Yes | 19.4 | 20.2 | -0.8 | B47D874349F14334AA437D508071075F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5053 |  | 2014-08-27 | 2014-08-27 13:09 | 2014-08-27 14:10 | GOODMAN - GPG1324045M41AD | 80 | 3.2 | Yes | Yes | 23.3 | 21.5 | 1.8 | 771C293C7F1749E8B83D3FABE539C6FA |  | R410A | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Woodland | CA | 95695-3793 |  | 2014-08-06 | 2014-08-06 13:02 | 2014-08-06 13:36 | JANITROL - | 72 | 2.3 | Yes | Yes | 18 | 19.3 | -1.3 | DAB9B01D060C48318285DCBF1A6ACA03 |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Clovis | CA | 93612-4247 |  | 2014-08-25 | 2014-08-25 13:29 | 2014-08-25 13:52 | TEMPSTAR - PGF336060K01 | 115 | 6.5 | Yes | Yes | 21.3 | 20.4 | 0.9 | 4304F1B1D4DF422D80932C3D760A5DEA |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Bakersfield | CA | 93311-1820 |  | 2014-10-02 | 2014-10-02 14:31 | 2014-10-02 14:31 | HEIL - PGF348080K01A1 | 208 | 0 | Yes | Yes | 21.6 | 22.2 | -0.5 | 47D138D5B9664941908C4DFD97ACF927 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4581 |  | 2014-09-23 | 2014-09-23 11:00 | 2014-09-23 11:00 | OTHER - EAFF-049JAZ | 163 | 0 | Yes | Yes | 19.9 | 22.6 | -2.7 | 1C67F3D9D5434C9CBE98A25D023C7196 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8910 |  | 2014-08-14 | 2014-08-14 15:47 | 2014-08-14 16:06 | RHEEM - RAND060JBZ | 176 | 9.2 | Yes | Yes | 22.5 | 20.1 | 2.4 | D4D50A18264F4D07ACA20A4C8967AE13 |  | R22 | Non-TXV |  | 5.227% | 0.94773 | 10.05% | [5 empty] | Non-TXV | 5.227%
Bakersfield | CA | 93313-4345 |  | 2014-10-04 | 2014-10-04 18:34 | 2014-10-04 18:50 | OTHER - UNK | 85 | 3.8 | Yes | Yes | 23.3 | 22.2 | 1.1 | DD7DF0C34EB64EF2935EBC35C10BB849 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Bakersfield | CA | 93313-6074 |  | 2014-10-17 | 2014-10-17 10:31 | 2014-10-17 10:31 | OTHER - GPF036K060A | 71 | 0 | Yes | Yes | 20.6 | 19.5 | 1.1 | 30DBE48A33AF44689A3DDB8BC056B82B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3018 |  | 2014-08-11 | 2014-08-11 10:38 | 2014-08-11 11:09 | RHEEM - RRPLB042JK08Y | 112 | 5.9 | Yes | Yes | 23.6 | 20.4 | 3.2 | B3FEA012A31841CFAADA6CDFD99E64B9 |  | R410A | Non-TXV |  | 5.268% | 0.94732 | 10.12% | [5 empty] | Non-TXV | 5.268%
Fresno | CA | 93706-4624 |  | 2014-08-21 | 2014-08-21 18:32 | 2014-08-21 18:32 | OTHER - UNK | 68 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 97009865CA884C9AA323F1168503DC87 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2333 |  | 2014-09-27 | 2014-09-27 14:09 | 2014-09-27 14:09 | RHEEM - UNK | 190 | 0 | Yes | Yes | 16.4 | 20.7 | -4.3 | AE8CCB1A996D4836A996C82334C1CF3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2302 |  | 2014-09-23 | 2014-09-23 14:18 | 2014-09-23 14:18 | OTHER - UNK | 149 | 0 | Yes | Yes | 27.7 | 21.9 | 5.8 | FD9F59DDAF3D4F52BBA912F2240505DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1464 |  | 2014-08-25 | 2014-08-25 14:11 | 2014-08-25 14:11 | YORK - D2NP030N05606A | 73 | 0 | Yes | Yes | 23.5 | 23.5 | 0 | 8B9AFC6344D54A37A07F409049D16AC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4396 |  | 2014-08-22 | 2014-08-22 10:02 | 2014-08-22 10:02 | OTHER - EAFF-049JAZ | 163 | 0 | Yes | Yes | 21 | 23.1 | -2.1 | BF36D82A88BE45D1BB72B0B0386A0E31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1418 |  | 2014-08-21 | 2014-08-21 10:12 | 2014-08-21 10:36 | CARRIER - UNK | 68 | 3.3 | Yes | Yes | 23.8 | 19.8 | 4 | 9A4B162C6DE74CA2BDCBA2956F5DD2B0 |  | R22 | Non-TXV |  | 4.853% | 0.95147 | 9.326% | [5 empty] | Non-TXV | 4.853%
Fresno | CA | 93720-2444 |  | 2014-08-26 | 2014-08-26 12:47 | 2014-08-26 13:29 | INTERTHERM - BRCS0361BD | 63 | 2.1 | Yes | Yes | 22.3 | 21 | 1.3 | 77D4E2904BDF4E1F96151527610B8330 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Vacaville | CA | 95687-5522 |  | 2014-10-13 | 2014-10-13 12:54 | 2014-10-13 14:37 | CARRIER - 38BRCO24330 | 82 | 6.4 | Yes | Yes | 19.3 | 20.4 | -1.1 | F42C828694464668851407ADC7E53793 |  | R22 | Non-TXV |  | 7.805% | 0.92195 | 15% | [5 empty] | Non-TXV | 7.805%
Fresno | CA | 93702-3629 |  | 2014-08-05 | 2014-08-05 14:54 | 2014-08-05 15:16 | PAYNE - 585CJ036075 | 84 | 10.3 | Yes | Yes | 23.9 | 20.4 | 3.5 | 70F6D849AC7F4E3EADC9EF6A0F6286E2 |  | R22 | Non-TXV |  | 12.26% | 0.87738 | 23.56% | [5 empty] | Non-TXV | 12.26%
San Jose | CA | 95130-1216 |  | 2014-08-05 | 2014-08-05 12:46 | 2014-08-05 12:46 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 17.2 | 16.5 | 0.7 | FE27723C3E464D0CBEB67B25E9A285F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4160 |  | 2014-08-20 | 2014-08-20 11:41 | 2014-08-20 12:07 | TRANE - YCY048G1H0AC | 183 | 8 | Yes | Yes | 25.6 | 21 | 4.6 | B0C2EF05AAEC40E19F362A9487B5F83B |  | R22 | Non-TXV |  | 4.372% | 0.95628 | 8.401% | [5 empty] | Non-TXV | 4.372%
Clovis | CA | 93611-1482 |  | 2014-08-20 | 2014-08-20 09:57 | 2014-08-20 10:39 | RHEEM - RRMAA048JK10X | 117 | 6 | Yes | Yes | 22.2 | 21 | 1.2 | 6CD14EB5714A4C0A8A9FE8D9EBEC1002 |  | R22 | Non-TXV |  | 5.128% | 0.94872 | 9.855% | [5 empty] | Non-TXV | 5.128%
Fresno | CA | 93722-2271 |  | 2014-08-07 | 2014-08-07 15:13 | 2014-08-07 15:48 | OTHER - WCA3602GKR2 | 168 | 6.5 | Yes | Yes | 20.4 | 21.5 | -1.1 | 48C0F3BF28C44C7D9BA8A83780EE9EB3 |  | R22 | Non-TXV |  | 3.869% | 0.96131 | 7.435% | [5 empty] | Non-TXV | 3.869%
Bakersfield | CA | 93313-2223 |  | 2014-11-11 | 2014-11-11 12:35 | 2014-11-11 12:35 | RHEEM - RRNLB030JK06X | 76 | 0 | Yes | Yes | 15.9 | 18.7 | -2.8 | AB310C6636CD49EBBEA21332A2DF0E5B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6428 |  | 2014-08-14 | 2014-08-14 09:41 | 2014-08-14 10:13 | OTHER - 38BRB030300 | 105 | 4 | Yes | Yes | 22.4 | 20.1 | 2.3 | 30CE52DF50324F9BB2C88B6144DCDBF7 |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Bakersfield | CA | 93309-1158 |  | 2014-09-30 | 2014-09-30 14:13 | 2014-09-30 14:13 | GOODMAN - GPG13300451BB | 77 | 0 | Yes | Yes | 22.4 | 17.6 | 4.8 | 55EDF1071DBD4E34B09DC0B3A5802156 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6806 |  | 2014-08-14 | 2014-08-14 12:36 | 2014-08-14 13:09 | CARRIER - UNK | 102 | 29.6 | Yes | Yes | 20.8 | 20.4 | 0.4 | C598F598091B4B4FA6228558141403D5 |  | R22 | Non-TXV |  | 29.02% | 0.7098 | 55.77% | [5 empty] | Non-TXV | 29.02%
Fresno | CA | 93727-7102 |  | 2014-08-14 | 2014-08-14 11:34 | 2014-08-14 12:08 | YORK - D1NP042N06506A | 150 | 6.2 | Yes | Yes | 21.5 | 19.3 | 2.2 | 08093D5E1AE04708A93A28D22CC135DE |  | R22 | Non-TXV |  | 4.133% | 0.95867 | 7.943% | [5 empty] | Non-TXV | 4.133%
Fresno | CA | 93727-5674 |  | 2014-08-14 | 2014-08-14 13:42 | 2014-08-14 13:42 | OTHER - V85BD060KA | 160 | 29 | Yes | Yes | 6.9 | 20.4 | -13.5 | 42E51851F29349FCB787089032A950D2 | Add refrigerant: 29 oz | R22 | Non-TXV |  | 18.12% | 0.81875 | 34.83% | [5 empty] | Non-TXV | 18.12%
Concord | CA | 94521-3419 |  | 2014-09-03 | 2014-09-03 12:14 | 2014-09-03 12:14 | ICP - TCA036AKA5 | 80 | 0 | Yes | Yes | 20.4 | 18.8 | 1.7 | 5C4536FC6601490C8046AD4DD86F36CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6465 |  | 2014-08-14 | 2014-08-14 14:30 | 2014-08-14 14:52 | LENNOX - 12ACB364P | 103 | 10.8 | Yes | Yes | 21.3 | 20.2 | 1.1 | 2493F03B51854F4BA2FCA17CE4121DDD |  | R22 | Non-TXV |  | 10.49% | 0.89515 | 20.15% | [5 empty] | Non-TXV | 10.49%
Fresno | CA | 93722-4561 |  | 2014-08-08 | 2014-08-08 15:33 | 2014-08-08 15:59 | RHEEM - UNK | 76 | 12.8 | Yes | Yes | 23.7 | 21 | 2.7 | 1D6F7F8E310A42858D233CCD717FB3E2 |  | R22 | Non-TXV |  | 16.84% | 0.83158 | 32.37% | [5 empty] | Non-TXV | 16.84%
Suisun City | CA | 94585-2213 |  | 2014-09-29 | 2014-09-29 10:23 | 2014-09-30 07:52 | PAYNE - | 85 | 4.6 | Yes | Yes | 13.2 | 15 | -1.8 | 9CFA70B32BDA4F059D53EF4D2F517FB5 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Bakersfield | CA | 93313-2210 |  | 2014-11-11 | 2014-11-11 13:40 | 2014-11-11 13:40 | RHEEM - RRNAB042JK08X | 104 | 0 | Yes | Yes | 16.4 | 18.7 | -2.3 | 745D5025375240928E73D7321C64C831 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2416 |  | 2014-08-06 | 2014-08-06 12:36 | 2014-08-06 13:06 | YORK - DAYAF030N070C | 76 | -7.2 | Yes | Yes | 21.7 | 16.2 | 5.5 | 0B710C0587474350A2DFD9D80D6E2B0E |  | R22 | Non-TXV |  | -9.474% | 1.0947 | 2.653% |  |  |  |  | Non-TXV |  |  | -9.474%
San Jose | CA | 95116-3117 |  | 2014-08-05 | 2014-08-05 14:23 | 2014-08-05 22:08 | CARRIER - 561CJX036-D | 85 | 3.9 | Yes | Yes | 21.7 | 20.4 | 1.3 | F18827C4840946199736B60CEA8438E5 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Bakersfield | CA | 93309-5626 |  | 2014-10-08 | 2014-10-08 14:04 | 2014-10-08 14:04 | OTHER - UNK | 85 | 39.4 | Yes | Yes | 1.1 | 22.8 | -21.7 | 791571D9BA0545F0948933EFE98EEBF1 | Add refrigerant: 39.4 oz Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 46.35% | 0.53647 | 89.08% | [5 empty] | Non-TXV | 46.35%
Bakersfield | CA | 93312-2029 |  | 2014-08-15 | 2014-08-15 09:42 | 2014-08-15 09:42 | ICP - PGAD30D1K7 | 73 | 0 | Yes | Yes | 21 | 18.1 | 2.9 | 1C83A06DF4CE41DF846C4C2B5F68D8D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6518 |  | 2014-08-21 | 2014-08-21 10:08 | 2014-08-21 10:08 | UNITARY PRODUCTS GROUP - H1RA048S06G | 117 | 0 | Yes | Yes | 21.9 | 20.1 | 1.8 | C95A79B8026A465FB625A945E7B0A30C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1882 |  | 2014-10-07 | 2014-10-07 12:44 | 2014-10-07 12:44 | RHEEM - RRNAB030JK06X | 72 | 0 | Yes | Yes | 22 | 23.9 | -1.8 | F97ECB2F95024C6D94291A060F8AE873 | Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-3508 |  | 2014-08-26 | 2014-08-26 11:31 | 2014-08-26 11:31 | RHEEM - RRGG-05N303K9 | 46 | 0 | Yes | Yes | 22.7 | 21.1 | 1.6 | A2CEEAAF2B7043F5B25E2FDF9E30F90A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2908 |  | 2014-08-11 | 2014-08-11 09:51 | 2014-08-11 10:13 | CARRIER - UNK | 76 | 8.2 | Yes | Yes | 22.1 | 19.9 | 2.2 | 53BEEAB818F14227B61F37A03EAAC602 |  | R22 | Non-TXV |  | 10.79% | 0.89211 | 20.73% | [5 empty] | Non-TXV | 10.79%
Bakersfield | CA | 93312-4456 |  | 2014-10-11 | 2014-10-11 15:36 | 2014-10-11 15:53 | RHEEM - RRHA-038JAZ | 85 | 4.5 | Yes | Yes | 18.6 | 21.6 | -3 | 2B4282D03E7E46259CC6EC69B704C9CB |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Bakersfield | CA | 93311-2304 |  | 2014-09-24 | 2014-09-24 09:59 | 2014-09-24 09:59 | BRYANT - 574DNWA30040NATP | 98 | 0 | Yes | Yes | 21.8 | 19.3 | 2.5 | 1554B6DB3DE345E98BD00B8E67F7FEF3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94538-3970 |  | 2014-08-20 | 2014-08-20 11:50 | 2014-08-20 11:50 | CARRIER - 38TXA036330 | 181 | -17 | Yes | Yes | 18.8 | 18.8 | 0 | 26B5762790974F2CAD21D77B97CB0F70 | Remove refrigerant: 17 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | -9.392% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.392%
Fresno | CA | 93705-0319 |  | 2014-08-12 | 2014-08-12 12:33 | 2014-08-12 12:58 | RHEEM - RRNLB030JK06X | 77 | 3.3 | Yes | Yes | 20.9 | 22.1 | -1.2 | A49516397F4C494F82A83603E57FA029 |  | R410A | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Fresno | CA | 93722-4015 |  | 2014-08-08 | 2014-08-08 11:49 | 2014-08-08 11:49 | RHEEM - RRNLB030JK06X | 77 | 0 | Yes | Yes | 19 | 19.5 | -0.5 | 57F1A714027B4029AB85765C0B290C59 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3118 |  | 2014-08-18 | 2014-08-18 11:53 | 2014-08-18 12:14 | OTHER - 110A42A1NB | 135 | 5.8 | Yes | Yes | 23.5 | 21.4 | 2.1 | D1955D960CC648D7B932620A79C0691F |  | R22 | Non-TXV |  | 4.296% | 0.95704 | 8.257% | [5 empty] | Non-TXV | 4.296%
Bakersfield | CA | 93301-2267 |  | 2014-09-09 | 2014-09-09 17:39 | 2014-09-09 17:41 | OTHER - DBYP-F024N045A | 100 | 6.4 | Yes | Yes | 20.3 | 20.4 | -0.1 | 77AE8E4FB6A84EF881496C79F862C146 |  | R22 | TXV |  | 6.4% | 0.936 | 12.3% | [5 empty] | TXV | 6.4%
Fresno | CA | 93703-3209 |  | 2014-08-06 | 2014-08-06 16:22 | 2014-08-06 17:15 | RUUD - URKAA036JK06E | 62 | 5.2 | Yes | Yes | 27 | 21.3 | 5.7 | 118067D8A5AE435DAE87E56392CF9F26 |  | R22 | Non-TXV |  | 8.387% | 0.91613 | 16.12% | [5 empty] | Non-TXV | 8.387%
Bakersfield | CA | 93307-3527 |  | 2014-09-12 | 2014-09-12 21:05 | 2014-09-12 21:07 | ARCOAIRE - PGF036K060B | 71 | 3.2 | Yes | Yes | 19.8 | 19.7 | 0.1 | 494F0D7CD99F4210A9913A20932BA5AF |  | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
San Jose | CA | 95136-4201 |  | 2014-08-06 | 2014-08-06 09:09 | 2014-08-06 09:57 | GOODMAN - GSC130241DA | 83 | 3.8 | Yes | Yes | 20.3 | 19.3 | 1 | 62A6257AC20B4C5A9C69C29DB720CC48 |  | R22 | Non-TXV |  | 4.578% | 0.95422 | 8.799% | [5 empty] | Non-TXV | 4.578%
Bakersfield | CA | 93307-4586 |  | 2014-10-20 | 2014-10-20 14:54 | 2014-10-20 14:54 | OTHER - UNK | 91 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | FD692949A1A140B289A21BA5C2B219A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7040 |  | 2014-08-13 | 2014-08-13 09:36 | 2014-08-13 09:57 | CARRIER - 382E42310 | 128 | 7.6 | Yes | Yes | 21.3 | 20.4 | 0.9 | 0A9BB6C262EC468BB0552883E9EBB4E2 |  | R22 | Non-TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | Non-TXV | 5.938%
Bakersfield | CA | 93306-0000 |  | 2014-10-11 | 2014-10-11 12:15 | 2014-10-11 12:15 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 21.8 | 20.8 | 1 | B70631D67FA4400D913BC70FB97107A6 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1145 |  | 2014-08-18 | 2014-08-18 15:01 | 2014-08-18 15:01 | RHEEM - RRNLB024JK06X | 78 | 0 | Yes | Yes | 21.7 | 21 | 0.7 | E2B81B5F1BB34A6494AD8A9141708603 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1671 |  | 2014-08-25 | 2014-08-25 09:59 | 2014-08-25 10:24 | BRYANT - 113RNA048A | 120 | 4.4 | Yes | Yes | 22.7 | 20.2 | 2.5 | 78C841F6D0F841D4A1D86CAEFC71CDE9 |  | R22 | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Bakersfield | CA | 93312-3198 |  | 2014-09-19 | 2014-09-19 15:51 | 2014-09-19 15:51 | RHEEM - RRMAA042JK08X | 114 | 0 | Yes | Yes | 18 | 19.1 | -1.1 | 08DA9321D9964EEBABE68EE9B3B5DB67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2917 |  | 2014-10-31 | 2014-10-31 13:44 | 2014-10-31 13:44 | CARRIER - UNK | 152 | 0 | Yes | Yes | 21.1 | 18.7 | 2.4 | 8EF32237F2064E489B68D79CD40CA9A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2593 |  | 2014-10-30 | 2014-10-30 10:25 | 2014-10-30 10:25 | OTHER - CCU12A30A1 | 90 | 0 | Yes | Yes | 17 | 19.1 | -2.1 | 06AA80200B184C3991DAEA9C3F42C7A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2505 |  | 2014-08-18 | 2014-08-18 13:30 | 2014-08-18 13:57 | YORK - D1NP036N05606A | 108 | 26.7 | Yes | Yes | 23.7 | 24.2 | -0.5 | 64F1EF2CD949437A9FD03F4F2F96F209 |  | R22 | Non-TXV |  | 24.72% | 0.75278 | 47.51% | [5 empty] | Non-TXV | 24.72%
Fresno | CA | 93722-5454 |  | 2014-08-08 | 2014-08-08 13:25 | 2014-08-08 13:52 | CARRIER - 48XLNA3606030TP | 152 | 5.5 | Yes | Yes | 22.3 | 18.9 | 3.4 | 2683FBA49D90468EB19D1530E0D639A7 |  | R410A | Non-TXV |  | 3.618% | 0.96382 | 6.954% | [5 empty] | Non-TXV | 3.618%
Bakersfield | CA | 93312-8214 |  | 2014-09-03 | 2014-09-03 12:05 | 2014-09-03 12:05 | LENNOX - 10ACE-048-230 | 96 | 0 | Yes | Yes | 20.7 | 23.2 | -2.5 | 1C001F3B58834A90A1350612C538BB56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1907 |  | 2014-08-15 | 2014-08-15 08:37 | 2014-08-15 09:54 | HEIL - NAC036AKA1 | 87 | -7.2 | Yes | Yes | 13.7 | 16.4 | -2.7 | 86B2142C3DBB4C5480372318883108E8 |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Bakersfield | CA | 93313-2794 |  | 2014-10-19 | 2014-10-19 17:09 | 2014-10-19 17:12 | OTHER - FS5BD-060K | 232 | 8.7 | Yes | Yes | 22.4 | 21.5 | 0.9 | 4A000C86DBB04D00A2C14A570FB5D381 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Bakersfield | CA | 93313-9813 |  | 2014-08-27 | 2014-08-27 14:23 | 2014-08-27 14:23 | YORK - 4HRC060506HS | 143 | 0 | Yes | Yes | 17 | 20 | -3 | 1975659BFB5B4E158717F2EDDAA18D25 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5047 |  | 2014-09-23 | 2014-09-23 16:26 | 2014-09-23 16:26 | TRANE - 2TTR2048A1200AA | 120 | 0 | Yes | Yes | 19.5 | 19.1 | 0.4 | 9B28088ACBA642E8B2A04C481C4F6E00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7305 |  | 2014-09-10 | 2014-09-10 12:29 | 2014-09-10 12:55 | RUUD - UAJBB-049JAZ | 163 | 13 | Yes | Yes | 22.6 | 19 | 3.6 | 35F54A3E552C4ADD8963DAEFFE99DEEE |  | R22 | Non-TXV |  | 7.975% | 0.92025 | 15.33% | [5 empty] | Non-TXV | 7.975%
Antioch | CA | 94531-8597 |  | 2014-10-27 | 2014-10-27 13:17 | 2014-10-27 13:36 | CARRIER - 38CKC048370 | 100 | -5.8 | Yes | Yes | 17.5 | 20.3 | -2.8 | 60B6FF3CB267484FB2E45E51BD06C494 |  | R22 | TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | TXV |  |  | -5.8%
Bakersfield | CA | 93307-0000 |  | 2014-08-11 | 2014-08-11 11:11 | 2014-08-11 11:11 | CARRIER - 24ABB330W0031010 | 65 | 0 | Yes | Yes | 20.7 | 20.7 | 0 | D60F4D66308045BBB68232890E8E3D09 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6775 |  | 2014-08-06 | 2014-08-06 12:17 | 2014-08-06 12:35 | CARRIER - 38EN030340 | 109 | 5.9 | Yes | Yes | 18 | 20.4 | -2.4 | BEF180CEE2F1470D81A3E14F68D9174E |  | R22 | Non-TXV |  | 5.413% | 0.94587 | 10.4% | [5 empty] | Non-TXV | 5.413%
Shafter | CA | 93263-1904 |  | 2014-08-23 | 2014-08-23 19:44 | 2014-08-23 19:45 | YORK - D2NP036N05606NXA | 108 | -4.2 | Yes | Yes | 23.5 | 21.3 | 2.2 | D42AE1B743A14E09BBB1A8DF4B779307 |  | R22 | TXV |  | -3.889% | 1.0389 | 1.089% |  |  |  |  | TXV |  |  | -3.889%
Bakersfield | CA | 93314-9824 |  | 2014-11-12 | 2014-11-12 13:38 | 2014-11-12 13:38 | OTHER - H1RD042S06G | 152 | 0 | Yes | Yes | 15.2 | 18.2 | -3 | 4B2B427A703E45168175890E9047ACA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-7854 |  | 2014-10-22 | 2014-10-22 11:05 | 2014-10-22 11:05 | RUUD - UAJB042JAZ | 99 | 0 | Yes | Yes | 13.7 | 19.5 | -5.8 | D61E6A4F93AE4D4F96A28725E7BB4560 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-7854 |  | 2014-10-22 | 2014-10-22 11:11 | 2014-10-22 11:11 | RUUD - UNK | 110 | 0 | Yes | Yes | 10.1 | 19.1 | -9 | CBE4A46E3B764086AD9A2E7AE38624BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3211 |  | 2014-08-12 | 2014-08-12 14:43 | 2014-08-12 20:36 | BDP - 561CJ048-A | 106 | -7.5 | Yes | Yes | 16.8 | 17.8 | -1 | 7D2088976A994BB48863056FAA8A70BD |  | R22 | Non-TXV |  | -7.075% | 1.0708 | 1.981% |  |  |  |  | Non-TXV |  |  | -7.075%
Vallejo | CA | 94589-1450 |  | 2014-08-25 | 2014-08-25 13:05 | 2014-08-25 13:33 | CARRIER - 24ABA336A80 | 83 | 7.3 | Yes | Yes | 20.1 | 20.2 | -0.1 | 798BE0B989034AF08BAC6F86675733B0 |  | R410A | Non-TXV |  | 8.795% | 0.91205 | 16.9% | [5 empty] | Non-TXV | 8.795%
Fresno | CA | 93711-1812 |  | 2014-08-22 | 2014-08-22 15:53 | 2014-08-22 16:13 | BRYANT - 583ANW048090ABHF | 132 | 4.7 | Yes | Yes | 23.8 | 21.3 | 2.5 | 3B17F9E0E08A432EB5971FE3CF65F1D7 |  | R22 | Non-TXV |  | 3.561% | 0.96439 | 6.843% | [5 empty] | Non-TXV | 3.561%
Shafter | CA | 93263-0000 |  | 2014-08-23 | 2014-08-23 20:00 | 2014-08-23 20:01 | YORK - D1NA0J6N05606C | 67 | 4.7 | Yes | Yes | 24.1 | 20.7 | 3.4 | 490F91C391264D689D815913EEEC7EC2 |  | R22 | Non-TXV |  | 7.015% | 0.92985 | 13.48% | [5 empty] | Non-TXV | 7.015%
Vacaville | CA | 95687-3117 |  | 2014-08-13 | 2014-08-13 09:27 | 2014-08-13 10:55 | YORK - HIDE030S06B | 80 | 2.4 | Yes | Yes | 15.7 | 17.9 | -2.2 | AA5A0BA4A1964D22BBAE9498C7D3E5AA |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Bakersfield | CA | 93314-9675 |  | 2014-09-03 | 2014-09-03 10:35 | 2014-09-03 10:35 | BDP - 585HJ0360ABAF | 102 | 0 | Yes | Yes | 18.9 | 21.5 | -2.6 | 1E921AEC2D38443E87BC43DFF7472441 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7852 |  | 2014-08-13 | 2014-08-13 10:08 | 2014-08-13 10:55 | CARRIER - 38BRB042300 | 131 | 6.6 | Yes | Yes | 15.6 | 17.5 | -1.9 | 6A0E28CA339A48678F3BAA3A5BCBE4CF |  | R22 | Non-TXV |  | 5.038% | 0.94962 | 9.682% | [5 empty] | Non-TXV | 5.038%
Pittsburg | CA | 94565-6517 |  | 2014-09-24 | 2014-09-24 10:41 | 2014-09-24 10:41 | BRYANT - 114ANA060 | 222 | 0 | Yes | Yes | 16 | 18.9 | -2.9 | 448AB845BF344C6BBA354424D0366240 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5216 |  | 2014-09-16 | 2014-09-16 16:02 | 2014-09-16 16:02 | YORK - D1GH024N03206A | 132 | 0 | Yes | Yes | 7.4 | 20.4 | -13 | 1C234EC8B3C4471EBD799DBB0E569D9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1915 |  | 2014-08-25 | 2014-08-25 11:54 | 2014-08-25 11:54 | OTHER - UNK | 60 | 0 | Yes | Yes | -0.9 | 21.5 | -22.4 | 9ABE11EF7B234529819E9FE03981EB58 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4510 |  | 2014-11-14 | 2014-11-14 12:34 | 2014-11-14 12:34 | YORK - H2RC048S06G | 124 | 0 | Yes | Yes | 20.5 | 17.4 | 3.1 | 27C4F9833826491C82AF2CA637FC3473 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2434 |  | 2014-08-14 | 2014-08-14 13:36 | 2014-08-14 13:36 | RUUD - UKNUKN | 90 | 0 | Yes | Yes | 25 | 23.4 | 1.7 | F3338390300A4FB8B4440344A691C53F |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-6035 |  | 2014-08-11 | 2014-08-11 15:37 | 2014-08-11 16:29 | GIBSON - JS3BA-030KA | 68 | 5.6 | Yes | Yes | 22.6 | 19.7 | 3 | E6458552DD2A4E61872B8A4B95F11066 |  | R22 | Non-TXV |  | 8.235% | 0.91765 | 15.83% | [5 empty] | Non-TXV | 8.235%
W Sacramento | CA | 95605-2239 |  | 2014-08-11 | 2014-08-11 12:51 | 2014-08-11 13:46 | GOODMAN - CK36-1A | 73 | 5.6 | Yes | Yes | 21.9 | 19.3 | 2.6 | 7A7E8A988BB444C9994634D5B1299B5F |  | R22 | Non-TXV |  | 7.671% | 0.92329 | 14.74% | [5 empty] | Non-TXV | 7.671%
Bakersfield | CA | 93314-4723 |  | 2014-09-03 | 2014-09-03 15:37 | 2014-09-03 15:37 | ICP - NAC260AKA5 | 133 | 0 | Yes | Yes | 20.6 | 20.4 | 0.2 | 595C49697E6D40E38EDA4A0DCC994B3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3315 |  | 2014-08-15 | 2014-08-15 10:36 | 2014-08-15 11:05 | TRANE - 4TTR2030A1000AA | 66 | 6.6 | Yes | Yes | 21.4 | 20.3 | 1.2 | AA4CCAEDEDE94CF2AC937B9078AE11D1 |  | R410A | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Antioch | CA | 94509-5873 |  | 2014-10-28 | 2014-10-28 10:51 | 2014-10-28 11:12 | CARRIER - 38CKC048360 | 99 | 5.4 | Yes | Yes | 23.6 | 20.4 | 3.2 | 0161DBAAE370457B8415CE56C1A1F615 |  | R22 | TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | TXV | 5.455%
Martinez | CA | 94553-2064 |  | 2014-08-27 | 2014-08-27 10:11 | 2014-08-27 10:36 | TRANE - TTB042C100A1 | 96 | 5.6 | Yes | Yes | 15.5 | 17.3 | -1.8 | 77172AD4107448B78D1E5C43706C91B4 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Martinez | CA | 94553-2064 |  | 2014-08-27 | 2014-08-27 12:09 | 2014-08-27 12:38 | CARRIER - 38CKC030340 | 66 | -6.2 | Yes | Yes | 23.4 | 17 | 6.4 | C2EFF172FE9B492E985B5173B1FB5B59 |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
Bakersfield | CA | 93314-9200 |  | 2014-10-20 | 2014-10-20 14:07 | 2014-10-20 14:07 | LUXAIRE - HARB-F048SD | 207 | 0 | Yes | Yes | 21 | 22.6 | -1.6 | 828D9938ECDC4349A3F2EC98D8BEA796 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-2340 |  | 2014-08-05 | 2014-08-05 13:44 | 2014-08-05 14:18 | TRANE - 2TTB0048A1000AA | 109 | -10.3 | Yes | Yes | 19.4 | 18.4 | 1 | 3312367E3FFF4468867421118F27F904 |  | R22 | Non-TXV |  | -9.45% | 1.0945 | 2.646% |  |  |  |  | Non-TXV |  |  | -9.45%
Fairfield | CA | 94534-1036 |  | 2014-08-15 | 2014-08-15 09:53 | 2014-08-15 09:53 | CARRIER - 38TXA36340 | 104 | 0 | Yes | Yes | 16.7 | 17.8 | -1.1 | 570493A6C804456881A65AC71F5E8085 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4227 |  | 2014-08-15 | 2014-08-15 09:41 | 2014-08-15 10:00 | RHEEM - UNK | 76 | 5.5 | Yes | Yes | 21.2 | 19.9 | 1.3 | E7EDCCE5A4B6428E90C9037B4764BBC9 |  | R22 | Non-TXV |  | 7.237% | 0.92763 | 13.91% | [5 empty] | Non-TXV | 7.237%
Fremont | CA | 94536-4073 |  | 2014-08-21 | 2014-08-21 10:16 | 2014-08-21 10:27 | RUUD - UAND-036JAZ | 116 | -6.8 | Yes | Yes | 23.3 | 17.5 | 5.8 | 2F7734C93623478E92A09F56B3D32384 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
San Jose | CA | 95127-2412 |  | 2014-08-11 | 2014-08-11 12:52 | 2014-08-11 13:18 | RHEEM - RAKA037JAZ | 79 | 6.7 | Yes | Yes | 17.3 | 18.2 | -0.9 | 61BB460362EC4978B4F3AD79F2028114 |  | R22 | Non-TXV |  | 8.481% | 0.91519 | 16.3% | [5 empty] | Non-TXV | 8.481%
Clovis | CA | 93611-6965 |  | 2014-08-20 | 2014-08-20 14:17 | 2014-08-20 14:38 | GOODMAN - CKL491A | 112 | 4.6 | Yes | Yes | 21.9 | 21.3 | 0.6 | 643F0DDDA4C341B2A4E7C5B99F40C36A |  | R22 | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Clovis | CA | 93611-6965 |  | 2014-08-20 | 2014-08-20 14:41 | 2014-08-20 15:02 | GOODMAN - CKL491A | 112 | 4.5 | Yes | Yes | 22.3 | 21.4 | 0.9 | 3FA3319B7CE34A51AE94321CD7F24F3C |  | R22 | Non-TXV |  | 4.018% | 0.95982 | 7.721% | [5 empty] | Non-TXV | 4.018%
Fresno | CA | 93710-4110 |  | 2014-08-13 | 2014-08-13 12:21 | 2014-08-13 12:49 | TRANE - YCX036F1M0BC | 118 | 6.6 | Yes | Yes | 21.9 | 20.4 | 1.5 | CECBC41D664D4F688BD8529F1DCFEA0A |  | R22 | Non-TXV |  | 5.593% | 0.94407 | 10.75% | [5 empty] | Non-TXV | 5.593%
Shafter | CA | 93263-0000 |  | 2014-10-05 | 2014-10-05 18:12 | 2014-10-05 18:20 | OTHER - CA5548VKA | 139 | 8.6 | Yes | Yes | 20.1 | 21 | -0.9 | DFDF951354F54D6B82963A0BE37AEC66 |  | R22 | Non-TXV |  | 6.187% | 0.93813 | 11.89% | [5 empty] | Non-TXV | 6.187%
Fresno | CA | 93722-2910 |  | 2014-08-07 | 2014-08-07 14:19 | 2014-08-07 14:47 | CARRIER - UNK | 102 | 5 | Yes | Yes | 20.2 | 19.9 | 0.3 | C41147C7FEC54334AA8CFAB1CD9EAF54 |  | R22 | Non-TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | Non-TXV | 4.902%
Antioch | CA | 94509-1839 |  | 2014-10-29 | 2014-10-29 08:31 | 2014-10-29 08:31 | DAY & NIGHT - N2A336AKB300 | 85 | 0 | Yes | Yes | 20.6 | 20.2 | 0.5 | 4F3F21D8F6A94C478BAF8CB26A9843F8 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1869 |  | 2014-11-14 | 2014-11-14 12:00 | 2014-11-14 20:55 | DAY & NIGHT - | 102 | 3.1 | Yes | Yes | 18.5 | 20.4 | -1.9 | 1CE5535855154FCC8B41A13CB3A3AB1B |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Bakersfield | CA | 93306-3436 |  | 2014-09-29 | 2014-09-29 15:25 | 2014-09-29 15:25 | BDP - 588ANW0600B0ADAG | 112 | 0 | Yes | Yes | 24 | 20.4 | 3.6 | D135674A3E3545408D71D2A07FF222A6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-6027 |  | 2014-08-27 | 2014-08-27 09:24 | 2014-08-27 10:12 | GIBSON - JS38A-036KA | 68 | 4.5 | Yes | Yes | 23.4 | 17.9 | 5.5 | 0FB2FFED3E60405D92C167A9C5BD311C |  | R22 | Non-TXV |  | 6.618% | 0.93382 | 12.72% | [5 empty] | Non-TXV | 6.618%
Bakersfield | CA | 93314-9679 |  | 2014-10-23 | 2014-10-23 16:02 | 2014-10-23 16:02 | OTHER - NAC048AKC3 | 112 | 0 | Yes | Yes | 28.2 | 22.6 | 5.6 | 6B0DBAD50258422DABC20CF1FA107FA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-6028 |  | 2014-08-27 | 2014-08-27 09:57 | 2014-08-27 10:56 | ARCOAIRE - R2A330GKC1 | 75 | 8.1 | Yes | Yes | 20.8 | 20.4 | 0.4 | CF8179C77B1641809C07709FEE855988 | Add refrigerant: 2.4 oz | R22 | Non-TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | Non-TXV | 10.8%
Fresno | CA | 93720-1714 |  | 2014-08-26 | 2014-08-26 11:46 | 2014-08-26 12:09 | DAY & NIGHT - UNK | 128 | 15.5 | Yes | Yes | 20.3 | 20.2 | 0.1 | A411833C72994CE5841AE6908B0ACC98 |  | R22 | Non-TXV |  | 12.11% | 0.87891 | 23.27% | [5 empty] | Non-TXV | 12.11%
Fresno | CA | 93726-1145 |  | 2014-08-27 | 2014-08-27 08:51 | 2014-08-27 09:14 | RHEEM - RRNLB024JK06X | 78 | 2.4 | Yes | Yes | 20.6 | 18.8 | 1.8 | 61754716CB38424DBA3FA104A035279B |  | R410A | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Fresno | CA | 93710-4631 |  | 2014-08-26 | 2014-08-26 15:17 | 2014-08-26 18:49 | GOODMAN - CK4918 | 97 | 3.9 | Yes | Yes | 21 | 22.3 | -1.3 | 5178C2AD57D546B4A34FF5237534122C |  | R22 | Non-TXV |  | 4.021% | 0.95979 | 7.727% | [5 empty] | Non-TXV | 4.021%
Bakersfield | CA | 93307-3965 |  | 2014-10-12 | 2014-10-12 16:47 | 2014-10-12 16:47 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 22 | 22 | 0 | CF4DB213D8EA495A843ACF3EA2160E7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4309 |  | 2014-08-28 | 2014-08-28 11:47 | 2014-08-28 12:19 | CARRIER - UNK | 96 | 4.8 | Yes | Yes | 20.9 | 21.3 | -0.4 | F7C88FFEE8804F45B3E2F43A87842302 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fairfield | CA | 94533-7054 |  | 2014-09-08 | 2014-09-08 14:09 | 2014-09-08 22:02 | CARRIER - 38TKB0060340 | 85 | 3.2 | Yes | Yes | 16.5 | 16.6 | -0.1 | E6ED6333DD92407284525C4B4B234F25 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Fresno | CA | 93726-3602 |  | 2014-08-27 | 2014-08-27 12:09 | 2014-08-27 12:33 | RHEEM - RRKAA030JK06X | 54 | 9.1 | Yes | Yes | 25.1 | 22 | 3.1 | 56FF7C95462145B39865026A2F44AD76 |  | R22 | Non-TXV |  | 16.85% | 0.83148 | 32.39% | [5 empty] | Non-TXV | 16.85%
Bakersfield | CA | 93314-8844 |  | 2014-11-12 | 2014-11-12 10:44 | 2014-11-12 10:44 | - PGADA24G0406 | 73 | 0 | Yes | Yes | 20.6 | 19.1 | 1.5 | 12211DF931564ABC8988278879859A2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-8844 |  | 2014-11-12 | 2014-11-12 11:07 | 2014-11-12 11:07 | HEIL - PGAD36D1K6 | 102 | 0 | Yes | Yes | 18.1 | 18.7 | -0.6 | E57E4DF6FE894334AD41F2669CA3D1B2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3965 |  | 2014-10-12 | 2014-10-12 17:13 | 2014-10-12 17:13 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 20.9 | 20.7 | 0.3 | 109C43DD6CCA4E89B06A5DB11B72206E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2218 |  | 2014-10-20 | 2014-10-20 17:13 | 2014-10-20 21:20 | RHEEM - RRNLB036JK06X | 92 | 9.8 | Yes | Yes | 22.9 | 20.7 | 2.2 | C3F88AE897FB402598E898F71E4EFDF6 |  | R22 | Non-TXV |  | 10.65% | 0.89348 | 20.47% | [5 empty] | Non-TXV | 10.65%
Bakersfield | CA | 93307-3962 |  | 2014-10-12 | 2014-10-12 15:32 | 2014-10-12 15:32 | DUCANE - 2AC13B24P1A | 89 | 0 | Yes | Yes | 21.6 | 22 | -0.4 | 7A8AF2B6B2294591B2FE2BFBC6F4D51B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3963 |  | 2014-10-12 | 2014-10-12 15:41 | 2014-10-12 15:41 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 22.5 | 22.4 | 0.1 | EDBA4BB98FC34C08A9C053ABDDC12604 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3962 |  | 2014-10-12 | 2014-10-12 15:38 | 2014-10-12 15:38 | DUCANE - 2AC13B24P1A | 89 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 5655FBA653134EEB9DC4F095AD389A1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-9566 |  | 2014-09-09 | 2014-09-09 15:40 | 2014-09-09 15:40 | AMERICAN STANDARD - YCPO42F1M0AA | 128 | 0 | Yes | Yes | 19.2 | 21.6 | -2.3 | CDFA285CD98C4A528C2F2FF0B5DFC4CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2428 |  | 2014-08-21 | 2014-08-21 15:28 | 2014-08-21 15:52 | YORK - D1NA024N03606C | 54 | 5.5 | Yes | Yes | 24.7 | 21 | 3.7 | A8BB5BA041DC438D8DA4D33E0B8DD487 |  | R22 | Non-TXV |  | 10.19% | 0.89815 | 19.57% | [5 empty] | Non-TXV | 10.19%
Bakersfield | CA | 93307-3969 |  | 2014-10-12 | 2014-10-12 18:13 | 2014-10-12 18:13 | DUCANE - 2AC13630P1A | 89 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | AFBAECA923D74BFE9112E2F612568859 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1841 |  | 2014-10-01 | 2014-10-01 13:31 | 2014-10-01 13:31 | GOODMAN - GPG13600901AA | 85 | 0 | Yes | Yes | 16.2 | 18.9 | -2.7 | F8E97637A694421DA5C23F93D52E3294 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1158 |  | 2014-09-30 | 2014-09-30 14:07 | 2014-09-30 14:07 | GOODMAN - GPG1330045M41AC | 80 | 0 | Yes | Yes | 25.2 | 20.8 | 4.4 | 68B6F89726A44D20A18BBE264B034D12 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1400 |  | 2014-08-15 | 2014-08-15 10:03 | 2014-08-15 10:23 | LENNOX - 14ACX-024-230-11 | 104 | 3.1 | Yes | Yes | 18.9 | 17.7 | 1.2 | 47632013D444479FA4B179D4CE71AEA9 |  | R410A | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Bakersfield | CA | 93307-3968 |  | 2014-10-12 | 2014-10-12 17:56 | 2014-10-12 17:56 | ICP - WCA3302GKR1 | 75 | 0 | Yes | Yes | 21.4 | 22.6 | -1.2 | 2887FCF99C354A11BF72411DF378C967 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3964 |  | 2014-10-12 | 2014-10-12 16:20 | 2014-10-12 16:20 | GOODMAN - CTSC130301EC | 66 | 0 | Yes | Yes | 20.7 | 21.5 | -0.8 | 9780E457EF4E46CCA8B879894ABA12C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3967 |  | 2014-10-12 | 2014-10-12 17:32 | 2014-10-12 17:32 | DUCANE - 2AC13624P1A | 89 | 0 | Yes | Yes | 22.4 | 20.4 | 2 | 2EDAC18ABCB94675BDE7537F586D10D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3533 |  | 2014-08-13 | 2014-08-13 09:03 | 2014-08-13 09:03 | UNITARY PRODUCTS GROUP - D2NP036N05606NXA | 108 | 0 | Yes | Yes | 24 | 20.4 | 3.6 | C0E75B854F564815A000BC19E6891E9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2416 |  | 2014-08-21 | 2014-08-21 14:50 | 2014-08-21 15:24 | GOODMAN - GPG10300701A | 50 | 2.9 | Yes | Yes | 22.1 | 20.4 | 1.7 | 6E7BC3A6F84646E8961F1B87697458DE |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Fremont | CA | 94536-4022 |  | 2014-08-22 | 2014-08-22 09:31 | 2014-08-22 09:31 | CARRIER - 38QR024C331 | 32 | 0 | Yes | Yes | 18.9 | 19.3 | -0.4 | DC0249AD5FEE47F1B6647447F17CDACE | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-1511 |  | 2014-09-05 | 2014-09-05 09:17 | 2014-09-05 09:17 | CARRIER - 584ANW036080 | 88 | 0 | Yes | Yes | 18.1 | 20.4 | -2.3 | 7642F6BB8FB2469AA81902C01676165E | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-1808 |  | 2014-09-17 | 2014-09-17 10:05 | 2014-09-17 10:05 | HEIL - PGF036K080B | 71 | 0 | Yes | Yes | 16.2 | 17.8 | -1.6 | 7AB3C279EC9443C09E0DE62CE4E418D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2906 |  | 2014-09-07 | 2014-09-07 17:58 | 2014-09-07 18:00 | DAY & NIGHT - DAYH-F036N070C | 108 | 5.7 | Yes | Yes | 21.8 | 19.9 | 1.9 | D9B721667FC04306A98BA51E06AC4401 |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Woodland | CA | 95695-4309 |  | 2014-08-12 | 2014-08-12 10:47 | 2014-08-12 11:38 | CARRIER - 48XS-024060311AA | 62 | 4.2 | Yes | Yes | 20.5 | 19.7 | 0.9 | 9EFCBCD519DD434D923848393ADB72F2 |  | R22 | Non-TXV |  | 6.774% | 0.93226 | 13.02% | [5 empty] | Non-TXV | 6.774%
Fresno | CA | 93722-2617 |  | 2014-08-07 | 2014-08-07 11:43 | 2014-08-07 12:36 | OTHER - 38CK036330 | 74 | 5.3 | Yes | Yes | 20.8 | 19.7 | 1.1 | 238DF180FCE745BCAAB04127720E32E4 |  | R22 | Non-TXV |  | 7.162% | 0.92838 | 13.76% | [5 empty] | Non-TXV | 7.162%
Antioch | CA | 94509-4422 |  | 2014-10-28 | 2014-10-28 11:34 | 2014-10-28 11:55 | ARMSTRONG - 015120 | 85 | 4 | Yes | Yes | 18.1 | 19.9 | -1.8 | BAAE59FBB2F5459AA8996EF61AE4CEFA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 39°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
San Jose | CA | 95120-2858 |  | 2014-08-11 | 2014-08-11 14:11 | 2014-08-11 14:11 | GUARDIAN - GCGD36S21S2B | 85 | 0 | Yes | Yes | 21.1 | 18.9 | 2.2 | 4D7CEA0947574B919E926109869588C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3895 |  | 2014-10-13 | 2014-10-13 15:25 | 2014-10-13 15:25 | CONCORD - CCV10A18A1 | 60 | 0 | Yes | Yes | 18.9 | 21.5 | -2.6 | C19F788A2EF64212B9B38EB0643CC417 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5071 |  | 2014-09-15 | 2014-09-15 12:44 | 2014-09-17 07:46 | CARRIER - 38TZA036320 | 84 | -6.9 | Yes | Yes | 16.4 | 17.3 | -0.9 | 11F1ACDF50AC4E339AB1D7D8A3E6C978 |  | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Bakersfield | CA | 93305-4509 |  | 2014-10-15 | 2014-10-15 09:49 | 2014-10-15 09:49 | UNITARY PRODUCTS GROUP - D2NX036N06506NXB | 76 | 0 | Yes | Yes | 22.9 | 17.9 | 5.1 | 706280F024784B3C8A6CEBD11FD0118D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-0000 |  | 2014-08-23 | 2014-08-23 19:38 | 2014-08-23 19:41 | PAYNE - PY1PNB042060AAAA | 102 | -5.6 | Yes | Yes | 22.8 | 20.3 | 2.5 | 341DFB529841440A9C14F3821C2B7F83 |  | R22 | Non-TXV |  | -5.49% | 1.0549 | 1.538% |  |  |  |  | Non-TXV |  |  | -5.49%
Fresno | CA | 93722-4108 |  | 2014-08-08 | 2014-08-08 10:55 | 2014-08-08 11:27 | YORK - DCYZF036N070A | 64 | -6 | Yes | Yes | 21.1 | 19.2 | 1.9 | 565720251D4E4E45973B0F395A969167 |  | R410A | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Bakersfield | CA | 93307-3969 |  | 2014-10-12 | 2014-10-12 18:23 | 2014-10-12 18:23 | DUCANE - 2AC13B24P1A | 89 | 0 | Yes | Yes | 20.9 | 21.5 | -0.6 | 410AE481F44441F5B4E30AD509742753 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1757 |  | 2014-09-05 | 2014-09-05 19:09 | 2014-09-05 19:09 | DAY & NIGHT - UNK | 96 | 0 | Yes | Yes | 24.9 | 21.3 | 3.6 | 943F0E7C82B44CBC981F711C7C151EF9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0350 |  | 2014-08-12 | 2014-08-12 11:45 | 2014-08-12 12:11 | GOODMAN - 88X160481BA | 138 | 8.3 | Yes | Yes | 20.6 | 19.9 | 0.7 | C4C9F521141B464794BD1A52BEADC30C |  | R410A | Non-TXV |  | 6.014% | 0.93986 | 11.56% | [5 empty] | Non-TXV | 6.014%
Fresno | CA | 93722-5546 |  | 2014-08-08 | 2014-08-08 09:43 | 2014-08-08 10:26 | CARRIER - UNK | 76 | 5.6 | Yes | Yes | 20.8 | 18.9 | 1.9 | 127C44E2145D445F879DF191E7507D4F |  | R22 | Non-TXV |  | 7.368% | 0.92632 | 14.16% | [5 empty] | Non-TXV | 7.368%
Bakersfield | CA | 93307-3968 |  | 2014-10-12 | 2014-10-12 17:50 | 2014-10-12 17:50 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 21.2 | 21.5 | -0.3 | 2BB409359EDA456292C2E255EE007BA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5266 |  | 2014-10-07 | 2014-10-07 16:48 | 2014-10-07 17:08 | GOODMAN - VSC130481AN | 145 | 5 | Yes | Yes | 18.7 | 19.6 | -0.9 | 3196A3FB86C2475E9F21DA4A9DC89ADC |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Bakersfield | CA | 93308-1518 |  | 2014-10-02 | 2014-10-02 15:22 | 2014-10-02 15:22 | BDP - 585HJ043060 | 80 | 0 | Yes | Yes | 18.5 | 21.2 | -2.7 | AB7FC40D8FB845A3BBC69AB8300BDE06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-3226 |  | 2014-10-16 | 2014-10-16 17:55 | 2014-10-16 18:17 | CARRIER - CTK-9030E2368 | 98 | 6 | Yes | Yes | 21 | 20.2 | 0.9 | 3571F073354F48CBB576A6A6DA7A4B75 |  | R22 | Non-TXV |  | 6.122% | 0.93878 | 11.77% | [5 empty] | Non-TXV | 6.122%
Fresno | CA | 93726-3114 |  | 2014-08-11 | 2014-08-11 12:28 | 2014-08-11 12:51 | GOODMAN - GPG1342070M41AD | 105 | 3.8 | Yes | Yes | 23 | 18.4 | 4.7 | 954EDA65B2394D52BC2B06F3C847E2C6 |  | R410A | Non-TXV |  | 3.619% | 0.96381 | 6.955% | [5 empty] | Non-TXV | 3.619%
Fremont | CA | 94536-7072 |  | 2014-08-22 | 2014-08-22 09:56 | 2014-08-22 10:09 | OTHER - CA5536VKD2 | 82 | 4.1 | Yes | Yes | 21.1 | 17.5 | 3.7 | 9B629DA7F9D147A999478BECCE2A82B0 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93307-3964 |  | 2014-10-12 | 2014-10-12 16:23 | 2014-10-12 16:23 | GOODMAN - CTSC130301ED | 66 | 0 | Yes | Yes | 21 | 22 | -1 | 57A46074BE4A4BF894BFD1E13ED6A07B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2439 |  | 2014-08-05 | 2014-08-05 13:45 | 2014-08-05 14:09 | AMERICAN STANDARD - YCX036G1M0AA | 109 | 4.6 | Yes | Yes | 20.9 | 17.9 | 3 | 2EE3518665C04B0D83BF947C633760A3 |  | R22 | Non-TXV |  | 4.22% | 0.9578 | 8.11% | [5 empty] | Non-TXV | 4.22%
Bakersfield | CA | 93306-3350 |  | 2014-08-08 | 2014-08-08 12:04 | 2014-08-08 12:04 | YORK - D1GH036N04806B | 112 | 0 | Yes | Yes | 24.6 | 20.7 | 3.9 | 102B7FC3DDEA4AE091B40F85DDFBD8C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3519 |  | 2014-08-25 | 2014-08-25 12:28 | 2014-08-25 12:49 | CARRIER - 48SS036080311 | 70 | 4 | Yes | Yes | 19 | 20.5 | -1.5 | D264788A5DA74849B4E1AA2F924462FF |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Clovis | CA | 93611-8172 |  | 2014-08-25 | 2014-08-25 10:59 | 2014-08-25 11:17 | LENNOX - 13ACC04823001 | 158 | 13.2 | Yes | Yes | 26.3 | 20.7 | 5.6 | 0A64B5E2E31C4C259CB54AEF60556221 |  | R22 | Non-TXV |  | 8.354% | 0.91646 | 16.06% | [5 empty] | Non-TXV | 8.354%
Dixon | CA | 95620-4547 |  | 2014-10-10 | 2014-10-10 09:56 | 2014-10-10 10:28 | CARRIER - 38CKC030330 | 67 | 3.4 | Yes | Yes | 21.7 | 20.4 | 1.3 | 7AE2D72028A4483EADF2428C6BBCEFBF |  | R22 | Non-TXV |  | 5.075% | 0.94925 | 9.752% | [5 empty] | Non-TXV | 5.075%
Shafter | CA | 93263-2142 |  | 2014-08-24 | 2014-08-24 19:31 | 2014-08-24 19:33 | LENNOX - 12GCS036X | 110 | 5.9 | Yes | Yes | 24.3 | 21 | 3.3 | AB4C5A6C46A64F1F880B5D51756E930D |  | R22 | Non-TXV |  | 5.364% | 0.94636 | 10.31% | [5 empty] | Non-TXV | 5.364%
Bakersfield | CA | 93314-4774 |  | 2014-10-22 | 2014-10-22 18:53 | 2014-10-22 18:53 | YORK - H2RD048S06B | 134 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 7F8AC11E47094779A5A8EE7FB57BFF45 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3929 |  | 2014-08-14 | 2014-08-14 12:31 | 2014-08-14 20:44 | - | 85 | -6 | Yes | Yes | 14.5 | 16.8 | -2.3 | 066F8BDEF865499E87EA67A9B876E5BC |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Suisun City | CA | 94585-6311 |  | 2014-09-09 | 2014-09-09 13:43 | 2014-09-09 20:53 | - 38TD036300 | 183 | 6.5 | Yes | Yes | 17 | 17.4 | -0.4 | DE6EED6B708B41D0910E6054D17B3E16 |  | R22 | Non-TXV |  | 3.552% | 0.96448 | 6.826% | [5 empty] | Non-TXV | 3.552%
Woodland | CA | 95695-5058 |  | 2014-09-04 | 2014-09-04 12:53 | 2014-09-04 14:09 | GOODMAN - GSX130301AB | 64 | 6.4 | Yes | Yes | 21.7 | 20.4 | 1.3 | A157BFD1ED6645DFA77AA0A6A709C198 |  | R410A | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
San Jose | CA | 95126-4067 |  | 2014-08-13 | 2014-08-13 09:04 | 2014-08-13 09:26 | GOODMAN - TCGD42S21S2A | 66 | -6.2 | Yes | Yes | 19.8 | 17.7 | 2.1 | 0AA3565A17EC43C0A08408547A7BC350 |  | R22 | Non-TXV |  | -9.394% | 1.0939 | 2.631% |  |  |  |  | Non-TXV |  |  | -9.394%
Bakersfield | CA | 93314-5201 |  | 2014-10-22 | 2014-10-22 14:28 | 2014-10-22 14:28 | RHEEM - RAMA060JBZ | 192 | 0 | Yes | Yes | 23.4 | 19.4 | 4 | 47A7F52823284D648F34A68A41B03047 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-3922 |  | 2014-08-11 | 2014-08-11 15:18 | 2014-08-11 15:41 | TRANE - TTN030C100C2 | 95 | 14.5 | Yes | Yes | 22.7 | 18.2 | 4.5 | 251CAD545596420E98E3FF1B83F0D2FE |  | R22 | Non-TXV |  | 15.26% | 0.84737 | 29.33% | [5 empty] | Non-TXV | 15.26%
Fresno | CA | 93726-7105 |  | 2014-08-15 | 2014-08-15 11:27 | 2014-08-15 11:43 | DAY & NIGHT - 42/110YAC102AK | 124 | -11.7 | Yes | Yes | 15.3 | 17.3 | -2 | 684F1F0054FD454CBF3EDC4D4AE74B36 |  | R22 | Non-TXV |  | -9.435% | 1.0944 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.435%
Suisun City | CA | 94585-3005 |  | 2014-09-30 | 2014-09-30 07:51 | 2014-09-30 07:51 | GE - BTR736B100A0 | 168 | 0 | Yes | Yes | 14.3 | 16.3 | -2 | D0838E96A2BC42E6B77419D49E62A327 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3824 |  | 2014-08-11 | 2014-08-11 09:45 | 2014-08-11 09:45 | PAYNE - PY3GNAA42090NA | 97 | 0 | Yes | Yes | 22.3 | 16.4 | 5.9 | D3C318307B344F5398C978AA7514FDDB |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2437 |  | 2014-08-11 | 2014-08-11 13:25 | 2014-08-11 13:46 | TRANE - 4TT3030A1000AA | 91 | 5.6 | Yes | Yes | 17.4 | 19.2 | -1.8 | B8EA05FA9397456DA5FB7FB5F9BD5664 |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Fresno | CA | 93722-2749 |  | 2014-08-07 | 2014-08-07 10:58 | 2014-08-07 11:37 | OTHER - PA13NR036H | 86 | -4.2 | Yes | Yes | 21.3 | 19.6 | 1.7 | A093574B30CD4CBD930BA3E2366179F8 |  | R22 | Non-TXV |  | -4.884% | 1.0488 | 1.368% |  |  |  |  | Non-TXV |  |  | -4.884%
Fremont | CA | 94536-7348 |  | 2014-08-20 | 2014-08-20 12:23 | 2014-08-20 12:45 | TRANE - 2TTR1036A1000AA | 73 | 7.6 | Yes | Yes | 20.4 | 19.9 | 0.5 | 5C38269576A1436B85813EDA6BFAFC46 |  | R22 | Non-TXV |  | 10.41% | 0.89589 | 20.01% | [5 empty] | Non-TXV | 10.41%
Fresno | CA | 93701-2243 |  | 2014-08-19 | 2014-08-19 09:35 | 2014-08-19 09:59 | LENNOX - 10GCS036X753PA | 58 | 4 | Yes | Yes | 25 | 20 | 5.1 | A5382EF6C0C148C5A74841EF0C784FAE |  | R22 | Non-TXV |  | 6.897% | 0.93103 | 13.25% | [5 empty] | Non-TXV | 6.897%
Bakersfield | CA | 93314-9673 |  | 2014-10-22 | 2014-10-22 12:08 | 2014-10-22 12:08 | OTHER - CA5548VKC1 | 113 | 0 | Yes | Yes | 16.4 | 19.1 | -2.7 | 3C3DA839A31D483AAD3E8F0E63053B34 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3801 |  | 2014-08-06 | 2014-08-06 15:32 | 2014-08-06 15:59 | YORK - DAYPF030N070A | 73 | 2.4 | Yes | Yes | 20.9 | 19.1 | 1.8 | B9CFBE7B8D854158BBD897F885A9C9FE |  | R22 | Non-TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | Non-TXV | 3.288%
Bakersfield | CA | 93313-2204 |  | 2014-09-15 | 2014-09-15 12:57 | 2014-09-15 12:57 | YORK - DN2P036N05606A | 108 | 0 | Yes | Yes | 16.2 | 17.2 | -1 | 3783EBD83E164B88BC29F24C45F853A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3968 |  | 2014-10-12 | 2014-10-12 18:07 | 2014-10-12 18:07 | DUCANE - 2AC13618P1A | 89 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | 6F1C013C3B074315AF2481CC53E04FCD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2592 |  | 2014-09-08 | 2014-09-08 14:08 | 2014-09-08 18:36 | YORK - M2CB042S06A | 108 | 3.9 | Yes | Yes | 22.3 | 21 | 1.3 | ED48682206CF43DEAAAB4D05E8535B75 |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Antioch | CA | 94509-5231 |  | 2014-10-29 | 2014-10-29 11:17 | 2014-10-29 11:34 | PAYNE - PA13NR03600GAJAA | 88 | -5.2 | Yes | Yes | 24.3 | 20.4 | 3.9 | FE9929506230462C904A0178BE85B037 |  | R22 | TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | TXV |  |  | -5.909%
Bakersfield | CA | 93304-2315 |  | 2014-08-21 | 2014-08-21 12:28 | 2014-08-21 12:28 | WESTINGHOUSE - UKN | 90 | 0 | Yes | Yes | 20.5 | 23.5 | -3 | C8268F66143649ADA6692C771EE27B96 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3963 |  | 2014-10-12 | 2014-10-12 16:04 | 2014-10-12 16:04 | DUCANE - 2AC13630P1A | 89 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 1D1C74B34A454FB5A94A428BC71F382A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4582 |  | 2014-10-08 | 2014-10-08 11:14 | 2014-10-08 11:41 | OTHER - UNK | 85 | 4.7 | Yes | Yes | 17.5 | 20.4 | -2.9 | 665323378B9F4545B970DC3BF94D51C7 |  | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
W Sacramento | CA | 95691-6101 |  | 2014-08-27 | 2014-08-27 13:25 | 2014-08-27 15:36 | CARRIER - 38CKC030---341 | 70 | 5.3 | Yes | Yes | 21.1 | 20.4 | 0.7 | A97DE3845EBB497BA1DEBDA76A982A98 |  | R22 | Non-TXV |  | 7.571% | 0.92429 | 14.55% | [5 empty] | Non-TXV | 7.571%
Fairfield | CA | 94533-1334 |  | 2014-08-14 | 2014-08-14 15:19 | 2014-08-14 20:46 | - | 85 | 4.9 | Yes | Yes | 17.4 | 18.2 | -0.8 | F1EB429DF38544A1BA931010C1C490F8 |  | R22 | Non-TXV |  | 5.765% | 0.94235 | 11.08% | [5 empty] | Non-TXV | 5.765%
Fresno | CA | 93720-2555 |  | 2014-08-26 | 2014-08-26 14:14 | 2014-08-26 14:50 | BRYANT - 583ANW0360NAAF | 83 | 3.5 | Yes | Yes | 24.8 | 20.6 | 4.2 | 2F4DC48DCC5A4F8BA3DEFDE12E318DFE |  | R22 | Non-TXV |  | 4.217% | 0.95783 | 8.104% | [5 empty] | Non-TXV | 4.217%
Suisun City | CA | 94585-1786 |  | 2014-09-09 | 2014-09-09 13:27 | 2014-09-09 20:52 | TRANE - 2TTR3042A1000AA | 109 | 5.6 | Yes | Yes | 19.7 | 19.6 | 0.1 | 69C9BA125D55453AB1225AA8FEBFEBEC |  | R22 | Non-TXV |  | 5.138% | 0.94862 | 9.873% | [5 empty] | Non-TXV | 5.138%
Antioch | CA | 94509-6973 |  | 2014-11-14 | 2014-11-14 12:49 | 2014-11-14 20:54 | CARRIER - 38TR030300 | 85 | 3 | Yes | Yes | 18.8 | 20.4 | -1.6 | 8EF119529548460885D7683CF257AA76 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93313-0000 |  | 2014-10-20 | 2014-10-20 16:31 | 2014-10-20 16:31 | RHEEM - RRNLB030JK06X | 76 | 0 | Yes | Yes | 19.1 | 19.7 | -0.5 | 7336A8097B124ED3ACE454A193E6496E |  | R410A | TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2213 |  | 2014-08-24 | 2014-08-24 19:52 | 2014-08-24 19:54 | ICP - PGAD60E1K6 | 215 | 7.1 | Yes | Yes | 25.9 | 22.5 | 3.4 | 674702047B214A5C8C07AF6E2D7A4CF7 |  | R22 | Non-TXV |  | 3.302% | 0.96698 | 6.346% | [5 empty] | Non-TXV | 3.302%
Fresno | CA | 93722-0000 |  | 2014-08-07 | 2014-08-07 17:12 | 2014-08-07 18:15 | CARRIER - 24ABA336A310 | 85 | 13.9 | Yes | Yes | 20.4 | 20.1 | 0.3 | 3D5853CCE8D14F43AFE7FDE472FEE069 |  | R410A | Non-TXV |  | 16.35% | 0.83647 | 31.43% | [5 empty] | Non-TXV | 16.35%
Vacaville | CA | 95687-5008 |  | 2014-10-13 | 2014-10-13 12:07 | 2014-10-13 14:38 | TRANE - 4TTX4048B1000AA | 121 | 6.8 | Yes | Yes | 19.7 | 20.4 | -0.7 | CC505971D689411A9FA774EB9DA413EB |  | R22 | Non-TXV |  | 5.62% | 0.9438 | 10.8% | [5 empty] | Non-TXV | 5.62%
Fresno | CA | 93722-5430 |  | 2014-08-08 | 2014-08-08 12:49 | 2014-08-08 13:21 | GOODMAN - CKL0361H | 71 | 5.5 | Yes | Yes | 21.3 | 18.5 | 2.9 | 7F83FE2254B0417A9792A3D2E2B368CF |  | R22 | Non-TXV |  | 7.746% | 0.92254 | 14.89% | [5 empty] | Non-TXV | 7.746%
Bakersfield | CA | 93308-1146 |  | 2014-10-24 | 2014-10-24 10:49 | 2014-10-24 10:49 | OTHER - BRCS0481BDG | 117 | 0 | Yes | Yes | 20.3 | 19.5 | 0.8 | F80483D7D16F42F5834CC5BABBFE25C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-5064 |  | 2014-08-12 | 2014-08-12 10:49 | 2014-08-12 11:08 | BRYANT - 582ANW024040AAAD | 56 | 3.3 | Yes | Yes | 20.4 | 19.9 | 0.5 | 95B3070FDE0447F983867CCD532216BA |  | R22 | Non-TXV |  | 5.893% | 0.94107 | 11.32% | [5 empty] | Non-TXV | 5.893%
Fresno | CA | 93705-4507 |  | 2014-08-12 | 2014-08-12 15:02 | 2014-08-12 15:27 | GOODMAN - UNK | 101 | 6.8 | Yes | Yes | 20.3 | 20.7 | -0.4 | BFBA227C8C4745C8ABE60190DFA7EE4E |  | R22 | Non-TXV |  | 6.733% | 0.93267 | 12.94% | [5 empty] | Non-TXV | 6.733%
Vallejo | CA | 94591-6624 |  | 2014-10-01 | 2014-10-01 14:27 | 2014-10-01 14:43 | CARRIER - 38EH024320 | 104 | 3.7 | Yes | Yes | 20.1 | 20.7 | -0.6 | 8A5867CE955D4DE68DD7F3A996ACD046 |  | R22 | Non-TXV |  | 3.558% | 0.96442 | 6.837% | [5 empty] | Non-TXV | 3.558%
Bakersfield | CA | 93306-6842 |  | 2014-09-17 | 2014-09-17 13:21 | 2014-09-17 13:21 | ICP - A2A336AKB300 | 84 | 0 | Yes | Yes | 20.4 | 19.9 | 0.5 | BDABA418D2014962ACFA4BE4A24A62BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2095 |  | 2014-08-08 | 2014-08-08 14:35 | 2014-08-08 16:15 | CARRIER - 2ABA33A300 | 76 | 4.5 | Yes | Yes | 21.3 | 16.1 | 5.2 | D72D014A85DC46248F0039E90E3F220F |  | R22 | Non-TXV |  | 5.921% | 0.94079 | 11.38% | [5 empty] | Non-TXV | 5.921%
Fresno | CA | 93726-3217 |  | 2014-08-11 | 2014-08-11 13:28 | 2014-08-11 13:50 | RHEEM - RRKAA036JK06X | 62 | 2.6 | Yes | Yes | 23.9 | 22.1 | 1.8 | D82C1FC04EAD498EB22F59EE8B025E75 |  | R22 | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
W Sacramento | CA | 95605-1954 |  | 2014-08-27 | 2014-08-27 14:30 | 2014-08-27 15:50 | GE - | 72 | 4.6 | Yes | Yes | 21.2 | 19.3 | 1.9 | B2BB88BBCD8948B9B43E5F373B158C37 |  | R22 | Non-TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | Non-TXV | 6.389%
Fresno | CA | 93703-2303 |  | 2014-08-06 | 2014-08-06 11:25 | 2014-08-06 11:25 | YORK - DCYZF024N045C | 58 | 0 | Yes | Yes | 20.5 | 18.5 | 2 | 282F6075893941D6B8FDF5AB9F85DF40 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1210 |  | 2014-09-27 | 2014-09-27 15:39 | 2014-09-27 15:39 | COMFORT AIRE - PGC048K080A | 102 | 0 | Yes | Yes | 25.2 | 21 | 4.2 | EF8C67DB4866415BADDBDBBC4C87BF02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3345 |  | 2014-08-28 | 2014-08-28 13:48 | 2014-08-28 14:06 | CARRIER - 569EBX060000AAAA | 200 | 22.1 | Yes | Yes | 25 | 22.3 | 2.7 | 50691C70FC084F419A1CE3506271F955 |  | R22 | Non-TXV |  | 11.05% | 0.8895 | 21.24% | [5 empty] | Non-TXV | 11.05%
Fremont | CA | 94536-4634 |  | 2014-08-27 | 2014-08-27 08:59 | 2014-08-27 09:19 | TRANE - 4TTX4060C1000AA | 85 | 5.2 | Yes | Yes | 21.7 | 17.7 | 4 | 4172C84132234636B635D61AD77036CE |  | R410A | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
W Sacramento | CA | 95691-4807 |  | 2014-08-12 | 2014-08-12 08:55 | 2014-08-12 08:55 | CARRIER - | 108 | 0 | Yes | Yes | 25.8 | 21.1 | 4.8 | BF87C25DE2CD41D6AEAE502359F981C8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95128-3203 |  | 2014-08-13 | 2014-08-13 08:16 | 2014-08-13 08:44 | BRYANT - 561CJX048000AAAA | 85 | -8 | Yes | Yes | 18.1 | 17.7 | 0.4 | AFA210D9715040259828E8BFD9ACF591 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Fresno | CA | 93702-2040 |  | 2014-08-05 | 2014-08-05 12:46 | 2014-08-05 13:08 | GOODMAN - PGB0360751A | 60 | -3.5 | Yes | Yes | 23.5 | 22.1 | 1.4 | ED12A6DC52624BCDB42368D31712DB20 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Fresno | CA | 93704-4015 |  | 2014-08-13 | 2014-08-13 13:48 | 2014-08-13 14:08 | RUUD - UAFD025JAS | 51 | 5 | Yes | Yes | 19.7 | 19.9 | -0.2 | BCE9E64803D946369DD585F2DC6A1007 |  | R22 | Non-TXV |  | 9.804% | 0.90196 | 18.84% | [5 empty] | Non-TXV | 9.804%
Woodland | CA | 95695-2736 |  | 2014-08-12 | 2014-08-12 11:18 | 2014-08-12 11:37 | - PGE10B24D050LA-2A | 62 | 6.5 | Yes | Yes | 21.1 | 18.8 | 2.3 | DD187B6ED1D347EB8B18D3A48E8BFE5D |  | R22 | Non-TXV |  | 10.48% | 0.89516 | 20.15% | [5 empty] | Non-TXV | 10.48%
Bakersfield | CA | 93304-2361 |  | 2014-08-21 | 2014-08-21 10:39 | 2014-08-21 10:39 | GOODMAN - BCUP-F030AA | 95 | 0 | Yes | Yes | 21.2 | 17.1 | 4.1 | 36C8E012024541BF9805162865290D9F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2230 |  | 2014-10-04 | 2014-10-04 18:55 | 2014-10-04 19:13 | OTHER - UNK | 85 | 10.3 | Yes | Yes | 19.5 | 22.3 | -2.8 | C27E2EE47F684014ACF8856240EC53D0 |  | R22 | Non-TXV |  | 12.12% | 0.87882 | 23.29% | [5 empty] | Non-TXV | 12.12%
Shafter | CA | 93263-2211 |  | 2014-08-24 | 2014-08-24 19:36 | 2014-08-24 19:36 | CARRIER - 48D1004 | 81 | 0 | Yes | Yes | 23.9 | 21 | 3 | C69440A27D474CBAB4BE9EFCF513D4D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3968 |  | 2014-10-12 | 2014-10-12 17:52 | 2014-10-12 17:52 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 20.4 | 21.8 | -1.4 | 3B23ED31E9B3441B845A95FD331249D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6302 |  | 2014-08-13 | 2014-08-13 11:26 | 2014-08-13 11:55 | CARRIER - 48SX042080311AA | 90 | 3.7 | Yes | Yes | 20.6 | 19.9 | 0.7 | 4A72E07482744C63B7CD83BE49D03464 |  | R22 | Non-TXV |  | 4.111% | 0.95889 | 7.901% | [5 empty] | Non-TXV | 4.111%
Fresno | CA | 93703-3905 |  | 2014-08-19 | 2014-08-19 11:37 | 2014-08-19 12:02 | OTHER - UNK | 67 | -4.7 | Yes | Yes | 20.3 | 21.3 | -1 | 534AEE3B7AAD4E889E12C0200FA03A7A |  | R22 | Non-TXV |  | -7.015% | 1.0701 | 1.965% |  |  |  |  | Non-TXV |  |  | -7.015%
Fresno | CA | 93720-0277 |  | 2014-08-26 | 2014-08-26 10:43 | 2014-08-26 11:07 | OTHER - 598N036B | 188 | 22.6 | Yes | Yes | 21.7 | 22.9 | -1.2 | CFC823B6B8A44B59AD2BB5A57C61A668 |  | R22 | Non-TXV |  | 12.02% | 0.87979 | 23.1% | [5 empty] | Non-TXV | 12.02%
Davis | CA | 95618-4834 |  | 2014-08-14 | 2014-08-14 11:28 | 2014-08-14 13:18 | GOODMAN - CK18-18 | 69 | -5.7 | Yes | Yes | 22.5 | 20.4 | 2.1 | E53757D1B5CC48498F3A442AB473C464 |  | R22 | Non-TXV |  | -8.261% | 1.0826 | 2.313% |  |  |  |  | Non-TXV |  |  | -8.261%
Bakersfield | CA | 93314-8891 |  | 2014-11-12 | 2014-11-12 09:50 | 2014-11-12 09:50 | YORK - DAYPF042N080A | 150 | 0 | Yes | Yes | 23.1 | 19.1 | 4 | 01AFB7FB4AC345C1A587DD3D5A5374C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-7425 |  | 2014-08-20 | 2014-08-20 13:05 | 2014-08-20 13:28 | CARRIER - 39EA024310 | 55 | 8.5 | Yes | Yes | 17.4 | 18.2 | -0.8 | 032D6C5E661045DD8E26DE4D66AC68D4 |  | R22 | Non-TXV |  | 15.45% | 0.84545 | 29.7% | [5 empty] | Non-TXV | 15.45%
Fairfield | CA | 94533-7085 |  | 2014-08-20 | 2014-08-20 12:05 | 2014-08-20 13:31 | RHEEM - | 70 | 6.3 | Yes | Yes | 18.8 | 19.7 | -0.8 | 983009ABDC034A049490F55B1591D11D |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Fremont | CA | 94538-2638 |  | 2014-08-27 | 2014-08-27 11:33 | 2014-08-27 11:52 | PAYNE - PA13NA042 | 103 | 4.1 | Yes | Yes | 20.6 | 18.7 | 1.9 | 85965A31F8694E5B86A0679E45FF81F8 |  | R410A | TXV |  | 3.981% | 0.96019 | 7.65% | [5 empty] | TXV | 3.981%
Davis | CA | 95616-2862 |  | 2014-08-15 | 2014-08-15 09:25 | 2014-08-15 10:36 | LENNOX - 10ACB18-5 | 58 | 9.5 | Yes | Yes | 25.8 | 19.9 | 5.9 | 5496908B8AF142A8A04ED02F43CBBC8F |  | R22 | Non-TXV |  | 16.38% | 0.83621 | 31.48% | [5 empty] | Non-TXV | 16.38%
Bakersfield | CA | 93314-9187 |  | 2014-11-12 | 2014-11-12 12:26 | 2014-11-12 12:26 | YORK - D1NH048N06506C | 128 | 0 | Yes | Yes | 15.4 | 17.2 | -1.8 | E28CA24267074239B57A9BDCB155CB42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5127 |  | 2014-08-20 | 2014-08-20 18:53 | 2014-08-20 18:53 | OTHER - 80WR30G1NA | 86 | 0 | Yes | Yes | 35 | 21 | 14 | C0C6D7982D8740068A5DC19E9FA5FD73 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2649 |  | 2014-08-18 | 2014-08-18 10:51 | 2014-08-18 11:17 | GOODMAN - GPG153609041AA | 102 | 5.1 | Yes | Yes | 24.5 | 19.8 | 4.7 | 1A2676B2DC364A308D680A7FC520F284 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93308-4098 |  | 2014-09-26 | 2014-09-26 16:50 | 2014-09-26 16:50 | GOODMAN - SSX160421AA | 109 | 0 | Yes | Yes | 18.9 | 21.9 | -3 | 49BCD3BD52994FD4A921358A72B912E8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3601 |  | 2014-08-11 | 2014-08-11 14:03 | 2014-08-11 14:23 | CARRIER - 48GS-036090311 | 68 | 4.6 | Yes | Yes | 17.1 | 19.3 | -2.2 | DB169B956B4C47538580D42F6AAC2E3C |  | R22 | Non-TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | Non-TXV | 6.765%
Vallejo | CA | 94590-3303 |  | 2014-09-17 | 2014-09-17 11:56 | 2014-09-17 12:20 | TRANE - TTB036C100A1 | 90 | 2.7 | Yes | Yes | 19.6 | 20.4 | -0.8 | 85E56A0E5D5849F2BD3BC2B8CC392EA8 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Wasco | CA | 93280-2114 |  | 2014-11-05 | 2014-11-05 17:45 | 2014-11-05 17:45 | OTHER - CA5536VKD2 | 82 | 0 | Yes | Yes | 21.5 | 19.5 | 2 | 11EF6121C33B4801917EA0A506D07436 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6914 |  | 2014-10-01 | 2014-10-01 09:09 | 2014-10-01 09:09 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 20 | 19.7 | 0.4 | 4A4EA6FAC05F436890CAA8A591133623 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4439 |  | 2014-08-13 | 2014-08-13 12:29 | 2014-08-13 20:51 | - | 85 | -8 | Yes | Yes | 14.7 | 17.4 | -2.7 | 1308EA8F190649D2928741A9CDDEED1C |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Vallejo | CA | 94591-7801 |  | 2014-08-13 | 2014-08-13 11:35 | 2014-08-13 11:55 | RUUD - MFD | 76 | 4.2 | Yes | Yes | 23.2 | 20.4 | 2.8 | 436B8C79F1274E399F5769FB8F7B2BDE |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Shafter | CA | 93263-2104 |  | 2014-08-24 | 2014-08-24 19:26 | 2014-08-24 19:28 | GOODMAN - CK49-1B | 97 | -6.8 | Yes | Yes | 25.1 | 21.5 | 3.6 | 36AB521FD6AE4A1780FD19ECB0F3C78F |  | R22 | Non-TXV |  | -7.01% | 1.0701 | 1.963% |  |  |  |  | Non-TXV |  |  | -7.01%
Bakersfield | CA | 93309-4742 |  | 2014-09-16 | 2014-09-16 15:00 | 2014-09-16 15:00 | CARRIER - UNK | 116 | 0 | Yes | Yes | 24.1 | 20.6 | 3.5 | 042535AAD8FB4A4295579227A903A91C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-3824 |  | 2014-08-14 | 2014-08-14 10:07 | 2014-08-14 10:07 | DAY & NIGHT - 591AN060-A | 169 | 0 | Yes | Yes | 16.9 | 18.3 | -1.4 | 375EB4E29D344921B6544C49AA310593 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3984 |  | 2014-10-13 | 2014-10-13 15:36 | 2014-10-13 15:36 | GOODMAN - GSC130181CA | 67 | 0 | Yes | Yes | 20.6 | 20.9 | -0.3 | 3F78E0F6F1FB49FCBE417779508D202E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2159 |  | 2014-08-22 | 2014-08-22 11:48 | 2014-08-22 12:19 | RHEEM - RRNAB024JK06X | 70 | 4.8 | Yes | Yes | 21 | 19.1 | 2 | 665A30B46F8B4449B1E3F6C3AE0CA763 |  | R22 | Non-TXV |  | 6.857% | 0.93143 | 13.18% | [5 empty] | Non-TXV | 6.857%
Fresno | CA | 93711-2159 |  | 2014-08-22 | 2014-08-22 12:23 | 2014-08-22 13:11 | ARCOAIRE - HAC436AKA4 | 194 | 5.8 | Yes | Yes | 20.6 | 18.8 | 1.8 | AED96AC9D4EF4B10B38ECC56144A08A8 |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Bakersfield | CA | 93307-3984 |  | 2014-10-13 | 2014-10-13 15:22 | 2014-10-13 15:22 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 40FA8603712F42958E21F253B0F69D6E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3982 |  | 2014-10-13 | 2014-10-13 14:21 | 2014-10-13 14:21 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 20.7 | 21.5 | -0.8 | FC524447E5C047D7BE08777FAC718879 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2565 |  | 2014-10-31 | 2014-10-31 12:40 | 2014-10-31 12:40 | RHEEM - RRGH05N30JKR | 79 | 0 | Yes | Yes | 4.7 | 17.9 | -13.2 | 4A80B4D89CE44B72B974499C90281840 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2313 |  | 2014-08-22 | 2014-08-22 16:47 | 2014-08-22 17:06 | YORK - DCYZF030N070A | 64 | 3.2 | Yes | Yes | 24.5 | 19.7 | 4.8 | 4FAE68662BA247549AD68DAEF8211506 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Fresno | CA | 93703-2724 |  | 2014-08-06 | 2014-08-06 11:58 | 2014-08-06 12:26 | PAYNE - UNK | 74 | -5.2 | Yes | Yes | 21.5 | 19.2 | 2.3 | 83592E5B9372449EBEC8EC50E3E35820 |  | R22 | Non-TXV |  | -7.027% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.027%
Fairfield | CA | 94534-4334 |  | 2014-09-15 | 2014-09-15 10:46 | 2014-09-17 07:45 | PAYNE - PA13NR036-K | 83 | 4 | Yes | Yes | 14.4 | 17.2 | -2.8 | 01001173D7054178AB2BA6EE22BDC4F3 |  | R22 | Non-TXV |  | 4.819% | 0.95181 | 9.262% | [5 empty] | Non-TXV | 4.819%
Bakersfield | CA | 93307-3983 |  | 2014-10-13 | 2014-10-13 14:55 | 2014-10-13 14:55 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.6 | 22.6 | -1 | F9A628C9479E467B85B9B32B819A5F0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2427 |  | 2014-11-04 | 2014-11-04 16:25 | 2014-11-04 16:42 | OTHER - UNK | 85 | 7.2 | Yes | Yes | 18.7 | 19.5 | -0.8 | E85C23B7550C4CEBBD4CE4BADDD6A00B |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Bakersfield | CA | 93307-1526 |  | 2014-08-11 | 2014-08-11 10:06 | 2014-08-11 10:06 | UNITARY PRODUCTS GROUP - DAYP-F030N070A | 73 | 0 | Yes | Yes | 23.2 | 17.2 | 6 | D5A3CA1B2E9B46558A55B5F6B4FBB952 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7261 |  | 2014-08-22 | 2014-08-22 10:24 | 2014-08-22 11:05 | HEIL - CA3036VKAI | 94 | 0 | Yes | Yes | 18.1 | 19.9 | -1.8 | 6C854CAC0741494E8092989A9B13FA48 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3983 |  | 2014-10-13 | 2014-10-13 14:39 | 2014-10-13 14:39 | CONCORD - CCV10A18A2 | 50 | 0 | Yes | Yes | 21.4 | 21.8 | -0.4 | 9AA7A6DC679846319939DC531B236A7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3982 |  | 2014-10-13 | 2014-10-13 14:42 | 2014-10-13 14:42 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.1 | 21.5 | -0.4 | DF603991B4B8455C8DEF95CF1CE1C5AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1048 |  | 2014-08-13 | 2014-08-13 15:28 | 2014-08-13 15:55 | TRANE - TTX4048A1000AA | 127 | 7 | Yes | Yes | 21.5 | 23.3 | -1.8 | C874C2E1F95D4A5689C3F65CB4C2BCC4 |  | R410A | Non-TXV |  | 5.512% | 0.94488 | 10.59% | [5 empty] | Non-TXV | 5.512%
Vacaville | CA | 95687-7716 |  | 2014-08-13 | 2014-08-13 10:53 | 2014-08-13 20:45 | LENNOX - 14ACX-041-230-03 | 161 | 6 | Yes | Yes | 16.1 | 18.4 | -2.3 | 79B68CA6DB8748188F3B2E8952D5757B |  | R22 | Non-TXV |  | 3.727% | 0.96273 | 7.162% | [5 empty] | Non-TXV | 3.727%
Milpitas | CA | 95035-0000 |  | 2014-09-19 | 2014-09-19 08:10 | 2014-09-19 08:47 | - 24ABB330A310 | 74 | 5 | Yes | Yes | 17.7 | 17.5 | 0.2 | 123FCB256F2C4B4881ADA040ABEFF8E9 |  | R410A | TXV |  | 6.757% | 0.93243 | 12.98% | [5 empty] | TXV | 6.757%
Vacaville | CA | 95688-2738 |  | 2014-08-12 | 2014-08-12 14:54 | 2014-08-12 20:33 | TRANE - YCP042F1M0AB | 85 | 3 | Yes | Yes | 17.6 | 18.7 | -1.1 | 68470B6D9E954B81B1212151F12F1300 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Bakersfield | CA | 93307-3895 |  | 2014-10-13 | 2014-10-13 15:48 | 2014-10-13 15:48 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | A832167FDF574F39BDADB4A6E88C4EB8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3983 |  | 2014-10-13 | 2014-10-13 15:33 | 2014-10-13 15:33 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 18.9 | 21.8 | -2.9 | 52AFA05AD618496B894F852B4F7A6F7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2614 |  | 2014-08-22 | 2014-08-22 15:02 | 2014-08-22 15:02 | PAYNE - UNK | 76 | 0 | Yes | Yes | 19.6 | 19.6 | 0 | 77F719BAA2F848588D2214397F34EDEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2341 |  | 2014-10-29 | 2014-10-29 17:22 | 2014-10-29 17:22 | RHEEM - RRRLC024JK06X | 97 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | 64237F3A6A5A40DF9E3CF1B2956DFDB9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7867 |  | 2014-09-10 | 2014-09-10 11:52 | 2014-09-10 12:56 | RHEEM - 3AJA36AD175 | 106 | 4.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | 35FB6E5029004BA1B2E4CEA4441CAA80 |  | R22 | Non-TXV |  | 4.151% | 0.95849 | 7.977% | [5 empty] | Non-TXV | 4.151%
Bakersfield | CA | 93312-5767 |  | 2014-11-11 | 2014-11-11 18:17 | 2014-11-11 18:19 | GOODMAN - CLJ60-1 | 141 | -10 | Yes | Yes | 22.3 | 17.6 | 4.7 | 00FB10A556064D5B963C385771756958 |  | R22 | Non-TXV |  | -7.092% | 1.0709 | 1.986% |  |  |  |  | Non-TXV |  |  | -7.092%
Bakersfield | CA | 93304-2363 |  | 2014-08-21 | 2014-08-21 10:44 | 2014-08-21 10:44 | GOODMAN - GPH1336M41CA | 128 | 0 | Yes | Yes | 22.6 | 21.3 | 1.3 | F27E9D1449A849089D54A101F604ACE9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2539 |  | 2014-10-30 | 2014-10-30 13:13 | 2014-10-30 13:13 | RHEEM - RRGH07N36JKR | 81 | 0 | Yes | Yes | 17.6 | 19.9 | -2.3 | 8741B48F52D448B693A2B4C101E9C0F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3983 |  | 2014-10-13 | 2014-10-13 15:12 | 2014-10-13 15:12 | GOODMAN - GSC130241FA | 77 | 0 | Yes | Yes | 21.1 | 22 | -0.9 | F0DF9543AEED41829FDC2BE63F54F480 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2363 |  | 2014-08-21 | 2014-08-21 10:47 | 2014-08-21 10:47 | GOODMAN - GPH1336M41C | 128 | 0 | Yes | Yes | 23 | 22.3 | 0.7 | 52D3D4B8DFC64909A6975C8C5E305829 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2427 |  | 2014-08-09 | 2014-08-09 17:02 | 2014-08-09 17:04 | BRYANT - 583ANW0360NAAF | 84 | 7.3 | Yes | Yes | 20.9 | 20.4 | 0.5 | 8DD5F20407BD4C02A730599926E16B36 |  | R22 | Non-TXV |  | 8.69% | 0.9131 | 16.7% | [5 empty] | Non-TXV | 8.69%
Bakersfield | CA | 93307-3983 |  | 2014-10-13 | 2014-10-13 15:08 | 2014-10-13 15:24 | GOODMAN - GSC130181FA | 75 | 5.8 | Yes | Yes | 21 | 22.6 | -1.6 | EDD7FB05118342C2B549BB434C312830 |  | R22 | Non-TXV |  | 7.733% | 0.92267 | 14.86% | [5 empty] | Non-TXV | 7.733%
Davis | CA | 95616-3912 |  | 2014-08-15 | 2014-08-15 10:17 | 2014-08-15 10:35 | GOODMAN - PG036075-1AB REVC | 90 | 6.2 | Yes | Yes | 21.8 | 20.4 | 1.4 | 228AD3FE5FA247D9A154032F65D16658 |  | R22 | Non-TXV |  | 6.889% | 0.93111 | 13.24% | [5 empty] | Non-TXV | 6.889%
Bakersfield | CA | 93307-3892 |  | 2014-10-13 | 2014-10-13 11:41 | 2014-10-13 11:41 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 22.3 | 20.7 | 1.6 | 2A82F5C5F4FB440F81C32DF5F565D363 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3892 |  | 2014-10-13 | 2014-10-13 11:46 | 2014-10-13 11:46 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 20.5 | 20.3 | 0.2 | 31BA0279CE7F4C60968F609BA5E51B97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3979 |  | 2014-10-13 | 2014-10-13 12:31 | 2014-10-13 12:31 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 18.9 | 20.7 | -1.8 | 9BF9BF00FCB44804AF44A536EEEFC101 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4212 |  | 2014-08-26 | 2014-08-26 08:27 | 2014-08-26 08:27 | TRANE - TTN030C100C2 | 95 | 0 | Yes | Yes | 23.3 | 20.9 | 2.4 | 8F7204E0EBA74E3C8363118559AF5185 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3881 |  | 2014-10-13 | 2014-10-13 12:51 | 2014-10-13 12:51 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | 5A83DB0CA18F4AC696C467EC4ADB33CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1527 |  | 2014-09-09 | 2014-09-09 12:13 | 2014-09-09 12:13 | CARRIER - 18GS-024040301 | 53 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | 202AB37902404955A381DD51C30991E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2521 |  | 2014-10-10 | 2014-10-10 14:53 | 2014-10-10 15:10 | ICP - WPG348409LKC1 | 85 | 7.6 | Yes | Yes | 22.5 | 20.5 | 2 | 3EA23E2F905F49038F115438D11090BA |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Bakersfield | CA | 93307-3965 |  | 2014-10-12 | 2014-10-12 16:54 | 2014-10-12 16:54 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 21.2 | 21.8 | -0.5 | 69E4EEA7A98047888BEB1CB19969A232 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6240 |  | 2014-08-20 | 2014-08-20 13:12 | 2014-08-20 13:39 | CARRIER - UNK | 96 | 21.6 | Yes | Yes | 21.5 | 20.4 | 1.1 | B19205DA7F4147B6B1756C6152AC7E10 |  | R22 | Non-TXV |  | 22.5% | 0.775 | 43.24% | [5 empty] | Non-TXV | 22.5%
Bakersfield | CA | 93307-3894 |  | 2014-10-13 | 2014-10-13 13:40 | 2014-10-13 13:40 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 20.9 | 21.8 | -0.9 | E0D9B983CA9C45F192996C8C8BEAD33A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3979 |  | 2014-10-13 | 2014-10-13 13:20 | 2014-10-13 13:20 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 22.2 | 21 | 1.2 | F845CF52974D4C5D9648FE2B51BF413F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1742 |  | 2014-08-09 | 2014-08-09 16:56 | 2014-08-09 16:59 | GOODMAN - GPG13300451BB | 77 | 3.7 | Yes | Yes | 23.4 | 20.2 | 3.3 | E998A7C7A74249CAAA735BC17DF86C69 |  | R22 | Non-TXV |  | 4.805% | 0.95195 | 9.235% | [5 empty] | Non-TXV | 4.805%
Rio Vista | CA | 94571-2253 |  | 2014-09-03 | 2014-09-03 10:41 | 2014-09-03 11:42 | YORK - H2RCO2460634 | 85 | 2.5 | Yes | Yes | 20.2 | 19.9 | 0.3 | C35C3894A8F14395A10632CAFB3E7E01 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
San Jose | CA | 95119-1704 |  | 2014-08-13 | 2014-08-13 13:01 | 2014-08-13 13:22 | TRANE - TTN036C100B4 | 100 | 39.1 | Yes | Yes | 21 | 19.3 | 1.7 | 95EBD65DA423449997A1C6610706C68A |  | R22 | Non-TXV |  | 39.1% | 0.609 | 75.14% | [5 empty] | Non-TXV | 39.1%
Suisun City | CA | 94585-6312 |  | 2014-09-09 | 2014-09-09 08:53 | 2014-09-09 12:00 | CARRIER - 38TH036300 | 83 | 2.7 | Yes | Yes | 18.2 | 18.5 | -0.3 | 2FBF8E79B92A4E2FB2F4036DFDF652E7 |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Fresno | CA | 93726-0423 |  | 2014-08-18 | 2014-08-18 09:56 | 2014-08-18 10:23 | GOODMAN - GPG154911541AB | 167 | 5.9 | Yes | Yes | 24.3 | 19.1 | 5.2 | BF1E52D71E104D33A079D87B207E898F |  | R410A | Non-TXV |  | 3.533% | 0.96467 | 6.79% | [5 empty] | Non-TXV | 3.533%
Bakersfield | CA | 93313-5028 |  | 2014-10-28 | 2014-10-28 20:48 | 2014-10-28 21:05 | YORK - H3RC060S06HA | 85 | 3.5 | Yes | Yes | 19.2 | 21 | -1.8 | D342A05E90A744E08435AF37EB7C9326 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Bakersfield | CA | 93309-3481 |  | 2014-09-13 | 2014-09-13 15:07 | 2014-09-13 15:07 | ALLEGIANCE - PGB48809020 | 132 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 9A2A0D3514944F9F8629EA1A826E5C81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1608 |  | 2014-08-11 | 2014-08-11 16:07 | 2014-08-11 17:01 | CARRIER - 48KHA136300BE | 84 | 3.3 | Yes | Yes | 20.9 | 20.4 | 0.5 | FF99278A8D81471A96B1108D675906B7 |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Bakersfield | CA | 93312-6832 |  | 2014-10-14 | 2014-10-14 15:51 | 2014-10-14 16:07 | OTHER - UNK | 85 | 9.8 | Yes | Yes | 20 | 22.3 | -2.3 | 976F59BAF9584D7CBA727E7E7726C207 |  | R22 | Non-TXV |  | 11.53% | 0.88471 | 22.16% | [5 empty] | Non-TXV | 11.53%
Woodland | CA | 95695-5856 |  | 2014-09-15 | 2014-09-15 12:33 | 2014-09-15 16:49 | CARRIER - 9804-030479 | 55 | 3.9 | Yes | Yes | 19.9 | 20.4 | -0.5 | A67D7C9243D642D8B175A449C88305A0 |  | R22 | Non-TXV |  | 7.091% | 0.92909 | 13.63% | [5 empty] | Non-TXV | 7.091%
Fresno | CA | 93722-1164 |  | 2014-08-07 | 2014-08-07 12:42 | 2014-08-07 13:13 | RHEEM - RAK048JAZ | 103 | 25.4 | Yes | Yes | 21.5 | 20.4 | 1.1 | 9945FE4734BA41049BDC55C07FA06502 |  | R22 | Non-TXV |  | 24.66% | 0.7534 | 47.39% | [5 empty] | Non-TXV | 24.66%
Fresno | CA | 93703-3701 |  | 2014-08-06 | 2014-08-06 14:56 | 2014-08-06 14:56 | KENMORE - UNK | 60 | 0 | Yes | Yes | 40.7 | 19.6 | 21.1 | A8223B7F8B1341EABD17246EED6B1D70 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2200 |  | 2014-10-17 | 2014-10-17 09:36 | 2014-10-17 09:36 | YORK - D1NP036N05606 | 108 | 0 | Yes | Yes | 16.3 | 18.7 | -2.4 | 216659BFE6E54E11BAB773C97219E3EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94534-1429 |  | 2014-09-09 | 2014-09-09 10:02 | 2014-09-09 12:01 | CARRIER - 48VTNA480903OTP | 85 | 2.5 | Yes | Yes | 14.9 | 16.4 | -1.5 | 7BE7D5F403F54E29907B58D1440072CC |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Bakersfield | CA | 93307-3965 |  | 2014-10-12 | 2014-10-12 17:10 | 2014-10-12 17:10 | DUCANE - 2AC13B18P1A | 84 | 0 | Yes | Yes | 20.6 | 22.1 | -1.5 | DCEA1B7823BC4E7F9B18CD43B76F2929 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3202 |  | 2014-09-09 | 2014-09-09 13:05 | 2014-09-09 13:05 | TRANE - 591AN048-C | 123 | 0 | Yes | Yes | 16.4 | 16.1 | 0.3 | 46E51BD5406B43B7A54448D62C163978 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1196 |  | 2014-09-26 | 2014-09-26 16:28 | 2014-09-26 16:28 | TRANE - 4YCC0324A1064AA | 93 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | A585A65B0BD14CC6A9117808C82A3702 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4309 |  | 2014-08-12 | 2014-08-12 09:52 | 2014-08-12 10:31 | CARRIER - 48SS-024060331-- | 38 | 7.3 | Yes | Yes | 23.8 | 19.9 | 3.9 | 0AAF9E4C16564610A159099022961E18 |  | R22 | Non-TXV |  | 19.21% | 0.80789 | 36.92% | [5 empty] | Non-TXV | 19.21%
Fairfield | CA | 94533-8020 |  | 2014-08-15 | 2014-08-15 11:09 | 2014-08-15 11:09 | - | 85 | 0 | Yes | Yes | 16.8 | 17.1 | -0.3 | 1E55A77A37434F4EAE9273E7BB1CC454 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3982 |  | 2014-10-13 | 2014-10-13 14:50 | 2014-10-13 14:50 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | FCC17128E9FB4A5595E0F7B2BC66686D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-4525 |  | 2014-08-13 | 2014-08-13 12:43 | 2014-08-13 13:08 | PHILCO - | 104 | 5.3 | Yes | Yes | 17.5 | 20.2 | -2.7 | 8796B3F4093348B89D79CBFE0C301FF1 |  | R410A | Non-TXV |  | 5.096% | 0.94904 | 9.794% | [5 empty] | Non-TXV | 5.096%
Bakersfield | CA | 93301-5926 |  | 2014-09-09 | 2014-09-09 17:28 | 2014-09-09 17:30 | COLEMAN - 95480901 | 102 | 4 | Yes | Yes | 21.3 | 19.9 | 1.4 | 99FF30E1EC5D456D8F609E749377C8F0 |  | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Fresno | CA | 93703-4739 |  | 2014-08-19 | 2014-08-19 15:10 | 2014-08-19 15:34 | YORK - DAYPF042N080A | 150 | 9.7 | Yes | Yes | 20.3 | 21.9 | -1.6 | F8B71E85C72D47E79F00E7FEEECE027D |  | R22 | Non-TXV |  | 6.467% | 0.93533 | 12.43% | [5 empty] | Non-TXV | 6.467%
Bakersfield | CA | 93305-2910 |  | 2014-08-13 | 2014-08-13 15:11 | 2014-08-13 15:11 | OTHER - R2A336GKK2 | 131 | 0 | Yes | Yes | 19.4 | 18 | 1.4 | 2417BE32C4CE43D397815461EBA011B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6806 |  | 2014-10-20 | 2014-10-20 12:20 | 2014-10-20 12:20 | UNITARY PRODUCTS GROUP - H1RD048506H | 227 | 0 | Yes | Yes | 21.5 | 20.2 | 1.4 | 3BADCE927777428B9F03B96AC0B125D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6806 |  | 2014-10-20 | 2014-10-20 12:17 | 2014-10-20 12:17 | UNITARY PRODUCTS GROUP - H1RD036S06G | 145 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | 325DDD0BB0E84E8999E8091A956F4B3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7140 |  | 2014-08-13 | 2014-08-13 12:12 | 2014-08-13 13:01 | TRANE - 2TTBD42A1000AA | 97 | 4.2 | Yes | Yes | 15.8 | 18.3 | -2.5 | 500C7A7E192A4B7497D5DDFDB3EF6D7A |  | R410A | Non-TXV |  | 4.33% | 0.9567 | 8.321% | [5 empty] | Non-TXV | 4.33%
Bakersfield | CA | 93304-7144 |  | 2014-08-21 | 2014-08-21 13:28 | 2014-08-21 13:28 | AMANA - PGD36C075399 | 110 | 0 | Yes | Yes | 20 | 22.1 | -2.1 | 1A03739C79594490A9CDA2C3611DE58E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1857 |  | 2014-09-29 | 2014-09-29 12:42 | 2014-09-29 12:42 | PAYNE - PA10JA036-A | 84 | 0 | Yes | Yes | 13.4 | 15.5 | -2.1 | B64EF8A5A4FF4E189830F6236AB906FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3982 |  | 2014-10-13 | 2014-10-13 14:37 | 2014-10-13 14:37 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | 2E40AD7D5940447CA92345FE12D789CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3223 |  | 2014-09-19 | 2014-09-19 16:23 | 2014-09-19 16:23 | CARRIER - UNK | 108 | 0 | Yes | Yes | 21.2 | 17.5 | 3.7 | 3612C62DBA3C4587B83CD1E6D23684C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5972 |  | 2014-09-08 | 2014-09-08 19:40 | 2014-09-08 19:44 | OTHER - N/A | 85 | 9.2 | Yes | Yes | 19.7 | 20.7 | -1 | 8851BB83B9F24F6DAAA52739197D4641 |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
Bakersfield | CA | 93304-7118 |  | 2014-08-13 | 2014-08-13 13:27 | 2014-08-13 13:27 | PAYNE - PY3PNA036090NB | 114 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | 738C5EBAA64C42798EA92CAAE2BAD927 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3892 |  | 2014-10-13 | 2014-10-13 12:26 | 2014-10-13 12:26 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 19.3 | 22 | -2.7 | 69765A59D3E74295B6756800C07DB204 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2335 |  | 2014-10-08 | 2014-10-08 10:49 | 2014-10-08 10:49 | GOODMAN - CKJ36-1B | 97 | 0 | Yes | Yes | 21.4 | 20.9 | 0.5 | B65E129D9CFA4BACA038E449B4B46658 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1743 |  | 2014-09-09 | 2014-09-09 17:23 | 2014-09-09 17:25 | RHEEM - RRNAA036JK06X | 114 | 6.2 | Yes | Yes | 20.7 | 19.3 | 1.4 | 80DD433BDCEA4C3C906AC05E677D5F3F |  | R22 | TXV |  | 5.439% | 0.94561 | 10.45% | [5 empty] | TXV | 5.439%
Bakersfield | CA | 93307-4011 |  | 2014-10-01 | 2014-10-01 14:38 | 2014-10-01 14:38 | ICP - PGME24G0401 | 69 | 0 | Yes | Yes | 23 | 21.9 | 1.1 | 6518D4A413B74CF88A06CF324AEF16D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2630 |  | 2014-08-18 | 2014-08-18 12:44 | 2014-08-18 13:05 | YORK - D1NH060N09006C | 140 | 4.9 | Yes | Yes | 20.4 | 18.3 | 2.1 | DBE1D527456E47ECAF3E424FF7039872 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Bakersfield | CA | 93307-3981 |  | 2014-10-13 | 2014-10-13 13:23 | 2014-10-13 13:23 | GOODMAN - CC1V10A241 | 50 | 0 | Yes | Yes | 20.9 | 22.6 | -1.7 | BCDDB98DCED14695B49D3E0B0B1591BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-4131 |  | 2014-08-13 | 2014-08-13 11:19 | 2014-08-13 11:38 | CARRIER - TTR060C100A0 | 147 | -13.8 | Yes | Yes | 20.6 | 18.7 | 1.9 | 86CD2B288FAB4FF4B23F4D9342251464 |  | R22 | Non-TXV |  | -9.388% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.388%
Bakersfield | CA | 93313-2206 |  | 2014-09-15 | 2014-09-15 13:51 | 2014-09-15 13:51 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 11.4 | 19.5 | -8.1 | 5CDB94CF47AE4B9695D4D1488FDF8068 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3981 |  | 2014-10-13 | 2014-10-13 13:57 | 2014-10-13 13:57 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 21 | 22.9 | -1.9 | 5F38755B27D146CF9550287B210C6B6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2895 |  | 2014-08-12 | 2014-08-12 12:01 | 2014-08-12 13:32 | MAMMOTH - HS29-036-2P | 70 | 5 | Yes | Yes | 24.1 | 19.4 | 4.7 | AEE7161C33FD4FE6A9FBE17604821684 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Pittsburg | CA | 94565-5641 |  | 2014-10-03 | 2014-10-03 11:33 | 2014-10-03 11:33 | RHEEM - UNK | 85 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | D0AD6D0D7D7B4900A174BEFD39026ADD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2913 |  | 2014-08-15 | 2014-08-15 11:18 | 2014-08-15 11:50 | GE - BGG736B1B | 68 | 3.3 | Yes | Yes | 20.4 | 18.8 | 1.6 | 3BF90BF343494A1887CD429BA804DB07 |  | R22 | Non-TXV |  | 4.853% | 0.95147 | 9.326% | [5 empty] | Non-TXV | 4.853%
San Jose | CA | 95120-4240 |  | 2014-08-14 | 2014-08-14 11:53 | 2014-08-14 12:19 | BRYANT - 561CJ042 | 80 | 2.9 | Yes | Yes | 18.5 | 19.4 | -0.9 | DAAE37C0BF9148EE8A34F9C102F88389 | Remove refrigerant: 3.1 oz | R22 | TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | TXV | 3.625%
San Jose | CA | 95120-4240 |  | 2014-08-14 | 2014-08-14 12:43 | 2014-08-14 12:58 | BRYANT - 561CJ042 | 80 | -3 | Yes | Yes | 18.5 | 18.8 | -0.3 | 903DBE59C79C4C56BA1583DF7AA19398 |  | R22 | TXV |  | -3.75% | 1.0375 | 1.05% |  |  |  |  | TXV |  |  | -3.75%
Bakersfield | CA | 93311-2405 |  | 2014-10-02 | 2014-10-02 10:31 | 2014-10-02 10:31 | OTHER - PY3GNAA42090NA | 106 | 0 | Yes | Yes | 23.6 | 18 | 5.6 | E221382DAD2447308ABA9D6FB2FBD806 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7423 |  | 2014-08-14 | 2014-08-14 14:04 | 2014-08-14 20:45 | CARRIER - 38EH036300 | 116 | 18.2 | Yes | Yes | 16 | 16.1 | -0.1 | C22314EB4D024E459D0F0004EF9D6C18 |  | R22 | Non-TXV |  | 15.69% | 0.8431 | 30.15% | [5 empty] | Non-TXV | 15.69%
Davis | CA | 95618-1552 |  | 2014-08-15 | 2014-08-15 12:13 | 2014-08-15 12:44 | COMFORT AIRE - M2AC3036A000AA | 104 | 5.3 | Yes | Yes | 21.7 | 20.4 | 1.3 | 2C1A78B79F9C4CD99CC5B051F13703DD |  | R22 | Non-TXV |  | 5.096% | 0.94904 | 9.794% | [5 empty] | Non-TXV | 5.096%
Bakersfield | CA | 93313-2226 |  | 2014-10-19 | 2014-10-19 17:04 | 2014-10-19 17:07 | RHEEM - RRNA-C048JK10X | 98 | 6.1 | Yes | Yes | 21.7 | 21 | 0.7 | EF2B1AB6E3FF42899371EB1980D6BAEB |  | R22 | TXV |  | 6.224% | 0.93776 | 11.96% | [5 empty] | TXV | 6.224%
Bakersfield | CA | 93304-1741 |  | 2014-09-10 | 2014-09-10 11:54 | 2014-09-10 11:54 | AMERICAN STANDARD - YCY048G1HTCT0AB | 186 | 0 | Yes | Yes | 22.2 | 20.8 | 1.4 | 5B00B4D1A02542A5AB9E1BA1D649D5DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3139 |  | 2014-08-13 | 2014-08-13 12:30 | 2014-08-13 12:30 | GOODMAN - GSC130601CB | 131 | 0 | Yes | Yes | 22.6 | 20.8 | 1.8 | 04E7998EB6AE4CBBA9C4A66480F41DB9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4466 |  | 2014-09-12 | 2014-09-12 11:01 | 2014-09-12 15:02 | RHEEM - | 110 | 4.2 | Yes | Yes | 22.3 | 19.4 | 2.9 | 31F1449205AC4FC8941098308CA560B1 | Add refrigerant: 3.8 oz | R22 | Non-TXV |  | 3.818% | 0.96182 | 7.338% | [5 empty] | Non-TXV | 3.818%
Bakersfield | CA | 93304-2530 |  | 2014-08-13 | 2014-08-13 10:51 | 2014-08-13 10:51 | CARRIER - 40GXN042090301 | 118 | 0 | Yes | Yes | 24 | 23.2 | 0.8 | 01B48750E73840889F799A216ACDE548 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3266 |  | 2014-08-28 | 2014-08-28 12:08 | 2014-08-28 16:12 | CARRIER - ERCS0301BBB | 93 | 5.1 | Yes | Yes | 21.5 | 21 | 0.5 | 122E28F92EFE422CBDB1FFBE7B6D0FBB |  | R22 | Non-TXV |  | 5.484% | 0.94516 | 10.54% | [5 empty] | Non-TXV | 5.484%
Pittsburg | CA | 94565-5517 |  | 2014-09-25 | 2014-09-25 09:35 | 2014-09-25 09:35 | BRYANT - 561CJ030 | 76 | 0 | Yes | Yes | 14.4 | 17 | -2.6 | D28B70B86AE947BF9B05AF24799611C6 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3881 |  | 2014-10-13 | 2014-10-13 11:49 | 2014-10-13 11:49 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 22.1 | 21.7 | 0.4 | 6D640FFE37B2469594402859347F9946 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Mc Farland | CA | 93250-1610 |  | 2014-10-28 | 2014-10-28 10:50 | 2014-10-28 10:50 | RHEEM - UNK | 98 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 2D5DE423EF1341049AFEA46DCE3BC7F4 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2225 |  | 2014-10-06 | 2014-10-06 15:57 | 2014-10-06 16:15 | RHEEM - RRNA-C048JK10X | 85 | 5.4 | Yes | Yes | 23.9 | 18 | 5.9 | 64FDCB8B92C74546BEE9F6BEF64E22B4 |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Vacaville | CA | 95687-3398 |  | 2014-08-13 | 2014-08-13 16:06 | 2014-08-13 16:06 | GUARDIAN - GHG018S21S1A | 85 | 0 | Yes | Yes | 18.5 | 18.1 | 0.4 | 0F0D9981077742F2A4ACD03D5DD81B7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3980 |  | 2014-10-13 | 2014-10-13 13:17 | 2014-10-13 13:17 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.6 | 22 | -0.4 | 780E3E3168A645E681BCCCDD1C750D7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3702 |  | 2014-08-11 | 2014-08-11 16:18 | 2014-08-11 18:39 | GOODMAN - PGJ042075-1 | 90 | 5.5 | Yes | Yes | 19.9 | 19.9 | 0 | C74478F40C484B1A95DF1DE0C24005A2 |  | R22 | Non-TXV |  | 6.111% | 0.93889 | 11.74% | [5 empty] | Non-TXV | 6.111%
Bakersfield | CA | 93304-7316 |  | 2014-09-24 | 2014-09-24 13:05 | 2014-09-24 13:05 | ICP - PGC048K080A | 86 | 0 | Yes | Yes | 20.3 | 23.1 | -2.8 | 80E57A9612034E67847B74E6E3ECE03C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7039 |  | 2014-08-13 | 2014-08-13 09:51 | 2014-08-13 09:51 | TRANE - YCZ036F1M0BD | 160 | 0 | Yes | Yes | 19.3 | 19.9 | -0.6 | 0D49F184D78E4B7DA0759B393015DD8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7233 |  | 2014-08-13 | 2014-08-13 10:41 | 2014-08-13 10:41 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21.3 | 20.6 | 0.7 | 5B21C91AA3924A8EBEBEFB29C6F074A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4418 |  | 2014-09-24 | 2014-09-24 12:14 | 2014-09-24 12:14 | ICP - PGC036K060E | 68 | 0 | Yes | Yes | 21.5 | 19.9 | 1.6 | 2350D5D47325442DBB39FE87A38E48CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4250 |  | 2014-10-20 | 2014-10-20 09:35 | 2014-10-20 09:35 | CARRIER - 584BN60042060AABF | 75 | 0 | Yes | Yes | 22.5 | 19.1 | 3.4 | EE2D6F2706854B54B30925F6BE903FEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4514 |  | 2014-09-10 | 2014-09-10 15:34 | 2014-09-10 15:34 | AMERICAN STANDARD - YCC048F1M0BH | 103 | 0 | Yes | Yes | 19.2 | 20.2 | -0.9 | 019E31C1540A4BDE873E3F7F557F1E23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3881 |  | 2014-10-13 | 2014-10-13 12:53 | 2014-10-13 12:53 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21 | 23.1 | -2.1 | 6F834DEB73644109B4011CCF18A176A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6447 |  | 2014-10-07 | 2014-10-07 12:32 | 2014-10-09 06:47 | CARRIER - 48GCS-042090301 | 85 | 4.3 | Yes | Yes | 11.7 | 14.4 | -2.7 | 5D11EC714670484DBFB4D78617F60A10 |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Wasco | CA | 93280-1944 |  | 2014-08-09 | 2014-08-09 17:07 | 2014-08-09 17:09 | PAYNE - NA | 85 | 3.4 | Yes | Yes | 19.2 | 19 | 0.2 | FAB8E57AF5114A99B4B1994E9310E32A |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Bakersfield | CA | 93313-6023 |  | 2014-10-06 | 2014-10-06 13:41 | 2014-10-06 14:04 | RUUD - UNK | 96 | 18.2 | Yes | Yes | 21 | 23.1 | -2.1 | 9B2E1B0E815847BAAD35FEB7BE2F824B |  | R22 | Non-TXV |  | 18.96% | 0.81042 | 36.43% | [5 empty] | Non-TXV | 18.96%
Bakersfield | CA | 93307-3894 |  | 2014-10-13 | 2014-10-13 13:45 | 2014-10-13 13:45 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 20.9 | 21 | -0.1 | 8951339540C0495588564FD7D93DE51F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2505 |  | 2014-08-14 | 2014-08-14 13:20 | 2014-08-14 13:43 | GOODMAN - CKL49-1 | 109 | 3.5 | Yes | Yes | 20.9 | 18.5 | 2.4 | 7ED2208854774D7BB3A2657B975A34D3 |  | R22 | Non-TXV |  | 3.211% | 0.96789 | 6.171% | [5 empty] | Non-TXV | 3.211%
W Sacramento | CA | 95691-5430 |  | 2014-08-28 | 2014-08-28 09:54 | 2014-08-28 10:13 | CARRIER - 561AJ042-D | 80 | 6.4 | Yes | Yes | 20.8 | 20.8 | 0 | E107811AB9F54D7099F172BAB64AB79D |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Bakersfield | CA | 93304-5311 |  | 2014-09-10 | 2014-09-10 14:20 | 2014-09-10 14:20 | ICP - PGC036K060B | 71 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | C198D3F95C9C4B5688A4C52B4F163C9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4311 |  | 2014-09-13 | 2014-09-13 12:39 | 2014-09-13 12:39 | OTHER - UNK | 111 | 0 | Yes | Yes | 12.7 | 15.5 | -2.8 | 15B752B11B2843EBA9BEC8AD512C7164 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5553 |  | 2014-09-30 | 2014-09-30 11:30 | 2014-09-30 11:30 | OTHER - UNK | 100 | 0 | Yes | Yes | 22 | 19.7 | 2.4 | 8AF879F7BCF44FD3B0D64BA4FDAFB0A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1327 |  | 2014-11-17 | 2014-11-17 10:31 | 2014-11-17 10:31 | PAYNE - PA13NA036-B | 72 | 0 | Yes | Yes | 21.7 | 17.3 | 4.5 | DFC063E244064A7AA17A0287BBF093DF |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3964 |  | 2014-08-13 | 2014-08-13 09:57 | 2014-08-13 09:57 | GOODMAN - GPG154211541AA | 162 | 0 | Yes | Yes | 20.1 | 23.1 | -3 | 077187522B9140AFB6D419580F1A7916 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4421 |  | 2014-08-13 | 2014-08-13 11:10 | 2014-08-13 11:10 | CARRIER - 48TMX036---301 | 109 | 0 | Yes | Yes | 27.4 | 21.5 | 5.9 | 5E455651E2F4463592B975FE615589B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3965 |  | 2014-09-04 | 2014-09-04 09:51 | 2014-09-04 09:51 | CARRIER - UNK | 85 | 0 | Yes | Yes | 21.3 | 17.7 | 3.6 | 17A583B7BE6B467EA25DA02FB788C611 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3710 |  | 2014-10-03 | 2014-10-03 13:46 | 2014-10-03 16:19 | AIRE-FLO - PGD330060K001C1 | 98 | 4.5 | Yes | Yes | 20.5 | 20.4 | 0.1 | 5B1EF482EBF0426197833AE1CC336F71 |  | R22 | Non-TXV |  | 4.592% | 0.95408 | 8.824% | [5 empty] | Non-TXV | 4.592%
San Jose | CA | 95120-3122 |  | 2014-08-15 | 2014-08-15 12:13 | 2014-08-15 12:40 | PAYNE - PA10JA04800ACAA | 96 | -11.9 | Yes | Yes | 15.2 | 18 | -2.8 | 8D72F23C1B9044ECBC9445B4414E9090 |  | R22 | TXV |  | -12.4% | 1.124 | 3.471% |  |  |  |  | TXV |  |  | -12.4%
Woodland | CA | 95776-9400 |  | 2014-09-29 | 2014-09-29 13:11 | 2014-09-29 13:32 | CLIMATEMASTER - DRS604818D | 119 | 3.6 | Yes | Yes | 22.3 | 20.4 | 1.9 | 58A96EBAC9354C90A6875C48584121EC |  | R22 | Non-TXV |  | 3.025% | 0.96975 | 5.814% | [5 empty] | Non-TXV | 3.025%
Fairfield | CA | 94533-1409 |  | 2014-08-27 | 2014-08-27 08:36 | 2014-08-27 11:07 | HEIL - N2A336AKA200 | 94 | 3.2 | Yes | Yes | 16.6 | 17.9 | -1.3 | 199ACE27F533444DB953B75FACB31940 |  | R22 | Non-TXV |  | 3.404% | 0.96596 | 6.542% | [5 empty] | Non-TXV | 3.404%
Woodland | CA | 95776-5399 |  | 2014-09-05 | 2014-09-05 09:43 | 2014-09-05 10:01 | YORK - H1DE042S06B | 99 | 9.3 | Yes | Yes | 18.6 | 19.9 | -1.3 | 3B75C66F4A4F4C5A91DE46236AE42CE7 |  | R22 | Non-TXV |  | 9.394% | 0.90606 | 18.05% | [5 empty] | Non-TXV | 9.394%
Bakersfield | CA | 93304-4013 |  | 2014-09-10 | 2014-09-10 15:01 | 2014-09-10 15:01 | DAY & NIGHT - 587ANZ036060 | 90 | 0 | Yes | Yes | 25.6 | 20.9 | 4.7 | A6DD08A731974FC6804A57A4164EF2EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6226 |  | 2014-08-13 | 2014-08-13 14:47 | 2014-08-13 14:47 | LENNOX - UKN | 90 | 0 | Yes | Yes | 18.5 | 19.9 | -1.4 | 404185BC64C44D6FBA3B896E28611E52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3237 |  | 2014-08-21 | 2014-08-21 11:19 | 2014-08-21 11:19 | PAYNE - PY2PNB060090NAAA | 55 | 0 | Yes | Yes | 26.6 | 20.8 | 5.8 | B4BF97EA90E34B91B1D7ACA9154C5914 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5402 |  | 2014-09-09 | 2014-09-09 10:13 | 2014-09-09 10:31 | CARRIER - 24ABA324A310 | 74 | 6.7 | Yes | Yes | 20.5 | 20.7 | -0.2 | 7A6AAF42C60245E8AD4487C5B044B99E |  | R410A | Non-TXV |  | 9.054% | 0.90946 | 17.4% | [5 empty] | Non-TXV | 9.054%
Bakersfield | CA | 93311-2668 |  | 2014-09-24 | 2014-09-24 15:08 | 2014-09-24 15:08 | OTHER - 13AJA30A01757 | 101 | 0 | Yes | Yes | 19.6 | 20.3 | -0.6 | 89EC258480804427AD10504752E6D3B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4720 |  | 2014-09-16 | 2014-09-16 14:06 | 2014-09-16 14:06 | YORK - D1NH042N06506C | 94 | 0 | Yes | Yes | 25.5 | 20 | 5.5 | E8FDAD1A354A44C3A37E50AD5360154B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5317 |  | 2014-10-29 | 2014-10-29 13:11 | 2014-10-29 13:11 | COLEMAN - CCJF42S41S1A | 68 | 0 | Yes | Yes | 23 | 20.4 | 2.6 | 5132825F4BB7404B97E22BC3DB6633C8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4157 |  | 2014-09-16 | 2014-09-16 09:25 | 2014-09-16 09:51 | TRANE - 4TTB3036A1000AA | 103 | 3.8 | Yes | Yes | 20.8 | 20.4 | 0.4 | 08FA101A27E04EC49A2D1492D5210BFA |  | R410A | TXV |  | 3.689% | 0.96311 | 7.09% | [5 empty] | TXV | 3.689%
Bakersfield | CA | 93309-5967 |  | 2014-10-08 | 2014-10-08 11:53 | 2014-10-08 12:09 | OTHER - UNK | 85 | 11.5 | Yes | Yes | 21 | 23.4 | -2.4 | 11FAAE4CADB1424482D31A8E81C5EF81 |  | R22 | Non-TXV |  | 13.53% | 0.86471 | 26% | [5 empty] | Non-TXV | 13.53%
Bakersfield | CA | 93304-5928 |  | 2014-09-30 | 2014-09-30 09:45 | 2014-09-30 09:45 | RHEEM - RRNAB036JK06X | 83 | 0 | Yes | Yes | 28 | 20.4 | 7.6 | 1491F753C2C540B0B45CA10A82AD9371 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-4547 |  | 2014-09-23 | 2014-09-23 10:04 | 2014-09-23 10:09 | OTHER - PA13NR036-H | 99 | 4.6 | Yes | Yes | 19 | 19.3 | -0.3 | 5BF68E4F81EA4DE18BB806912CE1ECEC |  | R22 | TXV |  | 4.646% | 0.95354 | 8.929% | [5 empty] | TXV | 4.646%
Rio Vista | CA | 94571-1812 |  | 2014-09-03 | 2014-09-03 10:16 | 2014-09-03 11:02 | GUARDIAN - 0789B24470 | 68 | 4.9 | Yes | Yes | 22.8 | 20.7 | 2.1 | 4F4D46C0C6BD434E9C8DF2ECB1150B90 |  | R22 | Non-TXV |  | 7.206% | 0.92794 | 13.85% | [5 empty] | Non-TXV | 7.206%
Bakersfield | CA | 93306-3409 |  | 2014-09-02 | 2014-09-02 11:58 | 2014-09-02 12:22 | OTHER - 3A-80-0H-1-4 | 90 | 0 | Yes | Yes | 20.5 | 22.7 | -2.2 | 6280C7CC54E0465D8A46AB4393DC369C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4723 |  | 2014-09-25 | 2014-09-25 12:27 | 2014-09-25 12:27 | CONCORD - CCU10A36A | 78 | 0 | Yes | Yes | 16.7 | 17.7 | -1 | 9E39FAC28B444C31BCE03A2E960E79BE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7664 |  | 2014-09-17 | 2014-09-17 13:03 | 2014-09-17 13:03 | YORK - D1NHO36N05606C | 108 | 0 | Yes | Yes | 15.5 | 17 | -1.5 | 498155F12BDC442FB65FB50D400E2E2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6079 |  | 2014-11-11 | 2014-11-11 11:55 | 2014-11-11 11:55 | OTHER - GPF036K060A | 71 | 0 | Yes | Yes | 14.5 | 18.7 | -4.2 | 68DE57B6B8274E29AC507972CFE04F3C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5315 |  | 2014-09-17 | 2014-09-17 13:06 | 2014-09-17 13:06 | WESTINGHOUSE - IE048SCAON | 137 | 0 | Yes | Yes | 31.9 | 21 | 10.9 | 43D235DBE80844149A68FAEA9B032CB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6070 |  | 2014-10-06 | 2014-10-06 17:36 | 2014-10-06 17:54 | ICP - PGMD36G0606 | 69 | 8 | Yes | Yes | 21.7 | 21.5 | 0.2 | 3F5DE3F4A745461C8212ED24B255F19A |  | R22 | Non-TXV |  | 11.59% | 0.88406 | 22.28% | [5 empty] | Non-TXV | 11.59%
Bakersfield | CA | 93301-5950 |  | 2014-09-08 | 2014-09-08 19:23 | 2014-09-08 19:25 | YORK - H2RD036306B | 85 | 7.4 | Yes | Yes | 22.1 | 19.3 | 2.8 | 4244821B9BA74C9DBA8AAFE9E2FF184C |  | R22 | Non-TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | Non-TXV | 8.706%
Fairfield | CA | 94533-2119 |  | 2014-08-15 | 2014-08-15 14:11 | 2014-08-15 21:00 | - | 85 | 4.6 | Yes | Yes | 16.2 | 17.2 | -1 | D516EDFEC78D42F38DB41105CAE66200 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Suisun City | CA | 94585-1762 |  | 2014-09-11 | 2014-09-11 10:22 | 2014-09-11 11:04 | CARRIER - 38EH036300 | 116 | 4.3 | Yes | Yes | 21.9 | 19.9 | 2 | E3391636A5E84E1894174F30A295259C |  | R22 | Non-TXV |  | 3.707% | 0.96293 | 7.124% | [5 empty] | Non-TXV | 3.707%
San Jose | CA | 95132-3607 |  | 2014-08-15 | 2014-08-15 11:08 | 2014-08-15 11:26 | AMANA - RCC36A2B | 114 | 3.5 | Yes | Yes | 16.7 | 17.7 | -1 | E3A4CA3BF2BB4E359D2BD1801488FB1A |  | R22 | Non-TXV |  | 3.07% | 0.9693 | 5.9% | [5 empty] | Non-TXV | 3.07%
San Jose | CA | 95131-3439 |  | 2014-08-15 | 2014-08-15 13:21 | 2014-08-15 13:52 | CARRIER - 38CKC042350 | 93 | 3.6 | Yes | Yes | 20.5 | 18.2 | 2.3 | 0A3930F173CD45B48D3E5A28019251ED |  | R22 | TXV |  | 3.871% | 0.96129 | 7.439% | [5 empty] | TXV | 3.871%
Fairfield | CA | 94533-4264 |  | 2014-08-18 | 2014-08-18 12:42 | 2014-08-18 14:00 | TRANE - 118741000A01 | 106 | 6.1 | Yes | Yes | 19.9 | 19.8 | 0.1 | 5D390FE96B5B41E69AB58DE46C3E9D2E |  | R22 | Non-TXV |  | 5.755% | 0.94245 | 11.06% | [5 empty] | Non-TXV | 5.755%
Bakersfield | CA | 93301-5936 |  | 2014-09-08 | 2014-09-08 19:35 | 2014-09-08 19:37 | YORK - H1RC060S06A | 167 | 32.3 | Yes | Yes | 21.7 | 20.2 | 1.5 | 3181D4B6FD5D41339A7B61F142DFB367 |  | R22 | Non-TXV |  | 19.34% | 0.80659 | 37.17% | [5 empty] | Non-TXV | 19.34%
Concord | CA | 94518-4311 |  | 2014-09-04 | 2014-09-04 12:29 | 2014-09-04 12:29 | CARRIER - 38CLKB048 | 108 | 0 | Yes | Yes | 21.5 | 20.7 | 0.8 | CA31F74DB0CE40B98429ECD5A15C9FFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95128-3204 |  | 2014-08-29 | 2014-08-29 09:45 | 2014-08-29 09:45 | CARRIER - 38CKC042300 | 80 | 0 | Yes | Yes | 20.3 | 18.5 | 1.8 | 947FADD1B4124F5B8DB4E0BEDB974742 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4930 |  | 2014-09-16 | 2014-09-16 10:45 | 2014-09-16 10:45 | GOODMAN - PGB030075-1A | 56 | 0 | Yes | Yes | 20.3 | 20.2 | 0.1 | 2CE3B451F74A492399E6B1BDBDCA9E8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5450 |  | 2014-09-02 | 2014-09-02 09:21 | 2014-09-02 09:21 | RHEEM - UKN | 248 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 649BA665F00545508492F697EDBEA6E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3475 |  | 2014-09-29 | 2014-09-29 11:13 | 2014-09-29 11:13 | OTHER - DDYZF060N110C | 150 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C8E1E6E6FA704D199129701E4C319FEA | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5613 |  | 2014-09-10 | 2014-09-10 09:56 | 2014-09-10 09:56 | GOODMAN - PGB036075-1A | 60 | 0 | Yes | Yes | 21 | 19.6 | 1.4 | 4BE180B6CA644F4789E3D669E218CAFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2164 |  | 2014-09-24 | 2014-09-24 10:54 | 2014-09-24 10:54 | LENNOX - 13ACD-036-237-02 | 111 | 0 | Yes | Yes | 21 | 21.8 | -0.8 | 4A54B3971ABA49E38C6F4BF7E363687B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-5119 |  | 2014-10-03 | 2014-10-03 10:52 | 2014-10-03 10:52 | OTHER - H2RC048S06HA | 120 | 0 | Yes | Yes | 25.7 | 20.6 | 5.2 | 6ADA5581CC814D39A4A560AE44A301C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-5119 |  | 2014-10-03 | 2014-10-03 11:35 | 2014-10-03 11:35 | YORK - H2RC036S06HA | 83 | 0 | Yes | Yes | 24.6 | 19.3 | 5.3 | BD26667842A842898D52007044817FB1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5291 |  | 2014-09-26 | 2014-09-26 15:26 | 2014-09-26 15:26 | GOODMAN - GSC1300361D | 119 | 0 | Yes | Yes | 21 | 22.1 | -1.1 | B021CA748A35419C87646A3C8E9FD30C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2908 |  | 2014-09-29 | 2014-09-29 14:35 | 2014-09-29 14:35 | TRANE - YCY036G1M0AD | 130 | 0 | Yes | Yes | 23.5 | 22.6 | 0.9 | 40AF046DD03D4D3CADB3CB97473F0FEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2543 |  | 2014-09-22 | 2014-09-22 16:49 | 2014-09-22 16:49 | YORK - D3NZ042N06506NXB | 78 | 0 | Yes | Yes | 20.9 | 18.1 | 2.8 | 6D1CEA2401014727AC9288C461903EF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5433 |  | 2014-09-26 | 2014-09-26 09:34 | 2014-09-26 09:55 | COLEMAN - BRCS0481BD | 117 | 15.8 | Yes | Yes | 19.5 | 17.4 | 2.1 | 5FCFFF9F89C140588E7484C176730777 |  | R22 | Non-TXV |  | 13.5% | 0.86496 | 25.95% | [5 empty] | Non-TXV | 13.5%
Bakersfield | CA | 93304-4945 |  | 2014-09-10 | 2014-09-10 09:37 | 2014-09-10 09:37 | GOODMAN - GSX130421BA | 121 | 0 | Yes | Yes | 16.5 | 19.5 | -3 | 0FC759F91792480BA25929D7655E0E2F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3545 |  | 2014-09-25 | 2014-09-25 09:37 | 2014-09-25 09:37 | BRYANT - UKN | 61 | 0 | Yes | Yes | 18.9 | 21.9 | -3 | 6D4E7CE3AA084E0183258A5328CA6C3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6041 |  | 2014-11-14 | 2014-11-14 10:10 | 2014-11-14 10:10 | COLEMAN - BRCS0361BD | 63 | 0 | Yes | Yes | 15.2 | 17.1 | -1.9 | DDA759847F914A709476A54B6512A2CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1730 |  | 2014-09-16 | 2014-09-16 10:06 | 2014-09-16 10:43 | TRANE - 4TTX4036B1000AA | 91 | 8.1 | Yes | Yes | 21.3 | 20.2 | 1.2 | DA0A006798A647CFB45CB6A34ADF2695 |  | R410A | TXV |  | 8.901% | 0.91099 | 17.11% | [5 empty] | TXV | 8.901%
Bakersfield | CA | 93311-8960 |  | 2014-10-03 | 2014-10-03 09:50 | 2014-10-03 09:50 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 21.7 | 19.9 | 1.8 | 5FD12C1160F34545B24C561DB046C3F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4834 |  | 2014-10-09 | 2014-10-09 10:16 | 2014-10-09 10:38 | CARRIER - 383RC036350 | 106 | 4.3 | Yes | Yes | 22.7 | 20.4 | 2.3 | 786023CEB0D14ED98D51FD87288E125E |  | R22 | Non-TXV |  | 4.057% | 0.95943 | 7.796% | [5 empty] | Non-TXV | 4.057%
Wasco | CA | 93280-2775 |  | 2014-10-30 | 2014-10-30 16:12 | 2014-10-30 16:12 | OTHER - | 59 | 0 | Yes | Yes | 18.7 | 21 | -2.3 | F986EAE7BBA94F6A87A32BD55DC74CF3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5403 |  | 2014-09-05 | 2014-09-05 12:19 | 2014-09-05 12:34 | CARRIER - 24AB324A310 | 74 | 3.7 | Yes | Yes | 18.6 | 20.4 | -1.8 | E0732F5A49CE47DB86A1D9D99C835C16 |  | R410A | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Bakersfield | CA | 93306-8401 |  | 2014-09-17 | 2014-09-17 14:08 | 2014-09-17 14:08 | ICP - WCA3362GKR2 | 85 | 0 | Yes | Yes | 22.2 | 21.8 | 0.5 | B537342F117B4C89BE9431EF4DD103F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5934 |  | 2014-09-02 | 2014-09-02 11:37 | 2014-09-02 11:37 | CARRIER - 38CKC048300 | 102 | 0 | Yes | Yes | 19.4 | 19.9 | -0.5 | D30E09FE5EBE407AB6941630C08D442C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5524 |  | 2014-10-19 | 2014-10-19 17:15 | 2014-10-19 17:17 | YORK - H2RE060S06A | 243 | 11.7 | Yes | Yes | 26 | 22.3 | 3.8 | 7C598A6778E1480A8B0105DBEE916143 |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Bakersfield | CA | 93307-1526 |  | 2014-09-17 | 2014-09-17 11:52 | 2014-09-17 11:52 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 20.5 | 22.5 | -2 | F7689A93AA9F424689960A34D1F396AF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7164 |  | 2014-09-30 | 2014-09-30 15:01 | 2014-09-30 15:01 | ICP - PGDB48090K001C1 | 102 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | 908A55D4113B4BC3A693E8D5CD63C9B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6544 |  | 2014-11-04 | 2014-11-04 15:50 | 2014-11-04 15:50 | GOODMAN - CH48-IFC | 109 | 0 | Yes | Yes | 23.5 | 20.2 | 3.4 | 2CF59779B15747BFAE025813CBED3D63 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6262 |  | 2014-09-17 | 2014-09-17 16:23 | 2014-09-17 16:23 | PAYNE - PY3NAA42090NA | 97 | 0 | Yes | Yes | 19.6 | 19.3 | 0.3 | A230BFAA0B1147278EC962A01CC47BD7 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2427 |  | 2014-10-30 | 2014-10-30 10:15 | 2014-10-30 10:15 | YORK - H4DB036S06A | 67 | 0 | Yes | Yes | 22.6 | 20.1 | 2.5 | 24EA10E744C14C38B095C3C61D170E53 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fremont | CA | 94536-5564 |  | 2014-09-03 | 2014-09-03 08:39 | 2014-09-03 08:46 | CARRIER - 38EN030300 | 86 | 0 | Yes | Yes | 16.8 | 18.2 | -1.4 | 3521871C9D6B49C9B022AF9F08994328 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2633 |  | 2014-09-24 | 2014-09-24 11:51 | 2014-09-29 08:16 | ALLEGIANCE - 7A0036A100A2 | 85 | 3 | Yes | Yes | 15.6 | 18.4 | -2.8 | 56FFFAB6C4D8489DB9BC9FC423D19143 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Vacaville | CA | 95687-6407 |  | 2014-09-15 | 2014-09-15 13:37 | 2014-09-17 07:47 | - | 85 | -8 | Yes | Yes | 14.9 | 17.9 | -3 | CC5FAADA79434FB9B718E8980EC11EFC |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93304-4924 |  | 2014-09-30 | 2014-09-30 11:59 | 2014-09-30 11:59 | AMANA - PGD36C0902G | 123 | 0 | Yes | Yes | 18.4 | 20.8 | -2.4 | 187373770FED413386AB7A9F3ED72416 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7850 |  | 2014-10-01 | 2014-10-01 14:21 | 2014-10-01 14:42 | - | 85 | 5.3 | Yes | Yes | 20.8 | 20.4 | 0.4 | DE30AE7255AA4AAEA37BEDB02750FDFE |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Bakersfield | CA | 93313-5005 |  | 2014-10-21 | 2014-10-21 12:56 | 2014-10-21 12:56 | YORK - D1NA0330N03606C | 76 | 0 | Yes | Yes | 16.8 | 19.1 | -2.3 | 272C27A046314A2387F260E3A875C523 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5682 |  | 2014-10-06 | 2014-10-06 17:06 | 2014-10-06 17:06 | DAY & NIGHT - N4A342AKA300 | 88 | 0 | Yes | Yes | 20.5 | 23.1 | -2.6 | A0786F613C15485CBE579745D11095FE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4746 |  | 2014-10-19 | 2014-10-19 16:45 | 2014-10-19 16:48 | YORK - D1NH036N05606C | 108 | 6.9 | Yes | Yes | 23.1 | 20.8 | 2.3 | 8B8BAAE6B5814BB297104E45C2BD4C84 |  | R22 | Non-TXV |  | 6.389% | 0.93611 | 12.28% | [5 empty] | Non-TXV | 6.389%
Bakersfield | CA | 93313-3995 |  | 2014-10-04 | 2014-10-04 19:54 | 2014-10-04 19:57 | YORK - D2NX048N0656NXA | 152 | 8.8 | Yes | Yes | 21.8 | 21 | 0.8 | 2743C1AFCB704A44A136044F74A63C63 |  | R410A | TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | TXV | 5.789%
Pittsburg | CA | 94565-6272 |  | 2014-09-26 | 2014-09-26 08:50 | 2014-09-26 09:10 | GE - BTB936A10002 | 83 | -7.8 | Yes | Yes | 19.5 | 15.1 | 4.4 | 057DFF87335B4FBDAB4F6DAC9AF36D34 |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Bakersfield | CA | 93305-1618 |  | 2014-09-09 | 2014-09-09 09:21 | 2014-09-09 09:21 | ICP - PGAA36C1K4 | 69 | 0 | Yes | Yes | 17.4 | 20.2 | -2.8 | B326148C02FF400DA2B22DCF401B2E64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1546 |  | 2014-09-09 | 2014-09-09 12:44 | 2014-09-09 12:44 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 19 | 21.4 | -2.4 | 4DB571D5401B4A0F9CA8E4F09D6AD71D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5009 |  | 2014-11-11 | 2014-11-11 10:27 | 2014-11-11 10:27 | YORK - D1NP048N06506A | 132 | 0 | Yes | Yes | 32.5 | 20.1 | 12.4 | 64AAA53792A14874957F739D235E8B71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5503 |  | 2014-10-06 | 2014-10-06 09:48 | 2014-10-06 09:48 | RUUD - UAMB036JAZ | 93 | 0 | Yes | Yes | 17.6 | 20.6 | -3 | 27B2C218112F4CF881495FC976D6119E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4306 |  | 2014-10-21 | 2014-10-21 12:00 | 2014-10-21 12:00 | BDP - 585HJ036060 | 102 | 0 | Yes | Yes | 21 | 17.7 | 3.3 | 1461EF120EBA41A3A20CED54F655F949 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3059 |  | 2014-10-04 | 2014-10-04 20:23 | 2014-10-04 20:26 | OTHER - N/A | 85 | 6.7 | Yes | Yes | 19 | 20.7 | -1.7 | 2A4D5291F14641E6B0C6BF8F9D25898D |  | R22 | Non-TXV |  | 7.882% | 0.92118 | 15.15% | [5 empty] | Non-TXV | 7.882%
Vacaville | CA | 95687-4139 |  | 2014-09-19 | 2014-09-19 08:40 | 2014-09-19 09:27 | AIRE-FLO - PA13MF048-L | 134 | 5.4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 79AC939A62FC4366B0EB5B0D2B6B4479 |  | R22 | Non-TXV |  | 4.03% | 0.9597 | 7.744% | [5 empty] | Non-TXV | 4.03%
Bakersfield | CA | 93309-5362 |  | 2014-09-17 | 2014-09-17 11:18 | 2014-09-17 11:18 | PAYNE - PY1PNB042060AAAA | 85 | 0 | Yes | Yes | 21.1 | 18.5 | 2.6 | 27B685ED7EB6478396EB2CFE10A4EC52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1518 |  | 2014-09-17 | 2014-09-17 12:02 | 2014-09-17 12:02 | ICP - PGF336060K01 | 145 | 0 | Yes | Yes | 20.9 | 19.4 | 1.5 | 65932071733949E4814AB1E94DB732C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-0000 |  | 2014-09-09 | 2014-09-09 10:22 | 2014-09-09 10:22 | DAY & NIGHT - 587ANZ024040 | 90 | 30 | Yes | Yes | 17.7 | 21.1 | -3.4 | 025CD43C1D2F41089AF5A3482C5D9C45 | Add refrigerant: 30 oz | R22 | Non-TXV |  | 33.33% | 0.66667 | 64.06% | [5 empty] | Non-TXV | 33.33%
Bakersfield | CA | 93305-2542 |  | 2014-09-09 | 2014-09-09 09:59 | 2014-09-09 09:59 | ICP - D6NZ036N05606NXA | 64 | 0 | Yes | Yes | 19.2 | 20.2 | -0.9 | 04827DBF30DE49F1B4B63CE33523B6FB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6068 |  | 2014-09-10 | 2014-09-10 15:03 | 2014-09-10 16:46 | GE - 98FD-5600-00 | 68 | 3.8 | Yes | Yes | 18 | 20.4 | -2.4 | F963CDF6369F4857882A6DED273988E1 |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Vacaville | CA | 95687-6065 |  | 2014-10-14 | 2014-10-14 17:13 | 2014-10-14 18:10 | - | 72 | 4.7 | Yes | Yes | 22.8 | 20.4 | 2.4 | FB3D49F026FA4B8D86F2479414B921D0 |  | R22 | Non-TXV |  | 6.528% | 0.93472 | 12.54% | [5 empty] | Non-TXV | 6.528%
Bakersfield | CA | 93307-5644 |  | 2014-09-09 | 2014-09-09 15:20 | 2014-09-09 15:20 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 22.5 | 21.3 | 1.2 | 51330C7341444B6D902A7E13FE8CA0ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3657 |  | 2014-09-08 | 2014-09-08 11:33 | 2014-09-08 11:33 | HEIL - H2A324GKA100 | 87 | 0 | Yes | Yes | 25.3 | 19.9 | 5.4 | AAF6EF729BF441E8AE4C35C2AB36ADFB |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4974 |  | 2014-10-07 | 2014-10-07 17:08 | 2014-10-07 17:08 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 22.3 | 22.6 | -0.3 | 4B80F225E66F40478B5CE1E1EADCAE7E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5361 |  | 2014-10-12 | 2014-10-12 16:20 | 2014-10-12 16:23 | YORK - D1NH048N06506C | 128 | 4.8 | Yes | Yes | 24.7 | 21 | 3.7 | 334FA9EF33F64BC5B8154501EF8580D5 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Bakersfield | CA | 93313-4322 |  | 2014-11-11 | 2014-11-11 14:17 | 2014-11-11 14:17 | YORK - D1NA030N05606C | 76 | 0 | Yes | Yes | 18.1 | 18.9 | -0.8 | C048844B024D478DBC2D9FF952DBAB9B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5308 |  | 2014-11-17 | 2014-11-17 13:42 | 2014-11-17 13:42 | OTHER - PGADA42D1K5 | 180 | 0 | Yes | Yes | 23.1 | 20.1 | 3 | D0E1760E0BD1417CBBDAE402F1FE877D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3661 |  | 2014-09-30 | 2014-09-30 13:41 | 2014-09-30 13:41 | GMC - V8X13048B1 | 104 | 0 | Yes | Yes | 24.1 | 18.8 | 5.3 | 0BA4B781A85547719C1C821303FD91A9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4753 |  | 2014-10-03 | 2014-10-03 10:26 | 2014-10-03 10:26 | TRANE - TTB030C100A2 | 66 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | C69A05C7F97A468EA641C633649AFAC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3362 |  | 2014-10-28 | 2014-10-28 09:59 | 2014-10-28 09:59 | UNITARY PRODUCTS GROUP - DAYP-F030N070A | 73 | 0 | Yes | Yes | 23.9 | 20.8 | 3.1 | 65DF0CDA7CF5470C9DB08703E37D3D6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4973 |  | 2014-10-07 | 2014-10-07 17:01 | 2014-10-07 17:01 | RHEEM - UKN | 90 | 0 | Yes | Yes | 18.7 | 21 | -2.3 | 83D7373AFD304D8A8BC9F514E06A7547 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-3677 |  | 2014-09-05 | 2014-09-05 08:06 | 2014-09-05 08:22 | NORDYNE - FS5BD--048KA | 126 | 17 | Yes | Yes | 19.5 | 17.2 | 2.3 | 5828050700CA48D5833BC32328857CFD |  | R22 | Non-TXV |  | 13.49% | 0.86508 | 25.93% | [5 empty] | Non-TXV | 13.49%
Bakersfield | CA | 93307-4973 |  | 2014-10-07 | 2014-10-07 16:11 | 2014-10-07 16:36 | RHEEM - UKN | 90 | 8.2 | Yes | Yes | 20.5 | 21.5 | -1 | 0C111FF09EC140968C27F6CF5A25701F |  | R22 | Non-TXV |  | 9.111% | 0.90889 | 17.51% | [5 empty] | Non-TXV | 9.111%
Fairfield | CA | 94533-2426 |  | 2014-09-17 | 2014-09-17 12:12 | 2014-09-22 08:47 | CARRIER - 38TRA030320 | 100 | -9.4 | Yes | Yes | 14.6 | 17.5 | -2.9 | 3C28F113E48C4FF1972B150952A8A83F |  | R22 | Non-TXV |  | -9.4% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.4%
Bakersfield | CA | 93305-2558 |  | 2014-09-29 | 2014-09-29 10:03 | 2014-09-29 10:03 | DAY & NIGHT - UKN | 60 | 0 | Yes | Yes | 23.8 | 18.2 | 5.6 | 111B202E41244CF2B7ACB56534B3B7A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6461 |  | 2014-10-30 | 2014-10-30 11:07 | 2014-10-30 11:25 | CARRIER - 38CKC030 | 70 | 7.4 | Yes | Yes | 18.1 | 20.8 | -2.7 | 1827A05DAACC4FAB80D27357FD22B05F |  | R22 | Non-TXV |  | 10.57% | 0.89429 | 20.32% | [5 empty] | Non-TXV | 10.57%
Antioch | CA | 94509-6461 |  | 2014-10-30 | 2014-10-30 11:30 | 2014-10-30 11:50 | - | 85 | 7.8 | Yes | Yes | 22.9 | 19.9 | 3 | E5E91B3863D8494591005ED8C9534923 |  |  |  |  | 9.176% | 0.90824 | 17.64% | [5 empty] | 0 | 9.176%
Bakersfield | CA | 93309-4929 |  | 2014-09-16 | 2014-09-16 16:58 | 2014-09-16 16:58 | TEMPSTAR - PGF048K120A | 102 | 0 | Yes | Yes | 20.8 | 22.4 | -1.6 | 6D3D2FF4348D430F83D84D7880F2D8F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2510 |  | 2014-09-17 | 2014-09-17 12:37 | 2014-09-22 08:48 | FRIGIDAIRE - | 85 | -6 | Yes | Yes | 14 | 16.9 | -2.9 | A8FADF300A9549E7847488B50C7CDEEB |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Rio Vista | CA | 94571-2180 |  | 2014-10-15 | 2014-10-15 10:31 | 2014-10-15 11:09 | YORK - H2RCO24S06A | 72 | 5 | Yes | Yes | 19 | 20.7 | -1.7 | 8B2DEA3834304F0DA903A80336456543 |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Suisun City | CA | 94585-3516 |  | 2014-09-09 | 2014-09-09 15:06 | 2014-09-09 20:55 | - | 85 | 3.1 | Yes | Yes | 13.9 | 16.8 | -2.9 | D3B9E805D6634E97A16581293023B26B |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Woodland | CA | 95695-5507 |  | 2014-08-28 | 2014-08-28 12:51 | 2014-08-28 16:08 | PAYNE - PY1PNB03606060ABAA | 67 | 4 | Yes | Yes | 20.8 | 21 | -0.2 | 3FFF3BF32CC041FC94D1678A89A566FD |  | R22 | Non-TXV |  | 5.97% | 0.9403 | 11.47% | [5 empty] | Non-TXV | 5.97%
Bakersfield | CA | 93306-7488 |  | 2014-10-21 | 2014-10-21 11:02 | 2014-10-21 11:02 | UNITARY PRODUCTS GROUP - H2RD042S06B | 141 | 0 | Yes | Yes | 23.5 | 21.5 | 2 | 1AA5626EA3B54E35AF7D4C266D9F2BFB |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-1108 |  | 2014-09-05 | 2014-09-05 09:04 | 2014-09-05 09:13 | RUUD - UAKA-048JAZ | 103 | -9.7 | Yes | Yes | 20 | 18.3 | 1.7 | 23809F0C68184ED7B814D749C9427A66 |  | R22 | Non-TXV |  | -9.417% | 1.0942 | 2.637% |  |  |  |  | Non-TXV |  |  | -9.417%
Antioch | CA | 94531-9361 |  | 2014-11-05 | 2014-11-05 09:14 | 2014-11-05 09:14 | CARRIER - 38CKC060300 | 158 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 59866BCE903844F48F833C63F727055B |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5528 |  | 2014-09-16 | 2014-09-16 11:12 | 2014-09-16 11:34 | CARRIER - 38TKB036340 | 83 | 10.2 | Yes | Yes | 20.4 | 20.4 | 0 | 55ADC2DEF8CF4A43A0EF7F46CC7179B2 |  | R22 | Non-TXV |  | 12.29% | 0.87711 | 23.62% | [5 empty] | Non-TXV | 12.29%
W Sacramento | CA | 95691-3938 |  | 2014-09-09 | 2014-09-09 08:54 | 2014-09-09 09:51 | CARRIER - 48SDN030060311 | 96 | 6.1 | Yes | Yes | 18.2 | 21.2 | -3 | EE884BA7F4A94FE0BE90A6CA4FFFBE7D |  | R22 | Non-TXV |  | 6.354% | 0.93646 | 12.21% | [5 empty] | Non-TXV | 6.354%
W Sacramento | CA | 95691-5839 |  | 2014-09-04 | 2014-09-04 10:47 | 2014-09-04 11:46 | GOODMAN - H28A0S06D | 62 | 0 | Yes | Yes | 22.1 | 19.9 | 2.2 | B9CDF38F622B47E2B0E64AB9CEAD95A3 | Add refrigerant: 1.8 oz | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4730 |  | 2014-09-05 | 2014-09-05 13:18 | 2014-09-05 13:41 | CARRIER - 48SX-0300B0381AA | 69 | 3.5 | Yes | Yes | 18.5 | 20.4 | -1.9 | 69463EADAE004D4D8F052B2CCC399247 |  | R22 | Non-TXV |  | 5.072% | 0.94928 | 9.748% | [5 empty] | Non-TXV | 5.072%
Woodland | CA | 95695-5532 |  | 2014-09-15 | 2014-09-15 12:04 | 2014-09-15 12:23 | LENNOX - HS29-030-1P | 68 | 4.6 | Yes | Yes | 21.3 | 19.9 | 1.4 | 12B2C78B8573448CB37167E21353702E |  | R22 | Non-TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | Non-TXV | 6.765%
Suisun City | CA | 94585-3032 |  | 2014-09-09 | 2014-09-09 14:34 | 2014-09-09 20:54 | PAYNE - 591ANX0360000AAA | 86 | -8.1 | Yes | Yes | 15.7 | 17.2 | -1.5 | 0F0E065EA3BA41FE896FD3EAE0600C9D |  | R22 | Non-TXV |  | -9.419% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.419%
Woodland | CA | 95695-6038 |  | 2014-09-05 | 2014-09-05 14:21 | 2014-09-05 14:37 | AIRE-FLO - PA13NR042-J | 113 | -5.6 | Yes | Yes | 20.7 | 19.9 | 0.8 | 1A49EB9DB98941719A64CB39204D8DB9 |  | R22 | TXV |  | -4.956% | 1.0496 | 1.388% |  |  |  |  | TXV |  |  | -4.956%
Woodland | CA | 95695-6038 |  | 2014-09-05 | 2014-09-05 14:38 | 2014-09-05 14:38 | CARRIER - H2RA036S06G | 62 | 0 | Yes | Yes | 17.7 | 18.7 | -1 | 95EA85E77C524845B82C75E4F1B4C372 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7886 |  | 2014-09-05 | 2014-09-05 11:37 | 2014-09-05 12:48 | CARRIER - 24ABA324A310 | 85 | 3.8 | Yes | Yes | 20.9 | 20.4 | 0.5 | 29C99127B2564B64BF1BC62DA5AC0E7B |  | R410A | TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | TXV | 4.471%
Bakersfield | CA | 93309-1708 |  | 2014-09-05 | 2014-09-05 20:33 | 2014-09-05 20:33 | OTHER - PGAD48D1KE | 164 | 0 | Yes | Yes | 23.1 | 22.1 | 1 | 71A4A8E85B264D2AB315A56E493030D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3114 |  | 2014-11-11 | 2014-11-11 18:03 | 2014-11-11 18:06 | OTHER - PGME480908 | 212 | 6.5 | Yes | Yes | 19.1 | 15.9 | 3.2 | 48D57E20C563487188B5A46B141859B1 |  | R22 | Non-TXV |  | 3.066% | 0.96934 | 5.892% | [5 empty] | Non-TXV | 3.066%
Antioch | CA | 94509-6411 |  | 2014-11-14 | 2014-11-14 10:43 | 2014-11-14 10:43 | DAY & NIGHT - | 85 | 0 | Yes | Yes | 19.9 | 18.4 | 1.5 | 32D033593BF84775985791BC6D5B90B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7708 |  | 2014-11-05 | 2014-11-05 10:40 | 2014-11-05 10:40 | AMANA - RCC48C2C | 85 | 0 | Yes | Yes | 21.1 | 19.3 | 1.8 | 5940524D3B1146B1AD40BF292F039C91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3431 |  | 2014-09-02 | 2014-09-02 12:59 | 2014-09-02 13:25 | CARRIER - 561AJO024-B | 62 | 6.7 | Yes | Yes | 21.6 | 19.9 | 1.7 | 0E5E9E10084F4A52888F66C2D10081BC |  | R22 | Non-TXV |  | 10.81% | 0.89194 | 20.77% | [5 empty] | Non-TXV | 10.81%
Bakersfield | CA | 93305-5316 |  | 2014-09-17 | 2014-09-17 09:07 | 2014-09-17 09:07 | ICP - N2A336AKA200 | 94 | 0 | Yes | Yes | 22.6 | 19.3 | 3.3 | 1FDBAEBE075C468FAAFA86CB9DE03867 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1789 |  | 2014-10-01 | 2014-10-01 09:29 | 2014-10-03 07:57 | DAY & NIGHT - 591AN042-D | 122 | 11.8 | Yes | Yes | 12.5 | 15.5 | -3 | 963411FD44D0498EBF6D651D0FD5F912 |  | R22 | Non-TXV |  | 9.672% | 0.90328 | 18.59% | [5 empty] | Non-TXV | 9.672%
San Jose | CA | 95111-1578 |  | 2014-08-29 | 2014-08-29 08:11 | 2014-08-29 08:37 | CARRIER - 38EH036300 | 116 | 3.8 | Yes | Yes | 20.1 | 18.8 | 1.3 | A5C389E29B884D328ACCDE9047A5CF56 |  | R22 | Non-TXV |  | 3.276% | 0.96724 | 6.295% | [5 empty] | Non-TXV | 3.276%
Bakersfield | CA | 93304-5338 |  | 2014-09-30 | 2014-09-30 10:27 | 2014-09-30 10:27 | DAY & NIGHT - 585A030080YAC | 50 | 0 | Yes | Yes | 23.8 | 19.9 | 3.9 | 398100BAD7AC4929AC6D07760C471B66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5046 |  | 2014-10-04 | 2014-10-04 17:02 | 2014-10-04 17:21 | RHEEM - RAMC-048JBZ | 85 | 6.1 | Yes | Yes | 26 | 22.3 | 3.7 | 60D0183F1EC140D0BD24C9FA39B12EAF |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Bakersfield | CA | 93307-5057 |  | 2014-10-07 | 2014-10-07 10:20 | 2014-10-07 10:20 | GOODMAN - CLQ48-1B | 120 | 0 | Yes | Yes | 20.6 | 21.4 | -0.8 | 8A4350610EBF47DE8EF1F99B6C74C8A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5926 |  | 2014-09-02 | 2014-09-02 10:52 | 2014-09-02 11:22 | BDP - 565BJO36-A | 82 | 5.9 | Yes | Yes | 21.4 | 21.3 | 0.1 | B84E68359717480C9371D047148C136C |  | R22 | Non-TXV |  | 7.195% | 0.92805 | 13.83% | [5 empty] | Non-TXV | 7.195%
Suisun City | CA | 94585-3731 |  | 2014-09-12 | 2014-09-12 09:58 | 2014-09-12 10:21 | GOODMAN - CKL | 114 | 4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 46304EBEE2124D6EAA399CA97E7D1947 |  | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Bakersfield | CA | 93306-4521 |  | 2014-09-29 | 2014-09-29 13:16 | 2014-09-29 14:10 | ARCOAIRE - PGAD30D1K6 | 78 | 7.7 | Yes | Yes | 18.6 | 19.9 | -1.3 | 2156FD97B6A94ACD9AE0FA98D3B892FB |  | R22 | Non-TXV |  | 9.872% | 0.90128 | 18.97% | [5 empty] | Non-TXV | 9.872%
Bakersfield | CA | 93304-2049 |  | 2014-10-08 | 2014-10-08 10:10 | 2014-10-08 10:10 | UNITARY PRODUCTS GROUP - D1NH042N06506C | 94 | 0 | Yes | Yes | 23.8 | 19.3 | 4.5 | C3121C766090413FB179EA55091693C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3000 |  | 2014-09-24 | 2014-09-24 12:57 | 2014-09-24 12:57 | OTHER - CA7542VKA2 | 126 | 0 | Yes | Yes | 21.9 | 23.2 | -1.3 | B285642EF028418086E26C5004CEA4F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-2042 |  | 2014-08-29 | 2014-08-29 09:06 | 2014-08-29 09:28 | GOODMAN - GS3BA-048KA | 115 | 15.6 | Yes | Yes | 20.3 | 19.4 | 0.9 | B6B5DA92856543C799A1F9A867146E09 |  | R22 | Non-TXV |  | 13.57% | 0.86435 | 26.07% | [5 empty] | Non-TXV | 13.57%
Bakersfield | CA | 93305-1832 |  | 2014-09-29 | 2014-09-29 11:03 | 2014-09-29 11:03 | YORK - D3NZ030N03606NXC | 64 | 0 | Yes | Yes | 19.6 | 18 | 1.6 | C3218790298E4057AFB5F19D6C21ACDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1315 |  | 2014-09-22 | 2014-09-22 10:01 | 2014-09-22 10:01 | ICP - PGC042K080E | 84 | 0 | Yes | Yes | 19.6 | 22.4 | -2.8 | F18874FC77624076A6A59809F5C90ECA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1230 |  | 2014-09-05 | 2014-09-05 12:20 | 2014-09-05 12:37 | CARRIER - 24APA542A0030010 | 168 | 15 | Yes | Yes | 21.1 | 16.4 | 4.7 | 48B992A1BC774C128386324B29B4DE10 |  | R410A | TXV |  | 8.929% | 0.91071 | 17.16% | [5 empty] | TXV | 8.929%
San Jose | CA | 95123-2541 |  | 2014-08-29 | 2014-08-29 10:39 | 2014-08-29 10:39 | BRYANT - PA13NA048-C | 132 | 0 | Yes | Yes | 20.4 | 17.2 | 3.2 | D3B03814C764491798CE6A12A995E8D4 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1254 |  | 2014-09-27 | 2014-09-27 13:06 | 2014-09-27 13:06 | RHEEM - UNK | 120 | 0 | Yes | Yes | 17.9 | 19.5 | -1.6 | 7F840B9087F54F60823D91F03AA8F996 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2902 |  | 2014-08-29 | 2014-08-29 11:03 | 2014-08-29 11:03 | NORDYNE - UNK | 100 | 0 | Yes | Yes | 17.9 | 17.6 | 0.3 | C4F3C85E64FD40A0B05E30B3CEC1D302 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2902 |  | 2014-08-29 | 2014-08-29 11:13 | 2014-08-29 11:13 | NORDYNE - UNK | 100 | 0 | Yes | Yes | 19.4 | 18.5 | 0.9 | D5CD9624D58749CE98AD2CFD3EEA7B81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1839 |  | 2014-09-12 | 2014-09-12 15:06 | 2014-09-12 17:27 | HEIL - H4A336GKD200 | 87 | 4.6 | Yes | Yes | 22.4 | 19.9 | 2.5 | DEE03207FC6643BA90B964AA035C4075 |  | R410A | Non-TXV |  | 5.287% | 0.94713 | 10.16% | [5 empty] | Non-TXV | 5.287%
Woodland | CA | 95776-5401 |  | 2014-09-15 | 2014-09-15 10:08 | 2014-09-15 12:27 | CARRIER - 24ABA324A310 | 74 | 4.7 | Yes | Yes | 22 | 20.4 | 1.6 | DB087287D7814B8EAF24ACF764AFED2C |  | R410A | TXV |  | 6.351% | 0.93649 | 12.21% | [5 empty] | TXV | 6.351%
Bakersfield | CA | 93311-1928 |  | 2014-09-23 | 2014-09-23 15:37 | 2014-09-23 15:37 | OTHER - UNK | 104 | 0 | Yes | Yes | 18.4 | 19.5 | -1.1 | 87350A313E3D45BBB591EBCD053010BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3924 |  | 2014-09-24 | 2014-09-24 09:26 | 2014-09-24 10:08 | TRANE - 4TTX3048A1000AB | 126 | 4.7 | Yes | Yes | 20.9 | 20.4 | 0.5 | 4C5A59EC1E884D4B86D819A739A1A730 |  | R22 | TXV |  | 3.73% | 0.9627 | 7.169% | [5 empty] | TXV | 3.73%
Bakersfield | CA | 93307-1513 |  | 2014-09-29 | 2014-09-29 12:57 | 2014-09-29 12:57 | GOODMAN - GPG13242481CB | 74.2 | 0 | Yes | Yes | 24.1 | 18.9 | 5.2 | 7534A1DDB23342EDBA23529703BD25B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2166 |  | 2014-09-05 | 2014-09-05 09:51 | 2014-09-05 09:51 | DAY & NIGHT - FDMCA25519 | 89 | 0 | Yes | Yes | 26.3 | 20.7 | 5.6 | 2A70D0EF190341498D44954CB278B7CA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3909 |  | 2014-09-09 | 2014-09-09 13:44 | 2014-09-09 13:44 | YORK - D1NHO30N05606C | 73 | 0 | Yes | Yes | 18.5 | 20.7 | -2.2 | D7C3CA37C3004CE89B0D4C4A2AF37DC9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4816 |  | 2014-10-20 | 2014-10-20 11:48 | 2014-10-20 12:28 | BARD - 2910944431 | 83 | 2.7 | Yes | Yes | 19.4 | 20.4 | -1 | 32F5DE58DBC14199B9166CADE60782C1 |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Bakersfield | CA | 93304-6951 |  | 2014-09-22 | 2014-09-22 11:21 | 2014-09-22 11:21 | RUUD - UR55-07E42JKR | 100 | 0 | Yes | Yes | 21 | 22.8 | -1.8 | D73D436F07BE42AC943C00E9B1F7C546 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3223 |  | 2014-09-24 | 2014-09-24 17:32 | 2014-09-24 17:32 | OTHER - AC042X1012A | 84 | 0 | Yes | Yes | 15.3 | 17.7 | -2.4 | ED1FA2C1D84545AA965F234A10F79A90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3592 |  | 2014-09-17 | 2014-09-17 10:06 | 2014-09-17 10:06 | GOODMAN - GPG13300451A | 85 | 0 | Yes | Yes | 21.5 | 19.1 | 2.4 | 8886273BAFBC438C9B0A856B27BD661E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6335 |  | 2014-09-23 | 2014-09-23 14:41 | 2014-09-23 14:41 | LENNOX - ``13ACD-048-230-02 | 204 | 0 | Yes | Yes | 23 | 20.4 | 2.6 | 178ECF292A2B45C18D3942188F8E318A |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3755 |  | 2014-10-10 | 2014-10-10 14:06 | 2014-10-10 14:25 | CARRIER - 585GJ042062 | 84 | 10.9 | Yes | Yes | 19.9 | 14.1 | 5.8 | D06194A2D6CA4D2FB7F4C0A82F76DD12 |  | R22 | Non-TXV |  | 12.98% | 0.87024 | 24.94% | [5 empty] | Non-TXV | 12.98%
Vallejo | CA | 94589-1718 |  | 2014-10-20 | 2014-10-20 12:10 | 2014-10-20 12:29 | CARRIER - CKC840-030E45 | 100 | 4.5 | Yes | Yes | 20.1 | 20.4 | -0.3 | AA17A5E0E7C14945B472B371CE20FDFF |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Byron | CA | 94514-0000 |  | 2014-11-07 | 2014-11-07 09:55 | 2014-11-07 10:17 | CARRIER - 38TH030310 | 68 | 4.6 | Yes | Yes | 17.8 | 19.5 | -1.7 | 2491E2CEAD8F48EB81A1EC81077293EB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | Non-TXV | 6.765%
Bakersfield | CA | 93311-1615 |  | 2014-10-02 | 2014-10-02 12:37 | 2014-10-02 12:37 | OTHER - 5850JW036060ABAF | 82 | 0 | Yes | Yes | 20 | 19.3 | 0.7 | 8ACEE2563F5E442BAB94C2F81A635EEA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7114 |  | 2014-10-31 | 2014-10-31 12:32 | 2014-10-31 12:32 | TRANE - 2TWR4024A1000AA | 128 | 0 | Yes | Yes | 16.8 | 17.2 | -0.4 | 043A408C05A845F99B55F5EF78930E03 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6142 |  | 2014-10-22 | 2014-10-22 11:25 | 2014-10-22 12:02 | YORK - 11DE042S06B | 98 | 5.2 | Yes | Yes | 19.4 | 20.9 | -1.5 | 79FBD0A7B5DA47CD8B45C31D4F0BF5DE |  | R22 | Non-TXV |  | 5.306% | 0.94694 | 10.2% | [5 empty] | Non-TXV | 5.306%
Antioch | CA | 94509-1433 |  | 2014-10-30 | 2014-10-30 13:55 | 2014-10-30 13:55 | YORK - CMA036 11A | 95 | 0 | Yes | Yes | 24.3 | 21.5 | 2.8 | 49BC83F5BB7948A5816C0E1E7A517D67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-2552 |  | 2014-09-08 | 2014-09-08 19:47 | 2014-09-08 19:49 | RHEEM - RRNA-A036JK08X | 114 | 4.6 | Yes | Yes | 20.3 | 21 | -0.7 | 5B0E0DEE72F04FAB95810A0E9326A45D |  | R22 | Non-TXV |  | 4.035% | 0.95965 | 7.755% | [5 empty] | Non-TXV | 4.035%
Antioch | CA | 94509-4519 |  | 2014-11-14 | 2014-11-14 11:15 | 2014-11-14 11:15 | CARRIER - 38BRC048370 | 140 | 0 | Yes | Yes | 17.9 | 17.5 | 0.4 | 1142EA4D732E488E897C8990CA69A960 |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-5016 |  | 2014-09-05 | 2014-09-05 11:22 | 2014-09-05 11:22 | HEIL - CA3060UKA2 | 144 | 0 | Yes | Yes | 18.8 | 19 | -0.2 | 0C6CB02B7ADF42C695B7E3ADF9F2DC76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3099 |  | 2014-09-24 | 2014-09-24 10:48 | 2014-09-24 10:48 | OTHER - AC060X1022B | 98 | 0 | Yes | Yes | 17.4 | 19.4 | -2 | 14A1C721B25E43AEBCA0AB6DF78DFB10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5905 |  | 2014-10-15 | 2014-10-15 14:45 | 2014-10-15 14:45 | OTHER - UNK | 50 | 0 | Yes | Yes | 21.5 | 18.5 | 3 | A379DAEF4A104076858B64F77E85DB1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1858 |  | 2014-09-09 | 2014-09-09 13:16 | 2014-09-09 13:16 | ICP - PGAD36D1K6 | 102 | 0 | Yes | Yes | 24.2 | 21.5 | 2.7 | E5FF87FE006746D4A6C248F50B41B133 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9177 |  | 2014-11-13 | 2014-11-13 10:26 | 2014-11-13 10:26 | YORK - H1RD036S06G | 145 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 9ACCEB3A5FF44487BAADF8E843368E65 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9177 |  | 2014-11-13 | 2014-11-13 10:29 | 2014-11-13 10:29 | YORK - H2RD030S06B | 93 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 41891CA8755040D287551CE7127039B5 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-2598 |  | 2014-09-08 | 2014-09-08 20:00 | 2014-09-08 20:02 | RHEEM - RRGF05E24JKR | 42 | 3.8 | Yes | Yes | 27.4 | 21.8 | 5.6 | AA9271559E6A46CA825BC2DBC7EF49B7 |  | R22 | Non-TXV |  | 9.048% | 0.90952 | 17.39% | [5 empty] | Non-TXV | 9.048%
Bakersfield | CA | 93311-1421 |  | 2014-09-23 | 2014-09-23 11:17 | 2014-09-23 11:17 | OTHER - UNK | 125 | 0 | Yes | Yes | 19.7 | 18.5 | 1.2 | 010F7A0A63F04A77BD6317169DC6BB85 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2747 |  | 2014-09-27 | 2014-09-27 12:30 | 2014-09-27 12:30 | RHEEM - RRMAA036JK08X | 99 | 0 | Yes | Yes | 18.4 | 18.6 | -0.2 | 1BDBCFD3FADF46848C9EBCB6A6260A08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5020 |  | 2014-10-01 | 2014-10-01 09:59 | 2014-10-01 09:59 | YORK - D6NZ036N05606NA | 64 | 0 | Yes | Yes | 20 | 18.3 | 1.7 | 81A4FEC51E704A198CBAE95D21BF2714 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2102 |  | 2014-10-01 | 2014-10-01 08:50 | 2014-10-01 08:50 | - | 85 | 0 | Yes | Yes | 14.3 | 17.1 | -2.8 | D66639C922324B9BAEBD56AE3B2287B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3886 |  | 2014-10-24 | 2014-10-24 18:24 | 2014-10-24 18:24 | CONCORD - CCU10A24A-1 | 50 | 0 | Yes | Yes | 23.2 | 20.4 | 2.8 | 9D8CB8DBCF67498CBD4BF7D2396B1FA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1457 |  | 2014-10-15 | 2014-10-15 18:26 | 2014-10-15 18:43 | BRYANT - 583ANW036060AAAF | 82 | 5.4 | Yes | Yes | 22.5 | 19.6 | 3 | A444D193EF784FA29AB5034BB2CF9B15 |  | R22 | Non-TXV |  | 6.585% | 0.93415 | 12.66% | [5 empty] | Non-TXV | 6.585%
Bakersfield | CA | 93301-3134 |  | 2014-09-04 | 2014-09-04 16:08 | 2014-09-04 16:08 | DAY & NIGHT - 585CJ036075 | 84 | 0 | Yes | Yes | 25.7 | 21.2 | 4.5 | 9662ED01B7FC40038C9B8073489F970A | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5158 |  | 2014-10-17 | 2014-10-17 13:22 | 2014-10-17 14:19 | CARRIER - 38BR036300 | 122 | 15.1 | Yes | Yes | 19.1 | 18.7 | 0.4 | 381310AF066F49E88E2FE65BABD63116 |  | R22 | Non-TXV |  | 12.38% | 0.87623 | 23.79% | [5 empty] | Non-TXV | 12.38%
Bakersfield | CA | 93301-1516 |  | 2014-09-22 | 2014-09-22 10:23 | 2014-09-22 10:23 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | BBF6D4E5EE1B4720B7EB80FF1A699739 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3069 |  | 2014-09-24 | 2014-09-24 16:33 | 2014-09-24 16:33 | YORK - AC042X1021A | 84 | 0 | Yes | Yes | 23.6 | 25.9 | -2.3 | 8A8AC9AAF8174335811152F3FC41CCA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9184 |  | 2014-10-28 | 2014-10-28 20:37 | 2014-10-28 20:54 | YORK - H2RD042S065B | 141 | -13.3 | Yes | Yes | 17.2 | 20.1 | -2.9 | 4F5564FE2FCF490BA7C9BBC4417EA866 |  | R22 | Non-TXV |  | -9.433% | 1.0943 | 2.642% |  |  |  |  | Non-TXV |  |  | -9.433%
Bakersfield | CA | 93313-2953 |  | 2014-10-04 | 2014-10-04 20:03 | 2014-10-04 20:04 | CARRIER - 48XPN036060311-- | 152 | -5.9 | Yes | Yes | 20.3 | 20.4 | -0.1 | BE991935D7324150BFF9FEC6D1F8A461 |  | R410A | TXV |  | -3.882% | 1.0388 | 1.087% |  |  |  |  | TXV |  |  | -3.882%
Bakersfield | CA | 93308-5625 |  | 2014-10-24 | 2014-10-24 12:14 | 2014-10-24 12:14 | RHEEM - UNK | 85 | 0 | Yes | Yes | 19.9 | 18.7 | 1.2 | 7487BD8089FB42D0A715B95F87FDD87E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2426 |  | 2014-09-25 | 2014-09-25 09:08 | 2014-09-25 09:08 | UNITARY PRODUCTS GROUP - DBYP-F036N070A | 108 | 0 | Yes | Yes | 20.1 | 16.5 | 3.6 | FE3A89ED8F8243EA93C9B6E440D0FCD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9552 |  | 2014-10-19 | 2014-10-19 17:20 | 2014-10-19 17:23 | OTHER - 563CN060-G | 192 | -13.6 | Yes | Yes | 23 | 18.8 | 4.2 | 20E01E137DE8430788295678A0FC18B6 |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Fairfield | CA | 94533-6562 |  | 2014-09-24 | 2014-09-24 11:19 | 2014-09-29 08:13 | CARRIER - 38BRC036330 | 104 | 6.7 | Yes | Yes | 17.2 | 15.4 | 1.8 | DECD8D09B76A4D3195A14970BCA81DA6 |  | R22 | Non-TXV |  | 6.442% | 0.93558 | 12.38% | [5 empty] | Non-TXV | 6.442%
Concord | CA | 94521-1672 |  | 2014-09-08 | 2014-09-08 14:01 | 2014-09-08 14:30 | PAYNE - PA12NAO48-B | 158 | 23.8 | Yes | Yes | 22.9 | 20.7 | 2.3 | BF0AEAE3580840368423A869514C8E0B |  | R22 | Non-TXV |  | 15.06% | 0.84937 | 28.95% | [5 empty] | Non-TXV | 15.06%
Bakersfield | CA | 93306-4930 |  | 2014-09-29 | 2014-09-29 09:31 | 2014-09-29 09:31 | RHEEM - UNK | 133 | 0 | Yes | Yes | 22.9 | 19.1 | 3.8 | 23384C073C6E40E3AFCB62701EACD3FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2203 |  | 2014-09-09 | 2014-09-09 09:36 | 2014-09-09 09:36 | ICP - N4A336AKB200 | 69 | 0 | Yes | Yes | 21.8 | 22.1 | -0.3 | 0579C9DD194044748D00C89876C2DDF8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3964 |  | 2014-10-12 | 2014-10-12 16:25 | 2014-10-12 16:25 | DUCANE - 2AC13B24P1A | 89 | 0 | Yes | Yes | 21.1 | 22 | -0.9 | 85C323FE9F924B848AB135456762EF89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4438 |  | 2014-09-29 | 2014-09-29 10:25 | 2014-09-29 10:25 | RUUD - UNK | 108 | 0 | Yes | Yes | 25.3 | 19.3 | 6 | 87011DB93D9A4F199B3311BFA60C2BEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9014 |  | 2014-10-03 | 2014-10-03 15:17 | 2014-10-03 16:35 | YORK - H2RC036S0SHG | 83 | 6.4 | Yes | Yes | 19.9 | 21.8 | -1.9 | 3EDFEA50CA464CCFB373B1FE5A5E9D8C |  | R22 | Non-TXV |  | 7.711% | 0.92289 | 14.82% | [5 empty] | Non-TXV | 7.711%
Bakersfield | CA | 93311-9014 |  | 2014-10-03 | 2014-10-03 16:37 | 2014-10-03 16:37 | YORK - H2RC036S06HG | 83 | 0 | Yes | Yes | 24.1 | 21.2 | 2.9 | 14BC43EE84D84BBB81F8DD613A0C6418 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3895 |  | 2014-10-13 | 2014-10-13 15:42 | 2014-10-13 15:42 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.4 | 22 | -0.6 | 42104B61BD134036980234A905CEE9FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3824 |  | 2014-09-17 | 2014-09-17 18:01 | 2014-09-17 18:26 | GE - 565BJ036-A | 80 | 8.3 | Yes | Yes | 23.7 | 20.4 | 3.3 | C14DD6237E764134825A126855E19E57 |  | R22 | Non-TXV |  | 10.38% | 0.89625 | 19.94% | [5 empty] | Non-TXV | 10.38%
Bakersfield | CA | 93311-3228 |  | 2014-09-24 | 2014-09-24 14:18 | 2014-09-24 14:18 | OTHER - AC048X1021A | 117 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 74AC5B31B0724A5CAABE89DC181F73CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3883 |  | 2014-10-24 | 2014-10-24 17:34 | 2014-10-24 17:34 | CONCORD - CCU10A18A | 60 | 0 | Yes | Yes | 22.6 | 21 | 1.6 | 6288DCF15EC544A194CA79CE5FB09929 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2942 |  | 2014-08-28 | 2014-08-28 12:44 | 2014-08-28 12:44 | NORDYNE - R4GD036K072X | 100 | 0 | Yes | Yes | 35 | 21.4 | 13.6 | 39FDCC0366DD44949FD834745DD21C41 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5441 |  | 2014-10-15 | 2014-10-15 16:11 | 2014-10-15 16:11 | OTHER - UKN | 90 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | 1EE818CFC0654451A18C7992501D1E27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4959 |  | 2014-09-09 | 2014-09-09 14:04 | 2014-09-09 14:04 | ICP - 80PGF336060K01 | 146 | 0 | Yes | Yes | 25 | 22.4 | 2.7 | 2100B5E8ABBE49B785B8D798B46A4512 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7753 |  | 2014-09-17 | 2014-09-17 18:18 | 2014-09-17 18:18 | PAYNE - PY2PNB036060AAAA | 82 | 0 | Yes | Yes | 23.8 | 20.2 | 3.6 | CF5F921908A440698EE4DCC97AE4A223 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3884 |  | 2014-10-24 | 2014-10-24 18:41 | 2014-10-24 18:41 | CONCORD - CCU10A18A-2 | 60 | 0 | Yes | Yes | 22.1 | 21.8 | 0.3 | 20DA113793E64ACCB6C51D0CDCD47737 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5086 |  | 2014-10-09 | 2014-10-09 12:50 | 2014-10-09 13:12 | OTHER - UNK | 85 | 3.9 | Yes | Yes | 16.4 | 19.4 | -3 | 9FA36C7837084E6387C2C1692FC6D060 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Fairfield | CA | 94534-6613 |  | 2014-09-24 | 2014-09-24 10:18 | 2014-09-29 08:15 | GOODMAN - CK60-1C | 192 | -18.1 | Yes | Yes | 15.6 | 18.1 | -2.5 | 10E4476D373D419DB17D79199B291BB2 |  | R22 | Non-TXV |  | -9.427% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.427%
Bakersfield | CA | 93313-5240 |  | 2014-10-06 | 2014-10-06 12:15 | 2014-10-06 12:35 | OTHER - PA12NA048 | 135 | -11.1 | Yes | Yes | 20.7 | 19.5 | 1.2 | 965ADC33AE2249909FC40DDBD90BF160 |  | R22 | Non-TXV |  | -8.222% | 1.0822 | 2.303% |  |  |  |  | Non-TXV |  |  | -8.222%
Bakersfield | CA | 93301-5947 |  | 2014-09-09 | 2014-09-09 17:33 | 2014-09-09 17:35 | OTHER - AC042X121G | 109 | 6.6 | Yes | Yes | 23.3 | 21.5 | 1.8 | F2B3F39B5345457B8BFE50BD5FB2F258 |  | R22 | Non-TXV |  | 6.055% | 0.93945 | 11.64% | [5 empty] | Non-TXV | 6.055%
Suisun City | CA | 94585-6311 |  | 2014-09-11 | 2014-09-11 10:50 | 2014-09-11 12:02 | CARRIER - 38TD036300 | 180 | 5.6 | Yes | Yes | 21.3 | 20.4 | 0.9 | D1D02C63FC3E4C43B34C5A7CB9EA253E |  | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Bakersfield | CA | 93306-4576 |  | 2014-09-29 | 2014-09-29 12:07 | 2014-09-29 12:07 | YORK - D1NH024N03606C | 70 | 0 | Yes | Yes | 19.8 | 19.8 | 0 | DAD53F209B1C4ABAB95691BEADBD68E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5240 |  | 2014-09-26 | 2014-09-26 15:11 | 2014-09-26 15:11 | PAYNE - PA12NA036 | 100 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | 616B47AE58FE48A482F1D6DAC32ABF9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6212 |  | 2014-10-03 | 2014-10-03 09:19 | 2014-10-03 09:39 | TRANE - 2TTB0048A1000AA | 109 | 34.4 | Yes | Yes | 17.3 | 18.8 | -1.5 | F2E355FFC6E04B869614D7DE79CCD085 |  | R22 | Non-TXV |  | 31.56% | 0.6844 | 60.65% | [5 empty] | Non-TXV | 31.56%
Bakersfield | CA | 93301-5908 |  | 2014-09-08 | 2014-09-08 19:27 | 2014-09-08 19:30 | OTHER - N/A | 85 | 6.8 | Yes | Yes | 22.6 | 22.6 | 0 | CD214C13E8234E90B0A9AED4F961CB8A |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Vacaville | CA | 95687-4129 |  | 2014-09-02 | 2014-09-02 12:18 | 2014-09-02 12:39 | CARRIER - 38TH048310 | 112 | 27.3 | Yes | Yes | 18.6 | 19.9 | -1.3 | D8280F55CC1049C1BA5266FC8E1D718B |  | R22 | Non-TXV |  | 24.38% | 0.75625 | 46.84% | [5 empty] | Non-TXV | 24.38%
Suisun City | CA | 94585-9792 |  | 2014-09-11 | 2014-09-11 12:58 | 2014-09-11 13:35 | PAYNE - PY3NA048090NBP | 197 | 6.4 | Yes | Yes | 18.8 | 19.9 | -1.1 | 2D9E2228004D46CF878F3882F0D8A8B6 |  | R22 | Non-TXV |  | 3.249% | 0.96751 | 6.243% | [5 empty] | Non-TXV | 3.249%
Vallejo | CA | 94589-1730 |  | 2014-09-17 | 2014-09-17 10:13 | 2014-09-17 10:45 | TRANE - YCC036F1MOBH | 83 | 4.7 | Yes | Yes | 21.6 | 20.4 | 1.2 | 6C8A98A035874D139B044A04B80DF4BF |  | R22 | Non-TXV |  | 5.663% | 0.94337 | 10.88% | [5 empty] | Non-TXV | 5.663%
Bakersfield | CA | 93306-8400 |  | 2014-10-12 | 2014-10-12 15:28 | 2014-10-12 15:29 | OTHER - 24ABB360W320 | 130 | 7.1 | Yes | Yes | 22.1 | 22 | 0.1 | 57CD971ABBED4A2F9CAACF1ED26233DA |  | R22 | Non-TXV |  | 5.462% | 0.94538 | 10.5% | [5 empty] | Non-TXV | 5.462%
Bakersfield | CA | 93307-5578 |  | 2014-09-17 | 2014-09-17 10:54 | 2014-09-17 10:54 | YORK - D1NH048N06506C | 128 | 0 | Yes | Yes | 25 | 22.8 | 2.2 | AAD341BE467341EBB07D4DD2339BC2B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4030 |  | 2014-10-15 | 2014-10-15 14:45 | 2014-10-15 14:45 | BDP - 585EJ042075 | 84 | 0 | Yes | Yes | 21.4 | 19.9 | 1.5 | 6247B45B01D14BCBAB11B1D5F89D71B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4526 |  | 2014-09-22 | 2014-09-22 17:58 | 2014-09-22 17:58 | OTHER - PGFM36K060E | 68 | 0 | Yes | Yes | 23.3 | 20.6 | 2.7 | 85ABF6AB57D7495C9A4CD37EC0911EF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5243 |  | 2014-09-23 | 2014-09-23 09:18 | 2014-09-23 09:18 | PAYNE - PA12NA036-H | 146 | 0 | Yes | Yes | 18.5 | 20 | -1.5 | 08DE119D1B30482BAB85A2C24E0D0033 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8344 |  | 2014-10-20 | 2014-10-20 11:58 | 2014-10-20 13:21 | YORK - DBYPF042N080A | 150 | 17.5 | Yes | Yes | 19.7 | 18.7 | 1 | F8268B0281A24F8E9B497A34C024CC7C |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Bakersfield | CA | 93313-5241 |  | 2014-09-23 | 2014-09-23 15:19 | 2014-09-23 15:19 | PAYNE - PA12NA036-H | 100 | 0 | Yes | Yes | 19 | 21.2 | -2.2 | 89875112D6B4415D9D2CA574E7E4C527 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9356 |  | 2014-10-03 | 2014-10-03 16:32 | 2014-10-03 16:32 | YORK - HRC036S06G | 83 | 0 | Yes | Yes | 20.9 | 19.8 | 1.1 | FC80E82987044CEA847EABD338E1C337 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9356 |  | 2014-10-03 | 2014-10-03 16:41 | 2014-10-03 16:41 | YORK - HRC036S06G | 83 | 0 | Yes | Yes | 20.3 | 19.3 | 1 | DC3F33FBA39C4BF68F85116299BA0F31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-0000 |  | 2014-09-23 | 2014-09-23 18:57 | 2014-09-23 18:57 | LENNOX - 13ACD04223001 | 111 | 0 | Yes | Yes | 22 | 19.6 | 2.4 | 3D8E52A7514044348C549CE300426C58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1408 |  | 2014-09-23 | 2014-09-23 13:10 | 2014-09-23 13:10 | OTHER - PGC042K080B | 87 | 0 | Yes | Yes | 18.9 | 19.3 | -0.4 | B4720666B38D4613978B517C3F8C72EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-4141 |  | 2014-10-16 | 2014-10-16 07:51 | 2014-10-16 07:51 | - | 85 | 0 | Yes | Yes | 14.4 | 15.3 | -0.9 | D0694056F060421697FB111C9CFCB5DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5903 |  | 2014-09-04 | 2014-09-04 10:12 | 2014-09-04 11:01 | CARRIER - 561CJO48-F | 109 | 5.5 | Yes | Yes | 22.3 | 19.9 | 2.4 | F2DBBAE2890D4477933F4EE11FAAE0B5 |  | R22 | Non-TXV |  | 5.046% | 0.94954 | 9.697% | [5 empty] | Non-TXV | 5.046%
Bakersfield | CA | 93301-5984 |  | 2014-09-22 | 2014-09-22 09:45 | 2014-09-22 09:45 | DAY & NIGHT - UKN | 90 | 5.2 | Yes | Yes | 20 | 20.4 | -0.4 | 6E31F87B854E4B6EA20C611A936DB09E | Add refrigerant: 5.2 oz | R22 | Non-TXV |  | 5.778% | 0.94222 | 11.1% | [5 empty] | Non-TXV | 5.778%
Bakersfield | CA | 93306-6268 |  | 2014-10-09 | 2014-10-09 13:27 | 2014-10-09 13:45 | WEATHER KING - 13AJA36A01 | 85 | 2.6 | Yes | Yes | 18.2 | 21 | -2.8 | EF6E97C4E0344A5984152844B20E5C3F |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
San Jose | CA | 95136-2122 |  | 2014-09-04 | 2014-09-04 10:05 | 2014-09-04 10:07 | PAYNE - PA10JA030000ACAA | 77 | -16.6 | Yes | Yes | 19.9 | 19.4 | 0.5 | C3C6B53256A94BCC80E10D4419CFADD1 |  | R22 | TXV |  | -21.56% | 1.2156 | 6.037% |  |  |  |  | TXV |  |  | -21.56%
Bakersfield | CA | 93304-4051 |  | 2014-09-30 | 2014-09-30 12:23 | 2014-09-30 12:23 | OTHER - PGAD30D1K4 | 78 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | 9F569B04E56A4FB4A19C3D57A523C68B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5737 |  | 2014-09-09 | 2014-09-09 10:38 | 2014-09-09 11:14 | AMANA - | 76 | 8.7 | Yes | Yes | 20.4 | 20.4 | 0 | 5D1D8BD828C349EFB894DBCD07C006E5 |  | R22 | Non-TXV |  | 11.45% | 0.88553 | 22% | [5 empty] | Non-TXV | 11.45%
Bakersfield | CA | 93305-1916 |  | 2014-09-29 | 2014-09-29 14:12 | 2014-09-29 14:12 | PAYNE - PA1OJA036-C | 78 | 0 | Yes | Yes | 24.5 | 20.4 | 4.1 | F73B37759D7A4EFE9436756E54FC795C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2852 |  | 2014-10-23 | 2014-10-23 13:42 | 2014-10-23 13:42 | ALLEGIANCE - RCB36A2A | 150 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | AA5353654BF2490FBBE2A9F0066CBEC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2907 |  | 2014-09-29 | 2014-09-29 14:54 | 2014-09-29 14:54 | GOODMAN - GPG154811541AB | 172 | 0 | Yes | Yes | 20.2 | 18.3 | 1.9 | 48346DC696564B89A3FFDA7358643ED3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2327 |  | 2014-09-17 | 2014-09-17 15:52 | 2014-09-17 15:52 | UNITARY PRODUCTS GROUP - DAYA-F036N070C | 67 | 0 | Yes | Yes | 22.5 | 21.7 | 0.8 | 66492F2A854B40F6915411A1A30807F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9249 |  | 2014-09-24 | 2014-09-24 12:43 | 2014-09-24 12:43 | UNITARY PRODUCTS GROUP - H2RC036506HA | 83 | 0 | Yes | Yes | 20 | 22 | -2 | 89659E05652643ED87EB01E69C1058E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9249 |  | 2014-09-24 | 2014-09-24 12:44 | 2014-09-24 12:44 | UNITARY PRODUCTS GROUP - H2RC048S0GHA | 120 | 0 | Yes | Yes | 20.5 | 23.2 | -2.7 | 9E19E2B5B7024AAA9036CFC8D1FAC093 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1447 |  | 2014-09-23 | 2014-09-23 11:55 | 2014-09-23 11:55 | DAY & NIGHT - UNK | 74 | 0 | Yes | Yes | 18.5 | 18.8 | -0.3 | 215BF549451A4B01B97093AA91258746 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6744 |  | 2014-09-02 | 2014-09-02 10:07 | 2014-09-02 10:07 | ICP - PGF342080K01 | 188 | 0 | Yes | Yes | 25.7 | 20.8 | 4.9 | EBBF81B96D614174AB5671D86376EECC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5968 |  | 2014-09-09 | 2014-09-09 17:44 | 2014-09-09 17:46 | GIBSON - JS5BBD-042K | 170 | 5.5 | Yes | Yes | 22.1 | 20.4 | 1.7 | C4961D3FE22948BFAE06E243E4530D99 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Suisun City | CA | 94585-3723 |  | 2014-09-11 | 2014-09-11 12:19 | 2014-09-11 12:46 | RUUD - UFAFD-036JAS | 90 | 10 | Yes | Yes | 18.2 | 19.9 | -1.7 | EA24E04734254EB7863797AFD5AE1BF2 |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Bakersfield | CA | 93307-1442 |  | 2014-10-07 | 2014-10-07 09:35 | 2014-10-07 09:35 | UNITARY PRODUCTS GROUP - D2NP036N05606NXA | 108 | 0 | Yes | Yes | 21.9 | 18.2 | 3.7 | CF3C0374A7EC4A689B5C3DEBA4881409 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5732 |  | 2014-09-23 | 2014-09-23 11:46 | 2014-09-23 11:46 | UNITARY PRODUCTS GROUP - H4DH048S06A | 138 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 9E622995ACC145CD8A29303D34F8648F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1929 |  | 2014-10-02 | 2014-10-02 13:33 | 2014-10-02 13:33 | RHEEM - UNK | 117 | 0 | Yes | Yes | 23.5 | 19.3 | 4.2 | 1B4F99C30DFA44F0900914674A2895E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3967 |  | 2014-10-12 | 2014-10-12 17:35 | 2014-10-12 17:35 | DUCANE - 2AC13B18P1A | 84 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 27B112AE531F4BD5AAD1C38374C7840D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4268 |  | 2014-09-15 | 2014-09-15 12:59 | 2014-09-15 17:17 | HEIL - FS3BA-024KA | 74 | 5.5 | Yes | Yes | 22.2 | 20.4 | 1.8 | 6E363E9C03B240319B798E19F8A7A0C6 |  | R22 | Non-TXV |  | 7.432% | 0.92568 | 14.28% | [5 empty] | Non-TXV | 7.432%
Bakersfield | CA | 93304-5766 |  | 2014-11-17 | 2014-11-17 14:21 | 2014-11-17 14:21 | CARRIER - 48GSN036060301 | 56 | 0 | Yes | Yes | 34.5 | 20.2 | 14.4 | 31A7B6D7FC2F449B837D647511EB560D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5169 |  | 2014-09-24 | 2014-09-24 10:11 | 2014-09-29 08:11 | CARRIER - 38BRC030320 | 99 | 12.4 | Yes | Yes | 14.1 | 16.9 | -2.8 | 5A64BCF030044C20AC1E6386A72B3EA4 |  | R22 | Non-TXV |  | 12.53% | 0.87475 | 24.07% | [5 empty] | Non-TXV | 12.53%
Fairfield | CA | 94533-5507 |  | 2014-10-01 | 2014-10-01 14:10 | 2014-10-01 14:10 | - | 85 | 0 | Yes | Yes | 13.5 | 14.8 | -1.3 | E5404717D1BA44DC92C68FDA2326D0F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1276 |  | 2014-09-25 | 2014-09-25 09:54 | 2014-09-25 09:54 | OTHER - PGAA47D1K3 | 129 | 0 | Yes | Yes | 19.1 | 18.7 | 0.4 | 22FC362545394466B1051C914B411276 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3253 |  | 2014-09-17 | 2014-09-17 15:34 | 2014-09-17 15:34 | YORK - D1NP036N05606 | 108 | 0 | Yes | Yes | 19.5 | 21.5 | -2 | 5BE55417E9C94119AE5F8AD5D04B398F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3253 |  | 2014-09-17 | 2014-09-17 15:36 | 2014-09-17 15:36 | BDP - 5838030080YA6R | 50 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | D9276DC21A53401B9530D8241ADCFDD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95120-4151 |  | 2014-09-23 | 2014-09-23 09:20 | 2014-09-23 09:37 | GE - 561AJ048-B | 101 | 11.5 | Yes | Yes | 18.4 | 17.6 | 0.8 | 59EABD5284984BACA19C5606E5BF8FE0 |  | R22 | Non-TXV |  | 11.39% | 0.88614 | 21.88% | [5 empty] | Non-TXV | 11.39%
Bakersfield | CA | 93311-2762 |  | 2014-10-03 | 2014-10-03 21:17 | 2014-10-03 21:43 | AMERICAN STANDARD - C470488UKA2 | 85 | 3 | Yes | Yes | 27.4 | 21.9 | 5.5 | 37FBF804EFB346928CE7E4EE3131A3B5 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Fairfield | CA | 94533-1814 |  | 2014-09-25 | 2014-09-25 14:03 | 2014-09-25 16:08 | DAY & NIGHT - | 106 | 4.1 | Yes | Yes | 20.6 | 21.4 | -0.8 | C6B0C9A57F934A3CA710792A572302F3 |  | R22 | Non-TXV |  | 3.868% | 0.96132 | 7.433% | [5 empty] | Non-TXV | 3.868%
Bakersfield | CA | 93304-4534 |  | 2014-09-22 | 2014-09-22 13:15 | 2014-09-22 13:15 | ALLEGIANCE - 7A2036A100AJ | 120 | 0 | Yes | Yes | 21.5 | 20.2 | 1.4 | 260D0C63ED954993B66AEA46D7C1E78D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2738 |  | 2014-09-24 | 2014-09-24 16:35 | 2014-09-24 16:35 | CARRIER - 591ANX042000ABAA | 50 | 0 | Yes | Yes | 19.5 | 22.1 | -2.6 | 1D96FB40BAEA4C87BBFECA37689476DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8404 |  | 2014-11-04 | 2014-11-04 15:05 | 2014-11-04 15:23 | CARRIER - 38CKB042300 | 80 | 7.6 | Yes | Yes | 22.8 | 19.9 | 2.9 | C9F27988B1924B36AB00CE9D3A8BB6DF |  | R22 | TXV |  | 9.5% | 0.905 | 18.26% | [5 empty] | TXV | 9.5%
Bakersfield | CA | 93307-7630 |  | 2014-09-22 | 2014-09-22 12:26 | 2014-09-22 12:26 | YORK - D1NA03605606A | 67 | 0 | Yes | Yes | 23.3 | 19.4 | 3.9 | 815ED68DAF5B4210A62BD273BE608936 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-2670 |  | 2014-09-22 | 2014-09-22 09:12 | 2014-09-22 09:12 | ICP - PGC024K060A | 58 | 0 | Yes | Yes | 19.6 | 20.4 | -0.8 | D76D197E00BC4209B25E3FB660429D1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3882 |  | 2014-10-24 | 2014-10-24 14:28 | 2014-10-24 14:28 | CONCORD - CCU10A24A-1 | 50 | 0 | Yes | Yes | 22 | 19.8 | 2.2 | 38407D6849C141CFA6A0A3954A89BFA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4334 |  | 2014-10-15 | 2014-10-15 13:59 | 2014-10-15 13:59 | BRYANT - 583ANW036060AAAF | 83 | 0 | Yes | Yes | 25.7 | 20.9 | 4.8 | 44D6C0711D1348A484234E3E305A2F43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3885 |  | 2014-10-24 | 2014-10-24 18:18 | 2014-10-24 18:18 | CONCORD - CCU10A18A-2 | 50 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 037E79106F264E4C8330A9DDA6488A39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3884 |  | 2014-10-24 | 2014-10-24 19:01 | 2014-10-24 19:01 | CONCORD - CCU10A18A-2 | 60 | 0 | Yes | Yes | 21 | 19.8 | 1.2 | F3DFC566AA784F91924B5B71E9DD2969 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3883 |  | 2014-10-24 | 2014-10-24 17:49 | 2014-10-24 17:49 | CONCORD - CCU10A18A-2 | 60 | 0 | Yes | Yes | 25 | 20.4 | 4.6 | 13D71D05B5EA4B1CB73CB9DA3C79725A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3804 |  | 2014-09-11 | 2014-09-11 11:25 | 2014-09-11 11:53 | PAYNE - 591ANX034000AAA | 95 | 6.9 | Yes | Yes | 19.8 | 19.9 | -0.1 | D1A219225C5B4D28852650D6971D0296 |  | R22 | Non-TXV |  | 7.263% | 0.92737 | 13.96% | [5 empty] | Non-TXV | 7.263%
Bakersfield | CA | 93301-3448 |  | 2014-10-15 | 2014-10-15 11:16 | 2014-10-15 11:16 | DAY & NIGHT - 3080YAC106T | 65 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 53DFF38B708D47789E18986678F96BE7 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3980 |  | 2014-10-13 | 2014-10-13 14:05 | 2014-10-13 14:05 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.4 | 22.6 | -1.2 | 4E33FDD89C334D8391AA90F673DC362F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3013 |  | 2014-09-24 | 2014-09-24 10:06 | 2014-09-24 10:06 | ICP - CA9036VKC1 | 97 | 0 | Yes | Yes | 24.5 | 21.5 | 3 | 604E94EC59EA4ACDA9D4B866EF01242A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4430 |  | 2014-11-07 | 2014-11-07 13:05 | 2014-11-07 13:31 | RHEEM - RACA030ABC | 35 | 9.1 | Yes | Yes | 18.8 | 17.9 | 0.9 | EC5F9971A2DB41B8A4612DB954000C39 |  | R22 | Non-TXV |  | 26% | 0.74 | 49.97% | [5 empty] | Non-TXV | 26%
Bakersfield | CA | 93307-3981 |  | 2014-10-13 | 2014-10-13 14:10 | 2014-10-13 14:10 | CONCORD - CCV10A24A1 | 50 | 0 | Yes | Yes | 21.1 | 20.7 | 0.4 | BBE7DFB9CBD247B89CE89B063CDB9C09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3930 |  | 2014-09-23 | 2014-09-23 12:29 | 2014-09-23 12:29 | RHEEM - UKN | 90 | 0 | Yes | Yes | 20 | 20.6 | -0.6 | 690FB1B9357D43FC8B90C36BF2A91D80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2009 |  | 2014-10-23 | 2014-10-23 11:44 | 2014-10-23 11:44 | CARRIER - 48GSN036060301 | 56 | 0 | Yes | Yes | 21.2 | 20.2 | 1.1 | CD03C1F7BC00462BADB2A9B181B7A4B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3208 |  | 2014-08-28 | 2014-08-28 17:35 | 2014-08-28 17:35 | CARRIER - 38E6108 | 92 | 0 | Yes | Yes | 35 | 21 | 14 | 986620DAAA9C47B6B5FD3FD40C1CBEB8 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6313 |  | 2014-09-17 | 2014-09-17 10:53 | 2014-09-17 11:19 | CARRIER - 38CKC060370 | 131 | 5.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | 6DF7262AF35943F4BB0A6C6450F0D37C |  | R22 | Non-TXV |  | 4.122% | 0.95878 | 7.922% | [5 empty] | Non-TXV | 4.122%
Bakersfield | CA | 93305-1013 |  | 2014-10-09 | 2014-10-09 11:15 | 2014-10-09 11:15 | AMERICAN STANDARD - 4YCZ6036A1075AB | 111 | 0 | Yes | Yes | 25.2 | 22.6 | 2.6 | 17C3AE7E01644C29B5DD16007860616E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2251 |  | 2014-10-07 | 2014-10-07 15:46 | 2014-10-07 15:46 | GOODMAN - UKN | 86 | 0 | Yes | Yes | 25.9 | 22.5 | 3.4 | 0024131A377B45B9BF06A4E77A946C24 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3881 |  | 2014-10-13 | 2014-10-13 12:29 | 2014-10-13 12:29 | CONCORD - CCV10A241 | 50 | 0 | Yes | Yes | 21.4 | 21.8 | -0.4 | 470481A1C6BE4C9691F750D53FBB7A42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6911 |  | 2014-10-20 | 2014-10-20 13:05 | 2014-10-20 13:05 | LENNOX - 13ACD-042-230-02 | 111 | 0 | Yes | Yes | 21 | 21 | 0 | 6804AE8E89CF4D2BA538E3162AA5220D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-2515 |  | 2014-09-22 | 2014-09-22 09:31 | 2014-09-22 09:31 | ICP - WPG3244040LKC1 | 72 | 0 | Yes | Yes | 24.5 | 19.7 | 4.9 | 43AD8A42254D411A949CA076E9EBFA51 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4819 |  | 2014-10-07 | 2014-10-07 15:19 | 2014-10-07 15:19 | UNITARY PRODUCTS GROUP - DCYP-F024N045A | 100 | 0 | Yes | Yes | 17.4 | 17.9 | -0.5 | 4FBCB3E0FF7B4691AB894A609F1AB2C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1613 |  | 2014-09-23 | 2014-09-23 13:43 | 2014-09-23 14:18 | AMANA - PCC36A2B | 114 | 4.6 | Yes | Yes | 20.8 | 20.7 | 0.1 | 07525534DC6147138501C2C9DA327A71 |  | R22 | Non-TXV |  | 4.035% | 0.95965 | 7.755% | [5 empty] | Non-TXV | 4.035%
Vallejo | CA | 94591-4153 |  | 2014-10-01 | 2014-10-01 11:02 | 2014-10-01 11:02 | CARRIER - 24APA548A310 | 180 | 0 | Yes | Yes | 19.4 | 20.9 | -1.5 | 9DDADD1E5FD346B28BA68033D82E29A6 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9670 |  | 2014-09-26 | 2014-09-26 16:13 | 2014-09-26 16:13 | BRYANT - 113RNA036-B | 93 | 0 | Yes | Yes | 19.9 | 22.1 | -2.2 | 01DF22922AE94A77A692D72C9E0A0C92 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2777 |  | 2014-10-06 | 2014-10-06 14:48 | 2014-10-06 14:48 | UNITARY PRODUCTS GROUP - D2NP030N03606NXA | 73 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | 2CED15109D354F00AAFD52E2550A6F8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1543 |  | 2014-09-23 | 2014-09-23 10:50 | 2014-09-23 11:19 | CARRIER - 38TXAO36330 | 85 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | EB016C4EA5994A74A41759FA7EAB4F0E |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2778 |  | 2014-10-06 | 2014-10-06 14:38 | 2014-10-06 14:38 | UNITARY PRODUCTS GROUP - D2NP030N03606NXA | 73 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 9B76CA03EAFD4B358CF067AB8E74F48E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1700 |  | 2014-09-23 | 2014-09-23 11:23 | 2014-09-23 16:19 | YORK - H2CB02406B | 65 | 3.3 | Yes | Yes | 19.2 | 20.4 | -1.2 | 8A7211BC53054F8F89BA672B3435E81C |  | R22 | Non-TXV |  | 5.077% | 0.94923 | 9.757% | [5 empty] | Non-TXV | 5.077%
Antioch | CA | 94509-6262 |  | 2014-11-17 | 2014-11-17 11:19 | 2014-11-17 11:46 | COLEMAN - UNK | 85 | 7.2 | Yes | Yes | 18.7 | 13.4 | 5.3 | F3F7786D33BD4361BE00DCE38C636794 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Bakersfield | CA | 93307-7105 |  | 2014-10-19 | 2014-10-19 18:16 | 2014-10-19 18:19 | CARRIER - 584BNN036060AA2F | 64 | 2.6 | Yes | Yes | 24.7 | 19.3 | 5.4 | 8CACD73F551046249284A90D1B339E9D |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Antioch | CA | 94531-9068 |  | 2014-11-17 | 2014-11-17 12:38 | 2014-11-17 12:38 | PAYNE - PA13NA042 | 103 | 0 | Yes | Yes | 20.1 | 18.3 | 1.8 | 5BD93047A674461E805EEEF966E60330 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8513 |  | 2014-11-18 | 2014-11-18 10:36 | 2014-11-18 11:24 | GOODMAN - CK42-1A | 96 | 3.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | 976E690F16614C919017EB5B2D418170 |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Bakersfield | CA | 93307-3476 |  | 2014-10-07 | 2014-10-07 16:48 | 2014-10-07 16:48 | UNITARY PRODUCTS GROUP - DAYP-F042N080A | 150 | 0 | Yes | Yes | 28.5 | 22.5 | 6 | DE6E5435A8F64D9AB1424038B28A048E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4984 |  | 2014-09-25 | 2014-09-25 11:00 | 2014-09-25 11:00 | ALLEGIANCE - 4A7A6036E1000AA | 157 | 0 | Yes | Yes | 19.7 | 20.2 | -0.5 | 137743CFA4D3433DB5EB0DB0781FE8C7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7554 |  | 2014-09-24 | 2014-09-24 19:30 | 2014-09-24 19:30 | PAYNE - UKN | 90 | 0 | Yes | Yes | 20.7 | 23.7 | -3 | E8B0540413084FF78C3C83794897B32A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3215 |  | 2014-09-24 | 2014-09-24 10:36 | 2014-09-24 10:36 | UNITARY PRODUCTS GROUP - AC042X1021A | 84 | 0 | Yes | Yes | 25 | 19.4 | 5.6 | 78E54871ADEB4E9BB5AAD656019D7458 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3723 |  | 2014-10-16 | 2014-10-16 13:53 | 2014-10-16 13:53 | YORK - D1NA030N05606C | 76 | 0 | Yes | Yes | 18.2 | 18.7 | -0.5 | D62C1C5899A84746B58E487FE1CAA42E |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6312 |  | 2014-09-30 | 2014-09-30 09:01 | 2014-09-30 09:01 | GMC - V8X130361EB | 64 | 0 | Yes | Yes | 17.2 | 17.3 | 0 | A5134CAEE4094A8290D4DC320CCE8321 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9421 |  | 2014-10-17 | 2014-10-17 11:24 | 2014-10-17 11:42 | LENNOX - HS29-048-1P | 83 | 2.5 | Yes | Yes | 18.2 | 21 | -2.8 | 75E5FFAE916C40F3AC116917781A4840 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Fairfield | CA | 94533-2212 |  | 2014-09-25 | 2014-09-25 11:18 | 2014-09-25 12:03 | BRYANT - 54FDY-0300DE-0002A | 85 | 3.1 | Yes | Yes | 21.3 | 19.9 | 1.4 | AB1BA2C8C11C43F893DC831608ED6EA2 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Bakersfield | CA | 93309-7306 |  | 2014-09-30 | 2014-09-30 16:27 | 2014-09-30 16:27 | ICP - PGF354100K01A1 | 213 | 0 | Yes | Yes | 23.4 | 20.4 | 3 | A9C904908842480CBE452A73AFBB0D76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1318 |  | 2014-09-24 | 2014-09-24 08:31 | 2014-09-24 08:46 | BDP - 568DJ042 | 152 | -14.3 | Yes | Yes | 20.1 | 17.7 | 2.4 | 3036CA833A10486E925EA398E4B416DF |  | R22 | Non-TXV |  | -9.408% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.408%
Woodland | CA | 95695-4951 |  | 2014-09-29 | 2014-09-29 13:55 | 2014-09-29 18:56 | COLEMAN - | 90 | 4.4 | Yes | Yes | 18.3 | 19.9 | -1.6 | B470D7C315FC4E9F8061A7775B80885A |  | R22 | Non-TXV |  | 4.889% | 0.95111 | 9.395% | [5 empty] | Non-TXV | 4.889%
Bakersfield | CA | 93312-4358 |  | 2014-10-29 | 2014-10-29 14:09 | 2014-10-29 14:09 | RUUD - UKN | 90 | 0 | Yes | Yes | 25.6 | 20.7 | 4.9 | CB95164A496143B7925C33E31B6B9F72 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9008 |  | 2014-09-24 | 2014-09-24 12:04 | 2014-09-24 12:04 | WEATHER KING - 12AJB36A01 | 107 | 0 | Yes | Yes | 20 | 21.8 | -1.8 | 698540E6F895416F9DD31FF22680EF80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2313 |  | 2014-09-24 | 2014-09-24 13:55 | 2014-09-24 13:55 | TRANE - YCC048F1H0BB | 128 | 0 | Yes | Yes | 22.2 | 22.6 | -0.4 | C1EECB9356A74B459579A9F6F7A49190 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5709 |  | 2014-10-20 | 2014-10-20 12:46 | 2014-10-20 13:05 | CARRIER - N4A330AKC200 | 74 | 4.8 | Yes | Yes | 19.3 | 20.2 | -0.9 | CA0002EFEBB4485A8EF89B032A61A964 |  | R410A | Non-TXV |  | 6.486% | 0.93514 | 12.47% | [5 empty] | Non-TXV | 6.486%
Fairfield | CA | 94533-7063 |  | 2014-10-16 | 2014-10-16 09:05 | 2014-10-17 08:34 | - | 85 | 3.5 | Yes | Yes | 16.4 | 15.5 | 0.9 | 262A46FF9A9B4B16B2B8EE1B6605569A |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fairfield | CA | 94533-7735 |  | 2014-09-25 | 2014-09-25 11:14 | 2014-09-25 12:04 | PAYNE - 591ANY048000ABAA | 116 | 4.4 | Yes | Yes | 20.6 | 21 | -0.4 | 95CDE035DC334C3CADA7A7D7A64C2830 | Add refrigerant: 4.4 oz | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Bakersfield | CA | 93307-3885 |  | 2014-10-24 | 2014-10-24 18:30 | 2014-10-24 18:30 | CONCORD - CCU10A24A-1 | 50 | 0 | Yes | Yes | 23.9 | 19.8 | 4.1 | 6FCF625F60B843AB9F2B32CAB8A9A835 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3924 |  | 2014-10-20 | 2014-10-20 13:41 | 2014-10-20 13:41 | PAYNE - PY3PNA036060NB | 115 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | ECEF79958A2842E9B088698A9219943B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3885 |  | 2014-10-24 | 2014-10-24 17:21 | 2014-10-24 17:21 | CONCORD - CCU10A18A-2 | 60 | 0 | Yes | Yes | 24.5 | 20.4 | 4.1 | CF68BE6CEC9E433FAA6957C18327A181 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1159 |  | 2014-09-25 | 2014-09-25 12:02 | 2014-09-25 12:39 | OTHER - 585CB048100 | 120 | 20.6 | Yes | Yes | 26.9 | 21 | 5.9 | 27483DF2712B4481B462E3E9FDACA7C9 |  | R22 | Non-TXV |  | 17.17% | 0.82833 | 32.99% | [5 empty] | Non-TXV | 17.17%
Bakersfield | CA | 93306-1412 |  | 2014-11-10 | 2014-11-10 09:35 | 2014-11-10 09:35 | LENNOX - LC4260Y9CG | 120 | 0 | Yes | Yes | 20.6 | 19.9 | 0.7 | 0B6D3CD9529342A681E60D60255540CF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9671 |  | 2014-09-24 | 2014-09-24 11:17 | 2014-09-24 11:17 | BRYANT - 113RNA036-C | 93 | 0 | Yes | Yes | 27.5 | 22.4 | 5.2 | A56E49E9FD10448D9EA631C3C20363EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9117 |  | 2014-09-24 | 2014-09-24 15:15 | 2014-09-24 15:15 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 19.6 | 21.4 | -1.8 | 90803E6EB43941D78FB82C2425EE4D31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9117 |  | 2014-09-24 | 2014-09-24 15:19 | 2014-09-24 15:19 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 23.5 | 22.9 | 0.6 | D8FAFEAE8A5B4C11A1DCECC0C10029D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2016 |  | 2014-09-25 | 2014-09-25 15:02 | 2014-09-25 15:02 | OTHER - GR6GDX48K096C | 224 | 13.7 | Yes | Yes | 9.9 | 18.3 | -8.4 | C924713BFEAD43F9BE2DD78D04C3722C | Add refrigerant: 13.7 oz Evaporator saturation temperature is <25°F. Please check entries. | R410A | Non-TXV |  | 6.116% | 0.93884 | 11.75% | [5 empty] | Non-TXV | 6.116%
Bakersfield | CA | 93306-1027 |  | 2014-10-11 | 2014-10-11 12:58 | 2014-10-11 12:58 | GOODMAN - GPG1360090M41AC | 185 | 0 | Yes | Yes | 22 | 19.6 | 2.4 | 1AFF700617864318BD8E6657F03320A5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-5938 |  | 2014-09-29 | 2014-09-29 08:10 | 2014-09-29 08:12 | CARRIER - S38A-036KA- | 69 | 2.1 | Yes | Yes | 20.6 | 17.7 | 2.9 | 5CE9AB4CD6DD463A8C811B2E0C568578 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Bakersfield | CA | 93312-8255 |  | 2014-10-29 | 2014-10-29 14:39 | 2014-10-29 14:39 | YORK - H1RA048S06D | 117 | 0 | Yes | Yes | 22.2 | 20.7 | 1.5 | FDBE1A7518484EA69C88121D1580C58D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2608 |  | 2014-09-26 | 2014-09-26 13:39 | 2014-09-26 14:32 | CARRIER - 48GSN30060301 | 71 | 2.3 | Yes | Yes | 20.9 | 20.4 | 0.5 | 66793182FEEF4F7B8FA2D097C06CE0E8 |  | R22 | Non-TXV |  | 3.239% | 0.96761 | 6.225% | [5 empty] | Non-TXV | 3.239%
Bakersfield | CA | 93307-3981 |  | 2014-10-13 | 2014-10-13 14:26 | 2014-10-13 14:26 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 21.3 | 22 | -0.7 | AF76B3ECCA3A4A4AB151E136682CA7CE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-1229 |  | 2014-09-26 | 2014-09-26 11:52 | 2014-09-26 11:52 | TRANE - TT036A100A0 | 102 | 0 | Yes | Yes | 20.2 | 22.1 | -1.9 | E3AD7BFDE96B462EB77149B2088D8391 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1349 |  | 2014-09-25 | 2014-09-25 09:28 | 2014-09-25 10:10 | AMERICAN STANDARD - 4A7A6060B1000AA | 160 | 5.8 | Yes | Yes | 21.3 | 20.4 | 0.9 | 670F3E06C54E48CA92094A0CB5C825C6 |  | R410A | TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | TXV | 3.625%
Bakersfield | CA | 93312-2305 |  | 2014-10-11 | 2014-10-11 15:31 | 2014-10-11 15:48 | ICP - PGC048K080K | 85 | 4.6 | Yes | Yes | 21.4 | 24.4 | -3 | A0461DACB74A41809FD8CADEA199F2B6 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Antioch | CA | 94509-4740 |  | 2014-11-03 | 2014-11-03 10:32 | 2014-11-03 10:52 | PAYNE - PA13NA036-B | 72 | 8.1 | Yes | Yes | 19.5 | 18.8 | 0.7 | C8F48269FF7241EB8906D2D3EE85DF05 |  | R410A | TXV |  | 11.25% | 0.8875 | 21.62% | [5 empty] | TXV | 11.25%
Bakersfield | CA | 93309-2159 |  | 2014-09-24 | 2014-09-24 19:37 | 2014-09-24 19:37 | RHEEM - RRNAB036JK06X | 83 | 0 | Yes | Yes | 20.6 | 19.3 | 1.3 | 30931FC0C4B148058D8DD34BB5BC9EEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1235 |  | 2014-09-25 | 2014-09-25 10:46 | 2014-09-25 11:35 | CARRIER - 48XN042060301 | 118 | 12.9 | Yes | Yes | 19.1 | 20.4 | -1.3 | 259874DBB2854F139938433373B8A9CA |  | R22 | Non-TXV |  | 10.93% | 0.89068 | 21.01% | [5 empty] | Non-TXV | 10.93%
Bakersfield | CA | 93306-1775 |  | 2014-09-25 | 2014-09-25 13:15 | 2014-09-25 13:15 | DAY & NIGHT - UNK | 115 | 0 | Yes | Yes | 16.3 | 17.7 | -1.4 | F908C7FCEFDB4069A2B94D316A6125D7 | Final Suction Temperature must be between 20°F and 80°F. Please check entries. Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3984 |  | 2014-10-13 | 2014-10-13 15:39 | 2014-10-13 15:39 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 21.4 | 22 | -0.6 | 3F970518281B44AC8938F155C033AD4A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3983 |  | 2014-10-13 | 2014-10-13 14:53 | 2014-10-13 14:53 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | 4A049CFC2D0A4E6EA58E317DF1BDD935 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-8648 |  | 2014-10-29 | 2014-10-29 15:00 | 2014-10-29 15:00 | UNITARY PRODUCTS GROUP - AC042X1221A | 107 | 0 | Yes | Yes | 22.3 | 20.4 | 1.9 | 6C5EBCD7DEDF4A438D1BE85FE832DC41 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-2879 |  | 2014-09-20 | 2014-09-20 17:26 | 2014-09-20 17:29 | RHEEM - RRGG-05N31JKR | 48 | 3.7 | Yes | Yes | 20.1 | 20.9 | -0.8 | 74F0D2BF5D114D75B9A38971C9F09A0B |  | R22 | Non-TXV |  | 7.708% | 0.92292 | 14.81% | [5 empty] | Non-TXV | 7.708%
Bakersfield | CA | 93306-1404 |  | 2014-10-28 | 2014-10-28 12:43 | 2014-10-28 12:43 | UNK - UNK | 85 | 0 | Yes | Yes | 25 | 20.7 | 4.3 | 85C7AD39281947BA9619CF055657CA38 |  |  |  |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5667 |  | 2014-09-25 | 2014-09-25 15:17 | 2014-09-25 15:17 | CARRIER - 4105E42707 | 133 | 0 | Yes | Yes | 20.7 | 19.7 | 1 | 9C9BC155221746F19598D721F25F3B6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1308 |  | 2014-10-06 | 2014-10-06 16:02 | 2014-10-06 16:02 | RHEEM - RKMA-A060J610E | 42 | 0 | Yes | Yes | 27 | 21.7 | 5.4 | D8617973505A4E55BCF662682BF725C3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4404 |  | 2014-10-16 | 2014-10-16 09:25 | 2014-10-16 09:25 | RHEEM - RRGG05N37JKR | 77 | 0 | Yes | Yes | 0 | N/A | N/A | 5C4B04D18BE14FA5AAFA41CF5BCF1F26 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2932 |  | 2014-09-23 | 2014-09-23 14:32 | 2014-09-23 14:32 | BDP - 585HJ030040 | 78 | 0 | Yes | Yes | 19 | 21.3 | -2.3 | C897078AA03946BFBD2AA8A3A45B1074 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95139-1433 |  | 2014-09-29 | 2014-09-29 09:00 | 2014-09-29 09:03 | CARRIER - 24ABA348A310 | 195 | 19.5 | Yes | Yes | 19.6 | 18.2 | 1.4 | E5B2BD29D5B1415E824CC582EB242282 |  | R410A | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Bakersfield | CA | 93307-5870 |  | 2014-10-16 | 2014-10-16 15:12 | 2014-10-16 15:12 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 21.2 | 19.3 | 1.9 | E8C54F7CFEFA455C90A31261CDFB9FEA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2512 |  | 2014-10-15 | 2014-10-15 18:30 | 2014-10-15 18:48 | AMERICAN STANDARD - 4YCY4048A1096AA | 85 | 11.9 | Yes | Yes | 17.4 | 19.3 | -1.9 | 7EEC60F7C1574F1885D8A278C9D662E6 |  | R410A | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Woodland | CA | 95776-9347 |  | 2014-09-24 | 2014-09-24 10:22 | 2014-09-24 11:00 | GOODMAN - CKT60-1B | 150 | 5.4 | Yes | Yes | 18.9 | 20.2 | -1.3 | 8AEB4562D38B4CF6A97FD9756FF504CB |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Fairfield | CA | 94533-5232 |  | 2014-09-25 | 2014-09-25 11:33 | 2014-09-25 12:01 | GOODMAN - GPG13300701BB | 78 | 3.8 | Yes | Yes | 17.6 | 20.4 | -2.8 | 4FCBDF887C4B4368B60677D319749432 |  | R22 | Non-TXV |  | 4.872% | 0.95128 | 9.363% | [5 empty] | Non-TXV | 4.872%
Bakersfield | CA | 93312-8231 |  | 2014-10-02 | 2014-10-02 10:37 | 2014-10-02 10:37 | AIRE-FLO - 2AC13B42P-1A | 36 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | CB241D326D0748068477EE6CDBE54E2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3115 |  | 2014-09-26 | 2014-09-26 10:48 | 2014-09-26 11:19 | NORDYNE - JS5BD-030KA | 97 | 3.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | 1F9C11E4DA4A441793A77A887C4E269F |  | R22 | Non-TXV |  | 3.505% | 0.96495 | 6.736% | [5 empty] | Non-TXV | 3.505%
Suisun City | CA | 94585-4110 |  | 2014-09-29 | 2014-09-29 09:43 | 2014-09-29 09:43 | PAYNE - 597ANX030000AAAA | 88 | 0 | Yes | Yes | 17.4 | 19.1 | -1.7 | 772753FE1A8B4ADD8EE902A7755E399A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-5918 |  | 2014-10-06 | 2014-10-06 09:53 | 2014-10-06 09:53 | RHEEM - RRNA-B036JK06X | 83 | 0 | Yes | Yes | 20.1 | 18.8 | 1.3 | 77B52625A10648CD9EBD29F4AFD42CF9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6036 |  | 2014-11-03 | 2014-11-03 14:09 | 2014-11-03 14:09 | TRANE - TTR036C100A2 | 87 | 0 | Yes | Yes | 17.2 | 19.3 | -2.1 | 1BFC6EF703A6426F899F7D223306A881 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6024 |  | 2014-10-07 | 2014-10-07 12:00 | 2014-10-07 12:00 | CARRIER - 4855-030040301 | 55 | 0 | Yes | Yes | 22.2 | 23.1 | -0.9 | 2DD5B8727B174C3D812BB0EDC9F2C40C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3360 |  | 2014-09-30 | 2014-09-30 11:18 | 2014-09-30 11:18 | - | 85 | 0 | Yes | Yes | 14.4 | 16.6 | -2.2 | C8BD1D8F49954B2088C5157D682BDBC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2928 |  | 2014-09-29 | 2014-09-29 10:46 | 2014-09-29 10:46 | UNITARY PRODUCTS GROUP - DAYP-F048N080F` | 132 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 287F683E35C94C87A3B65031104D07BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3979 |  | 2014-10-13 | 2014-10-13 12:56 | 2014-10-13 12:56 | GOODMAN - GSC130181AE | 89 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | 223FED40C47F4C669A695D557C0635EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4472 |  | 2014-10-03 | 2014-10-03 11:42 | 2014-10-03 16:21 | GE - ETC-9450248689-10 | 76 | 2.9 | Yes | Yes | 21.2 | 20.4 | 0.8 | BFC9886C936244F1B84C65E73AD9CD0B |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Bakersfield | CA | 93307-3886 |  | 2014-10-24 | 2014-10-24 17:23 | 2014-10-24 17:23 | CONCORD - CCU10A24A-1 | 50 | 0 | Yes | Yes | 21.1 | 20.7 | 0.4 | 1E60292887074C8E86604424131D6D07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5759 |  | 2014-09-22 | 2014-09-22 15:17 | 2014-09-22 15:17 | OTHER - 24ABB336W310 | 83 | 0 | Yes | Yes | 16.7 | 19.2 | -2.5 | 2A8A657911C04D44BED4CD71942EED34 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4635 |  | 2014-10-11 | 2014-10-11 11:15 | 2014-10-11 11:15 | YORK - D1NH048N06506C | 128 | 0 | Yes | Yes | 26.3 | 21 | 5.3 | A76FAD6B10194DFC8A5078F49CA0E87C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6712 |  | 2014-10-23 | 2014-10-23 14:24 | 2014-10-23 14:24 | CARRIER - 38CKC060370 | 133 | 0 | Yes | Yes | 22.6 | 19.8 | 2.8 | 4CA12EE7E0784E83A4518C0170ED775A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2518 |  | 2014-10-16 | 2014-10-16 11:20 | 2014-10-16 11:20 | YORK - D1NH030N05606C | 73 | 0 | Yes | Yes | 19.5 | 19.5 | 0 | 910DCEFDB7594D6F9140E205B7DEF2FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2120 |  | 2014-09-25 | 2014-09-25 16:13 | 2014-09-25 16:13 | OTHER - UNK | 148 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | F8A0357A07D84E0B9F381063F6E246A0 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3594 |  | 2014-09-23 | 2014-09-23 12:38 | 2014-09-23 12:38 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 22 | 21.8 | 0.2 | FC81B44DCB424E1EB14775192467D386 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1931 |  | 2014-11-03 | 2014-11-03 13:54 | 2014-11-03 13:54 | RHEEM - RRPL-B036JK06X | 92 | 0 | Yes | Yes | 27.2 | 21.5 | 5.7 | E2C8CC9F0EC945C09AD4276FFF4F5B4C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2510 |  | 2014-09-30 | 2014-09-30 13:41 | 2014-09-30 13:41 | RUUD - URMA-A048JK08X | 117 | 0 | Yes | Yes | 24 | 22.1 | 1.9 | 35E557C89C244255A39858E325E0BF54 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-5963 |  | 2014-10-28 | 2014-10-28 15:57 | 2014-10-28 15:57 | OTHER - UKN | 90 | 0 | Yes | Yes | 24.2 | 20.1 | 4.2 | C459B0E0B816470392A9BAFC89CB26B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8654 |  | 2014-11-17 | 2014-11-17 11:35 | 2014-11-17 11:57 | GOODMAN - GSC130301AE | 151 | 4.6 | Yes | Yes | 18 | 19.9 | -1.9 | 6843D61F1B784CCFB4F0401E21295DFB |  | R22 | Non-TXV |  | 3.046% | 0.96954 | 5.854% | [5 empty] | Non-TXV | 3.046%
Suisun City | CA | 94585-2103 |  | 2014-09-30 | 2014-09-30 07:53 | 2014-09-30 07:53 | - | 85 | 0 | Yes | Yes | 14.2 | 16.4 | -2.2 | 640D7E8024504BB38E9BBEA382406730 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2252 |  | 2014-10-16 | 2014-10-16 10:28 | 2014-10-16 10:28 | - | 85 | 0 | Yes | Yes | 13.6 | 15.8 | -2.2 | A8BF016BA26D46C68F542605F390060B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3253 |  | 2014-10-07 | 2014-10-07 14:36 | 2014-10-07 14:36 | AMERICAN STANDARD - 2YCC3030A1040AA | 88 | 0 | Yes | Yes | 27 | 21.3 | 5.7 | 145FD26D2E4246A48B6CDD336C7482C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4352 |  | 2014-09-30 | 2014-09-30 15:11 | 2014-09-30 16:31 | YORK - D1NH042N06506C | 92 | -8.7 | Yes | Yes | 23.8 | 21 | 2.8 | 80D604D74CE94B07BD5859904F6F0FBE |  | R22 | Non-TXV |  | -9.457% | 1.0946 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.457%
San Jose | CA | 95123-4517 |  | 2014-09-26 | 2014-09-26 08:28 | 2014-09-26 08:36 | YORK - H2DB048S06A | 111 | 4.3 | Yes | Yes | 19.2 | 18.5 | 0.7 | 777253C84F614EBE910E1569F5711BA9 |  | R22 | Non-TXV |  | 3.874% | 0.96126 | 7.445% | [5 empty] | Non-TXV | 3.874%
Bakersfield | CA | 93313-6070 |  | 2014-10-06 | 2014-10-06 14:08 | 2014-10-06 14:27 | ICP - PGAA36C11K6 | 69 | -5.7 | Yes | Yes | 19.5 | 19.8 | -0.3 | FB481E807DC64AA69D50E1BC1BACC88C |  | R22 | Non-TXV |  | -8.261% | 1.0826 | 2.313% |  |  |  |  | Non-TXV |  |  | -8.261%
Bakersfield | CA | 93311-2715 |  | 2014-10-02 | 2014-10-02 12:28 | 2014-10-02 12:28 | GOODMAN - GPG1342070M41BA | 81 | 0 | Yes | Yes | 21.7 | 22 | -0.3 | A906A9899C3E494ABDDE1A5CDEF010BA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4161 |  | 2014-10-06 | 2014-10-06 10:40 | 2014-10-06 10:40 | AMERICAN STANDARD - YCY048G1HON0 | 187 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | 6A04C4387E9D4578BD2E8314B8DAB00C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2817 |  | 2014-10-03 | 2014-10-03 11:39 | 2014-10-03 16:20 | CARRIER - 48GX-030060311AD | 69 | 4.4 | Yes | Yes | 21.1 | 20.4 | 0.7 | ABA9773AE35442528D3F2F7E5D2B44CD |  | R22 | Non-TXV |  | 6.377% | 0.93623 | 12.25% | [5 empty] | Non-TXV | 6.377%
Woodland | CA | 95776-5708 |  | 2014-09-24 | 2014-09-24 11:15 | 2014-09-24 11:32 | AMERICAN STANDARD - 4A7B4036E1000AA | 117 | 11.6 | Yes | Yes | 21.3 | 20.4 | 0.9 | 8BE5901ECE6F4ABEAC42A3DD877308B4 |  | R22 | TXV |  | 9.915% | 0.90085 | 19.05% | [5 empty] | TXV | 9.915%
Vacaville | CA | 95688-2563 |  | 2014-09-26 | 2014-09-26 11:42 | 2014-09-26 11:42 | CARRIER - TCGD48S21S2A | 69 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | C47E44BF2BE245648DB6FCA913970B7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1507 |  | 2014-10-03 | 2014-10-03 13:20 | 2014-10-06 08:20 | CARRIER - 24ABA336A300 | 84 | 2.7 | Yes | Yes | 14.9 | 13.7 | 1.3 | 9E56DEACF7C54B3E905BC73B57BBFBFE |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Vacaville | CA | 95687-3413 |  | 2014-10-22 | 2014-10-22 13:20 | 2014-10-22 13:51 | CARRIER - 38TRA024-321 | 87 | 5 | Yes | Yes | 20.7 | 20.4 | 0.3 | 9FD316787134451CB87D245C1433E352 |  | R22 | Non-TXV |  | 5.747% | 0.94253 | 11.04% | [5 empty] | Non-TXV | 5.747%
Fairfield | CA | 94533-1149 |  | 2014-09-25 | 2014-09-25 12:36 | 2014-09-25 13:13 | CARRIER - 38TDB060--311 | 218 | 6.9 | Yes | Yes | 19.4 | 20.4 | -1 | F1A2389EF0B644B2A8AD2810451BF064 |  | R410A | Non-TXV |  | 3.165% | 0.96835 | 6.083% | [5 empty] | Non-TXV | 3.165%
Antioch | CA | 94509-5142 |  | 2014-11-03 | 2014-11-03 15:04 | 2014-11-03 15:04 | DAY & NIGHT - N2A34BAKA400 | 118 | 0 | Yes | Yes | 17.5 | 19.9 | -2.4 | 98CC4785D9D44515A68F078DFAE59082 |  | R22 | TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5852 |  | 2014-10-06 | 2014-10-06 13:42 | 2014-10-06 13:59 | CARRIER - H2RAO36S06E | 100 | 6.2 | Yes | Yes | 20.7 | 18.8 | 1.9 | 260481A6756F47B88431C69C3741EC2B |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Vacaville | CA | 95687-6931 |  | 2014-11-11 | 2014-11-11 12:33 | 2014-11-11 13:09 | GE - AC036X1021A | 63 | 5 | Yes | Yes | 21.3 | 19.9 | 1.4 | 9C1029A37BF14B0A85506EF58B114A8C |  | R22 | Non-TXV |  | 7.937% | 0.92063 | 15.25% | [5 empty] | Non-TXV | 7.937%
Bakersfield | CA | 93312-4970 |  | 2014-10-17 | 2014-10-17 23:48 | 2014-10-18 00:05 | OTHER - UNK | 85 | 10 | Yes | Yes | 20 | 22 | -2 | AFF1773CFDC54F48BC16848076071066 |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Bakersfield | CA | 93313-9811 |  | 2014-10-06 | 2014-10-06 16:23 | 2014-10-06 16:41 | OTHER - H2RC036S06HG | 83 | 5 | Yes | Yes | 22.7 | 24 | -1.3 | 44E085B79A4A4F55A4136488A611D20B |  | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Vacaville | CA | 95687-7314 |  | 2014-09-26 | 2014-09-26 12:11 | 2014-09-26 18:34 | CARRIER - 38EH048320629 | 138 | 4.1 | Yes | Yes | 22.3 | 20.7 | 1.6 | EB362EF5A25749A08001AADE7EE88B9D |  | R22 | Non-TXV |  | 2.971% | 0.97029 | 5.71% | [5 empty] | Non-TXV | 2.971%
Bakersfield | CA | 93313-4299 |  | 2014-09-26 | 2014-09-26 13:57 | 2014-09-26 13:57 | ICP - CA9042VKD2 | 128 | 0 | Yes | Yes | 18 | 20.5 | -2.5 | 4D43290B0F55474DA178415E5A6DACBD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5085 |  | 2014-09-30 | 2014-09-30 11:18 | 2014-09-30 11:18 | OTHER - 561CJO36-D | 84 | 0 | Yes | Yes | 24 | 20.4 | 3.6 | 45749BE203B6494AB88E3186E2C8CFAD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9811 |  | 2014-10-19 | 2014-10-19 16:58 | 2014-10-19 17:00 | YORK - H2R048S06HG | 119 | 4.4 | Yes | Yes | 22.5 | 21 | 1.5 | FA7FF9EEC0D34BD9AE01EBDABE01319C |  | R22 | Non-TXV |  | 3.697% | 0.96303 | 7.106% | [5 empty] | Non-TXV | 3.697%
Bakersfield | CA | 93312-4921 |  | 2014-10-02 | 2014-10-02 11:58 | 2014-10-02 11:58 | CARRIER - 38CK042300 | 93 | 0 | Yes | Yes | 22.5 | 22.1 | 0.4 | 066413BCD47D4E53BB681EB61D5B7C2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4299 |  | 2014-09-23 | 2014-09-23 12:08 | 2014-09-23 12:08 | ICP - CA9049VKD2 | 164 | 0 | Yes | Yes | 23 | 20.2 | 2.9 | 8EC3E0753B3B46A4AF82359A20143781 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6222 |  | 2014-10-02 | 2014-10-02 12:20 | 2014-10-02 12:20 | RUUD - VAMB-042JAZ | 96 | 0 | Yes | Yes | 24.5 | 20.4 | 4.1 | 23AAEA5E624B4C7F85572DAA5F79C40B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-9811 |  | 2014-10-06 | 2014-10-06 16:48 | 2014-10-06 17:06 | OTHER - H2RC048S06HG | 119 | 8.4 | Yes | Yes | 24.5 | 24.6 | -0.1 | 546CB8BE693A4F9FB63968AFB53788B7 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Bakersfield | CA | 93311-8802 |  | 2014-09-24 | 2014-09-24 12:13 | 2014-09-24 12:13 | ICP - N2A348AKA200 | 124 | 0 | Yes | Yes | 25 | 21.5 | 3.5 | DD55205A77F64E1F9C9B495B5E8E62A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4378 |  | 2014-10-23 | 2014-10-23 15:44 | 2014-10-23 15:44 | RHEEM - RAMA-042JBZ | 95 | 0 | Yes | Yes | 23.5 | 20.2 | 3.4 | D12424FE677A4E0185D5C2A832D5C04B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9438 |  | 2014-11-03 | 2014-11-03 13:15 | 2014-11-03 13:41 | NORDYNE - JS5BD-060K | 232 | 23.8 | Yes | Yes | 16.9 | 19.7 | -2.8 | 6DD59E6B016E4DB6975D813DD37FD7DF |  | R22 | Non-TXV |  | 10.26% | 0.89741 | 19.71% | [5 empty] | Non-TXV | 10.26%
Bakersfield | CA | 93304-6324 |  | 2014-09-30 | 2014-09-30 16:37 | 2014-09-30 16:37 | CARRIER - UNK | 116 | 0 | Yes | Yes | 22.7 | 20.9 | 1.8 | E353A7FFD2534A38A878257C3939D374 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4350 |  | 2014-09-24 | 2014-09-24 12:02 | 2014-09-24 13:57 | LENNOX - `13ACD-030-230 | 77 | 3.4 | Yes | Yes | 19.3 | 20.7 | -1.4 | 0CDACF72E9E54345BF3CB84C16BCC009 |  | R22 | Non-TXV |  | 4.416% | 0.95584 | 8.486% | [5 empty] | Non-TXV | 4.416%
Vacaville | CA | 95687-7320 |  | 2014-10-21 | 2014-10-21 12:04 | 2014-10-21 12:20 | CARRIER - 38TH048310 | 114 | 3.7 | Yes | Yes | 19.2 | 21.1 | -1.9 | BBDB7A7971154A329D7D222216708719 |  | R22 | Non-TXV |  | 3.246% | 0.96754 | 6.237% | [5 empty] | Non-TXV | 3.246%
Bakersfield | CA | 93312-3231 |  | 2014-09-25 | 2014-09-25 13:19 | 2014-09-25 13:19 | BDP - 588ANW04208ACAG | 83 | 0 | Yes | Yes | 20.5 | 20.1 | 0.4 | 151A7A9F5F2C42C2806829382B13A77E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6968 |  | 2014-11-04 | 2014-11-04 14:17 | 2014-11-04 14:38 | LENNOX - XC21-060-230-01 | 208 | -19.6 | Yes | Yes | 24.2 | 20.4 | 3.8 | 6B9F9E0357E146B1A90C267112C03B7B |  | R410A | Non-TXV |  | -9.423% | 1.0942 | 2.639% |  |  |  |  | Non-TXV |  |  | -9.423%
Woodland | CA | 95776-9333 |  | 2014-09-29 | 2014-09-29 10:31 | 2014-09-29 10:58 | CARRIER - 24APA536A310 | 163 | 5.9 | Yes | Yes | 19.6 | 20.4 | -0.8 | 982E2F6CE57440C395C1F0B4F4D04626 |  | R410A | TXV |  | 3.62% | 0.9638 | 6.956% | [5 empty] | TXV | 3.62%
Bakersfield | CA | 93304-4603 |  | 2014-10-21 | 2014-10-21 11:07 | 2014-10-21 11:07 | GOODMAN - GSC130481AF | 152 | 0 | Yes | Yes | 23 | 19.5 | 3.5 | 3D1D8749694E4979B044D96E80F3F16A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4316 |  | 2014-10-20 | 2014-10-20 13:36 | 2014-10-20 16:48 | AMANA - 3409E030- | 87 | 2.8 | Yes | Yes | 20.2 | 20.4 | -0.2 | 29B96459032F430980A61F76ADA01A18 |  | R22 | Non-TXV |  | 3.218% | 0.96782 | 6.185% | [5 empty] | Non-TXV | 3.218%
Bakersfield | CA | 93314-9630 |  | 2014-10-22 | 2014-10-22 09:23 | 2014-10-22 09:23 | OTHER - HAC260AKA5 | 182 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | 207DCA68555E4158A8396D4944F13B87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1764 |  | 2014-11-24 | 2014-11-24 12:11 | 2014-11-24 12:33 | LENNOX - 13ACC-048-230-02 | 158 | 30.9 | Yes | Yes | 20 | 15 | 5 | 543D9EB54260491A8D27FF3D1B2CF831 |  | R22 | Non-TXV |  | 19.56% | 0.80443 | 37.58% | [5 empty] | Non-TXV | 19.56%
Brentwood | CA | 94513-1764 |  | 2014-11-24 | 2014-11-24 12:41 | 2014-11-24 13:02 | LENNOX - 13ACC-030-230-02 | 106 | 12.5 | Yes | Yes | 17.2 | 16.3 | 0.9 | 2449C9673B1F4C418530E859ED2E9406 |  | R22 | Non-TXV |  | 11.79% | 0.88208 | 22.66% | [5 empty] | Non-TXV | 11.79%
Woodland | CA | 95695-4730 |  | 2014-10-01 | 2014-10-01 09:13 | 2014-10-01 11:59 | TRANE - 4YCY4036B1075AA | 118 | 8.6 | Yes | Yes | 21.4 | 20.4 | 1 | 8F33D09C303E4CF4B82B010858A83A27 |  | R410A | Non-TXV |  | 7.288% | 0.92712 | 14.01% | [5 empty] | Non-TXV | 7.288%
Bakersfield | CA | 93306-4007 |  | 2014-10-06 | 2014-10-06 11:55 | 2014-10-06 11:55 | UNITARY PRODUCTS GROUP - DNIP060N09006A(S)NOH6816803 | 140 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | AC9618187653480192D730E49C66BA69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6410 |  | 2014-10-21 | 2014-10-21 09:13 | 2014-10-21 09:13 | OTHER - UNK | 109 | 0 | Yes | Yes | 15.9 | 18.7 | -2.8 | 0202E4329DFB45178146514D16B47258 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3236 |  | 2014-10-11 | 2014-10-11 15:21 | 2014-10-11 15:55 | CARRIER - UNK | 100 | 15.8 | Yes | Yes | 17.8 | 20.7 | -2.9 | 766E6D9A033B444891E541B7C96E7FA3 |  | R22 | Non-TXV |  | 15.8% | 0.842 | 30.36% | [5 empty] | Non-TXV | 15.8%
Bakersfield | CA | 93312-6766 |  | 2014-10-02 | 2014-10-02 10:25 | 2014-10-02 10:25 | CARRIER - RAMC-E36JBZ | 93 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 75C5EA28582D4835B531E814E55876A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6766 |  | 2014-10-02 | 2014-10-02 10:28 | 2014-10-02 10:28 | - | 85 | 0 | Yes | Yes | 18.5 | 21 | -2.5 | EA28E7A1906B4167801FEFF1B5ACF7FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3253 |  | 2014-11-19 | 2014-11-19 16:34 | 2014-11-19 16:34 | AMERICAN STANDARD - 2YCC3030A1040AA | 88 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | E53DFC0FAEA24EBE84864313C20F5E95 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4558 |  | 2014-10-06 | 2014-10-06 15:19 | 2014-10-06 15:19 | DAY & NIGHT - UNK | 90 | 0 | Yes | Yes | 19 | 21.7 | -2.7 | FC49C6DDB34741C3B6349F2721FBBAF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4504 |  | 2014-10-08 | 2014-10-08 12:39 | 2014-10-08 12:39 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 18.5 | 18.8 | -0.3 | A8896FF501B34277914175C424DB459A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2538 |  | 2014-09-26 | 2014-09-26 18:04 | 2014-09-26 18:20 | CARRIER - 561CJ024 | 67 | 2.2 | Yes | Yes | 21.1 | 20.4 | 0.7 | 58712671B5504AA99F77424790C411CA |  | R22 | Non-TXV |  | 3.284% | 0.96716 | 6.31% | [5 empty] | Non-TXV | 3.284%
Pittsburg | CA | 94565-4718 |  | 2014-10-01 | 2014-10-01 08:33 | 2014-10-01 08:33 | TRANE - TTR030C1000A2 | 74 | 0 | Yes | Yes | 17.8 | 19.1 | -1.3 | 51C0A4D299214534A1C4E2E7981CB8DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7011 |  | 2014-10-06 | 2014-10-06 09:14 | 2014-10-06 09:14 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 20.4 | 18.3 | 2.1 | 3EFD43EF9D4F403F80D4BDE3EEE250B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4441 |  | 2014-10-20 | 2014-10-20 09:15 | 2014-10-20 09:15 | GOODMAN - GPG13600900M41BA | 144 | 0 | Yes | Yes | 19.5 | 17.5 | 2.1 | 6EE960BE32DE4195969417C24DBEF4F6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3082 |  | 2014-10-13 | 2014-10-13 18:08 | 2014-10-13 18:27 | YORK - D2NY036N05606A | 120 | 8.1 | Yes | Yes | 18.3 | 19.1 | -0.8 | 63159064B4C54C639C574243B67EF857 |  | R410A | Non-TXV |  | 6.75% | 0.9325 | 12.97% | [5 empty] | Non-TXV | 6.75%
Bakersfield | CA | 93306-7580 |  | 2014-11-03 | 2014-11-03 11:01 | 2014-11-03 11:01 | GOODMAN - GSC130481BA | 102 | 0 | Yes | Yes | 23.9 | 21.3 | 2.6 | FB299516977B4C1E89C2721887285D8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5980 |  | 2014-10-21 | 2014-10-21 15:10 | 2014-10-21 15:10 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 22.7 | 20.4 | 2.3 | 5F3C440EAB734FE587EC830E0648AEC4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-9684 |  | 2014-09-25 | 2014-09-25 12:06 | 2014-09-25 12:06 | GOODMAN - GSC130361GB | 77 | 0 | Yes | Yes | 26.6 | 21 | 5.6 | 77F719E500024E2B9D577B030228ACDA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2632 |  | 2014-10-02 | 2014-10-02 15:12 | 2014-10-02 15:12 | OTHER - 38CK030300 | 79 | 0 | Yes | Yes | 22.2 | 22.8 | -0.6 | 649C5ECFE5104555B1F02E3D44D64C4C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1707 |  | 2014-10-16 | 2014-10-16 15:15 | 2014-10-16 15:15 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | BA256798DB184C769E7A0A694496F8E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2123 |  | 2014-10-11 | 2014-10-11 16:45 | 2014-10-11 16:45 | DAY & NIGHT - 568EJX048000ACAA | 178 | 0 | Yes | Yes | 20.1 | 19.3 | 0.8 | DD787A831B124AAD92970248EA69E872 | Final Suction Temperature must be between 20°F and 80°F. Please check entries. Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Liquid Temperature cannot be less than outdoor air temperature. Check entries and calibration. Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3705 |  | 2014-10-21 | 2014-10-21 10:34 | 2014-10-21 10:34 | ICP - PGAA48D1K1 | 124 | 0 | Yes | Yes | 19.5 | 19.1 | 0.4 | CFD31E99C1174DA4B4A8B00968EE80AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3883 |  | 2014-10-24 | 2014-10-24 14:31 | 2014-10-24 14:31 | CONCORD - CCU10A18A-2 | 60 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | 93701CAEF6B6453689B0EF727F5D3120 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2839 |  | 2014-10-08 | 2014-10-08 11:50 | 2014-10-08 11:50 | OTHER - PA10JA060000AGAA | 118 | 0 | Yes | Yes | 19.1 | 20.7 | -1.6 | A6586CE6143B4A73BB426CC44D5D0931 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2828 |  | 2014-10-16 | 2014-10-16 12:48 | 2014-10-16 12:48 | RHEEM - RRPLB030JK06X | 76 | 0 | Yes | Yes | 17 | 18.8 | -1.8 | 246A237351CA4C7898A85AF6290DCF55 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-1939 |  | 2014-10-13 | 2014-10-13 16:53 | 2014-10-13 16:53 | OTHER - AC060X1221A | 147 | 0 | Yes | Yes | 26.8 | 21.2 | 5.6 | 58AD409F9765483B923E311C38524D45 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4775 |  | 2014-09-30 | 2014-09-30 09:39 | 2014-09-30 09:39 | AMERICAN STANDARD - 2A7B3030A1000AA | 88 | 0 | Yes | Yes | 19.4 | 18.2 | 1.2 | A17F2420BFAB4F6188F210E32E8AF0D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6113 |  | 2014-10-07 | 2014-10-07 16:14 | 2014-10-07 16:14 | YORK - DDUC-F036N100A | 96 | 0 | Yes | Yes | 30.2 | 24.2 | 6 | 1AEF5FCBBB034BEC87EB8CC8CF95D33C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6489 |  | 2014-10-14 | 2014-10-14 16:29 | 2014-10-14 16:48 | CARRIER - 38BRC036340 | 101 | 4.1 | Yes | Yes | 19.5 | 21.1 | -1.6 | 45002A9901014312A91D7AE41F887639 |  | R22 | Non-TXV |  | 4.059% | 0.95941 | 7.801% | [5 empty] | Non-TXV | 4.059%
Bakersfield | CA | 93312-3410 |  | 2014-09-25 | 2014-09-25 13:46 | 2014-09-25 13:46 | YORK - D1NH042N06506C | 94 | 0 | Yes | Yes | 25.2 | 19.3 | 5.9 | 7CD25C59EC534338B12DF604718CC95B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4331 |  | 2014-10-13 | 2014-10-13 15:15 | 2014-10-13 15:31 | RHEEM - UNK | 100 | 9.1 | Yes | Yes | 18 | 20.4 | -2.4 | 057506C816904E63B47615F723F81EB8 |  | R22 | Non-TXV |  | 9.1% | 0.909 | 17.49% | [5 empty] | Non-TXV | 9.1%
Bakersfield | CA | 93307-5620 |  | 2014-10-07 | 2014-10-07 11:42 | 2014-10-07 11:42 | DAY & NIGHT - UKN | 85 | 0 | Yes | Yes | 27.3 | 21.5 | 5.8 | 9E02D9C607EC4AF08F484FEBD0DB6359 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7327 |  | 2014-10-07 | 2014-10-07 13:12 | 2014-10-07 13:12 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 25.7 | 21.8 | 3.9 | D2C37223CDC14DC48A6022F07EAEB1BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-3219 |  | 2014-10-11 | 2014-10-11 15:59 | 2014-10-11 16:17 | GOODMAN - VSX130481BA | 85 | 2.7 | Yes | Yes | 18.1 | 21.1 | -3 | DF01047D01704B5F8701DE9D06197386 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Fairfield | CA | 94533-1659 |  | 2014-09-25 | 2014-09-25 13:25 | 2014-09-25 16:07 | CONCORD - SCU10G36A | 80 | 4.3 | Yes | Yes | 21.4 | 20.4 | 1 | A32277A102EF44D58399079F2BE95FB1 |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
San Jose | CA | 95112-1652 |  | 2014-09-29 | 2014-09-29 09:45 | 2014-09-29 09:54 | OTHER - CK49-1B | 97 | 10.3 | Yes | Yes | 20.9 | 18.8 | 2.1 | 3C3BE6F80AD5485FAAB04324EDAAE483 |  | R22 | Non-TXV |  | 10.62% | 0.89381 | 20.41% | [5 empty] | Non-TXV | 10.62%
Bakersfield | CA | 93309-4596 |  | 2014-09-30 | 2014-09-30 12:50 | 2014-09-30 12:50 | UNITARY PRODUCTS GROUP - D1NA024N03606C | 64 | 0 | Yes | Yes | 25.9 | 20.4 | 5.5 | 02E7C990C279435E9A651F9F3FA8A6C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6752 |  | 2014-10-14 | 2014-10-14 15:07 | 2014-10-14 15:07 | OTHER - 38CKC048360 | 109 | 0 | Yes | Yes | 13.7 | 18.6 | -4.9 | FC8B2F2E54F2409E972BF766A2E15A1E | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4168 |  | 2014-10-04 | 2014-10-04 20:19 | 2014-10-04 20:21 | DAY & NIGHT - N/A | 110 | 5.5 | Yes | Yes | 22.6 | 22.1 | 0.5 | D9290E308ADC4E5AB7D251CFC87B854F |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93308-3419 |  | 2014-10-10 | 2014-10-10 14:32 | 2014-10-10 14:49 | DAY & NIGHT - F048N080A | 132 | 11.5 | Yes | Yes | 26.9 | 21 | 5.9 | BD9A836CF38C4EF58187A85D32106C89 |  | R22 | Non-TXV |  | 8.712% | 0.91288 | 16.74% | [5 empty] | Non-TXV | 8.712%
Bakersfield | CA | 93306-2647 |  | 2014-11-10 | 2014-11-10 20:22 | 2014-11-10 20:42 | - D1NH048N09006C | 128 | 3.9 | Yes | Yes | 19.4 | 17.7 | 1.7 | 071B1433428D49469F14A0DAF77C2056 |  | R22 | Non-TXV |  | 3.047% | 0.96953 | 5.855% | [5 empty] | Non-TXV | 3.047%
Bakersfield | CA | 93304-1935 |  | 2014-10-08 | 2014-10-08 09:26 | 2014-10-08 09:26 | CARRIER - CNRVT6024ACAABA | 178 | 0 | Yes | Yes | 17.3 | 19.1 | -1.8 | C6B0DEE139254AC685838E22716DEA2E |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9744 |  | 2014-11-12 | 2014-11-12 14:57 | 2014-11-12 14:57 | LENNOX - UNK | 147 | 0 | Yes | Yes | 18.7 | 19.1 | -0.4 | 010E377C30624AFEB803CE8159190FDD |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2634 |  | 2014-11-13 | 2014-11-13 12:36 | 2014-11-13 12:36 | GOODMAN - GSC130301EB | 66 | 0 | Yes | Yes | 14.1 | 16.5 | -2.4 | DA7DFA86F62B436D97EE230AD15D3729 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4971 |  | 2014-10-08 | 2014-10-08 14:29 | 2014-10-08 14:29 | GOODMAN - GSX130481BB | 104 | 0 | Yes | Yes | 28.2 | 22.3 | 6 | C373A4E6E5894437B991A6311A714710 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6965 |  | 2014-10-02 | 2014-10-02 08:42 | 2014-10-02 09:02 | PAYNE - 591ANX0600000AAAA | 170 | 16.6 | Yes | Yes | 16.7 | 15.9 | 0.8 | 2218D9F59EE043D881F9DC6258C9BFF4 |  | R22 | Non-TXV |  | 9.765% | 0.90235 | 18.77% | [5 empty] | Non-TXV | 9.765%
Bakersfield | CA | 93304-1723 |  | 2014-10-23 | 2014-10-23 12:36 | 2014-10-23 12:36 | DAY & NIGHT - 2460YAC108TC | 54 | 0 | Yes | Yes | 23.1 | 19.3 | 3.8 | E8E629F6A936413FADDDA18F9AA03D39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3718 |  | 2014-11-11 | 2014-11-11 17:02 | 2014-11-11 17:02 | OTHER - UNK | 121 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | B356F81C2A824835964EA18365E5738D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2304 |  | 2014-11-05 | 2014-11-05 15:19 | 2014-11-05 15:19 | BRYANT - 563CN036-A | 114 | 0 | Yes | Yes | 20.1 | 19.5 | 0.6 | E9A65F8DD96C48CE97359B57234B205F |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3770 |  | 2014-10-09 | 2014-10-09 15:31 | 2014-10-09 15:31 | OTHER - SRM5182 | 56 | 4.3 | Yes | Yes | 22.9 | 24.8 | -1.9 | 640CB61B8A284435AE9795C948BB9462 | Add refrigerant: 4.3 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.679% | 0.92321 | 14.76% | [5 empty] | Non-TXV | 7.679%
Bakersfield | CA | 93305-3770 |  | 2014-10-09 | 2014-10-09 16:01 | 2014-10-09 16:34 | OTHER - UNK | 56 | -4.6 | Yes | Yes | 22.8 | 19.6 | 3.2 | 8DA1946DB09242A6B834DE861761F7A0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -8.214% | 1.0821 | 2.3% |  |  |  |  | Non-TXV |  |  | -8.214%
Bakersfield | CA | 93305-3770 |  | 2014-10-09 | 2014-10-09 16:37 | 2014-10-09 16:37 | GOODMAN - GPG1324045M41BA | 68 | 0 | Yes | Yes | 26.4 | 21 | 5.4 | 9BFA355C1C744B73AA1472337CD981A9 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7834 |  | 2014-10-13 | 2014-10-13 09:38 | 2014-10-13 10:06 | PAYNE - 563AW042-A | 132 | 6 | Yes | Yes | 20.9 | 20.4 | 0.5 | 0D8B0A1FE8674A75A186FB929479348D |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Bakersfield | CA | 93306-4785 |  | 2014-10-06 | 2014-10-06 11:17 | 2014-10-06 11:17 | UNITARY PRODUCTS GROUP - DNPG24N03606NXA | 100 | 0 | Yes | Yes | 20 | 21 | -1 | 7D41E92F2C0B48A7A3F0F891ACA21D67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-5053 |  | 2014-11-19 | 2014-11-19 15:18 | 2014-11-19 15:18 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 20.6 | 20.4 | 0.2 | 2284C567430742FE88A91051EB7E85D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2210 |  | 2014-10-07 | 2014-10-07 11:26 | 2014-10-09 06:46 | TRANE - TTN036C100B3 | 117 | 8.1 | Yes | Yes | 14.4 | 15.7 | -1.3 | 1C9B1ED321234D76B46DB6E1098DF591 |  | R22 | Non-TXV |  | 6.923% | 0.93077 | 13.3% | [5 empty] | Non-TXV | 6.923%
Bakersfield | CA | 93309-5945 |  | 2014-10-07 | 2014-10-07 10:46 | 2014-10-07 11:05 | YORK - DAYPF036N070A | 108 | 17.9 | Yes | Yes | 20 | 19.9 | 0.1 | 3AFA985137844E8DBBFCB0EBEAC439C6 |  | R22 | Non-TXV |  | 16.57% | 0.83426 | 31.85% | [5 empty] | Non-TXV | 16.57%
Fairfield | CA | 94534-3311 |  | 2014-11-17 | 2014-11-17 10:06 | 2014-11-17 11:10 | ARMSTRONG - RCE48A2A | 150 | 5.9 | Yes | Yes | 18.4 | 20.9 | -2.5 | 01F22D1F72F14AEB9C4350551A8019DC |  | R22 | Non-TXV |  | 3.933% | 0.96067 | 7.559% | [5 empty] | Non-TXV | 3.933%
Bakersfield | CA | 93307-7270 |  | 2014-10-07 | 2014-10-07 13:35 | 2014-10-07 13:35 | DUCANE - SG10B36075 | 82 | 0 | Yes | Yes | 21.1 | 21.4 | -0.3 | 128DAB3B0BD94F9EB1FC1EB8E4B1BFDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8424 |  | 2014-10-21 | 2014-10-21 09:51 | 2014-10-21 09:51 | CARRIER - 38CKC060370 | 85 | 0 | Yes | Yes | 21.5 | 19.7 | 1.9 | A7B1FCAD7840434CB1119362DE8AB143 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4153 |  | 2014-10-06 | 2014-10-06 11:41 | 2014-10-06 11:41 | OTHER - 80AW36106 | 106 | 0 | Yes | Yes | 18.5 | 21.5 | -3 | 1630DDF692784D1EA463E0BCE7A1FB38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7725 |  | 2014-11-05 | 2014-11-05 13:38 | 2014-11-05 13:38 | DAY & NIGHT - 591AN048C | 121 | 0 | Yes | Yes | 17.7 | 19.4 | -1.7 | 09AB214B4D8F465D96CADD4AD135E6F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7498 |  | 2014-11-05 | 2014-11-05 14:30 | 2014-11-05 14:30 | BRYANT - BRCS0601BD | 118 | 0 | Yes | Yes | 22.3 | 20.4 | 1.9 | FC549F278F5F4007B2DAE7925148B7E1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5007 |  | 2014-10-08 | 2014-10-08 10:03 | 2014-10-08 10:52 | TRANE - TTP030C100B1 | 151 | 6.7 | Yes | Yes | 21.3 | 21.4 | -0.1 | 3D2A58945D544C3AB3DFFF99F03F9710 |  | R22 | Non-TXV |  | 4.437% | 0.95563 | 8.527% | [5 empty] | Non-TXV | 4.437%
Bakersfield | CA | 93306-3458 |  | 2014-10-29 | 2014-10-29 16:13 | 2014-10-29 16:13 | UNITARY PRODUCTS GROUP - DDYZ-F048N080C | 68 | 0 | Yes | Yes | 24 | 21.3 | 2.8 | 7C3EAD927EE9480FAF812B4347ECD079 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2806 |  | 2014-10-08 | 2014-10-08 11:39 | 2014-10-08 12:29 | CARRIER - 38BRC60360 | 199 | 6.7 | Yes | Yes | 20.7 | 20.4 | 0.3 | D91322DC5BD0499595DF807A9C90F9DE |  | R22 | Non-TXV |  | 3.367% | 0.96633 | 6.47% | [5 empty] | Non-TXV | 3.367%
Bakersfield | CA | 93311-1409 |  | 2014-10-02 | 2014-10-02 11:18 | 2014-10-02 11:44 | BRYANT - 583ANW042060NAAF | 118 | 18.7 | Yes | Yes | 20 | 20.4 | -0.4 | E28CC29B0EEB453FAAA4D9A79E360A29 |  | R22 | Non-TXV |  | 15.85% | 0.84153 | 30.46% | [5 empty] | Non-TXV | 15.85%
Bakersfield | CA | 93312-2717 |  | 2014-11-11 | 2014-11-11 18:10 | 2014-11-11 18:12 | TEMPSTAR - PGAA47D1K1 | 129 | 4.2 | Yes | Yes | 18.9 | 17.5 | 1.5 | 85799FDC30B3423C91C02CFCD5D8027C |  | R22 | Non-TXV |  | 3.256% | 0.96744 | 6.257% | [5 empty] | Non-TXV | 3.256%
Bakersfield | CA | 93305-3931 |  | 2014-10-09 | 2014-10-09 12:18 | 2014-10-09 12:18 | PAYNE - PY2NB024040ABAA | 55 | 0 | Yes | Yes | 24.3 | 19.8 | 4.5 | 68E3C501061D4C919B7AA5EA94EE1621 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5232 |  | 2014-10-07 | 2014-10-07 10:06 | 2014-10-09 06:43 | - | 85 | 3.7 | Yes | Yes | 14.1 | 15.5 | -1.4 | 8E98819DF1E44AA7826674FF65F8B5F5 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Antioch | CA | 94531-8124 |  | 2014-11-06 | 2014-11-06 12:18 | 2014-11-06 12:42 | CARRIER - 38TH060300 | 170 | 27.9 | Yes | Yes | 19.5 | 20 | -0.4 | AF2626B11E214DA1A48A61BB6F852514 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 16.41% | 0.83588 | 31.54% | [5 empty] | Non-TXV | 16.41%
Antioch | CA | 94509-7342 |  | 2014-11-06 | 2014-11-06 13:26 | 2014-11-06 13:45 | CARRIER - 38EH030340 | 126 | 12.4 | Yes | Yes | 22.1 | 20.7 | 1.4 | C828BCD4080946458D3006F794139A49 |  | R22 | Non-TXV |  | 9.841% | 0.90159 | 18.91% | [5 empty] | Non-TXV | 9.841%
Antioch | CA | 94509-8935 |  | 2014-11-06 | 2014-11-06 14:15 | 2014-11-06 14:33 | BRYANT - 561CJ060-A | 136 | 17.8 | Yes | Yes | 23.3 | 19.9 | 3.4 | 3F8632F5123549969649CFCBE70B6113 |  | R22 | TXV |  | 13.09% | 0.86912 | 25.15% | [5 empty] | TXV | 13.09%
Vallejo | CA | 94590-3549 |  | 2014-10-06 | 2014-10-06 10:56 | 2014-10-06 13:51 | COOLERADO - N4A336AKB200 | 83 | 5.6 | Yes | Yes | 20.2 | 19.9 | 0.3 | 7A5847CA44064095A957DE7C97AB3220 |  | R410A | Non-TXV |  | 6.747% | 0.93253 | 12.97% | [5 empty] | Non-TXV | 6.747%
Fairfield | CA | 94533-8900 |  | 2014-10-07 | 2014-10-07 10:05 | 2014-10-09 06:44 | CARRIER - 38BRC030320 | 100 | 6.2 | Yes | Yes | 11.9 | 14.4 | -2.5 | 3139AEAC39F34F45A599CC64E9D6FB0F |  | R22 | Non-TXV |  | 6.2% | 0.938 | 11.92% | [5 empty] | Non-TXV | 6.2%
Wasco | CA | 93280-2747 |  | 2014-11-07 | 2014-11-07 19:16 | 2014-11-07 19:16 | OTHER - UNK | 102 | 0 | Yes | Yes | 19.1 | 19.1 | 0 | BC0AE999BE6948FB9D73E0583DF7F4D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7618 |  | 2014-11-06 | 2014-11-06 15:29 | 2014-11-06 15:29 | BRYANT - 113ANA042-B | 100 | 0 | Yes | Yes | 18 | 20.7 | -2.7 | CE0484FDFE40482EA651A0B895C1F602 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8370 |  | 2014-10-20 | 2014-10-20 10:34 | 2014-10-20 11:03 | CARRIER - 38CKC048300 | 102 | 3.1 | Yes | Yes | 21.2 | 19.9 | 1.3 | 644773935E2941B180BE78D72E38EDB7 |  | R22 | Non-TXV |  | 3.039% | 0.96961 | 5.841% | [5 empty] | Non-TXV | 3.039%
Bakersfield | CA | 93313-4349 |  | 2014-11-11 | 2014-11-11 11:30 | 2014-11-11 11:30 | YORK - H4DH060S06A | 125 | 0 | Yes | Yes | 16.8 | 18.2 | -1.4 | 52F3BA86F40F468C920C70FC1DF35D15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5287 |  | 2014-10-06 | 2014-10-06 15:45 | 2014-10-06 15:45 | OTHER - 2AC13L36P | 128 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | C132D335C2B74B719A07634CC989932E | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5287 |  | 2014-10-06 | 2014-10-06 16:16 | 2014-10-06 16:16 | - | 85 | 0 | Yes | Yes | 28.7 | 22.8 | 5.9 | 0C2112213C6949CF984959DBF4EA353E |  |  |  |  | 0% | 1 | 0%
Vacaville | CA | 95687-6778 |  | 2014-10-21 | 2014-10-21 11:16 | 2014-10-21 11:38 | CARRIER - 561CJ042- | 80 | 3 | Yes | Yes | 20.6 | 20.4 | 0.2 | A9627875FD4443FCA563906AF18FA777 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Bakersfield | CA | 93306-6277 |  | 2014-10-28 | 2014-10-28 13:26 | 2014-10-28 13:26 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 24.6 | 20.4 | 4.2 | 086F25CA079241FCBDB11E6206D88B70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1140 |  | 2014-10-07 | 2014-10-07 10:45 | 2014-10-09 06:45 | PAYNE - PA10JA03000AAA | 78 | 6.1 | Yes | Yes | 14.3 | 16.6 | -2.3 | 754F88071B874162B5FEB4A963AAA5B4 |  | R22 | Non-TXV |  | 7.821% | 0.92179 | 15.03% | [5 empty] | Non-TXV | 7.821%
Bakersfield | CA | 93309-4462 |  | 2014-11-19 | 2014-11-19 10:55 | 2014-11-19 10:55 | OTHER - PGAA30C1K6 | 79 | 0 | Yes | Yes | 26.2 | 20.7 | 5.5 | 144EFF256BA0414496AC8131D7518510 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4529 |  | 2014-11-07 | 2014-11-07 11:11 | 2014-11-07 11:38 | LENNOX - 10ACC-042-230-02 | 83 | 9.3 | Yes | Yes | 16.7 | 18.2 | -1.5 | AC6C4F7E2596467E8F72D795E7C5A862 |  | R22 | Non-TXV |  | 11.2% | 0.88795 | 21.53% | [5 empty] | Non-TXV | 11.2%
Bakersfield | CA | 93306-2650 |  | 2014-10-06 | 2014-10-06 15:03 | 2014-10-06 15:03 | UNITARY PRODUCTS GROUP - D1NHO42N06506A | 90 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 5D034308F8954CCEA48A4A1712F0BE55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5203 |  | 2014-11-18 | 2014-11-18 11:52 | 2014-11-18 12:17 | RHEEM - | 93 | 3 | Yes | Yes | 17.7 | 20.4 | -2.7 | 779BDBFCA87A4141965FF4FB9F81635E |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Bakersfield | CA | 93313-3069 |  | 2014-10-17 | 2014-10-17 15:17 | 2014-10-17 15:17 | DAY & NIGHT - UNK | 102 | 0 | Yes | Yes | 15.4 | 19.5 | -4.1 | 79D5004753684B41B94D2EF36B90C919 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93301-1613 |  | 2014-10-15 | 2014-10-15 10:10 | 2014-10-15 10:10 | TEMPSTAR - GPCM24K040F | 54 | 0 | Yes | Yes | 24.6 | 18.7 | 5.9 | 48D53C6B9F0C42188A775D09CAC7A47A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5156 |  | 2014-10-07 | 2014-10-07 11:00 | 2014-10-07 11:00 | UNITARY PRODUCTS GROUP - DAYA-F048N080C | 85 | 0 | Yes | Yes | 27.6 | 22 | 5.6 | EA68ED4315D24AFDB6D1183E2C4138AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5132 |  | 2014-10-21 | 2014-10-21 14:43 | 2014-10-21 14:43 | DAY & NIGHT - UKN | 90 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | FA1ADD09B2CE4383BCB9C123AE57A775 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8056 |  | 2014-10-06 | 2014-10-06 10:25 | 2014-10-07 07:25 | TRANE - BTD730A100B | 74 | -7 | Yes | Yes | 14.4 | 15.3 | -0.8 | 9D1710D4D58040BFAC3CC5C43191BBDB |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Bakersfield | CA | 93301-2516 |  | 2014-10-15 | 2014-10-15 18:19 | 2014-10-15 18:39 | YORK - D1NH024N03666 | 70 | 3.4 | Yes | Yes | 19.4 | 20.4 | -1 | 020F6E87990E45A988C9C6762AA8843F |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Fairfield | CA | 94533-4164 |  | 2014-10-16 | 2014-10-16 12:33 | 2014-10-17 08:35 | LENNOX - LCS13DC-024-230-01 | 85 | 3.1 | Yes | Yes | 14.2 | 15.7 | -1.5 | C522A93B54424D5F94FC4E57705BF0E4 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Fairfield | CA | 94533-2516 |  | 2014-10-16 | 2014-10-16 12:58 | 2014-10-17 08:36 | YORK - YCJF30S41S1A | 55 | -5.2 | Yes | Yes | 14.5 | 16.6 | -2.1 | 6AD24897F31E4AABAEA3520EFAF2002D |  | R22 | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Bakersfield | CA | 93304-3645 |  | 2014-10-08 | 2014-10-08 10:43 | 2014-10-08 10:43 | YORK - H4D060S06A | 125 | 0 | Yes | Yes | 18.1 | 20.1 | -2 | 50C8A29EE27F40C188BB05CF0DA27B71 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7152 |  | 2014-11-12 | 2014-11-12 10:06 | 2014-11-12 10:24 | YORK - UNK | 85 | 12 | Yes | Yes | 17.3 | 18.2 | -0.9 | BDDE271682214F77AE8DD28D11BA68BB |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Bakersfield | CA | 93313-5531 |  | 2014-10-21 | 2014-10-21 12:23 | 2014-10-21 12:23 | RHEEM - RAMB060JBZ | 192 | 0 | Yes | Yes | 15.7 | 18.7 | -3 | 0EDB326EBD2942E9A7EC500B2CBB8994 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5048 |  | 2014-10-07 | 2014-10-07 17:12 | 2014-10-07 17:31 | TRANE - 2TTR2048A1000AA | 120 | 9.1 | Yes | Yes | 14.6 | 16.2 | -1.6 | EA19C5ADFFE14DC19105BE1EC174D945 |  | R22 | Non-TXV |  | 7.583% | 0.92417 | 14.57% | [5 empty] | Non-TXV | 7.583%
Wasco | CA | 93280-3302 |  | 2014-11-04 | 2014-11-04 12:07 | 2014-11-04 12:07 | BRYANT - UNK | 56 | 0 | Yes | Yes | 14.4 | 17.2 | -2.8 | F277F1CCBA28412CAA43467FD8C1A68B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5723 |  | 2014-10-27 | 2014-10-27 13:59 | 2014-10-27 13:59 | NORDYNE - JS3BD-030K | 114 | 0 | Yes | Yes | 22.1 | 20.4 | 1.7 | DDC5D504094544069AD82980037ED4AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5736 |  | 2014-10-27 | 2014-10-27 16:43 | 2014-10-27 16:43 | NORDYNE - JS5BD-030KA | 99 | 0 | Yes | Yes | 22.9 | 21 | 1.9 | 3FE50D2425DA44119FC16707C6DF7B19 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3412 |  | 2014-11-18 | 2014-11-18 11:27 | 2014-11-18 11:27 | CARRIER - 38CKC03640 | 72 | 0 | Yes | Yes | 13.8 | 13.4 | 0.4 | F96F92AAF7F548E99C26CC0746E213F5 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5736 |  | 2014-10-27 | 2014-10-27 17:59 | 2014-10-27 17:59 | NORDYNE - JS5BD-030KA | 99 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 534686AFFE9C48EE8C01CAA3EBAC021E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3003 |  | 2014-10-03 | 2014-10-03 09:49 | 2014-10-03 09:49 | NORDYNE - | 85 | 0 | Yes | Yes | 14.1 | 16.6 | -2.5 | 76925A9CE58B4EF78C34B8C2892CBC44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4153 |  | 2014-10-20 | 2014-10-20 09:47 | 2014-10-20 09:47 | TRANE - YCP042FLMOAC | 128 | 0 | Yes | Yes | 23.4 | 18.3 | 5.1 | DD0F384A248D4F958C0606C4DA82DB70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3946 |  | 2014-10-09 | 2014-10-09 17:36 | 2014-10-09 17:36 | OTHER - WPG3244040LKC1 | 72 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | E2F17D9EC44D4D32AB83D436D811F1D6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1871 |  | 2014-10-03 | 2014-10-03 13:52 | 2014-10-03 13:52 | YORK - UNK | 63 | 0 | Yes | Yes | 19.9 | 21.8 | -1.9 | 8DCF6A8BD69B4E20835D2B1DF629D135 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1228 |  | 2014-10-09 | 2014-10-09 13:07 | 2014-10-09 13:55 | OTHER - UNK | 113 | 13 | Yes | Yes | 27.5 | 21.9 | 5.6 | A4F6C6730A0C4D1F9915E905768A1771 |  | R22 | Non-TXV |  | 11.5% | 0.88496 | 22.11% | [5 empty] | Non-TXV | 11.5%
Vallejo | CA | 94591-8613 |  | 2014-10-07 | 2014-10-07 09:37 | 2014-10-07 10:15 | BDP - 5410J018 | 83 | 5 | Yes | Yes | 19.4 | 20.4 | -1 | 491C3FB9CF4C495BB37F31E6387432D1 |  | R22 | Non-TXV |  | 6.024% | 0.93976 | 11.58% | [5 empty] | Non-TXV | 6.024%
Bakersfield | CA | 93307-3966 |  | 2014-10-12 | 2014-10-12 17:15 | 2014-10-12 17:15 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 20.9 | 21.3 | -0.4 | D0AE0D97CCB04896A6C45D3253286F8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8412 |  | 2014-11-10 | 2014-11-10 10:43 | 2014-11-10 11:04 | PAYNE - 591AN036-A | 81 | 5.6 | Yes | Yes | 21.2 | 17 | 4.2 | 7F989CF8496242B2A3E386833E821F29 |  | R22 | Non-TXV |  | 6.914% | 0.93086 | 13.29% | [5 empty] | Non-TXV | 6.914%
Arvin | CA | 93203-9746 |  | 2014-11-07 | 2014-11-07 13:46 | 2014-11-07 14:03 | RHEEM - UNK | 85 | -8 | Yes | Yes | 20.1 | 21.8 | -1.7 | 5AE054E23CD447ABBBD610A7827B1028 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Antioch | CA | 94531-9346 |  | 2014-11-07 | 2014-11-07 12:39 | 2014-11-07 12:39 | YORK - H2RA036306D | 63 | 0 | Yes | Yes | 18 | 19.1 | -1.1 | 6BD9266A48A945B9988C853BC40B5668 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-1158 |  | 2014-10-31 | 2014-10-31 10:37 | 2014-10-31 10:37 | YORK - DCYPF024N045A | 100 | 0 | Yes | Yes | 18.6 | 19.1 | -0.5 | 0D2DC1902B6B4A068FA01C5AC2F1E80A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Wasco | CA | 93280-2518 |  | 2014-10-30 | 2014-10-30 11:25 | 2014-10-30 11:25 | HEIL - PGME48G080E | 160 | 0 | Yes | Yes | 17.3 | 19.8 | -2.5 | 3EA1C001377E4B1EAA22A0474FBD2557 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3963 |  | 2014-10-12 | 2014-10-12 15:58 | 2014-10-12 15:58 | DUCANE - 2AC13B30P1A | 129 | 0 | Yes | Yes | 20.2 | 21.4 | -1.2 | C05AE47C733B417097B798D37BC0F5B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3965 |  | 2014-10-12 | 2014-10-12 16:50 | 2014-10-12 16:50 | DUCANE - 2AC13B24P1A | 89 | 0 | Yes | Yes | 21.7 | 20.7 | 1 | 33FD8EDF1FD744479150726C03FFD55B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3895 |  | 2014-10-13 | 2014-10-13 15:10 | 2014-10-13 15:10 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 21.5 | 21.5 | 0 | 7DECE222A79B4A7989849D84E2BD6CA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4916 |  | 2014-11-17 | 2014-11-17 13:03 | 2014-11-17 13:03 | RHEEM - RRMAA036JK06X | 99 | 0 | Yes | Yes | 20.6 | 20.1 | 0.5 | 566F8E925FC846A1A859BED88B3FAEFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6627 |  | 2014-10-21 | 2014-10-21 11:33 | 2014-10-21 11:33 | CARRIER - 48XPN03609311 | 145 | 0 | Yes | Yes | 22.5 | 20.2 | 2.4 | AF244E3A2575440BA5ED0337F5D1ED3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4257 |  | 2014-10-06 | 2014-10-06 11:00 | 2014-10-07 07:26 | AMERICAN STANDARD - 7A0042A100A0 | 100 | 5.1 | Yes | Yes | 14.4 | 16.6 | -2.2 | 6BF07C20ACF94105A75EF8D6B2A05A5C |  | R22 | Non-TXV |  | 5.1% | 0.949 | 9.801% | [5 empty] | Non-TXV | 5.1%
Antioch | CA | 94531-8410 |  | 2014-11-10 | 2014-11-10 14:50 | 2014-11-10 16:46 | CARRIER - 561AJ036-B | 73 | 5 | Yes | Yes | 18.3 | 20.4 | -2.1 | 8EAA0C57E9B0497F82BCA8942D6FAC97 |  | R22 | Non-TXV |  | 6.849% | 0.93151 | 13.16% | [5 empty] | Non-TXV | 6.849%
Bakersfield | CA | 93307-3969 |  | 2014-10-12 | 2014-10-12 18:15 | 2014-10-12 18:15 | DUCANE - 2AC13618P1A | 84 | 0 | Yes | Yes | 20.9 | 21.8 | -0.9 | A88B1F2A4EBB446B931079E70212F832 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5736 |  | 2014-10-27 | 2014-10-27 19:17 | 2014-10-27 19:17 | NORDYNE - JS5BD-030KA | 99 | 0 | Yes | Yes | 23.8 | 21 | 2.8 | 93700544067347B2BC8766D30CD4D338 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3969 |  | 2014-10-12 | 2014-10-12 18:18 | 2014-10-12 18:18 | DUCANE - 2AC13630P1A | 129 | 0 | Yes | Yes | 18.8 | 21 | -2.2 | 0B5F2B65697C4ECFB40349545588BA86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5737 |  | 2014-10-27 | 2014-10-27 19:23 | 2014-10-27 19:23 | NORDYNE - JS5BD-030KA | 99 | 0 | Yes | Yes | 22.5 | 21 | 1.5 | C54497DD297648A9A2E3D62FC436B3ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3969 |  | 2014-10-12 | 2014-10-12 18:20 | 2014-10-12 18:20 | DUCANE - 2AC13B24P1A | 89 | 0 | Yes | Yes | 21.3 | 21.1 | 0.2 | B5DC3EE832D8435EB0A4D69563835014 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3886 |  | 2014-10-24 | 2014-10-24 18:36 | 2014-10-24 18:36 | CONCORD - CCU10A18A-2 | 60 | 0 | Yes | Yes | 23.9 | 20.4 | 3.5 | BFFF3002BD4E4708A3133181C6A24ECE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6406 |  | 2014-10-23 | 2014-10-23 14:28 | 2014-10-23 14:28 | OTHER - 589ANW042080ACBF | 87 | 0 | Yes | Yes | 18.4 | 18.2 | 0.2 | B373EA9049C94645A1562049C759C69C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3963 |  | 2014-10-12 | 2014-10-12 16:01 | 2014-10-12 16:01 | DUCANE - 2AC13B24AP1A | 89 | 0 | Yes | Yes | 20.7 | 22 | -1.3 | C7BC554287974D998942FE9A96EEC812 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3969 |  | 2014-10-12 | 2014-10-12 18:10 | 2014-10-12 18:10 | DUCANE - 2AC13624P1A | 89 | 0 | Yes | Yes | 21.5 | 20.7 | 0.8 | 092221BA96044E26817519FA3AB1FEC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6460 |  | 2014-11-10 | 2014-11-10 12:10 | 2014-11-10 12:36 | YORK - H2RA036S06E | 63 | 10.3 | Yes | Yes | 22 | 18.4 | 3.7 | 3FD8FEC23AF94F0BB5CDC591DD70145A |  | R22 | Non-TXV |  | 16.35% | 0.83651 | 31.42% | [5 empty] | Non-TXV | 16.35%
Antioch | CA | 94509-6460 |  | 2014-11-10 | 2014-11-10 12:43 | 2014-11-10 13:01 | YORK - H2RA030S06D | 62 | 7.9 | Yes | Yes | 20.3 | 18.7 | 1.6 | 0BA08A6501A74D3BB9273EF8096697E8 |  | R22 | Non-TXV |  | 12.74% | 0.87258 | 24.49% | [5 empty] | Non-TXV | 12.74%
Antioch | CA | 94509-6288 |  | 2014-11-18 | 2014-11-18 12:14 | 2014-11-18 12:34 | OTHER - 24ABC648A310 | 208 | 20.6 | Yes | Yes | 19.5 | 18.8 | 0.7 | 77500CB69B5B473B9D8B68E8896420B6 |  | R410A | TXV |  | 9.904% | 0.90096 | 19.03% | [5 empty] | TXV | 9.904%
Bakersfield | CA | 93313-3961 |  | 2014-10-04 | 2014-10-04 19:49 | 2014-10-04 19:52 | OTHER - 56AJX036-B | 76 | 4.3 | Yes | Yes | 21.5 | 22.1 | -0.6 | 535803F7320D4E78A40E848C195E02B1 |  | R22 | Non-TXV |  | 5.658% | 0.94342 | 10.87% | [5 empty] | Non-TXV | 5.658%
Bakersfield | CA | 93307-0000 |  | 2014-10-28 | 2014-10-28 10:55 | 2014-10-28 10:55 | ICP - N2A342AKA100 | 115 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | F26CA6C2C08046C1BD1FAC51B681491B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5742 |  | 2014-10-27 | 2014-10-27 18:18 | 2014-10-27 18:18 | NORDYNE - JS5BD-030KA | 99 | 0 | Yes | Yes | 23.4 | 21 | 2.4 | E2138D657BBE4FA9A92B751C71F490DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5742 |  | 2014-10-27 | 2014-10-27 19:36 | 2014-10-27 19:36 | NORDYNE - JS5BD-030KA | 99 | 0 | Yes | Yes | 25.7 | 20.4 | 5.3 | DB5FFB5A59014D12A9EA76FE411062D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5742 |  | 2014-10-27 | 2014-10-27 19:50 | 2014-10-27 19:50 | NORDYNE - JS5BD-030KA | 99 | 0 | Yes | Yes | 25.7 | 19.9 | 5.8 | 6AE95F6335404FAABFAC850FA9DD6DE8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-6546 |  | 2014-10-22 | 2014-10-22 13:11 | 2014-10-22 14:26 | GIBSON - JS3BC036KA | 82 | 8.4 | Yes | Yes | 17.9 | 20.4 | -2.5 | 23891547DCBC4ED69C2EF979052EA507 |  | R22 | Non-TXV |  | 10.24% | 0.89756 | 19.69% | [5 empty] | Non-TXV | 10.24%
Bakersfield | CA | 93314-6546 |  | 2014-10-22 | 2014-10-22 13:17 | 2014-10-22 13:17 | GIBSON - JS3BC042KA | 102 | 0 | Yes | Yes | 19.3 | 19.3 | 0 | F89B8F16D16F46EFA9EC1E0D8F309034 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-2924 |  | 2014-10-01 | 2014-10-01 10:10 | 2014-10-01 10:12 | YORK - H2RD036S06B | 96 | -9 | Yes | Yes | 19.5 | 19.3 | 0.2 | 3468A62A28CE4A9FB7E31EE7020E2738 |  | R22 | Non-TXV |  | -9.375% | 1.0938 | 2.625% |  |  |  |  | Non-TXV |  |  | -9.375%
Antioch | CA | 94531-8132 |  | 2014-11-10 | 2014-11-10 11:08 | 2014-11-10 11:34 | CARRIER - 38TH060300 | 167 | 5 | Yes | Yes | 18.8 | 20.9 | -2.1 | B200DD4E3B9D4185A675F9ED227CE5A2 |  | R22 | Non-TXV |  | 2.994% | 0.97006 | 5.754% | [5 empty] | Non-TXV | 2.994%
Fresno | CA | 93722-3727 |  | 2014-10-02 | 2014-10-02 13:02 | 2014-10-02 13:04 | ICP - N2A360AKA200 | 146 | 18.4 | Yes | Yes | 21.2 | 18.7 | 2.6 | 7268D3D2E60A4F93A571AD3299DA903C |  | R22 | Non-TXV |  | 12.6% | 0.87397 | 24.22% | [5 empty] | Non-TXV | 12.6%
Bakersfield | CA | 93307-5723 |  | 2014-10-27 | 2014-10-27 15:46 | 2014-10-27 15:46 | NORDYNE - JS3BD-030K | 114 | 0 | Yes | Yes | 25.9 | 20.4 | 5.5 | F72F45CE3ACE4A158F551FBD6CA15F84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1050 |  | 2014-11-04 | 2014-11-04 15:53 | 2014-11-04 16:12 | GOODMAN - GPG1336045M41BA | 85 | 12.1 | Yes | Yes | 17.7 | 20.7 | -3 | D14DA242B72F4BA89B2E03DBE7F1E442 |  | R410A | Non-TXV |  | 14.24% | 0.85765 | 27.36% | [5 empty] | Non-TXV | 14.24%
Bakersfield | CA | 93307-3966 |  | 2014-10-12 | 2014-10-12 17:30 | 2014-10-12 17:30 | DUCANE - 2AC13624P1A | 89 | 0 | Yes | Yes | 21.8 | 21.3 | 0.5 | CE082A0E390B482BA65FAB4FB1B146C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7703 |  | 2014-11-10 | 2014-11-10 14:06 | 2014-11-10 14:23 | TRANE - TTB048C100A1 | 97 | 6.4 | Yes | Yes | 20.6 | 20.4 | 0.2 | 5E1DE95F70604837A33F09BC3D562389 |  | R22 | Non-TXV |  | 6.598% | 0.93402 | 12.68% | [5 empty] | Non-TXV | 6.598%
Antioch | CA | 94531-7621 |  | 2014-11-18 | 2014-11-18 12:20 | 2014-11-18 18:14 | TRANE - TTB742A100A0 | 104 | 5.8 | Yes | Yes | 18.3 | 20.4 | -2.1 | BB25F261E9364283A3DC5A1D21C5C487 |  | R22 | Non-TXV |  | 5.577% | 0.94423 | 10.72% | [5 empty] | Non-TXV | 5.577%
Antioch | CA | 94531-7717 |  | 2014-11-10 | 2014-11-10 12:13 | 2014-11-10 12:39 | RHEEM - RAFD-048J8S | 101 | 4.9 | Yes | Yes | 18.5 | 20.4 | -1.9 | 6BF6A08CAE334EF38B806A4254B3A3CA |  | R22 | Non-TXV |  | 4.851% | 0.95149 | 9.323% | [5 empty] | Non-TXV | 4.851%
Bakersfield | CA | 93305-4370 |  | 2014-10-23 | 2014-10-23 10:20 | 2014-10-23 10:20 | YORK - DBYPF024N045A | 100 | 0 | Yes | Yes | 20.1 | 19 | 1.1 | C472F7165AAB4782B06AE6932C6BA300 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5689 |  | 2014-10-07 | 2014-10-07 11:26 | 2014-10-07 11:26 | DAY & NIGHT - 580AN036060 | 96 | 0 | Yes | Yes | 21.6 | 22.6 | -1 | 2AE06D1069B8499192CBA82D389B3118 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-1624 |  | 2014-10-30 | 2014-10-30 04:49 | 2014-10-30 05:08 | TEMPSTAR - WPG3244040LK01 | 85 | 15.6 | Yes | Yes | 25.5 | 23.1 | 2.4 | CADE5F94E7A54384B458828184E4B784 |  | R410A | Non-TXV |  | 18.35% | 0.81647 | 35.27% | [5 empty] | Non-TXV | 18.35%
Bakersfield | CA | 93306-4602 |  | 2014-10-21 | 2014-10-21 11:45 | 2014-10-21 11:45 | GOODMAN - APG13360451AB | 112 | 0 | Yes | Yes | 22 | 17.7 | 4.3 | 2810D1AAD99C428F87DC57E4763C8021 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6443 |  | 2014-10-14 | 2014-10-14 10:27 | 2014-10-14 10:27 | OTHER - 38BRC060340 | 200 | 0 | Yes | Yes | 24.1 | 18.6 | 5.5 | 940C868B9CB744519AC73B5C28E7703E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2022 |  | 2014-10-21 | 2014-10-21 16:16 | 2014-10-21 16:16 | RUUD - URMA-A042JK08X | 114 | 0 | Yes | Yes | 22.6 | 20.4 | 2.2 | 2B5D8687C37E4E91B5FE9297245FF50F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8610 |  | 2014-11-10 | 2014-11-10 13:17 | 2014-11-10 14:24 | CARRIER - CKD457-036-046711 | 87 | 5.5 | Yes | Yes | 20.4 | 20.4 | 0 | 0C2A90F20CD84980B35BF8C1B65B36AC |  | R22 | Non-TXV |  | 6.322% | 0.93678 | 12.15% | [5 empty] | Non-TXV | 6.322%
Bakersfield | CA | 93307-3877 |  | 2014-10-13 | 2014-10-13 13:47 | 2014-10-13 13:47 | CONCORD - CC10A24A1 | 50 | 0 | Yes | Yes | 19.7 | 22.5 | -2.8 | 1CE4B037557E4E1FA0C4BE55B2054569 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2730 |  | 2014-11-07 | 2014-11-07 14:07 | 2014-11-07 14:24 | GOODMAN - UNK | 85 | 4.5 | Yes | Yes | 21.5 | 20.8 | 0.7 | 4C0BF4C734ED4BF095132117C77123C2 |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Arvin | CA | 93203-2730 |  | 2014-11-07 | 2014-11-07 14:26 | 2014-11-07 14:42 | GOODMAN - UNK | 85 | 7.3 | Yes | Yes | 16.4 | 19.3 | -2.9 | 72A32915FA3146F99120D9033864ECB5 |  | R22 | Non-TXV |  | 8.588% | 0.91412 | 16.5% | [5 empty] | Non-TXV | 8.588%
Bakersfield | CA | 93307-3982 |  | 2014-10-13 | 2014-10-13 14:28 | 2014-10-13 14:28 | CONCORD - CCV10A18A2 | 60 | 0 | Yes | Yes | 20.5 | 21 | -0.5 | D638951B812746CCBC286F38971F9DAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7674 |  | 2014-11-10 | 2014-11-10 12:24 | 2014-11-10 12:43 | CARRIER - 38CKC042340 | 80 | 4.6 | Yes | Yes | 18.2 | 20.4 | -2.2 | 15042CAAEC7C43A892F28A5727D59EAA |  | R22 | Non-TXV |  | 5.75% | 0.9425 | 11.05% | [5 empty] | Non-TXV | 5.75%
Arvin | CA | 93203-2067 |  | 2014-10-30 | 2014-10-30 05:03 | 2014-10-30 05:21 | GOODMAN - CPLE42-12 | 85 | 2.9 | Yes | Yes | 15.5 | 18.5 | -3 | 14D56DB82AF04C7191533F71A80A5AEC |  | R22 | Non-TXV |  | 3.412% | 0.96588 | 6.557% | [5 empty] | Non-TXV | 3.412%
Bakersfield | CA | 93308-3412 |  | 2014-10-24 | 2014-10-24 10:04 | 2014-10-24 10:04 | OTHER - N2A342AKA200 | 127 | 0 | Yes | Yes | 24.4 | 19.5 | 4.9 | 6675B93F8AB348488B7A9B4ED8EF6F83 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8230 |  | 2014-11-18 | 2014-11-18 13:17 | 2014-11-18 13:17 | CARRIER - 38CKC030340 | 70 | 0 | Yes | Yes | 18.6 | 18.2 | 0.4 | 7FCA9C08F8C34218B839C3B6A1A98DB2 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3025 |  | 2014-10-21 | 2014-10-21 10:13 | 2014-10-21 10:13 | PAYNE - UNK | 134 | 0 | Yes | Yes | 23.5 | 18.9 | 4.6 | 2EAD753896B943A286F2EABF3F16F029 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4710 |  | 2014-10-07 | 2014-10-07 10:40 | 2014-10-07 10:40 | PAYNE - PY2PNB060090NAAA | 85 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | 90370B3500AF44FEB7F2424E5DE553BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1903 |  | 2014-10-16 | 2014-10-16 07:50 | 2014-10-16 07:50 | DAY & NIGHT - 36DNR-10BC | 72 | 0 | Yes | Yes | 15.1 | 16.9 | -1.8 | F1C2B977F69A4B999F9BCA40757F18EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1928 |  | 2014-10-21 | 2014-10-21 12:23 | 2014-10-21 12:23 | PAYNE - PY2PNB036060AAAA | 83 | 0 | Yes | Yes | 21.5 | 22.4 | -0.9 | 088ADEE5783F4A79B0666522EF6F40D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8426 |  | 2014-11-10 | 2014-11-10 14:17 | 2014-11-10 14:40 | RHEEM - RAJC-042-JAS | 99 | 18.8 | Yes | Yes | 21.7 | 19 | 2.7 | FB7DEA511B4849C78B066C4601C16846 |  | R22 | Non-TXV |  | 18.99% | 0.8101 | 36.49% | [5 empty] | Non-TXV | 18.99%
Lamont | CA | 93241-1625 |  | 2014-10-30 | 2014-10-30 17:08 | 2014-10-30 17:25 | YORK - SDA3Y489J0A | 85 | 5.4 | Yes | Yes | 21 | 22.5 | -1.5 | E7B6E0E198094379B7C33C39A755541A |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Fairfield | CA | 94533-8923 |  | 2014-10-09 | 2014-10-09 13:40 | 2014-10-10 08:38 | CARRIER - 38CKC042350 | 93 | 3 | Yes | Yes | 14.7 | 17.1 | -2.4 | 4994E2D88D0544BAAB87FA9D60EB0C91 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Arvin | CA | 93203-2806 |  | 2014-11-06 | 2014-11-06 12:44 | 2014-11-06 13:00 | OTHER - UNK | 85 | 4.1 | Yes | Yes | 20.9 | 23.7 | -2.8 | A5C0FC0AD11F44BCAAF86D3ED903D373 |  | R22 | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Wasco | CA | 93280-1927 |  | 2014-10-29 | 2014-10-29 13:22 | 2014-10-29 13:22 | ARCOAIRE - GPCM24K040F | 54 | 0 | Yes | Yes | 19.3 | 20.1 | -0.8 | 1A09DEB2257947C69F0C261F9CA0BEE8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2517 |  | 2014-10-07 | 2014-10-07 13:04 | 2014-10-09 06:48 | ICP - CA9642VKA2 | 156 | 6.2 | Yes | Yes | 12.9 | 14.4 | -1.5 | 6BFD0146F0A14E3390C77079E1FEF1EF |  | R22 | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
Antioch | CA | 94531-8199 |  | 2014-11-10 | 2014-11-10 13:41 | 2014-11-10 14:24 | CARRIER - 2396E19048 | 95 | 4.9 | Yes | Yes | 18.8 | 20.4 | -1.6 | DF05E46725D7439BBCE50355E71EAB3F |  | R22 | Non-TXV |  | 5.158% | 0.94842 | 9.912% | [5 empty] | Non-TXV | 5.158%
Fairfield | CA | 94533-2605 |  | 2014-10-09 | 2014-10-09 08:46 | 2014-10-10 08:39 | TRANE - 4TTX4030A1000AB | 79 | 4.9 | Yes | Yes | 13.3 | 15.5 | -2.2 | 26B78F97A6E949ADA4C1D800B846DA7D |  | R22 | Non-TXV |  | 6.203% | 0.93797 | 11.92% | [5 empty] | Non-TXV | 6.203%
Vacaville | CA | 95687-9424 |  | 2014-10-08 | 2014-10-08 11:58 | 2014-10-08 12:28 | TRANE - WCY060G100AB | 168 | 5.9 | Yes | Yes | 18.3 | 20.4 | -2.1 | BEE885B945304660BCBC40F3C657EE2E |  | R22 | Non-TXV |  | 3.512% | 0.96488 | 6.749% | [5 empty] | Non-TXV | 3.512%
Arvin | CA | 93203-1034 |  | 2014-11-04 | 2014-11-04 15:41 | 2014-11-04 16:10 | YORK - D1NH036N05606C | 108 | 7.9 | Yes | Yes | 21.7 | 23.4 | -1.7 | FF0677C7D976486594980D95AB9E1288 |  | R22 | Non-TXV |  | 7.315% | 0.92685 | 14.06% | [5 empty] | Non-TXV | 7.315%
Bakersfield | CA | 93304-5165 |  | 2014-10-08 | 2014-10-08 15:22 | 2014-10-08 15:22 | GOODMAN - GPG13480701AC | 145 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | EE607037D41946309EB66AE44E21DB12 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2180 |  | 2014-10-10 | 2014-10-10 09:55 | 2014-10-12 21:02 | TRANE - 2TTR1036A1000AA | 73 | 3.3 | Yes | Yes | 12.8 | 15.3 | -2.5 | FB8C491FDDDA4C00A5882D39D7F31BA2 |  | R22 | Non-TXV |  | 4.521% | 0.95479 | 8.687% | [5 empty] | Non-TXV | 4.521%
Rio Vista | CA | 94571-2107 |  | 2014-10-15 | 2014-10-15 12:21 | 2014-10-15 14:47 | YORK - H1RC030S06D | 71 | 4.1 | Yes | Yes | 20.6 | 20.4 | 0.2 | 2D12270F684744329F7DE46958882942 |  | R22 | Non-TXV |  | 5.775% | 0.94225 | 11.1% | [5 empty] | Non-TXV | 5.775%
Vacaville | CA | 95687-5210 |  | 2014-10-14 | 2014-10-14 19:22 | 2014-10-14 19:40 | CARRIER - 24ABB330W310 | 78 | 5.3 | Yes | Yes | 20.4 | 20.4 | 0 | 747EDA4403AF4CD8AF10CFD244B9895D |  | R410A | Non-TXV |  | 6.795% | 0.93205 | 13.06% | [5 empty] | Non-TXV | 6.795%
Rio Vista | CA | 94571-2112 |  | 2014-10-15 | 2014-10-15 11:56 | 2014-10-15 23:14 | - H1RC030S060 | 70 | 3.5 | Yes | Yes | 20.2 | 20.9 | -0.7 | 55155DED87B348DD95F7C6C8EA280342 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Davis | CA | 95616-2861 |  | 2014-10-16 | 2014-10-16 11:53 | 2014-10-16 12:25 | LENNOX - 10ACB818-5P | 58 | 4 | Yes | Yes | 20.7 | 21 | -0.3 | 15C11CE601B14F1F864DE11B277408EC |  | R22 | Non-TXV |  | 6.897% | 0.93103 | 13.25% | [5 empty] | Non-TXV | 6.897%
Lamont | CA | 93241-2760 |  | 2014-11-01 | 2014-11-01 09:54 | 2014-11-01 10:10 | DAY & NIGHT - UNK | 85 | 8 | Yes | Yes | 17.4 | 19.2 | -1.8 | E9865D8350E84A2D82ABCBEB88E9D3A0 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Davis | CA | 95616-2809 |  | 2014-10-10 | 2014-10-10 13:55 | 2014-10-10 19:24 | LENNOX - HS29-018-3P | 60 | 3.4 | Yes | Yes | 19 | 20.4 | -1.4 | 68999C011D8E406AB1D9648A58A3DD76 |  | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Antioch | CA | 94531-8425 |  | 2014-11-10 | 2014-11-10 15:36 | 2014-11-10 15:55 | AMERICAN STANDARD - UNK | 85 | -9 | Yes | Yes | 22.9 | 18.3 | 4.7 | 18448130474D4F1BAB17CF0C8EF1C31F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | -10.59% | 1.1059 | 2.965% |  |  |  |  | Non-TXV |  |  | -10.59%
Bakersfield | CA | 93306-1036 |  | 2014-10-20 | 2014-10-20 10:34 | 2014-10-20 10:34 | RHEEM - YCP042FLMOAC | 128 | 0 | Yes | Yes | 22 | 21 | 1 | 29471CDECC1D4AF487EA359389E707C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1036 |  | 2014-10-20 | 2014-10-20 10:30 | 2014-10-20 10:30 | RUUD - S-6267F170208333 | 162 | 0 | Yes | Yes | 20 | 18 | 2 | 4C374BDD1B454493BE4964EB228B54A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4703 |  | 2014-10-21 | 2014-10-21 10:22 | 2014-10-21 10:22 | RHEEM - HC-80-36-21C | 90 | 0 | Yes | Yes | 26 | 21.3 | 4.8 | 35AC05A11D3847C9B22CD829A6DD0F7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4229 |  | 2014-11-11 | 2014-11-11 09:49 | 2014-11-11 10:37 | GE - | 89 | 4.7 | Yes | Yes | 20.5 | 20.7 | -0.2 | 436B900024974B7A8782E3E66A03D8BE |  | R22 | Non-TXV |  | 5.281% | 0.94719 | 10.15% | [5 empty] | Non-TXV | 5.281%
Davis | CA | 95616-3101 |  | 2014-10-10 | 2014-10-10 10:48 | 2014-10-10 11:12 | RHEEM - K11-67-3609777 | 72 | 3.6 | Yes | Yes | 22.8 | 20.4 | 2.4 | B101BDFE226A45439693AA7F4F24CA1E |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Bakersfield | CA | 93306-1423 |  | 2014-11-03 | 2014-11-03 11:49 | 2014-11-03 11:49 | GOODMAN - CK36-1B | 76 | 0 | Yes | Yes | 26.1 | 21 | 5.1 | 5DDCACE6FDF943DA9A037A69FCE72F81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3046 |  | 2014-11-17 | 2014-11-17 11:24 | 2014-11-17 11:24 | HEIL - PGD360090K001C1 | 160 | 0 | Yes | Yes | 29.6 | 19.9 | 9.7 | 72B7A7D6F8814B76B32FB3E443F844D7 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5619 |  | 2014-10-06 | 2014-10-06 17:11 | 2014-10-06 17:33 | TRANE - 2TTB30361000AA | 101 | 4.2 | Yes | Yes | 19.3 | 20.4 | -1.1 | 44809E80BBE34FCEA3B1388B5D137A5A |  | R22 | TXV |  | 4.158% | 0.95842 | 7.992% | [5 empty] | TXV | 4.158%
Bakersfield | CA | 93304-4011 |  | 2014-10-15 | 2014-10-15 18:37 | 2014-10-15 18:53 | YORK - DWQ042N06506NXA | 72 | 6 | Yes | Yes | 15.5 | 18.3 | -2.8 | 5E618304747943DB9A1DD608DB6A2003 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Bakersfield | CA | 93304-7607 |  | 2014-10-21 | 2014-10-21 15:00 | 2014-10-21 15:00 | GOODMAN - GSC130481AF | 152 | 0 | Yes | Yes | 19.9 | 19.7 | 0.2 | F3B4B194FA40410F9214EA73FFB1EC49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Shafter | CA | 93263-3117 |  | 2014-11-18 | 2014-11-18 14:40 | 2014-11-18 14:40 | BRYANT - 582ANW03606060AAAF | 56 | 0 | Yes | Yes | 20 | 18.7 | 1.3 | D107D91C5DCB4EBF8066A94F0677C2E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3826 |  | 2014-10-08 | 2014-10-08 13:45 | 2014-10-08 13:45 | ARCOAIRE - PGF030K060D | 52 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 6C5468EF336F447DBE5DA6AAE63418A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1525 |  | 2014-10-15 | 2014-10-15 12:37 | 2014-10-15 12:37 | HEIL - PGCM030K060F | 51 | 0 | Yes | Yes | 24.9 | 19 | 5.9 | 2FF8F7611E6A4D5898F4A0E16E982DBB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Arvin | CA | 93203-2830 |  | 2014-11-06 | 2014-11-06 13:07 | 2014-11-06 13:26 | RHEEM - RR07-42MP0 | 118 | -8.3 | Yes | Yes | 18.8 | 20.9 | -2.1 | B2ED41579A794DF28AEAF60CCC7D68A1 |  | R22 | Non-TXV |  | -7.034% | 1.0703 | 1.97% |  |  |  |  | Non-TXV |  |  | -7.034%
Bakersfield | CA | 93306-5086 |  | 2015-07-28 | 2015-07-28 12:19 | 2015-07-28 12:19 | CARRIER - 25HBR360A300 | 246 | 0 | Yes | Yes | 21.6 | 22 | -0.4 | 0A7F8FBA39E141C7A5DC5C0BADEA5EA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3615 |  | 2015-07-30 | 2015-07-30 09:57 | 2015-07-30 09:57 | GOODMAN - GPG1324045M41DA | 75 | 0 | Yes | Yes | 27.9 | 23.1 | 4.8 | B64C83C011104A91A9F1D3CB358BFE36 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94506-4424 |  | 2015-08-12 | 2015-08-12 16:28 | 2015-08-12 16:44 | NORDYNE - FS3BA-030KA | 68 | 6.2 | Yes | Yes | 22.6 | 21.8 | 0.8 | 4C2604F6AE6A4D6C97DF21CCA7F7834B |  | R22 | Non-TXV |  | 9.118% | 0.90882 | 17.52% | [5 empty] | Non-TXV | 9.118%
Bakersfield | CA | 93306-6134 |  | 2015-07-28 | 2015-07-28 15:02 | 2015-07-28 15:02 | YORK - D6NZ030N03606NXA | 85 | 0 | Yes | Yes | 20.9 | 21.7 | -0.8 | F0619A0207624F3AA0410EED86A455DF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2889 |  | 2015-08-18 | 2015-08-18 16:42 | 2015-08-18 16:42 | AMERICAN STANDARD - 2A7A2036A1000AA | 96 | 0 | Yes | Yes | 18.6 | 16.9 | 1.7 | 902FDADDC49D45B386B0A5E7480ADCFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-6404 |  | 2015-09-09 | 2015-09-09 11:43 | 2015-09-09 11:48 | GOODMAN - GPG1336070M41BA | 77 | 26.8 | Yes | Yes | 27 | 21.4 | 5.6 | 9507B5682734443497638472D3C58794 |  | R410A | Non-TXV |  | 34.81% | 0.65195 | 66.89% | [5 empty] | Non-TXV | 34.81%
W Sacramento | CA | 95691-6111 |  | 2015-11-06 | 2015-11-06 11:13 | 2015-11-06 11:13 | LENNOX - 13ACD04223002 | 110 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | BEDFBC3790BC4AEC95421936129F4130 |  | R22 | TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95409-4112 |  | 2015-08-13 | 2015-08-13 13:08 | 2015-08-13 13:08 | UNITARY PRODUCTS GROUP - BRCQ0361BD | 52 | 0 | Yes | Yes | 18.7 | 18.8 | -0.1 | 896F6ACE13C04B50AEF2BEB9B88C3E5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5512 |  | 2015-07-28 | 2015-07-28 15:08 | 2015-07-28 15:08 | RHEEM - HG-80-30-21C | 75 | 0 | Yes | Yes | 27.5 | 21.7 | 5.8 | 25AD290E7E8647C38454E4714CBE632A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6800 |  | 2015-07-27 | 2015-07-27 12:30 | 2015-07-27 12:30 | BDP - 585BJO36 | 85 | 0 | Yes | Yes | 19.4 | 22.4 | -3 | 6C5C8A6BFA6E41C7AFFB766C26C1F601 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6529 |  | 2015-08-17 | 2015-08-17 13:54 | 2015-08-17 13:54 | CARRIER - 38BRC048370 | 142 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 868DD4EC66644F8BBD285C5977B1F631 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6529 |  | 2015-08-17 | 2015-08-17 14:15 | 2015-08-17 14:15 | CARRIER - 38BRC036330 | 104 | 0 | Yes | Yes | 18.7 | 19.3 | -0.6 | E35E8A869EB34F0D946EB5EC2E42AB67 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3398 |  | 2015-07-13 | 2015-07-13 11:28 | 2015-07-13 11:28 | CARRIER - 25HCD318A300 | 71 | 0 | Yes | Yes | 17.3 | 20.2 | -2.9 | 57F96919D60A462BBAEBC52646115ABD |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2168 |  | 2015-09-10 | 2015-09-10 12:10 | 2015-09-10 12:40 | BRYANT - 583ANW048115AAAF | 116 | 10.4 | Yes | Yes | 22.5 | 21.4 | 1.1 | 46700306DB8241F09657B4CD49B580D7 |  | R22 | Non-TXV |  | 8.966% | 0.91034 | 17.23% | [5 empty] | Non-TXV | 8.966%
Fairfield | CA | 94533-4172 |  | 2015-08-14 | 2015-08-14 12:00 | 2015-08-14 12:00 | TRANE - BTD730A100HO | 74 | 0 | Yes | Yes | 19.4 | 19.3 | 0.1 | 03F0DD2ACB804AF0A6CE0142B22739A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95409-0000 |  | 2015-10-27 | 2015-10-27 13:35 | 2015-10-27 13:35 | CARRIER - 38HDRO24-301 | 101 | 0 | Yes | Yes | 21 | 19.9 | 1.1 | 4BD820EA22AF424DB59E77CCB77965D6 |  | R410A | TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-3903 |  | 2015-11-04 | 2015-11-04 10:42 | 2015-11-04 10:42 | TRANE - YCXO36G1MOAB | 109 | 0 | Yes | Yes | 22.5 | 18.7 | 3.8 | 8488F3EAC48C4808A18F382E5E0287CE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-3210 |  | 2015-07-31 | 2015-07-31 10:00 | 2015-07-31 10:00 | BRYANT - 113ANA024-D | 85 | 0 | Yes | Yes | 15 | 17.7 | -2.7 | FF150A66AE884E3F90EF4F14314376DF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-6373 |  | 2015-10-06 | 2015-10-06 15:55 | 2015-10-06 15:55 | LENNOX - 13CD-024-05 | 67 | 0 | Yes | Yes | 18.6 | 18.8 | -0.2 | A37CB11688B34017AEC1AA30D243F8AD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-1226 |  | 2015-07-30 | 2015-07-30 13:54 | 2015-07-30 13:54 | OTHER - 2TTR3042A1000AA | 109 | 0 | Yes | Yes | 21.1 | 17.6 | 3.5 | 640DDD79245B463ABEDC51E276077A28 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3460 |  | 2015-09-10 | 2015-09-10 14:12 | 2015-09-10 14:12 | GOODMAN - GPG1324070M41AC | 80 | 0 | Yes | Yes | 20.3 | 23.1 | -2.8 | BED791A4F5744B67B5F765B80F987B02 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-3831 |  | 2015-07-29 | 2015-07-29 11:57 | 2015-07-29 11:57 | RUUD - UACB-036JAS | 48 | 0 | Yes | Yes | 21.5 | 19.7 | 1.8 | 89E64E7E356C49FA8171D16F0F37EE6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3460 |  | 2015-09-10 | 2015-09-10 14:10 | 2015-09-10 14:44 | RHEEM - N/A | 85 | 9 | Yes | Yes | 21.8 | 21.4 | 0.4 | 03EF6F1B559E4936B669C06926873859 |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Antioch | CA | 94509-4911 |  | 2015-07-01 | 2015-07-01 09:38 | 2015-07-01 09:56 | YORK - H4DB036806A | 73 | 22.5 | Yes | Yes | 22.4 | 20.7 | 1.7 | 14F38272AD5C4640AF5778B1400F5A20 |  | R22 | Non-TXV |  | 30.82% | 0.69178 | 59.23% | [5 empty] | Non-TXV | 30.82%
Bakersfield | CA | 93313-6011 |  | 2015-07-29 | 2015-07-29 14:49 | 2015-07-29 14:49 | NORDYNE - FS3BD-048K | 143 | 0 | Yes | Yes | 19.2 | 21.9 | -2.7 | 2BD2CA276C714840A2B316A1B38F9BC3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3010 |  | 2015-07-16 | 2015-07-16 15:21 | 2015-07-16 15:21 | TRANE - 4TTR4036A1000 | 91 | 0 | Yes | Yes | 16.6 | 19.3 | -2.7 | DEEC11DF4C8342C0840F91C7E575D145 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3056 |  | 2015-08-27 | 2015-08-27 09:13 | 2015-08-27 09:13 | RHEEM - N/A | 85 | 0 | Yes | Yes | 19.7 | 19.4 | 0.3 | B5BC902489444586AE30695E0A2F15F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1728 |  | 2015-08-04 | 2015-08-04 08:37 | 2015-08-04 08:58 | KENMORE - H4A345GKA100 | 85 | 5.3 | Yes | Yes | 20.9 | 19.1 | 1.9 | A1679CC5F6CA4EF7B0B6D7D33EFF5707 |  | R410A | TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | TXV | 6.235%
Martinez | CA | 94553-4150 |  | 2015-07-24 | 2015-07-24 10:08 | 2015-07-24 10:08 | CARRIER - 569BJO36 | 93 | 0 | Yes | Yes | 17.5 | 18.7 | -1.2 | 4BDFA453BA57482DBDF67CD62A76F8F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3341 |  | 2015-06-26 | 2015-06-26 14:20 | 2015-06-26 14:47 | DUCANE - 2AC13L42P-1A | 146 | 11 | Yes | Yes | 16.6 | 18.8 | -2.2 | 394ED5A8F3EA496C880706B6327F5796 |  | R22 | TXV |  | 7.534% | 0.92466 | 14.48% | [5 empty] | TXV | 7.534%
Vallejo | CA | 94589-2116 |  | 2015-08-17 | 2015-08-17 10:37 | 2015-08-17 10:37 | BRYANT - 113ANA035E | 86 | 0 | Yes | Yes | 18.3 | 17.9 | 0.4 | A1A1C165BF434202A0B7C7D6DA4B4F4E |  | R410A | TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1538 |  | 2015-07-23 | 2015-07-23 14:27 | 2015-07-23 14:27 | RUUD - UAKA048JAS | 85 | 0 | Yes | Yes | 20.7 | 19.3 | 1.4 | DE1820FC2DAC4CA484B0C0AECA8349A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5086 |  | 2015-07-28 | 2015-07-28 12:27 | 2015-07-28 12:27 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 21.3 | 22.6 | -1.3 | C5C89033CF24419A93E23A877F9871D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2737 |  | 2015-07-29 | 2015-07-29 11:28 | 2015-07-29 12:05 | YORK - 561AJX030000AAAA | 72 | 17.8 | Yes | Yes | 12.2 | 15.1 | -2.9 | 3178A509FA30449685E4FEAB894ECBEA |  | R22 | Non-TXV |  | 24.72% | 0.75278 | 47.51% | [5 empty] | Non-TXV | 24.72%
Bakersfield | CA | 93304-5407 |  | 2015-07-27 | 2015-07-27 10:54 | 2015-07-27 10:54 | LENNOX - HSB3119FFP | 66 | 0 | Yes | Yes | 20.6 | 16.4 | 4.2 | 1AE2C08069F3471CB729E8A87642681B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2437 |  | 2015-09-17 | 2015-09-17 11:56 | 2015-09-17 11:56 | UNITARY PRODUCTS GROUP - DBYP-F036N070A | 108 | 0 | Yes | Yes | 25.3 | 21 | 4.3 | CFA77158A3F84B70AD2CFA1233C68440 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2879 |  | 2015-10-05 | 2015-10-05 09:24 | 2015-10-05 09:24 | CARRIER - 38THO48320 | 128 | 0 | Yes | Yes | 19.7 | 18.7 | 1 | 129E7472F94E451D9972BF7E5200C1D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5570 |  | 2015-09-10 | 2015-09-10 15:08 | 2015-09-10 15:08 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 21.4 | 22.2 | -0.8 | A9632AA2A84A4DC99D26CF7DE57753FD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1573 |  | 2015-08-12 | 2015-08-12 09:21 | 2015-08-12 09:39 | TRANE - TTB036C100A2 | 90 | 3.3 | Yes | Yes | 22.1 | 19.3 | 2.8 | 113E27C05F644D97AB4DB80ABA9902A9 |  | R22 | TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | TXV | 3.667%
Vacaville | CA | 95687-5182 |  | 2015-07-27 | 2015-07-27 10:44 | 2015-07-27 10:44 | GOODMAN - GSC130861DE | 85 | 0 | Yes | Yes | 16.8 | 19.3 | -2.5 | ED12D03A03A247D7BF5BC1517FA612D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6312 |  | 2015-08-17 | 2015-08-17 08:47 | 2015-08-17 08:47 | YORK - D6NZ036N05606NXA | 85 | 0 | Yes | Yes | 22.3 | 19.9 | 2.4 | A110C4A4457D4A28B65C9E1A7B1DC312 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6455 |  | 2015-07-28 | 2015-07-28 14:39 | 2015-07-28 14:39 | ICP - PGX448100K00A1 | 237 | 0 | Yes | Yes | 20.8 | 21.4 | -0.6 | E55E3BFA3DBD4B64A3CB9F75BDF6B7B1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5140 |  | 2015-09-10 | 2015-09-10 08:38 | 2015-09-10 08:38 | ICP - PGC042K080D | 87 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | 3DC48730503E48B0AC92E0D1B0CD4069 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3461 |  | 2015-08-17 | 2015-08-17 09:30 | 2015-08-17 09:49 | YORK - D1NP048N06506A | 132 | 4.5 | Yes | Yes | 25.7 | 22.5 | 3.2 | DC448F56ADA04A46916FFD8CFF076B29 |  | R22 | Non-TXV |  | 3.409% | 0.96591 | 6.552% | [5 empty] | Non-TXV | 3.409%
Bakersfield | CA | 93309-4515 |  | 2015-07-27 | 2015-07-27 10:02 | 2015-07-27 10:02 | PAYNE - PY2PNB042060AAAA | 121.6 | 0 | Yes | Yes | 20.4 | 20.2 | 0.2 | F182606CBDE94D1CBB44B94926C5C248 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2025 |  | 2015-07-27 | 2015-07-27 09:13 | 2015-07-27 09:13 | PAYNE - PA10JA036-C | 85 | 0 | Yes | Yes | 16.8 | 18.3 | -1.5 | A37F8FA346394742933B661129015376 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7174 |  | 2015-07-24 | 2015-07-24 08:51 | 2015-07-24 08:51 | UNITARY PRODUCTS GROUP - D1NA042N05606C | 76 | 0 | Yes | Yes | 19.3 | 19.3 | 0 | 218349DA75014259B4F85227A909E0FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6684 |  | 2015-09-10 | 2015-09-10 09:29 | 2015-09-10 09:29 | TRANE - 2TTR2048A1000AA | 120 | 0 | Yes | Yes | 19.5 | 19.7 | -0.2 | 237EE0EE74554E83A23F412E72F21FFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4052 |  | 2015-07-10 | 2015-07-10 13:43 | 2015-07-10 13:43 | CARRIER - 38TKBO24300 | 65 | 0 | Yes | Yes | 14.7 | 17.7 | -3 | 327C45C21AE24850B895B04243AD6F75 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4027 |  | 2015-07-08 | 2015-07-08 14:05 | 2015-07-08 14:05 | GE - BTB824A100A | 43 | 0 | Yes | Yes | 25.7 | 20.4 | 5.3 | B83681E56D2247849941DD33C1060287 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1147 |  | 2015-08-13 | 2015-08-13 12:20 | 2015-08-13 12:20 | LENNOX - HS290361P | 73 | 0 | Yes | Yes | 15.1 | 17.1 | -2 | 623148D398324ECFB5B13030E5A033DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3839 |  | 2015-11-23 | 2015-11-23 11:30 | 2015-11-23 11:30 | CARRIER - 2ABB330A300 | 64 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | 7493F4F26A5F44E79BA7C0C737E6F9C0 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-2235 |  | 2015-08-03 | 2015-08-03 10:18 | 2015-08-03 10:18 | AMERICAN STANDARD - YCZ036F1M0BD | 160 | 0 | Yes | Yes | 25.1 | 20.2 | 4.9 | 7B0471551AEA431EADAD58C24AD5498F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rodeo | CA | 94572-1832 |  | 2015-07-29 | 2015-07-29 16:21 | 2015-07-29 16:21 | GOODMAN - GSX130361BA | 85 | 0 | Yes | Yes | 16.8 | 19.3 | -2.5 | 4BBB24C49E4E4B779B596737C02F32F9 |  | R410A | TXV |  | 0% | 1 | 0%
Rodeo | CA | 94572-1726 |  | 2015-08-03 | 2015-08-03 08:34 | 2015-08-03 08:34 | TRANE - 4TTX48A1000AA | 127 | 0 | Yes | Yes | 23.8 | 18.6 | 5.3 | 2B031D9F8D384182B13E8796D6302D2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-1338 |  | 2015-07-10 | 2015-07-10 12:15 | 2015-07-10 12:58 | PAYNE - PA101A048 | 106 | 0 | Yes | Yes | 30.3 | 20.4 | 9.9 | 05516D651FCF49A8912944DDB9F01CEA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5635 |  | 2015-08-19 | 2015-08-19 12:01 | 2015-08-19 12:01 | TRANE - 2TTR2048A1000AA | 120 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 0B7AC33ED65844DA8AA8DE6872732B98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-3583 |  | 2015-09-22 | 2015-09-22 10:34 | 2015-09-22 10:34 | CARRIER - 24ABB348A310 | 85 | 0 | Yes | Yes | 18.1 | 18.9 | -0.8 | 1710DC123843478D906FB14E4E0DB34F |  | R410A | TXV |  | 0% | 1 | 0%
Napa | CA | 94559-3583 |  | 2015-09-22 | 2015-09-22 10:58 | 2015-09-22 11:15 | CARRIER - 25HBA318A330 | 85 | 10.5 | Yes | Yes | 15.5 | 18.2 | -2.7 | 023E25B7F47D4EB694BD3E9ABF112853 |  | R410A | TXV |  | 12.35% | 0.87647 | 23.74% | [5 empty] | TXV | 12.35%
Fairfield | CA | 94533-5835 |  | 2015-07-08 | 2015-07-08 13:08 | 2015-07-08 13:08 | GE - UNK | 72 | 0 | Yes | Yes | 24.9 | 19.9 | 5 | BB56380378F34C029C9DFEA47EAE56FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5731 |  | 2015-07-17 | 2015-07-17 18:06 | 2015-07-17 18:06 | ARCOAIRE - CA9036VKCL | 97 | 0 | Yes | Yes | 25.1 | 21.5 | 3.6 | 76D2DD6FA893412B8DC58B26DC09894A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1628 |  | 2015-07-24 | 2015-07-24 10:10 | 2015-07-24 10:10 | TRANE - 2TTR3036A1000AA | 101 | 0 | Yes | Yes | 16.1 | 18.8 | -2.7 | 8E9182BDB5BB41F7AF7D079B040D3132 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4722 |  | 2015-08-20 | 2015-08-20 14:26 | 2015-08-20 14:26 | TRANE - TTD736B10041 | 80 | 0 | Yes | Yes | 18.5 | 21 | -2.5 | 073C1DA34A6D471EA95996C6B4D24C58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4151 |  | 2015-07-08 | 2015-07-08 10:28 | 2015-07-08 10:28 | LENNOX - 5175L06281 | 69 | 0 | Yes | Yes | 19.1 | 21 | -1.9 | 2965C6A4F68E46AE8292BF6BDF90B311 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4231 |  | 2015-10-07 | 2015-10-07 13:31 | 2015-10-07 13:31 | CARRIER - 48SS-036080311 | 85 | 0 | Yes | Yes | 19 | 20.3 | -1.3 | 2B9C602256124E459A7DB22F13DDFCA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5810 |  | 2015-07-08 | 2015-07-08 11:46 | 2015-07-08 11:46 | CARRIER - 38EN036300 | 88 | 0 | Yes | Yes | 19.8 | 22.4 | -2.6 | 3DB7EC9383B94E0B9A0DC9CD4A313ED2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1616 |  | 2015-08-07 | 2015-08-07 08:42 | 2015-08-07 08:42 | YORK - H1DE042S068 | 99 | 0 | Yes | Yes | 22.4 | 20.2 | 2.3 | 79B99465C9454BAC8BE8D3CBFF90613C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5938 |  | 2015-07-17 | 2015-07-17 12:46 | 2015-07-17 12:46 | OTHER - N2A342AKA300 | 104 | 0 | Yes | Yes | 19.5 | 20.5 | -1 | C5BD6B7C0AB64EFDB706FFF6DA3F956C |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5335 |  | 2015-10-26 | 2015-10-26 11:58 | 2015-10-26 11:58 | CARRIER - 24ABA336A300 | 85 | 0 | Yes | Yes | 14.5 | 15 | -0.5 | 13CE34BC036D462182ECAAD1FAE6365D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6808 |  | 2015-07-13 | 2015-07-13 08:22 | 2015-07-13 08:44 | CARRIER - 38ENO30300 | 86 | 8.5 | Yes | Yes | 16.4 | 18.8 | -2.4 | 6CF648FD66A24833879DCCD77E812736 |  | R22 | Non-TXV |  | 9.884% | 0.90116 | 18.99% | [5 empty] | Non-TXV | 9.884%
Napa | CA | 94558-4818 |  | 2015-09-30 | 2015-09-30 15:31 | 2015-09-30 15:31 | RUUD - UAND-036JA | 116 | 0 | Yes | Yes | 21 | 18.6 | 2.5 | 3B6CC665F11347DC97789950928711D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-2802 |  | 2015-08-05 | 2015-08-05 10:15 | 2015-08-05 10:15 | CARRIER - 38CK048330 | 112 | 0 | Yes | Yes | 22.7 | 20.5 | 2.2 | 0AAE9CC457C742919F15E752E8CB728C |  | R22 | TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1148 |  | 2015-09-03 | 2015-09-03 11:33 | 2015-09-03 11:33 | CARRIER - 38BRC042330 | 85 | 0 | Yes | Yes | 16.5 | 15.4 | 1.2 | 3A9355B8360049C593B79922FEB90560 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2541 |  | 2015-07-16 | 2015-07-16 12:00 | 2015-07-16 12:00 | TEMPSTAR - T2A330GKA100 | 83 | 0 | Yes | Yes | 17.3 | 19.3 | -2 | EA9F710692824948823A4DD9031A65C6 |  | R22 | TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-5344 |  | 2015-08-03 | 2015-08-03 13:07 | 2015-08-03 13:07 | OTHER - BRCS0301BC | 69 | 0 | Yes | Yes | 19.1 | 18.8 | 0.3 | 2CEC3D00332F4E9A8FB47C74C3E649AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4964 |  | 2015-07-14 | 2015-07-14 14:50 | 2015-07-14 14:50 | OTHER - CK36-1A | 73 | 0 | Yes | Yes | 16.7 | 19.2 | -2.5 | E5605E9022C747E2B5B1EDED8CD5420E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4637 |  | 2015-08-10 | 2015-08-10 14:37 | 2015-08-10 14:37 | TRANE - TTB042C100AR | 85 | 0 | Yes | Yes | 25.3 | 20.2 | 5.1 | 4FBA41864DC74C40ABFF47CCB947D923 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94583-4130 |  | 2015-08-05 | 2015-08-05 13:58 | 2015-08-05 13:58 | BDP - 589ANW024040ABAD | 57 | 0 | Yes | Yes | 27.1 | 24.7 | 2.4 | BD12FA18ADB64BBF8C9CDAF3A10524F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8227 |  | 2015-06-26 | 2015-06-26 13:51 | 2015-06-26 14:46 | HEIL - CA5048VKA1 | 178 | 0 | Yes | Yes | -0.4 | 18.7 | -19.1 | AC9A4F898506414B93FA21314100E8EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5555 |  | 2015-08-18 | 2015-08-18 12:01 | 2015-08-18 12:01 | GOODMAN - GSC130241FA | 77 | 0 | Yes | Yes | 25.3 | 21.3 | 4 | 6C91248883B04B98852D1BAF1A2082D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2775 |  | 2015-09-29 | 2015-09-29 15:13 | 2015-09-29 15:13 | CARRIER - 38CKCO42340 | 85 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | 96FD09F54ED648928E97C961FCF22799 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6461 |  | 2015-09-11 | 2015-09-11 14:03 | 2015-09-11 14:03 | CARRIER - UNK | 165 | 0 | Yes | Yes | 21.1 | 20.2 | 1 | C2CD4EE1F21B4F3385B6BB90BA5161AA |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1615 |  | 2015-08-11 | 2015-08-11 16:22 | 2015-08-11 16:22 | OTHER - ARCF36U01D | 112 | 0 | Yes | Yes | 20.8 | 19.3 | 1.5 | BDF03FC3A3394BAEAFE260B8C81F50CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7107 |  | 2015-07-30 | 2015-07-30 11:15 | 2015-07-30 11:39 | TRANE - BTD724A10001 | 68 | 3.7 | Yes | Yes | 25.1 | 19.3 | 5.8 | F6E1D1FD0F3645CE906A57DE6C0F9652 |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Antioch | CA | 94531-7130 |  | 2015-06-26 | 2015-06-26 09:43 | 2015-06-26 10:38 | PAYNE - 591ANX042000ASAA | 112 | 0 | Yes | Yes | 27 | 21.8 | 5.2 | C5B02881B77A49B3A20EEB06FE2103AF | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3248 |  | 2015-08-18 | 2015-08-18 15:10 | 2015-08-18 15:10 | GIBSON - JS5BD048KA | 126 | 0 | Yes | Yes | 15.4 | 18.2 | -2.8 | B4D2DBCD8DE846EBADDC5C5FD80C74B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7847 |  | 2015-07-28 | 2015-07-28 14:35 | 2015-07-28 14:35 | CARRIER - 38BRG036320 | 85 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 411D1D4FC02B4F8290625CD42909896D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-6110 |  | 2015-07-27 | 2015-07-27 10:22 | 2015-07-27 10:22 | GOODMAN - CRT36-1A | 85 | 0 | Yes | Yes | 18.8 | 20.3 | -1.5 | DE9F285EFCFC4BACACAA5241BF883AF9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3315 |  | 2015-08-05 | 2015-08-05 11:43 | 2015-08-05 11:43 | CARRIER - 38TRA048360 | 152 | 0 | Yes | Yes | 22.2 | 19.1 | 3.2 | 1798BDAE113C4F9FB1A97AB9A2A34C26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3315 |  | 2015-08-05 | 2015-08-05 12:12 | 2015-08-05 12:12 | CARRIER - PA10JA036-C | 72 | 0 | Yes | Yes | 9 | 17 | -8 | 354CB07831E04CFA89EAFAA33BB6D5A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4891 |  | 2015-09-16 | 2015-09-16 12:01 | 2015-09-16 12:20 | GOODMAN - GPH1430M41AA | 128 | 37 | Yes | Yes | 20.9 | 22.6 | -1.7 | 9629B31F0D5C4ECE8820E7314F67728C |  | R410A | Non-TXV |  | 28.91% | 0.71094 | 55.55% | [5 empty] | Non-TXV | 28.91%
Bakersfield | CA | 93305-1148 |  | 2015-08-31 | 2015-08-31 09:33 | 2015-08-31 09:33 | DAY & NIGHT - N/A | 85 | 0 | Yes | Yes | 18.7 | 20.4 | -1.7 | FF3DDF9602D042BC93859E5C152F1DE0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1148 |  | 2015-09-03 | 2015-09-03 11:49 | 2015-09-03 11:49 | BRYANT - 583ANW024040NBAD | 59 | 0 | Yes | Yes | 19 | 19.4 | -0.4 | 8CE335A78EBC435CAE8F4409F45EDD49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1904 |  | 2015-08-17 | 2015-08-17 09:21 | 2015-08-17 09:21 | YORK - X2DA048506A | 124 | 0 | Yes | Yes | 17.3 | 12.8 | 4.5 | 6ED695B649334542A82AEB386F046388 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1014 |  | 2015-08-10 | 2015-08-10 09:40 | 2015-08-10 10:09 | RUUD - UAKB-042JAZ | 85 | 7.2 | Yes | Yes | 24.5 | 18.8 | 5.7 | 104E668A540C4B5691FE4E63C797D419 |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Pittsburg | CA | 94565-6338 |  | 2015-08-31 | 2015-08-31 15:13 | 2015-08-31 15:13 | CARRIER - 38CKC036-341 | 70 | 0 | Yes | Yes | 19.6 | 20.9 | -1.3 | E1737ED306AA41F7A14FF0A7E91660FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1929 |  | 2015-10-19 | 2015-10-19 13:22 | 2015-10-19 13:22 | AMERICAN STANDARD - 2YCX3048A1096AA | 85 | 0 | Yes | Yes | 24.2 | 20.4 | 3.8 | 5544F9D7BE4D45A197833FAE3F4757F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5369 |  | 2015-08-20 | 2015-08-20 10:46 | 2015-08-20 11:11 | CARRIER - 38TH03630P0 | 85 | 9.6 | Yes | Yes | 23.6 | 18.8 | 4.8 | 6FFBAC75177145B585457A867010BDC8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 11.29% | 0.88706 | 21.7% | [5 empty] | Non-TXV | 11.29%
Bay Point | CA | 94565-3121 |  | 2015-08-14 | 2015-08-14 15:22 | 2015-08-14 15:45 | PAYNE - PA12NA048-A | 167 | 15.5 | Yes | Yes | 25.4 | 19.5 | 5.9 | 7AAA0675751C4191B198948C3B01AD92 |  | R22 | TXV |  | 9.281% | 0.90719 | 17.84% | [5 empty] | TXV | 9.281%
Vallejo | CA | 94590-3969 |  | 2015-07-22 | 2015-07-22 09:39 | 2015-07-22 09:39 | DAY & NIGHT - 593CJ048-A | 85 | 0 | Yes | Yes | 16.4 | 17.7 | -1.3 | 1FC81B3C9A6041E4B27B0830117B656D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-2632 |  | 2015-08-04 | 2015-08-04 09:20 | 2015-08-04 09:20 | GIBSON - JS5BD-060K | 232 | 0 | Yes | Yes | 24.9 | 19.9 | 5 | BEAE9D89B9914F3A8055B676DCAD63E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-3141 |  | 2015-09-09 | 2015-09-09 13:12 | 2015-09-09 13:12 | AMERICAN STANDARD - YCY036G1M0AC | 131 | 0 | Yes | Yes | 19.3 | 21.8 | -2.5 | 567B187F129B457DB9160BC077AA00EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4053 |  | 2015-07-22 | 2015-07-22 15:38 | 2015-07-22 15:38 | AMERICAN STANDARD - TTRO36C100A0 | 92 | 0 | Yes | Yes | 25.1 | 20.2 | 5 | 9786DDFA58114EA184D146FFD1434B2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winters | CA | 95694-1506 |  | 2015-10-28 | 2015-10-28 15:20 | 2015-10-28 15:20 | BRYANT - 113ANA042-C | 92 | 0 | Yes | Yes | 17.9 | 20.3 | -2.4 | 848173A1918E4E8D9360B724A5632B10 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6242 |  | 2015-07-02 | 2015-07-02 10:55 | 2015-07-02 10:55 | RHEEM - RACA024ABO | 85 | 0 | Yes | Yes | 24.3 | 20.2 | 4.1 | 85B14789F8AF410FB2A8E090AD964826 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5338 |  | 2015-07-29 | 2015-07-29 09:52 | 2015-07-29 09:52 | CARRIER - 24ABC636A300 | 85 | 0 | Yes | Yes | 23.9 | 21.9 | 2 | ADD47E2ECE674C30BDF94F4EB1DF19A7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1657 |  | 2015-09-23 | 2015-09-23 13:26 | 2015-09-23 13:36 | BDP - 585GJW024040ABAE | 54 | 4.2 | Yes | Yes | 20.2 | 22.8 | -2.6 | 0C39D1989D8741098C3CD4AAF2378927 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Bakersfield | CA | 93307-2887 |  | 2015-09-01 | 2015-09-01 09:16 | 2015-09-01 09:16 | RHEEM - RRNA-B042JK08X | 104 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 5F59F55490254DD29652FC671ED9FFCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6154 |  | 2015-09-10 | 2015-09-10 11:06 | 2015-09-10 11:22 | BRYANT - 582ANW024060AAAD | 55 | 9.8 | Yes | Yes | 20.1 | 22.1 | -2 | 6A1C6B652136465E928993EC1ECAB069 |  | R22 | Non-TXV |  | 17.82% | 0.82182 | 34.24% | [5 empty] | Non-TXV | 17.82%
Bakersfield | CA | 93307-6932 |  | 2015-09-01 | 2015-09-01 09:43 | 2015-09-01 09:43 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 20.9 | 20.9 | 0 | 39CA3F4D520946D4BB1C9DEEA3DFEE31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6236 |  | 2015-09-01 | 2015-09-01 11:33 | 2015-09-01 11:33 | YORK - D2NP048N09006NXA | 132 | 0 | Yes | Yes | 20 | 18.3 | 1.7 | 9C1A6C52BB5440FCB96F453F6A2DB096 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4176 |  | 2015-08-13 | 2015-08-13 11:17 | 2015-08-13 11:17 | GOODMAN - GPG1360090M41AC | 185 | 0 | Yes | Yes | 21.3 | 23.1 | -1.8 | F87F230FF5AC4834A7F6452D41B746A1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3044 |  | 2015-08-28 | 2015-08-28 11:53 | 2015-08-28 11:53 | OTHER - N/A | 85 | 0 | Yes | Yes | 20.4 | 22 | -1.6 | 62ED07FE6F9548148D855D6CBFDA1D11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5745 |  | 2015-07-27 | 2015-07-27 15:37 | 2015-07-27 15:37 | ALLEGIANCE - 2A7A2030A1000AA | 64 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | ABA7051DF3A146C499745688F80BFA31 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2137 |  | 2015-07-24 | 2015-07-24 09:36 | 2015-07-24 09:36 | RHEEM - RRNL-B036JK06X | 93 | 0 | Yes | Yes | 22.3 | 19.6 | 2.8 | B8342424751D4C9A932D4E5B03379F45 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5608 |  | 2015-07-28 | 2015-07-28 13:53 | 2015-07-28 13:53 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 23.5 | 19.6 | 3.9 | 4552406033674F82BC16ED6FA318C35E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4657 |  | 2015-07-21 | 2015-07-21 09:21 | 2015-07-21 09:21 | YORK - D1NHO30NO3686A | 69 | 0 | Yes | Yes | 19.8 | 18.7 | 1.1 | FF9DE93F1C9040E39BF9DA66480680FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5344 |  | 2015-09-10 | 2015-09-10 09:06 | 2015-09-10 09:06 | UNITARY PRODUCTS GROUP - PGAD30D1K6 | 78 | 0 | Yes | Yes | 21.5 | 20.6 | 0.9 | 320E994F868A4A248E5B90BAB999A4FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5963 |  | 2015-07-31 | 2015-07-31 13:43 | 2015-07-31 13:43 | GE - BTB930A100A1 | 53 | 0 | Yes | Yes | 20.5 | 19.3 | 1.2 | 1885E69163684C64B88B65711A30F5C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9203 |  | 2015-08-03 | 2015-08-03 08:58 | 2015-08-03 08:58 | WEATHER KING - 12AJA3001 | 96 | 0 | Yes | Yes | 19 | 21.3 | -2.3 | 8BBE717D56704F93A33C5D4B3A4A9E27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-1961 |  | 2015-07-20 | 2015-07-20 10:04 | 2015-07-20 10:04 | RHEEM - RAMA-048JAZ | 85 | 0 | Yes | Yes | 21.8 | 19 | 2.8 | E01E6BF2F92143ACAB8239E1F14E6E56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5243 |  | 2015-10-13 | 2015-10-13 14:35 | 2015-10-13 14:35 | ARCOAIRE - N4A336AKB300 | 85 | 0 | Yes | Yes | 18.9 | 18.6 | 0.3 | B779CD262CC34B74AE32272B214956DF |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6417 |  | 2015-09-28 | 2015-09-28 15:24 | 2015-09-28 15:24 | ICP - PGC042K080E | 86 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | BC4A1046C347474D83121C83E298EB1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-3930 |  | 2015-07-24 | 2015-07-24 11:21 | 2015-07-24 11:21 | CARRIER - 38CKC060370 | 131 | 0 | Yes | Yes | 24.5 | 18.6 | 6 | 0BFA145E41404727BA93FF410AE74820 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7051 |  | 2015-08-17 | 2015-08-17 10:45 | 2015-08-17 11:19 | OTHER - N/A | 85 | 6.9 | Yes | Yes | 21.4 | 23.1 | -1.7 | 8131879FE095402AAAF3CA8F31B1D70A |  | R22 | Non-TXV |  | 8.118% | 0.91882 | 15.6% | [5 empty] | Non-TXV | 8.118%
Fairfield | CA | 94533-2729 |  | 2015-07-29 | 2015-07-29 12:15 | 2015-07-29 12:15 | TRANE - 2TTR2042B1000AA | 86 | 0 | Yes | Yes | 18.8 | 19 | -0.2 | C4D8526CFF074588A5E8D56C7465256E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5610 |  | 2015-07-28 | 2015-07-28 15:14 | 2015-07-28 15:14 | YORK - D2NP036N05606NXA | 108 | 0 | Yes | Yes | 23.2 | 21.2 | 2 | CE8FA2D559E54581949F721041935580 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4419 |  | 2015-07-29 | 2015-07-29 09:18 | 2015-07-29 09:18 | OTHER - N/A | 90 | 0 | Yes | Yes | 20.2 | 19.8 | 0.4 | E7CBAE3455564927BE35A86A7FF65A5A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5522 |  | 2015-07-13 | 2015-07-13 14:20 | 2015-07-13 14:20 | GOODMAN - CFPJ42 | 160 | 0 | Yes | Yes | 14.6 | 16.4 | -1.8 | 6B071096E3F044F7BC3A401E8723E440 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3404 |  | 2015-07-15 | 2015-07-15 14:28 | 2015-07-15 14:28 | GOODMAN - GSX130301BC | 69 | 0 | Yes | Yes | 21.5 | 18.2 | 3.3 | 3A157CF2EC834DA1BCD21B61B9AE8585 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9824 |  | 2015-08-03 | 2015-08-03 09:51 | 2015-08-03 09:51 | YORK - H2RC042S06G | 109 | 0 | Yes | Yes | 21.6 | 22.5 | -0.9 | ACFFAF6E80CD4417B8C42797EFD30887 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2065 |  | 2015-07-22 | 2015-07-22 14:34 | 2015-07-22 14:34 | CARRIER - 38BRC030320 | 85 | 0 | Yes | Yes | 17.2 | 17.7 | -0.5 | 50529AD21D674533953F6AB30A014A73 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-6710 |  | 2015-07-02 | 2015-07-02 09:27 | 2015-07-02 09:27 | RUUD - UARL036JEZ | 150 | 0 | Yes | Yes | 19.9 | 18.1 | 1.8 | 6CE62B994E59499A91B1BD05132239E7 |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5149 |  | 2015-10-07 | 2015-10-07 11:20 | 2015-10-07 11:20 | GUARDIAN - GCGD42S21S2C | 85 | 0 | Yes | Yes | 16 | 18.7 | -2.7 | 8426C943FC604E8695CF5F7BAC34DE83 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-3210 |  | 2015-08-05 | 2015-08-05 08:17 | 2015-08-05 08:17 | ALLEGIANCE - 7A0036A100A2 | 95 | 0 | Yes | Yes | 19.7 | 20.1 | -0.4 | 36C151897AC347908B3B70E15058B656 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-1423 |  | 2015-10-07 | 2015-10-07 13:26 | 2015-10-07 13:26 | HEIL - CA5036VKA1 | 105 | 0 | Yes | Yes | 19.1 | 17.7 | 1.4 | 4F953B565A99455C9DCEA10D6D9BAC7B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1984 |  | 2015-10-08 | 2015-10-08 13:12 | 2015-10-08 13:47 | CARRIER - 38CKC048360 | 98 | 11 | Yes | Yes | 17.7 | 18.7 | -1 | D7E47239EF03474194E28E4FD5305872 |  | R22 | TXV |  | 11.22% | 0.88776 | 21.57% | [5 empty] | TXV | 11.22%
Fairfield | CA | 94533-3243 |  | 2015-09-10 | 2015-09-10 10:52 | 2015-09-10 10:52 | AMERICAN STANDARD - 2YCX3036A1096AA | 82 | 0 | Yes | Yes | 19.5 | 19.2 | 0.3 | A0424C9E56064B7A89E8C107011F3C53 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7224 |  | 2015-09-01 | 2015-09-01 10:32 | 2015-09-01 10:32 | OTHER - AC036X1021A | 63 | 0 | Yes | Yes | 18.9 | 21.3 | -2.4 | EE61A08AC3914691BD4DA242F0F1CD14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Alamo | CA | 94507-2618 |  | 2015-08-18 | 2015-08-18 15:43 | 2015-08-18 16:04 | RHEEM - UNK | 85 | 4.5 | Yes | Yes | 23.1 | 18.1 | 5 | 51C62A4E4A0A444DAFEC43156967C6F7 | Remove refrigerant: 5 oz | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Fairfield | CA | 94533-2728 |  | 2015-08-03 | 2015-08-03 11:11 | 2015-08-03 11:11 | CARRIER - UNK | 85 | 0 | Yes | Yes | 17.1 | 18.7 | -1.6 | 437F6CB1646A48F893E5195CCF439A8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6790 |  | 2015-10-12 | 2015-10-12 16:02 | 2015-10-12 16:02 | - UNKNOWN | 87 | 0 | Yes | Yes | 20.4 | 21.4 | -1 | A9D17A01348442A0ADC27D95566C46BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-6648 |  | 2015-10-06 | 2015-10-06 13:24 | 2015-10-06 13:24 | OTHER - CBN024- | 85 | 0 | Yes | Yes | 15 | 17.2 | -2.2 | FE2EFCCD849241A5BA828E429F2E3881 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4609 |  | 2015-11-19 | 2015-11-19 15:21 | 2015-11-19 15:21 | LENNOX - UNK | 85 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | D4F923BD908E49DA8D5782842275CCD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3349 |  | 2015-10-16 | 2015-10-16 16:29 | 2015-10-16 16:29 | PAYNE - PA10JA030-C | 77 | 0 | Yes | Yes | 23.6 | 20.4 | 3.2 | C8E9F7BA223E49A1A115B3731EE1FA61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4556 |  | 2015-09-25 | 2015-09-25 11:43 | 2015-09-25 11:43 | PAYNE - PA13NR024-J | 85 | 0 | Yes | Yes | 15.2 | 17.4 | -2.2 | 5F1F8484ED5F4A199AD7E7A15D69DE81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3767 |  | 2015-07-08 | 2015-07-08 15:26 | 2015-07-08 15:26 | CARRIER - 24ABB336W340 | 85 | 0 | Yes | Yes | 16.5 | 16.4 | 0.1 | 280E8C50372E4167A4C43A15BC04E390 |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2000 |  | 2015-07-16 | 2015-07-16 09:00 | 2015-07-16 09:00 | CARRIER - 561CJ024C | 69 | 0 | Yes | Yes | 21.9 | 17.7 | 4.2 | 9F3FDDC5D53047D6BD03B62870F53622 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4711 |  | 2015-07-30 | 2015-07-30 16:08 | 2015-07-30 16:08 | YORK - TCGD42S21S1HA | 72 | 0 | Yes | Yes | 20.2 | 21.5 | -1.3 | 43EDCE37E64748E6A8521356D1CD5C8E |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3922 |  | 2015-10-27 | 2015-10-27 16:41 | 2015-10-27 16:41 | TRANE - YCC018F1L0BE | 56 | 0 | Yes | Yes | 22.1 | 18.7 | 3.4 | 7312620EE3D54D9DB61D3D47F6AE3CE0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5210 |  | 2015-07-13 | 2015-07-13 13:31 | 2015-07-13 13:31 | TRANE - 4TTX6036B1000AA | 106 | 0 | Yes | Yes | 28.1 | 22.5 | 5.6 | 717BD4D7F7D942F9BE1ADCB708FD9DC0 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4236 |  | 2015-09-10 | 2015-09-10 08:22 | 2015-09-10 08:22 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 21.7 | 18.9 | 2.8 | F4CA284B21C946698889E1417E2B1EDE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6158 |  | 2015-09-10 | 2015-09-10 11:21 | 2015-09-10 11:52 | OTHER - N/A | 55 | 9.9 | Yes | Yes | 23.1 | 21.8 | 1.3 | A2758E9B7FD44EAC814791730C172FA0 |  | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Bakersfield | CA | 93306-5646 |  | 2015-07-28 | 2015-07-28 14:03 | 2015-07-28 14:03 | PAYNE - PY1PNB036060ABAA | 70 | 0 | Yes | Yes | 25.7 | 19.9 | 5.8 | 9A0A1D43432C4171B940CDAA74B9955E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7755 |  | 2015-07-17 | 2015-07-17 09:55 | 2015-07-17 10:11 | LENNOX - 13ACC-048-230-01 | 158 | 18.7 | Yes | Yes | 26.1 | 20.4 | 5.7 | 781AEA8AD58446D69AF9EFB43DFAE8F6 |  | R22 | Non-TXV |  | 11.84% | 0.88165 | 22.75% | [5 empty] | Non-TXV | 11.84%
Bakersfield | CA | 93306-4715 |  | 2015-09-17 | 2015-09-17 09:03 | 2015-09-17 09:48 | YORK - D6NZ03N05606NXA | 85 | 23.7 | Yes | Yes | 24 | 19.1 | 4.9 | 3340E4C6516944AF8B291F204D0DEA80 |  | R410A | Non-TXV |  | 27.88% | 0.72118 | 53.58% | [5 empty] | Non-TXV | 27.88%
Bakersfield | CA | 93304-4610 |  | 2015-07-24 | 2015-07-24 09:15 | 2015-07-24 09:15 | CARRIER - 48XPN036060311 | 152 | 0 | Yes | Yes | 23.1 | 20.1 | 3 | C97FF73BC5D94AC7A801C26D2F62E4FA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6028 |  | 2015-07-06 | 2015-07-06 14:00 | 2015-07-06 14:00 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 19.3 | 19.5 | -0.2 | 9EA52092FA654CB3B36C907F8987278B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4731 |  | 2015-07-16 | 2015-07-16 09:43 | 2015-07-16 10:06 | BDP - 561CJO36-C | 85 | 16.1 | Yes | Yes | 21.9 | 19.8 | 2.1 | 777CAEA0A2EB47FD88E82EE83DA90FB2 |  | R22 | TXV |  | 18.94% | 0.81059 | 36.4% | [5 empty] | TXV | 18.94%
Bakersfield | CA | 93306-6649 |  | 2015-07-28 | 2015-07-28 09:04 | 2015-07-28 09:04 | AMERICAN STANDARD - YCY048F1H0AA | 178 | 0 | Yes | Yes | 19.1 | 21.9 | -2.8 | FC64273BE99E4FBF831429329ADE88B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-4858 |  | 2015-09-09 | 2015-09-09 09:25 | 2015-09-09 09:25 | UNITARY PRODUCTS GROUP - TCGD48S21S1A | 75 | 0 | Yes | Yes | 20.3 | 19.9 | 0.4 | 69DA80C54BB8423DA2DDE2E4835DD85E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1221 |  | 2015-07-15 | 2015-07-15 13:09 | 2015-07-15 13:09 | AMANA - ASX140301CC | 93 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | AD6BC9619883476EA5EB88A38EA63A14 |  | R410A | TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-5312 |  | 2015-09-04 | 2015-09-04 08:37 | 2015-09-04 08:37 | RHEEM - RAKA-48JAZ | 142 | 0 | Yes | Yes | 30.2 | 19.9 | 10.3 | 1354ADBC3B794A29BB89B603225AE07C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2019 |  | 2015-10-20 | 2015-10-20 13:46 | 2015-10-20 13:46 | LENNOX - 13ACX03623017 | 84 | 0 | Yes | Yes | 21.5 | 21.7 | -0.2 | EF573AF6069A4CE482733C7813FCF504 |  | R410A | TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4320 |  | 2015-10-28 | 2015-10-28 11:38 | 2015-10-28 11:38 | LENNOX - GCS20-030-75-2P | 74 | 0 | Yes | Yes | 16.4 | 18.2 | -1.8 | 09C8823BED2D4199B65FD102710D9BB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94534-1470 |  | 2015-07-28 | 2015-07-28 11:01 | 2015-07-28 11:01 | PAYNE - PA13NR036K | 85 | 0 | Yes | Yes | 17.3 | 18.8 | -1.5 | 87BFF2086F8648A78186456C0283F106 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6822 |  | 2015-07-15 | 2015-07-15 12:11 | 2015-07-15 12:11 | UNITARY PRODUCTS GROUP - BRCSO421BD | 85 | 0 | Yes | Yes | 20.7 | 18.8 | 1.9 | EA808A3D684B4ADEA2FAD0BD28CBACF6 |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3220 |  | 2015-08-06 | 2015-08-06 11:48 | 2015-08-06 11:48 | TRANE - 4TTR3042D1000AB | 98 | 0 | Yes | Yes | 14.9 | 18.2 | -3.3 | 8B25CFBE7CAA4BD99BE86A77A13C85CA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4045 |  | 2015-07-17 | 2015-07-17 08:24 | 2015-07-17 08:24 | OTHER - HAC036AKAS | 80 | 0 | Yes | Yes | 16.9 | 17.6 | -0.7 | 6CB78870F59D4A52BD2097EC18D66684 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-1509 |  | 2015-07-16 | 2015-07-16 09:34 | 2015-07-16 09:34 | ARCOAIRE - NAC030AKA1 | 85 | 0 | Yes | Yes | 18.7 | 18.5 | 0.2 | 8AF515FA1C8145AF83400821D1DCEAC2 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9127 |  | 2015-08-21 | 2015-08-21 13:19 | 2015-08-21 13:19 | GOODMAN - CK42-1C | 86 | 0 | Yes | Yes | 16 | 18.9 | -2.9 | 4BAC308D1EC241268F88A312ED065975 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5718 |  | 2015-07-13 | 2015-07-13 11:10 | 2015-07-13 11:10 | RHEEM - UNK | 85 | 0 | Yes | Yes | 21.8 | 18.6 | 3.2 | C44B2936BF86495EB4B8FCD2C00C6A09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3304 |  | 2015-07-22 | 2015-07-22 10:12 | 2015-07-22 10:12 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 20.7 | 18.2 | 2.5 | 2D46CF9BFED74857895BE6EBC1B59A21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4221 |  | 2015-07-31 | 2015-07-31 15:03 | 2015-07-31 15:03 | CARRIER - 24AB336A310 | 84 | 0 | Yes | Yes | 18.6 | 19.9 | -1.3 | 12EFBEE911B44C5E89324A40A299E5AF |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6017 |  | 2015-08-26 | 2015-08-26 13:02 | 2015-08-26 13:02 | RHEEM - UNK | 102 | 0 | Yes | Yes | 20 | 20.2 | -0.1 | C5EE76E6DC7647589A850A8FB27C7D62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9066 |  | 2015-07-02 | 2015-07-02 12:41 | 2015-07-02 13:20 | YORK - H1RA042S06D | 84 | 3.3 | Yes | Yes | 24.9 | 23.5 | 1.4 | F99D919AFA6E416D9A0FD5368F4671DF |  | R22 | Non-TXV |  | 3.929% | 0.96071 | 7.55% | [5 empty] | Non-TXV | 3.929%
Fairfield | CA | 94533-5240 |  | 2015-08-10 | 2015-08-10 13:30 | 2015-08-10 13:30 | CARRIER - 24ABA336A0031010 | 85 | 0 | Yes | Yes | 17.7 | 18.6 | -0.9 | 2635B112F6B9453982A4CCB44567E2CC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9021 |  | 2015-07-13 | 2015-07-13 12:13 | 2015-07-13 12:13 | GOODMAN - CK60-1C | 85 | 0 | Yes | Yes | 24.6 | 20.2 | 4.4 | D22748BE431C4165BA3BF3817AF745FF |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4512 |  | 2015-07-29 | 2015-07-29 10:19 | 2015-07-29 10:19 | CARRIER - 38BR048300 | 168 | 0 | Yes | Yes | 19.5 | 21.8 | -2.3 | 9B0D117940E54B129172EDAF0B42B361 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2785 |  | 2015-10-19 | 2015-10-19 15:01 | 2015-10-19 15:01 | PAYNE - UNKNOWN | 105 | 0 | Yes | Yes | 21.5 | 21.8 | -0.3 | D0E6EF8E69374A0A9EFEE2C627257E3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2954 |  | 2015-08-10 | 2015-08-10 15:17 | 2015-08-10 15:17 | CARRIER - 3ABRO42300 | 85 | 0 | Yes | Yes | 18.9 | 19.9 | -1 | 350E38D8403F4B4D855961A11A2E4F61 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4730 |  | 2015-07-24 | 2015-07-24 13:20 | 2015-07-24 13:20 | PAYNE - UNK | 85 | 0 | Yes | Yes | 17.1 | 18.8 | -1.7 | 9821CDFC8E0F439AB57955BFF4E7C6DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5548 |  | 2015-08-18 | 2015-08-18 09:29 | 2015-08-18 09:29 | OTHER - AT24B10 | 51 | 0 | Yes | Yes | 18.1 | 19.8 | -1.7 | 5CF982F0D0934AA485526FA2596947E7 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-5611 |  | 2015-07-29 | 2015-07-29 14:02 | 2015-07-29 14:02 | DAY & NIGHT - 565DJ048 | 125 | 0 | Yes | Yes | 21.8 | 22.4 | -0.6 | 3E563324F5AA4F88AF0FAC4387F50C04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-5230 |  | 2015-07-15 | 2015-07-15 14:37 | 2015-07-15 14:37 | DAY & NIGHT - UKNOWN | 76 | 0 | Yes | Yes | 16.8 | 19.3 | -2.5 | 714BE8A607D0451F99161B2CBBE1B744 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-4081 |  | 2015-07-23 | 2015-07-23 15:59 | 2015-07-23 15:59 | GOODMAN - CKJ601C | 149 | 0 | Yes | Yes | 18.2 | 19.3 | -1.1 | 8D57AD8D402A499D9186A03B1FD66F33 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4642 |  | 2015-08-20 | 2015-08-20 10:37 | 2015-08-20 10:37 | DAY & NIGHT - 569DJ036 | 110 | 0 | Yes | Yes | 16.7 | 16.7 | 0 | CC366EF2144B44D7B60B835F077FDE2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-3114 |  | 2015-10-19 | 2015-10-19 09:26 | 2015-10-19 09:26 | AMANA - ER0F36-0913 | 85 | 0 | Yes | Yes | 14.9 | 17.7 | -2.8 | 5A58B4FF2191432188730F2AEAC8F535 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2714 |  | 2015-09-09 | 2015-09-09 08:43 | 2015-09-09 09:13 | GOODMAN - PGB024050-1 | 54 | 14.4 | Yes | Yes | 19.4 | 21.8 | -2.4 | E6344C0FD1FB4BA5A85E0D7BACE191A1 |  | R22 | Non-TXV |  | 26.67% | 0.73333 | 51.25% | [5 empty] | Non-TXV | 26.67%
Byron | CA | 94505-9201 |  | 2015-08-04 | 2015-08-04 14:03 | 2015-08-04 14:03 | HEIL - HCA8A36V802 | 60 | 0 | Yes | Yes | 22.2 | 21.3 | 0.9 | 78947213771A45D29883B42FF783A8F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1856 |  | 2015-07-24 | 2015-07-24 09:54 | 2015-07-24 09:54 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 20.2 | 16.4 | 3.8 | 24545C2784D3448E97AD5A1990638D08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6050 |  | 2015-09-10 | 2015-09-10 10:22 | 2015-09-10 11:04 | YORK - DAYH-F036N070C | 108 | 17.7 | Yes | Yes | 21.5 | 20.4 | 1.1 | 0D366B84CEC74AFEACC79CE3A49F0C30 |  | R22 | Non-TXV |  | 16.39% | 0.83611 | 31.5% | [5 empty] | Non-TXV | 16.39%
Woodland | CA | 95695-4433 |  | 2015-11-04 | 2015-11-04 09:56 | 2015-11-04 09:56 | PAYNE - PA13NA042-B | 103 | 0 | Yes | Yes | 25.2 | 22.3 | 2.9 | 8975FA98903741C9B67E8B8A3E951530 |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2742 |  | 2015-08-26 | 2015-08-26 16:32 | 2015-08-26 16:32 | TEMPSTAR - TCAA036AKA4 | 80 | 0 | Yes | Yes | 25.5 | 21.4 | 4.1 | F22FBFE037C74B1D97FB24701FE35A57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4008 |  | 2015-07-29 | 2015-07-29 13:08 | 2015-07-29 13:08 | PAYNE - PY3GNAA30040NA | 99 | 0 | Yes | Yes | 23.1 | 22.4 | 0.7 | 97FB39843959426DB24B4C09BB2B0948 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1929 |  | 2015-08-03 | 2015-08-03 12:45 | 2015-08-03 12:45 | ICP - GPCM030K060D | 54 | 0 | Yes | Yes | 22.4 | 21.2 | 1.2 | 4184339974254E229774D1211256C79F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4858 |  | 2015-07-24 | 2015-07-24 11:33 | 2015-07-24 11:33 | AMANA - APG13360451AC | 112 | 0 | Yes | Yes | 20.5 | 15 | 5.5 | 84EE600DEA1D4BC5B25FE0CD4075DC39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5795 |  | 2015-07-29 | 2015-07-29 09:33 | 2015-07-29 09:33 | NORDYNE - GS3BA-030KA | 68 | 0 | Yes | Yes | 20.2 | 21.3 | -1.1 | 1E93CAEDB35F43CCB9B572D5C7CAA8D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3322 |  | 2015-07-28 | 2015-07-28 11:36 | 2015-07-28 11:36 | YORK - D6NZ036N05606NXA | 85 | 0 | Yes | Yes | 26.8 | 21 | 5.8 | A54BFDF251FF4D01B5D01994AEFBF5A0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1234 |  | 2015-08-31 | 2015-08-31 11:53 | 2015-08-31 11:53 | TRANE - 2TTB303 | 88 | 0 | Yes | Yes | 15.7 | 18.7 | -3 | 777B01773FB6496D8FC2DF8E20E0C571 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-2507 |  | 2015-09-03 | 2015-09-03 13:00 | 2015-09-03 13:00 | CARRIER - PA10JA030000AAA | 72 | 0 | Yes | Yes | 20 | 21 | -1 | 840F80244A694FF1921C78463A2B368A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7117 |  | 2015-09-15 | 2015-09-15 11:17 | 2015-09-15 11:17 | YORK - UNK | 64 | 0 | Yes | Yes | 17.6 | 19.7 | -2.1 | A1535A25BC6D4B248D7FD8454E834F61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-6451 |  | 2015-09-30 | 2015-09-30 13:28 | 2015-09-30 13:28 | BRYANT - 561CJ024-D | 85 | 0 | Yes | Yes | 15.2 | 18.2 | -3 | 4785B2FAA34C40EABF31758E883F0397 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6034 |  | 2015-06-30 | 2015-06-30 09:23 | 2015-06-30 09:23 | CONCORD - 2AC13L36P-2B | 128 | 0 | Yes | Yes | 18.3 | 19.5 | -1.2 | A69E184B173E418D9487F03BE0EA573D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-4433 |  | 2015-10-20 | 2015-10-20 09:32 | 2015-10-20 09:32 | DAY & NIGHT - 597CN042-D | 112 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | 67A986909DF14E0494A42C4FF4581240 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1794 |  | 2015-08-10 | 2015-08-10 14:10 | 2015-08-10 14:10 | YORK - H1RA048S06G | 117 | 0 | Yes | Yes | 18.2 | 19.7 | -1.5 | 814595094EA3448E9FFC0A56ECAC69A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1794 |  | 2015-08-10 | 2015-08-10 14:25 | 2015-08-10 14:25 | YORK - H2RC036S06G | 83 | 0 | Yes | Yes | 16.7 | 18.9 | -2.2 | 003BFE289D904A57A434CD531213FB5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4625 |  | 2015-07-10 | 2015-07-10 12:28 | 2015-07-10 12:28 | BRYANT - 563CN042E | 85 | 0 | Yes | Yes | 22.6 | 22.9 | -0.3 | 2ECF7CD519F24E17B6B0F00A28CB12F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1908 |  | 2015-08-17 | 2015-08-17 12:20 | 2015-08-17 12:20 | HEIL - CA3042VKA1 | 99 | 0 | Yes | Yes | 27.8 | 22.1 | 5.7 | B3F9853A1FA74B3DBA31D3EDDC0C9857 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2430 |  | 2015-07-08 | 2015-07-08 15:05 | 2015-07-08 15:31 | GE - BTB948A100A | 141 | 14.4 | Yes | Yes | 22.5 | 20.4 | 2.1 | 7978190723E84F3C845D8232BA1F67D6 |  | R22 | Non-TXV |  | 10.21% | 0.89787 | 19.63% | [5 empty] | Non-TXV | 10.21%
Antioch | CA | 94509-5068 |  | 2015-08-14 | 2015-08-14 10:05 | 2015-08-14 10:05 | OTHER - H1RDO36S06G | 145 | 0 | Yes | Yes | 22.6 | 19.3 | 3.3 | 9CDCF634FB524A948B144AC86B3D4F15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8033 |  | 2015-09-11 | 2015-09-11 12:32 | 2015-09-11 12:49 | OTHER - PA13NH060 J | 165 | 8 | Yes | Yes | 21.8 | 21 | 0.8 | 99A056D7C0CA4B048DAB28A2A93E3AE2 |  | R22 | TXV |  | 4.848% | 0.95152 | 9.318% | [5 empty] | TXV | 4.848%
Napa | CA | 94558-6488 |  | 2015-09-11 | 2015-09-11 15:27 | 2015-09-11 15:27 | CARRIER - 38BRC036340 | 85 | 0 | Yes | Yes | 18.4 | 16.6 | 1.8 | 2AEA0E16DA424F2B9EAFFE285BF9C492 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winters | CA | 95694-1902 |  | 2015-10-28 | 2015-10-28 13:19 | 2015-10-28 13:19 | RHEEM - RRNL-B48JK08X | 161 | 0 | Yes | Yes | 19.2 | 17.7 | 1.5 | 66859A235CD2490DA2550AE737FB192D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1904 |  | 2015-07-30 | 2015-07-30 10:28 | 2015-07-30 10:28 | ICP - PGD336060K001C1 | 102 | 0 | Yes | Yes | 28.6 | 22.6 | 6 | A84EAE84F64443169FAA6A23C2884929 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6471 |  | 2015-10-06 | 2015-10-06 09:49 | 2015-10-06 09:49 | RHEEM - N/A | 85 | 0 | Yes | Yes | 22.2 | 25.2 | -3 | AC7640E6EC024D9299B6EEA61BA03B86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3593 |  | 2015-07-29 | 2015-07-29 12:41 | 2015-07-29 12:41 | UNITARY PRODUCTS GROUP - C048X1222A | 119 | 0 | Yes | Yes | 21.2 | 22.6 | -1.4 | 1694FCA58D074DEEBDF9A48B066E6AA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8356 |  | 2015-07-09 | 2015-07-09 14:21 | 2015-07-09 14:21 | OTHER - PA13NR060-J | 167 | 0 | Yes | Yes | 20.8 | 19 | 1.8 | F79C7C17826742DE9D3E697C7677A7A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2109 |  | 2015-08-19 | 2015-08-19 16:12 | 2015-08-19 16:12 | OTHER - UNK | 85 | 0 | Yes | Yes | 26.3 | 21.5 | 4.8 | CF4FC321F93C4E13B9D2E8CF72C0055C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-3923 |  | 2015-09-09 | 2015-09-09 09:48 | 2015-09-09 09:48 | GOODMAN - GSC130481AF | 150 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | 42C1544767AF4ED885D6D3AC0DB01E95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4406 |  | 2015-07-28 | 2015-07-28 10:41 | 2015-07-28 10:41 | YORK - D2NP024N03606A | 100 | 0 | Yes | Yes | 19.5 | 20.6 | -1.1 | F2FB90A823204C79ABA10D297439C6B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-2809 |  | 2015-07-30 | 2015-07-30 15:55 | 2015-07-30 15:55 | CARRIER - 38TKB042330 | 85 | 0 | Yes | Yes | 18.3 | 17.2 | 1.1 | 00DA175B06C84CBAB6B661D67E04B396 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6430 |  | 2015-07-28 | 2015-07-28 15:35 | 2015-07-28 15:35 | AMERICAN STANDARD - YCY036G1M0AC | 131 | 0 | Yes | Yes | 22.5 | 21.7 | 0.8 | E9178AC2D39E46FCB16852676A273891 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6837 |  | 2015-11-06 | 2015-11-06 12:01 | 2015-11-06 12:01 | CARRIER - UNKNOWN | 87 | 0 | Yes | Yes | 20.2 | 21.4 | -1.2 | 21E2AC1D0A8D4FC5B85090B60B4C791F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2953 |  | 2015-07-15 | 2015-07-15 09:50 | 2015-07-15 09:50 | GMC - 241BC | 85 | -8 | Yes | Yes | 20.3 | 19.9 | 0.4 | 54CEFB23044B4BB8BB26AAF3CC3C0F3A | Remove refrigerant: 8 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Antioch | CA | 94531-6730 |  | 2015-08-14 | 2015-08-14 10:51 | 2015-08-14 10:51 | CARRIER - 561AJO42-E | 85 | 0 | Yes | Yes | 19.8 | 21 | -1.2 | 368161677B934FA7B874A54D4A8AAB7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3780 |  | 2015-10-29 | 2015-10-29 12:28 | 2015-10-29 12:28 | GOODMAN - UNK | 85 | 0 | Yes | Yes | 21.9 | 20.4 | 1.5 | C80B1C58DABD4A9DBE331DCBD984FF3A |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7710 |  | 2015-09-10 | 2015-09-10 14:43 | 2015-09-10 15:06 | BDP - 585CJ036075 | 84 | 8.2 | Yes | Yes | 20.2 | 22.1 | -1.9 | 4B121640FA5B4140AB1912964F238815 |  | R22 | Non-TXV |  | 9.762% | 0.90238 | 18.76% | [5 empty] | Non-TXV | 9.762%
Suisun City | CA | 94585-1827 |  | 2015-09-04 | 2015-09-04 15:11 | 2015-09-04 15:11 | TRANE - BTD730A100B0 | 74 | 0 | Yes | Yes | 22 | 18.6 | 3.4 | 3B53DDB5336C428595726E42E14C4D56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5589 |  | 2015-09-10 | 2015-09-10 12:42 | 2015-09-10 12:42 | AMANA - PGD36C0702E | 131 | 0 | Yes | Yes | 17.8 | 22 | -4.2 | 9007092A14CE4B068E9322171CD4F4CB | Actual Superheat must be between 0°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7300 |  | 2015-07-01 | 2015-07-01 10:59 | 2015-07-01 10:59 | CARRIER - 38BRCO42340 | 171 | 0 | Yes | Yes | 23.6 | 24.6 | -1 | 7D5299CA593945638AA8F6E0F576A4FA |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6211 |  | 2015-09-14 | 2015-09-14 09:42 | 2015-09-14 09:42 | ICP - PGAA30C1K3 | 75 | 0 | Yes | Yes | 21.5 | 16.1 | 5.4 | 3E2F7CB0C03A49669A1CBBBD16DC828C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1656 |  | 2015-09-22 | 2015-09-22 14:42 | 2015-09-22 14:42 | RHEEM - RAFD-024JAS | 66 | 0 | Yes | Yes | 27 | 22.8 | 4.2 | CA662978103648A799824E12A8B8D608 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1634 |  | 2015-09-01 | 2015-09-01 08:51 | 2015-09-01 08:51 | WESTINGHOUSE - N/A | 85 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 308681D23B4E40CAB1C31C175A07F331 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5638 |  | 2015-07-15 | 2015-07-15 15:37 | 2015-07-15 15:37 | PAYNE - PA13NA036-C | 85 | 0 | Yes | Yes | 18.5 | 18.1 | 0.4 | 889D30B4B6AF43C9A0FBDC2E1F483C15 |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5954 |  | 2015-08-11 | 2015-08-11 11:15 | 2015-08-11 11:15 | GE - BTR724D100A0 | 68 | 0 | Yes | Yes | 17.1 | 18.2 | -1.1 | A8607796BAB84286B970EDE2C6774E85 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4302 |  | 2015-09-29 | 2015-09-29 15:08 | 2015-09-29 15:08 | LENNOX - 12ACB364P | 103 | 0 | Yes | Yes | 22.7 | 21.5 | 1.2 | 632F2B86340F46C588AD4631D410D099 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8332 |  | 2015-09-16 | 2015-09-16 15:44 | 2015-09-16 15:44 | YORK - DBYP-F036N070A | 108 | 0 | Yes | Yes | 21.3 | 23 | -1.7 | 797EB3BBF743406FBE809F91C036723A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9499 |  | 2015-08-03 | 2015-08-03 12:05 | 2015-08-03 12:05 | OTHER - FAFF-043JAZ | 99 | 0 | Yes | Yes | 23.5 | 21.9 | 1.6 | A23D0440FA0B47A4BFC2D23A60DDF3EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1039 |  | 2015-09-16 | 2015-09-16 13:25 | 2015-09-16 13:25 | OTHER - UNKNOWN | 81 | 0 | Yes | Yes | 18.9 | 20.9 | -2 | FF4535461C5F4AA789202A3B2B04E3A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1941 |  | 2015-09-03 | 2015-09-03 10:52 | 2015-09-03 10:52 | YORK - H2RD060S06B | 162 | 0 | Yes | Yes | 17.8 | 18.7 | -0.9 | 9AFCB2954E3E49278DF948B22EF228DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9405 |  | 2015-08-11 | 2015-08-11 11:16 | 2015-08-11 11:16 | CARRIER - 38CKC048360 | 109 | 0 | Yes | Yes | 20.6 | 19.6 | 1 | 35510BF466E243FA8B3F1FDA089D5712 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6155 |  | 2015-09-23 | 2015-09-23 10:38 | 2015-09-23 10:38 | OTHER - N2A348AKA200 | 121 | 0 | Yes | Yes | 20 | 22.6 | -2.6 | 014D3FB678B047C3BF9BC993DDBBC553 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-3408 |  | 2015-07-29 | 2015-07-29 08:41 | 2015-07-29 08:41 | RUUD - UAKA-037JAZ | 79 | 0 | Yes | Yes | 21.1 | 18.5 | 2.6 | EC6BB148480D4DD3A2434F7634103EC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4108 |  | 2015-07-16 | 2015-07-16 12:11 | 2015-07-16 12:11 | BRYANT - 180ANA036000DBAA | 85 | 0 | Yes | Yes | 9 | 20.4 | -11.4 | 6AAFD3C9FA0F47CABCC7353BB5969866 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2724 |  | 2015-08-14 | 2015-08-14 13:57 | 2015-08-14 13:57 | TRANE - TTN036C100B3 | 117 | 0 | Yes | Yes | 20.5 | 20.8 | -0.3 | F729EBA5BEA7446FA4FA023F340398D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3218 |  | 2015-08-04 | 2015-08-04 10:38 | 2015-08-04 10:38 | TRANE - TTN036C100B4 | 93 | 0 | Yes | Yes | 20.4 | 18 | 2.4 | FDAC7B7B853944C1A108597A3500676A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2056 |  | 2015-07-27 | 2015-07-27 09:39 | 2015-07-27 09:39 | CARRIER - 38THO42330 | 80 | 0 | Yes | Yes | 18.8 | 19.1 | -0.3 | 5C37ED5395104ACC96AA29DCC7F97CE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6508 |  | 2015-08-05 | 2015-08-05 16:05 | 2015-08-05 16:05 | PAYNE - PA13NAO36-E | 85 | 0 | Yes | Yes | 23.9 | 19.2 | 4.7 | 02F6FA8A433641C7A1BAF16A0D3591BC |  | R410A | TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-1027 |  | 2015-07-24 | 2015-07-24 14:21 | 2015-07-24 14:21 | OTHER - PA13NR018-J | 53 | 0 | Yes | Yes | 22 | 21.3 | 0.7 | 22B9213B0FBB46D09DEAFF074BB31C55 |  | R22 | TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2221 |  | 2015-07-20 | 2015-07-20 13:11 | 2015-07-20 13:11 | PAYNE - PA12NA042A | 100 | 0 | Yes | Yes | 14.6 | 17.6 | -3 | 7FE01ACF42EC4C9EBAB042A42CF68156 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clayton | CA | 94517-1334 |  | 2015-09-08 | 2015-09-08 11:07 | 2015-09-08 11:07 | RHEEM - RAMB-060JBZ | 192 | 0 | Yes | Yes | 18.3 | 12.4 | 6 | B0012B6C51D042CE95B743B1D0B51DC4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-4103 |  | 2015-08-19 | 2015-08-19 13:37 | 2015-08-19 13:37 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 16.5 | 19 | -2.5 | 1FC08AABA8EB418C8A4C42EE6FD2C7DE |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-4103 |  | 2015-08-19 | 2015-08-19 14:08 | 2015-08-19 14:08 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 18.7 | 19.5 | -0.8 | 7F851D9F1158491DA547132A4776575B |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2538 |  | 2015-08-04 | 2015-08-04 14:20 | 2015-08-04 14:20 | LENNOX - 14ACX-30-230-15 | 107 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | 20B7D1C63E1B41B5A991A59BCF901B53 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5944 |  | 2015-10-15 | 2015-10-15 09:43 | 2015-10-15 09:43 | GOODMAN - CLQ48-1 | 225 | 0 | Yes | Yes | 21.3 | 22.5 | -1.2 | 1B9B93C4B21F449BB172B3C1BD5D1C7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5945 |  | 2015-07-15 | 2015-07-15 13:22 | 2015-07-15 13:22 | BDP - A13NR042- | 113 | 0 | Yes | Yes | 26.7 | 23.2 | 3.5 | 22B91EFA5A4E456890EB2B2A8CE0B7E4 |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2408 |  | 2015-09-17 | 2015-09-17 12:12 | 2015-09-17 12:12 | RHEEM - RAKA-042JAZ | 79 | 0 | Yes | Yes | 17 | 19.7 | -2.7 | 01FDE894C87648A1BC208F82923D108D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-3500 |  | 2015-08-06 | 2015-08-06 08:46 | 2015-08-06 08:46 | TRANE - TTP042D100A0 | 139 | 0 | Yes | Yes | 18.9 | 17.2 | 1.7 | 0573C3B6D52248A7A76D031C24309577 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8408 |  | 2015-11-05 | 2015-11-05 11:34 | 2015-11-05 11:34 | BRYANT - 38TH060300 | 170 | 0 | Yes | Yes | 18 | 18.5 | -0.5 | 45D900553324437889B6B492417A1D44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-1719 |  | 2015-08-05 | 2015-08-05 13:31 | 2015-08-05 13:56 | - BRCS0481BB | 119 | 5.8 | Yes | Yes | 20.1 | 19.9 | 0.2 | 347BF882ECD7466AAB07D37E49302A34 |  | R22 | Non-TXV |  | 4.874% | 0.95126 | 9.367% | [5 empty] | Non-TXV | 4.874%
Dixon | CA | 95620-9736 |  | 2015-07-22 | 2015-07-22 09:50 | 2015-07-22 09:50 | PAYNE - PA13NR036C | 128 | 0 | Yes | Yes | 19.1 | 19.3 | -0.2 | 13230C55A0524C3D82B48B503CB26B4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4905 |  | 2015-07-01 | 2015-07-01 13:41 | 2015-07-01 13:41 | PAYNE - 597CNO30-A | 109 | 0 | Yes | Yes | 20.1 | 21.1 | -0.9 | E2F2FCF8CE4F42CA816FDE4AEF9D407A |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-3845 |  | 2015-07-27 | 2015-07-27 11:34 | 2015-07-27 11:34 | GOODMAN - CK42-1A | 85 | 0 | Yes | Yes | 17.1 | 20.1 | -3 | 9A37233FA2AE45AAA6221CA10F573D8A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8401 |  | 2015-07-22 | 2015-07-22 14:55 | 2015-07-22 15:33 | AMANA - GSC140361AE | 85 | 0 | Yes | Yes | 20.7 | 19.9 | 0.9 | 4DDD500C22124720A37FDBFC101FC766 | Add refrigerant: -10.9 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8175 |  | 2015-07-21 | 2015-07-21 16:11 | 2015-07-21 16:11 | CARRIER - 563CN048-A | 85 | 0 | Yes | Yes | 14 | 15.6 | -1.6 | 4F620E3F704B4526BD9FC88AE00E18C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4500 |  | 2015-08-20 | 2015-08-20 17:30 | 2015-08-20 17:30 | - 563AN048-A | 85 | 0 | Yes | Yes | 15.1 | 17.5 | -2.4 | 2D9B99BF65C147089A4D15A9006C2E87 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8198 |  | 2015-08-24 | 2015-08-24 09:44 | 2015-08-24 10:03 | CARRIER - 38BRB030300 | 85 | 12.3 | Yes | Yes | 22.6 | 18.7 | 3.9 | 7E7BB77FEEB44DDC8120157875C04654 |  | R22 | TXV |  | 14.47% | 0.85529 | 27.81% | [5 empty] | TXV | 14.47%
Pittsburg | CA | 94565-4041 |  | 2015-08-19 | 2015-08-19 15:03 | 2015-08-19 15:03 | COLEMAN - ERCS0361BBB | 96 | 0 | Yes | Yes | 23.1 | 19.4 | 3.7 | 981733C8ABF1438AA001FB5D56FA0685 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8563 |  | 2015-09-11 | 2015-09-11 11:38 | 2015-09-11 11:57 | YORK - H2RA060S06D | 118 | 5.1 | Yes | Yes | 22 | 18.9 | 3.2 | DFABA4327C7743B693CDCD1EE5131936 |  | R22 | Non-TXV |  | 4.322% | 0.95678 | 8.306% | [5 empty] | Non-TXV | 4.322%
Antioch | CA | 94509-7358 |  | 2015-08-24 | 2015-08-24 11:01 | 2015-08-24 11:01 | CARRIER - 591ANX036000AAA | 85 | 0 | Yes | Yes | 25.4 | 19.7 | 5.8 | C76C4FCDD3D94DCFB49A7A2A2821C301 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4252 |  | 2015-08-20 | 2015-08-20 14:12 | 2015-08-20 14:12 | OTHER - UNKNOWN | 85 | 0 | Yes | Yes | 14.2 | 13.7 | 0.6 | C4824D2EBDF943B28A6354FD62CEEB51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2541 |  | 2015-07-30 | 2015-07-30 08:57 | 2015-07-30 08:57 | YORK - D1NH030N05606A | 69 | 0 | Yes | Yes | 27.7 | 21.8 | 5.9 | AC41A55316E340FF970D17C7497DF10B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2726 |  | 2015-07-21 | 2015-07-21 09:39 | 2015-07-21 09:39 | DAY & NIGHT - N4A336AKB300 | 85 | 0 | Yes | Yes | 20 | 18.7 | 1.3 | B8F48AE1BF4A44FDB2F05D508AD466CF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-1403 |  | 2015-10-01 | 2015-10-01 12:17 | 2015-10-01 12:17 | GOODMAN - GSX130361EA | 74 | 0 | Yes | Yes | 18.7 | 18.2 | 0.5 | BDE793EB536649A3A15F40FC5594DD26 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5618 |  | 2015-08-24 | 2015-08-24 12:48 | 2015-08-24 12:48 | OTHER - CA5536VKD2 | 81 | 0 | Yes | Yes | 22.3 | 19.3 | 3 | E506C3F172DF42BBB7AF8DD3828CEB32 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7841 |  | 2015-07-07 | 2015-07-07 14:16 | 2015-07-07 14:16 | PAYNE - 386KBO30320 | 55 | 0 | Yes | Yes | 23.6 | 20.1 | 3.5 | 7B327ED8CE054B30B2E7AEB5AD542B98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8081 |  | 2015-07-16 | 2015-07-16 14:18 | 2015-07-16 14:41 | CARRIER - 38CKCO60300 | 85 | 18 | Yes | Yes | 14.4 | 17.4 | -3 | 9A48928ACDED4A12B662F9225D1A909D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | TXV |  | 21.18% | 0.78824 | 40.7% | [5 empty] | TXV | 21.18%
Vacaville | CA | 95688-2918 |  | 2015-07-01 | 2015-07-01 14:41 | 2015-07-01 14:41 | YORK - D1NA036N05606A | 63 | 0 | Yes | Yes | 25.5 | 19.9 | 5.6 | 370E255DAC634496AEDD09C5AE62A3C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1702 |  | 2015-08-25 | 2015-08-25 10:31 | 2015-08-25 10:31 | ALLEGIANCE - 2A7A4030B1000AA | 105 | 0 | Yes | Yes | 21.4 | 18.3 | 3.1 | 28504DB2C8E44E8C9CE65FA3E91F86B6 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2634 |  | 2015-07-30 | 2015-07-30 10:41 | 2015-07-30 10:41 | GOODMAN - GPG153709041AA | 115 | 0 | Yes | Yes | 25.7 | 19.7 | 6 | 2ADD19543A2B4B9899CD0ED803381D06 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-6615 |  | 2015-07-15 | 2015-07-15 11:00 | 2015-07-15 11:29 | DAY & NIGHT - 593ANX036000AAAA | 117 | -11 | Yes | Yes | 16.3 | 18.2 | -1.9 | F1968397878D40D4841CB8554D7ADC80 |  | R22 | Non-TXV |  | -9.402% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.402%
Fairfield | CA | 94533-5874 |  | 2015-07-21 | 2015-07-21 08:34 | 2015-07-21 08:34 | TRANE - 2TTBOO36A1000AA | 76 | 0 | Yes | Yes | 17.3 | 18.7 | -1.4 | 1477E9457302468E8756D2071E297B4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3437 |  | 2015-09-04 | 2015-09-04 10:34 | 2015-09-04 10:34 | CARRIER - 380H018300 | 85 | 0 | Yes | Yes | 17.7 | 19.4 | -1.7 | 373B748738CE4E4BBB8B10654B8C8E9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-4531 |  | 2015-07-22 | 2015-07-22 15:04 | 2015-07-22 15:04 | ICP - TCA248AKA4 | 148 | 0 | Yes | Yes | 26.1 | 19 | 7.1 | 7DCF872254BA4DC6B93432144C1564D1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3663 |  | 2015-08-27 | 2015-08-27 14:45 | 2015-08-27 14:45 | CARRIER - UNKNOWN | 85 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | 1F3E1FF9437A4A31BA5363434F7784E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2947 |  | 2015-11-06 | 2015-11-06 12:10 | 2015-11-06 12:10 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 18.7 | 18.7 | 0 | E50A4B6DDDA34733B8ABC9AC198B9B37 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6212 |  | 2015-07-20 | 2015-07-20 10:08 | 2015-07-20 10:28 | PAYNE - PA10JA036-G | 85 | 20.5 | Yes | Yes | 16.3 | 19 | -2.7 | C9C9D912DB114406BD16B1D19C49A4FD |  | R22 | Non-TXV |  | 24.12% | 0.75882 | 46.35% | [5 empty] | Non-TXV | 24.12%
Antioch | CA | 94531-8263 |  | 2015-07-17 | 2015-07-17 12:07 | 2015-07-17 12:07 | GOODMAN - CK60-1AB | 122 | 0 | Yes | Yes | 25.6 | 21.3 | 4.3 | 29F7DC4B97404DB5818A2F977ED9F678 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3415 |  | 2015-07-24 | 2015-07-24 11:53 | 2015-07-24 11:53 | ICP - PGAA42C1K4 | 70 | 0 | Yes | Yes | 24.6 | 20.8 | 3.8 | 26BEC144D398455B9BA69BC17F25C006 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95403-1265 |  | 2015-08-13 | 2015-08-13 14:14 | 2015-08-13 14:35 | CARRIER - 38CKC024330 | 85 | 21.9 | Yes | Yes | 19.4 | 18.7 | 0.7 | D5B2E391CAC24121B14AC1A2F685529B |  | R22 | Non-TXV |  | 25.76% | 0.74235 | 49.51% | [5 empty] | Non-TXV | 25.76%
Bakersfield | CA | 93305-3749 |  | 2015-10-19 | 2015-10-19 08:46 | 2015-10-19 08:46 | YORK - D2P036N05606A | 108 | 0 | Yes | Yes | 23.3 | 19.9 | 3.4 | 2FCB1FD48B8E4322A173A11AD074B64B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-24 | 2015-08-24 10:40 | 2015-08-24 10:40 | ICP - PGD33606K001C1 | 102 | 0 | Yes | Yes | 26.2 | 21 | 5.2 | 857BF68F8FE342D99F135401281FCD9D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-24 | 2015-08-24 10:44 | 2015-08-24 10:44 | ICP - PGD33606K001C1 | 102 | 0 | Yes | Yes | 26.4 | 21.5 | 4.9 | C19FA091F4694CE2B5C4E5C975791BA1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-24 | 2015-08-24 10:49 | 2015-08-24 10:49 | ICP - PGD33606K001C1 | 102 | 0 | Yes | Yes | 26.1 | 21.5 | 4.6 | F22FB41F07C94B719AC296DDCCDCF1FE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6065 |  | 2015-07-29 | 2015-07-29 10:57 | 2015-07-29 10:57 | YORK - H2RA036S06D | 63 | 0 | Yes | Yes | 21.3 | 20.3 | 1.1 | 0915F69B930F47C0BB66F5D9F62BD425 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-24 | 2015-08-24 11:04 | 2015-08-24 11:04 | ICP - PGD33606K001C1 | 102 | 0 | Yes | Yes | 26.6 | 22.6 | 4 | E132E95D37B6444E8064687569AD865A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6443 |  | 2015-07-13 | 2015-07-13 09:28 | 2015-07-13 09:28 | MAYTAG - DS5BD | 136 | 0 | Yes | Yes | 23.2 | 18.7 | 4.5 | DCB7ACCD16924C608399A67C5BF63C2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-24 | 2015-08-24 11:09 | 2015-08-24 11:09 | COMFORT AIRE - C4A36GKD200 | 85 | 0 | Yes | Yes | 25.1 | 22.6 | 2.5 | 0C4BE4768BBD4A458E485D703484C9AF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3616 |  | 2015-08-20 | 2015-08-20 12:02 | 2015-08-20 12:35 | TRANE - TTN030C100C2 | 95 | 5.7 | Yes | Yes | 16.8 | 18.9 | -2.1 | 40F29648D7BE44B186AB460462B9E07E |  | R22 | TXV |  | 6% | 0.94 | 11.53% | [5 empty] | TXV | 6%
Bakersfield | CA | 93307-8506 |  | 2015-08-24 | 2015-08-24 11:18 | 2015-08-24 11:18 | ICP - PGD33606K001C1 | 102 | 0 | Yes | Yes | 26.6 | 22.6 | 4 | 0F24E89C8DCC42428CB0865FE073C96B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4229 |  | 2015-09-02 | 2015-09-02 16:04 | 2015-09-02 16:04 | CARRIER - 383DB048300 | 85 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | 188E4C0E994241E199F782C90FC86257 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Alamo | CA | 94507-2638 |  | 2015-08-04 | 2015-08-04 16:05 | 2015-08-04 16:05 | LENNOX - XC13-036-230-01 | 116 | 0 | Yes | Yes | -11.9 | 18.2 | -30.1 | 5FE220987C5D47A6A3B3931932BF0F09 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Alamo | CA | 94507-2638 |  | 2015-08-04 | 2015-08-04 16:36 | 2015-08-04 16:36 | TRANE - TTR018D100A0 | 60 | 0 | Yes | Yes | 19.5 | 19.4 | 0.1 | 6821E6168E664A11BBB427BD6A678B2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1439 |  | 2015-08-14 | 2015-08-14 10:33 | 2015-08-14 11:09 | YORK - AC042X1021A | 84 | -7.9 | Yes | Yes | 18.4 | 18.2 | 0.2 | 432048973C0246CE85A45908817AE8C0 |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Suisun City | CA | 94585-2124 |  | 2015-08-31 | 2015-08-31 10:14 | 2015-08-31 10:14 | GE - UNK | 85 | 0 | Yes | Yes | 20.8 | 19.4 | 1.4 | AD30E22ACBEB481696BA3900B3F0742B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-05 | 2015-08-05 11:53 | 2015-08-05 11:53 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 22.7 | 18.6 | 4.2 | 5FF4098B968149C185900E65B7D57431 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 11:05 | 2015-08-05 11:05 | ICP - C4A324GKD200 | 61 | 0 | Yes | Yes | 23.2 | 22.1 | 1.1 | 8D4B53AE157A4615B97BBB337D998619 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2518 |  | 2015-07-24 | 2015-07-24 16:02 | 2015-07-24 16:02 | YORK - UNK | 105 | 0 | Yes | Yes | 17.5 | 19.3 | -1.8 | 6CD9E75507E74C42AC80668022284E76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-4107 |  | 2015-07-08 | 2015-07-08 10:26 | 2015-07-08 10:26 | YORK - H1CCOC2 4A10A | 54 | 0 | Yes | Yes | 17.5 | 19.1 | -1.6 | 6F41DEA0808945C58BE2950567C500C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1233 |  | 2015-08-04 | 2015-08-04 13:42 | 2015-08-04 13:42 | RUUD - UAKA-037JAZ | 85 | 0 | Yes | Yes | 19.8 | 18.8 | 1 | 109A22B1112B49F9B4D52BC892F145C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-6253 |  | 2015-07-29 | 2015-07-29 11:14 | 2015-07-29 11:34 | GE - BTB930A100A1 | 53 | 3.4 | Yes | Yes | 18.5 | 18.5 | 0 | 08F566606F634C5C9EB0803ABEA2B314 |  | R22 | Non-TXV |  | 6.415% | 0.93585 | 12.33% | [5 empty] | Non-TXV | 6.415%
Bakersfield | CA | 93305-1816 |  | 2015-07-30 | 2015-07-30 12:07 | 2015-07-30 12:07 | RHEEM - RRMA-A048JK10X | 115 | 0 | Yes | Yes | 25.5 | 21.5 | 4.1 | F8E3D6728AEF46D882733F12ECE9E281 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-05 | 2015-08-05 09:38 | 2015-08-05 09:38 | ICP - C4A336GKD200 | 85 | 0 | Yes | Yes | 19.4 | 19.7 | -0.3 | CFCC397814BA4EE5B47C1D109BB0E59D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8925 |  | 2015-08-28 | 2015-08-28 15:29 | 2015-08-28 15:29 | - | 85 | 0 | Yes | Yes | 19.1 | 21 | -1.9 | 15A67EEC754C40D38EE3BC0C8B3AD6FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 11:40 | 2015-08-05 11:40 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 21.2 | 20.2 | 1 | 48FAFA2638424400A09C8656A25098B6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4851 |  | 2015-09-16 | 2015-09-16 13:22 | 2015-09-16 13:22 | BRYANT - 588ANW048100AFBG | 104 | 0 | Yes | Yes | 20.6 | 19.7 | 0.9 | 000B3D1DBDED4A8C8677FB6FEA87C69B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 11:56 | 2015-08-05 11:56 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 19.6 | 18.5 | 1.1 | 7D4A0623322047C7ADF5BE6F3BC7D1CE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 10:18 | 2015-08-05 10:18 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 19 | 20.7 | -1.7 | FA021DDA51A64653B1FA4CF1FBFD4AB8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2214 |  | 2015-07-27 | 2015-07-27 17:07 | 2015-07-27 17:07 | GUARDIAN - GCGD48S21 | 69 | 0 | Yes | Yes | 13.1 | 15.9 | -2.8 | 2439F5261E184F2FB0CED0EEAB0C751B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 10:32 | 2015-08-05 10:32 | ICP - C4A324GKD200 | 61 | 0 | Yes | Yes | 21 | 22.1 | -1.1 | 4D0DBB1CAF024BF49A27B37EC14C8D7B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4409 |  | 2015-10-19 | 2015-10-19 09:59 | 2015-10-19 09:59 | ICP - PGF324040K01 | 85 | 0 | Yes | Yes | 25 | 20.4 | 4.6 | 387A523D83974C188C20A5F8EE5A9E9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-8981 |  | 2015-07-21 | 2015-07-21 08:37 | 2015-07-21 08:37 | - H1RA042S06D | 85 | 0 | Yes | Yes | 15.1 | 17.9 | -2.8 | 33E300AD38EB4403AEA4D75ACC02248C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 10:14 | 2015-08-05 10:14 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | B339D92A37C44E2F9A3C4674E0917F8A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2169 |  | 2015-07-17 | 2015-07-17 11:07 | 2015-07-17 11:07 | PAYNE - PA13NR036-0 | 83 | 0 | Yes | Yes | 19.6 | 19.3 | 0.3 | E57B2B65EF824D9C982EBFD3416C943E |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4331 |  | 2015-08-17 | 2015-08-17 12:16 | 2015-08-17 12:16 | GOODMAN - GPG1342070M41DA | 99 | 0 | Yes | Yes | 25.5 | 23.1 | 2.4 | 78485B2E0D794AAB8D4FE2BCEF2C0A19 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7017 |  | 2015-08-19 | 2015-08-19 15:37 | 2015-08-19 15:37 | CARRIER - 593ANX036000AAAA | 117 | 0 | Yes | Yes | 25.3 | 20.1 | 5.2 | D6230DAA7DD54CA08105974A2680051C |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-1825 |  | 2015-11-13 | 2015-11-13 14:28 | 2015-11-13 14:28 | CARRIER - 48ESNA2406030 | 76 | 0 | Yes | Yes | 17.5 | 20.1 | -2.6 | C34BF594C2B04DDEB49C36274DA1D683 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4406 |  | 2015-07-30 | 2015-07-30 12:32 | 2015-07-30 12:56 | PAYNE - PA10JAO42-B | 80 | 5.7 | Yes | Yes | 16.9 | 19.9 | -3 | 506444077A984307B80CEB02059A073C |  | R22 | Non-TXV |  | 7.125% | 0.92875 | 13.69% | [5 empty] | Non-TXV | 7.125%
Concord | CA | 94520-1506 |  | 2015-09-01 | 2015-09-01 12:10 | 2015-09-01 12:10 | CARRIER - 24ABB336W0031010 | 83 | 0 | Yes | Yes | 19 | 18.1 | 0.9 | AB9C0FE7A32E49849E25B616155C2CAE |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1042 |  | 2015-07-29 | 2015-07-29 09:08 | 2015-07-29 09:08 | PAYNE - PA10JA030C | 77 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | BF0B4291838F41B785F75743CEB53B5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3301 |  | 2015-07-01 | 2015-07-01 12:50 | 2015-07-01 12:50 | HEIL - CA3024VKA2 | 57 | 0 | Yes | Yes | 17.3 | 20.2 | -2.9 | 30EBC26F8DED492B9739B020E4C3D10D |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4119 |  | 2015-08-17 | 2015-08-17 09:48 | 2015-08-17 09:48 | OTHER - CA9060VKD2 | 191 | 0 | Yes | Yes | 23.5 | 22.2 | 1.3 | 4349F6FD396D433CB4F22B5384CF2D9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3367 |  | 2015-07-24 | 2015-07-24 11:19 | 2015-07-24 11:19 | ICP - PGAD36D1K5 | 102 | 0 | Yes | Yes | 20.3 | 21.4 | -1.1 | CC9FFE6A41AF48729CAACDB89678B845 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4020 |  | 2015-07-09 | 2015-07-09 13:16 | 2015-07-09 13:16 | GE - BTB824A100A | 43 | 0 | Yes | Yes | 18.6 | 19.9 | -1.3 | 8A36614FD79D4C40A910B18F51EC32F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9344 |  | 2015-08-03 | 2015-08-03 15:30 | 2015-08-03 15:30 | YORK - H2RA036S06E | 63 | 0 | Yes | Yes | 17.2 | 19.9 | -2.7 | 5098B7929ABF46EFB08DC71A63521E02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5382 |  | 2015-07-29 | 2015-07-29 12:01 | 2015-07-29 12:01 | YORK - TCGD42S21S1A | 72 | 0 | Yes | Yes | 22 | 21.8 | 0.2 | C431FA28B6EF460E96DD473CBB1F0F49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-05 | 2015-08-05 09:22 | 2015-08-05 09:22 | ICP - C4A336GKD200 | 85 | 0 | Yes | Yes | 21 | 22.1 | -1.1 | 587168222A314673940DBF514AC41978 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:09 | 2015-08-05 14:09 | RHEEM - RRMA-A042JK08X | 114 | 0 | Yes | Yes | 23.3 | 19.9 | 3.4 | F56A4A42FA3A453B833D4723C95CC0EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5464 |  | 2015-06-26 | 2015-06-26 10:54 | 2015-06-26 10:54 | CARRIER - 24ABA336A300 | 105 | 0 | Yes | Yes | 20.3 | 19.7 | 0.6 | 5C9805C7C25B447CA7D5EB9ED882BC47 | Actual Subcooling cannot be negative. Please check entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5664 |  | 2015-08-06 | 2015-08-06 16:57 | 2015-08-06 16:57 | CARRIER - 38CK036310 | 85 | 0 | Yes | Yes | 10.9 | 13.7 | -2.8 | 0AB2B9629F604616995C6D388967EA64 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:23 | 2015-08-05 14:23 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 22 | 22.4 | -0.4 | 1612EFEFB0644E7D89B3A02603FAD132 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-5237 |  | 2015-10-13 | 2015-10-13 13:52 | 2015-10-13 14:14 | CARRIER - 24AB R360A330 | 161 | 18.2 | Yes | Yes | 18.9 | 19.7 | -0.8 | 8FE859C9ECE64D09ADB8A8E2BD5BA997 |  | R22 | TXV |  | 11.3% | 0.88696 | 21.72% | [5 empty] | TXV | 11.3%
Vacaville | CA | 95687-5210 |  | 2015-07-10 | 2015-07-10 09:52 | 2015-07-10 09:52 | GE - UNK | 53 | 0 | Yes | Yes | 24.8 | 18.8 | 6 | 482D6A075FD44CE2A9704E8E3773F0FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8509 |  | 2015-08-05 | 2015-08-05 14:04 | 2015-08-05 14:04 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 21.6 | 21.2 | 0.4 | 9EACD0469A464FE488CB261B207D2DD2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rodeo | CA | 94572-1612 |  | 2015-07-29 | 2015-07-29 14:02 | 2015-07-29 14:02 | PAYNE - PA13NA036 | 85 | 0 | Yes | Yes | 21 | 19.7 | 1.4 | B6EEABAAAA234A7C98BACEAF236EA4DD |  | R22 | TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9111 |  | 2015-08-05 | 2015-08-05 14:32 | 2015-08-05 14:32 | LENNOX - XC14-047-230-04 | 179 | 0 | Yes | Yes | 23.2 | 19.9 | 3.3 | B98F40B564DD447EB34ABFB6DB16B056 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1530 |  | 2015-08-12 | 2015-08-12 10:39 | 2015-08-12 11:09 | DAY & NIGHT - N4A336AKB300 | 85 | 8.9 | Yes | Yes | 20.6 | 18.2 | 2.4 | 58DBDF7516F8477E991C5698D32C7201 |  | R410A | TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | TXV | 10.47%
Dixon | CA | 95620-4812 |  | 2015-07-20 | 2015-07-20 09:30 | 2015-07-20 09:30 | CARRIER - 38CKC060370 | 132 | 0 | Yes | Yes | 16.7 | 19.3 | -2.6 | 42DD29870A0A48F4A399783D2041A5C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 13:51 | 2015-08-05 13:51 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 18.9 | 18.3 | 0.6 | EB4C0FABF3E34B10B8676E97D04EF52F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8509 |  | 2015-08-05 | 2015-08-05 18:40 | 2015-08-05 18:40 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 20.8 | 22.6 | -1.8 | FCA794EA77834C54AB68F052887067E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4990 |  | 2015-10-19 | 2015-10-19 10:14 | 2015-10-19 10:14 | BDP - 585GJW018040ABAC | 55 | 0 | Yes | Yes | 22.4 | 22.1 | 0.3 | 9753508E5BE94F0B93EB005CBA01191F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8509 |  | 2015-08-05 | 2015-08-05 18:37 | 2015-08-05 18:37 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 23.6 | 23.1 | 0.5 | B57ECAD4A4CE48FAA1F72A35EAF0CEA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4128 |  | 2015-08-27 | 2015-08-27 10:57 | 2015-08-27 10:57 | RHEEM - RRKA-042JK08E | 69 | 0 | Yes | Yes | 19.9 | 20.9 | -1 | 646BF8026C1249F1BC086B5A5970C2B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8509 |  | 2015-08-05 | 2015-08-05 18:46 | 2015-08-05 18:46 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 20.1 | 23.4 | -3.3 | 1249F2CC0FC04F9BBC1028D5A93F5541 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 18:42 | 2015-08-05 18:42 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 24.4 | 23.6 | 0.8 | 37421E3643334D868563E3925E5566B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:36 | 2015-08-05 14:36 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 17.3 | 20.1 | -2.7 | C167CE042A204F1C9EDDCDF1155B9410 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:50 | 2015-08-05 14:50 | RHEEM - RRMA-A030JK08X | 80 | 0 | Yes | Yes | 24.5 | 24 | 0.6 | 60B7D8EC902147E79DE5BFA8439178F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 12:13 | 2015-08-05 12:13 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 21 | 21.8 | -0.7 | 9071B6F34C454DB4845E166033BF7E4A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3351 |  | 2015-08-14 | 2015-08-14 12:34 | 2015-08-14 12:34 | YORK - H1RA024S06A | 59 | 0 | Yes | Yes | 19.1 | 16.1 | 3 | BD8924B62AFE4FCCA98A48F52B9AE6B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8509 |  | 2015-08-05 | 2015-08-05 14:34 | 2015-08-05 14:34 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 22.1 | 21.4 | 0.7 | A7A5F91DCDFA4A128CF970892B210DC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:47 | 2015-08-05 14:47 | RHEEM - RRMA-A042JK08X | 80 | 0 | Yes | Yes | 21.7 | 22.6 | -0.9 | 2EF8938C78234578AE82F0ED6B0019CE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3242 |  | 2015-07-22 | 2015-07-22 09:42 | 2015-07-22 09:42 | BDP - PA13NRO18-J | 85 | 0 | Yes | Yes | 22.7 | 20.7 | 2 | 6641FAB167D649EFB9D1348ED64DBA2E |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1559 |  | 2015-07-21 | 2015-07-21 14:03 | 2015-07-21 14:03 | OTHER - H1DBO18506G | 62 | 0 | Yes | Yes | 16.2 | 16.1 | 0.1 | C5B1E54094B74534A1BBAE454A2BCFA2 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 36°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:52 | 2015-08-05 14:52 | RHEEM - RRMA-A030JK08X | 80 | 0 | Yes | Yes | 20 | 23.6 | -3.6 | 982FF02DB64E4A60B76819212B8337D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2252 |  | 2015-09-02 | 2015-09-02 09:53 | 2015-09-02 09:53 | GE - UNK | 85 | 0 | Yes | Yes | 18.9 | 17.1 | 1.8 | 2F8783B809D1439E9DB011438545A2FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:40 | 2015-08-05 14:40 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 20.4 | 21.7 | -1.3 | CB5B6B930D004688A00CF2722CC9DC39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 12:29 | 2015-08-05 12:29 | ICP - C4A336GKD200 | 85 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | 7D15131926BC442BB3695815757701A5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 14:43 | 2015-08-05 14:43 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 19.1 | 22 | -2.9 | E4976C8D71AE4843ADB497005428AA46 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8509 |  | 2015-08-05 | 2015-08-05 14:55 | 2015-08-05 14:55 | RHEEM - RRMA-A0430JK08X | 80 | 0 | Yes | Yes | 21 | 23.1 | -2.1 | C7515A2206144365BDE6D002223F3533 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4621 |  | 2015-08-20 | 2015-08-20 13:13 | 2015-08-20 13:13 | OTHER - BTR730D1000A0 | 74 | 0 | Yes | Yes | 17.8 | 18.6 | -0.8 | 1F20DFF9C8864635B4A6B41A34677924 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4023 |  | 2015-06-26 | 2015-06-26 15:39 | 2015-06-26 15:39 | GE - BTB818A100A | 36 | 0 | Yes | Yes | 16.6 | 19.1 | -2.5 | 05D187E641F94BC3892814FC4E62FB07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4030 |  | 2015-06-26 | 2015-06-26 12:30 | 2015-06-26 12:30 | GE - BTB824A100A | 43 | 0 | Yes | Yes | 22.2 | 17.5 | 4.8 | CB0F71A440E146E0AF132C4367C5559D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3004 |  | 2015-08-17 | 2015-08-17 12:57 | 2015-08-17 13:18 | TRANE - 4TTB3030D10000AA | 82 | 7.1 | Yes | Yes | 23.1 | 19.3 | 3.8 | 785B584688FF4B64BE663B44771A3755 |  | R410A | Non-TXV |  | 8.659% | 0.91341 | 16.64% | [5 empty] | Non-TXV | 8.659%
Pleasant Hill | CA | 94523-2121 |  | 2015-07-24 | 2015-07-24 08:43 | 2015-07-24 08:43 | YORK - H4DH048S06A | 138 | 0 | Yes | Yes | 18 | 18.7 | -0.7 | 2518BBD230D546E391AC0619BA9257EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
El Sobrante | CA | 94803-3436 |  | 2015-07-16 | 2015-07-16 08:42 | 2015-07-16 08:42 | CARRIER - 38CKB048300 | 104 | 0 | Yes | Yes | 18.9 | 16.4 | 2.5 | 97C49B30FFBB4DED9B4AE7DC53B32BF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2817 |  | 2015-10-19 | 2015-10-19 14:46 | 2015-10-19 14:46 | CARRIER - UNK | 85 | 0 | Yes | Yes | 19.9 | 21.4 | -1.5 | 88688FD3DE16448EA01820812DD464AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-1146 |  | 2015-07-27 | 2015-07-27 09:39 | 2015-07-27 09:39 | OTHER - 561AJ048-D | 112 | 0 | Yes | Yes | 18.9 | 19.3 | -0.4 | 4BB18E5DCCCB4FF3B00BE107A16599B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4125 |  | 2015-09-17 | 2015-09-17 15:21 | 2015-09-17 15:21 | YORK - D1NH060NO9006C | 140 | 0 | Yes | Yes | 17.7 | 19.3 | -1.6 | 21537DD283404B9FBD8629E0C61B5B62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-2315 |  | 2015-08-13 | 2015-08-13 08:40 | 2015-08-13 08:40 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 18.3 | 18.8 | -0.5 | F616507299F54892BB9A4DF31084ABFE |  | R22 | TXV |  | 0% | 1 | 0%
Byron | CA | 94505-2315 |  | 2015-08-13 | 2015-08-13 08:58 | 2015-08-13 08:58 | CARRIER - 38CKC036350 | 73 | 0 | Yes | Yes | 17.5 | 17.7 | -0.2 | 26B2D9652DF04AA3BA7DDDC471CD2D85 |  | R22 | TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94597-2027 |  | 2015-08-18 | 2015-08-18 14:50 | 2015-08-18 14:50 | OTHER - HAC042AKA4 | 98 | 0 | Yes | Yes | 21.2 | 18.4 | 2.8 | 6F9ABA425C1142ECB04324C8668A58F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2525 |  | 2015-07-31 | 2015-07-31 16:31 | 2015-07-31 16:31 | GOODMAN - GS3B030KA | 68 | 0 | Yes | Yes | 19.6 | 19.4 | 0.2 | 0B41B1A1132A4974BEFA4C6C7A43EA58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2741 |  | 2015-07-28 | 2015-07-28 11:05 | 2015-07-28 11:05 | RHEEM - N/A | 80 | 0 | Yes | Yes | 27.9 | 22.4 | 5.5 | 3CF2A2E303EA48D8849B14A890C5DF98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 12:00 | 2015-08-05 12:00 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 17.4 | 20.1 | -2.7 | C0FF604DF7F04EE0BE0DE5C24EC43932 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-0000 |  | 2015-09-11 | 2015-09-11 15:07 | 2015-09-11 15:07 | CARRIER - 24ABA360A30 | 140 | 0 | Yes | Yes | 24.4 | 19.3 | 5.1 | 0F76C157C7484F428E77158B64F6FB7A |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1447 |  | 2015-07-16 | 2015-07-16 13:14 | 2015-07-16 13:14 | RHEEM - 13AJN24A101 | 68.8 | 0 | Yes | Yes | 14.9 | 18.5 | -3.6 | CD4B488D46CC4C3EB61522DB1211F189 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 11:42 | 2015-08-05 11:42 | ICP - PGD0336060K001C1 | 103 | 0 | Yes | Yes | 19.7 | 22.6 | -2.9 | D6672E8527D6409384C98F3167A6AFF3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8397 |  | 2015-07-21 | 2015-07-21 13:40 | 2015-07-21 13:40 | CARRIER - 38CKCD4 | 127 | 0 | Yes | Yes | 22.9 | 21 | 1.9 | B776C1C3B4764B6B8BF969DEE852F3E7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1470 |  | 2015-06-24 | 2015-06-24 13:33 | 2015-06-24 13:33 | TRANE - BTD736A100B0 | 88 | 0 | Yes | Yes | 29.5 | 20.8 | 8.7 | DCEC69FCEE6A4177BB7342F9F611B0D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5505 |  | 2015-08-18 | 2015-08-18 13:04 | 2015-08-18 13:04 | BDP - 5670036RCO | 67 | 0 | Yes | Yes | 18.1 | 21 | -2.9 | 8A5E84A326C749C1BA809B2AFF595F25 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5136 |  | 2015-07-13 | 2015-07-13 08:25 | 2015-07-13 08:25 | DAY & NIGHT - N4A324AKC100 | 56 | 0 | Yes | Yes | 17.7 | 18.7 | -1 | A4F7E49CB5054F249A70D5FAB7E1972D |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-9330 |  | 2015-07-20 | 2015-07-20 15:13 | 2015-07-20 15:13 | YORK - D4DED42S06A | 93 | 0 | Yes | Yes | 18.2 | 17.1 | 1.1 | A395FD1F1871479FB309574F9E266953 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4618 |  | 2015-07-29 | 2015-07-29 12:20 | 2015-07-29 12:20 | YORK - 24ABB360W320 | 132 | 0 | Yes | Yes | 18.3 | 18.5 | -0.2 | A9E4AEAA5F4F4FF0AD88A70ACAAF440D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 11:18 | 2015-08-05 11:18 | ICP - C4A324GKD200 | 61 | 0 | Yes | Yes | 18.2 | 21 | -2.8 | 816F5DE901EE44BDA5909B7F0E9094A3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pacheco | CA | 94553-6344 |  | 2015-08-07 | 2015-08-07 13:22 | 2015-08-07 13:22 | RHEEM - RAKA0480AZ | 85 | 0 | Yes | Yes | 21 | 17.3 | 3.7 | D0FD908982EE4B1F9C537F4B92EF4DB2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 11:23 | 2015-08-05 11:23 | ICP - C4A324GKD200 | 61 | 0 | Yes | Yes | 18.4 | 22.1 | -3.7 | 92A0DC8C8B17465EBC021F462FC7C0A1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6435 |  | 2015-08-10 | 2015-08-10 12:14 | 2015-08-10 12:14 | TEMPSTAR - TCA548AKC4 | 147 | 0 | Yes | Yes | 22.2 | 18.8 | 3.4 | 5D255E1A9A00432FA0F5833AD1935AD0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2204 |  | 2015-10-19 | 2015-10-19 12:48 | 2015-10-19 12:49 | YORK - D1HN036N05606C | 108 | 12.4 | Yes | Yes | 16 | 18.7 | -2.7 | 42DD31E9F8554D54AB61BC7933B42836 |  | R22 | Non-TXV |  | 11.48% | 0.88519 | 22.06% | [5 empty] | Non-TXV | 11.48%
Antioch | CA | 94531-8381 |  | 2015-07-20 | 2015-07-20 13:23 | 2015-07-20 13:23 | BDP - 561AJ042-D | 85 | 0 | Yes | Yes | 18.7 | 17.4 | 1.3 | 6BE49CD08DC04ABDB61122388A2D6E21 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7348 |  | 2015-09-17 | 2015-09-17 15:23 | 2015-09-17 15:23 | - 13AJA36A01 | 108 | 0 | Yes | Yes | 20.5 | 20 | 0.6 | 23020B2A54034913A38A07541242BAC4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3206 |  | 2015-10-16 | 2015-10-16 11:14 | 2015-10-16 11:14 | LENNOX - GCS29X036752PA | 58 | 0 | Yes | Yes | 16.3 | 15.4 | 0.9 | 3853C89A281F4C72BD78C93F6C0355E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3725 |  | 2015-10-08 | 2015-10-08 13:16 | 2015-10-08 13:16 | CARRIER - 38CKC018 | 85 | 0 | Yes | Yes | 13.6 | 15.8 | -2.2 | 077F4B2211FC424B9D38C9F63F9ACCE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-4107 |  | 2015-06-24 | 2015-06-24 11:56 | 2015-06-24 12:30 | GOODMAN - GSC130241AE | 93 | 9.4 | Yes | Yes | 15.4 | 18.3 | -2.9 | A637690C2E71485998454B38AE1DE612 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.11% | 0.89892 | 19.42% | [5 empty] | Non-TXV | 10.11%
Fairfield | CA | 94534-6675 |  | 2015-08-10 | 2015-08-10 16:29 | 2015-08-10 16:29 | BRYANT - 113RNA048D200 | 118 | 0 | Yes | Yes | 21 | 22.1 | -1.1 | 87B83B73C2304A4F9F025EC95F7E4F4C |  | R22 | TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94596-4759 |  | 2015-07-27 | 2015-07-27 10:39 | 2015-07-27 10:39 | RUUD - UARL-36JAZ | 157 | 0 | Yes | Yes | 24.2 | 19.6 | 4.7 | A3EC3F9291D743FAAF5A2BEF0F192854 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6201 |  | 2015-08-31 | 2015-08-31 14:25 | 2015-08-31 14:25 | CARRIER - 38GS048316 | 86 | 0 | Yes | Yes | 21.5 | 20.3 | 1.3 | CB75397FABE3498BB20B6B724166AD74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3118 |  | 2015-10-21 | 2015-10-21 09:46 | 2015-10-21 09:46 | PAYNE - PY3PNA030 | 85 | 0 | Yes | Yes | 21.5 | 20 | 1.6 | 4D35B7CD2E974C78AA58F0AF1BF2163D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3272 |  | 2015-09-10 | 2015-09-10 16:33 | 2015-09-10 16:33 | RHEEM - N/A | 85 | 0 | Yes | Yes | 20.9 | 21 | -0.1 | 0E5FEB6772A34FE6B74AB0E2C80087C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5536 |  | 2015-09-01 | 2015-09-01 09:40 | 2015-09-01 10:01 | OTHER - H2RC036S06G | 83 | 14.7 | Yes | Yes | 19.2 | 19.4 | -0.2 | A33E0A12D8FD4485AF651388B0264A78 |  | R22 | Non-TXV |  | 17.71% | 0.82289 | 34.04% | [5 empty] | Non-TXV | 17.71%
Concord | CA | 94519-2208 |  | 2015-07-30 | 2015-07-30 12:07 | 2015-07-30 12:07 | YORK - RCB30B2A | 77 | 0 | Yes | Yes | 23.8 | 19.3 | 4.6 | BC95FC5A4A2D4647B7CCB78C8F56AAB6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1119 |  | 2015-07-21 | 2015-07-21 12:04 | 2015-07-21 12:04 | GE - BGTA842R1C | 108 | 0 | Yes | Yes | 24.1 | 18.2 | 5.9 | 41D924074B794E1D820383B6DE623E1C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2002 |  | 2015-08-31 | 2015-08-31 09:34 | 2015-08-31 09:34 | YORK - AC036X1021A | 63 | 0 | Yes | Yes | 16.3 | 18.8 | -2.5 | 1C5962AF665F4B18B4E1B78521DC6C40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 12:05 | 2015-08-05 12:05 | ICP - PGD3366060K001C1 | 103 | 0 | Yes | Yes | 24.1 | 18.3 | 5.8 | 935EAF3620DD4132B85FF2277C856237 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2431 |  | 2015-09-15 | 2015-09-15 09:38 | 2015-09-15 09:38 | GOODMAN - GPG13300451AA | 77 | 0 | Yes | Yes | 20.1 | 19.1 | 1.1 | DC285A207F3E4C2480E165B434DFC5AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-1810 |  | 2015-08-12 | 2015-08-12 08:02 | 2015-08-12 08:02 | OTHER - CKJ60-1 | 142 | 0 | Yes | Yes | 18.4 | 19.3 | -0.9 | 82DAE422B8A7425FABAF9D74831CCB57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5456 |  | 2015-11-10 | 2015-11-10 11:12 | 2015-11-10 11:12 | CARRIER - 38CKC042350 | 93 | 0 | Yes | Yes | 22 | 20.1 | 1.9 | ABE17F8EF69B47E8A9D99A3BEAAA0CB5 |  | R22 | TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-2612 |  | 2015-07-30 | 2015-07-30 17:56 | 2015-07-30 17:56 | TRANE - | 85 | 0 | Yes | Yes | 17 | 19.3 | -2.3 | D6D29B69C7AC48E4B571B9C7C384042B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3220 |  | 2015-07-27 | 2015-07-27 13:46 | 2015-07-27 13:46 | NORDYNE - FS5BD-036KA | 85 | 0 | Yes | Yes | 19.1 | 19.3 | -0.2 | 21C8304C8D1A46FA882CF9D0DF9206ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5457 |  | 2015-08-10 | 2015-08-10 13:26 | 2015-08-10 13:26 | YORK - 40E48S06A | 85 | 0 | Yes | Yes | 18.7 | 19.3 | -0.6 | 75057D8885EE4C8A98844FC7E20D4F9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4237 |  | 2015-07-27 | 2015-07-27 15:52 | 2015-07-27 15:52 | GE - UNK | 69 | 0 | Yes | Yes | 15.7 | 18.3 | -2.6 | B5738656EFD84E9788A07D78F6FA4937 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7076 |  | 2015-09-15 | 2015-09-15 10:33 | 2015-09-15 10:33 | UNITARY PRODUCTS GROUP - D1NA036N05606C | 67 | 0 | Yes | Yes | 20.3 | 20.7 | -0.4 | C4DD1F4682D940C5AFF5679B792EDBF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4823 |  | 2015-09-01 | 2015-09-01 12:06 | 2015-09-01 12:06 | PAYNE - PY1PNB036060ABAA | 70 | 0 | Yes | Yes | 18.9 | 21.5 | -2.6 | 55BCC0D3496A4F37A3C759B16FC06289 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7338 |  | 2015-09-15 | 2015-09-15 09:58 | 2015-09-15 09:58 | BRYANT - 563CN030-C | 100 | 0 | Yes | Yes | 22.3 | 20.9 | 1.4 | 8A70FFC54D0342D4804CA50626B6DBAE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7330 |  | 2015-08-07 | 2015-08-07 10:26 | 2015-08-07 10:26 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 19.1 | 18.3 | 0.8 | 68D0C745934E4C5BADBAB9FEB03B581D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6216 |  | 2015-07-29 | 2015-07-29 15:18 | 2015-07-29 15:18 | CARRIER - 38BRC048370 | 141 | 0 | Yes | Yes | 18.4 | 20.4 | -2 | B64235278A8D4914817707EA083D9D81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7290 |  | 2015-09-15 | 2015-09-15 12:43 | 2015-09-15 12:43 | RUUD - 12AJB36A01 | 117 | 0 | Yes | Yes | 22.4 | 20.9 | 1.5 | 201F8209682E44D5ADC10AD919EE0C9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7763 |  | 2015-07-30 | 2015-07-30 15:14 | 2015-07-30 15:14 | RHEEM - RAKA060JAZ | 85 | 0 | Yes | Yes | 26.2 | 20.4 | 5.8 | B42532483F6543A188F32416EA696A64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9301 |  | 2015-11-18 | 2015-11-18 09:22 | 2015-11-18 09:22 | CARRIER - 38BRB042300 | 135 | 0 | Yes | Yes | 18.4 | 18.8 | -0.4 | E5B73FCE3B274A9CB1DDCF90281DB6D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6620 |  | 2015-08-18 | 2015-08-18 12:57 | 2015-08-18 12:57 | TRANE - BTR730E100A0 | 138 | 0 | Yes | Yes | 18.5 | 15.8 | 2.7 | 358F7E8BCC104C0CBEF6493DF509D5E1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5857 |  | 2015-07-30 | 2015-07-30 08:30 | 2015-07-30 08:59 | LENNOX - HS26-060-4P | 162 | 13.1 | Yes | Yes | 25 | 20.4 | 4.6 | F2DC68723D8C4F84B1242D566F9B33EE |  | R22 | Non-TXV |  | 8.086% | 0.91914 | 15.54% | [5 empty] | Non-TXV | 8.086%
Woodland | CA | 95695-9359 |  | 2015-10-19 | 2015-10-19 12:08 | 2015-10-19 12:08 | CARRIER - UNK | 85 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 5A56D5222B3A4A4DBE3AE45DA217C821 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 18:32 | 2015-08-05 18:32 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 21.8 | 22.6 | -0.8 | 6F7018EF10964C169D50FA73D8B78CE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2905 |  | 2015-07-28 | 2015-07-28 11:04 | 2015-07-28 11:04 | TRANE - TTYO36A100AO | 310 | 0 | Yes | Yes | 23.2 | 19.3 | 3.9 | 99D512D5AE2B45A594298330B231F0D3 |  | R22 | TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1318 |  | 2015-08-14 | 2015-08-14 10:14 | 2015-08-14 10:35 | CARRIER - 38CK036310 | 72 | 20.4 | Yes | Yes | 21.3 | 17.7 | 3.6 | 5577CE2C31C94362B141839B3FA6F235 |  | R22 | TXV |  | 28.33% | 0.71667 | 54.45% | [5 empty] | TXV | 28.33%
Brentwood | CA | 94513-5475 |  | 2015-09-01 | 2015-09-01 11:07 | 2015-09-01 11:31 | PAYNE - PA13NR048-H | 141 | 12.6 | Yes | Yes | 19.6 | 18.7 | 0.9 | 57048B83ACCC4257901865E391CF49D5 |  | R22 | TXV |  | 8.936% | 0.91064 | 17.17% | [5 empty] | TXV | 8.936%
Antioch | CA | 94509-6022 |  | 2015-09-19 | 2015-09-19 15:13 | 2015-09-19 15:13 | TEMPSTAR - 30MCD-000094CR | 63 | 0 | Yes | Yes | 22.5 | 21.3 | 1.2 | 51259BFB16574E87B037A3B3B6119BDD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3216 |  | 2015-07-23 | 2015-07-23 08:51 | 2015-07-23 08:51 | AMANA - RCB48B2D | 112 | 0 | Yes | Yes | 17.6 | 17.7 | -0.1 | A6FD7081CEAA4506B38F71D2E2FD11D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1512 |  | 2015-08-12 | 2015-08-12 14:02 | 2015-08-12 14:02 | CARRIER - N2A330AKC100 | 67 | 0 | Yes | Yes | 18.2 | 20.7 | -2.5 | 1DEA0C3609BC4D39A9B292CD85F03FD8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5430 |  | 2015-08-18 | 2015-08-18 14:08 | 2015-08-18 14:08 | CARRIER - 597BN048 | 169 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | 32753E510FAE46548DA6A115FCF3F2C5 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4202 |  | 2015-09-23 | 2015-09-23 14:08 | 2015-09-23 14:08 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 20.1 | 22.6 | -2.5 | DC9A97FDDFD34CCF8E1B5E6B163434BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6397 |  | 2015-09-15 | 2015-09-15 16:30 | 2015-09-15 16:30 | UNITARY PRODUCTS GROUP - D2NZ036N05606NXA | 112 | 0 | Yes | Yes | 23.3 | 19.7 | 3.6 | 56CFB54D403F403086227C8503285CB0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3927 |  | 2015-10-28 | 2015-10-28 11:55 | 2015-10-28 11:56 | YORK - D2NP036N05606A | 108 | 22.4 | Yes | Yes | 19.2 | 18.8 | 0.4 | 7B5B020E654B4C7F861C2B858895B336 |  | R22 | Non-TXV |  | 20.74% | 0.79259 | 39.86% | [5 empty] | Non-TXV | 20.74%
Bakersfield | CA | 93304-3424 |  | 2015-07-27 | 2015-07-27 09:12 | 2015-07-27 09:12 | GOODMAN - VSC130301AA | 106 | 0 | Yes | Yes | 17.2 | 20.1 | -2.8 | C65F754B0F5446299ED1B1FD35ACA195 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2276 |  | 2015-08-19 | 2015-08-19 13:07 | 2015-08-19 13:07 | TRANE - 2TTX4036B1000AA | 118 | 0 | Yes | Yes | 19.7 | 18.9 | 0.8 | EC7571631501427684ABF09B1A21204B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2314 |  | 2015-10-09 | 2015-10-09 09:44 | 2015-10-09 09:44 | PAYNE - PA10JA036-A | 85 | 0 | Yes | Yes | 19.8 | 20.3 | -0.5 | DE1C5B3130514FFFA3414DEC09F48E89 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6762 |  | 2015-07-14 | 2015-07-14 09:08 | 2015-07-14 09:08 | GOODMAN - DS5BD030K | 134 | 0 | Yes | Yes | 18.2 | 19.7 | -1.5 | 2A08C90073D446E7900EEFDEA7E2C2DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-05 | 2015-08-05 09:28 | 2015-08-05 09:28 | ICP - C4A336GKD200 | 85 | 0 | Yes | Yes | 19.4 | 19.5 | -0.1 | 5543A9F15478400EBEF43544D86DC5B2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6818 |  | 2015-09-23 | 2015-09-23 09:49 | 2015-09-23 10:16 | CARRIER - CCGD48S41Q3A | 57 | 8.2 | Yes | Yes | 23.5 | 22 | 1.5 | 6B228919F6EA4986BDB6BBCE5F3DB3E7 |  | R410A | Non-TXV |  | 14.39% | 0.85614 | 27.65% | [5 empty] | Non-TXV | 14.39%
Bakersfield | CA | 93309-5927 |  | 2015-10-12 | 2015-10-12 12:54 | 2015-10-12 12:54 | ICP - PGD442060K001C1 | 138 | 0 | Yes | Yes | 21.4 | 20.7 | 0.7 | F5274C104CD54851B1539A2B54BB140C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9128 |  | 2015-07-21 | 2015-07-21 12:20 | 2015-07-21 12:20 | GOODMAN - CKL60-1 | 115 | 0 | Yes | Yes | 10.1 | 10 | 0.1 | 9325F893ABF9416EA6E1CEFE964D02A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4236 |  | 2015-09-29 | 2015-09-29 09:21 | 2015-09-29 09:21 | AMERICAN STANDARD - 4A7A6036B1000AA | 106 | 0 | Yes | Yes | 19.4 | 18.8 | 0.6 | 33B23CAA08D04C61AD0C1B36771F18BD |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4025 |  | 2015-07-31 | 2015-07-31 17:44 | 2015-07-31 17:44 | CARRIER - 38TR042330 | 112 | 0 | Yes | Yes | 25.4 | 20.4 | 5 | 1FE93C622EE24229A2BA142410DA2223 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4249 |  | 2015-08-21 | 2015-08-21 15:12 | 2015-08-21 15:12 | CARRIER - CKL-241F | 72 | 0 | Yes | Yes | 20 | 18.2 | 1.8 | 0B53A8C72F5D4E65B92CC42FC6DEF24B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4978 |  | 2015-10-14 | 2015-10-14 16:24 | 2015-10-14 16:24 | CARRIER - 38BRG030 | 85 | 0 | Yes | Yes | 19.4 | 18.5 | 0.9 | 935B0F2B8F1745A9AEEFB6ED0317174C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5721 |  | 2015-08-31 | 2015-08-31 11:03 | 2015-08-31 11:26 | AIRE-FLO - 4AC13L36P-7A | 84 | -28.5 | Yes | Yes | 21.1 | 18.8 | 2.3 | AB9B06586BD44E2EB00710089AE22ACB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -33.93% | 1.3393 | 9.502% |  |  |  |  | Non-TXV |  |  | -33.93%
Concord | CA | 94521-2692 |  | 2015-07-21 | 2015-07-21 16:08 | 2015-07-21 16:08 | CARRIER - 38TRA024320 | 83 | 0 | Yes | Yes | 21.2 | 19.3 | 1.9 | 2D05CBCD2532412A801228ACFD70E3F9 | Actual Subcooling cannot be negative. Please check entries. | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2313 |  | 2015-07-21 | 2015-07-21 10:23 | 2015-07-21 10:23 | CARRIER - 48ESNA3606030 | 100 | 0 | Yes | Yes | 25.5 | 19.9 | 5.6 | 39D3239CC3454C0FAFA2CCB36EDC1AA9 |  | R410A | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-4464 |  | 2015-08-07 | 2015-08-07 12:37 | 2015-08-07 12:37 | COMFORT AIRE - CAC036AKA1 | 80 | 0 | Yes | Yes | 17.9 | 19.9 | -2 | 71F42CF093C94849BA3016223EED8D91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2427 |  | 2015-10-09 | 2015-10-09 14:16 | 2015-10-09 14:44 | RUUD - 0ANA--030JRZ | 94 | 25.3 | Yes | Yes | 18.4 | 19.9 | -1.5 | 5F82736B979449D4886FAC4FAB8CD0A8 |  | R22 | Non-TXV |  | 26.91% | 0.73085 | 51.72% | [5 empty] | Non-TXV | 26.91%
Davis | CA | 95618-2575 |  | 2015-11-12 | 2015-11-12 13:14 | 2015-11-12 13:14 | BRYANT - 187BNA048-A | 185 | 0 | Yes | Yes | 17.2 | 18.3 | -1.1 | 71A73244A68D4CED847E65270FFF8CD6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7055 |  | 2015-07-31 | 2015-07-31 15:52 | 2015-07-31 15:52 | CARRIER - CA13NA036C | 75 | 0 | Yes | Yes | 20.5 | 19.5 | 1 | 67DBC06C5E544A66BE7DF0D861C4BE15 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3843 |  | 2015-07-22 | 2015-07-22 10:55 | 2015-07-22 10:55 | WESTINGHOUSE - IE030BAA0N | 90 | 0 | Yes | Yes | 19.9 | 20.6 | -0.6 | 9DEBD592B1934A99984B2E7A3BD663D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8659 |  | 2015-07-20 | 2015-07-20 16:05 | 2015-07-20 16:05 | OTHER - UNK | 84 | 0 | Yes | Yes | 23.7 | 21.3 | 2.4 | A727F84ADFF64353A6BA7E36278DC048 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8501 |  | 2015-07-22 | 2015-07-22 11:57 | 2015-07-22 12:21 | GOODMAN - CKL49-1 | 111 | 9.7 | Yes | Yes | 20.2 | 19.3 | 0.9 | 2C80E836EFC54E7C8059E4B7E2CFF1D9 |  | R22 | Non-TXV |  | 8.739% | 0.91261 | 16.79% | [5 empty] | Non-TXV | 8.739%
Antioch | CA | 94531-7813 |  | 2015-07-23 | 2015-07-23 10:46 | 2015-07-23 10:46 | CARRIER - 38CK048 | 85 | 0 | Yes | Yes | 20.7 | 18.8 | 1.9 | 8B49A1E484BB4CA9BBAD41AEE5028352 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7602 |  | 2015-08-20 | 2015-08-20 09:23 | 2015-08-20 09:46 | CARRIER - 38BRC036330 | 101 | 15 | Yes | Yes | 7 | 16.8 | -9.8 | B0F89149B95344D59D61FFE80CE244ED | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.85% | 0.85149 | 28.54% | [5 empty] | Non-TXV | 14.85%
Antioch | CA | 94509-5768 |  | 2015-07-21 | 2015-07-21 14:38 | 2015-07-21 14:38 | YORK - H2RA036S06E | 63 | 0 | Yes | Yes | 18.1 | 19.8 | -1.7 | C0F962E0F2A541ACBBBE292AD6AF49D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8507 |  | 2015-08-05 | 2015-08-05 18:34 | 2015-08-05 18:34 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 22.9 | 23.1 | -0.2 | 7E7D4C37BB744464B5ADDF3037BDFECF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1637 |  | 2015-07-30 | 2015-07-30 10:39 | 2015-07-30 10:39 | GOODMAN - VSX130421AB | 90 | 0 | Yes | Yes | 21.1 | 22 | -0.9 | 26619CC7672247348699E365751C5BA4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-1012 |  | 2015-07-31 | 2015-07-31 09:34 | 2015-07-31 09:34 | OTHER - 5616JO36-C | 72 | 0 | Yes | Yes | 24.1 | 18.6 | 5.5 | 05D2A755A6EE481E9FCEE69395E14042 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8508 |  | 2015-08-05 | 2015-08-05 18:23 | 2015-08-05 18:23 | RHEEM - RRMA-A030JK06X | 80 | 0 | Yes | Yes | 20.7 | 23.1 | -2.4 | 2016569979F84E2E94B9A2D7C079F0C8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7333 |  | 2015-07-17 | 2015-07-17 10:03 | 2015-07-17 10:03 | - | 85 | -8 | Yes | Yes | 18.2 | 18.2 | 0 | FC8AD80B92554508930084867CC6A3E7 | Remove refrigerant: 8 oz | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Vallejo | CA | 94591-6374 |  | 2015-07-22 | 2015-07-22 10:50 | 2015-07-22 10:50 | CARRIER - 38CKC030330 | 85 | -5 | Yes | Yes | 19.2 | 18.6 | 0.6 | E1E8AB2FB6D24290915B07C83AEB8E6E | Remove refrigerant: 5 oz Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Pittsburg | CA | 94565-3661 |  | 2015-08-25 | 2015-08-25 10:17 | 2015-08-25 10:17 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 16.3 | 19.3 | -3 | 1178C42CCF5D43E9BCA0C468D68E3834 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1629 |  | 2015-08-06 | 2015-08-06 14:13 | 2015-08-06 14:13 | UNITARY PRODUCTS GROUP - D1NH048N06506C | 128 | 0 | Yes | Yes | 21.3 | 20.5 | 0.8 | CBD8BC984C244432BF3D3B4B67BFDB4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8160 |  | 2015-07-22 | 2015-07-22 10:39 | 2015-07-22 10:39 | GOODMAN - UNK | 85 | 0 | Yes | Yes | 21.7 | 20.2 | 1.6 | B8976ABAF19741B9AC52299C842E79F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9204 |  | 2015-08-12 | 2015-08-12 11:31 | 2015-08-12 11:31 | RHEEM - RAJC-030JAS | 88 | 0 | Yes | Yes | 23 | 19.9 | 3.1 | 0410E6F4BC324E488266ED6400D9DDDE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8506 |  | 2015-08-05 | 2015-08-05 09:37 | 2015-08-05 09:37 | ICP - PGD336060K001C1 | 105 | 0 | Yes | Yes | 20 | 18.8 | 1.2 | AB74F85CCD5B4AE0BEA9ABEE72B9007F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1696 |  | 2015-09-17 | 2015-09-17 13:14 | 2015-09-17 13:34 | GOODMAN - GSC130601CB | 131 | 22.3 | Yes | Yes | 22.9 | 22.9 | 0.1 | 6B5FF6BBBF84464BBB6FCA791635A748 |  | R22 | Non-TXV |  | 17.02% | 0.82977 | 32.71% | [5 empty] | Non-TXV | 17.02%
Pittsburg | CA | 94565-4869 |  | 2015-09-01 | 2015-09-01 14:05 | 2015-09-01 14:05 | TRANE - 10AACC-036-230 | 74 | 0 | Yes | Yes | 18.2 | 21 | -2.8 | 4C0DA5F597DF40DD8782934FA2CEF91D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2342 |  | 2015-08-06 | 2015-08-06 13:22 | 2015-08-06 13:22 | TRANE - TTB036C100A1 | 90 | 0 | Yes | Yes | 18.7 | 18.8 | -0.1 | 50F485FBAE0141A78510C308CDC304A6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3778 |  | 2015-10-29 | 2015-10-29 12:33 | 2015-10-29 12:33 | CARRIER - 38ENO15310 | 52 | 0 | Yes | Yes | 20.2 | 19.3 | 0.9 | 27AD46BDBB1B420094C7A8A9B44DBC3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3781 |  | 2015-10-29 | 2015-10-29 11:59 | 2015-10-29 11:59 | CARRIER - 38EN015310 | 50 | 0 | Yes | Yes | 17.9 | 19.9 | -2 | B6671DBBEADD4DE9A433F940DE5E47B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1540 |  | 2015-10-08 | 2015-10-08 11:14 | 2015-10-08 11:14 | PAYNE - PA13NA042C | 101 | 0 | Yes | Yes | 20.1 | 20.4 | -0.3 | 1B32AFA7463546FEBD247203BB74C7F0 |  | R410A | TXV |  | 0% | 1 | 0%
Winters | CA | 95694-1621 |  | 2015-10-28 | 2015-10-28 12:35 | 2015-10-28 12:35 | PAYNE - PA10J030-C | 77 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | 218A0A89A09B48308B78CBCC3A3FB280 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6438 |  | 2015-10-06 | 2015-10-06 10:58 | 2015-10-06 10:58 | GOODMAN - GPG1336045M41AC | 85 | 0 | Yes | Yes | 20.6 | 22.6 | -2 | C030B24FAEB74D52ADF92DEA6AFB58E4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5158 |  | 2015-07-29 | 2015-07-29 15:58 | 2015-07-29 15:58 | YORK - 38BR036300 | 117 | 0 | Yes | Yes | 24.1 | 22.5 | 1.6 | 31D4B94648D04135A2547F37486526B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6331 |  | 2015-09-17 | 2015-09-17 15:02 | 2015-09-17 15:02 | ICP - PGAA42C1K3 | 82 | 0 | Yes | Yes | 23.9 | 21.5 | 2.4 | C43B3525D0944A6CB4074CAF1E1856CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5941 |  | 2015-07-09 | 2015-07-09 14:55 | 2015-07-09 14:55 | TRANE - 2TTR1048A1000AA | 85 | 0 | Yes | Yes | 16.7 | 18.3 | -1.6 | C56B34B717CA477DA03E807BFCCB7637 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3346 |  | 2015-07-09 | 2015-07-09 13:38 | 2015-07-09 13:38 | GE - UNK | 85 | 0 | Yes | Yes | 20.1 | 19.9 | 0.2 | C8E5C123558A439FB888ADA8C9B09AE7 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1836 |  | 2015-08-10 | 2015-08-10 10:58 | 2015-08-10 10:58 | CARRIER - UNK | 85 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | 56C4CF8DB2524ABE8CD21E4E2C312702 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1139 |  | 2015-08-06 | 2015-08-06 14:52 | 2015-08-06 14:52 | TRANE - TTB036C100A2 | 90 | 0 | Yes | Yes | 20.1 | 21.5 | -1.4 | CCC58129F74C46908D6D255723585B30 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2951 |  | 2015-08-26 | 2015-08-26 10:14 | 2015-08-26 10:14 | TRANE - 4YCZ6048A1096BA | 136 | 0 | Yes | Yes | 20.2 | 21.5 | -1.3 | 3355E6C5BB454253ADE328D7407806E6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4445 |  | 2015-07-09 | 2015-07-09 09:03 | 2015-07-09 09:03 | TRANE - YCY048G1HOAD | 85 | 0 | Yes | Yes | 24.2 | 18.8 | 5.4 | 76879DFE7044444FA1317B918ED5D6C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4410 |  | 2015-09-08 | 2015-09-08 15:00 | 2015-09-08 15:00 | LENNOX - 13ACC-36-230-1 | 115 | 0 | Yes | Yes | 20.5 | 19.4 | 1.1 | E53CA3058041411D875F0E9A212CF322 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6256 |  | 2015-08-25 | 2015-08-25 11:56 | 2015-08-25 11:56 | ALLEGIANCE - 2A7A4048A1000AA | 150 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | CDCB199EF7FF4CADA58EB978DD255859 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3623 |  | 2015-08-20 | 2015-08-20 14:59 | 2015-08-20 14:59 | OTHER - CA9630VKC1 | 121 | 0 | Yes | Yes | 16.8 | 18.5 | -1.7 | 6034ED6AF276499D8F3DEB87B7D00947 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7634 |  | 2015-09-01 | 2015-09-01 12:51 | 2015-09-01 12:51 | OTHER - GCGD42S21S2C | 130 | 0 | Yes | Yes | 18.9 | 21 | -2.1 | B13D272FA71B43D0832005AFC7620A13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5727 |  | 2015-08-13 | 2015-08-13 10:19 | 2015-08-13 10:19 | YORK - H2RC048S06A | 119 | 0 | Yes | Yes | 22.5 | 19.5 | 3 | C6A1504D02444134AF28F90557A472DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3086 |  | 2015-10-09 | 2015-10-09 10:47 | 2015-10-09 10:47 | KENMORE - CA5542VKD2 | 98 | 0 | Yes | Yes | 25.5 | 21.5 | 4 | F20CC9D86A7447FFB48ACD8D60D4F9F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2636 |  | 2015-07-29 | 2015-07-29 10:15 | 2015-07-29 10:15 | LENNOX - UNK | 85 | 0 | Yes | Yes | 23.2 | 19.9 | 3.3 | 94B4AC038B2247EE9743E6CCB5CE2A6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Richmond | CA | 94801-1730 |  | 2015-07-13 | 2015-07-13 09:14 | 2015-07-13 09:14 | CARRIER - 24ABA342A310 | 319 | 0 | Yes | Yes | 15.2 | 17.7 | -2.5 | BEF5759C20FC40CF97DC79627B16B4A5 |  | R22 | TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-2100 |  | 2015-07-23 | 2015-07-23 12:22 | 2015-07-23 12:22 | YORK - 82RAO30SO6D | 85 | 0 | Yes | Yes | 18.3 | 18.8 | -0.5 | 239955671BBB483B935F20AAD5A1A202 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4509 |  | 2015-08-25 | 2015-08-25 12:28 | 2015-08-25 12:28 | CARRIER - PA13NA036-E | 71 | 0 | Yes | Yes | 23 | 18.8 | 4.2 | AD5D192C07F74308B20F27C36AA4A8E9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1558 |  | 2015-08-13 | 2015-08-13 09:22 | 2015-08-13 09:22 | GOODMAN - GSX130301BA | 84 | 0 | Yes | Yes | 23.8 | 18.8 | 5 | 03A1459BB0B044EFB49E793E99638E80 |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5971 |  | 2015-08-20 | 2015-08-20 11:23 | 2015-08-20 11:23 | OTHER - CA5536VKD1 | 82 | 0 | Yes | Yes | 13.4 | 17.1 | -3.7 | 05724FBA638A4ECC9B1D3798B18AE72A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-3212 |  | 2015-08-10 | 2015-08-10 14:38 | 2015-08-10 14:38 | BRYANT - 165ANA036 | 165 | 0 | Yes | Yes | 15.9 | 18.5 | -2.6 | 0F9463ABCD034916AFD1B5E896767356 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3410 |  | 2015-07-21 | 2015-07-21 08:57 | 2015-07-21 08:57 | PAYNE - 561CJO36 | 72 | 0 | Yes | Yes | 17.3 | 18.5 | -1.2 | 90164E916C5143938D6AF9D9D7B9CFC6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6311 |  | 2015-07-28 | 2015-07-28 08:49 | 2015-07-28 08:49 | BRYANT - 567A048D | 68 | 0 | Yes | Yes | 25.5 | 19.6 | 5.9 | EEE96DC32FB64459B0B0665DE4DAC899 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9118 |  | 2015-09-04 | 2015-09-04 16:44 | 2015-09-04 16:44 | GOODMAN - CK60-1C | 115 | 0 | Yes | Yes | 21.6 | 22.1 | -0.5 | 32A42595B3DA422CA0AC1398D8D8AE5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2554 |  | 2015-08-05 | 2015-08-05 13:23 | 2015-08-05 13:23 | TRANE - TTB024C100A2 | 85 | 0 | Yes | Yes | 15.9 | 18.8 | -2.9 | 2BCEBF952C0746B6BC5ADEB32A779D01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8831 |  | 2015-09-16 | 2015-09-16 10:32 | 2015-09-16 10:32 | BRYANT - 113ANA048-E | 112 | 0 | Yes | Yes | 23.2 | 19 | 4.2 | 7AC0F1194CC540B494045F5E030DF7BB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-3749 |  | 2015-07-20 | 2015-07-20 08:51 | 2015-07-20 08:51 | ALLEGIANCE - 2A7A1042A1000AA | 85 | 0 | Yes | Yes | 18.4 | 18.8 | -0.4 | 527FDD08853B448B9CE09991727AB045 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3728 |  | 2015-10-19 | 2015-10-19 12:28 | 2015-10-19 12:28 | ALLEGIANCE - 7A0018A100A2 | 61 | 0 | Yes | Yes | 18.7 | 17.9 | 0.8 | ACFC4146E33942658DE76A301CAD1697 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-3846 |  | 2015-07-07 | 2015-07-07 12:00 | 2015-07-07 12:00 | PAYNE - PA12NAO48B | 151 | 0 | Yes | Yes | 28.8 | 23.1 | 5.7 | 3D26149BA72C4F5F922CD96168BB7634 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3064 |  | 2015-09-11 | 2015-09-11 11:00 | 2015-09-11 11:00 | GOODMAN - 0SH13018AC | 107 | 0 | Yes | Yes | 17.8 | 20 | -2.2 | DD374D144076410083341C5C80F16D4D |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5230 |  | 2015-08-13 | 2015-08-13 09:57 | 2015-08-13 10:16 | HEIL - N2A342AKA100 | 62 | 8.5 | Yes | Yes | 21.5 | 21.8 | -0.3 | 68B7577B10904B3BB9D44184F34A3ED1 |  | R22 | Non-TXV |  | 13.71% | 0.8629 | 26.35% | [5 empty] | Non-TXV | 13.71%
Antioch | CA | 94509-3064 |  | 2015-09-11 | 2015-09-11 14:44 | 2015-09-11 14:44 | GOODMAN - GSH130181AC | 127 | 0 | Yes | Yes | 15.8 | 18.5 | -2.7 | F43888EE984C4BA6BF11E9E2723E7DC7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5420 |  | 2015-07-27 | 2015-07-27 14:44 | 2015-07-27 14:44 | YORK - YCJD36S41S1HA | 73 | 0 | Yes | Yes | 19.4 | 20.2 | -0.8 | 4049AC0F87CA46F9ABF067FF9AFE898F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5416 |  | 2015-08-19 | 2015-08-19 14:16 | 2015-08-19 14:16 | YORK - UNK | 105 | 0 | Yes | Yes | 23.7 | 19.3 | 4.4 | C4A3B354C8104631BC7D63B8820D34DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2203 |  | 2015-09-16 | 2015-09-16 09:43 | 2015-09-16 10:09 | YORK - DAYP-F030N070A | 148 | 14.1 | Yes | Yes | 20 | 19.1 | 0.9 | 536F73268E9341B48E41EA9B48B910D4 |  | R22 | Non-TXV |  | 9.527% | 0.90473 | 18.31% | [5 empty] | Non-TXV | 9.527%
Antioch | CA | 94509-5671 |  | 2015-07-29 | 2015-07-29 09:47 | 2015-07-29 09:47 | GOODMAN - CK30-18 | 76 | 0 | Yes | Yes | 18.6 | 21.5 | -2.9 | A06333A70FEF4B84A103151251F7E7FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2886 |  | 2015-09-16 | 2015-09-16 09:10 | 2015-09-16 09:10 | RHEEM - RRNA-B042JK08K | 104 | 0 | Yes | Yes | 19.9 | 22.4 | -2.5 | FCAB13E9B992425BBC737A5923C47249 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3329 |  | 2015-07-27 | 2015-07-27 09:43 | 2015-07-27 09:43 | YORK - D2NP024N03606NXB | 100 | 0 | Yes | Yes | 20.3 | 18.7 | 1.6 | 73E905B205DB4472A23DC584A4239B49 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2995 |  | 2015-08-12 | 2015-08-12 15:14 | 2015-08-12 15:14 | CARRIER - 24ABA360A310 | 132 | 0 | Yes | Yes | 18.5 | 21.5 | -3 | F150051251164FFEBACCEB7978B30914 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7308 |  | 2015-07-31 | 2015-07-31 14:51 | 2015-07-31 15:10 | LENNOX - 10ACC-036-230-02 | 77 | -7.2 | Yes | Yes | 26.8 | 21.3 | 5.5 | B501EFA25D8645848975AE0F21A876FC |  | R22 | Non-TXV |  | -9.351% | 1.0935 | 2.619% |  |  |  |  | Non-TXV |  |  | -9.351%
W Sacramento | CA | 95691-3735 |  | 2015-11-06 | 2015-11-06 15:09 | 2015-11-06 15:09 | HEIL - PGAA24B1K1 | 64 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | B4ACFB8D7A2746009B76AF1B79A9A9B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3312 |  | 2015-07-27 | 2015-07-27 09:22 | 2015-07-27 09:22 | YORK - D3NZ036N05606NXA | 85 | 0 | Yes | Yes | 22.5 | 20.2 | 2.3 | 867851B69D40444D9025D83457F40124 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5772 |  | 2015-08-25 | 2015-08-25 10:54 | 2015-08-25 10:54 | RHEEM - UNKNOWN | 89 | 0 | Yes | Yes | 20.6 | 20.2 | 0.4 | B0ECB7072D284244BA9109EDB7C361EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9382 |  | 2015-08-06 | 2015-08-06 12:13 | 2015-08-06 12:13 | CARRIER - 24ACA4448A0030010 | 176 | 0 | Yes | Yes | 20.7 | 19.9 | 0.8 | EF552215690F411DAF3D33AB5F03EE31 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3348 |  | 2015-07-27 | 2015-07-27 08:47 | 2015-07-27 08:47 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 23.7 | 19.1 | 4.6 | 954044D8EA4146998D61841B2AD8C501 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3732 |  | 2015-11-04 | 2015-11-04 15:43 | 2015-11-04 15:43 | CARRIER - 38CKC024330 | 55 | 0 | Yes | Yes | 21.5 | 19.3 | 2.2 | 32E5194F64154B28B941A489353A957B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3724 |  | 2015-11-05 | 2015-11-05 10:09 | 2015-11-05 10:09 | AMERICAN STANDARD - 7B0017B100A1 | 47 | 0 | Yes | Yes | 23.2 | 18.6 | 4.6 | D1331D78884C457B92574CBADCD0BCAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2468 |  | 2015-09-16 | 2015-09-16 10:24 | 2015-09-16 10:24 | OTHER - UNKNOWN | 61 | 0 | Yes | Yes | 20.1 | 19.7 | 0.4 | 6943DE01598B420DA4DBA17E49B4D3B5 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2948 |  | 2015-10-13 | 2015-10-13 11:41 | 2015-10-13 11:41 | RHEEM - N/A | 85 | 0 | Yes | Yes | 20.2 | 22.5 | -2.3 | 21D8B47698414C88A5380DF69FBC70AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-5463 |  | 2015-08-28 | 2015-08-28 12:09 | 2015-08-28 12:56 | AMERICAN STANDARD - HAC024AKC4 | 68 | 6.4 | Yes | Yes | 17.4 | 18.1 | -0.7 | F137DDD9BCDF4B77844E6D42F39ACCA9 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Antioch | CA | 94531-8333 |  | 2015-07-31 | 2015-07-31 11:15 | 2015-07-31 11:15 | CARRIER - 38TH048320 | 85 | 0 | Yes | Yes | 26.2 | 20.6 | 5.7 | 779B6AFACFC1450994E49DE62EDC0D95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3749 |  | 2015-09-25 | 2015-09-25 14:35 | 2015-09-25 14:35 | - UNKNOWN | 93 | 0 | Yes | Yes | 17.2 | 18.8 | -1.6 | 1B66E3D0A72A42F3A650B7A76456939C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5927 |  | 2015-08-21 | 2015-08-21 17:25 | 2015-08-21 17:25 | LENNOX - 14ACX047239001 | 179 | 0 | Yes | Yes | 18.2 | 19.3 | -1.1 | 665576BBEFF64979AE7C9452EB9A0A37 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5637 |  | 2015-08-21 | 2015-08-21 15:15 | 2015-08-21 15:15 | CARRIER - 38EZGO48300 | 85 | 0 | Yes | Yes | 21.3 | 19.5 | 1.8 | 0573341BF5084F3EA3BFEB12116AF91D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2639 |  | 2015-08-25 | 2015-08-25 13:25 | 2015-08-25 13:25 | CARRIER - 38CKC0 | 70 | 0 | Yes | Yes | 24.3 | 20.7 | 3.7 | 9057DCE1C85F47F8ABCA72F1AD6D7CA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3003 |  | 2015-07-28 | 2015-07-28 08:17 | 2015-07-28 08:17 | BRYANT - 561CJX042000ABAA | 93 | 0 | Yes | Yes | 18.7 | 18.8 | -0.1 | 2421A8FA684E483C8E58495B54DA6370 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6471 |  | 2015-08-25 | 2015-08-25 15:22 | 2015-08-25 15:22 | YORK - H1RA048SO6D | 117 | 0 | Yes | Yes | 17.2 | 20.2 | -3 | 89888268CCDC494DAEA96C7FE7575556 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7061 |  | 2015-09-16 | 2015-09-16 16:19 | 2015-09-16 16:19 | ARMSTRONG - PGE10A24D050A-3A | 52 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | AD1669959D844025833BC66A429A9127 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1534 |  | 2015-08-03 | 2015-08-03 13:36 | 2015-08-03 13:58 | UNITARY PRODUCTS GROUP - H2RD036S06B | 85 | 3.9 | Yes | Yes | 18.6 | 18.2 | 0.4 | 82E9C8F585FD4F6AAF8E6B1D2C4950F6 |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Antioch | CA | 94531-8087 |  | 2015-08-03 | 2015-08-03 11:26 | 2015-08-03 11:26 | CARRIER - 38CKC048300 | 85 | 0 | Yes | Yes | 24.7 | 21 | 3.7 | 6661C81F01ED47EA93FE3DD60D55482A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1534 |  | 2015-08-25 | 2015-08-25 12:35 | 2015-08-25 12:35 | TRANE - 2TTB3036A1000AA | 101 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | 9CCA809A619E4BC683BE6732C79C3038 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6455 |  | 2015-08-25 | 2015-08-25 14:46 | 2015-08-25 15:05 | OTHER - UNKNOWN | 167 | 14.6 | Yes | Yes | 16.6 | 16.6 | 0 | 40D23F47A1A7413F9665DCB4F96CD7FA |  | R22 | Non-TXV |  | 8.743% | 0.91257 | 16.8% | [5 empty] | Non-TXV | 8.743%
Pittsburg | CA | 94565-6453 |  | 2015-08-24 | 2015-08-24 11:34 | 2015-08-24 11:34 | OTHER - ACD48X102A | 117 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 388BFA96CEEC4A9D855A97129502738E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6024 |  | 2015-11-04 | 2015-11-04 13:30 | 2015-11-04 13:30 | TRANE - TTR036C100A3 | 87 | 0 | Yes | Yes | 21.1 | 20.6 | 0.5 | CF746E61C17A48008B73186081A873DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7372 |  | 2015-09-15 | 2015-09-15 10:13 | 2015-09-15 10:13 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 17.1 | 19.4 | -2.3 | DF8F6C4BB9CE41529B10F3DBE87E3E94 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3746 |  | 2015-09-16 | 2015-09-16 11:22 | 2015-09-16 11:22 | TRANE - 4YCC3030A1075AA | 97 | 0 | Yes | Yes | 24.4 | 20.2 | 4.2 | 100F160B62BC4581BEC76D16AEEFE53C |  | R410A | TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-2225 |  | 2015-08-26 | 2015-08-26 12:53 | 2015-08-26 12:53 | TRANE - TTR030C10AA | 66 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | BA9F3099666B4227884D78D533973F5B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5970 |  | 2015-09-17 | 2015-09-17 09:47 | 2015-09-17 10:03 | LENNOX - 13GCSXA-48-083X-230-2A | 100 | 28.1 | Yes | Yes | 25.4 | 20.4 | 5 | F8FC1CC51C9B41818D04F004B6D74795 |  | R410A | Non-TXV |  | 28.1% | 0.719 | 54% | [5 empty] | Non-TXV | 28.1%
Antioch | CA | 94509-4724 |  | 2015-07-08 | 2015-07-08 14:01 | 2015-07-08 14:01 | CARRIER - 24ABA348A310 | 128 | 0 | Yes | Yes | 17.2 | 17.5 | -0.3 | 00E346AF64D246D99F19009B8AEDB877 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2636 |  | 2015-10-02 | 2015-10-02 15:28 | 2015-10-02 15:28 | PAYNE - PA13NR036-J | 85 | 0 | Yes | Yes | 17.9 | 18.5 | -0.6 | 8396392BFE00449B8AFD83EBE4C42DBF |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1147 |  | 2015-08-05 | 2015-08-05 09:37 | 2015-08-05 09:37 | CARRIER - 388RC048350 | 85 | 0 | Yes | Yes | 13.7 | 16.7 | -3 | A1072762F2E545689EA15AE3BD313CA6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6373 |  | 2015-08-11 | 2015-08-11 10:18 | 2015-08-11 10:18 | CARRIER - 38CKC30330 | 85 | 0 | Yes | Yes | 15.8 | 18.6 | -2.8 | B550B505F3ED46B5A03A4CDAD6F42A72 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2135 |  | 2015-09-23 | 2015-09-23 10:48 | 2015-09-23 10:48 | GE - BTB930A100A3 | 53 | 0 | Yes | Yes | 18.4 | 18.7 | -0.3 | B4D7EF12688E4208A333EF398D976F72 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5804 |  | 2015-08-17 | 2015-08-17 17:17 | 2015-08-17 17:46 | CARRIER - 38TRA042330 | 112 | 12.4 | Yes | Yes | 14.7 | 17.4 | -2.7 | DB06B478F85546AAA4714AEF7A7D3BE4 |  | R22 | TXV |  | 11.07% | 0.88929 | 21.28% | [5 empty] | TXV | 11.07%
Antioch | CA | 94509-5024 |  | 2015-07-06 | 2015-07-06 12:24 | 2015-07-06 12:24 | CARRIER - 38EBO36310 | 117 | 0 | Yes | Yes | 21.4 | 21.4 | 0 | 1ED149CFD06A429EA044BA84CE6FEC5C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1943 |  | 2015-07-08 | 2015-07-08 09:07 | 2015-07-08 09:07 | BRYANT - 123RNA042-A | 127 | 0 | Yes | Yes | 22.2 | 19.5 | 2.7 | 44E87A4276E847249F3457CC321A4ADD |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2340 |  | 2015-08-05 | 2015-08-05 11:30 | 2015-08-05 11:30 | RUUD - UAKA-037JAZ | 85 | 0 | Yes | Yes | 19.5 | 18 | 1.5 | 67F67CA40BEB49088AA1437F2D86E294 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9414 |  | 2015-07-31 | 2015-07-31 12:12 | 2015-07-31 12:32 | CARRIER - 38CKC042340 | 85 | 8.1 | Yes | Yes | 19.8 | 20.1 | -0.3 | 04A8694FC59E4BE795B12883E2003858 |  | R22 | TXV |  | 9.529% | 0.90471 | 18.31% | [5 empty] | TXV | 9.529%
Pittsburg | CA | 94565-5083 |  | 2015-09-15 | 2015-09-15 14:08 | 2015-09-15 14:08 | TRANE - 4TTM3036A1000AA | 69 | 0 | Yes | Yes | 19.7 | 19.5 | 0.2 | 50C5707FB4D147E6ABCD950BC8E9A973 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3939 |  | 2015-08-28 | 2015-08-28 13:23 | 2015-08-28 13:41 | TRANE - 2TTR301810000AA | 64 | 2.7 | Yes | Yes | 20.7 | 19.9 | 0.8 | F4410A1A4BB6496CBCFB7AEDE26574CE |  | R22 | Non-TXV |  | 4.219% | 0.95781 | 8.108% | [5 empty] | Non-TXV | 4.219%
Pittsburg | CA | 94565-5624 |  | 2015-09-01 | 2015-09-01 16:15 | 2015-09-01 16:15 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 17.9 | 19 | -1.1 | 9DB7E6CACAB74357BB053034D4EE373C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5361 |  | 2015-09-16 | 2015-09-16 09:18 | 2015-09-16 09:18 | GOODMAN - GSH13181CB | 127 | 0 | Yes | Yes | 17.4 | 19.1 | -1.7 | 8C2085EE1EE44B849DA2FA61354C41F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6677 |  | 2015-08-13 | 2015-08-13 12:32 | 2015-08-13 12:32 | TRANE - TTX036C100A1 | 136 | 0 | Yes | Yes | 20.4 | 18.1 | 2.3 | 0916F80C7EA3481DB2685160F5BF3092 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2627 |  | 2015-07-30 | 2015-07-30 10:16 | 2015-07-30 10:16 | RHEEM - HC-10036-21G | 85 | 0 | Yes | Yes | 20.7 | 19.4 | 1.3 | DCDA5D262043454CB403305B247B648F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3396 |  | 2015-09-02 | 2015-09-02 14:42 | 2015-09-02 14:42 | YORK - H1CB018506 | 56 | 0 | Yes | Yes | 21.8 | 20.2 | 1.6 | 781B8BD6381F48ACAE080D0184644293 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2659 |  | 2015-09-14 | 2015-09-14 14:04 | 2015-09-14 14:04 | CARRIER - 38CKC036350 | 72 | 0 | Yes | Yes | 20.1 | 21 | -0.9 | 834C30A00DC24B56892CB0ED216C1224 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-5347 |  | 2015-08-14 | 2015-08-14 13:41 | 2015-08-14 13:41 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 16.8 | 18.8 | -2 | 8BEED5AA7A3F46DC982AA972943319A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8329 |  | 2015-08-05 | 2015-08-05 08:33 | 2015-08-05 08:33 | DAY & NIGHT - N2A448GKA200 | 85 | 0 | Yes | Yes | 20.4 | 18.9 | 1.5 | 4A16F4CE46144B04B603FF8500B1E912 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-2067 |  | 2015-07-10 | 2015-07-10 09:00 | 2015-07-10 09:00 | RHEEM - RAFD-048JBS | 101 | 0 | Yes | Yes | 19.9 | 18.2 | 1.7 | 181CBFBC38AF4F6BB8C3FE6369AAF1F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8597 |  | 2015-08-03 | 2015-08-03 14:44 | 2015-08-03 14:44 | CARRIER - 38CKC048360 | 85 | 0 | Yes | Yes | 20.3 | 21.3 | -1 | C017BC52B6184FDBA03434BB8DAB81C2 |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2035 |  | 2015-07-28 | 2015-07-28 15:51 | 2015-07-28 15:51 | CLIMATEMASTER - N2A342AKA200 | 85 | 0 | Yes | Yes | 21.6 | 20.2 | 1.4 | 22535B5A366446859F90EDB4AF71DDE5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4325 |  | 2015-07-21 | 2015-07-21 08:49 | 2015-07-21 08:49 | GOODMAN - ASC130421AA | 143 | 0 | Yes | Yes | 21.9 | 19.5 | 2.4 | 46F4912B12164FC6B15B9782996AE084 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-3268 |  | 2015-07-27 | 2015-07-27 14:29 | 2015-07-27 14:29 | PAYNE - PA10JA048-A | 99 | 0 | Yes | Yes | 27.5 | 22.3 | 5.2 | 8D05CA473669463780DB51AF01BE0D20 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9407 |  | 2015-08-05 | 2015-08-05 14:34 | 2015-08-05 14:34 | CARRIER - 38CKC060370 | 85 | 0 | Yes | Yes | 18.9 | 20.1 | -1.2 | AD120DF7572341469DC7122EC362E643 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1312 |  | 2015-07-28 | 2015-07-28 09:47 | 2015-07-28 09:47 | GUARDIAN - GCGD48S21S2B | 85 | 0 | Yes | Yes | 19.3 | 22 | -2.7 | 4FB83A90A779491D8EFC1E36FA23E91C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6426 |  | 2015-07-14 | 2015-07-14 11:05 | 2015-07-14 11:05 | GE - BTD736A1000A0 | 88 | 0 | Yes | Yes | 18.1 | 20.3 | -2.2 | 9E9D74DACF1A4C2E8D43D89AF829D6D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1409 |  | 2015-07-24 | 2015-07-24 09:26 | 2015-07-24 09:26 | TRANE - TTN036C100B2 | 117 | 0 | Yes | Yes | 22 | 19.1 | 2.9 | ADE312FB169C4A12919CC391611B53F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5371 |  | 2015-07-23 | 2015-07-23 09:37 | 2015-07-23 09:37 | CARRIER - 38TH036300 | 85 | 0 | Yes | Yes | 20.1 | 19.1 | 1.1 | 64D6D130EADC400EBE2C88661B8C42D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3578 |  | 2015-08-13 | 2015-08-13 09:44 | 2015-08-13 09:44 | OTHER - N/A | 85 | 0 | Yes | Yes | 23 | 22.9 | 0.1 | F51E8C3F1C4B42F3BA151B91EB9BD43A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5159 |  | 2015-08-13 | 2015-08-13 08:24 | 2015-08-13 08:24 | COPELAND - GSX30481BB | 104 | 0 | Yes | Yes | 24 | 23.1 | 0.9 | F01B0553EA1742E888D38AA87657141D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-0000 |  | 2015-09-15 | 2015-09-15 10:55 | 2015-09-15 10:55 | OTHER - 2C13B60P-1A | 234 | 0 | Yes | Yes | 22 | 24.2 | -2.2 | 8C6C42599C024B0CBAF9CA47DCA42EB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1820 |  | 2015-07-22 | 2015-07-22 13:38 | 2015-07-22 13:38 | CARRIER - 24ACR336A300 | 126 | 0 | Yes | Yes | 23.2 | 20.4 | 2.8 | 42DFBAB86D274314890F78AF7157E98B |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7260 |  | 2015-07-14 | 2015-07-14 13:14 | 2015-07-14 13:14 | PAYNE - PA10JA048D | 97 | 0 | Yes | Yes | 18.3 | 20.1 | -1.8 | 29E1023E5BED46F79F20E65B3D71589B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5433 |  | 2015-07-29 | 2015-07-29 11:05 | 2015-07-29 11:05 | CARRIER - 24ABB336W310 | 86 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 52A2DFD86806486BA87AA05D9CFEFC97 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8828 |  | 2015-09-16 | 2015-09-16 10:05 | 2015-09-16 10:05 | UNITARY PRODUCTS GROUP - D2NP030N05606A | 73 | 0 | Yes | Yes | 24 | 20.2 | 3.8 | 2AAC188427CA4334BE8FF58AAD86E59C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3732 |  | 2015-11-04 | 2015-11-04 15:29 | 2015-11-04 15:29 | BRYANT - 561CJ024-D | 54 | 0 | Yes | Yes | 18.1 | 16.5 | 1.6 | 46AAF0FCE17F4BFD85181C5E37BE9915 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4557 |  | 2015-09-30 | 2015-09-30 11:06 | 2015-09-30 11:41 | PAYNE - PY3GNAA24040NA-- | 74 | 12 | Yes | Yes | 21.3 | 22.4 | -1.1 | A0DFFF3AB04B440598C207BA3DF7B035 |  | R410A | Non-TXV |  | 16.22% | 0.83784 | 31.16% | [5 empty] | Non-TXV | 16.22%
Vallejo | CA | 94591-7967 |  | 2015-07-27 | 2015-07-27 12:53 | 2015-07-27 12:53 | GOODMAN - GSC1300361DE | 85 | 0 | Yes | Yes | 15.2 | 18.1 | -2.9 | A6A81F659FA447819BAB1524F628722B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8464 |  | 2015-10-01 | 2015-10-01 16:23 | 2015-10-01 16:23 | TRANE - 2TWR10181000AB | 114 | 0 | Yes | Yes | 15.2 | 12.1 | 3.1 | 9EDDFE9A4F11400198E9E18F007ADB7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-2931 |  | 2015-07-24 | 2015-07-24 11:08 | 2015-07-24 11:08 | CARRIER - 38TKBO60330 | 136 | 0 | Yes | Yes | 15.9 | 18.5 | -2.6 | BAFC92EE4D4A4004BA49B8AB6D82217B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8322 |  | 2015-06-29 | 2015-06-29 14:23 | 2015-06-29 14:23 | CARRIER - 38CK060310 | 131 | 0 | Yes | Yes | 27.9 | 20.4 | 7.5 | 7086D47E36B141E1816639B051228549 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3064 |  | 2015-08-11 | 2015-08-11 09:40 | 2015-08-11 09:40 | GOODMAN - GH130181AC | 127 | 0 | Yes | Yes | 16.6 | 17.6 | -1 | 68FD1314C92E498E814FCFD75D3C973F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2238 |  | 2015-08-04 | 2015-08-04 08:52 | 2015-08-04 08:52 | TRANE - TTP048D100A0 | 131 | 0 | Yes | Yes | 19.8 | 18.2 | 1.6 | 281E4F7539A24DA9B1F9F070526CFAAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5102 |  | 2015-09-16 | 2015-09-16 14:10 | 2015-09-16 14:10 | LUXAIRE - 60WE24G1 | 55 | 0 | Yes | Yes | 21.1 | 22.1 | -1 | 4DB47E755F4E431AAF2E9883FBF6556F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6121 |  | 2015-09-21 | 2015-09-21 17:58 | 2015-09-21 17:58 | OTHER - NCABA30AB02 | 44 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | F15D5859D3074E19BC7AB81AF1808815 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4301 |  | 2015-08-13 | 2015-08-13 08:54 | 2015-08-13 08:55 | CARRIER - N/A | 85 | 8.2 | Yes | Yes | 20.3 | 21.3 | -1 | B67124A507894D4CAF28C83CA75D5B7C |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Concord | CA | 94518-3209 |  | 2015-07-31 | 2015-07-31 13:56 | 2015-07-31 13:56 | OTHER - UNKNOWN | 77 | 0 | Yes | Yes | 21.3 | 15.5 | 5.8 | ACFD67CA7A714D08B11F5E99557939D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4214 |  | 2015-08-13 | 2015-08-13 10:29 | 2015-08-13 10:29 | GOODMAN - V8X130601BC | 100 | 0 | Yes | Yes | 24.2 | 23.4 | 0.8 | 26B9D895545240F8907C8D47A87043D7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5909 |  | 2015-06-30 | 2015-06-30 10:08 | 2015-06-30 10:08 | RHEEM - RA-FD-036JAS | 80 | 0 | Yes | Yes | 24.3 | 19.3 | 5 | C103A63132204B56A8F3342B44D4B524 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1605 |  | 2015-08-18 | 2015-08-18 11:07 | 2015-08-18 11:07 | CARRIER - 124ANA060 | 224 | 0 | Yes | Yes | 21.6 | 19.3 | 2.3 | 755822EA82C8467C851122AA6F11ED59 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3228 |  | 2015-09-30 | 2015-09-30 09:19 | 2015-09-30 09:19 | PAYNE - 561AJ030A | 67 | 0 | Yes | Yes | 22.3 | 19.3 | 3 | C6978972B0FB49B29F19E498FFB1B3F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3087 |  | 2015-08-05 | 2015-08-05 11:50 | 2015-08-05 11:50 | CARRIER - 38CKC042340 | 85 | 0 | Yes | Yes | 14.7 | 17.6 | -2.9 | 8E7E8D6D55F64AEEBECAA63DC367F8ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8485 |  | 2015-08-28 | 2015-08-28 16:35 | 2015-08-28 16:35 | DAY & NIGHT - 541DJ08 | 83 | 0 | Yes | Yes | 15.8 | 18.5 | -2.7 | D8C73352D831452AB5094EFCA72E7339 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5124 |  | 2015-07-27 | 2015-07-27 11:27 | 2015-07-27 11:27 | UNITARY PRODUCTS GROUP - D6NZ030N03606NXA | 85 | 0 | Yes | Yes | 22.8 | 18.8 | 4 | 0BD40B2A051D47C196AF1111E0490BF7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5234 |  | 2015-08-07 | 2015-08-07 14:32 | 2015-08-07 14:32 | ICP - NAC336AKA1 | 278 | 0 | Yes | Yes | 21 | 22.7 | -1.7 | C0C27E3D5FC44D99A39551B1557B3D37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5121 |  | 2015-09-16 | 2015-09-16 12:19 | 2015-09-16 12:19 | BDP - 588ANW030040ACD | 55 | 0 | Yes | Yes | 21.1 | 23.4 | -2.3 | 80213DD8A24A416E81330D44748F523E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7278 |  | 2015-07-30 | 2015-07-30 14:16 | 2015-07-30 14:16 | TRANE - 2TTX40421000AA | 137 | 0 | Yes | Yes | 20.7 | 20.2 | 0.5 | 9781C6EBC9BA461E98B16F55CA17C7B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1616 |  | 2015-07-30 | 2015-07-30 09:29 | 2015-07-30 09:29 | RHEEM - | 90 | 0 | Yes | Yes | 25.1 | 22 | 3.1 | 4BF61EB23DD4459E8892A9A77D5D8FD1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2608 |  | 2015-07-16 | 2015-07-16 10:07 | 2015-07-16 10:07 | RHEEM - UNK | 85 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | E50FF11D97A14DDEB30DA4D1161ECFF1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6719 |  | 2015-10-16 | 2015-10-16 12:50 | 2015-10-16 12:50 | CARRIER - 38EH036300 | 120 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | 1528195711014D53A389D3EE2A253407 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4448 |  | 2015-07-30 | 2015-07-30 09:02 | 2015-07-30 09:02 | ICP - WCA3302GKH2 | 78 | 0 | Yes | Yes | 22.7 | 22.6 | 0.1 | 1C99E59704EA432DBA8D4CF82A187EE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1945 |  | 2015-07-29 | 2015-07-29 14:23 | 2015-07-29 14:23 | DAY & NIGHT - UNK | 85 | 0 | Yes | Yes | 19.6 | 19.9 | -0.3 | 769482924C474027955C54CA04621846 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4504 |  | 2015-08-05 | 2015-08-05 09:50 | 2015-08-05 09:50 | CARRIER - 38CKC036350 | 73 | 0 | Yes | Yes | 16 | 18.5 | -2.5 | FB68C3960F5F4C9D8C70EA88E5A9DEE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4409 |  | 2015-10-07 | 2015-10-07 13:18 | 2015-10-07 13:43 | OTHER - UNKNOWN | 76 | 16.2 | Yes | Yes | 19.9 | 19.9 | 0 | 94B19CE3C9C744E7A69CECA17EE05DE0 |  | R22 | Non-TXV |  | 21.32% | 0.78684 | 40.96% | [5 empty] | Non-TXV | 21.32%
Vacaville | CA | 95688-2710 |  | 2015-08-04 | 2015-08-04 13:43 | 2015-08-04 13:43 | - JS3BA036KA | 85 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | C68C96B789AE4FF0876ED0C43075401A | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3102 |  | 2015-07-21 | 2015-07-21 14:22 | 2015-07-21 14:52 | TRANE - 2TTR1036A1000AA | 73 | 12.9 | Yes | Yes | 22 | 18.8 | 3.2 | 3508630439B548E88CE56D5CFD148B82 |  | R22 | Non-TXV |  | 17.67% | 0.82329 | 33.96% | [5 empty] | Non-TXV | 17.67%
Pittsburg | CA | 94565-5741 |  | 2015-09-01 | 2015-09-01 14:35 | 2015-09-01 14:35 | LENNOX - 13ACC-036-230-01 | 115 | 0 | Yes | Yes | 20.9 | 19.1 | 1.9 | 9C7A13F56999415897FF3A4B7F97331E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2002 |  | 2015-09-17 | 2015-09-17 09:49 | 2015-09-17 09:49 | DAY & NIGHT - 565AJ036 | 87 | 0 | Yes | Yes | 22 | 18.7 | 3.3 | 336E47D0594144E9B1460608F706314F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5765 |  | 2015-09-19 | 2015-09-19 13:39 | 2015-09-19 13:39 | AIRE-FLO - | 96 | 0 | Yes | Yes | 21.8 | 19.8 | 2 | 5AEAC50DF5C542939AE9D146959CE856 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4828 |  | 2015-08-24 | 2015-08-24 09:40 | 2015-08-24 10:01 | CARRIER - 24ABB330W310 | 74 | 7.1 | Yes | Yes | 13.5 | 15.7 | -2.2 | 46EF849A9BC04033B896E98E09D8A7FB |  | R410A | TXV |  | 9.595% | 0.90405 | 18.44% | [5 empty] | TXV | 9.595%
Pittsburg | CA | 94565-6209 |  | 2015-08-24 | 2015-08-24 10:58 | 2015-08-24 10:58 | CARRIER - 561CJ048000AAAA | 102 | 0 | Yes | Yes | 20.2 | 18.9 | 1.3 | 9F8340DBBFF34774B4F3B0FB7BBBB090 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2342 |  | 2015-08-03 | 2015-08-03 08:20 | 2015-08-03 08:20 | CARRIER - 38THO42310 | 112 | 0 | Yes | Yes | 17.1 | 18.2 | -1.1 | 496028E50EED45FEAFABBCCF57420C70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5739 |  | 2015-07-14 | 2015-07-14 08:07 | 2015-07-14 08:07 | AMERICAN STANDARD - 2A7A4042A1000AA | 137 | 0 | Yes | Yes | 16.8 | 19.5 | -2.7 | 605D3AD80B6040CDAB4B9C8FAEEEBBF9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2748 |  | 2015-10-09 | 2015-10-09 13:36 | 2015-10-09 13:36 | GIBSON - JS3BA-060KB | 114 | 0 | Yes | Yes | 27.9 | 22.4 | 5.6 | 129C53E7A4A64DB29096F00655109EE0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1773 |  | 2015-09-03 | 2015-09-03 15:15 | 2015-09-03 15:15 | TEMPSTAR - CA5548VDK2 | 134 | 0 | Yes | Yes | 17.2 | 20.2 | -3 | B23DB13F5CC14413BCD9C15728ABB60D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1413 |  | 2015-07-23 | 2015-07-23 13:25 | 2015-07-23 13:25 | CARRIER - 38TRA048340 | 195 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | 3669838FA9054A55ACF234A4186C0BB3 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6819 |  | 2015-08-26 | 2015-08-26 10:45 | 2015-08-26 10:45 | CARRIER - 565BJ018 | 50 | 0 | Yes | Yes | 20.9 | 19.3 | 1.6 | 2E22D15E90A647B8A85FAA5303FE803C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2314 |  | 2015-07-21 | 2015-07-21 11:14 | 2015-07-21 11:14 | RHEEM - RAKA-048JAZ | 103 | 0 | Yes | Yes | 20.1 | 23.1 | -3 | B813A12FCD1A4BBBB8FA06CCADF8E097 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1629 |  | 2015-09-15 | 2015-09-15 14:27 | 2015-09-15 14:27 | TRANE - TTB048C100A1 | 97 | 0 | Yes | Yes | 25 | 20.2 | 4.9 | DA32BB24A34B46198DB960F24130EFF1 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5144 |  | 2015-07-22 | 2015-07-22 11:22 | 2015-07-22 11:22 | TRANE - YCZ060F1M0BD | 205 | 0 | Yes | Yes | 20.1 | 19.1 | 1 | F6AEC14C4B4D421E816E89DBF069B2CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5101 |  | 2015-10-19 | 2015-10-19 10:30 | 2015-10-19 10:30 | PAYNE - PA13NR030-J | 75 | 0 | Yes | Yes | 16.7 | 18.2 | -1.5 | 2EBCF49B69DF4C3896D18D793A14D4DD |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1676 |  | 2015-06-23 | 2015-06-23 09:56 | 2015-06-23 10:23 | CARRIER - 38CK018300 | 63 | -2.9 | Yes | Yes | 19.9 | 19.9 | 0 | E2ED14317940403DAE40A1F5F852B894 | Remove refrigerant: 6.2 oz | R22 | TXV |  | -4.603% | 1.046 | 1.289% |  |  |  |  | TXV |  |  | -4.603%
Bakersfield | CA | 93305-1519 |  | 2015-08-06 | 2015-08-06 11:10 | 2015-08-06 11:10 | RUUD - URGH-07E42JKR | 112 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | C601D0CA28A64FF981F2434D79C3D882 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4725 |  | 2015-07-30 | 2015-07-30 09:44 | 2015-07-30 09:44 | CARRIER - 38BRC036320 | 85 | 0 | Yes | Yes | 16.9 | 18.2 | -1.3 | F4A4CACA10D440E9A73D6EF8DC6B28E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5965 |  | 2015-09-10 | 2015-09-10 09:53 | 2015-09-10 10:23 | ICP - GPCM24K040F | 53 | 12.8 | Yes | Yes | 20.7 | 20.4 | 0.3 | 61F2AB01E03946FB9FDA5E15D3089A38 |  | R22 | Non-TXV |  | 24.15% | 0.75849 | 46.41% | [5 empty] | Non-TXV | 24.15%
Antioch | CA | 94509-4610 |  | 2015-06-29 | 2015-06-29 11:58 | 2015-06-29 11:58 | YORK - HH4DB036S06A | 73 | 0 | Yes | Yes | 25.1 | 22.1 | 3 | F83DD18AA37244FEB96A5A555334A47D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9301 |  | 2015-09-17 | 2015-09-17 14:47 | 2015-09-17 14:47 | CARRIER - 563CN048-D | 167 | 0 | Yes | Yes | 26.2 | 20.6 | 5.6 | 042D59E6B3144BD0BA9254BB90BE04F9 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9398 |  | 2015-08-06 | 2015-08-06 12:37 | 2015-08-06 13:20 | CARRIER - 38CK048360 | 98 | 17.3 | Yes | Yes | 17 | 18.7 | -1.7 | F5AF9DBB2A4D481B8E7E86C5280B650C |  | R22 | Non-TXV |  | 17.65% | 0.82347 | 33.93% | [5 empty] | Non-TXV | 17.65%
Bakersfield | CA | 93306-7613 |  | 2015-09-15 | 2015-09-15 10:32 | 2015-09-15 10:32 | - N/A | 85 | 0 | Yes | Yes | 23 | 23.4 | -0.4 | 24B476B7F1644561AEF06AE4ED350029 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pinole | CA | 94564-1135 |  | 2015-10-29 | 2015-10-29 12:19 | 2015-10-29 12:19 | PAYNE - 591AANX036 | 85 | 0 | Yes | Yes | 20.1 | 17.7 | 2.4 | 848BED703D094FAD9B21451175AA153A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clayton | CA | 94517-1323 |  | 2015-08-24 | 2015-08-24 10:23 | 2015-08-24 10:23 | ALLEGIANCE - 2A7A2060B11000AA | 146 | 0 | Yes | Yes | 22.6 | 19.7 | 2.9 | 8DE2967AB9FA4A6AAAD832C953467F19 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8558 |  | 2015-08-24 | 2015-08-24 14:21 | 2015-08-24 14:21 | HEIL - N4A460AKB400 | 85 | 0 | Yes | Yes | 18.9 | 21 | -2.1 | A1F380C484F247DCBDEB642D96E558E0 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7718 |  | 2015-08-18 | 2015-08-18 10:50 | 2015-08-18 10:50 | YORK - D1H036N05606C | 108 | 0 | Yes | Yes | 24 | 21.1 | 3 | 02EF523F0EF7469288F6BBF6FB82700A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-5016 |  | 2015-08-20 | 2015-08-20 10:17 | 2015-08-20 10:17 | CARRIER - 38TDB060310 | 211 | 0 | Yes | Yes | 15.4 | 17.5 | -2.1 | DC094A3DE01F4BF095B4AEC3379E75DC |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8822 |  | 2015-09-15 | 2015-09-15 09:45 | 2015-09-15 09:45 | CARRIER - 38CKC036 341 | 70 | 0 | Yes | Yes | 22 | 19.3 | 2.7 | 770E1E53DDF64A45BECA22762E1E3F78 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5390 |  | 2015-09-10 | 2015-09-10 13:10 | 2015-09-10 14:07 | OTHER - N/A | 85 | 17.6 | Yes | Yes | 23.4 | 21.5 | 1.9 | D0E9A0C187224E7EB6F2C3E794AC57B7 |  | R22 | Non-TXV |  | 20.71% | 0.79294 | 39.79% | [5 empty] | Non-TXV | 20.71%
Martinez | CA | 94553-9799 |  | 2015-08-03 | 2015-08-03 14:00 | 2015-08-03 14:00 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 24.7 | 20.4 | 4.3 | 0BB2D7DF1F4C4F4DB08B5A11246C8A1C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3781 |  | 2015-10-29 | 2015-10-29 11:54 | 2015-10-29 11:54 | CARRIER - UNK | 85 | 0 | Yes | Yes | 18.3 | 19.7 | -1.3 | 14A18C4646B34E09886F3F41C468C21A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94514-0000 |  | 2015-08-18 | 2015-08-18 18:10 | 2015-08-18 18:10 | PAYNE - PY3GNAA36060NA | 103 | 0 | Yes | Yes | 23.2 | 21 | 2.2 | 186557EEBE15424BB2F910AC99F6B206 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-5470 |  | 2015-08-31 | 2015-08-31 10:47 | 2015-08-31 10:47 | CARRIER - 24ABA336A300 | 83 | 0 | Yes | Yes | 18.7 | 17.8 | 0.9 | 736E0429E93946DBB821B6D1F2F1C770 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6257 |  | 2015-09-11 | 2015-09-11 12:59 | 2015-09-11 12:59 | CARRIER - UNKNOWN | 73 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | F083229FEB3540B686DD7304037EB745 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8053 |  | 2015-07-02 | 2015-07-02 11:51 | 2015-07-02 11:51 | CARRIER - 38CKBO36330 | 82 | 0 | Yes | Yes | 20.5 | 21.4 | -0.9 | CA1A086D139947D7A9178F5C4020FA51 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7454 |  | 2015-08-10 | 2015-08-10 15:49 | 2015-08-10 15:49 | CARRIER - 38CKC060300 | 85 | 0 | Yes | Yes | 24.6 | 21.3 | 3.3 | 5B07E8D7710145F4BB84087979ED6E20 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5536 |  | 2015-08-07 | 2015-08-07 14:34 | 2015-08-07 14:34 | RHEEM - RAMC-060JBZ | 250 | 0 | Yes | Yes | 22.2 | 24.4 | -2.2 | 46F1C7D896D54A19A82A17BB9B7C5BFB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-3213 |  | 2015-10-13 | 2015-10-13 17:14 | 2015-10-13 17:14 | GOODMAN - GSC130301A8 | 123 | 0 | Yes | Yes | 20 | 21.3 | -1.3 | C75FC195F0A7434E92D788BB4F6FAE2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-5719 |  | 2015-09-22 | 2015-09-22 10:39 | 2015-09-22 10:39 | PAYNE - PA13NR042-J | 113 | 0 | Yes | Yes | 17.1 | 18.2 | -1.1 | 3BFD368EDD044ED290543787DBF03521 |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3189 |  | 2015-10-02 | 2015-10-02 12:13 | 2015-10-02 12:13 | LENNOX - 13ACX-042-230-18 | 104 | 0 | Yes | Yes | 18.6 | 20.9 | -2.3 | 01283335DF1E443D84EC9EA63231F462 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3977 |  | 2015-08-07 | 2015-08-07 14:37 | 2015-08-07 14:37 | BDP - 588ANW030040ACAD | 56 | 0 | Yes | Yes | 20.4 | 21.2 | -0.8 | 540ACBA983294677A9C8269EA21A3998 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1927 |  | 2015-08-04 | 2015-08-04 10:56 | 2015-08-04 10:56 | ICP - N2A324AKC200 | 51 | 0 | Yes | Yes | 22.2 | 19.3 | 2.9 | 4D97591B3F3C4CE2B1CF9EE8A99DD2AE |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2238 |  | 2015-08-05 | 2015-08-05 10:38 | 2015-08-05 10:38 | OTHER - UNKNOWN | 75 | 0 | Yes | Yes | 14.9 | 17.6 | -2.7 | 74BB5847954340AB81CD1F33D35F4628 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2431 |  | 2015-08-31 | 2015-08-31 16:20 | 2015-08-31 16:20 | ALLEGIANCE - 7A0036A100A0 | 85 | 0 | Yes | Yes | 22.2 | 17.7 | 4.5 | ED9A98E8BDED43C084A7DE87F12C288C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4652 |  | 2015-08-26 | 2015-08-26 09:41 | 2015-08-26 09:41 | PAYNE - 565BJ036 | 84 | 0 | Yes | Yes | 18.7 | 19.4 | -0.7 | 5FDF229797D4408C881E4AE64E1346FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3416 |  | 2015-07-30 | 2015-07-30 14:50 | 2015-07-30 14:50 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 19.4 | 19.3 | 0.1 | C2829AFA779F4A26A43980A7F512E36E |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3316 |  | 2015-11-10 | 2015-11-10 12:54 | 2015-11-10 12:54 | RHEEM - RAKA-024JAS | 51 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | 3E7A12FD73164E02B7434E5035AF3C69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8471 |  | 2015-08-07 | 2015-08-07 14:18 | 2015-08-07 14:18 | CARRIER - 38TKB024300 | 65 | 0 | Yes | Yes | 22.4 | 20.8 | 1.6 | E2169FA6F0F147D7A5EF2FE9805B1AF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7534 |  | 2015-08-31 | 2015-08-31 11:55 | 2015-08-31 11:55 | CARRIER - UNK | 133 | 0 | Yes | Yes | 20 | 19 | 1 | 40B5C47520394DA9807C64BCFC5E07FF |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3922 |  | 2015-08-07 | 2015-08-07 14:38 | 2015-08-07 14:38 | OTHER - N/A | 85 | 0 | Yes | Yes | 23.4 | 21.7 | 1.7 | A224ABE6D70E4DA7B49D0D56E637242F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3923 |  | 2015-08-26 | 2015-08-26 10:27 | 2015-08-26 10:27 | RHEEM - RRNL-B048JK08X | 161 | 0 | Yes | Yes | 26.4 | 20.5 | 5.9 | 5089005062D84CE79A61BFE058802A73 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4756 |  | 2015-08-26 | 2015-08-26 11:36 | 2015-08-26 11:36 | RUUD - UNK | 85 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 80E3FAE13CF14A65B589C5CA581F4C62 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-3093 |  | 2015-08-03 | 2015-08-03 11:08 | 2015-08-03 11:08 | ECONAIR - AC036X1021A | 63 | 0 | Yes | Yes | 24 | 21.9 | 2.1 | 86033F147FC54596BB0626210D77F662 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2367 |  | 2015-08-04 | 2015-08-04 14:30 | 2015-08-04 14:30 | CARRIER - 24ABA336A310 | 85 | 0 | Yes | Yes | 19.8 | 19 | 0.8 | F5226112E5F8494EAE096A11CCA6ED88 |  | R410A | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2367 |  | 2015-08-04 | 2015-08-04 14:47 | 2015-08-04 14:47 | CARRIER - 54ABA336A310 | 85 | 0 | Yes | Yes | 24.9 | 19.9 | 5 | 15199F2EEF694A99ADABF0465595C70D |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6211 |  | 2015-07-14 | 2015-07-14 14:29 | 2015-07-14 14:29 | CARRIER - 38CKC04B370 | 100 | 0 | Yes | Yes | 19.1 | 18.6 | 0.5 | D8EF3468077F4581A080BDEF3EFAA2D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4517 |  | 2015-08-24 | 2015-08-24 15:13 | 2015-08-24 15:13 | CARRIER - 591ANX036000AAAA | 84 | 0 | Yes | Yes | 20.1 | 19.6 | 0.6 | AEF877B27AE54A2F8E8F96990734E489 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1574 |  | 2015-08-14 | 2015-08-14 17:32 | 2015-08-14 17:32 | CARRIER - 38CK036350 | 85 | 0 | Yes | Yes | 18.5 | 19.3 | -0.8 | D0703AD01D8F41EDA60D6810D0D84470 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7908 |  | 2015-08-25 | 2015-08-25 09:45 | 2015-08-25 09:45 | CARRIER - 24AB342A310 | 98 | 0 | Yes | Yes | 17.9 | 18.8 | -0.9 | 486162C81F6A46FF848EF2184027DC47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4921 |  | 2015-07-31 | 2015-07-31 14:17 | 2015-07-31 14:17 | - | 85 | 0 | Yes | Yes | 20.8 | 19.7 | 1.1 | 592CA37EECD84F89A381A62BDBAF400C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94506-4420 |  | 2015-07-29 | 2015-07-29 13:18 | 2015-07-29 13:18 | CARRIER - 38EH036300 | 128 | 0 | Yes | Yes | 24 | 24.8 | -0.8 | C5C7DD83551C4A64A0C749EAEA9A9A15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2800 |  | 2015-09-18 | 2015-09-18 15:36 | 2015-09-18 15:36 | RHEEM - TRDO24AH-A | 85 | 0 | Yes | Yes | 19.6 | 21.8 | -2.2 | 19D85FBBF1204EB1998BBED987F23916 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7288 |  | 2015-09-16 | 2015-09-16 14:35 | 2015-09-16 14:35 | WEATHER KING - N/A | 85 | 0 | Yes | Yes | 24.7 | 23.7 | 1 | 9565C852AB71406E9277ECF01EE035C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-2744 |  | 2015-07-10 | 2015-07-10 15:46 | 2015-07-10 15:46 | OTHER - FSA050204141 | 85 | 0 | Yes | Yes | 16.4 | 18.2 | -1.8 | 7C08949BDCF44D798E6043F1A2DDAC4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6060 |  | 2015-10-21 | 2015-10-21 12:02 | 2015-10-21 12:02 | CARRIER - UNKNOWN | 97 | 0 | Yes | Yes | 20.7 | 21.7 | -1 | 0075AB0811E6434793A09F9FBA3C6631 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1944 |  | 2015-09-01 | 2015-09-01 15:39 | 2015-09-01 15:39 | CARRIER - H2ROD3606B | 96 | 0 | Yes | Yes | 19.3 | 20.7 | -1.4 | 9ECF6E889DEF455596DA329D479855EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6915 |  | 2015-08-03 | 2015-08-03 09:40 | 2015-08-03 09:40 | TRANE - BTD748A100B0 | 152 | 0 | Yes | Yes | 23.6 | 18.2 | 5.4 | 52F8D5DA20CB46FE8E17153746121C2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2225 |  | 2015-07-28 | 2015-07-28 10:04 | 2015-07-28 10:04 | BDP - 589ANW048080ADBG | 93 | 0 | Yes | Yes | 26 | 24.2 | 1.8 | E7BDBF94AD124F8B9BE1EFFA7C98E14B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-3803 |  | 2015-07-29 | 2015-07-29 11:38 | 2015-07-29 11:38 | TRANE - BTDT18A100A0 | 46 | 0 | Yes | Yes | 16.6 | 18.2 | -1.6 | B1B367A79F3C4F6EA092E481049E4793 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6440 |  | 2015-08-05 | 2015-08-05 09:57 | 2015-08-05 09:57 | PAYNE - PA10JAO42-C | 85 | 0 | Yes | Yes | 22.4 | 19.1 | 3.3 | 8A4ABF05DFBA49F6B66F89149B2CE9F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5909 |  | 2015-08-26 | 2015-08-26 08:42 | 2015-08-26 08:42 | OTHER - JS3BC-036KA | 82 | 0 | Yes | Yes | 23.5 | 22.5 | 1 | BBFDB8A9E0E6403B8FED379676A3490F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3522 |  | 2015-09-11 | 2015-09-11 09:19 | 2015-09-11 09:19 | PAYNE - PA16NA024A | 86 | 0 | Yes | Yes | 21.9 | 19.8 | 2.1 | 92416123D26D4803A277C4CDD1E2FF68 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4877 |  | 2015-09-24 | 2015-09-24 15:17 | 2015-09-24 15:17 | CARRIER - 561AJ060-B | 131 | 0 | Yes | Yes | 20.5 | 18.7 | 1.8 | ECD5F02E32144EEB82E9518572327BF3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9254 |  | 2015-07-09 | 2015-07-09 10:42 | 2015-07-09 10:42 | CARRIER - 38THO36300 | 83 | 0 | Yes | Yes | 25.1 | 20.2 | 4.9 | 177210AC6F3A48CBA7D8E8942216E698 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6310 |  | 2015-09-10 | 2015-09-10 15:03 | 2015-09-10 15:03 | - CJ30-1FB | 150 | 0 | Yes | Yes | 15.4 | 18.4 | -3 | 200A8E5C84E34385BC91169F7FCDB9AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-5031 |  | 2015-08-06 | 2015-08-06 11:04 | 2015-08-06 11:04 | ICP - PGF330060K01 | 91 | 0 | Yes | Yes | 16.2 | 18.9 | -2.7 | 26E19C593E7F4418AF4276548E1B136C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4606 |  | 2015-09-25 | 2015-09-25 17:17 | 2015-09-25 17:17 | CARRIER - 561CJ036-E | 70 | 0 | Yes | Yes | 21.9 | 21.3 | 0.6 | 1034E1CE4CFE4574A78CB72DF12E5BFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2435 |  | 2015-08-31 | 2015-08-31 13:02 | 2015-08-31 13:02 | AMERICAN STANDARD - 7A0036A100A0 | 95 | 0 | Yes | Yes | 15.1 | 18.1 | -3 | B09EDCDF09154A5EBB44B68AA40C1B51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-1732 |  | 2015-07-24 | 2015-07-24 12:02 | 2015-07-24 12:02 | ALLEGIANCE - 2A7A1042A1000AA | 95 | 0 | Yes | Yes | 18.8 | 17.7 | 1.1 | D9B1525FDE08497E94C7E4ABA9B57B7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7103 |  | 2015-07-27 | 2015-07-27 11:47 | 2015-07-27 11:47 | PAYNE - 591ANX048000ABAA | 116 | 0 | Yes | Yes | 21.1 | 21.4 | -0.3 | 3ABD65FB6B804E50BF1E9C8185BE3F61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2829 |  | 2015-09-22 | 2015-09-22 11:19 | 2015-09-22 11:39 | PAYNE - PA10JA048-A | 102 | 17 | Yes | Yes | 23.9 | 21 | 2.9 | EB293E64F9FB4FC99068E86856096109 |  | R22 | TXV |  | 16.67% | 0.83333 | 32.03% | [5 empty] | TXV | 16.67%
Pittsburg | CA | 94565-3612 |  | 2015-08-24 | 2015-08-24 12:40 | 2015-08-24 13:02 | GOODMAN - GSC10361FA | 83 | -11.7 | Yes | Yes | 17 | 19.3 | -2.3 | 0B2C05982EDE47A08D3EF73E40037D18 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -14.1% | 1.141 | 3.948% |  |  |  |  | Non-TXV |  |  | -14.1%
Bakersfield | CA | 93307-1932 |  | 2015-09-17 | 2015-09-17 14:16 | 2015-09-17 14:16 | YORK - D3NZ036N05606NXA | 85 | 0 | Yes | Yes | 18.5 | 18.7 | -0.2 | F3120970CF4645EFA4BD0D5032E5BB78 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4736 |  | 2015-08-06 | 2015-08-06 11:00 | 2015-08-06 11:00 | YORK - D3NZ030N03606NXA | 85 | 0 | Yes | Yes | 22.9 | 20.4 | 2.5 | 7EBF368FE3E64319A8B8A66B92911737 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2676 |  | 2015-08-13 | 2015-08-13 15:19 | 2015-08-13 16:15 | CARRIER - 38TDA036300 | 189 | 19.1 | Yes | Yes | 20.8 | 18.2 | 2.6 | 52D8666489D44B3E9E231BC5969B523C |  | R22 | TXV |  | 10.11% | 0.89894 | 19.42% | [5 empty] | TXV | 10.11%
Vacaville | CA | 95687-6137 |  | 2015-07-20 | 2015-07-20 08:28 | 2015-07-20 08:28 | TRANE - 2TTB00421000AA | 85 | 0 | Yes | Yes | 24.8 | 20.4 | 4.4 | B26E867D666A45CFB4B4D1686BBA51DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5548 |  | 2015-08-04 | 2015-08-04 08:36 | 2015-08-04 08:36 | ICP - PGF342080K01A1 | 189 | 0 | Yes | Yes | 23.7 | 21 | 2.7 | 110B593C6F424B18B75704ED08E5E4E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5727 |  | 2015-09-18 | 2015-09-18 09:55 | 2015-09-18 09:55 | NORDYNE - JS3BD-030K | 114 | 0 | Yes | Yes | 21.5 | 19.7 | 1.8 | 5212F8674FD44FC2A195A6AB795E6321 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2728 |  | 2015-10-27 | 2015-10-27 15:56 | 2015-10-27 15:56 | LENNOX - HS260362P | 90 | 0 | Yes | Yes | 18.8 | 19.3 | -0.5 | 8FAF371995F74B6BBBF232444841E4B9 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3073 |  | 2015-07-28 | 2015-07-28 16:17 | 2015-07-28 16:17 | - 2AC13B30P | 121 | 0 | Yes | Yes | 20.4 | 22.6 | -2.2 | 6CD45B8D7FFE43089D9E9B20AA978745 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3446 |  | 2015-08-27 | 2015-08-27 12:40 | 2015-08-27 13:03 | CARRIER - 38CKC042340 | 80 | 15.1 | Yes | Yes | 21.7 | 19.4 | 2.3 | 4C8091E24C934423ABBE33112D3B060D |  | R22 | Non-TXV |  | 18.88% | 0.81125 | 36.27% | [5 empty] | Non-TXV | 18.88%
Bakersfield | CA | 93306-6272 |  | 2015-07-28 | 2015-07-28 09:28 | 2015-07-28 09:28 | WEATHER KING - 13AJA42A01 | 121 | 0 | Yes | Yes | 19.4 | 20.2 | -0.8 | F3F535EFEB204F52AE02C9CB6B343E74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1673 |  | 2015-10-13 | 2015-10-13 11:20 | 2015-10-13 11:20 | RUUD - UAMB-036JAZ | 93 | 0 | Yes | Yes | 18.6 | 21.5 | -2.9 | 10A9E4338AD349FE98DC7CF5F3970F20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9331 |  | 2015-10-09 | 2015-10-09 10:13 | 2015-10-09 10:13 | GOODMAN - CKJ30-B | 92 | 0 | Yes | Yes | 15.2 | 18 | -2.8 | 8EB91CA4215A45D2AC2FBEF9A5B9A979 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-2604 |  | 2015-07-23 | 2015-07-23 09:56 | 2015-07-23 09:56 | CARRIER - 38CKC036350 | 70 | 0 | Yes | Yes | 18.2 | 18 | 0.2 | B576891725FD4C39B4EB0D4430395067 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-2604 |  | 2015-07-23 | 2015-07-23 10:01 | 2015-07-23 10:01 | CARRIER - 38CKC042340 | 80 | 0 | Yes | Yes | 16 | 18.3 | -2.3 | C1997D888BC0458BB00736E263F3B8AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4567 |  | 2015-08-24 | 2015-08-24 13:28 | 2015-08-24 13:28 | CARRIER - 36EN018300 | 54 | 0 | Yes | Yes | 5.1 | 21.4 | -16.3 | 16DCBFC768784851B512908A62A76AE2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6468 |  | 2015-08-24 | 2015-08-24 14:30 | 2015-08-24 14:30 | YORK - H1RA042S06D | 84 | 0 | Yes | Yes | 16.2 | 18.3 | -2.1 | EB2FD3E0FDD24742B7EAAE566AD7916F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1651 |  | 2015-10-06 | 2015-10-06 14:49 | 2015-10-06 15:11 | PAYNE - PA13NR036-D | 115 | -17 | Yes | Yes | 18.2 | 20.7 | -2.5 | 24DD1C9708334DB686F3E7D0A7F6B6CD |  | R22 | TXV |  | -14.78% | 1.1478 | 4.14% |  |  |  |  | TXV |  |  | -14.78%
Napa | CA | 94558-2825 |  | 2015-09-22 | 2015-09-22 14:35 | 2015-09-22 14:35 | TRANE - 2TTR10306A1000AA | 85 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | BA53F7AB7FDD4C539B3F2153CDA30719 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2622 |  | 2015-08-03 | 2015-08-03 15:19 | 2015-08-03 15:19 | HEIL - NACO30AKA1 | 85 | 0 | Yes | Yes | 16.1 | 16.9 | -0.8 | FC6E6C99189D4051A079F7E91721C7BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5845 |  | 2015-08-03 | 2015-08-03 10:13 | 2015-08-03 10:13 | GOODMAN - CK301A | 76 | 0 | Yes | Yes | 17.9 | 17.7 | 0.2 | 94A90B65290446C6AC27B210B3F68619 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4692 |  | 2015-10-07 | 2015-10-07 13:05 | 2015-10-07 13:25 | UNITARY PRODUCTS GROUP - H1RA042SO6D | 84 | 14.1 | Yes | Yes | 17 | 19.9 | -2.9 | 43332CB89B874407A9484DF224CB543F |  | R22 | Non-TXV |  | 16.79% | 0.83214 | 32.26% | [5 empty] | Non-TXV | 16.79%
Brentwood | CA | 94513-1281 |  | 2015-08-07 | 2015-08-07 15:35 | 2015-08-07 15:35 | LENNOX - 13ACC-024-230-01 | 81 | 0 | Yes | Yes | 22.3 | 19.1 | 3.2 | 50AF69645CFF4CAD896CEC0F59FB617B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lafayette | CA | 94549-4145 |  | 2015-08-04 | 2015-08-04 09:12 | 2015-08-04 09:40 | PAYNE - PA10JA048-A | 100 | -8 | Yes | Yes | 24.2 | 22.9 | 1.4 | B327D55587D74F09AEDCB98DD4BA87F6 |  | R22 | TXV |  | -8% | 1.08 | 2.24% |  |  |  |  | TXV |  |  | -8%
Brentwood | CA | 94513-4440 |  | 2015-08-05 | 2015-08-05 16:15 | 2015-08-05 16:15 | DAY & NIGHT - 561CJ036-C | 76 | 0 | Yes | Yes | 20.4 | 21.5 | -1.1 | D375644826CB4C678D34D1B825380015 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7321 |  | 2015-11-06 | 2015-11-06 10:25 | 2015-11-06 10:25 | AMERICAN STANDARD - 561AJ048-C | 105 | 0 | Yes | Yes | 22.6 | 19.3 | 3.3 | 7A022BE5F83A499289B7AF8496F662A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4779 |  | 2015-08-24 | 2015-08-24 13:44 | 2015-08-24 13:44 | TRANE - 4TTR3036D1000AA | 105 | -28.7 | Yes | Yes | 22.1 | 19.4 | 2.7 | 348011C87524495B810E8E9ABFF897D6 | Remove refrigerant: 28.7 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | TXV |  | -27.33% | 1.2733 | 7.655% |  |  |  |  | TXV |  |  | -27.33%
Oakley | CA | 94561-0000 |  | 2015-09-11 | 2015-09-11 13:40 | 2015-09-11 13:40 | CARRIER - 38CKC036350 | 74 | 0 | Yes | Yes | 25.8 | 23.1 | 2.7 | C0CE0D58959149F1BECDCE795D7F4909 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4857 |  | 2015-09-01 | 2015-09-01 10:57 | 2015-09-01 10:57 | OTHER - RAC13J424S21A | 74 | 0 | Yes | Yes | 26.9 | 21.3 | 5.7 | 0690FC38EFC84B82800F7326691A017F |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-4183 |  | 2015-09-08 | 2015-09-08 10:28 | 2015-09-08 10:28 | CARRIER - 38CKC48300 | 85 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | 888C0630FC604CC2800F8AE8840A1671 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3645 |  | 2015-10-20 | 2015-10-20 09:24 | 2015-10-20 09:24 | OTHER - N4A336AKB300 | 87 | 0 | Yes | Yes | 21.5 | 20.9 | 0.6 | 327A7FD3C704417C84B306018CF0D339 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3228 |  | 2015-09-16 | 2015-09-16 09:23 | 2015-09-16 09:23 | PAYNE - PA13NR030J | 75 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | C9D01A134F2B4BCFA8652AAF8A41E04C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3044 |  | 2015-08-12 | 2015-08-12 11:59 | 2015-08-12 11:59 | TRANE - BTD73A100B0 | 85 | 0 | Yes | Yes | 23.8 | 19.5 | 4.3 | A79D24628F7141B2B0EA5FE1D48B435F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6052 |  | 2015-07-31 | 2015-07-31 10:00 | 2015-07-31 10:21 | UNITARY PRODUCTS GROUP - H3RA060S06G | 98 | 10.1 | Yes | Yes | 25.3 | 20.2 | 5.2 | 34CE48C30F704352A5E8D72E8BCFBBF4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.31% | 0.89694 | 19.81% | [5 empty] | Non-TXV | 10.31%
Hercules | CA | 94547-3695 |  | 2015-07-20 | 2015-07-20 13:23 | 2015-07-20 13:23 | OTHER - 2TTR3036A1000AA | 101 | 10.4 | Yes | Yes | 18.4 | 18.3 | 0.1 | 0F6B99642EBC4D2CA74D8712EE3DC8FE | Add refrigerant: 10.4 oz | R22 | Non-TXV |  | 10.3% | 0.89703 | 19.79% | [5 empty] | Non-TXV | 10.3%
Antioch | CA | 94509-6047 |  | 2015-08-31 | 2015-08-31 09:28 | 2015-08-31 09:28 | RUUD - UAKA-048JAZ | 103 | 0 | Yes | Yes | 26 | 20.8 | 5.2 | 27702FF7CDE94F63B24E801D93611D45 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1034 |  | 2015-07-28 | 2015-07-28 16:30 | 2015-07-28 16:30 | CARRIER - 24ABB330W310 | 74 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | D347CF3C0E4D40BAB17DA9630C1C1193 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2436 |  | 2015-10-02 | 2015-10-02 09:19 | 2015-10-02 09:19 | OTHER - H5DB048S06A | 96 | 0 | Yes | Yes | 21 | 21.1 | -0.1 | A6C9EB0AA85D4EB5A5111F0BF7DE3B38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5313 |  | 2015-08-03 | 2015-08-03 10:23 | 2015-08-03 10:41 | RHEEM - RAJC-036JAS | 85 | 13.8 | Yes | Yes | 19.6 | 20.2 | -0.5 | 7A109E2827774D8C9061316DEEAB2991 |  | R22 | Non-TXV |  | 16.24% | 0.83765 | 31.2% | [5 empty] | Non-TXV | 16.24%
Napa | CA | 94559-4752 |  | 2015-09-25 | 2015-09-25 10:44 | 2015-09-25 10:44 | RUUD - UPGC025JAS | 66 | 0 | Yes | Yes | 17.6 | 20.1 | -2.5 | 90DC808D121A43C5A13EC99C9CCBF2B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-1216 |  | 2015-09-12 | 2015-09-12 11:40 | 2015-09-12 11:40 | OTHER - 4TTB3036E1000AA | 92 | 0 | Yes | Yes | 17.3 | 20 | -2.7 | 35C2D09AC53442F9A96BF7CE1EE9941A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4342 |  | 2015-08-06 | 2015-08-06 15:39 | 2015-08-06 15:39 | RHEEM - RAKA037JAZ | 85 | 0 | Yes | Yes | 22 | 18 | 4 | DFB55592335C439CA57412C0A7B86618 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-2243 |  | 2015-09-23 | 2015-09-23 13:41 | 2015-09-23 13:41 | CARRIER - 38ENO18310 | 55 | 0 | Yes | Yes | 19.2 | 17.7 | 1.5 | 134F22DB8FAF4BC096938440B16B84CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2447 |  | 2015-07-29 | 2015-07-29 10:01 | 2015-07-29 10:01 | FRIGIDAIRE - FS3BD030K | 85 | 0 | Yes | Yes | 17.1 | 18.7 | -1.6 | A9E9D28F5D9E45D78B81120133903CD8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pacheco | CA | 94553-5276 |  | 2015-08-07 | 2015-08-07 11:06 | 2015-08-07 11:06 | CARRIER - BRCS0421BD | 84 | 0 | Yes | Yes | 16 | 18.8 | -2.8 | 9A60425F297142678366D75ED21668B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-1432 |  | 2015-07-28 | 2015-07-28 14:26 | 2015-07-28 14:56 | RHEEM - AT-24B1M | 76 | 8.1 | Yes | Yes | 16.6 | 19.5 | -2.9 | 1133DC25F093493F801287F0426DDB39 |  | R22 | Non-TXV |  | 10.66% | 0.89342 | 20.48% | [5 empty] | Non-TXV | 10.66%
Pinole | CA | 94564-1516 |  | 2015-10-29 | 2015-10-29 09:51 | 2015-10-29 09:51 | CARRIER - 38CKC36 | 85 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 8943F13177EE4DC5801AA8936A082D21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-6057 |  | 2015-11-10 | 2015-11-10 10:12 | 2015-11-10 10:12 | GIBSON - JS3BA-036KA | 69 | 0 | Yes | Yes | 20.3 | 19.5 | 0.8 | 283C793590FD445087C350266AABF0EA |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-6001 |  | 2015-10-19 | 2015-10-19 11:50 | 2015-10-19 11:50 | GMC - CK36-1A9808507107 | 73 | 0 | Yes | Yes | 25.3 | 19.9 | 5.4 | A6CD30A8C5A14FDB8C8916B64B084E94 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7912 |  | 2015-09-21 | 2015-09-21 14:29 | 2015-09-21 14:29 | GOODMAN - CKJ421AB | 105 | 0 | Yes | Yes | 22.3 | 21.5 | 0.8 | F95C0A9016A34B07AAE81D600C01D41D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4157 |  | 2015-07-24 | 2015-07-24 12:27 | 2015-07-24 12:27 | TRANE - 4TTX6036G1000AA | 157 | 0 | Yes | Yes | 21.9 | 19.4 | 2.5 | 3F2277E1C039457E8ECABC05A1D7015C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4106 |  | 2015-08-20 | 2015-08-20 11:15 | 2015-08-20 11:15 | ALLEGIANCE - 2A7A3036A1000AA | 101 | 0 | Yes | Yes | 15 | 17.7 | -2.7 | BCCEFC60494B475885662C55121FF875 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5003 |  | 2015-07-15 | 2015-07-15 11:44 | 2015-07-15 11:44 | BRYANT - UNK | 69 | 0 | Yes | Yes | 24.6 | 19.6 | 5 | 183C99E9A8194334BB38A81C6E1BBF83 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94597-7831 |  | 2015-09-08 | 2015-09-08 12:00 | 2015-09-08 12:00 | DAY & NIGHT - 594DNX024000AAAA | 69 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | F8C044FB241E4A41BB37BC939DE41FB6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7521 |  | 2015-07-13 | 2015-07-13 10:21 | 2015-07-13 10:21 | ICP - AD030GD | 91 | 0 | Yes | Yes | 24.3 | 18.5 | 5.8 | 6B540935180C46FBAFFC9868C8774138 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pinole | CA | 94564-1133 |  | 2015-07-08 | 2015-07-08 09:54 | 2015-07-08 09:54 | BRYANT - 113RNA042 | 127 | 0 | Yes | Yes | 20.6 | 17.2 | 3.4 | 9615E802067542DFB1102936F48EB60B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winters | CA | 95694-1937 |  | 2015-10-28 | 2015-10-28 14:42 | 2015-10-28 14:42 | LENNOX - XC14-036-230-03 | 107 | 0 | Yes | Yes | 18.7 | 19.1 | -0.4 | C4B4B1D71A8C43F6A63AC56023E44BE2 |  | R410A | TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9438 |  | 2015-08-12 | 2015-08-12 09:36 | 2015-08-12 09:58 | CARRIER - 38GS036330 | 57 | 7.5 | Yes | Yes | 15.1 | 17.2 | -2.1 | 4B48628CAAF64F65A5F3C95DFFD9A7BC |  | R22 | Non-TXV |  | 13.16% | 0.86842 | 25.29% | [5 empty] | Non-TXV | 13.16%
Davis | CA | 95616-0000 |  | 2015-09-29 | 2015-09-29 14:23 | 2015-09-29 14:23 | COLEMAN - UNK | 53 | 0 | Yes | Yes | 24.4 | 20.6 | 3.8 | 4C62A995C92B4EA5A6F37E638FFF18B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4624 |  | 2015-09-23 | 2015-09-23 16:42 | 2015-09-23 16:42 | CARRIER - 38TKB036330 | 85 | 0 | Yes | Yes | 18 | 16.8 | 1.3 | 26ADEF039AB04590BD6632460AC3E6CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2988 |  | 2015-07-15 | 2015-07-15 11:07 | 2015-07-15 11:07 | YORK - H1CE018A06A | 58 | 0 | Yes | Yes | 17.7 | 18.2 | -0.5 | 8046E70BDDDB455689E99268B1719E1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4672 |  | 2015-07-15 | 2015-07-15 09:43 | 2015-07-15 09:43 | CARRIER - 38CK036300 | 80 | 0 | Yes | Yes | 16.4 | 18.2 | -1.8 | 507F82A2E6A44E7CBF6C7E3494206F83 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6507 |  | 2015-07-29 | 2015-07-29 15:43 | 2015-07-29 15:43 | TRANE - TTN036C100B2 | 117 | 0 | Yes | Yes | 25.7 | 19.7 | 6 | EB5BC07A3CFE4572BAC814AB26A67DE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-1508 |  | 2015-08-03 | 2015-08-03 11:45 | 2015-08-03 11:45 | OTHER - AC036X1021G | 63 | 0 | Yes | Yes | 26 | 20.1 | 6 | 54F91F4FAFB947939951A68B79333895 |  | R22 | Non-TXV |  | 0% | 1 | 0%
El Sobrante | CA | 94803-3121 |  | 2015-07-29 | 2015-07-29 09:05 | 2015-07-29 09:05 | CARRIER - 38CKC048370 | 85 | 0 | Yes | Yes | 18.1 | 18.9 | -0.8 | 49D6392B9F0D4F3281F4C4A00DA059BC |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1711 |  | 2015-07-21 | 2015-07-21 12:42 | 2015-07-21 12:42 | AMERICAN STANDARD - YCC36F1MOBF | 83 | 0 | Yes | Yes | 13.7 | 16.5 | -2.8 | 33F22350396F4384821BE9E18F01F353 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-6245 |  | 2015-08-11 | 2015-08-11 08:19 | 2015-08-11 08:19 | LENNOX - HS941139 | 84 | 0 | Yes | Yes | 24.9 | 22 | 2.9 | B2AC6EBE256C4261A4365F80DDDC37ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3809 |  | 2015-07-20 | 2015-07-20 12:08 | 2015-07-20 12:08 | TRANE - 4TTB3036D1000AA | 105 | 0 | Yes | Yes | 22 | 19.3 | 2.7 | EEEF6EB90A754E40B626C3437621736E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9388 |  | 2015-07-09 | 2015-07-09 09:44 | 2015-07-09 09:44 | CARRIER - 38CKC036---351 | 85 | 0 | Yes | Yes | 24.5 | 18.7 | 5.8 | 5AD7CBDCCA1941C9A0C0F909CF5D1A17 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5413 |  | 2015-11-17 | 2015-11-17 15:41 | 2015-11-17 15:41 | LENNOX - 13CD048 | 120 | 0 | Yes | Yes | 18 | 19.3 | -1.3 | CBCDE3180A8C4C81B74EC774F8F4FB2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-3940 |  | 2015-08-12 | 2015-08-12 13:17 | 2015-08-12 13:17 | YORK - YHJD48S41S4A | 236 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | 42F5C53ED0E045A88423FAC1818212CF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7145 |  | 2015-08-10 | 2015-08-10 17:43 | 2015-08-10 17:43 | GOODMAN - CM48-1EC | 86 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 1C316D68B768489CA4C726383E257023 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95407-7101 |  | 2015-08-18 | 2015-08-18 12:01 | 2015-08-18 12:01 | TRANE - TTR030C100A2 | 74 | 0 | Yes | Yes | 16.9 | 18.6 | -1.7 | 468A607C949D446BB6C7E1BF8778D0F7 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-9779 |  | 2015-08-03 | 2015-08-03 13:16 | 2015-08-03 13:16 | GOODMAN - TCGF36S41S1A | 58 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | C17F14B727B5457C85B49F8C519C98DF |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4221 |  | 2015-10-19 | 2015-10-19 11:45 | 2015-10-19 11:45 | PAYNE - PA13NA024000ABAA | 62 | 0 | Yes | Yes | 20.5 | 21.7 | -1.2 | B01A2C20524C4BAC89E2FDAEF4134A39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4407 |  | 2015-08-26 | 2015-08-26 14:23 | 2015-08-26 14:23 | OTHER - TCA036AKC4 | 96 | 0 | Yes | Yes | 23.5 | 20.4 | 3.1 | 5A1D7547805F42DB95F1CFE47C71BD92 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3038 |  | 2015-09-12 | 2015-09-12 14:02 | 2015-09-12 14:27 | - JSBD 036K | 138 | 14.3 | Yes | Yes | 26.4 | 20.4 | 6 | 39B77659CF3944519A9DC5259C79F808 |  | R22 | TXV |  | 10.36% | 0.89638 | 19.91% | [5 empty] | TXV | 10.36%
Walnut Creek | CA | 94595-1958 |  | 2015-08-26 | 2015-08-26 10:02 | 2015-08-26 10:02 | CARRIER - PA13NA024-F | 63 | 0 | Yes | Yes | 16.5 | 18.8 | -2.3 | D07BA94DC98E4F9D8A679D8DC85AF932 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9301 |  | 2015-08-10 | 2015-08-10 16:53 | 2015-08-10 16:53 | CARRIER - 38CKC036350 | 80 | 0 | Yes | Yes | 14.5 | 17.5 | -3 | 8A8E4F4BD33545A7AC5D39BCA607C066 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-1610 |  | 2015-11-06 | 2015-11-06 09:21 | 2015-11-06 09:21 | GE - UNK | 85 | 0 | Yes | Yes | 15.6 | 18.2 | -2.6 | 555D97BBBE78441BA4236FCC08FC2683 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2736 |  | 2015-07-09 | 2015-07-09 12:50 | 2015-07-09 12:50 | PAYNE - PA10JA036-A | 90 | 0 | Yes | Yes | 18.6 | 19.3 | -0.7 | FC435D73A694400983F257B93F84C1DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7704 |  | 2015-08-21 | 2015-08-21 10:01 | 2015-08-21 10:01 | PAYNE - PA10JA048000AAAA | 99 | 0 | Yes | Yes | 17.9 | 19.7 | -1.8 | 036122F19E6846159AED1F411887D808 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9392 |  | 2015-11-05 | 2015-11-05 14:25 | 2015-11-05 14:25 | GOODMAN - CKJ301B | 92 | 0 | Yes | Yes | 22.3 | 17.7 | 4.6 | 4361DAD5A4EF44389882C6A5C25D159C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5638 |  | 2015-07-30 | 2015-07-30 15:06 | 2015-07-30 15:06 | GE - UNK | 85 | 0 | Yes | Yes | 17.3 | 19.3 | -2 | F135AA2B211340FD8700EC33BA6B4BEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1841 |  | 2015-07-29 | 2015-07-29 11:02 | 2015-07-29 11:02 | TRANE - 2TTR3036A1000AA | 85 | 0 | Yes | Yes | 18.7 | 19.1 | -0.3 | 8B8772B814314DADA1CC8E0198423C2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-6414 |  | 2015-07-31 | 2015-07-31 13:03 | 2015-07-31 13:03 | CARRIER - 38CK042 | 80 | 0 | Yes | Yes | 18.5 | 18.9 | -0.3 | 7BA4E35E5E0B4C8CBC31355489BBDA66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-6560 |  | 2015-10-14 | 2015-10-14 08:39 | 2015-10-14 08:39 | OTHER - PH13NR018 | 87 | 0 | Yes | Yes | 22.4 | 21.5 | 0.9 | 3C9934D5E474425586F755052505BA6D |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2231 |  | 2015-07-27 | 2015-07-27 11:06 | 2015-07-27 11:31 | GOODMAN - CLT24-1B | 85 | 7.4 | Yes | Yes | 16.4 | 19.4 | -3 | 9838A9941A104272A8EFA53A545F951A |  | R22 | TXV |  | 8.706% | 0.91294 | 16.73% | [5 empty] | TXV | 8.706%
Vacaville | CA | 95687-4906 |  | 2015-07-23 | 2015-07-23 12:32 | 2015-07-23 12:32 | GOODMAN - CK361C | 85 | 0 | Yes | Yes | 23 | 19.3 | 3.7 | B99C7E4C128C4321B202ABCBD2896180 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2202 |  | 2015-08-04 | 2015-08-04 12:14 | 2015-08-04 12:14 | CARRIER - PA10JA030-A | 72 | 0 | Yes | Yes | 21.2 | 19.5 | 1.7 | 5727455A4B78416C8A57C61B694E3475 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8242 |  | 2015-08-11 | 2015-08-11 10:25 | 2015-08-11 10:25 | CARRIER - PA10JA0-60-A | 121 | 0 | Yes | Yes | 23 | 20.4 | 2.6 | 0F84F362CD044E9384AAD7188AAB9979 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5473 |  | 2015-09-11 | 2015-09-11 13:29 | 2015-09-11 13:29 | TRANE - TTB036C100A | 90 | 0 | Yes | Yes | 26.7 | 22.1 | 4.6 | 90B0BDB5AEFA4B67983DD5276B3A2E5C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6302 |  | 2015-10-19 | 2015-10-19 15:58 | 2015-10-19 15:58 | AMERICAN STANDARD - TCA236AKA4 | 112 | 0 | Yes | Yes | 20.9 | 21.9 | -1 | C8A4C640C5BC48AA9008E6A7A2955211 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4850 |  | 2015-08-06 | 2015-08-06 19:18 | 2015-08-06 19:18 | TRANE - TTB036C100A | 90 | 0 | Yes | Yes | 17.5 | 19.4 | -1.9 | 65FD3FED67CD40F7AC8CF8E9C34133D9 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4334 |  | 2015-11-04 | 2015-11-04 14:07 | 2015-11-04 14:07 | OTHER - CA5536VKD1 | 83 | 0 | Yes | Yes | 21.9 | 19.6 | 2.4 | 743AD8D86F274A1295C11B50621D9218 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1712 |  | 2015-08-21 | 2015-08-21 10:18 | 2015-08-21 10:18 | PAYNE - 5658JO36-A | 85 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 2F2DA597E45C4A00B769381CE83083BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5505 |  | 2015-10-30 | 2015-10-30 16:12 | 2015-10-30 16:12 | TRANE - 4TTR3036B100AA | 126 | 0 | Yes | Yes | 18.6 | 18.3 | 0.3 | B43F2FE5810146F7A7D212FDB1249728 |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3647 |  | 2015-09-16 | 2015-09-16 11:09 | 2015-09-16 11:09 | CARRIER - UNKNOWN | 53 | 0 | Yes | Yes | 17.6 | 20.6 | -2.9 | B922DA246E404E8AB0747DDEF28B658E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5162 |  | 2015-10-13 | 2015-10-13 12:28 | 2015-10-13 12:28 | CARRIER - 38CKC036350 | 85 | 0 | Yes | Yes | 18.7 | 19.9 | -1.2 | 861501369A084AAF89DB400CD14CAC4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4813 |  | 2015-08-10 | 2015-08-10 13:41 | 2015-08-10 13:41 | YORK - CZE04811A | 226 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 9970F0D654454CC88076533177F76176 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4830 |  | 2015-08-31 | 2015-08-31 11:11 | 2015-08-31 11:11 | RHEEM - UNK | 100 | 0 | Yes | Yes | 20.2 | 19.3 | 0.9 | 39A84B93A54A4A22A4C2EA9997379071 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5760 |  | 2015-09-02 | 2015-09-02 14:59 | 2015-09-02 14:59 | RHEEM - RAJC-048JAS | 156 | 0 | Yes | Yes | 19.6 | 16.1 | 3.5 | C03B36A4532F4032843BB98984EF03D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1972 |  | 2015-08-11 | 2015-08-11 12:36 | 2015-08-11 12:36 | OTHER - D6NZ060N09006NXA | 82 | 0 | Yes | Yes | 20.5 | 20.4 | 0.1 | 5925895F3578416FA7A517C945D9DA4A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4215 |  | 2015-11-03 | 2015-11-03 10:44 | 2015-11-03 10:44 | RUUD - UAMB-042JAZ | 96 | 0 | Yes | Yes | 17.4 | 20.2 | -2.8 | EF384A3184C34CBE979E903F65115A8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5755 |  | 2015-09-18 | 2015-09-18 11:49 | 2015-09-18 11:49 | - AC030M1021SA | 57 | 0 | Yes | Yes | 23.9 | 21.4 | 2.5 | 62D6662176BF43129CCB50A98E957585 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3731 |  | 2015-10-21 | 2015-10-21 12:49 | 2015-10-21 12:49 | PAYNE - PA13NR018 | 85 | 0 | Yes | Yes | 18 | 20.1 | -2.1 | B53901B0252040BFBE9E566A3DE2D7E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3732 |  | 2015-10-15 | 2015-10-15 10:46 | 2015-10-15 10:46 | UNK - UNK | 85 | 0 | Yes | Yes | 18.6 | 18.8 | -0.2 | B6FC0D6606BC4F6792F9A69EDBD3BDD3 |  |  |  |  | 0% | 1 | 0%
Woodland | CA | 95695-5873 |  | 2015-10-12 | 2015-10-12 15:16 | 2015-10-12 15:16 | AMERICAN STANDARD - 4A7A5036E1000AB | 116 | 0 | Yes | Yes | 18.5 | 17.8 | 0.7 | 1C7380633D6642E5B1A4E4E43ED4A59A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3733 |  | 2015-11-04 | 2015-11-04 10:55 | 2015-11-04 10:55 | AMERICAN STANDARD - 2A7A3018A1000AA | 64 | 0 | Yes | Yes | 22.6 | 20.9 | 1.7 | 07B21632C4764325B4AB8517510BF893 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3732 |  | 2015-11-04 | 2015-11-04 13:54 | 2015-11-04 13:54 | BRYANT - 113RNA018-E | 56 | 0 | Yes | Yes | 22.6 | 18.7 | 3.9 | 7F12DA7B9EC947FF82B8CC2A2380E95C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94597-3103 |  | 2015-08-03 | 2015-08-03 10:49 | 2015-08-03 10:49 | GOODMAN - GSC130241AE | 93 | 0 | Yes | Yes | 16.7 | 19.4 | -2.7 | 1275546EE4F9478999DE571742CE42F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6328 |  | 2015-08-19 | 2015-08-19 15:12 | 2015-08-19 15:12 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 19.5 | 18.5 | 1 | A2CE901763C44D42BD0E85D2F0090982 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3734 |  | 2015-11-04 | 2015-11-04 15:18 | 2015-11-04 15:18 | AMERICAN STANDARD - 2A7A1024A1000AA | 62 | 0 | Yes | Yes | 23.8 | 19.3 | 4.5 | 774CFE2B093447B4875584CE4CB25F81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5022 |  | 2015-08-13 | 2015-08-13 12:32 | 2015-08-13 13:09 | RHEEM - RAKA-048JAZ | 103 | 23.4 | Yes | Yes | 18 | 19.8 | -1.8 | C0E30F29CD6947B2AC2955DC0E641526 |  | R22 | Non-TXV |  | 22.72% | 0.77282 | 43.66% | [5 empty] | Non-TXV | 22.72%
Brentwood | CA | 94513-5022 |  | 2015-08-13 | 2015-08-13 13:15 | 2015-08-13 13:15 | RHEEM - RAKA-042JAZ | 79 | 0 | Yes | Yes | 16.3 | 18.8 | -2.5 | 5D2F1A55294046F8BDEBDBD6B0C10F47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5800 |  | 2015-09-04 | 2015-09-04 09:15 | 2015-09-04 09:15 | TRANE - BTD730A100B0 | 74 | 0 | Yes | Yes | 24.1 | 18.6 | 5.6 | 72A396D00E2445BB99AFE825F4DB6542 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2608 |  | 2015-10-26 | 2015-10-26 08:31 | 2015-10-26 08:31 | PAYNE - PA13NR030 | 74 | 0 | Yes | Yes | 19.8 | 19.8 | 0 | 6B6284C92B344F43BD93F739F68074E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6057 |  | 2015-10-30 | 2015-10-30 10:09 | 2015-10-30 10:09 | CARRIER - 38EN030300 | 86 | 0 | Yes | Yes | 19.5 | 20.9 | -1.4 | E750824127EF4468AEC09173554BD7D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1228 |  | 2015-06-23 | 2015-06-23 13:49 | 2015-06-23 13:49 | AMERICAN STANDARD - 2A7A2042A1000AA | 95 | 0 | Yes | Yes | 26.6 | 19.9 | 6.7 | C09FD6DC90864BBBB86B9C5CF3225438 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5166 |  | 2015-08-20 | 2015-08-20 15:48 | 2015-08-20 15:48 | CARRIER - 24ABC648A310 | 85 | 0 | Yes | Yes | 22.1 | 19 | 3.1 | BAB5C8DACEB14B1E89DC7AF980C5671D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8601 |  | 2015-09-11 | 2015-09-11 11:11 | 2015-09-11 11:11 | PAYNE - 591NX060 | 85 | 0 | Yes | Yes | 19.4 | 18.6 | 0.8 | 5DA8E01AC148475892E150BFD9C3699B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8601 |  | 2015-09-11 | 2015-09-11 11:29 | 2015-09-11 11:29 | PAYNE - 591NX024 | 85 | 0 | Yes | Yes | 14.2 | 15.7 | -1.5 | 3A89064678714DB98BC9A406A1214141 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3523 |  | 2015-09-11 | 2015-09-11 15:12 | 2015-09-11 15:12 | TEMPSTAR - TCA048AKC4 | 85 | 0 | Yes | Yes | 26 | 25.3 | 0.7 | C09407FB36BF4B668EFCA90E287010DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2636 |  | 2015-08-03 | 2015-08-03 09:06 | 2015-08-03 09:06 | GUARDIAN - GCGD36S21SA2 | 63 | 0 | Yes | Yes | 18.3 | 18.2 | 0.1 | 3E701BBDD7884F6BA9850CA4AB5BAA99 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-1088 |  | 2015-08-17 | 2015-08-17 11:41 | 2015-08-17 12:10 | RHEEM - RAKA-048JAZ | 103 | -9.7 | Yes | Yes | 21.7 | 19.3 | 2.4 | 2389AFB7ACA84E1D97550DBEA72408D8 |  | R22 | Non-TXV |  | -9.417% | 1.0942 | 2.637% |  |  |  |  | Non-TXV |  |  | -9.417%
Brentwood | CA | 94513-5132 |  | 2015-09-10 | 2015-09-10 16:14 | 2015-09-10 16:34 | CARRIER - 38BRC048---371-- | 140 | -20.6 | Yes | Yes | 16.3 | 18.1 | -1.8 | BB64A14C8EB8473CA2F93A1193384500 |  | R22 | TXV |  | -14.71% | 1.1471 | 4.121% |  |  |  |  | TXV |  |  | -14.71%
Pittsburg | CA | 94565-3647 |  | 2015-09-02 | 2015-09-02 12:07 | 2015-09-02 12:26 | GOODMAN - CKL36-1D | 72 | 8.9 | Yes | Yes | 18 | 19.6 | -1.6 | 68CD5C1BE09A407EA1FC4A4C5E6DAE3E |  | R22 | Non-TXV |  | 12.36% | 0.87639 | 23.76% | [5 empty] | Non-TXV | 12.36%
Oakley | CA | 94561-5037 |  | 2015-09-25 | 2015-09-25 11:16 | 2015-09-25 11:38 | TEMPSTAR - T4A336GKA100 | 93 | 13.1 | Yes | Yes | 20.5 | 19.9 | 0.6 | 08E9F2805F644A3D8B5D425A86A37FCB |  | R410A | TXV |  | 14.09% | 0.85914 | 27.07% | [5 empty] | TXV | 14.09%
Vallejo | CA | 94591-7570 |  | 2015-07-30 | 2015-07-30 10:54 | 2015-07-30 10:54 | BRYANT - 582ANW036060AAAF | 85 | 0 | Yes | Yes | 19.7 | 18.2 | 1.5 | 39CDC4D8767A447B80613A8C42FF2E44 | Final Suction Temperature must be between 20°F and 80°F. Please check entries. Actual Superheat must be between 0°F and 100°F. Check entries and calibration. | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2086 |  | 2015-09-03 | 2015-09-03 09:56 | 2015-09-03 09:56 | RHEEM - RAFD-036JAS | 80 | 0 | Yes | Yes | 23.7 | 19.3 | 4.4 | 31DA251E0E3C460BBC1A467333EF8BE7 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4269 |  | 2015-10-16 | 2015-10-16 10:02 | 2015-10-16 10:02 | RHEEM - RAFD-036JAS | 80 | 0 | Yes | Yes | 21.4 | 21.7 | -0.3 | 376F09F71B5B49B5B3B718A416AB6A87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4814 |  | 2015-10-07 | 2015-10-07 12:02 | 2015-10-07 12:02 | RHEEM - RAKA-036JAZ | 77 | 0 | Yes | Yes | 19.8 | 19.9 | -0.1 | C9369AE4EFA14E788D0449A13520A6A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4423 |  | 2015-09-02 | 2015-09-02 09:44 | 2015-09-02 10:05 | OTHER - UNK | 86 | -8.1 | Yes | Yes | 18.1 | 17.7 | 0.4 | 8E7ACC947CE641E7A844B94F52698BDD |  | R22 | Non-TXV |  | -9.419% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.419%
Suisun City | CA | 94585-1962 |  | 2015-09-26 | 2015-09-26 14:08 | 2015-09-26 14:08 | BRYANT - 113RNA024000BCAA | 85 | 0 | Yes | Yes | 19 | 19 | 0 | B53E6D7FB1E741ED8195575BA7BD6FCA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4835 |  | 2015-08-31 | 2015-08-31 10:23 | 2015-08-31 10:23 | YORK - D1NA030N05606C | 76 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | 7B6C1B03657F4A19BB3219B893E3C3A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4344 |  | 2015-08-26 | 2015-08-26 13:55 | 2015-08-26 13:55 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | 88EBB5649CC24E11B76C7E3ED46C0F5C |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-0000 |  | 2015-09-03 | 2015-09-03 10:40 | 2015-09-03 10:40 | CARRIER - 38CK060370 | 85 | 0 | Yes | Yes | 19.7 | 19.7 | 0 | 9CAE0AF66B6A418EA82A69DB848E1648 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1574 |  | 2015-08-24 | 2015-08-24 14:53 | 2015-08-24 15:20 | CARRIER - 38EZG036310 | 100 | 14 | Yes | Yes | 25.2 | 20.4 | 4.8 | B7D1FDAE7DFD4875814D2BB7D74D9C63 |  | R410A | TXV |  | 14% | 0.86 | 26.9% | [5 empty] | TXV | 14%
Oakley | CA | 94561-2134 |  | 2015-09-29 | 2015-09-29 09:27 | 2015-09-29 09:27 | TRANE - 2TTBOO36A1000AA | 76 | 0 | Yes | Yes | 20.8 | 19.5 | 1.3 | 2F03FCE4132C45D3ADAF16A02008471A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5860 |  | 2015-09-12 | 2015-09-12 09:26 | 2015-09-12 09:26 | OTHER - PA13NABAA | 53 | 0 | Yes | Yes | 20.6 | 20.6 | 0 | 0A1905D4526745B7902A2AD99B314F2F |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1273 |  | 2015-10-12 | 2015-10-12 09:12 | 2015-10-12 09:12 | UNITARY PRODUCTS GROUP - 24ABA336A310 | 85 | 0 | Yes | Yes | 22.5 | 17.7 | 4.8 | A3985E536D4B455E950E895317E57BDA |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8521 |  | 2015-07-22 | 2015-07-22 12:01 | 2015-07-22 12:01 | - BRCS0361BD | 63 | 0 | Yes | Yes | 15.6 | 18.6 | -3 | 68B0D92BB5D34018BBB7B9875B3AE16F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4729 |  | 2015-10-19 | 2015-10-19 10:10 | 2015-10-19 10:10 | RHEEM - RAKA-030JAZ | 66 | 0 | Yes | Yes | 21.5 | 21.7 | -0.1 | E5BC13D863364F249D73DE41478A7117 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2933 |  | 2015-10-13 | 2015-10-13 11:22 | 2015-10-13 11:22 | CARRIER - 585HJ030040BAF | 68 | 0 | Yes | Yes | 20 | 19 | 1.1 | 51146B0EE821468481E1505355275B82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
El Sobrante | CA | 94803-1674 |  | 2015-07-14 | 2015-07-14 10:59 | 2015-07-14 10:59 | RUUD - UAKA-030JAZ | 66 | 0 | Yes | Yes | 18 | 18.7 | -0.7 | F234A1A926484021AA201A6C98A4AA63 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4018 |  | 2015-09-18 | 2015-09-18 10:29 | 2015-09-18 10:29 | DAY & NIGHT - N/A | 40 | 0 | Yes | Yes | 22.4 | 19.7 | 2.8 | E714C8AD6BDB426782EA410D069824E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-0000 |  | 2015-07-09 | 2015-07-09 10:43 | 2015-07-09 10:43 | CARRIER - 24ABB336A310 | 83 | 0 | Yes | Yes | 19.4 | 18.2 | 1.2 | 2C6EC8AA7AD64C28B45D9877CE4C551B |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2223 |  | 2015-08-03 | 2015-08-03 16:35 | 2015-08-03 16:35 | RHEEM - RAKA030JAS | 85 | 0 | Yes | Yes | 17.1 | 19.5 | -2.4 | 4ECE0F4984B14C06960D3C1E6A5204C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5718 |  | 2015-10-08 | 2015-10-08 11:54 | 2015-10-08 11:54 | PAYNE - PA15NC036-A | 71 | 0 | Yes | Yes | 19.5 | 20.6 | -1.1 | 6A8946CE37464EFA872AF2E9B78AA884 |  | R22 | TXV |  | 0% | 1 | 0%
Davis | CA | 95616-1342 |  | 2015-10-01 | 2015-10-01 10:28 | 2015-10-01 10:28 | CARRIER - 38CKC042310 | 85 | 0 | Yes | Yes | 18.6 | 15.6 | 3 | 3CA57327802A44B38B88FAD05D3F1420 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3086 |  | 2015-09-01 | 2015-09-01 14:17 | 2015-09-01 14:45 | CARRIER - 38EN018300 | 54 | 7 | Yes | Yes | 0.4 | 18 | -17.6 | F55CC53B4A894BE7B051574748472D72 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 12.96% | 0.87037 | 24.91% | [5 empty] | Non-TXV | 12.96%
Brentwood | CA | 94513-6235 |  | 2015-08-26 | 2015-08-26 16:17 | 2015-08-26 16:17 | CARRIER - 563CN036-D | 104 | 0 | Yes | Yes | 17.8 | 20.1 | -2.3 | 70743370C8BB4FD090D7F1B5ECE70287 |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3217 |  | 2015-10-09 | 2015-10-09 10:38 | 2015-10-09 10:38 | CARRIER - 38CKC036350 | 70 | 0 | Yes | Yes | 20.3 | 21.2 | -0.9 | F38CECEB986D4F6FA087855E19B4EC3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94596-6027 |  | 2015-08-05 | 2015-08-05 15:06 | 2015-08-05 15:06 | OTHER - TCA236AKAA | 113 | 0 | Yes | Yes | 25.4 | 20.4 | 5 | 5730C09FE5B3485184929A99FE773945 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-4515 |  | 2015-09-23 | 2015-09-23 12:10 | 2015-09-23 12:10 | RHEEM - RRNA-B036JK06X | 83.2 | 0 | Yes | Yes | 15 | 16.1 | -1.1 | ABA6D3D181D045F399A42CB39D75B5B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-0000 |  | 2015-07-09 | 2015-07-09 12:01 | 2015-07-09 12:01 | CARRIER - CA13NA036-C | 72 | 0 | Yes | Yes | 19 | 18.3 | 0.7 | 7F5CA59CE1424A579943671C8AB63533 |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-5333 |  | 2015-08-31 | 2015-08-31 16:23 | 2015-08-31 16:23 | TEMPSTAR - 38QH01310 | 148 | 0 | Yes | Yes | 15.2 | 17.7 | -2.5 | C749A9F9B3E1491F8EF5BB1300E5B4B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6043 |  | 2015-09-09 | 2015-09-09 12:53 | 2015-09-09 12:53 | TRANE - 277B0048A1000AA | 109 | 0 | Yes | Yes | 17.3 | 20.2 | -2.9 | 5DE5109BC8D6454480BD10321D8554EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-5735 |  | 2015-07-24 | 2015-07-24 13:53 | 2015-07-24 13:53 | BRYANT - 561CJ024-E | 85 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 24B0DA5E29294BA0B01EA2680607C919 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-9412 |  | 2015-09-22 | 2015-09-22 13:42 | 2015-09-22 13:42 | TRANE - 4TTX4048A1000AA | 127 | 0 | Yes | Yes | 21.9 | 18.8 | 3.1 | 04EFC03CEABC461EA3001B2CCB027529 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8264 |  | 2015-10-19 | 2015-10-19 14:23 | 2015-10-19 14:23 | GOODMAN - CK60-1C | 182 | 0 | Yes | Yes | 19 | 21.9 | -2.9 | 07099E9F32904D3F879F55AE90CA8A8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5182 |  | 2015-07-01 | 2015-07-01 15:02 | 2015-07-01 15:02 | BDP - 569BJO36 | 93 | 0 | Yes | Yes | 22.9 | 20.7 | 2.2 | 24A9F066D5AB47B6A3A7A9938A52E590 | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2611 |  | 2015-08-24 | 2015-08-24 11:48 | 2015-08-24 11:48 | PAYNE - 591ANX036000AAAA | 82 | 0 | Yes | Yes | 19.1 | 19.3 | -0.2 | 851E06D00DDB49C1A80F5FE12FE10AE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2611 |  | 2015-08-24 | 2015-08-24 12:09 | 2015-08-24 12:09 | PAYNE - 591ANX036000AAAA | 83 | 0 | Yes | Yes | 17.1 | 19.4 | -2.3 | 107D8047EF0342E2B9CE2EB247A1E6E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3611 |  | 2015-11-06 | 2015-11-06 14:26 | 2015-11-06 14:26 | TRANE - 3TD736A100B0 | 88 | 0 | Yes | Yes | 22.8 | 21 | 1.8 | 235D41A4263141778AAD93BDC14EE779 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2078 |  | 2015-09-03 | 2015-09-03 17:47 | 2015-09-03 17:47 | LUXAIRE - HAMC-F024SA | 85 | 0 | Yes | Yes | 23.5 | 20.4 | 3.1 | BB3A6DA115B64C2A92A956C6D06DADB6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-1416 |  | 2015-09-21 | 2015-09-21 12:32 | 2015-09-21 12:32 | DAY & NIGHT - 591AN060-A | 85 | 0 | Yes | Yes | 17.8 | 20.4 | -2.6 | 13849153BF824E7A939536DA404ED7C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-6734 |  | 2015-09-21 | 2015-09-21 10:32 | 2015-09-21 10:32 | YORK - H2RE060S06A | 241 | 0 | Yes | Yes | 12.6 | 19.4 | -6.8 | 32874362E325466DBFD47865FE73B55F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3733 |  | 2015-11-05 | 2015-11-05 09:19 | 2015-11-05 09:19 | AMERICAN STANDARD - 2A7A1018A1000AA | 50 | 0 | Yes | Yes | 23.5 | 20.4 | 3.1 | 322410D8702C4B7B85A58D444059C769 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6766 |  | 2015-10-16 | 2015-10-16 15:10 | 2015-10-16 15:10 | TRANE - 4TTX6036B1000AA | 106 | 0 | Yes | Yes | 22.1 | 23.5 | -1.4 | F6CE01CB1C464BAEB5B39697FFC0FCF3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3733 |  | 2015-10-15 | 2015-10-15 11:47 | 2015-10-15 11:47 | ALLEGIANCE - 7A0018A100A0 | 65 | 0 | Yes | Yes | 19.4 | 20.9 | -1.5 | 5897E5AC6C6F466F9A27C936954A4A06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5467 |  | 2015-08-05 | 2015-08-05 12:55 | 2015-08-05 12:55 | PAYNE - PA13NA036000AEAA | 85 | 0 | Yes | Yes | 15.7 | 15.7 | 0 | 5F8C1D882C8D4888B923D97DD5666EE4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-3609 |  | 2015-07-20 | 2015-07-20 16:53 | 2015-07-20 16:53 | ALLEGIANCE - 2A7A1030A1000AA | 85 | 0 | Yes | Yes | 19.7 | 18.4 | 1.4 | 65E51EC4D4CB4A828CA6F75128F1EE56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-4474 |  | 2015-08-25 | 2015-08-25 14:38 | 2015-08-25 14:38 | YORK - H1RA042S06D | 84 | 0 | Yes | Yes | 17.3 | 20.1 | -2.8 | D1495754CF2B42A480FC64BB1F8AFA80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7321 |  | 2015-08-19 | 2015-08-19 14:02 | 2015-08-19 14:02 | CARRIER - 38CKC048300 | 103 | 0 | Yes | Yes | 22 | 19.8 | 2.2 | BA0DB2B3250D48BA837A267FF89DF1DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-4444 |  | 2015-08-21 | 2015-08-21 11:34 | 2015-08-21 11:34 | - 561CJ036-D | 84 | 0 | Yes | Yes | 21.3 | 18.6 | 2.7 | 471C4623A84949E080C4FD089135A4F8 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4267 |  | 2015-09-02 | 2015-09-02 14:04 | 2015-09-02 14:04 | RHEEM - RAFD-036JAS | 80 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | 860149E5F2D045DEB094D6AA678DBBDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2728 |  | 2015-07-27 | 2015-07-27 15:39 | 2015-07-27 15:39 | BDP - UNK | 85 | 0 | Yes | Yes | 15.8 | 18.5 | -2.7 | A99C318D2DD84CEFBDE87A3F9BA4D6B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4076 |  | 2015-11-05 | 2015-11-05 13:41 | 2015-11-05 13:41 | OTHER - UNKNOWN | 70 | 0 | Yes | Yes | 18 | 17.5 | 0.6 | 9B1BEC314E45417EA818D573DB42AE8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7757 |  | 2015-11-03 | 2015-11-03 14:21 | 2015-11-03 14:21 | GOODMAN - VSX130481AC | 97 | 0 | Yes | Yes | 24.1 | 23.1 | 1 | 540CBEE1BA11459C9562B22B6CD511D7 |  | R410A | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1826 |  | 2015-09-16 | 2015-09-16 14:34 | 2015-09-16 14:34 | DAY & NIGHT - 591ANX036000AAAA | 86 | 0 | Yes | Yes | 21.4 | 18.2 | 3.2 | 06EE76FEC9144103987437E13F22B850 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4038 |  | 2015-08-03 | 2015-08-03 14:25 | 2015-08-03 14:25 | TRANE - 4TTB3036D1000AA | 105 | 0 | Yes | Yes | 23 | 20.4 | 2.6 | BCC989AD01C44D23B2D079A9A57C60F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4602 |  | 2015-09-25 | 2015-09-25 13:40 | 2015-09-25 13:40 | - AMO24MA322A | 85 | 0 | Yes | Yes | 14.3 | 17.2 | -2.9 | 177DB2572EBD43AF89AE789559AE9B3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4802 |  | 2015-10-06 | 2015-10-06 12:09 | 2015-10-06 12:09 | YORK - H20H048S06 | 190 | 0 | Yes | Yes | 14.4 | 17 | -2.6 | 9E39791C4223435C8C45CD431D44760A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6340 |  | 2015-07-14 | 2015-07-14 15:34 | 2015-07-14 15:34 | GE - B1B980A100A31 | 53 | 0 | Yes | Yes | 18.4 | 20.8 | -2.4 | 999C1D7DDFDA445A9DDDA18B5E830CA2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-4748 |  | 2015-07-30 | 2015-07-30 14:19 | 2015-07-30 14:19 | TRANE - TTB024C1 | 48 | 0 | Yes | Yes | 15.2 | 16.6 | -1.4 | E22C9F94BE034ADCA128B3377DAC8B58 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6037 |  | 2015-10-03 | 2015-10-03 14:24 | 2015-10-03 14:24 | CARRIER - 38BRB036300 | 122 | 0 | Yes | Yes | 25.8 | 21 | 4.8 | 7490C6C04F2843C8B424258174C0D0DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5192 |  | 2015-10-15 | 2015-10-15 14:09 | 2015-10-15 02:34 | RHEEM - UNKNOWN | 123 | 21.9 | Yes | Yes | 18.5 | 20.4 | -1.9 | E6120A9EFF0245CFBEFFF545FC57AA12 |  | R22 | Non-TXV |  | 17.8% | 0.82195 | 34.22% | [5 empty] | Non-TXV | 17.8%
Fairfield | CA | 94533-5026 |  | 2015-08-04 | 2015-08-04 10:53 | 2015-08-04 10:53 | AMANA - UNK | 85 | 0 | Yes | Yes | 21.9 | 18.8 | 3.1 | E914BCE04F674DFD97B6E11D142C7417 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6314 |  | 2015-09-09 | 2015-09-09 13:39 | 2015-09-09 13:39 | YORK - H1RA042S06 | 84 | 0 | Yes | Yes | 18.7 | 18.7 | 0 | D0753119D2A44D96B5986B5C4F8948AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6670 |  | 2015-08-19 | 2015-08-19 15:28 | 2015-08-19 15:28 | GOODMAN - GSC130361FA | 83 | 0 | Yes | Yes | 19.5 | 18.8 | 0.7 | 1F9242D98ADF4E93ACB8351D13E8BC14 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1057 |  | 2015-09-29 | 2015-09-29 12:57 | 2015-09-29 12:57 | RHEEM - RAKA037JAZ | 85 | 0 | Yes | Yes | 22.6 | 20.3 | 2.3 | 4CE62FD630AB4464BBB3C6769FC86759 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-3616 |  | 2015-07-31 | 2015-07-31 14:00 | 2015-07-31 14:00 | PAYNE - H1RA048S06D | 85 | 0 | Yes | Yes | 15 | 17.9 | -2.9 | 7D7C0759B4BD41438CBD2B775DFFBE95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-3130 |  | 2015-10-01 | 2015-10-01 09:28 | 2015-10-01 09:28 | BRYANT - 563CN024-C | 85 | 0 | Yes | Yes | 15 | 15.5 | -0.4 | 74AA404FD4324079911D8727D2F26147 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1061 |  | 2015-08-28 | 2015-08-28 15:23 | 2015-08-28 15:42 | TRANE - 2TTR1024A10000 | 62 | 2.2 | Yes | Yes | 16.6 | 18.7 | -2.1 | F0DFC57CA194468BA07C4BB619343DB0 |  | R22 | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Vacaville | CA | 95687-6216 |  | 2015-07-15 | 2015-07-15 14:26 | 2015-07-15 14:26 | CARRIER - 38CKC030320 | 85 | 0 | Yes | Yes | 20.5 | 19.7 | 0.8 | 19B7D3B1818C49B3B2A05D2AA99B36EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4144 |  | 2015-11-10 | 2015-11-10 09:18 | 2015-11-10 09:18 | RHEEM - RRKA-024JK06X | 50 | 0 | Yes | Yes | 18.8 | 18.2 | 0.6 | C85BCAB046F7450FAFD7EDF13F035272 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-0000 |  | 2015-09-10 | 2015-09-10 15:16 | 2015-09-10 15:16 | GOODMAN - TCGD36S21S2A | 63 | 0 | Yes | Yes | 19 | 17.7 | 1.3 | 61365CAB951946108D8D2A9D2A03B561 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7347 |  | 2015-10-16 | 2015-10-16 14:56 | 2015-10-16 14:56 | AMANA - ZRCF30U01D | 118 | 0 | Yes | Yes | 21.1 | 19.7 | 1.4 | 5F4F29A9D9B745CAA1601304B2C546D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6640 |  | 2015-08-13 | 2015-08-13 11:31 | 2015-08-13 11:31 | YORK - CZB04211A | 141 | 0 | Yes | Yes | 14 | 17 | -3 | 76DC10EC3579493D89A3AE1DBC4D24FD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3423 |  | 2015-08-10 | 2015-08-10 15:21 | 2015-08-10 15:21 | GOODMAN - GCGD24S41S3A | 61 | 0 | Yes | Yes | 19.2 | 19.2 | 0 | 5FE945CC3EE7424BB853BECE4BB714EF |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-5909 |  | 2015-07-29 | 2015-07-29 09:17 | 2015-07-29 09:17 | OTHER - 24AB342A300 | 111 | 0 | Yes | Yes | 25.4 | 22.9 | 2.6 | 84E8DCBA35BA4E088128228E0CD39741 |  | R410A | TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-5909 |  | 2015-07-29 | 2015-07-29 09:10 | 2015-07-29 09:49 | CARRIER - 24ABA336A300 | 95 | 10.3 | Yes | Yes | 25 | 21.2 | 3.8 | 5C8F20C203A44A5692C9158A30FB8EEF |  | R410A | TXV |  | 10.84% | 0.89158 | 20.84% | [5 empty] | TXV | 10.84%
Napa | CA | 94559-1853 |  | 2015-09-11 | 2015-09-11 13:38 | 2015-09-11 13:38 | - CCU12A36A-1 | 94 | 0 | Yes | Yes | 19 | 20.2 | -1.2 | 81E0CF481E314BD08EF762C57EC8ADFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-4554 |  | 2015-08-07 | 2015-08-07 16:35 | 2015-08-07 16:35 | CARRIER - 591ANX048000ACAA | 128 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 274F4A0F981D470782CE5D45B4E131B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3733 |  | 2015-10-15 | 2015-10-15 12:13 | 2015-10-15 12:13 | ALLEGIANCE - 7A0018A100A1 | 65 | 0 | Yes | Yes | 19.6 | 20.4 | -0.8 | D5FA3127783C4003B5629E48AB3BA974 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1307 |  | 2015-07-28 | 2015-07-28 08:35 | 2015-07-28 08:35 | OTHER - PA13NR036-C | 128 | 0 | Yes | Yes | 22.6 | 19.5 | 3.1 | 85708E9E18B044DEAB7186E934CDD021 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6661 |  | 2015-08-13 | 2015-08-13 11:19 | 2015-08-13 11:19 | CARRIER - 24ABB330W310 | 74 | 0 | Yes | Yes | 20.7 | 18 | 2.7 | F5D6B82B1E78499AB43547913D69297A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2735 |  | 2015-07-27 | 2015-07-27 14:28 | 2015-07-27 14:28 | AMERICAN STANDARD - 7A0036A100A1 | 88 | 0 | Yes | Yes | 23.1 | 20.4 | 2.7 | 6282FE5752FA4DB8A70D23DF8A111ABE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7014 |  | 2015-07-17 | 2015-07-17 10:23 | 2015-07-17 10:23 | WEATHER KING - 13PJA18A01 | 81 | 0 | Yes | Yes | 18.3 | 19.9 | -1.6 | D37775FE88284C3F929442F712811380 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-5508 |  | 2015-09-11 | 2015-09-11 12:43 | 2015-09-11 12:43 | CARRIER - 38CKC02434 | 85 | 0 | Yes | Yes | 17.6 | 17.2 | 0.4 | 7CDC87E123974BB7BABBD481322D2777 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7615 |  | 2015-08-24 | 2015-08-24 16:06 | 2015-08-24 16:06 | DAY & NIGHT - N2A336AKB200 | 85 | 0 | Yes | Yes | 19.3 | 19.9 | -0.6 | C4E3E6332D1549EF83CFBFCD7842D368 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9349 |  | 2015-07-28 | 2015-07-28 14:30 | 2015-07-28 14:55 | TRANE - TTNO36C100B3 | 117 | 11 | Yes | Yes | 21.4 | 22 | -0.6 | 0B24E3D1393642DBB89F92F9795374CA |  | R22 | Non-TXV |  | 9.402% | 0.90598 | 18.07% | [5 empty] | Non-TXV | 9.402%
Fairfield | CA | 94533-1257 |  | 2015-07-07 | 2015-07-07 15:12 | 2015-07-07 15:12 | UNITARY PRODUCTS GROUP - DRHSO421CD | 113 | 0 | Yes | Yes | 16.6 | 19.3 | -2.7 | DDF71566C220425180E93278811455D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3745 |  | 2015-07-31 | 2015-07-31 13:22 | 2015-07-31 13:22 | LENNOX - XC13-036-230-03 | 89 | 0 | Yes | Yes | 28.2 | 19.3 | 8.9 | 058254ECB4D24FFC9C3E5B6D6D5429F2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5726 |  | 2015-10-19 | 2015-10-19 10:45 | 2015-10-19 10:45 | RHEEM - 13AJN36A01 | 96 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | A5AEBA9025994FD7976F734FEF227852 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7866 |  | 2015-09-26 | 2015-09-26 15:08 | 2015-09-26 15:08 | - AC1CN030-A | 85 | 0 | Yes | Yes | 20.5 | 19.8 | 0.7 | FA49AC753F8541A6801C508E7B67FB90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7760 |  | 2015-08-04 | 2015-08-04 12:11 | 2015-08-04 12:11 | YORK - H2RA030S06A | 62 | 0 | Yes | Yes | 17.1 | 19.4 | -2.3 | 382FA642EE074106BE1FE779AE96479A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5719 |  | 2015-09-03 | 2015-09-03 13:43 | 2015-09-03 13:43 | OTHER - PA10JA036000ACAA | 74 | 0 | Yes | Yes | 18.7 | 18.5 | 0.2 | 7B5C783750C14FA1A674868063F164D1 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-9109 |  | 2015-10-29 | 2015-10-29 15:01 | 2015-10-29 15:01 | CARRIER - 38CKC042310 | 84 | 0 | Yes | Yes | 19.8 | 18.7 | 1.1 | 63F9FEE05D354E95823B893E50250DB0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-4103 |  | 2015-06-29 | 2015-06-29 09:45 | 2015-06-29 10:08 | PAYNE - 565BJO18 | 50 | 11.4 | Yes | Yes | 23.7 | 20.4 | 3.3 | BC84036E57B34C6A8A18EFA21E726454 | OK: Verified Refrigerant Charge Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 22.8% | 0.772 | 43.82% | [5 empty] | Non-TXV | 22.8%
Vacaville | CA | 95687-6225 |  | 2015-08-10 | 2015-08-10 10:54 | 2015-08-10 10:54 | RHEEM - URMAA036JK08E | 99 | 0 | Yes | Yes | 16.8 | 19.6 | -2.8 | 4A4EE03703424779976B1A4F4F5F8425 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8253 |  | 2015-10-23 | 2015-10-23 15:20 | 2015-10-23 15:20 | YORK - 38TH036300 | 83 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | EBB40F374051498FAC51B5C5BF3CC630 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2406 |  | 2015-07-28 | 2015-07-28 09:47 | 2015-07-28 09:47 | TRANE - 2TTZ9036B1000AA | 85 | 0 | Yes | Yes | 20 | 20.1 | -0.1 | 847DAEDF1E474D97B0AABA90E7AF5789 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7400 |  | 2015-07-28 | 2015-07-28 15:09 | 2015-07-28 15:09 | TRANE - TTR4048L1000AA | 105 | 0 | Yes | Yes | 20.9 | 20.1 | 0.8 | 505E12D6BEE8415CADEEA72569D28B62 |  | R410A | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4630 |  | 2015-11-13 | 2015-11-13 09:22 | 2015-11-13 09:22 | CARRIER - 38CKC060370 | 131 | 0 | Yes | Yes | 20.9 | 18.1 | 2.8 | 14ABF578AE17446494D426E1EDE536DD |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8380 |  | 2015-09-15 | 2015-09-15 14:10 | 2015-09-15 14:10 | PAYNE - 597CN030 B | 86 | 0 | Yes | Yes | 17.4 | 19.6 | -2.2 | DC4AC0A296654BDC9F9F426F6478CF4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1910 |  | 2015-09-30 | 2015-09-30 13:20 | 2015-09-30 13:20 | CARRIER - 38CK030340 | 68 | 0 | Yes | Yes | 22.4 | 19.9 | 2.5 | 4931EA9D010A4361ABE8AB03A6BC49D0 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-9334 |  | 2015-09-15 | 2015-09-15 11:54 | 2015-09-15 11:54 | OTHER - UNK | 100 | 0 | Yes | Yes | 33.7 | 18.7 | 15 | 047FFC5567004075BE12261BD5EF320E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7627 |  | 2015-09-03 | 2015-09-03 11:29 | 2015-09-03 11:29 | CARRIER - 38CKC048 371 | 100 | 30.6 | Yes | Yes | 14.6 | 19.8 | -5.2 | 4A455B2B20F24CE18F4B9C53EFEF12D6 | Add refrigerant: 30.6 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 30.6% | 0.694 | 58.81% | [5 empty] | Non-TXV | 30.6%
Fairfield | CA | 94533-1459 |  | 2015-09-04 | 2015-09-04 11:11 | 2015-09-04 11:11 | LENNOX - 13ACX04823019 | 124 | 0 | Yes | Yes | 22.8 | 17.2 | 5.6 | C6685E733AAA49ECBD14AA313F893174 |  | R410A | TXV |  | 0% | 1 | 0%
Napa | CA | 94558-5308 |  | 2015-10-05 | 2015-10-05 10:05 | 2015-10-05 10:05 | RUUD - RRN-B030JKO6X | 72 | 0 | Yes | Yes | 16.3 | 19.1 | -2.8 | B0D9714CABDA4F7EA2919C6DFCB8AE14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-5308 |  | 2015-10-05 | 2015-10-05 10:16 | 2015-10-05 10:16 | RUUD - RRN-B030JKO6X | 72 | 0 | Yes | Yes | 23.8 | 20.6 | 3.2 | A761EBCBBACE4A708F3B31385C25DC7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3915 |  | 2015-10-22 | 2015-10-22 12:41 | 2015-10-22 12:41 | DAY & NIGHT - N4A336AKB300 | 81 | 0 | Yes | Yes | 24.4 | 21.9 | 2.5 | EC92F54F3C374D76AF491D2A70CC7BDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5882 |  | 2015-08-04 | 2015-08-04 14:15 | 2015-08-04 14:15 | DAY & NIGHT - 591ANX030000ABAA | 68 | 0 | Yes | Yes | 24.4 | 20.4 | 4 | 47486F54305B41ADA8A5711447995BDD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4631 |  | 2015-08-27 | 2015-08-27 11:12 | 2015-08-27 11:12 | CARRIER - PA10JA024-A | 68 | 0 | Yes | Yes | 25.8 | 19.8 | 6 | 03AC7EFE5AFA4B2BAE47C4E0D2697396 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Richmond | CA | 94803-2749 |  | 2015-07-07 | 2015-07-07 09:30 | 2015-07-07 09:30 | WEATHER KING - 10AJB36A01 | 80 | 0 | Yes | Yes | 19.1 | 18.8 | 0.3 | D14D3E482E6046F5B61392FCE6D6D78D | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-0000 |  | 2015-08-24 | 2015-08-24 15:59 | 2015-08-24 15:59 | COLEMAN - DRCS0421BE | 109 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | 15BC38C14BB74617A66AE1D7DFFD7494 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94596-6403 |  | 2015-08-12 | 2015-08-12 13:38 | 2015-08-12 13:38 | CARRIER - 38TDB048300 | 181 | 0 | Yes | Yes | 20.9 | 21 | 0 | 6770B372B9254CCDA3810CC68706E6B3 |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3910 |  | 2015-07-30 | 2015-07-30 08:32 | 2015-07-30 08:32 | TRANE - TTR036D1000A0 | 79 | 0 | Yes | Yes | 18.2 | 17.8 | 0.4 | 29B683B72D794C13B8D73B03E07B830D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3732 |  | 2015-10-15 | 2015-10-15 11:13 | 2015-10-15 11:13 | PAYNE - PA13NR018-H | 56 | 0 | Yes | Yes | 18.4 | 20.4 | -2 | 90F131E095AC474BA168CD1A981E087D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1144 |  | 2015-06-30 | 2015-06-30 11:17 | 2015-06-30 11:17 | OTHER - CCU10A30A-1 | 60 | 0 | Yes | Yes | 20.2 | 18.1 | 2.1 | 2E2FC86290334DFE93FA9422E771FE3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5165 |  | 2015-10-12 | 2015-10-12 10:54 | 2015-10-12 10:54 | CARRIER - 38CKC042 | 85 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 43B491DE03FF47CB8CF790D93BD5C963 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9398 |  | 2015-10-13 | 2015-10-13 13:13 | 2015-10-13 13:13 | YORK - DE042506A | 99 | 0 | Yes | Yes | 18.3 | 17.8 | 0.5 | ED4EC7BD48BE4AE0BEEDB11F6E2B65EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4269 |  | 2015-09-21 | 2015-09-21 15:50 | 2015-09-21 15:50 | DAY & NIGHT - 591ANX018000AAAA | 85 | 0 | Yes | Yes | 19.7 | 20.9 | -1.2 | 933ACAFC9013461787D935BD4A28A699 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8654 |  | 2015-08-03 | 2015-08-03 13:21 | 2015-08-03 13:21 | LENNOX - 10ACB18 | 68 | 0 | Yes | Yes | 9.7 | 12.2 | -2.5 | A9C272792B7E49F08A532D78B2F4DDFA | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6457 |  | 2015-08-04 | 2015-08-04 09:08 | 2015-08-04 09:08 | PAYNE - PA10JAO24A | 70 | 0 | Yes | Yes | 16.3 | 18 | -1.7 | 8B224FF7811E435DA5942348080AC803 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8916 |  | 2015-08-04 | 2015-08-04 10:00 | 2015-08-04 10:00 | CARRIER - 38BRC036340 | 104 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 34D2C8E0F0F145688F2CDDC852AB95B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8479 |  | 2015-10-21 | 2015-10-21 13:33 | 2015-10-21 13:33 | AMERICAN STANDARD - UNKNOWN | 93 | 0 | Yes | Yes | 22.5 | 20.9 | 1.6 | 37B863F119B749389906B21FA0DDA99C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7330 |  | 2015-07-28 | 2015-07-28 13:29 | 2015-07-28 13:29 | CARRIER - 38EHO30340 | 85 | 0 | Yes | Yes | 19.8 | 19.9 | -0.1 | 46D1EBF47FA44519B064723CE1745387 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7616 |  | 2015-09-19 | 2015-09-19 13:35 | 2015-09-19 13:35 | CARRIER - 08TH024300 | 53 | 0 | Yes | Yes | 19.5 | 19.3 | 0.2 | 4E6377A2C29A427085C8849E1CC01638 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-5618 |  | 2015-08-05 | 2015-08-05 14:26 | 2015-08-05 14:26 | RHEEM - RAHE-036JAS | 91 | 0 | Yes | Yes | 24.7 | 22 | 2.7 | 8F352EEE46DF45A199D74A4B263D6417 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-5618 |  | 2015-08-05 | 2015-08-05 14:47 | 2015-08-05 14:47 | RHEEM - RAHE-023JAS | 64 | 0 | Yes | Yes | 24.1 | 21.5 | 2.6 | 9A6EF1C7F99D42F1AC3A556BE3A76F14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4854 |  | 2015-07-16 | 2015-07-16 10:29 | 2015-07-16 10:29 | CARRIER - 38TH036300 | 84 | 0 | Yes | Yes | 15.3 | 17.6 | -2.3 | 3D51B9D11DA94A0881F6D4423D380A51 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1608 |  | 2015-08-04 | 2015-08-04 09:46 | 2015-08-04 09:46 | TRANE - TTR36D100A0 | 79 | 0 | Yes | Yes | 18.9 | 18.3 | 0.6 | 0AF251EA74994168B63CBA207FAB29AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6314 |  | 2015-09-25 | 2015-09-25 12:05 | 2015-09-25 12:05 | PAYNE - PY3GNAA24040NA | 72 | 0 | Yes | Yes | 26.2 | 20.4 | 5.8 | 4F4730780FA342C592168F7A6A28AF49 |  | R410A | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1758 |  | 2015-09-11 | 2015-09-11 10:38 | 2015-09-11 10:38 | CARRIER - 24ABA336A300 | 84 | 0 | Yes | Yes | 18.9 | 19.9 | -1 | 2E9F7BF21FF34C21876371BD2C44D785 |  | R410A | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1758 |  | 2015-09-11 | 2015-09-11 10:53 | 2015-09-11 10:53 | CARRIER - 24ABA336A300 | 84 | 0 | Yes | Yes | 18.9 | 19.9 | -1 | 6CA34A9883B54DD8A608200FC83532AF |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3301 |  | 2015-10-26 | 2015-10-26 14:23 | 2015-10-26 14:23 | YORK - H1RA042S06D | 84 | 0 | Yes | Yes | 17.5 | 18.7 | -1.2 | 43F397FD341D4EDCA2EB21CB38205EA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5004 |  | 2015-08-12 | 2015-08-12 11:46 | 2015-08-12 11:46 | AMANA - GSX130301BA | 84 | 0 | Yes | Yes | 15.6 | 18.5 | -2.9 | 980B479FC0F1468C89B5FD94FCCAA2C9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95407-2507 |  | 2015-09-22 | 2015-09-22 14:31 | 2015-09-22 14:31 | GOODMAN - CK30-1B | 85 | 0 | Yes | Yes | 15.7 | 18.7 | -3 | 9DC2016E8AD2410AB5632F7FB5B384D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-4147 |  | 2015-08-18 | 2015-08-18 11:10 | 2015-08-18 11:10 | CARRIER - 38CKC042350 | 85 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | BD060ADD4EA24BA5833C857F6D6D343F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2217 |  | 2015-08-21 | 2015-08-21 13:08 | 2015-08-21 13:08 | RHEEM - RAKA048JA | 113 | 0 | Yes | Yes | 17 | 17.4 | -0.4 | 5CF5D899B8D84193A76A42C9AC27C0A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3004 |  | 2015-08-04 | 2015-08-04 14:52 | 2015-08-04 14:52 | OTHER - CA5542VKD2 | 98 | 0 | Yes | Yes | 21.6 | 19.9 | 1.7 | 65DD97C69B47465E8E3FF6BFDF387BC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-7032 |  | 2015-09-03 | 2015-09-03 09:58 | 2015-09-03 09:58 | YORK - H1CB030506C | 78 | 0 | Yes | Yes | 17.8 | 18.2 | -0.4 | 44C95244667040B1903357F749883755 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-7032 |  | 2015-09-03 | 2015-09-03 10:04 | 2015-09-03 10:04 | YORK - H1CB030506C | 78 | 0 | Yes | Yes | 16.7 | 19.4 | -2.7 | 6904F41B0AE149478C66CE157C53EEC8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94597-1806 |  | 2015-09-04 | 2015-09-04 09:41 | 2015-09-04 09:41 | COLEMAN - TCGD30S21S2A | 55 | 0 | Yes | Yes | 23.7 | 19.1 | 4.6 | E87566CEADE3467CB2CDCAE0F75BCB86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6706 |  | 2015-08-17 | 2015-08-17 15:43 | 2015-08-17 15:43 | CARRIER - 24ABA336A310 | 85 | 0 | Yes | Yes | 20 | 18.3 | 1.7 | 3DE9CE57018346AE8A85357DC9F34498 |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3110 |  | 2015-10-08 | 2015-10-08 09:54 | 2015-10-08 09:54 | GOODMAN - CKJ30-1A | 92 | 0 | Yes | Yes | 14.5 | 17.5 | -3 | 8C043B9B069248F7A1099F0A94725F48 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6314 |  | 2015-09-26 | 2015-09-26 09:23 | 2015-09-26 09:23 | GOODMAN - PGB024050-1 | 54 | 0 | Yes | Yes | 17.7 | 17.7 | 0 | 6BB1616560404C8C9986B38DC0E9575D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4555 |  | 2015-08-24 | 2015-08-24 13:59 | 2015-08-24 13:59 | OTHER - CA5024VKB1 | 67 | 0 | Yes | Yes | 18.2 | 18.1 | 0.1 | 55234897808045E2B252CF9678DC0034 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2163 |  | 2015-09-03 | 2015-09-03 11:59 | 2015-09-03 11:59 | AMERICAN STANDARD - 2A7B00361000AA | 76 | 0 | Yes | Yes | 22.9 | 19.9 | 3 | EDC9122D35504060A534A25D8D7ABE3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8521 |  | 2015-09-15 | 2015-09-15 16:04 | 2015-09-15 16:04 | OTHER - PA10JA042 C | 81 | 0 | Yes | Yes | 21 | 22.5 | -1.5 | 9223091A221E4A79863500AED967784C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95407-7628 |  | 2015-08-20 | 2015-08-20 10:46 | 2015-08-20 11:06 | ICP - NXA636GKA100 | 85 | 10.7 | Yes | Yes | 16.4 | 18.7 | -2.3 | 10697C7BFE134DCE82D4BB2B734F28DD |  | R410A | TXV |  | 12.59% | 0.87412 | 24.19% | [5 empty] | TXV | 12.59%
Clayton | CA | 94517-1702 |  | 2015-08-28 | 2015-08-28 09:53 | 2015-08-28 09:53 | CARRIER - 38BRC060340 | 201 | 0 | Yes | Yes | 18.3 | 19.1 | -0.8 | 1B9D951F08FF4C1895881E5F64888A58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5102 |  | 2015-10-21 | 2015-10-21 10:41 | 2015-10-21 10:41 | GOODMAN - CX24-1B | 71 | 0 | Yes | Yes | 24 | 19.9 | 4.1 | 1544F0DFC4754F00AE47CA5450CF14B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2600 |  | 2015-08-26 | 2015-08-26 17:20 | 2015-08-26 17:20 | CARRIER - 38CKC042310 | 81 | 0 | Yes | Yes | 15.5 | 18.5 | -3 | 331F5B9BCC4D45CDABBC03DC71E1C0E1 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7332 |  | 2015-08-21 | 2015-08-21 11:59 | 2015-08-21 11:59 | CARRIER - 38TH030300 | 65 | 0 | Yes | Yes | 18.5 | 21 | -2.5 | 99C8128170154CF2AF91CB96FB7D34C4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2315 |  | 2015-07-17 | 2015-07-17 11:21 | 2015-07-17 11:21 | AMERICAN STANDARD - 2A7A1030A1000AA | 85 | 0 | Yes | Yes | 20.5 | 19.6 | 0.9 | 5C67BAAB20CD47F39CC1B334468E0CE8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9375 |  | 2015-10-19 | 2015-10-19 11:05 | 2015-10-19 11:05 | GOODMAN - GSC130301EA | 82 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | CBBFD8CC840742729878BB8C3A441441 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1037 |  | 2015-07-02 | 2015-07-02 13:31 | 2015-07-02 13:31 | GUARDIAN - GCG036S21S2A | 63 | 0 | Yes | Yes | 24.5 | 21 | 3.5 | 7E92617EF13641B09931E59722D712D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3039 |  | 2015-07-20 | 2015-07-20 16:12 | 2015-07-20 16:12 | YORK - H1DE036506C | 84 | 0 | Yes | Yes | 19.4 | 22.3 | -2.9 | 0DC415EA4AD146B0A25D7642ADD4E1DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4709 |  | 2015-10-09 | 2015-10-09 14:29 | 2015-10-09 14:29 | OTHER - 13AJAA42A01 | 129 | 0 | Yes | Yes | 20.1 | 21.3 | -1.2 | 6D1AD1DC37A14002917CBAF05F10B8E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2180 |  | 2015-10-14 | 2015-10-14 09:31 | 2015-10-14 09:31 | PAYNE - 588ANW036060ABAF | 67 | 0 | Yes | Yes | 18.8 | 21.5 | -2.7 | 2C99281025214D12AC4ABF649CC58166 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3731 |  | 2015-11-04 | 2015-11-04 13:34 | 2015-11-04 13:34 | AMERICAN STANDARD - 2A7A1024A1000AA | 62 | 0 | Yes | Yes | 24.1 | 21.5 | 2.6 | 20EAF7BFD26740708AF2A5B6A39FFE9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-9421 |  | 2015-09-03 | 2015-09-03 10:30 | 2015-09-03 10:30 | RHEEM - N/A | 85 | 0 | Yes | Yes | 19.8 | 19.6 | 0.2 | DC6B8AEA4AD247A0A957F9FE2D00FAA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-1249 |  | 2015-08-07 | 2015-08-07 12:17 | 2015-08-07 12:17 | OTHER - 38EH024300DL | 86 | 0 | Yes | Yes | 17.1 | 16.9 | 0.2 | 103BA5C1007B4B69BD22787448ABB059 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2856 |  | 2015-08-18 | 2015-08-18 15:57 | 2015-08-18 15:57 | DAY & NIGHT - 561AJ042A | 93 | 0 | Yes | Yes | 25.6 | 19.9 | 5.7 | 965CD233184C42AA99F2E9FD267C83BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5062 |  | 2015-11-18 | 2015-11-18 10:02 | 2015-11-18 10:02 | CARRIER - 24ACR336A330 | 106 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | 55C66EA166D6403FB00200E270D744AC |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5362 |  | 2015-10-19 | 2015-10-19 11:40 | 2015-10-19 11:40 | GOODMAN - CM36-1EB | 85 | 0 | Yes | Yes | 23.3 | 21.8 | 1.5 | AB1F6A1125B64AA58B67BE143EB89499 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3522 |  | 2015-08-07 | 2015-08-07 11:48 | 2015-08-07 11:48 | PAYNE - 42RAC1S8KC | 85 | 0 | Yes | Yes | 24.1 | 19.3 | 4.8 | FA5E43473C3C406881847D6802B27FA0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3227 |  | 2015-10-15 | 2015-10-15 14:49 | 2015-10-15 14:49 | PAYNE - PA13NR024-E | 85 | 0 | Yes | Yes | 18.6 | 21 | -2.4 | 1C58BC71AB8C49C4AC17A97D3A2753DC |  | R22 | TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1417 |  | 2015-08-05 | 2015-08-05 13:58 | 2015-08-05 13:58 | CARRIER - 38CKC048360 | 85 | 0 | Yes | Yes | 14.1 | 16.9 | -2.8 | 9EDAF939CC584F269879164D1C18B6B9 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2367 |  | 2015-09-09 | 2015-09-09 11:59 | 2015-09-09 11:59 | CARRIER - 38TDA048 | 168 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | B5ECD1B8B837494EA7E889DAFA0B1AFF |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4607 |  | 2015-08-10 | 2015-08-10 18:31 | 2015-08-10 18:31 | - WCA3482GKA1 | 85 | 0 | Yes | Yes | 20 | 22.1 | -2.1 | A8D47E4972074BFDB158940B5FEF2A31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4919 |  | 2015-09-24 | 2015-09-24 09:34 | 2015-09-24 09:34 | OTHER - CA5548VKC1 | 113 | 0 | Yes | Yes | 20.9 | 22.9 | -2 | 3134CA290C78412EB379741E3FC52113 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6831 |  | 2015-09-09 | 2015-09-09 14:37 | 2015-09-09 14:37 | GOODMAN - CK24 1D | 65 | 0 | Yes | Yes | 24.1 | 19.3 | 4.8 | E90921C7F2F24A16861726961378413E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5745 |  | 2015-08-10 | 2015-08-10 12:35 | 2015-08-10 12:35 | DAY & NIGHT - N4A336AKB300 | 85 | 0 | Yes | Yes | 23.4 | 20.2 | 3.2 | FDEFD54FEAFE4266AAB60ACD004156E3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5802 |  | 2015-09-04 | 2015-09-04 09:15 | 2015-09-04 09:15 | YORK - H1DB036S06B | 72 | 0 | Yes | Yes | 22.3 | 19.7 | 2.6 | 06E854A9D9754CEF92E41CD7F65EFE86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1558 |  | 2015-06-24 | 2015-06-24 15:24 | 2015-06-24 15:24 | RHEEM - RAKA-030JAZ | 66 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | 80C6AC33E47E493EB546D5583065A8B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3163 |  | 2015-09-04 | 2015-09-04 11:45 | 2015-09-04 11:45 | YORK - H1RA018S06D | 54 | 0 | Yes | Yes | 24.9 | 19.3 | 5.6 | 2B96F556E84B4FCFAAD7978DB7EFF5BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2482 |  | 2015-10-28 | 2015-10-28 10:43 | 2015-10-28 10:43 | YORK - AC048X1021A | 117 | 0 | Yes | Yes | 17.9 | 20.8 | -2.9 | 3F3E6D9D7FA845FFB49C99FA3627895A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4356 |  | 2015-07-13 | 2015-07-13 14:04 | 2015-07-13 14:35 | OTHER - 565BU030 | 85 | 22.6 | Yes | Yes | 22.6 | 17.9 | 4.7 | 11F8559A838344FAA3A224A47446D546 |  | R22 | Non-TXV |  | 26.59% | 0.73412 | 51.1% | [5 empty] | Non-TXV | 26.59%
Pittsburg | CA | 94565-3799 |  | 2015-09-03 | 2015-09-03 10:37 | 2015-09-03 10:37 | CARRIER - 38CKC042 351 | 81 | 0 | Yes | Yes | 20.6 | 19.5 | 1.1 | 4961AC089F884B2CA7A2003F4ADDD5B9 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2214 |  | 2015-10-16 | 2015-10-16 13:37 | 2015-10-16 13:37 | CARRIER - 38BRC030320 | 100 | 0 | Yes | Yes | 25.8 | 23.7 | 2.1 | A1399FFA6B3A4FDAB999F3B0D39C0D73 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-2537 |  | 2015-07-29 | 2015-07-29 13:04 | 2015-07-29 13:04 | COMFORT AIRE - CA556OVKD2 | 150 | 0 | Yes | Yes | 26.1 | 20.4 | 5.7 | C5B6E8CF055D4FC08427E5644341C842 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3924 |  | 2015-08-28 | 2015-08-28 11:36 | 2015-08-28 11:36 | COLEMAN - TCD48S4 | 73 | 0 | Yes | Yes | 15.8 | 15.7 | 0.1 | B6E154C5A50143B88E70CF333A226E59 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-1926 |  | 2015-07-09 | 2015-07-09 11:19 | 2015-07-09 11:19 | OTHER - NRGE24SAK02 | 49 | 0 | Yes | Yes | 18.3 | 17.7 | 0.6 | 4E0398C429E84D6683D03D1B71E6ABA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2352 |  | 2015-10-30 | 2015-10-30 10:52 | 2015-10-30 10:52 | CARRIER - UNK | 85 | 0 | Yes | Yes | 17.5 | 19.7 | -2.2 | 83837BFA71B9462A888711C6FC315769 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-4636 |  | 2015-10-05 | 2015-10-05 11:47 | 2015-10-05 11:47 | OTHER - TZAA-330-2A | 98 | 0 | Yes | Yes | 15 | 16.7 | -1.7 | 6EA685C51C6E47C6B86E3D783D954CF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-1746 |  | 2015-07-27 | 2015-07-27 11:49 | 2015-07-27 11:49 | AMERICAN STANDARD - PA13NR048-E | 181 | 0 | Yes | Yes | 22.2 | 20.4 | 1.8 | 30A73567326A43CD87FE732CE3DA02C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-1544 |  | 2015-07-29 | 2015-07-29 15:13 | 2015-07-29 15:13 | GOODMAN - GSC140421AD | 174 | 0 | Yes | Yes | 18.5 | 19.3 | -0.8 | CA3ADFF950CE47F284C137F44B6395E2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2048 |  | 2015-09-03 | 2015-09-03 13:03 | 2015-09-03 13:03 | LENNOX - HS29-024-1P | 62 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | A54196B9ED3944D0A6CA2598E304404A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1777 |  | 2015-09-03 | 2015-09-03 15:51 | 2015-09-03 15:51 | OTHER - TZAA-360-2A757 | 130 | 0 | Yes | Yes | 22.2 | 20.8 | 1.4 | DACB74DB53A44999A688A1A8C05C25FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2615 |  | 2015-10-15 | 2015-10-15 12:40 | 2015-10-15 12:40 | RHEEM - AT-42B10 | 115 | 0 | Yes | Yes | 15 | 16.2 | -1.2 | 33EF29B0CB164A758296645C3C629100 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3022 |  | 2015-11-05 | 2015-11-05 16:13 | 2015-11-05 16:13 | GE - BTR736 | 88 | 0 | Yes | Yes | 19 | 20 | -1 | FD77102DE98941E0A359C1C8EFBE9C13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3944 |  | 2015-07-31 | 2015-07-31 15:11 | 2015-07-31 15:11 | BRYANT - 588ANW036080 | 85 | 0 | Yes | Yes | 26.2 | 20.4 | 5.8 | 5469BA6982AF4785B0273ADFF2D95A52 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3429 |  | 2015-08-17 | 2015-08-17 10:22 | 2015-08-17 10:22 | CARRIER - 38CKB060300 | 152 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | 13BA3080F5864343999706896161DCE1 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4624 |  | 2015-09-15 | 2015-09-15 13:45 | 2015-09-15 13:45 | CARRIER - PA10JA36 | 72 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | 82AEE276C2104C409F0645FFBB186A51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5475 |  | 2015-07-24 | 2015-07-24 10:19 | 2015-07-24 10:19 | TRANE - BTD724A100C0 | 68 | 0 | Yes | Yes | 24.8 | 19.7 | 5.1 | ECC1B17A6E474D13AA0974F143B9D71D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2151 |  | 2015-08-03 | 2015-08-03 09:11 | 2015-08-03 09:26 | YORK - H2RA0366063 | 63 | 9.5 | Yes | Yes | 12.7 | 15.7 | -3 | D88D28A2875D4AE081D5F88E99405073 |  | R22 | Non-TXV |  | 15.08% | 0.84921 | 28.98% | [5 empty] | Non-TXV | 15.08%
Vacaville | CA | 95687-7018 |  | 2015-07-20 | 2015-07-20 10:17 | 2015-07-20 10:17 | TRANE - BWD718A199B0 | 85 | 0 | Yes | Yes | 15.7 | 18.7 | -3 | E8ED1ACB31F54B54B15B1812DB5D07F9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3164 |  | 2015-09-03 | 2015-09-03 14:06 | 2015-09-03 14:06 | YORK - HR018S06D | 54 | 0 | Yes | Yes | 17.5 | 19.1 | -1.6 | E9B2FEFEE8394001961CF2884150A6B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3164 |  | 2015-08-27 | 2015-08-27 16:10 | 2015-08-27 16:10 | CARRIER - 541DN018 | 85 | 0 | Yes | Yes | 14.5 | 16.6 | -2.1 | E7B20370BF354FD5B4A73920C68AB841 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3946 |  | 2015-09-01 | 2015-09-01 14:27 | 2015-09-01 14:27 | TRANE - 2TTR1036A | 73 | 0 | Yes | Yes | 21.6 | 19.5 | 2.1 | 8922EB9982514AFFA3BE6DF2C864AC91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2405 |  | 2015-09-15 | 2015-09-15 15:09 | 2015-09-15 15:09 | RHEEM - UNKNOWN | 51 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | D30997BEEAB24A31956B5EE977DB7046 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-1710 |  | 2015-07-27 | 2015-07-27 17:08 | 2015-07-27 17:08 | PAYNE - PA1CJA036-C | 78 | 0 | Yes | Yes | 15.3 | 17.7 | -2.4 | 73CAEBC96A4D4858A1355E64E8CD03C1 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1231 |  | 2015-08-03 | 2015-08-03 12:05 | 2015-08-03 12:05 | TRANE - 4TTB3030D1000AA | 85 | 0 | Yes | Yes | 20.8 | 19.3 | 1.5 | DF83099D016D489884348517A0F2CC3C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3772 |  | 2015-09-15 | 2015-09-15 12:28 | 2015-09-15 12:28 | OTHER - CA5548VKD | 134 | 0 | Yes | Yes | 16.8 | 19.6 | -2.8 | 0FA4B55F54FB4CC7AA0D97C11397647B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2937 |  | 2015-07-06 | 2015-07-06 09:42 | 2015-07-06 09:42 | DAY & NIGHT - 591ANX036000AAAA | 117 | 0 | Yes | Yes | 15.8 | 18.2 | -2.4 | 505E5337944F445597F2F103572B5D34 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2715 |  | 2015-10-06 | 2015-10-06 13:20 | 2015-10-06 13:20 | OTHER - SA 36G0806P | 53 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | BF847F924FA341A78CB38A4F98F103DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1306 |  | 2015-09-15 | 2015-09-15 12:38 | 2015-09-15 12:38 | PAYNE - 597BN042-A | 85 | 0 | Yes | Yes | 25.9 | 20.1 | 5.8 | 1077F5217113427A922B063DEB98FB2A |  | R22 | TXV |  | 0% | 1 | 0%
Davis | CA | 95618-5493 |  | 2015-10-06 | 2015-10-06 14:29 | 2015-10-06 14:29 | LENNOX - 14ACX0242316 | 92 | 0 | Yes | Yes | 20.5 | 17.8 | 2.8 | 5BEF92D575B141A1A39EBCDAE0C68792 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3708 |  | 2015-08-11 | 2015-08-11 15:08 | 2015-08-11 15:08 | PAYNE - PA13NR024-C | 85 | 0 | Yes | Yes | 20.5 | 18.3 | 2.2 | 1B4C78D73C9348DA85A43E4A32E17619 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3160 |  | 2015-09-02 | 2015-09-02 13:44 | 2015-09-02 13:44 | YORK - H1RA018S06 | 54 | 0 | Yes | Yes | 23 | 17.5 | 5.5 | F3AE5C6FE577461FA38DE3C396F66092 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1775 |  | 2015-09-11 | 2015-09-11 14:24 | 2015-09-11 14:24 | CARRIER - 24AB A348A300 | 127 | 0 | Yes | Yes | 26.1 | 23 | 3.1 | 1EA964DD58A84736A8F062C55B423CC3 |  | R410A | TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3918 |  | 2015-08-13 | 2015-08-13 13:46 | 2015-08-13 13:46 | COLEMAN - 2442-901 | 85 | 0 | Yes | Yes | 18.5 | 17.1 | 1.4 | 45F1553FA9D54EC0B81EB0BB98FF343B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4030 |  | 2015-08-21 | 2015-08-21 09:58 | 2015-08-21 09:58 | CARRIER - 561CJ036-C | 72 | 0 | Yes | Yes | 18.2 | 17.5 | 0.7 | 829A025C4DD744809C550B39CFD48626 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4346 |  | 2015-09-25 | 2015-09-25 09:29 | 2015-09-25 09:29 | GOODMAN - CLJ301 | 86 | 0 | Yes | Yes | 17.9 | 19.9 | -2 | FCB2F79D3AD642458F65700592CF7A26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4390 |  | 2015-10-26 | 2015-10-26 15:34 | 2015-10-26 15:34 | OTHER - E020AV | 86.57 | 0 | Yes | Yes | 19 | 18.6 | 0.4 | 356AFC85CD4B4CEA886612FB5FA869A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-1829 |  | 2015-11-10 | 2015-11-10 12:03 | 2015-11-10 12:03 | COLEMAN - BRCQ0361BD | 52 | 0 | Yes | Yes | 18.4 | 18.6 | -0.2 | 2A51D82845F9499684D9C950808A9E47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Richmond | CA | 94803-3849 |  | 2015-07-07 | 2015-07-07 14:16 | 2015-07-07 14:16 | OTHER - TTD736100A | 80 | 0 | Yes | Yes | 19.7 | 19 | 0.7 | DE78A1675EE04210AD3B72CD0212A1F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-9324 |  | 2015-09-21 | 2015-09-21 16:03 | 2015-09-21 16:36 | CARRIER - 48NLT036320 | 87 | 17.2 | Yes | Yes | 21.7 | 23.4 | -1.7 | 65DB705BC8344F488B5EB8D93121336E |  | R22 | Non-TXV |  | 19.77% | 0.8023 | 37.99% | [5 empty] | Non-TXV | 19.77%
Woodland | CA | 95695-3919 |  | 2015-10-07 | 2015-10-07 15:00 | 2015-10-07 15:00 | PAYNE - PA13NA030-B | 85 | 0 | Yes | Yes | 13.5 | 16.4 | -2.9 | 4EB5B8BC4B594CB89F359887E2161448 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2726 |  | 2015-08-06 | 2015-08-06 14:22 | 2015-08-06 14:49 | CARRIER - 38BR036300 | 114 | -10.7 | Yes | Yes | 15.6 | 16.6 | -1 | 983E9D5B89674DCCB5C7605A1766974D |  | R22 | Non-TXV |  | -9.386% | 1.0939 | 2.629% |  |  |  |  | Non-TXV |  |  | -9.386%
Fairfield | CA | 94533-4089 |  | 2015-08-25 | 2015-08-25 15:34 | 2015-08-25 15:34 | CARRIER - 561CJ018C | 68 | 0 | Yes | Yes | 18 | 20.6 | -2.6 | D1265C403D334EF19106A403E23A208D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-4542 |  | 2015-08-04 | 2015-08-04 09:59 | 2015-08-04 10:15 | RHEEM - RPBC-018JAS | 55 | 3.3 | Yes | Yes | 23 | 22.4 | 0.6 | D31611AD5D6147549D22B8204DBBF33D |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Antioch | CA | 94509-2410 |  | 2015-08-11 | 2015-08-11 11:57 | 2015-08-11 11:57 | CARRIER - H1RD036S06G | 145 | 0 | Yes | Yes | 25.4 | 19.9 | 5.5 | 28CA5060DF8D4A2ABCD5413090346FCD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2423 |  | 2015-07-27 | 2015-07-27 14:24 | 2015-07-27 14:24 | CARRIER - 38TKB036330 | 85 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 60268D3A812E4AE6A091631B3480183C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4083 |  | 2015-09-02 | 2015-09-02 11:37 | 2015-09-02 11:37 | BRYANT - 561CJ024D | 55 | 0 | Yes | Yes | 18.5 | 19.4 | -0.9 | 26477D215EDE4064AF56549BFE9ABBE0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2050 |  | 2015-10-12 | 2015-10-12 15:52 | 2015-10-12 15:52 | BRYANT - UNK | 85 | 0 | Yes | Yes | 23.2 | 22.1 | 1.1 | 6B38E02CD32241BFB0237D16CEEB9F20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4831 |  | 2015-09-04 | 2015-09-04 12:37 | 2015-09-04 12:37 | OTHER - SCU10E48-3 | 98 | 0 | Yes | Yes | 24 | 19.4 | 4.6 | 7940494266C14D57855E7130B0D47EA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1853 |  | 2015-08-07 | 2015-08-07 10:01 | 2015-08-07 10:01 | AMANA - RCC42A2B | 116 | 0 | Yes | Yes | 19.5 | 16.4 | 3.1 | FB7D1F1F59CA4BB1A27B4288562673AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5516 |  | 2015-08-06 | 2015-08-06 15:57 | 2015-08-06 15:57 | BARD - PA13NR036-H | 85 | 0 | Yes | Yes | 23.4 | 19.5 | 3.9 | 3BC7FBC32F02429AB0C142DFE4BA871F |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5011 |  | 2015-08-12 | 2015-08-12 09:30 | 2015-08-12 09:30 | - NCAFB36AB01 | 85 | 0 | Yes | Yes | 22.8 | 19.9 | 2.9 | F53E3D23C02A491193AABB01E2E67CAF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2609 |  | 2015-08-07 | 2015-08-07 14:01 | 2015-08-07 14:32 | CARRIER - 38TH036300 | 85 | 19.4 | Yes | Yes | 19.3 | 19.7 | -0.4 | 49F439EA0DC943E9B8B37500A9BF4192 |  | R22 | Non-TXV |  | 22.82% | 0.77176 | 43.86% | [5 empty] | Non-TXV | 22.82%
Woodland | CA | 95695-4016 |  | 2015-10-16 | 2015-10-16 13:45 | 2015-10-16 13:45 | GOODMAN - CK42C1 | 92 | 0 | Yes | Yes | 19.9 | 20.9 | -1 | E7D6A36DE35C4A36B5CAFFCEB17C0D62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7200 |  | 2015-09-04 | 2015-09-04 10:48 | 2015-09-04 10:48 | OTHER - 4AC13L36P-7A | 68 | 0 | Yes | Yes | 19 | 20.1 | -1.1 | 1AD2375ACCE6404E9E6DE15912ACE0D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5643 |  | 2015-09-04 | 2015-09-04 14:47 | 2015-09-04 14:47 | TRANE - TTN036C10062 | 117 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | DADBB96D164E4F58A1869D35A8EE8EC3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7348 |  | 2015-11-17 | 2015-11-17 11:01 | 2015-11-17 11:01 | GOODMAN - UNK | 85 | 0 | Yes | Yes | 21.9 | 18.3 | 3.6 | F921733B4222453DAF95C679499287FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1859 |  | 2015-08-12 | 2015-08-12 11:40 | 2015-08-12 11:40 | TRANE - 4TTX4030B1000AA | 85 | 0 | Yes | Yes | 19.9 | 18.8 | 1.1 | D9153AB357DC4CEFAB39452B12C876CB |  | R410A | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1972 |  | 2015-10-09 | 2015-10-09 13:26 | 2015-10-09 13:26 | BRYANT - 113RNA024B | 70 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | 22F3FA71AD0B4234941AD536CEF0D254 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3827 |  | 2015-10-14 | 2015-10-14 12:43 | 2015-10-14 12:43 | CARRIER - 24ABA348A300 | 122 | 0 | Yes | Yes | 21.9 | 22.4 | -0.5 | F5C8C71C837B4D8EB80D573EC035E1B4 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4504 |  | 2015-08-12 | 2015-08-12 12:47 | 2015-08-12 12:47 | CARRIER - 113ANA048-1 | 85 | 0 | Yes | Yes | 21.5 | 18.5 | 3 | E646AC3D0A76434BAB748764C999C7EE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94597-6824 |  | 2015-08-10 | 2015-08-10 15:15 | 2015-08-10 15:15 | OTHER - 703458 | 56 | 0 | Yes | Yes | 22.5 | 20.6 | 1.9 | A7415EAB81B940AABA35532EBD15484A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1978 |  | 2015-10-12 | 2015-10-12 09:52 | 2015-10-12 09:52 | BRYANT - 1130NA024 | 71 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | D112AB4D53B548C4AB17A8E5EEF17353 |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1978 |  | 2015-10-12 | 2015-10-12 10:04 | 2015-10-12 10:04 | BRYANT - 113RNA024C | 71 | 0 | Yes | Yes | 17.7 | 19.9 | -2.2 | 348B74A09AD14FEA8D2600404364CA2C |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1960 |  | 2015-10-13 | 2015-10-13 15:47 | 2015-10-13 15:47 | BRYANT - UNK | 75 | 0 | Yes | Yes | 23.9 | 21 | 2.9 | 9FBCBFA487E24F40AD8D69A403162466 |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1965 |  | 2015-10-28 | 2015-10-28 09:19 | 2015-10-28 09:19 | BRYANT - 113RNA030-E | 84 | 0 | Yes | Yes | 17.9 | 18.7 | -0.8 | 8E9E242CFB494BD1AFC8D404A12DFC6B |  | R22 | TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1296 |  | 2015-08-04 | 2015-08-04 11:39 | 2015-08-04 12:04 | UNITARY PRODUCTS GROUP - H2RC024S06A | 71 | 7.4 | Yes | Yes | 14.9 | 17.7 | -2.8 | A602160EFD404533AE13B6EFFE124EAC |  | R22 | TXV |  | 10.42% | 0.89577 | 20.03% | [5 empty] | TXV | 10.42%
Suisun City | CA | 94585-1978 |  | 2015-10-12 | 2015-10-12 09:37 | 2015-10-12 09:37 | BRYANT - 113RNA024B | 71 | 0 | Yes | Yes | 18.5 | 20.9 | -2.4 | CDC24A61CFD54A949070D644A7D6CDB3 |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3053 |  | 2015-09-29 | 2015-09-29 14:04 | 2015-09-29 14:26 | COLEMAN - TCGD36S21S2A | 63 | 5 | Yes | Yes | 24.8 | 20.4 | 4.4 | 10BA20037CBD4FE7A727A8637A3DA89F |  | R22 | TXV |  | 7.937% | 0.92063 | 15.25% | [5 empty] | TXV | 7.937%
Vacaville | CA | 95687-4059 |  | 2015-07-17 | 2015-07-17 14:41 | 2015-07-17 14:41 | UNITARY PRODUCTS GROUP - BRCQ0361BD | 52 | 0 | Yes | Yes | 26.8 | 21.5 | 5.3 | 913F631075D74B60801C2B323E0B3C17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6506 |  | 2015-08-14 | 2015-08-14 13:54 | 2015-08-14 13:54 | PAYNE - PA10JA036C | 76 | 0 | Yes | Yes | 22.5 | 20.6 | 1.9 | 7265563DAD644C6CA887F4E810F5381D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-3343 |  | 2015-08-25 | 2015-08-25 13:01 | 2015-08-25 13:01 | RHEEM - 13PJL2401 | 91 | 0 | Yes | Yes | 17.6 | 18.7 | -1.1 | 1D5D041A6E6C4947A84A65AD2448796A |  | R410A | TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3922 |  | 2015-09-01 | 2015-09-01 11:20 | 2015-09-01 11:20 | COLEMAN - BRCS042C | 85 | 0 | Yes | Yes | 13.3 | 15.7 | -2.4 | D831785476C04AF19F8D6AEADA784339 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-1674 |  | 2015-09-23 | 2015-09-23 16:02 | 2015-09-23 16:02 | - BRCS0421BD | 84 | 0 | Yes | Yes | 19 | 17.9 | 1.1 | A8129D3A9E5B4EB7A1C8DB1ED7862F37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-7024 |  | 2015-08-25 | 2015-08-25 10:39 | 2015-08-25 10:39 | LENNOX - 12ACB60-4P | 173 | 0 | Yes | Yes | 21.8 | 19 | 2.8 | C4A5483BA93243778F68E90AF905C7F0 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3310 |  | 2015-07-17 | 2015-07-17 07:59 | 2015-07-17 07:59 | CARRIER - 38CKC824 | 85 | -8 | Yes | Yes | 19.9 | 19.9 | 0 | B7287A9D7EFA437BBD6DE427DA0997F5 | Remove refrigerant: 8 oz | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Antioch | CA | 94531-9406 |  | 2015-07-16 | 2015-07-16 15:45 | 2015-07-16 16:07 | CARRIER - 38CKC048360 | 109 | 7.3 | Yes | Yes | 18 | 18.8 | -0.8 | 977E6AD8A1CE460D929679A7A2FE5F6F |  | R22 | TXV |  | 6.697% | 0.93303 | 12.87% | [5 empty] | TXV | 6.697%
Martinez | CA | 94553-5347 |  | 2015-08-05 | 2015-08-05 13:13 | 2015-08-05 13:30 | CARRIER - 38CKC036350 | 70 | 11.4 | Yes | Yes | 15.6 | 18.3 | -2.7 | C47E01B2671B476AABDA1D4E459BC7FD |  | R22 | Non-TXV |  | 16.29% | 0.83714 | 31.3% | [5 empty] | Non-TXV | 16.29%
Antioch | CA | 94531-9312 |  | 2015-10-20 | 2015-10-20 11:39 | 2015-10-20 11:39 | OTHER - UNKNOWN | 87 | 0 | Yes | Yes | 21.7 | 22.2 | -0.4 | D30104E4D5DF435D9E47CDC10F9ADB56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7322 |  | 2015-09-11 | 2015-09-11 09:39 | 2015-09-11 09:39 | CARRIER - 561AJ048-C | 105 | 0 | Yes | Yes | 22.9 | 21.2 | 1.7 | 76F699A99593417BB23F3310832CD869 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3344 |  | 2015-09-28 | 2015-09-28 13:46 | 2015-09-28 13:46 | AMERICAN STANDARD - 4A7A6036C1008A | 106 | 0 | Yes | Yes | 18.6 | 19.4 | -0.8 | 0F228AAAB6B946359954C84B90387FA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7208 |  | 2015-07-31 | 2015-07-31 16:28 | 2015-07-31 16:28 | CARRIER - 563CH060 | 85 | 0 | Yes | Yes | 21.5 | 17.1 | 4.5 | CC4F3968226B4211A63F9A78E4A2B8AF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6472 |  | 2015-09-12 | 2015-09-12 09:33 | 2015-09-12 09:33 | YORK - H1RA048S06D | 117 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | 6698329FB1064DD7B53409A677B4BF06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2604 |  | 2015-08-07 | 2015-08-07 13:33 | 2015-08-07 13:33 | SEARS - UNK | 85 | 0 | Yes | Yes | 21.9 | 18.8 | 3.1 | 942F6E57158A4931BF28FF8CF71C135A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2752 |  | 2015-09-14 | 2015-09-14 15:54 | 2015-09-14 15:54 | CARRIER - 588ANW048080AEBG | 85 | 0 | Yes | Yes | 22.8 | 17.9 | 4.9 | 546B0113408A486BA8EC0E561BC79326 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-5356 |  | 2015-09-21 | 2015-09-21 13:14 | 2015-09-21 13:14 | GOODMAN - 541DJ024 | 118 | 0 | Yes | Yes | 17.1 | 19.3 | -2.2 | 19A960787E5E431F88305D2CB3133F98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9300 |  | 2015-08-12 | 2015-08-12 08:49 | 2015-08-12 08:49 | OTHER - 2AC13L60O-1A | 234 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | 8BB9EDE7B70A4A8D889115B5DE1ED581 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4286 |  | 2015-07-20 | 2015-07-20 14:44 | 2015-07-20 14:44 | CARRIER - 24ABB336W0031010 | 83 | 0 | Yes | Yes | 18.4 | 20.9 | -2.5 | 08A9058EE5F1427EBB047A9BF7EAF1E5 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2185 |  | 2015-07-21 | 2015-07-21 13:04 | 2015-07-21 13:04 | AMERICAN STANDARD - 2A7A3042A1000AA | 109 | 0 | Yes | Yes | 19.6 | 19.4 | 0.2 | 5D813D9EC2DF4CF382206E4123FCC942 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6246 |  | 2015-07-20 | 2015-07-20 11:39 | 2015-07-20 11:39 | CARRIER - 24ABA330A320 | 85 | 0 | Yes | Yes | 19.1 | 19.9 | -0.8 | 43E84D9E6CFC47F4BEE742C455BF625D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7852 |  | 2015-07-07 | 2015-07-07 09:48 | 2015-07-07 09:48 | CARRIER - 38BRBO42300 | 131 | 0 | Yes | Yes | 23.2 | 19.3 | 3.9 | 720ADA47D0C24827952576204C71DF58 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1910 |  | 2015-10-12 | 2015-10-12 08:23 | 2015-10-12 08:23 | UNITARY PRODUCTS GROUP - H2A336GKA100 | 141 | 0 | Yes | Yes | 20.8 | 19.1 | 1.7 | 00C67FD3957A419D98169FAB52C623EA |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-8988 |  | 2015-08-21 | 2015-08-21 10:53 | 2015-08-21 11:15 | OTHER - CKJ42-1AB | 106 | 8.4 | Yes | Yes | 18.5 | 19.9 | -1.4 | 98C4FA0B0B2C4F0C88086C36D977F1D7 | Add refrigerant: 7.9 oz | R22 | Non-TXV |  | 7.925% | 0.92075 | 15.23% | [5 empty] | Non-TXV | 7.925%
Esparto | CA | 95627-2018 |  | 2015-10-20 | 2015-10-20 14:13 | 2015-10-20 14:13 | DAY & NIGHT - 593ANX024000AAAA | 96 | 0 | Yes | Yes | 18.7 | 21.5 | -2.8 | A8AEEBB8CDDA45B7858657B2C6A38B8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8913 |  | 2015-08-24 | 2015-08-24 10:29 | 2015-08-24 10:29 | CARRIER - 38BRCO42340 | 104 | 0 | Yes | Yes | 18.9 | 17.7 | 1.2 | 735827BABCC84A5189FA485DF8DE055A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1746 |  | 2015-08-21 | 2015-08-21 09:11 | 2015-08-21 09:11 | TRANE - TTN030C100CZ | 95 | 0 | Yes | Yes | 18.1 | 19.3 | -1.2 | 5646730ED74948D8809C69E9ED5D8DBC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4451 |  | 2015-08-27 | 2015-08-27 12:09 | 2015-08-27 12:09 | WHIRLPOOL - W2GC336A-1 | 111 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | C944AFD177244FFB85769D6B0FE49C6E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5198 |  | 2015-07-06 | 2015-07-06 11:30 | 2015-07-06 11:30 | BDP - 565BJO36 | 85 | 0 | Yes | Yes | 19.5 | 19.4 | 0.1 | 27121847DDE0407E99F80FF73BA1B781 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3941 |  | 2015-08-07 | 2015-08-07 15:27 | 2015-08-07 15:27 | TRANE - TTR030C100A3 | 70 | 0 | Yes | Yes | 20.4 | 18.3 | 2.2 | DACE6FD78B49410CA6E307625D5D1512 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9506 |  | 2015-08-17 | 2015-08-17 15:46 | 2015-08-17 16:14 | TEMPSTAR - N4A336AKB200 | 85 | 14 | Yes | Yes | 21.8 | 20.8 | 1 | A74D2A70B29D4722AAD3CB605E17F435 |  | R410A | TXV |  | 16.47% | 0.83529 | 31.65% | [5 empty] | TXV | 16.47%
Fairfield | CA | 94534-6700 |  | 2015-07-28 | 2015-07-28 09:22 | 2015-07-28 09:22 | CARRIER - 38CK036350 | 69 | 0 | Yes | Yes | 17.9 | 20.7 | -2.8 | 606CE31407AF46C381235D2CA22E52C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6226 |  | 2015-09-15 | 2015-09-15 11:30 | 2015-09-15 11:30 | GOODMAN - CE36-1GB | 79 | 0 | Yes | Yes | 21.6 | 19 | 2.6 | 74DD8C20A7DD4332B91E7C628FE02429 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-5229 |  | 2015-10-06 | 2015-10-06 09:48 | 2015-10-06 09:48 | CARRIER - 38BRC048370 | 141 | 0 | Yes | Yes | 18.8 | 18.2 | 0.6 | 6ADAFCCB93AC4C53A518621BE06701C3 |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1963 |  | 2015-09-30 | 2015-09-30 11:29 | 2015-09-30 11:29 | BRYANT - 113RNA024C | 71 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | F213247E017746AFA492E39ED14D85E7 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2717 |  | 2015-07-10 | 2015-07-10 10:58 | 2015-07-10 10:58 | CARRIER - 38TKBO30300 | 85 | 0 | Yes | Yes | 15.9 | 18.8 | -2.9 | 100AD992523745179C6EF426FDE01372 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1624 |  | 2015-09-21 | 2015-09-21 15:22 | 2015-09-21 15:22 | TRANE - 2TTB3036A1000AA | 101 | 0 | Yes | Yes | 20.7 | 21.4 | -0.7 | C6D177CD40AE40F89363704B749BFF0D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2614 |  | 2015-07-17 | 2015-07-17 12:41 | 2015-07-17 12:41 | AMERICAN STANDARD - 4A7B3024D | 80 | 2.6 | Yes | Yes | 16.4 | 18.7 | -2.3 | D2B6575A6C3149D59766158F2BA9189D | Add refrigerant: 2.6 oz | R410A | Non-TXV |  | 3.25% | 0.48 | 99.93% | [5 empty] | Non-TXV | 3.25%
Oakley | CA | 94561-5221 |  | 2015-09-25 | 2015-09-25 13:58 | 2015-09-25 13:58 | CARRIER - 38BRC048370 | 142 | 0 | Yes | Yes | 21.1 | 21.3 | -0.2 | 9A8CF7E150794772B8EFB6CFEF9F80E8 |  | R22 | TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2034 |  | 2015-09-29 | 2015-09-29 16:01 | 2015-09-29 16:01 | GUARDIAN - GCGD24S41S3A | 60 | 0 | Yes | Yes | 20.2 | 21.5 | -1.3 | A2F664125BD4441F8B74C2AC7E9358D4 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2422 |  | 2015-07-23 | 2015-07-23 15:04 | 2015-07-23 15:04 | GOODMAN - PGB030075-1 REV A | 56 | 0 | Yes | Yes | 24.9 | 19 | 5.9 | FB3C9C27FB3E4C869FA827861D3E8061 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2007 |  | 2015-10-13 | 2015-10-13 10:33 | 2015-10-13 10:33 | DAY & NIGHT - N4A336AKB200 | 84 | 0 | Yes | Yes | 19.9 | 22.5 | -2.6 | 74C22B4B3EED478B9EF7FA017E05427C |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8907 |  | 2015-08-17 | 2015-08-17 18:53 | 2015-08-17 18:53 | AIRE-FLO - 13ACD-048-230-15 | 120 | 0 | Yes | Yes | 25.5 | 22.8 | 2.7 | 8FD05F982A554E918F237CB95DD7A09E |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1814 |  | 2015-08-25 | 2015-08-25 16:26 | 2015-08-25 16:26 | CARRIER - 38EH030340 | 130 | 0 | Yes | Yes | 21.1 | 19.3 | 1.8 | 88BF293ED7C8403FB58D1E6AB31BA16E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-2318 |  | 2015-08-04 | 2015-08-04 12:18 | 2015-08-04 12:18 | YORK - 38CKC060370 | 133 | 0 | Yes | Yes | 17.2 | 19.3 | -2.1 | 498EDE969FA94C4B9AEF4A46AC2A0AFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-2182 |  | 2015-07-29 | 2015-07-29 11:03 | 2015-07-29 11:03 | OTHER - 38EH036300 | 116 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | 47B87E98E7C34B6487DA4B1589182B7D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2112 |  | 2015-08-18 | 2015-08-18 14:06 | 2015-08-18 14:06 | HEIL - HAC030AKA4 | 74 | 0 | Yes | Yes | 21 | 18.8 | 2.2 | D85920E58932465184F855C00FC5B69B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lafayette | CA | 94549-3709 |  | 2015-08-05 | 2015-08-05 11:45 | 2015-08-05 11:45 | COLEMAN - TCGD36S21S2A | 63 | 0 | Yes | Yes | 22.5 | 22.2 | 0.4 | 96BFD79555244F04907DDD62D999904C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4528 |  | 2015-08-14 | 2015-08-14 15:57 | 2015-08-14 15:57 | TRANE - 2TTB0048A1000AA | 109 | 0 | Yes | Yes | 19.1 | 21.6 | -2.5 | 2758C185615F48DA9241B7F6F576C058 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2329 |  | 2015-08-03 | 2015-08-03 16:21 | 2015-08-03 16:21 | TRANE - 2TTB3030A1000AA | 88 | 0 | Yes | Yes | 21.5 | 20.2 | 1.4 | B0B7A27E5E0D4C3B9CA681EF5CE4978E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2329 |  | 2015-08-03 | 2015-08-03 16:31 | 2015-08-03 16:31 | TRANE - 2TTB3036A1000AA | 101 | 0 | Yes | Yes | 21.6 | 21 | 0.6 | B2C7090CFD1540B0B7899BCA5FA7DE53 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4918 |  | 2015-07-17 | 2015-07-17 09:42 | 2015-07-17 09:42 | NORDYNE - JS3BA-036KA | 69 | 0 | Yes | Yes | 20.2 | 19.3 | 0.9 | 3E54007B37A043B0A4189AC65C6B0566 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7087 |  | 2015-08-11 | 2015-08-11 08:43 | 2015-08-11 08:43 | DAY & NIGHT - 591ANX03600AAAA | 88 | 0 | Yes | Yes | 19.9 | 19.9 | 0 | 751A806B3ABB47F2A5CD42FB918320B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6317 |  | 2015-11-04 | 2015-11-04 13:25 | 2015-11-04 13:25 | GOODMAN - CLJ48 | 136 | 0 | Yes | Yes | 16.6 | 19.4 | -2.8 | 67B91D580C604165833AD5FC7FCDAE8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6456 |  | 2015-10-19 | 2015-10-19 11:19 | 2015-10-19 11:19 | CARRIER - 38CKC048370 | 101 | 0 | Yes | Yes | 20.9 | 20.8 | 0.1 | 0CEB1767AD3B47A48644DDB0E3F45A5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1824 |  | 2015-11-05 | 2015-11-05 09:23 | 2015-11-05 09:23 | CARRIER - 38CKC48 | 85 | 0 | Yes | Yes | 20 | 19.7 | 0.3 | 3E033B1FB8EE443B9DDBDAF37414CD1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7065 |  | 2015-08-20 | 2015-08-20 15:22 | 2015-08-20 15:22 | PAYNE - UNK | 101 | 0 | Yes | Yes | 23.8 | 21.4 | 2.4 | 7058F41753A04E02B85F83FEAE7C0D6F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8392 |  | 2015-08-05 | 2015-08-05 16:06 | 2015-08-05 16:06 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 16.2 | 18 | -1.8 | 780372B4113847FE98BA14FA5E0A278D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5151 |  | 2015-07-17 | 2015-07-17 15:46 | 2015-07-17 15:46 | AMERICAN STANDARD - 2TTB0030A1000AA | 85 | 0 | Yes | Yes | 23.9 | 19.3 | 4.6 | A2BF7181AC8A4C618C24946ABDDD8032 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5641 |  | 2015-08-31 | 2015-08-31 11:36 | 2015-08-31 11:36 | RUUD - UAKA037JAZ | 79 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | C05D5AE1E2644929ABAF74815BC5FAAB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2310 |  | 2015-08-18 | 2015-08-18 12:57 | 2015-08-18 12:57 | HEIL - CA5536VKD2 | 82 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | 5B8FB59D6212400CAE5A68E3A286EEFF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2729 |  | 2015-07-24 | 2015-07-24 08:29 | 2015-07-24 08:29 | AMERICAN STANDARD - 4TTB3030E1000AA | 82 | 0 | Yes | Yes | 21.5 | 19.1 | 2.4 | 9E56EEE4E0D844C4A015D60D859F4582 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3414 |  | 2015-07-22 | 2015-07-22 11:49 | 2015-07-22 11:49 | BRYANT - UNK | 86 | 0 | Yes | Yes | 18 | 17.6 | 0.4 | 1794ED7B37884F05A6D55C320C9AC3B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3909 |  | 2015-08-20 | 2015-08-20 13:24 | 2015-08-20 13:24 | CARRIER - 38TXA048300 | 173 | 0 | Yes | Yes | 19.4 | 19.2 | 0.2 | 63BC6062F49B43FB85E98E7859728655 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5804 |  | 2015-08-07 | 2015-08-07 09:02 | 2015-08-07 09:02 | HEIL - N4A436AKA300 | 109 | 0 | Yes | Yes | 22 | 18.3 | 3.7 | 47002E24DB7A4B839F5AD2CDCB8FDAEA |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8390 |  | 2015-07-20 | 2015-07-20 11:15 | 2015-07-20 11:15 | BDP - 561CJO42-A | 85 | 0 | Yes | Yes | 29 | 20.7 | 8.3 | 9812ADE5AF454BA6BF3B551DDFAF7322 |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3747 |  | 2015-09-10 | 2015-09-10 16:01 | 2015-09-10 16:01 | TRANE - TTR760A100A0 | 164 | 0 | Yes | Yes | 17.4 | 18 | -0.6 | 5E5FA05591474955BA140DF43A0EF161 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1121 |  | 2015-08-07 | 2015-08-07 16:35 | 2015-08-07 16:35 | CARRIER - 24ABB330W310 | 74 | 0 | Yes | Yes | 17.9 | 18.6 | -0.7 | 1E85F2F4B57B4B87907D6F178440ABDE |  | R410A | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1351 |  | 2015-09-01 | 2015-09-01 10:02 | 2015-09-01 10:02 | CARRIER - 48ESNA30006030 | 85 | 0 | Yes | Yes | 15 | 17.1 | -2.1 | 27C30DB7E6EB4A95AC2F150E2B4F8E42 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1050 |  | 2015-07-28 | 2015-07-28 12:01 | 2015-07-28 12:01 | PAYNE - 597BNX030000AAAA | 109 | 0 | Yes | Yes | 21.7 | 21 | 0.7 | 5349E78CF047486C82E2BD56744A51E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-4179 |  | 2015-10-09 | 2015-10-09 15:22 | 2015-10-09 15:22 | YORK - ACKMC05620024X1221A | 76 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 81863C2434EB463A81B649158415B16E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-9326 |  | 2015-10-15 | 2015-10-15 14:16 | 2015-10-15 14:16 | COLEMAN - BRCS0481BD | 117 | 0 | Yes | Yes | 19 | 17.2 | 1.8 | E6B051782C6148BA8061639A3790E5A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-6781 |  | 2015-08-17 | 2015-08-17 16:30 | 2015-08-17 16:30 | CARRIER - 38CKC042350 | 93 | 0 | Yes | Yes | 18.2 | 20.2 | -2 | 415A61CA4ECA4F3186C0D3A7600762A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2222 |  | 2015-08-19 | 2015-08-19 11:01 | 2015-08-19 11:01 | OTHER - 5655BJ042 | 94 | 0 | Yes | Yes | 16.9 | 19.6 | -2.7 | E3C3AC3315C24844A49606EB9B95C244 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7411 |  | 2015-07-16 | 2015-07-16 11:17 | 2015-07-16 11:17 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 19.7 | 19.7 | 0 | 8ED5153F8A8749149FF55B99EDE1254F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-8732 |  | 2015-07-17 | 2015-07-17 12:19 | 2015-07-17 12:31 | BRYANT - 563CN036-E | 96 | 0 | Yes | Yes | 19.7 | 18.8 | 0.9 | 935CD8B2735C4F2797F78B5DC44722C1 |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1423 |  | 2015-08-11 | 2015-08-11 12:22 | 2015-08-11 12:22 | TRANE - 4TTX3036A1000AA | 78 | 0 | Yes | Yes | 13.4 | 16.4 | -3 | F0F5AA8873DD45B8B1B51CEA44480997 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6820 |  | 2015-09-21 | 2015-09-21 10:03 | 2015-09-21 10:03 | GOODMAN - CRT24-1A | 102 | 0 | Yes | Yes | 17.1 | 18.7 | -1.6 | B947DE7F368243FE8F1B7D34AF9D581F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2327 |  | 2015-08-10 | 2015-08-10 08:09 | 2015-08-10 08:09 | LENNOX - HS260362P | 93 | 0 | Yes | Yes | 23.7 | 18.7 | 5 | 1A2CCD54D99A496BBBD5A9C1CD238AE0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5411 |  | 2015-08-18 | 2015-08-18 11:29 | 2015-08-18 11:29 | YORK - H4DH060S06A | 125 | 0 | Yes | Yes | 19.1 | 15.8 | 3.3 | 06FC6B3CD7054EBAA7837893F3CB7DE6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-5709 |  | 2015-09-24 | 2015-09-24 10:39 | 2015-09-24 10:39 | TRANE - TTB036C100A2 | 90 | 0 | Yes | Yes | 18.5 | 17.4 | 1.2 | 9CC012D819574D4AACAD13E384CF7425 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8900 |  | 2015-10-16 | 2015-10-16 13:53 | 2015-10-16 13:53 | PAYNE - 591ANX048000ACAA | 128 | 0 | Yes | Yes | 26.4 | 23.5 | 2.9 | 1B21C0BE10E94E878F6F924E2BF88321 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3008 |  | 2015-08-20 | 2015-08-20 10:20 | 2015-08-20 10:20 | DAY & NIGHT - 5690642 | 119 | 0 | Yes | Yes | 21.2 | 18.2 | 3 | 07348F6B07C64B458B46DAD92C798E72 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1960 |  | 2015-09-17 | 2015-09-17 12:55 | 2015-09-17 12:55 | RUUD - UAKA-060JAZ | 112 | 0 | Yes | Yes | 22 | 19.9 | 2.1 | 5FABB07D4A944A97B81652B71AEF68EB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2082 |  | 2015-09-03 | 2015-09-03 12:36 | 2015-09-03 12:36 | CARRIER - 38CKC024320 | 72 | 0 | Yes | Yes | 19.3 | 18.7 | 0.6 | 6728DA89BC56420CAD89FA90BF7A0F8C |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6451 |  | 2015-08-11 | 2015-08-11 13:37 | 2015-08-11 13:37 | PAYNE - PA10JA036C | 76 | 0 | Yes | Yes | 16.6 | 18.2 | -1.6 | 7C9599B16D894427862C07162F7E7CDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7743 |  | 2015-07-31 | 2015-07-31 11:30 | 2015-07-31 11:30 | PAYNE - JS3BA060KB | 85 | 0 | Yes | Yes | 21.5 | 18.2 | 3.3 | A92E05D2FD5742788FB4AFE51F2B2C2E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-4087 |  | 2015-09-03 | 2015-09-03 14:39 | 2015-09-03 14:39 | CARRIER - 24ABB342W300 | 86 | 0 | Yes | Yes | 19.4 | 19.6 | -0.2 | D5423191A8F742F7A7F4D41A25E2B6CA |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8112 |  | 2015-07-20 | 2015-07-20 09:04 | 2015-07-20 09:27 | RHEEM - RAJC042JAS | 99 | 6.6 | Yes | Yes | 17.5 | 20.2 | -2.7 | 7474CDB265C540568568B2CE618C3C1A |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
San Ramon | CA | 94583-2485 |  | 2015-08-03 | 2015-08-03 10:17 | 2015-08-03 10:17 | YORK - YCJD60S21S2A | 84 | 0 | Yes | Yes | 19.7 | 19.4 | 0.3 | B01EB8AE5EA74FBE9C3EA83AD77A7360 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1764 |  | 2015-08-31 | 2015-08-31 08:53 | 2015-08-31 08:53 | BRYANT - AA1AJ036B | 74 | 0 | Yes | Yes | 22.8 | 19 | 3.8 | AB1F810103C04F9BAD1BB9448DDDC0E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4252 |  | 2015-10-15 | 2015-10-15 16:32 | 2015-10-15 16:32 | BRYANT - 574DNWA30040NA | 98 | 0 | Yes | Yes | 24 | 21.5 | 2.5 | 692EC2329233415AB994DBC02D1D784B |  | R410A | TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2614 |  | 2015-10-09 | 2015-10-09 17:02 | 2015-10-09 17:02 | PAYNE - PA13NA036B | 71 | 0 | Yes | Yes | 20.7 | 21.4 | -0.7 | D30D3186DCA34275AE2526313841D668 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Pablo | CA | 94806-5048 |  | 2015-07-09 | 2015-07-09 08:33 | 2015-07-09 08:50 | CARRIER - 38CKC036350 | 70 | 5.6 | Yes | Yes | 17.6 | 18.5 | -0.8 | 2AC24C3DDC7746E1B2BF2770C06AE17D |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Brentwood | CA | 94513-5505 |  | 2015-08-25 | 2015-08-25 11:11 | 2015-08-25 11:38 | CARRIER - 38BRC042340 | 108 | 8.6 | Yes | Yes | 23.9 | 19.3 | 4.6 | 05157B60FEE44194B25D5FDA46CF4692 |  | R22 | TXV |  | 7.963% | 0.92037 | 15.3% | [5 empty] | TXV | 7.963%
Vacaville | CA | 95688-2705 |  | 2015-07-17 | 2015-07-17 14:19 | 2015-07-17 14:19 | CARRIER - D3GH036N06006A | 85 | 0 | Yes | Yes | 18.9 | 19.7 | -0.8 | 363D148688F4439494D6CF5E488C9982 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7618 |  | 2015-07-22 | 2015-07-22 16:09 | 2015-07-22 16:09 | BRYANT - 113ANA042-B | 116 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | C39F5D869F7D44A5B7537A8D91FF495C |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3202 |  | 2015-07-07 | 2015-07-07 13:24 | 2015-07-07 13:24 | COLEMAN - TCGD30S21S2A | 55 | 0 | Yes | Yes | 25 | 21.6 | 3.5 | AA56CBBBE6FC41ECB87AB012C54B80FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5503 |  | 2015-08-21 | 2015-08-21 12:35 | 2015-08-21 12:35 | CARRIER - 38CKC042340 | 85 | 0 | Yes | Yes | 21.3 | 18.3 | 3 | 96475290668B43AAB3F8A4F235F66298 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3636 |  | 2015-07-20 | 2015-07-20 12:25 | 2015-07-20 12:25 | DAY & NIGHT - 58561030 | 85 | 0 | Yes | Yes | 17.8 | 18.8 | -1 | EA85BB8F26D34531BB82BFF80E040CAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4516 |  | 2015-09-16 | 2015-09-16 15:14 | 2015-09-16 15:14 | OTHER - ASC036A2C1 | 83 | 0 | Yes | Yes | 20 | 19.6 | 0.4 | 9837051F0AA84DCFBD17A48D4B8F869F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9424 |  | 2015-10-26 | 2015-10-26 13:37 | 2015-10-26 13:37 | COLEMAN - TCJF36S41S3A | 58 | 0 | Yes | Yes | 17.1 | 18.8 | -1.7 | 12D2F8424D76400B8106D1A2FF78D3B4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6744 |  | 2015-10-13 | 2015-10-13 13:58 | 2015-10-13 13:58 | RHEEM - RAFD036JAS | 80 | 0 | Yes | Yes | 18 | 19.8 | -1.8 | A43C39FC2EF6442E8BD4457D59E0BE16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1821 |  | 2015-09-15 | 2015-09-15 14:44 | 2015-09-15 14:44 | TRANE - 4TTX4042B1000AA | 103 | 0 | Yes | Yes | 23.9 | 19.3 | 4.6 | 2C65512BBFFE4BF5B70AB466AC653C9A |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94520-1105 |  | 2015-07-28 | 2015-07-28 11:17 | 2015-07-28 11:17 | CARRIER - 24ABC624A300 | 96 | 0 | Yes | Yes | 14.8 | 17.7 | -2.9 | F2DDBDFED998428CB49D5CB989B65C55 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4442 |  | 2015-10-12 | 2015-10-12 10:20 | 2015-10-12 10:20 | OTHER - 38ETG036300 | 85 | 0 | Yes | Yes | 18.9 | 19.1 | -0.2 | FE31EC43A6E342C1B9812ACE70CBC97C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-0000 |  | 2015-09-16 | 2015-09-16 15:01 | 2015-09-16 15:01 | OTHER - S3QA-024KA | 64 | 0 | Yes | Yes | 18.7 | 21.5 | -2.8 | 197C6E4F9729451EAE5674D6927CC753 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2209 |  | 2015-10-14 | 2015-10-14 14:31 | 2015-10-14 14:31 | CARRIER - UNK | 85 | 0 | Yes | Yes | 22.6 | 21.5 | 1.1 | 6A53F8B3F92C4AD09386D7D97F409913 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2404 |  | 2015-08-25 | 2015-08-25 12:21 | 2015-08-25 12:21 | CARRIER - 38TH060300 | 169 | 0 | Yes | Yes | 18.7 | 18.6 | 0.1 | E1947AA9F0474AE396513445458F8936 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4702 |  | 2015-07-28 | 2015-07-28 15:43 | 2015-07-28 15:43 | OTHER - TCA060AKA1 | 131 | 5.2 | Yes | Yes | 11 | 17.2 | -6.2 | 038FA2AF94F747F1BD6232B00277D097 | Add refrigerant: 5.2 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.969% | 0.96031 | 7.628% | [5 empty] | Non-TXV | 3.969%
Pittsburg | CA | 94565-5923 |  | 2015-09-09 | 2015-09-09 13:17 | 2015-09-09 13:35 | OTHER - PA13NA036 C | 70 | 6.3 | Yes | Yes | 23.7 | 24.2 | -0.5 | 62F18869C43643B983E4748B5DD3B600 |  | R410A | TXV |  | 9% | 0.91 | 17.3% | [5 empty] | TXV | 9%
Pittsburg | CA | 94565-3764 |  | 2015-10-13 | 2015-10-13 16:44 | 2015-10-13 16:44 | GOODMAN - GSH130181CB | 127 | 0 | Yes | Yes | 22.9 | 23.3 | -0.4 | DD893C6B3A8E4C0A95936FF83284F18B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2048 |  | 2015-07-16 | 2015-07-16 12:29 | 2015-07-16 12:29 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 16.5 | 18 | -1.5 | 3EEC0530B9514010A888887E2D9D996B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2130 |  | 2015-07-20 | 2015-07-20 14:17 | 2015-07-20 14:17 | PAYNE - PA13NAO48-E | 85 | 0 | Yes | Yes | 23.9 | 18.6 | 5.4 | FB9897C5999A4970AFAB20584C73916D |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3061 |  | 2015-10-05 | 2015-10-05 10:57 | 2015-10-05 10:57 | DAY & NIGHT - 591ANX036000AAAA | 85 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | DDC1C8D630554330B75DF33C0B0AD6D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-4255 |  | 2015-08-31 | 2015-08-31 17:37 | 2015-08-31 17:37 | RUUD - UAKA-048JAS | 103 | 0 | Yes | Yes | 18.5 | 16.6 | 1.9 | AA6E48841C8C4AD4A3F2FD314719ED53 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2302 |  | 2015-08-21 | 2015-08-21 15:14 | 2015-08-21 15:14 | PAYNE - PA13NRO36K | 86 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | D95D1BC471D24F8792B6E0AE18970196 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1810 |  | 2015-08-10 | 2015-08-10 11:32 | 2015-08-10 11:32 | TRANE - 4TTR3036E1000AA | 105 | 0 | Yes | Yes | 18 | 19.8 | -1.8 | EC4AF6BD52564C669947B66E0419D6CE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3737 |  | 2015-10-16 | 2015-10-16 12:04 | 2015-10-16 12:04 | AMANA - PGD36C0902E | 110 | 0 | Yes | Yes | 24.6 | 21 | 3.6 | EB95DD739B97464A9F62B0A27211139C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2136 |  | 2015-08-06 | 2015-08-06 16:58 | 2015-08-06 16:58 | TRANE - TTR042C100A2 | 110 | 0 | Yes | Yes | 23.1 | 20.4 | 2.7 | 036234C07DDF499F8730C002ED4EDA25 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2136 |  | 2015-11-18 | 2015-11-18 12:51 | 2015-11-18 12:51 | PAYNE - PA10JA036-C | 77 | 0 | Yes | Yes | 16.9 | 19.8 | -2.9 | 02BB3A4B2BC94BECB3FBE05548B956AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-1545 |  | 2015-08-03 | 2015-08-03 09:27 | 2015-08-03 09:27 | RUUD - UAFD-036JAS | 80 | 0 | Yes | Yes | 21.4 | 22.5 | -1.1 | F13458513F8B40DFB202D4E6442E66EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5653 |  | 2015-08-18 | 2015-08-18 13:57 | 2015-08-18 13:57 | RHEEM - RAKA0300JAZ | 66 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | 49AB676CDE364DC38487C882999F119F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-4228 |  | 2015-10-14 | 2015-10-14 10:12 | 2015-10-14 10:12 | YORK - EH2DH042S06A | 85 | 0 | Yes | Yes | 15.7 | 18.6 | -2.9 | CBA53438E5584E66AD171351415000FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1759 |  | 2015-09-24 | 2015-09-24 12:23 | 2015-09-24 12:23 | ICP - 0GD342090K001C1 | 106 | 0 | Yes | Yes | 22 | 19.5 | 2.5 | BBF6250831C64AADA3953BE91CE859A2 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5835 |  | 2015-09-10 | 2015-09-10 10:54 | 2015-09-10 10:54 | AMERICAN STANDARD - 2A7A3024A10000AA | 80 | 0 | Yes | Yes | 24.2 | 21.4 | 2.8 | 392C14D294174693A9F531A36F8D46F2 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8361 |  | 2015-10-20 | 2015-10-20 16:49 | 2015-10-20 16:49 | CARRIER - UNKNOWN | 76 | 0 | Yes | Yes | 23.1 | 21.5 | 1.6 | 458D065A418046FAA21A1D8C09B9B091 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2036 |  | 2015-08-26 | 2015-08-26 09:27 | 2015-08-26 09:27 | RHEEM - RACC-030JAS | 58 | 0 | Yes | Yes | 22.5 | 18.8 | 3.7 | 2A403039973A4EF884BD34F5237FFA8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4266 |  | 2015-08-27 | 2015-08-27 08:15 | 2015-08-27 08:15 | PAYNE - 591ANX018000AAAA | 48 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | A8160DF425EF4B3488FE193829904874 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Richmond | CA | 94803-2634 |  | 2015-07-10 | 2015-07-10 09:52 | 2015-07-10 09:52 | CARRIER - 38CK048300 | 102 | 0 | Yes | Yes | 22.9 | 18.7 | 4.2 | D167E02BA8C64FAAA98AD7137455E791 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5193 |  | 2015-09-22 | 2015-09-22 11:50 | 2015-09-22 12:34 | ICP - PGC036K060A | 85 | 14.1 | Yes | Yes | 20.9 | 22.8 | -1.9 | C700677BA9244695B6AFEDBAFC202A24 |  | R22 | Non-TXV |  | 16.59% | 0.83412 | 31.88% | [5 empty] | Non-TXV | 16.59%
W Sacramento | CA | 95691-6219 |  | 2015-11-13 | 2015-11-13 10:08 | 2015-11-13 10:08 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 22.7 | 20.9 | 1.8 | 8743C68828F64E77B374AC86B3CCB165 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1418 |  | 2015-09-23 | 2015-09-23 11:47 | 2015-09-23 12:01 | GOODMAN - GPG13360451AC | 112 | 11.8 | Yes | Yes | 22.3 | 21.7 | 0.6 | 525449EF389E4D92A3B9F6AE330268E9 |  | R22 | Non-TXV |  | 10.54% | 0.89464 | 20.25% | [5 empty] | Non-TXV | 10.54%
Napa | CA | 94558-3247 |  | 2015-10-24 | 2015-10-24 09:33 | 2015-10-24 09:33 | RUUD - UAKB-036JAZ | 79 | 0 | Yes | Yes | 20.6 | 18.3 | 2.3 | 7A7E0AF6B9564860BC45218CFB545B5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3927 |  | 2015-09-18 | 2015-09-18 11:44 | 2015-09-18 11:50 | ICP - PGAA24B1K3 | 85 | 14.8 | Yes | Yes | 25.8 | 21.4 | 4.4 | FFDE08688EBB4FEFB8844D487D81900C |  | R22 | Non-TXV |  | 17.41% | 0.82588 | 33.46% | [5 empty] | Non-TXV | 17.41%
Suisun City | CA | 94585-2904 |  | 2015-09-11 | 2015-09-11 14:26 | 2015-09-11 14:26 | GOODMAN - UNK | 85 | 0 | Yes | Yes | 20.9 | 18.8 | 2.1 | FC009297D22445CE9545559D75056D6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3921 |  | 2015-07-27 | 2015-07-27 14:09 | 2015-07-27 14:09 | AMERICAN STANDARD - YCY036F1M0AA | 129 | 0 | Yes | Yes | 19.2 | 21.3 | -2.1 | 308853F1E23C47ADA02DF1C45BCD77DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1785 |  | 2015-09-08 | 2015-09-08 15:53 | 2015-09-08 15:53 | CARRIER - 561AJ048-B | 103 | 0 | Yes | Yes | 16 | 18.8 | -2.8 | E53216FAAAF445FA8D1EE1F4B14CD4BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3978 |  | 2015-09-18 | 2015-09-18 10:05 | 2015-09-18 10:05 | OTHER - UKN | 85 | 0 | Yes | Yes | 21.3 | 19.8 | 1.5 | 00EB33B9D21146E9A2E831627E178252 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3977 |  | 2015-09-18 | 2015-09-18 09:15 | 2015-09-18 09:15 | OTHER - UKN | 85 | 0 | Yes | Yes | 20.7 | 19.5 | 1.2 | 52D2492A599C4C408849741ACF66D028 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1337 |  | 2015-08-24 | 2015-08-24 09:07 | 2015-08-24 09:33 | RHEEM - RAKA-042JAZ | 79 | 15.7 | Yes | Yes | 23.8 | 20.3 | 3.6 | 837D360766B64221B1120ACE11705907 |  | R22 | Non-TXV |  | 19.87% | 0.80127 | 38.19% | [5 empty] | Non-TXV | 19.87%
Davis | CA | 95618-0368 |  | 2015-10-01 | 2015-10-01 14:25 | 2015-10-01 14:25 | AMERICAN STANDARD - CM18418 | 46 | 0 | Yes | Yes | 14.7 | 15.9 | -1.2 | FFD66568761A424EAF49416C885A1E3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6426 |  | 2015-08-17 | 2015-08-17 09:21 | 2015-08-17 09:21 | RUUD - UKN | 90 | 0 | Yes | Yes | 21.9 | 21.1 | 0.8 | 6B71150571E9494AB608452FEEF29993 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4727 |  | 2015-07-16 | 2015-07-16 11:53 | 2015-07-16 11:53 | BRYANT - 583NW048115ABHF | 131 | 0 | Yes | Yes | 15.3 | 18.2 | -2.9 | CF10F2285075443495047A3B503BBB01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5842 |  | 2015-08-11 | 2015-08-11 14:25 | 2015-08-11 14:25 | PAYNE - 561AJ036B | 88 | 0 | Yes | Yes | 21.6 | 18.5 | 3.1 | 7B0255BC321F4C56A82198B724BFB7AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6245 |  | 2015-07-22 | 2015-07-22 14:15 | 2015-07-22 14:15 | TRANE - 2TTB3036A1000AA | 101 | 0 | Yes | Yes | 22.5 | 21.3 | 1.2 | 36ACF44E8D814C728E3317BFFA3CA9FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1404 |  | 2015-09-08 | 2015-09-08 15:46 | 2015-09-08 15:46 | PAYNE - PA13NA036000AEAA | 70 | 0 | Yes | Yes | 18.2 | 18.3 | -0.1 | 384E6FFEFF10437E95B56158A87268EE |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5768 |  | 2015-08-25 | 2015-08-25 12:55 | 2015-08-25 12:55 | GIBSON - JS3BA036KA | 69 | 0 | Yes | Yes | 19.5 | 14.9 | 4.7 | 1BD953DA224C47E79C6A604EB0B98B64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1517 |  | 2015-08-13 | 2015-08-13 09:44 | 2015-08-13 09:44 | AMERICAN STANDARD - 4TTB3036E100AA | 92 | 0 | Yes | Yes | 19.3 | 18.8 | 0.5 | 2272F530BC244ECDB852C5788BFE9542 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7075 |  | 2015-09-22 | 2015-09-22 08:55 | 2015-09-22 09:27 | GOODMAN - CKL36-IL | 84 | 14.8 | Yes | Yes | 21.4 | 22.6 | -1.2 | 495A2AD25BEB4F3F9169A064E0B248D1 |  | R22 | Non-TXV |  | 17.62% | 0.82381 | 33.86% | [5 empty] | Non-TXV | 17.62%
Vacaville | CA | 95687-6131 |  | 2015-07-23 | 2015-07-23 14:52 | 2015-07-23 14:52 | PAYNE - 593AND30B | 105 | 0 | Yes | Yes | 15.3 | 16.8 | -1.5 | C638BA5D31744F168C1709F33EBA4717 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3750 |  | 2015-09-18 | 2015-09-18 08:54 | 2015-09-18 08:54 | - UKN | 85 | 0 | Yes | Yes | 24.8 | 19.3 | 5.5 | 40FD07DC5C20432F809E0FB5E842AF15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2228 |  | 2015-08-31 | 2015-08-31 10:52 | 2015-08-31 11:03 | YORK - D1NP048N06506A | 72 | 23 | Yes | Yes | 20.3 | 20.2 | 0.1 | 1C8EF02C8C784E578252BF239BCEAAED |  | R22 | Non-TXV |  | 31.94% | 0.68056 | 61.39% | [5 empty] | Non-TXV | 31.94%
Antioch | CA | 94509-2172 |  | 2015-10-12 | 2015-10-12 10:42 | 2015-10-12 10:42 | PAYNE - PA13NRO36-H | 85 | 0 | Yes | Yes | 15.9 | 18.2 | -2.3 | 6EC967201BF1418CB7431A12CB501C05 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5040 |  | 2015-07-02 | 2015-07-02 12:32 | 2015-07-02 12:32 | DAY & NIGHT - N2A336AKB200 | 84 | 0 | Yes | Yes | 21 | 19.8 | 1.2 | B04E47CBE87D4F78BFF683D2963A016B |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2221 |  | 2015-08-07 | 2015-08-07 14:40 | 2015-08-07 14:40 | - | 85 | 0 | Yes | Yes | 20.5 | 22.9 | -2.4 | FBBA65121417447DBE96AB7C900F93D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3415 |  | 2015-09-18 | 2015-09-18 12:36 | 2015-09-18 13:30 | ICP - PGD436060K001C1 | 151 | 5.8 | Yes | Yes | 24.5 | 23.1 | 1.4 | E8949A5BB6D0423A99A426ECEAB8E9FF |  | R410A | Non-TXV |  | 3.841% | 0.96159 | 7.382% | [5 empty] | Non-TXV | 3.841%
Campbell | CA | 95008-1817 |  | 2015-07-27 | 2015-07-27 15:14 | 2015-07-27 15:14 | CARRIER - 24ACB448A300 | 176 | 0 | Yes | Yes | 25 | 21 | 4 | 8933C561BA2E4EE6BF89F5AE9AB56A4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5950 |  | 2015-11-13 | 2015-11-13 15:12 | 2015-11-13 15:12 | CARRIER - 38CKC042340 | 80 | 0 | Yes | Yes | 17 | 19.4 | -2.4 | CDC0330B2FE24FA7A4F6652788EC53DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6048 |  | 2015-09-01 | 2015-09-01 11:02 | 2015-09-01 11:31 | YORK - D1NH03605606C | 108 | 11.4 | Yes | Yes | 22.5 | 23.4 | -0.9 | 63CA2F01FD984467961CDF1B115BDBF8 |  | R22 | Non-TXV |  | 10.56% | 0.89444 | 20.29% | [5 empty] | Non-TXV | 10.56%
Antioch | CA | 94509-6458 |  | 2015-10-26 | 2015-10-26 14:29 | 2015-10-26 14:29 | YORK - H1RA048S06D | 121 | 0 | Yes | Yes | 23.6 | 21.3 | 2.4 | 11BE7C9B594A4CEAB29E014BBD5F14DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4133 |  | 2015-09-21 | 2015-09-21 12:49 | 2015-09-21 12:49 | YORK - DCYP-F024N045B | 100 | 0 | Yes | Yes | 20.8 | 22.6 | -1.8 | 6900C4CB22BC4497A1DBC7A3EC2BF67F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2117 |  | 2015-08-31 | 2015-08-31 12:25 | 2015-08-31 12:25 | CARRIER - N4A342AKA300 | 88 | 0 | Yes | Yes | 20.1 | 19.9 | 0.2 | A3FFED38F36B44B68370CE2D98BBB8F6 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8912 |  | 2015-10-15 | 2015-10-15 15:18 | 2015-10-15 15:18 | CARRIER - 38CK036340 | 74 | 0 | Yes | Yes | 19.1 | 21.7 | -2.5 | F5B662888D894E459D7A298F1DFE04BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6869 |  | 2015-09-21 | 2015-09-21 11:39 | 2015-09-21 12:51 | YORK - D1NH036N05606C | 108 | 18.9 | Yes | Yes | 18 | 18.2 | -0.2 | 996ECF3A9459419E879EFD298F9D164B |  | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Bakersfield | CA | 93313-5746 |  | 2015-08-07 | 2015-08-07 14:49 | 2015-08-07 14:49 | YORK - H2RC042S06HA | 109 | 0 | Yes | Yes | 21.6 | 22.2 | -0.5 | 5D9188DE6BB847CAAF5DED436A3F8E7D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4319 |  | 2015-09-11 | 2015-09-11 10:53 | 2015-09-11 10:53 | OTHER - CK36-1A | 73 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | AB5FC618DD7E43C88D3452108BD66822 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5508 |  | 2015-08-24 | 2015-08-24 12:54 | 2015-08-24 12:54 | CARRIER - 38BRC036350 | 108 | 0 | Yes | Yes | 18.9 | 19.3 | -0.4 | E19300A9CD7F4BC79DE259D8BC4A7928 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3611 |  | 2015-08-07 | 2015-08-07 14:46 | 2015-08-07 14:46 | RHEEM - RRNA-B042JK08X | 104 | 0 | Yes | Yes | 21 | 23.1 | -2.1 | 7B2E44E9C6D1406F841F8DBFF5AE2016 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2716 |  | 2015-07-23 | 2015-07-23 13:51 | 2015-07-23 13:51 | TRANE - RAUC302-B | 85 | 0 | Yes | Yes | 17 | 19.4 | -2.4 | AF089A026ABA4305AC088C0728BB7BBD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5157 |  | 2015-09-12 | 2015-09-12 11:22 | 2015-09-12 11:22 | GOODMAN - CPKE24-1AB | 106 | 0 | Yes | Yes | 19.1 | 22 | -2.9 | 0807C26C93B34EA381012DD9057BC24D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-5170 |  | 2015-08-27 | 2015-08-27 08:26 | 2015-08-27 08:51 | ICP - PGME36G080E | 138 | 37.9 | Yes | Yes | 19.8 | 19.3 | 0.5 | CE5B817B792A41799459FF318064158E |  | R22 | Non-TXV |  | 27.46% | 0.72536 | 52.78% | [5 empty] | Non-TXV | 27.46%
Suisun City | CA | 94585-0000 |  | 2015-08-25 | 2015-08-25 10:01 | 2015-08-25 10:01 | INTERTHERM - S3QA 030KA | 85 | 0 | Yes | Yes | 14.8 | 17.7 | -2.9 | FCD8359B04E84610AC23F699C2B7C601 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-4628 |  | 2015-08-24 | 2015-08-24 16:56 | 2015-08-24 16:56 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 25.4 | 20.1 | 5.3 | 22DBA58F9A0D47E7BEDF0EF667B4E6DE |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4226 |  | 2015-08-17 | 2015-08-17 09:11 | 2015-08-17 09:11 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 26.8 | 21.5 | 5.3 | 082CC3CC6B50443F8A1ED99A11EE4109 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2660 |  | 2015-11-17 | 2015-11-17 14:38 | 2015-11-17 14:38 | LENNOX - GCS20030 | 74 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | 0AA77F1DA2A04420B62EB1CA6602A0BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-9439 |  | 2015-07-31 | 2015-07-31 11:32 | 2015-07-31 11:32 | CARRIER - 24APA748A310 | 85 | 0 | Yes | Yes | 16.4 | 19.3 | -2.9 | B2F6F7D453364AC198F1523B29BCAB22 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2934 |  | 2015-10-28 | 2015-10-28 10:31 | 2015-10-28 10:31 | RUUD - UAMB030JAZ | 77 | 0 | Yes | Yes | 18.9 | 17.2 | 1.7 | E54C02A8EBA7454887D787BA948676A0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5428 |  | 2015-08-17 | 2015-08-17 08:27 | 2015-08-17 08:27 | GOODMAN - GPG13300451BB | 77 | 0 | Yes | Yes | 19.4 | 22.1 | -2.7 | 9801AD809C85445389A16F18E919B22C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1923 |  | 2015-08-17 | 2015-08-17 10:21 | 2015-08-17 10:21 | OTHER - N/A | 85 | 0 | Yes | Yes | 25.4 | 23.2 | 2.2 | F21D18F674C7458FB9D7F99EEEA86C3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-5101 |  | 2015-09-23 | 2015-09-23 14:31 | 2015-09-23 14:31 | - DAYA-F030N070C | 76 | 0 | Yes | Yes | 16.8 | 16.6 | 0.2 | 10F078218730415893E8080CDC67015E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7033 |  | 2015-08-12 | 2015-08-12 10:19 | 2015-08-12 10:19 | YORK - UNK | 125 | 0 | Yes | Yes | 20.5 | 19.8 | 0.7 | BC70DCF803DD40B98A8CF7A527B8B496 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3612 |  | 2015-08-27 | 2015-08-27 08:50 | 2015-08-27 08:50 | YORK - D1NA036N05606C | 67 | 0 | Yes | Yes | 21.7 | 20 | 1.8 | C628D9B0D2E946B98D8857C23C7C43BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-2949 |  | 2015-08-19 | 2015-08-19 09:27 | 2015-08-19 09:27 | YORK - H4DH036S06A | 85 | 0 | Yes | Yes | 22.4 | 19.5 | 2.9 | 9B978E993AE240F3BA57945DAE1923B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1342 |  | 2015-06-23 | 2015-06-23 12:01 | 2015-06-23 12:30 | YORK - H2RD0425068 | 141 | 12.4 | Yes | Yes | 19.2 | 18.7 | 0.5 | 9F35B0428098400CA056D21D46E74E50 |  | R22 | Non-TXV |  | 8.794% | 0.91206 | 16.9% | [5 empty] | Non-TXV | 8.794%
Vallejo | CA | 94591-7149 |  | 2015-07-24 | 2015-07-24 15:27 | 2015-07-24 15:27 | GUARDIAN - GCGD48S21S2B | 85 | 0 | Yes | Yes | 24.8 | 23.6 | 1.3 | 6CC2492DD42D4471AD831C081274AB89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7149 |  | 2015-07-24 | 2015-07-24 16:07 | 2015-07-24 16:07 | GUARDIAN - GCGD48S21S2B | 85 | 0 | Yes | Yes | 18.7 | 19.4 | -0.7 | 341ED29FCD0E4B7B86AAC731FB462118 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-2930 |  | 2015-08-28 | 2015-08-28 12:09 | 2015-08-28 12:09 | YORK - D1NA048N09006C | 92 | 0 | Yes | Yes | 21.3 | 20.2 | 1.2 | 3F9EED3F0E52486CAAE26FE0A08C70B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1736 |  | 2015-08-14 | 2015-08-14 10:58 | 2015-08-14 10:58 | TRANE - TTBO42C100A1 | 96 | 0 | Yes | Yes | 19.1 | 18.8 | 0.3 | B9227D286B684122B58304B00B23862E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7825 |  | 2015-10-13 | 2015-10-13 17:06 | 2015-10-13 17:06 | TRANE - TTR736AT100A0 | 116 | 0 | Yes | Yes | 17.5 | 19.9 | -2.4 | 94DBDC64B0EF4A4994518CB39AFBFFF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7337 |  | 2015-10-20 | 2015-10-20 14:42 | 2015-10-20 14:42 | OTHER - 38TH036300 | 85 | 0 | Yes | Yes | 19.3 | 19.6 | -0.3 | 50923D14FD2C44E5AEEB84B392A17A96 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3048 |  | 2015-11-04 | 2015-11-04 15:56 | 2015-11-04 15:56 | TRANE - TTN036 | 87 | 0 | Yes | Yes | 22.5 | 19.4 | 3.1 | 9D49D371F2F6491998327AA719EB4490 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-3654 |  | 2015-09-22 | 2015-09-22 13:53 | 2015-09-22 13:53 | TRANE - 4TTX4024B1000AA | 82 | 0 | Yes | Yes | 17.3 | 18.2 | -0.9 | 05DEFE87C62E404290EA515B4C677568 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-2129 |  | 2015-07-28 | 2015-07-28 12:13 | 2015-07-28 12:13 | GE - BTB942A100A2 | 101 | 0 | Yes | Yes | 19.3 | 19.3 | 0 | 504A83B2A9EC440EBB53A8C0F2662AA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5182 |  | 2015-07-27 | 2015-07-27 11:50 | 2015-07-27 11:50 | ICP - PGD324040K001C1 | 77 | 0 | Yes | Yes | 19.9 | 20.1 | -0.2 | F6DE354796C844179DCF0EA74BF1AE5F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5411 |  | 2015-08-17 | 2015-08-17 09:51 | 2015-08-17 09:51 | ICP - PGAD42D1K1 | 180 | 0 | Yes | Yes | 20.2 | 19.9 | 0.3 | FB1A5377C4674EACB47283ACCC52E87D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-3447 |  | 2015-08-11 | 2015-08-11 13:13 | 2015-08-11 14:08 | DAY & NIGHT - N4A448GKB300 | 144 | 8.6 | Yes | Yes | 20.2 | 19.2 | 1 | 97CD9369A9594A948CB406F3AEE34F46 |  | R410A | TXV |  | 5.972% | 0.94028 | 11.48% | [5 empty] | TXV | 5.972%
Bakersfield | CA | 93304-6612 |  | 2015-07-27 | 2015-07-27 12:13 | 2015-07-27 12:13 | ICP - PGC036K960E | 71 | 0 | Yes | Yes | 21.8 | 16.3 | 5.5 | EF921D8D89134ABA824E4EA314E42A57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2805 |  | 2015-08-10 | 2015-08-10 11:14 | 2015-08-10 11:14 | YORK - D2NA060N09006D | 84 | 0 | Yes | Yes | 20.5 | 20.9 | -0.4 | 157E3E8E52104B9FB42F4D60E7853BCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6607 |  | 2015-08-18 | 2015-08-18 12:00 | 2015-08-18 12:00 | RHEEM - AT42B10 | 51 | 0 | Yes | Yes | 18.5 | 19.9 | -1.4 | AF6BB57E5C7B4D7ABC9D379C32F51566 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7256 |  | 2015-08-17 | 2015-08-17 09:39 | 2015-08-17 09:39 | YORK - H2CB048S06A | 162 | 0 | Yes | Yes | 18.3 | 19.9 | -1.6 | 99B83A838180463B8D6B0A9A62CF09E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-4463 |  | 2015-10-09 | 2015-10-09 16:06 | 2015-10-09 16:06 | GOODMAN - GSH30241CB | 122 | 0 | Yes | Yes | 14.5 | 16.1 | -1.6 | E645A3104E714610B09C7EB5B29E4296 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-0000 |  | 2015-08-17 | 2015-08-17 11:49 | 2015-08-17 11:49 | WEATHER KING - 13AJA42A01 | 121 | 0 | Yes | Yes | 21.2 | 23.2 | -2 | CF9360BA0B6C4313A0C25D6D5B8479B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4378 |  | 2015-07-24 | 2015-07-24 12:05 | 2015-07-24 12:05 | CARRIER - 38CK036320 | 85 | 0 | Yes | Yes | 23.7 | 19.5 | 4.2 | 8F6CB6CE0F6B4F21B432ED66837997C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3729 |  | 2015-09-10 | 2015-09-10 12:15 | 2015-09-10 12:15 | OTHER - TCA036AKA5 | 80 | 0 | Yes | Yes | 18.6 | 20.3 | -1.7 | 07DAFF083C5745AE97541EEA24635E72 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1816 |  | 2015-09-24 | 2015-09-24 13:19 | 2015-09-24 13:19 | RHEEM - RRKA-A042JK08E | 69 | 0 | Yes | Yes | 23 | 20.6 | 2.4 | 41862792A6614ED7818381C1467B6D20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6223 |  | 2015-09-30 | 2015-09-30 15:00 | 2015-09-30 15:00 | AMERICAN STANDARD - FS5BD036KA | 110 | 0 | Yes | Yes | 23.9 | 19.1 | 4.9 | 1D748374A2784B3D9ABFF3E90C3637DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3748 |  | 2015-09-22 | 2015-09-22 14:41 | 2015-09-22 14:41 | OTHER - N/A | 85 | 0 | Yes | Yes | 19.9 | 21.5 | -1.6 | F58AF92B38BA43DFB12A5A807C1668B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1005 |  | 2015-07-27 | 2015-07-27 13:18 | 2015-07-27 13:18 | GOODMAN - GPG1342070M41DA | 85 | 0 | Yes | Yes | 22 | 19.9 | 2.1 | 0F33FC7E340B4EE6A442C7DC43ACF223 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-0000 |  | 2015-09-24 | 2015-09-24 14:25 | 2015-09-24 14:25 | OTHER - WCA3362GKR2 | 85 | 0 | Yes | Yes | 22.3 | 20.3 | 2 | 6052C93F673C4A9B8A86EC42FC70EBAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Richmond | CA | 94806-6109 |  | 2015-07-08 | 2015-07-08 08:34 | 2015-07-08 08:34 | OTHER - UKW | 85 | 0 | Yes | Yes | 17.3 | 17.1 | 0.2 | 80B7D4E516924522B822E27474AE1A66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4167 |  | 2015-08-05 | 2015-08-05 14:02 | 2015-08-05 14:02 | AMERICAN STANDARD - PA13NA024-B | 63 | 0 | Yes | Yes | 14.3 | 17.3 | -3 | DE71AFA6EE024D25B4577E3E40BADD0A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6945 |  | 2015-09-24 | 2015-09-24 10:31 | 2015-09-24 10:31 | RUUD - N/A | 60 | 10.6 | Yes | Yes | 24.8 | 21 | 3.8 | DED4264A91744FB495EFE4CC944CDE1E | Add refrigerant: 10.6 oz | R22 | Non-TXV |  | 17.67% | 0.82333 | 33.95% | [5 empty] | Non-TXV | 17.67%
Pittsburg | CA | 94565-2283 |  | 2015-10-01 | 2015-10-01 12:45 | 2015-10-01 12:45 | TRANE - TTRRO42D100BO | 81 | 0 | Yes | Yes | 19.6 | 20.3 | -0.7 | 018CCCCFFDBC444888287AC6571D2F3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5150 |  | 2015-10-29 | 2015-10-29 11:03 | 2015-10-29 11:03 | CARRIER - 38CKC060370 | 132 | 0 | Yes | Yes | 22.9 | 21.5 | 1.4 | 074BBA1D9A184041B58871305DF57B39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4308 |  | 2015-07-24 | 2015-07-24 14:30 | 2015-07-24 14:30 | PAYNE - 561AJO36B | 76 | 0 | Yes | Yes | 24 | 20.1 | 3.9 | 35B98F1A2BAF469CA18F671D6FABA982 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94583-1266 |  | 2015-08-05 | 2015-08-05 12:56 | 2015-08-05 13:13 | CARRIER - 38CKB036 | 79 | 4.2 | Yes | Yes | 18.8 | 20.9 | -2.1 | 0A805E59EF524B56A30F872F811BAE6A |  | R22 | TXV |  | 5.316% | 0.94684 | 10.22% | [5 empty] | TXV | 5.316%
Antioch | CA | 94509-5874 |  | 2015-08-05 | 2015-08-05 08:37 | 2015-08-05 08:37 | PAYNE - PA13NR048-8 | 85 | 0 | Yes | Yes | 17.6 | 19.1 | -1.5 | 0DAF5D929A6E4460963F16F27059E8BB |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5153 |  | 2015-10-12 | 2015-10-12 14:27 | 2015-10-12 14:27 | TRANE - BTD736100B0 | 88 | 0 | Yes | Yes | 20.1 | 16.8 | 3.3 | 7C0A94A6F67F410ABE6B31AEBDE7B0B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5203 |  | 2015-11-10 | 2015-11-10 16:10 | 2015-11-10 16:10 | RHEEM - RAMA-036JAZ | 96 | 0 | Yes | Yes | 17.9 | 18.2 | -0.3 | 58331638274549D6B3EE0AA98829B9FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5054 |  | 2015-09-17 | 2015-09-17 14:41 | 2015-09-17 14:41 | RUUD - URMA-A042JK08X | 114 | 0 | Yes | Yes | 15.5 | 18.2 | -2.7 | 5A70107DE3FA4689A047622C8C55F5F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4547 |  | 2015-07-23 | 2015-07-23 14:11 | 2015-07-23 14:11 | OTHER - PA13NR018-J | 85 | 0 | Yes | Yes | 19.5 | 18.8 | 0.7 | AF1FAC327A4E45C58B8CC41E3000D2DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2310 |  | 2015-09-24 | 2015-09-24 11:38 | 2015-09-24 11:38 | UNITARY PRODUCTS GROUP - N2A336AKB300 | 85 | 0 | Yes | Yes | 16.6 | 18.8 | -2.2 | 860BE0232C6F45F3A4A2274E6E336154 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4009 |  | 2015-11-10 | 2015-11-10 15:36 | 2015-11-10 15:36 | GOODMAN - GPG153609041AB | 102 | 0 | Yes | Yes | 23.2 | 20.7 | 2.5 | 0C303206861B44538AFC3D925DE24ECF |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5426 |  | 2015-08-20 | 2015-08-20 16:47 | 2015-08-20 16:47 | CARRIER - 38TKBO30320 | 75 | 0 | Yes | Yes | 17.5 | 19.9 | -2.4 | BE2353EFBCC74A5495FB9787DDBF1556 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2147 |  | 2015-09-26 | 2015-09-26 12:17 | 2015-09-26 12:17 | AMERICAN STANDARD - 2A7A2030A1000AA | 68 | 0 | Yes | Yes | 19.2 | 22.2 | -3 | FBD88BB0AA2B4F7CA7A6AD54801ACC56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4244 |  | 2015-07-23 | 2015-07-23 11:10 | 2015-07-23 11:10 | OTHER - 591ANX30000ABAA | 66 | 0 | Yes | Yes | 24.3 | 21.4 | 2.9 | 9380F0C150BD481B87580D940032BB25 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3340 |  | 2015-10-13 | 2015-10-13 12:48 | 2015-10-13 12:48 | ICP - PGC036K060B | 71 | 0 | Yes | Yes | 21.7 | 21.8 | -0.1 | 68B3008E1B1642AAAEDEBD7840B07474 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7204 |  | 2015-08-05 | 2015-08-05 08:16 | 2015-08-05 08:16 | RHEEM - UNK | 85 | 0 | Yes | Yes | 23.4 | 18.7 | 4.7 | 32C3CD02AA6E454AA9527ECC467BFA47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2408 |  | 2015-07-17 | 2015-07-17 14:08 | 2015-07-17 14:08 | OTHER - TCA224AKC4 | 81 | 0 | Yes | Yes | 33.1 | 19.9 | 13.2 | 4D2F49CD3C594D27BFC91FE92E09426A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3829 |  | 2015-07-08 | 2015-07-08 12:05 | 2015-07-08 12:23 | GOODMAN - CK-42-1A | 85 | 16.2 | Yes | Yes | 22.6 | 20.4 | 2.2 | 383A2B7657F048C081061A775E13DD6B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.06% | 0.80941 | 36.63% | [5 empty] | Non-TXV | 19.06%
Pleasant Hill | CA | 94523-3146 |  | 2015-08-28 | 2015-08-28 12:20 | 2015-08-28 12:20 | OTHER - UNK | 85 | 0 | Yes | Yes | 14.9 | 17.4 | -2.5 | 9DC14012333A4FF086C1A0EBABFC33F9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1814 |  | 2015-08-27 | 2015-08-27 10:15 | 2015-08-27 10:15 | GE - BTR936C100AO | 168 | 0 | Yes | Yes | 15.3 | 18.2 | -2.9 | BC4320E445B746CC93DB6D0FE9DD90C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5215 |  | 2015-08-19 | 2015-08-19 09:36 | 2015-08-19 09:36 | CARRIER - UNK | 85 | 0 | Yes | Yes | 23 | 17.7 | 5.3 | 3804A41FEA0543FC99F212C1347747C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6277 |  | 2015-10-13 | 2015-10-13 13:01 | 2015-10-13 13:01 | WEATHER KING - 13AJA42A01 | 121 | 0 | Yes | Yes | 22.8 | 24.2 | -1.4 | D381984B726A40978982ADA61DDC7374 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1031 |  | 2015-08-28 | 2015-08-28 13:23 | 2015-08-28 13:23 | COLEMAN - M030M322 | 59 | 0 | Yes | Yes | 15.4 | 18.4 | -3 | 23667AECB18C4D22AF27D61DAC9027BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8926 |  | 2015-10-27 | 2015-10-27 08:39 | 2015-10-27 08:39 | CARRIER - 38BR036300 | 122 | 0 | Yes | Yes | 19.7 | 18.8 | 0.9 | FF0B49A9DE1D49AA8707DAEFCBCCED6A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2606 |  | 2015-08-12 | 2015-08-12 11:02 | 2015-08-12 11:02 | TRANE - TTN042C100A2 | 146 | 0 | Yes | Yes | 23.3 | 18.3 | 5 | 408286E787AE4AB19C3176E76F156413 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8000 |  | 2015-11-03 | 2015-11-03 12:35 | 2015-11-03 12:35 | CARRIER - 24ACR360A310 | 200 | 0 | Yes | Yes | 22.4 | 21.9 | 0.5 | 2F85164D685F4176A62C18BE1B4EC482 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1784 |  | 2015-09-01 | 2015-09-01 12:03 | 2015-09-01 12:03 | OTHER - ZRCF42UO1D | 133 | 0 | Yes | Yes | 19.6 | 19.7 | -0.1 | E2626829B6F645D294D822041C9C7BCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-5022 |  | 2015-06-22 | 2015-06-22 11:28 | 2015-06-22 11:28 | GOODMAN - 6GP10300701 | 85 | 0 | Yes | Yes | 27.2 | 20.4 | 6.8 | 00D34B4294954CE080BF59B81AD424CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2806 |  | 2015-09-30 | 2015-09-30 11:17 | 2015-09-30 11:17 | CARRIER - 38TKB036330 | 85 | 0 | Yes | Yes | 19.5 | 18.8 | 0.8 | 4897EB69A71740B792F02753BD6EF819 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-1718 |  | 2015-07-28 | 2015-07-28 10:54 | 2015-07-28 10:54 | YORK - H4DH048S06A | 138 | 0 | Yes | Yes | 14 | 20.7 | -6.7 | A490814B3A7742339D1887F0A3A5A9CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93311-9721 |  | 2015-08-03 | 2015-08-03 11:36 | 2015-08-03 11:36 | COLEMAN - DAYP-F036N070A | 108 | 0 | Yes | Yes | 24.5 | 21.1 | 3.4 | 6F61724B73A245E4B3FEBFCB0107F510 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2419 |  | 2015-08-03 | 2015-08-03 09:40 | 2015-08-03 09:40 | DAY & NIGHT - PGD3300C12160971860K001C1 | 85 | 0 | Yes | Yes | 23.3 | 18.2 | 5.1 | 8D5784EE81DF42D09230C93ACE5AF87D |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94583-1490 |  | 2015-08-04 | 2015-08-04 12:54 | 2015-08-04 12:54 | PAYNE - 565BJ024 | 70 | 0 | Yes | Yes | 25.7 | 21 | 4.7 | 954AB95CEAEC4068BF86B66DABAEA26D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4216 |  | 2015-09-24 | 2015-09-24 15:36 | 2015-09-24 15:36 | GE - BTN960A100A0 | 168 | 0 | Yes | Yes | 20.5 | 21.5 | -1 | 29681E7F9CD74583B9729904C36A8249 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5807 |  | 2015-08-10 | 2015-08-10 09:49 | 2015-08-10 09:49 | NORDYNE - FS3BC-060KA | 155 | 0 | Yes | Yes | 21.9 | 22.1 | -0.2 | 4F58BF63BF954E74B7AEA95B8071B9A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6316 |  | 2015-09-24 | 2015-09-24 11:36 | 2015-09-24 11:36 | OTHER - N/A | 85 | 0 | Yes | Yes | 21.3 | 19.6 | 1.8 | 48269612F34841B0855383733CBC5A8B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4606 |  | 2015-08-10 | 2015-08-10 09:24 | 2015-08-10 09:24 | RHEEM - RAKA-060JAZ | 112 | 0 | Yes | Yes | 20.1 | 21.4 | -1.3 | A9E6A9C5BE0F42918211EB3978A36D76 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pacheco | CA | 94553-6344 |  | 2015-07-24 | 2015-07-24 12:44 | 2015-07-24 12:44 | YORK - H2RA036SO6G | 63 | 0 | Yes | Yes | 19.9 | 19.3 | 0.6 | B9B39DC7E696440E8FDE3EEC0D062974 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2530 |  | 2015-09-08 | 2015-09-08 12:40 | 2015-09-08 12:40 | CARRIER - N4A336AKB200 | 84 | 0 | Yes | Yes | 22.3 | 21.8 | 0.5 | E507C0059D2B4D589CEAE0CF4C8BE675 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5541 |  | 2015-08-18 | 2015-08-18 09:35 | 2015-08-18 09:35 | DAY & NIGHT - 42110YAC 102AK | 124 | 0 | Yes | Yes | 18.6 | 20.8 | -2.2 | 11EB99043AF74A729F65B8852FBEBE0A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5373 |  | 2015-10-14 | 2015-10-14 15:33 | 2015-10-14 15:57 | ARCOAIRE - NAC230AKC3 | 112 | 13.7 | Yes | Yes | 24.3 | 19 | 5.3 | D9452994CD5D46238F317CB955F85444 |  | R22 | Non-TXV |  | 12.23% | 0.87768 | 23.51% | [5 empty] | Non-TXV | 12.23%
Fairfield | CA | 94533-2504 |  | 2015-08-14 | 2015-08-14 15:09 | 2015-08-14 15:09 | DAY & NIGHT - 5658JO42 | 92 | 0 | Yes | Yes | 20.3 | 23.2 | -2.9 | 088EC0BE41D841A7BC0954BE63CB46C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5698 |  | 2015-07-07 | 2015-07-07 10:46 | 2015-07-07 10:46 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 17.9 | 19.3 | -1.4 | 29F3956361384ED69E3FD3C48185703A |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2410 |  | 2015-10-13 | 2015-10-13 12:55 | 2015-10-13 12:55 | OTHER - UNKNOWN | 119 | 0 | Yes | Yes | 22.1 | 22.4 | -0.3 | 093E0ED9C0194C34B4F5FFD1F9EB14DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2963 |  | 2015-08-28 | 2015-08-28 12:14 | 2015-08-28 12:41 | CARRIER - 24ABB348A310 | 112 | 18.2 | Yes | Yes | 8.6 | 19.8 | -11.2 | 11F993F02ED24B7CA8F82317DFFA3E4A | Add refrigerant: 17.9 oz | R410A | TXV |  | 16.25% | 0.8375 | 31.23% | [5 empty] | TXV | 16.25%
Bakersfield | CA | 93313-5201 |  | 2015-08-10 | 2015-08-10 14:55 | 2015-08-10 14:55 | TEMPSTAR - CA9060VKD2 | 192 | 0 | Yes | Yes | 18.8 | 21 | -2.2 | 5BC18AAC67DC45FABF9516E44F7851B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-3844 |  | 2015-07-21 | 2015-07-21 14:27 | 2015-07-21 14:27 | CARRIER - 38TXA048320 | 173 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | 3E935972643448ECA73D073EDF88B072 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7656 |  | 2015-08-04 | 2015-08-04 15:16 | 2015-08-04 15:16 | CARRIER - 563CN036A | 122 | 0 | Yes | Yes | 21.1 | 18.9 | 2.3 | DDE6DFEEC2F2426DAB7F2DEFFB6FCE9C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2621 |  | 2015-08-19 | 2015-08-19 13:30 | 2015-08-19 13:30 | CARRIER - 38CK042300 | 85 | 0 | Yes | Yes | 23.6 | 19.2 | 4.5 | 76659C79B95B42148C833FD94D4A9D5B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2621 |  | 2015-08-19 | 2015-08-19 14:05 | 2015-08-19 14:05 | CARRIER - 38CK042300 | 85 | 0 | Yes | Yes | 18.1 | 20.2 | -2.1 | 6D09A068FF89471796ACA3D2FAD7E631 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2428 |  | 2015-08-10 | 2015-08-10 12:45 | 2015-08-10 12:45 | UNITARY PRODUCTS GROUP - D6NZ060N06506NXA | 85 | 0 | Yes | Yes | 25.2 | 20.6 | 4.6 | B0410C2C994E4227993D73D80134F243 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6132 |  | 2015-08-18 | 2015-08-18 10:00 | 2015-08-18 10:56 | ICP - PGAA36C1K4 | 69 | 15.5 | Yes | Yes | 24 | 21.3 | 2.7 | 2AA1D2739F004C12BB8CA00ADBC792F7 |  | R22 | Non-TXV |  | 22.46% | 0.77536 | 43.17% | [5 empty] | Non-TXV | 22.46%
Antioch | CA | 94509-5359 |  | 2015-10-28 | 2015-10-28 16:25 | 2015-10-28 16:25 | LENNOX - 10ACC-36-230-02 | 74 | 0 | Yes | Yes | 21 | 19.9 | 1.1 | 6EA2A600A1464FD1A93F3303B71F7139 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2018 |  | 2015-07-02 | 2015-07-02 11:07 | 2015-07-02 11:07 | PAYNE - ELD36B15A1 | 73 | 0 | Yes | Yes | 22.2 | 16.8 | 5.4 | 0A1012C3C54D4DA5B348A80550D5F773 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5511 |  | 2015-10-02 | 2015-10-02 14:52 | 2015-10-02 14:52 | OTHER - 38BRC036350 | 104 | 0 | Yes | Yes | 16.9 | 19.8 | -2.9 | 83E261569C4443638C8F6017B7172FDB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-8366 |  | 2015-09-24 | 2015-09-24 14:11 | 2015-09-24 14:12 | WEATHER KING - 13AJA36A01 | 108 | 15.1 | Yes | Yes | 20.7 | 22.5 | -1.8 | 53F322A8C16E4DBCA8254AD452DA34E8 |  | R22 | Non-TXV |  | 13.98% | 0.86019 | 26.87% | [5 empty] | Non-TXV | 13.98%
Bakersfield | CA | 93305-4060 |  | 2015-09-21 | 2015-09-21 13:40 | 2015-09-21 14:57 | TEMPSTAR - PGAD24B1K8 | 72 | 6.9 | Yes | Yes | 20.9 | 21 | -0.1 | 3B2905D7C72846B599F13B9628B6B51D |  | R22 | Non-TXV |  | 9.583% | 0.90417 | 18.42% | [5 empty] | Non-TXV | 9.583%
Pittsburg | CA | 94565-7911 |  | 2015-09-10 | 2015-09-10 11:23 | 2015-09-10 11:23 | CARRIER - 24ABA348A310 | 105 | 0 | Yes | Yes | 16.8 | 19.6 | -2.8 | 6110A28028954EB7BB1CBC4833A28921 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2623 |  | 2015-08-18 | 2015-08-18 09:01 | 2015-08-18 09:01 | ICP - PGC042K080B | 87 | 0 | Yes | Yes | 22 | 23.5 | -1.5 | 8E9AF6C89AC14CCEAD7371161F2A7D1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3048 |  | 2015-08-28 | 2015-08-28 09:26 | 2015-08-28 09:26 | RUUD - UAKA048JAZ | 103 | 0 | Yes | Yes | 19.6 | 18.7 | 0.9 | 23C2441DA7064C33A5A245BD71734977 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8210 |  | 2015-11-03 | 2015-11-03 09:23 | 2015-11-03 09:23 | TRANE - TTR7448B100A0 | 142 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 7683153275A24569A40847DD7F3A0DC4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4445 |  | 2015-07-28 | 2015-07-28 09:32 | 2015-07-28 09:32 | CARRIER - 24ABB348W310 | 85 | 0 | Yes | Yes | 20.7 | 20.2 | 0.5 | F6F0EC67E0C347F8A4B5BE95FCF88696 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6409 |  | 2015-09-24 | 2015-09-24 15:10 | 2015-09-24 15:10 | GOODMAN - GPG13420701AB | 107 | 0 | Yes | Yes | 20.8 | 23.4 | -2.6 | D82168EEC9734EE1AD001C9F27C8F868 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-6430 |  | 2015-08-12 | 2015-08-12 16:47 | 2015-08-12 16:47 | DAY & NIGHT - 561AJX048F | 105 | 0 | Yes | Yes | 21 | 19.1 | 1.9 | EC2DA936C4494C23BC351A7349B2F376 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6420 |  | 2015-08-11 | 2015-08-11 09:28 | 2015-08-11 09:28 | LENNOX - 13ACX03623017 | 84 | 0 | Yes | Yes | 20.2 | 18.7 | 1.5 | 870ED5E5F59D485CBD8842D90D479C57 |  | R410A | TXV |  | 0% | 1 | 0%
Lafayette | CA | 94549-4237 |  | 2015-08-05 | 2015-08-05 09:01 | 2015-08-05 09:01 | TRANE - TTX048C100A1 | 160 | 0 | Yes | Yes | 28.4 | 23.3 | 5.1 | 569CAB92F80841BCB4C5DE1A41B4D862 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Lafayette | CA | 94549-4237 |  | 2015-08-05 | 2015-08-05 09:18 | 2015-08-05 09:18 | TRANE - TTX048C100A1 | 160 | 0 | Yes | Yes | 25.6 | 20.3 | 5.3 | 9D24B9D5050B421B9FB1D0946D2691D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-3271 |  | 2015-08-25 | 2015-08-25 11:32 | 2015-08-25 11:32 | TEMPSTAR - CA5524VKC1 | 60 | 0 | Yes | Yes | 16.1 | 18.2 | -2.1 | 71A9B74EC79A49499B3400CED1194AC3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7424 |  | 2015-10-26 | 2015-10-26 13:46 | 2015-10-26 13:46 | CARRIER - 38CKC060300 | 160 | 0 | Yes | Yes | 23.1 | 19.6 | 3.6 | EE7BCAAFDAC840B9B1CC8E4762205665 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3714 |  | 2015-10-07 | 2015-10-07 15:40 | 2015-10-07 15:40 | CARRIER - 38CKC036350 | 85 | 0 | Yes | Yes | 18.3 | 18.5 | -0.2 | C68D398F34F747059ABD2B9C5540BD37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3081 |  | 2015-09-30 | 2015-09-30 13:58 | 2015-09-30 13:58 | TRANE - BTR730E100A0 | 106 | 0 | Yes | Yes | 23.8 | 19.7 | 4.1 | 5C3F05B9CAAC4AFAA77BACB7D5647D00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-5319 |  | 2015-07-21 | 2015-07-21 15:35 | 2015-07-21 15:35 | CARRIER - 48ESNA24040030 | 72 | 0 | Yes | Yes | 16.8 | 19.6 | -2.8 | 9737C135461C49F387CA524A359811D2 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2040 |  | 2015-07-28 | 2015-07-28 09:59 | 2015-07-28 09:59 | TRANE - | 85 | 0 | Yes | Yes | 17.5 | 16.6 | 0.9 | 86C71319FD8944EEBFC49AAC8DCDC29C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-5318 |  | 2015-07-28 | 2015-07-28 13:43 | 2015-07-28 13:43 | GOODMAN - GSX160301FA | 80 | 0 | Yes | Yes | 16.1 | 19 | -2.9 | FB26423F54CC42CBBDA07557BDFF4D5B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3425 |  | 2015-08-06 | 2015-08-06 10:29 | 2015-08-06 10:29 | TRANE - YCC030F1M0BH | 85 | 0 | Yes | Yes | 20 | 18.7 | 1.3 | 98E33A2857984BD3B5815FE2AA581209 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1303 |  | 2015-09-01 | 2015-09-01 16:22 | 2015-09-01 16:22 | TRANE - TTX036C00 | 152 | 0 | Yes | Yes | 16.2 | 15.1 | 1.1 | FD4B53BA63A8465595EC347976622055 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5199 |  | 2015-06-24 | 2015-06-24 17:07 | 2015-06-24 17:34 | OTHER - NAC048GKC3 | 112 | 0 | Yes | Yes | 14.7 | 20.4 | -5.7 | 11A121BAC8A5497EB5A83FA0E803C02F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-4411 |  | 2015-07-22 | 2015-07-22 13:04 | 2015-07-22 13:04 | RHEEM - BO42JK08X | 52 | 0 | Yes | Yes | 24.1 | 20 | 4.1 | 00FFDB25105D4F4D85665A2719AC1B9C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5373 |  | 2015-09-23 | 2015-09-23 10:03 | 2015-09-23 10:03 | ARCOAIRE - NAC230AKC3 | 112 | 0 | Yes | Yes | 23.7 | 19.9 | 3.8 | 1287019E98C24C87BE28FCB1C8D7C871 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2702 |  | 2015-09-21 | 2015-09-21 16:34 | 2015-09-21 16:34 | HEIL - N4A330AKC200 | 67 | 0 | Yes | Yes | 23.1 | 21 | 2.1 | E2660FEDC75146AFB15708FA892147E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5373 |  | 2015-08-25 | 2015-08-25 10:22 | 2015-08-25 10:22 | ARCOAIRE - NAC224AKA1 | 79 | 0 | Yes | Yes | 24.5 | 19.3 | 5.2 | 5E3F95E20A7540D7BABF7DE86285E8DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3527 |  | 2015-08-10 | 2015-08-10 09:18 | 2015-08-10 09:18 | BDP - 585GJW036060 | 82 | 0 | Yes | Yes | 21.7 | 19.5 | 2.2 | A737897944E24E6E9F9AC5D4FE42373A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1223 |  | 2015-08-24 | 2015-08-24 15:34 | 2015-08-24 15:34 | CARRIER - 38CKC036330 | 84 | 0 | Yes | Yes | 22.8 | 18.6 | 4.2 | 60AE146F78BA4153AB68B5648574AEA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5483 |  | 2015-08-10 | 2015-08-10 11:15 | 2015-08-10 11:15 | GIBSON - GS3BA-030KA | 68 | 0 | Yes | Yes | 22 | 22.6 | -0.6 | 3DFCEAAFEA75417CAD11A27DDD4013CF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4335 |  | 2015-09-11 | 2015-09-11 16:40 | 2015-09-11 16:40 | - GCGD36S21S2A | 60 | 0 | Yes | Yes | 25.2 | 20.4 | 4.8 | E8407AB4A85B487FBB0437B4E7328B3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8521 |  | 2015-10-23 | 2015-10-23 12:15 | 2015-10-23 12:15 | CARRIER - UNKNOWN | 167 | 0 | Yes | Yes | 18 | 19.4 | -1.4 | FE4A63C76CD94BE0AD1DCB14D4F32050 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5244 |  | 2015-08-19 | 2015-08-19 12:19 | 2015-08-19 12:19 | CARRIER - 48GSN02404040301 | 56 | 0 | Yes | Yes | 32.1 | 23.1 | 9 | BA9961EB4FEF4CB6A924F1E263EE8FAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3346 |  | 2015-10-28 | 2015-10-28 14:40 | 2015-10-28 14:40 | BDP - 589ANW0600B0ABBG | 103 | 0 | Yes | Yes | 25.2 | 20.4 | 4.8 | DFBB564FC86B469D8BF7EED0B9E294D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5830 |  | 2015-09-15 | 2015-09-15 15:05 | 2015-09-15 15:05 | BDP - 585A030080YAC | 85 | 0 | Yes | Yes | 20.2 | 19.3 | 0.9 | 2DC931D1B81F43E189D79DBD48840C2D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-8995 |  | 2015-08-31 | 2015-08-31 14:26 | 2015-08-31 14:26 | RHEEM - RRPL-B060JK10X | 172 | 0 | Yes | Yes | 22.4 | 20.7 | 1.7 | 4F4EFEB6FC9D4402B6B48F3BCDF6C91B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7125 |  | 2015-09-14 | 2015-09-14 12:14 | 2015-09-14 12:14 | ALLEGIANCE - | 64 | 0 | Yes | Yes | 18.6 | 19.3 | -0.7 | EFDB0D24902C40DF831788AB8E944A8A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-0000 |  | 2015-10-27 | 2015-10-27 14:36 | 2015-10-27 14:36 | TEMPSTAR - NA348AKB200 | 112 | 0 | Yes | Yes | 21.1 | 20.4 | 0.7 | 40008BA43A0E45719798972643C4EF3F |  | R410A | TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4517 |  | 2015-07-16 | 2015-07-16 16:16 | 2015-07-16 16:16 | GOODMAN - CKJ36-18 | 97 | 0 | Yes | Yes | 13.8 | 16.5 | -2.7 | 6F550BAEDA014F92A21B358D6B06C72E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6153 |  | 2015-09-29 | 2015-09-29 10:59 | 2015-09-29 10:59 | YORK - DAYH-F036N070C | 108 | 0 | Yes | Yes | 22.1 | 21 | 1.1 | 3D2CC035FC894454AA3F3044348377D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7028 |  | 2015-10-01 | 2015-10-01 09:27 | 2015-10-01 09:27 | OTHER - FBA036681 | 83 | 0 | Yes | Yes | 19.4 | 20.8 | -1.4 | E9F5D9CBAFCE4933BFE02CC1EFC8E7D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3527 |  | 2015-08-06 | 2015-08-06 14:51 | 2015-08-06 14:51 | TRANE - TTR048C100A3 | 74 | 0 | Yes | Yes | 22.8 | 19 | 3.8 | 8C4F1BBB970747B8B59856E42C8D7C3C |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1247 |  | 2015-08-17 | 2015-08-17 11:02 | 2015-08-17 11:24 | ALLEGIANCE - 7A2036A100A0 | 120 | 10 | Yes | Yes | 24.9 | 19.3 | 5.6 | FFEDA8B882F14DA0A47F297578ABD4A3 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Oakley | CA | 94561-0000 |  | 2015-09-11 | 2015-09-11 12:25 | 2015-09-11 12:25 | CARRIER - 24ABA342A300 | 99 | 0 | Yes | Yes | 19.9 | 20.7 | -0.8 | 53140D346E3F4453AE92990310F48589 |  | R410A | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-0000 |  | 2015-09-11 | 2015-09-11 12:29 | 2015-09-11 12:29 | CARRIER - 24ABA342A300 | 99 | 0 | Yes | Yes | 19.9 | 20.7 | -0.8 | E349CD03480D41B8AA79AE7742527068 |  | R410A | TXV |  | 0% | 1 | 0%
Danville | CA | 94526-1828 |  | 2015-08-04 | 2015-08-04 13:39 | 2015-08-04 13:58 | AMERICAN STANDARD - 561CJ036-C | 78 | 27.6 | Yes | Yes | 27.7 | 23.7 | 4 | BD7DBAA68D654B679AE731AE802B95EA |  | R22 | TXV |  | 35.38% | 0.64615 | 68% | [5 empty] | TXV | 35.38%
Woodland | CA | 95776-5102 |  | 2015-10-14 | 2015-10-14 14:34 | 2015-10-14 14:34 | PAYNE - PA13NR036-H | 85 | 0 | Yes | Yes | 22.5 | 21.9 | 0.6 | BF60F8FFD5144EF59F7FAA1236A84905 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6926 |  | 2015-08-06 | 2015-08-06 13:33 | 2015-08-06 13:33 | OTHER - UNK | 85 | 0 | Yes | Yes | 19.5 | 19.1 | 0.4 | EA6F3BAFD15D4887A4837206515DFFD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-7134 |  | 2015-09-02 | 2015-09-02 13:29 | 2015-09-02 13:29 | RUUD - N/A | 85 | 0 | Yes | Yes | 19.3 | 19.2 | 0.1 | 71CEE597308D490987D14EBFE4EA60F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2812 |  | 2015-08-19 | 2015-08-19 13:16 | 2015-08-19 13:50 | OTHER - TCJD36S41S3HA | 73 | 5.2 | Yes | Yes | 26.1 | 21.7 | 4.4 | 728CE5BE834D4DBFA8D6C2DAD3E2F98E |  | R410A | TXV |  | 7.123% | 0.92877 | 13.69% | [5 empty] | TXV | 7.123%
Clovis | CA | 93612-0458 |  | 2015-09-11 | 2015-09-11 14:24 | 2015-09-11 14:24 | CARRIER - PGD3601115K0001C1 | 160 | 0 | Yes | Yes | 21.8 | 20.7 | 1.1 | B6C87B98FF6B4D88968086F4F3169D56 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1809 |  | 2015-07-28 | 2015-07-28 11:11 | 2015-07-28 11:11 | PAYNE - PA13NA045 | 85 | 0 | Yes | Yes | 22.1 | 18 | 4.2 | E5218006E0ED465CAE48FB9C1A2B2A35 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4754 |  | 2015-07-20 | 2015-07-20 15:16 | 2015-07-20 15:42 | OTHER - GSC130361AA | 124 | 6.3 | Yes | Yes | 18.6 | 19.4 | -0.8 | D4ABB74F28194116A9923CD2B24EA455 |  | R22 | Non-TXV |  | 5.081% | 0.94919 | 9.764% | [5 empty] | Non-TXV | 5.081%
Fresno | CA | 93727-5709 |  | 2015-09-08 | 2015-09-08 15:36 | 2015-09-08 15:36 | RHEEM - RRNL-C060JK10X | 173 | 0 | Yes | Yes | 25.9 | 24.2 | 1.7 | 833E9E81D2344FB5BC2B8BF98DAC3AB8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7127 |  | 2015-09-09 | 2015-09-09 13:24 | 2015-09-09 13:24 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 14.8 | 17.6 | -2.7 | FCE438468C6149B6B461556D42584D1B |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-6082 |  | 2015-10-23 | 2015-10-23 14:28 | 2015-10-23 14:28 | CARRIER - 48NLT020320 | 85 | 0 | Yes | Yes | 21.8 | 19.6 | 2.3 | BF8D1001140D49B8B1B8F792264F1A7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2905 |  | 2015-11-05 | 2015-11-05 15:55 | 2015-11-05 15:55 | GOODMAN - CKL361H | 71 | 0 | Yes | Yes | 17.7 | 17.1 | 0.6 | 751E0E0EDA12430F8D60507122C45CFF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-4415 |  | 2015-08-21 | 2015-08-21 11:49 | 2015-08-21 11:49 | AMANA - RCC24A2A | 150 | 0 | Yes | Yes | 18.1 | 20.8 | -2.7 | 4D3CFB129FF14EE3959C64D2388AA595 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-5001 |  | 2015-11-10 | 2015-11-10 11:08 | 2015-11-10 11:28 | GOODMAN - GSX16031FA | 85 | 6.5 | Yes | Yes | 17.2 | 19.7 | -2.5 | D1DAA13DFC414D0F8A8C05402B27A304 |  | R410A | TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | TXV | 7.647%
Fresno | CA | 93704-4332 |  | 2015-08-19 | 2015-08-19 09:31 | 2015-08-19 09:31 | TEMPSTAR - PGD336060K001C1 | 100 | 0 | Yes | Yes | 21.5 | 17.4 | 4.1 | 2470004D29B941B28A5A21315CB83250 |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4562 |  | 2015-08-26 | 2015-08-26 10:07 | 2015-08-26 10:30 | BDP - 585EJ024050 | 54 | 15.2 | Yes | Yes | 18.5 | 19.9 | -1.4 | 8C03FD7D3EEF41CDB2C3186791830A15 |  | R22 | Non-TXV |  | 28.15% | 0.71852 | 54.09% | [5 empty] | Non-TXV | 28.15%
Pittsburg | CA | 94565-6481 |  | 2015-09-10 | 2015-09-10 09:18 | 2015-09-10 09:18 | YORK - H1RA048S06G | 117 | 0 | Yes | Yes | 19.8 | 21.3 | -1.5 | 0A96D04F5E814C0AB913733D85DF3C38 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5008 |  | 2015-08-28 | 2015-08-28 12:22 | 2015-08-28 12:22 | YORK - DBRA-F036NO6OC | 84 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | 8FDEFFC415E8445395C9AE7A5B037D27 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2712 |  | 2015-08-10 | 2015-08-10 12:08 | 2015-08-10 12:08 | COLEMAN - 9541B90 | 56 | 0 | Yes | Yes | 21.2 | 22.1 | -0.9 | 07646F83983348C4B6C7548181750A26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-4312 |  | 2015-09-16 | 2015-09-16 10:34 | 2015-09-16 10:34 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 21.4 | 19.5 | 1.9 | 5FC19A0F8CC6415DBFA53505A29DCE88 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9437 |  | 2015-08-05 | 2015-08-05 12:04 | 2015-08-05 12:04 | RHEEM - RACA-036ABS | 50 | 0 | Yes | Yes | 20.6 | 19.6 | 1.1 | 0F4137295E14404E831AADDE09C9BBDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5423 |  | 2015-08-21 | 2015-08-21 13:34 | 2015-08-21 13:34 | BRYANT - 550ANO48-E | 173 | 0 | Yes | Yes | 18 | 14.3 | 3.7 | 52425719BE674F3BAF86A46E959398BF |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3617 |  | 2015-10-08 | 2015-10-08 10:43 | 2015-10-08 10:43 | GOODMAN - CKC49-1A | 112 | 0 | Yes | Yes | 19.2 | 18.5 | 0.7 | 67DE30EC144D4969A0DE56E16F9C18C8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2558 |  | 2015-11-13 | 2015-11-13 10:57 | 2015-11-13 10:57 | CARRIER - UNK | 104 | 0 | Yes | Yes | 18.9 | 19.5 | -0.6 | 677C71CC8F3843A0BB6F0DE5F5040A67 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2146 |  | 2015-07-13 | 2015-07-13 10:12 | 2015-07-13 10:12 | TRANE - 4TTR3048D1000AB | 109 | 0 | Yes | Yes | 17.8 | 18.8 | -1 | D9A54CF50E6F4E9587AEBBC26B5B9E83 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2604 |  | 2015-09-16 | 2015-09-16 13:36 | 2015-09-16 13:36 | GOODMAN - PGB0360751AREVA | 61 | 0 | Yes | Yes | 25.2 | 19.9 | 5.3 | E04794CDBE004DF39C7256AE4F245029 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7004 |  | 2015-09-14 | 2015-09-14 14:36 | 2015-09-14 14:36 | - PH13NR018 | 85 | 0 | Yes | Yes | 14.5 | 15.4 | -0.9 | A7DC8A56905F48469CD639773EC7EB02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2339 |  | 2015-08-31 | 2015-08-31 13:45 | 2015-08-31 13:45 | TEMPSTAR - NPGAD36D1K3 | 78 | 0 | Yes | Yes | 21.7 | 22.1 | -0.4 | CEB92EBA4CB5434F8C7C86FDE5928471 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2268 |  | 2015-10-01 | 2015-10-01 14:42 | 2015-10-01 14:42 | GE - UNK | 85 | 0 | Yes | Yes | 22.1 | 21 | 1.1 | ABBA659BF2B84F3A865A5B5D4789AB8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3113 |  | 2015-09-15 | 2015-09-15 13:34 | 2015-09-15 13:34 | NORDYNE - VR8GD-024K045X | 60 | 0 | Yes | Yes | 22.2 | 19.8 | 2.4 | 381ADC4B587B47EC82331AE7B4CDDD0C |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2001 |  | 2015-09-29 | 2015-09-29 14:13 | 2015-09-29 14:13 | RHEEM - N/A | 85 | 0 | Yes | Yes | 21.3 | 23.1 | -1.8 | 5E3C357B4DF6411B8F66DE143FC0F827 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4027 |  | 2015-09-22 | 2015-09-22 16:18 | 2015-09-22 16:18 | GOODMAN - GPG1324045M41AD | 320 | 0 | Yes | Yes | 23.8 | 21.2 | 2.6 | 1D66CD07AF0F4DF9B6704C37B5A022BA |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4559 |  | 2015-08-31 | 2015-08-31 08:25 | 2015-08-31 08:25 | YORK - D1NH030N05606C | 73 | 0 | Yes | Yes | 21 | 19.4 | 1.7 | 6F0C6C443B42429EBAD64DC270A1F7BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6053 |  | 2015-07-06 | 2015-07-06 09:53 | 2015-07-06 09:53 | - 38CKCA36950 | 70 | 0 | Yes | Yes | 27.9 | 20.7 | 7.2 | D793DFB0015A4CC991E8EE2990F4D90E |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9119 |  | 2015-08-04 | 2015-08-04 12:49 | 2015-08-04 12:49 | CARRIER - 38CKC042300 | 85 | 0 | Yes | Yes | 19.9 | 19.8 | 0.1 | 3E4F26616BC74D51B2E73CD3B0628325 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1674 |  | 2015-09-24 | 2015-09-24 10:41 | 2015-09-24 10:41 | GOODMAN - SSX160241BB | 97 | 0 | Yes | Yes | 14.6 | 16.4 | -1.8 | 36E5120C454E4E5F97A1F8DF943B49C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2006 |  | 2015-11-06 | 2015-11-06 13:02 | 2015-11-06 13:02 | COLEMAN - DAYPF036N070A | 108 | 0 | Yes | Yes | 20 | 19 | 1 | 7DFD650C340F4D9D87008C641313A2E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3051 |  | 2015-09-08 | 2015-09-08 10:35 | 2015-09-08 10:35 | ICP - PGC036K060B | 71 | 0 | Yes | Yes | 19.4 | 17.4 | 2 | A5DA6B95484A4EBDA9A2ECB301AF59B3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4611 |  | 2015-09-16 | 2015-09-16 12:37 | 2015-09-16 12:37 | CARRIER - 48KLA136-321BE | 102 | 0 | Yes | Yes | 24.5 | 19.1 | 5.4 | 5928F5E5233E409D9EAFB5C72D763194 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4731 |  | 2015-09-29 | 2015-09-29 13:11 | 2015-09-29 13:11 | YORK - AY030MA322A | 59 | 0 | Yes | Yes | 21.3 | 20.1 | 1.2 | E0E71C3D91D14D0082F3AB13324B51BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3401 |  | 2015-07-23 | 2015-07-23 10:08 | 2015-07-23 10:08 | TRANE - 4TTR4024A1000AA | 82 | 0 | Yes | Yes | 17.2 | 19.8 | -2.6 | A4EC89F0D5CA4861BAEBAC7204F127A8 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2314 |  | 2015-07-22 | 2015-07-22 08:28 | 2015-07-22 08:28 | CARRIER - 38TKB036330 | 81 | 0 | Yes | Yes | 22.5 | 20.1 | 2.4 | 8810129599FA4A1892F744EFD2C54245 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4964 |  | 2015-08-07 | 2015-08-07 10:15 | 2015-08-07 10:15 | OTHER - H2DB048S06A | 111 | 0 | Yes | Yes | 25.3 | 19.3 | 6 | 133DF683B7084EB09A991AD68C117F80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5627 |  | 2015-07-27 | 2015-07-27 13:36 | 2015-07-27 13:36 | CARRIER - 38EH036300 | 120 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | B06A5540FFC94149AACDE9A4A8E80C1D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1637 |  | 2015-09-01 | 2015-09-01 13:42 | 2015-09-01 13:42 | GOODMAN - SSX160241BB | 97 | 0 | Yes | Yes | 16.3 | 16.4 | -0.1 | F5274C2DD4C9440DB5524567AB6F250B |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1674 |  | 2015-09-14 | 2015-09-14 11:32 | 2015-09-14 11:32 | GOODMAN - SSX160241BB | 88 | 0 | Yes | Yes | 20.4 | 19.1 | 1.3 | E04A872398234C69A1FFAEA7691161CE |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3925 |  | 2015-11-05 | 2015-11-05 11:21 | 2015-11-05 11:21 | RHEEM - UNK | 85 | 0 | Yes | Yes | 21.3 | 18.8 | 2.5 | 8D03A7AD64214629BCC05C275F40D686 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-8731 |  | 2015-10-13 | 2015-10-13 12:00 | 2015-10-13 12:00 | CARRIER - 24ACA480A3D310 | 208 | 0 | Yes | Yes | 19.4 | 21.5 | -2.1 | 4AA3907E68104703A6458C00C0557A36 |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5338 |  | 2015-10-15 | 2015-10-15 14:18 | 2015-10-15 14:18 | CARRIER - 24ABA360A320 | 131 | 0 | Yes | Yes | 26.1 | 23.2 | 2.9 | 34C6631AF8B44D0EBCEA39D752B18BB8 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4866 |  | 2015-09-30 | 2015-09-30 11:25 | 2015-09-30 11:49 | CARRIER - 38TH030310 | 68 | -6.8 | Yes | Yes | 18 | 17.7 | 0.4 | CC712A779528489AB156188E3E136DE5 |  | R22 | Non-TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | Non-TXV |  |  | -10%
Fairfield | CA | 94533-5845 |  | 2015-08-12 | 2015-08-12 13:00 | 2015-08-12 13:00 | TRANE - TTP036D100A0 | 133 | 0 | Yes | Yes | 20 | 19.8 | 0.2 | 9C1C564C21C04E96AE1AA9BD7BDB929D |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5233 |  | 2015-08-17 | 2015-08-17 15:21 | 2015-08-17 15:21 | GOODMAN - GPG1336045M41AC | 85 | 0 | Yes | Yes | 21 | 20.1 | 0.9 | 7CFC08F913914CC3B82DC2CC8DFF65CD |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5482 |  | 2015-09-10 | 2015-09-10 10:18 | 2015-09-10 10:18 | CARRIER - N2A336AKB300 | 85 | 0 | Yes | Yes | 22.2 | 21.5 | 0.7 | E57618EF352A46ECA8627A8B0553C5BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2029 |  | 2015-11-05 | 2015-11-05 09:16 | 2015-11-05 09:16 | BDP - 585C042100 | 85 | 0 | Yes | Yes | 22.3 | 18.5 | 3.9 | 104BD60B73C346FFB2B62C8DEAAE808A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1206 |  | 2015-10-27 | 2015-10-27 13:15 | 2015-10-27 13:15 | BRYANT - 597CN036-D | 98 | 0 | Yes | Yes | 21.7 | 19.3 | 2.4 | 9244A46B5D854A948B85C5F4A4B58455 |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4817 |  | 2015-08-11 | 2015-08-11 16:19 | 2015-08-11 16:19 | RHEEM - 13AJN36A01 | 90.6 | 0 | Yes | Yes | 15.8 | 18.7 | -2.9 | F217F3FC367347049C5E3D3C25BD8DED | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3217 |  | 2015-06-30 | 2015-06-30 11:16 | 2015-06-30 11:16 | WESTINGHOUSE - SF58D042KA | 85 | 0 | Yes | Yes | 22.7 | 19.3 | 3.4 | 0FD7651A7CE54499B9851214C9F031F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-9474 |  | 2015-11-06 | 2015-11-06 12:58 | 2015-11-06 12:58 | RUUD - URKAA048JKL0E | 116 | 0 | Yes | Yes | 21.1 | 17.2 | 3.9 | 5EB28D63F66546E493B1BA45CC0961A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4623 |  | 2015-08-19 | 2015-08-19 10:24 | 2015-08-19 10:52 | AMERICAN STANDARD - YCY030G1M0AD | 126 | 16.3 | Yes | Yes | 21.3 | 21.5 | -0.2 | 4BD2A16BAE0545EFA04A39017D9D043E |  | R22 | Non-TXV |  | 12.94% | 0.87063 | 24.86% | [5 empty] | Non-TXV | 12.94%
Fresno | CA | 93727-9013 |  | 2015-09-24 | 2015-09-24 11:18 | 2015-09-24 11:18 | LENNOX - 13ACD04823003 | 152 | 0 | Yes | Yes | 33 | 19.4 | 13.6 | F07E81A26660410AA0C846E278D92A3E |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5529 |  | 2015-08-27 | 2015-08-27 09:15 | 2015-08-27 09:15 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 15.6 | 14.4 | 1.2 | 0EA049E122C046788F5B1069A278F91A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3032 |  | 2015-09-15 | 2015-09-15 12:22 | 2015-09-15 12:22 | PAYNE - 591ANX042000ABAA | 112 | 0 | Yes | Yes | 19.6 | 17.5 | 2.1 | 1EC3819ED6D549E6B878E64323FB4171 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7156 |  | 2015-08-28 | 2015-08-28 10:22 | 2015-08-28 10:49 | CARRIER - 24ABA330A320 | 64 | -15.1 | Yes | Yes | 19.1 | 19.9 | -0.8 | EC1DB82A74214A9BA825CBDC0D64A9D8 |  | R410A | TXV |  | -23.59% | 1.2359 | 6.607% |  |  |  |  | TXV |  |  | -23.59%
Fresno | CA | 93730-3553 |  | 2015-10-29 | 2015-10-29 15:27 | 2015-10-29 15:27 | WEATHER KING - 10AJA3001 | 70 | 0 | Yes | Yes | 25.2 | 20.2 | 5 | C10A0BF0C85047AFADF3D943FFE01486 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7142 |  | 2015-10-27 | 2015-10-27 10:57 | 2015-10-27 10:57 | CARRIER - UNKNOWN | 104 | 0 | Yes | Yes | 21.4 | 20.4 | 1 | 24621BB83B4F41ADADB2088DEEBC2C21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-3875 |  | 2015-08-20 | 2015-08-20 09:34 | 2015-08-20 10:27 | BDP - 585HJ03060 | 102 | 16.8 | Yes | Yes | 21.8 | 22.5 | -0.7 | 102DF91BEF4949638A71BC50CE7DEF9E |  | R22 | Non-TXV |  | 16.47% | 0.83529 | 31.65% | [5 empty] | Non-TXV | 16.47%
Fresno | CA | 93710-5208 |  | 2015-09-17 | 2015-09-17 13:58 | 2015-09-17 14:23 | OTHER - 60WR24G1NA | 53 | 4.3 | Yes | Yes | 17.6 | 19.3 | -1.7 | 584717D1915A4370911AE20E22DA4353 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.113% | 0.91887 | 15.59% | [5 empty] | Non-TXV | 8.113%
Vacaville | CA | 95687-3207 |  | 2015-07-21 | 2015-07-21 16:36 | 2015-07-21 16:36 | YORK - BRCQ0361CB | 56 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | 48B780C4D03947BDAA3B8B9BB6406AD9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1600 |  | 2015-07-28 | 2015-07-28 12:28 | 2015-07-28 12:28 | CARRIER - 561CJ036-C | 85 | 0 | Yes | Yes | 14.3 | 17.2 | -2.9 | D0736D41118847F6900D57A06E2C7919 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5238 |  | 2015-09-17 | 2015-09-17 14:55 | 2015-09-17 15:19 | OTHER - 60WR24G1NA | 68 | 7.5 | Yes | Yes | 19.2 | 18 | 1.2 | 7D6DD0E9726C4342A7D69FB922C3BA16 |  | R22 | Non-TXV |  | 11.03% | 0.88971 | 21.2% | [5 empty] | Non-TXV | 11.03%
Fresno | CA | 93727-5269 |  | 2015-09-24 | 2015-09-24 15:25 | 2015-09-24 15:25 | CARRIER - 24ABA34BA360 | 85 | 0 | Yes | Yes | 19.2 | 13.7 | 5.5 | 314A1AAF438C43D5A0A2DF3209E74026 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2542 |  | 2015-09-24 | 2015-09-24 14:06 | 2015-09-24 14:06 | RHEEM - N/A | 85 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | DBBEC397D4544857B0EA6BD713379AA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2805 |  | 2015-11-06 | 2015-11-06 12:03 | 2015-11-06 12:03 | OTHER - 38BR036300 | 122 | 0 | Yes | Yes | 23 | 18.4 | 4.7 | 4DEDD35989F2428A90AC4F2E990ACF01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-2115 |  | 2015-08-25 | 2015-08-25 10:17 | 2015-08-25 10:35 | TRANE - 2TTB3024A1000AA | 82 | 5 | Yes | Yes | 18.3 | 18.2 | 0.1 | DC80B916A94B43CD895ED4DC03D2D4D5 |  | R22 | Non-TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | Non-TXV | 6.098%
Vallejo | CA | 94589-1726 |  | 2015-10-05 | 2015-10-05 14:12 | 2015-10-05 14:12 | - DRC30361B | 85 | 0 | Yes | Yes | 14.1 | 16.8 | -2.7 | 19E0EB55920A40B3A7E7D684DDED8120 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4643 |  | 2015-08-25 | 2015-08-25 10:29 | 2015-08-25 10:29 | HEIL - HAC036AKA4 | 88 | 0 | Yes | Yes | 16.7 | 18.1 | -1.4 | B85BC76D593D41B2B97A2E5418BAC164 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-0681 |  | 2015-09-29 | 2015-09-29 13:14 | 2015-09-29 13:14 | RHEEM - UNK | 85 | 0 | Yes | Yes | 18.3 | 19.9 | -1.6 | FDC42DCA43934A3FB2F8FAAAF4495FA8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3403 |  | 2015-09-24 | 2015-09-24 15:56 | 2015-09-24 15:56 | YORK - ACPO30G0701021C | 85 | 0 | Yes | Yes | 23.5 | 19 | 4.5 | A8485195FC9944B5961FEF5B99D121DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9528 |  | 2015-10-16 | 2015-10-16 12:23 | 2015-10-16 12:23 | BDP - 585EJ036075 | 85 | 0 | Yes | Yes | 17.9 | 19.2 | -1.3 | AEAAA06E97E94690BD84B4A1F9C48AE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7130 |  | 2015-11-03 | 2015-11-03 15:55 | 2015-11-03 15:55 | CARRIER - 24ABA324A310 | 74 | 0 | Yes | Yes | 22.7 | 19.9 | 2.8 | B21994E66C7344AEB6BB1EE523DC5C62 |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1487 |  | 2015-09-04 | 2015-09-04 10:02 | 2015-09-04 10:02 | GOODMAN - GSC130421AC | 137 | 0 | Yes | Yes | 21.5 | 18.8 | 2.7 | 1F35202223364ADC8D59B876AF2C7420 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3917 |  | 2015-10-07 | 2015-10-07 10:07 | 2015-10-07 10:07 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 21 | 19.3 | 1.7 | F77914F753524ADA9B3F63BB08506F54 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3827 |  | 2015-09-17 | 2015-09-17 11:53 | 2015-09-17 11:53 | GOODMAN - GPG13240701CB | 74 | 0 | Yes | Yes | 14.7 | 15.7 | -1 | E392B5D5899448B89876A9813FC6F839 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2112 |  | 2015-09-11 | 2015-09-11 15:24 | 2015-09-11 15:24 | CARRIER - 38EN036340 | 100 | 0 | Yes | Yes | 22.4 | 21.5 | 0.9 | B04C0870BBB148A896229AA4B67CE42F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-0000 |  | 2015-10-16 | 2015-10-16 14:52 | 2015-10-16 14:52 | CARRIER - 24ABB330W316 | 74 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | 233BE516E5D2462E96FD0FB8850C3F08 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5006 |  | 2015-09-29 | 2015-09-29 09:19 | 2015-09-29 09:19 | YORK - D1NA036N05606C | 67 | 0 | Yes | Yes | 20.8 | 21.5 | -0.7 | C78E9A4D97304E3FA4AD3401181518A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6922 |  | 2015-09-18 | 2015-09-18 08:29 | 2015-09-18 08:29 | AMANA - APG1324045M41DA | 75 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | 74C63993B1C1491C87145C69F55575C2 |  | R410A | TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1373 |  | 2015-10-16 | 2015-10-16 11:38 | 2015-10-16 11:38 | CARRIER - 24ABB320W310 | 74 | 0 | Yes | Yes | 21.9 | 19.8 | 2.1 | 91774AF611D348449A1354046AF3E2AF |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5843 |  | 2015-08-19 | 2015-08-19 12:05 | 2015-08-19 12:05 | DAY & NIGHT - 561ANX0030000ABAA | 68 | 0 | Yes | Yes | 19.3 | 18.2 | 1.1 | 27568E8D13284DB7AD55566C2F9877FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7133 |  | 2015-09-04 | 2015-09-04 11:14 | 2015-09-04 11:14 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 17.7 | 19.5 | -1.8 | F7397D93E7974FACBAE5D9DB9C2D49CD |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5116 |  | 2015-11-06 | 2015-11-06 08:36 | 2015-11-06 08:56 | LENNOX - 12ACB603P | 85 | 30.4 | Yes | Yes | 18.9 | 13.7 | 5.3 | E89BB895AB424250BC2DE98C21419122 |  | R22 | Non-TXV |  | 35.76% | 0.64235 | 68.73% | [5 empty] | Non-TXV | 35.76%
Bakersfield | CA | 93309-4165 |  | 2015-09-16 | 2015-09-16 08:26 | 2015-09-16 09:12 | YORK - H4DH042S06A | 108 | 6.8 | Yes | Yes | 21.4 | 22.3 | -0.8 | E6BB6173029F4502AB034AB4CE04E1BD |  | R22 | Non-TXV |  | 6.296% | 0.93704 | 12.1% | [5 empty] | Non-TXV | 6.296%
Fresno | CA | 93706-9144 |  | 2015-09-18 | 2015-09-18 14:50 | 2015-09-18 14:50 | YORK - DBYP-F030N070A | 73 | 0 | Yes | Yes | 21.7 | 19.8 | 1.9 | F799B4DB94FE409DA9F981A1C3BB51A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6325 |  | 2015-09-24 | 2015-09-24 14:12 | 2015-09-24 14:12 | GOODMAN - CKL42-1B | 85 | 0 | Yes | Yes | 19.9 | 19.5 | 0.4 | 9210259F13704C70995866D5E0A2A78B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1678 |  | 2015-09-17 | 2015-09-17 11:00 | 2015-09-17 11:00 | OTHER - N/A | 85 | 0 | Yes | Yes | 20.2 | 17 | 3.2 | 0DD7BABB6008499595E4244DE1988CD0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2034 |  | 2015-08-17 | 2015-08-17 11:37 | 2015-08-17 11:37 | RHEEM - RAMA-O36JAZ | 96 | 0 | Yes | Yes | 19.3 | 21.4 | -2.1 | 11F1EA31A03C4CE7B1592E0F94547F6C |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6214 |  | 2015-09-29 | 2015-09-29 09:39 | 2015-09-29 09:59 | ICP - PGAA36C1K6 | 69 | 14.7 | Yes | Yes | 20.6 | 21.9 | -1.3 | 8AC230E5F2824B6E9C1574F0BA8AE3A8 |  | R22 | Non-TXV |  | 21.3% | 0.78696 | 40.94% | [5 empty] | Non-TXV | 21.3%
Bakersfield | CA | 93306-7920 |  | 2015-08-25 | 2015-08-25 10:00 | 2015-08-25 10:18 | YORK - AC036X1222A | 83 | 19.6 | Yes | Yes | 21.5 | 21 | 0.5 | A25677D4A75147C3B44E03F6D482FC21 |  | R22 | Non-TXV |  | 23.61% | 0.76386 | 45.38% | [5 empty] | Non-TXV | 23.61%
Fairfield | CA | 94533-4528 |  | 2015-08-14 | 2015-08-14 09:42 | 2015-08-14 10:05 | CARRIER - 24ABA336A300 | 85 | 16.8 | Yes | Yes | 21.7 | 17.7 | 4 | 943F314DC63D41B8B87141AB7FA032D9 |  | R410A | TXV |  | 19.76% | 0.80235 | 37.98% | [5 empty] | TXV | 19.76%
Fresno | CA | 93706-0000 |  | 2015-09-21 | 2015-09-21 10:26 | 2015-09-21 10:26 | BRYANT - 116BNA036-A | 103 | 0 | Yes | Yes | 19.4 | 19.6 | -0.2 | EBBBB6E6D5594D10A51C147933DC25FC |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-9326 |  | 2015-09-14 | 2015-09-14 09:37 | 2015-09-14 09:37 | BRYANT - 582ANW024040AAAD | 55 | 0 | Yes | Yes | 20.3 | 19.9 | 0.4 | B1DCD7F7FACA4848BABDB028B395A8AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6332 |  | 2015-09-21 | 2015-09-21 13:34 | 2015-09-21 16:05 | RHEEM - RAND048JBZ | 146 | 0 | Yes | Yes | 0 | N/A | N/A | E1866727880346D08B6613F135C1183E |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2636 |  | 2015-10-01 | 2015-10-01 13:08 | 2015-10-01 13:08 | RHEEM - RRKA-A042JK08X | 85 | 0 | Yes | Yes | 21.5 | 18.7 | 2.8 | 2BB78F3E4F7743149BCC545B542A87C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2040 |  | 2015-08-20 | 2015-08-20 16:12 | 2015-08-20 16:12 | RHEEM - UNK | 85 | 0 | Yes | Yes | 20.9 | 20.6 | 0.3 | 858D9BC6E86A43AF9229A6E5435A4150 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1136 |  | 2015-10-07 | 2015-10-07 08:23 | 2015-10-07 08:23 | RUUD - N/A | 85 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | D30C980559B94FD5923F7D7D2524A661 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2401 |  | 2015-09-09 | 2015-09-09 12:25 | 2015-09-09 12:25 | YORK - D1NA024NO3606C | 54 | 0 | Yes | Yes | 19.4 | 19.1 | 0.3 | 1C71E566677F490A82FA74948648C0DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5899 |  | 2015-09-21 | 2015-09-21 14:49 | 2015-09-21 14:49 | CARRIER - CA13NAO42A | 98 | 0 | Yes | Yes | 39.1 | 22.6 | 16.5 | 022CD1B4C06643A184410884936E29FD |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-9525 |  | 2015-11-09 | 2015-11-09 10:13 | 2015-11-09 10:13 | CARRIER - 588ANW060100AEAG | 85 | 0 | Yes | Yes | 18.9 | 16.3 | 2.6 | A88CDEDD792D41E98C61961EDF098944 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6039 |  | 2015-08-19 | 2015-08-19 15:46 | 2015-08-19 15:46 | CARRIER - 38BRC036320 | 85 | 0 | Yes | Yes | 23.2 | 17.7 | 5.6 | BEEC069930E548B6B4C04022D924CD61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4505 |  | 2015-11-06 | 2015-11-06 12:41 | 2015-11-06 12:41 | BDP - UNKNOWN | 103 | 0 | Yes | Yes | 16.8 | 18.8 | -2 | C4FC5284EBA8487C8609CDDE3E57651C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6493 |  | 2015-09-21 | 2015-09-21 11:51 | 2015-09-21 11:51 | LENNOX - 12ACB485P | 171 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 958948B106A245D2A4EB3FD6663BB60C |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5129 |  | 2015-07-02 | 2015-07-02 14:01 | 2015-07-02 14:01 | RUUD - UANB042JAZ | 157 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | CC5F32917775426DB03E3B3D33C6C90C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2223 |  | 2015-10-14 | 2015-10-14 15:40 | 2015-10-14 15:40 | CARRIER - UNK | 85 | 0 | Yes | Yes | 21.4 | 22.4 | -1 | 7F98F25ADC284152A2EC7997CDAB8735 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4403 |  | 2015-09-15 | 2015-09-15 14:46 | 2015-09-15 14:46 | CARRIER - 48NLT | 85 | 0 | Yes | Yes | 19 | 17.2 | 1.8 | A8D29CBD306A4D1D8F7071A389C02CF2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7905 |  | 2015-10-13 | 2015-10-13 14:33 | 2015-10-13 14:33 | - N/A | 85 | 0 | Yes | Yes | 22.3 | 21.4 | 0.9 | 2F9BADD8110741EF91EE2911976EA097 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3523 |  | 2015-09-28 | 2015-09-28 11:09 | 2015-09-28 11:09 | AMERICAN STANDARD - YCP030F1M0AC | 106 | 0 | Yes | Yes | 17.2 | 19.7 | -2.5 | 09689C776E1A4B74839AF434537A45EB |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2685 |  | 2015-08-27 | 2015-08-27 12:19 | 2015-08-27 12:19 | RUUD - N/A | 85 | 0 | Yes | Yes | 24.8 | 20.1 | 4.7 | 052727494B284DF885DEA87F94AF90F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6943 |  | 2015-08-18 | 2015-08-18 13:26 | 2015-08-18 13:52 | CARRIER - 38BRC030310 | 100 | 6.8 | Yes | Yes | 21.7 | 20.8 | 0.9 | 8C8392F389274EFE9DD1942568922B49 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.8% | 0.932 | 13.07% | [5 empty] | Non-TXV | 6.8%
Woodland | CA | 95695-0000 |  | 2015-10-02 | 2015-10-02 16:27 | 2015-10-02 16:27 | INTERTHERM - S3QA036KA | 69 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | E78A7AB3D05E46CE8D77D3F45870477D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3295 |  | 2015-08-13 | 2015-08-13 16:12 | 2015-08-13 16:12 | CARRIER - 38ENO24310SM | 56 | 0 | Yes | Yes | 21.7 | 19.7 | 2 | 1EFC336F551D4E169595749CB2EB7FD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4692 |  | 2015-11-09 | 2015-11-09 12:15 | 2015-11-09 12:47 | OTHER - H2RC042S06HA | 109 | 24.6 | Yes | Yes | 20.3 | 20.4 | -0.1 | D0F48A4046EE4A04A46560AAB1B4897D |  | R22 | Non-TXV |  | 22.57% | 0.77431 | 43.37% | [5 empty] | Non-TXV | 22.57%
Fresno | CA | 93728-1061 |  | 2015-11-24 | 2015-11-24 08:59 | 2015-11-24 08:59 | OTHER - PYGNAA30060NA | 100 | 0 | Yes | Yes | 21.3 | 16.9 | 4.4 | 8ACEA80BADE149F8ADEF961CF70119BC |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4340 |  | 2015-11-06 | 2015-11-06 13:42 | 2015-11-06 13:59 | CARRIER - 585CJ036075 | 83 | 32.8 | Yes | Yes | 19.2 | 19.7 | -0.5 | 187013AB9E1E4BF6A287C6662C3FB567 |  | R22 | Non-TXV |  | 39.52% | 0.60482 | 75.95% | [5 empty] | Non-TXV | 39.52%
Fairfield | CA | 94533-2656 |  | 2015-08-12 | 2015-08-12 15:29 | 2015-08-12 15:29 | BRYANT - 113ANA042C | 92 | 0 | Yes | Yes | 17.7 | 19.4 | -1.7 | 9CC3296098F84FE497530DD3DD6605BF |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2424 |  | 2015-10-09 | 2015-10-09 13:17 | 2015-10-09 13:17 | GOODMAN - PGB024050-1 | 54 | 0 | Yes | Yes | 21.1 | 19.8 | 1.3 | 630C884FF8C14CD989FBB96468DCA252 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9397 |  | 2015-10-30 | 2015-10-30 11:26 | 2015-10-30 11:45 | UNITARY PRODUCTS GROUP - H2RC036S06G | 83 | 8.2 | Yes | Yes | 19.1 | 19.3 | -0.2 | 0132248AA0F042C8B88F3312E029210E |  | R22 | TXV |  | 9.88% | 0.9012 | 18.99% | [5 empty] | TXV | 9.88%
Brentwood | CA | 94513-7142 |  | 2015-09-09 | 2015-09-09 13:46 | 2015-09-09 13:46 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 19.5 | 19.8 | -0.3 | CF4B7927AFCB4B8CA87D478C789EEF15 |  | R410A | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7145 |  | 2015-09-12 | 2015-09-12 14:32 | 2015-09-12 14:32 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 17.7 | 19.9 | -2.2 | A0900A7552A9403EBE11CAD7AC19CDFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-7407 |  | 2015-08-28 | 2015-08-28 08:48 | 2015-08-28 09:07 | CARRIER - 563CN048-H | 136 | 9.9 | Yes | Yes | 19.2 | 18.3 | 1 | F5BA47BD6E3841B4AF8FECAABEBE14B4 |  | R22 | TXV |  | 7.279% | 0.92721 | 13.99% | [5 empty] | TXV | 7.279%
Fresno | CA | 93702-3530 |  | 2015-09-18 | 2015-09-18 09:34 | 2015-09-18 09:34 | BDP - 585A030080YAC | 51 | 0 | Yes | Yes | 20.7 | 21.3 | -0.5 | 77D23EAFC38B4EC4B379009900F4D67E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2740 |  | 2015-10-20 | 2015-10-20 10:55 | 2015-10-20 10:55 | TRANE - TTB030C100 | 73 | 0 | Yes | Yes | 14.8 | 17.6 | -2.8 | 3FB0D4C4774A46BCADA692D4576ACAD2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4395 |  | 2015-08-26 | 2015-08-26 14:53 | 2015-08-26 14:53 | UNITARY PRODUCTS GROUP - AC048X1221A | 122 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 24A9CFF0C04E4F018AFD38523BEB4459 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2906 |  | 2015-11-05 | 2015-11-05 12:53 | 2015-11-05 12:53 | BRYANT - 582ANW030060AAAD | 55 | 0 | Yes | Yes | 18.7 | 19.4 | -0.7 | 8A966170AE6341B4854F5EDF3602C98C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7904 |  | 2015-08-25 | 2015-08-25 10:17 | 2015-08-25 10:40 | OTHER - AC036X1021A | 63 | 9.9 | Yes | Yes | 21.6 | 22.6 | -1 | B4A1287B1FBA447A9DCF00F25445D7B0 |  | R22 | Non-TXV |  | 15.71% | 0.84286 | 30.2% | [5 empty] | Non-TXV | 15.71%
Kerman | CA | 93630-9175 |  | 2015-10-29 | 2015-10-29 12:55 | 2015-10-29 12:55 | TRANE - YCC036F1M0BK | 85 | 0 | Yes | Yes | 18.4 | 19.7 | -1.3 | 50B2D3939CD4413DA1BABC6E67D4E3D3 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7125 |  | 2015-09-24 | 2015-09-24 15:35 | 2015-09-24 15:35 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 16 | 18.8 | -2.8 | 3ADF881ED58246C7A040CEFC52410033 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7026 |  | 2015-11-06 | 2015-11-06 10:18 | 2015-11-06 10:18 | OTHER - PA13A036B | 73 | 0 | Yes | Yes | 24.7 | 19.7 | 5 | FD6648ABEB094AC8BDBFBE3108D7BDBA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3441 |  | 2015-09-09 | 2015-09-09 16:01 | 2015-09-09 16:19 | LENNOX - 13ACC-060-230-01 | 168 | 14.8 | Yes | Yes | 20.3 | 21.7 | -1.4 | 8F7E6F87DCD24FBB91E558B1B6D79998 |  | R22 | TXV |  | 8.81% | 0.9119 | 16.93% | [5 empty] | TXV | 8.81%
Fresno | CA | 93722-8010 |  | 2015-11-05 | 2015-11-05 10:30 | 2015-11-05 10:30 | YORK - H2RC030506HG | 88 | 0 | Yes | Yes | 21 | 17.7 | 3.3 | 4C6B25E5270245CF9B8F1E2F69BF3023 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4425 |  | 2015-07-28 | 2015-07-28 12:12 | 2015-07-28 12:32 | TRANE - TTNO30C100C2 | 95 | 9.5 | Yes | Yes | 20.5 | 19.9 | 0.6 | 3477B096909640B584D9A1B4EA20270B |  | R22 | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Fresno | CA | 93725-4005 |  | 2015-11-05 | 2015-11-05 12:05 | 2015-11-05 12:05 | OTHER - 24ABA342A3601806E26257 | 102 | 0 | Yes | Yes | 25.6 | 19.6 | 6 | C56F42DB93CA488789FBF0271B4BDE02 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1629 |  | 2015-08-24 | 2015-08-24 08:39 | 2015-08-24 08:39 | TRANE - 4TTM3030A1000AA | 66 | 0 | Yes | Yes | 23.9 | 19.1 | 4.8 | CF2916E3F00F40DD81DB9669B75308A4 |  | R410A | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1314 |  | 2015-09-17 | 2015-09-17 13:06 | 2015-09-17 13:06 | GIBSON - JT5BD030KA | 144 | 0 | Yes | Yes | 17.9 | 16.4 | 1.5 | D24CA4E20FB140DAAB3A53556829CEBF |  | R22 | TXV |  | 0% | 1 | 0%
Danville | CA | 94526-1806 |  | 2015-08-10 | 2015-08-10 09:11 | 2015-08-10 09:11 | GOODMAN - GPH1330M41AA | 115 | 0 | Yes | Yes | 26.1 | 22 | 4.1 | 1D04F84394C744EB80B9FFFE6C106316 |  | R410A | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3920 |  | 2015-08-31 | 2015-08-31 09:41 | 2015-08-31 09:41 | COLEMAN - | 85 | 0 | Yes | Yes | 15 | 14.4 | 0.6 | 56CEC79B96C346C686D122085936E5AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8731 |  | 2015-09-23 | 2015-09-23 13:30 | 2015-09-23 13:30 | YORK - DINA036N036 | 67 | 0 | Yes | Yes | 18.7 | 21 | -2.3 | 666FD2281655424B9F67DA4EB4DD4F15 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2677 |  | 2015-08-27 | 2015-08-27 09:19 | 2015-08-27 09:19 | RUUD - N/A | 85 | 0 | Yes | Yes | 18.2 | 18.7 | -0.5 | F2B36760C2704DBC8F20A0CEED9B0AB0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-6734 |  | 2015-09-25 | 2015-09-25 10:16 | 2015-09-25 10:16 | COMFORT AIRE - NAC048AKC3 | 111 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | A6B3AAA24BC447C1AD9746BE608503AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5035 |  | 2015-08-31 | 2015-08-31 12:56 | 2015-08-31 12:56 | RHEEM - RRNL-B036JK06X | 93 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | A50730CA70B440FCBFCA4C7C3C9EDA40 |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3615 |  | 2015-07-30 | 2015-07-30 09:52 | 2015-07-30 09:52 | DAY & NIGHT - 30DNR-10BC | 68 | 0 | Yes | Yes | 17.8 | 18.8 | -1 | 10037ED0405543CC85FE004F90B24201 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-3271 |  | 2015-08-28 | 2015-08-28 09:35 | 2015-08-28 09:53 | CARRIER - 38CK024320 | 69 | 6 | Yes | Yes | 18 | 18.2 | -0.2 | B54F3C79150B4D28B5B00F57957C7886 |  | R22 | TXV |  | 8.696% | 0.91304 | 16.71% | [5 empty] | TXV | 8.696%
Clovis | CA | 93619-4652 |  | 2015-09-17 | 2015-09-17 09:28 | 2015-09-17 09:46 | BRYANT - 563CN036-D | 101 | 5.8 | Yes | Yes | 18.6 | 16.4 | 2.2 | 2BC2BE537A8F483CA44AFF440E8FDDF3 |  | R22 | TXV |  | 5.743% | 0.94257 | 11.04% | [5 empty] | TXV | 5.743%
Fresno | CA | 93705-4403 |  | 2015-09-04 | 2015-09-04 09:21 | 2015-09-04 09:21 | PAYNE - 48RAC-158C | 103 | 0 | Yes | Yes | 20.3 | 19.3 | 1 | B49B7E90ED53445399768E2D5F2C1208 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1514 |  | 2015-09-04 | 2015-09-04 13:16 | 2015-09-04 13:16 | YORK - D1NP036N05606A | 110 | 0 | Yes | Yes | 22.4 | 22.3 | 0.1 | D2199104FBC54778A8B519BE10B477E3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7603 |  | 2015-09-12 | 2015-09-12 15:11 | 2015-09-12 15:30 | CARRIER - 38BRC036 331 | 101 | 5.9 | Yes | Yes | 17.8 | 20.4 | -2.6 | 24D14F912E6C41B3B83730DFE98CF23C | Add refrigerant: 6.9 oz | R22 | TXV |  | 5.842% | 0.94158 | 11.23% | [5 empty] | TXV | 5.842%
Woodland | CA | 95776-5336 |  | 2015-10-14 | 2015-10-14 15:39 | 2015-10-14 15:39 | CARRIER - 24ABA336A310 | 85 | 0 | Yes | Yes | 23.4 | 18.5 | 4.9 | 26A6607472B842F4A02EA0DD8EF994AB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4638 |  | 2015-08-13 | 2015-08-13 13:34 | 2015-08-13 13:34 | TRANE - 2TTBOO48A1000AA | 109 | 0 | Yes | Yes | 24.7 | 20.4 | 4.3 | A28FB9168F284472BC4CD13342ECA19D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3304 |  | 2015-11-05 | 2015-11-05 13:04 | 2015-11-05 13:04 | OTHER - 80WR30A0NA | 52 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | 07608A1E5CAA4B108FEBC61142B4F23C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3116 |  | 2015-08-13 | 2015-08-13 14:19 | 2015-08-13 14:19 | OTHER - PA13NA024B | 63 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | D23B20D5B466473D939ED6E506462C67 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5846 |  | 2015-08-31 | 2015-08-31 14:38 | 2015-08-31 14:57 | CARRIER - N/A | 85 | 8.2 | Yes | Yes | 20.4 | 19.9 | 0.5 | F9878FDBC5E944078ACC8CFB6DC0B7EA |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Hercules | CA | 94547-3852 |  | 2015-07-29 | 2015-07-29 13:07 | 2015-07-29 13:07 | TRANE - MTD718A100B0 | 46 | 0 | Yes | Yes | 16.6 | 19.5 | -2.9 | 16AECCCC83954764ABC4C7C73319B437 |  | R22 | TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3278 |  | 2015-08-20 | 2015-08-20 13:58 | 2015-08-20 14:16 | LENNOX - 13ACC-060-230-02 | 168 | 9.1 | Yes | Yes | 17.8 | 20.2 | -2.4 | B2BD9E08092C4533B523BBD0B1F95EB8 |  | R22 | TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | TXV | 5.417%
Benicia | CA | 94510-1728 |  | 2015-07-30 | 2015-07-30 09:40 | 2015-07-30 09:40 | TRANE - TTP048D100A0 | 131 | 0 | Yes | Yes | 18.4 | 17.7 | 0.7 | 3A5787F0C2F249E680B3752292E77F72 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5531 |  | 2015-08-10 | 2015-08-10 10:58 | 2015-08-10 10:58 | RHEEM - RAMB-060JBZ | 192 | 0 | Yes | Yes | 22.7 | 21.2 | 1.6 | 0B0A64F59C004061924C4FB1F12DD937 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7900 |  | 2015-11-05 | 2015-11-05 11:29 | 2015-11-05 11:29 | LENNOX - 10GCS042X753PA | 73 | 0 | Yes | Yes | 24.7 | 20.3 | 4.4 | 282ED656CAA24206AC5C171920F0B7AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pinole | CA | 94564-1155 |  | 2015-07-14 | 2015-07-14 11:57 | 2015-07-14 11:57 | YORK - H2RA036506A | 63 | 0 | Yes | Yes | 16.5 | 18.1 | -1.6 | 7BAFA4FB71204683B431B49090F6F245 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pinole | CA | 94564-1155 |  | 2015-07-14 | 2015-07-14 12:30 | 2015-07-14 12:30 | GOODMAN - CK36-1D | 72 | 0 | Yes | Yes | 16.8 | 18.3 | -1.5 | 17549B0E138E4BAAB48474520EBBF9D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6945 |  | 2015-08-12 | 2015-08-12 10:10 | 2015-08-12 10:10 | YORK - D1NH042N06506C | 94 | 0 | Yes | Yes | 22.3 | 22.8 | -0.5 | 5203E39DFC33496992F9FE8B533E951E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4267 |  | 2015-09-10 | 2015-09-10 14:11 | 2015-09-10 14:11 | OTHER - H2RD042S06B | 141 | 0 | Yes | Yes | 18.9 | 19.2 | -0.3 | CAC0E23D67E245F28C840EBC4D5894F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7167 |  | 2015-09-29 | 2015-09-29 10:02 | 2015-09-29 10:02 | BDP - 585EJW036075 | 82 | 0 | Yes | Yes | 20.6 | 22.1 | -1.5 | 66EB0E26F9764A7191A8FDC3EFE6E19C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-6741 |  | 2015-07-22 | 2015-07-22 17:03 | 2015-07-22 17:03 | YORK - H1RA048SO6D | 85 | 0 | Yes | Yes | 21.2 | 23.5 | -2.3 | C902F31D288B467BA2CC813E8C151C69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-1800 |  | 2015-08-04 | 2015-08-04 10:50 | 2015-08-04 10:50 | YORK - H2RA036S06E | 63 | 0 | Yes | Yes | 16.4 | 18.8 | -2.4 | C577BBC7C8F744F9B010A2492C44A23B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2930 |  | 2015-10-05 | 2015-10-05 10:03 | 2015-10-05 10:03 | LENNOX - GCS20R030753P | 74 | 0 | Yes | Yes | 24.4 | 20.2 | 4.2 | 2B1A9E88280E4EECB4BB1C60B44ED38E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3130 |  | 2015-08-26 | 2015-08-26 16:53 | 2015-08-26 16:53 | RHEEM - RRKA--A042JK08X | 69 | 0 | Yes | Yes | 19.1 | 21.4 | -2.3 | 5091B4B10442410D92C41ABD7E2E3C04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7145 |  | 2015-11-06 | 2015-11-06 10:40 | 2015-11-06 10:40 | YORK - HID5036506A | 136 | 0 | Yes | Yes | 18.5 | 13.7 | 4.9 | D5AF8E85691A4A5F855C6D6938074FE5 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4936 |  | 2015-08-12 | 2015-08-12 15:32 | 2015-08-12 15:32 | GOODMAN - GPG1324045M41DA | 75 | 0 | Yes | Yes | 19.4 | 21.5 | -2.1 | 2D3839DE342844DEAC5354F559D51D75 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1467 |  | 2015-09-08 | 2015-09-08 13:32 | 2015-09-08 13:32 | CARRIER - 38TXA036330 | 109 | 0 | Yes | Yes | 17.8 | 20.7 | -2.9 | D3F9D5CB10A14E03AB773B9CB5626E61 |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2035 |  | 2015-09-10 | 2015-09-10 12:33 | 2015-09-10 12:33 | RHEEM - RK-030J | 66 | 0 | Yes | Yes | 14.5 | 17.4 | -2.9 | 6338D82A934A4F1AA699F53C890230D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1028 |  | 2015-10-13 | 2015-10-13 13:51 | 2015-10-13 14:11 | AMERICAN STANDARD - 2A7B3042A1000AA | 85 | 5.3 | Yes | Yes | 18.8 | 20 | -1.2 | 05A0BB9E11D94B1D901504999E557FFD |  | R22 | TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | TXV | 6.235%
Bakersfield | CA | 93309-5556 |  | 2015-09-15 | 2015-09-15 15:49 | 2015-09-15 15:49 | UNITARY PRODUCTS GROUP - D1NA030N05606C | 76 | 0 | Yes | Yes | 20.8 | 20.4 | 0.4 | 434CD41E86F546C394BE711A3F1609BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3174 |  | 2015-09-29 | 2015-09-29 08:48 | 2015-09-29 09:21 | OTHER - AC030M1021CA | 57 | 6.7 | Yes | Yes | 20 | 20.9 | -0.9 | 188F373327D6459B9DDA3987E9A24F87 |  | R22 | Non-TXV |  | 11.75% | 0.88246 | 22.59% | [5 empty] | Non-TXV | 11.75%
Bakersfield | CA | 93307-3751 |  | 2015-08-12 | 2015-08-12 09:40 | 2015-08-12 09:48 | OTHER - N/A | 85 | 12.8 | Yes | Yes | 21.7 | 22 | -0.3 | 0E13D9BB3B6D4CE79E7840C9169A5027 |  | R22 | Non-TXV |  | 15.06% | 0.84941 | 28.94% | [5 empty] | Non-TXV | 15.06%
Fresno | CA | 93711-2135 |  | 2015-10-02 | 2015-10-02 11:39 | 2015-10-02 11:39 | AMERICAN STANDARD - YCZ036F1MOBD | 85 | 0 | Yes | Yes | 25.6 | 19.9 | 5.7 | F031613B84D54C6C85B758CE5643C093 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3913 |  | 2015-10-08 | 2015-10-08 14:39 | 2015-10-08 14:39 | RHEEM - N/A | 85 | 0 | Yes | Yes | 22.5 | 19.7 | 2.8 | 2D6F3A1EC33A4C1F87F9A4A97BEBE61F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6484 |  | 2015-10-01 | 2015-10-01 14:21 | 2015-10-01 14:21 | OTHER - H1RA048S06G | 117 | 0 | Yes | Yes | 19.4 | 20.2 | -0.7 | 236A6FF8238048B1ADFA791378BBFF3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3542 |  | 2015-08-26 | 2015-08-26 09:58 | 2015-08-26 09:58 | BDP - 588ANW042060ACAG | 83 | 0 | Yes | Yes | 24.1 | 19 | 5.1 | BDD91665186D4B339C7B9A3EABF9BB3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3542 |  | 2015-08-26 | 2015-08-26 10:02 | 2015-08-26 10:02 | BDP - 585CJ018050 | 70 | 0 | Yes | Yes | 20.7 | 22.1 | -1.4 | 6B0F1B718B094CFD8355452C01C9C669 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1526 |  | 2015-06-25 | 2015-06-25 12:42 | 2015-06-25 12:42 | OTHER - BTR736B100AO | 160 | 0 | Yes | Yes | 20.6 | 19 | 1.6 | 7E1D336D2EF7498FA78BE1366586EA4C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1510 |  | 2015-08-17 | 2015-08-17 11:38 | 2015-08-17 11:38 | PAYNE - PA13NA024 | 63 | 0 | Yes | Yes | 17.6 | 20.2 | -2.6 | 61A8C9088DB94B63842F2DE759E24FEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7147 |  | 2015-09-09 | 2015-09-09 12:35 | 2015-09-09 12:35 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 16.6 | 19.3 | -2.7 | 406CECEE83D1450A9CA4A8D302AD2D8F |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1535 |  | 2015-08-21 | 2015-08-21 15:55 | 2015-08-21 16:16 | CARRIER - 589ANW042060ADBP | 87 | 21 | Yes | Yes | 20.7 | 20.1 | 0.6 | 3FC6FDBA43CA45B9813876A17CEBAFA6 |  | R22 | Non-TXV |  | 24.14% | 0.75862 | 46.39% | [5 empty] | Non-TXV | 24.14%
Bakersfield | CA | 93304-2642 |  | 2015-09-29 | 2015-09-29 12:09 | 2015-09-29 12:09 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 20.7 | 20.7 | 0 | FA7F686F59A14D8A9E31DF23206B9CE9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6830 |  | 2015-10-06 | 2015-10-06 15:42 | 2015-10-06 15:42 | RHEEM - RRNA-B042JK08X | 104 | 0 | Yes | Yes | 20.9 | 22.1 | -1.2 | FC876E7549E449F590D7E393E68D377E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4111 |  | 2015-11-06 | 2015-11-06 14:05 | 2015-11-06 14:05 | YORK - D1H030N05606C | 73 | 0 | Yes | Yes | 18.3 | 19.9 | -1.6 | D1AAB8988CA3415C93565D9A00E172D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7615 |  | 2015-10-05 | 2015-10-05 11:55 | 2015-10-05 11:55 | CARRIER - 38CKC048370 | 99 | 0 | Yes | Yes | 18.2 | 20.2 | -2 | E5D5956959694945BDF8C2650E469CE2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5120 |  | 2015-10-27 | 2015-10-27 11:38 | 2015-10-27 11:38 | FRIGIDAIRE - FS3BA042KA | 87 | 0 | Yes | Yes | 20 | 21.4 | -1.4 | 5AA3D835415848F0A0FE9DC5E2E6408D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7112 |  | 2015-11-03 | 2015-11-03 09:58 | 2015-11-03 09:58 | YORK - UNK | 85 | 0 | Yes | Yes | 16.1 | 18.2 | -2.1 | 4B775564AE2844BA8DB8923CC819FC64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1954 |  | 2015-09-09 | 2015-09-09 14:05 | 2015-09-09 14:05 | BRYANT - 113RNA030B | 84 | 0 | Yes | Yes | 19.6 | 21.2 | -1.6 | F3725A11F42E462C84B53D09CC74A9C2 |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1954 |  | 2015-10-02 | 2015-10-02 14:06 | 2015-10-02 14:06 | BRYANT - 113RNA030B | 84 | 0 | Yes | Yes | 17.2 | 19.9 | -2.7 | 08BAF5D32A714CFB874143DDD8F6E9C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2829 |  | 2015-10-29 | 2015-10-29 15:35 | 2015-10-29 15:35 | PAYNE - PY1PNB30060AAAA | 55 | 0 | Yes | Yes | 19.9 | 21.2 | -1.3 | FA0542FF850341CF97038D1FCB6445C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4158 |  | 2015-07-20 | 2015-07-20 11:30 | 2015-07-20 11:30 | YORK - TC6D2454153HA | 61 | 0 | Yes | Yes | 16.2 | 18.3 | -2.1 | DDC4F7C772D944CFA1FAD7230C7F0039 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4516 |  | 2015-07-17 | 2015-07-17 08:40 | 2015-07-17 08:40 | CARRIER - CK49-1 | 85 | 0 | Yes | Yes | 20.2 | 17.9 | 2.3 | 85069DB622EB4716BA3429EDF5327889 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2721 |  | 2015-09-30 | 2015-09-30 12:22 | 2015-09-30 12:22 | OTHER - N/A | 85 | 0 | Yes | Yes | 22.4 | 23.1 | -0.7 | 035218EAB80E45EA9D41989F90AB701F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4920 |  | 2015-08-17 | 2015-08-17 13:19 | 2015-08-17 13:19 | YORK - DAYA-FO2N045C | 54 | 0 | Yes | Yes | 18.2 | 21.7 | -3.5 | A5FAFD5609784CD68127C291794AA798 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3748 |  | 2015-08-12 | 2015-08-12 09:49 | 2015-08-12 09:49 | OTHER - N/A | 85 | 0 | Yes | Yes | 20.5 | 22.9 | -2.4 | AB268423C8C947E8B562876E4996C478 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3810 |  | 2015-08-10 | 2015-08-10 12:16 | 2015-08-10 12:16 | COLEMAN - 2436-901 | 62 | 0 | Yes | Yes | 24.2 | 21.3 | 2.9 | 814E3F0D65444D3EB69904442ADB42EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3810 |  | 2015-11-03 | 2015-11-03 14:41 | 2015-11-03 14:41 | BDP - 585801050YACR | 69 | 0 | Yes | Yes | 18.7 | 18.9 | -0.2 | 261BD50020AE4F5BB79C3DC1BFA457C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0257 |  | 2015-09-04 | 2015-09-04 17:37 | 2015-09-04 17:37 | RHEEM - N/A | 85 | 0 | Yes | Yes | 18.7 | 20.9 | -2.2 | 616E4AB74D14401891CBE22A2D4EDAB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9110 |  | 2015-07-23 | 2015-07-23 11:34 | 2015-07-23 11:34 | - | 85 | 0 | Yes | Yes | 16.5 | 18.8 | -2.3 | 35097D9645D54218B54EA257C9DEAE33 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5109 |  | 2015-09-14 | 2015-09-14 11:59 | 2015-09-14 11:59 | ICP - GPCMO36K0G0D | 68 | 0 | Yes | Yes | 13.5 | 15.9 | -2.4 | 29C0D212DCB644E9AF734DE91A4667E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7112 |  | 2015-08-26 | 2015-08-26 12:16 | 2015-08-26 12:39 | DAY & NIGHT - N/A | 85 | 27.7 | Yes | Yes | 26.2 | 23.4 | 2.8 | 2F4F4DDBAC604A86ACBC6A3AF1594AED |  | R22 | Non-TXV |  | 32.59% | 0.67412 | 62.63% | [5 empty] | Non-TXV | 32.59%
Brentwood | CA | 94513-7138 |  | 2015-09-04 | 2015-09-04 14:52 | 2015-09-04 14:52 | CARRIER - 24ABA324A310 | 66 | 0 | Yes | Yes | 20.3 | 18.8 | 1.5 | C81BE14D2D164424A3FF63D78E5DC8CE |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-5106 |  | 2015-08-19 | 2015-08-19 10:46 | 2015-08-19 10:46 | YORK - DCYZ-F036NO70A | 65 | 0 | Yes | Yes | 17.8 | 19.2 | -1.4 | 6CABB087D4584256860588E33CDE976E |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4658 |  | 2015-07-30 | 2015-07-30 12:42 | 2015-07-30 12:42 | TRANE - 2A7B0042A1000AA | 95 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | EABBBC6D5B1944BDA4092093CFD4945B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7135 |  | 2015-09-04 | 2015-09-04 13:25 | 2015-09-04 13:25 | CARRIER - 24ABA336A310 | 84 | 0 | Yes | Yes | 18.8 | 19.7 | -0.9 | 30D526536DB94C7C96F0D1E482FC31CC |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2509 |  | 2015-10-02 | 2015-10-02 14:40 | 2015-10-02 14:40 | CARRIER - 48GS036090301 | 85 | 0 | Yes | Yes | 20.4 | 16.6 | 3.8 | 5821F5C87E064A5D8ADAE976294CAB10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3529 |  | 2015-10-13 | 2015-10-13 16:27 | 2015-10-13 16:27 | CARRIER - 38CKC60300 | 152 | 0 | Yes | Yes | 20.2 | 18.1 | 2.1 | 6B6CD3A347A34BFFB4C9727F31F5F94E |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-8235 |  | 2015-07-21 | 2015-07-21 11:07 | 2015-07-21 11:07 | CARRIER - 24ABB348W310 | 112 | 0 | Yes | Yes | 16.9 | 19.4 | -2.5 | A756A1D6C7154209A02662EDF2B547B0 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-8235 |  | 2015-07-27 | 2015-07-27 08:52 | 2015-07-27 08:52 | CARRIER - 24ABB348W310 | 112 | 0 | Yes | Yes | 18.4 | 19.1 | -0.7 | 11EF3C4D1827426AA6E2A70A1BE4FA31 |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5081 |  | 2015-08-26 | 2015-08-26 12:44 | 2015-08-26 12:44 | CARRIER - 24ABR348A310 | 119 | 0 | Yes | Yes | 21.4 | 22.1 | -0.7 | 1AB4C9FB30BE415A9FA60B0F5A12D28C |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2932 |  | 2015-10-07 | 2015-10-07 14:00 | 2015-10-07 14:00 | AMERICAN STANDARD - YCC036F1M | 89 | 0 | Yes | Yes | 20.2 | 19 | 1.2 | 5F3E2CF94FE3438DA7151C9BC81E8CFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-0000 |  | 2015-09-08 | 2015-09-08 14:12 | 2015-09-08 14:12 | CARRIER - 24ABB342W300 | 92 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 591606027DBF48A29E2942E7592D3744 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6313 |  | 2015-09-29 | 2015-09-29 10:34 | 2015-09-29 11:01 | GOODMAN - GPG1324045M41AC | 80 | 17.2 | Yes | Yes | 21.3 | 20.7 | 0.6 | 921B7FC84A9E4E19B7814173A66628B9 |  | R410A | Non-TXV |  | 21.5% | 0.785 | 41.32% | [5 empty] | Non-TXV | 21.5%
Clovis | CA | 93611-6620 |  | 2015-09-08 | 2015-09-08 14:51 | 2015-09-08 14:51 | RUUD - N/A | 85 | 0 | Yes | Yes | 19.5 | 17.9 | 1.6 | 5E44107D7571437BA932973C0BE98BC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6727 |  | 2015-09-03 | 2015-09-03 14:26 | 2015-09-03 14:26 | DAY & NIGHT - 591ANX036000AAAA | 85 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 667160E46D6E4F9EABE7C9D243A9C01C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4709 |  | 2015-09-21 | 2015-09-21 09:18 | 2015-09-21 09:18 | RHEEM - RAKA037JAZ | 85 | 0 | Yes | Yes | 22.6 | 20.2 | 2.5 | 7A2E01E2C6CA414D8A608E8469CDE8C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-1145 |  | 2015-10-16 | 2015-10-16 11:17 | 2015-10-16 11:17 | YORK - H20B060306A | 128 | 0 | Yes | Yes | 20.9 | 18.8 | 2.1 | 267E2825EDFC4BAA8FA29E0CE6BF3495 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2918 |  | 2015-10-07 | 2015-10-07 12:44 | 2015-10-07 13:01 | CARRIER - 48KL136-311BE | 76 | 22.8 | Yes | Yes | 21.4 | 19.6 | 1.9 | F85A994910B54DD2912A69D7E82BB741 |  | R22 | Non-TXV |  | 30% | 0.7 | 57.65% | [5 empty] | Non-TXV | 30%
Suisun City | CA | 94585-1963 |  | 2015-09-24 | 2015-09-24 10:21 | 2015-09-24 10:21 | BRYANT - 113RMA024-B | 85 | 0 | Yes | Yes | 20.5 | 19.6 | 0.9 | 362AF81C864C4D05AAD0EAD3A365CF22 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3454 |  | 2015-10-20 | 2015-10-20 11:01 | 2015-10-20 11:01 | YORK - H20H036506B | 124 | 0 | Yes | Yes | 23.5 | 20.7 | 2.8 | 4D96C1EE0B324E9F9A16D0343D2C19ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2928 |  | 2015-09-11 | 2015-09-11 10:02 | 2015-09-11 10:02 | GUARDIAN - GCGD36S41S3A | 73 | 0 | Yes | Yes | 25.8 | 20.6 | 5.2 | 83A906EAE0274C84A9B32BC3F3F7B110 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5167 |  | 2015-08-13 | 2015-08-13 10:14 | 2015-08-13 11:00 | CARRIER - 38ESG036300 | 168 | 23.5 | Yes | Yes | 22.2 | 17.8 | 4.5 | DE209E763DD14121B0F76D90A3210965 |  | R410A | TXV |  | 13.99% | 0.86012 | 26.88% | [5 empty] | TXV | 13.99%
Bakersfield | CA | 93309-7620 |  | 2015-10-06 | 2015-10-06 10:23 | 2015-10-06 10:23 | ICP - PGAA42C1K1 | 82 | 0 | Yes | Yes | 21.4 | 18.7 | 2.7 | C92D2C7D83774E978960E8D807DDE193 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3437 |  | 2015-10-13 | 2015-10-13 13:06 | 2015-10-13 13:06 | OTHER - 563AN060A | 193 | 0 | Yes | Yes | 20 | 17.2 | 2.8 | 64A8225E124A4339B1CB65BD93FBB684 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-5762 |  | 2015-08-10 | 2015-08-10 10:05 | 2015-08-10 10:05 | UNITARY PRODUCTS GROUP - AM024M1021A | 52 | 0 | Yes | Yes | 28 | 22.2 | 5.8 | 0AA073D7210C49F984DB8B6D4582F284 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3023 |  | 2015-09-24 | 2015-09-24 10:11 | 2015-09-24 10:11 | GOODMAN - GPG1348070M41EA | 99 | 0 | Yes | Yes | 19.6 | 17.2 | 2.4 | BB6C7455B3384208B50C48F52CFFCE9D |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-1464 |  | 2015-09-11 | 2015-09-11 10:37 | 2015-09-11 10:37 | CARRIER - 48VLNA6009030TP | 195 | 0 | Yes | Yes | 20.6 | 20.4 | 0.2 | 1D5DC7437371404290EAA7FA904B45E4 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4464 |  | 2015-08-18 | 2015-08-18 10:02 | 2015-08-18 10:02 | RUUD - N/A | 85 | 0 | Yes | Yes | 19.9 | 21 | -1.1 | 4261AD8E495F49CF8E4FF334DFDB5421 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2136 |  | 2015-09-29 | 2015-09-29 14:15 | 2015-09-29 14:15 | OTHER - N/A | 85 | 0 | Yes | Yes | 24.3 | 19.8 | 4.5 | 686E46C51B41483FA9C9C4628EB12B56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7130 |  | 2015-10-02 | 2015-10-02 13:40 | 2015-10-02 13:40 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 17.6 | 18.5 | -0.9 | C697920A151D4591B80CBB921426C859 |  | R410A | TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-5765 |  | 2015-08-04 | 2015-08-04 11:36 | 2015-08-04 11:36 | UNITARY PRODUCTS GROUP - AM024M1021G | 52 | 0 | Yes | Yes | 27.3 | 22.3 | 5 | 01227C83811442C5AD33F1C56FD5FC17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7147 |  | 2015-09-04 | 2015-09-04 10:10 | 2015-09-04 10:36 | CARRIER - 24ABA330A320 | 64 | 9.6 | Yes | Yes | 23.1 | 19.6 | 3.5 | 3215C252D11243CC9BFD66D9AA0B28C3 |  | R22 | TXV |  | 15% | 0.85 | 28.83% | [5 empty] | TXV | 15%
Pittsburg | CA | 94565-1906 |  | 2015-08-31 | 2015-08-31 10:06 | 2015-08-31 10:33 | RHEEM - RAFD-048JBS | 101 | 14.5 | Yes | Yes | 18.4 | 19.8 | -1.4 | 2FB27E9A7A3B466B855066D18ADC1FA8 | Add refrigerant: 23.5 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.36% | 0.85644 | 27.59% | [5 empty] | Non-TXV | 14.36%
Brentwood | CA | 94513-7154 |  | 2015-09-23 | 2015-09-23 09:33 | 2015-09-23 09:33 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 594152F153624039AF6AF35F6147B3F8 |  | R410A | TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-5764 |  | 2015-08-10 | 2015-08-10 09:47 | 2015-08-10 09:47 | YORK - AM018M1021A | 49 | 0 | Yes | Yes | 20.7 | 22 | -1.3 | 16806A240EDB4424A63A57823A2EC7EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7403 |  | 2015-10-19 | 2015-10-19 14:40 | 2015-10-19 14:40 | OTHER - COTC-48M2Z | 148 | 0 | Yes | Yes | 16.3 | 19.3 | -3 | 2E22F055B5354686AF21DB7C7E6CC58E |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7921 |  | 2015-08-19 | 2015-08-19 12:55 | 2015-08-19 13:33 | UNITARY PRODUCTS GROUP - AC036X1222A | 83 | 12.2 | Yes | Yes | 20.9 | 22.6 | -1.7 | FEF51886501B49618A0A976AE67CDF83 |  | R22 | Non-TXV |  | 14.7% | 0.85301 | 28.25% | [5 empty] | Non-TXV | 14.7%
Fresno | CA | 93722-7533 |  | 2015-10-02 | 2015-10-02 15:00 | 2015-10-02 15:00 | LENNOX - 12GCS036-75-5PB | 122 | 0 | Yes | Yes | 25.8 | 23 | 2.8 | 1AC8C9A44FBD4351A2C44850DA33699D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1321 |  | 2015-08-24 | 2015-08-24 13:07 | 2015-08-24 13:07 | LENNOX - 13GEP30075ALP-3A | 68 | 0 | Yes | Yes | 18.1 | 20.6 | -2.5 | 8D3CAC3DBE534413984EBC87BE22CABA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1503 |  | 2015-08-24 | 2015-08-24 08:36 | 2015-08-24 08:36 | CARRIER - 588ANW036080ABAF | 67 | 0 | Yes | Yes | 23.8 | 18 | 5.8 | 37413DB3AFEE4A029E672DAE16CAD097 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7504 |  | 2015-09-18 | 2015-09-18 13:42 | 2015-09-18 13:42 | CARRIER - 38TH048320 | 128 | 0 | Yes | Yes | 20.5 | 19.9 | 0.6 | 35FE818BB70242D695BA3AA3DC6630F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5504 |  | 2015-08-12 | 2015-08-12 11:18 | 2015-08-12 11:18 | MONTGOMERY WARD - SRM-51507A | 63 | 0 | Yes | Yes | 21.3 | 23.1 | -1.8 | CDA690CDCC874FA6BAC7D2C435CF70D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2203 |  | 2015-08-18 | 2015-08-18 10:20 | 2015-08-18 10:20 | RUUD - UNK | 85 | 0 | Yes | Yes | 20.2 | 19.4 | 0.8 | 7E7EB348EE2A43E39A4FB9A5B1901334 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1973 |  | 2015-11-05 | 2015-11-05 10:25 | 2015-11-05 10:25 | OTHER - 13RNA024 | 85 | 0 | Yes | Yes | 20.5 | 19.9 | 0.6 | 02CAE50FCFE94C58A9FA95E506181AD6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2470 |  | 2015-08-13 | 2015-08-13 10:10 | 2015-08-13 10:10 | GOODMAN - GPG13300451AA | 77 | 0 | Yes | Yes | 23 | 17.7 | 5.3 | C217DED7D3D54554B49E4529D53783A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2942 |  | 2015-09-10 | 2015-09-10 12:44 | 2015-09-10 12:44 | OTHER - DARA-F030N060C | 80 | 0 | Yes | Yes | 16.1 | 18.8 | -2.7 | 3884F981676E40F1A99F307533F2E076 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6972 |  | 2015-09-03 | 2015-09-03 09:18 | 2015-09-03 09:41 | LENNOX - 13ACC-42-230-01 | 123 | 9.4 | Yes | Yes | 18.8 | 21 | -2.2 | BBD0A8F1BB804E72B7F5EDAF04C2BBAB |  | R22 | TXV |  | 7.642% | 0.92358 | 14.69% | [5 empty] | TXV | 7.642%
Pittsburg | CA | 94565-1748 |  | 2015-09-04 | 2015-09-04 09:46 | 2015-09-04 09:46 | OTHER - CA3060VKA2 | 144 | 0 | Yes | Yes | 19.7 | 19.3 | 0.4 | E86C65F04D564690958F47DB13DE78B4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4497 |  | 2015-09-18 | 2015-09-18 10:42 | 2015-09-18 10:42 | YORK - H2RC036S06A | 83 | 0 | Yes | Yes | 16 | 17.6 | -1.6 | 71479884F5664FBD9C14F41B02AD5D91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7317 |  | 2015-10-13 | 2015-10-13 10:26 | 2015-10-13 10:26 | RHEEM - RAFD-048JBS | 101 | 0 | Yes | Yes | 23.5 | 22 | 1.5 | CF1E4A3DA7424ED482C0AAD411C1462C |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5916 |  | 2015-11-10 | 2015-11-10 13:45 | 2015-11-10 13:45 | YORK - H1RA048S06D | 117 | 0 | Yes | Yes | 22.2 | 20.3 | 1.9 | F1F33E6E8AB24D39B6B89A33605E1563 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4328 |  | 2015-08-12 | 2015-08-12 09:18 | 2015-08-12 09:18 | YORK - DAYP-F030N070A | 73 | 0 | Yes | Yes | 22.5 | 21.5 | 1 | 2DCBE3A54059497F8F5F570B61665EC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5504 |  | 2015-08-19 | 2015-08-19 09:15 | 2015-08-19 09:15 | CARRIER - 48ESNA4206030 | 101 | 0 | Yes | Yes | 25 | 21.4 | 3.6 | 98E6120127054320A39BB5AE94F0C856 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-5423 |  | 2015-11-09 | 2015-11-09 10:30 | 2015-11-09 10:30 | LENNOX - 13ACC04223001 | 123 | 0 | Yes | Yes | 23.5 | 19.5 | 4 | F32A6309F9F0429C9DA185085E21876E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1314 |  | 2015-09-17 | 2015-09-17 13:45 | 2015-09-17 13:45 | GIBSON - JT5BD030KA | 144 | 0 | Yes | Yes | 19 | 16.3 | 2.7 | A6F7A5ACE4D04F7091FA47B45172BD15 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6257 |  | 2015-10-09 | 2015-10-09 08:24 | 2015-10-09 08:24 | OTHER - PH13NR060-C | 301 | 0 | Yes | Yes | 21.8 | 21.8 | 0 | 18543B009CBB48578009F2387A8D3D28 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5238 |  | 2015-08-19 | 2015-08-19 10:51 | 2015-08-19 10:51 | GOODMAN - GPG13300451AB | 77 | 0 | Yes | Yes | 28.5 | 23.2 | 5.3 | 22E8564BE14645428DE767189C1A9D40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7154 |  | 2015-08-26 | 2015-08-26 15:03 | 2015-08-26 15:03 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 19.5 | 19.7 | -0.2 | 9174EFA59A9C416C99C12C0FD49AA30B |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1223 |  | 2015-11-06 | 2015-11-06 14:12 | 2015-11-06 14:12 | YORK - YCY048G1H0AC | 183 | 0 | Yes | Yes | 19.5 | 16.5 | 3.1 | 4C9916400FC64C199E6A7F22A9F8E901 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2425 |  | 2015-10-21 | 2015-10-21 14:55 | 2015-10-21 14:55 | GOODMAN - GBO48075 | 87 | 0 | Yes | Yes | 22.7 | 18.7 | 4 | C6FD20F674F3430DBAC807F6EF0F0184 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2361 |  | 2015-10-13 | 2015-10-13 15:51 | 2015-10-13 15:51 | GOODMAN - PCB024050-1 REVA | 54 | 0 | Yes | Yes | 19.4 | 22.1 | -2.7 | 6CAF514F7F65403CB21E21374F3A70C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7154 |  | 2015-08-26 | 2015-08-26 14:04 | 2015-08-26 14:41 | CARRIER - 24ABA336A310 | 84 | 12.7 | Yes | Yes | 25.6 | 20.7 | 4.9 | B89ACFAA2A3F43A396BFFF3CA3D15ACA |  | R410A | TXV |  | 15.12% | 0.84881 | 29.06% | [5 empty] | TXV | 15.12%
Fresno | CA | 93702-3226 |  | 2015-09-10 | 2015-09-10 16:12 | 2015-09-10 16:12 | OTHER - TCJD36S41S3HA | 73 | 0 | Yes | Yes | 20.2 | 16.8 | 3.4 | ED1FB244046D477B8BEDF286C386A129 |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5139 |  | 2015-10-14 | 2015-10-14 13:13 | 2015-10-14 13:13 | CARRIER - 38CKC036350 | 85 | 0 | Yes | Yes | 19.5 | 18.8 | 0.7 | F0D6AF49BC5F4E10833940E6BD9E8388 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2221 |  | 2015-09-03 | 2015-09-03 15:34 | 2015-09-03 15:34 | GE - BTB924B100A2 | 56 | 0 | Yes | Yes | 22.6 | 21 | 1.6 | 9D62567E132640D797180EF9299D86D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-0000 |  | 2015-09-02 | 2015-09-02 13:17 | 2015-09-02 13:17 | CARRIER - 24ABC642A0030010 | 134 | 0 | Yes | Yes | 18.8 | 18.8 | 0 | 6C3FB91DB3974708A68A5D31493E5BE9 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-2319 |  | 2015-10-08 | 2015-10-08 10:34 | 2015-10-08 10:34 | YORK - D6NZ036N05606NXA | 64 | 0 | Yes | Yes | 24.7 | 22.4 | 2.3 | 2CBF3CC64FBB4CCAB629F62DDB8D6293 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2625 |  | 2015-08-12 | 2015-08-12 14:15 | 2015-08-12 14:15 | HEIL - CA5036VKB1 | 86 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | 85878FC0D8854B64B34AF251041B6B55 |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-8637 |  | 2015-08-26 | 2015-08-26 11:35 | 2015-08-26 11:35 | CARRIER - 50SZ-036---301 | 169 | 0 | Yes | Yes | 22.4 | 19.9 | 2.5 | 8683B94CEAD445F682283B05E1DD7FCB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3352 |  | 2015-11-05 | 2015-11-05 10:37 | 2015-11-05 10:37 | CARRIER - 00000 | 88 | 0 | Yes | Yes | 23.7 | 20.6 | 3.1 | F6653D657BC74522992E5F66015AFA10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9441 |  | 2015-11-10 | 2015-11-10 11:57 | 2015-11-10 11:57 | YORK - H2RE048S06A | 227 | 0 | Yes | Yes | 17.3 | 17.7 | -0.4 | 2A4E081AAAD24973839654EADD685345 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4256 |  | 2015-10-28 | 2015-10-28 12:35 | 2015-10-28 12:35 | OTHER - N/A | 85 | 23.7 | Yes | Yes | 20.2 | 22.6 | -2.4 | E6A06A5932424256A1B7AE28A34CCF3C |  | R22 | Non-TXV |  | 27.88% | 0.72118 | 53.58% | [5 empty] | Non-TXV | 27.88%
Fresno | CA | 93705-0401 |  | 2015-09-01 | 2015-09-01 14:59 | 2015-09-01 15:18 | GOODMAN - GPG1348070M41DA | 80 | 3.1 | Yes | Yes | 23.9 | 21.2 | 2.7 | 12FA275F17F94992976B7B8D11FDF63D |  | R410A | TXV |  | 3.875% | 0.96125 | 7.447% | [5 empty] | TXV | 3.875%
Bakersfield | CA | 93307-1712 |  | 2015-09-22 | 2015-09-22 09:26 | 2015-09-22 10:13 | RHEEM - | 85 | 8.2 | Yes | Yes | 20.6 | 23 | -2.4 | CDBB7AC1ABAD4C79B2C3E29240DEDBE1 |  | R22 | Non-TXV |  | 9.647% | 0.90353 | 18.54% | [5 empty] | Non-TXV | 9.647%
Brentwood | CA | 94513-7152 |  | 2015-09-08 | 2015-09-08 16:50 | 2015-09-08 16:50 | CARRIER - 24ABA324A31P0 | 66 | 0 | Yes | Yes | 21.7 | 18.3 | 3.5 | C953C77CC81249F69A59D713A22242AA |  | R22 | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1314 |  | 2015-11-03 | 2015-11-03 16:21 | 2015-11-03 16:21 | GIBSON - JT5BD030 | 140 | 0 | Yes | Yes | 17 | 18.6 | -1.6 | ED49E890343C40C29FAA05B900AEEFE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2522 |  | 2015-07-31 | 2015-07-31 16:41 | 2015-07-31 16:41 | AMERICAN STANDARD - 2A7B0030A1000AA | 137 | 0 | Yes | Yes | 14.9 | 20.4 | -5.5 | 8C97A74C9B2B4AA4A8970A66923F58AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-1923 |  | 2015-10-21 | 2015-10-21 13:22 | 2015-10-21 13:22 | PAYNE - BRCS042C | 86 | 0 | Yes | Yes | 28 | 16.6 | 11.4 | 138B12281F8645B9BBDC23FDAA6DB5E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6021 |  | 2015-10-19 | 2015-10-19 08:31 | 2015-10-19 08:31 | LENNOX - 13ACC-060-230 | 168 | 0 | Yes | Yes | 21.8 | 18.3 | 3.5 | E035AEE7EAE746EC835B678A7F127916 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-9333 |  | 2015-10-29 | 2015-10-29 13:59 | 2015-10-29 13:59 | TEMPSTAR - PGF036K060B | 71 | 0 | Yes | Yes | 25.4 | 19.9 | 5.5 | 0D04AFDF8A484AB1AAD2B8653C0BAC55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5827 |  | 2015-09-09 | 2015-09-09 14:38 | 2015-09-09 14:58 | BDP - 585HJ036060 | 102 | 5.6 | Yes | Yes | 24.5 | 22.6 | 1.9 | A93676D9231845BCB44DBA8052D1639B |  | R22 | Non-TXV |  | 5.49% | 0.9451 | 10.55% | [5 empty] | Non-TXV | 5.49%
Suisun City | CA | 94585-1972 |  | 2015-10-12 | 2015-10-12 09:16 | 2015-10-12 09:16 | BRYANT - 113RNA024C | 71 | 0 | Yes | Yes | 20.8 | 23 | -2.2 | 16BEFDBD3373408C904166235FDC2116 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7350 |  | 2015-11-06 | 2015-11-06 11:57 | 2015-11-06 11:57 | OTHER - 12GCS030753PB | 85 | 0 | Yes | Yes | 22.9 | 20.2 | 2.8 | 181EF4DD6B75427DB48BFBA2D2DF9A55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0000 |  | 2015-10-12 | 2015-10-12 11:41 | 2015-10-12 11:41 | WEATHER KING - 14AJA42A01 | 237 | 0 | Yes | Yes | 22.8 | 19.3 | 3.5 | 9DD64A1F757E40A284D7EEEAE83601F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1037 |  | 2015-09-09 | 2015-09-09 09:27 | 2015-09-09 09:27 | RHEEM - RRKA-A030JK06X | 54 | 0 | Yes | Yes | 23.3 | 19.3 | 4 | 3C38D7030C80475EBA74814C1865B3FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-4109 |  | 2015-10-08 | 2015-10-08 16:21 | 2015-10-08 16:21 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 22.2 | 20.1 | 2.1 | 697C20150C374C9F87EC4A6139D95E20 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2926 |  | 2015-08-19 | 2015-08-19 14:57 | 2015-08-19 14:57 | OTHER - WCA3362GKR1 | 83 | 0 | Yes | Yes | 19.1 | 18.5 | 0.6 | F0C2044F65F946ED80A197FE127454B1 |  | R22 | TXV |  | 0% | 1 | 0%
Davis | CA | 95616-2716 |  | 2015-10-02 | 2015-10-02 11:07 | 2015-10-02 11:07 | GOODMAN - CKJ42-B | 106 | 0 | Yes | Yes | 16.6 | 19.4 | -2.8 | 778F9ADA91BC43DE948C0BE578CC6A4C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2603 |  | 2015-08-04 | 2015-08-04 11:40 | 2015-08-04 11:40 | PAYNE - PA13NA030 | 85 | 0 | Yes | Yes | 15.3 | 18.2 | -2.9 | 84BCB0B3F1284E89889B47E6E34767FE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7629 |  | 2015-10-05 | 2015-10-05 11:13 | 2015-10-05 11:13 | CARRIER - 38CKC048360 | 100 | 0 | Yes | Yes | 20.9 | 21.7 | -0.8 | F657D30F2C9A486D806A62DBE4C92B8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2521 |  | 2015-08-20 | 2015-08-20 11:08 | 2015-08-20 11:08 | CARRIER - 38CKC036350 | 72 | 0 | Yes | Yes | 15.9 | 18.5 | -2.6 | F0BCD731878945AD8FAD8E77C77FFFE8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-0158 |  | 2015-08-31 | 2015-08-31 11:20 | 2015-08-31 11:20 | LENNOX - 12ACB48-5B | 171 | 0 | Yes | Yes | 19.8 | 17.9 | 1.9 | 24CA343E42BF4F52BAEE726B96A251B2 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6914 |  | 2015-08-24 | 2015-08-24 13:49 | 2015-08-24 14:12 | CARRIER - 38BRC030310 | 100 | 9.5 | Yes | Yes | 18.7 | 18.8 | -0.1 | 21D5482B372847CA96A7CE2E6B9D3EF6 |  | R22 | TXV |  | 9.5% | 0.905 | 18.26% | [5 empty] | TXV | 9.5%
Fresno | CA | 93705-0339 |  | 2015-09-30 | 2015-09-30 14:57 | 2015-09-30 14:57 | PAYNE - 587ANZO42080 | 85 | 0 | Yes | Yes | 22 | 21.9 | 0.1 | E461471756524C44A3914D92C4A95595 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-4110 |  | 2015-09-03 | 2015-09-03 09:28 | 2015-09-03 09:28 | KENMORE - N4336KB200 | 85 | 0 | Yes | Yes | 18 | 17.5 | 0.6 | 320858AD39304848819B57E3CC1D0650 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5163 |  | 2015-08-04 | 2015-08-04 12:49 | 2015-08-04 12:49 | YORK - D2NP036N05606NXA | 108 | 0 | Yes | Yes | 16.9 | 21.3 | -4.4 | B24AFC458C0245A1BFFD967C11920EB0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3625 |  | 2015-09-18 | 2015-09-18 12:30 | 2015-09-18 12:30 | RUUD - URGG-05E24JKR | 40 | 0 | Yes | Yes | 20 | 19.3 | 0.7 | F4982DFDACD847D89A5247C4761D9DB7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6236 |  | 2015-08-12 | 2015-08-12 16:08 | 2015-08-12 16:08 | UNITARY PRODUCTS GROUP - D1NH036N05606C | 108 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | 1EEC17ACA5824F68B76769540F852A11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9619 |  | 2015-10-16 | 2015-10-16 14:12 | 2015-10-16 14:12 | CARRIER - 48GX-042060301 | 115 | 0 | Yes | Yes | 19.1 | 20.7 | -1.6 | 0560513961064D91AF04FF8C8092508D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4814 |  | 2015-10-12 | 2015-10-12 12:41 | 2015-10-12 12:41 | BDP - 561CJ048-B | 100 | 0 | Yes | Yes | 20.5 | 19.8 | 0.7 | 3B9F23E595D648D3A23C583F78C867A4 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4849 |  | 2015-10-06 | 2015-10-06 08:30 | 2015-10-06 08:30 | ICP - PGAA47D1K4 | 113 | 0 | Yes | Yes | 21.1 | 19.9 | 1.2 | 5709ADC419364D84A3D04830A9BDE048 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-4072 |  | 2015-08-20 | 2015-08-20 16:12 | 2015-08-20 16:12 | BDP - 585HJ030040 | 68 | 0 | Yes | Yes | 19.1 | 14.8 | 4.3 | 65C44B26C168466EB77F57952FC12B65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-8119 |  | 2015-08-12 | 2015-08-12 11:57 | 2015-08-12 11:57 | YORK - D2NH048N0506C | 85 | 0 | Yes | Yes | 21.8 | 19.9 | 1.9 | 3104F467822747BDB4AC23C3BC820F43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5424 |  | 2015-10-29 | 2015-10-29 12:27 | 2015-10-29 12:27 | BRYANT - 583ANW30060AAAD | 68 | 0 | Yes | Yes | 22 | 18.3 | 3.7 | 87888F7674E94D1FBA798A3755E1DA3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4488 |  | 2015-09-17 | 2015-09-17 11:50 | 2015-09-17 11:50 | CARRIER - 38CKC036350 | 70 | 0 | Yes | Yes | 16.5 | 19.4 | -2.9 | C5FC21AF068D439B9BD88E0453731B3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6540 |  | 2015-08-19 | 2015-08-19 17:40 | 2015-08-19 17:40 | YORK - H4DE036S06A | 82 | 0 | Yes | Yes | 25.4 | 22.2 | 3.3 | 8C2EEE07ECFD4B84ABF07EF225A5D44C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-0502 |  | 2015-08-31 | 2015-08-31 09:13 | 2015-08-31 09:13 | LENNOX - 12GCS024X-50-3PA | 72 | 0 | Yes | Yes | 23.6 | 19.9 | 3.7 | 9D6C2D23955A4FB4BFAD438CCE28320D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9708 |  | 2015-10-07 | 2015-10-07 12:58 | 2015-10-07 12:58 | GUARDIAN - GPG1336070M41AA | 85 | 0 | Yes | Yes | 24.6 | 24.7 | -0.1 | 66712B93153F48B29EFD9E1A0778DA60 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-8726 |  | 2015-10-01 | 2015-10-01 16:37 | 2015-11-06 13:48 | CARRIER - 24A3A348A300 | 121 | 0 | Yes | Yes | 25 | 20.4 | 4.6 | 3A4B695D214A418CA2507F1853734E75 |  | R410A | TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-5432 |  | 2015-08-05 | 2015-08-05 08:40 | 2015-08-05 09:02 | RHEEM - RACA-030AAQ | 35 | 20 | Yes | Yes | 21.6 | 17.2 | 4.4 | 7C762E4573524E79BA71BF62C0E2850D |  | R22 | Non-TXV |  | 57.14% | 0.42857 | 109.8% | [5 empty] | Non-TXV | 57.14%
Brentwood | CA | 94513-7125 |  | 2015-09-14 | 2015-09-14 14:41 | 2015-09-14 15:05 | CARRIER - 24ABA330A320 | 64 | 10.4 | Yes | Yes | 15.7 | 21 | -5.3 | 3338437083034190986D5549DB38F7F1 | Add refrigerant: 8.4 oz | R410A | TXV |  | 16.25% | 0.8375 | 31.23% | [5 empty] | TXV | 16.25%
Brentwood | CA | 94513-7331 |  | 2015-09-09 | 2015-09-09 10:25 | 2015-09-09 10:25 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 19.8 | 21.5 | -1.7 | CDEB00DACE474EE38C90FAB03909E3F5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1222 |  | 2015-09-16 | 2015-09-16 08:54 | 2015-09-16 08:54 | CARRIER - 48ESN042090311 | 97 | 0 | Yes | Yes | 21.4 | 16.5 | 4.9 | D5ABA422BBB04D43BCCCE6BF97B74171 |  | R410A | TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3079 |  | 2015-10-20 | 2015-10-20 09:36 | 2015-10-20 09:36 | GOODMAN - CK49-1B | 90 | 0 | Yes | Yes | 15 | 17.8 | -2.7 | 992E6EDBC65F448F9302BAD8C108F6DF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-2100 |  | 2015-10-27 | 2015-10-27 11:18 | 2015-10-27 11:18 | LENNOX - GCS29-030-75-1PA | 53 | 0 | Yes | Yes | 18.5 | 18.7 | -0.2 | D9E3BD19351A4E899EDBF72EA10550D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-5910 |  | 2015-09-01 | 2015-09-01 12:51 | 2015-09-01 12:51 | CARRIER - 38CKC030330 | 68 | 0 | Yes | Yes | 17.7 | 18.2 | -0.5 | 9C48B23B36C84848A0126A184E0EFC1E |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7018 |  | 2015-08-06 | 2015-08-06 15:49 | 2015-08-06 15:49 | LENNOX - XC1406023004 | 192 | 0 | Yes | Yes | 20.6 | 21 | -0.4 | 3262FEF5E6B6469C9B5DF8EA62D8050D |  | R410A | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7142 |  | 2015-09-09 | 2015-09-09 11:06 | 2015-09-09 11:06 | CARRIER - 24ABA324A310 | 66 | 0 | Yes | Yes | 20.3 | 19.3 | 1 | A53111CB67194418A32AB87AA35CC2A6 |  | R410A | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7149 |  | 2015-09-08 | 2015-09-08 11:28 | 2015-09-08 11:28 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 17.8 | 20.7 | -2.9 | D24DC17CE64D42BD9B3E8BD620CA9831 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4438 |  | 2015-09-15 | 2015-09-15 10:58 | 2015-09-15 10:58 | RHEEM - RRNL-B036JK06X | 93 | 0 | Yes | Yes | 18.4 | 17.4 | 1 | F775D757B67B4C2491DB99FB4A90990B |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5844 |  | 2015-08-05 | 2015-08-05 11:24 | 2015-08-05 11:24 | TRANE - YCC036F1HOBJ | 83 | 0 | Yes | Yes | 24.3 | 20.1 | 4.2 | B61E10AD7DBE4381AC69F54B5B49E7B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2513 |  | 2015-10-02 | 2015-10-02 13:42 | 2015-10-02 13:42 | AMANA - | 150 | 0 | Yes | Yes | 20.7 | 17.9 | 2.8 | 9242B6519BEA4FC098C00F28BA59039A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3020 |  | 2015-08-20 | 2015-08-20 15:14 | 2015-08-20 15:14 | GOODMAN - GPG1342070M41BA | 81 | 0 | Yes | Yes | 17 | 19 | -2 | 51EA8B3A2C6547E1A1CC7360A843D730 |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4710 |  | 2015-09-02 | 2015-09-02 09:22 | 2015-09-02 09:22 | AMANA - PGA36B0702C | 85 | 0 | Yes | Yes | 19.5 | 20.7 | -1.2 | 097BF7B3D7B547EBA95091D162947876 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4708 |  | 2015-08-31 | 2015-08-31 15:48 | 2015-08-31 15:48 | RHEEM - RRNA-B036JK06X | 83 | 0 | Yes | Yes | 19.7 | 18.6 | 1.1 | 11A6C1F79F5340FCAA2B77C5AEBB85DA |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3034 |  | 2015-09-10 | 2015-09-10 10:18 | 2015-09-10 10:40 | CARRIER - N/A | 85 | 17.2 | Yes | Yes | 19.5 | 20.6 | -1 | 0A69F5C284AC475B95E378E40D549FA6 |  | R22 | Non-TXV |  | 20.24% | 0.79765 | 38.89% | [5 empty] | Non-TXV | 20.24%
Fresno | CA | 93705-0336 |  | 2015-10-05 | 2015-10-05 13:46 | 2015-10-05 13:46 | UNITARY PRODUCTS GROUP - 042-C | 97 | 0 | Yes | Yes | 18.7 | 18.6 | 0.1 | A0D4DC31CB6C4B959E4C9EEA6AF58F3A |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1238 |  | 2015-10-08 | 2015-10-08 14:55 | 2015-10-08 14:55 | DUCANE - 2AC13L36P-2B | 128 | 0 | Yes | Yes | 19.7 | 21.5 | -1.8 | 15A67160087D4359A2C28BE90C2AE8C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95605-2048 |  | 2015-11-19 | 2015-11-19 14:02 | 2015-11-19 14:02 | GOODMAN - GSZ130301AG | 108 | 0 | Yes | Yes | 18 | 20.2 | -2.2 | 4AFD73EDF54D40EE9EFB2BE11D314934 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5368 |  | 2015-10-06 | 2015-10-06 09:14 | 2015-10-06 09:22 | BDP - 585CJ02450 | 72 | 7.8 | Yes | Yes | 20.2 | 22.3 | -2.1 | 383D3978EE0C4BAD95E8B3F0F6FDA2E0 |  | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Antioch | CA | 94531-7488 |  | 2015-11-18 | 2015-11-18 16:09 | 2015-11-18 16:09 | YORK - BRCS0601BD | 118 | 0 | Yes | Yes | 23.7 | 21.4 | 2.3 | FAA76F8C9F1F4442A42B4AF8D52087E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9398 |  | 2015-10-16 | 2015-10-16 13:04 | 2015-10-16 13:04 | YORK - EHDE042S06A | 99 | 0 | Yes | Yes | 19.8 | 17.3 | 2.6 | A7F60E7E949E478C9B85332429A3BA11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4501 |  | 2015-10-14 | 2015-10-14 08:19 | 2015-10-14 08:19 | ALLEGIANCE - 2A7A2036A1000AA | 96 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | 51193D9254954EA79233371E2D59BD4E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2755 |  | 2015-10-01 | 2015-10-01 14:10 | 2015-10-01 14:10 | CARRIER - 48SS-036060331 | 67 | 0 | Yes | Yes | 22.6 | 19.7 | 2.9 | B284E504EF4C4889AA0BE99FEF251290 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5891 |  | 2015-08-12 | 2015-08-12 11:35 | 2015-08-12 11:58 | WEATHER KING - 12AJA3001 | 96 | 8.9 | Yes | Yes | 24.7 | 23.1 | 1.6 | 63C9E571E4C347BE88E4CAD1F940907C |  | R22 | Non-TXV |  | 9.271% | 0.90729 | 17.82% | [5 empty] | Non-TXV | 9.271%
Clovis | CA | 93612-4611 |  | 2015-09-03 | 2015-09-03 13:01 | 2015-09-03 13:26 | CARRIER - 588ANW036060ADAF | 73 | 14.2 | Yes | Yes | 18.8 | 19.9 | -1.1 | 699CF7636BA84D6AAF0DB49357188A4F |  | R22 | Non-TXV |  | 19.45% | 0.80548 | 37.38% | [5 empty] | Non-TXV | 19.45%
Fairfield | CA | 94533-0000 |  | 2015-09-08 | 2015-09-08 14:57 | 2015-09-08 14:57 | CARRIER - 24BC642A300 | 135 | 0 | Yes | Yes | 18.5 | 18.1 | 0.4 | F07274449A514FDBAC3AD6E5FB885762 |  | R410A | TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3618 |  | 2015-11-19 | 2015-11-19 16:01 | 2015-11-19 16:01 | GOODMAN - GSC130361GA | 108 | 0 | Yes | Yes | 24.1 | 18.6 | 5.6 | 661B547E812B42F9B3CFDCADA52010D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2710 |  | 2015-10-28 | 2015-10-28 11:46 | 2015-10-28 11:46 | DAY & NIGHT - N/A | 85 | 0 | Yes | Yes | 19.1 | 18.8 | 0.3 | D101FB3E97C840CC955F0C61C8D89D62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2710 |  | 2015-10-28 | 2015-10-28 12:03 | 2015-10-28 12:03 | DAY & NIGHT - N/A | 85 | 0 | Yes | Yes | 17.4 | 18.8 | -1.4 | 2AAA0BA6E83D4170801E6B40969B0440 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5486 |  | 2015-08-04 | 2015-08-04 10:19 | 2015-08-04 10:19 | RUUD - UAKA037JAZ | 85 | 0 | Yes | Yes | 25.1 | 20.1 | 5.1 | C302434D53ED46BD9640DD924DA1C512 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3714 |  | 2015-08-18 | 2015-08-18 14:00 | 2015-08-18 14:00 | RHEEM - RRNL-B048JK10X | 161 | 0 | Yes | Yes | 19.2 | 21.4 | -2.2 | EC1FB6E2F70B4143B32EFA0638468023 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7604 |  | 2015-09-14 | 2015-09-14 10:43 | 2015-09-14 10:43 | GOODMAN - CKL421A | 95 | 0 | Yes | Yes | 16.6 | 16.5 | 0.1 | 694281F162DF412095906287ED13244A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7130 |  | 2015-09-18 | 2015-09-18 10:08 | 2015-09-18 10:27 | CARRIER - 24ABA330A320 | 64 | 8.6 | Yes | Yes | 16.6 | 19.4 | -2.8 | 3843A2BBA0C44E3D8FBC3DFE6D0D15BA |  | R410A | TXV |  | 13.44% | 0.86562 | 25.82% | [5 empty] | TXV | 13.44%
Bakersfield | CA | 93304-5424 |  | 2015-08-04 | 2015-08-04 12:02 | 2015-08-04 12:02 | PAYNE - PY1PNB036060ABAA | 71 | 0 | Yes | Yes | 21.1 | 18.8 | 2.3 | 216B644D8F704B81B7A49B4B603DDF3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-2809 |  | 2015-08-20 | 2015-08-20 10:27 | 2015-08-20 10:27 | BDP - 541B041SHP | 110 | 0 | Yes | Yes | 18.6 | 15.2 | 3.4 | 9B98E9D2D13B491D9841FB8501B27482 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7929 |  | 2015-10-09 | 2015-10-09 15:38 | 2015-10-09 15:38 | YORK - ND1P042N06506A | 150 | 0 | Yes | Yes | 20 | 22.9 | -2.9 | FEB660FA099A4C9C989E862B41DEAD68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7155 |  | 2015-08-31 | 2015-08-31 13:23 | 2015-08-31 13:23 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | 2FF8F4D1D5E24F9FBAFAF2E3DE25B887 |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4629 |  | 2015-08-18 | 2015-08-18 15:18 | 2015-08-18 15:18 | PAYNE - PY3GNAA30060NA | 100 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | CC97233218964AF0B26ECA8F44EA898C |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7760 |  | 2015-10-12 | 2015-10-12 13:15 | 2015-10-12 13:16 | ICP - GPCM36K060F | 87 | 12.3 | Yes | Yes | 17.5 | 20.2 | -2.7 | 57880417E54D4388BACB4832E1851617 |  | R22 | Non-TXV |  | 14.14% | 0.85862 | 27.17% | [5 empty] | Non-TXV | 14.14%
Concord | CA | 94518-2178 |  | 2015-08-07 | 2015-08-07 09:06 | 2015-08-07 09:06 | CARRIER - 24ABB336W310 | 84 | 0 | Yes | Yes | 22.7 | 18.5 | 4.2 | 31937522F2DF48BF8EBE58549197DBA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7139 |  | 2015-08-12 | 2015-08-12 08:37 | 2015-08-12 08:58 | OTHER - EADB-042JAS | 79 | 3.2 | Yes | Yes | 19.1 | 22 | -2.9 | F3A984744D2244A48D000E51AFDC1E6B |  | R22 | Non-TXV |  | 4.051% | 0.95949 | 7.784% | [5 empty] | Non-TXV | 4.051%
Fresno | CA | 93727-9015 |  | 2015-11-06 | 2015-11-06 09:58 | 2015-11-06 09:58 | LENNOX - 13ACD03623002 | 111 | 0 | Yes | Yes | 21 | 18.3 | 2.7 | 07E9D13896E840D384E06B0FE257BD1C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-9015 |  | 2015-11-06 | 2015-11-06 10:00 | 2015-11-06 10:00 | - | 85 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 048D3266EFDC4943B32673A88EA805C3 |  |  |  |  | 0% | 1 | 0%
Fresno | CA | 93727-5852 |  | 2015-09-29 | 2015-09-29 09:44 | 2015-11-06 13:51 | LENNOX - 13ACD-036-230-2 | 111 | 0 | Yes | Yes | 16.4 | 18.8 | -2.4 | AAD351B2F6F846AB90F295DA21347BE5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3212 |  | 2015-08-12 | 2015-08-12 10:37 | 2015-08-12 10:37 | ICP - PGAD47D1K4 | 215 | 0 | Yes | Yes | 19.2 | 20.6 | -1.3 | 54AA88BA354F4EE5A24D78DC38231F56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2826 |  | 2015-09-01 | 2015-09-01 10:52 | 2015-09-01 10:52 | GOODMAN - GPG1130070M41AB | 80 | 0 | Yes | Yes | 17 | 19.3 | -2.3 | 49FB876DCD12433286111314BC6FD30D |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7148 |  | 2015-11-09 | 2015-11-09 09:05 | 2015-11-09 09:25 | YORK - WCA3362GKR2 | 86 | 33.2 | Yes | Yes | 21.1 | 19.9 | 1.2 | 5E61795BEBAA463583698B33D67BEA38 |  | R22 | Non-TXV |  | 38.6% | 0.61395 | 74.19% | [5 empty] | Non-TXV | 38.6%
Fresno | CA | 93725-0934 |  | 2015-11-05 | 2015-11-05 11:35 | 2015-11-05 11:35 | CARRIER - 24ABA342A310 | 92 | 0 | Yes | Yes | 19.6 | 14.2 | 5.4 | FD93EBC5CBE04A309D8EE5A792632432 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5932 |  | 2015-10-02 | 2015-10-02 11:58 | 2015-10-02 12:26 | BDP - 585A030080YAC | 50 | 8.6 | Yes | Yes | 25.2 | 20.4 | 4.8 | 0FFF5638CCDC454D956D835C88420738 |  | R22 | Non-TXV |  | 17.2% | 0.828 | 33.05% | [5 empty] | Non-TXV | 17.2%
Fresno | CA | 93726-5424 |  | 2015-09-24 | 2015-09-24 14:22 | 2015-09-24 14:22 | ICP - PGN336060K01A1 | 96 | 0 | Yes | Yes | 28 | 22.8 | 5.2 | 8F3D70FB2DAA442EA9DC55E1777CC796 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1223 |  | 2015-07-30 | 2015-07-30 11:07 | 2015-07-30 11:07 | TEMPSTAR - TCA036A1SA1 | 80 | 0 | Yes | Yes | 19.6 | 18.8 | 0.8 | 96FB2D0402F24BB6985651FFEC4C48C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rio Vista | CA | 94571-1409 |  | 2015-08-14 | 2015-08-14 16:26 | 2015-08-14 16:26 | ICP - CA5542VKD1 | 98 | 0 | Yes | Yes | 21.7 | 20.4 | 1.3 | F27E8AC591C3438EB05ED1254C42B66F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7149 |  | 2015-10-26 | 2015-10-26 14:08 | 2015-10-26 14:26 | CARRIER - 24ABA330A320 | 85 | 15.2 | Yes | Yes | 17 | 18.5 | -1.5 | ED1DBCDDD4304EA7A45BB6F79E54B982 |  | R410A | TXV |  | 17.88% | 0.82118 | 34.37% | [5 empty] | TXV | 17.88%
Pittsburg | CA | 94565-4490 |  | 2015-09-18 | 2015-09-18 09:49 | 2015-09-18 09:49 | CARRIER - 38CKC030340 | 85 | 0 | Yes | Yes | 17.1 | 19 | -1.9 | 0BFA289C28E345A2BA878A27037AC05B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5704 |  | 2015-10-09 | 2015-10-09 16:21 | 2015-10-09 16:21 | GOODMAN - UNKNOWN | 70 | 0 | Yes | Yes | 17.8 | 20.7 | -2.9 | CB8BCFD91F40415B847C03151D030A2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5648 |  | 2015-09-12 | 2015-09-12 15:55 | 2015-09-12 15:55 | CARRIER - 38CKC04870 | 99 | 0 | Yes | Yes | 19.6 | 20.4 | -0.8 | 441DD5750E0F4BC98BD4B0F930D966E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3071 |  | 2015-11-23 | 2015-11-23 15:51 | 2015-11-23 15:51 | OTHER - FACD048J | 102 | 0 | Yes | Yes | 19.9 | 16.2 | 3.7 | 936AE5ACB1FD4D4D9E22E98893F93E23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4028 |  | 2015-10-12 | 2015-10-12 14:08 | 2015-10-12 14:36 | RHEEM - UNKNOWN | 57 | 5.7 | Yes | Yes | 17 | 19.9 | -2.9 | C77996F5F1FC45D1B88DA3169DFC73E6 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93722-4039 |  | 2015-09-29 | 2015-09-29 11:10 | 2015-11-06 13:52 | TEMPSTAR - PGME30G0907 | 73 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | DC3402249B2A4901ADD869781D66AF4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7133 |  | 2015-09-14 | 2015-09-14 13:59 | 2015-09-14 13:59 | CARRIER - 24ABA324A00310 | 64 | 0 | Yes | Yes | 24.3 | 19.9 | 4.4 | C989346DB7D44EAFB845BE0D01B2CE06 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3229 |  | 2015-09-23 | 2015-09-23 12:48 | 2015-09-23 12:48 | TEMPSTAR - PGAA42E1K1G4P042A3D1 | 82 | 0 | Yes | Yes | 19.4 | 19.8 | -0.4 | 1538B9683D4A4FA1BB94907689DAFB79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2245 |  | 2015-08-24 | 2015-08-24 10:08 | 2015-08-24 10:35 | YORK - DARA-F030N060B | 80 | 3.6 | Yes | Yes | 19.1 | 20.4 | -1.3 | 0A5237E8F436452880C5CCE0F8D874CA |  | R22 | TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | TXV | 4.5%
Clovis | CA | 93611-9281 |  | 2015-10-29 | 2015-10-29 08:57 | 2015-10-29 08:57 | CARRIER - 48NLT036300 | 84 | 0 | Yes | Yes | 24.7 | 19.8 | 4.9 | BE1C4EC7C6A44FDE94C0BA7A1DC00673 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2333 |  | 2015-08-05 | 2015-08-05 12:47 | 2015-08-05 12:47 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 17.3 | 18.8 | -1.5 | B2427FF7954F4350A465CF90AE85A953 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3148 |  | 2015-10-19 | 2015-10-19 09:58 | 2015-10-19 09:58 | OTHER - 38CK030310 | 69 | 0 | Yes | Yes | 19.3 | 16.8 | 2.5 | 37DE70445CC24FABAED7BBC7B89AEDF0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-2752 |  | 2015-07-27 | 2015-07-27 11:02 | 2015-07-27 11:45 | CARRIER - 48ESNA3606030 | 100 | 10.8 | Yes | Yes | 20.6 | 20.9 | -0.3 | E1A48C4766BA400BB1E4B0BEDD6D6450 |  | R410A | TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | TXV | 10.8%
Pittsburg | CA | 94565-5619 |  | 2015-08-21 | 2015-08-21 11:23 | 2015-08-21 11:23 | GOODMAN - 036-1B | 140 | 0 | Yes | Yes | 16 | 16.7 | -0.6 | 0B8977FE06B848F6994AA4DA5771AF16 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-2187 |  | 2015-11-05 | 2015-11-05 11:43 | 2015-11-05 12:02 | LENNOX - 10ACB4212P | 87 | 11.7 | Yes | Yes | 44 | 25.3 | 18.7 | 94535873426F47F9BC1BACE8AC2BF295 |  | R22 | Non-TXV |  | 13.45% | 0.86552 | 25.84% | [5 empty] | Non-TXV | 13.45%
Clovis | CA | 93612-2684 |  | 2015-09-03 | 2015-09-03 16:55 | 2015-09-03 16:55 | RHEEM - N/A | 85 | 0 | Yes | Yes | 20.8 | 20.1 | 0.8 | 90B05AB0DB69480DBA07F4967431605F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2208 |  | 2015-08-10 | 2015-08-10 12:05 | 2015-08-10 12:05 | YORK - D1NA042N0726B | 72 | 0 | Yes | Yes | 21.3 | 19.4 | 1.9 | C730762DFC1849CD84CFDE164AF2815F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1312 |  | 2015-09-17 | 2015-09-17 10:51 | 2015-09-17 10:51 | GIBSON - JT5BD030KA | 144 | 0 | Yes | Yes | 24.5 | 18.8 | 5.7 | 06AB0AC562014B609C0FF4AB2BA06DDD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3405 |  | 2015-07-29 | 2015-07-29 13:16 | 2015-07-29 13:16 | PAYNE - 597AN048A | 180 | 0 | Yes | Yes | 22.2 | 21.9 | 0.3 | 00B26AD0D7394C48B39767067C3BDAD2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4512 |  | 2015-10-27 | 2015-10-27 11:24 | 2015-10-27 11:24 | BRYANT - UNKNOWN | 81 | 0 | Yes | Yes | 25.1 | 19.6 | 5.5 | 381D8ABD274340D288FB640A4963B304 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3634 |  | 2015-08-21 | 2015-08-21 11:20 | 2015-08-21 11:20 | RUUD - VAHE-024JAS | 75 | 0 | Yes | Yes | 15.2 | 18.2 | -3 | 6AFDD40879004BFBBB54FBCF6473A9A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3694 |  | 2015-08-21 | 2015-08-21 10:38 | 2015-08-21 10:38 | GOODMAN - GSC130241AB | 99 | 0 | Yes | Yes | 14.2 | 17 | -2.8 | 913B49C06F9E49649B1BC9FFEDA4CCCB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6762 |  | 2015-10-07 | 2015-10-07 11:07 | 2015-10-07 11:28 | LENNOX - HS182618P | 42 | 7.9 | Yes | Yes | 16.4 | 18.2 | -1.8 | A8EE4AD9771A443997FDBD4CB416304A |  | R22 | Non-TXV |  | 18.81% | 0.8119 | 36.15% | [5 empty] | Non-TXV | 18.81%
Suisun City | CA | 94585-1316 |  | 2015-11-04 | 2015-11-04 14:25 | 2015-11-04 14:25 | GIBSON - JT5BD024 | 96 | 0 | Yes | Yes | 18.7 | 18.2 | 0.5 | D11A33B8794D40FC99FC2B24B043AC67 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-0301 |  | 2015-11-09 | 2015-11-09 12:54 | 2015-11-09 12:54 | DAY & NIGHT - NDYAC402AY | 124 | 0 | Yes | Yes | 23.6 | 19.6 | 4 | 35763DE6A1454773ADCFCDC8E454C3AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5538 |  | 2015-09-24 | 2015-09-24 13:46 | 2015-09-24 13:46 | RHEEM - RRKAA036JK08X | 62 | 0 | Yes | Yes | 22.2 | 23.1 | -0.9 | 08ED1CD279524AD0981DD49ABCDB7D84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-3727 |  | 2015-11-19 | 2015-11-19 11:31 | 2015-11-19 11:31 | PAYNE - 561CJO36-D | 84 | 0 | Yes | Yes | 17.9 | 19.3 | -1.4 | A544FD20390B43AF8980E37EF4667B44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1918 |  | 2015-09-04 | 2015-09-04 14:33 | 2015-09-04 14:33 | CARRIER - 38GS024330 | 48 | 0 | Yes | Yes | 21.2 | 19.7 | 1.5 | 68C584124D8C464583419D90C47C5B7D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-4451 |  | 2015-10-22 | 2015-10-22 14:45 | 2015-10-22 14:45 | BRYANT - 537GN036-A | 85 | 0 | Yes | Yes | 18.2 | 18.8 | -0.6 | 2CE384963A264339989EA7CC17BDCB03 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-4860 |  | 2015-09-22 | 2015-09-22 15:11 | 2015-09-22 15:11 | UNITARY PRODUCTS GROUP - FRCS0361CD | 150 | 0 | Yes | Yes | 21.2 | 20.2 | 1 | 8BF25B1C722A41529028681AE621E5F8 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5206 |  | 2015-08-11 | 2015-08-11 12:05 | 2015-08-11 12:05 | PAYNE - PA13NRO30J | 75 | 0 | Yes | Yes | 14.1 | 16.8 | -2.7 | 9C0FD92A1EE54227A0D6B549BBB158D0 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2631 |  | 2015-08-24 | 2015-08-24 11:40 | 2015-08-24 11:40 | PAYNE - PA14MA042-A | 135 | 0 | Yes | Yes | 21.6 | 19.3 | 2.3 | 628EB7A57B0045C590DB4EF3B038F6F4 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4450 |  | 2015-08-12 | 2015-08-12 08:59 | 2015-08-12 08:59 | OTHER - N/A | 85 | 0 | Yes | Yes | 16.8 | 18.7 | -1.9 | 5EAFE5EC79DA45AEA9F0124D01BFDB36 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1336 |  | 2015-08-28 | 2015-08-28 10:32 | 2015-08-28 10:32 | RHEEM - RAKA030JAS | 68 | 0 | Yes | Yes | 15.6 | 18.5 | -2.9 | 2B04CB04D1314AD5BFC7F088A0B8B8C3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4305 |  | 2015-08-10 | 2015-08-10 11:41 | 2015-08-10 11:41 | CARRIER - N/A | 85 | 0 | Yes | Yes | 19.9 | 21.3 | -1.4 | 20622555E49C4DA6B59BBAB007D2132D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4987 |  | 2015-08-26 | 2015-08-26 13:37 | 2015-08-26 13:37 | YORK - H1RA042S06D | 84 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | D1908A6C4D044B7BAFFCEACEF9F4F35A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-3305 |  | 2015-08-21 | 2015-08-21 12:21 | 2015-08-21 12:42 | GOODMAN - CK60-1C | 149 | 7.5 | Yes | Yes | 18.7 | 20.7 | -2 | C7376E739048475BB9D637879E882B45 |  | R22 | TXV |  | 5.034% | 0.94966 | 9.673% | [5 empty] | TXV | 5.034%
Fresno | CA | 93705-2237 |  | 2015-08-19 | 2015-08-19 15:54 | 2015-08-19 15:54 | GOODMAN - GPG1336070M41BA | 70 | 0 | Yes | Yes | 26.6 | 21.5 | 5.1 | 1AE757BF26C34BB78976223F22213807 |  | R410A | TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1336 |  | 2015-09-08 | 2015-09-08 09:18 | 2015-09-08 09:18 | GOODMAN - CKL42-1 | 50 | 0 | Yes | Yes | 19.6 | 21.7 | -2.1 | 366B61232D4E40248D68801AF2A12492 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2350 |  | 2015-09-28 | 2015-09-28 10:42 | 2015-09-28 10:42 | DAY & NIGHT - N/A | 85 | 0 | Yes | Yes | 19.8 | 18 | 1.8 | 5B682A0E88B040BD8547DF11AFA5792D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3663 |  | 2015-09-14 | 2015-09-14 10:41 | 2015-09-14 10:41 | DAY & NIGHT - 569BJ018 | 51 | 0 | Yes | Yes | 16.9 | 19.4 | -2.5 | 11802B5BB27E4C978B9D3330CC25B747 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1665 |  | 2015-08-21 | 2015-08-21 12:45 | 2015-08-21 12:45 | GUARDIAN - UNK | 101 | 0 | Yes | Yes | 23.3 | 18.7 | 4.6 | 014E751015564DA78A6D932F0D06B1C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6414 |  | 2015-09-01 | 2015-09-01 12:36 | 2015-09-01 12:36 | NORDYNE - GS3B024KA | 64 | 0 | Yes | Yes | 13.5 | 16.2 | -2.7 | 86D8E851D7B1485D8055FE6A34CBAD47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7922 |  | 2015-10-07 | 2015-10-07 10:56 | 2015-10-07 10:56 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 24.1 | 23.1 | 1 | 74EA2DB566AF4E11A954A66A89AA3242 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3121 |  | 2015-08-19 | 2015-08-19 09:37 | 2015-08-19 09:37 | ICP - N4A660GKA101 | 105 | 0 | Yes | Yes | 22.9 | 22.1 | 0.8 | AC8361A7751A471C88718D95B1DB4F1F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-1490 |  | 2015-08-26 | 2015-08-26 14:04 | 2015-08-26 14:30 | CARRIER - 48NLT042300 | 85 | 16.3 | Yes | Yes | 19.4 | 21.3 | -1.9 | 9BE95B2600364EE5983A1968E132FEFC |  | R22 | Non-TXV |  | 19.18% | 0.80824 | 36.85% | [5 empty] | Non-TXV | 19.18%
Fairfield | CA | 94533-7011 |  | 2015-10-13 | 2015-10-13 13:41 | 2015-10-13 13:41 | DAY & NIGHT - 591ANX042000AAA | 112 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 04A1E89B7DB24C3A84CAF9544495B55C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-6501 |  | 2015-09-24 | 2015-09-24 15:47 | 2015-09-24 15:47 | BDP - 583ANW036060 | 67 | 0 | Yes | Yes | 25.9 | 20.2 | 5.7 | 2EAD37AFFD6B4C5CAAAF87F1EAD2A136 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5172 |  | 2015-08-26 | 2015-08-26 09:24 | 2015-08-26 09:24 | RHEEM - UKN | 90 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | C232A68C6AB745799EE6446903529010 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-5120 |  | 2015-08-28 | 2015-08-28 10:05 | 2015-08-28 10:05 | BRYANT - 114ANA024-D | 69 | 0 | Yes | Yes | 25.9 | 20.9 | 5 | 8CA6AF7BD0F2403EB9D94026613483DD |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3800 |  | 2015-10-02 | 2015-10-02 09:20 | 2015-10-02 09:20 | ICP - PGC030K060A | 52 | 0 | Yes | Yes | 24.8 | 20.8 | 4 | 56083FAC46C74D309A0A0EF42023727B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4446 |  | 2015-08-07 | 2015-08-07 13:10 | 2015-08-07 13:10 | CARRIER - PA10JA048-A | 100 | 0 | Yes | Yes | 22.7 | 19.3 | 3.4 | DB7D8D0249D84005BEFA1DC833665C7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2609 |  | 2015-10-09 | 2015-10-09 10:20 | 2015-10-09 10:20 | YORK - D1NH036N07206C | 108 | 0 | Yes | Yes | 19.9 | 19.3 | 0.6 | DD1D693A4B184BE7BFD99D28EE9B4FA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3948 |  | 2015-08-05 | 2015-08-05 10:50 | 2015-08-05 10:50 | CARRIER - 38TK042300 | 85 | 0 | Yes | Yes | 19.8 | 15.8 | 4 | F8C7C150D2AA443686B44624E13FDEEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5215 |  | 2015-08-18 | 2015-08-18 12:20 | 2015-08-18 12:20 | ICP - WPGG3364060LKC1 | 103 | 0 | Yes | Yes | 21.8 | 24 | -2.2 | 1A191288131A4F64A66B2633775A3F12 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1748 |  | 2015-09-23 | 2015-09-23 11:08 | 2015-09-23 11:08 | RHEEM - HC-80-36-21C | 85 | 0 | Yes | Yes | 17.9 | 15.2 | 2.7 | 24D88D351E9B4390B89FFCD5C1899B63 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4725 |  | 2015-09-14 | 2015-09-14 15:27 | 2015-09-14 15:27 | GOODMAN - UNK | 69 | 0 | Yes | Yes | 17.5 | 19.3 | -1.8 | 94042A5C32214CF1965092C184F29D4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4641 |  | 2015-07-31 | 2015-07-31 10:08 | 2015-07-31 10:08 | CARRIER - 38THO60300 | 172 | 0 | Yes | Yes | 25.3 | 19.7 | 5.6 | 22BEDAC8637B400F99BE755F7734E2BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-3540 |  | 2015-08-04 | 2015-08-04 15:43 | 2015-08-04 15:43 | - CA306VKA1 | 85 | 0 | Yes | Yes | 17.1 | 18.4 | -1.3 | 51C08BE558B54FDFA28E16E0D297C5C7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2165 |  | 2015-10-02 | 2015-10-02 14:07 | 2015-10-02 14:36 | RHEEM - RRKA-A042JK08E | 69 | 9.9 | Yes | Yes | 21.2 | 22.8 | -1.6 | 6552653297944B99A3C10051784FA368 |  | R22 | Non-TXV |  | 14.35% | 0.85652 | 27.57% | [5 empty] | Non-TXV | 14.35%
Bakersfield | CA | 93309-6074 |  | 2015-10-02 | 2015-10-02 12:56 | 2015-10-02 12:56 | OTHER - 80AW36-105 | 85 | 0 | Yes | Yes | 22.8 | 22.9 | -0.1 | 782D03369B8D48AD97AA370B65ADC9DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2032 |  | 2015-10-14 | 2015-10-14 14:08 | 2015-10-14 14:08 | OTHER - UNKNOWN | 76 | 0 | Yes | Yes | 18.8 | 21.2 | -2.4 | 8CBCB28CDEF441F0AA5135D0051519BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1139 |  | 2015-10-02 | 2015-10-02 13:42 | 2015-10-02 13:42 | HEIL - HAC236AKA1 | 113 | 0 | Yes | Yes | 20.9 | 21.8 | -0.9 | A422AE902E7041149235AB2519460F77 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1837 |  | 2015-09-30 | 2015-09-30 12:24 | 2015-11-06 13:56 | LENNOX - HS16511V8P | 138 | 0 | Yes | Yes | 25.8 | 20.4 | 5.4 | C7693D9E9C3E4438B968A3DE16AE2C74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2451 |  | 2015-07-30 | 2015-07-30 12:26 | 2015-07-30 12:26 | PAYNE - 593BJ042-A | 85 | 0 | Yes | Yes | 16.8 | 18.8 | -2 | 9845F5D648824934B0CF65BFAEE9EE84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2763 |  | 2015-08-12 | 2015-08-12 11:39 | 2015-08-12 11:39 | RHEEM - RRNA-B036JK06X | 83 | 0 | Yes | Yes | 22.7 | 19.5 | 3.2 | 5256F56B06B74C7AB250B3ACE822E0AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7372 |  | 2015-10-08 | 2015-10-08 16:05 | 2015-10-08 16:05 | CARRIER - 38CKC036---341 | 70 | 0 | Yes | Yes | 20.9 | 21.7 | -0.8 | F102D305A0CF41F2B04F150C38E63589 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-9039 |  | 2015-08-26 | 2015-08-26 18:04 | 2015-08-26 18:04 | TRANE - YCP060F1MOAC` | 160 | 0 | Yes | Yes | 20.6 | 21.7 | -1.1 | 2AC1C0A1B1A74738BABBDFC374BBC571 |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1128 |  | 2015-07-31 | 2015-07-31 14:54 | 2015-07-31 14:54 | OTHER - H2DH042506B | 128 | 0 | Yes | Yes | 18.7 | 18.9 | -0.2 | D890183B4651437EBE0C960372C066B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4730 |  | 2015-08-14 | 2015-08-14 11:00 | 2015-08-14 11:00 | TRANE - 2YCC3024A1064AA | 72 | 0 | Yes | Yes | 21 | 17.7 | 3.3 | 9B7C2A1C9B3A43D2887282ED2038531D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6576 |  | 2015-10-02 | 2015-10-02 10:35 | 2015-10-02 10:54 | BDP - 36/80YAC-108C | 66 | 19.6 | Yes | Yes | 19.9 | 21 | -1.1 | 8DA732A2AA644CA1A466B753D0E6D4AB |  | R22 | Non-TXV |  | 29.7% | 0.70303 | 57.07% | [5 empty] | Non-TXV | 29.7%
Pittsburg | CA | 94565-6837 |  | 2015-10-01 | 2015-10-01 16:22 | 2015-10-01 16:22 | PAYNE - PA13NR030-J | 75 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | 8D3AE84FE339467D88C7BCB883D4E990 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7140 |  | 2015-09-18 | 2015-09-18 15:53 | 2015-09-18 16:11 | CARRIER - 24ABA336A310 | 84 | 13.6 | Yes | Yes | 18.3 | 21.4 | -3.1 | A0AC2DA86F0341DFBE3285F5533C759E |  | R410A | TXV |  | 16.19% | 0.8381 | 31.11% | [5 empty] | TXV | 16.19%
Fresno | CA | 93723-9251 |  | 2015-11-23 | 2015-11-23 15:45 | 2015-11-23 15:45 | BRYANT - 588ANW036060ADAF | 72 | 0 | Yes | Yes | 19.9 | 19 | 0.9 | 24562908EF054BB9AD2248813BB992B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1101 |  | 2015-08-03 | 2015-08-03 12:13 | 2015-08-03 12:13 | CARRIER - 38TKB036-341 | 85 | 0 | Yes | Yes | 16.5 | 18.7 | -2.2 | 120405ABEED7469A9961E1C08494DAF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-4109 |  | 2015-08-07 | 2015-08-07 10:48 | 2015-08-07 10:48 | CARRIER - 38CKC36350 | 88 | 0 | Yes | Yes | 21.1 | 17.7 | 3.4 | A454382C3E5A49928DBAD44754240555 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5331 |  | 2015-08-10 | 2015-08-10 10:07 | 2015-08-10 10:07 | CARRIER - 24AB348W310 | 85 | 0 | Yes | Yes | 19.9 | 21.5 | -1.6 | 14E64CD08D9C40FD8DF15B869C33D4F3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3078 |  | 2015-10-01 | 2015-10-01 15:24 | 2015-11-05 14:40 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 26.5 | 21 | 5.5 | 354DAE27770E45C0BD4C43AB76D18A9F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-0000 |  | 2015-11-05 | 2015-11-05 13:23 | 2015-11-05 13:39 | LENNOX - 13ACC04823001 | 158 | 5.1 | Yes | Yes | 26.6 | 20.9 | 5.7 | 7FDAF17117F04F0790203E556A4FA38D |  | R22 | Non-TXV |  | 3.228% | 0.96772 | 6.203% | [5 empty] | Non-TXV | 3.228%
Fresno | CA | 93705-2822 |  | 2015-10-23 | 2015-10-23 12:59 | 2015-10-23 12:59 | CARRIER - 588ANW0481OOACAG | 101 | 0 | Yes | Yes | 23.2 | 19.8 | 3.4 | D0CC4FB00CC64305B0D4489AFC34E0FD | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5584 |  | 2015-08-10 | 2015-08-10 10:43 | 2015-08-10 10:43 | YORK - H2RD060S06B | 162 | 0 | Yes | Yes | 20.4 | 22.6 | -2.2 | 9C6E295B8C6F43809175EDFA701D1ABC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4724 |  | 2015-09-25 | 2015-09-25 10:54 | 2015-09-25 10:54 | RHEEM - RRNA-B048JK10K | 153 | 0 | Yes | Yes | 20.6 | 21 | -0.4 | BF2243D59835427988A39B1AF9E48CC4 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93730-0850 |  | 2015-10-02 | 2015-10-02 12:19 | 2015-10-02 12:19 | RUUD - UAFD-036JAS | 80 | 0 | Yes | Yes | 22 | 22.8 | -0.8 | 139B98EE19674A6A99CF10E432FF3864 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7701 |  | 2015-09-02 | 2015-09-02 17:23 | 2015-09-02 17:23 | TRANE - TTB742A100A0 | 104 | 0 | Yes | Yes | 25.1 | 23.7 | 1.4 | 796BFC99144F43E086392F28BACB8DEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1221 |  | 2015-09-04 | 2015-09-04 16:09 | 2015-09-04 16:09 | AMANA - ASX130361BA | 95 | 0 | Yes | Yes | 18.5 | 18.7 | -0.2 | 7DC432E755224AFFBB50DF9084A94556 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2330 |  | 2015-08-24 | 2015-08-24 15:03 | 2015-08-24 15:21 | GOODMAN - CE60-1EB | 167 | 46.4 | Yes | Yes | 17.2 | 18 | -0.8 | 630400E2EAC343E9A2F1508296147F0A |  | R22 | Non-TXV |  | 27.78% | 0.72216 | 53.4% | [5 empty] | Non-TXV | 27.78%
Brentwood | CA | 94513-7133 |  | 2015-10-27 | 2015-10-27 09:29 | 2015-10-27 09:29 | BRYANT - UNKNWON | 91 | 0 | Yes | Yes | 23.4 | 20.3 | 3.1 | 013F3B5E929C4FFFB3EA98B32875B091 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7420 |  | 2015-10-26 | 2015-10-26 11:01 | 2015-10-26 11:01 | GOODMAN - CK42-1C | 92 | 0 | Yes | Yes | 21.5 | 21.6 | -0.1 | B6464662305F4D2984A43A50053DBBF0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5216 |  | 2015-08-26 | 2015-08-26 15:39 | 2015-08-26 16:01 | BDP - 585 | 85 | 7.6 | Yes | Yes | 24 | 20.9 | 3.1 | 88B098392BE042C389E7B8AB73CCDD04 |  | R22 | Non-TXV |  | 8.941% | 0.91059 | 17.18% | [5 empty] | Non-TXV | 8.941%
Fresno | CA | 93722-7163 |  | 2015-11-12 | 2015-11-12 12:56 | 2015-11-12 12:56 | GIBSON - J53BC036KA | 129 | 0 | Yes | Yes | 20.2 | 17.2 | 3 | AD7CEB26F36E4EF09E35B97DD9D64AEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-2505 |  | 2015-08-11 | 2015-08-11 09:42 | 2015-08-11 09:58 | CARRIER - 38ETG030300 | 133 | 10.8 | Yes | Yes | 24.7 | 21.8 | 2.9 | E4D6CFCCE99D477C941F8486B565329B |  | R410A | TXV |  | 8.12% | 0.9188 | 15.61% | [5 empty] | TXV | 8.12%
San Ramon | CA | 94582-2505 |  | 2015-08-11 | 2015-08-11 09:46 | 2015-08-11 10:03 | CARRIER - 38ETG024300 | 85 | 7.7 | Yes | Yes | 25.3 | 21.5 | 3.8 | 9971F55D67514176AA76D84391F8D443 |  | R410A | TXV |  | 9.059% | 0.90941 | 17.41% | [5 empty] | TXV | 9.059%
Vacaville | CA | 95688-9129 |  | 2015-07-29 | 2015-07-29 12:23 | 2015-07-29 12:23 | GOODMAN - CLK301D | 70 | 0 | Yes | Yes | 22.2 | 23.5 | -1.3 | 8310DBEE934F4861900D81B6C6664866 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0401 |  | 2015-11-09 | 2015-11-09 12:27 | 2015-11-09 12:27 | LENNOX - 13ACD04823002 | 204 | 0 | Yes | Yes | 21.2 | 18.2 | 3 | 310EFA0D248B46D1A8AA3FCB40435AED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1758 |  | 2015-09-23 | 2015-09-23 15:48 | 2015-09-23 15:48 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 17.8 | 20.4 | -2.6 | F415AFC6C4DA4EEC8C44BA7D559728AF |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-6557 |  | 2015-08-25 | 2015-08-25 12:46 | 2015-08-25 13:10 | BDP - 585G036060 | 82 | 46.2 | Yes | Yes | 20.5 | 21.5 | -1 | 2214931B7EA64067800F3FCDA610D6A6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 56.34% | 0.43659 | 108.3% | [5 empty] | Non-TXV | 56.34%
Fresno | CA | 93722-3146 |  | 2015-11-06 | 2015-11-06 14:48 | 2015-11-06 14:48 | OTHER - 38CK030300 | 68 | 0 | Yes | Yes | 25.8 | 20.4 | 5.4 | CE58181FD1AC4875924972328C35F1A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3603 |  | 2015-08-10 | 2015-08-10 09:39 | 2015-08-10 09:39 | BDP - 585HJ036060 | 102 | 0 | Yes | Yes | 24.6 | 21.1 | 3.6 | C39AA6EF1C6A4880B4E79B9E6805E233 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5408 |  | 2015-10-22 | 2015-10-22 13:27 | 2015-10-22 13:27 | ALLEGIANCE - UNKNOWN | 92 | 0 | Yes | Yes | 26.5 | 22.4 | 4.1 | 0EE160F4AF4B48428B9D6123910DC4DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5337 |  | 2015-10-26 | 2015-10-26 14:15 | 2015-10-26 14:15 | PAYNE - PA13NR036-H | 83 | 0 | Yes | Yes | 24 | 21.2 | 2.8 | 03BDEF7059FF4D1391BAEEEF6AEA6579 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6079 |  | 2015-08-26 | 2015-08-26 08:58 | 2015-08-26 08:58 | ICP - PGF036K060A | 71 | 0 | Yes | Yes | 23 | 21.5 | 1.5 | B4CBFE31A63144739DE402E7C3C78803 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7212 |  | 2015-08-12 | 2015-08-12 08:49 | 2015-08-12 08:49 | RHEEM - RRNL-B042JK08X | 112 | 0 | Yes | Yes | 23.3 | 19.9 | 3.5 | D98F68B736074E53ABFB35EF9E7B44F3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7925 |  | 2015-09-24 | 2015-09-24 10:35 | 2015-09-24 10:35 | ARCOAIRE - PGAA42C1K6 | 96 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | E4C33FCFB1D045D7A31312F8C98D8B2C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9143 |  | 2015-11-09 | 2015-11-09 10:37 | 2015-11-09 10:37 | CARRIER - 5856J036067 | 82 | 0 | Yes | Yes | 22.5 | 17.9 | 4.6 | 4B50B6F9960B4D04AE575A3CC2BCB74F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7147 |  | 2015-09-16 | 2015-09-16 11:16 | 2015-09-16 11:41 | CARRIER - 24ABA336A310 | 84 | 13.6 | Yes | Yes | 19.7 | 18.2 | 1.5 | E39C455C429C48C18E384817660EB017 |  | R410A | TXV |  | 16.19% | 0.8381 | 31.11% | [5 empty] | TXV | 16.19%
Fresno | CA | 93722-3630 |  | 2015-10-12 | 2015-10-12 13:51 | 2015-10-12 13:51 | PAYNE - PYGNAA36060NA | 100 | 0 | Yes | Yes | 19.5 | 19 | 0.5 | C4C185AF03A44230BC52A309FE5B2B0D |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-6902 |  | 2015-09-11 | 2015-09-11 11:38 | 2015-09-11 11:38 | CARRIER - N/A | 85 | 0 | Yes | Yes | 18.4 | 19.7 | -1.3 | A3CA9B9DE1A84D5AA1FAF25CC7E40215 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-9327 |  | 2015-10-14 | 2015-10-14 09:34 | 2015-10-14 09:34 | RHEEM - N/A | 85 | 0 | Yes | Yes | 24.9 | 20.4 | 4.5 | 8EE11C1FEA0F4E3FA94FD80838A72528 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2332 |  | 2015-08-12 | 2015-08-12 15:09 | 2015-08-12 15:09 | ICP - N2A348AKA300 | 120 | 0 | Yes | Yes | 21.5 | 21.3 | 0.2 | E683EA07C2B542AAAEEECBD2C1C621EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3507 |  | 2015-10-20 | 2015-10-20 15:36 | 2015-10-20 15:36 | RHEEM - RRNL-B042JK08X | 64 | 0 | Yes | Yes | 19.6 | 19.9 | -0.3 | EA94FBBC9C62490790EC1F3B5CD982C1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-6658 |  | 2015-08-21 | 2015-08-21 15:00 | 2015-08-21 15:28 | RHEEM - RAHE-048JAS | 114 | 12.2 | Yes | Yes | 14.6 | 19.6 | -5 | 09EA9287964B4516A704718FC1769322 | Add refrigerant: 23.3 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.7% | 0.89298 | 20.57% | [5 empty] | Non-TXV | 10.7%
Woodland | CA | 95776-6103 |  | 2015-10-19 | 2015-10-19 09:42 | 2015-10-19 09:42 | GOODMAN - CLQ60-1 | 312 | 0 | Yes | Yes | 19.8 | 18.7 | 1.1 | BACACA8608254AF48CDE706172762C17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-5018 |  | 2015-09-01 | 2015-09-01 08:17 | 2015-09-01 08:17 | CARRIER - 38EH036300 | 116 | 0 | Yes | Yes | 18.3 | 16.1 | 2.2 | F8C499C0A41E4879881DBDB00F5F3002 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4771 |  | 2015-11-06 | 2015-11-06 10:08 | 2015-11-06 10:08 | CARRIER - 48NLT030320 | 66 | 0 | Yes | Yes | 23 | 21.3 | 1.7 | E4532B21265D41058672B1E60AEB6059 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1277 |  | 2015-08-24 | 2015-08-24 16:50 | 2015-08-24 16:50 | RHEEM - RRKA-A036JK08X | 62 | 0 | Yes | Yes | 18.9 | 20.4 | -1.5 | C72780EC2354496AA6258F3CCBA59D6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1236 |  | 2015-10-21 | 2015-10-21 13:25 | 2015-10-21 13:25 | LENNOX - 12GCS036-75-1PA | 110 | 0 | Yes | Yes | 19 | 21 | -2 | 85CD727E436948FFB4CE8A94E03F2977 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-3250 |  | 2015-08-03 | 2015-08-03 10:35 | 2015-08-03 10:35 | GOODMAN - CKT48-18 | 85 | 0 | Yes | Yes | 20.6 | 20.2 | 0.5 | 8CAD18B51B9B409387F6BE436E6EA583 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-2428 |  | 2015-10-14 | 2015-10-14 11:23 | 2015-10-14 11:23 | LENNOX - 10GS036X753PB | 58 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 73592B186DE848CFA44ADD318C1EC884 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4460 |  | 2015-11-04 | 2015-11-04 10:04 | 2015-11-04 10:04 | CARRIER - UNKNOWN | 83 | 0 | Yes | Yes | 22 | 19.7 | 2.3 | EDD84E0B7CD1403693FB6F5A853FBB01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9031 |  | 2015-11-06 | 2015-11-06 12:20 | 2015-11-06 12:20 | GOODMAN - GPG123007018 | 73 | 0 | Yes | Yes | 20.5 | 18.2 | 2.3 | D56746521EFF47DF95921FCAF8825D27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9031 |  | 2015-11-06 | 2015-11-06 12:26 | 2015-11-06 12:26 | GOODMAN - GPG123007018 | 73 | 0 | Yes | Yes | 18.5 | 19.1 | -0.6 | 909A297A482A47F1B21A46C83A1336C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1755 |  | 2015-08-11 | 2015-08-11 12:13 | 2015-08-11 12:38 | BDP - 588ANW030040ACAD | 55 | 2 | Yes | Yes | 27.1 | 23.7 | 3.4 | C43A6E05E7204EFBA0B2B48E54474C28 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Fresno | CA | 93722-0421 |  | 2015-10-16 | 2015-10-16 13:28 | 2015-10-16 13:28 | LENNOX - 13ACD04223002 | 111 | 0 | Yes | Yes | 20 | 17.3 | 2.7 | 6BA80FB0C9E54D8DB64CBB8EF8A7A7CC |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7769 |  | 2015-08-03 | 2015-08-03 12:13 | 2015-08-03 12:13 | CARRIER - 38TH048310 | 85 | 0 | Yes | Yes | 14.5 | 17.5 | -3 | 6E80B89CE7B649C2A2F54032B576558D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4636 |  | 2015-10-15 | 2015-10-15 15:10 | 2015-10-15 15:10 | YORK - D1NA024N03606A | 50 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | 07F2CEAC84BC4E6C8EA808A63DF1BF4F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1610 |  | 2015-08-06 | 2015-08-06 12:50 | 2015-08-06 12:50 | NORDYNE - R4GE-X36K100X | 124 | 0 | Yes | Yes | 19.5 | 19.5 | 0 | D5FFF8956A9946458D3F4627FBEE9F21 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3506 |  | 2015-08-18 | 2015-08-18 12:40 | 2015-08-18 12:40 | BRYANT - 598BN060-A | 220 | 0 | Yes | Yes | 24.5 | 24.2 | 0.3 | 8EC4939601394A48B0E9F438A18A5EF8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-9201 |  | 2015-11-06 | 2015-11-06 10:44 | 2015-11-06 10:44 | ICP - PGF060K100B | 136 | 0 | Yes | Yes | 19.1 | 19.7 | -0.6 | B56255FB49A346A3907D7DAE490A941E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-4102 |  | 2015-11-05 | 2015-11-05 14:31 | 2015-11-05 14:31 | YORK - D1NA036N05606C | 68 | 0 | Yes | Yes | 19.8 | 19.8 | 0 | 820420E90B5046908162D44A75B2AE33 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3164 |  | 2015-10-30 | 2015-10-30 09:02 | 2015-10-30 09:02 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 23.5 | 19.3 | 4.2 | 8B903DA52F55410C9FC6D0586833C1F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2619 |  | 2015-08-11 | 2015-08-11 12:36 | 2015-08-11 13:01 | AMERICAN STANDARD - YCX036G1M0AB | 109 | 6 | Yes | Yes | 22.3 | 22 | 0.3 | 08B9EE542CC64BED991EA6556224390F |  | R22 | Non-TXV |  | 5.505% | 0.94495 | 10.58% | [5 empty] | Non-TXV | 5.505%
San Jose | CA | 95148-2031 |  | 2015-09-03 | 2015-09-03 12:43 | 2015-09-03 12:43 | CARRIER - 24ANA736A300 | 151 | 0 | Yes | Yes | 19.3 | 21.2 | -1.9 | 01A80FB1D09543DD9F842F6294C03DD4 |  | R410A | TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1519 |  | 2015-08-18 | 2015-08-18 15:12 | 2015-08-18 15:12 | OTHER - RACK-024JAZQ | 24 | 0 | Yes | Yes | 18.4 | 20.1 | -1.7 | 945B5CDA3F6A4EBA9D6E5062FEB64F6E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94597-2115 |  | 2015-08-03 | 2015-08-03 10:02 | 2015-08-03 10:02 | TRANE - TTR060C100A3 | 144 | 0 | Yes | Yes | 23.8 | 18.2 | 5.6 | 65B5C264FE8F493AA37F11FB6CEF1AA2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4415 |  | 2015-10-07 | 2015-10-07 09:43 | 2015-10-07 09:43 | CARRIER - 38CKC042310 | 93 | 0 | Yes | Yes | 17.9 | 18.9 | -1 | 8978A3263B2846DDBC6960A00A714EC2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94583-2729 |  | 2015-08-10 | 2015-08-10 10:40 | 2015-08-10 10:40 | TRANE - 2TTB0042A1000AA | 95 | 0 | Yes | Yes | 22.5 | 21.2 | 1.3 | 48303A963D604BE2B59C3019BE6BB1F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4025 |  | 2015-10-08 | 2015-10-08 09:27 | 2015-10-08 09:27 | YORK - DBYP-F036N070A | 100 | 0 | Yes | Yes | 28.1 | 23.3 | 4.8 | 166DF56564134A2DAAE4AF462FCCCC73 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2438 |  | 2015-07-29 | 2015-07-29 09:34 | 2015-07-29 09:34 | TRANE - R40B-302-F | 85 | 0 | Yes | Yes | 23.8 | 19.3 | 4.5 | DCDACBFFABC64FF6922E571E73D71161 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6155 |  | 2015-08-05 | 2015-08-05 09:22 | 2015-08-05 09:22 | YORK - D2NP036NO7206NXA | 109 | 0 | Yes | Yes | 23.6 | 17.7 | 5.9 | 72A067C87F5F4315979E7AC09B78E1D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2549 |  | 2015-10-06 | 2015-10-06 12:42 | 2015-10-06 12:42 | TRANE - TTR048D100A2 | 87 | 0 | Yes | Yes | 21.6 | 19.3 | 2.3 | B94E527FA3884BB2A7ED6E7FA76AC29D |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1323 |  | 2015-08-03 | 2015-08-03 13:47 | 2015-08-03 13:47 | YORK - TCGD36S21S1A | 65 | 0 | Yes | Yes | 27.8 | 21.9 | 5.9 | 36F9DB033DAE4AAE8CCB028C65724C2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4465 |  | 2015-10-07 | 2015-10-07 10:36 | 2015-10-07 10:36 | PAYNE - PA13NR048-E | 178 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | 6ABA24112A5C48EAAC3AC09CC1E3B651 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1526 |  | 2015-11-06 | 2015-11-06 08:34 | 2015-11-06 08:34 | YORK - DAYP-F036N070A | 109 | 0 | Yes | Yes | 24.2 | 20.6 | 3.6 | 6BAE41B60EB547DDA8E2F8F6E1F8E5D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3406 |  | 2015-11-05 | 2015-11-05 10:19 | 2015-11-05 10:19 | BRYANT - 577CNWA24040NA | 96 | 0 | Yes | Yes | 18.7 | 19.1 | -0.4 | C9B909FF13E743818F3651C85D2BD2B5 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2809 |  | 2015-10-13 | 2015-10-13 08:36 | 2015-10-13 09:05 | CARRIER - N/A | 85 | 14 | Yes | Yes | 17.1 | 17.2 | -0.1 | B18B9CC100EF4EE6B845270448FBD31E |  | R22 | Non-TXV |  | 16.47% | 0.83529 | 31.65% | [5 empty] | Non-TXV | 16.47%
Fresno | CA | 93727-5859 |  | 2015-11-05 | 2015-11-05 13:45 | 2015-11-05 13:45 | LENNOX - 13ACD04223002 | 111 | 0 | Yes | Yes | 24.1 | 22.1 | 2 | 64F7DB846A674820A73BE29641253532 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3626 |  | 2015-10-07 | 2015-10-07 14:56 | 2015-10-07 14:56 | CARRIER - UNKNOWN | 110 | 0 | Yes | Yes | 18.8 | 20.9 | -2.1 | 343CA25C179540EB8D6CE43657681556 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6742 |  | 2015-07-30 | 2015-07-30 08:47 | 2015-07-30 08:47 | GOODMAN - CKL361L | 84 | 0 | Yes | Yes | 15.4 | 18.2 | -2.8 | 9B3B856BC0D94FD592332B7EB2DBD3A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1312 |  | 2015-09-17 | 2015-09-17 11:06 | 2015-09-17 11:06 | GIBSON - JT5BD030KA | 144 | 0 | Yes | Yes | 18.9 | 19.9 | -1 | 69AEA7BBB91C46D796C81B66D8C443FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-0000 |  | 2015-08-06 | 2015-08-06 12:11 | 2015-08-06 12:11 | CARRIER - 24ABC636A300 | 85 | 0 | Yes | Yes | 16 | 18.8 | -2.8 | A2C9E49FA4AB4F53BB2A443FD8F507B8 |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4873 |  | 2015-10-07 | 2015-10-07 10:14 | 2015-10-07 10:14 | RHEEM - UNKNOWN | 62 | 0 | Yes | Yes | 19.1 | 21.7 | -2.6 | 5427F23F7D624668B5215B2F740DAC3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3803 |  | 2015-08-06 | 2015-08-06 14:06 | 2015-08-06 14:06 | AMANA - R2A348GKC1 | 85 | 0 | Yes | Yes | 18.7 | 20.4 | -1.7 | 63FF20C11A544AF8B4EDE5F6F70BC65C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3463 |  | 2015-07-29 | 2015-07-29 15:16 | 2015-07-29 15:16 | LENNOX - 14ACX036 | 102 | 0 | Yes | Yes | 18.1 | 20.7 | -2.6 | 60FF6CFB4BBE4AF2AE1DFBDF27D5E93A |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6528 |  | 2015-08-05 | 2015-08-05 10:29 | 2015-08-05 10:29 | DAY & NIGHT - 591ANX048000ACAA | 128 | 0 | Yes | Yes | 23 | 18.8 | 4.2 | 160FB69B38EF48A68C0E4F9775439DDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4355 |  | 2015-07-31 | 2015-07-31 17:41 | 2015-07-31 17:41 | CARRIER - 38BRC048330 | 85 | 0 | Yes | Yes | 15.8 | 17.6 | -1.8 | 40DC32374EC94506BC1EC583E418B203 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3048 |  | 2015-08-10 | 2015-08-10 12:14 | 2015-08-10 12:14 | ICP - D1NH036N05606C | 108 | 0 | Yes | Yes | 20.6 | 23.1 | -2.5 | EDF6681E21624828984BCDEACF7E0528 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2442 |  | 2015-08-11 | 2015-08-11 11:13 | 2015-08-11 11:13 | RHEEM - RRKA-A036JK06E | 62 | 0 | Yes | Yes | 19.2 | 20.7 | -1.5 | 47216ACE81B64F8CB7BECBBA3B2EB749 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4850 |  | 2015-09-18 | 2015-09-18 09:20 | 2015-09-18 11:04 | GOODMAN - | 85 | 16.2 | Yes | Yes | 21.6 | 18.7 | 2.9 | 9F75667F4B1B4B7999F7139EC3FA97EB |  | R22 | Non-TXV |  | 19.06% | 0.80941 | 36.63% | [5 empty] | Non-TXV | 19.06%
Suisun City | CA | 94585-3214 |  | 2015-10-08 | 2015-10-08 10:10 | 2015-10-08 10:10 | PAYNE - 591ANX036000AAAA | 90 | 0 | Yes | Yes | 20.1 | 18.8 | 1.3 | E922768D7FB4477DBDE06E3EC77F9AB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5232 |  | 2015-08-05 | 2015-08-05 14:25 | 2015-08-05 14:25 | TRANE - YCCO42F1MOBH | 101 | 0 | Yes | Yes | 22.8 | 19.7 | 3.1 | 586FB3F7502842E0836CC9CDFE6DF4B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4847 |  | 2015-09-21 | 2015-09-21 08:29 | 2015-09-21 08:29 | PAYNE - PA13NAO36-E | 85 | 0 | Yes | Yes | 22.3 | 20.9 | 1.4 | 107990410F56427689789E3617A5287B |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3508 |  | 2015-09-08 | 2015-09-08 12:05 | 2015-09-08 12:05 | OTHER - R2A330GKR1 | 75 | 0 | Yes | Yes | 19 | 18.8 | 0.3 | 771B488C282F4EDDA245DFBF847C4429 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3523 |  | 2015-10-15 | 2015-10-15 10:35 | 2015-10-15 10:35 | GE - FA030H1A01 | 85 | 0 | Yes | Yes | 18.4 | 20.4 | -2 | F3CD61B0D79F4875B7354785FB5616C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6942 |  | 2015-08-10 | 2015-08-10 14:28 | 2015-08-10 14:28 | YORK - D3NZ030N05606NXB | 85 | 0 | Yes | Yes | 21 | 21.2 | -0.2 | 24F377FD70C2412EB81A69B5D59CE2BB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4471 |  | 2015-08-28 | 2015-08-28 14:14 | 2015-08-28 14:14 | GIBSON - JS3BA24KA | 64 | 0 | Yes | Yes | 16.5 | 18.5 | -2 | 71CC575D09BF4EDEB58290E12AD78B42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Friant | CA | 93626-0000 |  | 2015-11-11 | 2015-11-11 11:00 | 2015-11-11 11:00 | CARRIER - 38BRC060320 | 200 | 0 | Yes | Yes | 15.6 | 18.2 | -2.6 | B0B58BD73C5147EDB686C106EB2FCCA2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3407 |  | 2015-07-30 | 2015-07-30 11:57 | 2015-07-30 11:57 | TRANE - 2TWB03024A1000AA | 91 | 0 | Yes | Yes | 19.8 | 19.7 | 0.1 | 4A78F8F8B67B4BAB9FD009ED7D0C25B1 |  | R22 | TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1560 |  | 2015-10-16 | 2015-10-16 10:46 | 2015-10-16 10:46 | GOODMAN - GPG1336-701AC | 112 | 0 | Yes | Yes | 18.2 | 17.8 | 0.5 | 274DD5A690EA42478C71C4C1B630B07C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Friant | CA | 93626-0000 |  | 2015-11-04 | 2015-11-04 10:30 | 2015-11-04 10:30 | ICP - HAC042AKC3 | 98 | 0 | Yes | Yes | 20.4 | 18 | 2.5 | 7593A697D23E400EBF3EF904EE7D36DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4632 |  | 2015-09-17 | 2015-09-17 13:59 | 2015-09-17 13:59 | CARRIER - PA13NR030-J | 75 | 0 | Yes | Yes | 15.4 | 18 | -2.6 | 8120DF57B0C144F794B2341BAE195296 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6810 |  | 2015-07-29 | 2015-07-29 15:55 | 2015-07-29 15:55 | TRANE - 4TTX6036A1000AA | 106 | 0 | Yes | Yes | 15.3 | 17.7 | -2.4 | E6B9940B9F7D411D9F2E16E8200D4E6D |  | R410A | TXV |  | 0% | 1 | 0%
Friant | CA | 93626-0000 |  | 2015-11-04 | 2015-11-04 08:55 | 2015-11-04 08:55 | TRANE - TTX048C100A1 | 148 | 0 | Yes | Yes | 23.5 | 18.2 | 5.3 | 38F13A1F39C04CE8A49BB93F6EC896C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3755 |  | 2015-10-02 | 2015-10-02 13:55 | 2015-10-02 13:55 | GOODMAN - GPG13300451BB | 77 | 0 | Yes | Yes | 20.1 | 17.2 | 2.9 | 1EB1DAED0B514C458FE29CBAB1227B8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2313 |  | 2015-08-07 | 2015-08-07 14:21 | 2015-08-07 14:21 | LENNOX - HS354111P | 129 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 275478C023D04920968174444DF3781C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3755 |  | 2015-09-01 | 2015-09-01 11:51 | 2015-09-01 11:51 | GOODMAN - GPG13360701AC | 121 | 0 | Yes | Yes | 22.1 | 19.3 | 2.8 | 9877D1624DAB4940BE856E4E32B20479 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1754 |  | 2015-09-04 | 2015-09-04 11:56 | 2015-09-04 11:56 | GOODMAN - PGB048075-1 | 86 | 0 | Yes | Yes | 21.1 | 22.6 | -1.5 | 90779B2FF2094ED89FBEA2E751F2B668 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-3705 |  | 2015-07-29 | 2015-07-29 14:24 | 2015-07-29 14:24 | BRYANT - UNK | 85 | 0 | Yes | Yes | 19.5 | 19.9 | -0.4 | F288B1431F304F7B8AE37465816BD307 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5162 |  | 2015-08-12 | 2015-08-12 15:26 | 2015-08-12 15:26 | BRYANT - 598BN060 | 85 | 0 | Yes | Yes | 25.5 | 21.6 | 3.9 | B4BAF71D08C34BB2BE5282A955A90091 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4424 |  | 2015-09-16 | 2015-09-16 15:20 | 2015-09-16 15:20 | TRANE - 2YCC3024A1040AA | 69 | 0 | Yes | Yes | 21.5 | 21.4 | 0.1 | EC77FAF830C2423298B71C8392D1F9BA |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3283 |  | 2015-09-08 | 2015-09-08 11:55 | 2015-09-08 11:55 | GOODMAN - GSH130181CB | 127 | 0 | Yes | Yes | 16.5 | 18.8 | -2.3 | 29F6EA77FEC74F5B8C0245F08807318E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3320 |  | 2015-08-19 | 2015-08-19 08:28 | 2015-08-19 08:28 | CARRIER - 48XPN030040311 | 85 | 0 | Yes | Yes | 21.1 | 20.9 | 0.2 | A176F4BD95D345869B58E22A4593A83A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5342 |  | 2015-10-16 | 2015-10-16 15:14 | 2015-10-16 15:14 | LENNOX - 13ACD03623002 | 110 | 0 | Yes | Yes | 20.8 | 21.7 | -0.9 | 3B71C745F55F417480D49DBA4E429EAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7340 |  | 2015-09-21 | 2015-09-21 14:37 | 2015-09-21 14:37 | BRYANT - 563CN036-F | 105 | 0 | Yes | Yes | 22.9 | 21 | 1.9 | 8D7A195FC9144CDDB4D28507E3473E5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4424 |  | 2015-09-03 | 2015-09-03 16:08 | 2015-09-03 16:08 | TRANE - YCC024F1LOBJ | 85 | 0 | Yes | Yes | 21.9 | 20.4 | 1.5 | 6D555F7FCCBC44309D29E01F2E01CD9E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5166 |  | 2015-09-18 | 2015-09-18 16:33 | 2015-09-18 16:33 | CARRIER - 38BRC030320 | 100 | 0 | Yes | Yes | 21.7 | 21.3 | 0.4 | 6DFF285E5C0443FBABC555B4998BE90D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5393 |  | 2015-08-10 | 2015-08-10 13:43 | 2015-08-10 13:43 | WEATHER KING - 13AJA6001 | 191 | 0 | Yes | Yes | 21.3 | 22.9 | -1.6 | C85015B9E7924901BB2F790F8E201B85 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4603 |  | 2015-09-28 | 2015-09-28 12:55 | 2015-09-28 12:55 | YORK - D1NH036N03606C | 108 | 0 | Yes | Yes | 28.4 | 22.6 | 5.8 | A236EB81E53B4CB7AD66855F0076F9BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-2118 |  | 2015-10-26 | 2015-10-26 11:53 | 2015-10-26 11:53 | ARCOAIRE - PGD336090K001C1 | 100 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | 65E39BC7B1EF4CEFACDA7958F81F6A90 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3122 |  | 2015-10-23 | 2015-10-23 09:37 | 2015-10-23 09:37 | RHEEM - 13AJN36A01 | 90 | 0 | Yes | Yes | 23.5 | 17.7 | 5.8 | DBEDC50B8CF441F3BA2307EDA8A1B39F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1660 |  | 2015-08-19 | 2015-08-19 14:50 | 2015-08-19 14:50 | TRANE - TTB042D100A0 | 78 | 0 | Yes | Yes | 15.4 | 17.8 | -2.4 | C6B0BB63490B4A30AC8C14BF886F06D2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5153 |  | 2015-10-23 | 2015-10-23 13:25 | 2015-10-23 13:25 | - 48K1A136300BE | 96 | 0 | Yes | Yes | 22.8 | 17.9 | 4.9 | 3AD4D19946884408873A03DD995436DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3840 |  | 2015-08-06 | 2015-08-06 11:14 | 2015-08-06 11:14 | CARRIER - 38TRA048360 | 158 | 0 | Yes | Yes | 19.2 | 21.5 | -2.3 | 0FBCD790A915475380E3BB2F2493C9D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3421 |  | 2015-08-31 | 2015-08-31 15:12 | 2015-08-31 15:12 | PAYNE - PA13NR030 | 75 | 0 | Yes | Yes | 24 | 23.1 | 0.9 | 2CD2206AA2684E9FBF3B1F047A8EADE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6150 |  | 2015-08-18 | 2015-08-18 11:16 | 2015-08-18 11:16 | CARRIER - 24ABS330A300 | 78 | 0 | Yes | Yes | 26 | 22.4 | 3.7 | 49C447306B144321940A5D968CD76FB6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3652 |  | 2015-09-22 | 2015-09-22 14:15 | 2015-09-22 14:15 | YORK - D1NA024N03606C | 54 | 0 | Yes | Yes | 19.3 | 20.3 | -0.9 | 37DC65533CA847E68B850BF72038491C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3651 |  | 2015-09-18 | 2015-09-18 10:48 | 2015-09-18 10:48 | YORK - D1NA024N03606C | 54 | 0 | Yes | Yes | 22 | 18.2 | 3.8 | EE27E2E133154AC29C516F3F25D7B1BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6523 |  | 2015-09-02 | 2015-09-02 12:16 | 2015-09-02 12:16 | PAYNE - PA10JA036C | 85 | 0 | Yes | Yes | 14.4 | 17.4 | -3 | FA7C9DC7C0F04BC8A2B9A1DB5DD63B4A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4502 |  | 2015-11-16 | 2015-11-16 16:27 | 2015-11-16 16:27 | GOODMAN - UNK | 69 | 0 | Yes | Yes | 18.1 | 20.2 | -2.1 | D72830DBF45940B6B680DB1C3908C359 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-1524 |  | 2015-10-08 | 2015-10-08 14:56 | 2015-10-08 14:56 | YORK - D2NP036N05606A | 108 | 0 | Yes | Yes | 25.5 | 23.1 | 2.4 | 9222A550E76C4422B9E8A25AAC175C10 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-5325 |  | 2015-08-20 | 2015-08-20 17:01 | 2015-08-20 17:01 | LENNOX - 10ACB30-7P | 69 | 0 | Yes | Yes | 20.9 | 19.5 | 1.5 | 0324E0D1493741A88B7C6FA0B960E3E1 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7149 |  | 2015-09-17 | 2015-09-17 15:45 | 2015-09-17 15:45 | CARRIER - 24ABA318A310 | 66 | 0 | Yes | Yes | 17.5 | 18.2 | -0.7 | 244DE2691FF2476CB52474382C49679E |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4834 |  | 2015-09-12 | 2015-09-12 13:19 | 2015-09-12 13:19 | RHEEM - ATL36B10 | 72 | 0 | Yes | Yes | 18.2 | 18.7 | -0.5 | DDBA659F340146E3841C9CC288C53EFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5183 |  | 2015-08-10 | 2015-08-10 14:09 | 2015-08-10 14:54 | OTHER - AC1CN042-B | 135 | 5 | Yes | Yes | 20.5 | 23.1 | -2.6 | 450FC573020B44DC94901DBBEA07107D |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Kerman | CA | 93630-7609 |  | 2015-10-19 | 2015-10-19 11:35 | 2015-10-19 11:35 | YORK - H1RD042S06G | 152 | 0 | Yes | Yes | 16.7 | 19.1 | -2.4 | 75D24C4CF8964D5094BF8E0518B6E019 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-3807 |  | 2015-08-20 | 2015-08-20 08:50 | 2015-08-20 08:50 | BDP - 585EJ03675 | 82 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | 65F7A238E632405AB826605164823ED7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-0000 |  | 2015-09-04 | 2015-09-04 20:59 | 2015-09-04 20:59 | CARRIER - 24ABA342A310 | 111 | 0 | Yes | Yes | 22.4 | 19.9 | 2.5 | F0FA25B2470741CDACBEC5A37ACAD153 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-0234 |  | 2015-11-09 | 2015-11-09 10:09 | 2015-11-09 10:09 | CARRIER - 38CK036310 | 76 | 0 | Yes | Yes | 25.3 | 21.4 | 3.9 | D82FE8CC9C1B4FD78B0699C16DCDEFDE |  | R22 | TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1256 |  | 2015-10-16 | 2015-10-16 15:29 | 2015-10-16 15:29 | BRYANT - 368RC06034D | 200 | 0 | Yes | Yes | 20.5 | 21.8 | -1.3 | E9123F05B9164A4E92C7E9C86DBBEAEB |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5110 |  | 2015-11-06 | 2015-11-06 13:20 | 2015-11-06 13:20 | BRYANT - UNKNOWN | 181 | 0 | Yes | Yes | 18.2 | 20.3 | -2.1 | 57069BD25BEF48BEB9270047F8CC6069 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Gilroy | CA | 95020-7233 |  | 2015-09-04 | 2015-09-04 09:21 | 2015-09-04 09:40 | BRYANT - 585AJ030 | 71 | 26.6 | Yes | Yes | 20.6 | 20.6 | 0 | B5A97F183639427B9496AC7411A3C386 |  | R22 | Non-TXV |  | 37.46% | 0.62535 | 72% | [5 empty] | Non-TXV | 37.46%
Pittsburg | CA | 94565-4311 |  | 2015-09-17 | 2015-09-17 10:14 | 2015-09-17 10:14 | AMERICAN STANDARD - 2A7A2042B10000AA | 86 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | 17478D5B0A9546919277A2BDD793BABF |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3413 |  | 2015-08-06 | 2015-08-06 14:27 | 2015-08-06 14:27 | CARRIER - 48SX-036060331AA | 87 | 0 | Yes | Yes | 22.2 | 22.6 | -0.4 | A83648793A0144D2863821595ECDF91D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-1047 |  | 2015-09-03 | 2015-09-03 10:43 | 2015-09-03 10:43 | TRANE - 4TTX6060B1000AA | 160 | 0 | Yes | Yes | 18.2 | 19.3 | -1.1 | 89BE5BBF3D614512AF6BD66967653540 |  | R410A | TXV |  | 0% | 1 | 0%
Napa | CA | 94558-3320 |  | 2015-08-25 | 2015-08-25 14:17 | 2015-08-25 14:17 | CARRIER - 24ACA436A0030010 | 85 | 0 | Yes | Yes | 20.7 | 18.6 | 2.2 | E9120FF97E1C468292575A3F3C33A68E |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1708 |  | 2015-11-06 | 2015-11-06 14:37 | 2015-11-06 15:03 | CARRIER - 48GX048090 | 132 | 24.5 | Yes | Yes | 18.6 | 17.9 | 0.8 | 40EB4AE807E94140B445D27EF735A6C3 |  | R22 | Non-TXV |  | 18.56% | 0.81439 | 35.67% | [5 empty] | Non-TXV | 18.56%
Dixon | CA | 95620-4502 |  | 2015-09-23 | 2015-09-23 14:17 | 2015-09-23 14:17 | GOODMAN - CKJ361B | 97 | 0 | Yes | Yes | 23.2 | 19.7 | 3.5 | 294943CFD5F74796AA0707D8D93F8D0A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9351 |  | 2015-11-10 | 2015-11-10 08:34 | 2015-11-10 09:09 | LENNOX - 13ACC-036-230-01 | 115 | 9.9 | Yes | Yes | 22.1 | 19.1 | 3 | BD8812A844A14D42A55C13B1E7BA3474 |  | R22 | TXV |  | 8.609% | 0.91391 | 16.54% | [5 empty] | TXV | 8.609%
Fresno | CA | 93725-1434 |  | 2015-11-11 | 2015-11-11 15:24 | 2015-11-11 15:24 | GOODMAN - GPGA10360701A | 132 | 0 | Yes | Yes | 19.9 | 16.6 | 3.3 | 0397E1B7BA8D470CBB6F42E241672800 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3924 |  | 2015-08-27 | 2015-08-27 11:56 | 2015-08-27 11:56 | CARRIER - 38CC024320 | 69 | 0 | Yes | Yes | 18.6 | 20.8 | -2.2 | 850EAB5086AF4B208DCB13CFDE5D0ABD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1066 |  | 2015-08-28 | 2015-08-28 14:44 | 2015-08-28 14:44 | CARRIER - TCGD36S21S1A | 65 | 0 | Yes | Yes | 21.4 | 19.3 | 2.1 | 2A632CC68548417BB4D1C2A3B2FECB87 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5542 |  | 2015-09-10 | 2015-09-10 10:08 | 2015-09-10 10:08 | DAY & NIGHT - 591ANX030000ABAA | 68 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | BDD560C4088749A8981BA68EB38F2F5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4424 |  | 2015-09-08 | 2015-09-08 18:02 | 2015-09-08 18:02 | TRANE - YC024F1L0BJ | 65 | 0 | Yes | Yes | 20.4 | 19.1 | 1.4 | 1383CAEFDD8E4726A58DA4C4C563BE7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5019 |  | 2015-10-26 | 2015-10-26 16:14 | 2015-10-26 16:14 | AMERICAN STANDARD - 2YC3048A1075A | 85 | 0 | Yes | Yes | 19 | 15.5 | 3.5 | 6DD41AA39F014210B5C60FA7F497F252 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5013 |  | 2015-10-16 | 2015-10-16 13:57 | 2015-10-16 13:57 | OTHER - 561CJ042-A | 85 | 0 | Yes | Yes | 16.9 | 16.5 | 0.4 | 6F620E12214B42DEBFCD834CE131F2DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4836 |  | 2015-10-01 | 2015-10-01 11:02 | 2015-10-01 11:02 | GOODMAN - GPG1330070M41BA | 85 | 0 | Yes | Yes | 24.3 | 18.8 | 5.5 | 5D5D611D20DB4F1BAB57C8C5C868BA3C |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3506 |  | 2015-11-18 | 2015-11-18 12:12 | 2015-11-18 12:12 | HEIL - HAC036AKA1 | 80 | 0 | Yes | Yes | 21.5 | 20.3 | 1.2 | 0E35EA31EAC94D669BFCDF88EECA168C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7366 |  | 2015-11-06 | 2015-11-06 15:59 | 2015-11-06 15:59 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 19.7 | 20.2 | -0.4 | FC37F00054594451B70191470128D3D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3393 |  | 2015-09-01 | 2015-09-01 13:42 | 2015-09-01 13:42 | YORK - MICB018506A | 56 | 0 | Yes | Yes | 14.9 | 16.5 | -1.6 | 13E9AB2E5DBE4A82B54E16FC9DD4783D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4739 |  | 2015-10-01 | 2015-10-01 08:31 | 2015-10-01 08:31 | BDP - 585CJ030050 | 78 | 0 | Yes | Yes | 22.8 | 18.7 | 4.1 | 97238CA4326D4638B9EC61FAB93C5797 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-0000 |  | 2015-09-01 | 2015-09-01 10:02 | 2015-09-01 10:02 | CARRIER - 24AB A330A320 | 64 | 0 | Yes | Yes | 19.8 | 19.9 | -0.1 | 08FEFF793128486B8D015662A6215037 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4734 |  | 2015-11-03 | 2015-11-03 09:39 | 2015-11-03 09:39 | GIBSON - N/A | 85 | 0 | Yes | Yes | 23 | 19.1 | 3.9 | 48D1DD74D93A41FF9B2D7702B1033F86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4458 |  | 2015-10-07 | 2015-10-07 14:47 | 2015-10-07 14:47 | OTHER - UNKNOWN | 90 | 0 | Yes | Yes | 19.9 | 20.2 | -0.3 | AE0207675B2D4F76902DD2763F4D1D4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2547 |  | 2015-08-06 | 2015-08-06 13:42 | 2015-08-06 13:42 | ICP - PGAA42C1K3 | 82 | 0 | Yes | Yes | 23 | 19.5 | 3.5 | C79715AB31E444308FCB4DC0C4DA35BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4739 |  | 2015-09-28 | 2015-09-28 10:21 | 2015-09-28 10:21 | BDP - 585CJ030050 | 85 | 0 | Yes | Yes | 21.5 | 19.3 | 2.2 | 9C583A59A43A410DAC611C3814EA0F2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1733 |  | 2015-08-20 | 2015-08-20 09:52 | 2015-08-20 10:10 | CARRIER - 24ABA342A0030010 | 110 | 10.1 | Yes | Yes | 22.9 | 23.1 | -0.2 | 58AED971A38D487D9BB4B81F136CC084 |  | R410A | TXV |  | 9.182% | 0.90818 | 17.65% | [5 empty] | TXV | 9.182%
Fresno | CA | 93702-1570 |  | 2015-09-04 | 2015-09-04 17:33 | 2015-09-04 17:33 | OTHER - 24ECW060GA | 84 | 0 | Yes | Yes | 19.4 | 21 | -1.6 | 83A6BDC8E1B84A779978E9F7B67D25E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-2158 |  | 2015-11-19 | 2015-11-19 14:27 | 2015-11-19 14:27 | LENNOX - 13ACX-036-230-15 | 89 | 0 | Yes | Yes | 22.4 | 19.6 | 2.9 | 8F310A076A50479F9DBBBA523129D9AB |  | R410A | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3607 |  | 2015-10-27 | 2015-10-27 12:28 | 2015-10-27 12:28 | BRYANT - PA10JA024C | 64 | 0 | Yes | Yes | 23 | 19.6 | 3.5 | 7C19290385D04DE3BE662495904C434E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2472 |  | 2015-09-02 | 2015-09-02 11:24 | 2015-09-02 11:56 | OTHER - BRCQO481BB | 87 | 2.7 | Yes | Yes | 19.4 | 19 | 0.4 | 76612AB39573430CA2F937C1DFD13195 |  | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Fresno | CA | 93711-1330 |  | 2015-08-27 | 2015-08-27 14:53 | 2015-08-27 14:53 | BDP - 568CJ048-A13 | 224 | 0 | Yes | Yes | 19.3 | 20.6 | -1.3 | 66B5AB597D254A74942E62411D458E6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3302 |  | 2015-09-14 | 2015-09-14 11:59 | 2015-09-14 11:59 | TRANE - TTD724A100A0 | 66 | 0 | Yes | Yes | 15.5 | 18.3 | -2.8 | 922FF54AFB8643BC8D33257B0E28DCEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5840 |  | 2015-10-12 | 2015-10-12 13:25 | 2015-10-12 13:25 | TRANE - BT030A100B0 | 122 | 0 | Yes | Yes | 15.2 | 18 | -2.8 | 8B0E0034044C4DD888B81A627EBAEF47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1305 |  | 2015-11-23 | 2015-11-23 15:55 | 2015-11-23 15:55 | GOODMAN - PGB0360754B | 85 | 0 | Yes | Yes | 17.8 | 13.9 | 3.9 | 90845426D4BA40AABACFA94CDD75E91E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-8897 |  | 2015-08-20 | 2015-08-20 11:38 | 2015-08-20 11:38 | OTHER - 2TTB0048A1000AA | 109 | 0 | Yes | Yes | 20.7 | 23.5 | -2.8 | 1C6F021BBB6D485B9229C66F93F83F33 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1456 |  | 2015-08-31 | 2015-08-31 10:48 | 2015-08-31 10:48 | KENMORE - TC036AKC4 | 96 | 0 | Yes | Yes | 15.2 | 17.4 | -2.2 | 604985CB2733461A9DB27AC1CEFD3D66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5718 |  | 2015-08-11 | 2015-08-11 09:20 | 2015-08-11 09:20 | CARRIER - 24ABB342W300 | 86 | 0 | Yes | Yes | 22.8 | 22 | 0.8 | 4B2608A935E141B5BB5862799CDA2D9C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6826 |  | 2015-09-08 | 2015-09-08 13:51 | 2015-09-08 13:51 | PAYNE - 591ANX036000AAAA | 90 | 0 | Yes | Yes | 21.9 | 20.8 | 1.1 | 7BFF2C39811C47C3A489E1350E0AD860 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-0000 |  | 2015-08-06 | 2015-08-06 10:30 | 2015-08-06 10:30 | HEIL - N2A348AKA30 | 120 | 0 | Yes | Yes | 18.9 | 20.4 | -1.5 | F333084F695B454485845DF52DF0C848 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95616-6616 |  | 2015-10-01 | 2015-10-01 13:21 | 2015-10-01 13:21 | TRANE - TTR748B100A0 | 85 | 0 | Yes | Yes | 17.4 | 17.6 | -0.1 | E52EE419C2D848D9914AF5ACE9DAD261 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5614 |  | 2015-08-18 | 2015-08-18 08:31 | 2015-08-18 09:03 | GOODMAN - GSX130601BA | 125 | 13.7 | Yes | Yes | 22.7 | 22.1 | 0.6 | 66D79CA9D84F4C48AFB8EFBC2D6D4135 |  | R410A | Non-TXV |  | 10.96% | 0.8904 | 21.06% | [5 empty] | Non-TXV | 10.96%
Fresno | CA | 93725-1661 |  | 2015-10-07 | 2015-10-07 23:06 | 2015-10-07 23:06 | CARRIER - 24ABC630A300 | 104 | 0 | Yes | Yes | 20.8 | 18.2 | 2.6 | 3952704EBC7743A48D14CD68F0B4CD5C | Actual Subcooling cannot be negative. Please check entries. | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1586 |  | 2015-10-09 | 2015-10-09 12:01 | 2015-10-09 12:18 | LENNOX - HS22-411V-3P | 129 | 4.8 | Yes | Yes | 22.1 | 21.3 | 0.9 | BC3024620A954A66A050969A5428CBFB |  | R22 | TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | TXV | 3.721%
Brentwood | CA | 94513-6719 |  | 2015-09-14 | 2015-09-14 10:55 | 2015-09-14 10:55 | CARRIER - 38BRRC060 361 | 200 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | 0760A65E55DA44C388A61C374F3E1B8B |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6116 |  | 2015-08-26 | 2015-08-26 13:18 | 2015-08-26 13:18 | AMANA - RCE30C2C | 125 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | 52D4AB5816F646E6BA9EC286ADD500FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4859 |  | 2015-08-04 | 2015-08-04 13:16 | 2015-08-04 13:16 | OTHER - N/A | 85 | 0 | Yes | Yes | 20.3 | 21.5 | -1.2 | C012A8B6B7824C989D81B582B6FB74AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4836 |  | 2015-08-11 | 2015-08-11 10:03 | 2015-08-11 10:03 | BDP - 585A030060YAC | 50 | 0 | Yes | Yes | 20.9 | 19.6 | 1.4 | 95D842070EC74847930B9696D9B39299 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2779 |  | 2015-09-09 | 2015-09-09 11:11 | 2015-09-09 11:48 | MAYTAG - N/ | 85 | 23.9 | Yes | Yes | 21.2 | 23.7 | -2.5 | 68F18100085743778C7C65CCF1828462 |  | R22 | Non-TXV |  | 28.12% | 0.71882 | 54.04% | [5 empty] | Non-TXV | 28.12%
Clovis | CA | 93612-3889 |  | 2015-09-08 | 2015-09-08 13:00 | 2015-09-08 13:00 | YORK - D3NZ030N05606NXA | 64 | 0 | Yes | Yes | 24.7 | 21.4 | 3.3 | 49C5EED9779A419882D418340781DF79 |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1823 |  | 2015-08-25 | 2015-08-25 16:19 | 2015-08-25 16:19 | RHEEM - UNK | 88 | 0 | Yes | Yes | 22.7 | 21.9 | 0.8 | CE78B03230CD4508835FA91390AF9959 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3474 |  | 2015-08-06 | 2015-08-06 09:22 | 2015-08-06 09:22 | BDP - 567GJ036 | 93 | 0 | Yes | Yes | 20.3 | 19.8 | 0.5 | 094FA01DF38A4061A7FB9CDE681028AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7706 |  | 2015-08-06 | 2015-08-06 11:16 | 2015-08-06 11:16 | UNITARY PRODUCTS GROUP - D1NH036N03606C | 108 | 0 | Yes | Yes | 21.5 | 18.5 | 3 | F40AB0D379E648A69F9DA7CC55D26700 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-4005 |  | 2015-08-25 | 2015-08-25 12:19 | 2015-08-25 12:19 | GE - UNK | 60 | 0 | Yes | Yes | 15.9 | 18.2 | -2.3 | 89D1CC3B637643C68EDBAAE2F17C0A62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9384 |  | 2015-10-19 | 2015-10-19 19:55 | 2015-10-19 19:55 | CARRIER - 48GX-048090311 | 131 | 0 | Yes | Yes | 18.5 | 19.9 | -1.4 | 4D6C76B24683418A949784235C98CBCB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4135 |  | 2015-09-17 | 2015-09-17 09:24 | 2015-09-17 09:24 | CARRIER - 38CKC03040 | 67 | 0 | Yes | Yes | 18.1 | 18.6 | -0.4 | 57BE17FB4F8A4705AE99CD4C0C21A8FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6119 |  | 2015-10-07 | 2015-10-07 12:18 | 2015-10-07 12:18 | AMERICAN STANDARD - 2A7A2036A1000AA | 85 | 0 | Yes | Yes | 21.3 | 17.7 | 3.6 | 937C0338A119400ABFBA49B485DEEB5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-3931 |  | 2015-08-07 | 2015-08-07 16:02 | 2015-08-07 16:02 | GOODMAN - VSX130361EA | 75 | 0 | Yes | Yes | 25.2 | 20.4 | 4.8 | ED69D5E0911D44EABF7292F54294AE11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-3931 |  | 2015-08-07 | 2015-08-07 16:18 | 2015-08-07 16:18 | GOODMAN - VSX130361EA | 64 | 0 | Yes | Yes | 4.9 | 18.5 | -13.6 | 89CCAF9E344F41898AF3E31C2F8C16B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4610 |  | 2015-11-05 | 2015-11-05 12:36 | 2015-11-05 13:01 | LENNOX - 12GC306-75-3PA | 110 | 31.7 | Yes | Yes | 22.1 | 16.8 | 5.3 | F4B586766E9E4AF4A68049D194F362B7 |  | R22 | Non-TXV |  | 28.82% | 0.71182 | 55.38% | [5 empty] | Non-TXV | 28.82%
Fresno | CA | 93704-6031 |  | 2015-08-24 | 2015-08-24 14:01 | 2015-08-24 14:01 | ICP - GPCM036K060F | 85 | 0 | Yes | Yes | 22.8 | 21.9 | 0.9 | C5061EDAD003436C8D35563AD42A40F1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5421 |  | 2015-11-06 | 2015-11-06 09:05 | 2015-11-06 09:26 | DAY & NIGHT - 588ANW036080ABAF | 67 | 32.5 | Yes | Yes | 20.9 | 20.5 | 0.5 | 7E4331E5C987451FB64E2006BDFB6CA5 |  | R22 | Non-TXV |  | 48.51% | 0.51493 | 93.22% | [5 empty] | Non-TXV | 48.51%
Fresno | CA | 93727-3058 |  | 2015-09-23 | 2015-09-23 13:46 | 2015-09-23 13:46 | OTHER - N42P13 | 85 | 0 | Yes | Yes | 22.5 | 21.2 | 1.4 | DE2070B2928941469D09EC63AB0359B9 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3308 |  | 2015-11-05 | 2015-11-05 13:12 | 2015-11-05 13:12 | GOODMAN - CK301A | 76 | 0 | Yes | Yes | 21 | 19.9 | 1.1 | F9A57BFEF2DC480CB59B277C59BCF133 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-6304 |  | 2015-10-08 | 2015-10-08 13:46 | 2015-10-08 13:46 | ALLEGIANCE - 7A0042A100A0 | 100 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | F7C3364EF0AD4114BA77288DEC7BF01F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-9234 |  | 2015-10-28 | 2015-10-28 10:01 | 2015-10-28 10:01 | CARRIER - 589ANW036080AABBF | 85 | 0 | Yes | Yes | 23.6 | 20.3 | 3.3 | 12B4642D77B34E3097B3EC6A72757428 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2145 |  | 2015-10-08 | 2015-10-08 03:25 | 2015-10-08 03:25 | RHEEM - RRNLB036JK06X | 38 | 0 | Yes | Yes | 21.5 | 16.7 | 4.8 | EA4C48B1DAA445018FC1FB583B169708 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5195 |  | 2015-08-11 | 2015-08-11 15:01 | 2015-08-11 15:01 | GOODMAN - GPG1342070M41AC | 105 | 0 | Yes | Yes | 20.2 | 21.2 | -1 | 1061A25A0DA042659260291F301441E2 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4837 |  | 2015-10-06 | 2015-10-06 16:10 | 2015-10-06 16:10 | CARRIER - 38BRC036350 | 105 | 0 | Yes | Yes | 28.8 | 25.3 | 3.5 | 4B093E2EF83C42F1B05FEAA8F6718F1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3607 |  | 2015-10-07 | 2015-10-07 09:33 | 2015-10-07 09:33 | AMERICAN STANDARD - 2A7A2036A1000AA | 85 | 0 | Yes | Yes | 15 | 17.1 | -2.1 | FDAD8F6D5E4D4335B359228384A770D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6532 |  | 2015-09-03 | 2015-09-03 15:03 | 2015-09-03 15:25 | CARRIER - 38CKC060300 | 85 | 18.4 | Yes | Yes | 21.1 | 22.1 | -1 | 2A59ADD1E23D4E92B20379D9EAADDCD4 |  | R22 | TXV |  | 21.65% | 0.78353 | 41.6% | [5 empty] | TXV | 21.65%
Brentwood | CA | 94513-0000 |  | 2015-09-08 | 2015-09-08 09:16 | 2015-09-08 09:16 | YORK - H2RD024S06B | 80 | 0 | Yes | Yes | 17.6 | 19.9 | -2.3 | 560E1033BE1B469FA51C38C4C9B0BCD3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95131-3623 |  | 2015-10-02 | 2015-10-02 12:36 | 2015-10-02 12:36 | BRYANT - 561CJ060-A | 153 | 0 | Yes | Yes | 21.6 | 15.8 | 5.8 | 6BAEC95FE7634EE4822FE549C01457A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2041 |  | 2015-10-20 | 2015-10-20 11:42 | 2015-10-20 11:42 | CARRIER - 24ABA360A310 | 132 | 0 | Yes | Yes | 18.7 | 19.3 | -0.6 | 8D08697DFE7A4A55A32F006FA4BC0452 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5932 |  | 2015-10-12 | 2015-10-12 09:30 | 2015-10-12 09:30 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 18.9 | 18.5 | 0.4 | 88DFB2BEBC03400AA9D7F9CBCA301A12 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-2104 |  | 2015-09-03 | 2015-09-03 12:00 | 2015-09-03 12:00 | - 2A7A1036A1000AA | 73 | 0 | Yes | Yes | 22 | 21.9 | 0.1 | 75883B9AECC248508B3124E5A53179AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6463 |  | 2015-09-25 | 2015-09-25 14:41 | 2015-09-25 15:00 | CARRIER - 38BRC0423202900E22027 | 108 | 9.4 | Yes | Yes | 24.5 | 22.6 | 1.9 | 1594787950BB48EBB669919FD8F36865 |  | R22 | TXV |  | 8.704% | 0.91296 | 16.73% | [5 empty] | TXV | 8.704%
Fresno | CA | 93722-5284 |  | 2015-10-01 | 2015-10-01 10:45 | 2015-11-09 11:04 | CARRIER - 585EJW03050ABAE | 58 | 0 | Yes | Yes | 25 | 21 | 4 | E028CA0B54B54FEDB252F627F3BA6704 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1971 |  | 2015-08-21 | 2015-08-21 09:04 | 2015-08-21 09:04 | TRANE - 4TTX4042B1000AA | 103 | 0 | Yes | Yes | 22.2 | 24.4 | -2.2 | 931186CD26EA439E956F74706AAE152B |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4686 |  | 2015-09-18 | 2015-09-18 12:31 | 2015-09-18 12:31 | COLEMAN - 9646F801 | 120 | 0 | Yes | Yes | 22.4 | 23.1 | -0.7 | 4585594767804DD8B7D952394F4DBE26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1845 |  | 2015-11-12 | 2015-11-12 12:37 | 2015-11-12 12:37 | OTHER - BRCQ0481BDG | 103 | 0 | Yes | Yes | 18.6 | 17.7 | 0.9 | 0F0AF46E9235441292A95976115FB116 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7012 |  | 2015-08-17 | 2015-08-17 11:17 | 2015-08-17 11:17 | YORK - D1NP060N09006A | 140 | 0 | Yes | Yes | 28.5 | 22.6 | 5.9 | 8D799AF321674DFE870A85BA310F2458 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8062 |  | 2015-10-20 | 2015-10-20 15:08 | 2015-10-20 15:08 | CARRIER - 38CKC042-311 | 93 | 0 | Yes | Yes | 18 | 21 | -3 | CD27F819BFA542EEADC3BDE908B621CC |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8011 |  | 2015-10-23 | 2015-10-23 10:01 | 2015-10-23 10:01 | CARRIER - UNKNOWN | 112 | 0 | Yes | Yes | 18.9 | 20.4 | -1.5 | 730209DC29C44E17811142F6E582215F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5837 |  | 2015-08-21 | 2015-08-21 10:55 | 2015-08-21 10:55 | YORK - DBYP-F024N045A | 100 | 0 | Yes | Yes | 23.4 | 17.8 | 5.6 | 0F8F37B76CEB404B8BF93B46FA371EB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4537 |  | 2015-08-31 | 2015-08-31 14:26 | 2015-08-31 14:26 | TRANE - TTP036D100A0 | 133 | 0 | Yes | Yes | 21.7 | 21.6 | 0.1 | 28516FBE460543728098C7B3C282CA15 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1462 |  | 2015-10-26 | 2015-10-26 15:15 | 2015-10-26 15:33 | DAY & NIGHT - 569BJ036 | 93 | 16.4 | Yes | Yes | 20.9 | 19.3 | 1.6 | 0802DF67892941308DF1189A6093938A |  | R22 | Non-TXV |  | 17.63% | 0.82366 | 33.89% | [5 empty] | Non-TXV | 17.63%
Woodland | CA | 95776-6731 |  | 2015-10-16 | 2015-10-16 10:24 | 2015-10-16 10:24 | DAY & NIGHT - 591ANX036000AAAA | 85 | 0 | Yes | Yes | 16.8 | 18.8 | -2 | BA38CADDB9BA4A1699CCC25E740B3EFE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1516 |  | 2015-08-06 | 2015-08-06 11:07 | 2015-08-06 11:07 | AMANA - APG13480901AB | 145 | 0 | Yes | Yes | 21.5 | 18.8 | 2.7 | 1E177E591BC343E08CCF9EFF8E83C3DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3133 |  | 2015-10-06 | 2015-10-06 11:19 | 2015-10-06 11:19 | OTHER - 4C13L36P-3 | 89 | 0 | Yes | Yes | 20 | 17.9 | 2.1 | 8D2FBA186704403491527CDFA4AD0F6A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4017 |  | 2015-09-02 | 2015-09-02 09:06 | 2015-09-02 09:06 | OTHER - 24ABB336W310 | 85 | 0 | Yes | Yes | 20.8 | 21.2 | -0.4 | 6D9CFFD5E11F4CC19F077C23664C208D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2055 |  | 2015-11-06 | 2015-11-06 14:20 | 2015-11-06 14:40 | LENNOX - 10ACC-042-230-03 | 81 | 3.1 | Yes | Yes | 19 | 18.2 | 0.8 | 84D7F8C9E43642DE8864515E9D555974 |  | R22 | TXV |  | 3.827% | 0.96173 | 7.355% | [5 empty] | TXV | 3.827%
Suisun City | CA | 94585-1304 |  | 2015-09-16 | 2015-09-16 13:14 | 2015-09-16 13:14 | GOODMAN - JT5BD030KA | 144 | 0 | Yes | Yes | 19.7 | 17.7 | 2 | 7FED3779D5DE412DAED982EE1A34240A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5872 |  | 2015-08-28 | 2015-08-28 14:12 | 2015-08-28 14:12 | BDP - 585HJ036060 | 85 | 0 | Yes | Yes | 19 | 21.7 | -2.7 | 9568D18FFD0F462AA41CF4BC8220412D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1841 |  | 2015-11-23 | 2015-11-23 16:03 | 2015-11-23 16:03 | COLEMAN - BRCQ0421BGD | 66 | 0 | Yes | Yes | 21 | 17.4 | 3.6 | 343774B0379A4BC4920363F4A4778915 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1304 |  | 2015-09-16 | 2015-09-16 10:16 | 2015-09-16 10:16 | CARRIER - 38TRA048360 | 152 | 0 | Yes | Yes | 23.2 | 17.7 | 5.5 | BAD266A521AB4725A63CB3400977B0E0 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-2230 |  | 2015-08-07 | 2015-08-07 09:06 | 2015-08-07 09:23 | - ACS060A2B2 | 120 | 2.6 | Yes | Yes | 24.7 | 22 | 2.7 | 21E7E8DB49D54E0380888B9085506289 |  | R22 | Non-TXV |  | 2.167% | 0.97833 | 4.164% | [5 empty] | Non-TXV | 2.167%
San Jose | CA | 95148-1202 |  | 2015-08-07 | 2015-08-07 08:03 | 2015-08-07 08:24 | RUUD - UAMA-036JBZ | 85 | -8 | Yes | Yes | 25.6 | 21.7 | 4 | ED2212833F42469894828517AB19BB89 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Bakersfield | CA | 93313-3758 |  | 2015-08-10 | 2015-08-10 14:30 | 2015-08-10 14:30 | WEATHER KING - 13AJA36A01 | 108 | 0 | Yes | Yes | 21.9 | 22.9 | -1 | F9A96A60919C4CAEBF031F88039DC126 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1237 |  | 2015-11-04 | 2015-11-04 12:52 | 2015-11-04 12:52 | YORK - H2R036S002 | 63 | 0 | Yes | Yes | 18 | 18.5 | -0.5 | A71B9B1E47BB48DDB0921C8C573321F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-9326 |  | 2015-10-20 | 2015-10-20 12:24 | 2015-10-20 12:25 | OTHER - N/A | 85 | 16.1 | Yes | Yes | 21.9 | 23.4 | -1.5 | 1E7BD1BF2F924521B3A2A03F2C92915E |  | R22 | Non-TXV |  | 18.94% | 0.81059 | 36.4% | [5 empty] | Non-TXV | 18.94%
Fresno | CA | 93722-7301 |  | 2015-08-10 | 2015-08-10 11:06 | 2015-08-10 11:06 | CARRIER - 38CK036330 | 73 | 0 | Yes | Yes | 21.7 | 19.9 | 1.9 | 5E09A3570B224AB99C292C10749918D5 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5428 |  | 2015-10-12 | 2015-10-12 09:13 | 2015-10-12 09:13 | RHEEM - URMA-A042JK08E | 114 | 0 | Yes | Yes | 23.2 | 21 | 2.2 | 13396025353D4E708A4A61DC7B4A40D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2721 |  | 2015-09-11 | 2015-09-11 13:19 | 2015-09-11 13:19 | CARRIER - 38CKCO36340 | 72 | 0 | Yes | Yes | 16.6 | 19.5 | -2.9 | BF17A9CA274C4C35B7533E68B4801E64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5615 |  | 2015-08-28 | 2015-08-28 09:11 | 2015-08-28 09:11 | OTHER - 2TTB3060A1000AA | 139 | 0 | Yes | Yes | 20.3 | 22.4 | -2.1 | 6F393031FC7940F191D5D2D46F17C80C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2902 |  | 2015-08-07 | 2015-08-07 08:22 | 2015-08-07 08:22 | LENNOX - HS22-511-1P | 216 | 0 | Yes | Yes | 17.4 | 17.7 | -0.3 | C43E0D3D50E64A23B70DC64CFDBE0B8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6547 |  | 2015-08-31 | 2015-08-31 16:25 | 2015-08-31 16:25 | RUUD - UPKA025JAZ | 73 | 0 | Yes | Yes | 21.5 | 21.9 | -0.4 | A5C8BF63F7404167B64748AD818BAD2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7760 |  | 2015-08-27 | 2015-08-27 12:26 | 2015-08-27 12:26 | YORK - H2RA030S06A | 62 | 0 | Yes | Yes | 18.6 | 19 | -0.4 | C32C145CAD0C40B5B077FD130244066C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3437 |  | 2015-09-25 | 2015-09-25 15:41 | 2015-09-25 15:41 | CARRIER - 48DL045 | 85 | 0 | Yes | Yes | -0.2 | 20.4 | -20.6 | FA32DD46709D40AAA5875C545C96D0E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5010 |  | 2015-09-10 | 2015-09-10 12:38 | 2015-09-10 12:38 | TRANE - 2TTR2048A1000AA | 120 | 0 | Yes | Yes | 20.1 | 18.6 | 1.5 | 68A980D48D614E2B91BC4F82DCCE709D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1304 |  | 2015-11-05 | 2015-11-05 15:28 | 2015-11-05 15:28 | GIBSON - JT5BD024 | 98 | 0 | Yes | Yes | 20.5 | 18 | 2.5 | ECD64BB7650B474BB0C0FCA48B9E28C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3042 |  | 2015-10-21 | 2015-10-21 11:45 | 2015-10-21 11:45 | LENNOX - 15GCSAV42083X2303A | 181 | 0 | Yes | Yes | 24 | 17.4 | 6.6 | BB0807E5DB7D45929353E54E44BEE567 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5587 |  | 2015-08-26 | 2015-08-26 12:31 | 2015-08-26 12:41 | YORK - H2RD042SC6B | 141 | 14.9 | Yes | Yes | 20.9 | 23.3 | -2.4 | 0E090068C94B40CFABF2637E4C7E7E1C |  | R22 | Non-TXV |  | 10.57% | 0.89433 | 20.31% | [5 empty] | Non-TXV | 10.57%
Bakersfield | CA | 93304-2311 |  | 2015-08-04 | 2015-08-04 10:47 | 2015-08-04 10:47 | ICP - PGAD36D1K7 | 103 | 0 | Yes | Yes | 20.4 | 20.1 | 0.3 | 614478A6474540A59C38C1C1C46F3476 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2137 |  | 2015-08-14 | 2015-08-14 11:25 | 2015-08-14 11:46 | CARRIER - 38CK036310 | 72 | 7.6 | Yes | Yes | 18.2 | 19.6 | -1.4 | 2618B217BAC042FE90685DA60044E39F |  | R22 | TXV |  | 10.56% | 0.89444 | 20.29% | [5 empty] | TXV | 10.56%
Vallejo | CA | 94589-3841 |  | 2015-08-26 | 2015-08-26 12:25 | 2015-08-26 12:25 | RHEEM - RAFD036JAS | 80 | 0 | Yes | Yes | 17 | 18.5 | -1.5 | 4F73FBAB43DA4C5D94B7CA08A5F4CA6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4025 |  | 2015-11-05 | 2015-11-05 11:53 | 2015-11-05 11:53 | COLEMAN - 9536E901 | 62 | 0 | Yes | Yes | 23.3 | 20.8 | 2.5 | AAFA560571594E4C9CB32169DC39E6C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5134 |  | 2015-11-05 | 2015-11-05 15:23 | 2015-11-05 15:23 | CARRIER - 38CKC036350 | 73 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | C672018071B14D86B2570B513F02330E |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4521 |  | 2015-08-06 | 2015-08-06 17:48 | 2015-08-06 17:48 | CARRIER - 38TH036300 | 85 | 0 | Yes | Yes | 19.1 | 17.1 | 2 | D92F0AF02F55495AA2ADD52AE8A8F525 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-4604 |  | 2015-08-18 | 2015-08-18 11:45 | 2015-08-18 11:45 | YORK - D1NAAO48NO9006C | 92 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 5BA4F35FE24F4D15B1DE7A3C2FF0D7DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-9222 |  | 2015-09-18 | 2015-09-18 09:37 | 2015-09-18 09:37 | UNITARY PRODUCTS GROUP - BRCQ0361BD | 52 | 0 | Yes | Yes | 23.8 | 19.1 | 4.7 | 3D22495495D1467BBA969661E6D05162 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-1746 |  | 2015-08-21 | 2015-08-21 11:51 | 2015-08-21 11:51 | BRYANT - | 85 | 0 | Yes | Yes | 28.3 | 23.3 | 5 | 881C3AA09CD84A14BB9D39EEEE917A4C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-4459 |  | 2015-08-20 | 2015-08-20 10:18 | 2015-08-20 10:18 | CARRIER - 38BR030300 | 105 | 0 | Yes | Yes | 21 | 22.5 | -1.5 | 76D0D8EAF84949E6BC3CA4AA724F4C09 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5163 |  | 2015-08-21 | 2015-08-21 09:35 | 2015-08-21 09:35 | CARRIER - 38ESGO36300 | 85 | 0 | Yes | Yes | 20.5 | 18.8 | 1.7 | 05ED6D7D3A3A4245A59CFC5574B3FE25 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9155 |  | 2015-11-09 | 2015-11-09 09:14 | 2015-11-09 09:14 | DAY & NIGHT - 585HJ036060 | 102 | 0 | Yes | Yes | 23.3 | 19.6 | 3.7 | F9921CECC9374C48B6FD26E1643AC7EC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1947 |  | 2015-09-11 | 2015-09-11 13:27 | 2015-09-11 13:27 | GOODMAN - GPG13300701BB | 77 | 0 | Yes | Yes | 20.8 | 20.2 | 0.6 | 3338705B9BA34525917FF18A09FF1C52 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5504 |  | 2015-09-02 | 2015-09-02 18:30 | 2015-09-02 18:30 | CARRIER - 24BB324W310 | 85 | 0 | Yes | Yes | 15 | 17.6 | -2.6 | 3295121E2F6E4FC1815D6A857EC3637F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4857 |  | 2015-10-09 | 2015-10-09 13:15 | 2015-10-09 13:15 | CARRIER - 38CKC030340 | 85 | 0 | Yes | Yes | 17.2 | 17 | 0.2 | DE1D3309D4984E06970F3AF611D0E60B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2252 |  | 2015-08-10 | 2015-08-10 09:40 | 2015-08-10 09:40 | YORK - D1NH048N09006B | 124 | 0 | Yes | Yes | 21.5 | 18.7 | 2.8 | A67D07F6EA9947BABBFF369833200D84 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2417 |  | 2015-08-24 | 2015-08-24 11:13 | 2015-08-24 11:13 | - NC036KA1 | 87 | 0 | Yes | Yes | 19 | 19 | 0 | 8F4C54B79757462F8D7685566EDF7891 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-0000 |  | 2015-09-24 | 2015-09-24 13:53 | 2015-09-24 13:53 | TRANE - 2TWR2060A1000AB | 195 | 0 | Yes | Yes | 26.6 | 21.3 | 5.3 | 1E170A53998546118E1F8FB6CF7C23F4 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1470 |  | 2015-08-18 | 2015-08-18 15:25 | 2015-08-18 15:25 | AMERICAN STANDARD - 4A7A4042A1000AA | 103 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | F22C774AE8054029AC705BA939E5F6DD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4432 |  | 2015-08-25 | 2015-08-25 13:20 | 2015-08-25 13:20 | CARRIER - UNK | 85 | 0 | Yes | Yes | 16.5 | 18.8 | -2.3 | 02C3B0B6BB284C09B1F7CFD7F150348F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3035 |  | 2015-09-23 | 2015-09-23 13:23 | 2015-09-23 13:23 | PAYNE - 591ANX036000AAAA | 85 | 0 | Yes | Yes | 21.1 | 19.9 | 1.2 | 38A580B4788F49F1866269A6CE7418B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3929 |  | 2015-07-29 | 2015-07-29 11:42 | 2015-07-29 12:05 | TRANE - 4TTR5036E1000AA | 116 | 15 | Yes | Yes | 18.1 | 19.9 | -1.8 | 4A47BAAC64474B82826F24F1A07AE39A |  | R410A | TXV |  | 12.93% | 0.87069 | 24.85% | [5 empty] | TXV | 12.93%
Oakley | CA | 94561-4236 |  | 2015-10-05 | 2015-10-05 11:41 | 2015-10-05 11:41 | TRANE - 2TTM3036A1000AA | 83 | 0 | Yes | Yes | 24.1 | 19.8 | 4.3 | E2792E1B5FDC4A8D97BA52B288369480 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4109 |  | 2015-10-20 | 2015-10-20 14:38 | 2015-10-20 14:38 | YORK - DAYH-F018N045C | 70 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | 42C9C4EAC0784543B026F5AE24DDCF38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5526 |  | 2015-08-11 | 2015-08-11 09:44 | 2015-08-11 09:44 | BDP - 585EJ030050 | 58 | 0 | Yes | Yes | 25.1 | 22 | 3.1 | E084F6CA85DC4290835FB18E2D923A71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-6722 |  | 2015-08-27 | 2015-08-27 10:49 | 2015-08-27 10:49 | CARRIER - 38CKC060370 | 135 | 0 | Yes | Yes | 19.1 | 19.9 | -0.8 | 7773B66688F8420CB08772A5AEB9EA66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2606 |  | 2015-09-08 | 2015-09-08 09:13 | 2015-09-08 09:13 | TRANE - 2TTR2036A1000AA | 96 | 0 | Yes | Yes | 16.4 | 18.8 | -2.4 | B8E9DD481F7C4B0BA0012B57781D2DDE |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-6610 |  | 2015-08-25 | 2015-08-25 08:36 | 2015-08-25 09:01 | BDP - 585EJ036075 | 72 | 4.8 | Yes | Yes | 22.3 | 21.9 | 0.4 | 4C10449504B742B5A6EC288BA7BB6E5F |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Antioch | CA | 94509-5704 |  | 2015-08-19 | 2015-08-19 19:00 | 2015-08-19 19:00 | RHEEM - RAKA037JAZ | 85 | 0 | Yes | Yes | 21.3 | 20.4 | 0.9 | 800B4AD0A007468B9E1240D3656996B5 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-6608 |  | 2015-08-27 | 2015-08-27 10:58 | 2015-08-27 11:20 | BDP - 585EJ030050 | 58 | 4.1 | Yes | Yes | 19.7 | 19.9 | -0.2 | 474CCD6C35F14175A88A422A3979F1F6 |  | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Walnut Creek | CA | 94597-7308 |  | 2015-09-03 | 2015-09-03 13:08 | 2015-09-03 13:08 | OTHER - PA13NA030-0 | 55 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | 6121BF7FA6A842858DCCB2C6209AFFCE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-2614 |  | 2015-10-29 | 2015-10-29 14:45 | 2015-10-29 14:45 | CARRIER - 38CKC42350 | 85 | 0 | Yes | Yes | 18.2 | 16.8 | 1.4 | 34C548B2DE5E40A09E8D86F41FD1418B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-3930 |  | 2015-07-29 | 2015-07-29 09:44 | 2015-07-29 09:44 | CARRIER - 38BRC036320 | 101 | 0 | Yes | Yes | 19.2 | 18.8 | 0.4 | C0D27D1279B449A681686BF009B3E815 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1218 |  | 2015-08-27 | 2015-08-27 10:28 | 2015-08-27 10:28 | CARRIER - N/A | 118 | 0 | Yes | Yes | 20.9 | 21.4 | -0.5 | F2B0818BC1A74061ACAD258E68795AE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1736 |  | 2015-08-18 | 2015-08-18 12:23 | 2015-08-18 12:23 | YORK - HIC3024S06A | 71 | 0 | Yes | Yes | 21.2 | 16.1 | 5.1 | A5BD11F06B3C4D69802EB9C525636EF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5202 |  | 2015-08-04 | 2015-08-04 09:58 | 2015-08-04 09:58 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 18.5 | 21.2 | -2.7 | C4328A0E3BB74B3E9F5D247C276220FA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1129 |  | 2015-11-06 | 2015-11-06 15:10 | 2015-11-06 15:10 | GE - DBYPF030N070A | 73 | 0 | Yes | Yes | 22.4 | 17.9 | 4.5 | C2D06F9F8A8A488C9CFC32A3D70AA176 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-6741 |  | 2015-10-01 | 2015-10-01 11:32 | 2015-10-01 11:32 | - 12A342GKA106 | 85 | 0 | Yes | Yes | 17.5 | 18.3 | -0.8 | C46E9755F38E41B9A5BA1143348E35C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3273 |  | 2015-08-20 | 2015-08-20 12:52 | 2015-08-20 12:52 | ICP - HAC248AKC4 | 147 | 0 | Yes | Yes | 15.3 | 17.5 | -2.2 | B586FB7ADCA44E06969F51F913368F82 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5114 |  | 2015-10-02 | 2015-10-02 12:45 | 2015-10-02 12:45 | HEIL - PGD336060K001C1 | 100 | 0 | Yes | Yes | 25.3 | 19.6 | 5.8 | 2E40EB5314394707BBEC921E08EC7FB8 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-4975 |  | 2015-11-06 | 2015-11-06 15:35 | 2015-11-06 15:51 | LENNOX - 13ACC482301 | 158 | 34.8 | Yes | Yes | 23.3 | 20.4 | 2.9 | B2E6480AD9D44391930B54A69111A7EB |  | R22 | Non-TXV |  | 22.03% | 0.77975 | 42.33% | [5 empty] | Non-TXV | 22.03%
Fresno | CA | 93720-4975 |  | 2015-11-06 | 2015-11-06 15:38 | 2015-11-06 15:54 | LENNOX - BACC06023001 | 85 | 16.2 | Yes | Yes | 22.1 | 21.3 | 0.9 | 4F99225C8CE94194A1B5B6BE633FF7A2 |  | R22 | Non-TXV |  | 19.06% | 0.80941 | 36.63% | [5 empty] | Non-TXV | 19.06%
Fresno | CA | 93727-7601 |  | 2015-10-29 | 2015-10-29 09:52 | 2015-10-29 09:52 | AMERICAN STANDARD - YCC036F1MOBK | 83 | 0 | Yes | Yes | 26.1 | 20.5 | 5.6 | DF9BDDD3AF1F48B29456293E44060EFA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9547 |  | 2015-10-27 | 2015-10-27 10:20 | 2015-10-27 10:20 | RHEEM - N/A | 85 | 0 | Yes | Yes | 21.1 | 17.7 | 3.4 | FD34BA00516A4E0C8A4E51C23688849F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Friant | CA | 93626-0000 |  | 2015-11-03 | 2015-11-03 15:45 | 2015-11-03 16:03 | CARRIER - 38EH060330 | 230 | 22.6 | Yes | Yes | 17.3 | 18.7 | -1.4 | D193A18CD0594424BC9F51D54D7FEAAB |  | R22 | Non-TXV |  | 9.826% | 0.90174 | 18.88% | [5 empty] | Non-TXV | 9.826%
Clovis | CA | 93612-3410 |  | 2015-10-14 | 2015-10-14 11:45 | 2015-10-14 18:59 | YORK - DAYP-F048N08080A | 132 | 13.3 | Yes | Yes | 13.5 | 19.3 | -5.8 | 9CAF2921304848A59A405A7096E41724 | Add refrigerant: 12.2 oz | R22 | Non-TXV |  | 10.08% | 0.89924 | 19.36% | [5 empty] | Non-TXV | 10.08%
Kerman | CA | 93630-1369 |  | 2015-11-03 | 2015-11-03 12:35 | 2015-11-03 12:54 | CARRIER - 24ABB336A310 | 83 | 14.1 | Yes | Yes | 16.3 | 18.2 | -1.9 | CB3FC6EC6F064D84A3659930C738B1E8 |  | R410A | TXV |  | 16.99% | 0.83012 | 32.65% | [5 empty] | TXV | 16.99%
Woodland | CA | 95695-6644 |  | 2015-10-12 | 2015-10-12 11:59 | 2015-10-12 11:59 | CARRIER - 38EH036300 | 85 | 0 | Yes | Yes | 15.6 | 18.5 | -2.9 | 00F7FA6B34FF489295C879203F62C5BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2338 |  | 2015-09-10 | 2015-09-10 15:20 | 2015-09-10 15:20 | DAY & NIGHT - N/.A | 85 | 0 | Yes | Yes | 21.6 | 19.5 | 2.1 | B85C2D662C584B25A3FA58CCD056DA64 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95118-3554 |  | 2015-08-20 | 2015-08-20 08:32 | 2015-08-20 08:32 | NORDYNE - FS3BD-024K | 85 | 0 | Yes | Yes | 21.3 | 21.1 | 0.2 | 72230025BFDA45F5907AC6A0F0B08245 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6984 |  | 2015-09-30 | 2015-09-30 13:38 | 2015-09-30 13:38 | OTHER - EADC-036JAS | 80 | 0 | Yes | Yes | 20.8 | 23.2 | -2.4 | 79461F4F3FB244689D9CFC7B5C2CB403 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2651 |  | 2015-07-31 | 2015-07-31 15:36 | 2015-07-31 16:06 | LUXAIRE - TCJD36S41S3A | 73 | 8.1 | Yes | Yes | 20.7 | 21 | -0.3 | 023C428B4679448993F11CDC5B19530E |  | R410A | Non-TXV |  | 11.1% | 0.88904 | 21.32% | [5 empty] | Non-TXV | 11.1%
Bakersfield | CA | 93313-2789 |  | 2015-08-26 | 2015-08-26 09:55 | 2015-08-26 09:55 | OTHER - FS5BD-048K | 147 | 0 | Yes | Yes | 21 | 23.1 | -2.1 | C8310E46E5614EF8AD6D5014158A9803 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6619 |  | 2015-09-28 | 2015-09-28 11:11 | 2015-09-28 11:11 | RHEEM - RAKA-042JAZ | 79 | 0 | Yes | Yes | 16.5 | 17.7 | -1.2 | B71261E502784D54917CD0E8E463DCE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2417 |  | 2015-09-01 | 2015-09-01 15:40 | 2015-09-01 15:40 | RHEEM - 13AJN48A01 | 116 | 0 | Yes | Yes | 24.7 | 20.2 | 4.5 | 9BFEA05ADD004E889FE006E30F6020CF |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5066 |  | 2015-11-23 | 2015-11-23 15:26 | 2015-11-23 15:26 | TEMPSTAR - PGD40060K001C1 | 115 | 0 | Yes | Yes | 18.6 | 15.4 | 3.2 | 9A6A122524B64ECA879F32E137A75A76 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-3039 |  | 2015-11-06 | 2015-11-06 15:16 | 2015-11-06 15:32 | OTHER - 3RCS03618D | 63 | 20.5 | Yes | Yes | 27.3 | 21.5 | 5.8 | 0E7F76806B9F4BD3AD139A345B30156F |  | R22 | Non-TXV |  | 32.54% | 0.6746 | 62.53% | [5 empty] | Non-TXV | 32.54%
Fairfield | CA | 94533-5836 |  | 2015-10-07 | 2015-10-07 14:58 | 2015-10-07 14:58 | CARRIER - 38CKCO36350 | 85 | 0 | Yes | Yes | 15 | 17.9 | -2.9 | 2FF6F09AAACE4737B552419942EE9536 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-1320 |  | 2015-08-07 | 2015-08-07 10:52 | 2015-08-07 11:38 | BRYANT - 113ANA036-E | 95 | 2.7 | Yes | Yes | 22.1 | 21.7 | 0.4 | B170AAD2150D4153A2FCBE5EB1EF06A8 |  | R22 | TXV |  | 2.842% | 0.97158 | 5.462% | [5 empty] | TXV | 2.842%
Vacaville | CA | 95687-5228 |  | 2015-09-16 | 2015-09-16 11:19 | 2015-09-16 11:19 | CARRIER - 38TXA036300 | 108 | 0 | Yes | Yes | 22.8 | 17.2 | 5.6 | 6FFDF4C3C8C44606A8D4843CDC58EFAC |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-3422 |  | 2015-10-23 | 2015-10-23 10:57 | 2015-10-23 10:57 | DAY & NIGHT - 30/80YAC106T-C | 65 | 0 | Yes | Yes | 22.3 | 19.8 | 2.5 | DD0C8AB7537F4861B4E29A9C17A8348A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2646 |  | 2015-08-06 | 2015-08-06 13:20 | 2015-08-06 13:20 | GOODMAN - GPG13420701AA | 107 | 0 | Yes | Yes | 27 | 21 | 6 | 4DF77AFE47344422BF171E0D30740FE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1540 |  | 2015-09-16 | 2015-09-16 12:14 | 2015-09-16 12:14 | GOODMAN - GH130181CB | 127 | 0 | Yes | Yes | 18.1 | 20.4 | -2.3 | 1AF612C45E414E029BE344A777AB6157 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1250 |  | 2015-08-21 | 2015-08-21 09:41 | 2015-08-21 09:41 | TRANE - YCP036F1MOAA | 85 | 0 | Yes | Yes | 19 | 22 | -3 | 8BF0337A7B944B7C8BDB3D9C4EC72406 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9115 |  | 2015-10-08 | 2015-10-08 00:20 | 2015-10-08 00:20 | DAY & NIGHT - 5852003675 | 67 | 0 | Yes | Yes | 20.7 | 21.3 | -0.5 | E58E664741124E62B3C6997C949F3851 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5460 |  | 2015-10-27 | 2015-10-27 15:23 | 2015-10-27 15:23 | PAYNE - PA13NA036-C | 85 | 0 | Yes | Yes | 19.9 | 18.3 | 1.6 | EF89095DAC9B478CA419D75FC30D78A1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-2056 |  | 2015-11-05 | 2015-11-05 12:18 | 2015-11-05 12:18 | CARRIER - 585FIW036075ARAF | 87 | 0 | Yes | Yes | 24.7 | 20.7 | 4 | 4624EDAE153F4F5CA1F8EE49278011FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-1546 |  | 2015-08-31 | 2015-08-31 13:08 | 2015-08-31 13:08 | CARRIER - 38CKB024310 | 56 | 0 | Yes | Yes | 19.3 | 20.7 | -1.4 | 667A83DF0F4447239B0648B1BB35BA40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7264 |  | 2015-10-24 | 2015-10-24 11:20 | 2015-10-24 11:20 | HEIL - CA3036VKA1 | 94 | 0 | Yes | Yes | 16.3 | 19.1 | -2.8 | F3836B004ED64D1D802E1778F1EE02E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4903 |  | 2015-09-02 | 2015-09-02 13:11 | 2015-09-02 13:11 | ALLEGIANCE - 7A2036A100A0 | 120 | 0 | Yes | Yes | 18.6 | 18.8 | -0.2 | 5E206E0C9568413F833784B233510DFE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7232 |  | 2015-08-04 | 2015-08-04 09:02 | 2015-08-04 09:02 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 29.2 | 22.5 | 6.7 | 7725148BCB494FCEB389AA0DCE00DFFD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-4304 |  | 2015-09-28 | 2015-09-28 10:05 | 2015-09-28 10:05 | BDP - 561CJ036-A | 85 | 0 | Yes | Yes | 21.6 | 19.3 | 2.3 | A0667F2037DC4F9FB35B2475CD645D35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5611 |  | 2015-08-12 | 2015-08-12 10:33 | 2015-08-12 10:33 | YORK - H5DB048S06A | 85 | 0 | Yes | Yes | 16.6 | 18.3 | -1.7 | BC88548DFE3B4AC8B22AB4416EDB0D02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-4047 |  | 2015-11-13 | 2015-11-13 12:33 | 2015-11-13 12:33 | COLEMAN - 2036-911 | 89 | 0 | Yes | Yes | 17.2 | 17.1 | 0.1 | 145C6490CE704AE0B5B1F1FF306CC188 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2203 |  | 2015-11-05 | 2015-11-05 13:52 | 2015-11-05 13:52 | YORK - D1NA36N073O6A | 63 | 0 | Yes | Yes | 22.1 | 19.3 | 2.8 | 0C6B0A87CFDB4382A80DB07FB1C60A29 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2364 |  | 2015-09-02 | 2015-09-02 10:18 | 2015-09-02 10:18 | PAYNE - PY3PNA036090NA | 167 | 0 | Yes | Yes | 21.9 | 20.4 | 1.5 | A920F9057D7145E7ACADE71EA44C56CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2258 |  | 2015-09-15 | 2015-09-15 08:21 | 2015-09-15 08:41 | YORK - D1NP048N09006A | 132 | 4.3 | Yes | Yes | 20.4 | 19.1 | 1.3 | 818E42CDD2BF45428B3465E890356750 |  | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.26% | [5 empty] | Non-TXV | 3.258%
Fresno | CA | 93722-9007 |  | 2015-10-20 | 2015-10-20 09:54 | 2015-10-20 09:54 | RUUD - UNKNOWN | 85 | 0 | Yes | Yes | 21.9 | 18.3 | 3.6 | EC39C0C1D46A4E069FC9111EBBC59DE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6818 |  | 2015-10-20 | 2015-10-20 10:57 | 2015-10-20 10:57 | DAY & NIGHT - 591ANY042000ABAA | 85 | 0 | Yes | Yes | 24.3 | 19.4 | 4.9 | 22A3DAB11D3A4A9992A1BFDC1222972B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1958 |  | 2015-08-24 | 2015-08-24 13:14 | 2015-08-24 13:14 | TRANE - TTN030C100C2 | 95 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 9C8D3D06B5C44997A49ADEB9B2B62502 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-1806 |  | 2015-10-08 | 2015-10-08 12:14 | 2015-10-08 12:14 | YORK - D3NZ024N0360NXA | 58 | 0 | Yes | Yes | 21.3 | 23.4 | -2.1 | 233760B12D5E4E9198B4FA49A167F6E1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4541 |  | 2015-08-13 | 2015-08-13 09:43 | 2015-08-13 09:43 | OTHER - 2AC13B42P-1A | 146 | 0 | Yes | Yes | 22.2 | 22.9 | -0.6 | B8D400EE1CEA4E5C87E43CC3ACC6C4D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-7602 |  | 2015-11-03 | 2015-11-03 11:35 | 2015-11-03 12:09 | YORK - H2RC030S0GHG | 88 | 5.2 | Yes | Yes | 23 | 19.5 | 3.5 | D159F54CA15A4BC29FADABE2FF7FA333 |  | R22 | Non-TXV |  | 5.909% | 0.94091 | 11.36% | [5 empty] | Non-TXV | 5.909%
Vacaville | CA | 95687-5524 |  | 2015-09-01 | 2015-09-01 13:16 | 2015-09-01 13:16 | AMERICAN STANDARD - 2A7B3030A1000AA | 88 | 0 | Yes | Yes | 21.2 | 19.7 | 1.5 | C9F7C1C6FFB742819B36A9D3C34FCC26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5134 |  | 2015-08-26 | 2015-08-26 08:58 | 2015-08-26 08:58 | GOODMAN - GPG1330045M41AC | 80 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | DAB1290A56DB4901860542DBD190C4C9 |  | R410A | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2312 |  | 2015-09-23 | 2015-09-23 11:25 | 2015-09-23 11:25 | LENNOX - XC13-042-230-01 | 138 | 0 | Yes | Yes | 23 | 19.3 | 3.7 | 69E65B41175D4352AA9E06B55D8A51B4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4134 |  | 2015-10-28 | 2015-10-28 15:46 | 2015-10-28 16:09 | YORK - DAYH-F018N045C | 70 | 5 | Yes | Yes | 17.9 | 20.4 | -2.5 | 3A67598761C84890B0F41D8D3CF86668 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Vacaville | CA | 95687-6227 |  | 2015-09-23 | 2015-09-23 15:51 | 2015-09-23 15:51 | GOODMAN - UNK | 85 | 0 | Yes | Yes | 16.9 | 19.4 | -2.5 | 509140DB34E147B1A4570C0100C58F1D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2779 |  | 2015-10-19 | 2015-10-19 14:30 | 2015-10-19 14:30 | GOODMAN - CKL18-1 | 53 | 0 | Yes | Yes | 13.4 | 16.3 | -2.9 | A5AE59B5A70448DA96E459AC23A94EAE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5338 |  | 2015-10-15 | 2015-10-15 13:30 | 2015-10-15 13:30 | CARRIER - 24ABA360A310 | 131 | 0 | Yes | Yes | 24 | 23.7 | 0.3 | 852DB7B6D1BC4BD981DD9195A29315CF |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-7407 |  | 2015-11-23 | 2015-11-23 15:14 | 2015-11-23 15:14 | YORK - DINP036N05606A | 108 | 0 | Yes | Yes | 21.9 | 23.1 | -1.2 | 2950B66A2D774BC1B284C5B0910A36E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2241 |  | 2015-07-31 | 2015-07-31 13:31 | 2015-07-31 14:27 | YORK - H4DH036S06A | 95 | 16.8 | Yes | Yes | 15.5 | 18.1 | -2.6 | 4F49081F73324FF4BC01ABEAA2CAE790 |  | R22 | Non-TXV |  | 17.68% | 0.82316 | 33.99% | [5 empty] | Non-TXV | 17.68%
Concord | CA | 94519-1244 |  | 2015-08-31 | 2015-08-31 10:08 | 2015-08-31 10:08 | AMERICAN STANDARD - UNKNOWN | 36 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | 6B460985C9DC4EFB917A17B90B29F763 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-0712 |  | 2015-09-01 | 2015-09-01 14:03 | 2015-09-01 14:03 | LENNOX - 12GCS036X | 110 | 0 | Yes | Yes | 19 | 20.9 | -1.9 | B16CCA8B0B0244AFB4F22D02C805CDD0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4124 |  | 2015-10-06 | 2015-10-06 15:15 | 2015-10-06 15:15 | OTHER - UNKNOWN | 85 | 0 | Yes | Yes | 21.5 | 22.5 | -0.9 | 12EBE5EBE2B24E8CBF666A2ABA42E1F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1531 |  | 2015-08-13 | 2015-08-13 15:10 | 2015-08-13 15:10 | PAYNE - PA13NRO48N | 140 | 0 | Yes | Yes | 22.4 | 20.4 | 2 | 1F2BAF0E175B4F2885521DDA35FBD3FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3534 |  | 2015-08-03 | 2015-08-03 10:43 | 2015-08-03 10:43 | AMERICAN STANDARD - 4TB3030G1000ASA | 78 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 176169F07AE74142BA8CCF4C949F535C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8929 |  | 2015-09-22 | 2015-09-22 13:22 | 2015-09-22 15:00 | NORDYNE - JS5BD042K | 170 | 0 | Yes | Yes | 24.4 | 24.2 | 0.2 | 4E0924EBDB2149858698AEB59F32EADC |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2388 |  | 2015-09-21 | 2015-09-21 16:17 | 2015-09-21 16:17 | TRANE - N/A | 80 | 0 | Yes | Yes | 18.8 | 19 | -0.2 | 2F41DD0A380C4EC18503ADCCF5C8888A |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5104 |  | 2015-11-05 | 2015-11-05 14:44 | 2015-11-05 14:44 | BRYANT - UNKNOWN | 69 | 0 | Yes | Yes | 18.2 | 18.8 | -0.6 | 47A8244C48524731A8B543B080BCAEFB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6630 |  | 2015-08-13 | 2015-08-13 13:04 | 2015-08-13 13:04 | YORK - THGD24S41S1A | 85 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | 52947261DAFD401D8D357B79E650FA86 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4322 |  | 2015-08-21 | 2015-08-21 14:48 | 2015-08-21 14:48 | RUUD - UAHE-O48JAS | 114 | 0 | Yes | Yes | 22.1 | 18.2 | 3.9 | 05C6D43673324C30B24B95C23A28EB9C |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3802 |  | 2015-10-26 | 2015-10-26 10:40 | 2015-10-26 10:58 | BRYANT - 561CJ060-A | 152 | 22.3 | Yes | Yes | 19.7 | 19.4 | 0.3 | 82C2A67DBBE14E68ABA138BFEB0D856F |  | R22 | Non-TXV |  | 14.67% | 0.85329 | 28.19% | [5 empty] | Non-TXV | 14.67%
Gilroy | CA | 95020-9263 |  | 2015-09-04 | 2015-09-04 09:51 | 2015-09-04 10:10 | LENNOX - XC16-060-230-03 | 227 | 9.2 | Yes | Yes | 22.7 | 19.6 | 3.1 | E17F8FC61022479C829C3F0099433133 |  | R410A | Non-TXV |  | 4.053% | 0.95947 | 7.789% | [5 empty] | Non-TXV | 4.053%
Fresno | CA | 93706-4134 |  | 2015-09-30 | 2015-09-30 10:12 | 2015-09-30 10:12 | UNITARY PRODUCTS GROUP - DAYH-F018N045C | 70 | 0 | Yes | Yes | 19.1 | 20.1 | -1 | D0A35BE57CF64B389E0A68402ACDCE6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5612 |  | 2015-09-28 | 2015-09-28 10:04 | 2015-09-28 10:04 | COLEMAN - TCGD36S21S2A | 223 | 0 | Yes | Yes | 19.8 | 18.8 | 1 | 2D6AFF0980D946A68EA47921273BEF16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-1918 |  | 2015-11-06 | 2015-11-06 14:33 | 2015-11-06 14:33 | RHEEM - RCBA4882 | 85 | 0 | Yes | Yes | 21.1 | 16 | 5.2 | B1F8624494B044AABBABE5AF982DD6B7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6632 |  | 2015-08-13 | 2015-08-13 12:35 | 2015-08-13 12:35 | YORK - E2HB024S06A | 82 | 0 | Yes | Yes | 22.3 | 22.1 | 0.2 | 91F1DF304E4142E5896A11859590ABE2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3115 |  | 2015-09-14 | 2015-09-14 16:53 | 2015-09-14 16:53 | CARRIER - 24ABB336W310 | 85 | 0 | Yes | Yes | 17.7 | 16.8 | 0.9 | 099296A5F44C4FD4B84ECEE817F43195 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7100 |  | 2015-09-08 | 2015-09-08 16:35 | 2015-09-08 16:35 | PAYNE - 591ANX060000AAAA | 167 | 0 | Yes | Yes | 23 | 17.5 | 5.5 | 9B98A44FCFAE458D86131DB37083F197 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4111 |  | 2015-10-29 | 2015-10-29 11:12 | 2015-10-29 11:46 | YORK - DAYH-F018N045C | 70 | 6.3 | Yes | Yes | 17.5 | 19.3 | -1.8 | 3FECDE032B724971AAC6E25F95D17626 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Gilroy | CA | 95020-4325 |  | 2015-09-25 | 2015-09-25 13:41 | 2015-09-25 13:41 | CARRIER - 38VH004300 | 144 | 28.1 | Yes | Yes | 29.6 | 21.4 | 8.2 | F1DB0340C7C04258A961906A83620781 | Add refrigerant: 28.1 oz | R22 | Non-TXV |  | 19.51% | 0.80486 | 37.5% | [5 empty] | Non-TXV | 19.51%
Bakersfield | CA | 93313-5151 |  | 2015-09-01 | 2015-09-01 14:41 | 2015-09-01 14:41 | CARRIER - 38BR030300 | 72 | 0 | Yes | Yes | 22.5 | 22.9 | -0.4 | 22D2A6A4181A41DF9E4E53C16E90EF7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2238 |  | 2015-08-12 | 2015-08-12 10:46 | 2015-08-12 11:03 | OTHER - H2A336GKA100 | 143 | 5 | Yes | Yes | 21 | 22.6 | -1.6 | 85997DBBEB15494FA184E5FFA7FD0412 |  | R22 | Non-TXV |  | 3.497% | 0.96503 | 6.72% | [5 empty] | Non-TXV | 3.497%
Fresno | CA | 93706-4121 |  | 2015-10-05 | 2015-10-05 12:11 | 2015-10-05 12:11 | YORK - DAYH-F018N045C | 70 | 0 | Yes | Yes | 21.3 | 19.3 | 2 | A2850998589C462B827D1CE7CB93E008 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94582-4244 |  | 2015-08-04 | 2015-08-04 12:15 | 2015-08-04 12:15 | CARRIER - 38EH024300 | 86 | 0 | Yes | Yes | 27.5 | 22.4 | 5.1 | AF30F8004D4B4126954FFE061449E142 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-5412 |  | 2015-11-05 | 2015-11-05 12:32 | 2015-11-05 12:50 | TRANE - YCP036FMOAA | 109 | 25.7 | Yes | Yes | 21.1 | 21.5 | -0.4 | 63C9AAE0D39C46F6B25AFDDAB98F5DDE |  | R22 | Non-TXV |  | 23.58% | 0.76422 | 45.31% | [5 empty] | Non-TXV | 23.58%
Clovis | CA | 93611-6620 |  | 2015-09-14 | 2015-09-14 10:39 | 2015-09-14 10:39 | RUUD - N/A | 85 | 0 | Yes | Yes | 21.7 | 19.3 | 2.4 | A17BE06709AC4A91A8BB5441B612F851 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1246 |  | 2015-10-07 | 2015-10-07 16:05 | 2015-10-07 16:05 | LENNOX - HP290361P | 117 | 0 | Yes | Yes | 23.7 | 21.5 | 2.2 | D452E586F1AC45DFA9DBDE402A253556 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1314 |  | 2015-10-23 | 2015-10-23 12:01 | 2015-10-23 12:01 | BDP - 585A036080YACR | 85 | 0 | Yes | Yes | 22.5 | 19.8 | 2.7 | 54C1EEF2C44E49E1B9739146281A08A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1771 |  | 2015-09-22 | 2015-09-22 16:41 | 2015-09-22 16:41 | GOODMAN - GPG13300451BB | 77 | 0 | Yes | Yes | 22.7 | 23.6 | -0.9 | 4AC4CC22D13F41FD8B88F334CC9A8184 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5537 |  | 2015-09-10 | 2015-09-10 15:02 | 2015-09-10 15:02 | DAY & NIGHT - UNK | 85 | 0 | Yes | Yes | 19.1 | 19.5 | -0.4 | BF1B00EBC535405CBED155BE81C2444E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1736 |  | 2015-08-20 | 2015-08-20 11:56 | 2015-08-20 11:56 | OTHER - 38TKB024301 | 65 | 0 | Yes | Yes | 16.2 | 18.3 | -2.1 | 3B27F9F2B71D4EFF94577202E8F69773 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clayton | CA | 94517-1222 |  | 2015-08-18 | 2015-08-18 13:25 | 2015-08-18 13:47 | OTHER - AEA036GC | 116 | 12.1 | Yes | Yes | 22.4 | 19.7 | 2.7 | F6C5A9C1ECAC405E9FD1FAE10A9308D2 |  | R22 | TXV |  | 10.43% | 0.89569 | 20.05% | [5 empty] | TXV | 10.43%
Clovis | CA | 93619-9239 |  | 2015-08-28 | 2015-08-28 13:27 | 2015-08-28 13:27 | PAYNE - Y3GNAA42090NA | 97 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | C71C0899B2DE48EEA07CEEA3C6656541 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4048 |  | 2015-08-27 | 2015-08-27 09:29 | 2015-08-27 09:29 | CARRIER - 48GSN036060301 | 58 | 0 | Yes | Yes | 26.2 | 21 | 5.2 | C2445AB4063C4B3CAB606DA8EB9C18AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5636 |  | 2015-08-31 | 2015-08-31 10:17 | 2015-08-31 10:17 | LENNOX - N/A | 85 | 0 | Yes | Yes | 24.3 | 19.6 | 4.7 | C3748AADFB57441E93046AC47DA8B2B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1618 |  | 2015-08-13 | 2015-08-13 11:32 | 2015-08-13 11:32 | AMANA - TCA48AKA4 | 85 | 0 | Yes | Yes | 17.8 | 19.3 | -1.5 | AB13D81F6A0B4B4094A93D0171556E2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-0000 |  | 2015-10-02 | 2015-10-02 12:25 | 2015-10-02 12:25 | CARRIER - 50HX030 | 85 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | 666B2125067F4F30848F5A7045C92A61 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3140 |  | 2015-08-11 | 2015-08-11 10:59 | 2015-08-11 10:59 | GOODMAN - GSC130481BA | 102 | 0 | Yes | Yes | 22.8 | 22.6 | 0.2 | EFA560F476D04F31B439FA68B3783145 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5262 |  | 2015-08-26 | 2015-08-26 10:42 | 2015-08-26 10:42 | OTHER - H2RD042S06B | 141 | 0 | Yes | Yes | 19.2 | 19.9 | -0.7 | 0A3DCABF0D4F4D35A811D16B45C39069 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-6707 |  | 2015-10-19 | 2015-10-19 16:04 | 2015-10-19 16:04 | TRANE - 4TTR4042A1000AA | 103 | 0 | Yes | Yes | 19.8 | 22 | -2.2 | CA9248A07D6C4B9786048AB3E646FF82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2326 |  | 2015-10-14 | 2015-10-14 13:22 | 2015-10-14 13:22 | GE - BTR948A100AO | 146 | 0 | Yes | Yes | 21.3 | 19.8 | 1.5 | 5FED4E2DD61041D2BA4E211E84203A07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4147 |  | 2015-08-27 | 2015-08-27 15:21 | 2015-08-27 15:21 | AMERICAN STANDARD - YCY048G1H0AD | 187 | 0 | Yes | Yes | 20.1 | 22.8 | -2.7 | 4CD14975AB7848AE9755CA167D8DCCF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3344 |  | 2015-08-13 | 2015-08-13 10:46 | 2015-08-13 10:46 | TRANE - TTBO42C100A1 | 96 | 0 | Yes | Yes | 16.9 | 18.7 | -1.8 | F45738D9AFC349879CECA0D4D097DD97 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5648 |  | 2015-10-12 | 2015-10-12 08:23 | 2015-10-12 08:23 | BDP - 585GJW036060A8AF | 86 | 0 | Yes | Yes | 18.6 | 18.7 | -0.1 | 34C4CCD1DF9748BE9CC8C151080E8C1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-1720 |  | 2015-08-04 | 2015-08-04 13:22 | 2015-08-04 13:22 | CARRIER - 38TRA036330 | 99 | 0 | Yes | Yes | 22.6 | 19.9 | 2.7 | 6FDD9B95C28640E3B9F022682B0F9B9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5203 |  | 2015-09-25 | 2015-09-25 10:58 | 2015-09-25 10:58 | TRANE - 4TTX4030A1000AB | 79 | 0 | Yes | Yes | 15.5 | 18.3 | -2.8 | 017CC0FF5B8E4F369D9F5F4CC811B24D |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5506 |  | 2015-08-10 | 2015-08-10 13:20 | 2015-08-10 13:20 | RUUD - UAKA-037JAZ | 79 | 0 | Yes | Yes | 19.7 | 22.5 | -2.8 | 642E46ABFD344444A713054357446AC9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7638 |  | 2015-10-19 | 2015-10-19 12:16 | 2015-10-19 12:16 | GOODMAN - GSC130421BB | 31 | 0 | Yes | Yes | 21.4 | 17.3 | 4.1 | 290BCAEFE0114FB681E3B5E81399B897 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3250 |  | 2015-08-11 | 2015-08-11 11:48 | 2015-08-11 11:48 | UNITARY PRODUCTS GROUP - H2RD048S06B | 134 | 0 | Yes | Yes | 20.6 | 21 | -0.4 | 33C94876D0704CCE9923AAE2A125D9D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3446 |  | 2015-09-10 | 2015-09-10 11:58 | 2015-09-10 11:58 | RHEEM - UNK | 85 | 0 | Yes | Yes | 22.5 | 18.3 | 4.2 | E6572BAA64C142B28B42C45066424CA4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8492 |  | 2015-08-27 | 2015-08-27 19:58 | 2015-08-27 19:58 | CARRIER - 018 | 85 | 0 | Yes | Yes | 14.5 | 17.5 | -3 | B8A26EAE6D6849BCA72C3CDB8A2F8A71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5912 |  | 2015-08-12 | 2015-08-12 13:46 | 2015-08-12 13:46 | - 13AJA30A01 | 98 | 0 | Yes | Yes | 18 | 18.6 | -0.6 | 333B5CCB97AE41828BB62FB8F3183588 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4133 |  | 2015-10-08 | 2015-10-08 09:42 | 2015-10-08 09:42 | YORK - DAYH-F018N045C | 70 | 0 | Yes | Yes | 20.2 | 18.7 | 1.5 | 5DEEFA3A574C4ADF9683C526FC766BB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1603 |  | 2015-07-31 | 2015-07-31 09:59 | 2015-07-31 09:59 | TRANE - YCC030F1M0BC | 72 | 0 | Yes | Yes | 28.8 | 22 | 6.8 | C9FA1A5304144E1E95706C566E66E9E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4327 |  | 2015-10-20 | 2015-10-20 13:19 | 2015-10-20 13:19 | GOODMAN - GPG1336045M41BA | 70 | 0 | Yes | Yes | 21.1 | 17.7 | 3.4 | A1AC361CFD2A46838DF7B6E85F0AE361 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2518 |  | 2015-08-10 | 2015-08-10 10:10 | 2015-08-10 10:10 | CARRIER - 561CJO30-E | 67 | 0 | Yes | Yes | 18.9 | 18.2 | 0.7 | FE89F5BE504F4B53AE0118B51B7F432F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6559 |  | 2015-09-29 | 2015-09-29 13:19 | 2015-09-29 13:19 | LENNOX - 13ACC06023002 | 168 | 0 | Yes | Yes | 23.2 | 19.1 | 4.2 | 6CC3739ED3744A9D923AF1FC390E0690 | Actual Subcooling cannot be negative. Please check entries. | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5729 |  | 2015-09-30 | 2015-09-30 16:43 | 2015-09-30 16:43 | RUUD - 13AJN36A01 | 90 | 0 | Yes | Yes | 21.9 | 19.9 | 2 | 7C61D4F6AC124E88815502ED7BFA370C |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7353 |  | 2015-10-20 | 2015-10-20 14:41 | 2015-10-20 14:41 | CARRIER - 12GCS030-75-3PA | 85 | 0 | Yes | Yes | 26.1 | 20.4 | 5.7 | 1717638F5688489887F6B4F904B60D08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0602 |  | 2015-09-04 | 2015-09-04 10:17 | 2015-09-04 10:17 | ICP - PGF036K060B | 71 | 0 | Yes | Yes | 18.1 | 19.7 | -1.6 | 620A9D2E6FA3490F87CAD1D665E7EAC3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7048 |  | 2015-09-03 | 2015-09-03 16:04 | 2015-09-03 16:04 | ARMSTRONG - PGE10A24D050LA-2A | 50 | 0 | Yes | Yes | 20.4 | 19.2 | 1.2 | A7C0EAEACFF647F8AC4A89AE339C43C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2216 |  | 2015-09-08 | 2015-09-08 13:54 | 2015-09-08 13:54 | CARRIER - N/A | 85 | 0 | Yes | Yes | 22.1 | 21.2 | 0.9 | D3E8571B0A4247E18EC9899DB41FF1B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2217 |  | 2015-07-31 | 2015-07-31 12:00 | 2015-07-31 12:00 | CARRIER - 38CKB030300 | 68 | 0 | Yes | Yes | 17.1 | 19.9 | -2.8 | 70A5BA93B8DE487D907F59FE26A1EA80 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0513 |  | 2015-09-01 | 2015-09-01 16:04 | 2015-09-01 16:04 | GOODMAN - 13G48AE | 152 | 0 | Yes | Yes | 19.5 | 21.8 | -2.3 | A23CCE23D75E4BCB97A370D2102C3A30 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4604 |  | 2015-09-24 | 2015-09-24 11:47 | 2015-09-24 11:47 | DAY & NIGHT - 565BU030 | 71 | 0 | Yes | Yes | 19.2 | 18.1 | 1.1 | F1B1D08D45E14711AC564E1D0B5AF030 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6358 |  | 2015-08-24 | 2015-08-24 14:14 | 2015-08-24 14:14 | YORK - H1RA048S06D | 117 | 0 | Yes | Yes | 16.7 | 19.6 | -2.9 | C1434DABEE20484E854D5201426D113F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3139 |  | 2015-08-11 | 2015-08-11 10:27 | 2015-08-11 10:27 | GOODMAN - GPG1336045M41AB | 85 | 0 | Yes | Yes | 28 | 22.4 | 5.6 | 96D3A7037374444EBDB26F9E66B05D98 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3142 |  | 2015-08-11 | 2015-08-11 11:13 | 2015-08-11 11:13 | CARRIER - 48SDN042060301 | 170 | 0 | Yes | Yes | 19.1 | 19 | 0.1 | E8526357875E43249200DFB635A28CD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3523 |  | 2015-09-21 | 2015-09-21 11:17 | 2015-09-21 11:17 | CARRIER - N/A | 85 | 0 | Yes | Yes | 23.3 | 22.5 | 0.8 | 46DA601D624F46499CDDAAA3D8C0A560 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6322 |  | 2015-08-20 | 2015-08-20 10:20 | 2015-08-20 10:20 | PAYNE - PA13NR04800GAJAA | 85 | 0 | Yes | Yes | 15.9 | 18.2 | -2.3 | 2DEA813AB1B8406E90C7A04A10A91BB2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4969 |  | 2015-09-01 | 2015-09-01 11:26 | 2015-09-01 11:26 | AMERICAN STANDARD - 2A7A1036A1000AA | 73 | 0 | Yes | Yes | 16.9 | 19.3 | -2.4 | 891330BB41B24D3A9129BA9CD8917ECA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1009 |  | 2015-10-02 | 2015-10-02 10:06 | 2015-10-02 10:06 | PAYNE - 568EJX024000ABAA | 63 | 0 | Yes | Yes | 25.9 | 24.6 | 1.3 | 313B936DB0D948F1BD4D83F572590C4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-2020 |  | 2015-10-08 | 2015-10-08 10:38 | 2015-10-08 10:38 | OTHER - UNK | 85 | 0 | Yes | Yes | 27.2 | 22.3 | 4.9 | C9D4E619F49A48BC9674434C6EB2443D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93314-3736 |  | 2015-08-20 | 2015-08-20 09:11 | 2015-08-20 09:11 | TEMPSTAR - 867 815035 | 90 | 0 | Yes | Yes | 18.3 | 20.4 | -2.1 | A3028EC14019433491EC0412E775DC60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5817 |  | 2015-08-13 | 2015-08-13 14:17 | 2015-08-13 14:17 | YORK - H1RA060S06A | 124 | 0 | Yes | Yes | 24.2 | 21.7 | 2.5 | 017F93EF45C2415BAD89310CCCB86565 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3753 |  | 2015-09-08 | 2015-09-08 14:39 | 2015-09-08 14:39 | CARRIER - 38CKC042 351 | 81 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | 3B97A598C5A8497EB3427025F475A0DA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3303 |  | 2015-10-20 | 2015-10-20 13:43 | 2015-10-20 13:43 | RHEEM - RRNL-B036JK06X | 47 | 0 | Yes | Yes | 25.5 | 20.4 | 5.1 | A80BE5F4A0794188B58F3F3946B72A29 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-0000 |  | 2015-11-06 | 2015-11-06 09:36 | 2015-11-06 09:36 | GUARDIAN - GCGD48521520 | 104 | 0 | Yes | Yes | 26.3 | 20.9 | 5.4 | 8BB0243AC3084BB5A695564CA9A11850 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3800 |  | 2015-09-12 | 2015-09-12 17:05 | 2015-09-12 17:05 | CARRIER - 24AB324A003001A | 72 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | 4EFC8BAA957042EDB270B2621F2F095E |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2659 |  | 2015-11-04 | 2015-11-04 14:30 | 2015-11-04 14:30 | CARRIER - UNKNOWN | 87 | 0 | Yes | Yes | 16.7 | 19.6 | -2.9 | FEB9AB6B51DD47B8BC4BC45B5114DD0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7017 |  | 2015-09-04 | 2015-09-04 12:16 | 2015-09-04 12:16 | RHEEM - RPKA019JAZ | 57 | 0 | Yes | Yes | 18.7 | 19.8 | -1.1 | B8C71D328A874C84AC17371C86B042AD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5122 |  | 2015-10-20 | 2015-10-20 12:15 | 2015-10-20 12:15 | GOODMAN - GPG13420701AB | 105 | 0 | Yes | Yes | 19.5 | 18.4 | 1.1 | 7E5BB02B237043AC9C0E7CE7EF132D17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-7377 |  | 2015-09-02 | 2015-09-02 14:38 | 2015-09-02 14:57 | BRYANT - 563AN036-A | 122 | 10.6 | Yes | Yes | 24.3 | 20.9 | 3.4 | 1F46B9B7C5D340BD94C11537A797B7E9 |  | R22 | Non-TXV |  | 8.689% | 0.91311 | 16.7% | [5 empty] | Non-TXV | 8.689%
Fresno | CA | 93706-4118 |  | 2015-09-30 | 2015-09-30 08:51 | 2015-09-30 08:51 | UNITARY PRODUCTS GROUP - DAYH-F018N04C | 70 | 0 | Yes | Yes | 21.4 | 19.5 | 1.9 | 97C27640F78E436EB2D2FE68D45BBA2D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-8210 |  | 2015-10-21 | 2015-10-21 14:19 | 2015-10-21 14:19 | BRYANT - 537GN030A | 85 | 0 | Yes | Yes | 24 | 20.4 | 3.6 | 359BE1AA71234B6BA15DCC254D65F27F |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6625 |  | 2015-09-14 | 2015-09-14 09:06 | 2015-09-14 09:06 | RUUD - N/A | 85 | 0 | Yes | Yes | 17.8 | 20.2 | -2.4 | 4AE2CF7D2A264200B36EA527FFBD398C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7070 |  | 2015-08-25 | 2015-08-25 14:52 | 2015-08-25 14:52 | PAYNE - 591ANX036000AAAA | 86 | 0 | Yes | Yes | 21.3 | 23.4 | -2.1 | 3B5562ECC9D24CA1B89420A2D4D7DA4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7741 |  | 2015-11-09 | 2015-11-09 12:44 | 2015-11-09 12:44 | OTHER - GCGD6052152B | 163 | 0 | Yes | Yes | 25 | 20.4 | 4.6 | 9DAD698842E34440B1324B9BC465EB27 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5172 |  | 2015-09-16 | 2015-09-16 14:44 | 2015-09-16 14:44 | CARRIER - 38QRR024-3 | 112 | 0 | Yes | Yes | 17.6 | 19.9 | -2.3 | 0EB53D8F443E4D00BF5D1C8401E6E991 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5377 |  | 2015-08-28 | 2015-08-28 08:49 | 2015-08-28 09:10 | LENNOX - 13ACD-036-230-02 | 111 | 18 | Yes | Yes | 26.3 | 22.1 | 4.2 | E4FEC791BD6F4C28A6B7CB1E890E5723 |  | R22 | Non-TXV |  | 16.22% | 0.83784 | 31.16% | [5 empty] | Non-TXV | 16.22%
Vacaville | CA | 95687-4361 |  | 2015-09-04 | 2015-09-04 13:33 | 2015-09-04 13:33 | GOODMAN - CLJ361A | 90 | 0 | Yes | Yes | 17.9 | 19.2 | -1.3 | 6C7900091811462BB683BCAAB848E947 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5237 |  | 2015-10-02 | 2015-10-02 15:32 | 2015-10-02 15:32 | LENNOX - EGCX29X-042-75-2PA | 73 | 0 | Yes | Yes | 21.4 | 21.5 | -0.1 | CFBB83DB82004FAAAB3B24EF08B48B87 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6408 |  | 2015-08-18 | 2015-08-18 10:18 | 2015-08-18 10:18 | DAY & NIGHT - 591ANX036000AAAA | 87 | 0 | Yes | Yes | 23.2 | 23.1 | 0.1 | 405B7FE834B54A05BC31B4D1D9D77173 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4921 |  | 2015-09-02 | 2015-09-02 09:26 | 2015-09-02 09:26 | RUUD - UAMB036JAS | 93 | 0 | Yes | Yes | 19 | 18 | 1 | 8ED0526FACB246349A6FF29F57D7E975 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Friant | CA | 93626-0000 |  | 2015-11-04 | 2015-11-04 09:44 | 2015-11-04 09:44 | GOODMAN - GPH1336M21AA | 165 | 0 | Yes | Yes | 20.9 | 18.2 | 2.7 | 41E5BDDEC8E04826B53162FA701D4C27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4013 |  | 2015-09-21 | 2015-09-21 12:16 | 2015-09-21 12:16 | GOODMAN - GPG1330045M41C4 | 78 | 0 | Yes | Yes | 27.1 | 21.3 | 5.8 | C51F6D319E6148C68FC9512FC45DA528 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4395 |  | 2015-11-05 | 2015-11-05 10:25 | 2015-11-05 10:25 | OTHER - CA7036VK2A | 140 | 0 | Yes | Yes | 25.8 | 20.6 | 5.2 | 8957F52BE7B04D0DB0F83F6F5C03C080 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6761 |  | 2015-08-26 | 2015-08-26 09:06 | 2015-08-26 09:06 | RHEEM - UAKA042JAZ | 88 | 0 | Yes | Yes | 20.1 | 19.3 | 0.8 | FF0BCF392F534D5CAACB385FBDE98579 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7723 |  | 2015-10-02 | 2015-10-02 09:36 | 2015-10-02 09:36 | PAYNE - 591ANX060000AAAA | 166 | 0 | Yes | Yes | 17.7 | 18.3 | -0.6 | 25770E2BB66549FF8932C097E7723E39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1847 |  | 2015-09-15 | 2015-09-15 13:37 | 2015-09-15 13:37 | TRANE - 2TTB0036A1000AA | 76 | 0 | Yes | Yes | 21.6 | 22.2 | -0.6 | 81913226F2DC4FA8A18C02743A70477C |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6261 |  | 2015-11-03 | 2015-11-03 11:35 | 2015-11-03 11:35 | YORK - UNK | 85 | 0 | Yes | Yes | 17.5 | 17.7 | -0.2 | 8860F443979C458BABC596C780031445 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-1150 |  | 2015-09-04 | 2015-09-04 15:49 | 2015-09-04 15:49 | CARRIER - 38BRC048350 | 85 | 0 | Yes | Yes | 17.2 | 19.8 | -2.6 | 895CC9BD1DF0430196875AF5B5298769 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-5508 |  | 2015-09-11 | 2015-09-11 09:30 | 2015-09-11 09:30 | CARRIER - 38CK036350 | 85 | 0 | Yes | Yes | 22.5 | 18.7 | 3.8 | 195E77A3F9E44BA6BD466913F5AC9A51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2313 |  | 2015-08-21 | 2015-08-21 09:13 | 2015-08-21 09:13 | TRANE - 2TTR3036A1000AA | 101 | 0 | Yes | Yes | 15.8 | 18.3 | -2.5 | 78E1E543D2684765B3B047A66E14EA0D |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4215 |  | 2015-08-04 | 2015-08-04 11:23 | 2015-08-04 11:23 | ICP - D1NH042N06506C | 94 | 0 | Yes | Yes | 28 | 23.2 | 4.8 | B354BE74AE204399AD00E6224B44C5C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4739 |  | 2015-09-28 | 2015-09-28 13:48 | 2015-09-28 13:48 | UNITARY PRODUCTS GROUP - DAYP-FO42N080A | 150 | 0 | Yes | Yes | 25.6 | 22.1 | 3.5 | 0AA30AB73669430B9DC7742F744DBCA6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2145 |  | 2015-10-08 | 2015-10-08 11:24 | 2015-10-08 11:24 | PAYNE - PY3PNA042060NA | 168 | 0 | Yes | Yes | 21.7 | 15.8 | 5.9 | 2A6944B625464C53894D2C9C207986B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4052 |  | 2015-09-03 | 2015-09-03 14:56 | 2015-09-03 14:56 | PAYNE - PA13NR36H | 91 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | D97F37368D4F4456B6EF58EEC47E4D2A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3150 |  | 2015-10-05 | 2015-10-05 13:43 | 2015-10-05 13:43 | BRYANT - 574DNWA30040NATP | 98 | 0 | Yes | Yes | 18.7 | 21 | -2.3 | 1116A5CB60C04A758D3D7BA9EC8DF191 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3688 |  | 2015-09-25 | 2015-09-25 11:52 | 2015-09-25 11:52 | OTHER - TCA024AKA1 | 69 | 0 | Yes | Yes | 22.1 | 22.4 | -0.3 | 592666D30F1A4E23B39FE12F49C4071E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3892 |  | 2015-09-02 | 2015-09-02 09:37 | 2015-09-02 09:37 | CARRIER - PA10JA024-C | 64 | 0 | Yes | Yes | 16.1 | 18.2 | -2.1 | D5CFC1653E344FB189FF4CA35F66FCAD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3931 |  | 2015-10-22 | 2015-10-22 11:31 | 2015-10-22 11:31 | TRANE - TTB036X100A1 | 90 | 0 | Yes | Yes | 25.1 | 21.1 | 4 | 7F401FBF65FE4073AE95EFE5ACFB28AA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5755 |  | 2015-08-10 | 2015-08-10 13:02 | 2015-08-10 13:02 | BRYANT - 113RNA036-B | 90 | 0 | Yes | Yes | 20.9 | 23.1 | -2.2 | 5C21EA0AEF944B568AB9991F7DFC3209 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1751 |  | 2015-09-01 | 2015-09-01 09:30 | 2015-09-01 09:51 | OTHER - BRCQ0481BB | 87 | 23.6 | Yes | Yes | 20.2 | 18.2 | 2 | 0C3AF1D9F02F497FA5D531282F626CE1 |  | R22 | Non-TXV |  | 27.13% | 0.72874 | 52.13% | [5 empty] | Non-TXV | 27.13%
Fresno | CA | 93727-3305 |  | 2015-09-22 | 2015-09-22 10:29 | 2015-11-05 15:00 | RHEEM - RRNABO42JKO8X | 104 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 876C208E72314713A1505E8394D8A6E8 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7071 |  | 2015-09-19 | 2015-09-19 11:01 | 2015-09-19 11:01 | OTHER - 591ANX036000AAAA | 84 | 0 | Yes | Yes | 19.8 | 19.3 | 0.5 | FCB5D2AAABE145638A7A1656E4C81B3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2941 |  | 2015-09-10 | 2015-09-10 10:05 | 2015-09-10 10:05 | WESTINGHOUSE - FS3BC-048KA | 110 | 0 | Yes | Yes | 24.8 | 21 | 3.8 | 3FDF965CD47A4F18ACF1B8F1E9BC5BBE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-1519 |  | 2015-11-23 | 2015-11-23 15:21 | 2015-11-23 15:21 | YORK - YCJD6054152A | 93 | 0 | Yes | Yes | 28.1 | 22.8 | 5.3 | 9D88CAD13BA14B748DB0B626DB38855C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4121 |  | 2015-10-26 | 2015-10-26 13:35 | 2015-10-26 13:35 | YORK - DAYH-F018N045C | 70 | 0 | Yes | Yes | 21.3 | 19.7 | 1.7 | 74067D03FFEA437FBF2C7EBE32D3D957 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4146 |  | 2015-10-06 | 2015-10-06 13:20 | 2015-10-06 13:20 | YORK - DAYH-F018N045C | 70 | 0 | Yes | Yes | 17.7 | 17.7 | 0 | D18B736D2F28465AAC338C52AB930F48 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-4235 |  | 2015-09-10 | 2015-09-10 10:13 | 2015-09-10 10:13 | - CA5548VKD1 | 134 | 0 | Yes | Yes | 18.7 | 19 | -0.3 | 05E4C114D4924C5CB4DAC49D84C75FF3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4134 |  | 2015-09-30 | 2015-09-30 13:45 | 2015-09-30 13:45 | UNITARY PRODUCTS GROUP - DAYH-F018N045C | 68 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | B8E311A20F07416E9A67AC5E142A54E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3413 |  | 2015-08-28 | 2015-08-28 12:03 | 2015-08-28 12:27 | RUUD - UAKA-O24JAZ | 85 | 5.8 | Yes | Yes | 18.7 | 20.2 | -1.5 | A22137669DDE4253A29684680D0090C1 |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Walnut Creek | CA | 94597-3687 |  | 2015-08-26 | 2015-08-26 14:50 | 2015-08-26 14:50 | TRANE - 8TD730A100B | 74 | 0 | Yes | Yes | 16.2 | 18.7 | -2.5 | 86338223265A49CFA339E33DECAEB099 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6957 |  | 2015-08-18 | 2015-08-18 12:24 | 2015-08-18 12:24 | YORK - H2RC030S06A | 88 | 0 | Yes | Yes | 17.9 | 20.6 | -2.7 | CD2E9C60674F46F2BBED1FE95FC656D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4815 |  | 2015-08-11 | 2015-08-11 08:50 | 2015-08-11 08:50 | RHEEM - RRNL-B048JK08X | 161 | 0 | Yes | Yes | 23.6 | 19.9 | 3.7 | 59F342485BD2403BADD9A267043AD11A |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94583-4103 |  | 2015-10-29 | 2015-10-29 16:32 | 2015-10-29 16:32 | CARRIER - 38CKB048---301-- | 102 | 0 | Yes | Yes | 27.1 | 22 | 5.1 | 3CC27C29AFEE46968DC862D5585AC40C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2188 |  | 2015-10-14 | 2015-10-14 14:04 | 2015-10-14 14:04 | GOODMAN - GSC130361DE | 119 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | EEB2C61ADE5041169FDAA35467890B4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1576 |  | 2015-08-06 | 2015-08-06 13:38 | 2015-08-06 13:38 | LENNOX - 13ACC-024-230-01 | 81 | 0 | Yes | Yes | 17.3 | 18.6 | -1.3 | 0616794A35E44E9FBFEDBCC11158D6E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5655 |  | 2015-08-12 | 2015-08-12 16:20 | 2015-08-12 16:20 | DAY & NIGHT - N4A336AKB300 | 85 | 0 | Yes | Yes | 20.5 | 18.3 | 2.2 | 1F7C7738442B4FB5908C9983DBC4AEFC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5212 |  | 2015-08-14 | 2015-08-14 11:48 | 2015-08-14 11:48 | TRANE - TTB036C100A1 | 90 | 0 | Yes | Yes | 23.3 | 21 | 2.3 | CDC6960C0A8C42B69511107EF985AB18 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6460 |  | 2015-09-19 | 2015-09-19 13:26 | 2015-09-19 13:26 | LENNOX - 10ACB18-9 | 68 | 0 | Yes | Yes | 17.9 | 18.5 | -0.6 | 2C7478AEA5674F0094F0804A4D9E6238 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1973 |  | 2015-09-29 | 2015-09-29 13:01 | 2015-09-29 13:01 | BRYANT - N2A336GKA200 | 85 | 0 | Yes | Yes | 21.2 | 18.8 | 2.4 | 4BEF26CDFEFF4E99BF92CE4BAB45F953 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5533 |  | 2015-08-31 | 2015-08-31 14:56 | 2015-08-31 14:56 | OTHER - CA5542VKD2 | 98 | 0 | Yes | Yes | 21.2 | 22.9 | -1.7 | 6CB13EB951DE45CDA691C038B812C1A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8063 |  | 2015-08-25 | 2015-08-25 10:44 | 2015-08-25 10:44 | ARCOAIRE - PGF036K060A | 71 | 0 | Yes | Yes | 17.5 | 13.3 | 4.3 | 8290351D97814CAC931A3A4C899C7B5E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2648 |  | 2015-09-09 | 2015-09-09 13:15 | 2015-09-09 13:38 | RHEEM - HC-100 42-21C | 150 | 14.8 | Yes | Yes | 23.4 | 22 | 1.4 | 458FD747A8814C48BFED2033729CB11C |  | R22 | Non-TXV |  | 9.867% | 0.90133 | 18.96% | [5 empty] | Non-TXV | 9.867%
Woodland | CA | 95695-2615 |  | 2015-10-06 | 2015-10-06 10:23 | 2015-10-06 10:23 | GOODMAN - CL-J30-1A | 105 | 0 | Yes | Yes | 14.3 | 17.2 | -2.9 | 850E05126F34446FAEC219660938EB07 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2740 |  | 2015-10-21 | 2015-10-21 16:42 | 2015-10-21 16:42 | TRANE - TTB030 | 70 | 0 | Yes | Yes | 14.5 | 20.4 | -5.9 | 6F76EFCE08E94FCB8EDBB8B5CF401152 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5326 |  | 2015-09-29 | 2015-09-29 10:53 | 2015-09-29 10:53 | CARRIER - 48DL029BB | 41 | 0 | Yes | Yes | 21.7 | 17.5 | 4.3 | E7FDA82AFD0948A0A57E360B1D329D77 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-3561 |  | 2015-08-25 | 2015-08-25 11:46 | 2015-08-25 11:46 | TRANE - 2TTR2042BB1000A | 85 | 0 | Yes | Yes | 14.9 | 15.5 | -0.6 | 3424A0183F5B4366ABCFF73EA695B90E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-3646 |  | 2015-08-17 | 2015-08-17 14:16 | 2015-08-17 14:16 | TRANE - TTB060D100A | 131 | 0 | Yes | Yes | 17.2 | 12.8 | 4.4 | 00B501F35A3A488FB65A3E90F662BD6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4486 |  | 2015-09-08 | 2015-09-08 12:17 | 2015-09-08 12:17 | CARRIER - 582ANW030040AAAD | 55 | 0 | Yes | Yes | 16.9 | 19 | -2.1 | 55ABBA7AB9F649DC94E14A637C2CCA44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-5021 |  | 2015-08-20 | 2015-08-20 13:09 | 2015-08-20 13:09 | DAY & NIGHT - 565BBX06000A0 | 120 | 0 | Yes | Yes | 18.1 | 18.3 | -0.2 | 49C5981B47744C26A027198990ED9A59 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5938 |  | 2015-09-21 | 2015-09-21 11:39 | 2015-09-21 11:39 | BDP - 56540036-A | 85 | 0 | Yes | Yes | 26.1 | 20.2 | 6 | C781D660A6BC4C5EA25DD478D8AAC1B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3221 |  | 2015-10-20 | 2015-10-20 11:42 | 2015-10-20 11:43 | CARRIER - 48SX4036080301AA | 86 | 3.8 | Yes | Yes | 19.6 | 22.6 | -3 | 35E823B578F140D1A2F4AC942760F8F8 |  | R22 | Non-TXV |  | 4.419% | 0.95581 | 8.492% | [5 empty] | Non-TXV | 4.419%
San Jose | CA | 95111-1712 |  | 2015-08-20 | 2015-08-20 09:11 | 2015-08-20 09:31 | UNITARY PRODUCTS GROUP - PA13NA036000ABAA | 70 | 5.4 | Yes | Yes | 20.4 | 21.4 | -1 | 09C3E734E28D448FA86D2162003358B4 |  | R410A | TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | TXV | 7.714%
Walnut Creek | CA | 94598-2608 |  | 2015-09-02 | 2015-09-02 12:14 | 2015-09-02 12:14 | GOODMAN - CK49-18 | 97 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | B940AFC13C934152B41BB413AFD0E215 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5510 |  | 2015-08-20 | 2015-08-20 09:39 | 2015-08-20 09:39 | TRANE - 2TTR2036A1000AA | 96 | 0 | Yes | Yes | 14.1 | 17 | -2.9 | AFED38EF453C440B89163882A68311F4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1508 |  | 2015-08-25 | 2015-08-25 09:48 | 2015-08-25 09:48 | PAYNE - 561CJ036C | 72 | 0 | Yes | Yes | 22.5 | 19.1 | 3.4 | 90BAFC9A11714F41A2F4ADF32579879B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6218 |  | 2015-09-01 | 2015-09-01 12:32 | 2015-09-01 12:32 | DAY & NIGHT - UNK | 85 | 0 | Yes | Yes | 21.5 | 19.9 | 1.6 | 5E3CB0959866416FA269ABFAD9571B53 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3262 |  | 2015-10-05 | 2015-10-05 13:29 | 2015-10-05 13:29 | COLEMAN - DRCS0361BE | 83 | 0 | Yes | Yes | 23.4 | 19.3 | 4.1 | 50D190367AF6491DAB6E32133FCD9358 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-2250 |  | 2015-09-18 | 2015-09-18 09:25 | 2015-09-18 09:49 | CARRIER - 38CKC042310 | 83 | 14.7 | Yes | Yes | 18 | 17.1 | 0.9 | D8D4EB179A81472B9F3F76633F2B4C1F |  | R22 | Non-TXV |  | 17.71% | 0.82289 | 34.04% | [5 empty] | Non-TXV | 17.71%
Pittsburg | CA | 94565-7917 |  | 2015-10-05 | 2015-10-05 00:31 | 2015-10-05 00:31 | OTHER - 24ABA342A310 | 85 | 0 | Yes | Yes | 21.2 | 21.5 | -0.3 | A58EAF3BC61A4B4B81E8620AAC081CAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6152 |  | 2015-09-28 | 2015-09-28 10:22 | 2015-09-28 10:22 | TRANE - 2TTR2042A1000AA | 95 | 0 | Yes | Yes | 21.2 | 18.8 | 2.4 | EBF05E737E1644FF8E7FB5A8EB13C588 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4346 |  | 2015-09-26 | 2015-09-26 10:42 | 2015-09-26 10:42 | GOODMAN - CLJ42-1A | 99 | 0 | Yes | Yes | 16 | 17.7 | -1.7 | 04265AE094CD4DE2B88A5EE8EA56232D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4346 |  | 2015-09-26 | 2015-09-26 10:48 | 2015-09-26 10:48 | GOODMAN - CLJ42-1A | 99 | 0 | Yes | Yes | 18.2 | 18.8 | -0.6 | 7DDAC3A7B89B4ECDADE3018EA87BFB94 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-7011 |  | 2015-09-04 | 2015-09-04 21:05 | 2015-09-04 21:05 | GIBSON - J53BA-036KA | 69 | 0 | Yes | Yes | 17.4 | 22.8 | -5.4 | AF001116FFF44230AF5D2A2B6D4CF9C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-8141 |  | 2015-08-26 | 2015-08-26 17:28 | 2015-08-26 17:28 | DAY & NIGHT - N4A442GKB200 | 85 | 0 | Yes | Yes | 16.5 | 16.7 | -0.1 | BC5D14191101442A84CD9762F045760E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1281 |  | 2015-09-29 | 2015-09-29 10:34 | 2015-09-29 10:34 | UNITARY PRODUCTS GROUP - H2RD024S06B | 85 | 0 | Yes | Yes | 21.3 | 18.5 | 2.9 | 8164C3E922B14EA1B7964C3CDCCB50FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-4519 |  | 2015-09-03 | 2015-09-03 13:22 | 2015-09-03 13:22 | TRANE - 2TTR1036A1000AA | 73 | 0 | Yes | Yes | 21.5 | 22.1 | -0.6 | 3C681B112F604794AFA70E01809DB0DE |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-4653 |  | 2015-08-20 | 2015-08-20 11:00 | 2015-08-20 11:00 | BRYANT - 563CN030-B | 102 | 0 | Yes | Yes | 29.7 | 24.5 | 5.2 | 31B8BC33C34C458DB41EEF19AFBF1894 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-4333 |  | 2015-11-06 | 2015-11-06 12:29 | 2015-11-06 12:29 | CARRIER - 38CKC042310 | 82 | 0 | Yes | Yes | 20.3 | 21.7 | -1.4 | E3AAF28CBBDA4CD9B71C55CDC4FE488B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3623 |  | 2015-09-10 | 2015-09-10 13:23 | 2015-09-10 13:23 | OTHER - UNK | 100 | 0 | Yes | Yes | 26.8 | 20.9 | 5.9 | 44CA3FC5DBB94C54996713D39B746A91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-6111 |  | 2015-08-07 | 2015-08-07 11:57 | 2015-08-07 11:57 | CARRIER - 38TMA036300 | 85 | 0 | Yes | Yes | 17.5 | 18.8 | -1.3 | 4625817843B84BA3B9C999E78C57C859 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-0361 |  | 2015-10-08 | 2015-10-08 13:10 | 2015-10-08 13:10 | LENNOX - HS29-018-2P | 55 | 0 | Yes | Yes | 16 | 18.8 | -2.8 | BC2B2F02893E4A9C94B8647ABC7CF948 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1259 |  | 2015-10-02 | 2015-10-02 11:20 | 2015-10-02 11:20 | AMANA - RCB42C2C | 90 | 0 | Yes | Yes | 12.5 | 15.3 | -2.8 | CB194040E65D4F5E8C070DC95EA0ACB8 |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6363 |  | 2015-08-21 | 2015-08-21 10:58 | 2015-08-21 10:58 | CARRIER - 38CKC048360 | 98 | 0 | Yes | Yes | 23.2 | 18.7 | 4.5 | 79ECAE40FB84491EBD9DF046CBCF4810 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6378 |  | 2015-08-31 | 2015-08-31 13:55 | 2015-08-31 13:55 | YORK - D1NA024N03606C | 134 | 0 | Yes | Yes | 17 | 19.6 | -2.6 | EAE1F51DC3B64DD1AF53F15485D98C3A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3905 |  | 2015-09-04 | 2015-09-04 21:02 | 2015-09-04 21:02 | TRANE - TTN048C100A3 | 135 | 0 | Yes | Yes | 18.5 | 21.1 | -2.6 | D63A6BD26AFF4BC89A5D5BB24353AF14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Lafayette | CA | 94549-1932 |  | 2015-10-14 | 2015-10-14 15:03 | 2015-10-14 15:03 | CARRIER - 24APA560A300 | 213 | 0 | Yes | Yes | 22.1 | 23.5 | -1.4 | 11F189374E8046DF8747F6EDF83774F1 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7789 |  | 2015-08-24 | 2015-08-24 13:25 | 2015-08-24 13:25 | GOODMAN - CK4918 | 97 | 0 | Yes | Yes | 18.6 | 19.3 | -0.7 | 92BE5F9180A643A197AFDA3BE2504B1C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3002 |  | 2015-09-28 | 2015-09-28 09:13 | 2015-09-28 09:13 | GUARDIAN - RAC13J364S21A | 73 | 0 | Yes | Yes | 16.2 | 19.1 | -2.9 | DA2585A36B0E43539FCEF4781B66A13B |  | R410A | TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1313 |  | 2015-09-18 | 2015-09-18 09:25 | 2015-09-18 09:25 | GIBSON - JT5BD018K | 93 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | E0D5AB545AE940B2A13E69B791BA6D40 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9786 |  | 2015-09-02 | 2015-09-02 14:07 | 2015-09-02 14:07 | PAYNE - PH13NR048H | 157 | 0 | Yes | Yes | 21.2 | 20.8 | 0.4 | C699FCAE0C9B48D494CD06BDB6D1A012 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2628 |  | 2015-10-16 | 2015-10-16 14:26 | 2015-10-16 14:26 | TRANE - TTN030D100A0 | 86 | 0 | Yes | Yes | 20.2 | 21 | -0.8 | 209E57C5058A4BFDAC1532F5692E649E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7011 |  | 2015-09-14 | 2015-09-14 13:56 | 2015-09-14 13:56 | TRANE - BWD718A100B0 | 88 | 0 | Yes | Yes | 15.8 | 18.5 | -2.7 | 4ABEC0EBCA1D4052BF33998BB6D588C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-4118 |  | 2015-09-25 | 2015-09-25 12:27 | 2015-09-25 12:27 | GOODMAN - GPG13360701AC | 112 | 0 | Yes | Yes | 20.7 | 19.7 | 1 | B796B595E599427EB0D2A027A7D8DBF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7239 |  | 2015-11-16 | 2015-11-16 12:48 | 2015-11-16 12:48 | CARRIER - 38TDB060310 | 221 | 0 | Yes | Yes | 19.4 | 19.3 | 0.1 | CF05C66639F64BDC868ABE1F2670162D |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6712 |  | 2015-08-26 | 2015-08-26 11:53 | 2015-08-26 11:53 | RHEEM - UAKA037JAZ | 79 | 0 | Yes | Yes | 20.4 | 19.3 | 1.1 | EA830175C1E7404D8A4694463488BA6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-3632 |  | 2015-09-03 | 2015-09-03 15:05 | 2015-09-03 15:05 | LENNOX - HS290241P | 62 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 0B0674294227441EBC5C085CB95E91FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2240 |  | 2015-08-06 | 2015-08-06 09:49 | 2015-08-06 10:13 | TRANE - TTR036C100A2 | 92 | 17.7 | Yes | Yes | 18.7 | 18.8 | -0.1 | 9D09D8BF3D4949408E12DF78329B4118 |  | R22 | Non-TXV |  | 19.24% | 0.80761 | 36.97% | [5 empty] | Non-TXV | 19.24%
Pittsburg | CA | 94565-4871 |  | 2015-09-21 | 2015-09-21 10:11 | 2015-09-21 10:11 | PAYNE - PA10JA036-A | 85 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | D50BE9571E3F4C6C9B6846F6B070A58F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1412 |  | 2015-08-26 | 2015-08-26 08:15 | 2015-08-26 08:15 | CARRIER - 38CKC042 | 93 | 0 | Yes | Yes | 19.1 | 17.2 | 1.9 | 184E0BD60BFA4F0DA56B03394E6677C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4742 |  | 2015-10-05 | 2015-10-05 13:41 | 2015-10-05 13:41 | OTHER - 38TH042310 | 113 | 0 | Yes | Yes | 20.5 | 21.9 | -1.4 | 57B5F2FE72E246148F603359330F4204 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4336 |  | 2015-09-21 | 2015-09-21 11:09 | 2015-09-21 11:09 | OTHER - 561AJ042-A | 89 | 0 | Yes | Yes | 19.7 | 19.3 | 0.4 | 31BB6CE320B04045AEC4923E90123982 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2739 |  | 2015-08-27 | 2015-08-27 13:58 | 2015-08-27 13:58 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 19.1 | 19.7 | -0.6 | 3AF9EEA688BA406AB8A1CBC0ACBC51EF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-1250 |  | 2015-10-20 | 2015-10-20 11:24 | 2015-10-20 11:24 | YORK - H2RD036S06B | 96 | 0 | Yes | Yes | 26.5 | 21.8 | 4.7 | 4E63CE7C9B7D4065AAE85224F7677D0B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4650 |  | 2015-11-23 | 2015-11-23 14:10 | 2015-11-23 14:10 | BRYANT - 116BNA048-B | 208 | 0 | Yes | Yes | 24.4 | 19.1 | 5.4 | 79ECD699B33C4A319B9B86F771E44681 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95132-1672 |  | 2015-10-08 | 2015-10-08 09:48 | 2015-10-08 09:48 | OTHER - S3BA-042K | 102 | 0 | Yes | Yes | 25 | 20.4 | 4.7 | 414690C7A2494786B88BF33CFB5470A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4610 |  | 2015-08-21 | 2015-08-21 09:20 | 2015-08-21 09:20 | RHEEM - UNKNOWN | 85 | 0 | Yes | Yes | 25.9 | 20 | 5.9 | EB8860D4E9BF44B8AA5C5BB6E115BBD7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-4469 |  | 2015-09-30 | 2015-09-30 16:54 | 2015-09-30 16:54 | PAYNE - PY3GNAA36060NATP | 85 | 0 | Yes | Yes | 17.3 | 20.2 | -2.9 | 6F3A7C39A06644E5BFDA7989484C4C31 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5094 |  | 2015-09-25 | 2015-09-25 09:41 | 2015-09-25 09:41 | BRYANT - UNKNOWN | 121 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | 9C102DA9C9D64CD480684DDE1E862FA8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8319 |  | 2015-08-26 | 2015-08-26 11:24 | 2015-08-26 11:24 | TRANE - TTD736B100A0 | 85 | 0 | Yes | Yes | 14.5 | 17.5 | -3 | DD26C2AEF724441E967036A09730F074 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7187 |  | 2015-10-26 | 2015-10-26 10:35 | 2015-10-26 10:35 | CARRIER - 24ABB348W310 | 123 | 0 | Yes | Yes | 19.3 | 21.5 | -2.2 | AEE188226F474E5DB64204FEEF9C53A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3418 |  | 2015-08-27 | 2015-08-27 09:16 | 2015-08-27 09:16 | DAY & NIGHT - 591ANX036000AAAA | 90 | 0 | Yes | Yes | 24.2 | 18.8 | 5.4 | 7852C522751A40FEBB2B75EC9EDBFE98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95133-2331 |  | 2015-10-08 | 2015-10-08 10:54 | 2015-10-08 10:54 | RHEEM - 13AJN36A01 | 91 | 0 | Yes | Yes | 26.7 | 21.4 | 5.3 | 8F1DDC2B38644EBAA6DCEDCC83B66677 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-4633 |  | 2015-10-05 | 2015-10-05 15:06 | 2015-10-05 15:06 | AMERICAN STANDARD - 7A0060A100A2 | 121 | 0 | Yes | Yes | 15.4 | 17.2 | -1.8 | C218BFA6E4044199AD3E5453FE08EF3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5044 |  | 2015-10-19 | 2015-10-19 12:58 | 2015-10-19 12:58 | TRANE - YCPO42F1MOAC | 100 | 0 | Yes | Yes | 21.1 | 17.7 | 3.4 | 5B1ABDE8BFCD4C1EBB0AF924DA7F1592 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6717 |  | 2015-08-26 | 2015-08-26 14:08 | 2015-08-26 14:08 | PAYNE - PA13NR036H | 87 | 0 | Yes | Yes | 27.5 | 21.5 | 6 | 593FBEFFB2834790A2BF68D82663B602 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4635 |  | 2015-10-16 | 2015-10-16 09:14 | 2015-10-16 09:14 | RUUD - UAKA048JAZ | 103 | 0 | Yes | Yes | 23 | 18.8 | 4.2 | 1BBCB2F4B8404A4CBD94ACC7EDF4F963 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9003 |  | 2015-10-08 | 2015-10-08 01:15 | 2015-10-08 01:15 | CARRIER - 585HJ030040ABAF | 68 | 0 | Yes | Yes | 21.4 | 19.3 | 2.1 | 15032E073F924D94978664CE76ADD9F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-4129 |  | 2015-08-21 | 2015-08-21 10:08 | 2015-08-21 10:25 | CARRIER - 38HDL048 | 85 | 4 | Yes | Yes | 28.4 | 24 | 4.4 | D816B8418D9B4945A0E86B81B6F25393 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Suisun City | CA | 94585-1306 |  | 2015-09-26 | 2015-09-26 13:13 | 2015-09-26 13:13 | GOODMAN - CLJ18-1 | 85 | 0 | Yes | Yes | 19 | 19 | 0 | DE2339545FD64A0CA3504DA81151ECE4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1574 |  | 2015-08-28 | 2015-08-28 15:53 | 2015-08-28 15:53 | CARRIER - 38BRC036350 | 108 | 0 | Yes | Yes | 16 | 18.6 | -2.6 | 84D2D48C094F40AC88C7F8BE5D110EDC |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4929 |  | 2015-10-08 | 2015-10-08 14:27 | 2015-10-08 14:27 | AMERICAN STANDARD - 2YCX3030075 | 88 | 0 | Yes | Yes | 16 | 18.2 | -2.2 | 0CE6ADD754FA40699D80D8F031D70FE9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-1607 |  | 2015-08-26 | 2015-08-26 11:52 | 2015-08-26 11:52 | CARRIER - 48GSN036090311 | 68 | 0 | Yes | Yes | 23.4 | 20.1 | 3.3 | 8196EC0BA92D4A1E821597EA54A12D3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1843 |  | 2015-10-12 | 2015-10-12 11:22 | 2015-10-12 11:22 | CARRIER - 38CK048-301 | 85 | 0 | Yes | Yes | 24.5 | 18.5 | 6 | D859715819354D9DBA9500E3836E5D82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6445 |  | 2015-09-08 | 2015-09-08 11:53 | 2015-09-08 11:53 | LENNOX - 10ACB18-9P | 68 | 0 | Yes | Yes | 13.4 | 16.1 | -2.7 | F1C4CED5D9464C568D9B9DBB918C1ED1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6109 |  | 2015-09-01 | 2015-09-01 16:40 | 2015-09-01 16:40 | CARRIER - 24ABB336W0031010 | 87 | 0 | Yes | Yes | 22.6 | 19.2 | 3.4 | E50A4D2B6D304B3086F0B7BD17837EDB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-3355 |  | 2015-08-05 | 2015-08-05 13:34 | 2015-08-05 13:34 | TEMPSTAR - T2A318GKA100 | 85 | 0 | Yes | Yes | 17.7 | 18.7 | -1 | 9C2A5FA966FA4E4EB31A0DF5CE1A44FC |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7152 |  | 2015-08-26 | 2015-08-26 17:54 | 2015-08-26 18:13 | CARRIER - 24ABA318A310 | 85 | 8.1 | Yes | Yes | 15.9 | 17.7 | -1.8 | CC73F8529A6A4333A566C4D198010993 |  | R410A | TXV |  | 9.529% | 0.90471 | 18.31% | [5 empty] | TXV | 9.529%
Vacaville | CA | 95687-5621 |  | 2015-08-28 | 2015-08-28 13:23 | 2015-08-28 13:45 | DUCANE - 2AC13L24P-2B | 89 | 18.3 | Yes | Yes | 14.2 | 17.2 | -3 | DEF6F74850134B30BFD42E25CF2B4842 |  | R22 | Non-TXV |  | 20.56% | 0.79438 | 39.52% | [5 empty] | Non-TXV | 20.56%
Bay Point | CA | 94565-3419 |  | 2015-09-08 | 2015-09-08 13:43 | 2015-09-08 13:43 | TEMPSTAR - T2A330GKA100 | 83 | 0 | Yes | Yes | 26.1 | 21.5 | 4.6 | F6703453EF6D461695A7767B327B533D |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5407 |  | 2015-11-18 | 2015-11-18 14:45 | 2015-11-18 14:45 | YORK - CMA04811A | 116 | 0 | Yes | Yes | 21.2 | 20.4 | 0.8 | B41202BA3C3F4BDFB9A62F05D927871F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2411 |  | 2015-10-13 | 2015-10-13 13:37 | 2015-10-13 13:37 | OTHER - UNKNOWN | 83 | 0 | Yes | Yes | 20.8 | 23.2 | -2.4 | 5C1EDA1D60784AAE8AD0EE56466B207C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2030 |  | 2015-10-15 | 2015-10-15 16:46 | 2015-10-15 16:46 | CARRIER - 38TH036300 | 85 | 0 | Yes | Yes | 22.3 | 19.5 | 2.8 | EC6957AEE7E840D7B9183EBBF74C9785 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1414 |  | 2015-08-24 | 2015-08-24 12:34 | 2015-08-24 12:34 | CARRIER - 38TH042310 | 112 | 0 | Yes | Yes | 18.2 | 19.3 | -1.1 | D87EB8D962644560A9DD53808309AD8C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-3317 |  | 2015-09-03 | 2015-09-03 09:39 | 2015-09-03 09:39 | TRANE - TTP036C100A2 | 85 | 0 | Yes | Yes | 21.6 | 18.7 | 2.9 | 6DDA6F1FD0FF49CB83F05EC609A0A211 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-9783 |  | 2015-09-16 | 2015-09-16 12:17 | 2015-09-16 12:17 | DAY & NIGHT - 591AN042D | 87 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 5212ABE5F27A4DC7A5953F6CF6DCA8BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-0000 |  | 2015-09-01 | 2015-09-01 14:39 | 2015-09-01 14:39 | BRYANT - 582ANW030060AAAD | 59 | 0 | Yes | Yes | 18.2 | 20.7 | -2.5 | D6040337213542019D5C71A73D27FBB3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-5203 |  | 2015-10-15 | 2015-10-15 11:34 | 2015-10-15 11:34 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 17.8 | 19.3 | -1.5 | EB45EBA3B2B349C680F1F298B0A815EC |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1455 |  | 2015-09-01 | 2015-09-01 15:22 | 2015-09-01 15:22 | PAYNE - PA10JA036-A | 85 | 0 | Yes | Yes | 24.3 | 19.4 | 5 | 72726B0448B740CA9C2BED83BE6228D8 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1920 |  | 2015-09-30 | 2015-09-30 08:55 | 2015-09-30 09:30 | RHEEM - RRNL-B024JK06X | 77 | 12.5 | Yes | Yes | 23.9 | 20.4 | 3.5 | 1C4DDB8D7A0144CA927047DE3A2E0CBC |  | R410A | Non-TXV |  | 16.23% | 0.83766 | 31.2% | [5 empty] | Non-TXV | 16.23%
Pittsburg | CA | 94565-4246 |  | 2015-10-12 | 2015-10-12 13:41 | 2015-10-12 13:41 | OTHER - AC018M1021CG | 49 | 0 | Yes | Yes | 18.9 | 20.2 | -1.3 | 5D931420EC274493814013468ED002D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1784 |  | 2015-10-12 | 2015-10-12 11:17 | 2015-10-12 11:17 | AMERICAN STANDARD - CA5560VKD2 | 150 | 0 | Yes | Yes | 19.8 | 21.3 | -1.5 | 8D0C80B8451B4B888CED94FB1A1086D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2007 |  | 2015-10-06 | 2015-10-06 14:16 | 2015-10-06 14:16 | CARRIER - 38TXA042330 | 140 | 0 | Yes | Yes | 24.2 | 20.9 | 3.3 | A2FD60B394984779B4F317DE25F4AD6D |  | R410A | TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3234 |  | 2015-09-18 | 2015-09-18 13:59 | 2015-09-18 13:59 | OTHER - C24ABD1V | 85 | 0 | Yes | Yes | 17.3 | 20.1 | -2.8 | F1B59DA8DF8147C1A0EA1A1FD32996B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2694 |  | 2015-09-02 | 2015-09-02 13:09 | 2015-09-02 13:29 | TRANE - TTR025C1000A0 | 66 | 10.6 | Yes | Yes | 17.7 | 18.8 | -1.1 | E5517401EAB240EA98870AD3AADAA60C |  | R22 | Non-TXV |  | 16.06% | 0.83939 | 30.86% | [5 empty] | Non-TXV | 16.06%
Pittsburg | CA | 94565-3908 |  | 2015-10-15 | 2015-10-15 17:01 | 2015-10-15 17:01 | OTHER - UNKNOWN | 104 | 0 | Yes | Yes | 20.9 | 21.3 | -0.4 | 9D2C94B5677F4AA194D041E327AB63E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-2213 |  | 2015-09-03 | 2015-09-03 08:50 | 2015-09-03 08:50 | CARRIER - 38BRC048350 | 170 | 0 | Yes | Yes | 21 | 15.7 | 5.3 | ED85C60E14F6435CA5B66A03181601A8 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5418 |  | 2015-10-08 | 2015-10-08 22:54 | 2015-10-08 22:54 | GOODMAN - PGB0480751REVA | 86 | 0 | Yes | Yes | 19.2 | 18.5 | 0.7 | 4B9F1CFC56344E74933A5948524570D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4651 |  | 2015-08-27 | 2015-08-27 09:54 | 2015-08-27 09:54 | CARRIER - 116BNA024-A | 96 | 0 | Yes | Yes | 18.6 | 19.3 | -0.7 | FA4A1644B39B4FDEA5C6DA7882C3FDC9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-9696 |  | 2015-09-29 | 2015-09-29 11:13 | 2015-09-29 11:13 | RHEEM - T38B0 | 49 | 0 | Yes | Yes | 17.7 | 18.3 | -0.6 | 178CCCECC22941A680301BC8F8B4E3D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6446 |  | 2015-09-08 | 2015-09-08 14:07 | 2015-09-08 14:07 | LENNOX - 10ACB24 | 85 | 0 | Yes | Yes | 15.7 | 18.7 | -3 | C82EBFA1A82040C593C0FDF0E40F0C79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1788 |  | 2015-08-26 | 2015-08-26 16:44 | 2015-08-26 16:44 | CARRIER - 24ABB336W0031010 | 85 | 0 | Yes | Yes | 16.2 | 19 | -2.8 | 4B16235B96994C5DB332792A62517312 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-4161 |  | 2015-09-15 | 2015-09-15 11:16 | 2015-09-15 11:16 | CARRIER - 38BRC036350 | 108 | 0 | Yes | Yes | 19.5 | 19.3 | 0.2 | 2CF146073A2D4771939EE28F6EA514E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6449 |  | 2015-09-08 | 2015-09-08 12:46 | 2015-09-08 12:46 | PAYNE - PA13NR024 | 85 | 0 | Yes | Yes | 16.7 | 19.3 | -2.6 | 94B3C733C29441728FAC751688A63D00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2017 |  | 2015-08-21 | 2015-08-21 08:14 | 2015-08-21 08:14 | RHEEM - RAMA024JAZ | 85 | 0 | Yes | Yes | 17.5 | 18.2 | -0.7 | 1C2A360AEB6D4E58B1D21D01563B6D8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-5136 |  | 2015-10-13 | 2015-10-13 15:00 | 2015-10-13 15:00 | TEMPSTAR - PGD330060K001C1 | 98 | 0 | Yes | Yes | 20.5 | 23 | -2.5 | 3EB634F834054E089B775509D5275971 |  | R410A | TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94596-5308 |  | 2015-08-26 | 2015-08-26 10:50 | 2015-08-26 10:50 | ALLEGIANCE - 2A7A2048A1000AA | 120 | 0 | Yes | Yes | 21.6 | 19.7 | 2 | 015801C20EED489F8ACD3671873D26C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4746 |  | 2015-08-27 | 2015-08-27 10:20 | 2015-08-27 10:20 | YORK - H4DH036S06A | 95 | 0 | Yes | Yes | 22 | 24.8 | -2.8 | EAA8B8F43FF6434A904EC6DC87D197AF | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4606 |  | 2015-10-22 | 2015-10-22 14:40 | 2015-10-22 14:40 | YORK - H20A036506A | 93 | 0 | Yes | Yes | 22.9 | 23.7 | -0.8 | 86BD2B95FA4C48679E939CA46F0C8D7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5232 |  | 2015-10-22 | 2015-10-22 10:16 | 2015-10-22 10:16 | LENNOX - 13ACX-030-230-17 | 82 | 0 | Yes | Yes | 20.6 | 21.2 | -0.6 | 47F144FA378342D2A0C63BAE3BDB649A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8020 |  | 2015-09-10 | 2015-09-10 09:19 | 2015-09-10 09:19 | GOODMAN - CM251E | 55 | 0 | Yes | Yes | 19.4 | 21.5 | -2.1 | D8D1803267DD4918B10B1338EAC6147A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2255 |  | 2015-10-12 | 2015-10-12 12:04 | 2015-10-12 12:24 | PAYNE - PA10JAO36 | 85 | 6.1 | Yes | Yes | 22.3 | 18.8 | 3.5 | 1B7D98244A3E417A9BFB5FA1CAB84AA4 |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Bay Point | CA | 94565-3341 |  | 2015-09-08 | 2015-09-08 12:57 | 2015-09-08 13:17 | TRANE - 2TTR2042B1000AA | 86 | 5 | Yes | Yes | 20.8 | 22.6 | -1.8 | ED3A57D7605F48AFA8968A1760DA5153 |  | R22 | TXV |  | 5.814% | 0.94186 | 11.17% | [5 empty] | TXV | 5.814%
Bay Point | CA | 94565-2924 |  | 2015-09-11 | 2015-09-11 14:20 | 2015-09-11 14:20 | CARRIER - 563CN048-H | 136 | 0 | Yes | Yes | 23.4 | 21.5 | 2 | 02E4D20EBE434F0F8EAF371E0C5191A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2161 |  | 2015-08-27 | 2015-08-27 13:28 | 2015-08-27 13:28 | DAY & NIGHT - 5638036RC | 85 | 0 | Yes | Yes | 16.3 | 16.8 | -0.5 | 0EA8B658667847E0A5EB617DA49D1266 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1139 |  | 2015-08-25 | 2015-08-25 11:55 | 2015-08-25 11:55 | BRYANT - 113RNA042C | 105 | 0 | Yes | Yes | 19.9 | 18.2 | 1.7 | 6D0F5A58BD704779A22DA4F58C76FECF |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95139-1520 |  | 2015-10-22 | 2015-10-22 13:36 | 2015-10-22 13:36 | BRYANT - 561CJ024-C | 69 | 0 | Yes | Yes | 23.5 | 21.4 | 2.1 | E05452D90CAD49B4A5F7B6A7FB29EB18 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1364 |  | 2015-08-28 | 2015-08-28 10:22 | 2015-08-28 10:22 | TRANE - 2TTR2036A1000AA | 96 | 0 | Yes | Yes | 20.6 | 18.8 | 1.8 | D102FD377A9640F1B874EC9BCDD30416 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6619 |  | 2015-09-08 | 2015-09-08 10:09 | 2015-09-08 10:09 | RHEEM - UNK | 85 | 0 | Yes | Yes | 22.5 | 19.3 | 3.2 | 2C67A0EAA5894AB3A5481BD9F80A0322 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Ramon | CA | 94583-2901 |  | 2015-10-14 | 2015-10-14 14:08 | 2015-10-14 14:08 | OTHER - TCA242AKA1 | 125 | 0 | Yes | Yes | 25.5 | 20.8 | 4.8 | 584BCC23E6E44ED3B464441874C45ACF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8380 |  | 2015-10-20 | 2015-10-20 14:16 | 2015-10-20 14:34 | BDP - 561AJ042-A | 85 | 18 | Yes | Yes | 18.3 | 21.2 | -2.9 | B3D489EC8B384AA3A3F0C41C508EAEF9 |  | R22 | TXV |  | 21.18% | 0.78824 | 40.7% | [5 empty] | TXV | 21.18%
Fairfield | CA | 94533-4402 |  | 2015-08-27 | 2015-08-27 14:54 | 2015-08-27 14:54 | CARRIER - 48GX036090301AD | 82 | 0 | Yes | Yes | 18.2 | 20.4 | -2.2 | 6D0EF01E01324252A98C02809A49F8B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94596-4261 |  | 2015-08-25 | 2015-08-25 14:06 | 2015-08-25 14:26 | DAY & NIGHT - 561AJ036-D | 70 | 6.2 | Yes | Yes | 22.7 | 21.5 | 1.2 | 1FCAD1B0A41A4855A43B82B40B8E9D57 |  | R22 | Non-TXV |  | 8.857% | 0.91143 | 17.02% | [5 empty] | Non-TXV | 8.857%
Martinez | CA | 94553-4338 |  | 2015-09-24 | 2015-09-24 13:24 | 2015-09-24 13:24 | BRYANT - 113ANA030-E | 85 | 0 | Yes | Yes | 15 | 17.8 | -2.8 | 63976124CC7E41819DC467E324FBD1CF |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-1037 |  | 2015-08-21 | 2015-08-21 08:25 | 2015-08-21 08:25 | MONTGOMERY WARD - ? | 85 | 0 | Yes | Yes | 24.7 | 21.4 | 3.3 | 10ED83DF621E4D7CB1BFB6A7E6B89CCA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6513 |  | 2015-08-25 | 2015-08-25 09:37 | 2015-08-25 09:37 | YORK - H4DH048S06A | 138 | 0 | Yes | Yes | 24.5 | 23.5 | 1.1 | 9F0BE1F84DCC4846B3983CB87D6D6614 | Actual Superheat must be between 0°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1200 |  | 2015-09-30 | 2015-09-30 11:40 | 2015-09-30 12:08 | AIRE-FLO - N/A | 85 | 16.1 | Yes | Yes | 21.5 | 22.1 | -0.6 | B56711D687D64B36844161C62D7182F7 |  | R22 | Non-TXV |  | 18.94% | 0.81059 | 36.4% | [5 empty] | Non-TXV | 18.94%
Bakersfield | CA | 93307-4612 |  | 2015-09-22 | 2015-09-22 13:09 | 2015-09-22 13:09 | GOODMAN - SSX160481AB | 244 | 0 | Yes | Yes | 22.2 | 22 | 0.2 | E566D9302B2C4A26AF602B5C9F172991 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2667 |  | 2015-09-23 | 2015-09-23 14:57 | 2015-09-23 14:57 | CARRIER - PA12NR030-H | 75 | 0 | Yes | Yes | 19.6 | 18.7 | 0.9 | EA877E6F9A774492B96478B59E8851A6 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5027 |  | 2015-10-08 | 2015-10-08 14:21 | 2015-10-08 14:21 | PAYNE - PA10JA36A | 84 | 0 | Yes | Yes | 20 | 20.4 | -0.4 | 4C71B3B90D8A41208D7FC846007BB094 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4856 |  | 2015-09-11 | 2015-09-11 10:07 | 2015-09-11 10:07 | DAY & NIGHT - N4A336AKB200 | 83 | -9.8 | Yes | Yes | 15.6 | 22.8 | -7.2 | 95A0F965627C40E38461166FCD148A13 | Remove refrigerant: 9.8 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | TXV |  | -11.81% | 1.1181 | 3.307% |  |  |  |  | TXV |  |  | -11.81%
Napa | CA | 94558-2371 |  | 2015-09-23 | 2015-09-23 11:15 | 2015-09-23 11:15 | BRYANT - 561CJ060-A | 85 | 0 | Yes | Yes | 16.9 | 19 | -2.1 | EBEA8533C94F42F79B850DF26539C67C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4722 |  | 2015-09-03 | 2015-09-03 13:08 | 2015-09-03 13:08 | PAYNE - 561CJ030A | 75 | 0 | Yes | Yes | 20.4 | 18.7 | 1.7 | C9D91798732346E5A41CDACD0A992021 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7789 |  | 2015-09-19 | 2015-09-19 12:43 | 2015-09-19 12:43 | GOODMAN - CK48-18 | 97 | 0 | Yes | Yes | 19.9 | 17.7 | 2.2 | C14D7B71B33744FABE779941269DF5EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5549 |  | 2015-09-30 | 2015-09-30 10:06 | 2015-09-30 10:06 | GOODMAN - GPG13420701AB | 107 | 0 | Yes | Yes | 21.4 | 22.5 | -1.1 | CFDE67DA75E1460EAF1EF3639D7531EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-3777 |  | 2015-10-28 | 2015-10-28 16:11 | 2015-10-28 16:32 | RUUD - UAKA-024JAZ | 50 | 4 | Yes | Yes | 19 | 19.1 | -0.1 | CEAC4930A7A340B59CBAE72BB1A6B4EB |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Bakersfield | CA | 93309-1248 |  | 2015-09-11 | 2015-09-11 12:53 | 2015-09-11 12:53 | ICP - PGC024KO40D | 58 | 0 | Yes | Yes | 20.6 | 22.1 | -1.5 | DBA9E625BBA24E79A06470366A9D2AD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-6665 |  | 2015-08-20 | 2015-08-20 15:41 | 2015-08-20 16:01 | OTHER - CA303VKA1 | 82 | 8 | Yes | Yes | 17.5 | 17 | 0.5 | 427F0A1BBE13474D9C480FF2B3446B56 |  | R22 | Non-TXV |  | 9.756% | 0.90244 | 18.75% | [5 empty] | Non-TXV | 9.756%
Sanger | CA | 93657-4240 |  | 2015-11-10 | 2015-11-10 12:47 | 2015-11-10 12:47 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 21.6 | 17.7 | 3.9 | 92BEBD46BDD04E1B9F6E528DD25D7CDD |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6222 |  | 2015-10-03 | 2015-10-03 10:13 | 2015-10-03 10:13 | BRYANT - 563CN030B | 100 | 0 | Yes | Yes | 18.8 | 21.4 | -2.6 | 715AFF8A70B940BB8F3D569036FC5B58 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3950 |  | 2015-09-25 | 2015-09-25 10:49 | 2015-09-25 10:49 | GOODMAN - GSC130181FA | 75 | 0 | Yes | Yes | 20.4 | 21.1 | -0.7 | F3E6AC08E57D4E16A15FEFEC27AFA42A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6032 |  | 2015-09-03 | 2015-09-03 13:54 | 2015-09-03 13:54 | CARRIER - 38BRC036320 | 104 | 0 | Yes | Yes | 26.3 | 21.5 | 4.8 | 7C5C874C09924985BFB1DA96DB74807E |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4816 |  | 2015-09-02 | 2015-09-02 15:30 | 2015-09-02 15:30 | TRANE - 4TTX6048A1000AA | 120 | 0 | Yes | Yes | 22.4 | 19.2 | 3.2 | 222B47374E58444BB9ABE809851184B3 |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7789 |  | 2015-09-15 | 2015-09-15 10:03 | 2015-09-15 10:03 | GOODMAN - CK601C | 85 | 0 | Yes | Yes | 19.4 | 19.4 | 0 | ED58341CA8634CBF95F458C67DD38A22 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4265 |  | 2015-08-28 | 2015-08-28 17:45 | 2015-08-28 17:45 | PAYNE - 591ANX018000AAAA | 48 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | 5045F779FD934AD5A55EB305837C4E4C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94595-1708 |  | 2015-08-25 | 2015-08-25 09:44 | 2015-08-25 09:44 | YORK - H2RA060S06A | 118 | 0 | Yes | Yes | 18.8 | 17.7 | 1.1 | 6DEE296484C64D5DBFE002AA028680D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1911 |  | 2015-08-25 | 2015-08-25 12:14 | 2015-08-25 12:36 | LENNOX - H394113P | 84 | 18.5 | Yes | Yes | 19.3 | 18.7 | 0.6 | 06BA07F52626403F994EE94F0AEFB1A8 |  | R22 | Non-TXV |  | 22.02% | 0.77976 | 42.32% | [5 empty] | Non-TXV | 22.02%
Pittsburg | CA | 94565-4715 |  | 2015-09-21 | 2015-09-21 14:58 | 2015-09-21 14:58 | PAYNE - PA13NR036-C | 85 | 0 | Yes | Yes | 20.5 | 19.6 | 0.9 | 584C32D270564A25B88566980E43D819 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8134 |  | 2015-09-18 | 2015-09-18 12:11 | 2015-09-18 12:11 | YORK - H2RA036S063 | 63 | 0 | Yes | Yes | 17.3 | 18.2 | -0.9 | BF01928F6EC84E89B890E012D4263B04 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-2930 |  | 2015-08-26 | 2015-08-26 13:49 | 2015-08-26 13:49 | GOODMAN - GSX130361BA | 319 | 0 | Yes | Yes | 21.4 | 19 | 2.4 | 508922E41FB1401CAA9AEDD13F63442C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2834 |  | 2015-10-06 | 2015-10-06 10:28 | 2015-10-06 10:28 | PAYNE - PA10JA060-A | 126 | 0 | Yes | Yes | 17.6 | 17.7 | -0.1 | C9083283E4D54A3C9F4F97EC2D9C39DC |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6037 |  | 2015-10-05 | 2015-10-05 10:02 | 2015-10-05 10:02 | OTHER - N4A348AKB200 | 112 | 0 | Yes | Yes | 17.9 | 20.7 | -2.8 | 55F6DD30F7B543F7BDDB1619825B2179 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-1515 |  | 2015-08-21 | 2015-08-21 09:46 | 2015-08-21 10:02 | ALLEGIANCE - 7A0036A100A1 | 86 | 3.7 | Yes | Yes | 24.1 | 20.9 | 3.2 | 4F706CC03A04461396EECD502EE9C6F5 |  | R22 | Non-TXV |  | 4.302% | 0.95698 | 8.268% | [5 empty] | Non-TXV | 4.302%
Fairfield | CA | 94533-4627 |  | 2015-09-23 | 2015-09-23 11:07 | 2015-09-23 11:07 | RHEEM - 13AJN2401 | 67 | 0 | Yes | Yes | 16.2 | 17.6 | -1.4 | 729A4E18742E40E887BAD00C243275BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6927 |  | 2015-08-31 | 2015-08-31 13:52 | 2015-08-31 13:52 | PAYNE - UNK | 85 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | AA8853F93EE745BDB670C0A9D32C2AB4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-6714 |  | 2015-09-16 | 2015-09-16 14:22 | 2015-09-16 14:22 | GOODMAN - GSC140601AC | 285 | 0 | Yes | Yes | 23.5 | 21.5 | 2 | 5D3C5A480D304D2C9F3E1C52C81C3B11 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5482 |  | 2015-10-05 | 2015-10-05 09:29 | 2015-10-05 09:29 | OTHER - 9541A801 | 50 | 0 | Yes | Yes | 19.5 | 20 | -0.5 | 86AECAC27FB34F76B585D95489973134 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-1629 |  | 2015-11-09 | 2015-11-09 10:02 | 2015-11-09 10:02 | OTHER - 3680YAAG708 | 74 | 0 | Yes | Yes | 23.3 | 19.9 | 3.4 | F10A8355143647ED9979AF5567EB0168 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4031 |  | 2015-09-12 | 2015-09-12 10:24 | 2015-09-12 10:47 | PAYNE - PA13NAD042000ABAA | 103 | 5.1 | Yes | Yes | 20.5 | 19.4 | 1.1 | 90951D71BD1A404AAAB4930DD4F4360D | Add refrigerant: 7.4 oz | R410A | TXV |  | 4.951% | 0.95049 | 9.516% | [5 empty] | TXV | 4.951%
Fresno | CA | 93702-2617 |  | 2015-10-12 | 2015-10-12 16:24 | 2015-10-12 16:41 | TRANE - 2TTR2048A1000AA | 120 | 6.6 | Yes | Yes | 18.2 | 18.5 | -0.3 | 4C4F6448F9294F348944FBE91B25A495 |  | R22 | Non-TXV |  | 5.5% | 0.945 | 10.57% | [5 empty] | Non-TXV | 5.5%
Bakersfield | CA | 93309-7602 |  | 2015-10-06 | 2015-10-06 16:09 | 2015-10-06 16:09 | PAYNE - PY3GNAA36060NA | 102 | 0 | Yes | Yes | 22 | 23.1 | -1.1 | 3A4BC0FD6EF44F6A8B821A03E587C329 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-4611 |  | 2015-08-20 | 2015-08-20 13:50 | 2015-08-20 13:50 | BRYANT - 550ANO36-E | 104 | 0 | Yes | Yes | 17.9 | 18.8 | -0.9 | 4958C5C8EEAE4592890AF678725219AD |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-1335 |  | 2015-08-20 | 2015-08-20 11:05 | 2015-08-20 11:05 | ICP - CA7030VKA2867.803151 | 130 | 0 | Yes | Yes | 25.6 | 22.9 | 2.7 | BD711F2608474769953E40D3C56F11AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-3615 |  | 2015-10-02 | 2015-10-02 14:10 | 2015-10-02 14:10 | CARRIER - 38HDL036-311 | 88 | 0 | Yes | Yes | 25.5 | 20.8 | 4.7 | F73FF854CEDE4BDF9AD5CF1E4D0513D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4501 |  | 2015-08-27 | 2015-08-27 11:16 | 2015-08-27 11:16 | TRANE - TTB036C100A1 | 90 | 0 | Yes | Yes | 20.2 | 22.1 | -1.9 | 22B2D890BA60431DADF983106B0B9EBC |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-3635 |  | 2015-10-02 | 2015-10-02 10:09 | 2015-10-02 10:09 | GOODMAN - GSX130301DB | 76 | 0 | Yes | Yes | 26.1 | 21.8 | 4.4 | 3EE4428AB37E4BD39513738A1CD386E8 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2115 |  | 2015-08-31 | 2015-08-31 13:44 | 2015-08-31 13:44 | RHEEM - 13AJA48A01757 | 121 | 0 | Yes | Yes | 18.6 | 19.7 | -1.1 | A9837068BF164503A51AC447088E8940 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6306 |  | 2015-10-01 | 2015-10-01 15:32 | 2015-10-01 15:32 | GOODMAN - CH421CB | 107 | 0 | Yes | Yes | 25.9 | 21 | 4.9 | 438B088BB4C046799BA434BF3EC56C5B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6719 |  | 2015-10-16 | 2015-10-16 12:10 | 2015-10-16 12:10 | TRANE - TTD73A100A0 | 100 | 0 | Yes | Yes | 21.1 | 22 | -0.9 | AB0BB4B3A4CE404E929D7B0D014AE4D5 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7459 |  | 2015-08-24 | 2015-08-24 13:22 | 2015-08-24 13:22 | CARRIER - 38BRC030-311 | 85 | 0 | Yes | Yes | 19.3 | 18.8 | 0.5 | 87234EE03DEA45D4A7F6F986B1D84B20 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7459 |  | 2015-08-24 | 2015-08-24 13:32 | 2015-08-24 13:32 | CARRIER - 38BRC030-310 | 85 | 0 | Yes | Yes | 23.4 | 19.5 | 3.9 | E783608518CC4301A2FF24263D952035 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6810 |  | 2015-08-26 | 2015-08-26 15:00 | 2015-08-26 15:00 | CARRIER - 38CK030300 | 67 | 0 | Yes | Yes | 17.6 | 20.4 | -2.8 | 5F7FB297C69B45A8BDE8B1BECB78A30D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-9501 |  | 2015-10-30 | 2015-10-30 12:33 | 2015-10-30 12:33 | PAYNE - PA12NA042B | 100 | 0 | Yes | Yes | 25.6 | 20.4 | 5.2 | 3BFE31E9143A4B78854158B1488DFF0B |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2609 |  | 2015-09-08 | 2015-09-08 09:47 | 2015-09-08 10:12 | CARRIER - 561CJO36-F | 70 | 10.1 | Yes | Yes | 23.4 | 21.4 | 2 | DC89AC4BCAA14B32A55E13B8A87EA161 |  | R22 | Non-TXV |  | 14.43% | 0.85571 | 27.73% | [5 empty] | Non-TXV | 14.43%
Dixon | CA | 95620-3044 |  | 2015-10-06 | 2015-10-06 15:28 | 2015-10-06 15:28 | YORK - H1DE036S06B | 84 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 0E1B7FA4701B4A1BB91BA2CEA2C4603B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4611 |  | 2015-08-25 | 2015-08-25 08:59 | 2015-08-25 08:59 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 19.5 | 19.1 | 0.4 | CBE8E6474C644509A3540E6403B3F1B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4336 |  | 2015-08-24 | 2015-08-24 09:55 | 2015-08-24 10:04 | GOODMAN - GPG1360090M41DA | 91 | 17.4 | Yes | Yes | 27.1 | 21.3 | 5.8 | 0B872B7F2CFF4E21A73CE15BC2AD0A5F |  | R410A | Non-TXV |  | 19.12% | 0.80879 | 36.75% | [5 empty] | Non-TXV | 19.12%
Pittsburg | CA | 94565-3541 |  | 2015-09-08 | 2015-09-08 13:42 | 2015-09-08 13:42 | RHEEM - RAKB-036JAZ | 79 | 0 | Yes | Yes | 18.4 | 19.9 | -1.5 | 6E66305B351F466F95E41E2E434DD243 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-6141 |  | 2015-08-31 | 2015-08-31 13:02 | 2015-08-31 13:02 | OTHER - AC048X1021A | 117 | 0 | Yes | Yes | 20.1 | 21.4 | -1.3 | 5F2B2D7B96B04F66983091E8F1EF7350 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1885 |  | 2015-09-01 | 2015-09-01 15:57 | 2015-09-01 16:19 | BRYANT - 563CN048-H | 136 | 11.5 | Yes | Yes | 19.3 | 19.3 | 0 | 3770E39B862A4409848C6A1A0F8CD87C |  | R22 | TXV |  | 8.456% | 0.91544 | 16.25% | [5 empty] | TXV | 8.456%
Martinez | CA | 94553-6029 |  | 2015-09-10 | 2015-09-10 15:39 | 2015-09-10 15:39 | RHEEM - RACA-042AAS | 52 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 382D2A6D53E84D48A7F21D9F022A1ABF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5009 |  | 2015-09-23 | 2015-09-23 12:53 | 2015-09-23 12:53 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 24.3 | 21 | 3.3 | 2C9E847811BB455F8D774F4AA3135CAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4471 |  | 2015-08-26 | 2015-08-26 09:23 | 2015-08-26 09:23 | OTHER - EADB-048JAS | 113 | 0 | Yes | Yes | 23 | 22.6 | 0.4 | CE2CD333A17A4BE9B8A991DCD0F001E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-5717 |  | 2015-08-28 | 2015-08-28 14:40 | 2015-08-28 14:40 | BRYANT - 561J036 | 85 | 0 | Yes | Yes | 16.7 | 19.7 | -3 | 938730CFDA834D50B2BE64652D96368C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Friant | CA | 93626-0000 |  | 2015-11-11 | 2015-11-11 10:22 | 2015-11-11 10:45 | GOODMAN - 8736-801 | 118 | 9.2 | Yes | Yes | 19.9 | 18.7 | 1.2 | 9670B605516B4D38B6F1FA87D5515557 |  | R22 | Non-TXV |  | 7.797% | 0.92203 | 14.98% | [5 empty] | Non-TXV | 7.797%
Martinez | CA | 94553-1411 |  | 2015-09-04 | 2015-09-04 12:10 | 2015-09-04 12:10 | TRANE - YCX024F1M0BA | 67 | 0 | Yes | Yes | 20.9 | 18.2 | 2.7 | B74F20125895445EBD541D24A73C0D7C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-9379 |  | 2015-10-30 | 2015-10-30 11:35 | 2015-10-30 11:35 | CARRIER - 24ABB342W300 | 88 | 0 | Yes | Yes | 19.9 | 22.2 | -2.3 | 78E3483E53A44C44A52090D2E4FD58EA |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7234 |  | 2015-11-11 | 2015-11-11 14:49 | 2015-11-11 14:49 | RHEEM - UNK | 65 | 0 | Yes | Yes | 18.3 | 18.7 | -0.4 | F6E24C24556E44FEA5E8449CA0C1D6C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3619 |  | 2015-09-10 | 2015-09-10 14:58 | 2015-09-10 14:58 | TRANE - TTB036C100A1 | 90 | 0 | Yes | Yes | 19.6 | 22.4 | -2.8 | 673256A638BD4AD88CEAA4D831F6D39E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8390 |  | 2015-08-24 | 2015-08-24 15:27 | 2015-08-24 15:27 | - H2RA030S06D | 85 | 0 | Yes | Yes | 14.5 | 15.4 | -0.9 | 019DBD9642994E7E8DB87282D1128472 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2315 |  | 2015-10-26 | 2015-10-26 09:58 | 2015-10-26 09:58 | CARRIER - 38BR036300 | 122 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | E4DADCACB8CC4992AEF225DF5D00D335 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-2430 |  | 2015-10-02 | 2015-10-02 14:35 | 2015-10-02 14:35 | GOODMAN - GSC130361DF | 120 | 0 | Yes | Yes | 19.1 | 19.6 | -0.5 | 173FF2825BB04A2D9173FDF1F2C2BE98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-2690 |  | 2015-10-20 | 2015-10-20 12:11 | 2015-10-20 12:11 | OTHER - UNK | 136 | 0 | Yes | Yes | 21.1 | 24.1 | -3 | 0DD1D5672933408391A532F1D5DD2C00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5594 |  | 2015-08-31 | 2015-08-31 12:40 | 2015-08-31 12:40 | GOODMAN - CK42-18 | 86 | 0 | Yes | Yes | 22.1 | 22.4 | -0.3 | 23CFB5ED48C54034A7A3EFE9A58CDB50 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4468 |  | 2015-09-11 | 2015-09-11 10:21 | 2015-09-11 10:54 | GOODMAN - GPG1324045M4AB | 80 | 29.2 | Yes | Yes | 17.5 | 18.8 | -1.3 | 7543964594D94D9E96F3CAADD6536511 |  | R410A | Non-TXV |  | 36.5% | 0.635 | 70.14% | [5 empty] | Non-TXV | 36.5%
Bakersfield | CA | 93313-2415 |  | 2015-08-28 | 2015-08-28 11:13 | 2015-08-28 11:13 | ICP - PGD360090K001C1 | 85 | 0 | Yes | Yes | 21.6 | 22.6 | -1 | C533F48F77764279A069CDD41AEA88FD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2800 |  | 2015-09-24 | 2015-09-24 13:15 | 2015-09-24 13:15 | RHEEM - UNK | 69 | 0 | Yes | Yes | 21.3 | 22 | -0.7 | 81A0D6A4DF0748378A03E4D52DFA656F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7058 |  | 2015-09-30 | 2015-09-30 10:30 | 2015-09-30 11:07 | PAYNE - PA12NA036-H | 100 | 9.7 | Yes | Yes | 24.3 | 21 | 3.3 | 61FA3CA773984C7BAC59A9BF63DD941A |  | R22 | Non-TXV |  | 9.7% | 0.903 | 18.64% | [5 empty] | Non-TXV | 9.7%
Fairfield | CA | 94533-1815 |  | 2015-08-21 | 2015-08-21 10:12 | 2015-08-21 10:12 | GOODMAN - CKL491L | 112 | 0 | Yes | Yes | 22.7 | 20.1 | 2.6 | 6DD88688092047F7BABD5099A285ECE5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4007 |  | 2015-09-03 | 2015-09-03 11:02 | 2015-09-03 11:02 | CARRIER - 38BR036300 | 113 | 0 | Yes | Yes | 22.9 | 20.4 | 2.5 | 057EF589B99745EC9CE48DC42D3B1BF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-2810 |  | 2015-08-20 | 2015-08-20 10:47 | 2015-08-20 10:47 | TRANE - 4YCZ6048A1096AA | 136 | 0 | Yes | Yes | 22.3 | 18.9 | 3.4 | 6AC39889379D47AF9F06E30768D83CA9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Selma | CA | 93662-4103 |  | 2015-10-26 | 2015-10-26 10:52 | 2015-10-26 10:52 | RHEEM - RRNAB048JK10X | 153 | 0 | Yes | Yes | 23.6 | 20.4 | 3.2 | CF5DC484C8654E808CB422E98BA964F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1619 |  | 2015-08-21 | 2015-08-21 14:21 | 2015-08-21 14:21 | LENNOX - HS293111P | 69 | 0 | Yes | Yes | 21.3 | 19.5 | 1.8 | 66F51EB53D844C88BD2A6F09915678D4 |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-4114 |  | 2015-10-05 | 2015-10-05 12:26 | 2015-10-05 12:26 | CARRIER - 38CKC036350 | 74 | 0 | Yes | Yes | 21.2 | 19.4 | 1.8 | A0CA4381B0AC43969BCE9A905D21D57A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-1743 |  | 2015-09-10 | 2015-09-10 17:21 | 2015-09-10 17:21 | CARRIER - 38CKC060300 | 85 | 0 | Yes | Yes | 17.8 | 20.2 | -2.4 | 7039F558A7184F2BBC1E3A34DBAAAF3C |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5936 |  | 2015-10-22 | 2015-10-22 12:15 | 2015-10-22 12:15 | TRANE - 4TTM3042A1000AA | 89 | 0 | Yes | Yes | 17.7 | 20.6 | -2.9 | B5B07D35312E45DF9F69C8A0EF980F5A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8401 |  | 2015-09-11 | 2015-09-11 09:44 | 2015-09-11 09:44 | RHEEM - RRMA-A036JK06E | 99 | 0 | Yes | Yes | 21.4 | 22.4 | -1 | 51DD5FA9B5ED4F569CDA172DD9A72A17 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-3934 |  | 2015-10-15 | 2015-10-15 11:41 | 2015-10-15 11:59 | UNITARY PRODUCTS GROUP - H2RD048S06A | 134 | 6.9 | Yes | Yes | 19 | 19.3 | -0.3 | 30EA959782D14D8DA7C0DF92D1DDA8B1 |  | R22 | Non-TXV |  | 5.149% | 0.94851 | 9.896% | [5 empty] | Non-TXV | 5.149%
Fairfield | CA | 94533-7340 |  | 2015-09-19 | 2015-09-19 16:25 | 2015-09-19 16:25 | GOODMAN - CPKE18-1B | 79 | 0 | Yes | Yes | 17.2 | 18.8 | -1.6 | 1B6E7527F2D54B599CFA2ABFDB949ED3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93312-5919 |  | 2015-08-31 | 2015-08-31 13:24 | 2015-08-31 13:24 | OTHER - AC042X1221A | 107 | 0 | Yes | Yes | 19.5 | 21.8 | -2.3 | E8489EA3F35949BB92C87558E6BD0E1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-2318 |  | 2015-10-19 | 2015-10-19 14:34 | 2015-10-19 14:34 | OTHER - WCA3482GKR2 | 136 | 0 | Yes | Yes | 25.7 | 22.6 | 3.1 | 7F39B7AD32754672A980C1FA83B8427E |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1918 |  | 2015-10-08 | 2015-10-08 12:55 | 2015-10-08 12:55 | GOODMAN - GPG104201A | 88 | 0 | Yes | Yes | 19.2 | 17.9 | 1.3 | A6BEEF94AEF04E95B36E49B68A0B80BA |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-1752 |  | 2015-10-08 | 2015-10-08 11:53 | 2015-10-08 11:53 | BRYANT - 561CJ042-B | 81 | 0 | Yes | Yes | 26.4 | 21.4 | 5 | AB5356CD147D43789A5490C0DDFE293D |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5157 |  | 2015-11-09 | 2015-11-09 10:24 | 2015-11-09 10:24 | CARRIER - 48KLA13030DBE | 68 | 0 | Yes | Yes | 20 | 19.4 | 0.7 | 34DC853BAA5A4901890EEF1FC92EEDFB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1957 |  | 2015-09-09 | 2015-09-09 09:32 | 2015-09-09 09:57 | ICP - GPFM36K060E | 70 | 11.5 | Yes | Yes | 23.9 | 24.2 | -0.3 | 9458EB2DA8A44DB6B149515D18C90225 |  | R22 | Non-TXV |  | 16.43% | 0.83571 | 31.57% | [5 empty] | Non-TXV | 16.43%
Bakersfield | CA | 93304-6224 |  | 2015-09-29 | 2015-09-29 14:55 | 2015-09-29 15:29 | OTHER - N/A | 85 | 15.3 | Yes | Yes | 20.8 | 21.9 | -1.1 | EEB8124A667B4ED3895447B4ABB68C7D |  | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Fresno | CA | 93722-5330 |  | 2015-11-05 | 2015-11-05 10:13 | 2015-11-05 10:13 | OTHER - WPG3364060LKC1 | 100 | 0 | Yes | Yes | 26.6 | 21.3 | 5.3 | 7C44F3DDDFF640E0921923075E0844D7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1491 |  | 2015-09-01 | 2015-09-01 13:47 | 2015-09-01 13:47 | - CA9036VKA1 | 140 | 0 | Yes | Yes | 14.3 | 17.3 | -3 | 5251B0AC53A44D29989136A4DDBCBD8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-7365 |  | 2015-08-24 | 2015-08-24 12:04 | 2015-08-24 12:04 | TRANE - 4TTX4036B1000AA | 91 | 0 | Yes | Yes | 13 | 15.7 | -2.7 | 50934F4EE0654D36B73981D7E03C1ADD | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7040 |  | 2015-09-30 | 2015-09-30 13:07 | 2015-09-30 13:07 | GOODMAN - GPG13420701AB | 107 | 0 | Yes | Yes | 20.8 | 22.4 | -1.6 | F2988F4C3AD845E68BD987A8083532C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-5726 |  | 2015-10-09 | 2015-10-09 10:43 | 2015-10-09 10:43 | BRYANT - 561CJ048-G | 100 | 0 | Yes | Yes | 20.5 | 19.3 | 1.2 | DC90B11669C3414EAC19F408167B5727 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2510 |  | 2015-09-30 | 2015-09-30 09:23 | 2015-09-30 09:23 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 20.8 | 21 | -0.2 | 33BE6AA0A7D6402BA4D1A348D09809FA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1782 |  | 2015-09-14 | 2015-09-14 09:40 | 2015-09-14 09:40 | ALLEGIANCE - 2A7A1036A1000AA | 73 | 0 | Yes | Yes | 15.6 | 15.4 | 0.3 | FDC1BEE7B15B4443BB801D8F14946036 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2517 |  | 2015-10-14 | 2015-10-14 09:40 | 2015-10-14 09:40 | PAYNE - PA13NR048-H | 142 | 0 | Yes | Yes | 24.2 | 19.4 | 4.8 | A5A34AF9B1FF451582C23DCE2C20D3A5 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5737 |  | 2015-09-01 | 2015-09-01 14:05 | 2015-09-01 14:39 | YORK - H2RC048S06HG | 119 | 4.4 | Yes | Yes | 19.9 | 22 | -2.1 | 12D3CD691D1F42858188DAD30AAAF49E |  | R22 | Non-TXV |  | 3.697% | 0.96303 | 7.106% | [5 empty] | Non-TXV | 3.697%
Walnut Creek | CA | 94598-1607 |  | 2015-09-03 | 2015-09-03 13:45 | 2015-09-03 13:45 | CARRIER - 48GS-036099311 | 68 | 0 | Yes | Yes | 20.9 | 19.9 | 1 | A6DB184EE4484267BB48DDE92B38A84B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6349 |  | 2015-09-03 | 2015-09-03 16:43 | 2015-09-03 17:03 | CARRIER - 38CKC042340 | 80 | 11.6 | Yes | Yes | 22 | 21.5 | 0.5 | AFA1D11F13CA47EE91A9B342B89BF2EB |  | R22 | TXV |  | 14.5% | 0.855 | 27.87% | [5 empty] | TXV | 14.5%
Bakersfield | CA | 93306-4341 |  | 2015-08-24 | 2015-08-24 08:33 | 2015-08-24 08:33 | ICP - PGME36G0907 | 102 | 0 | Yes | Yes | 20.7 | 22.4 | -1.7 | 89569F2B36724D4E847C896FC38429F1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7913 |  | 2015-08-24 | 2015-08-24 08:59 | 2015-08-24 09:25 | DUCANE - AC12B42 | 94 | 12.3 | Yes | Yes | 21.4 | 24.2 | -2.8 | BC45CC24326A421FB55A3D309E1A7E22 |  | R22 | Non-TXV |  | 13.09% | 0.86915 | 25.15% | [5 empty] | Non-TXV | 13.09%
Bakersfield | CA | 93307-5900 |  | 2015-09-17 | 2015-09-17 11:36 | 2015-09-17 12:09 | NORDYNE - GR6GD-X42K096X | 115 | 17.8 | Yes | Yes | 17.5 | 18.7 | -1.2 | E16DB42EC6DF48368BD864D1CBF6919F |  | R410A | Non-TXV |  | 15.48% | 0.84522 | 29.75% | [5 empty] | Non-TXV | 15.48%
Bakersfield | CA | 93307-6395 |  | 2015-09-17 | 2015-09-17 14:31 | 2015-09-17 14:31 | RHEEM - RRNL-B042JK08X | 112 | 0 | Yes | Yes | 24.9 | 19 | 5.9 | 661B03C361364EBA88D6B2B25E26F34C |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2645 |  | 2015-09-17 | 2015-09-17 13:37 | 2015-09-17 14:17 | OTHER - DAYP-F042N080A | 150 | 13.1 | Yes | Yes | 21.9 | 22 | -0.1 | 3B9A0984B61A439EBDA3110F28BADBDA |  | R22 | Non-TXV |  | 8.733% | 0.91267 | 16.78% | [5 empty] | Non-TXV | 8.733%
Dixon | CA | 95620-3410 |  | 2015-10-02 | 2015-10-02 15:25 | 2015-10-02 15:25 | BRYANT - 561CJ036F | 71 | 0 | Yes | Yes | 23.4 | 19.9 | 3.5 | ACC26031958746D5AC6393D55DFF2173 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Morgan Hill | CA | 95037-3204 |  | 2015-09-03 | 2015-09-03 10:56 | 2015-09-03 10:56 | OTHER - 561CJ036-D | 87 | 0 | Yes | Yes | 25.9 | 20.7 | 5.2 | 551DB1FD8A5F41F3AD957C9E3A638478 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6474 |  | 2015-10-03 | 2015-10-03 10:49 | 2015-10-03 10:49 | GOODMAN - GSC130481AG | 148 | 0 | Yes | Yes | 21.7 | 22.6 | -0.9 | CEB6FBACD3BF46CA8DE2FC65C1D34FC4 |  | R22 | TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3001 |  | 2015-09-02 | 2015-09-02 15:50 | 2015-09-02 15:50 | RHEEM - RRNL-B024JK06X | 78 | 0 | Yes | Yes | 18.5 | 20.4 | -1.9 | 65EB0BD7B6E84E38BE58A686BE26E304 |  | R410A | TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3532 |  | 2015-09-18 | 2015-09-18 14:44 | 2015-09-18 14:44 | PAYNE - PA12NA030-H | 85 | 0 | Yes | Yes | 20.7 | 20.4 | 0.3 | 311E4F64D61F43DAACEFEBB80BD69B7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6307 |  | 2015-09-09 | 2015-09-09 10:34 | 2015-09-09 10:34 | ICP - PGD336060K001C1 | 103 | 0 | Yes | Yes | 23.7 | 19.5 | 4.2 | 69A9BD24479E4B8488C168946C8546D7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2721 |  | 2015-10-19 | 2015-10-19 10:57 | 2015-10-19 10:57 | CARRIER - 593CJX048-A | 105 | 0 | Yes | Yes | 22 | 22 | 0 | 81413460B5D3426C9AC3344130364A39 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2936 |  | 2015-09-17 | 2015-09-17 16:36 | 2015-09-17 16:36 | BRYANT - 577CNWA42090NATP | 142 | 0 | Yes | Yes | 21.8 | 20.2 | 1.6 | 45A682E50CD2481592D71065B832E23F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2159 |  | 2015-10-07 | 2015-10-07 15:15 | 2015-10-07 15:16 | NORDYNE - JS5BD-030K | 85 | 8.8 | Yes | Yes | 20.5 | 22 | -1.5 | ACBDF11B125B4DCBBD191249CA530723 |  | R22 | Non-TXV |  | 10.35% | 0.89647 | 19.9% | [5 empty] | Non-TXV | 10.35%
Bakersfield | CA | 93307-2159 |  | 2015-10-08 | 2015-10-08 07:59 | 2015-10-08 07:59 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 20.3 | 22.6 | -2.3 | C16396D620914AB0911AD4DBA5FC3644 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2152 |  | 2015-10-13 | 2015-10-13 15:19 | 2015-10-13 15:20 | NORDYNE - JS5BD-024K | 104 | 4.4 | Yes | Yes | 22.5 | 24.2 | -1.7 | ECD931E39B14464A811F2BABE3351E27 |  | R22 | Non-TXV |  | 4.231% | 0.95769 | 8.131% | [5 empty] | Non-TXV | 4.231%
Bakersfield | CA | 93307-2190 |  | 2015-10-13 | 2015-10-13 15:05 | 2015-10-13 15:05 | NORDYNE - JS6BD-030K | 134 | 0 | Yes | Yes | 15.9 | 18.2 | -2.3 | 6AC2793B0B3645ECBAB9417AA0C4C6F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2161 |  | 2015-10-15 | 2015-10-15 11:27 | 2015-10-15 11:27 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.1 | 22.9 | -2.8 | C71A29F8308F4913A36ABE7FA84EBD03 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2190 |  | 2015-10-13 | 2015-10-13 15:11 | 2015-10-13 15:12 | NORDYNE - JS6BD-030K | 134 | 18.8 | Yes | Yes | 21 | 23.1 | -2.1 | FFA06C5B0CD749E695E74519339E3396 |  | R22 | Non-TXV |  | 14.03% | 0.8597 | 26.96% | [5 empty] | Non-TXV | 14.03%
Fresno | CA | 93725-9222 |  | 2015-11-09 | 2015-11-09 09:21 | 2015-11-09 09:21 | GE - DCYZF036NO7OC | 85 | 0 | Yes | Yes | 21.6 | 18.5 | 3.2 | 651EA8ECA98745A49802E6CA6FA9E718 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2161 |  | 2015-10-15 | 2015-10-15 11:28 | 2015-10-15 11:29 | NORDYNE - JS5BD-024K | 104 | 9.2 | Yes | Yes | 21.6 | 21.3 | 0.4 | 32DC7AF26DD34A99978561E01D6A5552 |  | R22 | Non-TXV |  | 8.846% | 0.91154 | 17% | [5 empty] | Non-TXV | 8.846%
Fresno | CA | 93722-2806 |  | 2015-11-09 | 2015-11-09 10:49 | 2015-11-09 10:49 | CARRIER - 38CK036330 | 67 | 0 | Yes | Yes | 20.9 | 18.8 | 2.1 | 8AC0E362AE094C509746A486D67617BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2434 |  | 2015-11-12 | 2015-11-12 09:18 | 2015-11-12 09:18 | CARRIER - 24ABC636A300 | 108 | 0 | Yes | Yes | 22.3 | 20.1 | 2.2 | 36FC2D4DBC5B403681BC71A23E282B25 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2015-10-15 | 2015-10-15 08:54 | 2015-10-15 08:54 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 21.3 | 23.1 | -1.8 | 1EEF102C11D44703831DCCAD9605AAE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2165 |  | 2015-10-15 | 2015-10-15 08:15 | 2015-10-15 08:16 | NORDYNE - JS5BD-024K | 104 | 16.7 | Yes | Yes | 23 | 24.2 | -1.2 | 352B84CA585C41CF902A99D5477C2D40 |  | R22 | Non-TXV |  | 16.06% | 0.83942 | 30.86% | [5 empty] | Non-TXV | 16.06%
Bakersfield | CA | 93307-2190 |  | 2015-10-13 | 2015-10-13 15:10 | 2015-10-13 15:10 | NORDYNE - JS6BD-030K | 132 | 9.6 | Yes | Yes | 19.8 | 22.4 | -2.6 | D49F3330E0D641ABA6E8495CA2FD751B |  | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Bakersfield | CA | 93307-2165 |  | 2015-10-15 | 2015-10-15 08:20 | 2015-10-15 08:20 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.4 | 23.1 | -2.7 | 3939299CAC1B437CA8CA4C5F9E808866 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:40 | 2015-10-13 14:41 | NORDYNE - JS5BD-030K | 104 | 20.3 | Yes | Yes | 19.2 | 22 | -2.8 | BB770A0E4D814EA7867E4B03565F86C9 |  | R22 | Non-TXV |  | 19.52% | 0.80481 | 37.51% | [5 empty] | Non-TXV | 19.52%
Bakersfield | CA | 93307-2169 |  | 2015-10-15 | 2015-10-15 09:06 | 2015-10-15 09:06 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 21.1 | 22.6 | -1.5 | 2A25BB6E6F4E4854A09BFA79A801EDC8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6700 |  | 2015-09-21 | 2015-09-21 11:59 | 2015-09-21 11:59 | TRANE - UNKNOWN | 95 | 0 | Yes | Yes | 17.8 | 17.9 | -0.1 | CB578E6D608942B483B4894BDA2350D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2607 |  | 2015-09-09 | 2015-09-09 13:09 | 2015-09-09 13:09 | TRANE - 4TTR3036D1000AA | 105 | 0 | Yes | Yes | 18.8 | 19.9 | -1.1 | 49C418A613BC43668AE0BF12A153F2D4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2190 |  | 2015-10-13 | 2015-10-13 15:08 | 2015-10-13 15:08 | NORDYNE - JS6BD-024K | 104 | 0 | Yes | Yes | 22 | 22 | 0 | DBAF64BA673F441ABB145F8EF05CE69D |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-2919 |  | 2015-10-22 | 2015-10-22 10:59 | 2015-10-22 10:59 | TRANE - TWX030D100A1 | 96 | 0 | Yes | Yes | 22.9 | 20.9 | 2 | 9EF635B9FF0F44F6BF72BCFC1BEF166E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2169 |  | 2015-10-15 | 2015-10-15 09:12 | 2015-10-15 09:12 | NORDYNE - JS5BD-024K | 104 | 10.3 | Yes | Yes | 22.8 | 22.3 | 0.5 | 5AF95391C5574BED9B6249752CBB381D |  | R22 | Non-TXV |  | 9.904% | 0.90096 | 19.03% | [5 empty] | Non-TXV | 9.904%
Vacaville | CA | 95687-5634 |  | 2015-11-10 | 2015-11-10 14:20 | 2015-11-10 14:20 | TRANE - TTN036 | 117 | 0 | Yes | Yes | 23 | 20.5 | 2.5 | D67F65CC430644599C7272231ED8FE53 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2150 |  | 2015-10-07 | 2015-10-07 18:47 | 2015-10-07 18:48 | NORDYNE - JS5BD-036K | 138 | 20.9 | Yes | Yes | 16.8 | 18.2 | -1.4 | 118C3EAF547C476FB658B930EC3084BB |  | R22 | Non-TXV |  | 15.14% | 0.84855 | 29.11% | [5 empty] | Non-TXV | 15.14%
Bakersfield | CA | 93309-5029 |  | 2015-09-11 | 2015-09-11 15:03 | 2015-09-11 15:03 | OTHER - N/A | 85 | 0 | Yes | Yes | 17.6 | 20.2 | -2.6 | 9DE7B7EAFAE3427B8F2BF7E28EA03AB1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:46 | 2015-10-13 14:47 | NORDYNE - JS5BD-030K | 134 | 6.2 | Yes | Yes | 23.2 | 22.1 | 1.1 | 1A3E949BCC8F439DB92234BD54AAECAD |  | R22 | Non-TXV |  | 4.627% | 0.95373 | 8.892% | [5 empty] | Non-TXV | 4.627%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:39 | 2015-10-13 15:40 | NORDYNE - JS6BD-030K | 134 | 18.2 | Yes | Yes | 21.1 | 21.5 | -0.4 | E3AC9D99AF444B6FAA6D79C5266C07EB |  | R22 | Non-TXV |  | 13.58% | 0.86418 | 26.1% | [5 empty] | Non-TXV | 13.58%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:51 | 2015-10-13 14:51 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 21.1 | 22.4 | -1.3 | 6384C06DEEBF4CCFA4200994C48D161D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2159 |  | 2015-10-07 | 2015-10-07 15:13 | 2015-10-07 15:14 | NORDYNE - JS5BD-030K | 134 | 16.1 | Yes | Yes | 21.8 | 22 | -0.2 | 03D9A5D0238A46A8AD49F811CDFCC6B6 |  | R22 | Non-TXV |  | 12.01% | 0.87985 | 23.09% | [5 empty] | Non-TXV | 12.01%
Bakersfield | CA | 93307-2153 |  | 2015-10-13 | 2015-10-13 15:25 | 2015-10-13 15:25 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 22.3 | 24 | -1.7 | 46564818DC41427B86FCBC54C2CD2703 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:39 | 2015-10-13 14:39 | NORDYNE - JS5BD-030K | 104 | 8.3 | Yes | Yes | 20.4 | 23.1 | -2.7 | E1141039F3AA44DD8FEF35F2460540E9 |  | R22 | Non-TXV |  | 7.981% | 0.92019 | 15.34% | [5 empty] | Non-TXV | 7.981%
Fairfield | CA | 94533-6504 |  | 2015-09-03 | 2015-09-03 09:26 | 2015-09-03 09:26 | DAY & NIGHT - 591ANX036000AAAA | 90 | 0 | Yes | Yes | 24.1 | 18.3 | 5.8 | 56256782056B47B6819EEE5A9C1809E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2163 |  | 2015-10-13 | 2015-10-13 15:53 | 2015-10-13 15:53 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.1 | 22 | -1.9 | F0E1A837A5414D4EA96D1EF1879389A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-7007 |  | 2015-08-25 | 2015-08-25 15:24 | 2015-08-25 15:24 | PAYNE - PA13NR048000AEAA | 85 | 0 | Yes | Yes | 13.9 | 16.6 | -2.7 | E95ECE844DE14AE99805103B9F8F9E2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0829 |  | 2015-09-01 | 2015-09-01 13:10 | 2015-09-01 13:10 | RHEEM - RRPL-B036JK06X | 92 | 0 | Yes | Yes | 18.4 | 19.9 | -1.5 | 9E8FFC47586A4D37977A568BA505C1B8 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2148 |  | 2015-10-07 | 2015-10-07 18:23 | 2015-10-07 18:23 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | 302080CCF97F4A0AB99D20E214B033EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2148 |  | 2015-10-07 | 2015-10-07 18:32 | 2015-10-07 18:32 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 19.8 | 22.1 | -2.3 | 8353E5C23F054C6E8384015177F607E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2159 |  | 2015-10-07 | 2015-10-07 15:18 | 2015-10-07 15:18 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 20.7 | 22.3 | -1.6 | 44A440E0DF9E48999125DF9B73EBEB0F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2148 |  | 2015-10-07 | 2015-10-07 18:28 | 2015-10-07 18:29 | NORDYNE - JS5BD-036K | 138 | 30.6 | Yes | Yes | 19.8 | 21.5 | -1.7 | E3E739A1FC89482B99805938852A1859 |  | R22 | Non-TXV |  | 22.17% | 0.77826 | 42.61% | [5 empty] | Non-TXV | 22.17%
Fresno | CA | 93703-1277 |  | 2015-09-23 | 2015-09-23 08:52 | 2015-09-23 08:52 | BRYANT - 574ANW0240609A | 120 | 0 | Yes | Yes | 19.2 | 18.3 | 0.9 | 3952CC59607F4C5BB14757AD06B46A4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95116-3091 |  | 2015-09-04 | 2015-09-04 10:56 | 2015-09-04 10:56 | CARRIER - 38CKC042300 | 80 | 0 | Yes | Yes | 23.4 | 20.4 | 3 | 770FE1B0F53F435A9D58AD8C5BA7BCC3 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:48 | 2015-10-13 14:48 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 23.6 | 21.8 | 1.8 | 0868876030A745E6933FD29C18431A5E |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95122-2910 |  | 2015-10-30 | 2015-10-30 11:04 | 2015-10-30 11:04 | TRANE - 2TTR2030A1000AA | 68 | 0 | Yes | Yes | 22.8 | 21.5 | 1.3 | DA120B1F88AA469A920733A5EEAE9D90 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2175 |  | 2015-10-15 | 2015-10-15 09:56 | 2015-10-15 09:57 | NORDYNE - JS5BD-036K | 138 | 8 | Yes | Yes | 25 | 22.4 | 2.7 | 82EEBF90C3E94153855B1589A7799035 |  | R22 | Non-TXV |  | 5.797% | 0.94203 | 11.14% | [5 empty] | Non-TXV | 5.797%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:44 | 2015-10-13 14:44 | NORDYNE - JS5BD-030K | 104 | 0 | Yes | Yes | 20.6 | 23.4 | -2.8 | 589FE71F66C34586A01A8B5158044863 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1915 |  | 2015-10-19 | 2015-10-19 09:45 | 2015-10-19 10:11 | YORK - D1NH024N036068 | 66 | 7.3 | Yes | Yes | 17.5 | 18.7 | -1.2 | 2C5535829EC64EC2B7F1A263D0D08BC9 |  | R22 | Non-TXV |  | 11.06% | 0.88939 | 21.26% | [5 empty] | Non-TXV | 11.06%
Santa Rosa | CA | 95401-0809 |  | 2015-09-22 | 2015-09-22 13:18 | 2015-09-22 13:18 | GE - N/A | 85 | 0 | Yes | Yes | 19.6 | 19.9 | -0.3 | C4F2747A764E4491809BAB7217A33016 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4296 |  | 2015-09-18 | 2015-09-18 11:29 | 2015-09-18 11:51 | CARRIER - 38TDA036300 | 85 | 10.3 | Yes | Yes | 17.3 | 19.3 | -2 | 34FEE1A74D1644C9B580F2C3873BC955 |  | R22 | TXV |  | 12.12% | 0.87882 | 23.29% | [5 empty] | TXV | 12.12%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:52 | 2015-10-13 14:52 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 27.3 | 21.9 | 5.4 | 7FC4E5A4B89F422BB3D59C0E24E5C1F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-8793 |  | 2015-11-16 | 2015-11-16 15:39 | 2015-11-16 15:39 | CARRIER - 24ABA436A310 | 116 | 0 | Yes | Yes | 18.9 | 18.2 | 0.7 | B12A975ED7C24228BBCDBDD268988E92 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2177 |  | 2015-10-15 | 2015-10-15 10:05 | 2015-10-15 10:05 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 23.5 | 22.6 | 0.9 | F82DA195FB3643F69D294535B163F7E8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4522 |  | 2015-09-02 | 2015-09-02 16:30 | 2015-09-02 16:30 | DAY & NIGHT - 36/80YAC-1080 | 66 | 0 | Yes | Yes | 21.6 | 21.5 | 0.1 | AFB2984D5779442AB62929013E48789A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2184 |  | 2015-10-15 | 2015-10-15 13:12 | 2015-10-15 13:12 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 19.6 | 22.1 | -2.5 | DF99135DD3BB4FD49D5C4DA02E4D9135 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2205 |  | 2015-10-06 | 2015-10-06 11:25 | 2015-10-06 11:25 | BRYANT - 561CJO42A | 80 | 0 | Yes | Yes | 24.4 | 20.3 | 4.1 | 6A602CC4F3CA4DA5819BA3E12B8ABDA3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2945 |  | 2015-08-28 | 2015-08-28 09:46 | 2015-08-28 09:46 | CARRIER - 585CJ030050 | 78 | 0 | Yes | Yes | 22 | 21.9 | 0.1 | 0E763E1B8125486595F0DA21EF4D5314 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:42 | 2015-10-13 15:42 | NORDYNE - JS6BD-030K | 134 | 0 | Yes | Yes | 22.1 | 22.2 | -0.1 | 5704B8EE7E48467EAB43ECC148A674F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2184 |  | 2015-10-15 | 2015-10-15 13:23 | 2015-10-15 13:24 | NORDYNE - JS5BD-030K | 134 | 32.9 | Yes | Yes | 23.7 | 22.1 | 1.6 | E2D8DA9C6D1045A098E4770EF6006BAE |  | R22 | Non-TXV |  | 24.55% | 0.75448 | 47.18% | [5 empty] | Non-TXV | 24.55%
Brentwood | CA | 94513-4933 |  | 2015-09-02 | 2015-09-02 10:11 | 2015-09-02 10:11 | OTHER - CNC36D70000A | 127 | 0 | Yes | Yes | 21.6 | 19.3 | 2.3 | 98C6ACE0A7174EF9B353ACA616715F55 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4024 |  | 2015-09-01 | 2015-09-01 10:48 | 2015-09-01 10:48 | GE - BTB818A100A | 36 | 0 | Yes | Yes | 19.2 | 19.9 | -0.7 | 8B6AF6372AF64356AB251659F624E4CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2184 |  | 2015-10-15 | 2015-10-15 13:25 | 2015-10-15 13:25 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 26 | 22.1 | 3.9 | EE59C354FEE84DD6A3DC97807F35C27E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2165 |  | 2015-10-15 | 2015-10-15 08:18 | 2015-10-15 08:19 | NORDYNE - JS5BD-024K | 104 | 10.5 | Yes | Yes | 20.3 | 21 | -0.7 | E3748C76564F4219B826C6D3A5E59938 |  | R22 | Non-TXV |  | 10.1% | 0.89904 | 19.4% | [5 empty] | Non-TXV | 10.1%
Bakersfield | CA | 93307-2192 |  | 2015-10-15 | 2015-10-15 13:27 | 2015-10-15 13:27 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 22.2 | 22.3 | -0.1 | 409A6D1F45EA46359AE37F11EC432C05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4047 |  | 2015-09-18 | 2015-09-18 11:05 | 2015-09-18 11:05 | KENMORE - NXA636GKA100 | 108 | 0 | Yes | Yes | 20.3 | 17.5 | 2.8 | C5B3923775AB40B89886C77E1C301F9F |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2165 |  | 2015-10-15 | 2015-10-15 08:22 | 2015-10-15 08:22 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 21.5 | 22.4 | -0.9 | 6BBD0BA5F1FF4D8AB9F70D49BA4DE2EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:43 | 2015-10-13 15:43 | NORDYNE - JS6BD-024K | 104 | 0 | Yes | Yes | 19.2 | 20.4 | -1.2 | C6F54D537FEC4798A4E618103F110EB7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-0809 |  | 2015-09-22 | 2015-09-22 12:51 | 2015-09-22 12:51 | UNITARY PRODUCTS GROUP - BRCSO361BD | 63 | 0 | Yes | Yes | 20.9 | 18.8 | 2.1 | 4A9983A64C364EB19E85D85934E2E526 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2856 |  | 2015-09-15 | 2015-09-15 13:26 | 2015-09-15 13:26 | NORDYNE - S3QA-036KA | 85 | 0 | Yes | Yes | 20 | 17.7 | 2.3 | 9512C3D3D50244CCAD28913E6581111B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2161 |  | 2015-09-16 | 2015-09-16 10:08 | 2015-09-16 10:08 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 24.9 | 22.6 | 2.3 | 6702BFBCC8DA49988112DD20A4B9BB81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2192 |  | 2015-10-15 | 2015-10-15 13:32 | 2015-10-15 13:32 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 24 | 22 | 2 | EC138FBA20FA4C1FB9F4A2195985AFAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2188 |  | 2015-09-16 | 2015-09-16 10:24 | 2015-09-16 10:24 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 22.1 | 22.6 | -0.5 | 2263E6EBAA3C4DAD9ED22D63822ECE0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3918 |  | 2015-09-01 | 2015-09-01 11:26 | 2015-09-01 11:26 | AMANA - ZRCF42VO1D | 133 | 0 | Yes | Yes | 19.9 | 18.2 | 1.7 | 49ED0B7E19B14009890D9FCD756D6029 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2188 |  | 2015-10-13 | 2015-10-13 14:58 | 2015-10-13 14:58 | NORDYNE - JS6BD-036K | 138 | 10.7 | Yes | Yes | 20.4 | 20.1 | 0.3 | 3DFB952887074133AFC35E36AC7F29D9 |  | R22 | Non-TXV |  | 7.754% | 0.92246 | 14.9% | [5 empty] | Non-TXV | 7.754%
Bakersfield | CA | 93307-2171 |  | 2015-10-15 | 2015-10-15 09:24 | 2015-10-15 09:25 | NORDYNE - JS5BD-030K | 134 | 12.6 | Yes | Yes | 21 | 21.4 | -0.4 | 5A17DEB5F6F145BBAE691DF48FBBF2E7 |  | R22 | Non-TXV |  | 9.403% | 0.90597 | 18.07% | [5 empty] | Non-TXV | 9.403%
Bakersfield | CA | 93307-2190 |  | 2015-10-13 | 2015-10-13 15:04 | 2015-10-13 15:04 | OTHER - N/A | 85 | 0 | Yes | Yes | 19.9 | 22.3 | -2.4 | EA3C81C5AF154687AB563B3E121D0DA1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7240 |  | 2015-10-29 | 2015-10-29 15:36 | 2015-10-29 15:36 | DUCANE - SG12B36075 | 98 | 0 | Yes | Yes | 20.4 | 20.4 | 0 | 8335D6C4EFE1459AAB55BBD2532D1930 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2188 |  | 2015-10-13 | 2015-10-13 14:59 | 2015-10-13 14:59 | NORDYNE - JS6BD-036K | 138 | 0 | Yes | Yes | 21.5 | 22.6 | -1.1 | 2E087125C8C54A67B8EEE4BD6ADEA938 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8351 |  | 2015-09-11 | 2015-09-11 08:51 | 2015-09-11 09:11 | RHEEM - N/A | 85 | 5.6 | Yes | Yes | 18.1 | 19.9 | -1.8 | ECF1E4EF3F004F2C9B7A8E87CF22C9ED |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Bakersfield | CA | 93307-2159 |  | 2015-10-07 | 2015-10-07 15:01 | 2015-10-07 15:01 | NORDYNE - JS5BD0-030K | 134 | 0 | Yes | Yes | 21.4 | 22 | -0.6 | 5A7182FC9A304113B71185F12F91030F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2184 |  | 2015-10-15 | 2015-10-15 13:21 | 2015-10-15 13:22 | NORDYNE - JS5BD-030K | 134 | 11 | Yes | Yes | 19.3 | 22.1 | -2.8 | 7B2489DC5AA946FE94DB81AA605DB3F5 |  | R22 | Non-TXV |  | 8.209% | 0.91791 | 15.78% | [5 empty] | Non-TXV | 8.209%
Bakersfield | CA | 93306-2809 |  | 2015-09-16 | 2015-09-16 11:08 | 2015-09-16 11:08 | ICP - PGC036K060E | 71 | 0 | Yes | Yes | 20.9 | 18.8 | 2.1 | F7FA6030A0C0492386CDD95A6E0AD983 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2188 |  | 2015-10-13 | 2015-10-13 14:56 | 2015-10-13 14:57 | NORDYNE - JS6BD-036K | 138 | 10.6 | Yes | Yes | 21.5 | 22 | -0.5 | CDEC7BFFC67E47469F2BFCE61E9C78C6 |  | R22 | Non-TXV |  | 7.681% | 0.92319 | 14.76% | [5 empty] | Non-TXV | 7.681%
Brentwood | CA | 94513-2082 |  | 2015-09-02 | 2015-09-02 12:20 | 2015-09-02 12:20 | CARRIER - 38CKC018320 | 68 | 0 | Yes | Yes | 23.8 | 20.4 | 3.4 | ED6A62B1F4224F1EA0A8577594F73B14 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2341 |  | 2015-10-08 | 2015-10-08 13:11 | 2015-10-08 13:11 | TRANE - 2TTB0030A1000AA | 64 | 0 | Yes | Yes | 19.2 | 21 | -1.8 | C901835C7930417CA88D0E55DDD6694A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2081 |  | 2015-10-14 | 2015-10-14 12:03 | 2015-10-14 12:03 | CARRIER - 38CKC018320 | 68 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 8D2C164F3043427581A769E6D5327245 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2184 |  | 2015-10-15 | 2015-10-15 13:20 | 2015-10-15 13:20 | NORDYNE - JS5BD-030K | 134 | 11.3 | Yes | Yes | 19.5 | 22.4 | -2.9 | 646B2E65CF874C7F97D54986E33D73F9 |  | R22 | Non-TXV |  | 8.433% | 0.91567 | 16.21% | [5 empty] | Non-TXV | 8.433%
Vacaville | CA | 95687-6746 |  | 2015-11-23 | 2015-11-23 10:02 | 2015-11-23 10:02 | RUUD - UAKA024JAZ | 50 | 0 | Yes | Yes | 20.4 | 18.8 | 1.6 | 7CEE4FFA0E3A45DAB92BB8C4519D7F4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2084 |  | 2015-09-02 | 2015-09-02 14:07 | 2015-09-02 14:07 | CARRIER - 38CKC018320 | 68 | 0 | Yes | Yes | 24.1 | 20.9 | 3.2 | 1ACCB590B55B43CA9B0065D0F7B75F85 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3324 |  | 2015-09-08 | 2015-09-08 11:07 | 2015-09-08 11:07 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 24.1 | 23.1 | 1 | 2FA18007BA374BE4A7D95BDFA933E4D6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2169 |  | 2015-10-15 | 2015-10-15 09:16 | 2015-10-15 09:17 | NORDYNE - JS5BD-030K | 134 | 6 | Yes | Yes | 19.8 | 22.1 | -2.3 | 21BE98C340F442E78649F994B5ACC8CE |  | R22 | Non-TXV |  | 4.478% | 0.95522 | 8.605% | [5 empty] | Non-TXV | 4.478%
Bakersfield | CA | 93309-5162 |  | 2015-09-11 | 2015-09-11 15:09 | 2015-09-11 18:54 | OTHER - N/A | 85 | 15.9 | Yes | Yes | 20.4 | 21.4 | -1 | A58E8A6532FA4418AFE5DDB4ACFFAF25 |  | R22 | Non-TXV |  | 18.71% | 0.81294 | 35.95% | [5 empty] | Non-TXV | 18.71%
Fresno | CA | 93722-7707 |  | 2015-11-09 | 2015-11-09 12:21 | 2015-11-09 12:21 | OTHER - 561CJ036E | 73 | 0 | Yes | Yes | 18.8 | 21 | -2.2 | 3BAE162C4BAF4691B39D0B31B1E39E05 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4414 |  | 2015-09-01 | 2015-09-01 13:44 | 2015-09-01 14:07 | RHEEM - RAKA-036JAS | 75 | 7 | Yes | Yes | 20.8 | 21.9 | -1.1 | 97F940D25EE3463DBFF6B61CD6106EA3 |  | R22 | Non-TXV |  | 9.333% | 0.90667 | 17.94% | [5 empty] | Non-TXV | 9.333%
Bakersfield | CA | 93307-2192 |  | 2015-10-15 | 2015-10-15 13:30 | 2015-10-15 13:30 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 21.2 | 22.1 | -0.9 | 72B2A3758E5A4108B5C3F844127AFBB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3689 |  | 2015-08-28 | 2015-08-28 10:17 | 2015-08-28 10:17 | ICP - PGF024K040E | 56 | 0 | Yes | Yes | 21.2 | 21.2 | 0 | 111D4843B040495DA9E326F53A2AF484 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2080 |  | 2015-09-03 | 2015-09-03 13:11 | 2015-09-03 13:11 | CARRIER - 38CKC018320 | 68 | 0 | Yes | Yes | 21.9 | 19.4 | 2.5 | 9E7C1B27A8F7487AAB725EAB4BAB0BDC |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2081 |  | 2015-09-01 | 2015-09-01 12:04 | 2015-09-01 12:29 | GMC - VSC130361AA | 119 | 20.9 | Yes | Yes | 16.3 | 17.7 | -1.4 | 4D34551777A648EBA10C5FA97EEADBFA |  | R22 | Non-TXV |  | 17.56% | 0.82437 | 33.75% | [5 empty] | Non-TXV | 17.56%
Brentwood | CA | 94513-2084 |  | 2015-09-02 | 2015-09-02 13:31 | 2015-09-02 13:31 | CARRIER - 38CKC018320 | 68 | 0 | Yes | Yes | 24.2 | 19.9 | 4.3 | 9483F772E41B4F14BD9A67E00E6A17F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2085 |  | 2015-09-02 | 2015-09-02 11:21 | 2015-09-02 11:21 | CARRIER - 38CKC024320 | 72 | 0 | Yes | Yes | 22.7 | 19.9 | 2.8 | 80F8167BF65448EE832E1B052256733D |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2148 |  | 2015-10-07 | 2015-10-07 18:26 | 2015-10-07 18:27 | NORDYNE - JS5BD-036K | 138 | 18.1 | Yes | Yes | 19.9 | 21.7 | -1.8 | 793001C54EFF4F40A66CD026DA3748C1 |  | R22 | Non-TXV |  | 13.12% | 0.86884 | 25.21% | [5 empty] | Non-TXV | 13.12%
Fresno | CA | 93727-6009 |  | 2015-10-02 | 2015-10-02 11:13 | 2015-10-02 11:13 | YORK - N1E1055691 | 212 | 0 | Yes | Yes | 22.9 | 22.2 | 0.7 | 031F8F890D784AF89632DBD9F3B0821A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5533 |  | 2015-10-21 | 2015-10-21 12:14 | 2015-10-21 12:14 | GOODMAN - PGB024050-V | 54 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | 1CDF86207A5344B0A056AD00214A7F6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-8636 |  | 2015-09-29 | 2015-09-29 14:26 | 2015-09-29 14:26 | LENNOX - 13ACD060263002 | 214 | 0 | Yes | Yes | 23.4 | 17.9 | 5.5 | 56A40FE166904C8A93FA434AC232C1D6 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2182 |  | 2015-10-15 | 2015-10-15 12:31 | 2015-10-15 12:31 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 19.3 | 21.5 | -2.2 | A8B337A08F48423FAF571234029555A9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Milpitas | CA | 95035-3752 |  | 2015-09-03 | 2015-09-03 14:42 | 2015-09-03 14:42 | GOODMAN - CK30-18 | 76 | 0 | Yes | Yes | 19.5 | 21.3 | -1.8 | DD14F0BF5FC04303AF35BB995AEE632F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4116 |  | 2015-09-22 | 2015-09-22 14:06 | 2015-09-22 14:06 | CARRIER - 48HMX042301BE | 85 | 0 | Yes | Yes | 24 | 25.1 | -1.1 | 1BC5DAD2009F4FFEA0F604329932AE20 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5063 |  | 2015-11-09 | 2015-11-09 09:37 | 2015-11-09 09:37 | TRANE - TCT036G1M0AD | 67 | 0 | Yes | Yes | 23.3 | 19.9 | 3.4 | 0795FDD23A48416CA0346FE7140859F2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5637 |  | 2015-10-08 | 2015-10-08 13:28 | 2015-10-08 13:28 | RHEEM - RAMA-048JAZ | 173 | 0 | Yes | Yes | 22 | 23.1 | -1.1 | 2E65D0996B114B969969CE10C3E1568A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2169 |  | 2015-10-15 | 2015-10-15 09:13 | 2015-10-15 09:14 | NORDYNE - JS5BD-030K | 134 | 17.1 | Yes | Yes | 17.8 | 20.4 | -2.6 | 036862CD765D46879878AE7F21FB2EC8 |  | R22 | Non-TXV |  | 12.76% | 0.87239 | 24.52% | [5 empty] | Non-TXV | 12.76%
San Jose | CA | 95131-3746 |  | 2015-10-08 | 2015-10-08 15:01 | 2015-10-08 15:01 | OTHER - H1RA018S06A | 54 | 0 | Yes | Yes | 18.3 | 20.8 | -2.5 | F8CBEBBB2C6D492FA6423A2AEF706E98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2150 |  | 2015-10-07 | 2015-10-07 18:36 | 2015-10-07 18:37 | NORDYNE - JS5BD-036K | 138 | 15.1 | Yes | Yes | 24.5 | 21.4 | 3.1 | 348ABB3A76814A1BB75ABFB939C35A09 |  | R22 | Non-TXV |  | 10.94% | 0.89058 | 21.03% | [5 empty] | Non-TXV | 10.94%
Fresno | CA | 93722-6003 |  | 2015-09-30 | 2015-09-30 12:48 | 2015-09-30 12:48 | CARRIER - CA3042VKA1 | 54 | 0 | Yes | Yes | 19.1 | 21.4 | -2.3 | FA2FF025CA32465C9075FCF7F6D8D752 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2150 |  | 2015-10-07 | 2015-10-07 18:38 | 2015-10-07 18:39 | NORDYNE - JS5BD-036K | 138 | 16.3 | Yes | Yes | 21.3 | 23.1 | -1.8 | 3BB19819CDF9435CBCB06D5161846643 |  | R22 | Non-TXV |  | 11.81% | 0.88188 | 22.7% | [5 empty] | Non-TXV | 11.81%
Bakersfield | CA | 93307-2181 |  | 2015-10-15 | 2015-10-15 12:21 | 2015-10-15 12:22 | NORDYNE - JS5BD-024K | 104 | 7.1 | Yes | Yes | 20.8 | 21.8 | -1 | 15651357E99B4232B27CDECB7ADD7EAF |  | R22 | Non-TXV |  | 6.827% | 0.93173 | 13.12% | [5 empty] | Non-TXV | 6.827%
Bakersfield | CA | 93307-2167 |  | 2015-10-15 | 2015-10-15 08:32 | 2015-10-15 08:32 | NORDYNE - JS5BD-036K | 85 | 0 | Yes | Yes | 20.6 | 22.5 | -1.9 | 80E01CC080B847EEAAF3C3D956E84698 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2161 |  | 2015-10-15 | 2015-10-15 11:22 | 2015-10-15 11:22 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 25.5 | 22.1 | 3.4 | 1BE00195B8594C78B13A8A3B3B11A177 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-9414 |  | 2015-09-19 | 2015-09-19 10:37 | 2015-09-19 10:37 | TRANE - 2TTR2048A100AA | 120 | 0 | Yes | Yes | 19 | 19.3 | -0.3 | D085A1086BC04CF18AD4DF950B8501C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2181 |  | 2015-10-15 | 2015-10-15 12:20 | 2015-10-15 12:20 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 19.9 | 22.1 | -2.2 | EE4136B8AE2E47099161789A6300CF5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6909 |  | 2015-09-11 | 2015-09-11 16:54 | 2015-09-11 16:54 | OTHER - GCGD36S21S2B | 85 | 0 | Yes | Yes | 21.4 | 21.4 | 0 | CF2013C0FB554B19B9CC874580C2C92E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2472 |  | 2015-09-08 | 2015-09-08 09:20 | 2015-09-08 09:41 | YORK - GCGD48S21S2C | 85 | 4.8 | Yes | Yes | 22.4 | 18.8 | 3.6 | 234E3C547B6342D2814C53980011368D |  | R22 | Non-TXV |  | 5.647% | 0.94353 | 10.85% | [5 empty] | Non-TXV | 5.647%
Fairfield | CA | 94533-3763 |  | 2015-09-09 | 2015-09-09 10:08 | 2015-09-09 10:08 | TRANE - TTR036C100A2 | 92 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | 849F41D5379F450180F0BA046D9F1E89 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 12:12 | 2015-10-15 12:12 | NORDYNE - JS5BD-024K | 104 | 15.8 | Yes | Yes | 21.4 | 22.1 | -0.7 | 8F87A74D5105499999A8C491B601CCE5 |  | R22 | Non-TXV |  | 15.19% | 0.84808 | 29.2% | [5 empty] | Non-TXV | 15.19%
Bakersfield | CA | 93307-2161 |  | 2015-10-15 | 2015-10-15 11:30 | 2015-10-15 11:30 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 21.2 | 22.6 | -1.4 | A41F5D0DF60F41218AFC889AB71FB235 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4269 |  | 2015-09-02 | 2015-09-02 08:51 | 2015-09-02 09:07 | GOODMAN - CK42-1C | 92 | 14.4 | Yes | Yes | 21.2 | 20.7 | 0.5 | E217F9141C5144E8A12B50C033E65652 |  | R22 | Non-TXV |  | 15.65% | 0.84348 | 30.08% | [5 empty] | Non-TXV | 15.65%
Antioch | CA | 94509-3412 |  | 2015-10-16 | 2015-10-16 12:19 | 2015-10-16 12:19 | RHEEM - RAKA-030JAZ | 66 | 0 | Yes | Yes | 21.6 | 17.8 | 3.8 | 9A1C51E40EA34DB08C749B3D93F76106 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2173 |  | 2015-10-15 | 2015-10-15 11:02 | 2015-10-15 11:02 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 22.1 | 21.4 | 0.7 | A4A3C37CD49645208175234A4AAAC9DD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 12:00 | 2015-10-15 12:00 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 19 | 21.4 | -2.4 | 5877C7E7B0ED457593E3511BC58B6F25 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasant Hill | CA | 94523-2149 |  | 2015-09-01 | 2015-09-01 09:56 | 2015-09-01 10:16 | AMERICAN STANDARD - 2A7A3048A1000AA | 142 | 12.9 | Yes | Yes | 23.2 | 17.7 | 5.5 | E78A2B5CBE1440F28A5D609C3353D832 |  | R22 | Non-TXV |  | 9.085% | 0.90915 | 17.46% | [5 empty] | Non-TXV | 9.085%
Bakersfield | CA | 93307-2163 |  | 2015-10-13 | 2015-10-13 16:00 | 2015-10-13 16:00 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 23.4 | 22.6 | 0.8 | 2D46D7EE942248B6ABD1865B56CFD979 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5701 |  | 2015-09-24 | 2015-09-24 14:50 | 2015-09-24 14:50 | - | 85 | 0 | Yes | Yes | 21.2 | 19.2 | 2 | AC0AB7E2BACE491683C9DA7E6FED2CC6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2152 |  | 2015-10-13 | 2015-10-13 15:18 | 2015-10-13 15:18 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 19.6 | 22.6 | -3 | DE7FF0C68DE2449195A70B5D97609817 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5374 |  | 2015-10-01 | 2015-10-01 11:49 | 2015-10-01 11:49 | LENNOX - N/A | 102 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | 0D25199E1AC74904BE1D98320333C7D9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2163 |  | 2015-10-13 | 2015-10-13 15:58 | 2015-10-13 15:59 | NORDYNE - JS5BD-024K | 104 | 20.4 | Yes | Yes | 23.4 | 23.1 | 0.3 | A7EB661CFA7C486E8C6B014F6ADAA885 |  | R22 | Non-TXV |  | 19.62% | 0.80385 | 37.7% | [5 empty] | Non-TXV | 19.62%
Bakersfield | CA | 93307-2182 |  | 2015-10-15 | 2015-10-15 12:30 | 2015-10-15 12:30 | NORDYNE - JS5BD-024K | 104 | 12.1 | Yes | Yes | 21.9 | 21.5 | 0.4 | 4A226FE859AC448D9F2313C160EB9578 |  | R22 | Non-TXV |  | 11.63% | 0.88365 | 22.36% | [5 empty] | Non-TXV | 11.63%
Bakersfield | CA | 93307-2182 |  | 2015-10-15 | 2015-10-15 12:28 | 2015-10-15 12:28 | NORDYNE - JS5BD-024KJSA | 104 | 0 | Yes | Yes | 21.1 | 22.1 | -1 | 6383A64A883C4A9486868A97ACDF87D3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2175 |  | 2015-10-15 | 2015-10-15 09:50 | 2015-10-15 09:51 | NORDYNE - JS5BD-036K | 138 | 4.7 | Yes | Yes | 23.1 | 22 | 1.1 | BD9B6FC01D0A4C29806DDA669989460E |  | R22 | Non-TXV |  | 3.406% | 0.96594 | 6.545% | [5 empty] | Non-TXV | 3.406%
Bakersfield | CA | 93307-2177 |  | 2015-10-15 | 2015-10-15 10:02 | 2015-10-15 10:03 | NORDYNE - JS5BD-036K | 138 | 9.4 | Yes | Yes | 22.3 | 22.6 | -0.3 | 78645C007FF2408CAA814E76AEB99367 |  | R22 | Non-TXV |  | 6.812% | 0.93188 | 13.09% | [5 empty] | Non-TXV | 6.812%
Bakersfield | CA | 93307-2163 |  | 2015-10-13 | 2015-10-13 15:57 | 2015-10-13 15:57 | HEIL - N2A324AKC200 | 60 | 10.9 | Yes | Yes | 19.6 | 22.1 | -2.5 | F244D0ED324B4FB3A10D15DA8543FB86 |  | R22 | Non-TXV |  | 18.17% | 0.81833 | 34.91% | [5 empty] | Non-TXV | 18.17%
Bakersfield | CA | 93307-2184 |  | 2015-10-15 | 2015-10-15 13:14 | 2015-10-15 13:14 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.5 | 23.5 | -3 | 16F8F0BF23FD429D8B8CFBF343F2A88B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3480 |  | 2015-09-11 | 2015-09-11 11:41 | 2015-09-11 11:41 | YORK - UNKNOWN | 150 | 0 | Yes | Yes | 20.8 | 20.2 | 0.6 | D6AD021C312B4E05A248FB1FC9B3BA31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-2851 |  | 2015-08-25 | 2015-08-25 11:53 | 2015-08-25 11:53 | GOODMAN - GPG1360090M41CA | 91 | 0 | Yes | Yes | 24.5 | 22.5 | 2 | BFB52428524642F3A7F745BA22B6CEA0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93308-2239 |  | 2015-09-22 | 2015-09-22 10:11 | 2015-09-22 10:33 | OTHER - | 85 | 10.8 | Yes | Yes | 20.3 | 22.8 | -2.5 | 6D04493FBFBD46EFBB21DFDFE73A414C |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
Bakersfield | CA | 93307-2173 |  | 2015-10-15 | 2015-10-15 11:15 | 2015-10-15 11:15 | NORDYNE - JS5BD-036K | 138 | 10.2 | Yes | Yes | 23.7 | 21.5 | 2.2 | 6F0856804D5F4ADAA04CCE887661D85A |  | R22 | Non-TXV |  | 7.391% | 0.92609 | 14.2% | [5 empty] | Non-TXV | 7.391%
Pittsburg | CA | 94565-7352 |  | 2015-09-28 | 2015-09-28 11:31 | 2015-09-28 11:31 | OTHER - UNKNOWN | 76 | 0 | Yes | Yes | 19.2 | 19.4 | -0.2 | D87F35E0B9AE4B5AA34A7BC412690CA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-1809 |  | 2015-09-24 | 2015-09-24 15:04 | 2015-09-24 15:04 | DAY & NIGHT - N2A330 | 85 | 0 | Yes | Yes | 12.7 | 14.7 | -2 | B26A0737F56F44F39B04691552156FA2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2210 |  | 2015-10-01 | 2015-10-01 15:53 | 2015-10-01 15:53 | RHEEM - RRNA-B042JK08X | 104 | 0 | Yes | Yes | 17 | 20 | -3 | C440CD1B22FD4FAA9BE157C467C08BEE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-1845 |  | 2015-09-28 | 2015-09-28 13:50 | 2015-09-28 13:50 | DAY & NIGHT - 567GJ030B | 80 | 0 | Yes | Yes | 24 | 19.3 | 4.7 | 6287947844834A3B87DDCA3B70E83740 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-1809 |  | 2015-10-05 | 2015-10-05 11:36 | 2015-10-05 11:36 | YORK - D1NH018N03606C | 70 | 0 | Yes | Yes | 15.6 | 18.2 | -2.6 | A8A4C0A91D9B4AA3BB1486E5F04F85BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4914 |  | 2015-09-28 | 2015-09-28 09:02 | 2015-09-28 09:02 | RHEEM - RRNA-B024JK06X | 70 | 0 | Yes | Yes | 18.3 | 19.5 | -1.2 | 78CE1DFFE651425780D96F50BE8861E4 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 12:07 | 2015-10-15 12:08 | NORDYNE - JS5BD-024K | 104 | 17.2 | Yes | Yes | 20.9 | 22.6 | -1.7 | A47C792C0F9C4577B2ADBF6D50CD27D4 |  | R22 | Non-TXV |  | 16.54% | 0.83462 | 31.78% | [5 empty] | Non-TXV | 16.54%
Bakersfield | CA | 93307-2153 |  | 2015-10-13 | 2015-10-13 15:23 | 2015-10-13 15:24 | OTHER - HCBE-FO30SB | 130 | 11.9 | Yes | Yes | 21.5 | 23.4 | -1.9 | B4830955985542608F884744597F08ED |  | R22 | Non-TXV |  | 9.154% | 0.90846 | 17.59% | [5 empty] | Non-TXV | 9.154%
Vallejo | CA | 94590-8198 |  | 2015-08-28 | 2015-08-28 15:34 | 2015-08-28 15:34 | LENNOX - LCS3DC02423004 | 67 | 0 | Yes | Yes | 14.1 | 16.9 | -2.8 | F2BB8A1CA5074264877FA93467D2CD3A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 31°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-2078 |  | 2015-09-24 | 2015-09-24 11:07 | 2015-09-24 11:07 | TRANE - YCP036F1MOAA | 109 | 0 | Yes | Yes | 21.2 | 19.2 | 2 | AABF76EAD79443B9A9C39A78CFEDF1C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-1809 |  | 2015-10-21 | 2015-10-21 10:08 | 2015-10-21 10:08 | YORK - D1NH018N036060 | 70 | 0 | Yes | Yes | 18.6 | 20.6 | -2 | E75BCE5874BB45EC8280987C5FBE87DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2167 |  | 2015-10-15 | 2015-10-15 08:35 | 2015-10-15 08:36 | NORDYNE - JS5BD-036K | 134 | 12 | Yes | Yes | 24.3 | 22 | 2.3 | 05D54970885E4ABDB6EBE8BF9701C2DF |  | R22 | Non-TXV |  | 8.955% | 0.91045 | 17.21% | [5 empty] | Non-TXV | 8.955%
Bakersfield | CA | 93307-2190 |  | 2015-10-13 | 2015-10-13 15:13 | 2015-10-13 15:13 | NORDYNE - JS6BD-030K | 134 | 0 | Yes | Yes | 20.7 | 22.6 | -1.9 | 4449455898EA41499ED79A7FFCE0BF21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-0000 |  | 2015-10-15 | 2015-10-15 11:09 | 2015-10-15 11:09 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 23 | 23.1 | -0.1 | 2AC39BAAC7EE4EF28F8AE49F08F54AEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7263 |  | 2015-09-17 | 2015-09-17 12:08 | 2015-09-17 12:10 | ICP - PGD336060K001C1 | 102 | 9.5 | Yes | Yes | 16.7 | 18.9 | -2.2 | 431487AD8CA247648F84BBAB2C87434D |  | R22 | Non-TXV |  | 9.314% | 0.90686 | 17.9% | [5 empty] | Non-TXV | 9.314%
Vacaville | CA | 95687-4111 |  | 2015-08-28 | 2015-08-28 11:05 | 2015-08-28 11:05 | TRANE - 4TTX3048A1000AB | 126 | 0 | Yes | Yes | 20.7 | 18.8 | 1.9 | 56B9620BE83F46D1B4F996547E72569F |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9788 |  | 2015-09-30 | 2015-09-30 10:40 | 2015-11-06 13:54 | TRANE - YCY048G140AD | 187 | 5.8 | Yes | Yes | 20.7 | 22.3 | -1.6 | 2E98BC12ACAD45ED88A3D73BCF7650F1 |  | R22 | Non-TXV |  | 3.102% | 0.96898 | 5.961% | [5 empty] | Non-TXV | 3.102%
Fairfield | CA | 94533-5169 |  | 2015-09-17 | 2015-09-17 09:27 | 2015-09-17 09:27 | CARRIER - 38BRC030320 | 100 | 0 | Yes | Yes | 19.1 | 21 | -1.9 | 7F1F48FBE471486495F729B89ECCEB51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4435 |  | 2015-09-09 | 2015-09-09 10:39 | 2015-09-09 10:58 | YORK - D1NA024N03606C | 54 | 8.1 | Yes | Yes | 19.5 | 21 | -1.5 | 9C29BCA103ED4FA1BB381031E7A569A8 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Bakersfield | CA | 93307-2150 |  | 2015-10-07 | 2015-10-07 18:41 | 2015-10-07 18:42 | NORDYNE - JS5BD-036K | 138 | 14.7 | Yes | Yes | 21 | 23.1 | -2.1 | 9CD948489D3942B792837A6C5F101420 |  | R22 | Non-TXV |  | 10.65% | 0.89348 | 20.47% | [5 empty] | Non-TXV | 10.65%
Hercules | CA | 94547-1539 |  | 2015-11-04 | 2015-11-04 17:24 | 2015-11-04 17:24 | CARRIER - 38BRC036 | 85 | 0 | Yes | Yes | 18.5 | 17.7 | 0.8 | 34F038F466D7459CACC771BC7B564BBF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4048 |  | 2015-09-14 | 2015-09-14 12:46 | 2015-09-14 12:46 | PAYNE - PA10JAA30G | 77 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 571FDF85CDCB4F0387A64C5B98636B55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 12:04 | 2015-10-15 12:04 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 21.3 | 22.1 | -0.8 | B4AFBB681AC44F628B9E8B79C4225477 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2177 |  | 2015-10-15 | 2015-10-15 10:04 | 2015-10-15 10:04 | NORDYNE - JS5BD-036K | 138 | 15 | Yes | Yes | 20.1 | 21.8 | -1.7 | 5B561F36632147CD8158EFD098144F05 |  | R22 | Non-TXV |  | 10.87% | 0.8913 | 20.89% | [5 empty] | Non-TXV | 10.87%
Bakersfield | CA | 93307-2139 |  | 2015-09-17 | 2015-09-17 11:23 | 2015-09-17 11:23 | GOODMAN - GPG13300451BB | 77 | 0 | Yes | Yes | 22.7 | 20.3 | 2.4 | 3AE392AC33834254B9FB39961B0E6975 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3653 |  | 2015-08-28 | 2015-08-28 08:25 | 2015-08-28 08:25 | GOODMAN - GSC130361GA | 77 | 0 | Yes | Yes | 20.3 | 20.4 | -0.1 | 38053A361E8C47A7BD518B7FD56247D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 12:02 | 2015-10-15 12:02 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.8 | 22.1 | -1.3 | A555434F4480441A9D5F66B06BB3FC74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-2006 |  | 2015-09-25 | 2015-09-25 09:48 | 2015-09-25 09:48 | YORK - D4CG048N06206A | 102 | 0 | Yes | Yes | 22.1 | 20.2 | 2 | 5AE98331C83C42D1A83CB1658E777277 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1347 |  | 2015-10-26 | 2015-10-26 14:24 | 2015-10-26 14:24 | UNITARY PRODUCTS GROUP - 13ACD-048-230-16 | 118 | 0 | Yes | Yes | 21 | 18.6 | 2.4 | 424BB612D9B343649C24446157B54732 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 11:49 | 2015-10-15 11:49 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.6 | 23.2 | -2.6 | EB743B24B6E642C39121890A4434FB0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2153 |  | 2015-10-13 | 2015-10-13 15:21 | 2015-10-13 15:22 | NORDYNE - JS5BD-030K | 134 | 27.4 | Yes | Yes | 18.7 | 21.4 | -2.7 | A501C043C3894B3898CA775DEA7624D4 |  | R22 | Non-TXV |  | 20.45% | 0.79552 | 39.3% | [5 empty] | Non-TXV | 20.45%
Bakersfield | CA | 93307-2181 |  | 2015-10-15 | 2015-10-15 12:23 | 2015-10-15 12:24 | NORDYNE - JS5BD-024K | 104 | 15.2 | Yes | Yes | 19.6 | 21.3 | -1.6 | DD6A485C64254747BA0DA8A2BA0470D5 |  | R22 | Non-TXV |  | 14.62% | 0.85385 | 28.09% | [5 empty] | Non-TXV | 14.62%
Pinole | CA | 94564-1546 |  | 2015-10-29 | 2015-10-29 10:57 | 2015-10-29 10:57 | BRYANT - 561C1036-F | 85 | 0 | Yes | Yes | 21.9 | 20.6 | 1.3 | A1399AA7E9A143CC86EE34E5898EE146 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2177 |  | 2015-10-15 | 2015-10-15 10:00 | 2015-10-15 10:00 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 22.7 | 22.1 | 0.6 | DB845CF33C3A413BAFDBC18BF4C8C7B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 12:10 | 2015-10-15 12:10 | NORDYNE - JS5BD-024K | 104 | 10.3 | Yes | Yes | 19.2 | 20.4 | -1.2 | 06558AAC73114524A85C6399F71B4F73 |  | R22 | Non-TXV |  | 9.904% | 0.90096 | 19.03% | [5 empty] | Non-TXV | 9.904%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:34 | 2015-10-13 15:35 | NORDYNE - JS6BD-030K | 134 | 18 | Yes | Yes | 19.3 | 21.5 | -2.2 | 800172015F3747ACAF66FF4FE0C0B6E3 |  | R22 | Non-TXV |  | 13.43% | 0.86567 | 25.81% | [5 empty] | Non-TXV | 13.43%
Martinez | CA | 94553-1945 |  | 2015-09-10 | 2015-09-10 13:07 | 2015-09-10 13:07 | AMERICAN STANDARD - 24ABA348310 | 120 | 0 | Yes | Yes | 19.7 | 20.1 | -0.4 | 8E6D24EBCA8542F5850B2EFD084FC7BA |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-2215 |  | 2015-11-05 | 2015-11-05 13:00 | 2015-11-05 13:16 | YORK - D3NZ030N03606 | 74 | 0 | Yes | Yes | 24.4 | 20.9 | 3.5 | 30979EFAD99143EB9C52EDE300109335 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2169 |  | 2015-10-15 | 2015-10-15 09:01 | 2015-10-15 09:01 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 20.8 | 22.4 | -1.6 | C2C00881F0A64D65B51308F939E9856C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1938 |  | 2015-09-11 | 2015-09-11 15:33 | 2015-09-11 15:33 | OTHER - N/A | 85 | 0 | Yes | Yes | 16.5 | 19.3 | -2.8 | 408C89CB800842CE96D4246883CC09EB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2169 |  | 2015-10-15 | 2015-10-15 09:07 | 2015-10-15 09:07 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 22 | 21.5 | 0.5 | 545D3E870EFB4D388F6132F1C4B39D1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2167 |  | 2015-10-15 | 2015-10-15 08:31 | 2015-10-15 08:31 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 21 | 21.5 | -0.5 | 54D5709B828C480E847D75A19B34D7F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6785 |  | 2015-09-11 | 2015-09-11 12:43 | 2015-09-11 12:43 | CARRIER - 561CJ030-A | 65 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 2548C3E9516F472A9088A1845DC1A0CB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4125 |  | 2015-09-29 | 2015-09-29 11:51 | 2015-09-29 11:51 | COPELAND - UNKNOWN | 85 | 0 | Yes | Yes | 21.4 | 18.8 | 2.6 | A355184659D648EDB7D16DE7FEBB2F56 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8009 |  | 2015-10-22 | 2015-10-22 09:13 | 2015-10-22 09:45 | BRYANT - 113ANA024D | 56 | 5.6 | Yes | Yes | 24 | 20.4 | 3.6 | D3C9948C2F334DF3B0F7F137FB755EE3 |  | R410A | TXV |  | 10% | 0.9 | 19.22% | [5 empty] | TXV | 10%
Bakersfield | CA | 93306-1906 |  | 2015-09-09 | 2015-09-09 09:06 | 2015-09-09 09:06 | RHEEM - RAMA-048JBX | 172 | 0 | Yes | Yes | 25.9 | 22.2 | 3.7 | 0216F604905846E1A1FCBE4695403653 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2167 |  | 2015-10-15 | 2015-10-15 08:31 | 2015-10-15 08:31 | NORDYNE - JS5BD-036K | 85 | 0 | Yes | Yes | 21.8 | 22.5 | -0.7 | 5F723EDC938C433DB7BE35C1FB8E94FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2184 |  | 2015-10-15 | 2015-10-15 13:18 | 2015-10-15 13:18 | OTHER - N2A324AKC200 | 60 | 0 | Yes | Yes | 20.9 | 21.5 | -0.6 | 4EFDFE18C929418F81A9EB89806241C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2192 |  | 2015-10-15 | 2015-10-15 13:28 | 2015-10-15 13:28 | - JS5BD-036K | 138 | 0 | Yes | Yes | 22.6 | 22.3 | 0.3 | 7AB0C4FB08124883AFBA8EC7FB001A82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2182 |  | 2015-10-15 | 2015-10-15 12:33 | 2015-10-15 12:33 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 23 | 22.6 | 0.4 | 92155D61B5844B48A2406B985BF92B02 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-3526 |  | 2015-09-25 | 2015-09-25 08:32 | 2015-09-25 08:32 | PAYNE - 588ANW036080ACAF | 67 | 0 | Yes | Yes | 21.9 | 17.4 | 4.5 | D4CFB141531E41A9A290AE1265F1EC1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5504 |  | 2015-09-21 | 2015-09-21 12:51 | 2015-09-21 12:51 | GOODMAN - CK36-1A | 85 | 0 | Yes | Yes | 21.4 | 21.4 | 0 | 5EA8C6054DCA44D7A26B47842CE7CEB4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-6303 |  | 2015-09-09 | 2015-09-09 12:11 | 2015-09-09 12:11 | PAYNE - UNK | 85 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | 2E425FC338D1484483B284A31F15356C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7532 |  | 2015-10-28 | 2015-10-28 10:12 | 2015-10-28 10:12 | CARRIER - 24ABA336A300 | 114 | 0 | Yes | Yes | 22.1 | 21.5 | 0.6 | 2BD7D8384D8442F2BA8FDD43DDA3F46E |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2173 |  | 2015-10-15 | 2015-10-15 11:11 | 2015-10-15 11:11 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 22.8 | 21.8 | 1 | 32C1DEEA34854435BA6D73DCEDC3372E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2557 |  | 2015-09-11 | 2015-09-11 12:07 | 2015-09-11 12:22 | OTHER - N/A | 85 | 8.8 | Yes | Yes | 21.5 | 22.1 | -0.6 | F37AB67514CB4FDCA8C8C0F30EECC5EF |  | R22 | Non-TXV |  | 10.35% | 0.89647 | 19.9% | [5 empty] | Non-TXV | 10.35%
Oakley | CA | 94561-2217 |  | 2015-09-18 | 2015-09-18 15:21 | 2015-09-18 15:21 | TEMPSTAR - TCA036AKC4 | 96 | 0 | Yes | Yes | 25.1 | 20.9 | 4.2 | 692202F1A19448ABB90057FA64D39298 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9069 |  | 2015-09-30 | 2015-09-30 15:17 | 2015-11-09 12:35 | LENNOX - 12GCS036X-75-3PA | 110 | 3.7 | Yes | Yes | 20.1 | 21.8 | -1.7 | 61E71461BA624C4680B9214B2CDE8CD7 |  | R22 | Non-TXV |  | 3.364% | 0.96636 | 6.464% | [5 empty] | Non-TXV | 3.364%
Bakersfield | CA | 93305-4379 |  | 2015-08-31 | 2015-08-31 08:41 | 2015-08-31 08:41 | GOODMAN - GPG1324045M41CA | 68 | 0 | Yes | Yes | 19.6 | 18.8 | 0.8 | 1AFD88154F824BD3A22A377C584DA2CC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-5357 |  | 2015-09-02 | 2015-09-02 12:32 | 2015-09-02 12:32 | NORDYNE - 591ANX042000ABAA | 112 | 0 | Yes | Yes | 20.6 | 19.3 | 1.3 | 5D850B92746E4F9688B4D07B70915F6C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5564 |  | 2015-11-06 | 2015-11-06 15:47 | 2015-11-06 15:47 | OTHER - 48VLNA3606030 | 152 | 0 | Yes | Yes | 22 | 17.6 | 4.5 | AE9DE60E1E0B4CD0ABF868D604CFD519 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4512 |  | 2015-09-09 | 2015-09-09 14:46 | 2015-09-09 14:46 | CARRIER - PA13NNR036 | 84 | 0 | Yes | Yes | 19.2 | 17.4 | 1.8 | 2678F33FD70C435895B828D4E4B0F210 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8966 |  | 2015-09-09 | 2015-09-09 14:42 | 2015-09-09 14:42 | CARRIER - 38CK036350 | 71 | 0 | Yes | Yes | 19.9 | 22 | -2.1 | DD1C0B02731D4692BE229194F525D28A |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1737 |  | 2015-09-01 | 2015-09-01 16:07 | 2015-09-01 16:07 | YORK - UNK | 66 | 0 | Yes | Yes | 23.5 | 20.4 | 3.1 | E7B27CFDFDAB493285E63B896FFA849D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-2747 |  | 2015-09-03 | 2015-09-03 13:05 | 2015-09-03 13:05 | OTHER - 38TKB024300 | 68 | 0 | Yes | Yes | 24.4 | 20.4 | 4 | 46687E5B5A7248CE9ED91A92DD86A4BB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-9766 |  | 2015-09-16 | 2015-09-16 17:28 | 2015-09-16 17:28 | AMANA - PGD42C0902E | 120 | 0 | Yes | Yes | 23.4 | 20.5 | 3 | FABDFCE8A94D43B1A3C783B74D75E002 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-3315 |  | 2015-11-06 | 2015-11-06 11:10 | 2015-11-06 11:10 | AMERICAN STANDARD - YCC030FLMOBE | 72 | 0 | Yes | Yes | 22 | 20.1 | 1.9 | 6C4DE535B36D47378EF59DF63662831D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7973 |  | 2015-09-09 | 2015-09-09 12:50 | 2015-09-09 12:50 | BRYANT - 530BN018000BAAA | 104 | 0 | Yes | Yes | 17.3 | 20.2 | -2.9 | 64716E7751734C11942DED530147FFB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5172 |  | 2015-09-10 | 2015-09-10 18:03 | 2015-09-10 18:03 | OTHER - UNKNOWN | 62 | 0 | Yes | Yes | 21 | 20.2 | 0.9 | 8CB077CC03EC410E83A7958137133458 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7627 |  | 2015-09-10 | 2015-09-10 09:19 | 2015-09-10 09:19 | CARRIER - UNK | 90 | 0 | Yes | Yes | 28.8 | 25.2 | 3.6 | A57CA2CFFD4F4EF98A47695CAA306207 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2031 |  | 2015-09-10 | 2015-09-10 11:50 | 2015-09-10 11:50 | OTHER - N/A FRAZER JONSON | 85 | 0 | Yes | Yes | 17.8 | 20.6 | -2.8 | E02C9C8416A446B6A25DE7FD010963E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2121 |  | 2015-09-11 | 2015-09-11 10:46 | 2015-09-11 10:46 | GE - BTB942A100A3 | 101 | 0 | Yes | Yes | 25.3 | 19.8 | 5.5 | 7C011C17691A4872ADD4509CF0CF4260 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-3576 |  | 2015-09-14 | 2015-09-14 14:38 | 2015-09-14 14:38 | DUCANE - AC10B24 | 60 | 0 | Yes | Yes | 21.2 | 18.1 | 3.1 | 7B6C777C748644B49898DD832CB4DD9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3710 |  | 2015-09-10 | 2015-09-10 17:09 | 2015-09-10 17:09 | GOODMAN - PGB036075 | 61 | 0 | Yes | Yes | 17.9 | 19.3 | -1.4 | E001D383900D4C1ABC3A910C0C9B1F69 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2175 |  | 2015-10-15 | 2015-10-15 09:54 | 2015-10-15 09:54 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 22.3 | 23.1 | -0.8 | 305B67153DD341E588CC5006C0547B68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:37 | 2015-10-13 15:37 | NORDYNE - JS6BD-024K | 104 | 21.2 | Yes | Yes | 19.6 | 21.5 | -1.9 | 2448C5B48A814562838C1E58E09B5466 |  | R22 | Non-TXV |  | 20.38% | 0.79615 | 39.17% | [5 empty] | Non-TXV | 20.38%
Bakersfield | CA | 93313-4119 |  | 2015-10-01 | 2015-10-01 10:49 | 2015-10-01 10:49 | CARRIER - 580AN036060 | 85 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | 32E17D0236D34FAFBCFD45A30536F805 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2171 |  | 2015-10-15 | 2015-10-15 09:27 | 2015-10-15 09:28 | NORDYNE - JS5BD-030K | 134 | 10.6 | Yes | Yes | 19.1 | 22.1 | -3 | 67F2844AB80E4D6F86106A11DDDFF418 |  | R22 | Non-TXV |  | 7.91% | 0.9209 | 15.2% | [5 empty] | Non-TXV | 7.91%
Bakersfield | CA | 93307-2171 |  | 2015-10-15 | 2015-10-15 09:30 | 2015-10-15 09:30 | OTHER - PA13NR024 | 67 | 0 | Yes | Yes | 20.9 | 21.4 | -0.5 | C8E06959A49E4C31A9803D937D6CEEEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2085 |  | 2015-09-02 | 2015-09-02 12:51 | 2015-09-02 13:11 | CARRIER - 38CKC018320 | 68 | 13.4 | Yes | Yes | 17.3 | 18.3 | -1 | A8FE7C029F4641478D97A02A5586731E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 32°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.71% | 0.80294 | 37.87% | [5 empty] | Non-TXV | 19.71%
Pittsburg | CA | 94565-4917 |  | 2015-09-11 | 2015-09-11 03:31 | 2015-09-11 03:31 | AMERICAN STANDARD - CA3030GKA1 | 63 | 0 | Yes | Yes | 26.2 | 21 | 5.2 | 1BC7DE5926E04E499312A1B80852CEE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4024 |  | 2015-11-09 | 2015-11-09 12:59 | 2015-11-09 12:59 | GOODMAN - F001210036 | 82 | 0 | Yes | Yes | 17 | 17.7 | -0.7 | C5642D49DDB34C8C9CDBBAF2A7A0D940 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3517 |  | 2015-10-29 | 2015-10-29 11:28 | 2015-10-29 11:28 | TEMPSTAR - PGF342080K01 | 184 | 0 | Yes | Yes | 24.2 | 18.8 | 5.4 | 332410A2C29C4AB0B7E5FCF2A0C4C953 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-2618 |  | 2015-10-19 | 2015-10-19 09:55 | 2015-10-19 09:55 | LENNOX - HS29-651-2P | 122 | 0 | Yes | Yes | 26.5 | 20.7 | 5.8 | B2A842C75BC44631A833DA00F97D6F9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2179 |  | 2015-10-15 | 2015-10-15 12:05 | 2015-10-15 12:06 | NORDYNE - N/A | 104 | 22.5 | Yes | Yes | 22.5 | 21.5 | 1 | D35F5FA0BF5D47E0B84BFEFF97C29B78 |  | R22 | Non-TXV |  | 21.63% | 0.78365 | 41.58% | [5 empty] | Non-TXV | 21.63%
Bakersfield | CA | 93307-2171 |  | 2015-10-15 | 2015-10-15 09:36 | 2015-10-15 09:36 | NORDYNE - JS5BD-024K | 134 | 0 | Yes | Yes | 22.6 | 22.6 | 0 | 6ACCDC27A455480E9E987C34C1B64551 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2153 |  | 2015-10-13 | 2015-10-13 15:27 | 2015-10-13 15:27 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 20.5 | 23.1 | -2.6 | 026A228135F14B53A16BCA52A7528B3B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2165 |  | 2015-10-15 | 2015-10-15 08:17 | 2015-10-15 08:17 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 21.7 | 23.7 | -2 | E2C8ACD99F594289803D3D52B6A04164 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8052 |  | 2015-10-15 | 2015-10-15 09:41 | 2015-10-15 09:41 | CARRIER - 38CKC060300 | 151 | 0 | Yes | Yes | 20.9 | 21.4 | -0.5 | E830E38EAB064E8C868CC13ECB96F11C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3358 |  | 2015-09-02 | 2015-09-02 11:39 | 2015-09-02 11:39 | CARRIER - 561C1JO36-C | 72 | 0 | Yes | Yes | 18.6 | 20.4 | -1.8 | 352F5B4F78924BBE825726ED0629441F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7486 |  | 2015-11-06 | 2015-11-06 13:10 | 2015-11-06 13:10 | AMERICAN STANDARD - M2AC3030B1000AA | 89 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | C860C2B9D2FD4D299BCE121F1C1A3EF1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-2558 |  | 2015-09-11 | 2015-09-11 11:49 | 2015-09-11 12:05 | OTHER - N/A | 85 | 4.4 | Yes | Yes | 18.8 | 19.7 | -0.9 | DCC7222C0CD04FDDB9BC1A78BD806D8C |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Bakersfield | CA | 93309-2557 |  | 2015-09-11 | 2015-09-11 12:19 | 2015-09-11 12:19 | OTHER - N/A | 85 | 0 | Yes | Yes | 21.4 | 22.4 | -1 | 579788EFA1B84EC98FCEE3669B9DD0D4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2623 |  | 2015-09-18 | 2015-09-18 14:08 | 2015-09-18 14:31 | CARRIER - 38TH036300 | 86 | 13.8 | Yes | Yes | 25.4 | 19.8 | 5.6 | 4BAD020D2D0E4154B2F82687D052E5E7 |  | R22 | Non-TXV |  | 16.05% | 0.83953 | 30.84% | [5 empty] | Non-TXV | 16.05%
Sanger | CA | 93657-9319 |  | 2015-11-10 | 2015-11-10 13:36 | 2015-11-10 13:36 | GOODMAN - PC036-1A | 63 | 0 | Yes | Yes | 23.8 | 18.7 | 5.1 | B35B0B90807246CAAB6BB5C81EE4B2FD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-3969 |  | 2015-09-21 | 2015-09-21 15:12 | 2015-09-21 15:12 | OTHER - 60WDE24G1NA | 52 | 0 | Yes | Yes | 21.8 | 22.8 | -1 | D3167728C4414D3380261F79AEC155C5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6420 |  | 2015-09-09 | 2015-09-09 11:42 | 2015-09-09 11:42 | OTHER - 36TD941670 | 57 | 0 | Yes | Yes | 17 | 19.7 | -2.7 | A127A775D43D40EAAD0E1C8B721AAB74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94505-9490 |  | 2015-10-07 | 2015-10-07 15:00 | 2015-10-07 15:00 | AMERICAN STANDARD - 2A7A4048A1000AA | 150 | 0 | Yes | Yes | 22.3 | 20 | 2.4 | B8A0068706C44606BF9CC30BC1911822 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2307 |  | 2015-09-03 | 2015-09-03 11:57 | 2015-09-03 12:15 | CARRIER - 48NLA130300BE | 68 | 24.2 | Yes | Yes | 19.6 | 20.4 | -0.8 | FCB3A7864FC84EA085AA566CA15C3876 |  | R22 | Non-TXV |  | 35.59% | 0.64412 | 68.39% | [5 empty] | Non-TXV | 35.59%
Brentwood | CA | 94513-6465 |  | 2015-09-24 | 2015-09-24 09:53 | 2015-09-24 09:53 | CARRIER - 38BRC030310 | 100 | 0 | Yes | Yes | 22.2 | 19.9 | 2.3 | 6EFCAA6B84854AC4ADC53B074038CF0E |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2204 |  | 2015-09-28 | 2015-09-28 11:30 | 2015-09-28 11:30 | YORK - D2NP030N05606A | 73 | 0 | Yes | Yes | 20.3 | 21 | -0.7 | 1F014FA6F343464986CB25D60D8A228C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5165 |  | 2015-10-13 | 2015-10-13 12:11 | 2015-10-13 12:11 | BRYANT - UNKNOWN | 197 | 0 | Yes | Yes | 21.9 | 22.5 | -0.6 | 42CF4B8B833A40F3B808DEC4AAA71761 |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5170 |  | 2015-09-16 | 2015-09-16 14:04 | 2015-09-16 14:04 | CARRIER - 38QRR036-3 | 197 | 0 | Yes | Yes | 18.2 | 19.9 | -1.7 | F5FA46F046F9428EB78AA3A93ECC252A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5171 |  | 2015-09-18 | 2015-09-18 12:40 | 2015-09-18 12:40 | CARRIER - 38QRR024-301 | 85 | 0 | Yes | Yes | 18.8 | 18.4 | 0.4 | E5AA74E272BF4015BD6734855EA2162F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7032 |  | 2015-09-21 | 2015-09-21 09:20 | 2015-09-21 09:20 | RUUD - UPKA019JAZ | 57 | 0 | Yes | Yes | 17.6 | 19.6 | -2 | E755CB57E24F4485A6CB3114F466CC8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1729 |  | 2015-08-31 | 2015-08-31 14:55 | 2015-08-31 14:55 | AMERICAN STANDARD - TCA036AKC4 | 96 | 0 | Yes | Yes | 20.2 | 18.4 | 1.8 | 9FDDBA1D73974611806681BF2790C802 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6638 |  | 2015-09-09 | 2015-09-09 15:36 | 2015-09-09 15:36 | CARRIER - 24ABB342W300 | 85 | 0 | Yes | Yes | 16.5 | 18.8 | -2.3 | 2AC39283190E4B8AB81138F33A9354BB |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8714 |  | 2015-11-23 | 2015-11-23 15:33 | 2015-11-23 15:33 | YORK - D1NA36N03606 | 67 | 0 | Yes | Yes | 18.3 | 14.8 | 3.5 | 2F10F5CF0EDD42B994D8DCC28E0DD11D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2171 |  | 2015-10-15 | 2015-10-15 09:32 | 2015-10-15 09:32 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 20.9 | 23.1 | -2.2 | 19F4DD9C28AF4055B8E5F66FD883A6B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1235 |  | 2015-09-23 | 2015-09-23 09:41 | 2015-09-23 09:41 | RHEEM - RRMA-A048JK10X | 115 | 0 | Yes | Yes | 19.2 | 15.2 | 4 | 46091CF3951F4E2E9A91D84FAA7D1406 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2171 |  | 2015-10-15 | 2015-10-15 09:26 | 2015-10-15 09:26 | NORDYNE - JS5BD-030K | 134 | 12.6 | Yes | Yes | 22.5 | 22 | 0.5 | 6E8566289F754577A874AD64A46581BF |  | R22 | Non-TXV |  | 9.403% | 0.90597 | 18.07% | [5 empty] | Non-TXV | 9.403%
Bakersfield | CA | 93307-0000 |  | 2015-10-15 | 2015-10-15 09:34 | 2015-10-15 09:35 | NORDYNE - JS5BD-030K | 134 | 5.8 | Yes | Yes | 21.6 | 23.1 | -1.5 | DD2F803EE8D94BAB995B63C9C9FE68CF |  | R22 | Non-TXV |  | 4.328% | 0.95672 | 8.318% | [5 empty] | Non-TXV | 4.328%
Bakersfield | CA | 93307-2175 |  | 2015-10-15 | 2015-10-15 09:52 | 2015-10-15 09:52 | NORDYNE - JS5BD-036K | 138 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 824333AF2C3E4BDA9B8F13A7001CFD2D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5954 |  | 2015-10-05 | 2015-10-05 11:44 | 2015-10-05 11:44 | COMFORT AIRE - PGAD30D1K5 | 78 | 0 | Yes | Yes | 20.9 | 23.3 | -2.4 | 604679C411DB4F3FA963DD971D9048A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:44 | 2015-10-13 15:44 | NORDYNE - JS6BD-030K | 134 | 0 | Yes | Yes | 20.5 | 21.8 | -1.3 | A3B3F4A3D48F46B680921C5989F629EE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Friant | CA | 93626-0000 |  | 2015-11-03 | 2015-11-03 08:13 | 2015-11-03 08:13 | BDP - 542EJ024 | 100 | -5.9 | Yes | Yes | 25.7 | 20.4 | 5.3 | 32F25EBC2E624691A09E0A09A918A0CE | Remove refrigerant: 5.9 oz | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Friant | CA | 93626-0000 |  | 2015-11-03 | 2015-11-03 08:33 | 2015-11-03 08:33 | BDP - 54EJ024 | 100 | 0 | Yes | Yes | 22.6 | 19.1 | 3.5 | F3914E9C746C4A91BBAB4E7320BB486E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2685 |  | 2015-10-06 | 2015-10-06 16:30 | 2015-10-06 16:30 | OTHER - RANL-048JAZ | 145 | 0 | Yes | Yes | 18.5 | 21.5 | -3 | F61F24452D514E09ADE1665E02ED4A73 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-6932 |  | 2015-09-19 | 2015-09-19 11:44 | 2015-09-19 11:44 | OTHER - UNKNOWN | 95 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 77CDE34EBDE14F7AB9DC7E99615FBC2F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-9686 |  | 2015-09-18 | 2015-09-18 13:29 | 2015-09-18 13:29 | BRYANT - 563CN060-F | 195 | 0 | Yes | Yes | 22.3 | 20.2 | 2.1 | 32519A7D835C476E9FD5FA5D895B638C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1602 |  | 2015-09-21 | 2015-09-21 09:53 | 2015-09-21 10:10 | AMERICAN STANDARD - 2A7B3048A1000AA | 142 | 18.7 | Yes | Yes | 21.2 | 22.6 | -1.4 | 224F864FA0C64E20940220D05C367E59 |  | R22 | Non-TXV |  | 13.17% | 0.86831 | 25.31% | [5 empty] | Non-TXV | 13.17%
Fresno | CA | 93727-5849 |  | 2015-11-12 | 2015-11-12 12:48 | 2015-11-12 12:48 | YORK - H2RC048S06G | 119 | 0 | Yes | Yes | 15.3 | 18.2 | -2.9 | 9E7823CD151D4F9E983913121DF449B0 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2308 |  | 2015-09-03 | 2015-09-03 10:19 | 2015-09-03 10:19 | ICP - PGC024K040D | 58 | 0 | Yes | Yes | 20.3 | 18.2 | 2.1 | 132DE87AA77841F5BBF75EF2B5084F08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5388 |  | 2015-09-18 | 2015-09-18 10:21 | 2015-09-18 10:21 | PAYNE - UNK | 85 | 0 | Yes | Yes | 18.6 | 19.2 | -0.6 | B643C63C101245119897CC25775546C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2654 |  | 2015-09-10 | 2015-09-10 14:12 | 2015-09-10 14:47 | YORK - D2NP042NO6506NXA | 150 | 17.3 | Yes | Yes | 22.1 | 23.1 | -1 | 38BCD53CF6264DB1A4F3DCE144743270 |  | R22 | Non-TXV |  | 11.53% | 0.88467 | 22.16% | [5 empty] | Non-TXV | 11.53%
Vacaville | CA | 95687-4661 |  | 2015-09-23 | 2015-09-23 12:14 | 2015-09-23 12:14 | CARRIER - 38THO36300 | 90 | 0 | Yes | Yes | 20.7 | 18.3 | 2.4 | 9BE38F226710459DBF144426F972FB95 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-1538 |  | 2015-09-24 | 2015-09-24 12:30 | 2015-09-24 12:30 | CARRIER - PA10JA024-A | 69 | 0 | Yes | Yes | 16.6 | 19.3 | -2.7 | 72C4F0D93EA146D78171DAED038A3206 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7454 |  | 2015-11-05 | 2015-11-05 13:34 | 2015-11-05 13:34 | RUUD - | 72 | 0 | Yes | Yes | 24.8 | 19.7 | 5.2 | BD973F1C69B54578AAE53019AE237EC5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7819 |  | 2015-09-28 | 2015-09-28 15:59 | 2015-09-28 15:59 | GOODMAN - CPE24-1A8 | 93 | 0 | Yes | Yes | 17.5 | 19.9 | -2.4 | 71402387720845A28FAC96250C4B664D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-3321 |  | 2015-11-10 | 2015-11-10 10:31 | 2015-11-10 10:31 | RHEEM - N/A | 85 | 0 | Yes | Yes | 20.9 | 19.1 | 1.8 | 13FEFE49ED2F4EA9A70A664A58F6D519 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5341 |  | 2015-10-08 | 2015-10-08 12:29 | 2015-10-08 12:29 | TRANE - 13291XYD5F | 114 | 0 | Yes | Yes | 18.7 | 21.5 | -2.8 | CC5F1036F8214E1BA333EADD01E19D47 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5012 |  | 2015-09-11 | 2015-09-11 16:00 | 2015-09-11 16:00 | OTHER - N/A | 85 | 0 | Yes | Yes | 15.8 | 18.6 | -2.8 | E6558447C7B44EAB9F495D0F0A370732 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1922 |  | 2015-10-13 | 2015-10-13 09:59 | 2015-10-13 09:59 | RHEEM - RAFD-036JAS | 81 | 0 | Yes | Yes | 20.8 | 21.1 | -0.3 | 1D0536B49DE7478CB4D7A2BFB47E7451 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2294 |  | 2015-10-12 | 2015-10-12 09:47 | 2015-10-12 09:47 | UNITARY PRODUCTS GROUP - 2TTB3048A1000CA | 142 | 0 | Yes | Yes | 19.4 | 20.2 | -0.8 | AD129D440ED64DE4B58EF4D6BCE62A3D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2159 |  | 2015-10-07 | 2015-10-07 15:05 | 2015-10-07 15:05 | NORDYNE - JS5BD-030K | 134 | 0 | Yes | Yes | 20.4 | 22.1 | -1.7 | AB64DB4D844740BC981495CF092B71F3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2163 |  | 2015-10-13 | 2015-10-13 15:55 | 2015-10-13 15:55 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 23.6 | 22.6 | 1 | 467B36E1545E47B08DEFBA2774508DE2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1654 |  | 2015-10-15 | 2015-10-15 09:14 | 2015-10-15 09:14 | RHEEM - UKNOWN | 61 | 0 | Yes | Yes | 18.9 | 21.7 | -2.7 | 68EA1C0EA6AA47F0893CC8FCB7AE62D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3342 |  | 2015-10-16 | 2015-10-16 09:12 | 2015-10-16 09:12 | GOODMAN - CK36-1A | 73 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | B8FF9EF348FE4062A093609A0E10647B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1708 |  | 2015-09-02 | 2015-09-02 11:19 | 2015-09-02 11:19 | RUUD - UAKA-024JAZ | 50 | 0 | Yes | Yes | 18.7 | 19.5 | -0.8 | BBB076578CAC46AC905E3B99F2FB8F8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3315 |  | 2015-09-18 | 2015-09-18 11:06 | 2015-09-18 11:06 | CARRIER - 38HDC036-321 | 83 | 0 | Yes | Yes | 16.7 | 18.4 | -1.7 | F0F035DA070B43E08E6BCEDAAC3B6C85 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5797 |  | 2015-09-24 | 2015-09-24 09:26 | 2015-09-24 09:26 | OTHER - UNKNOWN | 96 | 0 | Yes | Yes | 20.5 | 22.6 | -2.1 | 9AC70DDB4C0D41DA9D1A0E6EB0195200 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-2559 |  | 2015-10-08 | 2015-10-08 13:20 | 2015-10-08 13:20 | LENNOX - 10ACB36-12P | 80 | 0 | Yes | Yes | 21.9 | 22 | -0.1 | 824128A147694003813AE91E1A8F3295 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6505 |  | 2015-10-01 | 2015-10-01 13:42 | 2015-10-01 13:42 | TRANE - 2TTB3036A1000AA | 101 | 0 | Yes | Yes | 18.7 | 19.8 | -1.1 | 11CB99E5DE6E4E60BC68938BF5E6A476 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2909 |  | 2015-09-18 | 2015-09-18 13:31 | 2015-09-18 13:56 | OTHER - UNKNOWN | 56 | 0 | Yes | Yes | 24.8 | 20.7 | 4.1 | 51BBDBB71D3F4A3FA2D5FDF6FADBD244 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2045 |  | 2015-10-28 | 2015-10-28 15:32 | 2015-10-28 15:32 | TRANE - UNKNOWN | 106 | 0 | Yes | Yes | 22.2 | 20.8 | 1.4 | C88FF5D62F56494FB6355242F046BEA6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5563 |  | 2015-09-28 | 2015-09-28 15:10 | 2015-09-28 15:28 | BDP - 585CJ030075 | 78 | 9.9 | Yes | Yes | 23.1 | 20.2 | 2.9 | D981863E37B442DE84B303EB1ED68886 |  | R22 | Non-TXV |  | 12.69% | 0.87308 | 24.39% | [5 empty] | Non-TXV | 12.69%
Brentwood | CA | 94513-6356 |  | 2015-09-03 | 2015-09-03 09:37 | 2015-09-03 09:37 | CARRIER - 38CKC036350 | 74 | 0 | Yes | Yes | 17.3 | 19.8 | -2.5 | 4EB3B4EFCB3047BDB249BA3AE921FF95 |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-6937 |  | 2015-09-09 | 2015-09-09 10:51 | 2015-09-09 10:51 | TRANE - 4TTX49024000 | 82 | 0 | Yes | Yes | 23.6 | 18.8 | 4.8 | 3CF6FA7AC2C240B398C0AAF75C28531B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1910 |  | 2015-09-14 | 2015-09-14 16:32 | 2015-09-14 16:32 | BRYANT - 561CJO60H | 135 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | 6FC63321280245CFB57D4BDA442C1B3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-8549 |  | 2015-11-11 | 2015-11-11 09:04 | 2015-11-11 09:04 | LENNOX - GCX29X-036-7-1PA | 58 | 0 | Yes | Yes | 23.7 | 18.2 | 5.5 | 28A33D1FDC414CE29F1DEEA0DB352688 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2033 |  | 2015-10-22 | 2015-10-22 11:47 | 2015-10-22 11:47 | ALLEGIANCE - 7A2048A100A1 | 149 | 0 | Yes | Yes | 21.9 | 21.3 | 0.6 | FECE6159024C472E9A2091BDE855A233 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-1513 |  | 2015-10-02 | 2015-10-02 08:28 | 2015-10-02 08:49 | BRYANT - 582ANW030060AAAD | 55 | -6 | Yes | Yes | 21.4 | 17.7 | 3.7 | 0FDAEFB321CF40A8BB095FA1FB689EB3 |  | R22 | TXV |  | -10.91% | 1.1091 | 3.055% |  |  |  |  | TXV |  |  | -10.91%
Fairfield | CA | 94533-0000 |  | 2015-09-10 | 2015-09-10 17:11 | 2015-09-10 17:11 | PAYNE - 591AANX060000AAAA | 85 | 0 | Yes | Yes | 18.6 | 19 | -0.4 | 49949C16921B450BB86A8F035E615031 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-0000 |  | 2015-10-14 | 2015-10-14 09:28 | 2015-10-14 09:28 | LENNOX - 10GCS036-75-3PB | 58 | 0 | Yes | Yes | 22.1 | 19.3 | 2.8 | 7E73130525B44DB6898F4CEA111831FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7092 |  | 2015-09-17 | 2015-09-17 12:35 | 2015-09-17 12:35 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 20.3 | 21.3 | -1 | 6FD00C37BE834E0C9D7ED9B0BD7E9C66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5064 |  | 2015-10-15 | 2015-10-15 15:03 | 2015-10-15 15:23 | CARRIER - 38CKC048360 | 109 | 16.5 | Yes | Yes | 21.8 | 20.2 | 1.6 | 81E497E3B9CC4F0CBD06F088A7209129 |  | R22 | TXV |  | 15.14% | 0.84862 | 29.09% | [5 empty] | TXV | 15.14%
Brentwood | CA | 94513-5064 |  | 2015-10-15 | 2015-10-15 15:27 | 2015-10-15 15:27 | CARRIER - 38CKCO48360 | 109 | 0 | Yes | Yes | 20.6 | 21 | -0.4 | 65ED3DEF1CB5441A9D1B7E97B2B25545 |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-1415 |  | 2015-10-22 | 2015-10-22 10:40 | 2015-10-22 10:40 | RHEEM - RAKA-048JAZ | 103 | 0 | Yes | Yes | 26.7 | 22.2 | 4.5 | 8B98DCC6F012493298662573036E8B70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:36 | 2015-10-13 15:36 | NORDYNE - JS6BD-030K | 134 | 0 | Yes | Yes | 20.8 | 22.6 | -1.8 | F2540B19A49A40C7A4002A79A35383F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4756 |  | 2015-10-14 | 2015-10-14 10:25 | 2015-10-14 10:25 | CARRIER - 48SDN03600311 | 130 | 0 | Yes | Yes | 25.5 | 20.4 | 5.1 | B257EC2604614C3E9FEB2D0A211FC05C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2155 |  | 2015-10-13 | 2015-10-13 15:45 | 2015-10-13 15:45 | NORDYNE - JS6BD-030K | 134 | 0 | Yes | Yes | 21.9 | 22.6 | -0.7 | B1C3E79406244D40BF36927C598AC3BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6396 |  | 2015-09-18 | 2015-09-18 11:45 | 2015-09-18 11:45 | AMERICAN STANDARD - | 85 | 0 | Yes | Yes | 18.1 | 19.8 | -1.7 | 62D87590C11A40B48D625EB928D45188 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95126-4242 |  | 2015-11-02 | 2015-11-02 09:48 | 2015-11-02 09:48 | RHEEM - AT-18B10 | 34 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | 73A4471B55AB445481574C4DF68E72E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2558 |  | 2015-09-09 | 2015-09-09 14:42 | 2015-09-09 14:42 | CARRIER - 563CNX042-A | 85 | 0 | Yes | Yes | 21.6 | 18.3 | 3.4 | A4448A6672334551A31F3300BDD5B452 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3455 |  | 2015-10-13 | 2015-10-13 15:12 | 2015-10-13 15:12 | CARRIER - 58HJO42060 | 81 | 0 | Yes | Yes | 20.2 | 22 | -1.8 | C3D13AF32A75424CB6AACEB3E9EB4EF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5175 |  | 2015-09-22 | 2015-09-22 15:39 | 2015-09-22 15:39 | CARRIER - 38QRR036 | 197 | 0 | Yes | Yes | 16.7 | 19.3 | -2.6 | E04E53900C5040B4AE036FAE20EE0D81 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95125-4308 |  | 2015-10-29 | 2015-10-29 10:36 | 2015-10-29 10:36 | LENNOX - 12ACB30-2P | 104 | 0 | Yes | Yes | 21.4 | 21 | 0.4 | 75E608B21B3546CD9210A51A0162874C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5174 |  | 2015-09-22 | 2015-09-22 16:27 | 2015-09-22 16:27 | CARRIER - 38QRR024-3 | 112 | 0 | Yes | Yes | 19.4 | 16.4 | 3 | 1BF306BDB190433EB3DAB74A8E97560E |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1728 |  | 2015-09-21 | 2015-09-21 10:34 | 2015-09-21 11:04 | BDP - 585A042100YAC | 85 | 7.5 | Yes | Yes | 21.6 | 23.6 | -2 | 92247DFEAC1F4FF19FE5BBC0A42058A7 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Esparto | CA | 95627-2172 |  | 2015-10-27 | 2015-10-27 09:54 | 2015-10-27 09:54 | TRANE - 2TTB2036A1000AA | 96 | 0 | Yes | Yes | 16.9 | 15.9 | 1 | AC91A58790024FBFB8B2DFEE2CE8AD13 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7772 |  | 2015-09-21 | 2015-09-21 13:38 | 2015-09-21 13:38 | CARRIER - UNK | 85 | 0 | Yes | Yes | 20.8 | 17.7 | 3.1 | 13F069A45BF9476DA27EAC44E1E99E4D |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-4105 |  | 2015-09-25 | 2015-09-25 12:53 | 2015-09-25 12:53 | ARCOAIRE - PGAA24B1K5 | 66 | 0 | Yes | Yes | 20.5 | 19.6 | 0.9 | E6038359FD8A43C9AD62EAFBD43F6B84 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-2236 |  | 2015-09-24 | 2015-09-24 16:04 | 2015-09-24 16:04 | TRANE - 4TTR2036A1000AA | 78 | 0 | Yes | Yes | 20.3 | 16.8 | 3.5 | E1EC4E62B34543C19E9EABB09A25E700 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2172 |  | 2015-10-27 | 2015-10-27 09:23 | 2015-10-27 09:23 | GOODMAN - CK42-1C | 92 | 0 | Yes | Yes | 21.2 | 20.2 | 1 | 851FC29E50D544EAA0E3B88BFCABEA96 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7312 |  | 2015-09-17 | 2015-09-17 10:02 | 2015-09-17 10:02 | OTHER - N/A | 85 | 0 | Yes | Yes | 18.6 | 19.5 | -0.9 | 8E21BC8C7122466BA379CED04EC54CF2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6866 |  | 2015-11-06 | 2015-11-06 09:26 | 2015-11-06 09:26 | GOODMAN - GP134809014MEA | 153 | 0 | Yes | Yes | 26.4 | 20.7 | 5.7 | F243C24504914A6292D6C690C0B25D4A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2045 |  | 2015-10-14 | 2015-10-14 12:51 | 2015-10-14 12:51 | CARRIER - 24ABA336A310 | 84 | 0 | Yes | Yes | 22.5 | 21.4 | 1.1 | 8D1FFDC17DCC4BC3BB232769780A1891 |  | R410A | TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-2231 |  | 2015-09-24 | 2015-09-24 12:10 | 2015-09-24 12:10 | PAYNE - PY3GNA36060NA | 100 | 0 | Yes | Yes | 20.1 | 19.8 | 0.3 | 64218FF1E49E4EE88FEC32EB3CEB237A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2133 |  | 2015-10-09 | 2015-10-09 10:05 | 2015-10-09 10:05 | PAYNE - UNK | 85 | 0 | Yes | Yes | 16.3 | 19.3 | -3 | 425A9576CB71457C8324DBEC18DA1CCB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3617 |  | 2015-09-10 | 2015-09-10 10:07 | 2015-09-10 10:07 | TAPPAN - CM 30 44 C | 60 | 0 | Yes | Yes | 26.5 | 24.8 | 1.7 | 3695E4240B284F638BFDE58356D3140A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1344 |  | 2015-09-18 | 2015-09-18 12:11 | 2015-09-18 12:11 | PAYNE - PA10J024-A | 68 | 0 | Yes | Yes | 19.1 | 15.9 | 3.2 | 242B53BEA025477E97C0E40AC0B21505 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1618 |  | 2015-09-25 | 2015-09-25 13:05 | 2015-09-25 13:05 | GOODMAN - GSC130301AE | 117 | 0 | Yes | Yes | 18.1 | 19.9 | -1.8 | 4F273D1323894C6DBA258EAC15DA8FF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2163 |  | 2015-10-13 | 2015-10-13 15:52 | 2015-10-13 15:52 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.8 | 22.6 | -1.8 | 333378B730BD4EC0A56DFE298B75C21A |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-0000 |  | 2015-11-05 | 2015-11-05 15:04 | 2015-11-05 15:04 | OTHER - 593CJ060-A | 133 | 0 | Yes | Yes | 19.8 | 20 | -0.2 | DB8BD00B3A494B52B69BB94FE781A098 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1401 |  | 2015-09-24 | 2015-09-24 14:41 | 2015-09-24 15:05 | KENMORE - CA5036VKA1 | 105 | 30.8 | Yes | Yes | 26.1 | 22.5 | 3.6 | DED97F919B0B41C29967433F9104DB3C |  | R22 | Non-TXV |  | 29.33% | 0.70667 | 56.37% | [5 empty] | Non-TXV | 29.33%
Bakersfield | CA | 93306-5070 |  | 2015-09-15 | 2015-09-15 09:54 | 2015-09-15 10:22 | ARCOAIRE - ACS048A2B2 | 101 | 4.2 | Yes | Yes | 21.4 | 21 | 0.4 | DCFDBC273B5B4C5CB5FF192D87605DCB |  | R22 | Non-TXV |  | 4.158% | 0.95842 | 7.992% | [5 empty] | Non-TXV | 4.158%
Woodland | CA | 95695-9324 |  | 2015-10-12 | 2015-10-12 16:31 | 2015-10-12 16:31 | PAYNE - PH13B036 | 85 | 0 | Yes | Yes | 17.5 | 20.4 | -2.9 | 6144D7CBD60A4F168119F65D8223ED6D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6367 |  | 2015-09-15 | 2015-09-15 10:27 | 2015-09-15 10:27 | CARRIER - 38CK11152C048370 | 100 | 0 | Yes | Yes | 21 | 18.2 | 2.8 | FD002A91D0F946BB8E2504C513877C7A |  | R22 | TXV |  | 0% | 1 | 0%
Concord | CA | 94519-1717 |  | 2015-09-18 | 2015-09-18 12:56 | 2015-09-18 12:56 | TRANE - 2TTR4036A10000AA | 118 | 0 | Yes | Yes | 15.6 | 18.2 | -2.6 | ACF7EDBB9FD244C4AA5AD7BE17A1CF37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7224 |  | 2015-09-18 | 2015-09-18 11:52 | 2015-09-18 12:37 | - 24ABB348W310 | 85 | 10.8 | Yes | Yes | 19.8 | 18.5 | 1.4 | 0C1988ED43514C9AABE2C15D58EDB5B4 |  | R22 | Non-TXV |  | 12.71% | 0.87294 | 24.42% | [5 empty] | Non-TXV | 12.71%
Concord | CA | 94521-3606 |  | 2015-09-24 | 2015-09-24 14:38 | 2015-09-24 14:38 | GOODMAN - CK30-IT | 76 | 0 | Yes | Yes | 21.9 | 22.5 | -0.5 | FDB777654A8A431283F853A93F1316D8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4359 |  | 2015-11-09 | 2015-11-09 09:32 | 2015-11-09 09:32 | GOODMAN - PGB0240501 | 54 | 0 | Yes | Yes | 26.6 | 21 | 5.6 | B8B5A17FC0AF48E292A8ABCE310D30B1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94590-7130 |  | 2015-10-02 | 2015-10-02 09:21 | 2015-10-02 09:21 | AMERICAN STANDARD - YCC036F1LOBK | 85 | 0 | Yes | Yes | 21.6 | 18.7 | 2.9 | C08532C109344350B04C12D5FAED7BE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4241 |  | 2015-10-16 | 2015-10-16 12:06 | 2015-10-16 12:06 | YORK - D1NH036N05606C | 97 | 0 | Yes | Yes | 18.5 | 20.9 | -2.4 | 6B64E17E90174864A8E69DF66D56BCB8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4872 |  | 2015-10-16 | 2015-10-16 13:11 | 2015-10-16 13:11 | OTHER - 38TH036300 | 84 | 0 | Yes | Yes | 21.3 | 23.1 | -1.8 | 0EE1DF7D7EFF430E8ABBB65F24535BBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1605 |  | 2015-09-21 | 2015-09-21 09:02 | 2015-09-21 09:21 | BARD - | 85 | 15.3 | Yes | Yes | 19.1 | 18.5 | 0.7 | C33465E1A91A409590E856375083B787 |  | R22 | Non-TXV |  | 18% | 0.82 | 34.59% | [5 empty] | Non-TXV | 18%
Brentwood | CA | 94513-4118 |  | 2015-09-14 | 2015-09-14 13:16 | 2015-09-14 13:16 | OTHER - 38CKC048 371 | 105 | 0 | Yes | Yes | 24.8 | 21.3 | 3.5 | 2DC6A0CCF15848BCB01DF29FC8B3C4A7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7021 |  | 2015-10-07 | 2015-10-07 12:04 | 2015-10-07 12:04 | GOODMAN - GPG13480701AC | 143 | 0 | Yes | Yes | 20.9 | 18.9 | 2 | E426C5ED40C6405984D3C1B05C16622D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1438 |  | 2015-11-11 | 2015-11-11 12:18 | 2015-11-11 12:18 | BRYANT - 563CN36 | 85 | 0 | Yes | Yes | 23.5 | 19.7 | 3.8 | 7088A0BA5E5445B491BDB3DF35BAB4C1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5786 |  | 2015-09-17 | 2015-09-17 10:28 | 2015-09-17 10:28 | CARRIER - 24ABB32A300 | 80 | 0 | Yes | Yes | 20.4 | 18.7 | 1.7 | F36A08568A02414F85E659F608DE23D7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-0000 |  | 2015-11-03 | 2015-11-03 10:43 | 2015-11-03 10:43 | CARRIER - 48SDN036060301 | 167 | 0 | Yes | Yes | 23.5 | 19.7 | 3.8 | A824BEB12EAB407A9FE035D50D9DEA68 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6040 |  | 2015-09-16 | 2015-09-16 16:02 | 2015-09-16 16:02 | CARRIER - 3BRC048320 | 167 | 0 | Yes | Yes | 23.9 | 19.9 | 4 | 610AE64074A94F3C88397C53D3CDC925 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7480 |  | 2015-11-05 | 2015-11-05 14:07 | 2015-11-05 14:07 | RUUD - H20A036906A | 92 | 0 | Yes | Yes | 23 | 19.4 | 3.7 | F0D689F1CE5F416C87779680F25E2376 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Byron | CA | 94514-9380 |  | 2015-10-19 | 2015-10-19 10:22 | 2015-10-19 10:22 | BRYANT - 187BNA048-B | 207 | 0 | Yes | Yes | 19.5 | 17.7 | 1.8 | A2CDF0FE6419470C8161131D3402962E |  | R410A | TXV |  | 0% | 1 | 0%
Byron | CA | 94514-9380 |  | 2015-10-19 | 2015-10-19 10:47 | 2015-10-19 10:47 | BRYANT - 187BNA048-B | 207 | 0 | Yes | Yes | 20.1 | 17.2 | 2.9 | 9683C31A56EB439FB4A6BDB4165173D5 |  | R410A | TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-5017 |  | 2015-09-11 | 2015-09-11 09:29 | 2015-09-11 09:29 | LENNOX - 13ACX-048-230-1 | 153 | 0 | Yes | Yes | 19.5 | 17.7 | 1.8 | A6102DBC77C84ABFABE51CF936577DEB |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1143 |  | 2015-10-14 | 2015-10-14 12:16 | 2015-10-14 12:16 | DAY & NIGHT - 588ANW0300440AAD | 52 | 0 | Yes | Yes | 20.3 | 18.2 | 2.1 | DB30528FFEDE406A92BDE9814B59693F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-3002 |  | 2015-09-16 | 2015-09-16 09:59 | 2015-09-16 09:59 | OTHER - UNK | 76 | 0 | Yes | Yes | 21.1 | 18.7 | 2.4 | 1AFF05BD5DF248D299570E0B9F67D387 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5111 |  | 2015-09-21 | 2015-09-21 15:30 | 2015-09-21 15:30 | OTHER - 38QRR036 | 197 | 0 | Yes | Yes | 19.3 | 17 | 2.3 | BA9F582E324F4EA38FCA3EF6D425E807 |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2310 |  | 2015-10-15 | 2015-10-15 15:30 | 2015-10-15 15:30 | GMC - CK36-189801429930 | 74 | 0 | Yes | Yes | 25.6 | 19.9 | 5.7 | EF238862A0794B3980F64CDC9AB6203C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1211 |  | 2015-09-29 | 2015-09-29 11:44 | 2015-09-29 11:44 | UNITARY PRODUCTS GROUP - H2RA036SO6G | 63 | 0 | Yes | Yes | 25.5 | 20.3 | 5.2 | C42F4435C4024BCB80AAC3E741A53BFB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6947 |  | 2015-09-10 | 2015-09-10 13:36 | 2015-09-10 13:58 | YORK - H2RC024S06A | 71 | 7 | Yes | Yes | 17.7 | 20.4 | -2.7 | 174E070DBEA74843B410B1D3F58671EF |  | R22 | Non-TXV |  | 9.859% | 0.90141 | 18.95% | [5 empty] | Non-TXV | 9.859%
Pittsburg | CA | 94565-2365 |  | 2015-09-10 | 2015-09-10 14:11 | 2015-09-10 14:11 | CARRIER - 38TDA036 301 | 184 | 0 | Yes | Yes | 24 | 19.9 | 4.1 | B64471C9D5D245A1ACEA6290CE8F26CC |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5493 |  | 2015-09-28 | 2015-09-28 08:40 | 2015-09-28 08:40 | TRANE - 2TTB3030A1000AA | 88 | 0 | Yes | Yes | 21.8 | 22.9 | -1.1 | F3701C34619948D39A703D19930D6F1A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-7012 |  | 2015-11-18 | 2015-11-18 11:41 | 2015-11-18 11:41 | RHEEM - UNK | 85 | 0 | Yes | Yes | 21.8 | 19.9 | 1.9 | F55723B06DBD473FB3B49C19330A3BEE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3049 |  | 2015-11-06 | 2015-11-06 08:47 | 2015-11-06 08:47 | CONCORD - 13ACD06023013 | 85 | 0 | Yes | Yes | 23.9 | 23.1 | 0.8 | 73D644BE162B4086B1F55BF8C2AABC62 |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-4935 |  | 2015-10-26 | 2015-10-26 13:01 | 2015-10-26 13:01 | AMERICAN STANDARD - YCP042F1M0B | 85 | 0 | Yes | Yes | 22.7 | 17.9 | 4.8 | 527FA76BE9644EFFB0BA754ED195A5CE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2351 |  | 2015-09-17 | 2015-09-17 11:02 | 2015-09-17 11:02 | RHEEM - UNNOWN | 109 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | 08B1CB04733A49C8960D757DA4234345 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-1823 |  | 2015-11-09 | 2015-11-09 10:53 | 2015-11-09 10:53 | ARCOAIRE - HAC230AKA01 | 80 | 0 | Yes | Yes | 21.5 | 17 | 4.5 | A98FB4EE3F5E4DD9B1DC666D426ECA74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:42 | 2015-10-13 14:43 | NORDYNE - JS5BD-024K | 104 | 15.8 | Yes | Yes | 16.1 | 19.1 | -3 | EEE79DD2702243A1BCDE6AC1F860A1D0 |  | R22 | Non-TXV |  | 15.19% | 0.84808 | 29.2% | [5 empty] | Non-TXV | 15.19%
Brentwood | CA | 94513-1473 |  | 2015-09-10 | 2015-09-10 12:07 | 2015-09-10 12:07 | DAY & NIGHT - 567CJ036 | 82 | 0 | Yes | Yes | 27 | 21.5 | 5.5 | 803C614B679F4EB9A4D69BFC49BFB129 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8493 |  | 2015-10-15 | 2015-10-15 08:02 | 2015-10-15 08:02 | CARRIER - 38CKC042300 | 80 | 0 | Yes | Yes | 18.3 | 20.4 | -2.1 | 7724F007BFED49DFA0C4FC6645DDBD40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7275 |  | 2015-09-21 | 2015-09-21 10:19 | 2015-09-21 10:41 | TRANE - TTR742A100A0 | 138 | -9.7 | Yes | Yes | 20.8 | 19.1 | 1.7 | 7E9B5F1B9BBD4F439E49804FE0A7C454 |  | R22 | Non-TXV |  | -7.029% | 1.0703 | 1.968% |  |  |  |  | Non-TXV |  |  | -7.029%
Fresno | CA | 93727-3573 |  | 2015-10-09 | 2015-10-09 11:03 | 2015-10-09 11:03 | CARRIER - 585HJW042060ABAF | 80 | 0 | Yes | Yes | 19.1 | 21.7 | -2.6 | C7AD297ED724463C97F9D535A9E14D3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2160 |  | 2015-10-26 | 2015-10-26 11:11 | 2015-10-26 11:33 | TRANE - 4TTX4048A1000AA | 127 | 13.3 | Yes | Yes | 18.7 | 19.1 | -0.4 | 02A87D8E15F748B187C4D10815BF14AC |  | R410A | Non-TXV |  | 10.47% | 0.89528 | 20.13% | [5 empty] | Non-TXV | 10.47%
Clovis | CA | 93612-3321 |  | 2015-09-16 | 2015-09-16 09:46 | 2015-09-16 09:46 | HEIL - PGAA36C1K4 | 69 | 0 | Yes | Yes | 22.8 | 19.5 | 3.3 | F4775577A27141429BDFB4D6BDF64302 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93619-8345 |  | 2015-10-16 | 2015-10-16 08:39 | 2015-10-16 08:39 | BRYANT - 563CNO48-C | 164 | 0 | Yes | Yes | 19.7 | 19.3 | 0.4 | 1E133168E2FD4B35B3520AA10736723F |  | R22 | TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-9624 |  | 2015-09-16 | 2015-09-16 13:35 | 2015-09-16 13:35 | TEMPSTAR - N4A342AKA300 | 88 | 0 | Yes | Yes | 17.8 | 18.7 | -0.9 | 048B5C848C284667A41969DDC0C92BD3 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5493 |  | 2015-10-01 | 2015-10-01 12:27 | 2015-10-01 12:27 | NORDYNE - FS3BC-048KA | 110 | 0 | Yes | Yes | 23.3 | 23.7 | -0.4 | 6291A3B27FD840B58A76197978E8008F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2085 |  | 2015-09-15 | 2015-09-15 09:51 | 2015-09-15 09:51 | CARRIER - 38CKC018320 | 68 | 0 | Yes | Yes | 21.4 | 19.1 | 2.4 | 8F670EBD0A444CF2863F908AEB820E6E |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9078 |  | 2015-09-29 | 2015-09-29 13:49 | 2015-11-09 11:00 | LENNOX - 10GCS042X-75-3PA | 73 | 0 | Yes | Yes | 19.1 | 19.8 | -0.7 | B47619D890F44FA8A4567E75645BEEBA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5787 |  | 2015-09-21 | 2015-09-21 14:08 | 2015-09-21 14:27 | CARRIER - 38TKO48310 | 85 | 7.9 | Yes | Yes | 24.6 | 25.1 | -0.5 | 5D8355B12E4446EEB2FB79F6FE7ADC1B |  | R22 | Non-TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | Non-TXV | 9.294%
San Jose | CA | 95148-2032 |  | 2015-11-05 | 2015-11-05 15:10 | 2015-11-05 15:10 | ICP - N2A348AKA300 | 121 | 0 | Yes | Yes | 27.2 | 22.3 | 4.9 | DBE64CFA02D64F5C88C85A5966B1070C |  | R22 | TXV |  | 0% | 1 | 0%
Martinez | CA | 94553-4715 |  | 2015-09-24 | 2015-09-24 12:01 | 2015-09-24 12:01 | GOODMAN - GSX160601FA | 290 | 0 | Yes | Yes | 20.5 | 19.9 | 0.6 | 03962E2C67C744A89BACB2220C851713 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1732 |  | 2015-09-22 | 2015-09-22 14:47 | 2015-09-22 14:47 | OTHER - UNKNOWN | 76 | 0 | Yes | Yes | 19.7 | 19.6 | 0.2 | 9A637D39F6A14AD09E4A3B274F9D50BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-3410 |  | 2015-11-05 | 2015-11-05 10:39 | 2015-11-05 10:39 | TRANE - 4TTX4036B1000AA | 91 | 0 | Yes | Yes | 17.7 | 20.4 | -2.7 | 886C40763C324FACB42412D2EEFCF639 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2926 |  | 2015-09-22 | 2015-09-22 11:18 | 2015-09-22 11:18 | CARRIER - 38TFEO36300 | 121 | 0 | Yes | Yes | 21.8 | 19.4 | 2.4 | F9440742BAAF4A1FAF366EE90835A2AF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-2262 |  | 2015-09-21 | 2015-09-21 13:42 | 2015-09-21 13:42 | PAYNE - PA10JAO18-A | 85 | 0 | Yes | Yes | 15.2 | 17.9 | -2.7 | 672CE26E9CED42F595FA621692D21540 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3331 |  | 2015-10-30 | 2015-10-30 11:36 | 2015-10-30 11:37 | YORK - D1NA030N05606C | 76 | 14.3 | Yes | Yes | 19.9 | 20.4 | -0.5 | DBC106C9D23943C7BB34F2857E0E16EB |  | R22 | Non-TXV |  | 18.82% | 0.81184 | 36.16% | [5 empty] | Non-TXV | 18.82%
Dixon | CA | 95620-3627 |  | 2015-09-24 | 2015-09-24 12:46 | 2015-09-24 12:46 | PAYNE - UNK | 85 | 0 | Yes | Yes | 18.7 | 18.6 | 0.1 | 2BF06F30957B44AB8AE53EAC18E98EE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-3011 |  | 2015-09-28 | 2015-09-28 12:09 | 2015-09-28 12:09 | RHEEM - RRNLB036JK06X | 92 | 8.7 | Yes | Yes | 20.2 | 17.7 | 2.5 | 1ECE64B2924F4E5FA512AA001CED6841 | Add refrigerant: 8.7 oz | R410A | Non-TXV |  | 9.457% | 0.90543 | 18.17% | [5 empty] | Non-TXV | 9.457%
Fresno | CA | 93711-2907 |  | 2015-09-22 | 2015-09-22 10:49 | 2015-09-22 10:49 | TRANE - 2YCC3048A1075AA | 144 | 0 | Yes | Yes | 22.5 | 18.5 | 4 | 87FC70B58BA14014A4788DD4A410A236 |  | R22 | TXV |  | 0% | 1 | 0%
Esparto | CA | 95627-2100 |  | 2015-10-14 | 2015-10-14 10:54 | 2015-10-14 10:54 | AMANA - UNK | 138 | 0 | Yes | Yes | 23.9 | 18.8 | 5.1 | 541A845E210B45E6A8188568B91991D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2932 |  | 2015-09-15 | 2015-09-15 09:47 | 2015-09-15 09:47 | TRANE - WCX036A100BB | 148 | 0 | Yes | Yes | 23.7 | 18.1 | 5.6 | 84EC43222E9040309E52A2D0BD93FA60 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7002 |  | 2015-09-17 | 2015-09-17 10:50 | 2015-09-17 10:50 | PAYNE - PY3PNA036060NB | 116 | 0 | Yes | Yes | 21.6 | 19.8 | 1.8 | 4FF1F330B9C441D5BA0F80E352A7EA43 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2925 |  | 2015-09-15 | 2015-09-15 15:44 | 2015-09-15 15:44 | WESTINGHOUSE - FS4BF036K | 100 | 0 | Yes | Yes | 22.9 | 17 | 5.9 | DEE73DC6351D4C7EB57ED4D2447E94BD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5270 |  | 2015-10-01 | 2015-10-01 14:19 | 2015-10-01 14:57 | YORK - H2RD060S06A | 162 | 21.2 | Yes | Yes | 20.6 | 22.3 | -1.7 | D047F7FC51F44C3E86A8175541521547 |  | R22 | Non-TXV |  | 13.09% | 0.86914 | 25.15% | [5 empty] | Non-TXV | 13.09%
Brentwood | CA | 94513-6560 |  | 2015-09-16 | 2015-09-16 15:35 | 2015-09-16 15:35 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 18.2 | 21 | -2.8 | EE88677E8526453D8F7252FD4F5E1FD1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1763 |  | 2015-10-13 | 2015-10-13 10:04 | 2015-10-13 10:04 | CARRIER - 38THO36300 | 83 | 0 | Yes | Yes | 22.6 | 18.2 | 4.4 | F9F0B16E692C4F65A6052A5287672A45 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2755 |  | 2015-09-17 | 2015-09-17 10:12 | 2015-09-17 10:12 | CARRIER - 38CKC042310 | 93 | 0 | Yes | Yes | 20.7 | 17.7 | 3 | 487F83DED3E14CE9A925C30B6B85B329 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-0000 |  | 2015-09-21 | 2015-09-21 11:03 | 2015-09-21 11:03 | YORK - ERCS0421BBA | 141 | 0 | Yes | Yes | 21.3 | 23.7 | -2.4 | A7F6C449FDF748D2BEF77786A3BE831D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Walnut Creek | CA | 94598-2923 |  | 2015-10-14 | 2015-10-14 09:49 | 2015-10-14 10:26 | COLEMAN - BRCS0361BDG | 62 | 8.3 | Yes | Yes | 18.2 | 19.4 | -1.2 | 5CB35D2EDDE04D5EA4D67AE1FCFF91AC |  | R22 | Non-TXV |  | 13.39% | 0.86613 | 25.73% | [5 empty] | Non-TXV | 13.39%
Bakersfield | CA | 93307-2710 |  | 2015-09-16 | 2015-09-16 15:00 | 2015-09-16 15:00 | YORK - D6NZ042N06506NXA | 78 | 0 | Yes | Yes | 23 | 20.7 | 2.3 | 3BAECAC9D33D481E802C64B4EC23EB9E |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7505 |  | 2015-09-15 | 2015-09-15 15:56 | 2015-09-15 15:56 | OTHER - N/A | 85 | 0 | Yes | Yes | 19.5 | 20.2 | -0.7 | 1480E68F84274FD4A14D873A1FB0224B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-5964 |  | 2015-10-14 | 2015-10-14 14:30 | 2015-10-14 14:30 | GOODMAN - GPG1324045M41AB | 80 | 0 | Yes | Yes | 21.3 | 19 | 2.3 | 7699DB002B114CE6A9287AA214A13266 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1120 |  | 2015-11-09 | 2015-11-09 08:50 | 2015-11-09 09:10 | LENNOX - 1GCS036X756PB | 104 | 25.9 | Yes | Yes | 19.5 | 19.2 | 0.3 | B3CD5AA479804F96993C8EA6593413BD |  | R22 | Non-TXV |  | 24.9% | 0.75096 | 47.86% | [5 empty] | Non-TXV | 24.9%
Lafayette | CA | 94549-2016 |  | 2015-10-19 | 2015-10-19 13:44 | 2015-10-19 13:44 | BDP - 5658J024 | 70 | 0 | Yes | Yes | 25.3 | 21.4 | 3.9 | 54489A3EBBD249F88032563EEC8A83BE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4133 |  | 2015-09-15 | 2015-09-15 12:05 | 2015-09-15 14:17 | YORK - D6NZ048N06506NXA | 72 | 22.3 | Yes | Yes | 22 | 22.9 | -0.9 | 4DBCF52FD32E4F009CC17A92F1C6DB2B |  | R410A | Non-TXV |  | 30.97% | 0.69028 | 59.52% | [5 empty] | Non-TXV | 30.97%
Hercules | CA | 94547-3832 |  | 2015-11-03 | 2015-11-03 10:52 | 2015-11-03 10:52 | TRANE - BTD718A | 36 | 0 | Yes | Yes | 19.5 | 19.5 | 0 | 038E841D405544BDB9A243DDBDFEA149 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2131 |  | 2015-09-21 | 2015-09-21 11:32 | 2015-09-21 11:32 | TRANE - 2TTR3048A1000AA | 142 | 0 | Yes | Yes | 22.6 | 19.8 | 2.8 | 62C2535CAF544EF882D0C541798BC8CC |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7205 |  | 2015-09-09 | 2015-09-09 11:10 | 2015-09-09 11:10 | LENNOX - HS320361P | 126 | 0 | Yes | Yes | 21.5 | 18.3 | 3.2 | 7A456FCF8DA144DAAB5D9609C92C2A16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3768 |  | 2015-09-17 | 2015-09-17 13:29 | 2015-09-17 13:29 | OTHER - BWD718A100B0 | 88 | 0 | Yes | Yes | 18 | 19.3 | -1.3 | CCF6CD1129A842D9BE7CA638C6F7BF70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-4809 |  | 2015-09-28 | 2015-09-28 12:21 | 2015-09-28 12:21 | CARRIER - 38CKG060370 | 85 | 0 | Yes | Yes | 18.1 | 17.8 | 0.3 | 1C03BAC2426B4A4C9E53235F4761CC70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4967 |  | 2015-10-24 | 2015-10-24 12:29 | 2015-10-24 12:29 | GMC - CKJ36-1B | 102 | 0 | Yes | Yes | 15 | 18 | -3 | 205DB374B8DB451896E0583F7B954A16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6655 |  | 2015-09-24 | 2015-09-24 09:54 | 2015-09-24 10:33 | PAYNE - PY3GNAA36060NA | 102 | 8.6 | Yes | Yes | 22.2 | 20.3 | 1.9 | 1C92133AA27B4EBF8AEF393762BF2DB4 |  | R22 | Non-TXV |  | 8.431% | 0.91569 | 16.2% | [5 empty] | Non-TXV | 8.431%
Clovis | CA | 93619-0434 |  | 2015-09-11 | 2015-09-11 15:29 | 2015-09-11 15:58 | LENNOX - 13ACD-048-230-03 | 152 | 9.3 | Yes | Yes | 19.4 | 21.5 | -2.1 | 131EFEEF48E04881942707B102CB87CD |  | R22 | TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | TXV | 6.118%
Fresno | CA | 93706-1809 |  | 2015-10-09 | 2015-10-09 09:33 | 2015-10-09 09:33 | YORK - D1NH024N05606C | 66 | 0 | Yes | Yes | 21.7 | 16.6 | 5.1 | 419B03D6081848FC8EAEC1F9E0284352 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-7449 |  | 2015-09-15 | 2015-09-15 15:25 | 2015-09-15 15:25 | GOODMAN - GSC130481AE | 152 | 0 | Yes | Yes | 21.5 | 23.4 | -1.9 | AF317498039B4D8B81DA0FCCEE5A9B37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3645 |  | 2015-10-13 | 2015-10-13 11:38 | 2015-10-13 11:38 | TRANE - 4TTX30361000AA | 78 | 0 | Yes | Yes | 23.3 | 21.4 | 1.9 | CC27C93C67B24C628CE846B1CE785EAD |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7759 |  | 2015-09-23 | 2015-09-23 10:28 | 2015-09-23 10:28 | PAYNE - 563CNO42A | 131 | 0 | Yes | Yes | 25 | 19.3 | 5.7 | 8134E72DDD494E518025785A45CAD849 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-5279 |  | 2015-09-22 | 2015-09-22 16:28 | 2015-09-22 16:28 | CARRIER - 24ABB336W310 | 84 | 0 | Yes | Yes | 17.4 | 20.2 | -2.8 | AAB94C56C89F4DC483E29EDF73AC295F |  | R410A | TXV |  | 0% | 1 | 0%
Dixon | CA | 95620-3405 |  | 2015-10-06 | 2015-10-06 10:13 | 2015-10-06 10:13 | ARMSTRONG - UNK | 85 | 0 | Yes | Yes | 17.6 | 20.4 | -2.8 | 293E6CAE323940479CD1D2CB0EFB7C0B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5245 |  | 2015-10-22 | 2015-10-22 11:01 | 2015-10-22 11:01 | BRYANT - UNKNOWWN | 42 | 0 | Yes | Yes | 24.4 | 20.9 | 3.5 | 60502C3BB85B472A9098C6395521AE7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1471 |  | 2015-09-21 | 2015-09-21 16:35 | 2015-09-21 16:35 | TRANE - 2TTX4036B1000AA | 118 | 0 | Yes | Yes | 21.5 | 20.4 | 1.1 | D587352116F14F34B8769C31CB073CC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5163 |  | 2015-09-24 | 2015-09-24 17:26 | 2015-09-24 17:26 | CARRIER - UNKNOWN | 197 | 0 | Yes | Yes | 19.2 | 22 | -2.8 | 412D890845654E10923583B89F5903E0 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6136 |  | 2015-11-23 | 2015-11-23 15:37 | 2015-11-23 15:37 | YORK - D6NZ036N0560 | 85 | 0 | Yes | Yes | 20.3 | 19.7 | 0.6 | B69F3C4E30644532BFD209069BAB6AC6 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-6136 |  | 2015-11-23 | 2015-11-23 15:41 | 2015-11-23 15:41 | YORK - D1NP030N05606A | 73 | 0 | Yes | Yes | 19.7 | 15.7 | 4 | 7C5C1106DA864D7D886A26449ADFA8B3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3178 |  | 2015-09-23 | 2015-09-23 09:55 | 2015-09-23 09:55 | CARRIER - 24ABB336W310 | 85 | 0 | Yes | Yes | 15.8 | 17.1 | -1.3 | E6E4F7BEE7E444BCA7981661F0A0AC95 |  | R410A | Non-TXV |  | 0% | 1 | 0%
American Canyon | CA | 94503-3178 |  | 2015-09-23 | 2015-09-23 10:07 | 2015-09-23 10:07 | CARRIER - 24ABB336W310 | 85 | 0 | Yes | Yes | 18.4 | 17.7 | 0.7 | D4D9F6AE28984AC0B5FA0C99DA06D548 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4619 |  | 2015-09-23 | 2015-09-23 08:18 | 2015-09-23 08:18 | GOODMAN - PGB036100-1A | 57 | 0 | Yes | Yes | 23.1 | 18.9 | 4.2 | 2BC25A93EB8643F6BDCEF17A6A1F607A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2129 |  | 2015-09-29 | 2015-09-29 14:37 | 2015-09-29 14:37 | GOODMAN - RGB036 | 60 | 0 | Yes | Yes | 17.7 | 17.4 | 0.3 | ACA227CB79B142C697FE5F58C13F25AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-8507 |  | 2015-09-11 | 2015-09-11 11:25 | 2015-09-11 11:25 | OTHER - N/A | 85 | 0 | Yes | Yes | 19.7 | 21.7 | -2 | 6A6AB4D964674E739E6FB360D6BB3BB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4266 |  | 2015-09-28 | 2015-09-28 12:33 | 2015-09-28 13:15 | OTHER - CA9060UKC1 | 160 | 19.1 | Yes | Yes | 21.4 | 23.2 | -1.8 | E08EBA24C1CB411DB5025A0080596299 |  | R22 | Non-TXV |  | 11.94% | 0.88062 | 22.94% | [5 empty] | Non-TXV | 11.94%
Walnut Creek | CA | 94598-2812 |  | 2015-09-23 | 2015-09-23 14:30 | 2015-09-23 14:30 | OTHER - UNKNOWN | 85 | 0 | Yes | Yes | 18.5 | 17.6 | 0.9 | A7DA236B02E84F07B1BDE7C933338716 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5436 |  | 2015-11-17 | 2015-11-17 14:31 | 2015-11-17 14:31 | YORK - H4DBO36S06A | 73 | 0 | Yes | Yes | 21.9 | 18.8 | 3.1 | 45D06066A10F4B449975AFED0CD34809 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-3076 |  | 2015-09-16 | 2015-09-16 15:19 | 2015-09-16 15:19 | PAYNE - 565J030 | 72 | 0 | Yes | Yes | 21.5 | 21.7 | -0.2 | B0C039F426D14BDFB0445D8B85CDAAD6 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-8412 |  | 2015-10-09 | 2015-10-09 14:10 | 2015-10-09 14:10 | CARRIER - 38EN024300 | 56 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | A46359C8C3F04594ADB9EF5D30A5C889 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94521-2017 |  | 2015-09-22 | 2015-09-22 12:53 | 2015-09-22 12:53 | TRANE - 4TTX4048A1000AA | 127 | 0 | Yes | Yes | 18.7 | 19.3 | -0.6 | F27DE8FBD0E54D5FB7380E20DE774C94 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2046 |  | 2015-10-09 | 2015-10-09 15:51 | 2015-10-09 15:51 | OTHER - UNKNOWN | 62 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | 00422C2D50194B8BBC227F83237EAB8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2833 |  | 2015-09-15 | 2015-09-15 09:02 | 2015-09-15 09:02 | ICP - PGME42G09907 | 181 | 0 | Yes | Yes | 22.2 | 23.9 | -1.7 | B0E26BCA57804BD697B8B0BF7947CD2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5401 |  | 2015-09-28 | 2015-09-28 13:51 | 2015-09-28 13:51 | OTHER - CA9042VKD2 | 128 | 0 | Yes | Yes | 22 | 22.5 | -0.5 | F4CFDE73FC144D4BB139C06E02240FD0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-3909 |  | 2015-09-15 | 2015-09-15 12:08 | 2015-09-15 12:28 | LENNOX - 12ACB42-4P | 125 | 10.3 | Yes | Yes | 19.9 | 20.9 | -1 | 810552BA81B5443F901FF7D3475E1FD6 |  | R22 | TXV |  | 8.24% | 0.9176 | 15.84% | [5 empty] | TXV | 8.24%
Bakersfield | CA | 93305-5907 |  | 2015-09-22 | 2015-09-22 11:05 | 2015-09-22 11:05 | YORK - H2RD036S06B | 85 | 0 | Yes | Yes | 19.3 | 20.4 | -1.1 | E33299AB9C5A490BBF3D7742F7AF43A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7018 |  | 2015-09-24 | 2015-09-24 09:29 | 2015-09-24 09:29 | TRANE - BTD742A1000B0 | 148 | 0 | Yes | Yes | 26.2 | 20.4 | 5.8 | FB5FCC1DF7604485B541E88335E7F22B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1241 |  | 2015-10-23 | 2015-10-23 15:18 | 2015-10-23 15:18 | ICP - PGAD47D1K1 | 215 | 0 | Yes | Yes | 20.5 | 21.8 | -1.3 | C03A7AC1CD8643CD82764F5D25E76DEC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5177 |  | 2015-09-17 | 2015-09-17 11:09 | 2015-09-17 11:09 | BDP - 585EJW024050ARAE | 54 | 0 | Yes | Yes | 19 | 18.7 | 0.3 | 7BC72B08D2844996BA6A11E12218A6B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2169 |  | 2015-10-15 | 2015-10-15 09:04 | 2015-10-15 09:04 | NORDYNE - JS5BD-024K | 85 | 0 | Yes | Yes | 22.9 | 22.3 | 0.6 | 1FB9053020854E298A20D545EB24E7E9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2211 |  | 2015-09-24 | 2015-09-24 09:48 | 2015-09-24 09:48 | PAYNE - 591ANX036000AAAA | 90 | 0 | Yes | Yes | 23.3 | 18.8 | 4.5 | 01334BD9A6B34874B312AEDB0953DF9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2190 |  | 2015-10-13 | 2015-10-13 15:07 | 2015-10-13 15:07 | NORDYNE - JS6BD-036K | 138 | 7 | Yes | Yes | 22 | 24.2 | -2.2 | B9590620860F49248B1AD4BFB07D2F46 |  | R22 | Non-TXV |  | 5.072% | 0.94928 | 9.748% | [5 empty] | Non-TXV | 5.072%
Santa Rosa | CA | 95401-0809 |  | 2015-10-22 | 2015-10-22 12:11 | 2015-10-22 12:11 | COLEMAN - N/A | 85 | 0 | Yes | Yes | 20.1 | 18.2 | 1.9 | 8A7FCFAC2C28454C9C6A2608202FABDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-9325 |  | 2015-10-20 | 2015-10-20 11:44 | 2015-10-20 11:44 | YORK - H1RA042S06D | 84 | 0 | Yes | Yes | 17.5 | 19.1 | -1.6 | 1408289DDE5740898007AE9B683E4913 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1680 |  | 2015-09-19 | 2015-09-19 08:59 | 2015-09-19 08:59 | OTHER - RAFD-036JAS | 80 | 0 | Yes | Yes | 19.7 | 19.1 | 0.7 | 3A3873B73CAF41E8A57415E39948A18B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-1792 |  | 2015-10-01 | 2015-10-01 10:11 | 2015-10-01 10:11 | GOODMAN - CE421GC | 107 | 0 | Yes | Yes | 18.4 | 20.6 | -2.2 | 60D0CCB53719436B965CA49D3C701025 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1705 |  | 2015-09-22 | 2015-09-22 15:42 | 2015-09-22 15:54 | BDP - 585EJ030050 | 58 | 9.9 | Yes | Yes | 19.3 | 19.9 | -0.6 | 24ADD25C41F445B888E9562EF4EDD9C7 |  | R22 | Non-TXV |  | 17.07% | 0.82931 | 32.8% | [5 empty] | Non-TXV | 17.07%
Suisun City | CA | 94585-6301 |  | 2015-09-24 | 2015-09-24 10:50 | 2015-09-24 10:50 | GOODMAN - CE42-1GC | 85 | 0 | Yes | Yes | 17.4 | 20.4 | -3 | 47ABA4B2757A47E7B3457DD3F35027A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5927 |  | 2015-09-24 | 2015-09-24 09:04 | 2015-09-24 09:04 | CARRIER - 38CKC042310 | 82 | 0 | Yes | Yes | 18.7 | 19.8 | -1.1 | 9DD7966CB8EE4504A5B988B606F2FBDB |  | R22 | TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2516 |  | 2015-10-26 | 2015-10-26 10:49 | 2015-10-26 10:49 | PAYNE - PY1PNB030060 | 85 | 0 | Yes | Yes | 18.5 | 19.5 | -1 | 55637E2D5DDA44F49C29D7E82035AF14 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-6082 |  | 2015-09-28 | 2015-09-28 12:11 | 2015-09-28 12:11 | ICP - PGF036K060A | 71 | 0 | Yes | Yes | 21 | 21.8 | -0.8 | 57C00F4E556E4684991748B5B176F07B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4663 |  | 2015-09-15 | 2015-09-15 14:56 | 2015-09-15 15:36 | OTHER - N/A | 85 | 13 | Yes | Yes | 20.9 | 22.5 | -1.6 | B3EC3F18615447C2BD147329EFCA2681 |  | R22 | Non-TXV |  | 15.29% | 0.84706 | 29.39% | [5 empty] | Non-TXV | 15.29%
Bakersfield | CA | 93309-5334 |  | 2015-09-30 | 2015-09-30 14:27 | 2015-09-30 14:27 | ICP - PGAD47D1K5 | 215 | 0 | Yes | Yes | 26.1 | 20.7 | 5.4 | E2C9ACA5C8C04FF08D50E79F75ED63F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3002 |  | 2015-09-28 | 2015-09-28 09:04 | 2015-09-28 09:19 | DAY & NIGHT - N/A | 85 | 8 | Yes | Yes | 19.1 | 19.6 | -0.5 | 2C4B55051CA144EEADC1D7AD12F37116 |  | R22 | Non-TXV |  | 9.412% | 0.90588 | 18.09% | [5 empty] | Non-TXV | 9.412%
Fresno | CA | 93726-4531 |  | 2015-11-09 | 2015-11-09 09:57 | 2015-11-09 09:57 | RHEEM - RRNLB030JK06X | 76 | 0 | Yes | Yes | 25.4 | 20.4 | 5 | A0CEBB67AB3441899345E25E92A96E1D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-0000 |  | 2015-09-21 | 2015-09-21 12:33 | 2015-09-21 12:33 | CARRIER - 38TZA042 | 83 | 0 | Yes | Yes | 22.6 | 18.8 | 3.8 | BE304B7BB6BB411BA77BACFCBA80BC7C |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-2351 |  | 2015-09-18 | 2015-09-18 13:21 | 2015-09-18 13:38 | OTHER - GCGD30S41S34 | 62 | 2.8 | Yes | Yes | 24.3 | 18.6 | 5.7 | 0D27A8A58A7A40ECAA36C29F91E101D5 |  | R410A | TXV |  | 4.516% | 0.95484 | 8.679% | [5 empty] | TXV | 4.516%
Concord | CA | 94521-3609 |  | 2015-09-23 | 2015-09-23 15:30 | 2015-09-23 15:30 | OTHER - UNKNOWN | 73 | 0 | Yes | Yes | 18.1 | 20.9 | -2.8 | C0151CC1BE5A43AEBEA8C25C3DF23377 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2310 |  | 2015-10-08 | 2015-10-08 13:44 | 2015-10-08 13:44 | AMERICAN STANDARD - 7A2036A100A2 | 111 | 0 | Yes | Yes | 24.5 | 21.5 | 3 | C06854F94E8E468DBF1056FD54CD4FF1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5531 |  | 2015-10-01 | 2015-10-01 14:55 | 2015-10-01 14:55 | RHEEM - RAMB-060JBZ | 192 | 0 | Yes | Yes | 22.4 | 21 | 1.4 | 8C3496B28C344BFF8A882E7E09ED6795 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4713 |  | 2015-09-24 | 2015-09-24 09:03 | 2015-09-24 09:36 | ICP - PGC030K060A | 52 | 10.7 | Yes | Yes | 22.3 | 20.6 | 1.7 | ACECA1A030CD48D5ADA6B4F2E37DB2F4 |  | R22 | Non-TXV |  | 20.58% | 0.79423 | 39.54% | [5 empty] | Non-TXV | 20.58%
Bakersfield | CA | 93307-1887 |  | 2015-09-22 | 2015-09-22 12:23 | 2015-09-22 12:23 | GOODMAN - GPG133004541BA | 72 | 0 | Yes | Yes | 21.2 | 24 | -2.8 | 3F70463ED8F34439843C33EA0E7D781D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1140 |  | 2015-10-02 | 2015-10-02 15:09 | 2015-10-02 15:09 | CARRIER - 24ABB330W310 | 85 | 0 | Yes | Yes | 20.5 | 16.2 | 4.3 | E8DCCC56A9E148858FC5EFC1226CD50D |  | R410A | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3976 |  | 2015-10-06 | 2015-10-06 13:57 | 2015-10-06 14:19 | CARRIER - 38CKC060370 | 133 | 17.2 | Yes | Yes | 15.3 | 17.6 | -2.3 | 73D93743FB2945318484D4867F76648F |  | R22 | TXV |  | 12.93% | 0.87068 | 24.85% | [5 empty] | TXV | 12.93%
Fairfield | CA | 94533-7347 |  | 2015-10-07 | 2015-10-07 15:18 | 2015-10-07 15:18 | GOODMAN - CPKE181B | 79 | 0 | Yes | Yes | 19.7 | 20.4 | -0.7 | E852B960171043049269CB916C640C88 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5482 |  | 2015-10-07 | 2015-10-07 12:51 | 2015-10-07 12:51 | ALLEGIANCE - 2A7A2042B1000AA | 86 | 0 | Yes | Yes | 21.9 | 22.8 | -0.9 | EFF4B7F8707244EF8B5F6F2C421774FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-5525 |  | 2015-09-23 | 2015-09-23 09:29 | 2015-09-23 09:29 | OTHER - D1NA030N05606C | 76 | 0 | Yes | Yes | 19.6 | 18.3 | 1.3 | 3BE3658623014A0180E5AC3C79835A5F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1649 |  | 2015-09-24 | 2015-09-24 08:40 | 2015-09-24 08:40 | CARRIER - 48SX-048100341AA | 88 | 0 | Yes | Yes | 21.7 | 16.9 | 4.8 | D062A884360146778FC9C64500F94E51 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94506-5864 |  | 2015-10-14 | 2015-10-14 12:39 | 2015-10-14 12:39 | CARRIER - 38EN036340 | 98 | 0 | Yes | Yes | 30 | 24.2 | 5.9 | 29BA30D2A431472EB4DB7E072D35A212 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1453 |  | 2015-09-23 | 2015-09-23 14:50 | 2015-09-23 14:50 | YORK - D2NA060N09006D | 84 | 0 | Yes | Yes | 26.1 | 21.8 | 4.3 | 94BBE210D1E14FAEB4E8316D717B39D4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4336 |  | 2015-09-24 | 2015-09-24 08:38 | 2015-09-24 08:38 | OTHER - DBYP-F048N080A | 132 | 0 | Yes | Yes | 19.3 | 19.8 | -0.5 | 2DAA56CC2A4641B18C30CDF19BAC9649 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2186 |  | 2015-10-13 | 2015-10-13 14:37 | 2015-10-13 14:38 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 19.8 | 22.6 | -2.8 | 208DDF9C24F541978E77AE26EF745815 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7499 |  | 2015-10-20 | 2015-10-20 12:18 | 2015-10-20 12:18 | UNITARY PRODUCTS GROUP - BRCS0601BE | 106 | 0 | Yes | Yes | 22.6 | 20.2 | 2.4 | ECCDAA9CF0534239AC555C114C69D322 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-3311 |  | 2015-09-28 | 2015-09-28 15:15 | 2015-09-28 15:15 | OTHER - UNKNOWN | 72 | 0 | Yes | Yes | 20.4 | 20.6 | -0.2 | 81AAD0772E894CB39C8672E3D229AFCC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1802 |  | 2015-09-25 | 2015-09-25 09:34 | 2015-09-25 09:34 | BRYANT - 24ABA336A0030010 | 85 | 0 | Yes | Yes | 20.5 | 19 | 1.5 | 81B5D23F3E5545A590D38C2B369E7C03 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6605 |  | 2015-10-21 | 2015-10-21 10:35 | 2015-10-21 10:35 | BRYANT - 38BRC060360 | 199 | 0 | Yes | Yes | 21.6 | 21.3 | 0.4 | 0656225B37A8465D86F35BFEE65AF94A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2254 |  | 2015-10-08 | 2015-10-08 11:51 | 2015-10-08 11:51 | CARRIER - 38TXA030350 | 96 | 0 | Yes | Yes | 18 | 19.9 | -1.9 | 5FB1F55596C24807A0A2B25004F87578 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4445 |  | 2015-09-25 | 2015-09-25 13:34 | 2015-09-25 13:34 | OTHER - UNKOWN | 116 | 0 | Yes | Yes | 20.9 | 21 | -0.1 | E8FC5BC7244440F09A54769E1CB5FA06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5422 |  | 2015-10-20 | 2015-10-20 13:17 | 2015-10-20 13:18 | OTHER - N/A | 85 | 21.6 | Yes | Yes | 19.9 | 18.3 | 1.6 | 6D6029A5B019439399F394A05EF3800F |  | R22 | Non-TXV |  | 25.41% | 0.74588 | 48.84% | [5 empty] | Non-TXV | 25.41%
Fairfield | CA | 94533-2232 |  | 2015-10-02 | 2015-10-02 10:21 | 2015-10-02 10:21 | PAYNE - 561C018B | 52 | 0 | Yes | Yes | 17.2 | 18.8 | -1.6 | 7D3C6BAC3EE3442C908DA87C9DA49EDF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3951 |  | 2015-09-22 | 2015-09-22 13:44 | 2015-09-22 13:44 | CARRIER - PA13N036-E | 71 | 0 | Yes | Yes | 19.9 | 17.1 | 2.8 | DC4D9CCBE8984BA2AAACA8FA178EB01B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1564 |  | 2015-09-23 | 2015-09-23 13:42 | 2015-09-23 13:42 | ICP - PGAD30D1K3 | 78 | 0 | Yes | Yes | 23.3 | 19 | 4.3 | 43457C3B381C46B2B7F3C503159C5518 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2712 |  | 2015-09-28 | 2015-09-28 10:11 | 2015-09-28 10:11 | COLEMAN - 9536-901 | 58 | 0 | Yes | Yes | 21.4 | 22 | -0.6 | 0C7BE6BF00DE491086DE71C16C71198E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3665 |  | 2015-10-01 | 2015-10-01 13:34 | 2015-10-01 13:34 | CARRIER - 38TRA036330 | 99 | 0 | Yes | Yes | 19.7 | 21 | -1.3 | 50721094895547F98CFC62A5D219E220 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1276 |  | 2015-10-19 | 2015-10-19 13:31 | 2015-10-19 13:50 | YORK - H1RD048S06A | 227 | 15.7 | Yes | Yes | 21.5 | 21.3 | 0.3 | CB587A7A024E49D68FDFA51F3200D7EF |  | R22 | Non-TXV |  | 6.916% | 0.93084 | 13.29% | [5 empty] | Non-TXV | 6.916%
Clovis | CA | 93612-1671 |  | 2015-10-12 | 2015-10-12 13:32 | 2015-10-12 13:53 | BRYANT - 1113RNA048-D | 117 | -7 | Yes | Yes | 19.7 | 19.9 | -0.2 | 657F49BC861C4A27990814D908458557 |  | R22 | TXV |  | -5.983% | 1.0598 | 1.675% |  |  |  |  | TXV |  |  | -5.983%
Bakersfield | CA | 93313-2761 |  | 2015-09-28 | 2015-09-28 10:25 | 2015-09-28 10:50 | OTHER - BRCQ0361BD | 52 | 4.2 | Yes | Yes | 20.7 | 22.1 | -1.4 | 63D12AE4DE234168B80222EC446E0742 |  | R22 | Non-TXV |  | 8.077% | 0.91923 | 15.52% | [5 empty] | Non-TXV | 8.077%
Bakersfield | CA | 93307-2159 |  | 2015-10-07 | 2015-10-07 14:58 | 2015-10-07 14:58 | NORDYNE - JS5BD-024K | 104 | 0 | Yes | Yes | 20.3 | 21.8 | -1.5 | 99828D1FC528478A9984D8178C3E0108 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3987 |  | 2015-10-14 | 2015-10-14 10:15 | 2015-10-14 10:15 | CARRIER - 38CKC060370 | 133 | 0 | Yes | Yes | 20.8 | 18.7 | 2.1 | 252DFD94B07147A7911D651BF3626813 |  | R22 | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1742 |  | 2015-09-24 | 2015-09-24 11:02 | 2015-09-24 11:02 | GOODMAN - GSX130421BB | 90 | 0 | Yes | Yes | 20 | 19.3 | 0.7 | 7C6FD672A1714C95B726C153C9192742 |  | R410A | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3029 |  | 2015-10-14 | 2015-10-14 13:28 | 2015-10-14 13:28 | TRANE - TTD736A100A0 | 96 | 0 | Yes | Yes | 25.6 | 20.1 | 5.5 | 0BCE36B401D747B183B21BF3B96B20EB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-3978 |  | 2015-10-07 | 2015-10-07 14:02 | 2015-10-07 14:02 | GOODMAN - CK241B | 71 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | E26ADA56F85A46D894A86FF65D3E13C2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2601 |  | 2015-10-13 | 2015-10-13 10:59 | 2015-10-13 10:59 | BDP - 585GJW03606ABAF | 82 | 13 | Yes | Yes | 20.6 | 19.9 | 0.7 | FB0FE1C43A2A498EAE4EF9110B963E73 |  | R22 | Non-TXV |  | 15.85% | 0.84146 | 30.47% | [5 empty] | Non-TXV | 15.85%
Bakersfield | CA | 93304-2340 |  | 2015-09-23 | 2015-09-23 09:00 | 2015-09-23 09:00 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 20.5 | 21.3 | -0.8 | 74B91CB5023B4DEF9EC04905C0A43BD4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2015 |  | 2015-09-29 | 2015-09-29 13:49 | 2015-09-29 13:49 | YORK - TCGD24S41S3HA | 61 | 0 | Yes | Yes | 13.9 | 16.7 | -2.8 | EA56B98FA18B40D49EF8A93F7032E984 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5880 |  | 2015-10-02 | 2015-10-02 15:05 | 2015-10-02 15:24 | YORK - D2NH036N05606C | 108 | 22.4 | Yes | Yes | 20.7 | 22.1 | -1.4 | 1047714C944D4707B5CBB2D0E4EF1881 |  | R22 | Non-TXV |  | 20.74% | 0.79259 | 39.86% | [5 empty] | Non-TXV | 20.74%
Fairfield | CA | 94533-7077 |  | 2015-09-25 | 2015-09-25 15:09 | 2015-09-25 15:09 | PAYNE - 591ANX036000AAAA | 83 | 0 | Yes | Yes | 24.9 | 21.8 | 3.1 | 3EA7B8BE329E4951B649F9730555E4CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5114 |  | 2015-10-30 | 2015-10-30 14:46 | 2015-10-30 14:46 | RHEEM - AT-38B10 | 45 | 0 | Yes | Yes | 22.1 | 22.6 | -0.5 | A7CC0F28ECB14D6BAF21924683B69AEA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-0000 |  | 2015-10-02 | 2015-10-02 12:55 | 2015-10-02 12:55 | BRYANT - UNKNOWN | 74 | 0 | Yes | Yes | 21.7 | 21.5 | 0.2 | 774FB0B109DF484FB15AB637E0D3D850 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4843 |  | 2015-11-06 | 2015-11-06 14:56 | 2015-11-06 14:56 | OTHER - D1NA036N03606C | 63 | 0 | Yes | Yes | 22.3 | 18.4 | 4 | C871D627BD284C0EB413A3F4EAD0C5BC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1795 |  | 2015-09-28 | 2015-09-28 14:11 | 2015-09-28 14:11 | CARRIER - 38CKC048370 | 103 | 0 | Yes | Yes | 18 | 20.2 | -2.2 | 68C2F04081704900A8DAADF3DDB81B7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4722 |  | 2015-11-13 | 2015-11-13 12:03 | 2015-11-13 12:03 | LENNOX - N/A | 85 | 0 | Yes | Yes | 22.1 | 17.7 | 4.4 | 9CFE3E8FEFCE447E827B63A134DF7DFC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-5409 |  | 2015-10-06 | 2015-10-06 10:49 | 2015-10-06 10:49 | RHEEM - RAND-036JBZ | 116 | 0 | Yes | Yes | 18.7 | 21.3 | -2.6 | 3FFB5A063F62473FA2DD697615A2EA36 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4628 |  | 2015-09-28 | 2015-09-28 09:17 | 2015-09-28 09:17 | PAYNE - PA13NA030-B | 55 | 0 | Yes | Yes | 18.2 | 18.8 | -0.6 | 4F393B3DCC3E47868C206E9950DD7943 |  | R410A | TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-8361 |  | 2015-10-15 | 2015-10-15 15:39 | 2015-10-15 15:39 | OTHER - AD048GD | 153 | 0 | Yes | Yes | 20.9 | 21.6 | -0.7 | 5D16995EAD524BC29A37DF4F7019FA1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-5107 |  | 2015-10-16 | 2015-10-16 12:16 | 2015-10-16 12:16 | AMANA - ASXC16048 | 135 | 0 | Yes | Yes | 20 | 19.5 | 0.6 | B0F3773376FE43D58871F4A3BB105183 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4610 |  | 2015-09-28 | 2015-09-28 12:41 | 2015-09-28 12:41 | CARRIER - 38BRC036340 | 101 | 0 | Yes | Yes | 18.9 | 18.8 | 0.1 | 464C6CEBFD2148708137AB8DE198CC0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5610 |  | 2015-10-01 | 2015-10-01 10:24 | 2015-10-01 10:50 | TRANE - 2TTB30330A1000AA | 88 | 5.8 | Yes | Yes | 22.5 | 20.4 | 2.1 | 9A0383245ADD49B3A94BC4A30FB5D160 |  | R22 | Non-TXV |  | 6.591% | 0.93409 | 12.67% | [5 empty] | Non-TXV | 6.591%
Stockton | CA | 95210-1908 |  | 2015-11-20 | 2015-11-20 14:43 | 2015-11-20 14:43 | DAY & NIGHT - 561AJ036-B | 85 | 0 | Yes | Yes | 23.5 | 18 | 5.6 | 8CF8345E18804DEEBF26879E292F4790 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1707 |  | 2015-10-05 | 2015-10-05 13:23 | 2015-10-05 13:23 | ICP - PGD330040K001C1 | 100 | 0 | Yes | Yes | 29 | 21.8 | 7.3 | 89B5569331874275B000A955958CDAD1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-5031 |  | 2015-09-23 | 2015-09-23 10:18 | 2015-09-23 10:18 | YORK - D1NP048N06506A | 132 | 0 | Yes | Yes | 21.2 | 19.3 | 1.9 | EC54C186DDB34F558CE77EBB7ED8D608 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-1401 |  | 2015-09-28 | 2015-09-28 11:06 | 2015-09-28 11:06 | RHEEM - RRPLB048JK08X | 161 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | 25309A7CFF2A4897B29EFA733DCA1E08 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-1415 |  | 2015-10-06 | 2015-10-06 09:41 | 2015-10-06 09:41 | - CL30-6A | 56 | 0 | Yes | Yes | 19.9 | 21.1 | -1.2 | AC10C08F990E435EA290FC67B835AE96 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3801 |  | 2015-11-13 | 2015-11-13 10:20 | 2015-11-13 10:20 | CARRIER - 38CKC048326 | 85 | 0 | Yes | Yes | 22.2 | 17.7 | 4.5 | AFFD3920F0914A95B7393FE5ACFD8450 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5174 |  | 2015-10-09 | 2015-10-09 13:46 | 2015-10-09 13:46 | BRYANT - UNKNOWN | 180 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | C519B03E9FC04BE080375539BFBE6453 |  | R410A | TXV |  | 0% | 1 | 0%
Danville | CA | 94506-4566 |  | 2015-10-14 | 2015-10-14 16:55 | 2015-10-14 16:55 | OTHER - UNK | 92 | 0 | Yes | Yes | 26.5 | 21.4 | 5.1 | 0BC170B8D6E44C019746972621E6074E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5130 |  | 2015-10-01 | 2015-10-01 11:19 | 2015-10-01 12:10 | RHEEM - N/A | 85 | 11.2 | Yes | Yes | 20.3 | 22.8 | -2.5 | 5F76E7760CE14426B727D203CBF31865 |  | R22 | Non-TXV |  | 13.18% | 0.86824 | 25.32% | [5 empty] | Non-TXV | 13.18%
Woodland | CA | 95776-5103 |  | 2015-10-16 | 2015-10-16 15:58 | 2015-10-16 15:58 | CARRIER - 24ABR342A0031010 | 85 | 0 | Yes | Yes | 16.5 | 16.2 | 0.3 | DEE2948A512F41059709CAB213D089CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3749 |  | 2015-10-01 | 2015-10-01 10:30 | 2015-10-01 10:30 | CARRIER - 38CKC042350 | 93 | 0 | Yes | Yes | 19.7 | 20.5 | -0.8 | A3AE6E48B3424BB5AF7A4A6A97AEB7D1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3463 |  | 2015-10-30 | 2015-10-30 09:22 | 2015-10-30 09:22 | ICP - GPCM024K040D | 56 | 0 | Yes | Yes | 21 | 19.4 | 1.6 | 75C9C73FED48461197AFB0AA0D198984 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-3505 |  | 2015-09-25 | 2015-09-25 16:49 | 2015-09-25 16:49 | TRANE - TTN042C100A2 | 146 | -11 | Yes | Yes | 30.3 | 22.8 | 7.5 | 1844713EED954B5CBFEB1E26F50E492E | Remove refrigerant: 11 oz | R22 | TXV |  | -7.534% | 1.0753 | 2.11% |  |  |  |  | TXV |  |  | -7.534%
San Jose | CA | 95131-1929 |  | 2015-10-22 | 2015-10-22 09:59 | 2015-10-22 09:59 | INTERTHERM - S3BA-048K | 105 | 0 | Yes | Yes | 26.2 | 20.9 | 5.3 | B1D159F85DA74777A05A46A79CDECD00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-4546 |  | 2015-10-30 | 2015-10-30 15:35 | 2015-10-30 15:36 | OTHER - | 85 | 16.8 | Yes | Yes | 17.2 | 19.9 | -2.7 | 5ACA523694CE4C8CAB8DA93F5255A8E3 |  | R22 | Non-TXV |  | 19.76% | 0.80235 | 37.98% | [5 empty] | Non-TXV | 19.76%
Stockton | CA | 95206-1905 |  | 2015-11-06 | 2015-11-06 11:41 | 2015-11-06 11:41 | AMANA - RCC36A2D | 85 | 0 | Yes | Yes | 22.4 | 17.7 | 4.7 | B95A25079F0C4CC98A3224B0A54A8248 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-1241 |  | 2015-10-09 | 2015-10-09 11:16 | 2015-10-09 11:16 | GOODMAN - ASC130421AD | 127 | 0 | Yes | Yes | 21.8 | 22.3 | -0.5 | 5AB99C41CD9D4A70A12FA727A02FC2A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1762 |  | 2015-10-26 | 2015-10-26 13:41 | 2015-10-26 13:41 | GOODMAN - GPG1330045M41BA | 78 | 0 | Yes | Yes | 25 | 21 | 4 | 6773483732514D0395AC44ED71F31C82 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3778 |  | 2015-09-30 | 2015-09-30 10:27 | 2015-09-30 10:27 | PAYNE - 598AN036B | 196 | 0 | Yes | Yes | 22.9 | 18.7 | 4.2 | 72C78401A5BE4DFB9D42DF7D8F7D4C63 |  | R22 | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4814 |  | 2015-11-10 | 2015-11-10 13:09 | 2015-11-10 13:09 | TRANE - TTR025 | 62 | 0 | Yes | Yes | 20.5 | 19.2 | 1.3 | C62803C75665417391FC8E6D2B4047A1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5927 |  | 2015-11-19 | 2015-11-19 16:48 | 2015-11-19 16:48 | CARRIER - 38CKC036350 | 73 | 0 | Yes | Yes | 18.5 | 18.7 | -0.2 | 965AF05AD2344B1F94EAB11ABCA467B7 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2571 |  | 2015-10-06 | 2015-10-06 14:18 | 2015-10-06 14:18 | BDP - 58560300075YACR | 85 | 0 | Yes | Yes | 20.8 | 17.9 | 2.9 | 830DDAD2A2454A6EA5DC9C558A91387A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-7490 |  | 2015-11-06 | 2015-11-06 13:19 | 2015-11-06 13:19 | YORK - AC024ML021A | 132 | 0 | Yes | Yes | 19.5 | 14.1 | 5.4 | 4900AE9EC4684002B400C37AD5F31D7F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-3375 |  | 2015-10-01 | 2015-10-01 08:55 | 2015-10-01 08:55 | WEATHER KING - 13AJM36A01 | 96 | 0 | Yes | Yes | 19.3 | 21.5 | -2.2 | 57AF5FE2143248428AA287024311F2CD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5769 |  | 2015-10-28 | 2015-10-28 09:18 | 2015-10-28 09:18 | GOODMAN - SSX1400301BB | 80 | 0 | Yes | Yes | 21.2 | 19.1 | 2.1 | 3EB74C0CF0EE4C2EBB748EE2C56FE21A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3767 |  | 2015-10-12 | 2015-10-12 14:24 | 2015-10-12 14:24 | BRYANT - 113ANA060H | 135 | 0 | Yes | Yes | 18.1 | 19.8 | -1.7 | 2E40C265BDC84943ABD3EAB6D4EB9E4B |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-3343 |  | 2015-11-05 | 2015-11-05 13:47 | 2015-11-05 13:47 | OTHER - 38CKC030330 | 68 | 0 | Yes | Yes | 21.3 | 20.7 | 0.6 | 07A93DE6103E4A929A64E92052DF33FB |  | R22 | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1966 |  | 2015-10-15 | 2015-10-15 14:18 | 2015-10-15 14:46 | CARRIER - 38CKC060370 | 133 | -30.8 | Yes | Yes | 22.3 | 20 | 2.3 | 628F20290CE7439FB5398BE9BF0BE3A6 |  | R22 | TXV |  | -23.16% | 1.2316 | 6.485% |  |  |  |  | TXV |  |  | -23.16%
Fresno | CA | 93725-1882 |  | 2015-11-06 | 2015-11-06 10:53 | 2015-11-06 10:53 | LENNOX - 12GCS042753PA | 104 | 0 | Yes | Yes | 20.5 | 18.2 | 2.3 | 21AC6135853A4B1C9286F6F2D2FA0103 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4657 |  | 2015-10-14 | 2015-10-14 15:00 | 2015-10-14 15:00 | BRYANT - 563CN036-E | 101 | 0 | Yes | Yes | 22.5 | 22.9 | -0.4 | 4ADCAB45988B41FCAEC8BF3CE5D0CDBE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3004 |  | 2015-10-19 | 2015-10-19 09:16 | 2015-10-19 09:17 | GOODMAN - GPG1324045M41DA | 75 | 8.9 | Yes | Yes | 21.1 | 20.2 | 1 | 580F723EB28C437DA551A8A51808C049 |  | R410A | Non-TXV |  | 11.87% | 0.88133 | 22.81% | [5 empty] | Non-TXV | 11.87%
Pittsburg | CA | 94565-2004 |  | 2015-10-01 | 2015-10-01 11:30 | 2015-10-01 11:30 | OTHER - RAFD-042JBS | 70 | 0 | Yes | Yes | 16 | 18 | -2 | 0A5CFCE95EA64BEC9BA434726D039049 |  | R22 | Non-TXV |  | 0% | 1 | 0%
W Sacramento | CA | 95691-5878 |  | 2015-11-19 | 2015-11-19 10:36 | 2015-11-19 10:36 | GOODMAN - CKJ30-1A | 85 | 0 | Yes | Yes | 16.3 | 17.2 | -0.9 | 4F4EDD6B909D47BFB804076A73B392E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2861 |  | 2015-11-03 | 2015-11-03 14:21 | 2015-11-03 14:21 | CARRIER - 38CKC048 | 85 | 0 | Yes | Yes | 20 | 18 | 2 | 1F94F3F560A44A679D9A022E35F980F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-3052 |  | 2015-11-06 | 2015-11-06 14:37 | 2015-11-06 14:37 | AMANA - RCB30B2A | 77 | 0 | Yes | Yes | 26 | 21.5 | 4.5 | 2A6847FEB63349F6B28F5BCD87CC0ACD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4718 |  | 2015-10-26 | 2015-10-26 11:09 | 2015-10-26 11:09 | PAYNE - N/A | 85 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | ACC1B37F425C425FB2F700FD097BE666 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-9319 |  | 2015-10-16 | 2015-10-16 10:22 | 2015-10-16 10:22 | PAYNE - 585HJW030040ABAF | 68 | 0 | Yes | Yes | 20.2 | 20.3 | -0.1 | 401C4C0CAC0A45A9BD0EB0234484BAE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3004 |  | 2015-10-05 | 2015-10-05 12:26 | 2015-10-05 12:26 | YORK - D3NZ030N03606NXC | 85 | 0 | Yes | Yes | 20.3 | 22.6 | -2.3 | C7D0D762C5B5413689268EB222B6E85A |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-7186 |  | 2015-10-26 | 2015-10-26 09:00 | 2015-10-26 09:00 | RUUD - UAMB-030JAZ | 77 | 0 | Yes | Yes | 20.2 | 18.8 | 1.4 | FD794AE636FE4C9795A08F9F9337A249 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-3004 |  | 2015-10-05 | 2015-10-05 10:18 | 2015-10-05 10:18 | YORK - D3NZ024N03606NXC | 58 | 0 | Yes | Yes | 20.6 | 21.3 | -0.7 | 8F6ADA5387794480B37E407E8025E9A8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-1981 |  | 2015-10-26 | 2015-10-26 14:12 | 2015-10-26 14:13 | ICP - PGF330060K01A2 | 91 | 14.8 | Yes | Yes | 20.6 | 21 | -0.4 | FA9BDF0E2C7241BF94EC1EA7BFA9FB02 |  | R22 | Non-TXV |  | 16.26% | 0.83736 | 31.26% | [5 empty] | Non-TXV | 16.26%
Stockton | CA | 95204-3124 |  | 2015-11-06 | 2015-11-06 09:05 | 2015-11-06 09:05 | LENNOX - HS21651-1P | 222 | 0 | Yes | Yes | 19 | 18.5 | 0.6 | C2D8AE393D6D464B92AA1741375195DB |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6119 |  | 2015-10-30 | 2015-10-30 12:20 | 2015-10-30 12:20 | PAYNE - PA13NR042-H | 113 | 0 | Yes | Yes | 19.3 | 19.7 | -0.4 | E1D6040ABEE24766A7B4C85C9F44DDE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2720 |  | 2015-09-30 | 2015-09-30 09:40 | 2015-09-30 09:40 | RHEEM - RA1636AJ1NA | 108 | 0 | Yes | Yes | 18 | 18 | 0 | C24AE1EFFAAB4BFB97C43A5ABF8B3D07 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7081 |  | 2015-09-29 | 2015-09-29 12:49 | 2015-09-29 12:49 | OTHER - N/A | 85 | 0 | Yes | Yes | 21.8 | 23.3 | -1.5 | 1D254DDB91174E8FB4BB7A3C99966F4F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-3721 |  | 2015-10-06 | 2015-10-06 02:09 | 2015-10-06 02:09 | OTHER - N4A342AKA300 | 85 | 0 | Yes | Yes | 24.8 | 22.8 | 2 | D4578822ACE94D4B9317BC82B874434A |  | R410A | TXV |  | 0% | 1 | 0%
Concord | CA | 94521-1636 |  | 2015-10-06 | 2015-10-06 00:07 | 2015-10-06 00:07 | OTHER - CA5548VKB1 | 140 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | A24F3F6F4F2F4E04A4D64153660EADA6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1619 |  | 2015-10-05 | 2015-10-05 14:17 | 2015-10-05 14:17 | DAY & NIGHT - N/A | 85 | 0 | Yes | Yes | 21.6 | 22.2 | -0.6 | D0EC46DCDE964FE88B1D943EBEAE00EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3400 |  | 2015-09-26 | 2015-09-26 15:58 | 2015-09-26 15:58 | CARRIER - 38TXA024320 | 85 | 0 | Yes | Yes | 19 | 18.3 | 0.8 | B910CF92D34449F684D93FFF2A366B34 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2352 |  | 2015-10-09 | 2015-10-09 09:13 | 2015-10-09 09:13 | TRANE - 4TTR5030E1000AC | 112 | 0 | Yes | Yes | 23.3 | 20.4 | 2.9 | CC37B8CE59A14DEF8346EC1CE9ACE3A8 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6635 |  | 2015-09-23 | 2015-09-23 15:05 | 2015-09-23 15:05 | GOODMAN - GPG1336045M41AC | 85 | 0 | Yes | Yes | 28.1 | 23.1 | 5 | F0B09C91E9F74713928217AA4719013B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-9008 |  | 2015-10-26 | 2015-10-26 12:40 | 2015-10-26 12:40 | OTHER - | 85 | 0 | Yes | Yes | 20.1 | 21.5 | -1.4 | 5DEAFB668D2F4B3A87993AF22AFA8796 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95776-9347 |  | 2015-10-08 | 2015-10-08 15:19 | 2015-10-08 15:19 | GOODMAN - CK49-1B | 97 | 0 | Yes | Yes | 20.4 | 18.9 | 1.6 | DCF7C7D616C44BD4B0701E8CBBE1D576 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4710 |  | 2015-10-26 | 2015-10-26 10:54 | 2015-10-26 10:55 | OTHER - N/A | 85 | 13.4 | Yes | Yes | 17.6 | 20.6 | -3 | 7D5BC94B39204334A29C45A7CF89EA4F |  | R22 | Non-TXV |  | 15.76% | 0.84235 | 30.3% | [5 empty] | Non-TXV | 15.76%
Antioch | CA | 94509-3921 |  | 2015-10-20 | 2015-10-20 10:57 | 2015-10-20 10:57 | GOODMAN - GSC130361FB | 83 | 0 | Yes | Yes | 20.5 | 21.6 | -1.1 | 1552DCE50BAE496DB18011B806E29CBC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4262 |  | 2015-10-05 | 2015-10-05 09:02 | 2015-10-05 09:17 | ICP - GPCM024K040D | 56 | 6.7 | Yes | Yes | 25.6 | 22.1 | 3.5 | C77167EA86284D2888341C5246DFEF65 |  | R22 | Non-TXV |  | 11.96% | 0.88036 | 22.99% | [5 empty] | Non-TXV | 11.96%
San Jose | CA | 95123-4335 |  | 2015-10-31 | 2015-10-31 10:11 | 2015-10-31 10:11 | CARRIER - 38CKC048370 | 99 | 0 | Yes | Yes | 19.7 | 20.7 | -0.9 | E53B7CF7FB734620BB9BD2639BA5B50B |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3975 |  | 2015-10-26 | 2015-10-26 14:34 | 2015-10-26 14:34 | OTHER - 2AC13B36P-1A | 139 | 0 | Yes | Yes | 19.5 | 21.5 | -2 | 1DA71D3EE0C34BA0BBC6D95B3612AB8A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-5710 |  | 2015-10-05 | 2015-10-05 11:59 | 2015-10-05 11:59 | YORK - D5NZ024N03606NXA | 60 | 0 | Yes | Yes | 21.8 | 22.4 | -0.6 | AE4A8E76B9144B96996C3B6DDA6AB3CC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-6550 |  | 2015-10-07 | 2015-10-07 09:58 | 2015-10-07 09:58 | PAYNE - PA13NR060-J | 168 | 0 | Yes | Yes | 20.3 | 18.8 | 1.5 | 536753639A3548AE96E21B0A77786C7B |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1504 |  | 2015-10-05 | 2015-10-05 13:01 | 2015-10-05 13:01 | COMFORT AIRE - PGAD36D1KE | 102 | 0 | Yes | Yes | 24.3 | 24.2 | 0.1 | EF152E7A9ACF4E75A2C67FCDC44FC178 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1851 |  | 2015-09-30 | 2015-09-30 15:33 | 2015-09-30 15:33 | DAY & NIGHT - 585HJW0240040A | 68 | 0 | Yes | Yes | 25.2 | 22.1 | 3.1 | 1B94DCC0C1C34D3C865B3ED15199D925 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5246 |  | 2015-10-30 | 2015-10-30 09:19 | 2015-10-30 09:19 | LENNOX - 10ACC-036-230-02 | 74 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | 12F6D5C422D741A69002ABE19352F888 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-4248 |  | 2015-11-06 | 2015-11-06 10:44 | 2015-11-06 10:44 | TRANE - YCPO42F1MOAA | 85 | 0 | Yes | Yes | 23.5 | 18 | 5.6 | 803364E1CF8744098E41EAD8D129F2E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Davis | CA | 95618-7803 |  | 2015-10-13 | 2015-10-13 15:30 | 2015-10-13 15:30 | OTHER - AC030X1021A | 62 | 0 | Yes | Yes | 23.5 | 20.7 | 2.8 | 72A6899B35B64A9D9CF8088B201CA6AC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6050 |  | 2015-10-02 | 2015-10-02 10:14 | 2015-10-02 10:14 | ICP - PGAA42C1K4 | 70 | 0 | Yes | Yes | 19.5 | 19.5 | 0 | F987EC757EBF41079C32538B0210E709 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1627 |  | 2015-10-07 | 2015-10-07 11:34 | 2015-10-07 11:34 | TRANE - 4TTX4036B10000AA | 91 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | CF4BDBBF14D54A78AAC980BB8AC04586 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4305 |  | 2015-10-02 | 2015-10-02 11:21 | 2015-10-02 11:32 | YORK - D1NH048N06506C | 85 | 14.1 | Yes | Yes | 24.7 | 21.5 | 3.2 | 3CBC0F223C3F436EAB2566DD86C053B8 |  | R22 | Non-TXV |  | 16.59% | 0.83412 | 31.88% | [5 empty] | Non-TXV | 16.59%
Bakersfield | CA | 93305-4262 |  | 2015-10-05 | 2015-10-05 09:16 | 2015-10-05 09:16 | DAY & NIGHT - 24/60 YAC-108T | 56 | 0 | Yes | Yes | 22.9 | 23.1 | -0.2 | 66AEDA6C56DA4CA78AC46BB5FDC0544F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4216 |  | 2015-10-05 | 2015-10-05 09:04 | 2015-10-05 09:17 | ICP - GPCM030K060D | 53 | 7.2 | Yes | Yes | 21.9 | 22.6 | -0.7 | D8910A235F8541438A8942AB246C5157 |  | R22 | Non-TXV |  | 13.58% | 0.86415 | 26.11% | [5 empty] | Non-TXV | 13.58%
Fairfield | CA | 94533-5311 |  | 2015-10-07 | 2015-10-07 10:11 | 2015-10-07 10:11 | PAYNE - PA10JA024A | 67 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | 74ACEF46C68E44E9B49B096C93AB7969 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7067 |  | 2015-10-01 | 2015-10-01 09:17 | 2015-10-01 09:17 | YORK - D1NP048N06506A | 132 | 0 | Yes | Yes | 21.1 | 19.1 | 2 | EF9BEFAE1031417AABCB5E8565E3BF16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-1151 |  | 2015-09-29 | 2015-09-29 13:16 | 2015-09-29 13:16 | OTHER - N/A | 85 | 0 | Yes | Yes | 19.2 | 19.3 | -0.1 | 7FD9724B5EAC40DD9B5B35FF14AD910B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-2253 |  | 2015-10-06 | 2015-10-06 10:28 | 2015-10-06 10:28 | RHEEM - RRGH-07N36LKR | 81 | 0 | Yes | Yes | 20.9 | 18.2 | 2.7 | C872DCF0D71244FCB566D803D0E3E899 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3664 |  | 2015-10-08 | 2015-10-08 14:56 | 2015-10-08 14:56 | OTHER - CK36-1A | 73 | 0 | Yes | Yes | 19.4 | 21.7 | -2.3 | 689DDA44F8B24F44ADC526785BA468B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2679 |  | 2015-11-13 | 2015-11-13 09:40 | 2015-11-13 09:40 | CARRIER - 38E20036319 | 96 | 0 | Yes | Yes | 24 | 18.9 | 5.1 | C8EE351721F24666A441B12EC60C3E6F |  | R410A | TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-1446 |  | 2015-10-12 | 2015-10-12 14:38 | 2015-10-12 14:38 | BRYANT - 113ANA060H | 135 | 0 | Yes | Yes | 17.4 | 19.3 | -1.9 | 1AA50F323AF349CFB2583542ED125DAD |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3307 |  | 2015-11-06 | 2015-11-06 12:39 | 2015-11-06 12:39 | OTHER - RCB30 | 77 | 0 | Yes | Yes | 20 | 19.6 | 0.4 | 761DF0FA7F6B433F8F87476007BBCC54 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-3510 |  | 2015-10-02 | 2015-10-02 09:47 | 2015-10-02 09:47 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 26 | 21 | 5 | 99E32027CE854117B2E00B5A6BCBCB32 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5086 |  | 2015-10-13 | 2015-10-13 09:13 | 2015-10-13 09:14 | ARMSTRONG - N/A | 131 | 13.3 | Yes | Yes | 23.8 | 22.1 | 1.7 | FF1F995107CC4746A7509FE5FFF1C0C1 |  | R22 | Non-TXV |  | 10.15% | 0.89847 | 19.51% | [5 empty] | Non-TXV | 10.15%
Bakersfield | CA | 93307-1297 |  | 2015-10-26 | 2015-10-26 09:43 | 2015-10-26 09:44 | YORK - D3NZ030N03506NXA | 85 | 19.3 | Yes | Yes | 18.2 | 18.3 | -0.1 | BBA74BF80DBA4678812E38A3CCA58FE4 |  | R410A | Non-TXV |  | 22.71% | 0.77294 | 43.64% | [5 empty] | Non-TXV | 22.71%
San Jose | CA | 95136-1528 |  | 2015-10-08 | 2015-10-08 08:56 | 2015-10-08 08:56 | BRYANT - 561CJ048-A | 103 | 0 | Yes | Yes | 26.9 | 21.7 | 5.2 | 951AA8F8677B400BA878117DE80A271F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1819 |  | 2015-10-07 | 2015-10-07 14:38 | 2015-10-07 14:38 | AMERICAN STANDARD - YCY036G1MOAB | 129 | 0 | Yes | Yes | 19.7 | 18.6 | 1.1 | FB68DB5428D54C6F88B4CF6A5C1A6B2C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2735 |  | 2015-10-14 | 2015-10-14 08:39 | 2015-10-14 08:39 | AMERICAN STANDARD - YCY048G1H0AC | 155 | 0 | Yes | Yes | 22.1 | 18.2 | 3.9 | FB73D74E8DB74896B8A70D2CB6407B19 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95127-1034 |  | 2015-10-19 | 2015-10-19 09:14 | 2015-10-19 09:14 | RHEEM - RAHE-048JAS | 114 | 0 | Yes | Yes | 21.3 | 23 | -1.7 | A7EF91BAF3EF4099BD7E1559B9CFAA86 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1319 |  | 2015-10-05 | 2015-10-05 10:09 | 2015-10-05 10:31 | YORK - D1NH024N03606C | 70 | 4.4 | Yes | Yes | 16.9 | 15.7 | 1.2 | D855B208D3984E46A721C92B11FA4C05 |  | R22 | Non-TXV |  | 6.286% | 0.93714 | 12.08% | [5 empty] | Non-TXV | 6.286%
Woodland | CA | 95695-0000 |  | 2015-10-19 | 2015-10-19 15:27 | 2015-10-19 15:27 | GE - BWB942A100A3 | 153 | 0 | Yes | Yes | 15 | 17.8 | -2.8 | B8AA934D08E5453FAA93F630F20D29E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-4130 |  | 2015-10-09 | 2015-10-09 15:30 | 2015-10-09 15:30 | PAYNE - 563CNO48A | 166 | 0 | Yes | Yes | 20.6 | 19.7 | 0.9 | D912F39CD497470E83E9062D68B3983D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1757 |  | 2015-10-07 | 2015-10-07 09:17 | 2015-10-07 09:17 | CARRIER - 38BRC048370 | 133 | 0 | Yes | Yes | 18.2 | 18.2 | 0 | BB242370A50541F69B2E42DF4BB05369 |  | R22 | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-2083 |  | 2015-09-29 | 2015-09-29 15:47 | 2015-09-29 15:47 | DAY & NIGHT - 56J036-B | 85 | 0 | Yes | Yes | 15.8 | 18.6 | -2.8 | 79867E35C1AC40EAA210E72C013CA3F7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6216 |  | 2015-11-06 | 2015-11-06 09:57 | 2015-11-06 09:57 | BRYANT - 105ANA048-A | 85 | 0 | Yes | Yes | 21.8 | 17.7 | 4.1 | 945EBAA973A545DFA8238EEAC5A8C6A0 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4322 |  | 2015-10-12 | 2015-10-12 09:20 | 2015-10-12 09:20 | DAY & NIGHT - 591NX036 | 85 | 0 | Yes | Yes | 15.5 | 17.7 | -2.2 | 8658B7269D434C35B403FA49126022C6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4836 |  | 2015-10-26 | 2015-10-26 15:04 | 2015-10-26 15:04 | AMANA - PGD42C0902G | 113 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | E0C3723E821A47FBA3B33345318B3251 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5895 |  | 2015-10-26 | 2015-10-26 11:35 | 2015-10-26 11:35 | WEATHER KING - 12AJA30001 | 96 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | C0D21D39F26B4029A6FF08175713B74C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4488 |  | 2015-10-06 | 2015-10-06 15:18 | 2015-10-06 15:18 | OTHER - UNKNOWN | 83 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | 07E0A81156F4449A936280EB132072FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5656 |  | 2015-10-02 | 2015-10-02 10:52 | 2015-10-02 10:52 | ICP - PGAA42C1K4 | 70 | 0 | Yes | Yes | 23.3 | 19.1 | 4.2 | 0BA1E449663E422780788C62195D94B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Santa Rosa | CA | 95401-0809 |  | 2015-10-22 | 2015-10-22 12:48 | 2015-10-22 13:07 | COLEMAN - 7838901 | 72 | 11.1 | Yes | Yes | 20.6 | 18.2 | 2.4 | 23CFA697C147477F8A8206F974DCA3C2 |  | R22 | Non-TXV |  | 15.42% | 0.84583 | 29.63% | [5 empty] | Non-TXV | 15.42%
Suisun City | CA | 94585-6602 |  | 2015-10-08 | 2015-10-08 09:19 | 2015-10-08 09:19 | CARRIER - 38BTG048300 | 152 | 0 | Yes | Yes | 20.4 | 20.3 | 0.1 | AE4632736E324CA09F97B9B3F2B6BDF1 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-5435 |  | 2015-10-23 | 2015-10-23 09:40 | 2015-10-23 09:40 | OTHER - EESS36FAA | 69 | 0 | Yes | Yes | 20.3 | 18.8 | 1.6 | F4238EDB110B4716838C6429420CEFF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6278 |  | 2015-10-23 | 2015-10-23 13:57 | 2015-10-23 13:57 | OTHER - N/A | 85 | 0 | Yes | Yes | 20.2 | 21.5 | -1.3 | 6C63C3E8130047EE885EF0D30E6CA8E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-2467 |  | 2015-10-02 | 2015-10-02 10:35 | 2015-10-02 10:35 | RUUD - UNKNOWN | 85 | 0 | Yes | Yes | 18.5 | 19.6 | -1.1 | 70652334F60E47CFA2A44582AC4A230A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1434 |  | 2015-10-26 | 2015-10-26 09:28 | 2015-10-26 09:28 | ICP - PGF042K080B | 87 | 0 | Yes | Yes | 21.1 | 18.2 | 2.9 | DADF32C3CC0448ACBAD3B7692FBA4E7E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3269 |  | 2015-10-28 | 2015-10-28 14:21 | 2015-10-28 14:21 | YORK - D1NQ030N05606NXA | 53 | 0 | Yes | Yes | 19.8 | 19 | 0.8 | 2EE2FD880723420F9A329AB445F006FE |  | R410A | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1721 |  | 2015-10-13 | 2015-10-13 12:02 | 2015-10-13 12:29 | CARRIER - 38BRC060360 | 205 | 18.4 | Yes | Yes | 23.3 | 19.3 | 4 | DBA02F9A73854740BE1372995CE53BAC |  | R22 | Non-TXV |  | 8.976% | 0.91024 | 17.25% | [5 empty] | Non-TXV | 8.976%
Brentwood | CA | 94513-6914 |  | 2015-10-26 | 2015-10-26 12:14 | 2015-10-26 12:14 | CARRIER - 38BRCO30310 | 85 | 0 | Yes | Yes | 21.3 | 18.9 | 2.4 | 0AEF3CAB7AE5430C816B2C8D07A6F641 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6274 |  | 2015-10-13 | 2015-10-13 12:53 | 2015-10-13 12:53 | WEATHER KING - 13AJA42A01 | 121 | 0 | Yes | Yes | 19.3 | 22 | -2.7 | E24450675CAB48EEAAFD5805CB54F91A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3913 |  | 2015-10-07 | 2015-10-07 09:20 | 2015-10-07 09:20 | YORK - H2RC036S06A | 83 | 0 | Yes | Yes | 23.2 | 20.1 | 3.1 | 8F2D418F54A24C9DBBA78A3DEBB3B4F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2127 |  | 2015-10-03 | 2015-10-03 13:04 | 2015-10-03 13:04 | CARRIER - 38CKC042300 | 80 | 0 | Yes | Yes | 19.3 | 19.9 | -0.6 | DEC605CB480444ECA3383D35B7DDF1A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-3162 |  | 2015-10-07 | 2015-10-07 16:31 | 2015-10-07 16:31 | GOODMAN - GPG1442060M41AA | 121 | 0 | Yes | Yes | 21.6 | 20.4 | 1.2 | E00CDAB2C7B8477D85C2E6E3B69FC390 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1915 |  | 2015-10-27 | 2015-10-27 08:55 | 2015-10-27 08:55 | YORK - D1NH030N03606A | 69 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | 22C2D0FDE4FA41BFBC7909A9588673FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5328 |  | 2015-10-23 | 2015-10-23 11:10 | 2015-10-23 11:10 | LENNOX - 13A-CX-030-230- | 98 | 0 | Yes | Yes | 22.6 | 20.9 | 1.7 | 082B267BEBC1495E8B15B1DFF1426C08 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1620 |  | 2015-10-07 | 2015-10-07 09:18 | 2015-10-07 09:18 | YORK - D1NP042N06506A | 150 | 0 | Yes | Yes | 20.3 | 17.5 | 2.8 | 8BC5CA0C12774FB58CC32D01CC56A936 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2256 |  | 2015-10-19 | 2015-10-19 14:16 | 2015-10-19 14:16 | ICP - PGC048K080A | 102 | 0 | Yes | Yes | 20.3 | 19.9 | 0.4 | 4DBEE826943140E097D3738B836A0D23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-6010 |  | 2015-10-13 | 2015-10-13 10:06 | 2015-10-13 10:06 | RHEEM - HC-140-48210 | 105 | 0 | Yes | Yes | 19.7 | 19.3 | 0.4 | 11AEB46701C24C8E802A6D280EE21913 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-9740 |  | 2015-10-19 | 2015-10-19 14:38 | 2015-10-19 14:38 | CARRIER - 588ANW042080ACN | 87 | 0 | Yes | Yes | 21.8 | 20.4 | 1.4 | F0749FA9DE884822967B33B788512B7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2202 |  | 2015-11-05 | 2015-11-05 14:18 | 2015-11-05 14:18 | CARRIER - 38BRB036300 | 122 | 0 | Yes | Yes | 19.7 | 17.1 | 2.7 | 3AF4A4AC3A27424AA61E57B4FF8253F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1232 |  | 2015-10-05 | 2015-10-05 14:23 | 2015-10-05 14:23 | YORK - D1NP036N05606A | 108 | 0 | Yes | Yes | 19.7 | 18.5 | 1.2 | 9BA75A3695FA433D8036951FBB7E2EEB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-1032 |  | 2015-10-27 | 2015-10-27 14:35 | 2015-10-27 14:35 | BRYANT - UNKNOWN | 117 | 0 | Yes | Yes | 26.3 | 20.4 | 5.9 | FBBE5F4E752749FEA335A87E58CDE77D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-3734 |  | 2015-10-05 | 2015-10-05 09:19 | 2015-10-05 09:19 | BDP - 568FJO42 | 155 | 0 | Yes | Yes | 21.7 | 15.7 | 6 | 30130D4F861A4106875BC971ED80DB6A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-4895 |  | 2015-10-23 | 2015-10-23 12:43 | 2015-10-23 12:43 | - 4YCC3036A1075BB | 85 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | F03096E445DE41DE8AD85C0962122070 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-5467 |  | 2015-10-09 | 2015-10-09 02:35 | 2015-10-09 02:35 | CARRIER - 38CK036310 | 72 | 0 | Yes | Yes | 20 | 20.1 | -0.1 | BBCCD85A622046A2ABC77DA4057F49C3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-2770 |  | 2015-10-23 | 2015-10-23 08:56 | 2015-10-23 08:56 | RHEEM - RRNA-B030J06X | 72 | 0 | Yes | Yes | 19.6 | 19.8 | -0.2 | A75A90D20E1944E3A928922FD067576F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6737 |  | 2015-11-06 | 2015-11-06 11:50 | 2015-11-06 11:50 | PAYNE - PY3GNAA36060NA | 100 | 0 | Yes | Yes | 20.5 | 18.1 | 2.4 | B2FD44ED15A748E8949C29BF7146AFA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3513 |  | 2015-10-16 | 2015-10-16 09:31 | 2015-10-16 09:31 | RHEEM - UNKNOWN | 57 | 0 | Yes | Yes | 19.2 | 22 | -2.8 | 55462F1ADF0D4099945B4B957A671A9A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-5888 |  | 2015-11-09 | 2015-11-09 09:44 | 2015-11-09 09:44 | GOODMAN - G8C130601BC | 98 | 0 | Yes | Yes | 25.5 | 21.5 | 4 | 5EDEF7FF000C4FBA94A80594BE2F6580 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-3949 |  | 2015-11-09 | 2015-11-09 09:50 | 2015-11-09 09:50 | TRANE - YCC036F1M0BF | 83 | 0 | Yes | Yes | 26 | 21.5 | 4.5 | 801A5CCF3E34459694409E671338214C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93703-1621 |  | 2015-10-09 | 2015-10-09 08:35 | 2015-10-09 08:35 | RHEEM - RRNA-B036JK06X | 83 | 0 | Yes | Yes | 22.2 | 18.7 | 3.5 | FE1B44B828DB487082EDE2DE9AE68579 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-2372 |  | 2015-10-29 | 2015-10-29 13:03 | 2015-10-29 13:03 | BRYANT - 538JNX036000ABAA | 88 | 0 | Yes | Yes | 28.9 | 23.9 | 5 | F92D9E5F0B0B48A0B76BA9784149F89C |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-1419 |  | 2015-11-04 | 2015-11-04 10:46 | 2015-11-04 10:46 | CARRIER - 485DH024060301 | 140 | 0 | Yes | Yes | 24.4 | 21.5 | 2.9 | 4EFD971DE14F42F28312AACFCED74E98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95134-1355 |  | 2015-11-05 | 2015-11-05 13:06 | 2015-11-05 13:06 | COLEMAN - UNK | 64 | 0 | Yes | Yes | 20.8 | 20.5 | 0.3 | 5C767C17053F46F78D3FF1F7BEC8771E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-1315 |  | 2015-10-13 | 2015-10-13 11:15 | 2015-10-13 11:15 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 19.3 | 18.8 | 0.5 | 5F0F8B621AE74AB682852BE4B77DCEAA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-7138 |  | 2015-10-07 | 2015-10-07 12:34 | 2015-10-07 12:34 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 15.3 | 18.2 | -2.9 | 92D34939CB034BB19FBE2BBFE96B47A7 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-5555 |  | 2015-10-06 | 2015-10-06 08:51 | 2015-10-06 08:51 | RUUD - URKA-A048JK10E | 78 | 0 | Yes | Yes | 18.9 | 19.8 | -0.9 | 580811AA7EA54BA394BC4F22C7935AD2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93701-1229 |  | 2015-11-09 | 2015-11-09 09:00 | 2015-11-09 09:00 | BRYANT - 588ANW042080ACAG | 82 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 20355C79EF7742A3ACD85059BF3721BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6283 |  | 2015-10-13 | 2015-10-13 11:01 | 2015-10-13 11:01 | ICP - PGME60G100E | 229 | 0 | Yes | Yes | 19.5 | 21 | -1.5 | C006B96C9352492D8F408CF4C9B36173 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-6334 |  | 2015-10-26 | 2015-10-26 10:07 | 2015-10-26 10:07 | GOODMAN - CK42-1A | 85 | 0 | Yes | Yes | 21.7 | 18.7 | 3 | B0F931575F4D4A738C04380DDCC52680 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2939 |  | 2015-10-30 | 2015-10-30 14:27 | 2015-10-30 14:27 | RHEEM - | 85 | 0 | Yes | Yes | 16.6 | 19.9 | -3.3 | C410DB2C1C8E437EA986B8A7235FFB82 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-2940 |  | 2015-10-30 | 2015-10-30 14:45 | 2015-10-30 14:45 | BRYANT - 583ANW03606NAAF | 84 | 0 | Yes | Yes | 23.7 | 20.4 | 3.3 | FF43843B14054723AB7BD93EBE891427 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4110 |  | 2015-10-20 | 2015-10-20 13:23 | 2015-10-20 13:23 | RHEEM - 14AJM25A01 | 91 | 0 | Yes | Yes | 15.1 | 18 | -2.9 | 1DA78046C9AE4D3C93DDA2CEF4596906 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-2575 |  | 2015-10-19 | 2015-10-19 11:38 | 2015-10-19 11:38 | GOODMAN - GSH130241CE | 122 | 0 | Yes | Yes | 16.5 | 19.4 | -2.9 | EBC15807D22A4554970966641E92E1AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-9704 |  | 2015-10-20 | 2015-10-20 13:16 | 2015-10-20 13:16 | ICP - HACO30AKA4 | 85 | 0 | Yes | Yes | 18.1 | 18.7 | -0.6 | B8517E722F224FE994DE030B5EEDF757 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-6281 |  | 2015-10-13 | 2015-10-13 16:58 | 2015-10-13 16:58 | CARRIER - 38BRO36300 | 122 | 0 | Yes | Yes | 20.1 | 20.9 | -0.8 | 4490D14CEF9247B0A659E32C0ED04898 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3762 |  | 2015-11-06 | 2015-11-06 11:05 | 2015-11-06 11:05 | CARRIER - UNKNOWN | 93 | 0 | Yes | Yes | 21.3 | 21.5 | -0.2 | 200622503F254E91867351914B243455 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4498 |  | 2015-10-14 | 2015-10-14 17:05 | 2015-10-14 17:05 | YORK - UNKNOWN | 117 | 0 | Yes | Yes | 21.4 | 22.8 | -1.4 | 82D4C79251A743A5B4DCFE608AB7AA2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94559-4110 |  | 2015-10-20 | 2015-10-20 15:44 | 2015-10-20 15:44 | TRANE - 4TTX4036A1000AA | 91 | 0 | Yes | Yes | 16.5 | 18.2 | -1.7 | 67F5FA7569364D638C9F7316C93DFA7D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-3070 |  | 2015-10-08 | 2015-10-08 14:37 | 2015-10-08 15:01 | TRANE - TTR048D100A2 | 86 | 19.4 | Yes | Yes | 17.9 | 18.7 | -0.8 | E879C797E1E0428795A2CDA3D9C5FB0C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.56% | 0.77442 | 43.35% | [5 empty] | Non-TXV | 22.56%
Brentwood | CA | 94513-1579 |  | 2015-10-26 | 2015-10-26 13:06 | 2015-10-26 13:06 | CARRIER - 38CKCO30340 | 85 | 0 | Yes | Yes | 18.6 | 19 | -0.4 | 545D5702FA254B8B803402115FD088C0 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2719 |  | 2015-10-20 | 2015-10-20 10:02 | 2015-10-20 10:22 | RHEEM - RAKA042JAZ | 85 | 5.8 | Yes | Yes | 24.9 | 20.1 | 4.8 | 38859F967B3B4B22A31931D650B3D70A |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Oakley | CA | 94561-2626 |  | 2015-10-26 | 2015-10-26 13:10 | 2015-10-26 13:10 | OTHER - 38TH030300 | 76 | 0 | Yes | Yes | 18.9 | 20.8 | -1.9 | 694A73EF46A74676894D248CBD89EFF3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-3141 |  | 2015-10-15 | 2015-10-15 09:41 | 2015-10-15 09:41 | AMANA - PGD42C0902E | 120 | 0 | Yes | Yes | 25.9 | 19.9 | 6 | 6FA7FE0D001B4B22BAFA4B5E3D16F6E4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5701 |  | 2015-10-12 | 2015-10-12 10:34 | 2015-10-12 10:34 | TRANE - YCY048G1H0AC | 180 | 0 | Yes | Yes | 23.5 | 23.4 | 0.1 | D7645F7C786B487AAD0D87E199137390 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3884 |  | 2015-10-23 | 2015-10-23 09:22 | 2015-10-23 09:23 | OTHER - N/A | 85 | 3.5 | Yes | Yes | 18 | 18.3 | -0.3 | 0DE4158E9DBA4F719611856458F67DAF |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Fresno | CA | 93722-9148 |  | 2015-11-05 | 2015-11-05 14:30 | 2015-11-05 14:30 | CARRIER - 585HJ030040 | 68 | 0 | Yes | Yes | 23.2 | 22 | 1.2 | 36C170035A5C4E58B93018DEAB7D289B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-1420 |  | 2015-10-08 | 2015-10-08 08:33 | 2015-10-08 08:33 | CARRIER - 48GX-048090301AD | 114 | 0 | Yes | Yes | 21.5 | 18.7 | 2.8 | 435A4BEC78C243A583206745592AC1A5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7627 |  | 2015-10-15 | 2015-10-15 11:17 | 2015-10-15 11:17 | GIBSON - JS3BA048KA | 115 | 0 | Yes | Yes | 21.5 | 18.7 | 2.9 | 2AF76594256B414DBA728E3730CD3B1D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-0902 |  | 2015-11-06 | 2015-11-06 14:20 | 2015-11-06 14:20 | BRYANT - 563CN036C | 104 | 0 | Yes | Yes | 26 | 20.5 | 5.5 | F21FC8AD4CFC46F096C453018CD55AF9 |  | R22 | TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-2041 |  | 2015-10-12 | 2015-10-12 13:06 | 2015-10-12 13:06 | CARRIER - 38CKC848370 | 85 | 0 | Yes | Yes | 24.6 | 19.1 | 5.6 | E930653B996A4BC185221B395CC3FC56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-3884 |  | 2015-10-23 | 2015-10-23 14:40 | 2015-10-23 14:41 | OTHER - N/A | 85 | 25.7 | Yes | Yes | 17.8 | 20.4 | -2.6 | 68471D39C42D413CB17FA8FF389437E3 |  | R22 | Non-TXV |  | 30.24% | 0.69765 | 58.11% | [5 empty] | Non-TXV | 30.24%
Vallejo | CA | 94591-3819 |  | 2015-10-05 | 2015-10-05 16:18 | 2015-10-05 16:18 | CARRIER - 38CKC036350 | 85 | 0 | Yes | Yes | 15.9 | 18.6 | -2.7 | 5B505699E5D9439CAF666CABFB9996C9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-3819 |  | 2015-10-05 | 2015-10-05 16:32 | 2015-10-05 16:32 | CARRIER - 38CKC036350 | 85 | 0 | Yes | Yes | 17 | 17.9 | -0.9 | D03CE3AA981A48BCB48F5495B89BBE5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4708 |  | 2015-10-08 | 2015-10-08 16:59 | 2015-10-08 16:59 | TRANE - TTB036C100A1 | 90 | 0 | Yes | Yes | 20.8 | 23.1 | -2.3 | D0516A54B33C4780A07941EB928BEF71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94518-2725 |  | 2015-11-03 | 2015-11-03 09:38 | 2015-11-03 09:38 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 17.4 | 19.4 | -2 | 1E7D38A61ECE4A7F8DFAEE3E27641910 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7833 |  | 2015-10-05 | 2015-10-05 10:22 | 2015-11-05 14:28 | COLEMAN - 9536-901 | 56 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | 784C3D33497F4BAAA04A7FB92FE50291 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-8732 |  | 2015-11-06 | 2015-11-06 11:43 | 2015-11-06 11:43 | CARRIER - HD14648D175B2603AP | 98 | 0 | Yes | Yes | 21 | 18.8 | 2.2 | DD50FB701C3742819BB840BEC35C3BA7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5959 |  | 2015-10-12 | 2015-10-12 12:32 | 2015-10-12 12:32 | CARRIER - 48XN042060301 | 120 | 15.9 | Yes | Yes | 20.8 | 19.4 | 1.4 | 5969EAC24FDE49F9904B3A1876BEC48D |  | R22 | Non-TXV |  | 13.25% | 0.8675 | 25.46% | [5 empty] | Non-TXV | 13.25%
Oakley | CA | 94561-4165 |  | 2015-10-08 | 2015-10-08 15:33 | 2015-10-08 15:33 | CARRIER - 38CKC036350 | 73 | 0 | Yes | Yes | 15.9 | 18.5 | -2.6 | DAA89709B7274A51B0A3643605035678 |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-4165 |  | 2015-10-08 | 2015-10-08 15:46 | 2015-10-08 15:46 | CARRIER - 38CKC036350 | 73 | 0 | Yes | Yes | 14.8 | 17.7 | -2.9 | E5B6497C1E7544BE85C68F727170FBCD |  | R22 | TXV |  | 0% | 1 | 0%
Oakley | CA | 94561-1783 |  | 2015-10-19 | 2015-10-19 13:24 | 2015-10-19 13:24 | CARRIER - 38CKC048370 | 100 | 0 | Yes | Yes | 14.9 | 17.9 | -3 | 925091B87A444A2C83AF19A2F8CF95F7 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-8709 |  | 2015-11-05 | 2015-11-05 14:23 | 2015-11-05 14:23 | OTHER - 38ETG036300 | 136 | 0 | Yes | Yes | 25.3 | 20.9 | 4.4 | 9D14BDA42BEF40239D46D7EA8691BF85 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-3640 |  | 2015-11-04 | 2015-11-04 12:10 | 2015-11-04 12:10 | TRANE - H2RA036S06E | 63 | 0 | Yes | Yes | 25.2 | 21.1 | 4.1 | FBF0444F841F420F833B41831B3A2906 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3207 |  | 2015-10-30 | 2015-10-30 09:51 | 2015-10-30 09:51 | CARRIER - 585A030080YACR | 50 | 0 | Yes | Yes | 26.1 | 20.2 | 6 | F72E4C8AE8C74F41A5658DB1EDFD3A55 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3556 |  | 2015-11-03 | 2015-11-03 13:06 | 2015-11-03 13:06 | PAYNE - PA13NA036000ABAA | 72 | 0 | Yes | Yes | 21.7 | 21.2 | 0.5 | F70633BACDB244388FD79704E23EED31 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-1425 |  | 2015-10-05 | 2015-10-05 09:38 | 2015-10-05 09:38 | ICP - PGC036K060B | 71 | 0 | Yes | Yes | 23 | 19.1 | 3.9 | B34FFFAF445E4B03AAA550568F7F3551 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-6066 |  | 2015-10-22 | 2015-10-22 13:45 | 2015-10-22 13:45 | YORK - D1NH036N05606C | 108 | 0 | Yes | Yes | 20.7 | 22.6 | -1.9 | ED4BE9B6B8A74B60A57A9843F1F3859B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5902 |  | 2015-10-14 | 2015-10-14 12:15 | 2015-10-14 12:15 | BRYANT - 561CJ060-H | 133 | 0 | Yes | Yes | 22 | 23.3 | -1.3 | 51CC284A492547FAAF862CC0DAC9C9A2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-5421 |  | 2015-10-19 | 2015-10-19 15:23 | 2015-10-19 15:23 | AMERICAN STANDARD - YCP036F1M0AB | 109 | 0 | Yes | Yes | 20.6 | 19.4 | 1.2 | 598B3F475143414BB4F1BA3A57901516 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6223 |  | 2015-10-20 | 2015-10-20 14:26 | 2015-10-20 14:27 | OTHER - GR6GD-X36K072X | 112 | 18.6 | Yes | Yes | 23 | 19.8 | 3.2 | 70B00C4AB47E43BBA354A3C309328993 |  | R410A | Non-TXV |  | 16.61% | 0.83393 | 31.92% | [5 empty] | Non-TXV | 16.61%
Bakersfield | CA | 93307-7139 |  | 2015-10-22 | 2015-10-22 13:13 | 2015-10-22 13:13 | OTHER - EADB-037JAS | 85 | 0 | Yes | Yes | 18.8 | 21.5 | -2.7 | E9E130E0FC944C549A6556B4A4493DB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5027 |  | 2015-10-22 | 2015-10-22 14:00 | 2015-10-22 14:00 | LENNOX - LCS13DC-036-230 | 93 | 0 | Yes | Yes | 22.8 | 21 | 1.8 | 3572D26165D64A52A4CE2D43C0FAA4F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6147 |  | 2015-10-13 | 2015-10-13 11:11 | 2015-10-13 11:11 | YORK - UNKNOWN | 125 | 0 | Yes | Yes | 19.7 | 20.2 | -0.4 | 27496C94A580480CBCAD8B59F5CDD344 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6814 |  | 2015-11-06 | 2015-11-06 14:59 | 2015-11-06 14:59 | CARRIER - 38CKB036 | 85 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 47239DCFD0654034860D61F9BFD8C90C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2757 |  | 2015-11-04 | 2015-11-04 09:15 | 2015-11-04 09:15 | GOODMAN - VSX130361EA | 112 | 0 | Yes | Yes | 21 | 20.4 | 0.6 | 3B2AC89BD2324D0CA6F00CEC69D3B6A9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-7669 |  | 2015-10-22 | 2015-10-22 15:26 | 2015-10-22 15:26 | CARRIER - 38CKC036340 | 85 | 0 | Yes | Yes | 19 | 20 | -1 | 9D23B401F16449A9ADF9EF3BDB99E566 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-1137 |  | 2015-10-19 | 2015-10-19 15:01 | 2015-10-19 15:01 | BRYANT - 574DNWA60090NATP | 85 | 16.4 | Yes | Yes | 20.2 | 18.8 | 1.5 | 4344FB1F0D1A4FF59117BE546E8CFDF3 |  | R410A | Non-TXV |  | 19.29% | 0.80706 | 37.08% | [5 empty] | Non-TXV | 19.29%
Bakersfield | CA | 93306-2752 |  | 2015-10-19 | 2015-10-19 11:32 | 2015-10-19 11:32 | OTHER - N/A | 85 | 0 | Yes | Yes | 23.4 | 19.9 | 3.5 | 07B74D1761EF40F8A01FD7A99BE30E2B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-8722 |  | 2015-10-09 | 2015-10-09 12:12 | 2015-10-09 12:12 | YORK - D1NA036N03606C | 69 | 0 | Yes | Yes | 18.2 | 20.2 | -2 | AFF0D29FEFE9479996442067879F3638 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-2819 |  | 2015-11-06 | 2015-11-06 08:47 | 2015-11-06 08:47 | CARRIER - 24ABB342W300 | 93 | 3.5 | Yes | Yes | 20.6 | 20.6 | 0 | 2712FCE7329F4164939B148C26AF4C94 | Add refrigerant: 3.5 oz | R410A | TXV |  | 3.763% | 0.96237 | 7.233% | [5 empty] | TXV | 3.763%
Fresno | CA | 93705-4946 |  | 2015-10-15 | 2015-10-15 13:00 | 2015-10-15 13:00 | CARRIER - 38TK048310 | 178 | 0 | Yes | Yes | 19.9 | 21.5 | -1.6 | 35B590260CFB4F5EB9A26886C79C1E16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3750 |  | 2015-10-19 | 2015-10-19 16:37 | 2015-10-19 16:37 | CARRIER - 38CMC048300 | 137 | 0 | Yes | Yes | 21 | 20.6 | 0.4 | ACD3F0A5700F4C10A4445A300FD3E9B9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-9302 |  | 2015-10-09 | 2015-10-09 13:40 | 2015-10-09 13:40 | GOODMAN - PCB0360581A-REVA | 64 | 0 | Yes | Yes | 21.7 | 22.6 | -0.9 | 82764C812DC64128A37573EA99F18B16 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3519 |  | 2015-11-06 | 2015-11-06 13:32 | 2015-11-06 13:32 | GOODMAN - UNKNOWN | 113 | 0 | Yes | Yes | 23.8 | 21.7 | 2.2 | 8B7F916014A64C248A48622BCB8AA765 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5559 |  | 2015-10-30 | 2015-10-30 13:10 | 2015-10-30 13:10 | YORK - H2RC036S06G | 83 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | 3991B60CF5594A4D89104608D38F40DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5560 |  | 2015-10-30 | 2015-10-30 15:12 | 2015-10-30 15:12 | YORK - H2RC036S06G | 83 | 12.3 | Yes | Yes | 19 | 19.9 | -0.9 | 3DCA56CAE2C7414EA8873C07CB9C6818 |  | R22 | Non-TXV |  | 14.82% | 0.85181 | 28.48% | [5 empty] | Non-TXV | 14.82%
Bakersfield | CA | 93309-5126 |  | 2015-10-20 | 2015-10-20 08:56 | 2015-10-20 08:56 | YORK - D1NA036N03606C | 67 | 0 | Yes | Yes | 19.6 | 18.2 | 1.4 | 40DA8083CCA34CE29A71758654897526 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-2152 |  | 2015-11-04 | 2015-11-04 14:18 | 2015-11-04 14:18 | BRYANT - 550AN042-E | 140 | 0 | Yes | Yes | 23.8 | 18.3 | 5.5 | 3A4F9614036D47D892FA0DB1EE221B38 |  | R410A | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2497 |  | 2015-10-13 | 2015-10-13 14:43 | 2015-10-13 14:43 | YORK - H1RA048S06D | 117 | 0 | Yes | Yes | 23.2 | 24.4 | -1.2 | BDC537EA966E4BC1BD973A84DB9C9C1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-2497 |  | 2015-10-13 | 2015-10-13 14:48 | 2015-10-13 14:48 | YORK - H1RA048S06D | 117 | 0 | Yes | Yes | 21.2 | 22.9 | -1.7 | 8BC9AA1B194B4F85A4C2215957A0A2FE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5102 |  | 2015-10-12 | 2015-10-12 15:11 | 2015-10-12 15:11 | YORK - D6NZ030N03606NXA | 64 | 0 | Yes | Yes | 17.3 | 16.1 | 1.2 | 59D11FC1D49D443CB6707F4A8F7A92F9 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-4721 |  | 2015-10-15 | 2015-10-15 14:00 | 2015-10-15 14:00 | RHEEM - RRKA-A036JK06X | 62 | 0 | Yes | Yes | 19.7 | 19.9 | -0.2 | C716EA2CEB0C4419852C8856FA212E57 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1715 |  | 2015-10-20 | 2015-10-20 22:06 | 2015-10-20 22:06 | OTHER - 24ABB348W310 | 112 | 0 | Yes | Yes | 17.3 | 20 | -2.7 | D4780BC865AF4C2EAB1831D63A4C76CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4637 |  | 2015-11-18 | 2015-11-18 10:54 | 2015-11-18 10:54 | CARRIER - 38THO36300 | 84 | 0 | Yes | Yes | 23 | 20.9 | 2.1 | 3BADA52CA1A44CEEBA938230421AD784 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7034 |  | 2015-11-03 | 2015-11-03 12:27 | 2015-11-03 12:27 | RHEEM - UNKNOWN | 89 | 0 | Yes | Yes | 23.5 | 21 | 2.5 | 6331A99046A64121B111C92E58695CE8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93313-5185 |  | 2015-10-30 | 2015-10-30 11:02 | 2015-10-30 11:03 | YORK - D1NA030N03606C | 72 | 5 | Yes | Yes | 20 | 19.4 | 0.6 | 1B44536E36C741C9B8679F685F9CF8FD |  | R22 | Non-TXV |  | 6.944% | 0.93056 | 13.35% | [5 empty] | Non-TXV | 6.944%
Clovis | CA | 93611-4018 |  | 2015-10-13 | 2015-10-13 12:21 | 2015-10-13 12:21 | BDP - 585A036080YAC | 60 | 0 | Yes | Yes | 21.4 | 20.2 | 1.2 | FEB78E701F07484A8D89495B7AADCF4B |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95148-4342 |  | 2015-11-06 | 2015-11-06 12:57 | 2015-11-06 12:57 | CARRIER - 38CKC060300 | 157 | 0 | Yes | Yes | 20.8 | 20.7 | 0.1 | DFA9BE59BB2E4025B2290C4EE3289CFE |  | R22 | TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1407 |  | 2015-10-29 | 2015-10-29 13:53 | 2015-10-29 13:53 | GOODMAN - CK30-1B | 79 | 0 | Yes | Yes | 17.7 | 20.3 | -2.6 | 6725F39955D540D4B3616248492C6979 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Lafayette | CA | 94549-2424 |  | 2015-11-05 | 2015-11-05 09:32 | 2015-11-05 09:32 | TRANE - TTR048D100A1 | 86 | 0 | Yes | Yes | 21.4 | 20.7 | 0.7 | 1564F9B8D0C647D9AB0B9C7E6E91C1BF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6938 |  | 2015-10-22 | 2015-10-22 15:04 | 2015-10-22 15:04 | RHEEM - RRNA-B048JK08X | 153 | 0 | Yes | Yes | 20.9 | 20.4 | 0.5 | 9428ACBBEBC24AFBA1DF7EC8CD9E1344 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-1307 |  | 2015-10-21 | 2015-10-21 14:05 | 2015-10-21 14:05 | YORK - D1NP048N06506A | 130 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | B56C58778B9D4466A8A09046E0BCC499 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dublin | CA | 94568-3852 |  | 2015-10-20 | 2015-10-20 14:03 | 2015-10-20 14:03 | RHEEM - RAFD-025JAS | 51 | 0 | Yes | Yes | 20.7 | 16.1 | 4.6 | 5933E93E24B544D88963ABD64ADF7C91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2049 |  | 2015-10-26 | 2015-10-26 14:56 | 2015-10-26 14:56 | GOODMAN - N/A | 320 | 0 | Yes | Yes | 20.4 | 19 | 1.5 | D1968782A1884E0CBA59C463FE1D4B97 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-4909 |  | 2015-10-22 | 2015-10-22 09:12 | 2015-10-22 09:12 | PAYNE - PY3GNAA36060NA | 102 | 0 | Yes | Yes | 18.9 | 17.7 | 1.2 | E951B5DD78654164B26DEE38FB76115B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93710-3953 |  | 2015-10-12 | 2015-10-12 10:53 | 2015-10-12 10:53 | ICP - CA5530VKD1 | 74 | 0 | Yes | Yes | 16.8 | 18.8 | -2 | 80772D2782844865AA09BC2FE7586E60 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 33°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-7301 |  | 2015-10-16 | 2015-10-16 10:05 | 2015-10-16 10:05 | OTHER - TCJF36S41S3A | 58 | 0 | Yes | Yes | 19.4 | 19.3 | 0.1 | 51484B2F40AD41C0A3763B02E1571BB3 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-4641 |  | 2015-10-21 | 2015-10-21 08:40 | 2015-10-21 08:40 | BRYANT - 582ANW030060NAAD | 55 | 0 | Yes | Yes | 19.3 | 20.7 | -1.4 | 82E280E9F80E477CAC109984BD9EF820 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-6543 |  | 2015-10-16 | 2015-10-16 12:56 | 2015-10-16 12:56 | GMC - CE36-1GB | 79 | 0 | Yes | Yes | 22.3 | 19 | 3.3 | F0600782FEB64682AF4BCBDB30874A79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5511 |  | 2015-10-30 | 2015-10-30 09:33 | 2015-10-30 09:33 | PAYNE - PA10JA036-G | 72 | 0 | Yes | Yes | 22.2 | 20.2 | 2.1 | 9B5AA3B92156402EA618B2BAD62B1631 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-9445 |  | 2015-11-06 | 2015-11-06 11:35 | 2015-11-06 11:35 | YORK - D2NP036N05606A | 108 | 0 | Yes | Yes | 24.5 | 19.8 | 4.7 | BC06A2F2C6FE49FC9A32A486F324392F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6475 |  | 2015-10-20 | 2015-10-20 12:12 | 2015-10-20 12:13 | OTHER - N/A | 85 | 10.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | 9DCFEBD8EA544F2F9A9AF9B3F899585F |  | R22 | Non-TXV |  | 12.24% | 0.87765 | 23.51% | [5 empty] | Non-TXV | 12.24%
Vallejo | CA | 94591-5616 |  | 2015-10-15 | 2015-10-15 09:27 | 2015-10-15 09:27 | GUARDIAN - GCGD30S41S3A | 62 | 0 | Yes | Yes | 16.5 | 17.5 | -1 | AA274D6652FA40CBB90CD3BEC791DC2B |  | R410A | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1211 |  | 2015-10-27 | 2015-10-27 12:10 | 2015-10-27 12:10 | BRYANT - UNKNOWN | 107 | 0 | Yes | Yes | 24.5 | 20.9 | 3.6 | F17AD9ECC837464AA06DEF78AF101D9B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4188 |  | 2015-10-26 | 2015-10-26 12:14 | 2015-10-26 12:14 | LENNOX - 13ACCC-042-230-01 | 123 | 0 | Yes | Yes | 18 | 19.3 | -1.3 | D620DE3B8A064CF994639F2791CB1C5C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1362 |  | 2015-10-27 | 2015-10-27 16:50 | 2015-10-27 16:50 | PAYNE - PA10JA036-A | 85 | 0 | Yes | Yes | 16 | 18.8 | -2.8 | 00BED9C2B81F44B6B090FEAE2B127530 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Napa | CA | 94558-4250 |  | 2015-10-20 | 2015-10-20 14:43 | 2015-10-20 14:43 | OTHER - 38EH048320 | 85 | 0 | Yes | Yes | 15.5 | 16.7 | -1.2 | 60E442C1D2FD44C0863D9556C95A47E2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4249 |  | 2015-11-03 | 2015-11-03 13:55 | 2015-11-03 13:55 | GOODMAN - GOODMAN | 89 | 0 | Yes | Yes | 17 | 17.4 | -0.4 | DA758D83E4E644728099A8EC687096C0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-3232 |  | 2015-10-22 | 2015-10-22 12:38 | 2015-10-22 12:38 | ICP - PGME36080E | 138 | 0 | Yes | Yes | 18.9 | 18.3 | 0.6 | 68748B2F4B1A4933AAE8C1C142806BEA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Kerman | CA | 93630-1901 |  | 2015-11-03 | 2015-11-03 13:40 | 2015-11-03 13:40 | GOODMAN - GPG1336045M41AD | 85 | 0 | Yes | Yes | 20.4 | 16.8 | 3.6 | E692C7FB35C9471C9F906562256FEFB6 |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8416 |  | 2015-10-22 | 2015-10-22 09:29 | 2015-10-22 09:29 | TRANE - BTD730A100B0 | 74 | 0 | Yes | Yes | 15 | 16.2 | -1.2 | CF375824D15A4AE6A53E8BA74DB063C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7705 |  | 2015-10-20 | 2015-10-20 10:07 | 2015-10-20 10:09 | BRYANT - 582ANW030040AAAD | 57 | 5.5 | Yes | Yes | 19.2 | 18.7 | 0.5 | 33D0898EF6CC4422B3BC9A947D2E0887 |  | R22 | Non-TXV |  | 9.649% | 0.90351 | 18.54% | [5 empty] | Non-TXV | 9.649%
Bakersfield | CA | 93306-2356 |  | 2015-10-19 | 2015-10-19 14:15 | 2015-10-19 14:15 | LENNOX - GCS20R-411-75-4P | 70 | 0 | Yes | Yes | 20 | 17.7 | 2.3 | 9FA559C0A81D4738BF8AF7D3E087C36B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-2408 |  | 2015-10-19 | 2015-10-19 10:58 | 2015-10-19 10:58 | YORK - D1GA030N04806A | 80 | 0 | Yes | Yes | 20.2 | 19.6 | 0.6 | 6437C423733646D1A0E1DCF91C33CCB5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-3104 |  | 2015-11-05 | 2015-11-05 14:52 | 2015-11-05 14:52 | YORK - GFHHTD | 98 | 0 | Yes | Yes | 23.5 | 21 | 2.5 | F8757DF1608246E49EA92D754F7291FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-6380 |  | 2015-10-20 | 2015-10-20 09:30 | 2015-10-20 09:30 | AMANA - APG13480901A | 145 | 0 | Yes | Yes | 22.3 | 20.1 | 2.2 | 0EB5277EFBC04DD0A8A3262EADF7D2F4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-9189 |  | 2015-11-24 | 2015-11-24 10:29 | 2015-11-24 10:47 | CARRIER - 56588060 | 120 | 32.8 | Yes | Yes | 20.9 | 22 | -1.1 | 02C239F480144587A95C97192D549DE2 |  | R22 | Non-TXV |  | 27.33% | 0.72667 | 52.53% | [5 empty] | Non-TXV | 27.33%
Fresno | CA | 93704-2633 |  | 2015-10-20 | 2015-10-20 10:38 | 2015-10-20 10:38 | RHEEM - RRNA-B048JK10X | 153 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | FD60161A90C14F798B722A3A2DE90F35 |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4823 |  | 2015-10-21 | 2015-10-21 08:55 | 2015-10-21 08:55 | OTHER - UNKNOWN | 96 | 0 | Yes | Yes | 24.8 | 21.9 | 3 | 7B30CC5FF6274CD2A96D72E24C450C3F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1151 |  | 2015-10-27 | 2015-10-27 14:30 | 2015-10-27 14:30 | TRANE - BTD736A100B0 | 88 | 0 | Yes | Yes | 20.5 | 18 | 2.5 | 114EEB62BE7D4E5BBAC409070C917EDC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Benicia | CA | 94510-3706 |  | 2015-10-22 | 2015-10-22 10:28 | 2015-10-22 10:28 | HEIL - CA5548VKD2 | 134 | 0 | Yes | Yes | 20.5 | 17.7 | 2.8 | 5B4B82363A1640899A930695A2F40ECD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-5520 |  | 2015-10-20 | 2015-10-20 15:03 | 2015-10-20 15:03 | YORK - D1NA036N05606C | 67 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | BC1C0755F57240D7B8A681E1520DE77D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pleasanton | CA | 94588-3403 |  | 2015-10-20 | 2015-10-20 14:31 | 2015-10-20 14:31 | TAPPAN - CM-42-14-C | 94 | 0 | Yes | Yes | 19.5 | 21.3 | -1.8 | 8C0BF0A5B1274A458344BFDA365F56E5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7165 |  | 2015-10-23 | 2015-10-23 10:42 | 2015-10-23 10:42 | BDP - 585EJW036075ABAE | 82 | 0 | Yes | Yes | 22.8 | 20.4 | 2.4 | A96CD297D51C492D8585944EEBBE2916 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-6363 |  | 2015-10-20 | 2015-10-20 13:02 | 2015-10-20 13:02 | CARRIER - 49LT024300 | 84 | 0 | Yes | Yes | 23.7 | 20.4 | 3.3 | 946E472DE78B4CC6BBC7790FA87B4CA0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3102 |  | 2015-10-30 | 2015-10-30 12:25 | 2015-10-30 12:25 | GOODMAN - CK-36-1B | 76 | 0 | Yes | Yes | 16.5 | 18 | -1.5 | 5B22DFBA08984A60AECD2FAE4B5AD314 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-5621 |  | 2015-10-28 | 2015-10-28 13:14 | 2015-10-28 13:14 | GOODMAN - CKL60-1 | 115 | 0 | Yes | Yes | 18.7 | 17.5 | 1.2 | 9A5BFC4F28544353BE0D39E454F49F47 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6824 |  | 2015-10-22 | 2015-10-22 12:40 | 2015-10-22 12:41 | OTHER - DRC0421BE | 109 | 17.1 | Yes | Yes | 18.1 | 19.9 | -1.8 | F879DDE7C1934B5C98400BC7C524A587 |  | R22 | Non-TXV |  | 15.69% | 0.84312 | 30.15% | [5 empty] | Non-TXV | 15.69%
Fresno | CA | 93711-6020 |  | 2015-10-20 | 2015-10-20 09:02 | 2015-10-20 09:02 | CARRIER - 48XP-048090301 | 179 | 0 | Yes | Yes | 20.2 | 19.9 | 0.3 | 47752F294FF1441EBBD5B94D340DFAE2 |  | R410A | TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-4905 |  | 2015-11-06 | 2015-11-06 11:30 | 2015-11-06 11:30 | GOODMAN - PGB0360775 | 60 | 0 | Yes | Yes | 24 | 19.4 | 4.6 | 80A2D8E9CFEA4C9BA04980FF5C46A075 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-3008 |  | 2015-10-23 | 2015-10-23 08:43 | 2015-10-23 08:43 | TRANE - TTB048C100A0 | 115 | 0 | Yes | Yes | 21.2 | 18.8 | 2.4 | 71626B0C0CAE414F9EC659F6812A8551 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-2211 |  | 2015-10-28 | 2015-10-28 10:30 | 2015-10-28 10:30 | KENMORE - HAC442AKA1 | 272 | 0 | Yes | Yes | 21.7 | 18.8 | 2.9 | B515A2D03C244D13A7217DB01B9A9AF8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-6938 |  | 2015-10-22 | 2015-10-22 09:52 | 2015-10-22 09:52 | RHEEM - RRMA-A042JK08X | 114 | 0 | Yes | Yes | 21.9 | 18.6 | 3.4 | 162346F04EB0470988FF43CC84CF3977 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-9625 |  | 2015-10-26 | 2015-10-26 12:09 | 2015-10-26 12:09 | OTHER - | 85 | 0 | Yes | Yes | 19.9 | 22.1 | -2.2 | 7ADC903BE42A40BBBF505F7D26F2DF01 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2734 |  | 2015-10-30 | 2015-10-30 13:08 | 2015-10-30 13:08 | RHEEM - RRKA-A042JK08E | 70 | 0 | Yes | Yes | 18.2 | 19.9 | -1.7 | 7176F6E449384055AC01FED1DFADD38C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93705-0626 |  | 2015-10-20 | 2015-10-20 13:32 | 2015-10-20 13:32 | CARRIER - 48DL004 | 81 | 0 | Yes | Yes | 18.8 | 20.7 | -1.9 | FA7CBFCD85C449E69F9A7DCC6AFBFA73 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-4044 |  | 2015-10-20 | 2015-10-20 09:21 | 2015-10-20 09:21 | YORK - UNK | 127 | 0 | Yes | Yes | 27.8 | 22.9 | 4.9 | E26CC2CA114E4AAC816D89490E21D277 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4005 |  | 2015-10-23 | 2015-10-23 10:47 | 2015-10-23 10:47 | TEMPSTAR - PGAA30D1K3 | 75 | 0 | Yes | Yes | 18.6 | 20.6 | -2 | B3151289171542AEAB2ED03E928920FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3434 |  | 2015-10-19 | 2015-10-19 11:55 | 2015-10-19 11:55 | BRYANT - 583ANW048090AAAF | 116 | 0 | Yes | Yes | 22.3 | 17.5 | 4.9 | 12D673381AFC46808876FB3F4E3D7D71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95111-3117 |  | 2015-10-30 | 2015-10-30 13:14 | 2015-10-30 13:14 | CARRIER - 24ABA330A320 | 64 | 0 | Yes | Yes | 19.1 | 21.5 | -2.4 | 27E33D933FF7404AA90B4AE8AE900EE4 |  | R410A | TXV |  | 0% | 1 | 0%
San Jose | CA | 95123-3028 |  | 2015-11-02 | 2015-11-02 10:30 | 2015-11-02 10:30 | DAY & NIGHT - UNK | 96 | 0 | Yes | Yes | 19.8 | 21.9 | -2.1 | 204E41DBC2314FDDA17B5B359E94CCE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93720-4220 |  | 2015-10-27 | 2015-10-27 15:30 | 2015-10-27 15:30 | CARRIER - 38TDA036300 | 184 | 0 | Yes | Yes | 23.2 | 20.4 | 2.8 | 7BBE5C3958A04971A2E9612138209FDD |  | R22 | TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3700 |  | 2015-10-27 | 2015-10-27 10:07 | 2015-10-27 10:07 | OTHER - N4A44BGKA100 | 163 | 0 | Yes | Yes | 21.4 | 18.5 | 3 | 04CC89E6FF4A407888CEA927FCCD135A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93304-7237 |  | 2015-10-22 | 2015-10-22 14:04 | 2015-10-22 14:05 | BDP - 5856JW30040ABAF | 58 | 13.6 | Yes | Yes | 21.3 | 19.4 | 1.9 | 54CC4B2A063A40E6956E9F7FE6674F58 |  | R22 | Non-TXV |  | 23.45% | 0.76552 | 45.06% | [5 empty] | Non-TXV | 23.45%
Fresno | CA | 93725-1886 |  | 2015-10-22 | 2015-10-22 10:41 | 2015-10-22 10:41 | LENNOX - 12GCS0423PB | 133 | 0 | Yes | Yes | 15.3 | 16.3 | -1 | 5319A87669AA4F119DA51AEE013DB595 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95112-5258 |  | 2015-10-31 | 2015-10-31 09:23 | 2015-10-31 09:23 | GOODMAN - VSC130361BA | 83 | 0 | Yes | Yes | 23.6 | 23.7 | -0.1 | 6844A78F169E4A949403C6A67BD5E00E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4520 |  | 2015-10-23 | 2015-10-23 14:28 | 2015-10-23 14:28 | DAY & NIGHT - 36/80YAC-106C | 66 | 0 | Yes | Yes | 23.9 | 19.9 | 4 | 570E25569F364DA99B054C27740BD802 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-4348 |  | 2015-10-28 | 2015-10-28 12:48 | 2015-10-28 12:48 | BRYANT - 582ANW024040AA0 | 55 | 0 | Yes | Yes | 17.7 | 19.9 | -2.2 | 48F7FBEACE5F46ECB389AABDCE775242 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7916 |  | 2015-10-22 | 2015-10-22 12:24 | 2015-10-22 12:24 | OTHER - PGF336060K01A1 | 85 | 0 | Yes | Yes | 28.1 | 22.4 | 5.8 | 5883B5ECF5BF421BBA784E25DB59AA6B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-4623 |  | 2015-11-06 | 2015-11-06 14:28 | 2015-11-06 14:28 | CARRIER - 38BRCO30310 | 85 | 0 | Yes | Yes | 20.8 | 20 | 0.8 | 7F6A99F7DF124E0BB0AEE970F442336A |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5323 |  | 2015-10-22 | 2015-10-22 10:39 | 2015-10-22 10:40 | ICP - PGME36G080E | 138 | 9.4 | Yes | Yes | 18.7 | 19.4 | -0.7 | 7EEB1A2445BB417BB217B7E64244F2BB |  | R22 | Non-TXV |  | 6.812% | 0.93188 | 13.09% | [5 empty] | Non-TXV | 6.812%
Antioch | CA | 94509-7775 |  | 2015-10-28 | 2015-10-28 11:31 | 2015-10-28 11:31 | GOODMAN - CKJ60-1C | 149 | 0 | Yes | Yes | 20.5 | 20.2 | 0.4 | 932FD721EA87424E8D37B95C0127653D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2271 |  | 2015-11-06 | 2015-11-06 09:59 | 2015-11-06 09:59 | GOODMAN - G5C130181AA | 95 | 0 | Yes | Yes | 23.3 | 18.8 | 4.5 | 00C83AD575F14DC1AF4863A3A432B882 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2285 |  | 2015-11-06 | 2015-11-06 15:38 | 2015-11-06 15:38 | GOODMAN - CCRT-18-L | 96 | 0 | Yes | Yes | 23 | 19.8 | 3.2 | 3412B692765349FBB88E86F988F4325B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93728-2207 |  | 2015-10-23 | 2015-10-23 12:07 | 2015-10-23 13:13 | YORK - D1NA036NO5606C | 67 | 0 | Yes | Yes | 19.3 | 19.2 | 0.1 | 3C6FB264E8F640EBA516167E64652409 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4910 |  | 2015-11-03 | 2015-11-03 12:01 | 2015-11-03 12:01 | CARRIER - 561CJ030-D | 68 | 0 | Yes | Yes | 23.6 | 22 | 1.6 | F4A76A39A1F54182AA426D7900F7BD37 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Sanger | CA | 93657-2285 |  | 2015-11-06 | 2015-11-06 15:06 | 2015-11-06 15:06 | GOODMAN - CRT18-1 | 94 | 0 | Yes | Yes | 20.5 | 18.8 | 1.7 | 9384BA651C9F4251808D3F1AE082D098 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94520-4723 |  | 2015-11-04 | 2015-11-04 15:41 | 2015-11-04 15:41 | OTHER - UNKNOWN | 72 | 0 | Yes | Yes | 19.3 | 20.9 | -1.6 | 0A9DEB4C4EF84675A3AF0D773279AE23 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3622 |  | 2015-11-06 | 2015-11-06 10:16 | 2015-11-06 10:16 | HEIL - C5548 | 134 | 0 | Yes | Yes | 22 | 19 | 3 | 6F0B89966F124CC1BC7982BA66E536DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-7892 |  | 2015-10-20 | 2015-10-20 10:36 | 2015-10-20 10:36 | OTHER - N/A | 85 | 0 | Yes | Yes | 22.7 | 19.9 | 2.8 | 4F6F2D137147422BA76CF97B4C6BAB79 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-5302 |  | 2015-10-23 | 2015-10-23 09:09 | 2015-10-23 09:09 | TRANE - TTR042D100 | 81 | 0 | Yes | Yes | 22.3 | 20.7 | 1.6 | 3063B12D7B01435F8AE71E66A0429690 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Reedley | CA | 93654-2508 |  | 2015-10-30 | 2015-10-30 10:33 | 2015-10-30 10:33 | RHEEM - RRPLB060JK10X | 172 | 0 | Yes | Yes | 25.6 | 19.9 | 5.7 | D04DEA74CDE44D75A40CE096BBDFAAF7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93702-1241 |  | 2015-10-26 | 2015-10-26 08:45 | 2015-10-26 08:45 | YORK - D2NP036N056O6A | 108 | 0 | Yes | Yes | 21.6 | 18.2 | 3.4 | BF26B314398348D3BE1ECD208C22BD3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7350 |  | 2015-10-30 | 2015-10-30 16:42 | 2015-10-30 16:42 | GOODMAN - K36-1A | 73 | 0 | Yes | Yes | 23.4 | 21 | 2.4 | 30598820545F45139A4E96D40B86408C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94509-4535 |  | 2015-10-30 | 2015-10-30 15:21 | 2015-10-30 15:21 | RHEEM - UNK | 85 | 0 | Yes | Yes | 19.7 | 21.7 | -2 | D662B768ED7246A5BE78C43EE825EB98 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93307-5530 |  | 2015-10-23 | 2015-10-23 10:00 | 2015-10-23 10:00 | CARRIER - 48SS-024040311-- | 44 | 12.3 | Yes | Yes | 21.9 | 19.4 | 2.5 | FF15EC086A644EAD8A7FA696229D0669 |  | R22 | Non-TXV |  | 27.95% | 0.72045 | 53.72% | [5 empty] | Non-TXV | 27.95%
Vacaville | CA | 95687-8217 |  | 2015-11-16 | 2015-11-16 10:45 | 2015-11-16 10:45 | CARRIER - 24ABB348A310 | 112 | 0 | Yes | Yes | 16.7 | 18.3 | -1.6 | 27BB7746AA604451974901638AB3EC11 |  | R410A | TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-2098 |  | 2015-10-27 | 2015-10-27 13:35 | 2015-10-27 13:35 | CARRIER - 38CKC036340 | 70 | 0 | Yes | Yes | 21.9 | 20.6 | 1.4 | 40427C1B954841D7952573F8F21A0C2D |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-3833 |  | 2015-10-29 | 2015-10-29 12:00 | 2015-10-29 12:00 | ICP - NPGAD47D1K5 | 215 | 18 | Yes | Yes | 23.3 | 17.7 | 5.6 | 448340B26CF0417C934D466310BBBB72 |  | R22 | Non-TXV |  | 8.372% | 0.91628 | 16.09% | [5 empty] | Non-TXV | 8.372%
Santa Rosa | CA | 95401-4463 |  | 2015-10-22 | 2015-10-22 14:12 | 2015-10-22 14:12 | ICP - CACO60AKC4 | 85 | 0 | Yes | Yes | 23.8 | 19.6 | 4.3 | 3DDA0A0326AC44D893126FEDBAF0D7B6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-3274 |  | 2015-11-03 | 2015-11-03 09:27 | 2015-11-03 09:27 | BRYANT - 561CJ024 | 85 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | 4385140272D946E484ABEF51A1000286 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2041 |  | 2015-11-06 | 2015-11-06 11:39 | 2015-11-06 11:39 | TRANE - ATTXA048 | 85 | 0 | Yes | Yes | 17.1 | 15.5 | 1.6 | F0AF50B44863498185587999189E8A90 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Concord | CA | 94519-2149 |  | 2015-11-05 | 2015-11-05 10:29 | 2015-11-05 10:29 | PAYNE - PA13NA060-E | 123 | 0 | Yes | Yes | 22.4 | 20 | 2.4 | A9BA634EC31E40C2860899081A4F4A93 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-0000 |  | 2015-10-29 | 2015-10-29 13:00 | 2015-10-29 13:00 | GOODMAN - GSC130421AC | 137 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | 07C05669358A4171958A79D070D605E9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-7322 |  | 2015-11-06 | 2015-11-06 11:44 | 2015-11-06 11:44 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 17.1 | 17.6 | -0.5 | 3C6EAF8EF3FE459692988E4D564C6913 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-4967 |  | 2015-11-16 | 2015-11-16 11:49 | 2015-11-16 11:49 | CARRIER - 24ABB330W310 | 74 | 0 | Yes | Yes | 16.5 | 19.1 | -2.6 | 39B4475C97214B1DA6561457B4E63EED |  | R410A | TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-4308 |  | 2015-10-22 | 2015-10-22 11:39 | 2015-10-22 11:39 | AMERICAN STANDARD - 2A7B30421000AA | 99 | 0 | Yes | Yes | 18.8 | 18.3 | 0.5 | 3040D9274BD4458DAA4145326234CC7A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Brentwood | CA | 94513-1900 |  | 2015-10-28 | 2015-10-28 12:32 | 2015-10-28 12:32 | CARRIER - 38TH060300 | 163 | 0 | Yes | Yes | 21.1 | 19.3 | 1.8 | B573B6479D2A4EA892E0DD8AA808928A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-1941 |  | 2015-10-29 | 2015-10-29 15:07 | 2015-10-29 15:07 | YORK - D1NA036N05606C | 67 | 19.8 | Yes | Yes | 18.8 | 19.9 | -1.1 | 5FE57BD59E3740508B637E2E8A4F761A |  | R22 | Non-TXV |  | 29.55% | 0.70448 | 56.79% | [5 empty] | Non-TXV | 29.55%
Bakersfield | CA | 93307-5141 |  | 2015-10-23 | 2015-10-23 10:45 | 2015-10-23 10:45 | YORK - DBYP-F036N70A | 108 | 0 | Yes | Yes | 19.5 | 19.9 | -0.4 | 9E65EA7690E641FBA6EB7EEF62EADD9D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94589-1645 |  | 2015-10-22 | 2015-10-22 14:21 | 2015-10-22 14:21 | TRANE - 2TTX4036B1000AA | 118 | 0 | Yes | Yes | 15 | 17.2 | -2.2 | BC3A67ED1DF24BF7BE0C6A3012449C15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5659 |  | 2015-11-12 | 2015-11-12 10:53 | 2015-11-12 10:53 | TRANE - BTD748A100B0 | 152 | 0 | Yes | Yes | 18.9 | 18.8 | 0.1 | E04CAB76F2D64E3F9E6FBF7E53F7D016 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-5813 |  | 2015-10-28 | 2015-10-28 13:12 | 2015-10-28 13:12 | CARRIER - N/A | 85 | 0 | Yes | Yes | 18 | 17.9 | 0.1 | C71247A343C149B7B28B159D2CDE0BD0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5806 |  | 2015-11-06 | 2015-11-06 14:12 | 2015-11-06 14:12 | OTHER - 561AJ036 | 85 | 0 | Yes | Yes | 24 | 20.6 | 3.4 | 5F9990BF25CD4CDCB5645BF06DFF524C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1347 |  | 2015-10-27 | 2015-10-27 10:33 | 2015-10-27 10:33 | RUUD - UAMA-048JBZ | 172 | 0 | Yes | Yes | 17 | 17.6 | -0.6 | 08E13215039940E0BC6730AEDAB99D81 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Hercules | CA | 94547-5436 |  | 2015-10-29 | 2015-10-29 13:09 | 2015-10-29 13:09 | CARRIER - 38CKC060370 | 85 | 0 | Yes | Yes | 16.7 | 17.7 | -1 | 6DCFA8A98F64415EAC7C92DB0C26D69C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4452 |  | 2015-11-20 | 2015-11-20 10:22 | 2015-11-20 10:22 | OTHER - N/A | 74 | 0 | Yes | Yes | 21 | 15.6 | 5.5 | 2A23FF18430E44D581C9EFAB70824D15 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4514 |  | 2015-10-29 | 2015-10-29 10:31 | 2015-10-29 10:31 | GOODMAN - GPG1436040M41AA | 62 | 0 | Yes | Yes | 23.4 | 18.8 | 4.6 | 39E7A365D7454C13B3E93523ED29E213 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2580 |  | 2015-11-06 | 2015-11-06 13:23 | 2015-11-06 13:46 | CARRIER - 38EZGO48300 | 125 | 10.7 | Yes | Yes | 19.5 | 19.5 | 0 | DB4C257DCA4E42218137C9D5F06F89D8 |  | R410A | TXV |  | 8.56% | 0.9144 | 16.45% | [5 empty] | TXV | 8.56%
Fairfield | CA | 94533-8108 |  | 2015-10-27 | 2015-10-27 11:30 | 2015-10-27 11:30 | RHEEM - RAFD036JAS | 80 | 0 | Yes | Yes | 15.5 | 18 | -2.5 | 5DB23DE5B1C64DF89D2538F6AA3A6FDA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4555 |  | 2015-10-28 | 2015-10-28 13:12 | 2015-10-28 13:12 | BRYANT - 582ANW036060ABAF | 72 | 0 | Yes | Yes | 17.7 | 19.9 | -2.2 | 8F9DCAC29F8445E49FBB715040E3AD31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93309-4900 |  | 2015-10-28 | 2015-10-28 15:21 | 2015-10-28 15:21 | AMERICAN STANDARD - YCZ036F1M0BD | 85 | 0 | Yes | Yes | 21.6 | 22.1 | -0.5 | F80CD897621F4FC983E21D4E3FBD3354 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6759 |  | 2015-11-05 | 2015-11-05 15:51 | 2015-11-05 15:51 | OTHER - TCA042AKA5 | 98 | 0 | Yes | Yes | 16.2 | 17.4 | -1.2 | 7FF4A23E1B794E29A341ABB4ADE943F0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4507 |  | 2015-10-30 | 2015-10-30 11:31 | 2015-10-30 11:31 | PAYNE - PA10JA036-C | 72 | 0 | Yes | Yes | 20.1 | 19.9 | 0.2 | A3BC7218D2C749F0941998FB1748ED1B |  | R22 | TXV |  | 0% | 1 | 0%
San Jose | CA | 95124-5241 |  | 2015-10-31 | 2015-10-31 10:39 | 2015-10-31 10:39 | OTHER - S3BA-036K | 90 | 0 | Yes | Yes | 24.2 | 23.5 | 0.7 | 872D66BB9B004DD78675963FE93D7A36 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-3414 |  | 2015-11-12 | 2015-11-12 11:40 | 2015-11-12 11:40 | RUUD - UAKA-030JAZ | 66 | 0 | Yes | Yes | 17.7 | 18.7 | -1 | 7860DBFEC15D42A6A7DC2D692370220B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6561 |  | 2015-11-12 | 2015-11-12 12:23 | 2015-11-12 12:23 | RHEEM - UNK | 69 | 0 | Yes | Yes | 17.3 | 18.7 | -1.4 | 2C91C7F3DA214BC19E48BBD70B647F8F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-1863 |  | 2015-11-10 | 2015-11-10 16:25 | 2015-11-10 16:25 | DAY & NIGHT - N4A336 | 85 | 0 | Yes | Yes | 22 | 19.9 | 2.1 | A5FA792144804220A6BF11AA12971088 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8523 |  | 2015-11-04 | 2015-11-04 09:41 | 2015-11-04 09:41 | CARRIER - 38TH048 | 85 | 0 | Yes | Yes | 15.5 | 18.3 | -2.8 | C16BCA51956F4D08BC867AA5E7E4DAD7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Danville | CA | 94526-6247 |  | 2015-10-30 | 2015-10-30 08:07 | 2015-10-30 08:07 | UNITARY PRODUCTS GROUP - AC030M1021CA | 57 | 0 | Yes | Yes | 25.1 | 21.2 | 3.9 | 63E901D17AED4D65B91DA3A3084DC084 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-2104 |  | 2015-11-04 | 2015-11-04 10:03 | 2015-11-04 10:03 | COMFORT AIRE - RSD1048-1Z | 112 | 0 | Yes | Yes | 24.6 | 19.9 | 4.7 | F29FEA02A9EA477C98A3B2C092DA15A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6210 |  | 2015-11-03 | 2015-11-03 16:05 | 2015-11-03 16:05 | RHEEM - UNKNOWN | 108 | 0 | Yes | Yes | 21.7 | 21.8 | 0 | 9F41C0D7CC5145C2BE63670FA8107D74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93704-4352 |  | 2015-11-05 | 2015-11-05 11:33 | 2015-11-05 11:33 | YORK - DAYP-F036N070A | 108 | 0 | Yes | Yes | 19.8 | 19.1 | 0.7 | FD5EE9DE1E6D4A5BA18F213413835B70 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vallejo | CA | 94591-8561 |  | 2015-10-30 | 2015-10-30 13:39 | 2015-10-30 13:39 | GOODMAN - CLK49-1 | 109 | 0 | Yes | Yes | 17.5 | 18.4 | -0.9 | 291FF26C8B5A4D2BB63BDFFC0BB2CAE1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95135-2217 |  | 2015-11-06 | 2015-11-06 08:52 | 2015-11-06 08:52 | CARRIER - 38CKB060300 | 158 | 0 | Yes | Yes | 22.6 | 20.9 | 1.7 | EC1ED20672584282B174674DE7D1DB33 |  | R22 | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-4378 |  | 2015-10-28 | 2015-10-28 10:02 | 2015-10-28 10:02 | RHEEM - | 85 | 12 | Yes | Yes | 17.3 | 17.7 | -0.4 | 06C92002D9D14CA9A3A39DC4343FC69C |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Vallejo | CA | 94591-6345 |  | 2015-10-30 | 2015-10-30 10:14 | 2015-10-30 10:14 | CARRIER - 38CKC042300 | 85 | 0 | Yes | Yes | 15.1 | 17.7 | -2.6 | D4F256C0E1C0472B84C95EC4DFEC47FC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-4111 |  | 2015-10-27 | 2015-10-27 12:37 | 2015-10-27 12:37 | TRANE - 4TTB3036E1000AA | 92 | 0 | Yes | Yes | 15.5 | 18 | -2.5 | E0BB6CDEB97B496D9F5542BDDC98FA4D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7341 |  | 2015-11-16 | 2015-11-16 10:10 | 2015-11-16 10:10 | LENNOX - 12ACX03023017 | 82 | 0 | Yes | Yes | 22.1 | 19.7 | 2.4 | 4AA7C98A20094DF3A6D04C57D8682D7A |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93305-2126 |  | 2015-10-29 | 2015-10-29 10:28 | 2015-10-29 10:28 | ICP - PGAD42D1K6 | 180 | 0 | Yes | Yes | 23 | 19.4 | 3.6 | 79A18BD983EC4C0BB3AC42453983A678 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-3761 |  | 2015-11-03 | 2015-11-03 12:35 | 2015-11-03 12:35 | PAYNE - 591ANX036 | 85 | 0 | Yes | Yes | 22 | 19.3 | 2.7 | AC692C9B632A471BBF586CDEE5AFEEE7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-0000 |  | 2015-10-30 | 2015-10-30 14:05 | 2015-10-30 14:05 | CARRIER - UNKNOWN | 113 | 0 | Yes | Yes | 19.5 | 20.4 | -0.9 | 41B12811576B40B4838E20EE0ABB9A3D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Suisun City | CA | 94585-2402 |  | 2015-11-04 | 2015-11-04 11:54 | 2015-11-04 11:54 | CARRIER - 38BRB036 | 85 | 0 | Yes | Yes | 15.6 | 18.6 | -3 | F99895D1C6244622BF57D98E72380C21 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-2923 |  | 2015-11-10 | 2015-11-10 09:56 | 2015-11-10 09:56 | CARRIER - 38TKB030 | 85 | 0 | Yes | Yes | 20 | 20.1 | -0.1 | FFAB5C2081734A7FA83C67D51B3CA488 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-2923 |  | 2015-11-10 | 2015-11-10 10:01 | 2015-11-10 10:01 | CARRIER - 38TKB030 | 85 | 0 | Yes | Yes | 24 | 20.2 | 3.9 | 93E7744E4B844930A06667832F8FAE1C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-1528 |  | 2015-11-11 | 2015-11-11 15:39 | 2015-11-11 15:39 | RHEEM - RACC-036JAQ | 69 | 0 | Yes | Yes | 22.4 | 21.7 | 0.7 | 348944A55076457694C31AE26271D1B0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-2343 |  | 2015-11-05 | 2015-11-05 14:39 | 2015-11-05 14:39 | OTHER - 561CJ036 | 85 | 0 | Yes | Yes | 19.5 | 18.3 | 1.2 | DEB02A14E1404666A00B7C7ACB4F4A1E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-6538 |  | 2015-11-05 | 2015-11-05 13:31 | 2015-11-05 13:31 | CARRIER - 38BRC042 | 85 | 0 | Yes | Yes | 16.5 | 17.7 | -1.2 | 14C85E6286504CE1A60C212108C4549D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3647 |  | 2015-11-17 | 2015-11-17 12:07 | 2015-11-17 12:07 | GOODMAN - UNK | 75 | 0 | Yes | Yes | 24.8 | 21.2 | 3.6 | E61537149D594D079E05F64CEA1640A4 |  | R410A | TXV |  | 0% | 1 | 0%
Bakersfield | CA | 93306-6842 |  | 2015-10-30 | 2015-10-30 09:47 | 2015-10-30 09:47 | DUCANE - AC10B48-A | 100 | 0 | Yes | Yes | 22.1 | 18.6 | 3.6 | D821D59596BE4D42BC368D3DD842DEE5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7805 |  | 2015-11-05 | 2015-11-05 12:12 | 2015-11-05 12:12 | AMERICAN STANDARD - 4TTB036 | 92 | 0 | Yes | Yes | 20 | 17.7 | 2.3 | 1B831A804A0F455EBC720624DF405299 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94534-7805 |  | 2015-11-05 | 2015-11-05 12:18 | 2015-11-05 12:18 | AMERICAN STANDARD - 4TTB036 | 92 | 0 | Yes | Yes | 23.2 | 18.3 | 4.9 | 9EFDF66322C042EA9B6680EC7B2BE4F9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-5313 |  | 2015-11-06 | 2015-11-06 09:54 | 2015-11-06 09:54 | PAYNE - PA10JA036-A | 83 | 0 | Yes | Yes | 16.4 | 18.8 | -2.4 | DFC561F0907945A38FB2F3C4C267E0E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4833 |  | 2015-10-30 | 2015-10-30 10:12 | 2015-10-30 10:12 | GOODMAN - GSX130301BB | 70 | 0 | Yes | Yes | 21.9 | 19.6 | 2.3 | C8C569ACBFE14010ACA375D6C3BEC6C4 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-6733 |  | 2015-11-16 | 2015-11-16 14:28 | 2015-11-16 14:28 | PAYNE - PA10JA048A | 103 | 0 | Yes | Yes | 22.2 | 19.9 | 2.3 | 1B080D72B43747229D07D8069C90EBB2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7338 |  | 2015-11-23 | 2015-11-23 12:44 | 2015-11-23 12:44 | CARRIER - 38EH030340 | 120 | 0 | Yes | Yes | 17.9 | 18.8 | -0.9 | 779DD828E546412B9E6C02B317C9AFED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Bay Point | CA | 94565-6793 |  | 2015-11-17 | 2015-11-17 10:14 | 2015-11-17 10:14 | CARRIER - 38CKB036330 | 84 | 0 | Yes | Yes | 20.5 | 17.2 | 3.3 | 0D555F71F7FA49E3A554DCE8CD36EF74 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-6081 |  | 2015-11-05 | 2015-11-05 09:21 | 2015-11-05 09:21 | CARRIER - 591AN036-A | 83 | 0 | Yes | Yes | 19.2 | 18.8 | 0.5 | AC55F3461E8B4F5DAD0C34110F779426 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7408 |  | 2015-11-17 | 2015-11-17 16:56 | 2015-11-17 16:56 | RHEEM - RHE036 | 91 | 0 | Yes | Yes | 19.5 | 19 | 0.5 | 27AF44A0D485498B96C32BBE84A006F8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fairfield | CA | 94533-7716 |  | 2015-11-10 | 2015-11-10 11:18 | 2015-11-10 11:18 | TRANE - TTR748 | 158 | 0 | Yes | Yes | 22.5 | 19.1 | 3.4 | 540EC51170EE42B1831FCF072B4AEC7B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1943 |  | 2015-11-11 | 2015-11-11 09:07 | 2015-11-11 09:07 | CARRIER - 38CKC024330 | 56 | 0 | Yes | Yes | 17.4 | 20.1 | -2.7 | 7E7790FDC68540948FF3296A6DDF1962 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-1901 |  | 2015-11-11 | 2015-11-11 10:04 | 2015-11-11 10:04 | RHEEM - UNK | 53 | 0 | Yes | Yes | 19.1 | 17.6 | 1.5 | 86F55115F4A4404C8879C85EC00E5B5D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-4322 |  | 2015-11-11 | 2015-11-11 11:56 | 2015-11-11 11:56 | LENNOX - 12ACB36-5P | 103 | 0 | Yes | Yes | 20.3 | 21.5 | -1.2 | B1AF532F96B74420A4A47DCC3060CCA7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95136-1337 |  | 2015-11-04 | 2015-11-04 09:40 | 2015-11-04 09:40 | COLEMAN - 7836-901 | 68 | 0 | Yes | Yes | 21.5 | 21.4 | 0.1 | EED13D9AFC5643D083429F6F96B07D27 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3840 |  | 2015-11-11 | 2015-11-11 11:00 | 2015-11-11 11:00 | TRANE - YCX030G1MOAC | 85 | 0 | Yes | Yes | 15.7 | 16.5 | -0.8 | C8692DEE67564AF494E4E20ABAC0292D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Woodland | CA | 95695-5458 |  | 2015-11-05 | 2015-11-05 12:00 | 2015-11-05 12:00 | GOODMAN - CE361GB | 79 | 0 | Yes | Yes | 18.5 | 20.2 | -1.7 | ED4E06DD91BA4181A2E60FAE9E479CE3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-7328 |  | 2015-11-23 | 2015-11-23 16:49 | 2015-11-23 16:49 | CARRIER - 38EH030340 | 125 | 0 | Yes | Yes | 15.9 | 18.8 | -2.9 | 95F849D8A08C420D8C24151C6E6BF671 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Pittsburg | CA | 94565-3750 |  | 2015-11-16 | 2015-11-16 09:15 | 2015-11-16 09:15 | CARRIER - 38CKCO42350 | 93 | 0 | Yes | Yes | 17.9 | 17.7 | 0.2 | 665F6B90816C4C6C9E8CF934F9171BD5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95129-4228 |  | 2015-11-04 | 2015-11-04 08:48 | 2015-11-04 08:48 | GOODMAN - A5C130421AA | 143 | 0 | Yes | Yes | 18.1 | 18.8 | -0.7 | D7BCB58383704A7884D836A2E4E7969A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Antioch | CA | 94531-7156 |  | 2015-11-20 | 2015-11-20 09:29 | 2015-11-20 09:29 | YORK - UNK | 85 | 0 | Yes | Yes | 21.9 | 21.5 | 0.4 | CBBD40DDB59E40B595F12ECCD74D07FF |  | R22 | Non-TXV |  | 0% | 1 | 0%
San Jose | CA | 95121-1347 |  | 2015-11-06 | 2015-11-06 13:39 | 2015-11-06 13:39 | CARRIER - 38CKC042310 | 81 | 0 | Yes | Yes | 24.2 | 21.5 | 2.7 | 0A8A16CDD3634A6492DC5E4BB61A6E62 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-7185 |  | 2015-11-20 | 2015-11-20 11:34 | 2015-11-20 11:34 | RHEEM - RAMC036JBZ | 85 | 0 | Yes | Yes | 23 | 18 | 5 | 3B3082199FF1436C864E5EFE049CA322 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-7185 |  | 2015-11-20 | 2015-11-20 11:49 | 2015-11-20 11:49 | RHEEM - RAMC-036JBZ | 85 | 0 | Yes | Yes | 25.5 | 20.4 | 5.1 | 2E70A3180DA34762A50E2315196C63B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2312 |  | 2015-11-20 | 2015-11-20 13:36 | 2015-11-20 13:36 | PAYNE - N/A | 85 | 0 | Yes | Yes | 22.3 | 17.2 | 5.1 | A05E5480B936497CBFF69DFBBB4398A3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1461 |  | 2015-11-13 | 2015-11-13 11:08 | 2015-11-13 11:28 | UNITARY PRODUCTS GROUP - H1RDO36S06G | 145 | 9.4 | Yes | Yes | 21.1 | 15.9 | 5.2 | 013F331E611B48B4BBDF2A5639561400 |  | R22 | TXV |  | 6.483% | 0.93517 | 12.46% | [5 empty] | TXV | 6.483%
Vacaville | CA | 95687-3478 |  | 2015-11-23 | 2015-11-23 13:30 | 2015-11-23 13:30 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 21.3 | 18.2 | 3.1 | 2A92E3BD911A469CBDAB1BA307FB3492 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3125 |  | 2015-11-20 | 2015-11-20 15:25 | 2015-11-20 15:46 | YORK - H2RCO42S06HA | 109 | 19.8 | Yes | Yes | 19.2 | 19.1 | 0.1 | A1B1BB37E45E467FAF3C2C5E39FEC565 |  | R22 | Non-TXV |  | 18.17% | 0.81835 | 34.91% | [5 empty] | Non-TXV | 18.17%
Stockton | CA | 95207-2356 |  | 2015-11-20 | 2015-11-20 09:15 | 2015-11-20 09:15 | HEIL - PGCO36KO80A | 71 | 0 | Yes | Yes | 21 | 19.5 | 1.5 | 96046BC7E53944C2A8156BAA972B35ED |  | R22 | Non-TXV |  | 0% | 1 | 0%
Vacaville | CA | 95688-2128 |  | 2015-11-23 | 2015-11-23 16:12 | 2015-11-23 16:12 | GE - UNK | 85 | 0 | Yes | Yes | 19.8 | 19.9 | -0.1 | 2980AB4D9B7C4212AB42351B4FF84C60 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-3059 |  | 2015-11-13 | 2015-11-13 14:24 | 2015-11-13 14:24 | TRANE - 4TTX6036A1000AA | 106 | 0 | Yes | Yes | 16.9 | 17.2 | -0.3 | 2678F668B6B143FAB317A52E610FA334 |  | R410A | TXV |  | 0% | 1 | 0%
Vacaville | CA | 95687-5811 |  | 2015-11-23 | 2015-11-23 09:30 | 2015-11-23 09:30 | GOODMAN - GSX13036BA | 95 | 0 | Yes | Yes | 23 | 19.3 | 3.7 | C4C6202ADB354E508C4822B01F3B4216 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3441 |  | 2012-05-21 | 2012-05-21 11:19 | 2012-05-21 11:41 | CARRIER - 585CJ036075 | 84 | 3.7 | Yes | Yes | 18.5 | 20.9 | -2.4 | BFFD066E312949BB81CB3A8CA8EFEC4F |  | R22 | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Los Banos | CA | 93635-8800 |  | 2012-08-14 | 2012-08-14 14:39 | 2012-08-14 15:01 | BRYANT - 561CJ048G | 98 | 10.1 | Yes | Yes | 17.7 | 17.5 | 0.2 | B2A331CB6A334D43BEF59C6A7DD5D67F |  | R22 | Non-TXV |  | 10.31% | 0.89694 | 19.81% | [5 empty] | Non-TXV | 10.31%
Grass Valley | CA | 95945-5225 |  | 2012-05-08 | 2012-05-08 15:05 | 2012-05-08 15:28 | CARRIER - 38CKC024340 | 85 | 25.2 | Yes | Yes | 18 | 20.4 | -2.4 | D7386DC255C14EAF80ABE2FA39CD3E1B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 29.65% | 0.70353 | 56.98% | [5 empty] | Non-TXV | 29.65%
Grass Valley | CA | 95945-5633 |  | 2012-05-30 | 2012-05-30 13:58 | 2012-05-30 14:23 | LENNOX - HSS-41-2A | 84 | 14.6 | Yes | Yes | 22 | 19.7 | 2.3 | 73C36567D73F4DA9BB6A1FFF8FE69C6E |  | R22 | Non-TXV |  | 17.38% | 0.82619 | 33.4% | [5 empty] | Non-TXV | 17.38%
Chico | CA | 95926-2619 |  | 2012-08-01 | 2012-08-01 08:50 | 2012-08-01 09:22 | LENNOX - GCS10-411-75-1P | 73 | 2.1 | Yes | Yes | 23.1 | 19.4 | 3.8 | 0A611932C4654969A99F969B7EC70868 |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Chico | CA | 95973-7816 |  | 2012-08-13 | 2012-08-13 09:36 | 2012-08-13 09:59 | BRYANT - 604BNX02400AB | 117 | 8.3 | Yes | Yes | 20.7 | 21.8 | -1.1 | DEB1E31360094D12A430593ACC3DA842 |  | R410A | Non-TXV |  | 7.094% | 0.92906 | 13.63% | [5 empty] | Non-TXV | 7.094%
Grass Valley | CA | 95945-9031 |  | 2012-06-14 | 2012-06-14 12:04 | 2012-06-14 12:22 | GOODMAN - CLJ36-1A | 109 | 18.4 | Yes | Yes | 22 | 19.3 | 2.7 | D463A402DC2B46A3B035D015ABAC4638 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. |  |  |  | 16.88% | 0.83119 | 32.44% | [5 empty] | 0 | 16.88%
Chico | CA | 95973-0957 |  | 2012-05-24 | 2012-05-24 13:24 | 2012-05-24 13:24 | PAYNE - 24RAC 1S8C | 48 | 0 | Yes | Yes | 22.4 | 21 | 1.4 | 55D7FC145917425AB1D7348067C0262B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-2927 |  | 2012-08-01 | 2012-08-01 08:04 | 2012-08-01 08:37 | DAY & NIGHT - UNK | 75 | -6.2 | Yes | Yes | 23.3 | 21 | 2.3 | 624FFD6D62D34B3BB756771212C6AD90 |  | R22 | Non-TXV |  | -8.267% | 1.0827 | 2.315% |  |  |  |  | Non-TXV |  |  | -8.267%
Red Bluff | CA | 96080-2576 |  | 2012-08-02 | 2012-08-02 13:24 | 2012-08-02 13:57 | BRYANT - H2RA030S06D | 62 | 5.5 | Yes | Yes | 22.4 | 21.9 | 0.5 | 0AEC599F2A194BA4AEB4816FED8AFC6B |  | R22 | Non-TXV |  | 8.871% | 0.91129 | 17.05% | [5 empty] | Non-TXV | 8.871%
Red Bluff | CA | 96080-2583 |  | 2012-08-13 | 2012-08-13 18:48 | 2012-08-13 19:05 | OTHER - AC036X1071G | 56 | 5.8 | Yes | Yes | 25 | 21.3 | 3.8 | 6D2DAB70C287430590E7ED4B568E0773 |  | R22 | Non-TXV |  | 10.36% | 0.89643 | 19.9% | [5 empty] | Non-TXV | 10.36%
Chico | CA | 95926-1551 |  | 2012-08-13 | 2012-08-13 10:42 | 2012-08-13 10:42 | COLEMAN - UNK | 85 | 0 | Yes | Yes | 19 | 21 | -2 | 0BDEEC51FE5540158BFAEEAABF8F851E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-3517 |  | 2012-08-09 | 2012-08-09 15:28 | 2012-08-09 15:51 | BRYANT - 588ANW060100AEAG | 112 | 3.9 | Yes | Yes | 20 | 19.5 | 0.5 | 721EAE27D363499BBC3CEADF1C3E14A3 |  | R22 | Non-TXV |  | 3.482% | 0.96518 | 6.692% | [5 empty] | Non-TXV | 3.482%
Paradise | CA | 95969-5135 |  | 2012-05-15 | 2012-05-15 11:59 | 2012-05-15 11:59 | TEMPSTAR - PGC030K080E | 51 | 0 | Yes | Yes | 22.7 | 22 | 0.7 | C7A0352E2C064FFDB59FB5106D167A1F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4104 |  | 2012-08-06 | 2012-08-06 10:33 | 2012-08-06 10:50 | BDP - 565BJ024 | 70 | -4.1 | Yes | Yes | 22.9 | 19.9 | 3 | 419E3319975E4067879D43C217BC6544 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Chico | CA | 95926-7142 |  | 2012-08-01 | 2012-08-01 18:41 | 2012-08-01 18:41 | BRYANT - 550AN048-F | 70 | 0 | Yes | Yes | 24.5 | 22.1 | 2.4 | 278F1A4F349F46F1A4929F04C233D1DA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1950 |  | 2012-08-07 | 2012-08-07 11:04 | 2012-08-07 11:21 | RUUD - UAMB-036JAZ | 93 | 3.1 | Yes | Yes | 22.7 | 18.8 | 3.9 | BDD2D37FFC3C41B8AEFFE1B2AC6F2B7F |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93710-6211 |  | 2012-05-16 | 2012-05-16 11:03 | 2012-05-16 11:23 | YORK - D1NP042N06506A | 150 | 5.4 | Yes | Yes | 20.7 | 21 | -0.3 | 35E00627C72C4CADA90F54BFB39C631F |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Magalia | CA | 95954-9675 |  | 2012-07-19 | 2012-07-19 09:20 | 2012-07-19 09:44 | OTHER - JT3BC-036K | 60 | 4.1 | Yes | Yes | 22.1 | 20.4 | 1.7 | A1A3B140D54D4C759932670505DB9F92 |  | R22 | Non-TXV |  | 6.833% | 0.93167 | 13.13% | [5 empty] | Non-TXV | 6.833%
Chico | CA | 95973-8968 |  | 2012-08-09 | 2012-08-09 19:15 | 2012-08-09 19:15 | LENNOX - 10ACB48-5P | 99 | 0 | Yes | Yes | 26.5 | 21.8 | 4.7 | 9AECC0A4F72E4C859D5F9FBCEE756C65 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2235 |  | 2012-07-31 | 2012-07-31 08:55 | 2012-07-31 09:13 | YORK - H2RD036SO6B | 96 | 4.9 | Yes | Yes | 20.3 | 19 | 1.3 | 3C9F2A5E3112483DBB7C1833E9507CEE |  | R22 | Non-TXV |  | 5.104% | 0.94896 | 9.809% | [5 empty] | Non-TXV | 5.104%
Stockton | CA | 95205-2910 |  | 2012-08-09 | 2012-08-09 11:02 | 2012-08-09 11:24 | OTHER - PA13NR024 | 112 | 4.1 | Yes | Yes | 19.5 | 19.9 | -0.4 | F516DECA5EE44E7884BF6202E8DA8631 |  | R22 | TXV |  | 3.661% | 0.96339 | 7.035% | [5 empty] | TXV | 3.661%
Stockton | CA | 95207-1338 |  | 2012-08-01 | 2012-08-01 09:07 | 2012-08-01 09:25 | PAYNE - PA10JA036-A | 84 | 3.7 | Yes | Yes | 18.2 | 19.1 | -0.8 | BBA4664A056B45E4B717B5BD86509625 |  | R22 | Non-TXV |  | 4.405% | 0.95595 | 8.465% | [5 empty] | Non-TXV | 4.405%
Stockton | CA | 95210-5602 |  | 2012-08-10 | 2012-08-10 14:10 | 2012-08-10 14:28 | PAYNE - 591ANX048000ABAA | 117 | 6.4 | Yes | Yes | 20.7 | 19.5 | 1.2 | CA6782F34D974A18891E42D96FB23FBE |  | R22 | Non-TXV |  | 5.47% | 0.9453 | 10.51% | [5 empty] | Non-TXV | 5.47%
Stockton | CA | 95207-5116 |  | 2012-08-06 | 2012-08-06 14:48 | 2012-08-06 15:08 | RUUD - UAMB-036JAS | 93 | 13 | Yes | Yes | 15.6 | 18.6 | -3 | 9B9A9A92F0CB4E08822E068C518F5703 |  | R22 | Non-TXV |  | 13.98% | 0.86022 | 26.86% | [5 empty] | Non-TXV | 13.98%
Stockton | CA | 95219-3843 |  | 2012-06-15 | 2012-06-15 10:30 | 2012-06-15 10:50 | OTHER - UNK | 64 | 3.7 | Yes | Yes | 18.3 | 19.9 | -1.6 | FD1763BBE6E5408CB1CC7647CCC7D4E4 |  | R22 | Non-TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | Non-TXV | 5.781%
Stockton | CA | 95207-3013 |  | 2012-08-03 | 2012-08-03 14:30 | 2012-08-03 14:50 | AMERICAN STANDARD - 2YCX3042A1075AA | 131 | 5.3 | Yes | Yes | 19.5 | 18.8 | 0.7 | 7202A2F2D579497D9C196B96D322A58D |  | R22 | Non-TXV |  | 4.046% | 0.95954 | 7.775% | [5 empty] | Non-TXV | 4.046%
Stockton | CA | 95207-4671 |  | 2012-07-31 | 2012-07-31 12:31 | 2012-07-31 12:57 | RHEEM - RACB-018JAZ | 30 | 21.6 | Yes | Yes | 17.4 | 19.1 | -1.7 | C4B68631AC1349BDACEAF31D4466BFA0 |  | R22 | Non-TXV |  | 72% | 0.28 | 138.4% | [5 empty] | Non-TXV | 72%
Yuba City | CA | 95993-6434 |  | 2012-08-01 | 2012-08-01 09:32 | 2012-08-01 09:50 | GOODMAN - PGJ036075-1 | 81 | 6.6 | Yes | Yes | 22.5 | 19.9 | 2.6 | F717780ED2EA43369251C3B5B5D7FE55 |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Chico | CA | 95926-2908 |  | 2012-08-07 | 2012-08-07 12:00 | 2012-08-07 15:29 | ALLEGIANCE - 2A7A2036A1000AA | 96 | 2.9 | Yes | Yes | 20.1 | 21.5 | -1.4 | 6EBC439388D64EEEA372374B34D6BB8A |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Stockton | CA | 95219-3110 |  | 2012-06-19 | 2012-06-19 11:27 | 2012-06-19 11:43 | LENNOX - 10ACB36-3P | 80 | 6.4 | Yes | Yes | 16.8 | 19.4 | -2.6 | 12D980F479074D69BC4EF06AB0915436 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Magalia | CA | 95954-9361 |  | 2012-06-12 | 2012-06-12 10:30 | 2012-06-12 10:30 | OTHER - UNK | 70 | 0 | Yes | Yes | 20.5 | 18.8 | 1.8 | 3F643364621D43C6A3F6C35B86AA4151 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9579 |  | 2012-06-07 | 2012-06-07 10:59 | 2012-06-07 10:59 | OTHER - F4947020E | 52 | 0 | Yes | Yes | 21.3 | 19.8 | 1.5 | A1C532C7B99247D486B0F8BC4A69BD73 |  |  |  |  | 0% | 1 | 0%
Magalia | CA | 95954-9660 |  | 2012-08-15 | 2012-08-15 11:04 | 2012-08-15 11:04 | CARRIER - 48GP-04209034 | 144 | 0 | Yes | Yes | 23 | 20.4 | 2.6 | 7C9694750EED418FBF65EDD0AEB472FB |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95928-7654 |  | 2012-08-01 | 2012-08-01 13:27 | 2012-08-01 14:29 | AMANA - 56CN024-B | 84 | 12.8 | Yes | Yes | 24.5 | 21 | 3.5 | 0D61679265414A7389D2BCD1AEE3A871 |  | R22 | Non-TXV |  | 15.24% | 0.84762 | 29.28% | [5 empty] | Non-TXV | 15.24%
Los Banos | CA | 93635-6325 |  | 2012-08-09 | 2012-08-09 11:36 | 2012-08-09 11:59 | GOODMAN - CKJ301A | 92 | 9.4 | Yes | Yes | 22.9 | 21.7 | 1.2 | CB8528D8046145A392CF851AFB6161AB |  | R22 | Non-TXV |  | 10.22% | 0.89783 | 19.64% | [5 empty] | Non-TXV | 10.22%
Orland | CA | 95963-9485 |  | 2012-05-17 | 2012-05-17 13:41 | 2012-05-17 13:41 | WHIRLPOOL - W2GC324A-1 | 70 | 0 | Yes | Yes | 24.7 | 22.4 | 2.4 | BF4F5DBD1F5149C3847FB09CBBC60A4D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2248 |  | 2012-08-07 | 2012-08-07 10:07 | 2012-08-07 10:27 | DAY & NIGHT - 561CJ030-1 | 71 | 2.6 | Yes | Yes | 22.9 | 20.4 | 2.5 | A34E89ED5DB9443F989226E15511E950 |  | R22 | TXV |  | 3.662% | 0.96338 | 7.038% | [5 empty] | TXV | 3.662%
Orland | CA | 95963-9334 |  | 2012-08-14 | 2012-08-14 19:39 | 2012-08-14 19:39 | - H2RE0605061A | 178 | 0 | Yes | Yes | 23.4 | 21.2 | 2.3 | 7B6F039D207B4B6B8E929B2A50C02625 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-2999 |  | 2012-08-08 | 2012-08-08 15:09 | 2012-08-08 16:38 | BRYANT - 563CN042-C | 104 | 3.5 | Yes | Yes | 18.7 | 18.2 | 0.5 | 9A5774688D5C4FA5859BFAB49C16C567 |  | R22 | Non-TXV |  | 3.365% | 0.96635 | 6.468% | [5 empty] | Non-TXV | 3.365%
Marysville | CA | 95901-4275 |  | 2012-05-21 | 2012-05-21 11:29 | 2012-05-21 11:45 | UNK - 540JJ018 | 83 | 2.6 | Yes | Yes | 19 | 19.3 | -0.3 | BB799930123C4DBE8402C388208DB2D3 |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Atwater | CA | 95301-2001 |  | 2012-08-06 | 2012-08-06 11:43 | 2012-08-06 11:58 | COLEMAN - BRCS0421BD | 84 | -4.9 | Yes | Yes | 18.8 | 20.4 | -1.6 | B219910F4A034A8DAC3E1E39F97C1ADD |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Los Banos | CA | 93635-6361 |  | 2012-08-13 | 2012-08-13 16:11 | 2012-08-13 16:28 | BRYANT - 561CJ048-F653 | 100 | 3.2 | Yes | Yes | 17.6 | 19.7 | -2.1 | 028C737FB0154E698CC5EDC87571A5CE |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Los Banos | CA | 93635-2952 |  | 2012-08-01 | 2012-08-01 11:46 | 2012-08-01 12:12 | DAY & NIGHT - 591ANX036000AAAA | 84 | 2.6 | Yes | Yes | 20.6 | 18.2 | 2.4 | 99D15C73432345B68BE8DC6E59C8AE52 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Chico | CA | 95928-5948 |  | 2012-05-24 | 2012-05-24 12:35 | 2012-05-24 13:10 | TRANE - YCCO18F1LOBH | 62 | 2.2 | Yes | Yes | 21.7 | 20.4 | 1.3 | 46062F86C73E4DCB95D47F6FE9FB3EFF |  | R22 | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Yuba City | CA | 95993-1642 |  | 2012-07-31 | 2012-07-31 13:57 | 2012-07-31 14:15 | OTHER - GCG36S41S3A | 73 | 2.4 | Yes | Yes | 17 | 19.3 | -2.3 | 68895780AB8B49C796C286DDE8F17E1D |  | R410A | TXV |  | 3.288% | 0.96712 | 6.318% | [5 empty] | TXV | 3.288%
Orland | CA | 95963-0000 |  | 2012-05-17 | 2012-05-17 11:10 | 2012-05-17 12:54 | LENNOX - NA | 59 | 6.1 | Yes | Yes | 18.7 | 21.2 | -2.5 | B875EC42DA5A4D2CBC04F543F4906496 |  | R22 | Non-TXV |  | 10.34% | 0.89661 | 19.87% | [5 empty] | Non-TXV | 10.34%
Atwater | CA | 95301-4281 |  | 2012-08-08 | 2012-08-08 12:24 | 2012-08-08 13:00 | COLEMAN - BRC80481BB | 100 | 15 | Yes | Yes | 22.3 | 20.9 | 1.4 | A5592CB17C3A4718BA0CD19396B23B80 |  | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Red Bluff | CA | 96080-3952 |  | 2012-08-06 | 2012-08-06 14:08 | 2012-08-06 17:56 | RUUD - UANL-024JEZ | 72 | 2.8 | Yes | Yes | 18.4 | 21.4 | -3 | 0FC314F6C2FD445584AFBAC5B5BA7307 |  | R410A | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Clovis | CA | 93611-0605 |  | 2012-05-10 | 2012-05-10 10:12 | 2012-05-10 10:29 | YORK - D1NP048N09006A | 132 | 3.9 | Yes | Yes | 20.8 | 20.4 | 0.4 | 57A9C0A7F76E4382A8C756E1D57BC2E8 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Stockton | CA | 95210-6618 |  | 2012-08-13 | 2012-08-13 12:32 | 2012-08-13 12:50 | YORK - D3YS030N045068 | 66 | 6.6 | Yes | Yes | 26.4 | 21.7 | 4.7 | E43D40A429154EFFBAFEB2BF7C6EB49E |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Fresno | CA | 93726-5130 |  | 2012-07-06 | 2012-07-06 09:31 | 2012-07-06 09:49 | DAY & NIGHT - N/A | 80 | 2.4 | Yes | Yes | 23.7 | 21 | 2.7 | 1165F87FF32F47CA8D903433D391BD89 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-5106 |  | 2012-08-13 | 2012-08-13 12:35 | 2012-08-13 13:02 | TRANE - TTD736B100B0 | 96 | 3.5 | Yes | Yes | 28 | 22 | 6 | 372C53DBF9554BBDA1DA7D54EE678219 |  | R22 | Non-TXV |  | 3.646% | 0.96354 | 7.006% | [5 empty] | Non-TXV | 3.646%
Stockton | CA | 95206-6053 |  | 2012-08-15 | 2012-08-15 11:46 | 2012-08-15 12:05 | GOODMAN - CKJ36-1A | 90 | 9.4 | Yes | Yes | 21 | 19.5 | 1.5 | 9C793252783F4006948C56659059D87B |  | R22 | Non-TXV |  | 10.44% | 0.89556 | 20.07% | [5 empty] | Non-TXV | 10.44%
Colusa | CA | 95932-3309 |  | 2012-08-02 | 2012-08-02 15:14 | 2012-08-02 15:14 | DAY & NIGHT - 569BB060 | 144 | 0 | Yes | Yes | 0.1 | 10.3 | -10.2 | C8F68DC69A81437594B69196D74ED202 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6614 |  | 2012-05-09 | 2012-05-09 09:22 | 2012-05-09 09:41 | GOODMAN - GPG13240451BA | 77 | 3.2 | Yes | Yes | 22.4 | 20.3 | 2.1 | 88442E4EB0BD4EA787BCA50FABD33562 | OK: Verified Refrigerant Charge. |  |  |  | 4.156% | 0.95844 | 7.987% | [5 empty] | 0 | 4.156%
Colusa | CA | 95932-2808 |  | 2012-05-24 | 2012-05-24 12:08 | 2012-05-24 12:36 | CLIMATEMASTER - 48G-042090301AD | 118 | 18.7 | Yes | Yes | 19 | 21.9 | -2.9 | 9524A7A6D1F64030A7AF110EA17BC8D8 |  | R22 | Non-TXV |  | 15.85% | 0.84153 | 30.46% | [5 empty] | Non-TXV | 15.85%
Colusa | CA | 95932-2827 |  | 2012-07-16 | 2012-07-16 09:45 | 2012-07-16 10:04 | HEIL - PGC030K060E | 51 | 2 | Yes | Yes | 17 | 18.2 | -1.2 | 571AD91DC336422FBBAF850F635E2CA5 |  | R22 | Non-TXV |  | 3.922% | 0.96078 | 7.536% | [5 empty] | Non-TXV | 3.922%
Colusa | CA | 95932-3350 |  | 2012-08-06 | 2012-08-06 11:18 | 2012-08-06 11:36 | GOODMAN - GPG13360701AB | 112 | 6.3 | Yes | Yes | 18.5 | 19.3 | -0.8 | 752CFC7F50844A06ACD48BE7EC06678D |  | R22 | Non-TXV |  | 5.625% | 0.94375 | 10.81% | [5 empty] | Non-TXV | 5.625%
Oroville | CA | 95965-3129 |  | 2012-06-01 | 2012-06-01 10:07 | 2012-06-01 10:41 | COLEMAN - UNK | 65 | 9.6 | Yes | Yes | 19.4 | 20.9 | -1.5 | 062FCC82396042BF9E6F3555ED9C1A77 |  | R22 | Non-TXV |  | 14.77% | 0.85231 | 28.38% | [5 empty] | Non-TXV | 14.77%
Los Banos | CA | 93635-3401 |  | 2012-08-02 | 2012-08-02 11:45 | 2012-08-02 12:04 | DAY & NIGHT - UNK | 80 | 2.9 | Yes | Yes | 17.9 | 19.8 | -1.9 | E9A44B0919E740AA93CCD3E03CB8B0A2 |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Merced | CA | 95340-2364 |  | 2012-08-02 | 2012-08-02 09:33 | 2012-08-02 09:49 | OTHER - 587GJ030B | 80 | 9.8 | Yes | Yes | 25.3 | 21.6 | 3.8 | 8E30D1F13E28479BB9221883C603A4FB |  | R22 | Non-TXV |  | 12.25% | 0.8775 | 23.54% | [5 empty] | Non-TXV | 12.25%
Stockton | CA | 95210-1518 |  | 2012-07-31 | 2012-07-31 10:20 | 2012-07-31 10:37 | RHEEM - RRNA-A030JK06X | 112 | 3.4 | Yes | Yes | 17 | 19.3 | -2.3 | D0CE22432C71474D806058995BF9F08A |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Colusa | CA | 95932-3307 |  | 2012-08-06 | 2012-08-06 12:36 | 2012-08-06 12:58 | CARRIER - 38CKC042340 | 80 | 7.5 | Yes | Yes | 18.6 | 18.8 | -0.2 | BE810452CEC74903B088473510389CF3 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Colusa | CA | 95932-3345 |  | 2012-08-09 | 2012-08-09 13:12 | 2012-08-09 13:12 | LENNOX - UNK | 89 | 0 | Yes | Yes | 22.1 | 20.1 | 2 | C3B87A34CC01440A87DFD8B604AAAB73 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Colusa | CA | 95932-2911 |  | 2012-05-24 | 2012-05-24 15:36 | 2012-05-24 16:00 | TEMPSTAR - N2A34AKA400 | 117 | 3.9 | Yes | Yes | 23 | 22.2 | 0.8 | F4C89623814E48BA8238E520B480A840 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Colusa | CA | 95932-3390 |  | 2012-08-06 | 2012-08-06 13:17 | 2012-08-06 13:17 | RUUD - 13AJA48A01 | 123 | 0 | Yes | Yes | 25.3 | 20.1 | 5.2 | 2928D01C5DC2424FA157CCC8A62C5C5B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6150 |  | 2012-05-11 | 2012-05-11 11:02 | 2012-05-11 11:20 | GOODMAN - GSC130601CB | 131 | -4.9 | Yes | Yes | 21.2 | 20.9 | 0.3 | 80E276FCB392437ABA5EBAA7A1D64A4D | OK: Verified Refrigerant Charge | R22 | TXV |  | -3.74% | 1.0374 | 1.048% |  |  |  |  | TXV |  |  | -3.74%
Atwater | CA | 95301-4862 |  | 2012-07-02 | 2012-07-02 13:03 | 2012-07-02 13:34 | LENNOX - HS9-3114P | 69 | 4.1 | Yes | Yes | 18.2 | 20.2 | -2 | EA69BB4AF6F04AE5A54E36F764E455E7 |  | R22 | Non-TXV |  | 5.942% | 0.94058 | 11.42% | [5 empty] | Non-TXV | 5.942%
Winton | CA | 95388-9319 |  | 2012-08-02 | 2012-08-02 10:07 | 2012-08-02 10:32 | RHEEM - HC-80-36-21C | 49 | 1.5 | Yes | Yes | 16.3 | 18.8 | -2.5 | 23E5161BBBCD475E804F03903683189D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Merced | CA | 95341-5495 |  | 2012-05-08 | 2012-05-08 16:42 | 2012-05-08 17:00 | TRANE - 4YCC3036A1064AB | 124 | 3.7 | Yes | Yes | 23.3 | 20.7 | 2.6 | C07B6F3AA30043039579257CB25A14A3 | OK: Verified Refrigerant Charge. |  |  |  | 2.984% | 0.97016 | 5.734% | [5 empty] | 0 | 2.984%
Merced | CA | 95340-2376 |  | 2012-07-31 | 2012-07-31 14:20 | 2012-07-31 14:48 | GOODMAN - CK36-A1 | 73 | 4.2 | Yes | Yes | 20.6 | 19.3 | 1.3 | 20C526FD1C3C4D5899FF6A134E52B40D |  | R22 | Non-TXV |  | 5.753% | 0.94247 | 11.06% | [5 empty] | Non-TXV | 5.753%
Madera | CA | 93638-1223 |  | 2012-06-13 | 2012-06-13 15:46 | 2012-06-13 16:06 | OTHER - UNK | 50 | -3.5 | Yes | Yes | 23.1 | 19.5 | 3.7 | 1EBB903804054E0B85930967BC755112 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Winton | CA | 95388-9253 |  | 2012-08-01 | 2012-08-01 12:33 | 2012-08-01 12:56 | GOODMAN - UNK | 55 | 4.6 | Yes | Yes | 19.5 | 20.3 | -0.8 | B88E77DAA75A41119C12BBDF399E4AC5 |  | R22 | Non-TXV |  | 8.364% | 0.91636 | 16.07% | [5 empty] | Non-TXV | 8.364%
Los Banos | CA | 93635-6324 |  | 2012-08-09 | 2012-08-09 12:01 | 2012-08-09 12:01 | LENNOX - 10GCS042751PA | 73 | 0 | Yes | Yes | 0 | 10.8 | -10.8 | 613825E2F54846EDAD4B287483CBFFEC | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Willows | CA | 95988-3040 |  | 2012-06-12 | 2012-06-12 09:22 | 2012-06-12 09:40 | OTHER - 541B028SH | 90 | 6.5 | Yes | Yes | 22.6 | 21.5 | 1.1 | 27246298CC8949159FCE8C7A57148AE3 |  | R22 | Non-TXV |  | 7.222% | 0.92778 | 13.88% | [5 empty] | Non-TXV | 7.222%
Oroville | CA | 95965-8101 |  | 2012-08-10 | 2012-08-10 08:43 | 2012-08-10 09:29 | GOODMAN - CKT42-1B | 134 | 4.1 | Yes | Yes | 22 | 21 | 1 | 9A8EA6DA436E48FA86F249F7C93DB953 |  | R22 | Non-TXV |  | 3.06% | 0.9694 | 5.88% | [5 empty] | Non-TXV | 3.06%
Tracy | CA | 95377-8520 |  | 2012-08-03 | 2012-08-03 10:21 | 2012-08-03 10:50 | YORK - TCGD48S21S2HA | 69 | 25.8 | Yes | Yes | 19.5 | 20.4 | -0.9 | AA9BEA0C9F6A49DF93CDFF719D2EF70A |  | R22 | Non-TXV |  | 37.39% | 0.62609 | 71.86% | [5 empty] | Non-TXV | 37.39%
Dinuba | CA | 93618-9312 |  | 2012-07-31 | 2012-07-31 11:25 | 2012-07-31 11:51 | RHEEM - N/A | 120 | 14 | Yes | Yes | 21.3 | 20.5 | 0.8 | E1D78E2E12164961ABEB6B8A7DEA9AE7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Willows | CA | 95988-3426 |  | 2012-08-15 | 2012-08-15 12:21 | 2012-08-15 12:46 | YORK - D1NH036N05606C | 108 | 6.2 | Yes | Yes | 20.3 | 22 | -1.7 | 82AA7E81083A4A79BC242D91033CC431 |  | R22 | Non-TXV |  | 5.741% | 0.94259 | 11.03% | [5 empty] | Non-TXV | 5.741%
Cameron Park | CA | 95682-8930 |  | 2012-08-07 | 2012-08-07 15:17 | 2012-08-07 16:02 | CARRIER - UNK | 102 | 3.8 | Yes | Yes | 21.6 | 20 | 1.7 | 0BF7CE8EE85C498B894258DFC64F1213 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.725% | 0.96275 | 7.16% | [5 empty] | Non-TXV | 3.725%
Chico | CA | 95926-1752 |  | 2012-08-07 | 2012-08-07 11:32 | 2012-08-07 11:53 | TRANE - TTXO30C100A3 | 111 | 7 | Yes | Yes | 23 | 21 | 2 | 17B2D1F3AC2C47E08012DB69C6234450 |  | R22 | Non-TXV |  | 6.306% | 0.93694 | 12.12% | [5 empty] | Non-TXV | 6.306%
Winton | CA | 95388-9593 |  | 2012-08-08 | 2012-08-08 13:45 | 2012-08-08 13:45 | GUARDIAN - GCGD48S41S3A | 73 | 0 | Yes | Yes | 24.2 | 19.7 | 4.5 | E3933480AB504C1DBFECEA597D47368B |  | R410A | TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-9019 |  | 2012-06-26 | 2012-06-26 16:40 | 2012-06-26 17:05 | PAYNE - 565BJ030 | 73 | 19.1 | Yes | Yes | 22.3 | 21.5 | 0.8 | 28DD56533E55463993D52DAC4F0AC0B9 |  | R22 | Non-TXV |  | 26.16% | 0.73836 | 50.28% | [5 empty] | Non-TXV | 26.16%
Willows | CA | 95988-3040 |  | 2012-06-12 | 2012-06-12 11:17 | 2012-06-12 11:34 | OTHER - 541B028SHP | 90 | 7.9 | Yes | Yes | 20 | 22.3 | -2.3 | B5978A8977A643AE9F4C3A1253479E69 |  | R22 | Non-TXV |  | 8.778% | 0.91222 | 16.87% | [5 empty] | Non-TXV | 8.778%
Fresno | CA | 93726-5120 |  | 2012-05-08 | 2012-05-08 13:51 | 2012-05-08 14:10 | SEARS - N/A | 75 | 10.1 | Yes | Yes | 28.1 | 22.1 | 6 | E8FF44C53F8541B6BB3755A2629CE9AB | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 13.47% | 0.86533 | 25.88% | [5 empty] | Non-TXV | 13.47%
Los Banos | CA | 93635-2931 |  | 2012-08-01 | 2012-08-01 12:36 | 2012-08-01 13:03 | DAY & NIGHT - UNK | 75 | -4.4 | Yes | Yes | 24.9 | 20.4 | 4.5 | 78BC02C058E341878FE91936DF183254 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Chico | CA | 95973-8346 |  | 2012-05-07 | 2012-05-07 16:29 | 2012-05-07 16:50 | LENNOX - HS25-311-1P | 129 | 11.5 | Yes | Yes | 19.3 | 20.2 | -0.9 | 672943A6237F43DD9F36E8AE679AA0FD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.915% | 0.91085 | 17.13% | [5 empty] | Non-TXV | 8.915%
Willows | CA | 95988-2225 |  | 2012-05-29 | 2012-05-29 18:12 | 2012-05-29 18:29 | TRANE - HAUC-352-C | 69 | 4.7 | Yes | Yes | 19.7 | 20.9 | -1.2 | AFA1F1854C4F497DAD9009BC6B185858 |  | R22 | Non-TXV |  | 6.812% | 0.93188 | 13.09% | [5 empty] | Non-TXV | 6.812%
Stockton | CA | 95210-6608 |  | 2012-05-21 | 2012-05-21 13:44 | 2012-05-21 14:02 | YORK - D3YS036N04506B | 78 | 2.5 | Yes | Yes | 25 | 20.4 | 4.6 | 6BF9EA82F6074DD8B1188EA067D5A5B3 |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Chico | CA | 95928-5852 |  | 2012-05-24 | 2012-05-24 13:12 | 2012-05-24 13:12 | CARRIER - 38EB030310 | 85 | 0 | Yes | Yes | 21 | 21.3 | -0.3 | A41BF1A6432C414486968537EDF24FA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6357 |  | 2012-08-06 | 2012-08-06 17:03 | 2012-08-06 17:20 | BRYANT - 601ANX048000AAAG | 100 | -5.9 | Yes | Yes | 26 | 20.9 | 5.1 | 1A3C6C3EEE574709886EFDDA5CE8CCCD |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Stockton | CA | 95207-2720 |  | 2012-07-31 | 2012-07-31 09:48 | 2012-07-31 10:24 | LENNOX - HS25-311-1P | 129 | 10 | Yes | Yes | 21.3 | 20.4 | 0.9 | D54A847CF9ED4BF08FDD2CD8E2C1972C |  | R22 | Non-TXV |  | 7.752% | 0.92248 | 14.9% | [5 empty] | Non-TXV | 7.752%
Stockton | CA | 95210-6736 |  | 2012-08-07 | 2012-08-07 08:17 | 2012-08-07 08:34 | BDP - 561AJ042-D | 80 | -4.7 | Yes | Yes | 20 | 19.3 | 0.7 | 14A214F82D6442DA813EA206FB4EA7FE |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Los Banos | CA | 93635-3271 |  | 2012-08-01 | 2012-08-01 13:57 | 2012-08-01 14:15 | RUUD - UNK | 114 | 10.5 | Yes | Yes | 23.9 | 23.1 | 0.8 | 06B8D412FAB34B16A8ECBF84B9D51652 |  | R22 | Non-TXV |  | 9.211% | 0.90789 | 17.7% | [5 empty] | Non-TXV | 9.211%
Atwater | CA | 95301-2321 |  | 2012-05-08 | 2012-05-08 12:23 | 2012-05-08 12:43 | RUUD - URKA-A024JK06X | 50 | 1.5 | Yes | Yes | 20.1 | 20.4 | -0.3 | D192B584B941407C8C10F652CD372918 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Oroville | CA | 95966-3977 |  | 2012-05-31 | 2012-05-31 10:22 | 2012-05-31 10:54 | GE - BW0036B1000CD | 98 | 5.6 | Yes | Yes | 19.3 | 21.5 | -2.2 | B6E45390444C49E1A2725D0AFA0C15F3 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Stockton | CA | 95205-7039 |  | 2012-05-16 | 2012-05-16 17:27 | 2012-05-16 17:45 | COMFORTMAKER - NAC030AKC3 | 75 | 4.1 | Yes | Yes | 17.7 | 19.2 | -1.5 | B8CF007AB25B42D7A20073E35FACB26B |  | R22 | Non-TXV |  | 5.467% | 0.94533 | 10.51% | [5 empty] | Non-TXV | 5.467%
Red Bluff | CA | 96080-5208 |  | 2012-08-13 | 2012-08-13 20:05 | 2012-08-13 20:28 | OTHER - 561AJ042D | 80 | 2.6 | Yes | Yes | 21.3 | 21.1 | 0.2 | 982DD133D6AA477EB07F15CF85977917 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Red Bluff | CA | 96080-2580 |  | 2012-08-13 | 2012-08-13 19:43 | 2012-08-13 20:02 | YORK - H2RDC36506B | 96 | 3.7 | Yes | Yes | 26.3 | 20.6 | 5.7 | 576D07AC4F08418683DB069D5A91D12F |  | R22 | Non-TXV |  | 3.854% | 0.96146 | 7.407% | [5 empty] | Non-TXV | 3.854%
Los Banos | CA | 93635-9409 |  | 2012-08-16 | 2012-08-16 13:59 | 2012-08-16 14:24 | BRYANT - 561CJ042B | 93 | 9.8 | Yes | Yes | 24.6 | 18.6 | 6 | 9684261A6BDE4586A0B466E53638F5D6 |  | R22 | Non-TXV |  | 10.54% | 0.89462 | 20.25% | [5 empty] | Non-TXV | 10.54%
Los Banos | CA | 93635-2987 |  | 2012-05-15 | 2012-05-15 12:07 | 2012-05-15 12:27 | DAY AND NIGHT - 591ANX036000AAAA | 88 | 5.6 | Yes | Yes | 20.6 | 22.1 | -1.5 | E0A2B693C6404051844B196277F0603C |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Paradise | CA | 95969-2701 |  | 2012-07-31 | 2012-07-31 10:38 | 2012-07-31 11:20 | PAYNE - 9548C901 | 69 | 4.3 | Yes | Yes | 25 | 21.3 | 3.7 | 5692B361ED3B45838E94530CDBD8E4CB |  | R22 | Non-TXV |  | 6.232% | 0.93768 | 11.98% | [5 empty] | Non-TXV | 6.232%
Fresno | CA | 93706-5023 |  | 2012-06-12 | 2012-06-12 14:31 | 2012-06-12 14:58 | ICP - PGE48G0908 | 212 | 8.5 | Yes | Yes | 17.5 | 20.4 | -2.9 | 7B127274D7A043EF86AE812E2155822E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.009% | 0.95991 | 7.705% | [5 empty] | Non-TXV | 4.009%
Red Bluff | CA | 96080-2580 |  | 2012-08-06 | 2012-08-06 13:14 | 2012-08-06 13:39 | YORK - H1RA024S06D | 59 | 4 | Yes | Yes | 20.9 | 21.2 | -0.3 | 37FA91F67C634B34B0C531859B05473F |  | R22 | Non-TXV |  | 6.78% | 0.9322 | 13.03% | [5 empty] | Non-TXV | 6.78%
Red Bluff | CA | 96080-9624 |  | 2012-05-16 | 2012-05-16 14:01 | 2012-05-16 15:07 | BRYANT - 583ANW048090NBAF | 131 | 4.7 | Yes | Yes | 20.5 | 21.7 | -1.2 | 7C7F2D61A8AC4F54AA7D3F722ADF2FED |  | R22 | Non-TXV |  | 3.588% | 0.96412 | 6.895% | [5 empty] | Non-TXV | 3.588%
Fresno | CA | 93706-2610 |  | 2012-07-09 | 2012-07-09 13:02 | 2012-07-09 13:20 | YORK - DBYP-F030N045XA | 73 | 4.5 | Yes | Yes | 21.6 | 20.2 | 1.4 | 3E3FDA84FCB54B90ADB412BCFEEF0331 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 6.164% | 0.93836 | 11.85% | [5 empty] | Non-TXV | 6.164%
Red Bluff | CA | 96080-9642 |  | 2012-08-06 | 2012-08-06 10:11 | 2012-08-06 10:28 | MAYTAG - PSA4BF048K | 225 | 7 | Yes | Yes | 19.8 | 20.6 | -0.8 | 846307050C75410890D4B49BFD97C758 |  | R410A | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Atwater | CA | 95301-4563 |  | 2012-05-18 | 2012-05-18 08:38 | 2012-05-18 09:07 | BDP - 588ANW024040ABAD | 50 | 1.5 | Yes | Yes | 23.1 | 20.1 | 3 | 18A78B8ECF734E70A7B3D3B604380F95 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Oroville | CA | 95965-3520 |  | 2012-05-29 | 2012-05-29 09:47 | 2012-05-29 10:06 | CARRIER - 48SX-030060331AA | 69 | 5.2 | Yes | Yes | 24.6 | 22 | 2.6 | CF564ED84EAB4322A820DA174AE8F510 |  | R22 | Non-TXV |  | 7.536% | 0.92464 | 14.48% | [5 empty] | Non-TXV | 7.536%
Stockton | CA | 95206-5431 |  | 2012-08-15 | 2012-08-15 10:37 | 2012-08-15 10:54 | RUUD - UAHE-060JAS | 176 | 10.1 | Yes | Yes | 15 | 17.4 | -2.4 | 08AF6150F0544B47BE5564C52965BA90 |  | R22 | Non-TXV |  | 5.739% | 0.94261 | 11.03% | [5 empty] | Non-TXV | 5.739%
Atwater | CA | 95301-2106 |  | 2012-08-09 | 2012-08-09 08:33 | 2012-08-09 08:33 | PAYNE - 36RAC.1S8TC | 86 | 0 | Yes | Yes | 18.6 | 20.2 | -1.6 | 9502B2907DBB4DBE9617D6FCB63E9AF4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3107 |  | 2012-05-11 | 2012-05-11 10:18 | 2012-05-11 10:45 | UNK - 816221 | 35 | 3.7 | Yes | Yes | 18.9 | 21.7 | -2.8 | D5C48642195D4CCDBB2C39F51696E5C4 | OK: Verified Refrigerant Charge. |  |  |  | 10.57% | 0.89429 | 20.32% | [5 empty] | 0 | 10.57%
Pollock Pines | CA | 95726-9457 |  | 2012-08-16 | 2012-08-16 10:31 | 2012-08-16 10:52 | DAY & NIGHT - 591ANX036000AAAA | 86 | 15.2 | Yes | Yes | 21.8 | 19.7 | 2.1 | 66C460EC4CE54C9FABE10DE58F121614 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.67% | 0.82326 | 33.97% | [5 empty] | Non-TXV | 17.67%
Winton | CA | 95388-9766 |  | 2012-08-03 | 2012-08-03 09:03 | 2012-08-03 09:30 | RHEEM - 13AJM30A01 | 86 | -3.1 | Yes | Yes | 17.9 | 18.8 | -0.9 | 2F124E87439F4E639DD8AFA0196CC0E4 |  | R410A | TXV |  | -3.605% | 1.036 | 1.009% |  |  |  |  | TXV |  |  | -3.605%
Red Bluff | CA | 96080-2201 |  | 2012-08-13 | 2012-08-13 19:20 | 2012-08-13 19:40 | RHEEM - RAFD-048JBS | 102 | 5.7 | Yes | Yes | 20 | 21.3 | -1.3 | 35F2F488CB4F4EA3ABE60EB2A475CDDA |  | R22 | Non-TXV |  | 5.588% | 0.94412 | 10.74% | [5 empty] | Non-TXV | 5.588%
Fresno | CA | 93722-8007 |  | 2012-05-31 | 2012-05-31 13:58 | 2012-05-31 14:16 | COLEMAN - DAYH-F02N045C | 69 | 2.4 | Yes | Yes | 19.7 | 21 | -1.3 | 2EDF8586C448407797CA60221811BEFE |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Paradise | CA | 95969-3008 |  | 2012-08-03 | 2012-08-03 10:00 | 2012-08-03 10:36 | BRYANT - 583BNW0420961 | 144 | 7.3 | Yes | Yes | 21.3 | 22.8 | -1.5 | 29D69811D0C04833945CB7D763E94B62 |  | R22 | Non-TXV |  | 5.069% | 0.94931 | 9.742% | [5 empty] | Non-TXV | 5.069%
Los Banos | CA | 93635-2979 |  | 2012-08-15 | 2012-08-15 10:44 | 2012-08-15 11:06 | GOODMAN - GSC130481BB | 103 | 4.4 | Yes | Yes | 22.2 | 19.5 | 2.7 | C14FC80313D441BBBEF31BEAA0DCA3C8 |  | R22 | Non-TXV |  | 4.272% | 0.95728 | 8.21% | [5 empty] | Non-TXV | 4.272%
Chico | CA | 95926-1775 |  | 2012-05-11 | 2012-05-11 11:42 | 2012-05-11 12:00 | TRAIN - TTR036D100A0 | 77 | 2.5 | Yes | Yes | 22.4 | 22 | 0.4 | 826A9173293F43279283A8085A6B254A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.247% | 0.96753 | 6.24% | [5 empty] | Non-TXV | 3.247%
Atwater | CA | 95301-2116 |  | 2012-08-09 | 2012-08-09 09:13 | 2012-08-09 09:41 | RHEEM - RAPC-042JAZ | 168 | -15.8 | Yes | Yes | 18.2 | 17.9 | 0.3 | 61824800ADA94A6AA4B776629BAFBA0A |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Red Bluff | CA | 96080-4483 |  | 2012-08-03 | 2012-08-03 10:07 | 2012-08-03 10:38 | PAYNE - 541CJ024 | 92 | 13.4 | Yes | Yes | 35 | 20.4 | 14.6 | 6893AE9B12CC49C88ADB2D5235829C14 |  | R22 | Non-TXV |  | 14.57% | 0.85435 | 27.99% | [5 empty] | Non-TXV | 14.57%
Fresno | CA | 93726-6718 |  | 2012-05-09 | 2012-05-09 14:19 | 2012-05-09 14:39 | RUUD - UNK | 60 | 2 | Yes | Yes | 17.7 | 19.2 | -1.5 | C0018B211FC94C9F9B277D4073DBBB61 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Red Bluff | CA | 96080-4006 |  | 2012-08-03 | 2012-08-03 12:21 | 2012-08-03 13:22 | RHEEM - RRGG-05N31JKR | 50 | 2.1 | Yes | Yes | 19.5 | 21.8 | -2.3 | 49A676E5FD0549B1A8EBE607FAAFFAA6 |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Fresno | CA | 93727-1118 |  | 2012-05-08 | 2012-05-08 17:22 | 2012-05-08 17:40 | PAYNE - N/A | 67 | 2 | Yes | Yes | 18.8 | 20.1 | -1.3 | D9B279C75D8647A3A30111931D6A659C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Stockton | CA | 95210-5659 |  | 2012-08-03 | 2012-08-03 11:16 | 2012-08-03 11:34 | DAY & NIGHT - 591ANX030000ABAA | 68 | 2.6 | Yes | Yes | 25.4 | 19.9 | 5.5 | 548E8D62DEF04109A5822C35D1E99BB2 |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Merced | CA | 95340-2518 |  | 2012-06-07 | 2012-06-07 10:10 | 2012-06-07 10:10 | BRYANT - 574ANW060090NA | 184 | 0 | Yes | Yes | 22.6 | 20.3 | 2.3 | DE80DEFD653942119789F93994858427 |  |  |  |  | 0% | 1 | 0%
Corning | CA | 96021-9749 |  | 2012-08-02 | 2012-08-02 12:23 | 2012-08-02 13:07 | OTHER - GSX130241BA | 76 | 2.9 | Yes | Yes | 22.1 | 21.5 | 0.7 | CDD0E5B6DD8E41E2B8F938C968E14319 |  | R410A | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Chico | CA | 95973-9183 |  | 2012-08-07 | 2012-08-07 18:53 | 2012-08-07 19:11 | LENNOX - 12ACB36-5P | 103 | 3.9 | Yes | Yes | 18.7 | 20.4 | -1.7 | FA23055CCA3748FDB40614AF317C80CA |  | R22 | Non-TXV |  | 3.786% | 0.96214 | 7.277% | [5 empty] | Non-TXV | 3.786%
Corning | CA | 96021-9757 |  | 2012-05-17 | 2012-05-17 15:26 | 2012-05-17 15:26 | NA - NA | 114 | 0 | Yes | Yes | 20.6 | 22 | -1.4 | A01E9F6D06904210BD7446C62DAA0D2E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-7475 |  | 2012-06-01 | 2012-06-01 17:41 | 2012-06-01 18:15 | GOODMAN - GPG13240451CB | 76 | 9 | Yes | Yes | 17.6 | 19.5 | -1.9 | 8D82D80F6B5D40868AA11BE1AD565013 |  | R22 | Non-TXV |  | 11.84% | 0.88158 | 22.76% | [5 empty] | Non-TXV | 11.84%
Merced | CA | 95340-2559 |  | 2012-08-02 | 2012-08-02 08:56 | 2012-08-02 09:20 | OTHER - 582AJW048090AAAG | 81 | 5.4 | Yes | Yes | 19.9 | 18.8 | 1.1 | 2880729F5F094534944FFFF94F025E34 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Corning | CA | 96021-2635 |  | 2012-08-02 | 2012-08-02 08:39 | 2012-08-02 09:00 | TRANE - 2TTR1036A1000AA | 73 | 3.4 | Yes | Yes | 24.2 | 21.7 | 2.5 | 0BEFD1F2D6B94C4099D97D8D49511411 |  | R22 | Non-TXV |  | 4.658% | 0.95342 | 8.951% | [5 empty] | Non-TXV | 4.658%
Corning | CA | 96021-0000 |  | 2012-07-31 | 2012-07-31 09:37 | 2012-07-31 10:31 | WESTINGHOUSE - FS3BD-048K | 143 | 7.3 | Yes | Yes | 25 | 21.5 | 3.5 | BAB937E09F2A439BA61FA5231262D51B |  | R22 | Non-TXV |  | 5.105% | 0.94895 | 9.81% | [5 empty] | Non-TXV | 5.105%
Fresno | CA | 93727-4502 |  | 2012-05-30 | 2012-05-30 14:22 | 2012-05-30 14:42 | GOODMAN - DKJ42-1AB | 106 | 3.1 | Yes | Yes | 17.1 | 19.6 | -2.5 | F26F30FDE06545C29B8FD551B9A99E5F |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
Fresno | CA | 93727-4502 |  | 2012-05-30 | 2012-05-30 14:43 | 2012-05-30 14:52 | GOODMAN - DKJ42-1AB | 106 | 3.1 | Yes | Yes | 22.3 | 21.5 | 0.8 | 35620C29583640BB98A64E94603DD9F9 |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
Stockton | CA | 95210-3125 |  | 2012-06-11 | 2012-06-11 15:35 | 2012-06-11 15:53 | RHEEM - UNK | 54 | 2 | Yes | Yes | 22.9 | 23.5 | -0.6 | B2A5532B0BBB47F9B34082C29ED6568D |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Stockton | CA | 95212-3141 |  | 2012-05-17 | 2012-05-17 13:24 | 2012-05-17 13:40 | YORK - H2RA036S06G | 63 | 3.4 | Yes | Yes | 19.8 | 20.1 | -0.3 | F3EBB7356C324FA9A3FD057086D25D2B |  | R22 | Non-TXV |  | 5.397% | 0.94603 | 10.37% | [5 empty] | Non-TXV | 5.397%
Corning | CA | 96021-3605 |  | 2012-08-08 | 2012-08-08 11:54 | 2012-08-08 11:54 | OTHER - 165ANA036-B | 161 | 0 | Yes | Yes | 23.5 | 20.9 | 2.6 | 52445E75D86040828487EB3C499B7D7F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-2802 |  | 2012-07-31 | 2012-07-31 12:33 | 2012-07-31 13:02 | DAY & NIGHT - N2A330AKC200 | 70 | 2.4 | Yes | Yes | 22.9 | 20.6 | 2.3 | 8568A5DF89CB45DAAEED80E06A01F49C |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Stockton | CA | 95207-7474 |  | 2012-06-01 | 2012-06-01 18:13 | 2012-06-01 18:21 | GOODMAN - GPC103007A | 50 | 6.6 | Yes | Yes | 19.5 | 21 | -1.5 | AE198FBD08DA49C69A5182A0AFF845F7 |  | R22 | Non-TXV |  | 13.2% | 0.868 | 25.37% | [5 empty] | Non-TXV | 13.2%
Corning | CA | 96021-2702 |  | 2012-07-31 | 2012-07-31 12:16 | 2012-07-31 16:10 | WEATHER KING - 12AJB36A01 | 107 | 4.2 | Yes | Yes | 25 | 21.2 | 3.8 | 15550ADA6FB14BF78514B5555F6AB065 |  | R22 | Non-TXV |  | 3.925% | 0.96075 | 7.543% | [5 empty] | Non-TXV | 3.925%
Fresno | CA | 93722-9139 |  | 2012-07-02 | 2012-07-02 12:12 | 2012-07-02 12:30 | DAY & NIGHT - 585CJ024050 | 67 | 2 | Yes | Yes | 24.1 | 20.1 | 4 | C8273C3C5B234AE79A4E59607321B1EA |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Corning | CA | 96021-0000 |  | 2012-08-08 | 2012-08-08 18:27 | 2012-08-08 18:44 | BRYANT - 56CN042-E | 68 | 2.3 | Yes | Yes | 19.5 | 19.6 | -0.1 | D76EADA1402E4E7C979A35A89CEB64DD |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Stockton | CA | 95206-6155 |  | 2012-08-16 | 2012-08-16 13:34 | 2012-08-16 13:53 | CARRIER - 38CKC030340 | 67 | 3.1 | Yes | Yes | 23 | 20.2 | 2.8 | EB3A779244B946D98A17EB0D653CD176 |  | R22 | TXV |  | 4.627% | 0.95373 | 8.892% | [5 empty] | TXV | 4.627%
Chico | CA | 95928-4319 |  | 2012-08-02 | 2012-08-02 19:09 | 2012-08-02 19:09 | GOODMAN - GSC140481AE | 104 | 0 | Yes | Yes | 25.3 | 23.1 | 2.2 | F0BB4106F8424226A67293CBE36B47D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-2334 |  | 2012-06-08 | 2012-06-08 10:15 | 2012-06-08 10:15 | OTHER - 550AN030-E | 96 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | 0EE64E6F224A44218BA004AF26CD1CC1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-4510 |  | 2012-07-31 | 2012-07-31 14:02 | 2012-07-31 14:21 | DAY & NIGHT - 567C036RCU | 64 | 3.7 | Yes | Yes | 22.8 | 20.7 | 2.1 | 6D542CAB435C487AA0BC253A23A74287 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.781% | 0.94219 | 11.11% | [5 empty] | Non-TXV | 5.781%
Atwater | CA | 95301-4887 |  | 2012-06-15 | 2012-06-15 11:40 | 2012-06-15 12:01 | OTHER - NA | 33 | 2.6 | Yes | Yes | 17.6 | 19.6 | -2 | 6389161F07CA4DA498C8FBC75AFFEC22 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 7.879% | 0.92121 | 15.14% | [5 empty] | Non-TXV | 7.879%
Chico | CA | 95926-2867 |  | 2012-05-07 | 2012-05-07 19:56 | 2012-05-07 20:16 | ARI - 113ANA0360BEAA | 85 | 5.4 | Yes | Yes | 20.2 | 22.2 | -2 | EC5D61BBE17445D2BF5F67E21773CB4E | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Chico | CA | 95928-6860 |  | 2012-08-02 | 2012-08-02 09:09 | 2012-08-02 09:59 | AMANA - PGD42C0902E | 121 | 13.2 | Yes | Yes | 23.5 | 21.2 | 2.4 | 8B16E6473B36461F90784C5BB6A30153 |  | R22 | Non-TXV |  | 10.91% | 0.89091 | 20.96% | [5 empty] | Non-TXV | 10.91%
Madera | CA | 93637-4889 |  | 2012-07-31 | 2012-07-31 15:10 | 2012-07-31 15:33 | CARRIER - N/A | 166 | 5 | Yes | Yes | 23.8 | 19.5 | 4.3 | 87B7C364AD6741EBA9C5D75D7A568D22 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Atwater | CA | 95301-4862 |  | 2012-05-17 | 2012-05-17 14:30 | 2012-05-17 14:49 | LENNEX - HS93114P | 77 | 8.1 | Yes | Yes | 19.1 | 19.8 | -0.7 | F8DEA43AC99A4A97979E99F2B1C5B52F |  | R22 | Non-TXV |  | 10.52% | 0.89481 | 20.22% | [5 empty] | Non-TXV | 10.52%
Dinuba | CA | 93618-9219 |  | 2012-05-08 | 2012-05-08 12:31 | 2012-05-08 12:52 | ICP - PGF042K0808 | 87 | 4.1 | Yes | Yes | 20.5 | 18.5 | 2 | DC06B43FF4A94A75A3C1E4C935E210F8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.713% | 0.95287 | 9.057% | [5 empty] | Non-TXV | 4.713%
Stockton | CA | 95206-3867 |  | 2012-08-13 | 2012-08-13 08:42 | 2012-08-13 09:05 | CARRIER - 38ETG036300 | 130 | 4.7 | Yes | Yes | 23 | 20.2 | 2.8 | 2A7596B2A7414C67BB1ACE21CD9ABF66 |  | R410A | TXV |  | 3.615% | 0.96385 | 6.948% | [5 empty] | TXV | 3.615%
Kingsburg | CA | 93631-2307 |  | 2012-05-23 | 2012-05-23 10:22 | 2012-05-23 10:39 | GOODMAN - N/A | 86 | 3 | Yes | Yes | 22 | 20.4 | 1.6 | 5DCA5EE14B7E4FB19C56DCF446AB3494 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.488% | 0.96512 | 6.704% | [5 empty] | Non-TXV | 3.488%
Chico | CA | 95973-8233 |  | 2012-08-09 | 2012-08-09 20:06 | 2012-08-09 20:29 | LENNOX - HS26-042-4P | 101 | 8.6 | Yes | Yes | 20.1 | 20.1 | 0 | 573CD46985FB4D3291C93A28C2FF24AE |  | R22 | Non-TXV |  | 8.515% | 0.91485 | 16.36% | [5 empty] | Non-TXV | 8.515%
Chico | CA | 95973-8233 |  | 2012-08-09 | 2012-08-09 20:31 | 2012-08-09 20:53 | LENNOX - HS26-024-4P | 59 | 4.5 | Yes | Yes | 23.5 | 22.4 | 1.2 | 0F3D9C850231423C9548FFA48174D470 |  | R22 | Non-TXV |  | 7.627% | 0.92373 | 14.66% | [5 empty] | Non-TXV | 7.627%
Magalia | CA | 95954-9797 |  | 2012-08-09 | 2012-08-09 12:01 | 2012-08-09 12:17 | DAY & NIGHT - 50Q0024340 | 119 | 3.8 | Yes | Yes | 19.9 | 21 | -1.1 | 31A542AF65A442AA8841E3FEAD551833 |  | R22 | Non-TXV |  | 3.193% | 0.96807 | 6.137% | [5 empty] | Non-TXV | 3.193%
Magalia | CA | 95954-9797 |  | 2012-08-09 | 2012-08-09 12:20 | 2012-08-09 12:36 | DAY & NIGHT - 50Q0030340 | 119 | 4.5 | Yes | Yes | 20.2 | 21.2 | -1 | 554A8886DD16403AB39BC28C128F5D49 |  | R22 | Non-TXV |  | 3.782% | 0.96218 | 7.267% | [5 empty] | Non-TXV | 3.782%
Colusa | CA | 95932-3352 |  | 2012-05-24 | 2012-05-24 13:03 | 2012-05-24 13:27 | LENNOX - MN13ACD-039-230-02 | 85 | 4.4 | Yes | Yes | 20 | 22.4 | -2.4 | A10F7EDD128341DD9302B33686A9DB48 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Colusa | CA | 95932-2942 |  | 2012-08-02 | 2012-08-02 13:36 | 2012-08-02 14:00 | LENNOX - GCS26X-042-100-1PA | 133 | 4.5 | Yes | Yes | 22 | 21.5 | 0.5 | 699C106C3DD74731A0AE46915683F710 |  | R22 | Non-TXV |  | 3.383% | 0.96617 | 6.502% | [5 empty] | Non-TXV | 3.383%
Colusa | CA | 95932-2647 |  | 2012-08-02 | 2012-08-02 11:45 | 2012-08-02 12:06 | LENNOX - 10GCS036-75-3PA | 58 | 2.9 | Yes | Yes | 21 | 20.8 | 0.2 | C519A224EE2A4B1A9CCC592CE7C43E1D |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Cantua Creek | CA | 93608-9721 |  | 2012-07-13 | 2012-07-13 11:38 | 2012-07-13 11:59 | GOODMAN - GSC130301DA | 85 | 2.8 | Yes | Yes | 18.2 | 21 | -2.8 | 647DBABA3A9848CBA281E97C78AC607A |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Chico | CA | 95928-5100 |  | 2012-05-08 | 2012-05-08 11:52 | 2012-05-08 12:13 | AMERICAN STANDARD - 4A7B4030E1000AA | 112 | 8.4 | Yes | Yes | 19.7 | 22.4 | -2.7 | 37F3E2AB6ECA43CDA676D06509BA30A7 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Gustine | CA | 95322-1528 |  | 2012-06-08 | 2012-06-08 09:43 | 2012-06-08 10:06 | OTHER - PGC042K080B | 87 | 2.6 | Yes | Yes | 25.2 | 19.9 | 5.3 | 82D0D4EC3A8B4F03AE59E80EE805EF2D |  | R22 | Non-TXV |  | 2.989% | 0.97011 | 5.743% | [5 empty] | Non-TXV | 2.989%
Dinuba | CA | 93618-9318 |  | 2012-07-11 | 2012-07-11 09:42 | 2012-07-11 10:15 | CARRIER - 48GS-042090301 | 100 | 3.3 | Yes | Yes | 17.5 | 20.5 | -3 | 88FACC88FB8A48DEA1FB11230FB7ECF2 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.3% | 0.967 | 6.342% | [5 empty] | Non-TXV | 3.3%
Cantua Creek | CA | 93608-9721 |  | 2012-07-13 | 2012-07-13 12:16 | 2012-07-13 13:28 | - GSC130301DA | 88 | 2.6 | Yes | Yes | 20.6 | 20.4 | 0.2 | 0F7CE4EC26AE485CA91424100EED9DE2 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Chico | CA | 95928-4017 |  | 2012-07-02 | 2012-07-02 13:04 | 2012-07-02 13:19 | OTHER - 565BJ024 | 70 | 2.9 | Yes | Yes | 26.1 | 21.4 | 4.7 | A56887D203804D4D86EE49968828839A |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Colusa | CA | 95932-2344 |  | 2012-05-24 | 2012-05-24 14:42 | 2012-05-24 15:01 | LENNOX - UNK | 80 | 5.6 | Yes | Yes | 20 | 21.5 | -1.5 | 6D01C249066C4E66960448C8FA20B3EE |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Atwater | CA | 95301-2526 |  | 2012-08-06 | 2012-08-06 13:28 | 2012-08-06 13:46 | ARCOAIRE - HAC030AKA5 | 74 | 8.7 | Yes | Yes | 23.1 | 20.2 | 2.9 | 50B34DC4419F43FE8707FBA011B731DF |  | R22 | Non-TXV |  | 11.76% | 0.88243 | 22.59% | [5 empty] | Non-TXV | 11.76%
Los Banos | CA | 93635-3151 |  | 2012-08-02 | 2012-08-02 10:30 | 2012-08-02 10:50 | GOODMAN - CK36-18 | 76 | 3.8 | Yes | Yes | 22.2 | 20.4 | 1.8 | 80B2AB053ABA4B4BBA8060743A89C291 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Los Banos | CA | 93635-3295 |  | 2012-05-14 | 2012-05-14 11:20 | 2012-05-14 11:48 | TRANE - 2TTB3024A1000AA | 82 | 3.5 | Yes | Yes | 18.8 | 21.3 | -2.5 | 57D4129A8A1F4F1C8CC05B4A4E1147F5 |  | R22 | Non-TXV |  | 4.268% | 0.95732 | 8.203% | [5 empty] | Non-TXV | 4.268%
Madera | CA | 93638-0122 |  | 2012-08-03 | 2012-08-03 13:40 | 2012-08-03 14:08 | BRYANT - 5582ANW03060AAF | 58 | 3.5 | Yes | Yes | 17.2 | 20.1 | -2.9 | AF05D20CACF04FE69B4BD6EA8ACF6FFF |  | R22 | Non-TXV |  | 6.034% | 0.93966 | 11.6% | [5 empty] | Non-TXV | 6.034%
Chico | CA | 95973-0891 |  | 2012-05-24 | 2012-05-24 14:13 | 2012-05-24 14:34 | NA - G14BA-204KA | 70 | 2.4 | Yes | Yes | 25.9 | 22.8 | 3.1 | 1BA36BB9DF1646159ECCDB4232DFB4BD |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Colusa | CA | 95932-3211 |  | 2012-08-02 | 2012-08-02 14:35 | 2012-08-02 14:57 | COLEMAN - BRCS0421BD | 84 | 6.8 | Yes | Yes | 19 | 20.2 | -1.2 | 83EDF4B4B0B34FBF8FDA89F5AA94BA84 |  | R22 | Non-TXV |  | 8.095% | 0.91905 | 15.56% | [5 empty] | Non-TXV | 8.095%
Atwater | CA | 95301-2535 |  | 2012-08-16 | 2012-08-16 12:23 | 2012-08-16 12:40 | AMANA - RCE36A2D | 85 | -5 | Yes | Yes | 23.7 | 20.5 | 3.2 | 1DD18DF802644EAF99CEEFED954A7DF3 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Atwater | CA | 95301-2537 |  | 2012-05-09 | 2012-05-09 12:19 | 2012-05-09 12:40 | GOODMAN - VSC1361AA | 119 | 3.5 | Yes | Yes | 18.1 | 19.9 | -1.8 | 4B1C3EBD44DF49F6A2C6163DAC260949 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Corning | CA | 96021-9672 |  | 2012-08-02 | 2012-08-02 10:31 | 2012-08-02 10:57 | OTHER - ACS-048BCRBB | 87 | 3.3 | Yes | Yes | 23.9 | 22.1 | 1.9 | FF4B0663C2CF41D7A91F385AA0BC2A29 |  | R22 | Non-TXV |  | 3.793% | 0.96207 | 7.29% | [5 empty] | Non-TXV | 3.793%
Los Banos | CA | 93635-3281 |  | 2012-08-06 | 2012-08-06 12:52 | 2012-08-06 13:19 | DAY & NIGHT - 591AN048-C | 118 | 3.7 | Yes | Yes | 18.5 | 20.2 | -1.7 | 123B8E73B98845DAB13ECCED72BAFDD7 |  | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Stockton | CA | 95205-4604 |  | 2012-08-14 | 2012-08-14 13:01 | 2012-08-14 13:22 | RHEEM - RRNA-B024JK06X | 70 | 5.4 | Yes | Yes | 21.3 | 23 | -1.7 | ED54F265E0E645198FF1A98E642F43A4 |  | R22 | Non-TXV |  | 7.714% | 0.92286 | 14.83% | [5 empty] | Non-TXV | 7.714%
Clovis | CA | 93612-4623 |  | 2012-05-15 | 2012-05-15 17:22 | 2012-05-15 17:22 | YORK - D1NA036N05606C | 85 | 0 | Yes | Yes | 18 | 20.9 | -2.9 | FE2828DB0DE44A38A64D894118E5FBD9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-6370 |  | 2012-05-18 | 2012-05-18 10:47 | 2012-05-18 11:17 | BRYANT - 563CN042-D | 104 | -3.8 | Yes | Yes | 21.2 | 20.9 | 0.3 | E4293171D00C4E8D997D76F749B842F3 | OK: Verified Refrigerant Charge | R22 | TXV |  | -3.654% | 1.0365 | 1.023% |  |  |  |  | TXV |  |  | -3.654%
Los Banos | CA | 93635-5125 |  | 2012-08-06 | 2012-08-06 11:50 | 2012-08-06 12:19 | TRANE - TTD730B100A1 | 69 | 2.3 | Yes | Yes | 17.9 | 18.5 | -0.6 | 1E3A5A24B4FA4ED9A2CBFF86F967954B |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Camino | CA | 95709-9515 |  | 2012-08-16 | 2012-08-16 16:36 | 2012-08-16 16:57 | CARRIER - 380B036300 | 125 | 13.7 | Yes | Yes | 21.2 | 22 | -0.8 | C04789B0DD6F4C859FB4EC61D0D33EEA | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.96% | 0.8904 | 21.06% | [5 empty] | Non-TXV | 10.96%
Madera | CA | 93637-5443 |  | 2012-08-09 | 2012-08-09 10:36 | 2012-08-09 10:54 | CARRIER - 48GS-036090301 | 56 | 2.7 | Yes | Yes | 22.9 | 20.4 | 2.6 | 3C1C8B8EFA784234BE627E07054D018A |  | R22 | Non-TXV |  | 4.821% | 0.95179 | 9.266% | [5 empty] | Non-TXV | 4.821%
Chico | CA | 95973-9189 |  | 2012-08-07 | 2012-08-07 19:15 | 2012-08-07 20:17 | BRYANT - 550AN042-F | 139 | 5.1 | Yes | Yes | 23.9 | 21.5 | 2.4 | 63F4FBD0C74B483C98D1263CB8D5F12D |  | R410A | TXV |  | 3.669% | 0.96331 | 7.051% | [5 empty] | TXV | 3.669%
Chico | CA | 95973-9165 |  | 2012-08-07 | 2012-08-07 18:35 | 2012-08-07 18:51 | LENNOX - HS26-042-2P | 104 | 15.1 | Yes | Yes | 24 | 21.4 | 2.6 | F22E52654EF742C49C9BD2ADF001D0E9 |  | R22 | Non-TXV |  | 14.52% | 0.85481 | 27.9% | [5 empty] | Non-TXV | 14.52%
Willows | CA | 95988-3247 |  | 2012-08-15 | 2012-08-15 10:27 | 2012-08-15 11:01 | YORK - D1NA024N05606C | 54 | 6.1 | Yes | Yes | 24.3 | 22.9 | 1.4 | A487F51EAD434197A59CD2F2FBF5FF6D |  | R22 | Non-TXV |  | 11.3% | 0.88704 | 21.71% | [5 empty] | Non-TXV | 11.3%
Merced | CA | 95340-2686 |  | 2012-05-14 | 2012-05-14 10:43 | 2012-05-14 11:03 | PAYNE - PA13NR024000AAAA | 88 | -3.5 | Yes | Yes | 21.6 | 19.3 | 2.3 | 65B81D2FA669452DA8F5D74B0C7ED730 | OK: Verified Refrigerant Charge |  |  |  | -3.977% | 1.0398 | 1.114% |  |  |  |  | 0 |  |  | -3.977%
Willows | CA | 95988-2030 |  | 2012-05-29 | 2012-05-29 12:40 | 2012-05-29 12:40 | BRYANT - PGD324060K001C1 | 71 | 0 | Yes | Yes | 21 | 20.3 | 0.7 | DB8A079CCC164F25A56A99547598EC55 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2749 |  | 2012-08-03 | 2012-08-03 11:27 | 2012-08-03 11:42 | CARRIER - UNK | 86 | 3.9 | Yes | Yes | 17.2 | 19.9 | -2.7 | 02B31D89A9974900BEBC613E0C047758 |  | R22 | Non-TXV |  | 4.535% | 0.95465 | 8.715% | [5 empty] | Non-TXV | 4.535%
Willows | CA | 95988-2250 |  | 2012-08-14 | 2012-08-14 11:17 | 2012-08-14 11:35 | AMANA - VCA36B2A | 78 | 2.9 | Yes | Yes | 17.6 | 20.2 | -2.6 | 0369BCCAC9F44A3F84C8A72245BD23BC |  | R22 | Non-TXV |  | 3.718% | 0.96282 | 7.145% | [5 empty] | Non-TXV | 3.718%
Madera | CA | 93637-5003 |  | 2012-05-07 | 2012-05-07 15:26 | 2012-05-07 15:47 | GOODMAN - GPG13480901AC | 145 | 4.3 | Yes | Yes | 25.8 | 20.4 | 5.4 | 805034A4E29D439EA27BA6029CE3DB07 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.699% | [5 empty] | Non-TXV | 2.966%
Tracy | CA | 95376-4385 |  | 2012-08-08 | 2012-08-08 11:09 | 2012-08-08 11:32 | YORK - B1HA060A06B | 160 | 4.8 | Yes | Yes | 26.1 | 21.4 | 4.7 | 4DECB5404BB6497BB73C76EC546B890F |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95203-1115 |  | 2012-05-11 | 2012-05-11 10:58 | 2012-05-11 11:16 | LUX PAC - 60WE24G1 | 55 | 2.2 | Yes | Yes | 17.4 | 20 | -2.6 | D80AA13570534950A832A2C1F4B201C1 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Willows | CA | 95988-2252 |  | 2012-06-12 | 2012-06-12 14:36 | 2012-06-12 14:54 | YORK - HSDH030S06B | 80 | 8.5 | Yes | Yes | 25.5 | 22.9 | 2.7 | FDC2380F29C84B5D9FBA976AE8022891 |  | R22 | Non-TXV |  | 10.62% | 0.89375 | 20.42% | [5 empty] | Non-TXV | 10.62%
Willows | CA | 95988-2208 |  | 2012-08-14 | 2012-08-14 13:16 | 2012-08-14 13:16 | OTHER - NA | 65 | 0 | Yes | Yes | 26.1 | 22.9 | 3.2 | 0A1E1472CF9A4F8DA65530E29D32FE59 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-9401 |  | 2012-07-31 | 2012-07-31 08:51 | 2012-07-31 09:27 | YORK - DBYP-F030N070A | 73 | 2.1 | Yes | Yes | 24.8 | 19.6 | 5.2 | A39FC45AE733407B953E84821769ABA1 |  | R22 | Non-TXV |  | 2.877% | 0.97123 | 5.528% | [5 empty] | Non-TXV | 2.877%
Willows | CA | 95988-2029 |  | 2012-08-14 | 2012-08-14 10:19 | 2012-08-14 11:01 | LENNOX - GCS26X-030-75-1PA | 85 | 9.2 | Yes | Yes | 19.5 | 19.6 | -0.1 | E4D62801D3B24B7EAC0269AF6224A19E |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
Sanger | CA | 93657-2989 |  | 2012-05-10 | 2012-05-10 14:12 | 2012-05-10 14:34 | BDF COMPANY - 585A024055YAC | 51 | 9.4 | Yes | Yes | 28.6 | 22.5 | 6.1 | 191101E260DD4B999FF361DACC17153E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 18.43% | 0.81569 | 35.42% | [5 empty] | Non-TXV | 18.43%
Willows | CA | 95988-2030 |  | 2012-05-29 | 2012-05-29 09:30 | 2012-05-29 09:51 | BRYANT - 582ANW036090NBAF | 68 | 3.9 | Yes | Yes | 19.1 | 21.8 | -2.7 | 4FEF2DF618A54E68A15445934CB22064 |  | R22 | Non-TXV |  | 5.735% | 0.94265 | 11.02% | [5 empty] | Non-TXV | 5.735%
Stockton | CA | 95210-4217 |  | 2012-05-22 | 2012-05-22 11:19 | 2012-05-22 11:43 | GOODMAN - CK18-1B | 59 | 1.8 | Yes | Yes | 18.8 | 20.4 | -1.6 | BCB91FB5F0C9427EA09C001968FA39B8 |  | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Stockton | CA | 95210-4187 |  | 2012-05-24 | 2012-05-24 13:20 | 2012-05-24 13:42 | RHEEM - RRNL-B036JKO8X | 85 | 8.8 | Yes | Yes | 20 | 20.1 | -0.1 | 67E7655DDD084140B6F879550F5D184B |  | R410A | TXV |  | 10.35% | 0.89647 | 19.9% | [5 empty] | TXV | 10.35%
Chowchilla | CA | 93610-9471 |  | 2012-07-31 | 2012-07-31 10:38 | 2012-07-31 10:54 | GOODMAN - CIJ60-1C | 85 | 3 | Yes | Yes | 18.4 | 21 | -2.6 | EB215CB0B43544588AE83A8A77EECC8A |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Madera | CA | 93636-8540 |  | 2012-08-01 | 2012-08-01 08:49 | 2012-08-01 09:13 | CARRIER - 4BNLT036300 | 96 | 2.9 | Yes | Yes | 23.7 | 21.2 | 2.5 | 7BC31EFBA3B34F56822911528A8F88DA |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Orange Cove | CA | 93646-9417 |  | 2012-07-13 | 2012-07-13 09:33 | 2012-07-13 09:51 | GOODMAN - GPH1336M21AB | 65 | 2.6 | Yes | Yes | 21.2 | 20.4 | 0.8 | C6034B0D4591497CAC753BC5E9BD0246 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Fresno | CA | 93720-2485 |  | 2012-07-30 | 2012-07-30 16:18 | 2012-07-30 16:41 | OTHER - UNK | 84 | 2.8 | Yes | Yes | 18.1 | 20.4 | -2.3 | FDAF80E81AFE4C699C97E3E856C598EF |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95340-1511 |  | 2012-07-31 | 2012-07-31 10:40 | 2012-07-31 10:59 | BDP - 568CJ036 | 152 | 4.6 | Yes | Yes | 21.7 | 19.7 | 2.1 | 53BD6A1A800249A69A363154B19478C5 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Chico | CA | 95928-6934 |  | 2012-05-23 | 2012-05-23 11:02 | 2012-05-23 11:20 | DAY N NIGHT - 24/80 YAC106T | 57 | 2.6 | Yes | Yes | 21.6 | 21.5 | 0.1 | 1676D0B8C0B54D5DA2919F1CA8F4D5F8 |  | R22 | Non-TXV |  | 4.561% | 0.95439 | 8.766% | [5 empty] | Non-TXV | 4.561%
Paradise | CA | 95969-3117 |  | 2012-05-09 | 2012-05-09 19:48 | 2012-05-09 20:05 | - | 85 | 4.5 | Yes | Yes | 18.5 | 21.5 | -3 | 10CB99F9EDA541E180A60160AC368B70 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Newman | CA | 95360-9733 |  | 2012-06-14 | 2012-06-14 11:18 | 2012-06-14 11:36 | GOODMAN - GPG1330070M41AA | 80 | 2.4 | Yes | Yes | 21.7 | 19.3 | 2.4 | 4B8B3A07F8CE48B9B6E9BC35973475AE |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95215-1133 |  | 2012-05-31 | 2012-05-31 10:31 | 2012-05-31 10:52 | PAYNE - PA12NA042-C | 101 | 5.1 | Yes | Yes | 20.7 | 21 | -0.3 | 4CA4547BA2B946B5B7D38BB5F1E1C85F |  | R22 | TXV |  | 5.05% | 0.9495 | 9.704% | [5 empty] | TXV | 5.05%
Red Bluff | CA | 96080-8836 |  | 2012-08-06 | 2012-08-06 11:50 | 2012-08-06 12:19 | YORK - D1NH042N06506C | 94 | 5.4 | Yes | Yes | 19.9 | 21.7 | -1.8 | BE25F178E1BB4CB98DDDD00EE5DDE9D1 |  | R22 | Non-TXV |  | 5.745% | 0.94255 | 11.04% | [5 empty] | Non-TXV | 5.745%
Red Bluff | CA | 96080-8986 |  | 2012-05-16 | 2012-05-16 11:52 | 2012-05-16 12:15 | COLEMAN - NA | 51 | 5.1 | Yes | Yes | 20.8 | 20.9 | -0.1 | 990818D1DE96421DA987BDE4F82D0CCE |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95210-1402 |  | 2012-05-07 | 2012-05-07 16:19 | 2012-05-07 16:19 | RHEEM - HC-80-24-21C | 49 | 0 | Yes | Yes | 21.7 | 23.9 | -2.2 | DD46E946288B4B20BB821F0B10607338 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-6404 |  | 2012-08-06 | 2012-08-06 15:29 | 2012-08-06 15:59 | GUARDIAN - GCGD36S21S2B | 80 | 5 | Yes | Yes | 17 | 19.2 | -2.2 | A004DA0176F04B38AB8E3AC79A8A8AD7 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Los Banos | CA | 93635-3090 |  | 2012-05-09 | 2012-05-09 15:18 | 2012-05-09 15:46 | LENNOX - 12GCS042X-75-5PB | 133 | 4.7 | Yes | Yes | 25.7 | 19.9 | 5.8 | 500315753CA64FC48BB9E4DF9B3B5855 | OK: Verified Refrigerant Charge. |  |  |  | 3.534% | 0.96466 | 6.791% | [5 empty] | 0 | 3.534%
Merced | CA | 95348-1106 |  | 2012-05-11 | 2012-05-11 15:23 | 2012-05-11 15:23 | TRANE - YCC030F1M0AA | 73 | 0 | Yes | Yes | 17.6 | 19.3 | -1.7 | 1FECD54B2D8142A1B25681B36FFA4FF7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5213 |  | 2012-08-08 | 2012-08-08 13:35 | 2012-08-08 14:11 | CARRIER - 38TH048320 | 120 | 5 | Yes | Yes | 25.3 | 19.8 | 5.5 | 1969FEA9070D47E2BEAE6CE0B15CDC95 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Los Banos | CA | 93635-6311 |  | 2012-05-17 | 2012-05-17 13:37 | 2012-05-17 14:02 | GOODMAN - CK2418 | 71 | 7.4 | Yes | Yes | 27 | 21.5 | 5.5 | 146420FAF4F14BB7B8571F85EA492D9B |  | R22 | Non-TXV |  | 10.42% | 0.89577 | 20.03% | [5 empty] | Non-TXV | 10.42%
Red Bluff | CA | 96080-7740 |  | 2012-08-03 | 2012-08-03 10:40 | 2012-08-03 12:18 | UNK - UNK | 85 | 10 | Yes | Yes | 35 | 20.4 | 14.6 | DC12EA4861DC4030A3F85C7813232EF8 |  |  |  |  | 11.76% | 0.88235 | 22.61% | [5 empty] | 0 | 11.76%
Red Bluff | CA | 96080-4025 |  | 2012-08-03 | 2012-08-03 19:40 | 2012-08-03 20:00 | RHEEM - RACC-042JAS | 54 | 1.8 | Yes | Yes | 24.5 | 20.5 | 4 | C569143D58BA453DA108FB0EC9F5C43C |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95204-1705 |  | 2012-07-31 | 2012-07-31 15:12 | 2012-07-31 15:39 | RHEEM - RRPLA0B036JK06X | 93 | 3.3 | Yes | Yes | 22.5 | 21.3 | 1.2 | E90D3E60F5BA47BFBB766B108FDF96DB |  | R410A | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Grass Valley | CA | 95945-8859 |  | 2012-05-08 | 2012-05-08 13:34 | 2012-05-08 15:08 | TRANE - TTN030D100AD | 86 | -4.2 | Yes | Yes | 23.6 | 21.9 | 1.7 | DCDF33F3DACE4B5B856BF0CF4D784747 | OK: Verified Refrigerant Charge | R22 | TXV |  | -4.884% | 1.0488 | 1.368% |  |  |  |  | TXV |  |  | -4.884%
Newman | CA | 95360-9515 |  | 2012-08-14 | 2012-08-14 12:37 | 2012-08-14 13:10 | CARRIER - 38BRC036350 | 103 | 7.3 | Yes | Yes | 18.1 | 20.4 | -2.3 | 30D17D2E91094D6CB2D5FE74B7106960 |  | R22 | TXV |  | 7.087% | 0.92913 | 13.62% | [5 empty] | TXV | 7.087%
Stockton | CA | 95206-6040 |  | 2012-05-14 | 2012-05-14 15:11 | 2012-05-14 15:30 | COMFORTMAKER - FBA036GC1 | 83 | 15.3 | Yes | Yes | 19 | 20.4 | -1.4 | 300009D5053F4FF48D6458AA99645E2A |  | R22 | Non-TXV |  | 18.43% | 0.81566 | 35.43% | [5 empty] | Non-TXV | 18.43%
Stockton | CA | 95204-4155 |  | 2012-08-07 | 2012-08-07 16:18 | 2012-08-07 16:43 | DAY & NIGHT - 591ANX042000AAAA | 100 | 7.8 | Yes | Yes | 19.5 | 21 | -1.5 | 884C5B1D0F0A46C8B86814ABA378294B |  | R22 | Non-TXV |  | 7.8% | 0.922 | 14.99% | [5 empty] | Non-TXV | 7.8%
Fresno | CA | 93726-6318 |  | 2012-05-10 | 2012-05-10 12:36 | 2012-05-10 12:56 | AMANA - SPCG360451A | 119 | 3.5 | Yes | Yes | 23.8 | 21 | 2.8 | A5127485F049443090B8A8EAF57A760F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Red Bluff | CA | 96080-2714 |  | 2012-08-13 | 2012-08-13 12:13 | 2012-08-13 12:29 | DAY & NIGHT - 56701036 | 110 | 4.9 | Yes | Yes | 22.9 | 22.3 | 0.6 | 00B5FDDC52094BCA94F8208E71CB8B64 |  | R22 | Non-TXV |  | 4.455% | 0.95545 | 8.561% | [5 empty] | Non-TXV | 4.455%
Williams | CA | 95987-9003 |  | 2012-08-09 | 2012-08-09 15:00 | 2012-08-09 15:00 | CARRIER - 38CKC030340 | 68 | 0 | Yes | Yes | 15 | 17.4 | -2.4 | 6EEAF0AA22514A5C96CA124D03AC2386 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-9764 |  | 2012-08-08 | 2012-08-08 18:47 | 2012-08-08 19:04 | BRYANT - 561CJ06000A | 152 | 5.8 | Yes | Yes | 21.5 | 21.3 | 0.3 | 7E7CB51EE6C0438891F971E608169F94 |  | R22 | Non-TXV |  | 3.816% | 0.96184 | 7.333% | [5 empty] | Non-TXV | 3.816%
Red Bluff | CA | 96080-9764 |  | 2012-08-08 | 2012-08-08 19:11 | 2012-08-08 19:11 | RHEEM - RAKA-037JAZ | 79 | 0 | Yes | Yes | 24.8 | 20.6 | 4.3 | 5FD85176FAF5451AA7575FC930F75BF1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3522 |  | 2012-05-14 | 2012-05-14 11:57 | 2012-05-14 12:26 | GOODMAN - CKL241K | 76 | 3.3 | Yes | Yes | 18 | 19.4 | -1.4 | A8FBA228B64C4723BF92AF0D6DFF3F2B |  | R22 | Non-TXV |  | 4.342% | 0.95658 | 8.345% | [5 empty] | Non-TXV | 4.342%
Stockton | CA | 95207-7474 |  | 2012-06-01 | 2012-06-01 17:34 | 2012-06-01 17:38 | HEIL - PGC024K04E | 54 | 8.4 | Yes | Yes | 18 | 19.6 | -1.6 | DF652872C9CB402DBC8943BAB4D3B2B5 |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Grass Valley | CA | 95945-4124 |  | 2012-05-30 | 2012-05-30 11:04 | 2012-05-30 11:20 | OTHER - HDEC-0185B | 56 | 3.4 | Yes | Yes | 17 | 19.9 | -2.9 | D8F1E7C18DC54ED293B5AE6D1CAC8CA1 |  | R22 | Non-TXV |  | 6.071% | 0.93929 | 11.67% | [5 empty] | Non-TXV | 6.071%
Grass Valley | CA | 95945-4124 |  | 2012-05-16 | 2012-05-16 12:47 | 2012-05-16 13:12 | FRASER-JOHNSTON - HDEC-F018SB | 56 | 11.9 | Yes | Yes | 16.4 | 19.2 | -2.8 | 70B0ADED34144D15A3E950A4AD77EEE0 |  | R22 | Non-TXV |  | 21.25% | 0.7875 | 40.84% | [5 empty] | Non-TXV | 21.25%
Stockton | CA | 95206-4972 |  | 2012-08-13 | 2012-08-13 09:25 | 2012-08-13 09:47 | GOODMAN - CKL36-1L | 84 | -7.9 | Yes | Yes | 18 | 20.4 | -2.4 | F361926398424DD1B5ABFA14A52332AF |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Stockton | CA | 95206-2906 |  | 2012-05-10 | 2012-05-10 12:45 | 2012-05-10 13:11 | RHEEM - RRNL-BO24JK06X | 78 | 8.4 | Yes | Yes | 21.4 | 22.1 | -0.7 | 71F42FBCB47A410E95B60BDC56FC5A2D | OK: Verified Refrigerant Charge | R410A | TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | TXV | 10.77%
Stockton | CA | 95206-4972 |  | 2012-08-13 | 2012-08-13 16:03 | 2012-08-13 16:26 | GOODMAN - CKL36-1L | 84 | 5.6 | Yes | Yes | 17 | 19.9 | -2.9 | 481390B12D40411B8E9F4AB40778231F |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Dinuba | CA | 93618-3614 |  | 2012-07-31 | 2012-07-31 15:17 | 2012-07-31 15:45 | CARRIER - N/A | 90 | 2.9 | Yes | Yes | 21.3 | 19.9 | 1.4 | 4DAE0987CF1047E8AA385DE213770D05 |  | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Corning | CA | 96021-3615 |  | 2012-08-02 | 2012-08-02 09:23 | 2012-08-02 10:18 | RHEEM - RAF0-030JAS | 69 | 2.6 | Yes | Yes | 24.2 | 21.6 | 2.6 | 1369AFDC862E47E29F50555FA8592431 |  | R22 | Non-TXV |  | 3.768% | 0.96232 | 7.241% | [5 empty] | Non-TXV | 3.768%
Corning | CA | 96021-2159 |  | 2012-07-31 | 2012-07-31 16:38 | 2012-07-31 17:07 | RUUD - UAMC-036JAS | 95 | 5.2 | Yes | Yes | 24.3 | 21.3 | 3.1 | D04FF6756EFA43AE93F2E6BFF4B4F8AB |  | R22 | Non-TXV |  | 5.474% | 0.94526 | 10.52% | [5 empty] | Non-TXV | 5.474%
Corning | CA | 96021-2922 |  | 2012-08-08 | 2012-08-08 17:58 | 2012-08-08 18:15 | INTERTHERM - 530L-036K | 60 | 10.3 | Yes | Yes | 23.2 | 21.2 | 2 | CECE1CF4098943DA891DD7AF192D739A |  | R22 | Non-TXV |  | 17.17% | 0.82833 | 32.99% | [5 empty] | Non-TXV | 17.17%
Stockton | CA | 95206-2902 |  | 2012-05-10 | 2012-05-10 12:13 | 2012-05-10 12:32 | RHEEM - RRNL-BO24JK06X | 78 | 8.8 | Yes | Yes | 25 | 22.1 | 3 | 7D4B731D7DA542BD8B753A6894C9D9C2 | OK: Verified Refrigerant Charge | R410A | TXV |  | 11.28% | 0.88718 | 21.68% | [5 empty] | TXV | 11.28%
Corning | CA | 96021-9403 |  | 2012-08-02 | 2012-08-02 09:58 | 2012-08-02 10:18 | YORK - H4DH036S06A | 95 | 5.4 | Yes | Yes | 23.3 | 21.9 | 1.4 | 4F9571D339B84BA6BDF69023FBEED67C |  | R22 | Non-TXV |  | 5.684% | 0.94316 | 10.92% | [5 empty] | Non-TXV | 5.684%
Tracy | CA | 95377-6630 |  | 2012-07-11 | 2012-07-11 12:09 | 2012-07-11 12:38 | - BRCS0601BD | 118 | 16.1 | Yes | Yes | 18.5 | 19.7 | -1.2 | 5A3C9B15FD094A9EA52CA025B9F0F7CF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.64% | 0.86356 | 26.22% | [5 empty] | Non-TXV | 13.64%
Chico | CA | 95973-1082 |  | 2012-05-10 | 2012-05-10 10:32 | 2012-05-10 10:49 | PAYNE - 56ZGJ030-B | 80 | 6.6 | Yes | Yes | 21 | 22.9 | -1.9 | 7DC51AEBD817463BA7C6C8A8DDC06D6C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.25% | 0.9175 | 15.85% | [5 empty] | Non-TXV | 8.25%
Grass Valley | CA | 95949-9266 |  | 2012-06-19 | 2012-06-19 14:12 | 2012-06-19 14:28 | PAYNE - PY1PNB042090AAAA | 102 | 3.4 | Yes | Yes | 27 | 23.2 | 3.8 | 28AEDA279301487E90CFD5AE0DDCD066 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95348-2219 |  | 2012-05-11 | 2012-05-11 16:00 | 2012-05-11 16:00 | GOODMAN - PGB048 | 86 | 0 | Yes | Yes | 19.7 | 21.5 | -1.8 | E79E3E90FDAA4CDAA6EB690F2E5E6EAC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-9300 |  | 2012-08-08 | 2012-08-08 11:14 | 2012-08-08 11:51 | YORK - H1RA048506D | 117 | 11.2 | Yes | Yes | 24.5 | 20.8 | 3.7 | 9DB91C842D4E45E58D76323726776FFF |  | R22 | Non-TXV |  | 9.573% | 0.90427 | 18.4% | [5 empty] | Non-TXV | 9.573%
Madera | CA | 93637-4419 |  | 2012-05-08 | 2012-05-08 11:20 | 2012-05-08 11:20 | BDP - 385B030075YACR | 50 | 0 | Yes | Yes | 24.1 | 20.2 | 4 | B78403B8BC1644E8896FA1C51AD6D4DD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-0000 |  | 2012-08-07 | 2012-08-07 11:33 | 2012-08-07 11:51 | GOODMAN - CKL60-1L | 115 | -4.2 | Yes | Yes | 18 | 19.3 | -1.3 | F620713635F847F49A3E79F23F7EEA53 |  | R22 | TXV |  | -3.652% | 1.0365 | 1.023% |  |  |  |  | TXV |  |  | -3.652%
Stockton | CA | 95207-4048 |  | 2012-06-07 | 2012-06-07 13:02 | 2012-06-07 13:19 | RHEEM - RRMA-A042JK08X | 114 | 9.8 | Yes | Yes | 24.6 | 20.7 | 3.9 | 04063EE393844C90AE4821A3CA0EBA50 |  | R22 | Non-TXV |  | 8.596% | 0.91404 | 16.52% | [5 empty] | Non-TXV | 8.596%
Pollock Pines | CA | 95726-9734 |  | 2012-08-16 | 2012-08-16 13:15 | 2012-08-16 13:35 | TRANE - BYC030H1LNAA | 64 | 8.8 | Yes | Yes | 24.8 | 20.4 | 4.4 | FEBDB056F712465F9BE44D9F378B0029 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Chico | CA | 95928-6387 |  | 2012-08-01 | 2012-08-01 18:50 | 2012-08-01 19:26 | TEMPSTAR - H2CH036506A | 165 | 8.2 | Yes | Yes | 23.5 | 21.8 | 1.8 | EA0CA376C9134C80A6C2856030A96288 |  | R22 | Non-TXV |  | 4.97% | 0.9503 | 9.551% | [5 empty] | Non-TXV | 4.97%
Corning | CA | 96021-9232 |  | 2012-05-17 | 2012-05-17 12:31 | 2012-05-17 13:18 | COLEMAN - 9646F801 | 105 | 4.4 | Yes | Yes | 32.5 | 27.2 | 5.3 | BD11CA8A207A46F4A77BFB8D980CC2FA |  | R22 | Non-TXV |  | 4.19% | 0.9581 | 8.053% | [5 empty] | Non-TXV | 4.19%
Merced | CA | 95340-4031 |  | 2012-08-08 | 2012-08-08 15:41 | 2012-08-08 16:11 | AIRE-FLO - PGB24C0902E | 64 | 8.5 | Yes | Yes | 25.6 | 26.7 | -1.1 | 78F884CF792340B6A57144C89847E02D |  | R22 | Non-TXV |  | 13.28% | 0.86719 | 25.52% | [5 empty] | Non-TXV | 13.28%
Manteca | CA | 95336-4145 |  | 2012-08-02 | 2012-08-02 10:52 | 2012-08-02 11:18 | UNITARY PRODUCTS GROUP - GCGD48S41S3A | 73 | 25.6 | Yes | Yes | 17.2 | 19.8 | -2.6 | 9DF64617D1DA4658A1B223696C51AC44 |  | R410A | Non-TXV |  | 35.07% | 0.64932 | 67.39% | [5 empty] | Non-TXV | 35.07%
Atwater | CA | 95301-4859 |  | 2012-05-11 | 2012-05-11 11:34 | 2012-05-11 11:53 | LENNEX - HS9-311-6P | 67 | 6.7 | Yes | Yes | 18.7 | 21 | -2.3 | 91AE758AEAA24230B3D6037A9CAE0BC5 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Merced | CA | 95348-2218 |  | 2012-05-11 | 2012-05-11 12:07 | 2012-05-11 12:26 | FRASER - UNK | 100 | 5.4 | Yes | Yes | 23.2 | 21.5 | 1.7 | 2B0FA72D768140FC83763D8A5565DE45 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.4% | 0.946 | 10.38% | [5 empty] | Non-TXV | 5.4%
Grass Valley | CA | 95945-9331 |  | 2012-05-08 | 2012-05-08 18:16 | 2012-05-08 18:16 | DAY&NIGHT - 591ANX036000AAAA | 86 | 0 | Yes | Yes | 25.8 | 20.9 | 4.9 | 0022633E9E9640099896F84DCDE4DD27 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-9657 |  | 2012-08-14 | 2012-08-14 14:16 | 2012-08-14 14:41 | AMANA - SPCG360701A | 119.7 | -11.3 | Yes | Yes | 16.5 | 16.7 | -0.2 | B5517C962377450587BCCD05C744EB28 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.44% | 1.0944 | 2.644% |  |  |  |  | Non-TXV |  |  | -9.44%
Tracy | CA | 95376-8945 |  | 2012-08-14 | 2012-08-14 14:36 | 2012-08-14 14:59 | DAY & NIGHT - 561AJ048-F | 102 | 3 | Yes | Yes | 21.1 | 18.6 | 2.5 | E26FA9153F0D4B8B88A9B9898DD81EC9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95207-7624 |  | 2012-06-01 | 2012-06-01 15:04 | 2012-06-01 15:20 | WESTINGHOUSE - BRCS0181BB | 61 | 5.8 | Yes | Yes | 21.7 | 20.9 | 0.8 | 94C5A1AE3E8C474E8724DCAA1543E528 |  | R22 | Non-TXV |  | 9.508% | 0.90492 | 18.27% | [5 empty] | Non-TXV | 9.508%
Tracy | CA | 95376-2821 |  | 2012-07-03 | 2012-07-03 10:35 | 2012-07-03 10:55 | DAY & NIGHT - N2A324AKC200 | 56 | 1.9 | Yes | Yes | 19.5 | 19.9 | -0.4 | 41D089DB7BC348F5AE8B0AB6738DB601 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Atwater | CA | 95301-4540 |  | 2012-05-11 | 2012-05-11 11:50 | 2012-05-11 12:08 | BRYANT - 582ANW030040AAAD | 55 | 1.6 | Yes | Yes | 26 | 20.2 | 5.9 | D2BDBEC093DE49959123BE1EF36FA14B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Stockton | CA | 95205-3229 |  | 2012-05-17 | 2012-05-17 16:08 | 2012-05-17 16:26 | RUUD - URKA-A024JK06E | 50 | 3.9 | Yes | Yes | 16.9 | 19 | -2.1 | 672A6507D30F42C48D80B37A08F10AC8 |  | R22 | Non-TXV |  | 7.8% | 0.922 | 14.99% | [5 empty] | Non-TXV | 7.8%
Tracy | CA | 95376-4549 |  | 2012-06-20 | 2012-06-20 15:15 | 2012-06-20 15:36 | OTHER - PGE12B24D050A-2A | 72 | 14.9 | Yes | Yes | 20.3 | 22.1 | -1.8 | 599C2BE5B8F54657AA14DF220AC0E611 |  | R22 | Non-TXV |  | 20.69% | 0.79306 | 39.77% | [5 empty] | Non-TXV | 20.69%
Stockton | CA | 95210-4262 |  | 2012-05-22 | 2012-05-22 15:02 | 2012-05-22 15:21 | GOODMAN - VSX130301AA | 78 | -4.6 | Yes | Yes | 26.5 | 21.6 | 5 | C9EB09A925E846868584EB2751E9F401 |  | R410A | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Stockton | CA | 95205-3230 |  | 2012-08-03 | 2012-08-03 10:32 | 2012-08-03 10:53 | RHEEM - RRKA-A030JK06X | 54 | 3.1 | Yes | Yes | 21 | 20.4 | 0.6 | B592A8B41E634284ABB903EB9F719449 |  | R22 | Non-TXV |  | 5.741% | 0.94259 | 11.03% | [5 empty] | Non-TXV | 5.741%
Orland | CA | 95963-9813 |  | 2012-08-14 | 2012-08-14 19:43 | 2012-08-14 19:43 | PAYNE - PY1PNB03606060ABAD | 68 | 0 | Yes | Yes | 25.3 | 21.2 | 4.2 | 915ABE46591B4F8DA5BDDCEC84AB0E00 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-9218 |  | 2012-05-22 | 2012-05-22 13:57 | 2012-05-22 14:38 | GIBSON - JS3BC036KA | 82 | 14.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | 23837B1BFED843C598459B8FB3D7246E |  | R22 | Non-TXV |  | 17.8% | 0.82195 | 34.22% | [5 empty] | Non-TXV | 17.8%
Merced | CA | 95348-2215 |  | 2012-08-08 | 2012-08-08 08:48 | 2012-08-08 09:05 | RHEEM - H07536A1B | 74 | 2.9 | Yes | Yes | 18.2 | 20.3 | -2.1 | 9A89892D7F474234A1172708BBDD0A08 |  | R22 | Non-TXV |  | 3.919% | 0.96081 | 7.531% | [5 empty] | Non-TXV | 3.919%
Firebaugh | CA | 93622-2321 |  | 2012-05-31 | 2012-05-31 12:05 | 2012-05-31 12:24 | CARRIER - BBCKC060370 | 99 | 3.6 | Yes | Yes | 24 | 19.8 | 4.2 | 0A94E4CC7B3A466F9C97525F06B03F33 |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Oakdale | CA | 95361-9783 |  | 2012-08-16 | 2012-08-16 10:07 | 2012-08-16 10:26 | BRYANT - 563CN036-D | 101 | 3 | Yes | Yes | 25.9 | 19.9 | 6 | 076EDC6B577E4FCB8AB377D75D8D1803 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Oakdale | CA | 95361-9783 |  | 2012-08-16 | 2012-08-16 10:30 | 2012-08-16 10:55 | UNITARY PRODUCTS GROUP - BRCS04818D | 117 | 28.6 | Yes | Yes | 21.1 | 21 | 0.1 | 53B2F57893804DA0B6BF089D48284284 |  | R22 | Non-TXV |  | 24.44% | 0.75556 | 46.98% | [5 empty] | Non-TXV | 24.44%
Fresno | CA | 93722-7121 |  | 2012-05-16 | 2012-05-16 13:37 | 2012-05-16 14:03 | LENNOX - 12ACB36-4P | 106 | 3.1 | Yes | Yes | 24.3 | 18.3 | 6 | CEBFA20F40564D3EB49DC3C3951749D6 |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
Stockton | CA | 95207-3923 |  | 2012-06-07 | 2012-06-07 15:12 | 2012-06-07 15:31 | OTHER - UNK | 69 | 15.6 | Yes | Yes | 18.9 | 20.4 | -1.5 | 99F9232D6B5A412D80B25A30552A1405 |  | R22 | Non-TXV |  | 22.61% | 0.77391 | 43.45% | [5 empty] | Non-TXV | 22.61%
Paradise | CA | 95969-5304 |  | 2012-08-15 | 2012-08-15 13:24 | 2012-08-15 13:24 | AMERICAN STANDARD - YCP048F1H0AB | 161 | 0 | Yes | Yes | 22 | 20.4 | 1.6 | D03023D3D801498ABBE6E952C41F018B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-9237 |  | 2012-08-02 | 2012-08-02 14:50 | 2012-08-02 15:15 | GOODMAN - CKL49-1 | 109 | 4.2 | Yes | Yes | 18.6 | 20.8 | -2.2 | DEE19DB890054BCA91A9101D885E25C7 |  | R22 | Non-TXV |  | 3.853% | 0.96147 | 7.405% | [5 empty] | Non-TXV | 3.853%
Fresno | CA | 93726-4120 |  | 2012-05-08 | 2012-05-08 16:37 | 2012-05-08 16:58 | SEARS - N/A | 100 | 2.9 | Yes | Yes | 24.8 | 22.6 | 2.2 | BD343F58B2CE426987E23E594DB645B3 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Shingle Springs | CA | 95682-7506 |  | 2012-08-07 | 2012-08-07 12:54 | 2012-08-07 13:12 | LENNOX - HS22-411U-1P | 129 | -11.8 | Yes | Yes | 26.1 | 21.5 | 4.6 | B302558E439A47B6AF96D4BFD7A31530 |  | R22 | TXV |  | -9.147% | 1.0915 | 2.562% |  |  |  |  | TXV |  |  | -9.147%
Grass Valley | CA | 95945-4121 |  | 2012-05-16 | 2012-05-16 10:21 | 2012-05-16 10:43 | FRASER-JOHNSTON - HDEC-F018SC | 56 | 7.7 | Yes | Yes | 16 | 18.2 | -2.2 | 2A63080B3B1A4285BFAD63A36625FE0A | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Stockton | CA | 95204-1461 |  | 2012-07-31 | 2012-07-31 15:54 | 2012-07-31 16:15 | OTHER - CA5536VKD2 | 82 | 7 | Yes | Yes | 20.8 | 20.4 | 0.4 | A4FE8C5B97E74123BCD1C974DD7B1E90 |  | R22 | Non-TXV |  | 8.537% | 0.91463 | 16.41% | [5 empty] | Non-TXV | 8.537%
Stockton | CA | 95206-2627 |  | 2012-08-08 | 2012-08-08 13:40 | 2012-08-08 14:02 | RHEEM - HC-80-30-21C | 48 | 2.4 | Yes | Yes | 22 | 20.4 | 1.6 | 0691332A770B40D4B418EF002F049E13 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Colusa | CA | 95932-2126 |  | 2012-08-09 | 2012-08-09 11:20 | 2012-08-09 11:20 | LENNOX - HS26-060-2P | 165 | 0 | Yes | Yes | 21.5 | 19.9 | 1.6 | FCBA7C6930C44AE0B35CD6D9FBED1AE1 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2904 |  | 2012-05-10 | 2012-05-10 11:46 | 2012-05-10 11:46 | RHEEM - RRNL-B030JK06X | 78 | 0 | Yes | Yes | 23.6 | 21.9 | 1.7 | 50BBEB293A224EA58F3750FA73973D6C | OK: Verified Refrigerant Charge | R410A | TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-2710 |  | 2012-08-06 | 2012-08-06 17:24 | 2012-08-06 17:58 | CARRIER - 38UE004300A | 145 | 9.9 | Yes | Yes | 23.9 | 21.5 | 2.4 | 9D9AF518BFE24C55ADC11EEDDBAB652B |  | R22 | Non-TXV |  | 6.828% | 0.93172 | 13.12% | [5 empty] | Non-TXV | 6.828%
Chico | CA | 95926-3335 |  | 2012-05-07 | 2012-05-07 21:54 | 2012-05-07 21:54 | GAMA - 580ANW036060 | 60 | 0 | Yes | Yes | 20.5 | 22.5 | -2 | 6FAEB4CC9DDF451BBE2FCA7341EBC41F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-7902 |  | 2012-07-09 | 2012-07-09 14:04 | 2012-07-09 14:25 | YORK - H1RC42S06A | 105 | 3.3 | Yes | Yes | 18.4 | 19.7 | -1.3 | 28618FF2638A4161AAD78838444BF40E |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Colusa | CA | 95932-3192 |  | 2012-08-06 | 2012-08-06 12:00 | 2012-08-06 12:19 | RUUD - 13AJ48A01 | 123 | 10.1 | Yes | Yes | 22.7 | 19.7 | 3 | 002F7803F3114DDABD0A02BE3032A191 |  | R22 | TXV |  | 8.211% | 0.91789 | 15.78% | [5 empty] | TXV | 8.211%
Colusa | CA | 95932-0000 |  | 2012-08-02 | 2012-08-02 10:04 | 2012-08-02 10:30 | ALLEGIANCE - 2A7A4042B1000AA | 137 | 5 | Yes | Yes | 24 | 19.8 | 4.2 | B1232133858D4542AF7DDFC4271CEA26 |  | R22 | Non-TXV |  | 3.65% | 0.9635 | 7.014% | [5 empty] | Non-TXV | 3.65%
Colusa | CA | 95932-0000 |  | 2012-08-02 | 2012-08-02 10:32 | 2012-08-02 10:52 | LENNOX - HP22-261-3P | 132 | 4.3 | Yes | Yes | 20 | 19.9 | 0.1 | 0D9F053ACFA0420C9EBA07E9E19F9BDD |  | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.26% | [5 empty] | Non-TXV | 3.258%
Merced | CA | 95341-7014 |  | 2012-05-15 | 2012-05-15 13:09 | 2012-05-15 14:01 | BRYANT - 582ANW036060NABF | 72 | 4.2 | Yes | Yes | 23.4 | 19.8 | 3.6 | E6914B19D49D4737A0FA502BE70D6E9D |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Merced | CA | 95348-2821 |  | 2012-08-02 | 2012-08-02 08:43 | 2012-08-02 09:02 | GOODMAN - PCB048075 | 86 | 4.6 | Yes | Yes | 18.7 | 20.4 | -1.7 | B363B690A63A4F4A8D9D3945C4CFEC42 |  | R22 | Non-TXV |  | 5.349% | 0.94651 | 10.28% | [5 empty] | Non-TXV | 5.349%
Merced | CA | 95340-3214 |  | 2012-05-30 | 2012-05-30 11:25 | 2012-05-30 11:50 | PAYNE - 585HJ018040 | 61 | 8.3 | Yes | Yes | 20.2 | 19.1 | 1.1 | 2505281F151D4DDEAB2C73C2307F911F |  | R22 | Non-TXV |  | 13.61% | 0.86393 | 26.15% | [5 empty] | Non-TXV | 13.61%
Colusa | CA | 95932-2869 |  | 2012-05-24 | 2012-05-24 16:14 | 2012-05-24 16:30 | RHEEM - UNK | 54 | 2 | Yes | Yes | 18 | 20.4 | -2.4 | F73D0AA688054A81A52EBDB5AFBD4CF6 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Colusa | CA | 95932-2869 |  | 2012-05-24 | 2012-05-24 13:45 | 2012-05-24 14:02 | RHEEM - UNK | 56 | 1.9 | Yes | Yes | 25 | 21 | 4 | CDD5D9CC0C0D4F57ACEA186A1342B598 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Tracy | CA | 95377-7954 |  | 2012-08-14 | 2012-08-14 13:22 | 2012-08-14 13:40 | CARRIER - 38BRC060330 | 201 | 7.7 | Yes | Yes | 25.8 | 20.2 | 5.6 | AA4B1A791E2B477183ECA1844C011ED3 |  | R22 | Non-TXV |  | 3.831% | 0.96169 | 7.362% | [5 empty] | Non-TXV | 3.831%
Fresno | CA | 93727-4428 |  | 2012-05-09 | 2012-05-09 13:12 | 2012-05-09 13:32 | ARI - TCGD24S21S1A | 85 | 2.5 | Yes | Yes | 24.1 | 21 | 3.1 | 9F6483325A2C4D4C85F2C5669AE0854E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Paradise | CA | 95969-5111 |  | 2012-05-09 | 2012-05-09 13:33 | 2012-05-09 13:33 | BRYANT - 574DNW024060NB | 75 | 0 | Yes | Yes | 20.5 | 17.4 | 3.1 | 6B56F5E5418E43BC8375DB1BD34ED75D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-2204 |  | 2012-08-14 | 2012-08-14 11:04 | 2012-08-14 11:27 | YORK - H2RA030S06D | 61 | 9.1 | Yes | Yes | 20 | 20.4 | -0.4 | CF5F92B6FA2A421980A53B7DEA544CE3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 14.92% | 0.85082 | 28.67% | [5 empty] | Non-TXV | 14.92%
Merced | CA | 95348-2721 |  | 2012-08-10 | 2012-08-10 11:16 | 2012-08-10 12:01 | BRYANT - 582ANW042090NAAG | 111 | 4.9 | Yes | Yes | 22.6 | 20.8 | 1.8 | AE23959D14AB4117AEC94B3A370CC9C0 |  | R22 | Non-TXV |  | 4.414% | 0.95586 | 8.484% | [5 empty] | Non-TXV | 4.414%
Chico | CA | 95973-5600 |  | 2012-05-07 | 2012-05-07 19:01 | 2012-05-07 19:34 | DAY N NIGHT - 597ANX036000AAAA | 138 | 5.4 | Yes | Yes | 15.3 | 18 | -2.7 | 4BF9D75AB7D6460E9E525C16E9EED16F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Los Banos | CA | 93635-9218 |  | 2012-06-08 | 2012-06-08 09:06 | 2012-06-08 09:35 | GIBSON - JS3BC-042KA | 102 | 3.2 | Yes | Yes | 22.7 | 20.9 | 1.8 | 9AF7DE1C58984E8E972DCFFD7CC103A6 |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Stockton | CA | 95210-5349 |  | 2012-05-29 | 2012-05-29 11:13 | 2012-05-29 11:34 | BDP - 561CJ024-C | 72 | 2.2 | Yes | Yes | 17.2 | 18.7 | -1.5 | F90BFC6F42B84A80B27EE517B40F0243 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Stockton | CA | 95206-2888 |  | 2012-08-09 | 2012-08-09 11:53 | 2012-08-09 12:10 | OTHER - 561C030-B | 70 | -6.6 | Yes | Yes | 21 | 19.5 | 1.5 | 430DD8120EF247588219070FCF273440 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Orosi | CA | 93647-2109 |  | 2012-05-29 | 2012-05-29 13:57 | 2012-05-29 14:16 | YORK - D2NP036N05606A | 108 | 3.2 | Yes | Yes | 20.7 | 19.4 | 1.3 | 126C32637AE044B18A990D28A6F2CE34 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Paradise | CA | 95969-2461 |  | 2012-07-31 | 2012-07-31 09:19 | 2012-07-31 09:43 | CARRIER - 38EB042360 | 87 | 12.6 | Yes | Yes | 19.9 | 22 | -2.1 | 1EAF0E7DC46D435D85975B02E1B30D75 |  | R22 | Non-TXV |  | 14.48% | 0.85517 | 27.83% | [5 empty] | Non-TXV | 14.48%
Corning | CA | 96021-2304 |  | 2012-05-17 | 2012-05-17 13:16 | 2012-05-17 13:16 | LENNOX - HS26-042-3P | 104 | 0 | Yes | Yes | 23.8 | 19.1 | 4.7 | 066AD15A72D94BB6882472F8F64D5696 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-2408 |  | 2012-07-31 | 2012-07-31 16:17 | 2012-07-31 16:35 | TEMPSTAR - CA9036VKD2 | 55 | 4 | Yes | Yes | 23.5 | 22.1 | 1.4 | 3ABB022CD8624DFBB5930660619E20BA |  | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Corning | CA | 96021-0000 |  | 2012-07-31 | 2012-07-31 16:14 | 2012-07-31 16:14 | RHEEM - RRNA-B042JK08X | 106 | 0 | Yes | Yes | 21.5 | 22.1 | -0.6 | 21FAAE5759914C8BBF1F5209F22E084A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-1019 |  | 2012-08-15 | 2012-08-15 15:56 | 2012-08-15 16:18 | YORK - AC042X1021A | 84 | -7.9 | Yes | Yes | 21.5 | 19.1 | 2.4 | 02EBF5ABBB584CA6B6D9A157FE8BD4AB |  | R22 | Non-TXV |  | -9.405% | 1.094 | 2.634% |  |  |  |  | Non-TXV |  |  | -9.405%
Corning | CA | 96021-3633 |  | 2012-08-14 | 2012-08-14 08:59 | 2012-08-14 09:55 | GOODMAN - CKL30-1E | 72 | 7.8 | Yes | Yes | 24 | 20.8 | 3.2 | 242FE2335965418DAE1F4CEB44BC445B |  | R22 | Non-TXV |  | 10.83% | 0.89167 | 20.82% | [5 empty] | Non-TXV | 10.83%
Paradise | CA | 95969-2710 |  | 2012-07-31 | 2012-07-31 12:02 | 2012-07-31 12:31 | AMERICAN STANDARD - 2A7A5042A1000AA | 134 | 6.5 | Yes | Yes | 19.7 | 20.8 | -1.1 | 3E718C7A508849C59559EC121105CEE0 |  | R22 | Non-TXV |  | 4.851% | 0.95149 | 9.322% | [5 empty] | Non-TXV | 4.851%
Corning | CA | 96021-2902 |  | 2012-08-08 | 2012-08-08 09:05 | 2012-08-08 10:00 | YORK - H20H036906B | 114 | 6.2 | Yes | Yes | 20.9 | 21.8 | -0.9 | 8D3C77665CCE43E29F8D7DA1037D0599 |  | R22 | Non-TXV |  | 5.439% | 0.94561 | 10.45% | [5 empty] | Non-TXV | 5.439%
Manteca | CA | 95337-6881 |  | 2012-08-01 | 2012-08-01 11:58 | 2012-08-01 12:18 | BDP - 563CN030-A | 102 | 14.6 | Yes | Yes | 16.8 | 19.2 | -2.4 | 712B71568E904949B966AC18B593E3C1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.31% | 0.85686 | 27.51% | [5 empty] | Non-TXV | 14.31%
Stockton | CA | 95206-6109 |  | 2012-08-15 | 2012-08-15 14:44 | 2012-08-15 15:04 | BRYANT - 563CN036-C | 100 | 6.1 | Yes | Yes | 19 | 20.4 | -1.4 | 0F2109D3B6A44856AC830AA8555E04ED |  | R22 | Non-TXV |  | 6.1% | 0.939 | 11.72% | [5 empty] | Non-TXV | 6.1%
Fresno | CA | 93711-1307 |  | 2012-05-24 | 2012-05-24 13:36 | 2012-05-24 13:53 | PAYNE - N/A | 96 | 2.9 | Yes | Yes | 22.5 | 21 | 1.5 | 13C737A8E2054FD498802663B369358F |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Oroville | CA | 95966-3655 |  | 2012-08-16 | 2012-08-16 09:18 | 2012-08-16 09:18 | YORK - H4DB060506A | 130 | 0 | Yes | Yes | 20.5 | 21.2 | -0.7 | 2DA3AE5C704D413B9FD056261B8AD6A4 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-6206 |  | 2012-05-16 | 2012-05-16 14:34 | 2012-05-16 14:59 | TRANE - TTP026C100A3 | 140 | 12.1 | Yes | Yes | 24.8 | 21 | 3.8 | A7187BBBE50943B28DFA2288D2F4F5BE |  | R22 | Non-TXV |  | 8.643% | 0.91357 | 16.61% | [5 empty] | Non-TXV | 8.643%
Merced | CA | 95348-1440 |  | 2012-05-21 | 2012-05-21 10:17 | 2012-05-21 10:40 | TRANE - BTD24A100C1 | 68 | -6.4 | Yes | Yes | 27 | 21.3 | 5.8 | 443537E17D164CFABB98E0C9915B6413 |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Stockton | CA | 95206-3889 |  | 2012-06-08 | 2012-06-08 09:54 | 2012-06-08 09:54 | TEMPSTAR - N4A330AKC200 | 74 | 0 | Yes | Yes | 19.3 | 19.8 | -0.5 | F6ACE9CDF834459C802AF63E59A085D4 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2903 |  | 2012-05-29 | 2012-05-29 16:43 | 2012-05-29 17:04 | GUARDIAN - GCGD36S41S3A | 73 | 10.5 | Yes | Yes | 20.1 | 21 | -0.9 | 47ED665A8D4248DC8162AB748501E071 |  | R410A | Non-TXV |  | 14.38% | 0.85616 | 27.64% | [5 empty] | Non-TXV | 14.38%
Tracy | CA | 95376-4374 |  | 2012-08-03 | 2012-08-03 17:03 | 2012-08-03 17:31 | PAYNE - 591ANX042000ABAA | 112 | 3.4 | Yes | Yes | 17.6 | 19 | -1.4 | E2268CD94368439BA23C54A528B4CB34 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Orland | CA | 95963-9141 |  | 2012-08-13 | 2012-08-13 13:11 | 2012-08-13 13:38 | BRYANT - 607CNXA36000AB | 153 | 5.8 | Yes | Yes | 19.2 | 21.5 | -2.3 | BDBDD55D412D443F8A41E6730C4192DC |  | R410A | Non-TXV |  | 3.791% | 0.96209 | 7.285% | [5 empty] | Non-TXV | 3.791%
Corning | CA | 96021-2125 |  | 2012-05-23 | 2012-05-23 10:36 | 2012-05-23 11:06 | YORK - H1RO24S06D | 64 | 5.2 | Yes | Yes | 22 | 22.4 | -0.4 | EC9DA7160F634E23ACE16B2B742939A3 |  | R22 | Non-TXV |  | 8.125% | 0.91875 | 15.61% | [5 empty] | Non-TXV | 8.125%
Chico | CA | 95926-2957 |  | 2012-08-01 | 2012-08-01 12:12 | 2012-08-01 13:22 | AMANA - P121920SC | 84 | 11 | Yes | Yes | 21.7 | 21.5 | 0.2 | 58406C2A89A04B54BB1F82136016DA61 |  | R22 | Non-TXV |  | 13.1% | 0.86905 | 25.17% | [5 empty] | Non-TXV | 13.1%
Chico | CA | 95928-7650 |  | 2012-05-09 | 2012-05-09 10:02 | 2012-05-09 10:26 | DAY & NIGHT - 563CN030-A | 99 | 5.4 | Yes | Yes | 27.7 | 21.9 | 5.8 | 42D653362BF64D439364BEC9E6A0A47F | OK: Verified Refrigerant Charge | R22 | TXV |  | 5.455% | 0.94545 | 10.48% | [5 empty] | TXV | 5.455%
Merced | CA | 95340-5463 |  | 2012-08-09 | 2012-08-09 16:01 | 2012-08-09 16:30 | GE - UNK | 80 | 5.5 | Yes | Yes | 27.4 | 22.1 | 5.3 | 1ACB880451754F35B5E1B8164F194FEC |  | R22 | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Stockton | CA | 95206-1868 |  | 2012-05-07 | 2012-05-07 16:13 | 2012-05-07 16:33 | PAYNE - 580AN030040 | 85 | 8.6 | Yes | Yes | 29.3 | 25.3 | 4 | 236D129D1541420A8DAA98D344AD0A14 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.12% | 0.89882 | 19.44% | [5 empty] | Non-TXV | 10.12%
Merced | CA | 95341-7042 |  | 2012-08-07 | 2012-08-07 13:49 | 2012-08-07 14:10 | BRYANT - 574BNW030040NNB | 128 | 4.7 | Yes | Yes | 23.9 | 23.2 | 0.7 | 8EAFF957B2D547129AE216E8FC3C4333 |  | R22 | Non-TXV |  | 3.672% | 0.96328 | 7.057% | [5 empty] | Non-TXV | 3.672%
Chico | CA | 95973-9191 |  | 2012-05-10 | 2012-05-10 14:14 | 2012-05-10 14:14 | GOODMAN - GPG10300701A | 85 | 0 | Yes | Yes | 23.7 | 20.4 | 3.3 | 546EFC7A410848B5A34809EBA8DF24FC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4605 |  | 2012-08-13 | 2012-08-13 18:05 | 2012-08-13 18:23 | TRANE - 4TTX4048A1000AB | 127 | 7.8 | Yes | Yes | 23 | 20.1 | 2.9 | BA6B77460BFC44A6A4609E951EFEAEF0 |  | R410A | Non-TXV |  | 6.142% | 0.93858 | 11.8% | [5 empty] | Non-TXV | 6.142%
Orland | CA | 95963-9465 |  | 2012-08-14 | 2012-08-14 19:08 | 2012-08-14 19:36 | GOODMAN - G5H130481AD | 187 | 11.7 | Yes | Yes | 22.7 | 21.8 | 0.9 | D66F33C1E7F34284B360FF8B94CA0D5C |  | R22 | Non-TXV |  | 6.257% | 0.93743 | 12.02% | [5 empty] | Non-TXV | 6.257%
Merced | CA | 95341-7001 |  | 2012-05-09 | 2012-05-09 11:38 | 2012-05-09 12:00 | BRYANT - 582ANW036060NBAF | 68 | 7.2 | Yes | Yes | 26.6 | 22.1 | 4.5 | 5B7973A159364A02823DD52DC86494B4 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Tracy | CA | 95376-5411 |  | 2012-08-08 | 2012-08-08 14:10 | 2012-08-08 14:59 | TRANE - TTR748A100A0 | 140 | 4.3 | Yes | Yes | 22.7 | 19.2 | 3.5 | 6D878D745292409FBFA64972D860484E |  | R22 | Non-TXV |  | 3.071% | 0.96929 | 5.903% | [5 empty] | Non-TXV | 3.071%
Los Banos | CA | 93635-6448 |  | 2012-08-13 | 2012-08-13 14:28 | 2012-08-13 15:21 | GIBSON - JS3BA-048KA | 115 | 4.5 | Yes | Yes | 19 | 20.1 | -1.1 | 9BDC41C2A6504495B5B3D45E89DEDED2 |  | R22 | Non-TXV |  | 3.913% | 0.96087 | 7.52% | [5 empty] | Non-TXV | 3.913%
Chico | CA | 95928-8333 |  | 2012-08-01 | 2012-08-01 19:31 | 2012-08-01 19:31 | CARRIER - 48GS-03006034 | 55 | 0 | Yes | Yes | 27.2 | 21.4 | 5.8 | B313F6C8B32848528309696D2C902D42 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Orland | CA | 95963-0000 |  | 2012-05-21 | 2012-05-21 11:34 | 2012-05-21 11:40 | BRYANT - 574ANW048090NB | 196 | 7.6 | Yes | Yes | 21.3 | 21.7 | -0.4 | EFE9EDBA7F5D4B7C8DFD1CC807A14A76 |  | R22 | Non-TXV |  | 3.878% | 0.96122 | 7.452% | [5 empty] | Non-TXV | 3.878%
Stockton | CA | 95206-2802 |  | 2012-08-10 | 2012-08-10 11:09 | 2012-08-10 11:35 | CARRIER - 38CKC030340 | 67 | 7.3 | Yes | Yes | 22.5 | 20.8 | 1.7 | 0941B69CC579499EA8EA14CCE7C83B8A |  | R22 | TXV |  | 10.9% | 0.89104 | 20.94% | [5 empty] | TXV | 10.9%
Los Banos | CA | 93635-4549 |  | 2012-05-16 | 2012-05-16 13:53 | 2012-05-16 14:18 | BRYANT - 563CN36-A | 120 | 4.4 | Yes | Yes | 24.4 | 20.5 | 3.9 | 4A5EAF2A42BB4B819DADE8DC0039ED6E |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Stockton | CA | 95205-4366 |  | 2012-08-09 | 2012-08-09 15:16 | 2012-08-09 15:42 | BRYANT - 561CJ042-F | 93 | 5.1 | Yes | Yes | 23.2 | 21 | 2.2 | 6152D885CD074980B97E5149358DF73F |  | R22 | TXV |  | 5.484% | 0.94516 | 10.54% | [5 empty] | TXV | 5.484%
Orland | CA | 95963-1502 |  | 2012-08-13 | 2012-08-13 13:37 | 2012-08-13 21:34 | TEMPSTAR - PGC042K080B | 87 | 3.6 | Yes | Yes | 21.4 | 21.7 | -0.3 | EC3DC315877A490CA946681A0FC45A1D |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Winton | CA | 95388-9206 |  | 2012-08-01 | 2012-08-01 12:59 | 2012-08-01 13:33 | TRANE - TTB724B1000A1 | 66 | -3.9 | Yes | Yes | 18 | 19.8 | -1.8 | CC8B8DE04AF94181B904AF06B771DCE1 |  | R22 | Non-TXV |  | -5.909% | 1.0591 | 1.655% |  |  |  |  | Non-TXV |  |  | -5.909%
Merced | CA | 95341-5625 |  | 2012-08-07 | 2012-08-07 10:25 | 2012-08-07 10:43 | OTHER - DCYZ-F030N0708 | 64 | 4.3 | Yes | Yes | 20.6 | 19.2 | 1.4 | 1ACD9AC01E8047FAA85D5D001ECB9214 |  | R410A | Non-TXV |  | 6.719% | 0.93281 | 12.91% | [5 empty] | Non-TXV | 6.719%
Colusa | CA | 95932-2348 |  | 2012-08-02 | 2012-08-02 12:16 | 2012-08-02 12:41 | AMANA - ASX140481CA | 147 | 12.3 | Yes | Yes | 18 | 20.4 | -2.4 | B43E4CDA298145E68ED769E6EDFE3B8B |  | R410A | TXV |  | 8.367% | 0.91633 | 16.08% | [5 empty] | TXV | 8.367%
Stockton | CA | 95205-4722 |  | 2012-08-09 | 2012-08-09 11:37 | 2012-08-09 11:54 | FRIGIDAIRE - UNK | 64 | 3.8 | Yes | Yes | 22.9 | 21 | 1.9 | 737AA8E592B74690BCCC761DEB5C4F78 |  | R22 | Non-TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | Non-TXV | 5.938%
Stockton | CA | 95205-7792 |  | 2012-05-16 | 2012-05-16 14:40 | 2012-05-16 14:57 | CARRIER - 38TH036300 | 84 | 6.9 | Yes | Yes | 19 | 21.5 | -2.5 | 9A0F05C47FB049028F71E9A1B0827D56 |  | R22 | Non-TXV |  | 8.214% | 0.91786 | 15.79% | [5 empty] | Non-TXV | 8.214%
Magalia | CA | 95954-9438 |  | 2012-05-30 | 2012-05-30 14:31 | 2012-05-30 20:38 | GENERAL ELECTRIC - BWC030B100BO | 104 | 3.3 | Yes | Yes | 22.3 | 17.5 | 4.8 | 2C709725CD594FB989A18E47C45928E2 |  | R22 | Non-TXV |  | 3.173% | 0.96827 | 6.098% | [5 empty] | Non-TXV | 3.173%
Newman | CA | 95360-1112 |  | 2012-08-07 | 2012-08-07 10:50 | 2012-08-07 11:15 | PAYNE - UNK | 91 | 6.2 | Yes | Yes | 18.4 | 20.4 | -2 | 694BE958AE2A4C1293A0E6DB6DFB0CD6 |  | R22 | Non-TXV |  | 6.813% | 0.93187 | 13.09% | [5 empty] | Non-TXV | 6.813%
Colusa | CA | 95932-3143 |  | 2012-08-02 | 2012-08-02 12:48 | 2012-08-02 13:19 | LENNOX - 12ACB30-5P | 101 | 11.4 | Yes | Yes | 25 | 20.9 | 4.1 | 3E7667FF6B494A48A9BCD0180252ED3B |  | R22 | Non-TXV |  | 11.29% | 0.88713 | 21.69% | [5 empty] | Non-TXV | 11.29%
Colusa | CA | 95932-2130 |  | 2012-08-09 | 2012-08-09 10:25 | 2012-08-09 10:25 | CARRIER - 48GS-036090311-- | 70 | 0 | Yes | Yes | 17.3 | 19.9 | -2.6 | 1B4CD1AB02E7474CAEACF69058F79295 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Colusa | CA | 95932-2510 |  | 2012-08-02 | 2012-08-02 11:16 | 2012-08-02 11:34 | AMANA - RCE30A2D | 164 | 12.7 | Yes | Yes | 17 | 18.7 | -1.7 | B958E07E992943EFB5990D32AA8DB1AB |  | R22 | Non-TXV |  | 7.744% | 0.92256 | 14.88% | [5 empty] | Non-TXV | 7.744%
Stockton | CA | 95205-8400 |  | 2012-08-07 | 2012-08-07 13:54 | 2012-08-07 14:28 | CARRIER - 38TH036300 | 84 | 2.6 | Yes | Yes | 23 | 19.5 | 3.5 | D928C57C76B242D9A05DC69654D70486 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Los Banos | CA | 93635-2627 |  | 2012-05-09 | 2012-05-09 11:15 | 2012-05-09 11:35 | GOODMAN - CK36-1B | 76 | 2.5 | Yes | Yes | 24.5 | 19.8 | 4.7 | EEA027109BD54C03B60BC781940C808E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Stockton | CA | 95205-7879 |  | 2012-08-07 | 2012-08-07 11:55 | 2012-08-07 12:21 | HEIL - UNK | 64 | 3.2 | Yes | Yes | 19.8 | 19.3 | 0.5 | D17220E603B04B2BABD393C5A5AA01D4 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Atwater | CA | 95301-3717 |  | 2012-08-07 | 2012-08-07 13:30 | 2012-08-07 13:55 | AMERICAN STANDARD - YCC042F1MOBD | 101 | -5.9 | Yes | Yes | 24.3 | 21.3 | 3 | C50B493CE4814837BC9E05EFBEB5662E |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Madera | CA | 93638-1524 |  | 2012-06-11 | 2012-06-11 15:52 | 2012-06-11 17:25 | RHEEM - UNK | 80 | 3 | Yes | Yes | 21.6 | 23.2 | -1.5 | 44FD21E2B23B407B8FD2202872E0BB59 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Atwater | CA | 95301-4507 |  | 2012-08-16 | 2012-08-16 11:23 | 2012-08-16 11:48 | PAYNE - 588ANW036080ACAF | 67 | -3.9 | Yes | Yes | 26 | 21.5 | 4.5 | 3A9221EBE8454825919D8A293B819B69 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Newman | CA | 95360-1115 |  | 2012-08-08 | 2012-08-08 11:50 | 2012-08-08 12:16 | RUUD - URMA-A024JK06E | 78 | 4.2 | Yes | Yes | 18.9 | 20.4 | -1.5 | A0D7819BD0454C049E9E24CC44072487 |  | R22 | Non-TXV |  | 5.385% | 0.94615 | 10.35% | [5 empty] | Non-TXV | 5.385%
Stockton | CA | 95204-5921 |  | 2012-08-07 | 2012-08-07 15:16 | 2012-08-07 15:44 | PAYNE - 565BB060 | 128 | 12.3 | Yes | Yes | 15.6 | 17.7 | -2.1 | 65229FE47A634C63BECDD5536C16CAA3 |  | R22 | Non-TXV |  | 9.609% | 0.90391 | 18.47% | [5 empty] | Non-TXV | 9.609%
Stockton | CA | 95206-6058 |  | 2012-05-30 | 2012-05-30 15:50 | 2012-05-30 16:10 | GOODMAN - CKJ48-1A | 118 | 10.3 | Yes | Yes | 18 | 19.3 | -1.3 | D1CD3C0E40DD492DB8F1FEAAEA7C81EE |  | R22 | Non-TXV |  | 8.729% | 0.91271 | 16.77% | [5 empty] | Non-TXV | 8.729%
Manteca | CA | 95337-6508 |  | 2012-08-02 | 2012-08-02 16:03 | 2012-08-02 16:21 | DAY & NIGHT - UNK | 56 | 1.9 | Yes | Yes | 18.2 | 20.8 | -2.6 | D9C81DBF93AA4045969816772257DAD4 |  | R22 | Non-TXV |  | 3.393% | 0.96607 | 6.52% | [5 empty] | Non-TXV | 3.393%
Paradise | CA | 95969-2701 |  | 2012-07-31 | 2012-07-31 11:05 | 2012-07-31 11:20 | OTHER - 55136-001 | 74 | 3.8 | Yes | Yes | 18.6 | 20.8 | -2.2 | 9AC5C59A8DB149FCBC67304C9DF4F0DB |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Tracy | CA | 95376-5402 |  | 2012-06-26 | 2012-06-26 13:49 | 2012-06-26 13:49 | BDP - 561CJ042-A | 80 | 0 | Yes | Yes | 19.2 | 20.2 | -0.9 | BDBAA7BF459546F28C32581DC7D82F3A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-9464 |  | 2012-05-08 | 2012-05-08 15:30 | 2012-05-08 15:53 | CARRIER - 591AN024-A | 51 | 5.3 | Yes | Yes | 21.7 | 21.1 | 0.6 | 0901474F2FE84737B49865BF3A57FA57 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.39% | 0.89608 | 19.97% | [5 empty] | Non-TXV | 10.39%
Manteca | CA | 95336-6312 |  | 2012-08-02 | 2012-08-02 09:21 | 2012-08-02 09:42 | RHEEM - RRNA-A036JK08X | 114 | 3.6 | Yes | Yes | 17.1 | 18.8 | -1.7 | 1596DDCB358F4197A847AB876231E99F |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
Tracy | CA | 95376-3250 |  | 2012-06-25 | 2012-06-25 13:19 | 2012-06-25 14:10 | RHEEM - RAKA-042JAZ | 79 | 3.1 | Yes | Yes | 18.6 | 19.5 | -0.9 | FCA10DEF7BE74ACABD12E0DD24E52106 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Check for plugged/iced evaporator coil, dirty evaporator fan, or collapsed duct. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.924% | 0.96076 | 7.541% | [5 empty] | Non-TXV | 3.924%
Stockton | CA | 95205-7807 |  | 2012-05-17 | 2012-05-17 12:03 | 2012-05-17 12:26 | BRANT - 561CJ042-F | 93 | 3.4 | Yes | Yes | 18.3 | 20.9 | -2.6 | C9BE30031C954C9AA2BD89781E121EF3 | OK: Verified Refrigerant Charge | R22 | TXV |  | 3.656% | 0.96344 | 7.026% | [5 empty] | TXV | 3.656%
Magalia | CA | 95954-9320 |  | 2012-05-31 | 2012-05-31 11:57 | 2012-05-31 12:51 | COLEMAN - 6275E901 | 90 | 6.9 | Yes | Yes | 18.4 | 21 | -2.6 | E7F6D776F1FF473BBDA2FA7BC36D4A05 |  | R22 | Non-TXV |  | 7.667% | 0.92333 | 14.73% | [5 empty] | Non-TXV | 7.667%
Colusa | CA | 95932-3223 |  | 2012-05-24 | 2012-05-24 11:40 | 2012-05-24 11:57 | OTHER - PGE121348D100 | 168 | 5.3 | Yes | Yes | 23 | 17.6 | 5.4 | 5E0753EF31024041B9B39EEC562F1A96 |  | R22 | Non-TXV |  | 3.155% | 0.96845 | 6.063% | [5 empty] | Non-TXV | 3.155%
Oakdale | CA | 95361-4144 |  | 2012-08-16 | 2012-08-16 12:00 | 2012-08-16 12:24 | HEIL - CA5036VKB1 | 86 | 20.1 | Yes | Yes | 24.5 | 22.3 | 2.2 | BD5899E3778A4A8EB0341A44C930581D |  | R22 | Non-TXV |  | 23.37% | 0.76628 | 44.92% | [5 empty] | Non-TXV | 23.37%
Paradise | CA | 95969-2615 |  | 2012-07-31 | 2012-07-31 09:45 | 2012-07-31 10:12 | TRANE - 2TTR3036A1000AA | 101 | 4.5 | Yes | Yes | 23.5 | 19.2 | 4.3 | 2ACFD72BA40A4D6FA70612279649CD70 |  | R22 | Non-TXV |  | 4.455% | 0.95545 | 8.562% | [5 empty] | Non-TXV | 4.455%
Manteca | CA | 95336-5016 |  | 2012-08-02 | 2012-08-02 12:42 | 2012-08-02 12:42 | INTERTHERM - CN36I 80MAY8-T-0 | 49 | 0 | Yes | Yes | 19.9 | 20.4 | -0.5 | 9DD8EFFC47E74ADC92099F6CCB8AFCAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2134 |  | 2012-05-08 | 2012-05-08 15:14 | 2012-05-08 15:40 | SEARS - 4157-11-22A | 54 | 5.3 | Yes | Yes | 19.7 | 22.6 | -2.9 | AA82140A8D864419B2DA99D17ACAEE44 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.815% | 0.90185 | 18.86% | [5 empty] | Non-TXV | 9.815%
Atwater | CA | 95301-3722 |  | 2012-05-10 | 2012-05-10 10:14 | 2012-05-10 10:34 | COLEMAN - BRCS0361CB | 71 | 2.1 | Yes | Yes | 20.6 | 20.2 | 0.4 | 4D724894F0E343C6A086DE08CCAB5340 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Fresno | CA | 93726-6036 |  | 2012-05-08 | 2012-05-08 14:53 | 2012-05-08 14:53 | GOODMAN - GSX130421BA | 121 | 0 | Yes | Yes | 27 | 22 | 5 | ABB0F0E161264F1AA9DC1C6D2109DE06 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-2415 |  | 2012-06-25 | 2012-06-25 12:27 | 2012-06-25 12:47 | OTHER - 80WR36E1NA | 105 | 12.9 | Yes | Yes | 24.3 | 22.2 | 2.1 | 7F49E9D9117A4ED7B3617BE16DEB4619 |  | R22 | Non-TXV |  | 12.29% | 0.87714 | 23.61% | [5 empty] | Non-TXV | 12.29%
Fresno | CA | 93711-2686 |  | 2012-06-08 | 2012-06-08 10:10 | 2012-06-08 10:28 | GOODMAN - GSC130301DA | 87 | 2.6 | Yes | Yes | 25 | 20.4 | 4.6 | 11AF1A9A95A74A5693733185E1188081 |  | R22 | Non-TXV |  | 2.989% | 0.97011 | 5.743% | [5 empty] | Non-TXV | 2.989%
Willows | CA | 95988-2914 |  | 2012-08-15 | 2012-08-15 09:28 | 2012-08-15 10:02 | PAYNE - 5B0AN036 | 90 | 8.1 | Yes | Yes | 20.9 | 21 | -0.1 | 5E81F4CD270A41F4A3B23A87500071AF |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Chico | CA | 95928-5797 |  | 2012-05-22 | 2012-05-22 14:38 | 2012-05-22 16:31 | TRANE - YCCO24F1L0BH | 70 | 2.4 | Yes | Yes | 23.9 | 22.4 | 1.6 | CA9AF889D8C74D96AD0E719C49C9E897 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Willows | CA | 95988-2303 |  | 2012-08-15 | 2012-08-15 10:04 | 2012-08-15 10:24 | GOODMAN - CKJ36-1AB | 97 | 14.2 | Yes | Yes | 25.1 | 20.9 | 4.2 | B60CC282A8CC45EFBF2E796FF015252D |  | R22 | Non-TXV |  | 14.64% | 0.85361 | 28.13% | [5 empty] | Non-TXV | 14.64%
Willows | CA | 95988-3326 |  | 2012-08-15 | 2012-08-15 11:04 | 2012-08-15 11:33 | BDP - 585HJW036100ABAF | 84 | 2.7 | Yes | Yes | 20.4 | 20.8 | -0.4 | 871D1CFF8EAD4386A27B1023D1DDA056 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Willows | CA | 95988-3421 |  | 2012-08-15 | 2012-08-15 13:35 | 2012-08-15 17:38 | BRYANT - NA | 65 | 6.2 | Yes | Yes | 23.3 | 21.9 | 1.4 | B1E35C2DB8E44CAA907D49FC8075127C |  | R22 | Non-TXV |  | 9.538% | 0.90462 | 18.33% | [5 empty] | Non-TXV | 9.538%
Chico | CA | 95926-7338 |  | 2012-05-16 | 2012-05-16 15:53 | 2012-05-16 17:42 | GOODMAN - GPG13300701AB | 75 | 2.7 | Yes | Yes | 24.3 | 20.8 | 3.5 | 3E1C3101E48F4510B56D95FA6D7D69CD |  | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Orosi | CA | 93647-2124 |  | 2012-07-31 | 2012-07-31 10:34 | 2012-07-31 11:02 | CARRIER - 38BRC03640 | 101 | 4.9 | Yes | Yes | 17.7 | 20.4 | -2.7 | 0F2E977717CD49FAAF2167013AEC1112 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.851% | 0.95149 | 9.323% | [5 empty] | Non-TXV | 4.851%
Willows | CA | 95988-2034 |  | 2012-08-14 | 2012-08-14 11:49 | 2012-08-14 12:22 | RHEEM - RAHE-036JAS | 91 | 6.4 | Yes | Yes | 24.3 | 20.6 | 3.7 | 5771DCE885124DFBBBD88F8A81CDD363 |  | R22 | Non-TXV |  | 7.033% | 0.92967 | 13.52% | [5 empty] | Non-TXV | 7.033%
Orosi | CA | 93647-2124 |  | 2012-07-31 | 2012-07-31 09:57 | 2012-07-31 10:31 | ICP - PGAD36D1K7 | 100 | 3.2 | Yes | Yes | 16.9 | 16.8 | 0.1 | 73453AD44C714A77974A5E00AEDB7D98 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Atwater | CA | 95301-2323 |  | 2012-08-15 | 2012-08-15 12:04 | 2012-08-15 12:22 | OTHER - CA5548VKD2 | 134 | 12.9 | Yes | Yes | 29.1 | 23.5 | 5.6 | BF3AD533E459476AB36621CBC52C7095 |  | R22 | Non-TXV |  | 9.627% | 0.90373 | 18.5% | [5 empty] | Non-TXV | 9.627%
Stockton | CA | 95205-3035 |  | 2012-08-14 | 2012-08-14 12:15 | 2012-08-14 12:37 | TRANE - 2TTB0030A1000AA | 64 | 4.6 | Yes | Yes | 23.1 | 20.2 | 2.9 | F6AD920458B24240A9BD821506582554 |  | R22 | Non-TXV |  | 7.187% | 0.92812 | 13.81% | [5 empty] | Non-TXV | 7.187%
Willows | CA | 95988-2030 |  | 2012-08-14 | 2012-08-14 13:05 | 2012-08-14 14:09 | BDP - 585B036075YACR | 60 | 9.1 | Yes | Yes | 19.6 | 22.5 | -2.9 | FDCB95B34E1D418FA2D8EFB8484A5EF6 |  | R22 | Non-TXV |  | 15.17% | 0.84833 | 29.15% | [5 empty] | Non-TXV | 15.17%
Clovis | CA | 93612-3870 |  | 2012-05-15 | 2012-05-15 13:49 | 2012-05-15 14:08 | GOODMAN - PGB024050 | 85 | 2.5 | Yes | Yes | 19.3 | 20.4 | -1.1 | 8497E1A2ABAF404EB15A6516E2958FCC |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Willows | CA | 95988-3342 |  | 2012-08-15 | 2012-08-15 09:01 | 2012-08-15 09:25 | GOODMAN - CKL30-1L | 74 | 4 | Yes | Yes | 22.7 | 21.7 | 1 | 252197C4E4634E7389AC7EAED5DF4B7F |  | R22 | Non-TXV |  | 5.405% | 0.94595 | 10.39% | [5 empty] | Non-TXV | 5.405%
Chico | CA | 95926-3522 |  | 2012-05-23 | 2012-05-23 12:19 | 2012-05-23 12:35 | BRYANT - 552AN024-E | 83 | 3.6 | Yes | Yes | 20.4 | 21.3 | -0.9 | 852B76EEB2EB4CC484BAE2A45FB014E6 |  | R410A | TXV |  | 4.337% | 0.95663 | 8.335% | [5 empty] | TXV | 4.337%
Madera | CA | 93637-5004 |  | 2012-08-13 | 2012-08-13 10:44 | 2012-08-13 11:01 | PAYNE - 3680YAC107 | 84 | 10.5 | Yes | Yes | 23.6 | 21 | 2.7 | B7D7030A12414938A7C5CDAA29D38F36 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Willows | CA | 95988-3344 |  | 2012-08-15 | 2012-08-15 11:43 | 2012-08-15 12:19 | GOODMAN - GSC1302410 | 102 | 4.9 | Yes | Yes | 22.5 | 19.7 | 2.8 | 28899E9CEA1E4968A447B42D81B2094E |  | R22 | Non-TXV |  | 4.804% | 0.95196 | 9.232% | [5 empty] | Non-TXV | 4.804%
Newman | CA | 95360-1479 |  | 2012-08-08 | 2012-08-08 11:03 | 2012-08-08 11:28 | PAYNE - UNK | 70 | 3.3 | Yes | Yes | 22.8 | 20.4 | 2.4 | D8A6FE7F8BC0490D879360AE121D64E8 |  | R22 | Non-TXV |  | 4.714% | 0.95286 | 9.06% | [5 empty] | Non-TXV | 4.714%
Fresno | CA | 93710-4002 |  | 2012-05-10 | 2012-05-10 14:48 | 2012-05-10 15:09 | YORK - D1NAAC48N09006C | 92 | 2.8 | Yes | Yes | 25.3 | 20.5 | 4.8 | C25DFB21D6DB4C8CBBA4C23D6889313E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Merced | CA | 95348-9376 |  | 2012-08-06 | 2012-08-06 10:15 | 2012-08-06 10:46 | YORK - D1NA0300N5606C | 71 | 2.8 | Yes | Yes | 18.8 | 20.4 | -1.6 | 0C938BA0526B4CC3B0CCACB69A1F8473 |  | R22 | Non-TXV |  | 3.944% | 0.96056 | 7.579% | [5 empty] | Non-TXV | 3.944%
Magalia | CA | 95954-9118 |  | 2012-08-08 | 2012-08-08 11:18 | 2012-08-08 11:40 | BDP - 542EEJ024 | 100 | 3 | Yes | Yes | 18.9 | 20.3 | -1.4 | C4340ED3B47E4C9FA241902BDF05A58B |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95973-1008 |  | 2012-05-09 | 2012-05-09 16:15 | 2012-05-09 18:25 | LENNOX - HS16-411V-2P | 105 | 5.2 | Yes | Yes | 20.4 | 22.6 | -2.2 | 589D0E827DD64290853444E0A6A546F4 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.952% | 0.95048 | 9.517% | [5 empty] | Non-TXV | 4.952%
Clovis | CA | 93612-1305 |  | 2012-05-15 | 2012-05-15 11:16 | 2012-05-15 11:30 | RUUD - 4RGF-07E4JKR | 135 | -9.5 | Yes | Yes | 17.8 | 20.4 | -2.6 | 7DFC4304BEB74F91B90986DEF839919A |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Los Banos | CA | 93635-3084 |  | 2012-08-02 | 2012-08-02 13:42 | 2012-08-02 15:44 | GIBSON - JS3BC-036KA | 82 | 4.7 | Yes | Yes | 20.6 | 20.4 | 0.2 | 79DEF4B1C0DA4CC4ADA3DF4DA2DB17DA |  | R22 | Non-TXV |  | 5.732% | 0.94268 | 11.02% | [5 empty] | Non-TXV | 5.732%
Los Banos | CA | 93635-6358 |  | 2012-08-14 | 2012-08-14 11:13 | 2012-08-14 11:34 | AIRE-FLO - 561CJ036 | 70 | 8.9 | Yes | Yes | 27 | 21 | 6 | 2B943A3B041C44B9938F82DCD4031F35 |  | R22 | Non-TXV |  | 12.71% | 0.87286 | 24.43% | [5 empty] | Non-TXV | 12.71%
Los Banos | CA | 93635-3084 |  | 2012-05-16 | 2012-05-16 13:08 | 2012-05-16 13:33 | UNK - NAC030AKC3 | 75 | 2.3 | Yes | Yes | 16.7 | 19.3 | -2.6 | CBC2D51D2E0A446B986DB44DAEF71F14 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Stockton | CA | 95206-6337 |  | 2012-05-15 | 2012-05-15 10:02 | 2012-05-15 10:26 | GOODMAN - CKJ30-1A | 92 | -4.4 | Yes | Yes | 17.6 | 20.3 | -2.7 | FEC09F96B78E44888DEA2330D366384E | OK: Verified Refrigerant Charge | R22 | TXV |  | -4.783% | 1.0478 | 1.339% |  |  |  |  | TXV |  |  | -4.783%
Stockton | CA | 95210-3705 |  | 2012-05-31 | 2012-05-31 09:07 | 2012-05-31 09:24 | YORK - TCGD42S41S3HA | 69 | -4.1 | Yes | Yes | 19.2 | 20.2 | -0.9 | 57B03F53E57B48D59F19568CC02A53D0 |  | R410A | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Stockton | CA | 95205-3134 |  | 2012-05-14 | 2012-05-14 16:24 | 2012-05-14 16:42 | ARCOAIRE - HAC036AKA1 | 80 | 4 | Yes | Yes | 18.4 | 20.4 | -2 | 395768E5053A447FB3F8E5A29F747140 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Oroville | CA | 95966-5501 |  | 2012-05-31 | 2012-05-31 19:31 | 2012-05-31 19:31 | LENNOX - 10GCS030-75-6PA | 56 | 0 | Yes | Yes | 22.2 | 21.8 | 0.4 | 17985C37CB324B88B25E236006AE6DA9 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3617 |  | 2012-08-01 | 2012-08-01 15:50 | 2012-08-01 16:06 | BRYANT - 588ANW036080ACAF | 67 | 6.4 | Yes | Yes | 20.7 | 21.5 | -0.8 | BBF279A950C94CD59885C9DFDB12757F |  | R22 | Non-TXV |  | 9.552% | 0.90448 | 18.36% | [5 empty] | Non-TXV | 9.552%
Atwater | CA | 95301-3950 |  | 2012-05-21 | 2012-05-21 12:37 | 2012-05-21 12:58 | UNITARY - GCGD36S41S3A | 73 | 2.2 | Yes | Yes | 17.8 | 19.7 | -1.9 | 91F00D2D28F3466EAC73D50771697ACC |  | R410A | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Manteca | CA | 95337-6525 |  | 2012-07-02 | 2012-07-02 14:10 | 2012-07-02 15:15 | GOODMAN - VSK130241AA | 76 | 6.3 | Yes | Yes | 19.8 | 20.4 | -0.6 | 93ED55DCF424424091F7ED9858882546 |  | R410A | Non-TXV |  | 8.289% | 0.91711 | 15.93% | [5 empty] | Non-TXV | 8.289%
Corning | CA | 96021-0000 |  | 2012-07-31 | 2012-07-31 08:36 | 2012-07-31 08:58 | COLEMAN - ERCQ0481BBA | 125 | 4.7 | Yes | Yes | 21.4 | 20.4 | 1 | E235A4861BBC462D8CE04877A1413E87 |  | R22 | Non-TXV |  | 3.76% | 0.9624 | 7.226% | [5 empty] | Non-TXV | 3.76%
Merced | CA | 95340-0958 |  | 2012-05-14 | 2012-05-14 11:16 | 2012-05-14 11:45 | GOODMAN - PGJ0300501 | 72 | 3.8 | Yes | Yes | 23 | 19.5 | 3.5 | 875148367A7548BDB651D6E0CB45A858 |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Stockton | CA | 95206-4302 |  | 2012-08-10 | 2012-08-10 09:08 | 2012-08-10 09:28 | BRYANT - 561CJ048-A | 102 | 8.8 | Yes | Yes | 17.7 | 20.4 | -2.7 | 80099D537DCE478C988AB06A9176F8A8 |  | R22 | TXV |  | 8.627% | 0.91373 | 16.58% | [5 empty] | TXV | 8.627%
Manteca | CA | 95336-4021 |  | 2012-08-01 | 2012-08-01 11:06 | 2012-08-01 11:56 | GE - BGTA942H1B | 92 | 11.4 | Yes | Yes | 18.5 | 20.4 | -1.9 | EC41684F4C1D419F8B09AC5B46F17CC8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.39% | 0.87609 | 23.81% | [5 empty] | Non-TXV | 12.39%
Atwater | CA | 95301-2004 |  | 2012-05-08 | 2012-05-08 13:20 | 2012-05-08 13:40 | COLEMAN - DAYP-F030N070A | 73 | 2.2 | Yes | Yes | 18.8 | 20.2 | -1.4 | 2C7C3DF1ACA4488E9BFACF37D2B0739C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Merced | CA | 95341-5254 |  | 2012-06-06 | 2012-06-06 16:48 | 2012-06-06 17:07 | AMERICAN STANDARD - YCC042F1M0BH | 101 | -5.9 | Yes | Yes | 26.6 | 21 | 5.6 | 6F5D3AFD75E74D6EB4BA5252CB89F0C6 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Merced | CA | 95348-8709 |  | 2012-08-06 | 2012-08-06 14:11 | 2012-08-06 14:28 | GIBSON - JS3BA-042KA | 88 | 6.8 | Yes | Yes | 21.9 | 20.2 | 1.7 | C39D3294B29142C69D6DC60B776F0443 |  | R22 | Non-TXV |  | 7.727% | 0.92273 | 14.85% | [5 empty] | Non-TXV | 7.727%
Manteca | CA | 95337-8203 |  | 2012-08-01 | 2012-08-01 13:21 | 2012-08-01 13:49 | GOODMAN - CK49-1B | 97 | 12.3 | Yes | Yes | 19.2 | 20.8 | -1.6 | 8CF001DB02094E8D95980D32245E9A40 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.68% | 0.8732 | 24.37% | [5 empty] | Non-TXV | 12.68%
Merced | CA | 95348-1122 |  | 2012-08-09 | 2012-08-09 11:25 | 2012-08-09 11:47 | OTHER - UNK | 82 | 2.9 | Yes | Yes | 20.1 | 19 | 1.1 | B915E0CC4EB94CC3995FDA0317F6E699 |  | R22 | Non-TXV |  | 3.537% | 0.96463 | 6.797% | [5 empty] | Non-TXV | 3.537%
Madera | CA | 93638-0448 |  | 2012-07-31 | 2012-07-31 11:16 | 2012-07-31 11:42 | CARRIER - 48SS-030040321 | 53 | 1.6 | Yes | Yes | 21 | 20.2 | 0.8 | DEC98B22EBF24627B20BA163CEDBE645 |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Durham | CA | 95938-9422 |  | 2012-08-09 | 2012-08-09 09:26 | 2012-08-09 09:49 | TRANE - YCC0181L0BE | 56 | 3.5 | Yes | Yes | 22 | 21 | 1.1 | 6FAE4A1C47624DA0ADC6801FC06D4D23 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Chico | CA | 95926-1200 |  | 2012-05-15 | 2012-05-15 12:18 | 2012-05-15 12:43 | LENNOX - M/N HS26-036-4P | 89 | 6.3 | Yes | Yes | 25.2 | 22.8 | 2.4 | 116C6C017DA541F69DFF033A919AECF1 |  | R22 | Non-TXV |  | 7.079% | 0.92921 | 13.6% | [5 empty] | Non-TXV | 7.079%
Stockton | CA | 95219-3609 |  | 2012-08-15 | 2012-08-15 12:28 | 2012-08-15 12:45 | BRYANT - 561CJ048-A | 103 | 9.8 | Yes | Yes | 17.6 | 18.5 | -0.9 | B34BA8944B6D4A799C524CB3F43CEF02 |  | R22 | Non-TXV |  | 9.515% | 0.90485 | 18.28% | [5 empty] | Non-TXV | 9.515%
Merced | CA | 95340-2316 |  | 2012-08-08 | 2012-08-08 10:25 | 2012-08-08 10:45 | ALLEGIANCE - 7A2036A100A2 | 110 | 13.5 | Yes | Yes | 26.5 | 21.5 | 5 | 1776422988B44EECA7441BF27FB4CD8C |  | R22 | Non-TXV |  | 12.27% | 0.87727 | 23.59% | [5 empty] | Non-TXV | 12.27%
Placerville | CA | 95667-8906 |  | 2012-06-13 | 2012-06-13 15:37 | 2012-06-13 15:37 | YORK - D1NA036N05606C | 67 | 0 | Yes | Yes | 23.8 | 20.4 | 3.4 | 3AE8DAD8D7CD46F6BE4ACC299EBA60F8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9328 |  | 2012-08-02 | 2012-08-02 11:05 | 2012-08-02 11:29 | GOODMAN - PGB036075-1A | 60 | -3.5 | Yes | Yes | 23.1 | 20.1 | 3.1 | F431F825FC6A42CDA465C66C4F7B7BDD |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Livingston | CA | 95334-9429 |  | 2012-07-31 | 2012-07-31 11:17 | 2012-07-31 11:49 | RHEEM - URGG-05E24JKR | 49 | 1.5 | Yes | Yes | 18.9 | 19.5 | -0.6 | 6DFAC135D20C45CCA78DD922CC445358 |  | R22 | Non-TXV |  | 3.061% | 0.96939 | 5.883% | [5 empty] | Non-TXV | 3.061%
Dinuba | CA | 93618-9121 |  | 2012-05-23 | 2012-05-23 15:24 | 2012-05-23 15:46 | BDP - 885EB06012 | 121 | 3.6 | Yes | Yes | 27.4 | 21.5 | 5.9 | FAA7BBE906174E478139AB89F7EE472B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.975% | 0.97025 | 5.718% | [5 empty] | Non-TXV | 2.975%
Los Banos | CA | 93635-3951 |  | 2012-05-14 | 2012-05-14 13:27 | 2012-05-14 13:27 | TRANE - 4YCC3036A1075AA | 124 | 0 | Yes | Yes | 19.9 | 20.7 | -0.8 | 47818CB859E34FE6AE0E951587050206 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9742 |  | 2012-08-09 | 2012-08-09 12:38 | 2012-08-09 13:52 | COLEMAN - DRCS042 | 112 | 7.2 | Yes | Yes | 21.9 | 23 | -1.1 | A9A2BCA08B374E6DB5624FD579368CED |  | R22 | Non-TXV |  | 6.429% | 0.93571 | 12.35% | [5 empty] | Non-TXV | 6.429%
Madera | CA | 93637-4232 |  | 2012-08-01 | 2012-08-01 14:31 | 2012-08-01 14:49 | CARRIER - 48KL142300BE | 78 | 8.3 | Yes | Yes | 25.8 | 19.9 | 5.9 | E305DA43CA7A44CD8DCFAB3A61CCBE70 |  | R22 | Non-TXV |  | 10.64% | 0.89359 | 20.45% | [5 empty] | Non-TXV | 10.64%
Madera | CA | 93637-4232 |  | 2012-08-01 | 2012-08-01 14:53 | 2012-08-01 15:22 | CARRIER - 48KL118300BE | 51 | 10.5 | Yes | Yes | 21.7 | 20.7 | 1 | 95477C7AD22D4F6FBF0CD369AA526CB3 |  | R22 | Non-TXV |  | 20.59% | 0.79412 | 39.57% | [5 empty] | Non-TXV | 20.59%
Stockton | CA | 95210-1318 |  | 2012-06-06 | 2012-06-06 10:15 | 2012-06-06 10:43 | GOODMAN - GSC130361FA | 83 | -4.9 | Yes | Yes | 22.2 | 19.5 | 2.7 | DFC6B6D2FFD64D51AB04FA0156E4485F |  | R22 | Non-TXV |  | -5.904% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.904%
Corning | CA | 96021-0000 |  | 2012-05-17 | 2012-05-17 15:49 | 2012-05-17 15:49 | AMANDA - RCC42C2C | 107 | 0 | Yes | Yes | 21.7 | 23.7 | -2 | 59806A4F6CA441D4A14E03ED4C49829D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3840 |  | 2012-08-01 | 2012-08-01 16:36 | 2012-08-01 16:58 | OTHER - NRGE36SAK01 | 94 | 5.8 | Yes | Yes | 25.1 | 21.3 | 3.8 | 6759818B566B4070AB9530DE82D50F1C |  | R22 | Non-TXV |  | 6.17% | 0.9383 | 11.86% | [5 empty] | Non-TXV | 6.17%
Cameron Park | CA | 95682-9220 |  | 2012-05-31 | 2012-05-31 12:33 | 2012-05-31 12:33 | BDP - 524EJ024 | 100 | 0 | Yes | Yes | 27 | 22 | 5 | 4C5EEFCF2A51436C9121927D3FEDD313 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-1019 |  | 2012-08-07 | 2012-08-07 16:36 | 2012-08-07 16:36 | PAYNE - PA10JA042-H | 82 | 0 | Yes | Yes | 25.4 | 21.4 | 4 | 93AF1B0A5B674B859E0F3F09C204FDF6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-9786 |  | 2012-07-31 | 2012-07-31 13:06 | 2012-07-31 13:38 | RHEEM - RRNA-B036JK06X | 89 | 5.7 | Yes | Yes | 17.6 | 20.1 | -2.5 | 5D3956448EF744629CD4D1DD2F0CF9FA |  | R22 | Non-TXV |  | 6.404% | 0.93596 | 12.31% | [5 empty] | Non-TXV | 6.404%
Los Banos | CA | 93635-9204 |  | 2012-08-14 | 2012-08-14 11:50 | 2012-08-14 12:12 | AIRE-FLO - JS3BC030KA | 68 | 8.5 | Yes | Yes | 19.5 | 19.5 | 0 | A944D10896EB483D92537D741B0BE0D0 |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Stockton | CA | 95206-2833 |  | 2012-05-09 | 2012-05-09 13:36 | 2012-05-09 13:53 | RHEEM - RRNL-B024JK06X | 78 | 8 | Yes | Yes | 29.5 | 24 | 5.6 | A6751E17DE4243F490826DAF92681316 | OK: Verified Refrigerant Charge | R410A | TXV |  | 10.26% | 0.89744 | 19.71% | [5 empty] | TXV | 10.26%
Livingston | CA | 95334-9786 |  | 2012-08-01 | 2012-08-01 10:27 | 2012-08-01 10:32 | TRANE - TTB724B100A1 | 66 | 2.6 | Yes | Yes | 18.6 | 20.4 | -1.8 | DEB3C8A33D48474195E7FF10B60FFBCB |  | R22 | Non-TXV |  | 3.939% | 0.96061 | 7.571% | [5 empty] | Non-TXV | 3.939%
Merced | CA | 95340-3325 |  | 2012-05-07 | 2012-05-07 18:14 | 2012-05-07 18:14 | HEIL - PGC036K060B | 71 | 0 | Yes | Yes | 21.2 | 20.6 | 0.6 | 82B57AA34803410EB09B337FE5D7CF8D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2838 |  | 2012-05-09 | 2012-05-09 12:05 | 2012-05-09 12:23 | GOODMAN - GPG1300701AC | 77 | 8 | Yes | Yes | 24.2 | 20.4 | 3.8 | A7839210B3F146C9A763545D54F78382 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.39% | 0.8961 | 19.97% | [5 empty] | Non-TXV | 10.39%
Madera | CA | 93637-9296 |  | 2012-08-01 | 2012-08-01 13:59 | 2012-08-01 14:17 | CARRIER - 4BNLT060300 | 134 | 4 | Yes | Yes | 26.6 | 21.9 | 4.7 | 8BC9F0DD93B842C89EF1729732B15A7D |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Newman | CA | 95360-9812 |  | 2012-08-14 | 2012-08-14 15:03 | 2012-08-14 15:32 | GIBSON - JS38C-036KA | 82 | -4.8 | Yes | Yes | 16.7 | 19.3 | -2.6 | 417A76F9AF0347159B18EF01A87D5658 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Los Banos | CA | 93635-9205 |  | 2012-08-16 | 2012-08-16 10:24 | 2012-08-16 10:46 | OTHER - JS3BC048KA | 110 | 9.6 | Yes | Yes | 18.7 | 17.5 | 1.2 | AB1BC0B5C53F411B88D827F9532B3BCD |  | R22 | Non-TXV |  | 8.727% | 0.91273 | 16.77% | [5 empty] | Non-TXV | 8.727%
Stockton | CA | 95203-1405 |  | 2012-07-31 | 2012-07-31 11:59 | 2012-07-31 12:23 | DAY & NIGHT - 100YAC107AC | 67 | 2.5 | Yes | Yes | 23 | 20.1 | 2.9 | 5366297E608A4C1AA906A903C11265B7 |  | R22 | Non-TXV |  | 3.731% | 0.96269 | 7.171% | [5 empty] | Non-TXV | 3.731%
Madera | CA | 93637-5931 |  | 2012-05-07 | 2012-05-07 14:15 | 2012-05-07 14:15 | CARRIER - 38BRC060350 | 200 | 0 | Yes | Yes | 25.2 | 19.4 | 5.9 | 7331473FD6B44E9BAEE07C958F4CF18D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-2935 |  | 2012-08-03 | 2012-08-03 09:29 | 2012-08-03 10:01 | YORK - H1RA048SO6D | 117 | 6.4 | Yes | Yes | 20 | 21.2 | -1.2 | 179E8684E5834029922CB661F146F0E3 |  | R22 | Non-TXV |  | 5.47% | 0.9453 | 10.51% | [5 empty] | Non-TXV | 5.47%
Pollock Pines | CA | 95726-8801 |  | 2012-08-16 | 2012-08-16 12:06 | 2012-08-16 12:33 | BARD - PH36-1 | 69 | 6 | Yes | Yes | 20.5 | 20.3 | 0.2 | 77A06A03D050442AAD4C8631A63FF6C8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.696% | 0.91304 | 16.71% | [5 empty] | Non-TXV | 8.696%
Stockton | CA | 95206-2942 |  | 2012-05-18 | 2012-05-18 15:13 | 2012-05-18 15:13 | RHEEM - RRNL-B030JK06X | 77 | 0 | Yes | Yes | 21.6 | 20.7 | 0.9 | 6ED3E21B656045C1B32687FF2E661017 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2829 |  | 2012-06-15 | 2012-06-15 08:54 | 2012-06-15 09:11 | CARRIER - 38CK042300 | 88 | 2.6 | Yes | Yes | 19.9 | 19.3 | 0.6 | 3BA96AFA708D4850A1FF46C085610BED |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Red Bluff | CA | 96080-8822 |  | 2012-05-16 | 2012-05-16 12:22 | 2012-05-16 13:31 | PAYNE - PY3GNAA48090NA | 100 | 4.2 | Yes | Yes | 19.5 | 20.4 | -0.9 | F645D3CF400D46F490AB5B095EE56203 |  | R410A | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Los Banos | CA | 93635-2600 |  | 2012-08-01 | 2012-08-01 10:56 | 2012-08-01 11:13 | GOODMAN - CK30-1T | 76 | 2.3 | Yes | Yes | 26.5 | 22.3 | 4.2 | 1F033DD3B8E042C1BC36F8CB771F52B6 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Merced | CA | 95341-5259 |  | 2012-08-06 | 2012-08-06 11:55 | 2012-08-06 12:18 | LUXAIRE - 36ECW080GB | 129 | 12.1 | Yes | Yes | 27.8 | 24.8 | 3 | A207B1D65E90435AB8E00FD2D2B881A1 |  | R22 | Non-TXV |  | 9.38% | 0.9062 | 18.03% | [5 empty] | Non-TXV | 9.38%
Orosi | CA | 93647-2132 |  | 2012-07-31 | 2012-07-31 09:25 | 2012-07-31 09:53 | NORDYNE - R4GD-042K072C | 192 | 5.8 | Yes | Yes | 20.4 | 19.3 | 1.1 | 9FCFF94FAF424D67B67FC3AEABB78899 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Los Banos | CA | 93635-9205 |  | 2012-08-14 | 2012-08-14 13:34 | 2012-08-14 13:55 | OTHER - JS3BC036KA | 82 | 9.9 | Yes | Yes | 25.4 | 19.5 | 5.9 | 4D3A2832D7A7452EB3128BC2D78655B1 |  | R22 | Non-TXV |  | 12.07% | 0.87927 | 23.2% | [5 empty] | Non-TXV | 12.07%
Grass Valley | CA | 95945-7447 |  | 2012-05-30 | 2012-05-30 14:43 | 2012-05-30 15:05 | TRANE - TTN042C100A2 | 133 | -12.5 | Yes | Yes | 24 | 18.2 | 5.8 | 6EA206B3522E4A9794156B6B47E3BFB2 |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Los Banos | CA | 93635-7409 |  | 2012-08-14 | 2012-08-14 10:05 | 2012-08-14 10:26 | AIRE-FLO - JS5BD030K | 134 | 12.8 | Yes | Yes | 24.5 | 20.7 | 3.8 | E7DA478F333A4E128DDAC3B7FE41FD72 |  | R22 | Non-TXV |  | 9.552% | 0.90448 | 18.36% | [5 empty] | Non-TXV | 9.552%
Tracy | CA | 95376-1940 |  | 2012-06-20 | 2012-06-20 09:52 | 2012-06-20 10:14 | AMANA - P1248003C | 225 | 8.2 | Yes | Yes | 19 | 21 | -2 | 6A635D2F7ED84C5DA64D8FBF97E364B7 |  | R22 | TXV |  | 3.644% | 0.96356 | 7.004% | [5 empty] | TXV | 3.644%
Madera | CA | 93637-4253 |  | 2012-07-31 | 2012-07-31 13:45 | 2012-07-31 14:04 | DAY & NIGHT - 585A03680YAC | 77 | 3.2 | Yes | Yes | 18.7 | 20.2 | -1.5 | E499D4228F0442C0AEBC7EC8F89878EC |  | R22 | Non-TXV |  | 4.156% | 0.95844 | 7.987% | [5 empty] | Non-TXV | 4.156%
Madera | CA | 93637-4253 |  | 2012-07-31 | 2012-07-31 18:44 | 2012-07-31 18:44 | DAY & NIGHT - 585A03680YAC | 77 | 0 | Yes | Yes | 17.7 | 19.8 | -2.1 | CD559044CE7341CEBAB3241697FE1C31 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-4105 |  | 2012-08-08 | 2012-08-08 09:13 | 2012-08-08 09:37 | OTHER - 2TTB3030A1000AA | 88 | 11.5 | Yes | Yes | 24.2 | 20.4 | 3.8 | 94EA4B0107194831A9EC31C7E7B054F9 |  | R22 | Non-TXV |  | 13.07% | 0.86932 | 25.11% | [5 empty] | Non-TXV | 13.07%
Manteca | CA | 95336-3468 |  | 2012-05-17 | 2012-05-17 10:35 | 2012-05-17 10:35 | GOODMAN - GPG1336070M41AB | 85 | 0 | Yes | Yes | 22.5 | 19.6 | 3 | 545BB312099942C0AEA03C172CBB9F93 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-2837 |  | 2012-08-09 | 2012-08-09 10:41 | 2012-08-09 10:59 | RUUD - URKA-A036JK08X | 62 | 3.1 | Yes | Yes | 21.6 | 21 | 0.6 | BD9B2A6976484387BF5157617962B687 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95207-4126 |  | 2012-07-31 | 2012-07-31 10:58 | 2012-07-31 11:16 | OTHER - UNK | 96 | 11.2 | Yes | Yes | 26.2 | 21 | 5.2 | 57852C40464F4340B875966CABDA24C9 |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Shingle Springs | CA | 95682-9356 |  | 2012-08-02 | 2012-08-02 16:01 | 2012-08-02 16:58 | - YCY060G1M0AB | 155 | 10.9 | Yes | Yes | 19.6 | 18.9 | 0.7 | 4C6F283FD6F64DE2B20727F9992E61C0 |  | R22 | Non-TXV |  | 7.032% | 0.92968 | 13.51% | [5 empty] | Non-TXV | 7.032%
Shingle Springs | CA | 95682-9519 |  | 2012-08-07 | 2012-08-07 10:25 | 2012-08-07 10:25 | LENNOX - UNK | 94 | 0 | Yes | Yes | 18.7 | 21.7 | -3 | 48D1C8208BBE4E648D5AEEB0E9122594 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-5616 |  | 2012-08-02 | 2012-08-02 18:19 | 2012-08-02 18:43 | RHEEM - RAJA-024-JAS | 92 | 13.3 | Yes | Yes | 22.7 | 20.9 | 1.8 | 731A6D1B6C294A8EB3738D38B0284603 |  | R22 | Non-TXV |  | 14.46% | 0.85543 | 27.78% | [5 empty] | Non-TXV | 14.46%
Madera | CA | 93637-4252 |  | 2012-07-31 | 2012-07-31 17:57 | 2012-07-31 18:22 | DAY & NIGHT - 580AN0AAAF | 74 | 2.6 | Yes | Yes | 18.5 | 19.9 | -1.4 | 9AE756C802544A43B580DC699391817B |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Paradise | CA | 95969-3004 |  | 2012-07-31 | 2012-07-31 13:42 | 2012-08-01 19:30 | PAYNE - PY2PNB036060AAAA | 82 | 3.9 | Yes | Yes | 25.6 | 23.5 | 2.1 | 7FD66941E6E74B18A794DE2691E0E379 |  | R22 | Non-TXV |  | 4.756% | 0.95244 | 9.14% | [5 empty] | Non-TXV | 4.756%
Dos Palos | CA | 93620-2691 |  | 2012-08-03 | 2012-08-03 09:27 | 2012-08-03 09:57 | - 13ACD04223002 | 111 | 11.2 | Yes | Yes | 26.9 | 22.9 | 4 | 5E765FB0EBC6463795F82ECB821B2453 |  | R22 | Non-TXV |  | 10.09% | 0.8991 | 19.39% | [5 empty] | Non-TXV | 10.09%
Stockton | CA | 95204-4035 |  | 2012-08-13 | 2012-08-13 14:36 | 2012-08-13 14:55 | LENNOX - 13ACD-042-230-01 | 111 | 10.1 | Yes | Yes | 17.4 | 19.8 | -2.4 | 0E1A6AEF039B48EDA3113356D327C126 |  | R22 | Non-TXV |  | 9.099% | 0.90901 | 17.49% | [5 empty] | Non-TXV | 9.099%
Chico | CA | 95928-6778 |  | 2012-06-01 | 2012-06-01 09:40 | 2012-06-01 10:10 | AMERICAN STANDARD - 4A7B4030E1000AA | 112 | 4.5 | Yes | Yes | 22.7 | 21.7 | 1 | 5A2B8104E35445AC85504ACE70381385 |  | R410A | Non-TXV |  | 4.018% | 0.95982 | 7.721% | [5 empty] | Non-TXV | 4.018%
Fresno | CA | 93706-5354 |  | 2012-06-13 | 2012-06-13 09:40 | 2012-06-13 09:58 | ICP - PGF330060K01A2 | 89 | 2.9 | Yes | Yes | 22 | 20.2 | 1.9 | FAAB6F82EC6F44C59A53CF8064C2B626 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.258% | 0.96742 | 6.262% | [5 empty] | Non-TXV | 3.258%
Oroville | CA | 95965-3589 |  | 2012-06-06 | 2012-06-06 13:41 | 2012-06-06 13:54 | BDP - H1RA042506G | 85 | 9.2 | Yes | Yes | 19.7 | 20.7 | -1 | 4EB07C8693F14EE8BC8D253AFDD3AC8F |  | R22 | Non-TXV |  | 10.82% | 0.89176 | 20.8% | [5 empty] | Non-TXV | 10.82%
Stockton | CA | 95205-2681 |  | 2012-08-03 | 2012-08-03 10:06 | 2012-08-03 10:31 | CARRIER - 38EZG036310 | 99 | 4.9 | Yes | Yes | 17.5 | 20.4 | -2.9 | 7015F4E464524C5C94FD7E82CD8AC3DA |  | R410A | TXV |  | 4.949% | 0.95051 | 9.512% | [5 empty] | TXV | 4.949%
Merced | CA | 95348-4321 |  | 2012-08-03 | 2012-08-03 13:16 | 2012-08-03 13:49 | GOODMAN - CK-301B | 82 | 6.5 | Yes | Yes | 19.6 | 19.8 | -0.2 | C88BF74B92154876BF3200A47799B700 |  | R22 | Non-TXV |  | 7.927% | 0.92073 | 15.23% | [5 empty] | Non-TXV | 7.927%
Fresno | CA | 93710-4318 |  | 2012-05-14 | 2012-05-14 09:48 | 2012-05-14 10:09 | CARRIER - N/A | 85 | 2.5 | Yes | Yes | 23.6 | 20.9 | 2.7 | 23B904685A344A439CD5C805349895EF |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Merced | CA | 95340-3237 |  | 2012-08-02 | 2012-08-02 11:50 | 2012-08-02 12:14 | OTHER - CKL301B | 74 | 8.5 | Yes | Yes | 19.1 | 21.3 | -2.2 | D73763A7C8C549038A0CE9358E2C468F |  | R22 | Non-TXV |  | 11.49% | 0.88514 | 22.07% | [5 empty] | Non-TXV | 11.49%
Dos Palos | CA | 93620-2685 |  | 2012-08-01 | 2012-08-01 12:12 | 2012-08-01 12:32 | LENNOX - 13ACD-048-230-02 | 204 | 6.1 | Yes | Yes | 16.3 | 17.7 | -1.4 | 0279F10A855449C09EB81DED43FE814A |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Stockton | CA | 95206-2836 |  | 2012-05-09 | 2012-05-09 14:19 | 2012-05-09 14:37 | RHEEM - RRNL-B030JK06X | 77 | 9.8 | Yes | Yes | 22.7 | 22.8 | -0.1 | C1A1199E70224067986BD5DEB68A9E93 | OK: Verified Refrigerant Charge | R410A | Non-TXV |  | 12.73% | 0.87273 | 24.46% | [5 empty] | Non-TXV | 12.73%
Grass Valley | CA | 95949-6801 |  | 2012-05-30 | 2012-05-30 12:55 | 2012-05-30 12:55 | LENNOX - GCS16-311-75-1P | 67 | 0 | Yes | Yes | 24.6 | 19.9 | 4.7 | DCA6C6EE0551457DB3D6121BC69D9918 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-4136 |  | 2012-05-11 | 2012-05-11 14:30 | 2012-05-11 14:50 | PAYNE - PY3PNA036060NA-- | 167 | 7 | Yes | Yes | 15.7 | 18.6 | -2.9 | 3D46B4F835D84EFAAFF246800E79606B |  | R22 | Non-TXV |  | 4.192% | 0.95808 | 8.055% | [5 empty] | Non-TXV | 4.192%
Merced | CA | 95348-3510 |  | 2012-08-10 | 2012-08-10 12:03 | 2012-08-10 13:29 | TAPPAN - WCZ036F100AC | 155 | 8 | Yes | Yes | 20.2 | 20.4 | -0.2 | C7FDF655AC0F4B8D8A903B66EC639375 |  | R22 | Non-TXV |  | 5.161% | 0.94839 | 9.919% | [5 empty] | Non-TXV | 5.161%
Dos Palos | CA | 93620-2691 |  | 2012-08-01 | 2012-08-01 12:34 | 2012-08-01 13:00 | LENNOX - 13ACD-048-230-02 | 204 | 6.1 | Yes | Yes | 17.6 | 18.5 | -0.9 | 25F72AEC50E54631865FDE53E20A6F0D |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Yuba City | CA | 95991-8436 |  | 2012-07-31 | 2012-07-31 14:56 | 2012-07-31 15:13 | YORK - H1RD036S06G | 145 | -5.3 | Yes | Yes | 23 | 20.4 | 2.6 | 9D806C8850564EC1800542A00F3728EE |  | R22 | Non-TXV |  | -3.655% | 1.0366 | 1.024% |  |  |  |  | Non-TXV |  |  | -3.655%
Rocklin | CA | 95765-4980 |  | 2012-07-31 | 2012-07-31 13:18 | 2012-07-31 13:18 | GOODMAN - CKJ48-1B | 85 | 0 | Yes | Yes | 24 | 20.4 | 3.6 | 7A3F366B34CC47A49D98EB42E321B1E1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-9337 |  | 2012-05-21 | 2012-05-21 10:11 | 2012-05-21 10:28 | TRANE - YCX03???M0AA | 118 | 14.6 | Yes | Yes | 17.3 | 18.9 | -1.6 | 1FC024DBD6F446988B731063F3D37095 | Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.37% | 0.87627 | 23.78% | [5 empty] | Non-TXV | 12.37%
Loomis | CA | 95650-9743 |  | 2012-08-08 | 2012-08-08 13:47 | 2012-08-08 14:14 | BRYANT - 563CN048-F | 167 | -15.7 | Yes | Yes | 28.4 | 22.6 | 5.8 | 151EF8ABEA91405EBDD200A06DF98ED0 |  | R22 | Non-TXV |  | -9.401% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.401%
Newman | CA | 95360-9633 |  | 2012-08-14 | 2012-08-14 10:50 | 2012-08-14 11:05 | BRYANT - 563CN036-D | 101 | 3.7 | Yes | Yes | 22.8 | 19.9 | 2.9 | 2001F68AD73D4BEBA248756D5994414D |  | R22 | TXV |  | 3.663% | 0.96337 | 7.04% | [5 empty] | TXV | 3.663%
Los Banos | CA | 93635-3165 |  | 2012-08-01 | 2012-08-01 12:30 | 2012-08-01 12:53 | BDP - 561AJ036B | 71 | 7.3 | Yes | Yes | 23.5 | 17.5 | 6 | CC2BD4452A244FBB8BEF353718D0E9D0 |  | R22 | Non-TXV |  | 10.28% | 0.89718 | 19.76% | [5 empty] | Non-TXV | 10.28%
Stockton | CA | 95205-2929 |  | 2012-08-09 | 2012-08-09 13:00 | 2012-08-09 13:21 | OTHER - 561AJ024-A | 65 | 3.7 | Yes | Yes | 17.4 | 18.8 | -1.4 | F64E8AEB3EC942C195FBE6CC41C69495 |  | R22 | Non-TXV |  | 5.692% | 0.94308 | 10.94% | [5 empty] | Non-TXV | 5.692%
El Nido | CA | 95317-0000 |  | 2012-06-15 | 2012-06-15 13:04 | 2012-06-15 13:32 | COLEMAN - UNK | 125 | 4.1 | Yes | Yes | 25.3 | 21 | 4.3 | 987BDCA222A244F4B5F63CD5F20FACFE |  | R22 | Non-TXV |  | 3.28% | 0.9672 | 6.303% | [5 empty] | Non-TXV | 3.28%
Merced | CA | 95340-9176 |  | 2012-08-06 | 2012-08-06 10:28 | 2012-08-06 10:47 | ARCOAIRE - PGME42G0907 | 179 | 8.6 | Yes | Yes | 21.5 | 19.4 | 2.1 | 5E0A91885280411188652D94C580FB6F |  | R22 | Non-TXV |  | 4.804% | 0.95196 | 9.233% | [5 empty] | Non-TXV | 4.804%
Dos Palos | CA | 93620-9000 |  | 2012-08-01 | 2012-08-01 13:04 | 2012-08-01 13:32 | GIBSON - JS3BC-030KA | 68 | 2.7 | Yes | Yes | 20.7 | 18.5 | 2.2 | 52A164B628964C40B0CE7E48796B9639 |  | R22 | Non-TXV |  | 3.971% | 0.96029 | 7.631% | [5 empty] | Non-TXV | 3.971%
Tracy | CA | 95376-1925 |  | 2012-08-03 | 2012-08-03 13:54 | 2012-08-03 14:20 | TRANE - 2YCX3036A 1096AA | 82 | 3.2 | Yes | Yes | 23.6 | 20.8 | 2.8 | 036174F585314445BBFA214573F9EC68 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.902% | 0.96098 | 7.5% | [5 empty] | Non-TXV | 3.902%
Stockton | CA | 95206-5653 |  | 2012-05-18 | 2012-05-18 10:04 | 2012-05-18 10:22 | INTERTHERM - S3QC-036KA | 82 | 6.3 | Yes | Yes | 18.2 | 20.4 | -2.2 | DEE46FAD835D4F24965FE50F9373F94C |  | R22 | Non-TXV |  | 7.683% | 0.92317 | 14.76% | [5 empty] | Non-TXV | 7.683%
Tracy | CA | 95376-6706 |  | 2012-06-21 | 2012-06-21 15:17 | 2012-06-21 15:47 | BRYANT - 561CJ048-A | 104 | 3.1 | Yes | Yes | 19.4 | 20.1 | -0.7 | 162FC9846D2F4B919A564C4476F86632 |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Los Banos | CA | 93635-5479 |  | 2012-08-06 | 2012-08-06 11:28 | 2012-08-06 11:47 | OTHER - AC036X10218 | 63 | 4.2 | Yes | Yes | 21 | 19.6 | 1.4 | 296B1BD1AAC44B80AD4E298BA9A0F962 |  | R22 | Non-TXV |  | 6.667% | 0.93333 | 12.81% | [5 empty] | Non-TXV | 6.667%
Oroville | CA | 95966-5020 |  | 2012-08-07 | 2012-08-07 14:19 | 2012-08-07 19:07 | AMERICAN STANDARD - YCC048F1H0BB | 128 | 6.6 | Yes | Yes | 21.1 | 21.4 | -0.3 | 890D21599AEB4B40940B875C0E6CB0B9 |  | R22 | Non-TXV |  | 5.156% | 0.94844 | 9.909% | [5 empty] | Non-TXV | 5.156%
Stockton | CA | 95207-2226 |  | 2012-06-06 | 2012-06-06 10:06 | 2012-06-06 10:25 | RHEEM - UNK | 85 | 10.2 | Yes | Yes | 16.7 | 19 | -2.3 | DE2236DED7004869A34B8C2F3535274F |  | R22 | TXV |  | 12% | 0.88 | 23.06% | [5 empty] | TXV | 12%
Dos Palos | CA | 93620-0000 |  | 2012-05-15 | 2012-05-15 09:30 | 2012-05-15 10:00 | CARRIER - 38TRA036340 | 99 | 3.8 | Yes | Yes | 22.9 | 19 | 3.9 | A3FB3FEC139748639EF7241CE4FB8024 | OK: Verified Refrigerant Charge | R22 | TXV |  | 3.838% | 0.96162 | 7.377% | [5 empty] | TXV | 3.838%
Stockton | CA | 95210-1939 |  | 2012-07-31 | 2012-07-31 10:59 | 2012-07-31 11:17 | TRANE - TTP042C100A3 | 156 | 5 | Yes | Yes | 17.2 | 17.8 | -0.5 | F2CBE1BDB3F6471AA50B075AB8827EDA |  | R22 | Non-TXV |  | 3.205% | 0.96795 | 6.16% | [5 empty] | Non-TXV | 3.205%
Atwater | CA | 95301-3014 |  | 2012-08-16 | 2012-08-16 08:10 | 2012-08-16 08:38 | YORK - D1NH030N05606C | 73 | -6 | Yes | Yes | 24.7 | 19.3 | 5.4 | B58DB89D57B848769A11774ECB0D2E48 |  | R22 | Non-TXV |  | -8.219% | 1.0822 | 2.302% |  |  |  |  | Non-TXV |  |  | -8.219%
Merced | CA | 95348-2825 |  | 2012-05-11 | 2012-05-11 12:47 | 2012-05-11 13:07 | TRANE - YCX048F1H0BA | 161 | 4.9 | Yes | Yes | 22.8 | 21 | 1.8 | 85592CE5F8204164AD8B19E7EBE0BE0B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Fresno | CA | 93722-3736 |  | 2012-06-15 | 2012-06-15 09:19 | 2012-06-15 09:58 | YORK - HIRD036S06A | 145 | 4.4 | Yes | Yes | 17.2 | 19.9 | -2.7 | 7F326C59C2BC4CD2A6D1312ED70330FC |  | R22 | Non-TXV |  | 3.034% | 0.96966 | 5.832% | [5 empty] | Non-TXV | 3.034%
Manteca | CA | 95336-3339 |  | 2012-07-31 | 2012-07-31 14:05 | 2012-07-31 14:30 | GE - BTB930AI00A1 | 53 | 6.1 | Yes | Yes | 18.3 | 19.7 | -1.4 | C4676E4B35A24315866E9BABFA269CBB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.51% | 0.88491 | 22.12% | [5 empty] | Non-TXV | 11.51%
Stockton | CA | 95204-2641 |  | 2012-05-07 | 2012-05-07 16:53 | 2012-05-07 16:53 | LENNOX - 14ACX-036-230-10 | 107 | 0 | Yes | Yes | 9.4 | 15.8 | -6.4 | 7C8726AF2D824E6C8EC9B5AB41B8BD88 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 0% | 1 | 0%
Pollock Pines | CA | 95726-9555 |  | 2012-08-16 | 2012-08-16 14:00 | 2012-08-16 14:00 | AMANA - ARCF60U01C | 168.8 | 0 | Yes | Yes | 26.9 | 21.5 | 5.4 | 8398BC0DD80D49C3BFAC9D428FEE0D0C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-2799 |  | 2012-08-03 | 2012-08-03 14:54 | 2012-08-03 15:10 | CARRIER - 48GS-030040301 | 55 | 3.4 | Yes | Yes | 17.9 | 17.2 | 0.7 | 6887DDAA520F41FD945B187EC3695AC2 |  | R22 | Non-TXV |  | 6.182% | 0.93818 | 11.88% | [5 empty] | Non-TXV | 6.182%
Tracy | CA | 95376-4384 |  | 2012-08-03 | 2012-08-03 16:30 | 2012-08-03 16:50 | CARRIER - 38EH0363000 | 116 | 10.9 | Yes | Yes | 20.1 | 21.9 | -1.8 | 04B431C91F834A87BE0F69D1DF4902BE |  | R22 | Non-TXV |  | 9.397% | 0.90603 | 18.06% | [5 empty] | Non-TXV | 9.397%
Fresno | CA | 93727-3539 |  | 2012-07-06 | 2012-07-06 09:00 | 2012-07-06 09:00 | BDP - 585HJW036060ABAF | 102 | 0 | Yes | Yes | 17.8 | 17.7 | 0.1 | 98E556D5511840ECBDBB1F97D6DC156F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2925 |  | 2012-05-10 | 2012-05-10 13:30 | 2012-05-10 13:47 | RHEEM - RRNL-BO30JK06X | 78 | 7.9 | Yes | Yes | 19.1 | 21.5 | -2.4 | 81094EE0008A447886BBBF6784973EAC | OK: Verified Refrigerant Charge | R410A | TXV |  | 10.13% | 0.89872 | 19.46% | [5 empty] | TXV | 10.13%
Stockton | CA | 95210-2111 |  | 2012-08-06 | 2012-08-06 11:01 | 2012-08-06 11:31 | CARRIER - 24ACC636A300 | 112 | -4.3 | Yes | Yes | 21.5 | 19.9 | 1.6 | 527B51886ABB4254BE9DAA91C7D83BB2 |  | R410A | TXV |  | -3.839% | 1.0384 | 1.075% |  |  |  |  | TXV |  |  | -3.839%
Madera | CA | 93638-2692 |  | 2012-07-31 | 2012-07-31 10:42 | 2012-07-31 11:02 | YORK - HBBD-F060SB | 162 | 8.3 | Yes | Yes | 19.7 | 19.8 | -0.1 | 4E575A7A1CB2449483513ECF7D11945A |  | R22 | Non-TXV |  | 5.123% | 0.94877 | 9.846% | [5 empty] | Non-TXV | 5.123%
Newman | CA | 95360-2738 |  | 2012-08-08 | 2012-08-08 11:01 | 2012-08-08 11:01 | GIBSON - JS3BC-036KA | 81 | 0 | Yes | Yes | 18.8 | 20.4 | -1.6 | BCB9F536AEDE409A9F116216939CDE38 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-2110 |  | 2012-06-12 | 2012-06-12 11:00 | 2012-06-12 11:28 | ICP - NAC042AKA4 | 105 | 3.2 | Yes | Yes | 19.1 | 20.5 | -1.4 | 35FFC4E9784F483B8181F5613196FDA4 |  | R22 | Non-TXV |  | 3.048% | 0.96952 | 5.857% | [5 empty] | Non-TXV | 3.048%
Fresno | CA | 93706-2110 |  | 2012-06-12 | 2012-06-12 11:31 | 2012-06-12 12:04 | AMERICAN STANDARD - WCX030A100BA | 152 | 4.5 | Yes | Yes | 16.2 | 19.1 | -2.9 | 948BFCCE075044E1B55098E4B1C43011 |  | R22 | Non-TXV |  | 2.961% | 0.97039 | 5.689% | [5 empty] | Non-TXV | 2.961%
Stockton | CA | 95206-2845 |  | 2012-05-09 | 2012-05-09 15:41 | 2012-05-09 16:00 | REEM - RRNL-BO30JK06X | 78 | 9.6 | Yes | Yes | 21 | 21.8 | -0.8 | DE1E3E682F4942909DD1107A31324D2D | OK: Verified Refrigerant Charge | R410A | TXV |  | 12.31% | 0.87692 | 23.65% | [5 empty] | TXV | 12.31%
Los Banos | CA | 93635-9205 |  | 2012-08-16 | 2012-08-16 11:49 | 2012-08-16 12:09 | AIRE-FLO - JS3BC042KA | 102 | 10.7 | Yes | Yes | 22.3 | 19.3 | 3 | 868B7A4871864BA4B68DFD9895F22869 |  | R22 | Non-TXV |  | 10.49% | 0.8951 | 20.16% | [5 empty] | Non-TXV | 10.49%
Stockton | CA | 95204-2954 |  | 2012-08-01 | 2012-08-01 15:06 | 2012-08-01 15:25 | RHEEM - RRMA-A042JK08X | 88 | 7 | Yes | Yes | 21 | 21.4 | -0.4 | FE7056E0CF8F4051B0DD685C8D359FD5 |  | R22 | Non-TXV |  | 7.955% | 0.92045 | 15.29% | [5 empty] | Non-TXV | 7.955%
Stockton | CA | 95215-6003 |  | 2012-08-15 | 2012-08-15 09:40 | 2012-08-15 09:56 | ARCOAIRE - PGM036G0752 | 81 | 5.5 | Yes | Yes | 18.1 | 20.9 | -2.8 | 1D9975C1D25B4AF4AE8917293023292E |  | R22 | Non-TXV |  | 6.79% | 0.9321 | 13.05% | [5 empty] | Non-TXV | 6.79%
Dos Palos | CA | 93620-2668 |  | 2012-07-31 | 2012-07-31 11:28 | 2012-07-31 11:51 | BRYANT - 563CN030-C | 99 | -5.9 | Yes | Yes | 23.4 | 19.5 | 3.9 | 6AFA5D544352491FB17E01C522D47A16 |  | R22 | TXV |  | -5.96% | 1.0596 | 1.669% |  |  |  |  | TXV |  |  | -5.96%
Stockton | CA | 95206-2840 |  | 2012-05-18 | 2012-05-18 12:29 | 2012-05-18 12:53 | RHEEM - RRNL-B030JK06X | 76 | 4.5 | Yes | Yes | 18.2 | 20.4 | -2.2 | D6ED5B9FEE4E465185BB690565B7A331 |  | R410A | Non-TXV |  | 5.921% | 0.94079 | 11.38% | [5 empty] | Non-TXV | 5.921%
Stockton | CA | 95209-4832 |  | 2012-08-02 | 2012-08-02 12:19 | 2012-08-02 12:35 | PAYNE - 591ANX036000AAAA | 87 | 12.8 | Yes | Yes | 26.1 | 20.8 | 5.3 | B01309B5CC8447989D893D2C262DBBAC |  | R22 | Non-TXV |  | 14.71% | 0.85287 | 28.27% | [5 empty] | Non-TXV | 14.71%
Manteca | CA | 95337-5534 |  | 2012-05-11 | 2012-05-11 10:39 | 2012-05-11 11:01 | DAY & NIGHT - 588ANW024040ABAD | 40 | 1.5 | Yes | Yes | 23.4 | 21.2 | 2.2 | 083233AE72404F75BE3747D264C7F607 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Los Banos | CA | 93635-3165 |  | 2012-08-15 | 2012-08-15 11:48 | 2012-08-15 12:01 | CARRIER - 561AJ024000ABAA | 54 | 4.5 | Yes | Yes | 17.8 | 18.3 | -0.5 | 32F0B06DDC8B4C8A937051824AABFCD0 |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Chowchilla | CA | 93610-9764 |  | 2012-05-24 | 2012-05-24 10:31 | 2012-05-24 10:31 | CARRIER - 48ESNA2404030 | 72 | 0 | Yes | Yes | 19.7 | 19.8 | -0.1 | 7A994B6F65D746439473FA70B0F2451B |  | R410A | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5410 |  | 2012-08-06 | 2012-08-06 11:09 | 2012-08-06 11:26 | PAYNE - UNK | 72 | 2.6 | Yes | Yes | 17.3 | 18.8 | -1.5 | 45447B9184474A1B9AD0E6AB8FA4C18E |  | R22 | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Los Banos | CA | 93635-2927 |  | 2012-05-22 | 2012-05-22 11:16 | 2012-05-22 11:36 | BRYANT - 561CJ042-B | 93 | -5 | Yes | Yes | 19.3 | 20.2 | -0.8 | 81DE1E2346E446F993E7CF3FBC3D69AD |  | R22 | TXV |  | -5.376% | 1.0538 | 1.506% |  |  |  |  | TXV |  |  | -5.376%
Stockton | CA | 95206-6157 |  | 2012-05-11 | 2012-05-11 11:59 | 2012-05-11 12:16 | 38CK030340 - CARRIER | 70 | 5 | Yes | Yes | 23.9 | 22.2 | 1.7 | C9C8848B1BB54C108048F301E2B14FF6 | OK: Verified Refrigerant Charge | R22 | TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | TXV | 7.143%
Stockton | CA | 95210-3672 |  | 2012-05-22 | 2012-05-22 13:52 | 2012-05-22 14:10 | PAYNE - 591ANX036000AAAA | 86 | 2.9 | Yes | Yes | 21.4 | 19.2 | 2.2 | B4B08B4BEAB84DD08AC461CC5A72F0AE |  | R22 | Non-TXV |  | 3.372% | 0.96628 | 6.48% | [5 empty] | Non-TXV | 3.372%
Los Banos | CA | 93635-2714 |  | 2012-08-09 | 2012-08-09 08:34 | 2012-08-09 09:04 | AIRE-FLO - H2RA036S06E | 63 | 7 | Yes | Yes | 18 | 17.9 | 0.1 | C6257FE5FA814B5581857E9FD04FB45E |  | R22 | Non-TXV |  | 11.11% | 0.88889 | 21.35% | [5 empty] | Non-TXV | 11.11%
Grass Valley | CA | 95945-4507 |  | 2012-05-08 | 2012-05-08 13:52 | 2012-05-08 14:14 | LENNOX - GCS20R-411-75-1P | 70 | 2.2 | Yes | Yes | 24 | 20.4 | 3.6 | 9142FCBE2BE34BFA8C11C9FE28BCEDA5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Camino | CA | 95709-9513 |  | 2012-08-16 | 2012-08-16 15:59 | 2012-08-16 15:59 | TRANE - 2TWA0042A3000AA | 104 | 0 | Yes | Yes | 27.1 | 22.8 | 4.3 | 2C15C8739A624285BD753B8321AF0001 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3659 |  | 2012-08-02 | 2012-08-02 08:14 | 2012-08-02 08:32 | CARRIER - 591ANX030000ABAA | 65 | -3.8 | Yes | Yes | 21.6 | 19.2 | 2.4 | B634322796FD40D7B078D8136BC34FE8 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Stockton | CA | 95206-6076 |  | 2012-07-11 | 2012-07-11 11:35 | 2012-07-11 11:52 | BRYANT - 561CJ042-E | 80 | 7.2 | Yes | Yes | 17.1 | 18.1 | -1 | 9BAD2CE41B064EE4881BCF3688192CB3 |  | R22 | TXV |  | 9% | 0.91 | 17.3% | [5 empty] | TXV | 9%
Stockton | CA | 95205-0000 |  | 2012-08-06 | 2012-08-06 11:07 | 2012-08-06 11:24 | GOODMAN - CRT48-1 | 145 | 8 | Yes | Yes | 24 | 19.9 | 4.1 | AAF1416311C242A0A2227D7E1D697E55 |  | R22 | Non-TXV |  | 5.517% | 0.94483 | 10.6% | [5 empty] | Non-TXV | 5.517%
Stockton | CA | 95219-3109 |  | 2012-08-14 | 2012-08-14 09:31 | 2012-08-14 09:31 | RUUD - UAKB-030JAS | 66 | 0 | Yes | Yes | 17.9 | 20.4 | -2.5 | E6DCE5E98F2B48BC961DF43B269C0038 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2608 |  | 2012-07-31 | 2012-07-31 12:31 | 2012-07-31 12:48 | DAY & NIGHT - 30/80YAC106C | 72 | 2.3 | Yes | Yes | 23.9 | 20.7 | 3.2 | 3E5313B9F9F94BB18A9B8B4E11A90C7B |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Diamond Springs | CA | 95619-9476 |  | 2012-07-26 | 2012-07-26 09:46 | 2012-07-26 09:46 | ARMSTRONG - SCU10B36-1A | 71 | 0 | Yes | Yes | 22.5 | 20.4 | 2.1 | 6EBE2DB4A75A41788D626137609D3E86 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Shingle Springs | CA | 95682-9536 |  | 2012-08-07 | 2012-08-07 11:02 | 2012-08-07 11:02 | GOODMAN - CLJ30-1C | 105 | 0 | Yes | Yes | 24.7 | 19.7 | 5 | 58AC9315853D4736AC903C1338D5FF5C |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-2424 |  | 2012-08-14 | 2012-08-14 11:09 | 2012-08-14 11:09 | RHEEM - RAMB-048JAS | 162 | 0 | Yes | Yes | 21.7 | 17.9 | 3.8 | 7291B0616CDB4FB9BE6EC10F25A07E35 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9624 |  | 2012-08-08 | 2012-08-08 08:20 | 2012-08-08 08:37 | TRANE - TTB030C100A0 | 70 | -3.6 | Yes | Yes | 20.4 | 20.4 | 0 | D16B9253B51A47E09B7F69D0375E434F |  | R22 | TXV |  | -5.143% | 1.0514 | 1.44% |  |  |  |  | TXV |  |  | -5.143%
Winton | CA | 95388-9624 |  | 2012-08-08 | 2012-08-08 08:45 | 2012-08-08 09:03 | TRANE - TTB030C100A0 | 70 | -2.9 | Yes | Yes | 18.4 | 19.9 | -1.5 | 5062355DF59244C9A27C0D92FFB0D722 |  | R22 | TXV |  | -4.143% | 1.0414 | 1.16% |  |  |  |  | TXV |  |  | -4.143%
Los Banos | CA | 93635-3108 |  | 2012-08-01 | 2012-08-01 09:57 | 2012-08-01 10:24 | AMERICAN STANDARD - 4A7A4042A1000AB | 103 | 8.8 | Yes | Yes | 24.8 | 22.8 | 2 | F8C2916103EB4597965920549ABCBFAF |  | R22 | Non-TXV |  | 8.544% | 0.91456 | 16.42% | [5 empty] | Non-TXV | 8.544%
Los Banos | CA | 93635-2621 |  | 2012-08-01 | 2012-08-01 10:27 | 2012-08-01 10:27 | GOODMAN - 561J036-C | 70 | 0 | Yes | Yes | 28.5 | 22.8 | 5.7 | 0A6A84494B1047D7A7369651D0F63014 |  | R22 | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3102 |  | 2012-08-15 | 2012-08-15 11:20 | 2012-08-15 11:47 | TRANE - YCC036F1MOBJ | 85 | 4 | Yes | Yes | 16.2 | 18.3 | -2.1 | B884752E0DE748FDB257A440BF34E952 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Winton | CA | 95388-9358 |  | 2012-08-02 | 2012-08-02 13:59 | 2012-08-02 14:31 | LUXAIRE - UNK | 65 | 5.2 | Yes | Yes | 22.1 | 20.9 | 1.3 | 694C9103E9974265B058E5D72A5C9337 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Merced | CA | 95348-2100 |  | 2012-08-02 | 2012-08-02 09:04 | 2012-08-02 09:31 | TRANE - TTB736A100A0 | 88 | 2.9 | Yes | Yes | 18.8 | 21 | -2.2 | A3DF9DF4DE244D42881CDCD6E4A3EDC2 |  | R22 | Non-TXV |  | 3.295% | 0.96705 | 6.333% | [5 empty] | Non-TXV | 3.295%
Somerset | CA | 95684-9350 |  | 2012-08-02 | 2012-08-02 08:57 | 2012-08-02 09:16 | DAY & NIGHT - N2A330AKC200 | 68 | 4 | Yes | Yes | 24 | 20.3 | 3.8 | 7F4E3202EFEB49D9A4B601EFEC9F4F26 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.882% | 0.94118 | 11.3% | [5 empty] | Non-TXV | 5.882%
Chico | CA | 95973-0587 |  | 2012-05-09 | 2012-05-09 12:41 | 2012-05-09 13:03 | PAYNE - 565GJ030040 | 58 | 5.4 | Yes | Yes | 21.5 | 22.9 | -1.4 | 2ECF850ED7E5419EBFCA13BBF6A574F6 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.31% | 0.9069 | 17.89% | [5 empty] | Non-TXV | 9.31%
Stockton | CA | 95210-5662 |  | 2012-05-21 | 2012-05-21 14:50 | 2012-05-21 15:09 | RUUD - UAFD-025JAS | 51 | -3 | Yes | Yes | 22 | 20.4 | 1.6 | 128ED7BF4D704C2BA654A5FB1726F19B |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Grass Valley | CA | 95945-4806 |  | 2012-05-16 | 2012-05-16 14:19 | 2012-05-16 14:38 | CARRIER - 24ANA760A300 | 182 | 37.7 | Yes | Yes | 23.4 | 19.3 | 4.1 | 5ECFF9409BA04EC8868F9124375CBF5D | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 20.71% | 0.79286 | 39.81% | [5 empty] | Non-TXV | 20.71%
Corning | CA | 96021-2701 |  | 2012-07-31 | 2012-07-31 17:09 | 2012-07-31 18:14 | LENNOX - CC526-030-75-1PA | 66 | 3 | Yes | Yes | 23.2 | 21.4 | 1.8 | 8B8777B08A084C23ADC7B9837081BFD9 |  | R22 | Non-TXV |  | 4.545% | 0.95455 | 8.735% | [5 empty] | Non-TXV | 4.545%
Fresno | CA | 93710-4213 |  | 2012-05-16 | 2012-05-16 10:09 | 2012-05-16 11:49 | YORK - D1NA036N0506C | 67 | -3.9 | Yes | Yes | 20.8 | 19.9 | 0.9 | 3090C42628CF4C4BBA6CAB0F625A6081 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Merced | CA | 95340-4022 |  | 2012-05-07 | 2012-05-07 11:42 | 2012-05-07 11:42 | GOODMAN - GPG13240451CB | 74 | 0 | Yes | Yes | 25.9 | 21 | 4.9 | 6653F5298FBA4BF28226F9D18DF8D7AB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-5129 |  | 2012-06-15 | 2012-06-15 11:22 | 2012-06-15 11:40 | BDP - 585B042100YACR | 89 | -5.2 | Yes | Yes | 21.3 | 17.1 | 4.2 | 02D6C3F63FFD46C3AF28D97E76316C92 |  | R22 | Non-TXV |  | -5.843% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.843%
Paradise | CA | 95969-6635 |  | 2012-05-14 | 2012-05-14 13:01 | 2012-05-14 13:01 | LENNOX - 13GCSXA-36-068X-230-1A | 127 | 0 | Yes | Yes | 23.5 | 20.7 | 2.8 | F9F3CBA2A36542DDAE8F24FBF0D105EC |  | R410A | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-3836 |  | 2012-08-15 | 2012-08-15 11:18 | 2012-08-15 11:18 | OTHER - UNK | 52 | 0 | Yes | Yes | 15.7 | 19.6 | -3.9 | A3978DBB1127409B8AFAE12B656C8564 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-1112 |  | 2012-07-31 | 2012-07-31 16:17 | 2012-07-31 17:27 | OTHER - 4AC13L36P-3A | 85 | 9.1 | Yes | Yes | 28.1 | 23.1 | 5 | 8240849B7E8A493B86CEFBA93D99D1FE |  | R410A | TXV |  | 10.71% | 0.89294 | 20.57% | [5 empty] | TXV | 10.71%
Atwater | CA | 95301-2821 |  | 2012-08-07 | 2012-08-07 11:15 | 2012-08-07 11:15 | OTHER - PQWR36A1NB | 56 | 0 | Yes | Yes | 20.7 | 20.9 | -0.1 | 5C4509AD75C544BE8EEDF55C753CAFEE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9718 |  | 2012-08-02 | 2012-08-02 15:23 | 2012-08-02 15:52 | GIBSON - UNK | 100 | -5.8 | Yes | Yes | 20.8 | 20.6 | 0.3 | A5F99114B12841B5AD0F1DEA44ACE6E1 |  | R22 | TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | TXV |  |  | -5.8%
Stockton | CA | 95204-5256 |  | 2012-05-09 | 2012-05-09 14:08 | 2012-05-09 14:36 | GOODMAN - GPG13300701BB | 77 | 2.8 | Yes | Yes | 16.4 | 17.7 | -1.3 | 8FB6AB0205304B38B2EB4DA11D9CA438 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Atwater | CA | 95301-4426 |  | 2012-08-08 | 2012-08-08 11:50 | 2012-08-08 12:14 | YORK - D1NA042N05606C | 76 | -4.5 | Yes | Yes | 23.3 | 19.8 | 3.5 | D478E860181344D5BCA69DE203E5AD5F |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Stockton | CA | 95206-1835 |  | 2012-08-07 | 2012-08-07 13:28 | 2012-08-07 13:44 | PAYNE - PA10JA060-C | 118 | 3.5 | Yes | Yes | 19 | 19.5 | -0.5 | 654C5F3749D4477496131120AD300D9B |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Stockton | CA | 95207-4354 |  | 2012-07-31 | 2012-07-31 15:52 | 2012-07-31 16:12 | OTHER - RCE30C2C | 125 | 7.1 | Yes | Yes | 21.9 | 21.1 | 0.8 | 135F2C68D30D4D2E9B7E0DE17D4A49AC |  | R22 | TXV |  | 5.68% | 0.9432 | 10.92% | [5 empty] | TXV | 5.68%
Stockton | CA | 95205-3223 |  | 2012-08-03 | 2012-08-03 11:36 | 2012-08-03 12:04 | RHEEM - RRNA-B036JK06X | 83 | 3.8 | Yes | Yes | 23.6 | 21 | 2.6 | 603BA31A63004B1BACC89596E03C2D6B |  | R22 | Non-TXV |  | 4.578% | 0.95422 | 8.799% | [5 empty] | Non-TXV | 4.578%
Stockton | CA | 95206-2412 |  | 2012-08-08 | 2012-08-08 10:30 | 2012-08-08 10:48 | GOODMAN - GSC130361EB | 120 | 4.5 | Yes | Yes | 20 | 18.8 | 1.2 | CF2F7B92D5FC4B82B13CB74F99BFA625 |  | R22 | TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | TXV | 3.75%
Stockton | CA | 95205-7200 |  | 2012-06-20 | 2012-06-20 10:05 | 2012-06-20 10:35 | GIBSON - S3BA-030KA | 68 | 6.3 | Yes | Yes | 17.7 | 20.4 | -2.7 | 48C8B801F46F4BDFA415002FE217D30A |  | R22 | Non-TXV |  | 9.265% | 0.90735 | 17.8% | [5 empty] | Non-TXV | 9.265%
Stockton | CA | 95204-1529 |  | 2012-08-13 | 2012-08-13 12:17 | 2012-08-13 12:47 | RHEEM - RRMA0A042JK08X | 114 | 6.9 | Yes | Yes | 18.9 | 18.6 | 0.3 | 282FF934C081407F9A1238F64BDC2B52 |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
Chico | CA | 95928-6857 |  | 2012-08-09 | 2012-08-09 11:46 | 2012-08-09 12:48 | BRYANT - 583ANW036060NAAF | 82 | 0 | Yes | Yes | 21.9 | 20.9 | 1 | 688A9EEDDA354AF2AD4D49E031D404B5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1746 |  | 2012-08-08 | 2012-08-08 12:18 | 2012-08-08 12:41 | GOODMAN - GSC130361DF | 114 | 5.4 | Yes | Yes | 18.7 | 19 | -0.3 | D09BA78DB7D04ACFA031B985F7D38D33 |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Merced | CA | 95340-2320 |  | 2012-08-09 | 2012-08-09 15:05 | 2012-08-09 15:23 | GOODMAN - GPG12307018 | 85 | 5.4 | Yes | Yes | 25.5 | 20.5 | 5 | CCC06F6D0C6D44A3837F3A2984635CEE |  | R22 | Non-TXV |  | 6.353% | 0.93647 | 12.21% | [5 empty] | Non-TXV | 6.353%
Stockton | CA | 95206-2937 |  | 2012-05-18 | 2012-05-18 11:50 | 2012-05-18 12:07 | GOODMAN - GPG13360701AB | 112 | -6.6 | Yes | Yes | 24.4 | 20.6 | 3.8 | 5FEE366142BE411FB9645035300C0E08 |  | R22 | Non-TXV |  | -5.893% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.893%
Merced | CA | 95341-5628 |  | 2012-08-08 | 2012-08-08 13:56 | 2012-08-08 14:16 | AIRE-FLO - D1NH036N05606A | 104 | 8.9 | Yes | Yes | 26.5 | 21.5 | 5 | 9BB792EC3C4542CD922CED0E07F0D6E1 |  | R22 | Non-TXV |  | 8.558% | 0.91442 | 16.45% | [5 empty] | Non-TXV | 8.558%
Atwater | CA | 95301-9539 |  | 2012-08-16 | 2012-08-16 08:59 | 2012-08-16 09:18 | YORK - D1YS036N04508 | 92 | -6.5 | Yes | Yes | 26.2 | 20.4 | 5.8 | 76C8B31EE66C430E91EBD2ECEE16230E |  | R22 | Non-TXV |  | -7.065% | 1.0707 | 1.979% |  |  |  |  | Non-TXV |  |  | -7.065%
Atwater | CA | 95301-9539 |  | 2012-08-16 | 2012-08-16 09:34 | 2012-08-16 09:55 | PAYNE - PY1PNB036060ABAA | 68 | -4 | Yes | Yes | 21.8 | 19.8 | 2 | 0396B753852743A487329093263B724E |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Cameron Park | CA | 95682-8946 |  | 2012-05-31 | 2012-05-31 15:48 | 2012-05-31 15:48 | BDP - 541DJ024 | 118 | 0 | Yes | Yes | 23.6 | 20 | 3.6 | EB070BF4419244088EC5C82AF8182BA4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9502 |  | 2012-08-08 | 2012-08-08 10:46 | 2012-08-08 11:16 | LENNOX - 13HP-036-230-01 | 138 | 4.1 | Yes | Yes | 22.1 | 21.2 | 0.9 | D6F66395E6DA4F5986D2A4D9882A9807 |  | R22 | Non-TXV |  | 2.971% | 0.97029 | 5.71% | [5 empty] | Non-TXV | 2.971%
Stockton | CA | 95210-3644 |  | 2012-08-01 | 2012-08-01 10:23 | 2012-08-01 10:40 | ICP - ACS024A2C1 | 62 | 4.1 | Yes | Yes | 20.1 | 20.2 | -0.1 | CB3F2D0D0D1D4EEA9E4EB0B0D06BE94A |  | R22 | Non-TXV |  | 6.613% | 0.93387 | 12.71% | [5 empty] | Non-TXV | 6.613%
Magalia | CA | 95954-9463 |  | 2012-08-08 | 2012-08-08 10:25 | 2012-08-08 10:43 | BRYANT - 561CJ048-A | 102 | 5.2 | Yes | Yes | 20.5 | 20.8 | -0.3 | 9E8B2C9B174B466D8FB7133ECA482222 |  | R22 | TXV |  | 5.098% | 0.94902 | 9.797% | [5 empty] | TXV | 5.098%
Madera | CA | 93637-4345 |  | 2012-07-31 | 2012-07-31 11:38 | 2012-07-31 18:23 | OTHER - UNK | 81 | 2.7 | Yes | Yes | 18.3 | 19.8 | -1.5 | 910326C10DA444BC974C443E358515FA |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Yuba City | CA | 95991-6835 |  | 2012-08-16 | 2012-08-16 12:01 | 2012-08-16 12:26 | BRYANT - 113ANA048-B | 128 | 5.9 | Yes | Yes | 22 | 22 | 0 | C5049F245BC9452E82C64A478BDBB067 |  | R410A | TXV |  | 4.609% | 0.95391 | 8.858% | [5 empty] | TXV | 4.609%
Los Banos | CA | 93635-9448 |  | 2012-08-16 | 2012-08-16 09:24 | 2012-08-16 09:50 | BRYANT - 561CJ036E | 70 | 11.9 | Yes | Yes | 21.4 | 20.2 | 1.3 | 0103ECDAFE98435088F201B3F17E5AEC |  | R22 | Non-TXV |  | 17% | 0.83 | 32.67% | [5 empty] | Non-TXV | 17%
Los Banos | CA | 93635-9448 |  | 2012-08-16 | 2012-08-16 09:33 | 2012-08-16 09:56 | BRYANT - 561CJ036E | 70 | 8.2 | Yes | Yes | 16.6 | 16.4 | 0.2 | B604710F1F37429B91302115D5347DBB |  | R22 | Non-TXV |  | 11.71% | 0.88286 | 22.51% | [5 empty] | Non-TXV | 11.71%
Stockton | CA | 95210-3619 |  | 2012-08-08 | 2012-08-08 09:11 | 2012-08-08 09:28 | CARRIER - UNK | 80 | -4.7 | Yes | Yes | 20.7 | 18.2 | 2.5 | A2E9FF2CF1F04CED8AA613144E0B1208 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Yuba City | CA | 95991-3303 |  | 2012-07-31 | 2012-07-31 12:28 | 2012-07-31 12:50 | CARRIER - UNK | 96 | 3.2 | Yes | Yes | 24 | 21.4 | 2.6 | 427780B15C6749A29801CEC4271B2211 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95206-2802 |  | 2012-05-09 | 2012-05-09 12:50 | 2012-05-09 13:12 | PAYNE - PA13NR030-K | 75 | 7.8 | Yes | Yes | 18.2 | 20.4 | -2.2 | 2A20CD20A5084316BF36089885BBBE30 | OK: Verified Refrigerant Charge | R22 | TXV |  | 10.4% | 0.896 | 19.99% | [5 empty] | TXV | 10.4%
Fresno | CA | 93706-4723 |  | 2012-06-12 | 2012-06-12 12:21 | 2012-06-12 12:51 | ICP - PGC042K080F | 84 | 5.1 | Yes | Yes | 20.1 | 19.2 | 0.9 | EF14C36574E347BE953E31EF8BE88776 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.071% | 0.93929 | 11.67% | [5 empty] | Non-TXV | 6.071%
Stockton | CA | 95206-3834 |  | 2012-05-23 | 2012-05-23 16:21 | 2012-05-23 16:41 | TRANE - YCC036F1M0BF | 83 | 7.2 | Yes | Yes | 26.4 | 23.1 | 3.3 | 71DEC8FE100C41759FA2B75DA17CC9EF |  | R22 | Non-TXV |  | 8.675% | 0.91325 | 16.67% | [5 empty] | Non-TXV | 8.675%
Newman | CA | 95360-1746 |  | 2012-08-08 | 2012-08-08 10:05 | 2012-08-08 10:35 | CARRIER - H2RA030S060 | 60 | 2.5 | Yes | Yes | 17.4 | 19.9 | -2.5 | 7DC50AB09BFD4E8ABB2721627DF29390 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Stockton | CA | 95205-7807 |  | 2012-08-06 | 2012-08-06 11:51 | 2012-08-06 12:11 | BRYANT - 561CJ024-E | 55 | 1.6 | Yes | Yes | 18 | 18.7 | -0.7 | 42BCF01366394F8B97DE0BE580CF24A9 |  | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Yuba City | CA | 95993-6040 |  | 2012-08-01 | 2012-08-01 10:12 | 2012-08-01 10:30 | LENNOX - HS22-461V-2P | 133 | -19.6 | Yes | Yes | 19.4 | 19.7 | -0.3 | 3A6EAA95CC3E41DB9E074374875877AE |  | R22 | TXV |  | -14.74% | 1.1474 | 4.127% |  |  |  |  | TXV |  |  | -14.74%
Merced | CA | 95348-2319 |  | 2012-07-05 | 2012-07-05 13:43 | 2012-07-05 13:43 | OTHER - UNK | 52 | 0 | Yes | Yes | 20.9 | 21.7 | -0.8 | 79BB787C92AF46048FF552AB1540893E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3155 |  | 2012-08-01 | 2012-08-01 11:13 | 2012-08-01 11:33 | AMERICAN STANDARD - TTD730B100A1 | 69 | 12.5 | Yes | Yes | 30.3 | 27.7 | 2.6 | 8E54BC034CDB442C9C629573B8629FC7 |  | R22 | Non-TXV |  | 18.12% | 0.81884 | 34.81% | [5 empty] | Non-TXV | 18.12%
Gustine | CA | 95322-1742 |  | 2012-08-14 | 2012-08-14 11:06 | 2012-08-14 11:35 | PAYNE - PY1PNB036060AAAA | 62 | 6.3 | Yes | Yes | 17.8 | 19.7 | -1.9 | 82262DF4674A4CD68B067A38A42C419C |  | R22 | Non-TXV |  | 10.16% | 0.89839 | 19.53% | [5 empty] | Non-TXV | 10.16%
Stockton | CA | 95206-2937 |  | 2012-06-12 | 2012-06-12 10:37 | 2012-06-12 10:54 | RHEEM - RRNL-B030JK06X | 77 | 5.5 | Yes | Yes | 22.6 | 20.7 | 1.9 | 3270233C93174178B641B1C796D8C9EA |  |  |  |  | 7.143% | 0.92857 | 13.73% | [5 empty] | 0 | 7.143%
Stockton | CA | 95206-2940 |  | 2012-06-20 | 2012-06-20 12:15 | 2012-06-20 12:52 | RHEEM - RRNL-B024JK06X | 78 | 3.9 | Yes | Yes | 21.6 | 21.3 | 0.3 | 83B25A7DBAA446BD9BE84AAD42EA9A36 |  | R410A | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Chico | CA | 95973-0595 |  | 2012-05-09 | 2012-05-09 14:05 | 2012-05-09 15:03 | PAYNE - PA10JA036-C | 79 | 3.3 | Yes | Yes | 20.6 | 20.3 | 0.3 | E42C728DF8994A89B540B431C671FE13 | OK: Verified Refrigerant Charge | R22 | TXV |  | 4.177% | 0.95823 | 8.028% | [5 empty] | TXV | 4.177%
Los Banos | CA | 93635-3146 |  | 2012-08-01 | 2012-08-01 13:16 | 2012-08-01 13:32 | PAYNE - 591ANX042000ABAA | 112 | 16.2 | Yes | Yes | 24.2 | 22.4 | 1.8 | 07D5A6D78E7543D0BFADDB80B2C77F7C |  | R22 | Non-TXV |  | 14.46% | 0.85536 | 27.8% | [5 empty] | Non-TXV | 14.46%
Fresno | CA | 93725-1618 |  | 2012-05-10 | 2012-05-10 10:27 | 2012-05-10 10:49 | YORK - D1NA042N05606 | 76 | 2.3 | Yes | Yes | 21.5 | 18.8 | 2.7 | B4FDC21EA73649D18F2BE557619F4FB9 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Le Grand | CA | 95333-9653 |  | 2012-08-14 | 2012-08-14 10:58 | 2012-08-14 11:15 | YORK - B2PSO30A06A | 134 | 4.2 | Yes | Yes | 20.8 | 19.3 | 1.5 | 7FF49B0B56AB4F028D4B6815ABB633EA |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Yuba City | CA | 95993-9011 |  | 2012-05-09 | 2012-05-09 15:46 | 2012-05-09 16:08 | UNK - 561AJ036-B | 85 | 9.3 | Yes | Yes | 17.2 | 20.1 | -2.9 | 12DCC99B0BE946AFA5FD71114A16F5C6 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.94% | 0.89059 | 21.03% | [5 empty] | Non-TXV | 10.94%
Chico | CA | 95973-9115 |  | 2012-05-07 | 2012-05-07 13:42 | 2012-05-07 14:13 | TRAIN - YCC024F1LOBH | 65 | 2.3 | Yes | Yes | 21.5 | 18.8 | 2.7 | 1061BC9FA3774B549A9964324530A27A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.538% | 0.96462 | 6.8% | [5 empty] | Non-TXV | 3.538%
Newman | CA | 95360-1753 |  | 2012-08-07 | 2012-08-07 12:44 | 2012-08-07 13:05 | YORK - H2RC42S64 | 106 | 11 | Yes | Yes | 17.6 | 19.5 | -1.9 | D31E48C86E2042A596BDEAFE5D6ED61D |  | R22 | Non-TXV |  | 10.38% | 0.89623 | 19.94% | [5 empty] | Non-TXV | 10.38%
Madera | CA | 93637-3002 |  | 2012-08-01 | 2012-08-01 10:06 | 2012-08-01 11:09 | RHEEM - RRMA-A048JK10E | 117 | 3.5 | Yes | Yes | 23.3 | 20.7 | 2.6 | 8BB4578974684398A542121279E33C12 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Riverbank | CA | 95367-2887 |  | 2012-06-13 | 2012-06-13 14:26 | 2012-06-13 14:43 | COLEMAN - CCGD24S41Q3A | 42 | 3.1 | Yes | Yes | 19.2 | 20.4 | -1.2 | FC5AE4E4415C4091955BDC950D31C77E |  | R410A | Non-TXV |  | 7.381% | 0.92619 | 14.18% | [5 empty] | Non-TXV | 7.381%
Stockton | CA | 95210-4613 |  | 2012-08-06 | 2012-08-06 12:34 | 2012-08-06 12:51 | CARRIER - 38CKC024340 | 59 | 2.3 | Yes | Yes | 17.3 | 18.6 | -1.3 | 07BA8A3EC4744091B9FAA7FA237BC087 |  | R22 | Non-TXV |  | 3.898% | 0.96102 | 7.492% | [5 empty] | Non-TXV | 3.898%
Stockton | CA | 95209-4552 |  | 2012-08-01 | 2012-08-01 14:29 | 2012-08-01 14:29 | DAY & NIGHT - 38CKC042--351 | 93 | 0 | Yes | Yes | 17.6 | 18.6 | -1 | BEE2CF707A654D1794E4C7C207D8785E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93706-1902 |  | 2012-06-12 | 2012-06-12 10:07 | 2012-06-12 10:27 | CARRIER - 48HLA130---300BE | 68 | 2.2 | Yes | Yes | 23.8 | 20.1 | 3.7 | 3BEC189A937A4C14989C9B3F801AB170 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Los Banos | CA | 93635-3815 |  | 2012-05-15 | 2012-05-15 09:05 | 2012-05-15 09:22 | CARRIER - UNK | 63 | 6.4 | Yes | Yes | 22.5 | 19.5 | 3 | A18C97A7922F459089E7F2C82EAD0566 |  | R22 | Non-TXV |  | 10.16% | 0.89841 | 19.52% | [5 empty] | Non-TXV | 10.16%
Yuba City | CA | 95991-1937 |  | 2012-07-02 | 2012-07-02 09:04 | 2012-07-02 09:20 | OTHER - UNK | 85 | -8 | Yes | Yes | 18 | 17.2 | 0.8 | FA6AD5F9A8134FF382BEE6FC59913E4F |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Madera | CA | 93637-4358 |  | 2012-07-31 | 2012-07-31 16:02 | 2012-07-31 18:10 | OTHER - 580AN420AAF | 76 | -4.5 | Yes | Yes | 18.8 | 20.4 | -1.6 | EB61884FDC6645C4822F03AC3E319EED |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Stockton | CA | 95210-1473 |  | 2012-05-29 | 2012-05-29 16:37 | 2012-05-29 17:01 | CARRIER - 48GS-030060301-- | 55 | 2.3 | Yes | Yes | 24.7 | 20.4 | 4.3 | 31D6ED8D496945B4B6A551F5B16E3536 |  | R22 | TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | TXV | 4.182%
Yuba City | CA | 95991-8233 |  | 2012-08-10 | 2012-08-10 12:24 | 2012-08-10 12:44 | BDP - 561J036-D | 84 | 23.9 | Yes | Yes | 19.1 | 19 | 0.1 | 0240F6A5E1FF4F1598F1F420784C17DC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 28.45% | 0.71548 | 54.68% | [5 empty] | Non-TXV | 28.45%
Chico | CA | 95973-9284 |  | 2012-07-10 | 2012-07-10 14:21 | 2012-07-10 20:39 | - PHD342000K000C1 | 160 | 11 | Yes | Yes | 20.7 | 21.2 | -0.4 | 1FC2AB20863949E2BF7F031DBE418F4E |  | R410A | Non-TXV |  | 6.875% | 0.93125 | 13.21% | [5 empty] | Non-TXV | 6.875%
Merced | CA | 95348-3656 |  | 2012-08-03 | 2012-08-03 16:58 | 2012-08-03 17:31 | RUUD - URKA-A042JK08X | 63 | -3.7 | Yes | Yes | 18.6 | 20.5 | -1.9 | 70F3BEFC2EC04D5382E52D8327A106F6 |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Fresno | CA | 93710-7018 |  | 2012-05-14 | 2012-05-14 10:38 | 2012-05-14 11:06 | CARRIER - 48GX-042090301AD | 118 | 6.3 | Yes | Yes | 24.8 | 21.2 | 3.7 | E17E47ADC1794889A76FD979DA5FB038 |  | R22 | Non-TXV |  | 5.339% | 0.94661 | 10.26% | [5 empty] | Non-TXV | 5.339%
Los Banos | CA | 93635-2973 |  | 2012-05-08 | 2012-05-08 12:46 | 2012-05-08 13:08 | DAY AND NIGHT - 591ANX036000AAA | 95 | 3.2 | Yes | Yes | 28.6 | 22.6 | 6 | 43BE589DBEE34A509CEA74D94D1BBFC1 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.368% | 0.96632 | 6.473% | [5 empty] | Non-TXV | 3.368%
Gustine | CA | 95322-1904 |  | 2012-05-30 | 2012-05-30 11:12 | 2012-05-30 11:31 | DAY & NIGHT - UNK | 84 | 4.1 | Yes | Yes | 20.2 | 19.7 | 0.5 | 75B44F4AAB7E4FD88616DFA6600BD6CA |  | R22 | Non-TXV |  | 4.881% | 0.95119 | 9.38% | [5 empty] | Non-TXV | 4.881%
Yuba City | CA | 95991-2901 |  | 2012-08-10 | 2012-08-10 11:41 | 2012-08-10 11:41 | YORK - D1NA036N05606C | 67 | 0 | Yes | Yes | 25.2 | 19.5 | 5.7 | B1699BD1D2B548A0A7AC50B013C00239 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-9679 |  | 2012-05-24 | 2012-05-24 12:26 | 2012-05-24 12:43 | YORK - H1RA042S06D | 85 | 5.6 | Yes | Yes | 19 | 20.4 | -1.4 | 11F89AFFFCAE45F685E55F1F1C95A927 |  | R22 | Non-TXV |  | 6.588% | 0.93412 | 12.66% | [5 empty] | Non-TXV | 6.588%
Gustine | CA | 95322-9679 |  | 2012-05-24 | 2012-05-24 12:45 | 2012-05-24 13:01 | YORK - H1RA042S06D | 85 | 5.8 | Yes | Yes | 16.1 | 16.9 | -0.8 | 463C6E8098414C4591BD17ADFF0D72AD |  | R22 | Non-TXV |  | 6.824% | 0.93176 | 13.11% | [5 empty] | Non-TXV | 6.824%
Fresno | CA | 93727-1813 |  | 2012-05-08 | 2012-05-08 18:40 | 2012-05-08 18:40 | RHEEM - RRNL-B048JK10X | 85 | 0 | Yes | Yes | 23.4 | 20.6 | 2.8 | DF48CFDA9823425DA3385969C2AB66FF | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-1619 |  | 2012-08-09 | 2012-08-09 09:29 | 2012-08-09 09:30 | RHEEM - RAFD-036JAB | 82 | 4.6 | Yes | Yes | 17.5 | 20.4 | -2.9 | 63CD652BE7C646C8B316BAE6216DEB4F |  | R22 | Non-TXV |  | 5.61% | 0.9439 | 10.78% | [5 empty] | Non-TXV | 5.61%
Stockton | CA | 95205-3720 |  | 2012-05-15 | 2012-05-15 12:54 | 2012-05-15 13:12 | ARCOAIRE - GPCM036K060F | 86 | 3.2 | Yes | Yes | 18.4 | 21 | -2.6 | 62A887CA59684814AA734AE2B4DF39D6 |  | R22 | Non-TXV |  | 3.721% | 0.96279 | 7.151% | [5 empty] | Non-TXV | 3.721%
Dos Palos | CA | 93620-9004 |  | 2012-05-15 | 2012-05-15 13:45 | 2012-05-15 14:08 | YORK - H2RD036S06B | 96 | -5.6 | Yes | Yes | 25.1 | 21.1 | 4.1 | A3B0E3E1E1B24D37856224BF730E4B5A |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95212-1123 |  | 2012-08-09 | 2012-08-09 16:01 | 2012-08-09 16:18 | RUUD - AT-42B10 | 96 | 6.8 | Yes | Yes | 19.5 | 19.2 | 0.3 | 788F6D8F4E434738B64A7581140F8842 |  | R22 | Non-TXV |  | 7.083% | 0.92917 | 13.61% | [5 empty] | Non-TXV | 7.083%
Chico | CA | 95928-7556 |  | 2012-05-24 | 2012-05-24 10:06 | 2012-05-24 10:24 | RUUD - NA | 95 | 2.8 | Yes | Yes | 24.2 | 21.6 | 2.6 | E3F8A9D38CB140AFA2521EA779CF40F3 |  | R22 | Non-TXV |  | 2.947% | 0.97053 | 5.664% | [5 empty] | Non-TXV | 2.947%
Los Banos | CA | 93635-5400 |  | 2012-08-02 | 2012-08-02 13:10 | 2012-08-02 13:35 | RHEEM - UAKA-030JAZ | 66 | 3.8 | Yes | Yes | 20.8 | 19.5 | 1.3 | 45018BF5F79540A1BC60E0EF48F7B1B4 |  | R22 | Non-TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | Non-TXV | 5.758%
Stockton | CA | 95206-2837 |  | 2012-05-09 | 2012-05-09 11:09 | 2012-05-09 11:34 | RHEEM - RRNA-B030JKO6X | 85 | 7.9 | Yes | Yes | 20.1 | 20.4 | -0.3 | 885D2898C31A4A2CACF8B4889E0ADC5D | OK: Verified Refrigerant Charge | R22 | TXV |  | 9.294% | 0.90706 | 17.86% | [5 empty] | TXV | 9.294%
Atwater | CA | 95301-2089 |  | 2012-08-06 | 2012-08-06 14:36 | 2012-08-06 14:36 | TRANE - UNK | 75 | 0 | Yes | Yes | 21.7 | 19.9 | 1.8 | 4D32CBAD72504E7E9900430960FE4BFC | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-5422 |  | 2012-05-17 | 2012-05-17 11:08 | 2012-05-17 11:29 | BRYANT - 113RNA024 | 69 | -3.9 | Yes | Yes | 22.4 | 20.4 | 2 | 97D450E58AC3490F8E58A2FC765D4ABF | OK: Verified Refrigerant Charge | R22 | TXV |  | -5.652% | 1.0565 | 1.583% |  |  |  |  | TXV |  |  | -5.652%
Paradise | CA | 95969-5226 |  | 2012-06-11 | 2012-06-11 10:08 | 2012-06-11 10:34 | BRYANT - 5630N030 | 103 | 6.9 | Yes | Yes | 20.6 | 23.4 | -2.8 | 0049E25505B24FF1BFAC443CA4D7BF57 |  | R22 | TXV |  | 6.699% | 0.93301 | 12.87% | [5 empty] | TXV | 6.699%
Paradise | CA | 95969-4806 |  | 2012-08-03 | 2012-08-03 14:20 | 2012-08-03 14:31 | TEMPSTAR - PGAA30C1K4 | 79 | 6.8 | Yes | Yes | 19.8 | 19.8 | 0 | 89B5FEFAEDF64448B049CFC526DA50A6 |  | R22 | Non-TXV |  | 8.608% | 0.91392 | 16.54% | [5 empty] | Non-TXV | 8.608%
Auburn | CA | 95602-9520 |  | 2012-07-31 | 2012-07-31 11:02 | 2012-07-31 11:22 | BRYANT - 582ANW030060AAAD | 59 | 5.3 | Yes | Yes | 17.9 | 19.1 | -1.2 | 37A01895F4CE417FB6970D1FBDD58259 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.983% | 0.91017 | 17.26% | [5 empty] | Non-TXV | 8.983%
Merced | CA | 95348-3774 |  | 2012-08-02 | 2012-08-02 11:52 | 2012-08-02 12:32 | GOODMAN - CK42-1C | 104 | 4.2 | Yes | Yes | 18.6 | 20 | -1.4 | 2EA996E950F643FEA201F8F1B491791D |  | R22 | Non-TXV |  | 4.038% | 0.95962 | 7.761% | [5 empty] | Non-TXV | 4.038%
Chico | CA | 95973-7610 |  | 2012-08-09 | 2012-08-09 18:41 | 2012-08-09 19:12 | YORK - H1RA048506D | 117 | 3.5 | Yes | Yes | 23.9 | 21.2 | 2.7 | C50FA81CF5EC4AC6AEB228FAD68A681F |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Dinuba | CA | 93618-2754 |  | 2012-07-31 | 2012-07-31 12:28 | 2012-07-31 12:55 | WEATHER KING - N/A | 90 | 3.1 | Yes | Yes | 18.4 | 18.4 | 0 | F66DF81013844B8BA8ACF65AF2C3B41E |  | R22 | Non-TXV |  | 3.444% | 0.96556 | 6.619% | [5 empty] | Non-TXV | 3.444%
Red Bluff | CA | 96080-9332 |  | 2012-08-06 | 2012-08-06 08:45 | 2012-08-06 09:01 | YORK - H4DH048SO6A | 138 | 5.6 | Yes | Yes | 23.4 | 20.8 | 2.6 | 21676C217AD345B9A33BDA6BBC17B77E |  | R22 | Non-TXV |  | 4.058% | 0.95942 | 7.799% | [5 empty] | Non-TXV | 4.058%
Red Bluff | CA | 96080-9332 |  | 2012-08-06 | 2012-08-06 09:03 | 2012-08-06 09:20 | YORK - H2DH024S06B | 87 | 8.1 | Yes | Yes | 23.9 | 22.4 | 1.5 | 5D848CAC0FDD413DA15B6D7BFAFC337A |  | R22 | Non-TXV |  | 9.31% | 0.9069 | 17.89% | [5 empty] | Non-TXV | 9.31%
Stockton | CA | 95206-2960 |  | 2012-05-22 | 2012-05-22 13:15 | 2012-05-22 13:36 | RHEEM - RRNL-B024JK06X | 78 | 5 | Yes | Yes | 18.5 | 20.9 | -2.4 | 3B4F9C01A5154FDD8B05A69C746EA3D1 |  | R410A | Non-TXV |  | 6.41% | 0.9359 | 12.32% | [5 empty] | Non-TXV | 6.41%
Dinuba | CA | 93618-2530 |  | 2012-07-31 | 2012-07-31 14:02 | 2012-07-31 14:21 | LENNOX - 13HPD-024-230-01 | 99 | 9.6 | Yes | Yes | 17.6 | 19.1 | -1.5 | E896A41FCB4F42459C91E6478AD00BC5 |  | R22 | Non-TXV |  | 9.697% | 0.90303 | 18.64% | [5 empty] | Non-TXV | 9.697%
Merced | CA | 95348-3712 |  | 2012-08-02 | 2012-08-02 10:43 | 2012-08-02 11:15 | DUCANE - AC10B36-B | 96 | 3.3 | Yes | Yes | 18.9 | 19.7 | -0.8 | B6BA176784B34CC28F6DEE94C418B199 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Stockton | CA | 95206-2229 |  | 2012-08-07 | 2012-08-07 14:57 | 2012-08-07 15:21 | OTHER - UNK | 85 | 2.6 | Yes | Yes | 20 | 22.1 | -2.1 | D30646EE97FA4F33B1F2F80176F21E0C |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Auburn | CA | 95603-9740 |  | 2012-08-03 | 2012-08-03 09:28 | 2012-08-03 09:46 | RHEEM - RRKA-A048JK10E | 78 | 8.1 | Yes | Yes | 27 | 22 | 5 | 3094C5D4E49F4865813AFE640C249072 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.38% | 0.89615 | 19.96% | [5 empty] | Non-TXV | 10.38%
Livingston | CA | 95334-9421 |  | 2012-07-31 | 2012-07-31 10:15 | 2012-07-31 10:43 | CARRIER - 591ANX030000ABAA | 85 | 4.6 | Yes | Yes | 18.9 | 20.4 | -1.5 | D9942A09133848D49000CE12C531E25B |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Stockton | CA | 95209-1742 |  | 2012-08-03 | 2012-08-03 09:40 | 2012-08-03 09:57 | PAYNE - 567CB042 | 85 | 11 | Yes | Yes | 17.2 | 18.3 | -1.1 | D5C59CD150684683A417C793DE25747C |  | R22 | Non-TXV |  | 12.94% | 0.87059 | 24.87% | [5 empty] | Non-TXV | 12.94%
Stockton | CA | 95210-2247 |  | 2012-08-03 | 2012-08-03 11:56 | 2012-08-03 12:16 | CARRIER - 580AN036060 | 96 | 3.6 | Yes | Yes | 24.3 | 20.1 | 4.2 | 429A9582D30640898F6274B2AC9E3CF0 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Tracy | CA | 95376-4829 |  | 2012-08-08 | 2012-08-08 16:51 | 2012-08-08 17:11 | CARRIER - 88EB024300 | 51 | 4.6 | Yes | Yes | 24.7 | 20.4 | 4.3 | E4B81681C21D4173B6C1558F7361C077 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.02% | 0.9098 | 17.33% | [5 empty] | Non-TXV | 9.02%
Merced | CA | 95340-3944 |  | 2012-08-08 | 2012-08-08 09:45 | 2012-08-08 10:09 | CARRIER - 38EH048320SM | 137 | 11.2 | Yes | Yes | 26.5 | 20.9 | 5.6 | FC936D0189534880935268A5207268CF |  | R22 | Non-TXV |  | 8.175% | 0.91825 | 15.71% | [5 empty] | Non-TXV | 8.175%
Magalia | CA | 95954-9349 |  | 2012-05-30 | 2012-05-30 13:04 | 2012-05-30 13:24 | COLEMAN - 9541-904 | 76 | 3.8 | Yes | Yes | 26.3 | 20.9 | 5.4 | E366D032BFBE42AD8F5C2B992A2E44A4 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Red Bluff | CA | 96080-2834 |  | 2012-08-03 | 2012-08-03 17:32 | 2012-08-03 17:58 | AMANA - APG13360701AB | 115 | 7.5 | Yes | Yes | 25.1 | 22.6 | 2.5 | 91873E8013AB48D7BCCAD3EDA72F2154 |  | R22 | Non-TXV |  | 6.522% | 0.93478 | 12.53% | [5 empty] | Non-TXV | 6.522%
Dos Palos | CA | 93620-9013 |  | 2012-08-03 | 2012-08-03 13:14 | 2012-08-03 13:35 | NORDYNE - JS5BD030K | 134 | 14.8 | Yes | Yes | 25.4 | 24.8 | 0.6 | 684F38083A4441C88380FBB6551B6CFA |  | R22 | Non-TXV |  | 11.04% | 0.88955 | 21.23% | [5 empty] | Non-TXV | 11.04%
Stockton | CA | 95206-5729 |  | 2012-05-15 | 2012-05-15 15:06 | 2012-05-15 15:24 | CARRIER - 38CKC048---301-- | 105 | 10.3 | Yes | Yes | 17.5 | 20.3 | -2.8 | 456DB61273864805B54FD4DE3C50BD65 | OK: Verified Refrigerant Charge | R22 | Non-TXV |  | 9.81% | 0.9019 | 18.85% | [5 empty] | Non-TXV | 9.81%
Fresno | CA | 93722-8200 |  | 2012-05-16 | 2012-05-16 15:04 | 2012-05-16 15:04 | BRYANT - 114ANA030-A | 122 | 0 | Yes | Yes | 25 | 20.1 | 4.9 | 171A0B1BEAD74917849D02DD895E25A2 | OK: Verified Refrigerant Charge | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3442 |  | 2012-08-03 | 2012-08-03 11:02 | 2012-08-03 11:38 | YORK - D1NH030N05606A | 69 | 3.9 | Yes | Yes | 22.6 | 19.1 | 3.5 | A05887B846994C30ADC02C508A60729D |  | R22 | Non-TXV |  | 5.652% | 0.94348 | 10.86% | [5 empty] | Non-TXV | 5.652%
Livingston | CA | 95334-1629 |  | 2012-08-01 | 2012-08-01 09:08 | 2012-08-01 09:34 | GOODMAN - GSC130241DA | 88 | 3.6 | Yes | Yes | 19.4 | 21 | -1.6 | 0B5F6D8F6238470F88C44367E8157FA3 |  | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Stockton | CA | 95203-1200 |  | 2012-05-10 | 2012-05-10 13:25 | 2012-05-10 13:44 | AMERICAN STANDARD - YCY036G1M0AB | 129 | 9.2 | Yes | Yes | 16.8 | 19.3 | -2.5 | 3407878D87484CC49FCD63B197EED477 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.132% | 0.92868 | 13.71% | [5 empty] | Non-TXV | 7.132%
Rocklin | CA | 95765-5812 |  | 2012-07-31 | 2012-07-31 12:19 | 2012-07-31 12:41 | GOODMAN - CK49-1B | 97 | 9.8 | Yes | Yes | 21.5 | 19.9 | 1.6 | 8584CB8737DE4DD0AF95EF34E9991A64 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.1% | 0.89897 | 19.42% | [5 empty] | Non-TXV | 10.1%
Stockton | CA | 95204-2931 |  | 2012-08-01 | 2012-08-01 14:38 | 2012-08-01 14:54 | PAYNE - 589ANW060100ABBG | 101 | 3.4 | Yes | Yes | 20.1 | 20.1 | 0 | 2D33654B52BB4239BC2351BC49441381 |  | R22 | Non-TXV |  | 3.366% | 0.96634 | 6.469% | [5 empty] | Non-TXV | 3.366%
Stockton | CA | 95206-2848 |  | 2012-05-10 | 2012-05-10 10:24 | 2012-05-10 10:45 | RHEEM - RRNL-BO24JK06X | 78 | 9.5 | Yes | Yes | 25.1 | 20 | 5.1 | 55B84496925B491DB325D299CF44185C | OK: Verified Refrigerant Charge | R410A | TXV |  | 12.18% | 0.87821 | 23.41% | [5 empty] | TXV | 12.18%
Rocklin | CA | 95765-4291 |  | 2012-07-31 | 2012-07-31 15:52 | 2012-07-31 16:17 | - 38BRC030310 | 100 | 3.9 | Yes | Yes | 19.1 | 20.1 | -1 | BEF16EB02AFC458E91F12AB2185C79A7 |  | R22 | Non-TXV |  | 3.9% | 0.961 | 7.495% | [5 empty] | Non-TXV | 3.9%
Newman | CA | 95360-1803 |  | 2012-08-07 | 2012-08-07 11:19 | 2012-08-07 11:55 | CARRIER - 591ANX048000ACAA | 132 | 5.5 | Yes | Yes | 17.5 | 19.8 | -2.3 | 07A0F0C51B0D49F0A682721B2E395FD9 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Stockton | CA | 95207-2317 |  | 2012-05-31 | 2012-05-31 15:54 | 2012-05-31 16:14 | RHEEM - RRKA-A024JK06X | 50 | 6.4 | Yes | Yes | 18.4 | 20.4 | -2 | EA6BD6BB47E141B48452017D377A4A51 |  | R22 | TXV |  | 12.8% | 0.872 | 24.6% | [5 empty] | TXV | 12.8%
Dos Palos | CA | 93620-2667 |  | 2012-08-03 | 2012-08-03 10:44 | 2012-08-03 11:08 | BRYANT - 563CN030C | 101 | 6.7 | Yes | Yes | 27.3 | 21.3 | 6 | 9C4CA6325DED40E29E6148D6E995FAE6 |  | R22 | TXV |  | 6.634% | 0.93366 | 12.75% | [5 empty] | TXV | 6.634%
Stockton | CA | 95206-1877 |  | 2012-08-14 | 2012-08-14 11:55 | 2012-08-14 12:11 | RUUD - UNK | 80 | 2.6 | Yes | Yes | 22 | 21.3 | 0.7 | 8B6F62D3DD0F4D50886CEAFC6ACD8D73 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Stockton | CA | 95205-2575 |  | 2012-08-14 | 2012-08-14 11:41 | 2012-08-14 12:07 | CARRIER - 38EZG048300 | 125 | 6.9 | Yes | Yes | 20.9 | 21.5 | -0.6 | 97E0E36E8AE04DC59F3AB4DDFD050CDF |  | R410A | TXV |  | 5.52% | 0.9448 | 10.61% | [5 empty] | TXV | 5.52%
Stockton | CA | 95206-6451 |  | 2012-05-24 | 2012-05-24 10:48 | 2012-05-24 11:05 | GOODMAN - CKL30-16 | 74 | 4.2 | Yes | Yes | 19.2 | 21 | -1.8 | 7FEBFF21E8CE4702B15327799E6B4531 |  | R22 | Non-TXV |  | 5.676% | 0.94324 | 10.91% | [5 empty] | Non-TXV | 5.676%
Stockton | CA | 95206-3134 |  | 2012-08-15 | 2012-08-15 08:58 | 2012-08-15 09:14 | TRANE - UNK | 160 | 4.7 | Yes | Yes | 17 | 19.1 | -2.1 | 91255A48923543A1AFD2DA3BEC2402E6 |  | R22 | Non-TXV |  | 2.938% | 0.97062 | 5.645% | [5 empty] | Non-TXV | 2.938%
Merced | CA | 95340-1610 |  | 2012-07-31 | 2012-07-31 11:15 | 2012-07-31 11:43 | PAYNE - PY3PNA036090NA | 164 | 5.6 | Yes | Yes | 20.8 | 19.7 | 1.1 | 7EC8733BFC394A409563D93DBE5F384E |  | R22 | Non-TXV |  | 3.415% | 0.96585 | 6.562% | [5 empty] | Non-TXV | 3.415%
Merced | CA | 95340-9483 |  | 2012-08-06 | 2012-08-06 09:08 | 2012-08-06 09:28 | PAYNE - PY2PNB060090ABAA | 129 | 17.2 | Yes | Yes | 27.1 | 25 | 2.1 | 34F6252B4EEC489C92D39FBED72EF4BA |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Stockton | CA | 95210-4428 |  | 2012-05-22 | 2012-05-22 12:12 | 2012-05-22 12:31 | PAYNE - 591ANX030000ABAA | 68 | 5.8 | Yes | Yes | 22.2 | 20.2 | 2.1 | 87D4C6A270DA4ACA96F2C88AB102E1A6 |  | R22 | Non-TXV |  | 8.529% | 0.91471 | 16.39% | [5 empty] | Non-TXV | 8.529%
Los Banos | CA | 93635-2933 |  | 2012-05-22 | 2012-05-22 12:04 | 2012-05-22 12:04 | DAY & NIGHT - N/A | 75 | 0 | Yes | Yes | 21.7 | 22 | -0.3 | B8106BE4A2704BDFB330946303892873 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1758 |  | 2012-07-31 | 2012-07-31 12:42 | 2012-07-31 13:49 | TRANE - TTX736A100A2 | 130 | 6.3 | Yes | Yes | 18.8 | 20.1 | -1.3 | C6F63029D6D740A19256B4BAEEA6E565 |  | R22 | Non-TXV |  | 4.846% | 0.95154 | 9.313% | [5 empty] | Non-TXV | 4.846%
Fresno | CA | 93725-1129 |  | 2012-05-16 | 2012-05-16 13:54 | 2012-05-16 14:14 | RHEEM - RRMA-A036JK08X | 99 | 3.1 | Yes | Yes | 20.2 | 20.9 | -0.7 | 8F2CAE0E647244EC8C863948723AD482 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Dos Palos | CA | 93620-2691 |  | 2012-08-03 | 2012-08-03 12:31 | 2012-08-03 13:04 | LENNOX - 13ACD04223002 | 111 | 11.6 | Yes | Yes | 24.6 | 21.2 | 3.4 | 17CBFD0AE7F240AAB490BC00026182CC |  | R22 | Non-TXV |  | 10.45% | 0.8955 | 20.08% | [5 empty] | Non-TXV | 10.45%
Stockton | CA | 95204-5921 |  | 2012-05-23 | 2012-05-23 11:13 | 2012-05-23 11:30 | YORK - H4DB036S06A | 73 | 5.5 | Yes | Yes | 17.1 | 19.9 | -2.8 | D7D2F3653BF14524A511827CAFC6D2B6 |  | R22 | Non-TXV |  | 7.534% | 0.92466 | 14.48% | [5 empty] | Non-TXV | 7.534%
Stockton | CA | 95204-5921 |  | 2012-05-23 | 2012-05-23 11:20 | 2012-05-23 11:38 | GE - UNK | 32 | 6.8 | Yes | Yes | 18.8 | 19.8 | -1 | C00A7C4C525443CD83891F5F200C03A2 |  | R22 | Non-TXV |  | 21.25% | 0.7875 | 40.84% | [5 empty] | Non-TXV | 21.25%
Stockton | CA | 95209-2733 |  | 2012-08-01 | 2012-08-01 10:53 | 2012-08-01 11:10 | PAYNE - PA10JA042-D | 90 | 4.1 | Yes | Yes | 23.8 | 20 | 3.9 | 9C6B3564275C46AD84F4EC5C24BE769D |  | R22 | Non-TXV |  | 4.556% | 0.95444 | 8.755% | [5 empty] | Non-TXV | 4.556%
Fresno | CA | 93722-3304 |  | 2012-05-14 | 2012-05-14 13:10 | 2012-05-14 13:41 | CARRIER - 48NET036300 | 96 | 13.2 | Yes | Yes | 21.9 | 20.9 | 1 | F3C280F2455B4BCAADE81F5B9038928F |  | R22 | Non-TXV |  | 13.75% | 0.8625 | 26.42% | [5 empty] | Non-TXV | 13.75%
Merced | CA | 95340-2422 |  | 2012-08-02 | 2012-08-02 08:23 | 2012-08-02 08:46 | OTHER - 22JK | 69 | 6.1 | Yes | Yes | 17.2 | 18.1 | -0.9 | 08F4E7F115234A7A8C2BCAB7713DF6F9 |  | R22 | Non-TXV |  | 8.841% | 0.91159 | 16.99% | [5 empty] | Non-TXV | 8.841%
Paradise | CA | 95969-3279 |  | 2012-08-09 | 2012-08-09 18:26 | 2012-08-09 18:26 | LENNOX - GCS20H-311-75 | 48 | 0 | Yes | Yes | 19.9 | 21.3 | -1.4 | F284D1F462A044E7BBB76602E264721C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93722-4533 |  | 2012-07-06 | 2012-07-06 12:54 | 2012-07-06 13:12 | GOODMAN - GPG1324045M41AB | 80 | 2.4 | Yes | Yes | 19.9 | 18.1 | 1.8 | 891B21E30E5243EDBD6B3CC4782554D8 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Marysville | CA | 95901-3819 |  | 2012-05-15 | 2012-05-15 11:45 | 2012-05-15 12:08 | HEIL - PGAA48F1K1 | 124 | 22.6 | Yes | Yes | 18.6 | 18.8 | -0.2 | 10FEA7BA6E824310988BED15CF9EA1AB | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 18.23% | 0.81774 | 35.03% | [5 empty] | Non-TXV | 18.23%
Merced | CA | 95340-0943 |  | 2012-05-17 | 2012-05-17 10:23 | 2012-05-17 10:23 | FRASER JOHNSTON - 100WR42E1NA | 88 | 25.6 | Yes | Yes | 20.1 | 21 | -0.9 | 3C5A0F962CEE481F9333DAC5CF16F400 | Add refrigerant: 25.6 oz Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 29.09% | 0.70909 | 55.91% | [5 empty] | Non-TXV | 29.09%
Stockton | CA | 95206-2944 |  | 2012-05-22 | 2012-05-22 15:31 | 2012-05-22 15:53 | RHEEM - RRNL-B030JK06X | 78 | 7.4 | Yes | Yes | 18.7 | 20.3 | -1.6 | E318F1C616A04E3A8EBE4C2AA0674358 |  | R410A | Non-TXV |  | 9.487% | 0.90513 | 18.23% | [5 empty] | Non-TXV | 9.487%
Fresno | CA | 93722-6112 |  | 2012-05-15 | 2012-05-15 15:11 | 2012-05-15 15:30 | BDP - 585GJ036060 | 85 | 2.6 | Yes | Yes | 20.2 | 20.4 | -0.2 | 87A0EA4751B149AE81731C2740508EBE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93727-4429 |  | 2012-05-09 | 2012-05-09 12:46 | 2012-05-09 12:55 | BDP - 567024RCU | 60 | 1.9 | Yes | Yes | 23.1 | 21.5 | 1.6 | A0EB13CAF977435AB9468E88D11A5489 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Manteca | CA | 95337-8811 |  | 2012-05-15 | 2012-05-15 15:55 | 2012-05-15 16:15 | GOODMAN - PHK042-1 | 115 | 3.5 | Yes | Yes | 24 | 21 | 3 | 6680627D505D43788FDFCDD501EDB101 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Newman | CA | 95360-1711 |  | 2012-05-17 | 2012-05-17 12:00 | 2012-05-17 12:17 | RHEEM - RAHE-036JAS | 91 | 2.7 | Yes | Yes | 16.3 | 18.3 | -2 | E5D5D268733F4141BA2D897DE7136D66 |  | R22 | Non-TXV |  | 2.967% | 0.97033 | 5.702% | [5 empty] | Non-TXV | 2.967%
Clovis | CA | 93612-2171 |  | 2012-05-15 | 2012-05-15 12:47 | 2012-05-15 13:13 | PAYNE - 585EJ024050 | 54 | 11.1 | Yes | Yes | 24.2 | 21.3 | 3 | BA70D9619D98477FAEA8E8B8DB237717 |  | R22 | Non-TXV |  | 20.56% | 0.79444 | 39.5% | [5 empty] | Non-TXV | 20.56%
Dos Palos | CA | 93620-2666 |  | 2012-08-01 | 2012-08-01 11:04 | 2012-08-01 11:22 | BRYANT - 563CN024-D | 88 | 4.4 | Yes | Yes | 22.7 | 20.8 | 1.9 | 05E544DADAED4B7BBA50F1BA4C95CC56 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Oroville | CA | 95966-3919 |  | 2012-05-31 | 2012-05-31 13:21 | 2012-05-31 13:49 | GIBSON - GB3BM-060-CB | 76 | 2.5 | Yes | Yes | 23.5 | 22.3 | 1.3 | 1C4224C4BD684640917FDB5FF9181CCA |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Manteca | CA | 95337-6520 |  | 2012-05-30 | 2012-05-30 13:58 | 2012-05-30 14:23 | RHEEM - RAHE-030JAS | 78 | 3.2 | Yes | Yes | 18.5 | 19.9 | -1.4 | 35783F180F794B1FB697B11595C66EB2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.103% | 0.95897 | 7.884% | [5 empty] | Non-TXV | 4.103%
Merced | CA | 95340-3822 |  | 2012-08-09 | 2012-08-09 15:28 | 2012-08-09 15:47 | TRANE - YCZ060F1MOBB | 198 | 5.9 | Yes | Yes | 19.9 | 21.3 | -1.4 | D04D4F8E3E044CBD9260B918BE56DFAD |  | R22 | Non-TXV |  | 2.98% | 0.9702 | 5.727% | [5 empty] | Non-TXV | 2.98%
Dos Palos | CA | 93620-2017 |  | 2012-07-31 | 2012-07-31 09:57 | 2012-07-31 10:23 | AMERICAN STANDARD - YCC030F1M0BH | 69 | -4.1 | Yes | Yes | 22.9 | 20.6 | 2.3 | 83E739D85F4E48B18A825F3FC15F9435 |  | R22 | Non-TXV |  | -5.942% | 1.0594 | 1.664% |  |  |  |  | Non-TXV |  |  | -5.942%
Newman | CA | 95360-1706 |  | 2012-08-07 | 2012-08-07 11:58 | 2012-08-07 12:23 | RHEEM - RAHE-48JAS | 114 | 9.2 | Yes | Yes | 17.8 | 19.8 | -2 | 16D6507972B04D8BAD234DEA426FAD04 |  | R22 | Non-TXV |  | 8.07% | 0.9193 | 15.51% | [5 empty] | Non-TXV | 8.07%
Stockton | CA | 95207-7436 |  | 2012-06-12 | 2012-06-12 10:16 | 2012-06-12 10:35 | DAY & NIGHT - 565BJ00-B | 76 | 16.1 | Yes | Yes | 16.7 | 19.5 | -2.8 | BA4656D6957847D3B133EA499E0A13D1 |  | R22 | Non-TXV |  | 21.18% | 0.78816 | 40.71% | [5 empty] | Non-TXV | 21.18%
Stockton | CA | 95210-1778 |  | 2012-07-12 | 2012-07-12 15:41 | 2012-07-12 16:01 | HEIL - ACS024A2C1 | 62 | 7.7 | Yes | Yes | 21.7 | 20.5 | 1.2 | B2EE72C587BD41E7954580721ED088DE |  | R22 | Non-TXV |  | 12.42% | 0.87581 | 23.87% | [5 empty] | Non-TXV | 12.42%
Chowchilla | CA | 93610-2701 |  | 2012-05-08 | 2012-05-08 13:17 | 2012-05-08 13:17 | YORK - DBYP-F042NO80A | 150 | 0 | Yes | Yes | 17.2 | 19.9 | -2.7 | ADD1006E3A1A446B8F8572D6EE5C7952 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2701 |  | 2012-05-08 | 2012-05-08 13:23 | 2012-05-08 13:44 | YORK - DBYP-F042NO80A | 85 | 2.6 | Yes | Yes | 16.6 | 19.4 | -2.8 | 3E756279D7D14434BA65A8F9C0CED921 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Fresno | CA | 93710-7024 |  | 2012-05-16 | 2012-05-16 12:05 | 2012-05-16 12:22 | RUUD - URMA-A036JK8X | 80 | 3 | Yes | Yes | 17.1 | 19.9 | -2.8 | 1F9B8354346D4574A2732DB129D3BEE3 |  | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Dos Palos | CA | 93620-2650 |  | 2012-07-31 | 2012-07-31 09:07 | 2012-07-31 09:42 | CARRIER - 38CKC30340 | 67 | -2.4 | Yes | Yes | 20 | 18.2 | 1.8 | 4F880E602DD44FCB8AC4FD8729180D26 |  | R22 | TXV |  | -3.582% | 1.0358 | 1.003% |  |  |  |  | TXV |  |  | -3.582%
Stockton | CA | 95204-2838 |  | 2012-08-01 | 2012-08-01 17:30 | 2012-08-01 17:30 | YORK - D3NZ030N05606NXA | 64 | 0 | Yes | Yes | 22.8 | 19.8 | 3 | 9FDFEF8D812B4575AA2C9707ED828C1D |  | R410A | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-9224 |  | 2012-05-31 | 2012-05-31 14:45 | 2012-05-31 15:07 | GE - BWB936A10001 | 95 | 31.1 | Yes | Yes | 18.2 | 20.4 | -2.2 | 469A1FBDBC024B7A804426A1F0020E30 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 32.74% | 0.67263 | 62.91% | [5 empty] | Non-TXV | 32.74%
Dos Palos | CA | 93620-2902 |  | 2012-08-07 | 2012-08-07 14:50 | 2012-08-07 15:13 | TRANE - 2TTB3030A1000A | 88 | 11.5 | Yes | Yes | 24.2 | 22.4 | 1.8 | C4770481BF444B8D8AB1A8D2CC659C69 |  | R22 | Non-TXV |  | 13.07% | 0.86932 | 25.11% | [5 empty] | Non-TXV | 13.07%
Winton | CA | 95388-9345 |  | 2012-08-02 | 2012-08-02 14:51 | 2012-08-02 15:16 | TRANE - TTB724A100A1 | 54 | 1.6 | Yes | Yes | 25.9 | 20.8 | 5.1 | FD4EB44C4F394B12AF17A6195386E115 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95204-4132 |  | 2012-06-06 | 2012-06-06 11:52 | 2012-06-06 12:16 | LENNOX - HS18-261-10P | 68 | 2.4 | Yes | Yes | 20.8 | 20.4 | 0.4 | 0F6A935709934BDDBD4EA732F2F59B97 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Oroville | CA | 95965-3128 |  | 2012-05-29 | 2012-05-29 12:09 | 2012-05-29 12:33 | CARRIER - 38BRG042300 | 85 | 3.1 | Yes | Yes | 17.9 | 20.6 | -2.7 | 70D43E95A18F4B6385017020D884B353 |  | R22 | TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | TXV | 3.647%
Los Banos | CA | 93635-9445 |  | 2012-05-18 | 2012-05-18 10:58 | 2012-05-18 11:25 | GOODMAN - CKJ42-1D | 99 | 5.7 | Yes | Yes | 19.5 | 19.9 | -0.4 | F2DD1A16D3B7455897C99B5B6C1B582D |  | R22 | Non-TXV |  | 5.758% | 0.94242 | 11.06% | [5 empty] | Non-TXV | 5.758%
Merced | CA | 95340-3222 |  | 2012-08-02 | 2012-08-02 12:24 | 2012-08-02 12:41 | AIRE-FLO - 80WR36G1NA | 120 | 12.6 | Yes | Yes | 18 | 19.2 | -1.2 | 511C87CDFE9940ABB8AF10012EB2F996 |  | R22 | Non-TXV |  | 10.5% | 0.895 | 20.18% | [5 empty] | Non-TXV | 10.5%
Merced | CA | 95348-2243 |  | 2012-08-10 | 2012-08-10 10:45 | 2012-08-10 11:14 | GIBSON - JS3BA-048KA | 85 | 5.2 | Yes | Yes | 17.7 | 19.5 | -1.8 | B63B45ACA3364346A353FB44E2BDA8DC |  | R22 | Non-TXV |  | 6.118% | 0.93882 | 11.76% | [5 empty] | Non-TXV | 6.118%
Stockton | CA | 95205-7044 |  | 2012-08-06 | 2012-08-06 10:10 | 2012-08-06 10:32 | HEIL - PGC036K080D | 71 | 2.7 | Yes | Yes | 17 | 18.8 | -1.8 | 98F7C54CD0F14C05A99C42AD8629FD91 |  | R22 | Non-TXV |  | 3.803% | 0.96197 | 7.308% | [5 empty] | Non-TXV | 3.803%
Merced | CA | 95340-4215 |  | 2012-05-08 | 2012-05-08 13:30 | 2012-05-08 13:30 | BRYANT - 585A030080YAC | 50 | 0 | Yes | Yes | 24.4 | 22.9 | 1.5 | FBDD70FC64AF4F398E6BFE7DE19C3614 | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2308 |  | 2012-08-07 | 2012-08-07 11:36 | 2012-08-07 12:03 | GOODMAN - VSC130301BA | 87 | 3 | Yes | Yes | 15.8 | 18.5 | -2.7 | FB16EF50E45E4E20B86B7E4CC1C2156E |  | R22 | Non-TXV |  | 3.448% | 0.96552 | 6.627% | [5 empty] | Non-TXV | 3.448%
Madera | CA | 93637-0000 |  | 2012-08-01 | 2012-08-01 11:35 | 2012-08-01 11:55 | BDP - 585HJ036060 | 102 | 3 | Yes | Yes | 17.9 | 18.8 | -0.9 | 06A6E9E8DA58428BA0CA46CE9DE2F297 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Fresno | CA | 93722-5749 |  | 2012-05-29 | 2012-05-29 12:41 | 2012-05-29 13:02 | TEMPSTAR - PGAD47D1K3 | 215 | 6.3 | Yes | Yes | 26.8 | 21 | 5.8 | C91207F27A6F45B68BC60C537CD84109 |  | R22 | Non-TXV |  | 2.93% | 0.9707 | 5.631% | [5 empty] | Non-TXV | 2.93%
Stockton | CA | 95219-3579 |  | 2012-06-19 | 2012-06-19 12:07 | 2012-06-19 12:28 | OTHER - UNK | 54 | 2.3 | Yes | Yes | 22 | 19.9 | 2.1 | 457F760C5AFC4D07987C0C5488B35021 |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Merced | CA | 95340-3466 |  | 2012-08-03 | 2012-08-03 12:11 | 2012-08-03 12:38 | CARRIER - 38TR042300 | 166 | 5.2 | Yes | Yes | 17 | 17.8 | -0.8 | F6020392C9254831A3CC7E5E0A2B9C18 |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Stockton | CA | 95207-4419 |  | 2012-06-11 | 2012-06-11 09:54 | 2012-06-11 10:11 | GOODMAN - GPG13300701BB | 77 | 3.6 | Yes | Yes | 20.5 | 19.6 | 0.9 | 1479C11480294DBDAF5818EBE8DF9F94 |  | R22 | Non-TXV |  | 4.675% | 0.95325 | 8.985% | [5 empty] | Non-TXV | 4.675%
Stockton | CA | 95206-6086 |  | 2012-08-15 | 2012-08-15 14:03 | 2012-08-15 14:27 | CARRIER - 38BRC042340 | 103 | 7.1 | Yes | Yes | 16 | 18.6 | -2.6 | 8B870227B37A4312BAE17156A696FF08 |  | R22 | Non-TXV |  | 6.893% | 0.93107 | 13.25% | [5 empty] | Non-TXV | 6.893%
Stockton | CA | 95219-3579 |  | 2012-07-09 | 2012-07-09 14:06 | 2012-07-09 14:25 | DAY & NIGHT - UNK | 96 | 5.7 | Yes | Yes | 24.3 | 19.9 | 4.4 | D82C915C58A44A8385895CF3C3B604C5 |  | R22 | Non-TXV |  | 5.938% | 0.94063 | 11.41% | [5 empty] | Non-TXV | 5.938%
Merced | CA | 95348-3034 |  | 2012-08-10 | 2012-08-10 14:39 | 2012-08-10 14:57 | TRANE - TTR024C100A | 73 | -4.3 | Yes | Yes | 19.1 | 16.6 | 2.6 | E60DC768AF8A4E2085B257D2BDD60CDA |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Merced | CA | 95348-3712 |  | 2012-08-02 | 2012-08-02 11:20 | 2012-08-02 11:50 | TRANE - 2TTR20301A00A | 77 | 3.3 | Yes | Yes | 18.9 | 20.4 | -1.5 | 418BA232456D489DA26EB8B700AE4914 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Chico | CA | 95928-6805 |  | 2012-05-08 | 2012-05-08 13:12 | 2012-05-08 13:37 | AMERICAN STANDARD - YCC030F1MOBJ | 75 | 5.4 | Yes | Yes | 19.7 | 22 | -2.3 | BB001D5CE90E4EA28117740DC1DF2487 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.2% | 0.928 | 13.84% | [5 empty] | Non-TXV | 7.2%
Stockton | CA | 95210-1790 |  | 2012-05-29 | 2012-05-29 14:19 | 2012-05-29 14:40 | OTHER - 60WE2461 | 51 | 9.5 | Yes | Yes | 21.4 | 21.2 | 0.2 | 53DC3982A7BC41B5B75EACA432DF33C1 |  | R22 | Non-TXV |  | 18.63% | 0.81373 | 35.8% | [5 empty] | Non-TXV | 18.63%
Stockton | CA | 95206-2818 |  | 2012-08-13 | 2012-08-13 10:52 | 2012-08-13 11:14 | BRYANT - 561CJ048-A | 100 | -8.7 | Yes | Yes | 24.1 | 20.2 | 3.9 | B101A1E7AAFA470CA3BC9BEA2280C640 |  | R22 | Non-TXV |  | -8.7% | 1.087 | 2.436% |  |  |  |  | Non-TXV |  |  | -8.7%
Gustine | CA | 95322-9504 |  | 2012-05-15 | 2012-05-15 15:19 | 2012-05-15 15:41 | YORK - SHP48-6A | 72 | 9.4 | Yes | Yes | 20 | 21 | -1 | EB09981C62514D0EA672D09EACF75C6D |  | R22 | Non-TXV |  | 13.06% | 0.86944 | 25.09% | [5 empty] | Non-TXV | 13.06%
Stockton | CA | 95204-2825 |  | 2012-05-11 | 2012-05-11 16:02 | 2012-05-11 16:32 | OTHER - UNK | 67 | 8.9 | Yes | Yes | 15.9 | 17.2 | -1.3 | 49359C838E494A4589F19B0D3BB9907B |  | R22 | Non-TXV |  | 13.28% | 0.86716 | 25.53% | [5 empty] | Non-TXV | 13.28%
Los Banos | CA | 93635-3316 |  | 2012-08-06 | 2012-08-06 10:46 | 2012-08-06 11:06 | ARCOAIRE - PGND30G0752 | 75 | 3.7 | Yes | Yes | 22.3 | 20.7 | 1.6 | F238205AC7F3400FA8542AC4A675F361 |  | R22 | Non-TXV |  | 4.933% | 0.95067 | 9.481% | [5 empty] | Non-TXV | 4.933%
Durham | CA | 95938-9518 |  | 2012-08-09 | 2012-08-09 09:52 | 2012-08-09 10:41 | YORK - HDH060S06A | 114 | 15.9 | Yes | Yes | 35 | 20.4 | 14.6 | F10FC90A9F944C4EB4CBE1169AB78822 |  | R22 | Non-TXV |  | 13.95% | 0.86053 | 26.8% | [5 empty] | Non-TXV | 13.95%
Stockton | CA | 95210-3225 |  | 2012-08-01 | 2012-08-01 11:11 | 2012-08-01 11:31 | YORK - AC036X1021A | 63 | -3.7 | Yes | Yes | 22.1 | 18.9 | 3.2 | E97E82C2E33D479E940A1278A12F56BF |  | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Dos Palos | CA | 93620-9012 |  | 2012-08-01 | 2012-08-01 13:42 | 2012-08-01 14:05 | GIBSON - JS3BC-036KA | 82 | 2.5 | Yes | Yes | 16.8 | 19.3 | -2.5 | 120C0F3E8FBC4826883F531A2FD09A96 |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Merced | CA | 95341-6607 |  | 2012-08-07 | 2012-08-07 11:58 | 2012-08-07 12:18 | DAY & NIGHT - 588ANW036060ACAF | 66 | 2 | Yes | Yes | 15.4 | 17 | -1.6 | 1E37524B89D94163BF7C28DCA0E48DF0 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Stockton | CA | 95203-3026 |  | 2012-05-10 | 2012-05-10 16:55 | 2012-05-11 01:40 | GOODMAN - CK36-10 | 72 | 6.4 | Yes | Yes | 17 | 19.1 | -2.1 | 7C34BD2DBB504417AB6F9CFE1036B57A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.889% | 0.91111 | 17.08% | [5 empty] | Non-TXV | 8.889%
Stockton | CA | 95209-2807 |  | 2012-08-08 | 2012-08-08 12:00 | 2012-08-08 12:20 | CARRIER - 38TXA36330 | 105 | -4.9 | Yes | Yes | 22.8 | 18.6 | 4.2 | 6B364283C94643EA96CAFE6BD287F084 |  | R22 | TXV |  | -4.667% | 1.0467 | 1.307% |  |  |  |  | TXV |  |  | -4.667%
Stockton | CA | 95210-2017 |  | 2012-07-31 | 2012-07-31 11:40 | 2012-07-31 11:57 | PAYNE - PA10JA030-C | 66 | 2.3 | Yes | Yes | 22.8 | 20.4 | 2.4 | AFCB542C11CC4C6FAEE75E673AF23F33 |  | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Merced | CA | 95348-1563 |  | 2012-08-10 | 2012-08-10 08:23 | 2012-08-10 08:41 | TRANE - YCC030F1M0BC | 85 | 3.4 | Yes | Yes | 18.3 | 20.4 | -2.1 | 5349EA114A9C4F4BB931964B1594C24F |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Merced | CA | 95348-2802 |  | 2012-08-02 | 2012-08-02 15:34 | 2012-08-02 16:12 | OTHER - UNK | 62 | 4.5 | Yes | Yes | 20.7 | 21.9 | -1.2 | 7005706D05B448CFB94A9768870FD7FA |  | R22 | Non-TXV |  | 7.258% | 0.92742 | 13.95% | [5 empty] | Non-TXV | 7.258%
Stockton | CA | 95210-5239 |  | 2012-08-01 | 2012-08-01 13:42 | 2012-08-01 14:00 | CARRIER - UNK | 102 | 3.4 | Yes | Yes | 22.1 | 20.4 | 1.7 | 18C3D6198B814716B9FC2EF5F69CC0DA |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Merced | CA | 95348-9281 |  | 2012-08-06 | 2012-08-06 12:29 | 2012-08-06 13:37 | PAYNE - PY3PNA042060NB | 124 | 8.6 | Yes | Yes | 18.6 | 18.7 | 0 | DFFE6716ACB245749AA9806D8E400D57 |  | R22 | Non-TXV |  | 6.935% | 0.93065 | 13.33% | [5 empty] | Non-TXV | 6.935%
Fresno | CA | 93722-1159 |  | 2012-05-14 | 2012-05-14 10:34 | 2012-05-14 10:54 | RHEEM - RAKA-048JAZ | 103 | 3.1 | Yes | Yes | 22.7 | 19.5 | 3.2 | 70F2CA3C22FD4F808048ACA580DDCBDC |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Manteca | CA | 95337-4377 |  | 2012-05-09 | 2012-05-09 14:38 | 2012-05-09 15:14 | CARRIER - 38EN024300 | 56 | 24.1 | Yes | Yes | 24.3 | 19.8 | 4.5 | 82326ABF6B0F4D11A52EA56938672C29 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 43.04% | 0.56964 | 82.71% | [5 empty] | Non-TXV | 43.04%
Stockton | CA | 95219-7179 |  | 2012-08-15 | 2012-08-15 14:04 | 2012-08-15 14:04 | GOODMAN - CLJ48-1A | 130 | 0 | Yes | Yes | 18.7 | 20.7 | -2 | 0DB1AEF54B1E4DF1AAA30B88FC69D5C1 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2223 |  | 2012-08-01 | 2012-08-01 11:44 | 2012-08-01 12:03 | GOODMAN - CL030-1B | 131 | -15.1 | Yes | Yes | 16.7 | 18.4 | -1.7 | FFD9D54C4CDB43D794299A8E00363476 |  | R22 | TXV |  | -11.53% | 1.1153 | 3.228% |  |  |  |  | TXV |  |  | -11.53%
Los Banos | CA | 93635-5479 |  | 2012-07-23 | 2012-07-23 11:07 | 2012-07-23 11:29 | YORK - H2RA036S06E | 63 | 1.9 | Yes | Yes | 21.1 | 20.4 | 0.7 | 7E48998D6D924294B4E1A4FA8C190A24 |  | R22 | Non-TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | Non-TXV | 3.016%
Selma | CA | 93662-3147 |  | 2012-05-18 | 2012-05-18 14:10 | 2012-05-18 14:27 | UPG - TCJD30S41S3HA | 63 | -3.5 | Yes | Yes | 21.5 | 19.9 | 1.6 | 895A51B063114A8A91A1A8658FCC2559 | OK: Verified Refrigerant Charge | R410A | TXV |  | -5.556% | 1.0556 | 1.556% |  |  |  |  | TXV |  |  | -5.556%
Merced | CA | 95348-3525 |  | 2012-08-02 | 2012-08-02 10:14 | 2012-08-02 10:34 | YORK - D1NP030N056A | 74 | 3.2 | Yes | Yes | 19.3 | 20.4 | -1.1 | 101CF6DF68F84FAD93FA6C6AD1B3765D |  | R22 | Non-TXV |  | 4.324% | 0.95676 | 8.31% | [5 empty] | Non-TXV | 4.324%
Manteca | CA | 95337-8103 |  | 2012-05-15 | 2012-05-15 15:16 | 2012-05-15 15:34 | RHEEM - RRNA-B036JK06X | 84 | 3.4 | Yes | Yes | 27 | 21 | 6 | 6A7C100A164646B1997C2C93BB9CC960 |  | R22 | Non-TXV |  | 4.048% | 0.95952 | 7.779% | [5 empty] | Non-TXV | 4.048%
Yuba City | CA | 95991-3815 |  | 2012-06-11 | 2012-06-11 15:03 | 2012-06-11 15:24 | LENNOX - HS26-042-6P | 101 | -10.3 | Yes | Yes | 22 | 24.2 | -2.2 | CABB4FF33EF84495A2930B35EF65B86B |  | R22 | TXV |  | -10.2% | 1.102 | 2.856% |  |  |  |  | TXV |  |  | -10.2%
Yuba City | CA | 95991-2805 |  | 2012-08-10 | 2012-08-10 10:29 | 2012-08-10 10:29 | GOODMAN - GPG13480901AC | 134 | 0 | Yes | Yes | 25.9 | 20.5 | 5.5 | 6E92F85AD0E94908AD7E40B00C87690C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2116 |  | 2012-05-23 | 2012-05-23 13:00 | 2012-05-23 13:18 | GOODMAN - GPG1336070M41AA | 85 | -5 | Yes | Yes | 25.4 | 20.2 | 5.2 | E081219E6643437A8C6CC8AE0A119BA4 |  | R410A | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95204-1309 |  | 2012-05-07 | 2012-05-07 11:20 | 2012-05-07 11:20 | UNK - 563CN048-A | 165 | 0 | Yes | Yes | 6.1 | 15.2 | -9.1 | C0B1DEE3D1554674B7BBE055D0FE36C1 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-2315 |  | 2012-05-31 | 2012-05-31 09:08 | 2012-05-31 09:27 | OTHER - NA | 48 | 1.4 | Yes | Yes | 18.4 | 19.6 | -1.2 | 01D2B464EB564FE9B7E32234DA3BD6E8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.917% | 0.97083 | 5.605% | [5 empty] | Non-TXV | 2.917%
Stockton | CA | 95209-3747 |  | 2012-08-01 | 2012-08-01 12:48 | 2012-08-01 13:04 | PAYNE - 5C1CJ036-C | 72 | 12.6 | Yes | Yes | 23.3 | 20.8 | 2.5 | 29D39A30826B42D6A60F9934B3DC74EA |  | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Orland | CA | 95963-1723 |  | 2012-05-17 | 2012-05-17 13:15 | 2012-05-17 13:38 | PAYNE - PA 13 NA 03000O ABA | 76 | 2.6 | Yes | Yes | 23.8 | 22.1 | 1.7 | E9F8D40B692B4B2C97893668F2E8DDB9 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Stockton | CA | 95206-0000 |  | 2012-05-07 | 2012-05-07 12:04 | 2012-05-07 12:26 | PAYNE - PA13NRO24000AHAA | 72 | -7.7 | Yes | Yes | 21 | 21 | 0 | 861ED501AEFA4E46B4FC623CDF4C8AF0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -10.69% | 1.1069 | 2.995% |  |  |  |  | Non-TXV |  |  | -10.69%
Stockton | CA | 95206-0000 |  | 2012-05-07 | 2012-05-07 13:09 | 2012-05-07 13:32 | PAYNE - PA13NR024-4 | 72 | -13 | Yes | Yes | 17.8 | 15.9 | 1.9 | 1CA2974E1315429E834DD4AFB1675BDD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -18.06% | 1.1806 | 5.056% |  |  |  |  | Non-TXV |  |  | -18.06%
Yuba City | CA | 95991-2817 |  | 2012-06-11 | 2012-06-11 15:31 | 2012-06-11 15:49 | LENNOX - HS19-411V-2P | 111 | -25.1 | Yes | Yes | 25.7 | 20.4 | 5.3 | A526B296D50D4F35AA1EBD2519991997 |  | R22 | TXV |  | -22.61% | 1.2261 | 6.333% |  |  |  |  | TXV |  |  | -22.61%
Fresno | CA | 93722-7357 |  | 2012-06-06 | 2012-06-06 13:11 | 2012-06-06 13:28 | LENNOX - 12GCS036-75-3PB | 110 | 3.3 | Yes | Yes | 26.3 | 21 | 5.3 | 66023C638EB049CD9FDC2F3C230C1D10 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93726-0409 |  | 2012-05-10 | 2012-05-10 13:19 | 2012-05-10 13:40 | AMERICAN STANDARD - YCY042F1MOAA | 88 | 2.5 | Yes | Yes | 28 | 22.6 | 5.4 | 6E83B364A9AE4DD487288A5A120F68CE | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.841% | 0.97159 | 5.46% | [5 empty] | Non-TXV | 2.841%
Stockton | CA | 95207-7434 |  | 2012-05-30 | 2012-05-30 14:15 | 2012-05-30 14:35 | OTHER - UNK | 97 | 23.3 | Yes | Yes | 25.9 | 22.6 | 3.3 | E7D07EB2C0C948F5A638543F2EF45EEE |  | R22 | Non-TXV |  | 24.02% | 0.75979 | 46.16% | [5 empty] | Non-TXV | 24.02%
Atwater | CA | 95301-4869 |  | 2012-06-12 | 2012-06-12 12:07 | 2012-06-12 12:23 | OTHER - GCGD30S21S2A | 55 | 2.4 | Yes | Yes | 19.7 | 20.9 | -1.2 | D75509357BE14B5D8E8FA379B39FAF82 |  | R22 | Non-TXV |  | 4.364% | 0.95636 | 8.386% | [5 empty] | Non-TXV | 4.364%
Yuba City | CA | 95991-6756 |  | 2012-06-15 | 2012-06-15 15:55 | 2012-06-15 19:03 | YORK - 45DBO48506A | 96 | 4.8 | Yes | Yes | 24 | 20.4 | 3.6 | F020C1F9426447C89089C7CCC4620237 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Los Banos | CA | 93635-3036 |  | 2012-08-01 | 2012-08-01 10:38 | 2012-08-01 10:59 | ALLEGIANCE - 7A2030A100A2 | 85 | 13.7 | Yes | Yes | 24.4 | 26.5 | -2.1 | EB2309BBDFDC447F914B837B201E35E1 |  | R22 | Non-TXV |  | 16.12% | 0.83882 | 30.97% | [5 empty] | Non-TXV | 16.12%
Stockton | CA | 95219-7195 |  | 2012-08-15 | 2012-08-15 14:32 | 2012-08-15 14:32 | RUUD - RAMC-036JBZ | 93 | 0 | Yes | Yes | 24 | 19.8 | 4.3 | CFDD685614ED41738AE0A5989A65C560 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3719 |  | 2012-08-15 | 2012-08-15 13:31 | 2012-08-15 13:47 | CARRIER - 48GS-036060311 | 69 | 6.2 | Yes | Yes | 17.4 | 18.8 | -1.4 | 34519DD64311452EB3B752774504C1C4 |  | R22 | Non-TXV |  | 8.986% | 0.91014 | 17.27% | [5 empty] | Non-TXV | 8.986%
Atwater | CA | 95301-0000 |  | 2012-06-01 | 2012-06-01 09:10 | 2012-06-01 09:36 | RHEEM - NA | 71 | 2.1 | Yes | Yes | 19.6 | 18.1 | 1.5 | A013DE85C2C94D6DB2160CF97E8B2139 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.958% | 0.97042 | 5.684% | [5 empty] | Non-TXV | 2.958%
Stockton | CA | 95219-3726 |  | 2012-08-15 | 2012-08-15 11:16 | 2012-08-15 11:33 | DAY & NIGHT - 561AJ036-B | 73 | 12.8 | Yes | Yes | 17.6 | 18.3 | -0.7 | 0D47F6EDF094497B9CDF9D5EC30AB4F9 |  | R22 | Non-TXV |  | 17.53% | 0.82466 | 33.7% | [5 empty] | Non-TXV | 17.53%
Stockton | CA | 95206-6251 |  | 2012-08-16 | 2012-08-16 15:37 | 2012-08-16 15:37 | GOODMAN - CKJ30-1D | 85 | 0 | Yes | Yes | 22.2 | 19.7 | 2.5 | 9D1C1EDC4C8C45B38EC59903584360CA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4866 |  | 2012-05-14 | 2012-05-14 10:43 | 2012-05-14 11:01 | LENNOX - HSO-3113P | 78 | 2.3 | Yes | Yes | 22.9 | 19.8 | 3.1 | 0080165F541344D791CFEC5685B297FC | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Corning | CA | 96021-3633 |  | 2012-08-08 | 2012-08-08 12:22 | 2012-08-08 17:56 | GOODMAN - CKL36-1H | 71 | 2.4 | Yes | Yes | 22.5 | 21.5 | 1 | 39013DA0F2F942DA98C0436ABE25CEDA |  | R22 | Non-TXV |  | 3.38% | 0.9662 | 6.496% | [5 empty] | Non-TXV | 3.38%
Manteca | CA | 95336-3353 |  | 2012-05-16 | 2012-05-16 10:18 | 2012-05-16 10:47 | GOODMAN - CKL24-1F | 72 | -6.8 | Yes | Yes | 20.4 | 19.8 | 0.6 | B779574B0B254321B09B02825A18F05F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Oakdale | CA | 95361-3360 |  | 2012-05-23 | 2012-05-23 13:15 | 2012-05-23 13:41 | PAYNE - PA13NR030-H | 65 | 8.3 | Yes | Yes | 20.1 | 21.3 | -1.2 | 4A2653668A94486090195C86B0449E72 |  | R22 | Non-TXV |  | 12.77% | 0.87231 | 24.54% | [5 empty] | Non-TXV | 12.77%
Fresno | CA | 93711-0853 |  | 2012-05-30 | 2012-05-30 15:31 | 2012-05-30 15:50 | OTHER - 587ANZ042060 | 85 | 4.6 | Yes | Yes | 23 | 19.7 | 3.3 | E57DFFB5A3404F46AA8852ECDD108B39 |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Stockton | CA | 95204-1320 |  | 2012-07-31 | 2012-07-31 16:38 | 2012-07-31 17:13 | RUUD - 13AJA36A01 | 108 | 5.2 | Yes | Yes | 21.5 | 19 | 2.6 | 1434A5E50CBD41778308AE3E2052243F |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Stockton | CA | 95206-4725 |  | 2012-05-24 | 2012-05-24 13:31 | 2012-05-24 13:54 | RHEEM - RAHE-042JAS | 101 | 5.1 | Yes | Yes | 19.2 | 20.9 | -1.7 | C99791ADFFF9417EA50377DD3F63FA5A |  | R22 | Non-TXV |  | 5.05% | 0.9495 | 9.704% | [5 empty] | Non-TXV | 5.05%
Stockton | CA | 95210-6719 |  | 2012-08-08 | 2012-08-08 08:28 | 2012-08-08 08:51 | RHEEM - RAND-036JAZ | 116 | -6.8 | Yes | Yes | 19.9 | 19.4 | 0.5 | 4A4B01857B074FBEBFB258901AC4A5EA |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Stockton | CA | 95209-5035 |  | 2012-08-01 | 2012-08-01 15:34 | 2012-08-01 15:54 | DAY & NIGHT - 567G042 | 94 | 3.5 | Yes | Yes | 20 | 20.6 | -0.6 | 5D7B3089464B4AF6A18E8C4ED218335A |  | R22 | Non-TXV |  | 3.723% | 0.96277 | 7.156% | [5 empty] | Non-TXV | 3.723%
Yuba City | CA | 95991-4824 |  | 2012-06-13 | 2012-06-13 12:29 | 2012-06-13 12:49 | OTHER - UNK | 90 | 7.5 | Yes | Yes | 25 | 20.4 | 4.6 | ECA49113558E4245A80A5657812B6EDC |  | R22 | Non-TXV |  | 8.333% | 0.91667 | 16.01% | [5 empty] | Non-TXV | 8.333%
Yuba City | CA | 95993-9285 |  | 2012-08-16 | 2012-08-16 09:27 | 2012-08-16 09:47 | CARRIER - 38CKC036350 | 75 | 2.2 | Yes | Yes | 16 | 18.8 | -2.8 | 390BE29D114545138D80D9D4A194BCAE |  | R22 | Non-TXV |  | 2.933% | 0.97067 | 5.637% | [5 empty] | Non-TXV | 2.933%
Stockton | CA | 95219-4956 |  | 2012-07-05 | 2012-07-05 14:38 | 2012-07-05 14:57 | PAYNE - 561CJ042-A | 80 | 4 | Yes | Yes | 18.7 | 20.4 | -1.7 | 12795C79B9F44F339129EE6CDF6CBA44 |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Stockton | CA | 95205-7221 |  | 2012-05-16 | 2012-05-16 16:01 | 2012-05-16 16:28 | CARRIER - 38CKC042300 | 80 | 5.2 | Yes | Yes | 21.2 | 20.1 | 1.1 | 18C9CA703C4D478FB03B65E285CD831D | OK: Verified Refrigerant Charge | R22 | TXV |  | 6.5% | 0.935 | 12.49% | [5 empty] | TXV | 6.5%
Stockton | CA | 95205-3349 |  | 2012-08-14 | 2012-08-14 14:09 | 2012-08-14 14:09 | PAYNE - PA13NR03600ACAA | 128 | 0 | Yes | Yes | 23.2 | 20.4 | 2.8 | A6AD08D2B4784B4E9FD5627F8FD9DC20 |  | R22 | TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-4441 |  | 2012-05-09 | 2012-05-09 10:41 | 2012-05-09 10:59 | FRAISER JOHNSTON - N/A | 64 | 1.9 | Yes | Yes | 23.2 | 21.5 | 1.7 | FC32834A45C34940AE02755D6AA8A70A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Los Banos | CA | 93635-5412 |  | 2012-05-16 | 2012-05-16 14:54 | 2012-05-16 15:18 | PAYNE - N/A | 70 | -4.1 | Yes | Yes | 19 | 21.2 | -2.2 | 8EEF158868F94109A7DC4AC9A4FAE23B |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Stockton | CA | 95219-3121 |  | 2012-08-14 | 2012-08-14 08:50 | 2012-08-14 09:07 | DAY & NIGHT - 3URCU108L | 66 | 7.7 | Yes | Yes | 23.8 | 19.4 | 4.4 | F79386CB5CE344AD96073F163FFD8B70 |  | R22 | Non-TXV |  | 11.67% | 0.88333 | 22.42% | [5 empty] | Non-TXV | 11.67%
Tracy | CA | 95376-1743 |  | 2012-08-03 | 2012-08-03 11:19 | 2012-08-03 11:41 | CARRIER - 38EB036310 | 117 | 47.8 | Yes | Yes | 17.6 | 18.6 | -1 | 15F7AEE74164429CB8E147BEE162F736 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 40.85% | 0.59145 | 78.51% | [5 empty] | Non-TXV | 40.85%
Los Banos | CA | 93635-5412 |  | 2012-05-22 | 2012-05-22 09:42 | 2012-05-22 10:04 | PAYNE - UNK | 83 | 12.1 | Yes | Yes | 16.9 | 19.7 | -2.8 | 4197D467968B4CE7A6CFF17BF988A7D9 |  | R22 | Non-TXV |  | 14.58% | 0.85422 | 28.02% | [5 empty] | Non-TXV | 14.58%
Stockton | CA | 95210-1155 |  | 2012-08-01 | 2012-08-01 08:53 | 2012-08-01 09:09 | AMANA - PGB36B0702A | 117 | -6.9 | Yes | Yes | 24.2 | 18.2 | 6 | 45D6571E70F841EAA23D5DD68B045244 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Merced | CA | 95348-9239 |  | 2012-08-13 | 2012-08-13 09:34 | 2012-08-13 10:04 | TRANE - YCC048F1MOBG | 108 | 5 | Yes | Yes | 19.3 | 20.1 | -0.8 | B4BFD907627A4560A76B16EA9D488F4C |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Stockton | CA | 95209-3900 |  | 2012-08-01 | 2012-08-01 14:58 | 2012-08-01 15:16 | YORK - HRC024S06A | 76 | 4.2 | Yes | Yes | 24.6 | 22.1 | 2.5 | 6EFC637DE6444AFDB8C3F3D8F6D6F90A |  | R22 | Non-TXV |  | 5.526% | 0.94474 | 10.62% | [5 empty] | Non-TXV | 5.526%
Stockton | CA | 95204-2214 |  | 2012-05-07 | 2012-05-07 15:41 | 2012-05-07 16:08 | RHEEM - RRKA-A024JK06X | 51 | 1.7 | Yes | Yes | 5.4 | 18.7 | -13.3 | 9438B612E23D42FDA017E127A8752C1D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95205-7116 |  | 2012-06-07 | 2012-06-07 17:21 | 2012-06-07 17:49 | DAY & NIGHT - UNK | 53 | 3.1 | Yes | Yes | 21.2 | 21.5 | -0.3 | D19CDEDC962040DBB7A7DD4A75289A7C |  | R22 | Non-TXV |  | 5.849% | 0.94151 | 11.24% | [5 empty] | Non-TXV | 5.849%
Rocklin | CA | 95765-5207 |  | 2012-07-31 | 2012-07-31 16:42 | 2012-07-31 16:42 | OTHER - AC18N060-A | 184 | 0 | Yes | Yes | 0 | 19.5 | -19.5 | 710370A427954816B0BC12C0317F958E | Final Suction Temperature must be between 20°F and 80°F. Please check entries. Final Suction pressure must be between 43 psig and 100 psig. Please check entries. Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Condenser saturation temperature cannot be less then outdoor air temperature plus 5°F or greater than outdoor air temperature plus 60°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95203-2313 |  | 2012-05-10 | 2012-05-10 15:25 | 2012-05-10 15:47 | TRANE - TTD730B100A1 | 69 | -6.5 | Yes | Yes | 24.1 | 19 | 5.1 | B2391B6FD0EA4D68BD0766CC7335AD9E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -9.42% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.42%
Chico | CA | 95926-3609 |  | 2012-05-16 | 2012-05-16 15:07 | 2012-05-16 15:34 | UNK - 561AJO24-B | 59 | 5.1 | Yes | Yes | 16.1 | 16.1 | 0 | 7A6FBC5387984F0EA4A6625F3F287F9E |  | R22 | Non-TXV |  | 8.644% | 0.91356 | 16.61% | [5 empty] | Non-TXV | 8.644%
Auburn | CA | 95602-8005 |  | 2012-07-31 | 2012-07-31 09:37 | 2012-07-31 09:58 | YORK - H1DH030S06 | 122 | -8.6 | Yes | Yes | 25.5 | 19.5 | 6 | CEA9BC846ED14D599FD7F4F4292730BD |  | R22 | Non-TXV |  | -7.049% | 1.0705 | 1.974% |  |  |  |  | Non-TXV |  |  | -7.049%
Lincoln | CA | 95648-3246 |  | 2012-08-01 | 2012-08-01 16:26 | 2012-08-01 16:26 | CARRIER - 24ABA336A310 | 84 | 0 | Yes | Yes | 19.1 | 20.4 | -1.3 | F3820485A9A24F2B94B6ABE41C5AC7C6 |  | R410A | TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3765 |  | 2012-08-02 | 2012-08-02 12:08 | 2012-08-02 13:06 | YORK - D1NA042N5606C | 76 | 4.4 | Yes | Yes | 20 | 20.7 | -0.7 | 045D7E68F6BA41229E4051FBAA2417FC |  | R22 | Non-TXV |  | 5.789% | 0.94211 | 11.13% | [5 empty] | Non-TXV | 5.789%
Atwater | CA | 95301-2115 |  | 2012-08-07 | 2012-08-07 14:11 | 2012-08-07 14:28 | CARRIER - 48GP-048090311 | 149 | -5.4 | Yes | Yes | 23.4 | 21.2 | 2.2 | 606C3493F2834985981550A8E5CA9FAF |  | R410A | TXV |  | -3.624% | 1.0362 | 1.015% |  |  |  |  | TXV |  |  | -3.624%
Merced | CA | 95340-2339 |  | 2012-07-31 | 2012-07-31 12:02 | 2012-07-31 12:39 | AMERICAN STANDARD - YCC030F1MOBB | 69 | 2.2 | Yes | Yes | 21.6 | 20 | 1.6 | 3038CC56D9EF4393B5860D8419B812DB |  | R22 | Non-TXV |  | 3.188% | 0.96812 | 6.127% | [5 empty] | Non-TXV | 3.188%
Rocklin | CA | 95677-3520 |  | 2012-05-29 | 2012-05-29 12:43 | 2012-05-29 13:02 | CARRIER - 38EN018310 | 59 | 3.1 | Yes | Yes | 22.7 | 20.1 | 2.7 | 957838E957AE4D8F81AFB2EACA0258CA | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.254% | 0.94746 | 10.1% | [5 empty] | Non-TXV | 5.254%
Winton | CA | 95388-0000 |  | 2012-08-01 | 2012-08-01 12:07 | 2012-08-01 12:31 | OTHER - 024360901 | 67 | 6.2 | Yes | Yes | 19.4 | 20.4 | -1 | 8F26D7796746466186A0B56A87A7FE0C |  | R22 | Non-TXV |  | 9.254% | 0.90746 | 17.78% | [5 empty] | Non-TXV | 9.254%
Tracy | CA | 95377-8724 |  | 2012-08-14 | 2012-08-14 08:43 | 2012-08-14 09:00 | CARRIER - 38CKC060300 | 158 | -11.2 | Yes | Yes | 18.2 | 19.7 | -1.5 | 2B5F80B53E5C4CA2AE8513642B333262 |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Stockton | CA | 95206-2965 |  | 2012-05-22 | 2012-05-22 13:38 | 2012-05-22 13:38 | RHEEM - RRNL-B024JK06X | 78 | 0 | Yes | Yes | 21 | 19.9 | 1.1 | 5EA59EE2AA1D4A228EE8751352A945F7 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9689 |  | 2012-08-09 | 2012-08-09 10:48 | 2012-08-09 11:06 | GOODMAN - GSH130361AC | 188 | 5.8 | Yes | Yes | 20.4 | 20.1 | 0.3 | 7F6A271D20664B399B98BD943D5E78D0 |  | R22 | Non-TXV |  | 3.085% | 0.96915 | 5.929% | [5 empty] | Non-TXV | 3.085%
Livingston | CA | 95334-1729 |  | 2012-08-01 | 2012-08-01 10:00 | 2012-08-01 10:26 | ARCOAIRE - PGAD030D1K5 | 77 | 3.2 | Yes | Yes | 18.7 | 20.9 | -2.2 | 4D163933E2D4415EA4B872AB0A4A1066 |  | R22 | Non-TXV |  | 4.156% | 0.95844 | 7.987% | [5 empty] | Non-TXV | 4.156%
Stockton | CA | 95210-1160 |  | 2012-08-01 | 2012-08-01 09:48 | 2012-08-01 10:04 | DAY & NIGHT - UNK | 58 | -3.4 | Yes | Yes | 20.9 | 18.3 | 2.6 | 7FBAC268CCC94D4A864C2A52D6F315C6 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Rocklin | CA | 95677-1519 |  | 2012-07-31 | 2012-07-31 13:54 | 2012-07-31 13:54 | ICP - CAC248AKC3 | 147 | 0 | Yes | Yes | 22.5 | 19.3 | 3.2 | 35E8297A3A4F4FBD926956FA8F372C46 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-9741 |  | 2012-08-15 | 2012-08-15 12:30 | 2012-08-15 12:49 | YORK - D1NH036N05606C | 108 | 4.6 | Yes | Yes | 20.2 | 20.8 | -0.6 | 908D120EED5E4F9AAA78E0212608B86B |  | R22 | Non-TXV |  | 4.259% | 0.95741 | 8.185% | [5 empty] | Non-TXV | 4.259%
Fresno | CA | 93726-5133 |  | 2012-05-22 | 2012-05-22 14:44 | 2012-05-22 15:06 | CARRIER - 48NMT036---321BE | 85 | 2.6 | Yes | Yes | 23.1 | 19.7 | 3.4 | 0637255587A74CB68554AEF44569020D |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Merced | CA | 95341-9054 |  | 2012-05-11 | 2012-05-11 10:59 | 2012-05-11 11:39 | COLEMAN - BRCS0481BDG | 117 | 4.4 | Yes | Yes | 25.7 | 20.9 | 4.8 | 280E2B91253A4DBBA555E65136318780 | OK: Verified Refrigerant Charge. |  |  |  | 3.761% | 0.96239 | 7.227% | [5 empty] | 0 | 3.761%
Tracy | CA | 95377-1166 |  | 2012-08-14 | 2012-08-14 14:19 | 2012-08-14 14:36 | CARRIER - 38BRC060360 | 206 | 6.3 | Yes | Yes | 23.3 | 21 | 2.3 | A1259C58D1344C068E1905D2FC005D72 |  | R22 | Non-TXV |  | 3.058% | 0.96942 | 5.877% | [5 empty] | Non-TXV | 3.058%
Los Banos | CA | 93635-2628 |  | 2012-08-01 | 2012-08-01 09:55 | 2012-08-01 10:17 | GOODMAN - CK36-1C | 80 | 3.3 | Yes | Yes | 24.2 | 21 | 3.2 | 7099282521B84469AC71386B34E5A102 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.125% | 0.95875 | 7.927% | [5 empty] | Non-TXV | 4.125%
Los Banos | CA | 93635-3012 |  | 2012-08-01 | 2012-08-01 08:50 | 2012-08-01 09:13 | YORK - H4DB036S06A | 73 | 9.7 | Yes | Yes | 19.6 | 18.1 | 1.5 | E1AFCB2B145442B7ADD07B60C4D48348 |  | R22 | Non-TXV |  | 13.29% | 0.86712 | 25.54% | [5 empty] | Non-TXV | 13.29%
Fresno | CA | 93710-7015 |  | 2012-05-24 | 2012-05-24 11:42 | 2012-05-24 12:01 | CARRIER - 48SS-036080321 | 67 | 2 | Yes | Yes | 25.1 | 20.7 | 4.4 | 1484EC0444AD4787B7723A15C23AAF2B |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Merced | CA | 95340-6982 |  | 2012-08-06 | 2012-08-06 11:05 | 2012-08-06 11:25 | BRYANT - 582ANW042060NAAG | 100 | 13.1 | Yes | Yes | 22.1 | 20.4 | 1.7 | E38CD95873B84EC0B3459EBD069FD6A9 |  | R22 | Non-TXV |  | 13.1% | 0.869 | 25.18% | [5 empty] | Non-TXV | 13.1%
Rocklin | CA | 95677-3627 |  | 2012-07-31 | 2012-07-31 17:28 | 2012-07-31 17:28 | CARRIER - 25HCR330A300 | 120 | 0 | Yes | Yes | 18.9 | 20.8 | -1.9 | 31CF1587DFDE4A19957EB3E6F18A5BCD |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-4027 |  | 2012-05-21 | 2012-05-21 14:15 | 2012-05-21 14:32 | PAYNE - AC042X1021A | 84 | 12.3 | Yes | Yes | 20.8 | 21 | -0.2 | ED7A8ABC0B79408CA9F2CCF7E0615A9D |  | R22 | Non-TXV |  | 14.64% | 0.85357 | 28.14% | [5 empty] | Non-TXV | 14.64%
Fresno | CA | 93725-1105 |  | 2012-05-10 | 2012-05-10 19:03 | 2012-05-10 19:32 | BDP COMPANY - 595A030080YACR | 85 | 14.4 | Yes | Yes | 6.9 | 23 | -16.1 | 1DF55717D1A041C69E67AF4435D65F61 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.94% | 0.83059 | 32.56% | [5 empty] | Non-TXV | 16.94%
Merced | CA | 95340-2322 |  | 2012-08-02 | 2012-08-02 11:02 | 2012-08-02 11:25 | OTHER - 36T94167 | 57 | 5.8 | Yes | Yes | 25.2 | 20.2 | 5 | 8037D627121A44CCBDEB9FB78995F2B7 |  | R22 | Non-TXV |  | 10.18% | 0.89825 | 19.55% | [5 empty] | Non-TXV | 10.18%
Los Banos | CA | 93635-3000 |  | 2012-08-01 | 2012-08-01 14:01 | 2012-08-01 14:01 | DAY & NIGHT - 591ANX042000ABAA | 122 | 0 | Yes | Yes | 29.4 | 19.6 | 9.8 | E3612BF993CC414884140F1C0022BC88 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-3069 |  | 2012-08-07 | 2012-08-07 10:15 | 2012-08-07 11:17 | PAYNE - PY3PNA036060NB | 114 | 4.4 | Yes | Yes | 23 | 21.5 | 1.5 | AD057BCFDAF943C69BD9D00495DAA30E |  | R22 | Non-TXV |  | 3.86% | 0.9614 | 7.417% | [5 empty] | Non-TXV | 3.86%
Stockton | CA | 95210-4314 |  | 2012-05-22 | 2012-05-22 10:00 | 2012-05-22 10:21 | GOODMAN - CKJ18-1D | 84 | -4.9 | Yes | Yes | 16 | 18.8 | -2.8 | 79F1F36256804071AFAF8FFE8A171CA8 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Plumas Lake | CA | 95961-9081 |  | 2012-08-01 | 2012-08-01 12:54 | 2012-08-01 13:15 | CARRIER - 38CKC036350 | 75 | 19.2 | Yes | Yes | 18 | 20.4 | -2.4 | 86D5DB7A09FB47ECBF55F184E6828C94 |  | R22 | Non-TXV |  | 25.6% | 0.744 | 49.2% | [5 empty] | Non-TXV | 25.6%
Fresno | CA | 93722-4117 |  | 2012-05-17 | 2012-05-17 15:27 | 2012-05-17 15:45 | FRASER AD JOHNSON - 80LR30A1NF | 52 | 5.1 | Yes | Yes | 20.1 | 22.6 | -2.5 | 170A496A400D40D19EB4F680122C9981 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.808% | 0.90192 | 18.85% | [5 empty] | Non-TXV | 9.808%
Manteca | CA | 95336-3353 |  | 2012-07-31 | 2012-07-31 10:21 | 2012-07-31 10:21 | YORK - ??10830S06B | 70 | 0 | Yes | Yes | 17.3 | 19.7 | -2.4 | 9D8E9B67D05B49698DB76C111872B755 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-4202 |  | 2012-08-03 | 2012-08-03 09:22 | 2012-08-03 09:51 | PAYNE - PY1PN1303606060ABAA | 68 | 2.1 | Yes | Yes | 19.7 | 20.4 | -0.7 | 35F3A10E2C9043999DE50B4C883A29F3 |  | R22 | Non-TXV |  | 3.088% | 0.96912 | 5.935% | [5 empty] | Non-TXV | 3.088%
Plumas Lake | CA | 95961-8709 |  | 2012-08-15 | 2012-08-15 13:15 | 2012-08-15 13:35 | GOODMAN - CKL36-1L | 84 | 25.2 | Yes | Yes | 20.3 | 19.9 | 0.4 | 9F9FEC74E2F64852AE576644FB8E34D7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 30% | 0.7 | 57.65% | [5 empty] | Non-TXV | 30%
Tracy | CA | 95376-1903 |  | 2012-08-03 | 2012-08-03 11:55 | 2012-08-03 12:23 | LENNOX - 10ACC-036-230-02 | 77 | 14.5 | Yes | Yes | 19.5 | 20.4 | -0.9 | 28B49B1CE8284074A084F92721594DB5 |  | R22 | Non-TXV |  | 18.83% | 0.81169 | 36.19% | [5 empty] | Non-TXV | 18.83%
Fresno | CA | 93706-9356 |  | 2012-06-13 | 2012-06-13 12:15 | 2012-06-13 12:34 | GOODMAN - GPG13420701A | 107 | 3.4 | Yes | Yes | 23.5 | 20.4 | 3.1 | 80FB07675C6446649083998596C8CF72 |  | R22 | Non-TXV |  | 3.178% | 0.96822 | 6.107% | [5 empty] | Non-TXV | 3.178%
Stockton | CA | 95219-3605 |  | 2012-08-15 | 2012-08-15 11:50 | 2012-08-15 12:06 | FRESCHI - 47JQ | 101 | 8.8 | Yes | Yes | 16.9 | 16.7 | 0.3 | D68F58E82FC7482D81CD54C7F2E1E137 |  | R22 | Non-TXV |  | 8.713% | 0.91287 | 16.74% | [5 empty] | Non-TXV | 8.713%
Dos Palos | CA | 93620-9012 |  | 2012-08-01 | 2012-08-01 14:11 | 2012-08-01 15:10 | GIBSON - JS3BC-036KA | 82 | 3.2 | Yes | Yes | 19.6 | 18.3 | 1.3 | 0789311988774417910860F67587A787 |  | R22 | Non-TXV |  | 3.902% | 0.96098 | 7.5% | [5 empty] | Non-TXV | 3.902%
Marysville | CA | 95901-3564 |  | 2012-05-17 | 2012-05-17 11:52 | 2012-05-17 12:10 | OTHER - UNK | 73 | 17 | Yes | Yes | 23.1 | 19.5 | 3.6 | 6B416FCB51EA4444BDB8C24EC1656012 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 23.29% | 0.76712 | 44.75% | [5 empty] | Non-TXV | 23.29%
Durham | CA | 95938-9728 |  | 2012-07-30 | 2012-07-30 16:14 | 2012-07-30 16:32 | OTHER - CKL30-10 | 69 | 3.3 | Yes | Yes | 22.4 | 19.8 | 2.6 | 49E0553998E4438790C2D21D1019951D |  | R22 | Non-TXV |  | 4.783% | 0.95217 | 9.191% | [5 empty] | Non-TXV | 4.783%
Colusa | CA | 95932-2471 |  | 2012-05-24 | 2012-05-24 10:39 | 2012-05-24 11:12 | RHEEM - UNK | 54 | 1.9 | Yes | Yes | 20 | 20.3 | -0.3 | 5165BB2DBEB340A5AEDA56C4266C4F94 |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Chico | CA | 95926-4824 |  | 2012-05-23 | 2012-05-23 10:19 | 2012-05-23 10:50 | DAY N NIGHT - N4H324AKE100 | 105 | 6.2 | Yes | Yes | 20.3 | 22.3 | -2 | 27193347EA0742FE862E660102AD4DAA |  | R410A | TXV |  | 5.905% | 0.94095 | 11.35% | [5 empty] | TXV | 5.905%
Stockton | CA | 95204-4118 |  | 2012-08-02 | 2012-08-02 09:04 | 2012-08-02 09:28 | SEARS - 5017DB3D-22A | 57 | 6 | Yes | Yes | 18.1 | 20.4 | -2.3 | 57B2D272505841AEAA810D5129C799CD |  | R22 | Non-TXV |  | 10.53% | 0.89474 | 20.23% | [5 empty] | Non-TXV | 10.53%
Clovis | CA | 93611-3021 |  | 2012-05-10 | 2012-05-10 11:08 | 2012-05-10 11:26 | BDA - 585HJW03606ABAF | 85 | 2.7 | Yes | Yes | 18.9 | 21.4 | -2.5 | CED59C3B7B3B473789F01946A8E4D103 |  | R22 | Non-TXV |  | 3.176% | 0.96824 | 6.104% | [5 empty] | Non-TXV | 3.176%
Stockton | CA | 95210-2610 |  | 2012-05-24 | 2012-05-24 11:37 | 2012-05-24 11:54 | CARRIER - 593ANX036000ACAA | 76 | -4.5 | Yes | Yes | 25.7 | 19.9 | 5.8 | CB08E28A0C13407D8A014FD4CE0B7922 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Merced | CA | 95341-5788 |  | 2012-06-07 | 2012-06-07 13:53 | 2012-06-07 14:17 | RHEEM - HC-80-24-21C | 49 | -2.9 | Yes | Yes | 21 | 21.4 | -0.4 | 768F7B95F50343E6AE32D82B09C30E48 |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Stockton | CA | 95209-1771 |  | 2012-08-03 | 2012-08-03 10:26 | 2012-08-03 10:43 | PAYNE - 561CJ036-F | 70 | 10 | Yes | Yes | 15.8 | 17.7 | -1.9 | C2887292D6904B018102DD0B27A7A53A |  | R22 | Non-TXV |  | 14.29% | 0.85714 | 27.45% | [5 empty] | Non-TXV | 14.29%
Stockton | CA | 95204-3608 |  | 2012-08-06 | 2012-08-06 10:04 | 2012-08-06 10:25 | GOODMAN - PG042125-AB | 94 | 3.3 | Yes | Yes | 16.3 | 18.8 | -2.5 | E91EC7D258A24EA4B5DE113145A9128F |  | R22 | Non-TXV |  | 3.511% | 0.96489 | 6.747% | [5 empty] | Non-TXV | 3.511%
Orland | CA | 95963-9346 |  | 2012-08-14 | 2012-08-14 18:39 | 2012-08-14 19:06 | AMANA - RCE36C21A | 181 | 8 | Yes | Yes | 20.7 | 21 | -0.3 | 721EBA2329B847B7BC0302625DF75BE1 |  | R22 | Non-TXV |  | 4.42% | 0.9558 | 8.494% | [5 empty] | Non-TXV | 4.42%
Stockton | CA | 95207-4212 |  | 2012-07-02 | 2012-07-02 11:38 | 2012-07-02 11:57 | DAY & NIGHT - 30-80YAC106T | 65 | 10.4 | Yes | Yes | 14.9 | 17.5 | -2.6 | FA96A8E2DF8A4B25A6507D9AE3481B6E |  | R22 | Non-TXV |  | 16% | 0.84 | 30.75% | [5 empty] | Non-TXV | 16%
Red Bluff | CA | 96080-8884 |  | 2012-08-06 | 2012-08-06 10:51 | 2012-08-06 11:09 | GOODMAN - CKJ60-1 | 142 | 7.8 | Yes | Yes | 22.1 | 21.2 | 0.9 | 57388367DD384B4CAF5EA44678CC332D |  | R22 | Non-TXV |  | 5.493% | 0.94507 | 10.56% | [5 empty] | Non-TXV | 5.493%
Chico | CA | 95973-0370 |  | 2012-08-16 | 2012-08-16 14:40 | 2012-08-16 14:56 | COLEMAN - 95360901 | 62 | 1.9 | Yes | Yes | 19.8 | 21.2 | -1.4 | A2CCACEE3F6241C294BE176EC0CD7A75 |  | R22 | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Stockton | CA | 95207-2317 |  | 2012-06-07 | 2012-06-07 11:29 | 2012-06-07 11:34 | RHEEM - RRKA-A024JK06X | 50 | 4.5 | Yes | Yes | 19.1 | 19.7 | -0.5 | 6BAE8AAFD16645CEABA364E1D4392F04 |  | R22 | TXV |  | 9% | 0.91 | 17.3% | [5 empty] | TXV | 9%
Oroville | CA | 95965-3244 |  | 2012-08-16 | 2012-08-16 10:11 | 2012-08-16 11:26 | DAY & NIGHT - 589ANW048080ADAG | 88 | 0 | Yes | Yes | 35 | 20.4 | 14.6 | D9B7C73268984538B2D7392908F83830 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-3139 |  | 2012-06-15 | 2012-06-15 13:28 | 2012-06-15 13:48 | RHEEM - HC-80-30-21C | 48 | 1.6 | Yes | Yes | 22.3 | 18.5 | 3.8 | 0E25708567A042A9B0DB2A6E42C70858 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Tracy | CA | 95376-2004 |  | 2012-08-13 | 2012-08-13 09:46 | 2012-08-13 10:10 | AMANA - RCE42A2D | 230 | 6.8 | Yes | Yes | 19.7 | 18.8 | 0.9 | 68BE153CC423402C85D0B7B8441B0CB7 |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Livingston | CA | 95334-9764 |  | 2012-05-08 | 2012-05-08 17:21 | 2012-05-08 17:40 | RHEEM - UNK | 60 | 8.1 | Yes | Yes | 22.3 | 21.9 | 0.4 | 3949F1517CE3406AA1E48BACB7384C93 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 13.5% | 0.865 | 25.94% | [5 empty] | Non-TXV | 13.5%
Stockton | CA | 95209-4500 |  | 2012-08-06 | 2012-08-06 11:26 | 2012-08-06 11:49 | PAYNE - 38BRC042330 | 104 | 12.7 | Yes | Yes | 15.6 | 17.9 | -2.3 | 3ABF3835A17F43E6BF4F7F5F3129D190 |  | R22 | TXV |  | 12.21% | 0.87788 | 23.47% | [5 empty] | TXV | 12.21%
Fresno | CA | 93726-7022 |  | 2012-05-10 | 2012-05-10 14:03 | 2012-05-10 14:32 | DAY & NIGHT - 588ANW048080ABAG | 101 | 3 | Yes | Yes | 25.2 | 20.7 | 4.5 | 584DA4C01CF348C8B9F34E7C16D5CB81 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Clovis | CA | 93611-5929 |  | 2012-05-30 | 2012-05-30 15:30 | 2012-05-30 15:49 | CARRIER - 48NLT036---30.B | 66 | 2 | Yes | Yes | 20.1 | 21.1 | -1 | 1A896045EB9C4CD09CF7A84485061C50 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Lathrop | CA | 95330-9549 |  | 2012-06-22 | 2012-06-22 10:03 | 2012-06-22 10:25 | COLEMAN - UNK | 62 | 3.9 | Yes | Yes | 17.2 | 19.1 | -1.9 | 386326FCF07D41A9A18CDB45C578F725 |  | R22 | Non-TXV |  | 6.29% | 0.9371 | 12.09% | [5 empty] | Non-TXV | 6.29%
Los Banos | CA | 93635-8563 |  | 2012-08-14 | 2012-08-14 12:39 | 2012-08-14 13:08 | AIRE-FLO - 2A7B0042A1000AA | 95 | 11.1 | Yes | Yes | 24.8 | 21.7 | 3.1 | F9916099310A460CAC917C8E16E03945 |  | R22 | Non-TXV |  | 11.68% | 0.88316 | 22.45% | [5 empty] | Non-TXV | 11.68%
Stockton | CA | 95210-3271 |  | 2012-06-01 | 2012-06-01 10:53 | 2012-06-01 11:12 | GE - UNK | 80 | 2.8 | Yes | Yes | 25.1 | 19.1 | 6 | B7B3E3606FAF4B5E858C450EE7677008 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Merced | CA | 95340-3404 |  | 2012-05-07 | 2012-05-07 14:50 | 2012-05-07 14:50 | RHEEM - 80WE30G1 | 90 | 0 | Yes | Yes | 20.7 | 21 | -0.3 | 619F06A239B64AD5979D976EAD60A235 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3848 |  | 2012-06-11 | 2012-06-11 13:34 | 2012-06-11 14:00 | GOODMAN - CK24-18 | 71 | -4.2 | Yes | Yes | 24.3 | 22.3 | 2 | 2E1D895643774343B3DBE07C4D22EE1F |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Stockton | CA | 95215-6814 |  | 2012-08-15 | 2012-08-15 10:14 | 2012-08-15 10:32 | LENNOX - HS29-036-1P | 73 | 4.4 | Yes | Yes | 21.3 | 20.9 | 0.4 | 7AAD5E89665446C4B6AD46BFF325C9B5 |  | R22 | Non-TXV |  | 6.027% | 0.93973 | 11.58% | [5 empty] | Non-TXV | 6.027%
Los Banos | CA | 93635-8542 |  | 2012-08-14 | 2012-08-14 09:22 | 2012-08-14 09:43 | AIRE-FLO - CRT481 | 145 | 12.6 | Yes | Yes | 29.3 | 25.7 | 3.6 | 95400B44723845BA904FE7113B4FBE39 |  | R22 | Non-TXV |  | 8.69% | 0.9131 | 16.7% | [5 empty] | Non-TXV | 8.69%
Colusa | CA | 95932-3211 |  | 2012-08-09 | 2012-08-09 09:43 | 2012-08-09 09:43 | ICP - N2A330AKA200 | 84 | 0 | Yes | Yes | 20.8 | 19.9 | 0.9 | 31029C105A5C4A3FBE0B15AD3B519A2A |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-1713 |  | 2012-08-01 | 2012-08-01 11:20 | 2012-08-01 11:40 | BRYANT - 582ANW036060AAAF | 56 | 2.9 | Yes | Yes | 22.6 | 20.9 | 1.7 | 6DF18ADC013642CCA9D0AECD5B97E1EF |  | R22 | Non-TXV |  | 5.179% | 0.94821 | 9.952% | [5 empty] | Non-TXV | 5.179%
Stockton | CA | 95204-2840 |  | 2012-08-01 | 2012-08-01 12:47 | 2012-08-01 12:47 | RHEEM - RPL-B036JK08X | 93 | 0 | Yes | Yes | 23.5 | 19.2 | 4.3 | F321B5B421B74B8F8B65DAD51E75D8BA |  | R410A | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-1722 |  | 2012-08-14 | 2012-08-14 12:02 | 2012-08-14 12:18 | NORDYNE - 5S5B0-024KA | 96 | 3.3 | Yes | Yes | 17.9 | 18.5 | -0.6 | 818001F2BC2946E3818F55643F9F5AC5 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Manteca | CA | 95337-6604 |  | 2012-08-09 | 2012-08-09 14:03 | 2012-08-09 14:35 | BRYANT - 563CN036-C | 101 | 3 | Yes | Yes | 21.8 | 20.9 | 0.9 | 07CACF6B9DF646F78B48E0444B6BE17F |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Manteca | CA | 95337-6604 |  | 2012-08-09 | 2012-08-09 14:10 | 2012-08-09 14:36 | BRYANT - 563CN036-C | 101 | 6.3 | Yes | Yes | 19.2 | 19.7 | -0.5 | 76289C0F3C5F402091E2466694A35D0C |  | R22 | Non-TXV |  | 6.238% | 0.93762 | 11.99% | [5 empty] | Non-TXV | 6.238%
Paradise | CA | 95969-5831 |  | 2012-08-15 | 2012-08-15 12:37 | 2012-08-15 13:23 | CARRIER - 38CKB036320 | 71 | 6.6 | Yes | Yes | 25.8 | 20.7 | 5.1 | 166183A449B14F9B871098F19485A8F5 |  | R22 | Non-TXV |  | 9.296% | 0.90704 | 17.86% | [5 empty] | Non-TXV | 9.296%
Fresno | CA | 93723-8900 |  | 2012-07-11 | 2012-07-11 16:04 | 2012-07-11 16:30 | YORK - D6CG048NO9906A | 100 | 4.9 | Yes | Yes | 19 | 21.7 | -2.7 | 110A20B9B71F40818BE9F5F2AFD1FCF1 |  | R22 | Non-TXV |  | 4.9% | 0.951 | 9.417% | [5 empty] | Non-TXV | 4.9%
Paradise | CA | 95969-5473 |  | 2012-08-06 | 2012-08-06 19:11 | 2012-08-06 19:11 | RUUD - UAHE-030JAS | 70 | 0 | Yes | Yes | 23.1 | 19 | 4.1 | A0CC9909CCE547A0848D27719C768013 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2617 |  | 2012-05-30 | 2012-05-30 14:57 | 2012-05-30 15:15 | ICP - PGF324060K01 | 64 | -3.8 | Yes | Yes | 26.5 | 22.6 | 4 | BA582CDBA9A1460B8C9A3FADEB7BF376 |  | R22 | Non-TXV |  | -5.938% | 1.0594 | 1.663% |  |  |  |  | Non-TXV |  |  | -5.938%
Stockton | CA | 95209-2743 |  | 2012-05-16 | 2012-05-16 14:21 | 2012-05-16 14:38 | DAYNIGHT - 585A024055YACR | 51 | 4.1 | Yes | Yes | 22.5 | 19.9 | 2.6 | 042436FD41524528AE7B6F9A9D6E2227 |  | R22 | Non-TXV |  | 8.039% | 0.91961 | 15.45% | [5 empty] | Non-TXV | 8.039%
Los Banos | CA | 93635-2997 |  | 2012-08-01 | 2012-08-01 13:23 | 2012-08-01 13:23 | ARCOAIRE - PGF024K040A | 58 | 0 | Yes | Yes | 22.6 | 20.4 | 2.2 | B97A9121E2104259B53613B3C9449556 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-3174 |  | 2012-05-10 | 2012-05-10 14:17 | 2012-05-10 14:37 | GOODMAN - GSN130470A | 121 | 8.8 | Yes | Yes | 19.1 | 19.9 | -0.8 | 665D5846E251462FA3B2905B617805C4 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.273% | 0.92727 | 13.98% | [5 empty] | Non-TXV | 7.273%
Stockton | CA | 95210-2617 |  | 2012-05-30 | 2012-05-30 14:30 | 2012-05-30 14:49 | GOODMAN - GPG10240451A | 50 | 2 | Yes | Yes | 18.7 | 20.6 | -1.9 | 5BCD69E956124CAF971390812F6D7E61 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Tracy | CA | 95376-1743 |  | 2012-08-13 | 2012-08-13 10:34 | 2012-08-13 10:59 | GOODMAN - GSX130361BA | 92 | 5.8 | Yes | Yes | 17.9 | 18.8 | -0.9 | A95F6815FB154D2B8C2DCCBC2E378165 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 6.304% | 0.93696 | 12.12% | [5 empty] | Non-TXV | 6.304%
Oroville | CA | 95966-3938 |  | 2012-06-01 | 2012-06-01 10:45 | 2012-06-01 10:45 | - BRHS0481BE | 132 | 0 | Yes | Yes | 23 | 21.2 | 1.9 | 25250B007E2C4A009B9889CC0EA7CB71 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2115 |  | 2012-05-17 | 2012-05-17 13:53 | 2012-05-17 14:12 | ARCOAIR - PGC036K06OE---- | 68 | 11.7 | Yes | Yes | 20.1 | 19.9 | 0.2 | 3689C1A45BD7425EA0B05041A3B9E9C1 |  | R22 | Non-TXV |  | 17.21% | 0.82794 | 33.07% | [5 empty] | Non-TXV | 17.21%
Chico | CA | 95928-7661 |  | 2012-05-24 | 2012-05-24 12:41 | 2012-05-24 12:57 | BRYANT - 593CN030-B | 101 | 3.3 | Yes | Yes | 20.8 | 21.3 | -0.5 | 0FB4B5BE286E466098AB8DBAF92903BB |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Stockton | CA | 95209-1744 |  | 2012-08-02 | 2012-08-02 08:41 | 2012-08-02 08:58 | PAYNE - 569BJ036 | 93 | 9.5 | Yes | Yes | 20.6 | 19.8 | 0.8 | 20656D79AF424E268B99DE918525AABF |  | R22 | Non-TXV |  | 10.22% | 0.89785 | 19.63% | [5 empty] | Non-TXV | 10.22%
Fresno | CA | 93722-6888 |  | 2012-06-06 | 2012-06-06 15:27 | 2012-06-06 15:50 | CARRIER - 38BRC042340 | 103 | 3.8 | Yes | Yes | 26.1 | 21.4 | 4.7 | 0F9DAD66A82446959049FE98058CFF66 |  | R22 | TXV |  | 3.689% | 0.96311 | 7.09% | [5 empty] | TXV | 3.689%
Colusa | CA | 95932-2935 |  | 2012-07-25 | 2012-07-25 10:44 | 2012-07-25 11:11 | DAY & NIGHT - 591ANX048000ACAA | 128 | 4 | Yes | Yes | 22.7 | 20.4 | 2.3 | 7F03CE2E38D142988D94C2689D2D0161 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Los Banos | CA | 93635-3033 |  | 2012-05-08 | 2012-05-08 13:31 | 2012-05-08 13:52 | TRANE - YCC030F1M0BJ | 72 | 2.8 | Yes | Yes | 26.6 | 24.8 | 1.8 | 4E934079D419410B83879AC142F94C29 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Stockton | CA | 95212-3134 |  | 2012-05-24 | 2012-05-24 12:37 | 2012-05-24 12:57 | YORK - H2RC048S06HA | 120 | 9.8 | Yes | Yes | 19.2 | 20.4 | -1.2 | AEF59E323D69432FA160BEE55B15E5B8 |  | R22 | Non-TXV |  | 8.167% | 0.91833 | 15.69% | [5 empty] | Non-TXV | 8.167%
Chico | CA | 95926-3065 |  | 2012-05-16 | 2012-05-16 13:28 | 2012-05-16 13:28 | DAYNNIGHT - 591AX030000AAAA | 76 | 0 | Yes | Yes | 24.4 | 20.1 | 4.3 | 9DF2C7DE4196445CB30F9E8084643A40 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-2722 |  | 2012-08-02 | 2012-08-02 10:10 | 2012-08-02 10:37 | OTHER - RRMAA036JK08E | 99 | 12.3 | Yes | Yes | 19.4 | 21 | -1.6 | DB57999BC80646F1852D962C8E3A0A41 |  | R22 | Non-TXV |  | 12.42% | 0.87576 | 23.88% | [5 empty] | Non-TXV | 12.42%
Merced | CA | 95348-8712 |  | 2012-08-03 | 2012-08-03 14:28 | 2012-08-03 15:09 | GIBSON - JS3BA-042KA | 85 | -5 | Yes | Yes | 17.1 | 18.8 | -1.7 | 3672F22C35A84890B71AE4A082C0B614 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95210-3235 |  | 2012-06-14 | 2012-06-14 12:15 | 2012-06-14 12:31 | BDP - 585B024050YACR | 51 | 1.7 | Yes | Yes | 23.9 | 21.2 | 2.7 | FD498AD381DC41668F7FFBD9C1D12183 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Durham | CA | 95938-9617 |  | 2012-08-14 | 2012-08-14 09:41 | 2012-08-14 10:16 | GOODMAN - 55X140481AE | 189 | 8.4 | Yes | Yes | 20.5 | 21 | -0.4 | FF0A76E099FF4824BA3F011F9916E920 |  | R410A | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Lathrop | CA | 95330-9063 |  | 2012-08-10 | 2012-08-10 10:58 | 2012-08-10 11:23 | PAYNE - PA13NR042-C | 191 | 34.6 | Yes | Yes | 27.5 | 22.1 | 5.4 | AFFDB7E235C84113903DB7350832A89D |  | R22 | Non-TXV |  | 18.12% | 0.81885 | 34.81% | [5 empty] | Non-TXV | 18.12%
Dos Palos | CA | 93620-2650 |  | 2012-07-31 | 2012-07-31 08:21 | 2012-07-31 08:38 | CARRIER - 38CK030340 | 67 | -2.4 | Yes | Yes | 18.2 | 19.3 | -1.1 | A47A7FCE4BF045EF9B9682A68BA150DC |  | R22 | TXV |  | -3.582% | 1.0358 | 1.003% |  |  |  |  | TXV |  |  | -3.582%
Paso Robles | CA | 93446-5002 |  | 2012-07-09 | 2012-07-09 12:11 | 2012-07-09 12:29 | CARRIER - 38EN024310SM | 61 | -3.6 | Yes | Yes | 17.2 | 19.8 | -2.6 | 30C5282269634B0A9817ADBA417AD7FF |  | R22 | Non-TXV |  | -5.902% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.902%
Newman | CA | 95360-1801 |  | 2012-08-07 | 2012-08-07 12:24 | 2012-08-07 12:42 | PAYNE - UNK | 70 | 3.4 | Yes | Yes | 21.2 | 18.8 | 2.4 | CFD1FE03698242AFBCFDFE69E7650700 |  | R22 | Non-TXV |  | 4.857% | 0.95143 | 9.334% | [5 empty] | Non-TXV | 4.857%
Manteca | CA | 95337-8569 |  | 2012-08-01 | 2012-08-01 16:00 | 2012-08-01 16:28 | BRYANT - 563CN036-D | 101 | 3.3 | Yes | Yes | 18.4 | 19.5 | -1.1 | C4E4562CB3E34B569D512CB059EC919F |  | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Manteca | CA | 95337-8569 |  | 2012-08-01 | 2012-08-01 16:07 | 2012-08-01 16:35 | BRYANT - 563CN036-D | 101 | 6 | Yes | Yes | 18.4 | 20.2 | -1.8 | 24C202831C8E4F299F029975A49F140D |  | R22 | Non-TXV |  | 5.941% | 0.94059 | 11.42% | [5 empty] | Non-TXV | 5.941%
Winton | CA | 95388-9518 |  | 2012-08-02 | 2012-08-02 08:29 | 2012-08-02 08:29 | ARCOAIRE - PGC036K060D | 71 | 0 | Yes | Yes | 18.4 | 19.6 | -1.2 | 13BC75ECC65E4E658C1B49935A72A26E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1550 |  | 2012-07-31 | 2012-07-31 10:14 | 2012-07-31 10:33 | GOODMAN - GPG13420701AA | 107 | 5.2 | Yes | Yes | 24.7 | 21.2 | 3.5 | 0E9D50719DF740588DA4327289C82B84 |  | R22 | Non-TXV |  | 4.86% | 0.9514 | 9.339% | [5 empty] | Non-TXV | 4.86%
Madera | CA | 93637-4898 |  | 2012-08-11 | 2012-08-11 00:31 | 2012-08-11 00:55 | LENNOX - UNK | 80 | 2.5 | Yes | Yes | 24.9 | 19.3 | 5.6 | C225A98428AD44F7B535C101F9A5D8B9 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Woodbridge | CA | 95258-9730 |  | 2012-06-25 | 2012-06-25 08:29 | 2012-06-25 08:46 | BDP - 585HJ024040 | 68 | -4 | Yes | Yes | 23 | 18.9 | 4.1 | 470291AC54204A8E9F4B7EEDB314F0A6 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Madera | CA | 93637-5717 |  | 2012-05-14 | 2012-05-14 11:28 | 2012-05-14 11:44 | RHEEM - RRGH-051V30JKR | 70 | 5 | Yes | Yes | 19.1 | 20.2 | -1.1 | 3619B3558B1844BCBBAEC6B0CDA73521 |  | R22 | Non-TXV |  | 7.143% | 0.92857 | 13.73% | [5 empty] | Non-TXV | 7.143%
Sutter Creek | CA | 95685-4122 |  | 2012-07-17 | 2012-07-17 12:01 | 2012-07-17 12:17 | LENNOX - GCS20R-411-75-3P | 70 | 4.6 | Yes | Yes | 22 | 19.4 | 2.6 | DF575FFE8F454756948E9BC3A9995C46 |  | R22 | TXV |  | 6.571% | 0.93429 | 12.63% | [5 empty] | TXV | 6.571%
Magalia | CA | 95954-9019 |  | 2012-06-14 | 2012-06-14 10:44 | 2012-06-14 11:10 | YORK - H1RD024SO6G | 88 | 8.7 | Yes | Yes | 21 | 21.5 | -0.5 | 62E7F1853AC444E5AA4D74ED18DEED75 |  | R22 | Non-TXV |  | 9.886% | 0.90114 | 19% | [5 empty] | Non-TXV | 9.886%
Stockton | CA | 95204-2833 |  | 2012-08-03 | 2012-08-03 14:43 | 2012-08-03 15:01 | PAYNE - PY3PNA036060NB | 114 | 4 | Yes | Yes | 25.1 | 21.9 | 3.2 | 053774F7D4EF44F5BD6824646513CA38 |  | R22 | Non-TXV |  | 3.509% | 0.96491 | 6.743% | [5 empty] | Non-TXV | 3.509%
Stockton | CA | 95210-2615 |  | 2012-06-07 | 2012-06-07 10:31 | 2012-06-07 10:48 | DAY & NIGHT - 24/60YAC-108-C | 58 | -3.4 | Yes | Yes | 22.7 | 19.1 | 3.6 | 453F83E6A153470DB438FC7D0BE3281C |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Oroville | CA | 95965-4053 |  | 2012-05-29 | 2012-05-29 09:14 | 2012-05-29 09:45 | DAY N NIGHT - 36DNR-108 | 84 | 3.2 | Yes | Yes | 24.2 | 21.5 | 2.7 | 6EA8EAE8DD184F1BBA5B846EEBF9B96B |  | R22 | Non-TXV |  | 3.81% | 0.9619 | 7.321% | [5 empty] | Non-TXV | 3.81%
Winton | CA | 95388-9518 |  | 2012-08-02 | 2012-08-02 08:56 | 2012-08-02 09:17 | AMANA - RCE48C2A | 115 | 4.9 | Yes | Yes | 20.6 | 19.6 | 1.1 | 1731F8BADEC44BB7A0C61932F50DABE5 |  | R22 | TXV |  | 4.261% | 0.95739 | 8.188% | [5 empty] | TXV | 4.261%
Winton | CA | 95388-9518 |  | 2012-08-02 | 2012-08-02 09:27 | 2012-08-02 09:27 | AMANA - H2RA036S06E | 63 | 0 | Yes | Yes | 19.8 | 20.4 | -0.6 | F491F7C324DD49ADA48592422FFAB83F |  | R22 | TXV |  | 0% | 1 | 0%
Merced | CA | 95348-9400 |  | 2012-08-06 | 2012-08-06 11:50 | 2012-08-06 12:26 | LENNOX - 12ACB30-4P | 103 | 4.6 | Yes | Yes | 18.7 | 19.2 | -0.5 | 29AA15760A414969BCD7F870F653A7BE |  | R22 | Non-TXV |  | 4.466% | 0.95534 | 8.583% | [5 empty] | Non-TXV | 4.466%
Manteca | CA | 95336-4908 |  | 2012-08-09 | 2012-08-09 16:36 | 2012-08-09 17:07 | GUARDIAN - GCGD48S21S2B | 85 | 2.5 | Yes | Yes | 18.6 | 18.8 | -0.2 | 1F3DED88493C4B79B97D4580F3F056C4 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95206-2371 |  | 2012-08-08 | 2012-08-08 09:53 | 2012-08-08 10:14 | DAY & NIGHT - 588ANW03060ACAD | 53 | -3.7 | Yes | Yes | 19 | 20.9 | -1.9 | 493D6330A40348BE8074173C1B80BB6B |  | R22 | Non-TXV |  | -6.981% | 1.0698 | 1.955% |  |  |  |  | Non-TXV |  |  | -6.981%
Tracy | CA | 95377-1158 |  | 2012-07-09 | 2012-07-09 09:44 | 2012-07-09 10:05 | CARRIER - UNK | 137 | 6.8 | Yes | Yes | 19.1 | 20.3 | -1.2 | DB91D16362F74F18B859D7F1C3295102 |  | R22 | Non-TXV |  | 4.964% | 0.95036 | 9.539% | [5 empty] | Non-TXV | 4.964%
Stockton | CA | 95210-3513 |  | 2012-05-31 | 2012-05-31 15:34 | 2012-05-31 15:51 | GOODMAN - PGB036075-1A | 60 | -3.5 | Yes | Yes | 25 | 21.3 | 3.7 | AA92071BC1D545B680D20399765C5F0B |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Chico | CA | 95926-2538 |  | 2012-05-07 | 2012-05-07 17:08 | 2012-05-07 17:31 | YORK - DNP030N056606AY | 90 | 3.1 | Yes | Yes | 19.5 | 22.2 | -2.7 | 7D1D35218EEF45A3A8073C65DA6DECEE | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.444% | 0.225 | 148.9% | [5 empty] | Non-TXV | 3.444%
Livingston | CA | 95334-9429 |  | 2012-07-31 | 2012-07-31 10:45 | 2012-07-31 11:15 | RHEEM - URGGD5E24JKR | 45 | 2.5 | Yes | Yes | 20.1 | 20.4 | -0.3 | 5708791695FD4FDFB5B8BFC9A7475213 |  | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Fresno | CA | 93726-3314 |  | 2012-05-10 | 2012-05-10 11:47 | 2012-05-10 12:10 | WEATHERTECH - N/A | 70 | 2.1 | Yes | Yes | 22.2 | 20.2 | 2.1 | F211471A743C42C48DAA0FC7C0E4EA14 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Orland | CA | 95963-2500 |  | 2012-08-13 | 2012-08-13 12:45 | 2012-08-13 12:45 | BRYANT - H2RA030S06D | 62 | 0 | Yes | Yes | 22.8 | 21.4 | 1.4 | DD5324C1248B4A0CA5B91A75B402E4E0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-1617 |  | 2012-08-03 | 2012-08-03 12:52 | 2012-08-03 13:15 | HEIL - NAC036AKA1 | 87 | 12.7 | Yes | Yes | 17.8 | 19.3 | -1.5 | D0ACAF0E64134B08A9F59D6B225EBF0D |  | R22 | Non-TXV |  | 14.6% | 0.85402 | 28.05% | [5 empty] | Non-TXV | 14.6%
Atascadero | CA | 93422-2740 |  | 2012-07-10 | 2012-07-10 09:46 | 2012-07-10 10:03 | TEMPSTAR - CA5536VKD1 | 82 | -4.8 | Yes | Yes | 25.8 | 19.8 | 6 | C86D0D243648463481D7FE7542258884 |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Atwater | CA | 95301-4739 |  | 2012-08-10 | 2012-08-10 11:23 | 2012-08-10 11:40 | GOODMAN - UNK | 92 | 4 | Yes | Yes | 20.3 | 17.9 | 2.4 | 8026DF2116414D8F971E0920F93612A1 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Magalia | CA | 95954-9607 |  | 2012-08-15 | 2012-08-15 10:34 | 2012-08-15 10:34 | BRYANT - 6021BX036000AAAF | 66 | 0 | Yes | Yes | 22.5 | 21.2 | 1.4 | 786A5DDAD52746748753E4F57416A3E6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4631 |  | 2012-05-24 | 2012-05-24 14:41 | 2012-05-24 14:58 | BRYANT - 563CN018-B | 80 | -2.9 | Yes | Yes | 25.1 | 20.7 | 4.4 | ED5502EBD27346D584AC01EDCA909FF9 |  | R22 | TXV |  | -3.625% | 1.0362 | 1.015% |  |  |  |  | TXV |  |  | -3.625%
Atwater | CA | 95301-4507 |  | 2012-08-09 | 2012-08-09 12:21 | 2012-08-09 12:51 | YORK - H2RD030S06A | 93 | 2.7 | Yes | Yes | 17.3 | 18.5 | -1.2 | 35D566F46B1D460B823F822834BF2CAC |  | R22 | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Tracy | CA | 95376-1872 |  | 2012-06-15 | 2012-06-15 09:56 | 2012-06-15 10:12 | WEATHER KING - 13AJA24A01 | 77 | 7.5 | Yes | Yes | 19.2 | 20.4 | -1.2 | C8CB8CCE99E849FFAD8B072BC14438CE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.74% | 0.9026 | 18.72% | [5 empty] | Non-TXV | 9.74%
Red Bluff | CA | 96080-2262 |  | 2012-08-02 | 2012-08-02 22:19 | 2012-08-02 22:19 | YORK - D3NZ036N05606NXA | 64 | 0 | Yes | Yes | 23.2 | 21.5 | 1.7 | DD2AA0280B164949908F15959FCF2AFD |  | R410A | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2833 |  | 2012-06-06 | 2012-06-06 08:18 | 2012-06-06 08:38 | RHEEM - RRNA-B048JK10X | 154 | 4.6 | Yes | Yes | 24.1 | 19.4 | 4.7 | 1B1502BED40D4C37B994D5AF00294575 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.987% | 0.97013 | 5.74% | [5 empty] | Non-TXV | 2.987%
Fresno | CA | 93722-4535 |  | 2012-05-23 | 2012-05-23 13:52 | 2012-05-23 14:12 | TAPPAN - N/A | 45 | 1.3 | Yes | Yes | 20.1 | 19.9 | 0.2 | A33C0DECD5574B83A6025B3468CCB1AD |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Merced | CA | 95348-4009 |  | 2012-08-02 | 2012-08-02 13:09 | 2012-08-02 13:09 | OTHER - UNK | 66 | 0 | Yes | Yes | 18.2 | 19.8 | -1.6 | 6BDA3238AF54415FAF1310B85B079F91 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-3101 |  | 2012-08-03 | 2012-08-03 15:34 | 2012-08-03 16:18 | BRYANT - 588ANW042080ACAG | 82 | 2.6 | Yes | Yes | 19.9 | 21.2 | -1.3 | 82C8A722900A477183B6EBC1DF1C6FC6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.171% | 0.96829 | 6.093% | [5 empty] | Non-TXV | 3.171%
Stockton | CA | 95210-3253 |  | 2012-06-08 | 2012-06-08 12:57 | 2012-06-08 13:14 | BDP - 585B024050YACR | 51 | 1.5 | Yes | Yes | 24.5 | 23.1 | 1.4 | 05C42A8FFE00443C929D6E49A51C1DB9 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Grass Valley | CA | 95945-7209 |  | 2012-06-14 | 2012-06-14 14:10 | 2012-06-14 14:10 | CARRIER - 38EH030340 | 126 | 0 | Yes | Yes | 16.4 | 18.3 | -1.9 | 78209710D27E4E2DA3E01CF7F0DA32E3 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-2715 |  | 2012-08-02 | 2012-08-02 10:53 | 2012-08-02 11:11 | BDP - 561CJ036-D | 85 | 2.6 | Yes | Yes | 17.9 | 19.9 | -2 | D65228D88C5E4AAB81BDC2C3DD5233C3 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Chico | CA | 95928-6644 |  | 2012-05-11 | 2012-05-11 13:20 | 2012-05-11 13:20 | GIBSON - NA | 62 | 0 | Yes | Yes | 21.4 | 22 | -0.6 | AA7EC22FAF234B5D8B6A3CF8ABD1EAC1 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-8835 |  | 2012-08-10 | 2012-08-10 08:57 | 2012-08-10 09:15 | GOODMAN - CLJ36-1C | 109 | -6.4 | Yes | Yes | 20.9 | 20.4 | 0.5 | 513514A9CC3047B0A87C6DCF15E1021F |  | R22 | Non-TXV |  | -5.872% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.872%
Chico | CA | 95926-3062 |  | 2012-05-14 | 2012-05-14 13:26 | 2012-05-14 13:26 | DAY N NIGHT - 591ANX030000AAAA | 76 | 0 | Yes | Yes | 21.8 | 21.5 | 0.3 | F4A14E2D81E64A2182B062996DF5E8EA |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-5037 |  | 2012-08-02 | 2012-08-02 09:33 | 2012-08-02 09:49 | PAYNE - 567GJ036 | 85 | -8 | Yes | Yes | 22.8 | 19.3 | 3.5 | 5146694BA85D4317ADFEF2C69AD229CC |  | R22 | Non-TXV |  | -9.412% | 1.0941 | 2.636% |  |  |  |  | Non-TXV |  |  | -9.412%
Tracy | CA | 95377-1118 |  | 2012-08-13 | 2012-08-13 12:03 | 2012-08-13 12:32 | RHEEM - FADC-048JAS | 113 | 3.4 | Yes | Yes | 16.5 | 16.9 | -0.4 | 79B0D81F44A14B11BFDE9F68ADBCB77A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.009% | 0.96991 | 5.782% | [5 empty] | Non-TXV | 3.009%
Atwater | CA | 95301-4423 |  | 2012-08-13 | 2012-08-13 09:03 | 2012-08-13 09:31 | TRANE - YCP036F1MOAD | 107 | 3.8 | Yes | Yes | 19.2 | 20.4 | -1.2 | A6620FB4576347959B5E34630178A244 |  | R22 | Non-TXV |  | 3.551% | 0.96449 | 6.825% | [5 empty] | Non-TXV | 3.551%
Red Bluff | CA | 96080-7822 |  | 2012-08-06 | 2012-08-06 11:21 | 2012-08-06 11:21 | BRYANT - 550AN042F | 135 | 0 | Yes | Yes | 23.6 | 22.3 | 1.4 | AD6C61F199D24DF789AA74EA807BFCE5 |  | R410A | TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-1602 |  | 2012-08-13 | 2012-08-13 08:10 | 2012-08-13 08:30 | CARRIER - 38BRC048370 | 136 | -9.6 | Yes | Yes | 24.7 | 20.4 | 4.3 | 23BF5DCA4E6A42D6A279CA75F3D2B615 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Stockton | CA | 95206-3812 |  | 2012-07-11 | 2012-07-11 10:54 | 2012-07-11 11:12 | YORK - H4DE036S06A | 82 | 3.4 | Yes | Yes | 21.4 | 19.3 | 2.1 | 1ED73392A6364810804E03F067D8FAC8 |  | R22 | Non-TXV |  | 4.146% | 0.95854 | 7.968% | [5 empty] | Non-TXV | 4.146%
Stockton | CA | 95206-4887 |  | 2012-08-13 | 2012-08-13 14:40 | 2012-08-13 15:10 | CARRIER - 38TH030310 | 70 | -6.6 | Yes | Yes | 17 | 19.9 | -2.9 | C751CB7EE9714B19922BBFE5338C9DE1 |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Merced | CA | 95341-5485 |  | 2012-05-08 | 2012-05-08 14:19 | 2012-05-08 14:37 | GOODMAN - GPG13300451AC | 85 | 6.3 | Yes | Yes | 30 | 24.8 | 5.2 | 4302DB012F6241C88C48C53CB56D0893 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.412% | 0.92588 | 14.24% | [5 empty] | Non-TXV | 7.412%
Los Banos | CA | 93635-3109 |  | 2012-08-01 | 2012-08-01 09:20 | 2012-08-01 09:46 | BDP - 565BJ030 | 72 | 12.6 | Yes | Yes | 23 | 25.3 | -2.3 | B5C465AA1C97414EAC904EE36AF5D136 |  | R22 | Non-TXV |  | 17.5% | 0.825 | 33.63% | [5 empty] | Non-TXV | 17.5%
Los Banos | CA | 93635-2629 |  | 2012-05-08 | 2012-05-08 15:58 | 2012-05-08 16:17 | GOODMAN - CK30-1T | 76 | 4.7 | Yes | Yes | 24.1 | 21.5 | 2.6 | 6FB96DF0A1984FBBAAEA35623904869A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6.184% | 0.93816 | 11.88% | [5 empty] | Non-TXV | 6.184%
Los Banos | CA | 93635-3029 |  | 2012-05-08 | 2012-05-08 16:36 | 2012-05-08 17:00 | CARRIER - UNK | 102 | 3.7 | Yes | Yes | 23.7 | 21.5 | 2.2 | D2A585DAF7DE400C9BC198C3CEFBD83A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.627% | 0.96373 | 6.971% | [5 empty] | Non-TXV | 3.627%
Magalia | CA | 95954-9409 |  | 2012-06-11 | 2012-06-11 10:56 | 2012-06-11 11:12 | INTERTHERM - CN4801BAV | 74 | 3.1 | Yes | Yes | 21.5 | 21 | 0.5 | 9CAE37D5DEAD4D4A8F0B6A30B7F7AF56 |  | R22 | Non-TXV |  | 4.189% | 0.95811 | 8.051% | [5 empty] | Non-TXV | 4.189%
Stockton | CA | 95209-2746 |  | 2012-05-16 | 2012-05-16 14:57 | 2012-05-16 15:18 | DAYNIGHT - 585A024055YACR | 51 | 9.1 | Yes | Yes | 19.7 | 17.9 | 1.8 | 3E08DDA6CF764A76938F5DD3E105E97B |  | R22 | Non-TXV |  | 17.84% | 0.82157 | 34.29% | [5 empty] | Non-TXV | 17.84%
Yuba City | CA | 95993-1696 |  | 2012-08-01 | 2012-08-01 12:27 | 2012-08-01 12:44 | CARRIER - 38TXA048320 | 162 | 15.1 | Yes | Yes | 22.5 | 21.3 | 1.2 | A2DB2170F9D74553A4A99636F8E0B52B |  | R410A | TXV |  | 9.321% | 0.90679 | 17.91% | [5 empty] | TXV | 9.321%
Yuba City | CA | 95991-4901 |  | 2012-06-15 | 2012-06-15 14:33 | 2012-06-15 14:50 | DAY & NIGHT - 673 | 67 | 2 | Yes | Yes | 23 | 20.2 | 2.8 | C0B999760AF34563A56F50AEEA5455A8 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Winton | CA | 95388-9705 |  | 2012-08-02 | 2012-08-02 12:00 | 2012-08-02 12:24 | GOODMAN - PGB036050-1 | 60 | -4.2 | Yes | Yes | 24.2 | 18.5 | 5.7 | 432B1CDE7ED7418EBB67B4DABD0925E2 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Yuba City | CA | 95993-9731 |  | 2012-08-01 | 2012-08-01 13:35 | 2012-08-01 13:56 | YORK - H1RE036S06D | 150 | 23.9 | Yes | Yes | 19.1 | 19.2 | -0.1 | B8C3CAF6AB7441FEB178410773E805C1 |  | R22 | Non-TXV |  | 15.93% | 0.84067 | 30.62% | [5 empty] | Non-TXV | 15.93%
Chowchilla | CA | 93610-2758 |  | 2012-07-31 | 2012-07-31 10:01 | 2012-07-31 10:19 | PAYNE - PYGNAA42090NA | 97 | 3 | Yes | Yes | 18.6 | 20.4 | -1.8 | 0C9374EC62604DD89F8F4D907542869A |  | R410A | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Stockton | CA | 95204-4965 |  | 2012-05-11 | 2012-05-11 15:14 | 2012-05-11 15:35 | CARRIER - 48GS-0480900311 | 81 | 3.9 | Yes | Yes | 18.8 | 20.1 | -1.3 | 6A06AB0E3CB641F99706C2CF171B28E5 |  | R22 | Non-TXV |  | 4.815% | 0.95185 | 9.253% | [5 empty] | Non-TXV | 4.815%
Stockton | CA | 95205-7850 |  | 2012-08-06 | 2012-08-06 12:55 | 2012-08-06 13:19 | HEIL - UNK | 85 | 3.2 | Yes | Yes | 20 | 20.6 | -0.6 | 662976C952E34B1F888F65B82E75F3B0 |  | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Stockton | CA | 95210-1709 |  | 2012-07-31 | 2012-07-31 08:46 | 2012-07-31 09:04 | PAYNE - PY3GNAA30060NA | 98 | -5.8 | Yes | Yes | 23.5 | 19.4 | 4.1 | 3B9BF8AE0D914B8481CD07D12A45DD63 |  | R410A | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Stockton | CA | 95210-2614 |  | 2012-05-30 | 2012-05-30 11:43 | 2012-05-30 12:00 | DAY & NIGHT - UNK | 50 | -3.5 | Yes | Yes | 23 | 20.3 | 2.8 | 836D7EDD215943819C3973E84E55345D |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Merced | CA | 95341-6635 |  | 2012-06-12 | 2012-06-12 13:23 | 2012-06-12 13:50 | GOODMAN - CKL36-1D | 72 | 4.2 | Yes | Yes | 18.9 | 20.4 | -1.5 | 2E14A05D2C8E48A8ACB960F73DE43036 |  | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Woodbridge | CA | 95258-9602 |  | 2012-08-16 | 2012-08-16 14:12 | 2012-08-16 14:29 | YORK - H2CB042S06A | 108 | 3.6 | Yes | Yes | 19.9 | 20.1 | -0.2 | 1FC5D9A318CB48A3B2A1649B8C4E06F0 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Chico | CA | 95926-1102 |  | 2012-05-15 | 2012-05-15 11:44 | 2012-05-15 11:44 | YORK - H2RA036S06E | 61 | 0 | Yes | Yes | 26.4 | 22.9 | 3.6 | 7776EE8F94D54E1EAB8C40AA537A7195 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2614 |  | 2012-05-30 | 2012-05-30 11:03 | 2012-05-30 11:20 | RHEEM - RRKA-A024JK06X | 50 | -2.9 | Yes | Yes | 18.7 | 19.4 | -0.7 | 6EE70B33202547EFA35995C27AF15397 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Colusa | CA | 95932-9715 |  | 2012-08-09 | 2012-08-09 12:12 | 2012-08-09 12:12 | MONTGOMERY WARD - UNK | 65 | 0 | Yes | Yes | 22.2 | 19.8 | 2.4 | C9D98B147C5C4BAD99346757359D313E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93612-4829 |  | 2012-05-15 | 2012-05-15 15:10 | 2012-05-15 15:29 | PAYNE - PA10JA042-C | 90 | -5.3 | Yes | Yes | 18 | 20.7 | -2.7 | 53E9C57D5ED846D097BF60E5020F6481 |  | R22 | Non-TXV |  | -5.889% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.889%
Yuba City | CA | 95991-4861 |  | 2012-06-15 | 2012-06-15 09:26 | 2012-06-15 09:26 | RHEEM - RAFD-048BS | 99 | 0 | Yes | Yes | 20.5 | 18.8 | 1.8 | 74701C808C7345239B7B00A47B0A05D5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-2614 |  | 2012-05-30 | 2012-05-30 13:59 | 2012-05-30 14:17 | GOODMAN - GPG1324045M41AC | 80 | 2.4 | Yes | Yes | 19.5 | 19.6 | -0.1 | E2313890FC6242D2B4308AC4D88256DA |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Manteca | CA | 95336-5814 |  | 2012-05-10 | 2012-05-10 16:08 | 2012-05-10 16:38 | YORK - H2CH036S06A | 179 | 7.2 | Yes | Yes | 25.5 | 20.4 | 5.1 | 8B1DC8B0B4ED4197885C88732C60E6E9 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.022% | 0.95978 | 7.73% | [5 empty] | Non-TXV | 4.022%
Tracy | CA | 95376-2125 |  | 2012-08-15 | 2012-08-15 12:33 | 2012-08-15 12:50 | TRANE - 4TTX4060A1000AA | 132 | 4.1 | Yes | Yes | 25.4 | 19.5 | 5.9 | C102BD9335A148CC9C3D3FAB544FD157 |  | R410A | Non-TXV |  | 3.106% | 0.96894 | 5.969% | [5 empty] | Non-TXV | 3.106%
Valley Springs | CA | 95252-9242 |  | 2012-08-13 | 2012-08-13 11:01 | 2012-08-13 11:19 | YORK - H1CF060S06B | 213 | 6.5 | Yes | Yes | 26.2 | 22.6 | 3.6 | 5885DC152A7A483280922D6A5EC33D58 |  | R22 | Non-TXV |  | 3.052% | 0.96948 | 5.865% | [5 empty] | Non-TXV | 3.052%
Oakdale | CA | 95361-2769 |  | 2012-08-16 | 2012-08-16 11:23 | 2012-08-16 11:43 | GOODMAN - CKL60-1L | 115 | 4.7 | Yes | Yes | 17.8 | 20.4 | -2.6 | 9729FC0491CF4ECBB1AB08103E5BAB1D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.087% | 0.95913 | 7.854% | [5 empty] | Non-TXV | 4.087%
Stockton | CA | 95203-1531 |  | 2012-08-02 | 2012-08-02 11:08 | 2012-08-02 11:30 | GOODMAN - CK49-1B | 97 | 7 | Yes | Yes | 19.4 | 19.9 | -0.5 | ABBDC5012E4746AC8C64EA4EEB3DD1EE |  | R22 | Non-TXV |  | 7.216% | 0.92784 | 13.87% | [5 empty] | Non-TXV | 7.216%
Stockton | CA | 95209-2745 |  | 2012-08-02 | 2012-08-02 14:32 | 2012-08-02 14:49 | PAYNE - 585A024055YACR | 85 | 4.4 | Yes | Yes | 24.2 | 22.5 | 1.8 | C8AD2667A4524B3CBC2C2A80AAD9A5D2 |  | R22 | Non-TXV |  | 5.176% | 0.94824 | 9.948% | [5 empty] | Non-TXV | 5.176%
Stockton | CA | 95210-2617 |  | 2012-05-30 | 2012-05-30 12:45 | 2012-05-30 13:02 | RHEEM - RRKA-A024JK06X | 50 | 1.5 | Yes | Yes | 20.6 | 20.8 | -0.2 | 22A5FE3D6B0842A8A65C9813E54D182D |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Reedley | CA | 93654-9457 |  | 2012-07-23 | 2012-07-23 13:14 | 2012-07-23 13:38 | NORDYNE - GR6GD-X42K072C | 116 | 3.4 | Yes | Yes | 22.8 | 20.8 | 2 | A0F2C178D9434592966F307A51DE139D |  | R410A | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Loomis | CA | 95650-8871 |  | 2012-05-11 | 2012-05-11 10:21 | 2012-05-11 10:43 | DAY&NIGHT - N4A430GKB200 | 93 | 10 | Yes | Yes | 24.4 | 19.9 | 4.5 | 37B8B9D2EAB34D1D871D2656B9C9EDBE | OK: Verified Refrigerant Charge | R410A | TXV |  | 10.75% | 0.89247 | 20.66% | [5 empty] | TXV | 10.75%
Newman | CA | 95360-1516 |  | 2012-05-17 | 2012-05-17 09:01 | 2012-05-17 09:22 | PAYNE - PA13NR036-K | 84 | 2.5 | Yes | Yes | 13.4 | 15.8 | -2.4 | 210E08D4155A4BF6B21CD1594016ADF9 |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Madera | CA | 93638-2151 |  | 2012-06-13 | 2012-06-13 15:23 | 2012-06-13 15:47 | YORK - D2NP036N05606A | 108 | -6.4 | Yes | Yes | 24.7 | 21.3 | 3.4 | 28B3DF6985364A4FBAD3F74A64A5C50C |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Dinuba | CA | 93618-9114 |  | 2012-05-09 | 2012-05-09 10:54 | 2012-05-09 11:15 | CARRIER - 535HJ036660 | 102 | 6.4 | Yes | Yes | 15.7 | 18.2 | -2.5 | E172F665B04F414691F6A3C6F06218C1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.275% | 0.93725 | 12.06% | [5 empty] | Non-TXV | 6.275%
Winton | CA | 95388-9775 |  | 2012-08-03 | 2012-08-03 11:30 | 2012-08-03 11:58 | RHEEM - UNK | 75 | 5.2 | Yes | Yes | 27 | 22 | 5 | D7D19CFDA60B40AA9782F6276D23A936 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.933% | 0.93067 | 13.32% | [5 empty] | Non-TXV | 6.933%
Yuba City | CA | 95991-6221 |  | 2012-06-14 | 2012-06-14 11:34 | 2012-06-14 11:56 | OTHER - GSC3BA-036KA | 69 | 2.1 | Yes | Yes | 17 | 18.7 | -1.7 | 0513C87620CA4161A716281943EA9E16 |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Atwater | CA | 95301-3848 |  | 2012-05-15 | 2012-05-15 13:22 | 2012-05-15 13:50 | FRASER JOHNSON - NA | 76 | 2.3 | Yes | Yes | 19.8 | 19.6 | 0.2 | 6A747762AFFC4F1988AC8DEA9D7CB123 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Lathrop | CA | 95330-9209 |  | 2012-07-02 | 2012-07-02 10:37 | 2012-07-02 10:57 | YORK - H1RA4206D | 84 | 15.4 | Yes | Yes | 17.9 | 18.8 | -0.9 | 3A7A1CEA87374B4390267E2260B47183 |  | R22 | Non-TXV |  | 18.33% | 0.81667 | 35.23% | [5 empty] | Non-TXV | 18.33%
Stockton | CA | 95206-3300 |  | 2012-08-09 | 2012-08-09 14:05 | 2012-08-09 14:27 | COLEMAN - NAC030AKC3 | 75 | 6.1 | Yes | Yes | 15 | 17.9 | -2.9 | AF0E0729C7DF4236801E274868DAE2DE |  | R22 | Non-TXV |  | 8.133% | 0.91867 | 15.63% | [5 empty] | Non-TXV | 8.133%
Magalia | CA | 95954-9545 |  | 2012-08-08 | 2012-08-08 13:00 | 2012-08-08 13:33 | ARCOAIRE - WCH030B100CA | 140 | 4.2 | Yes | Yes | 19 | 20.9 | -1.9 | D1E0FA8453944DF48A3020541EF88BF0 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-3052 |  | 2012-05-09 | 2012-05-09 16:05 | 2012-05-09 16:38 | COLEMAN - TCDG42S21S1A | 72 | 22 | Yes | Yes | 21.8 | 22.8 | -1 | 20C702D5350A4224A775EC3DFD5A1E51 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 30.56% | 0.69444 | 58.72% | [5 empty] | Non-TXV | 30.56%
Madera | CA | 93637-4908 |  | 2012-07-31 | 2012-07-31 14:36 | 2012-07-31 14:53 | CARRIER - N/A | 80 | 2.4 | Yes | Yes | 26.4 | 21.5 | 4.9 | F7BB16DF46054790818E2EEF9BC86CCE |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Newman | CA | 95360-9661 |  | 2012-08-14 | 2012-08-14 09:21 | 2012-08-14 09:41 | BRYANT - 563CN042-E | 103 | 4 | Yes | Yes | 23.5 | 20.1 | 3.4 | 5CD958D6BC7645859BD8A9FC483D849E |  | R22 | TXV |  | 3.883% | 0.96117 | 7.463% | [5 empty] | TXV | 3.883%
Stockton | CA | 95210-1778 |  | 2012-05-09 | 2012-05-09 13:27 | 2012-05-09 13:45 | CARRIER - 38EA024 | 85 | 2.5 | Yes | Yes | 20.1 | 20.4 | -0.3 | 3C8346FB4E764FDB9BF1960614D35D1A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Yuba City | CA | 95991-3321 |  | 2012-06-11 | 2012-06-11 09:43 | 2012-06-11 10:13 | LENNOX - HS26-048-4P | 111 | -7.4 | Yes | Yes | 26 | 20.9 | 5.1 | B3A691E5CD614196935D689140CE0501 |  | R22 | TXV |  | -6.667% | 1.0667 | 1.867% |  |  |  |  | TXV |  |  | -6.667%
Dinuba | CA | 93618-3234 |  | 2012-07-31 | 2012-07-31 13:15 | 2012-07-31 13:48 | TEMPSTAR - H4A342AKA0300 | 88 | 3.7 | Yes | Yes | 19.2 | 18.5 | 0.7 | A4BEB7DFB55B441AB0F1621DC8F5195E |  | R410A | Non-TXV |  | 4.205% | 0.95795 | 8.08% | [5 empty] | Non-TXV | 4.205%
Stockton | CA | 95204-2124 |  | 2012-08-02 | 2012-08-02 11:53 | 2012-08-02 12:16 | COMFORT AIRE - NAC036AKC3 | 94 | 4.1 | Yes | Yes | 20.3 | 21 | -0.7 | 60E46C5D771144179289252B614E0559 |  | R22 | Non-TXV |  | 4.362% | 0.95638 | 8.382% | [5 empty] | Non-TXV | 4.362%
Stockton | CA | 95210-2079 |  | 2012-08-01 | 2012-08-01 14:26 | 2012-08-01 14:52 | GOODMAN - PGB036075-1A | 60 | 2 | Yes | Yes | 23 | 19.9 | 3.1 | 42119FBB122E4D17B87A473F7B9F5C7F |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Gustine | CA | 95322-1742 |  | 2012-08-14 | 2012-08-14 10:40 | 2012-08-14 11:04 | BRYANT - 561CJ030-D | 76 | 7.6 | Yes | Yes | 17.3 | 20.2 | -2.9 | 63748389C0D0461BAB69B51FA5DEDD57 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Red Bluff | CA | 96080-2031 |  | 2012-08-03 | 2012-08-03 18:01 | 2012-08-03 19:16 | INTERTHERM - UC648 | 48 | 7.9 | Yes | Yes | 24.7 | 22 | 2.7 | 4A4D1E087B584CB69D40C5B40C615F0C |  | R22 | Non-TXV |  | 16.46% | 0.83542 | 31.63% | [5 empty] | Non-TXV | 16.46%
Red Bluff | CA | 96080-9657 |  | 2012-08-06 | 2012-08-06 09:43 | 2012-08-06 10:28 | GOODMAN - KL49-1 | 109 | 3.4 | Yes | Yes | 30.2 | 24.5 | 5.8 | E06528EA231E4A1F814DBF590F946D0F |  | R22 | Non-TXV |  | 3.119% | 0.96881 | 5.995% | [5 empty] | Non-TXV | 3.119%
Corning | CA | 96021-9511 |  | 2012-08-02 | 2012-08-02 11:46 | 2012-08-02 12:20 | COLEMAN - BRCQ0361BD | 52 | 3.4 | Yes | Yes | 24.7 | 20.4 | 4.3 | 2C4B84A484BE433AA5942D486E7E2D84 |  | R22 | Non-TXV |  | 6.538% | 0.93462 | 12.57% | [5 empty] | Non-TXV | 6.538%
Lathrop | CA | 95330-8820 |  | 2012-08-10 | 2012-08-10 08:18 | 2012-08-10 08:36 | CARRIER - 38BRC048370 | 140 | 59.1 | Yes | Yes | 6.6 | 20.5 | -13.9 | 2C9EAF427A5246C8BEA83D2ADC85E5E5 | Add refrigerant: 53.9 oz Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 42.21% | 0.57786 | 81.13% | [5 empty] | Non-TXV | 42.21%
Rocklin | CA | 95677-1911 |  | 2012-05-11 | 2012-05-11 13:42 | 2012-05-11 14:16 | TRANE - YCC030F1L0BJ | 70 | 8.8 | Yes | Yes | 26.8 | 22.1 | 4.7 | FFF49921E7DD48E291A2C410DCE54B51 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 12.57% | 0.87429 | 24.16% | [5 empty] | Non-TXV | 12.57%
Orland | CA | 95963-1122 |  | 2012-07-30 | 2012-07-30 18:38 | 2012-07-30 19:07 | TEMPSTAR - PGC042K080E | 85 | 4.6 | Yes | Yes | 22.5 | 20.8 | 1.7 | 0A463D3B159D4810A3B3A81D724D32CF |  | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Winton | CA | 95388-0000 |  | 2012-08-01 | 2012-08-01 11:13 | 2012-08-01 11:38 | TEMPSTAR - NCAF036VKB | 89 | 3.7 | Yes | Yes | 18.5 | 20.4 | -1.9 | C8C4FE53E27F4CFEB760E52E129ADBE5 |  | R22 | Non-TXV |  | 4.157% | 0.95843 | 7.989% | [5 empty] | Non-TXV | 4.157%
Atwater | CA | 95301-2127 |  | 2012-08-10 | 2012-08-10 09:37 | 2012-08-10 10:05 | DAY & NIGHT - UNK | 76 | 2.3 | Yes | Yes | 24.7 | 20.4 | 4.3 | 191BE1BC7DB8426F81C00E14A9F4C31D |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Tracy | CA | 95377-8219 |  | 2012-08-15 | 2012-08-15 13:30 | 2012-08-15 13:55 | RHEEM - RAHE-042JAS | 101 | 4 | Yes | Yes | 22.9 | 20.4 | 2.5 | 2E439D4D6DAD48C2985A80E1E53DD379 |  | R22 | Non-TXV |  | 3.96% | 0.9604 | 7.611% | [5 empty] | Non-TXV | 3.96%
Merced | CA | 95341-5808 |  | 2012-06-07 | 2012-06-07 10:08 | 2012-06-07 10:35 | OTHER - GPG13300451A | 77 | 7.1 | Yes | Yes | 23.8 | 19.2 | 4.6 | 547EAFA44BE244FB95D6DB86698F4912 |  | R22 | Non-TXV |  | 9.221% | 0.90779 | 17.72% | [5 empty] | Non-TXV | 9.221%
Stockton | CA | 95204-1833 |  | 2012-05-08 | 2012-05-08 11:51 | 2012-05-08 12:12 | GENERAL ELECTRIC - 21TAO4241B | 103 | 3.5 | Yes | Yes | 8 | 19.1 | -11.1 | 0F8D386E4E9247598A83C9F76509800E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.398% | 0.96602 | 6.53% | [5 empty] | Non-TXV | 3.398%
Rocklin | CA | 95765-4974 |  | 2012-07-31 | 2012-07-31 15:07 | 2012-07-31 15:25 | CARRIER - 38TXA060340 | 192 | 37 | Yes | Yes | 26.5 | 21.7 | 4.8 | 35509FB6604C4A3D8CF08B3514274981 |  | R410A | Non-TXV |  | 19.27% | 0.80729 | 37.03% | [5 empty] | Non-TXV | 19.27%
Madera | CA | 93638-0649 |  | 2012-07-31 | 2012-07-31 09:46 | 2012-07-31 10:06 | CARRIER - 48GS-0360301 | 56 | 1.6 | Yes | Yes | 24.6 | 22.4 | 2.2 | 2C5FAE1DC46147AC99CB5082F4D0A831 |  | R22 | Non-TXV |  | 2.857% | 0.97143 | 5.491% | [5 empty] | Non-TXV | 2.857%
Atwater | CA | 95301-4589 |  | 2012-05-11 | 2012-05-11 12:22 | 2012-05-11 12:41 | GOODMAN - CK30-1A | 76 | 2.3 | Yes | Yes | 16.5 | 19 | -2.5 | E2F5BA3DC95B455380B63E0908D5CC3B | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Rocklin | CA | 95765-4151 |  | 2012-05-22 | 2012-05-22 16:29 | 2012-05-22 16:29 | CARRIER - 38EH030340 | 126 | 0 | Yes | Yes | 17.7 | 20.1 | -2.4 | 41044C4572FE48CABAB3D52BA9FCA61A | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Woodbridge | CA | 95258-9219 |  | 2012-08-16 | 2012-08-16 14:44 | 2012-08-16 15:05 | YORK - D1NP042N06506A | 150 | 4.6 | Yes | Yes | 23.8 | 19.4 | 4.5 | 4B2F923AA4AB4C4B9885774A8319B1EA |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Merced | CA | 95340-3466 |  | 2012-08-02 | 2012-08-02 13:11 | 2012-08-02 13:11 | AIRE-FLO - AD060G | 191 | 0 | Yes | Yes | 12 | 14.7 | -2.7 | A820CE8BCB5542C6A7703722B577DCA5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-2967 |  | 2012-08-01 | 2012-08-01 12:08 | 2012-08-01 12:37 | RUUD - N/A | 80 | 2.4 | Yes | Yes | 19.1 | 19.7 | -0.6 | 65F09D1B27364E1581C6E4334D8CAE42 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Lincoln | CA | 95648-1569 |  | 2012-08-01 | 2012-08-01 15:26 | 2012-08-01 15:43 | RHEEM - RRKA-A030JK06X | 54 | 10.3 | Yes | Yes | 23.9 | 20.6 | 3.3 | 5F5AE62993CA4184AFF2F87038356B61 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.07% | 0.80926 | 36.66% | [5 empty] | Non-TXV | 19.07%
Firebaugh | CA | 93622-9787 |  | 2012-05-31 | 2012-05-31 10:25 | 2012-05-31 10:43 | GOODMAN - PHK024-1F | 76 | 2.3 | Yes | Yes | 22.7 | 20.7 | 2 | B965118B0DFA4FB2A8302E2BC8826762 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95209-5010 |  | 2012-05-16 | 2012-05-16 12:35 | 2012-05-16 13:06 | WESTINGHOUSE - IE024PAA0N | 58 | 17.2 | Yes | Yes | 18.2 | 20.4 | -2.2 | D99DA003BDE14A8BA66FC1F9552A3392 |  | R22 | Non-TXV |  | 29.66% | 0.70345 | 56.99% | [5 empty] | Non-TXV | 29.66%
Chico | CA | 95926-3064 |  | 2012-05-14 | 2012-05-14 17:22 | 2012-05-14 17:26 | DAYNNIGHT - UNK | 85 | 3.9 | Yes | Yes | 24 | 20.9 | 3.1 | 92BF0EDB785547F8B203335F68B9192C |  | R22 | Non-TXV |  | 4.588% | 0.95412 | 8.818% | [5 empty] | Non-TXV | 4.588%
Los Banos | CA | 93635-2982 |  | 2012-05-08 | 2012-05-08 15:13 | 2012-05-08 15:13 | DAY AND NIGHT - UNK | 95 | 0 | Yes | Yes | 20.1 | 20.2 | -0.1 | 66A07C29EE884314B41B0DEC2422CEA5 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-9636 |  | 2012-08-13 | 2012-08-13 13:22 | 2012-08-13 13:41 | BRYANT - 607CNXA42000AB | 181 | 6 | Yes | Yes | 24.1 | 21.2 | 2.9 | 2BB1B080413F4D638C0E1C2E0C8AC59D |  | R410A | Non-TXV |  | 3.315% | 0.96685 | 6.371% | [5 empty] | Non-TXV | 3.315%
Livingston | CA | 95334-9580 |  | 2012-07-31 | 2012-07-31 12:26 | 2012-07-31 12:37 | RUUD - UAKA-060JAS | 108 | 3.8 | Yes | Yes | 18.7 | 20.4 | -1.7 | 12C4BD283A704F77BF2D1D8A17A02ECC |  | R22 | Non-TXV |  | 3.519% | 0.96481 | 6.762% | [5 empty] | Non-TXV | 3.519%
Firebaugh | CA | 93622-9787 |  | 2012-05-31 | 2012-05-31 10:46 | 2012-05-31 11:03 | GOODMAN - PHC030-1F | 83 | 2.5 | Yes | Yes | 19.5 | 19.7 | -0.2 | F138BDCA102945F1BC04AF54EAFA8001 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Chico | CA | 95926-3059 |  | 2012-05-14 | 2012-05-14 11:45 | 2012-05-14 13:12 | DAY N NIGHT - 591ANX030000AAAA | 76 | -5.4 | Yes | Yes | 15.8 | 17.9 | -2.1 | 76E472BF38BE46AFADA6D5FD5B340BB9 |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Stockton | CA | 95207-3547 |  | 2012-08-08 | 2012-08-08 10:34 | 2012-08-08 10:34 | AMERICAN STANDARD - YCY030F1MOAA | 148 | 0 | Yes | Yes | 20.6 | 19.4 | 1.2 | D0EC2CBB74094FD6A612B0BC12FD8668 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9587 |  | 2012-05-30 | 2012-05-30 13:50 | 2012-05-30 14:06 | CARRIER - NA | 83 | 2.7 | Yes | Yes | 21.1 | 22.6 | -1.5 | 412C2B85E5C44EB7AB5B3813A32EA28F |  | R22 | Non-TXV |  | 3.253% | 0.96747 | 6.252% | [5 empty] | Non-TXV | 3.253%
Madera | CA | 93638-3720 |  | 2012-07-31 | 2012-07-31 18:25 | 2012-07-31 18:41 | RHEEM - HC1204818 | 80 | 2.8 | Yes | Yes | 17.9 | 20.4 | -2.5 | 23082DB450044FD3B5CA552964CA2875 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Livingston | CA | 95334-1610 |  | 2012-06-07 | 2012-06-07 09:31 | 2012-06-07 10:00 | GOODMAN - NA | 60 | 1.8 | Yes | Yes | 23 | 19.7 | 3.3 | AFEA761A8B22441793EC2D1D8D6859A4 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Auburn | CA | 95602-2140 |  | 2012-05-09 | 2012-05-09 16:55 | 2012-05-09 17:23 | G&E - UNK | 64 | 6 | Yes | Yes | 20 | 22.6 | -2.6 | 9D211193B87C4F70A387F792DC582A27 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Firebaugh | CA | 93622-9787 |  | 2012-05-31 | 2012-05-31 10:01 | 2012-05-31 10:23 | GOODMAN - PHK030-1F | 83 | 2.4 | Yes | Yes | 19.7 | 18.8 | 0.9 | 8EB8162A528542C58A3B853DB22E1D04 |  | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Livingston | CA | 95334-9562 |  | 2012-07-31 | 2012-07-31 11:50 | 2012-07-31 12:23 | RUUD - UNK | 232 | 8.2 | Yes | Yes | 16.9 | 18.5 | -1.6 | B9420DDC188945378029A56446C6FB53 |  | R22 | Non-TXV |  | 3.534% | 0.96466 | 6.792% | [5 empty] | Non-TXV | 3.534%
Manteca | CA | 95336-7054 |  | 2012-07-31 | 2012-07-31 15:11 | 2012-07-31 15:34 | CARRIER - 563CN042-C | 104 | 6.5 | Yes | Yes | 18.1 | 19.7 | -1.6 | BC88FAE230CC4B28943932AB378C9679 |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Auburn | CA | 95602-2219 |  | 2012-05-09 | 2012-05-09 13:19 | 2012-05-09 13:39 | OTHER - UNK | 45 | -4.2 | Yes | Yes | 16.5 | 19.1 | -2.6 | 6580883643A045FD9C6D7CC4CEEC0B59 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.333% | 1.0933 | 2.614% |  |  |  |  | Non-TXV |  |  | -9.333%
Lathrop | CA | 95330-8610 |  | 2012-08-09 | 2012-08-09 09:38 | 2012-08-09 09:55 | CARRIER - 24ABA360A300 | 140 | -8.2 | Yes | Yes | 22.1 | 19.9 | 2.2 | 1351CC9C664A44D0BF89D59E8BB5EE7E |  | R410A | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Livingston | CA | 95334-1631 |  | 2012-08-01 | 2012-08-01 09:35 | 2012-08-01 09:58 | RUUD - UNK | 58 | 2.3 | Yes | Yes | 18.8 | 20.9 | -2.1 | ACEECEFD7CBF4E2781F154EED1800B21 |  | R22 | Non-TXV |  | 3.966% | 0.96034 | 7.621% | [5 empty] | Non-TXV | 3.966%
Madera | CA | 93638-0561 |  | 2012-08-13 | 2012-08-13 12:08 | 2012-08-13 12:08 | YORK - D1NP030N05606A | 73 | 9.8 | Yes | Yes | 19.6 | 19.3 | 0.4 | 62478BFCD3534135B9ABF0147E296AB7 |  | R22 | Non-TXV |  | 13.42% | 0.86575 | 25.8% | [5 empty] | Non-TXV | 13.42%
Stockton | CA | 95205-3701 |  | 2012-08-10 | 2012-08-10 11:44 | 2012-08-10 12:04 | GMC - VSC130301BA | 87 | 6.1 | Yes | Yes | 18.3 | 20.4 | -2.1 | C1751C4287634E0B9A9E2FEF99316409 |  | R22 | Non-TXV |  | 7.011% | 0.92989 | 13.47% | [5 empty] | Non-TXV | 7.011%
Los Banos | CA | 93635-9495 |  | 2012-05-31 | 2012-05-31 10:44 | 2012-05-31 11:18 | BRYANT - 561CJ042-F | 93 | -3.6 | Yes | Yes | 14.9 | 17.5 | -2.6 | 5054DDD521B64EC596BC9ADCE96AEE82 |  | R22 | TXV |  | -3.871% | 1.0387 | 1.084% |  |  |  |  | TXV |  |  | -3.871%
Valley Springs | CA | 95252-9648 |  | 2012-08-13 | 2012-08-13 14:46 | 2012-08-13 14:46 | BDP - 561CJ060-A | 158 | 0 | Yes | Yes | 18.2 | 20.9 | -2.7 | F41FA26F12B044C99FC2CB2815C58A66 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3818 |  | 2012-05-11 | 2012-05-11 16:13 | 2012-05-11 16:13 | BRYANT - 561CJ030-E | 68 | 0 | Yes | Yes | 16.9 | 19.3 | -2.4 | 52B39B3D08FE4CCAA063A789761A96C4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3613 |  | 2012-05-07 | 2012-05-07 19:21 | 2012-05-07 19:21 | DAY & NIGHT - PGD336060K001C1 | 100 | 0 | Yes | Yes | 15.2 | 15.5 | -0.3 | C8A0CDB2870F460DA64156B7DCDBAD94 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-1901 |  | 2012-07-31 | 2012-07-31 13:21 | 2012-07-31 13:38 | YORK - H2RD036S06B | 96 | 5.2 | Yes | Yes | 15.6 | 15 | 0.6 | DE04C4F50E9F47529E4410E8FAB3478E |  | R22 | Non-TXV |  | 5.417% | 0.94583 | 10.41% | [5 empty] | Non-TXV | 5.417%
Fresno | CA | 93726-6208 |  | 2012-05-22 | 2012-05-22 12:42 | 2012-05-22 13:00 | YORK - DBYP-F060N080XA | 140 | 4.2 | Yes | Yes | 22.8 | 19.2 | 3.6 | 941D4663820240EB8C0DA35841BC309C |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Shingle Springs | CA | 95682-8352 |  | 2012-08-02 | 2012-08-02 10:18 | 2012-08-02 10:43 | COLEMAN - BRCS0361BD | 63 | 7.7 | Yes | Yes | 22.4 | 22.1 | 0.3 | 2C7F17E82FCB453C8BC4268C2FFF40FB | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.22% | 0.87778 | 23.49% | [5 empty] | Non-TXV | 12.22%
Clovis | CA | 93612-5011 |  | 2012-05-22 | 2012-05-22 13:48 | 2012-05-22 13:54 | TEMPSTAR - PGAD036DK2 | 75 | 2.2 | Yes | Yes | 24.4 | 22.6 | 1.8 | F042CDCAFED44224AD564FC16F9E5255 |  | R22 | Non-TXV |  | 2.933% | 0.97067 | 5.637% | [5 empty] | Non-TXV | 2.933%
Camino | CA | 95709-9505 |  | 2012-08-16 | 2012-08-16 15:02 | 2012-08-16 15:02 | GOODMAN - GSX130361BA | 89 | 0 | Yes | Yes | 24 | 21.9 | 2.1 | 9CD05B008BC442C1A5F653937E1F2B78 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4613 |  | 2012-08-01 | 2012-08-01 13:08 | 2012-08-01 13:25 | BRYANT - 113ANA024-D | 61 | 3.7 | Yes | Yes | 19.7 | 19.9 | -0.1 | 15C1FF41D03A4D8C95282652431397B3 |  | R410A | Non-TXV |  | 6.066% | 0.93934 | 11.66% | [5 empty] | Non-TXV | 6.066%
Paso Robles | CA | 93446-9369 |  | 2012-07-12 | 2012-07-12 09:14 | 2012-07-12 09:32 | DUCANE - AC10B24 | 60 | 1.8 | Yes | Yes | 25.9 | 21.3 | 4.7 | B408B7FE930544D390CD9E629990DEA0 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Merced | CA | 95340-2617 |  | 2012-08-08 | 2012-08-08 08:32 | 2012-08-08 08:57 | OTHER - D2GA030N048O6C | 80 | 8.1 | Yes | Yes | 10.6 | 12.8 | -2.2 | D4A5E8DC32F84FBE9ABE769E3C620267 |  | R22 | Non-TXV |  | 10.12% | 0.89875 | 19.46% | [5 empty] | Non-TXV | 10.12%
Stockton | CA | 95212-9487 |  | 2012-08-08 | 2012-08-08 14:27 | 2012-08-08 14:27 | GE - BGTA948H1B02 | 128 | 0 | Yes | Yes | 17.6 | 19 | -1.4 | 278D39A618A647F8A646BF7EFB2CEC56 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3236 |  | 2012-06-08 | 2012-06-08 15:25 | 2012-06-08 15:44 | BDP - 585B024050YACR | 51 | -3 | Yes | Yes | 28.5 | 22.5 | 6 | EB425D3863B04FD6AA27B506288EC680 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Stockton | CA | 95203-1439 |  | 2012-08-08 | 2012-08-08 17:33 | 2012-08-08 17:57 | RHEEM - RRKA-A024JK06X | 50 | 5.1 | Yes | Yes | 20.7 | 21 | -0.3 | 2B71EF6851E149F59037420B674050FA |  | R22 | Non-TXV |  | 10.2% | 0.898 | 19.6% | [5 empty] | Non-TXV | 10.2%
Chico | CA | 95926-3057 |  | 2012-05-14 | 2012-05-14 11:17 | 2012-05-14 11:31 | DAY N NIGHT - 591ANX030000AAAA | 76 | 4.6 | Yes | Yes | 19.5 | 21.3 | -1.8 | 51553F726DD0421CBDBF4C60D56B5D7D |  | R22 | Non-TXV |  | 6.053% | 0.93947 | 11.63% | [5 empty] | Non-TXV | 6.053%
Lathrop | CA | 95330-8938 |  | 2012-08-09 | 2012-08-09 15:28 | 2012-08-09 15:46 | GOODMAN - CKL49-1 | 99 | 3.1 | Yes | Yes | 18.2 | 20.5 | -2.3 | 7A530775917745EEBFB46FFBB96995C5 |  | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Chico | CA | 95926-2821 |  | 2012-05-07 | 2012-05-07 20:28 | 2012-05-07 20:46 | YORK - H2RD036506B | 85 | 4.6 | Yes | Yes | 19.5 | 22.2 | -2.7 | 5E3F318FFC0D4C3CB1B71E4CFA724CB1 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.412% | 0.94588 | 10.4% | [5 empty] | Non-TXV | 5.412%
Clovis | CA | 93611-4510 |  | 2012-05-10 | 2012-05-10 13:01 | 2012-05-10 13:19 | BDA COMPANY - 585A03608OYAC | 85 | 3.4 | Yes | Yes | 16.9 | 19.9 | -3 | 97BAB0BBE528417C90D24C9725EBDDFB |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Madera | CA | 93637-4231 |  | 2012-05-07 | 2012-05-07 17:31 | 2012-05-07 18:00 | CARRIER - 48KLAI24--300CBE | 68 | 2.2 | Yes | Yes | 23.3 | 23.5 | -0.2 | 955D73F598BB4674B5E4E148560DB395 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Madera | CA | 93637-4231 |  | 2012-05-07 | 2012-05-07 18:05 | 2012-05-07 18:23 | CARRIER - 48KLAI36--300CBE | 102 | 3 | Yes | Yes | 22.8 | 20.4 | 2.4 | A28EFC820EE34C4886C2AB272DB1EA1A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Clovis | CA | 93612-6005 |  | 2012-05-22 | 2012-05-22 10:53 | 2012-05-22 11:10 | CARRIER - UNK | 85 | 2.6 | Yes | Yes | 18.1 | 21 | -2.9 | C64006C7CC19400DABBC3BB2FCEBC177 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Stockton | CA | 95205-3057 |  | 2012-08-06 | 2012-08-06 10:48 | 2012-08-06 11:12 | GOODMAN - GPG1324070M41AA | 80 | 2.8 | Yes | Yes | 22.3 | 20.2 | 2.1 | 4C9329F05B624A44844EE9DD32D677C8 |  | R410A | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Willows | CA | 95988-3344 |  | 2012-08-15 | 2012-08-15 14:49 | 2012-08-15 17:37 | PAYNE - PA12NA042-A | 101 | 5.6 | Yes | Yes | 23.6 | 22 | 1.6 | 89D0C068AC694DCE99FACA1C86B1A871 |  | R22 | TXV |  | 5.545% | 0.94455 | 10.66% | [5 empty] | TXV | 5.545%
Planada | CA | 95365-0000 |  | 2012-05-22 | 2012-05-22 13:04 | 2012-05-22 13:22 | OTHER - EAFF-031JAZ | 96 | 3.7 | Yes | Yes | 18.4 | 18.8 | -0.4 | 4C4134C1064B4B94A7FAD24D97FEF000 |  | R22 | Non-TXV |  | 3.854% | 0.96146 | 7.407% | [5 empty] | Non-TXV | 3.854%
Chico | CA | 95926-2905 |  | 2012-08-01 | 2012-08-01 19:34 | 2012-08-01 20:27 | BRYANT - 563CN036-A | 50 | 1.5 | Yes | Yes | 20.8 | 21.8 | -1 | D398421E954B42E4A42D7EAC178553DA |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-6336 |  | 2012-05-24 | 2012-05-24 15:43 | 2012-05-24 15:43 | GOODMAN - CK30-1C | 76 | 0 | Yes | Yes | 21.1 | 23.4 | -2.3 | F71114384D664710B84D288945306A3E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dos Palos | CA | 93620-2661 |  | 2012-08-01 | 2012-08-01 11:34 | 2012-08-01 11:54 | CARRIER - 38CKC030340 | 72 | 3.2 | Yes | Yes | 21.1 | 20.4 | 0.7 | CB0C402582CE469784E0704B24D339B0 |  | R22 | Non-TXV |  | 4.444% | 0.95556 | 8.541% | [5 empty] | Non-TXV | 4.444%
Manteca | CA | 95336-7031 |  | 2012-08-07 | 2012-08-07 14:16 | 2012-08-07 14:38 | BRYANT - 563CN036-C | 101 | 3.3 | Yes | Yes | 19.3 | 21.3 | -2 | 91117A27F48149E0926951B5ADEC2C53 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.267% | 0.96733 | 6.279% | [5 empty] | Non-TXV | 3.267%
Madera | CA | 93637-8654 |  | 2012-07-31 | 2012-07-31 12:48 | 2012-07-31 13:05 | CARRIER - 38BRC060360 | 200 | 7.3 | Yes | Yes | 21.7 | 21 | 0.7 | 4F7D12B669474BE0ABAA65B3186A7FFA |  | R22 | TXV |  | 3.65% | 0.9635 | 7.014% | [5 empty] | TXV | 3.65%
Madera | CA | 93637-8654 |  | 2012-07-31 | 2012-07-31 13:08 | 2012-07-31 14:18 | YORK - D2NP024N05606A | 100 | 3 | Yes | Yes | 23.7 | 20.4 | 3.3 | F48A428675A44FE0A6996A96351153F3 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Olivehurst | CA | 95961-0000 |  | 2012-05-17 | 2012-05-17 16:37 | 2012-05-17 16:55 | LENNOX - GSC10-411-75-1P | 71 | 11.1 | Yes | Yes | 17 | 19.7 | -2.7 | 6DFC3602DD8543D89AB591A5C43137B0 |  | R22 | Non-TXV |  | 15.63% | 0.84366 | 30.04% | [5 empty] | Non-TXV | 15.63%
Marysville | CA | 95901-4403 |  | 2012-08-13 | 2012-08-13 15:13 | 2012-08-13 15:13 | BRYANT - 577CNWA30060NA-- | 90 | 0 | Yes | Yes | 20.4 | 19.3 | 1.1 | 042744383E5145B293CE501E4D5B70E4 |  | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-4134 |  | 2012-08-01 | 2012-08-01 13:41 | 2012-08-01 13:57 | DAY & NIGHT - 561AJ036-B | 73 | 12.4 | Yes | Yes | 22.9 | 20.2 | 2.8 | F15FB013BE874082870CFC80A329C8FA |  | R22 | Non-TXV |  | 16.99% | 0.83014 | 32.64% | [5 empty] | Non-TXV | 16.99%
Stockton | CA | 95204-3335 |  | 2012-08-16 | 2012-08-16 09:00 | 2012-08-16 09:17 | ICP - PGC042K080E | 84 | 4.3 | Yes | Yes | 20.1 | 20.3 | -0.2 | E52DA2D311CC48AF9BCBC12E5F1A8134 |  | R22 | Non-TXV |  | 5.119% | 0.94881 | 9.838% | [5 empty] | Non-TXV | 5.119%
Stockton | CA | 95212-1019 |  | 2012-08-07 | 2012-08-07 15:50 | 2012-08-07 16:15 | BRYANT - 561AJX036-D | 74 | 12.6 | Yes | Yes | 19.5 | 22.5 | -3 | FEC49043B2524CF2A5B52AB432DD19D7 |  | R22 | Non-TXV |  | 17.03% | 0.82973 | 32.72% | [5 empty] | Non-TXV | 17.03%
Madera | CA | 93637-6505 |  | 2012-07-05 | 2012-07-05 11:32 | 2012-07-05 12:01 | YORK - H2RD036S06B | 96 | 3.9 | Yes | Yes | 23.4 | 19.5 | 3.9 | 6F50EAB7C5CD4748B22614D5F82E5410 |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Marysville | CA | 95901-3101 |  | 2012-08-16 | 2012-08-16 15:06 | 2012-08-16 15:31 | GOODMAN - SSX140481AE | 189 | 5.7 | Yes | Yes | 20 | 19.3 | 0.7 | 3BDEDC4B6C6244C68D188AC55905077F |  | R410A | TXV |  | 3.016% | 0.96984 | 5.796% | [5 empty] | TXV | 3.016%
Dos Palos | CA | 93620-2150 |  | 2012-07-31 | 2012-07-31 10:37 | 2012-07-31 11:12 | GOODMAN - CK42-1C | 92 | -5.4 | Yes | Yes | 17.7 | 19.1 | -1.4 | 15C09B4C5C3141338A6C618ABFECE82C |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Marysville | CA | 95901-8241 |  | 2012-07-31 | 2012-07-31 10:23 | 2012-07-31 10:45 | CARRIER - 38KC036350 | 75 | -7.1 | Yes | Yes | 14 | 16.9 | -2.9 | 8110F0E5EA1C45968ED880C78A7C4772 |  | R22 | Non-TXV |  | -9.467% | 1.0947 | 2.651% |  |  |  |  | Non-TXV |  |  | -9.467%
Valley Springs | CA | 95252-8858 |  | 2012-08-13 | 2012-08-13 10:22 | 2012-08-13 10:40 | WHIRLPOOL - D1NA030N05606C | 76 | 2.3 | Yes | Yes | 20.5 | 20.4 | 0.1 | 5699037A16114FF89144165DBDE99E4F |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Los Banos | CA | 93635-9431 |  | 2012-08-16 | 2012-08-16 12:31 | 2012-08-16 12:58 | BRYANT - 561CJ060A | 152 | 12.5 | Yes | Yes | 26.4 | 20.4 | 6 | D5CA5136AA8049B7867C63A627F3C84D |  | R22 | Non-TXV |  | 8.224% | 0.91776 | 15.8% | [5 empty] | Non-TXV | 8.224%
Dos Palos | CA | 93620-2679 |  | 2012-08-03 | 2012-08-03 12:01 | 2012-08-03 12:28 | LENNOX - 13ACD04823002 | 204 | 10.7 | Yes | Yes | 18.4 | 20.4 | -2 | FF6FFB7DAC724AEB96CBC446E01F4B4C |  | R22 | Non-TXV |  | 5.245% | 0.94755 | 10.08% | [5 empty] | Non-TXV | 5.245%
Livingston | CA | 95334-1730 |  | 2012-07-31 | 2012-07-31 09:50 | 2012-07-31 10:11 | ARCOAIRE - NPGAD36D1K4 | 85 | 3.7 | Yes | Yes | 20.8 | 20.5 | 0.3 | 17B08839877F4C85AF5F733A92BEB326 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Dos Palos | CA | 93620-2691 |  | 2012-08-07 | 2012-08-07 15:25 | 2012-08-07 15:49 | OTHER - UNK | 118 | 12.6 | Yes | Yes | 27.1 | 22.7 | 4.4 | 266DFD66661F461CB8573DAAD3888FCE |  | R22 | Non-TXV |  | 10.68% | 0.89322 | 20.52% | [5 empty] | Non-TXV | 10.68%
Winton | CA | 95388-9705 |  | 2012-05-24 | 2012-05-24 14:50 | 2012-05-24 14:50 | CARRIER - 48GS-030060301 | 55 | 0 | Yes | Yes | 2.5 | 21.1 | -18.6 | 35BBF0AE16654DCE8AE4A5709DB2346F | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6607 |  | 2012-08-06 | 2012-08-06 18:21 | 2012-08-06 18:46 | BRYANT - 574BNW060115NB | 210 | 6.2 | Yes | Yes | 18.5 | 21 | -2.5 | BC48F370EB5A454CA2AC84DA6E66CE79 |  | R410A | Non-TXV |  | 2.952% | 0.97048 | 5.674% | [5 empty] | Non-TXV | 2.952%
Magalia | CA | 95954-9669 |  | 2012-08-13 | 2012-08-13 09:37 | 2012-08-13 09:52 | BRYANT - 582ANW036090AAAF | 56 | 3 | Yes | Yes | 20.4 | 20.2 | 0.3 | 47CF093BA38A4BFFA4E6183CBDB6F32A |  | R22 | Non-TXV |  | 5.357% | 0.94643 | 10.3% | [5 empty] | Non-TXV | 5.357%
Winton | CA | 95388-9705 |  | 2012-08-08 | 2012-08-08 10:22 | 2012-08-08 10:39 | AMERICAN STANDARD - YCY042F1M0AA | 133 | -7.8 | Yes | Yes | 26.8 | 22.8 | 4.1 | 6D0DA553F7014C30BCE0EA97DCFD3FBE |  | R22 | Non-TXV |  | -5.865% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.865%
Williams | CA | 95987-9012 |  | 2012-07-26 | 2012-07-26 08:57 | 2012-07-26 09:18 | GIBSON - JS3BA-018KA | 63 | 5.4 | Yes | Yes | 18 | 19.2 | -1.2 | CBFDFDF4AF074D8FBA03A75697606444 |  | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Copperopolis | CA | 95228-9693 |  | 2012-07-17 | 2012-07-17 13:45 | 2012-07-17 14:03 | TRANE - 4TTX4036A1000AA | 91 | 2.8 | Yes | Yes | 21.6 | 20.4 | 1.2 | 9D8CCF6C13CB45D9AC0731F8ED7F2523 |  | R410A | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95206-1851 |  | 2012-08-07 | 2012-08-07 14:13 | 2012-08-07 14:13 | GOODMAN - CKJ30-1A | 92 | 0 | Yes | Yes | 12 | 12.7 | -0.7 | C5DDAF9BA249400D8C7A2ACBD2CE282F | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-5600 |  | 2012-05-09 | 2012-05-09 14:44 | 2012-05-09 15:04 | HEIL - UNK | 85 | 3.2 | Yes | Yes | 23.2 | 22.2 | 1 | E6553C86924A4E4681D25CE4520E12CC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.765% | 0.96235 | 7.235% | [5 empty] | Non-TXV | 3.765%
Merced | CA | 95340-5033 |  | 2012-08-06 | 2012-08-06 12:51 | 2012-08-06 13:13 | RHEEM - RRNAA036JK08X | 114 | 15.2 | Yes | Yes | 20.4 | 19.2 | 1.2 | F56B3B1D291A423CAF025D3311CFC473 |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Stockton | CA | 95205-4664 |  | 2012-08-06 | 2012-08-06 13:01 | 2012-08-06 13:28 | OTHER - 4AC13L18P | 61 | 2 | Yes | Yes | 19.1 | 20.4 | -1.3 | DE908368A5C94359A6E6A84C218330BD |  | R410A | Non-TXV |  | 3.279% | 0.96721 | 6.301% | [5 empty] | Non-TXV | 3.279%
Los Banos | CA | 93635-3228 |  | 2012-07-23 | 2012-07-23 08:52 | 2012-07-23 09:11 | BRYANT - 582NW024040AAAD | 53 | 2 | Yes | Yes | 20 | 19.5 | 0.5 | EC9E606A1C98474AB51A897F69396A97 |  | R22 | TXV |  | 3.774% | 0.96226 | 7.252% | [5 empty] | TXV | 3.774%
Stockton | CA | 95212-1616 |  | 2012-08-13 | 2012-08-13 11:35 | 2012-08-13 11:35 | HEIL - PGDA36D1KE---- | 100 | 0 | Yes | Yes | 18.7 | 17.7 | 1 | C15F877208AF47208851B262E8CE89B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-4269 |  | 2012-08-03 | 2012-08-03 12:02 | 2012-08-03 12:40 | CARRIER - 24ACC648A300 | 71 | 4.3 | Yes | Yes | 20.2 | 20.9 | -0.7 | 04DDBB039B3642879A3135BC8B367D03 |  | R410A | TXV |  | 6.056% | 0.93944 | 11.64% | [5 empty] | TXV | 6.056%
Dos Palos | CA | 93620-2133 |  | 2012-08-03 | 2012-08-03 08:44 | 2012-08-03 09:03 | AIRE-FLO - RRNAB036JK06X | 83 | 10.6 | Yes | Yes | 24.2 | 23 | 1.2 | 27E142F1BEF6454984B02D9A1DF5BC6B |  | R22 | Non-TXV |  | 12.77% | 0.87229 | 24.54% | [5 empty] | Non-TXV | 12.77%
Madera | CA | 93637-5035 |  | 2012-06-08 | 2012-06-08 15:23 | 2012-06-08 15:23 | CARRIER - 38BRC030323 | 77 | 0 | Yes | Yes | 24.4 | 20.4 | 4 | 8BA5F8B4EE6249B085EFF316FCD2D903 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-9504 |  | 2012-08-16 | 2012-08-16 11:16 | 2012-08-16 11:34 | RHEEM - RAKA-042JAZ | 79 | 2.6 | Yes | Yes | 25.6 | 23.1 | 2.5 | 475E31BC5EC540CB8C9B03FE573E9851 |  | R22 | Non-TXV |  | 3.291% | 0.96709 | 6.325% | [5 empty] | Non-TXV | 3.291%
Madera | CA | 93638-3364 |  | 2012-06-15 | 2012-06-15 10:53 | 2012-06-15 11:14 | AIRE-FLO - D5YS018N03206A | 52 | 5.1 | Yes | Yes | 23.1 | 19.9 | 3.2 | F62F16CFC4F6416BBFF0B0D3A6E8746C |  | R22 | Non-TXV |  | 9.808% | 0.90192 | 18.85% | [5 empty] | Non-TXV | 9.808%
Merced | CA | 95341-6542 |  | 2012-06-12 | 2012-06-12 12:02 | 2012-06-12 13:07 | YORK - D1NA030N05606C | 76 | 2.5 | Yes | Yes | 18.9 | 21.4 | -2.5 | 067653E7D1FD4484AA9237AB518159A5 |  | R22 | Non-TXV |  | 3.289% | 0.96711 | 6.322% | [5 empty] | Non-TXV | 3.289%
Manteca | CA | 95336-3265 |  | 2012-08-07 | 2012-08-07 16:02 | 2012-08-07 16:29 | TRANE - BTD730A100A0 | 74 | 2.4 | Yes | Yes | 19.4 | 20.9 | -1.5 | 0C36C10E227A4CE9858AFA16A0FAE50A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.243% | 0.96757 | 6.233% | [5 empty] | Non-TXV | 3.243%
Madera | CA | 93638-3364 |  | 2012-06-12 | 2012-06-12 10:03 | 2012-06-12 10:33 | YORK - D5YS018N03206A | 52 | 2.5 | Yes | Yes | 17 | 19.7 | -2.7 | D1A2BB2F7E654D9C88A0A8C867E60B83 |  | R22 | Non-TXV |  | 4.808% | 0.95192 | 9.239% | [5 empty] | Non-TXV | 4.808%
Valley Springs | CA | 95252-9555 |  | 2012-07-05 | 2012-07-05 10:34 | 2012-07-05 10:53 | RUUD - UNK | 76 | -4.5 | Yes | Yes | 27 | 21 | 6 | E546473BF8884AD4A0FA377CFB5250EA |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Merced | CA | 95340-3560 |  | 2012-05-07 | 2012-05-07 15:45 | 2012-05-07 16:04 | INTERNATIONAL COMFORT - PGC036K06B | 71 | 4.8 | Yes | Yes | 23 | 21.5 | 1.5 | ABFFB4966C8744CD891228D285DD7597 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6.761% | 0.93239 | 12.99% | [5 empty] | Non-TXV | 6.761%
Gustine | CA | 95322-1822 |  | 2012-08-13 | 2012-08-13 12:18 | 2012-08-13 12:40 | PAYNE - PY3PNA042060NB | 120 | 9.7 | Yes | Yes | 25.1 | 20.4 | 4.7 | D3DE799BABA7492BA2767BA4D88AD9D6 |  | R22 | Non-TXV |  | 8.083% | 0.91917 | 15.53% | [5 empty] | Non-TXV | 8.083%
Fresno | CA | 93711-2639 |  | 2012-05-14 | 2012-05-14 12:25 | 2012-05-14 13:00 | PAYNE - N/A | 72 | 7.5 | Yes | Yes | 23.4 | 19.9 | 3.5 | EFF6E9381E4446D6B0159F7A5547E03E |  | R22 | Non-TXV |  | 10.42% | 0.89583 | 20.02% | [5 empty] | Non-TXV | 10.42%
Stockton | CA | 95207-1917 |  | 2012-05-31 | 2012-05-31 12:27 | 2012-05-31 12:44 | LENNOX - HS25-311-1P | 129 | 8.7 | Yes | Yes | 23 | 19.5 | 3.5 | 6EE1031E5177464D90F39E098537ECEA |  | R22 | TXV |  | 6.744% | 0.93256 | 12.96% | [5 empty] | TXV | 6.744%
Clovis | CA | 93612-4608 |  | 2012-07-10 | 2012-07-10 08:29 | 2012-07-10 08:50 | PAYNE - 585A0360BDYAC | 60 | 1.8 | Yes | Yes | 21.9 | 19.3 | 2.6 | 9FF01CC1506041BDB1644D16BFC2C169 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95210-1162 |  | 2012-05-18 | 2012-05-18 14:59 | 2012-05-18 15:18 | FRIGIDAIRE - UNK | 50 | -2.9 | Yes | Yes | 25.8 | 22.1 | 3.8 | 3D753F5CBAA049CE9230C5CB7A9F7496 |  | R22 | Non-TXV |  | -5.8% | 1.058 | 1.624% |  |  |  |  | Non-TXV |  |  | -5.8%
Madera | CA | 93637-4218 |  | 2012-05-07 | 2012-05-07 11:23 | 2012-05-07 11:45 | YORK - D1NP048N09006A | 140 | 4.7 | Yes | Yes | 24 | 20.7 | 3.3 | 3AF2DFE88B8B4C3885261411DBA03108 |  | R22 | Non-TXV |  | 3.357% | 0.96643 | 6.452% | [5 empty] | Non-TXV | 3.357%
Stockton | CA | 95209-3906 |  | 2012-08-08 | 2012-08-08 12:54 | 2012-08-08 12:54 | GOODMAN - CKJ36-1AB | 97 | 0 | Yes | Yes | 17.9 | 19.2 | -1.3 | 39CE0F2F4CA54D4EB34656A58DCA1ED2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-4231 |  | 2012-08-01 | 2012-08-01 13:06 | 2012-08-01 13:26 | YORK - D1NH060N11006C | 140 | 4.2 | Yes | Yes | 25.4 | 20.8 | 4.6 | 9BCCC9A5AECA41C7A54CEDBE1ED8D1E0 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-8805 |  | 2012-05-31 | 2012-05-31 09:01 | 2012-05-31 09:37 | BRYANT - 561CJ042-F | 93 | 10.1 | Yes | Yes | 18.3 | 21 | -2.7 | C9EE0B121C484E11B0998B69CF8F3B14 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 10.86% | 0.8914 | 20.87% | [5 empty] | Non-TXV | 10.86%
Livingston | CA | 95334-1625 |  | 2012-05-08 | 2012-05-08 16:44 | 2012-05-08 17:02 | CARRIER - 48SS-030040321 | 54 | 5.8 | Yes | Yes | 20 | 20.9 | -0.9 | 41A112DF65CD41BB8570F93F0871A1CA | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.74% | 0.89259 | 20.64% | [5 empty] | Non-TXV | 10.74%
Valley Springs | CA | 95252-8402 |  | 2012-08-13 | 2012-08-13 08:47 | 2012-08-13 09:06 | PAYNE - 591ANX030000ABAA | 68 | -4 | Yes | Yes | 25.4 | 22 | 3.4 | C9738D8FB13E4986A29D5423E0425C78 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Winton | CA | 95388-9301 |  | 2012-08-01 | 2012-08-01 11:40 | 2012-08-01 12:05 | BDP - 588AN03060AAAD | 52 | 3.8 | Yes | Yes | 19.6 | 17.9 | 1.8 | F1DC787D7D14482C80C44F33CC8B97AB |  | R22 | Non-TXV |  | 7.308% | 0.92692 | 14.04% | [5 empty] | Non-TXV | 7.308%
Madera | CA | 93637-8656 |  | 2012-07-31 | 2012-07-31 13:44 | 2012-07-31 14:18 | UNITARY PRODUCTS GROUP - H2RD060S06B | 162 | 7.6 | Yes | Yes | 23 | 21 | 2 | 795D17706F444F2EB3F615AE6CAA30A0 |  | R22 | Non-TXV |  | 4.691% | 0.95309 | 9.016% | [5 empty] | Non-TXV | 4.691%
Fresno | CA | 93726-2915 |  | 2012-05-09 | 2012-05-09 15:30 | 2012-05-09 15:47 | GOODMAN - CKL36-1H | 85 | 2.5 | Yes | Yes | 17.2 | 18.3 | -1.1 | 70CDE34FD5B54174A1F1AF648F5023C2 |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Lathrop | CA | 95330-8895 |  | 2012-08-09 | 2012-08-09 10:24 | 2012-08-09 10:43 | CARRIER - 24ABA348A300 | 127 | 24.5 | Yes | Yes | 17.8 | 20.4 | -2.6 | 7E80142525364924BF92A281BEEB5042 |  | R410A | Non-TXV |  | 19.29% | 0.80709 | 37.07% | [5 empty] | Non-TXV | 19.29%
Madera | CA | 93638-3364 |  | 2012-06-12 | 2012-06-12 12:12 | 2012-06-12 12:41 | YORK - D5YSO18NO3206A | 52 | 5.6 | Yes | Yes | 18.1 | 19.5 | -1.4 | 64CD067817394F1BBC25F540F5CE69FF |  | R22 | Non-TXV |  | 10.77% | 0.89231 | 20.7% | [5 empty] | Non-TXV | 10.77%
Winton | CA | 95388-9348 |  | 2012-08-02 | 2012-08-02 12:56 | 2012-08-02 13:40 | DAY & NIGHT - 595HUW024040ABAE | 68 | 7.6 | Yes | Yes | 25 | 20 | 5.1 | 98F8E5D3609346BE8E537F8E79B44908 |  | R22 | Non-TXV |  | 11.18% | 0.88824 | 21.48% | [5 empty] | Non-TXV | 11.18%
Stockton | CA | 95210-3201 |  | 2012-06-11 | 2012-06-11 12:28 | 2012-06-11 12:45 | GOODMAN - GPG13360701AC | 112 | 5.3 | Yes | Yes | 27.2 | 22.6 | 4.6 | DC68A7905F1641EA9077D8A5CB10B771 |  | R22 | Non-TXV |  | 4.732% | 0.95268 | 9.094% | [5 empty] | Non-TXV | 4.732%
Dos Palos | CA | 93620-2670 |  | 2012-07-31 | 2012-07-31 14:47 | 2012-07-31 15:07 | LENNOX - JS3BC-030KA | 68 | -7 | Yes | Yes | 17.3 | 18.3 | -1 | AB0823B108B34460A14C5D4BFE1F1BB9 |  | R22 | TXV |  | -10.29% | 1.1029 | 2.883% |  |  |  |  | TXV |  |  | -10.29%
Lathrop | CA | 95330-8914 |  | 2012-08-09 | 2012-08-09 12:08 | 2012-08-09 12:26 | GOODMAN - CKJ48-1A | 118 | 3.7 | Yes | Yes | 20.5 | 19.2 | 1.3 | CBE8046C2E4D4F63A79E98642BB9F2FA |  | R22 | Non-TXV |  | 3.136% | 0.96864 | 6.026% | [5 empty] | Non-TXV | 3.136%
Stockton | CA | 95207-4603 |  | 2012-06-22 | 2012-06-22 09:35 | 2012-06-22 09:53 | DAY & NIGHT - 569CB060 | 150 | 14.6 | Yes | Yes | 21.9 | 17.5 | 4.5 | 6877191B4C43478E91721E80C46761D2 |  | R22 | Non-TXV |  | 9.733% | 0.90267 | 18.71% | [5 empty] | Non-TXV | 9.733%
Manteca | CA | 95336-8537 |  | 2012-08-02 | 2012-08-02 14:00 | 2012-08-02 14:20 | YORK - H1RA048S06D | 117 | 3.5 | Yes | Yes | 18.1 | 20.8 | -2.7 | D237ED9E05BA4A3392230AD90CE7EF57 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Stockton | CA | 95209-1590 |  | 2012-08-01 | 2012-08-01 16:09 | 2012-08-01 16:31 | DAY & NIGHT - 585A042100YACR | 89 | 5.5 | Yes | Yes | 22.9 | 21.7 | 1.2 | 231798387A38425193C640F0EC915E90 |  | R22 | Non-TXV |  | 6.18% | 0.9382 | 11.88% | [5 empty] | Non-TXV | 6.18%
Manteca | CA | 95336-3627 |  | 2012-08-01 | 2012-08-01 10:39 | 2012-08-01 11:03 | RUUD - UNK | 56 | 2.4 | Yes | Yes | 18.4 | 18.8 | -0.4 | F1431979848D4B47AFC833F77FCBF0D8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Dos Palos | CA | 93620-2679 |  | 2012-07-31 | 2012-07-31 12:27 | 2012-07-31 12:45 | LENNOX - 13ACD-042-230-02 | 111 | 4.2 | Yes | Yes | 20.7 | 19.9 | 0.8 | 112952BE8A0048D996992F692B6C5374 |  | R22 | TXV |  | 3.784% | 0.96216 | 7.272% | [5 empty] | TXV | 3.784%
Winton | CA | 95388-9707 |  | 2012-05-09 | 2012-05-09 11:01 | 2012-05-09 11:22 | TRANE - 4YCC3036A1064AB | 124 | 3.7 | Yes | Yes | 22.8 | 19.9 | 2.9 | FCB391AFBADD4388A6BB64A8013114F2 | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 2.984% | 0.97016 | 5.734% | [5 empty] | Non-TXV | 2.984%
Manteca | CA | 95337-8590 |  | 2012-08-02 | 2012-08-02 17:04 | 2012-08-02 17:31 | RHEEM - RAMB-060JAZ | 192 | 9.5 | Yes | Yes | 19.2 | 20.2 | -1 | 0FFBE7080F3B47E7A6EF60690648EB7A |  | R22 | Non-TXV |  | 4.948% | 0.95052 | 9.509% | [5 empty] | Non-TXV | 4.948%
Dos Palos | CA | 93620-2684 |  | 2012-07-31 | 2012-07-31 13:45 | 2012-07-31 13:45 | LENNOX - 13ACD-048-230-03 | 152 | 0 | Yes | Yes | 16.3 | 19.2 | -2.9 | AD00CE507BF9408F8D786C83C39ECE40 |  | R22 | TXV |  | 0% | 1 | 0%
Madera | CA | 93638-1969 |  | 2012-06-12 | 2012-06-12 11:19 | 2012-06-12 11:19 | YORK - H2RD060S06B | 162 | 0 | Yes | Yes | 22.6 | 20.7 | 1.9 | 68DC840DFC574171A082837AD763402F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Dos Palos | CA | 93620-2677 |  | 2012-08-03 | 2012-08-03 11:22 | 2012-08-03 11:47 | LENNOX - 13ACD03623002 | 111 | 9.7 | Yes | Yes | 21 | 20.8 | 0.2 | 6D3319D71F6D42F2A27A37FD7221BEC4 |  | R22 | Non-TXV |  | 8.739% | 0.91261 | 16.79% | [5 empty] | Non-TXV | 8.739%
Madera | CA | 93638-9674 |  | 2012-06-13 | 2012-06-13 08:38 | 2012-06-13 09:00 | AMANA - APG13360451AC | 112 | -5.9 | Yes | Yes | 25.1 | 19.4 | 5.7 | 9A66913BCBB64AC09E7BA4A274DD7C2D |  | R22 | TXV |  | -5.268% | 1.0527 | 1.475% |  |  |  |  | TXV |  |  | -5.268%
Selma | CA | 93662-9512 |  | 2012-05-18 | 2012-05-18 15:24 | 2012-05-18 15:56 | DAY & NIGHT - N/A | 120 | 18.2 | Yes | Yes | 23.5 | 17.7 | 5.8 | 900AFD230C8E488E9F48E6223BD1096D |  | R22 | Non-TXV |  | 15.17% | 0.84833 | 29.15% | [5 empty] | Non-TXV | 15.17%
Fresno | CA | 93725-1744 |  | 2012-05-16 | 2012-05-16 14:34 | 2012-05-16 14:34 | YORK - D1NA024N03606C | 54 | 0 | Yes | Yes | 23 | 20.5 | 2.6 | 7AEECDE1BBA84D67A8650A668A1C2C1B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-7817 |  | 2012-08-06 | 2012-08-06 13:31 | 2012-08-06 13:52 | BRYANT - 113RNA042-B | 117 | 4.3 | Yes | Yes | 19 | 20.2 | -1.2 | 14CC1BC82F5F47DF88BA317952EA518A |  | R22 | Non-TXV |  | 3.675% | 0.96325 | 7.063% | [5 empty] | Non-TXV | 3.675%
Stockton | CA | 95205-5727 |  | 2012-08-06 | 2012-08-06 14:51 | 2012-08-06 15:08 | YORK - H2RD036S06A | 96 | 4.2 | Yes | Yes | 19.6 | 19.5 | 0.1 | F1507FEA9C3B41EFA0F54B2CB30C242B |  | R22 | Non-TXV |  | 4.375% | 0.95625 | 8.408% | [5 empty] | Non-TXV | 4.375%
Stockton | CA | 95206-6413 |  | 2012-05-07 | 2012-05-07 14:16 | 2012-05-07 14:36 | CARRIER - 38BRC036---341-- | 100 | 8.5 | Yes | Yes | 25 | 23.2 | 1.8 | D0B57069D2B24DAAB4B009056FD5BC82 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Stockton | CA | 95219-7191 |  | 2012-08-15 | 2012-08-15 14:53 | 2012-08-15 15:12 | GOODMAN - CKL49-A | 112 | 4 | Yes | Yes | 17.4 | 18.9 | -1.5 | B03B614ABB734C64A447BF4B39634F34 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Stockton | CA | 95206-5305 |  | 2012-08-15 | 2012-08-15 10:58 | 2012-08-15 11:18 | YORK - H1CB030S06 | 79 | 9.2 | Yes | Yes | 17 | 19.3 | -2.3 | 2EC521A553C04DCC922E19957AD56252 |  | R22 | Non-TXV |  | 11.65% | 0.88354 | 22.38% | [5 empty] | Non-TXV | 11.65%
Winton | CA | 95388-9300 |  | 2012-06-11 | 2012-06-11 15:01 | 2012-06-11 15:37 | BDP - 5A5HJ024040 | 67 | 11.4 | Yes | Yes | 18.4 | 20.8 | -2.4 | C2C6186A2FB24FFA8C59F7277205634F |  | R22 | Non-TXV |  | 17.01% | 0.82985 | 32.7% | [5 empty] | Non-TXV | 17.01%
Atwater | CA | 95301-4774 |  | 2012-08-15 | 2012-08-15 13:16 | 2012-08-15 13:33 | BRYANT - 561CJ024-C | 69 | -6.3 | Yes | Yes | 22.4 | 17.9 | 4.5 | B6D0EDE8792341D4ABCB48192981D443 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | -9.13% | 1.0913 | 2.557% |  |  |  |  | TXV |  |  | -9.13%
Winton | CA | 95388-9769 |  | 2012-08-03 | 2012-08-03 10:44 | 2012-08-03 11:11 | CARRIER - 48SX-036060331AA | 84 | 7.1 | Yes | Yes | 25.7 | 22 | 3.7 | 50BA9380517345BA8BE7F3FE44B95BF7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.452% | 0.91548 | 16.24% | [5 empty] | Non-TXV | 8.452%
Tracy | CA | 95377-8276 |  | 2012-06-25 | 2012-06-25 14:53 | 2012-06-25 15:17 | LENNOX - 13ACD-060-230-02 | 214 | 7.8 | Yes | Yes | 19.2 | 20.1 | -0.9 | 33422EB7473C4C69B71558E3127F3486 |  | R22 | TXV |  | 3.645% | 0.96355 | 7.005% | [5 empty] | TXV | 3.645%
Stockton | CA | 95204-2754 |  | 2012-08-01 | 2012-08-01 12:05 | 2012-08-01 12:26 | CARRIER - 38GS036330 | 56 | 9 | Yes | Yes | 19.1 | 18 | 1.1 | E971B1FF645A43498FB02C2D647DCDF9 |  | R22 | Non-TXV |  | 16.07% | 0.83929 | 30.89% | [5 empty] | Non-TXV | 16.07%
Fresno | CA | 93727-4424 |  | 2012-05-16 | 2012-05-16 11:32 | 2012-05-16 11:52 | YORK - AC024M1021CG | 52 | 9.5 | Yes | Yes | 16.4 | 17.9 | -1.5 | 85AC319EF126468B91E14584A7BCA460 |  | R22 | Non-TXV |  | 18.27% | 0.81731 | 35.11% | [5 empty] | Non-TXV | 18.27%
Tracy | CA | 95377-6632 |  | 2012-08-13 | 2012-08-13 14:37 | 2012-08-13 14:59 | UNITARY PRODUCTS GROUP - BRCS0601BD | 118 | 3.6 | Yes | Yes | 23.5 | 17.6 | 5.9 | 584BDF6415034238A585058BBF4AD26E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.051% | 0.96949 | 5.863% | [5 empty] | Non-TXV | 3.051%
Atwater | CA | 95301-4449 |  | 2012-05-11 | 2012-05-11 11:12 | 2012-05-11 11:30 | GOODMAN - PGB030075-1 | 56 | 1.7 | Yes | Yes | 23.8 | 20.4 | 3.4 | E3F66DF3842440E9957BB622C7AE02DF | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Stockton | CA | 95210-1150 |  | 2012-05-07 | 2012-05-07 11:58 | 2012-05-07 11:58 | BDP - 567C030RCU | 63 | 0 | Yes | Yes | 19.2 | 19.9 | -0.7 | DB70380F154D413999E47E5307C7BB6F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-8353 |  | 2012-08-01 | 2012-08-01 15:00 | 2012-08-01 15:25 | YORK - H2RD060S06B | 162 | 24.6 | Yes | Yes | 18.4 | 20.2 | -1.8 | 6E613B103A764E0B835590DD1584E747 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.19% | 0.84815 | 29.18% | [5 empty] | Non-TXV | 15.19%
Fresno | CA | 93722-3119 |  | 2012-06-07 | 2012-06-07 14:40 | 2012-06-07 14:57 | CARRIER - 8NLT036---32 | 70 | 2.1 | Yes | Yes | 17.7 | 20.4 | -2.7 | ED3CF09AED5646B6B029C2A63FF8CC1A |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-4538 |  | 2012-07-06 | 2012-07-06 13:28 | 2012-07-06 13:51 | GOODMAN - PGB024050-1 | 54 | 1.6 | Yes | Yes | 20.4 | 20.2 | 0.3 | EDE719B2CD09409F9375B2A729442B44 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Tracy | CA | 95377-2289 |  | 2012-08-13 | 2012-08-13 11:19 | 2012-08-13 11:42 | BRYANT - 561CJ060-A | 153 | 19.3 | Yes | Yes | 24.9 | 19.1 | 5.8 | 564C40F13D7E4249AB14691B649F4E32 |  | R22 | TXV |  | 12.61% | 0.87386 | 24.24% | [5 empty] | TXV | 12.61%
Manteca | CA | 95336-7055 |  | 2012-07-31 | 2012-07-31 14:29 | 2012-07-31 15:09 | GOODMAN - GCC130601BC | 169 | 5 | Yes | Yes | 18 | 19.7 | -1.7 | F5B16E84E22044E5B4D96D808A4BFBC2 |  | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.686% | [5 empty] | Non-TXV | 2.959%
Lathrop | CA | 95330-9363 |  | 2012-08-10 | 2012-08-10 12:15 | 2012-08-10 12:35 | CARRIER - 38CKC048370 | 100 | 3.1 | Yes | Yes | 20.6 | 21.7 | -1.1 | 55ECAA812CEB4F358767AC44E221EDE8 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Grass Valley | CA | 95945-7803 |  | 2012-08-14 | 2012-08-14 11:08 | 2012-08-14 11:30 | PAYNE - PA10J048-A | 102 | 24.6 | Yes | Yes | 23 | 21 | 2 | D84A65078CEB4BF5B4AC8FCB007AB0B0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 24.12% | 0.75882 | 46.35% | [5 empty] | Non-TXV | 24.12%
Stockton | CA | 95219-3502 |  | 2012-06-11 | 2012-06-11 10:51 | 2012-06-11 11:11 | DAY & NIGHT - UNK | 84 | 8.1 | Yes | Yes | 18.7 | 21.4 | -2.7 | A4A6360E2D774E0B8ECE421C85CF573B |  | R22 | Non-TXV |  | 9.643% | 0.90357 | 18.53% | [5 empty] | Non-TXV | 9.643%
Tracy | CA | 95377-7926 |  | 2012-08-13 | 2012-08-13 13:43 | 2012-08-13 14:10 | YORK - H1RA042S06D | 84 | 14.4 | Yes | Yes | 17.9 | 20.6 | -2.7 | CD342BE64C2F4BFAA6E10E5AB4A3EB04 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.14% | 0.82857 | 32.94% | [5 empty] | Non-TXV | 17.14%
Manteca | CA | 95336-3402 |  | 2012-08-01 | 2012-08-01 10:01 | 2012-08-01 10:22 | RUUD - URMA-A036JK08E | 99 | 2.9 | Yes | Yes | 16.4 | 18.7 | -2.3 | 662D49F995BF41FD9CAC146C2313D9C2 |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Fresno | CA | 93722-4535 |  | 2012-06-01 | 2012-06-01 13:00 | 2012-06-01 13:18 | TAPPAN - N/A | 64 | 1.9 | Yes | Yes | 19 | 18.5 | 0.5 | A0476E216E444638BB6557E8009D6F96 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Merced | CA | 95340-3928 |  | 2012-08-06 | 2012-08-06 09:37 | 2012-08-06 10:00 | AMERICAN STANDARD - YCC036F1MOBA | 83 | 14.1 | Yes | Yes | 23.7 | 22.2 | 1.5 | 8C573ACB008F43D2A5ECEF791BA2451D |  | R22 | Non-TXV |  | 16.99% | 0.83012 | 32.65% | [5 empty] | Non-TXV | 16.99%
Williams | CA | 95987-9011 |  | 2012-07-26 | 2012-07-26 08:19 | 2012-07-26 08:41 | GIBSON - JS3BA-024KA | 64 | 1.9 | Yes | Yes | 17 | 17.9 | -0.9 | A3CC3EC5328A4482BB77CA2AE48189F6 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Tracy | CA | 95377-7963 |  | 2012-08-14 | 2012-08-14 16:09 | 2012-08-14 16:53 | CARRIER - 38CMC060300 | 160 | -14.5 | Yes | Yes | 20.2 | 18.6 | 1.6 | C182E35AA24E445F93A583A94E1A3D1C |  | R22 | TXV |  | -9.062% | 1.0906 | 2.538% |  |  |  |  | TXV |  |  | -9.062%
Lathrop | CA | 95330-8816 |  | 2012-08-10 | 2012-08-10 09:39 | 2012-08-10 09:57 | CARRIER - 38CKC060370 | 133 | -7.8 | Yes | Yes | 17.3 | 19.2 | -1.9 | C41ACF45586342AF87A0B578A79765B9 |  | R22 | Non-TXV |  | -5.865% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.865%
Stockton | CA | 95203-1409 |  | 2012-07-31 | 2012-07-31 12:55 | 2012-07-31 13:24 | BRYANT - 563CN042-C | 102 | 5 | Yes | Yes | 23.1 | 19.2 | 3.9 | 40F10D21C58A49269E41C2FD1FF8680B |  | R22 | TXV |  | 4.902% | 0.95098 | 9.42% | [5 empty] | TXV | 4.902%
Atwater | CA | 95301-4875 |  | 2012-05-17 | 2012-05-17 13:54 | 2012-05-17 14:18 | UARDIAN - GCGD30S41S1A | 79 | 5.3 | Yes | Yes | 20.4 | 20.4 | 0 | CED5AAB37B1647F6B5214EF10536AA25 |  | R410A | Non-TXV |  | 6.709% | 0.93291 | 12.89% | [5 empty] | Non-TXV | 6.709%
Paradise | CA | 95969-2803 |  | 2012-07-31 | 2012-07-31 13:13 | 2012-07-31 13:34 | AMERICAN STANDARD - YCY036G1MOAC | 129 | 9.7 | Yes | Yes | 22.7 | 22.8 | -0.1 | EDEF8889794743F093263489AFCC5403 |  | R22 | Non-TXV |  | 7.519% | 0.92481 | 14.45% | [5 empty] | Non-TXV | 7.519%
Stockton | CA | 95215-2033 |  | 2012-08-08 | 2012-08-08 10:50 | 2012-08-08 11:31 | RHEEM - RAND-060JAZ | 176 | 5.9 | Yes | Yes | 18.7 | 20.4 | -1.7 | 702AC93862824C7B88519A51B8C0932B |  | R22 | Non-TXV |  | 3.352% | 0.96648 | 6.442% | [5 empty] | Non-TXV | 3.352%
Fresno | CA | 93726-1717 |  | 2012-06-07 | 2012-06-07 12:29 | 2012-06-07 12:44 | WESTINGHOUSE - SSCG030CCW | 58 | -3.4 | Yes | Yes | 17.9 | 20.7 | -2.8 | C786BB72D83E4C15A4B13C7712CAC758 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Winton | CA | 95388-9775 |  | 2012-05-09 | 2012-05-09 11:37 | 2012-05-09 11:58 | PAYNE - PY1PNB030060AAAA | 55 | 1.6 | Yes | Yes | 22.1 | 19.7 | 2.5 | 2CCEE71D89C64B64A3FA67F64FA38613 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Red Bluff | CA | 96080-2252 |  | 2012-05-15 | 2012-05-15 13:28 | 2012-05-15 13:47 | RUUD - RRKA-A060JK10X | 119 | 3.9 | Yes | Yes | 18.5 | 20.1 | -1.6 | F6F19EEFE3A345F9A53D190349C141EF |  | R22 | Non-TXV |  | 3.277% | 0.96723 | 6.298% | [5 empty] | Non-TXV | 3.277%
Tracy | CA | 95376-3502 |  | 2012-08-15 | 2012-08-15 10:26 | 2012-08-15 10:44 | CARRIER - UNK | 84 | -4.9 | Yes | Yes | 19.1 | 19.9 | -0.8 | D7018541FEBF421C9EB6884915494DC0 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Tracy | CA | 95377-1139 |  | 2012-08-13 | 2012-08-13 15:30 | 2012-08-13 15:59 | RHEEM - FADC-060JAS | 112 | 3.4 | Yes | Yes | 18.3 | 20.2 | -1.9 | A23F76EFF296487390C6A695FBE94C06 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Los Banos | CA | 93635-4213 |  | 2012-05-22 | 2012-05-22 16:33 | 2012-05-22 16:57 | DAY & NIGHT - 589NW030040ACAD | 69 | 3.1 | Yes | Yes | 27.5 | 23.2 | 4.3 | E5365B9D594B4033A62EC9CC232C4D9A | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 4.493% | 0.95507 | 8.634% | [5 empty] | Non-TXV | 4.493%
Stockton | CA | 95210-2241 |  | 2012-08-07 | 2012-08-07 09:47 | 2012-08-07 10:04 | ICP - CAC236AKA4 | 113 | -6.6 | Yes | Yes | 25.2 | 19.4 | 5.8 | 0FA2CE33BD0342F8A0E787E8CDE532BA |  | R22 | Non-TXV |  | -5.841% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.841%
Oroville | CA | 95965-4429 |  | 2012-08-07 | 2012-08-07 09:21 | 2012-08-07 09:59 | CARRIER - 48GP-060090311VS | 160 | 6.7 | Yes | Yes | 18.4 | 21.2 | -2.8 | 0F273F0D3726465CBCC9375B35137707 |  | R410A | Non-TXV |  | 4.188% | 0.95813 | 8.047% | [5 empty] | Non-TXV | 4.188%
Atwater | CA | 95301-4763 |  | 2012-05-17 | 2012-05-17 15:02 | 2012-05-17 15:19 | TRANE - YC030F1M01 | 64 | -4.5 | Yes | Yes | 20.2 | 20.4 | -0.2 | 472489DD936A45C9A11D60AFA9106833 |  | R22 | Non-TXV |  | -7.031% | 1.0703 | 1.969% |  |  |  |  | Non-TXV |  |  | -7.031%
Winton | CA | 95388-9775 |  | 2012-08-06 | 2012-08-06 08:30 | 2012-08-06 08:30 | RHEEM - RRPL-B030JK06X | 76 | 0 | Yes | Yes | 18.6 | 18.2 | 0.4 | 7894714BD0CC45DAAD8A59F9AF398868 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-6353 |  | 2012-05-22 | 2012-05-22 11:38 | 2012-05-22 11:59 | LENNOX - 12GCS0481002PA | 167 | 7.4 | Yes | Yes | 23.3 | 18.7 | 4.6 | CA1CC5ADB1834786A4A0C883DBBAB7C2 |  | R22 | Non-TXV |  | 4.431% | 0.95569 | 8.516% | [5 empty] | Non-TXV | 4.431%
Stockton | CA | 95206-4645 |  | 2012-08-13 | 2012-08-13 12:32 | 2012-08-13 12:52 | RHEEM - RAM-024JAS | 85 | 8.9 | Yes | Yes | 17 | 19.9 | -2.9 | D05ECBD006B942C881B5A3F504E3641C |  | R22 | Non-TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | Non-TXV | 10.47%
Merced | CA | 95340-4502 |  | 2012-05-08 | 2012-05-08 16:33 | 2012-05-08 16:59 | AMERICAN STANDARD - YCC042F1M0BH | 101 | 3.1 | Yes | Yes | 25.2 | 22.9 | 2.4 | 8D17D1123BEE4B8295709ABC4E4757AA | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.069% | 0.96931 | 5.899% | [5 empty] | Non-TXV | 3.069%
Madera | CA | 93638-1615 |  | 2012-06-15 | 2012-06-15 09:53 | 2012-06-15 10:19 | AIRE-FLO - 48SX0420B0321AA | 87 | 11.5 | Yes | Yes | 26.5 | 25.3 | 1.2 | E5B141FEBAE84A5C8A7A85CB06DD504B |  | R22 | Non-TXV |  | 13.22% | 0.86782 | 25.4% | [5 empty] | Non-TXV | 13.22%
Madera | CA | 93638-1615 |  | 2012-06-15 | 2012-06-15 10:20 | 2012-06-15 10:39 | AIRE-FLO - 48SX0420B0321AA | 87 | 9.2 | Yes | Yes | 25.4 | 22.5 | 2.9 | D362FF0FAAB84ABDB5695EBF25542021 |  | R22 | Non-TXV |  | 10.57% | 0.89425 | 20.32% | [5 empty] | Non-TXV | 10.57%
Los Banos | CA | 93635-6353 |  | 2012-08-13 | 2012-08-13 13:08 | 2012-08-13 13:51 | KENMORE - 12GCS042-75-3PA | 133 | 4 | Yes | Yes | 23.3 | 19.3 | 4 | 3D4C8763F11740C69CA64FF042F281CF |  | R22 | Non-TXV |  | 3.008% | 0.96992 | 5.78% | [5 empty] | Non-TXV | 3.008%
Stockton | CA | 95209-2038 |  | 2012-05-18 | 2012-05-18 10:49 | 2012-05-18 11:07 | HEIL - GPGM36KO8OA | 71 | -4.2 | Yes | Yes | 22.9 | 20.1 | 2.8 | 0873CA2F67EF4F72B6A260FC7B99B012 |  | R22 | Non-TXV |  | -5.915% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.915%
Willows | CA | 95988-3453 |  | 2012-06-08 | 2012-06-08 09:30 | 2012-06-08 09:49 | DAY N NIGHT - 24DNR108C | 67 | 3.9 | Yes | Yes | 23.9 | 20.6 | 3.3 | AA39E5AD1F9845FB8C699AB127195F4A |  | R22 | Non-TXV |  | 5.821% | 0.94179 | 11.19% | [5 empty] | Non-TXV | 5.821%
Stockton | CA | 95209-4019 |  | 2012-08-07 | 2012-08-07 12:12 | 2012-08-07 12:32 | PAYNE - 585A042100YAC | 89 | 8.6 | Yes | Yes | 19.5 | 19.6 | -0.1 | F3480997755F43B6A3D735ED966C1A5B |  | R22 | Non-TXV |  | 9.663% | 0.90337 | 18.57% | [5 empty] | Non-TXV | 9.663%
Yuba City | CA | 95993-8882 |  | 2012-08-03 | 2012-08-03 11:09 | 2012-08-03 11:34 | LENNOX - 13ACC-060-23001 | 168 | 9.4 | Yes | Yes | 22 | 21 | 1 | D71CF77C379447E9861498F4D618EF06 |  | R22 | Non-TXV |  | 5.595% | 0.94405 | 10.75% | [5 empty] | Non-TXV | 5.595%
Stockton | CA | 95203-1905 |  | 2012-06-14 | 2012-06-14 10:24 | 2012-06-14 10:24 | CARRIER - 48ESN024040301 | 105 | 0 | Yes | Yes | 20.2 | 19.4 | 0.8 | 2EB4C2F076AD49BCA1566EA0D97FC1E1 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-3309 |  | 2012-06-13 | 2012-06-13 11:40 | 2012-06-13 12:06 | LENNOX - GCS20R-511-75-1P | 115 | -6.8 | Yes | Yes | 22 | 22 | 0 | 6BD70EC9951E42AB9BAC8DEA81392E3C |  | R22 | Non-TXV |  | -5.913% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.913%
Stockton | CA | 95215-7512 |  | 2012-08-08 | 2012-08-08 14:50 | 2012-08-08 15:10 | RUUD - UNK | 64 | 6 | Yes | Yes | 21.3 | 22.3 | -1 | 75A400257FD248EDAEB2E758A91A9104 |  | R22 | Non-TXV |  | 9.375% | 0.90625 | 18.02% | [5 empty] | Non-TXV | 9.375%
Stockton | CA | 95209-1351 |  | 2012-05-22 | 2012-05-22 12:38 | 2012-05-22 13:00 | YORK - D1NP048N06506A | 132 | 7 | Yes | Yes | 22.3 | 20.4 | 1.9 | DB8A32B090C14F9A8A842C66C0DC1EF4 |  | R22 | TXV |  | 5.303% | 0.94697 | 10.19% | [5 empty] | TXV | 5.303%
Manteca | CA | 95337-7923 |  | 2012-08-01 | 2012-08-01 14:11 | 2012-08-01 14:57 | CARRIER - 38CKC048---371-- | 99 | 3 | Yes | Yes | 18.4 | 19.5 | -1.1 | 2B92345A624F4E7E8C86B80C9B911FA1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Yuba City | CA | 95993-1722 |  | 2012-08-01 | 2012-08-01 11:10 | 2012-08-01 11:39 | OTHER - AA1CJ048-B | 112 | 20.8 | Yes | Yes | 25.3 | 20.4 | 4.9 | 1D0E1D768A7C4F7B8219E361152DF243 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Chico | CA | 95926-3060 |  | 2012-05-16 | 2012-05-16 12:57 | 2012-05-16 12:57 | DAYNNIGHT - 591ANX030000AAAA | 77 | 0 | Yes | Yes | 22.9 | 22.1 | 0.8 | 18E42FD0101E4D7B9BAF6359A96B59B8 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-6106 |  | 2012-05-11 | 2012-05-11 10:18 | 2013-11-20 10:20 | AMANA - RCB4882A | 105 | 3.2 | Yes | Yes | 22.3 | 22 | 0.3 | 5C371D48A6C349819F34C936CC5273A7 |  | R22 | Non-TXV |  | 3.048% | 0.96952 | 5.857% | [5 empty] | Non-TXV | 3.048%
Yuba City | CA | 95993-5186 |  | 2012-08-03 | 2012-08-03 08:37 | 2012-08-03 08:58 | LENNOX - 12ACB42-5P | 125 | 4.1 | Yes | Yes | 19 | 19.2 | -0.2 | 76DC781A125C4A98A3C25CF5C02F1A15 |  | R22 | Non-TXV |  | 3.28% | 0.9672 | 6.303% | [5 empty] | Non-TXV | 3.28%
Stockton | CA | 95205-0000 |  | 2012-05-29 | 2012-05-29 12:06 | 2012-05-29 12:36 | RUUD - UAFD-031JAS | 64 | 2.6 | Yes | Yes | 17.7 | 20.4 | -2.7 | 5946EF64106F4F29AAF8DC1967E4E775 |  | R22 | Non-TXV |  | 4.062% | 0.95937 | 7.807% | [5 empty] | Non-TXV | 4.062%
Fresno | CA | 93711-6608 |  | 2012-05-14 | 2012-05-14 13:32 | 2012-05-14 13:54 | DAY& NIGHT - 585EJ036075 | 82 | 14.9 | Yes | Yes | 25.5 | 19.9 | 5.6 | DB35E16803AA41A6AD758277A92734AE |  | R22 | Non-TXV |  | 18.17% | 0.81829 | 34.92% | [5 empty] | Non-TXV | 18.17%
Chico | CA | 95926-3051 |  | 2012-05-15 | 2012-05-15 15:07 | 2012-05-15 15:07 | DAYNNIGHT - 591ANX030000AAAA | 76 | 0 | Yes | Yes | 22.9 | 24 | -1.1 | 68FAB2CD4F7A4532B6E8AFDAABD47FAF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-6036 |  | 2012-06-08 | 2012-06-08 12:30 | 2012-06-08 12:50 | OTHER - HARB-F024SA | 118 | 4 | Yes | Yes | 21 | 19.7 | 1.3 | 877ED31E2AFD47A78DF10DCD2A57ECE6 |  | R22 | Non-TXV |  | 3.39% | 0.9661 | 6.515% | [5 empty] | Non-TXV | 3.39%
Yuba City | CA | 95991-1566 |  | 2012-07-16 | 2012-07-16 13:43 | 2012-07-16 14:01 | PAYNE - PH10JA024-C | 75 | -10.7 | Yes | Yes | 21 | 20.4 | 0.6 | 3C94398E696B4CFEA7978BC0FA3ABD22 |  | R22 | TXV |  | -14.27% | 1.1427 | 3.995% |  |  |  |  | TXV |  |  | -14.27%
Yuba City | CA | 95991-2852 |  | 2012-07-31 | 2012-07-31 15:24 | 2012-07-31 15:46 | OTHER - 561AJ048-B | 100 | 2.9 | Yes | Yes | 21.4 | 19.8 | 1.6 | 2723680A0C6F435C8B505496DCB06088 |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Valley Springs | CA | 95252-9704 |  | 2012-08-16 | 2012-08-16 08:44 | 2012-08-16 09:02 | BDP - 561CJ036-C | 76 | -4.5 | Yes | Yes | 27.3 | 22 | 5.3 | BD983C20100846BFAFB768CF00D9F118 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Stockton | CA | 95212-3554 |  | 2012-08-07 | 2012-08-07 15:45 | 2012-08-07 16:02 | CARRIER - 38CKC036350 | 71 | 3.6 | Yes | Yes | 18.9 | 20.4 | -1.5 | 3E31D855B280413B94A4784E560E2D90 |  | R22 | Non-TXV |  | 5.07% | 0.9493 | 9.744% | [5 empty] | Non-TXV | 5.07%
Stockton | CA | 95205-0000 |  | 2012-06-07 | 2012-06-07 11:06 | 2012-06-07 11:26 | RUUD - UAFD-031JAS | 64 | 3 | Yes | Yes | 17.7 | 19.3 | -1.6 | 44BF309D40C84A88894C32A33F922D92 |  | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Stockton | CA | 95210-1729 |  | 2012-05-09 | 2012-05-09 09:26 | 2012-05-09 09:46 | GOODMAN - PGB036075-1A | 85 | 1.8 | Yes | Yes | 21.3 | 18.3 | 3.1 | 1ED943E0EBB94C3DA27957951A2340AB | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.118% | 0.97882 | 4.07% | [5 empty] | Non-TXV | 2.118%
Selma | CA | 93662-4069 |  | 2012-06-07 | 2012-06-07 13:39 | 2012-06-07 14:20 | ICP - PGF324040K01A2 | 64 | 2.2 | Yes | Yes | 20.6 | 21 | -0.4 | 265241DDB027486CA10CAEB56E739CA8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Yuba City | CA | 95991-9504 |  | 2012-06-15 | 2012-06-15 09:03 | 2012-06-15 09:16 | TEMPSTAR - NA | 85 | 7.1 | Yes | Yes | 25.2 | 21.7 | 3.5 | 54825B908FFA429D9D9CEC0F1A6B6618 |  | R22 | Non-TXV |  | 8.353% | 0.91647 | 16.05% | [5 empty] | Non-TXV | 8.353%
Valley Springs | CA | 95252-9202 |  | 2012-07-16 | 2012-07-16 10:42 | 2012-07-16 11:00 | HEIL - UNK | 80 | 2.4 | Yes | Yes | 15.6 | 18.2 | -2.6 | 84BB0A64CE6A4EC29C2CB8488E34B1FC |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Pollock Pines | CA | 95726-9794 |  | 2012-07-05 | 2012-07-05 10:53 | 2012-07-05 10:53 | CARRIER - 38CKB042300 | 80 | 0 | Yes | Yes | 25.1 | 19.5 | 5.6 | 56F6BE6E8A6D47A3BDC38FDA725E6DA7 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95205-0000 |  | 2012-05-29 | 2012-05-29 12:37 | 2012-05-29 12:55 | RUUD - UAFD-031JAS | 64 | 4 | Yes | Yes | 20 | 20.9 | -0.9 | 081AD6A5FB2B4EDC8574CCC6455DE12A |  | R22 | Non-TXV |  | 6.25% | 0.9375 | 12.01% | [5 empty] | Non-TXV | 6.25%
Los Banos | CA | 93635-9230 |  | 2012-08-14 | 2012-08-14 14:06 | 2012-08-14 14:27 | - JS5BD042K | 170 | 6.6 | Yes | Yes | 19.5 | 19.3 | 0.2 | 165A6682E24D4D4C99973FBDE6ED3993 |  | R22 | Non-TXV |  | 3.882% | 0.96118 | 7.461% | [5 empty] | Non-TXV | 3.882%
Winton | CA | 95388-9763 |  | 2012-05-15 | 2012-05-15 12:03 | 2012-05-15 12:21 | BDP - 395A030080Y482 | 76 | 2.3 | Yes | Yes | 25.7 | 20.1 | 5.6 | 88E4E84B01C54FE8AB9CC0173D50E0D3 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Madera | CA | 93638-9645 |  | 2012-06-12 | 2012-06-12 11:20 | 2012-06-12 11:40 | BDP - 588ANW036080ACAF | 67 | 9.5 | Yes | Yes | 18.5 | 19.3 | -0.8 | 4B35F45AC5FE4396864C4023480E783C |  | R22 | Non-TXV |  | 14.18% | 0.85821 | 27.25% | [5 empty] | Non-TXV | 14.18%
Chico | CA | 95926-3050 |  | 2012-05-14 | 2012-05-14 16:42 | 2012-05-14 16:42 | DAY N NIGHT - 591ANX030000AAAA | 76 | 0 | Yes | Yes | 19 | 20.3 | -1.3 | 0F0F90C36A314CC781656B77857137B2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Magalia | CA | 95954-9620 |  | 2012-08-13 | 2012-08-13 10:01 | 2012-08-13 10:39 | RUUD - UPND-048J | 146 | 11.9 | Yes | Yes | 20.8 | 20.6 | 0.2 | 76CBC14FCDF64B4EAC3B186CF2966046 |  | R22 | Non-TXV |  | 8.151% | 0.91849 | 15.66% | [5 empty] | Non-TXV | 8.151%
Stockton | CA | 95212-3525 |  | 2012-08-07 | 2012-08-07 13:12 | 2012-08-07 13:28 | YORK - R2RCO48S06HG | 119 | 6.2 | Yes | Yes | 17.8 | 17.7 | 0.1 | A7999AACA4F747B589CEB62BABDBBA5E |  | R22 | TXV |  | 5.21% | 0.9479 | 10.01% | [5 empty] | TXV | 5.21%
Pollock Pines | CA | 95726-8805 |  | 2012-05-14 | 2012-05-14 10:42 | 2012-05-14 10:42 | AMANA - RCA36A2A | 100 | 0 | Yes | Yes | 24.9 | 19.9 | 5 | 52D42744A1BB462D8DDB6256C809454A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-2822 |  | 2012-05-14 | 2012-05-14 11:35 | 2012-05-14 11:53 | RHEEM - RRPL-B036JK08X | 93 | 2.7 | Yes | Yes | 24.9 | 20.1 | 4.8 | EF510EB61D6C47AE903B1A1B40E0F128 |  | R410A | Non-TXV |  | 2.903% | 0.97097 | 5.579% | [5 empty] | Non-TXV | 2.903%
Yuba City | CA | 95993-9114 |  | 2012-05-09 | 2012-05-09 14:49 | 2012-05-09 15:06 | CARRIER - 38CKC036350 | 74 | -19.8 | Yes | Yes | 17.1 | 19.9 | -2.8 | C706EEFA83FD44BB9F891D8A3B8353AD |  | R22 | TXV |  | -26.76% | 1.2676 | 7.493% |  |  |  |  | TXV |  |  | -26.76%
Fresno | CA | 93722-3146 |  | 2012-05-15 | 2012-05-15 12:06 | 2012-05-15 12:27 | UPG - TCGD36521S1A | 65 | 5.5 | Yes | Yes | 23.8 | 19.8 | 4 | B9327DFFE1CF4671B513DEFA328B39D2 |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Live Oak | CA | 95953-9440 |  | 2012-07-05 | 2012-07-05 10:45 | 2012-07-05 11:13 | CARRIER - 24ABA336A0030010 | 95 | 12 | Yes | Yes | 17.5 | 19.9 | -2.4 | 413A2277FF17410E8B2D5B1795A88BFE |  | R410A | TXV |  | 12.63% | 0.87368 | 24.28% | [5 empty] | TXV | 12.63%
Merced | CA | 95348-9461 |  | 2012-08-06 | 2012-08-06 10:48 | 2012-08-06 11:31 | AMERICAN STANDARD - YCC036F1HOBC | 88 | 8.4 | Yes | Yes | 18.5 | 21 | -2.5 | A6C114C66D9C4C6DB37681CB31450417 |  | R22 | Non-TXV |  | 9.545% | 0.90455 | 18.34% | [5 empty] | Non-TXV | 9.545%
Stockton | CA | 95210-2514 |  | 2012-08-10 | 2012-08-10 14:59 | 2012-08-10 15:20 | YORK - H20H030S06A | 80 | 7.8 | Yes | Yes | 17.2 | 18.9 | -1.7 | C49410E4F59B4A4DA9D9383B35CE472F |  | R22 | Non-TXV |  | 9.75% | 0.9025 | 18.74% | [5 empty] | Non-TXV | 9.75%
Clovis | CA | 93612-2322 |  | 2012-05-15 | 2012-05-15 12:51 | 2012-05-15 13:12 | RHEEM - UNK | 58 | 11.7 | Yes | Yes | 18 | 20.4 | -2.4 | 6FDE027BFE4C417EAEEFE2F81B31F14D |  | R22 | Non-TXV |  | 20.17% | 0.79828 | 38.77% | [5 empty] | Non-TXV | 20.17%
Stockton | CA | 95203-1337 |  | 2012-07-31 | 2012-07-31 08:58 | 2012-07-31 09:22 | PAYNE - PY3PNA048090NB-- | 196 | 6.1 | Yes | Yes | 23.1 | 22.1 | 1 | D13C9AA34C9549C0913DE6D13015E295 |  | R22 | Non-TXV |  | 3.112% | 0.96888 | 5.981% | [5 empty] | Non-TXV | 3.112%
Winton | CA | 95388-9775 |  | 2012-08-06 | 2012-08-06 09:14 | 2012-08-06 09:38 | RHEEM - RRKA-A036JK06X | 62 | -3.6 | Yes | Yes | 25.8 | 20.4 | 5.4 | 3AC68F28CB9D46F4A4F2E96DF8986895 |  | R22 | Non-TXV |  | -5.806% | 1.0581 | 1.626% |  |  |  |  | Non-TXV |  |  | -5.806%
Grass Valley | CA | 95949-6568 |  | 2012-08-14 | 2012-08-14 15:18 | 2012-08-14 15:18 | LENNOX - HS18-411-6P | 79 | 0 | Yes | Yes | 24.5 | 21 | 3.5 | AE4BA60C55B64A05A762CB957F89F709 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Paradise | CA | 95969-3333 |  | 2012-08-06 | 2012-08-06 18:02 | 2012-08-06 18:19 | RHEEM - 58JCJ036075 | 74 | 8.8 | Yes | Yes | 22.9 | 20.7 | 2.3 | 2939419A6A8B48579CCFEE6A12E0C7A5 |  | R22 | Non-TXV |  | 11.89% | 0.88108 | 22.85% | [5 empty] | Non-TXV | 11.89%
Paradise | CA | 95969-5751 |  | 2012-08-06 | 2012-08-06 19:14 | 2012-08-06 19:35 | RHEEM - UNK | 73 | 5.5 | Yes | Yes | 23 | 21.8 | 1.2 | F1685E461912489EA6FD4F53DC33BCE7 |  | R22 | Non-TXV |  | 7.534% | 0.92466 | 14.48% | [5 empty] | Non-TXV | 7.534%
Paradise | CA | 95969-5751 |  | 2012-08-06 | 2012-08-06 19:40 | 2012-08-06 20:21 | RHEEM - 585CJ0245050 | 73 | 2.2 | Yes | Yes | 24.3 | 22.4 | 2 | B7910767A2FB4649800D6365048A65E5 |  | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Stockton | CA | 95207-4678 |  | 2012-07-31 | 2012-07-31 13:22 | 2012-07-31 13:40 | GOODMAN - CKL18-10 | 83 | 3.2 | Yes | Yes | 23 | 20 | 3 | 355BE0E44B8C4E2CB945169ACAC30B89 |  | R22 | Non-TXV |  | 3.855% | 0.96145 | 7.409% | [5 empty] | Non-TXV | 3.855%
Manteca | CA | 95337-9665 |  | 2012-08-15 | 2012-08-15 14:13 | 2012-08-15 14:29 | PAYNE - 591ANX060000AAAA | 166 | 27.5 | Yes | Yes | 22.7 | 21 | 1.7 | 43C40C112E6144C8BF837367571D1AF6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.57% | 0.83434 | 31.84% | [5 empty] | Non-TXV | 16.57%
Manteca | CA | 95336-2880 |  | 2012-07-31 | 2012-07-31 11:26 | 2012-07-31 11:54 | RUUD - UAMA-048JBZ | 172 | 28 | Yes | Yes | 18.7 | 20.4 | -1.7 | 4988A8ED9D714ACC8D15A038CC4EA7FD |  | R22 | Non-TXV |  | 16.28% | 0.83721 | 31.28% | [5 empty] | Non-TXV | 16.28%
Winton | CA | 95388-9443 |  | 2012-08-03 | 2012-08-03 14:27 | 2012-08-03 14:27 | CARRIER - 48GS-030040301 | 55 | 0 | Yes | Yes | 24 | 22 | 2 | B495A2408F5C405E9C6A10F9562FE45F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3508 |  | 2012-05-22 | 2012-05-22 11:10 | 2012-05-22 11:31 | CARRIER - 38EN018310 | 59 | 18.2 | Yes | Yes | 20.2 | 19.9 | 0.3 | 2A9470E9D6784648BD9C1F431C1DC3E1 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 30.85% | 0.69153 | 59.28% | [5 empty] | Non-TXV | 30.85%
Paradise | CA | 95969-6242 |  | 2012-05-14 | 2012-05-14 12:14 | 2012-05-14 12:47 | DAYN NIGHT - 5849HW 024040 | 75 | 5.5 | Yes | Yes | 24 | 23.2 | 0.8 | B856768DC30E488EAD899B8D3170BD93 |  | R22 | Non-TXV |  | 7.333% | 0.92667 | 14.09% | [5 empty] | Non-TXV | 7.333%
Durham | CA | 95938-9624 |  | 2012-08-09 | 2012-08-09 09:23 | 2012-08-09 09:23 | PAYNE - PY1PNB03060AAAA | 40 | 0 | Yes | Yes | 27 | 21.8 | 5.2 | 97E931B038204F80A52E78A9DD39FD06 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Olivehurst | CA | 95961-0000 |  | 2012-08-01 | 2012-08-01 09:57 | 2012-08-01 10:15 | OTHER - HAMC-036OSA | 83 | 2.5 | Yes | Yes | 19.9 | 21 | -1.1 | E86C0D4A59A643DAB10C7AD99871AB52 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Chico | CA | 95926-2029 |  | 2012-08-01 | 2012-08-01 09:24 | 2012-08-01 09:50 | TEMPSTAR - PGC036K080B | 71 | 9.5 | Yes | Yes | 24.1 | 20.9 | 3.2 | 0DD52AB5DAE747AFB2D2F213F954B1E5 |  | R22 | Non-TXV |  | 13.38% | 0.8662 | 25.71% | [5 empty] | Non-TXV | 13.38%
Oroville | CA | 95966-6301 |  | 2012-08-10 | 2012-08-10 10:50 | 2012-08-10 11:40 | AMERICAN STANDARD - 2A7A2042B1000AA | 86 | 2.6 | Yes | Yes | 25.2 | 20.1 | 5.1 | 1F0A8B4E08D046028B6A4339EEFA3AC8 |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Chico | CA | 95926-1525 |  | 2012-08-01 | 2012-08-01 10:50 | 2012-08-01 11:14 | LENNOX - HS29-311-3P | 69 | 6.5 | Yes | Yes | 22.8 | 20.4 | 2.4 | BA25023C282E4A7E8526376DCF8046AA |  | R22 | Non-TXV |  | 9.42% | 0.9058 | 18.1% | [5 empty] | Non-TXV | 9.42%
Tracy | CA | 95376-2038 |  | 2012-08-03 | 2012-08-03 14:37 | 2012-08-03 15:21 | RHEEM - RRAB-08F42JR | 74 | -7 | Yes | Yes | 18.9 | 19.1 | -0.2 | 651011E4E8F441E3A9DD7C373DDB45C5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Marysville | CA | 95901-3405 |  | 2012-08-03 | 2012-08-03 15:30 | 2012-08-03 15:47 | PAYNE - PA13NR042-E | 159 | 6.1 | Yes | Yes | 17 | 19.3 | -2.3 | E7D40FE1F6744603A30213BDB85B5678 |  | R22 | Non-TXV |  | 3.836% | 0.96164 | 7.373% | [5 empty] | Non-TXV | 3.836%
Plumas Lake | CA | 95961-9017 |  | 2012-08-01 | 2012-08-01 14:11 | 2012-08-01 14:42 | CARRIER - 38CC030340 | 75 | 10.3 | Yes | Yes | 18 | 21 | -3 | 0CC089F23C8642F6826F0FE7CF9AEF58 |  | R22 | Non-TXV |  | 13.73% | 0.86267 | 26.39% | [5 empty] | Non-TXV | 13.73%
Plumas Lake | CA | 95961-9016 |  | 2012-08-01 | 2012-08-01 12:06 | 2012-08-01 12:31 | YORK - H2RA0306D | 62 | 4.6 | Yes | Yes | 18 | 19.9 | -1.9 | DA614617737D4BA39876372778AB60DC |  | R22 | Non-TXV |  | 7.419% | 0.92581 | 14.26% | [5 empty] | Non-TXV | 7.419%
Marysville | CA | 95901-3819 |  | 2012-07-31 | 2012-07-31 09:22 | 2012-07-31 09:52 | PAYNE - PA13NR036000AHAA | 83 | 6.4 | Yes | Yes | 21 | 20.7 | 0.3 | 460E08C3E5D94B8F9D76C3AF35B09AD5 |  | R22 | Non-TXV |  | 7.711% | 0.92289 | 14.82% | [5 empty] | Non-TXV | 7.711%
Chico | CA | 95928-3917 |  | 2012-08-02 | 2012-08-02 10:02 | 2012-08-02 11:06 | LENNOX - H522-311V-2P | 130 | 8.7 | Yes | Yes | 22 | 20.8 | 1.2 | 36DB27EE46C9416191495E4593552FA9 |  | R22 | Non-TXV |  | 6.692% | 0.93308 | 12.86% | [5 empty] | Non-TXV | 6.692%
Lathrop | CA | 95330-9714 |  | 2012-05-15 | 2012-05-15 11:09 | 2012-05-15 11:32 | YORK - H2RD048S06SB | 134 | 29.6 | Yes | Yes | 16.4 | 19.1 | -2.7 | 521DB64F22974B9CB1F3BFF93F4FEE90 |  | R22 | Non-TXV |  | 22.09% | 0.7791 | 42.45% | [5 empty] | Non-TXV | 22.09%
Yuba City | CA | 95991-3919 |  | 2012-06-13 | 2012-06-13 13:45 | 2012-06-13 14:10 | GOODMAN - GSC130301DA | 87 | -7.2 | Yes | Yes | 17 | 19.5 | -2.5 | 959F5887D1664FC482D97A7CB58194C1 |  | R22 | Non-TXV |  | -8.276% | 1.0828 | 2.318% |  |  |  |  | Non-TXV |  |  | -8.276%
Merced | CA | 95340-2616 |  | 2012-07-31 | 2012-07-31 14:51 | 2012-07-31 15:15 | TRANE - TTR030C100A0 | 74 | 2.6 | Yes | Yes | 16.1 | 16.3 | -0.2 | 8B89364AFC804E3ABB06D0F223B91221 |  | R22 | Non-TXV |  | 3.514% | 0.96486 | 6.752% | [5 empty] | Non-TXV | 3.514%
Paradise | CA | 95969-5249 |  | 2012-05-14 | 2012-05-14 10:39 | 2012-05-14 11:08 | COLEMANH - H2 R CO 30S 06A | 86 | 2.6 | Yes | Yes | 19.3 | 21.2 | -1.9 | 157939D9CA6F4641954C9B2B695D6D21 |  | R22 | Non-TXV |  | 3.023% | 0.96977 | 5.81% | [5 empty] | Non-TXV | 3.023%
Atwater | CA | 95301-2133 |  | 2012-08-06 | 2012-08-06 10:52 | 2012-08-06 11:16 | CARRIER - 585HJ030040 | 68 | 7.1 | Yes | Yes | 23.7 | 20.4 | 3.3 | E8F2FAD56D54407E9549CA37E606E0F5 |  | R22 | Non-TXV |  | 10.44% | 0.89559 | 20.07% | [5 empty] | Non-TXV | 10.44%
Stockton | CA | 95212-3495 |  | 2012-05-17 | 2012-05-17 09:31 | 2012-05-17 09:48 | CARRIER - 38CK036350 | 74 | -4.4 | Yes | Yes | 21 | 20.2 | 0.9 | 26642C2095244FB8B772C7B427C13179 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Auburn | CA | 95603-3314 |  | 2012-05-09 | 2012-05-09 16:02 | 2012-05-09 16:02 | TRANE - 4YCC3030A1075AA | 85 | 0 | Yes | Yes | 20 | 19.5 | 0.5 | 83D0181448E44D038E1813B779610F65 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | 0% | 1 | 0%
Pollock Pines | CA | 95726-9257 |  | 2012-08-16 | 2012-08-16 12:37 | 2012-08-16 12:37 | CARRIER - 38BRC042330 | 108 | 0 | Yes | Yes | 20.2 | 18.6 | 1.6 | B887D53EC027426E92D60484907E78E7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-9500 |  | 2012-08-08 | 2012-08-08 11:29 | 2012-08-08 11:48 | GOODMAN - UNK | 88 | 5.2 | Yes | Yes | 19.4 | 19.8 | -0.4 | 9ED41DA63A134423B1A8524122DE92F8 |  | R22 | Non-TXV |  | 5.909% | 0.94091 | 11.36% | [5 empty] | Non-TXV | 5.909%
Rocklin | CA | 95765-4142 |  | 2012-05-23 | 2012-05-23 14:27 | 2012-05-23 14:27 | AMERICAN STANDARD - 7B0036B100AD | 90 | 0 | Yes | Yes | 20.4 | 21.7 | -1.3 | 473D6E96F14F4BE4BCC65E04A0D1E142 |  | R22 | TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-5433 |  | 2012-06-01 | 2012-06-01 12:35 | 2012-06-01 12:35 | GOODMAN - CK36-1D | 72 | 0 | Yes | Yes | 15 | 17.7 | -2.7 | 5115F7E56EEE4A0B9D846D8E1D723E06 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3579 |  | 2012-08-02 | 2012-08-02 10:04 | 2012-08-02 10:31 | TRANE - TTD742B100A0 | 97 | 3.3 | Yes | Yes | 26.5 | 21 | 5.5 | 763AC97FBBA644ECA7C3AEC227F37A5B |  | R22 | Non-TXV |  | 3.402% | 0.96598 | 6.538% | [5 empty] | Non-TXV | 3.402%
Rocklin | CA | 95765-4927 |  | 2012-06-07 | 2012-06-07 11:36 | 2012-06-07 11:54 | GOODMAN - GSC130601BA | 175 | 15.1 | Yes | Yes | 21.5 | 19.8 | 1.7 | 5D075186E3DD4C29A84CAA7D7313AD82 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 8.629% | 0.91371 | 16.58% | [5 empty] | Non-TXV | 8.629%
Los Banos | CA | 93635-9447 |  | 2012-05-24 | 2012-05-24 11:09 | 2012-05-24 11:28 | BRYANT - 561CJX06000AAAA | 155 | 4.8 | Yes | Yes | 18.4 | 20.4 | -2 | 6FD486683A5B480D97D703110C2C1824 |  | R22 | Non-TXV |  | 3.097% | 0.96903 | 5.951% | [5 empty] | Non-TXV | 3.097%
Stockton | CA | 95212-3403 |  | 2012-08-09 | 2012-08-09 13:37 | 2012-08-09 13:53 | YORK - H1RA048S06D | 117 | 15.2 | Yes | Yes | 16.1 | 17 | -0.9 | 218F0183FDB74E72876D6B316D87C34F |  | R22 | Non-TXV |  | 12.99% | 0.87009 | 24.97% | [5 empty] | Non-TXV | 12.99%
Manteca | CA | 95336-2853 |  | 2012-07-31 | 2012-07-31 10:38 | 2012-07-31 11:07 | RHEEM - RRNA-B036JK08X | 83 | 2.6 | Yes | Yes | 17.8 | 19.4 | -1.6 | 4E8F7113DD714033AE3619A3A147302B |  | R22 | Non-TXV |  | 3.133% | 0.96867 | 6.02% | [5 empty] | Non-TXV | 3.133%
Livingston | CA | 95334-1726 |  | 2012-08-10 | 2012-08-10 09:04 | 2012-08-10 09:32 | COLEMAN - UNK | 77 | 4.6 | Yes | Yes | 19.9 | 19 | 0.9 | 9B6B6F4EA22B4E3D98D565A11CDCC7CC |  | R22 | Non-TXV |  | 5.974% | 0.94026 | 11.48% | [5 empty] | Non-TXV | 5.974%
Los Banos | CA | 93635-2606 |  | 2012-08-01 | 2012-08-01 09:03 | 2012-08-01 09:31 | DAY & NIGHT - 561AJ030-A | 66 | -3.2 | Yes | Yes | 23 | 19.9 | 3.1 | AB6C47A3A4604786BF899D58C5508FFB |  | R22 | TXV |  | -4.848% | 1.0485 | 1.358% |  |  |  |  | TXV |  |  | -4.848%
Williams | CA | 95987-0000 |  | 2012-08-06 | 2012-08-06 15:20 | 2012-08-06 17:16 | RUUD - UNK | 87 | 7.5 | Yes | Yes | 25.4 | 19.6 | 5.8 | D7207DF14897401AB9AEB61A2300C60D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.621% | 0.91379 | 16.57% | [5 empty] | Non-TXV | 8.621%
Atwater | CA | 95301-3314 |  | 2012-08-07 | 2012-08-07 12:54 | 2012-08-07 12:54 | RHEEM - RRMA-A042JK08X | 114 | 0 | Yes | Yes | 16.9 | 19.9 | -3 | E32E3F1F4A274961856428BBB006DB44 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95348-3628 |  | 2012-08-02 | 2012-08-02 09:33 | 2012-08-02 10:35 | AMERICAN STANDARD - YCC030F1M0MBC | 67 | 2.9 | Yes | Yes | 20 | 20.4 | -0.4 | AB8A680619FD4AFDB07619F0490DF383 |  | R22 | Non-TXV |  | 4.328% | 0.95672 | 8.318% | [5 empty] | Non-TXV | 4.328%
Stockton | CA | 95207-3641 |  | 2012-07-31 | 2012-07-31 11:45 | 2012-07-31 12:06 | AMERICAN STANDARD - 2A7A8048B1000A | 232 | 18.8 | Yes | Yes | 19.1 | 21.7 | -2.6 | 3804F80D1C2F4B45915BB1B1B51458DC |  | R22 | TXV |  | 8.103% | 0.91897 | 15.57% | [5 empty] | TXV | 8.103%
Valley Springs | CA | 95252-0000 |  | 2012-08-13 | 2012-08-13 09:38 | 2012-08-13 09:58 | RUUD - UNK | 80 | 2.8 | Yes | Yes | 21.2 | 21.9 | -0.7 | 29696A016D6442BA8981E2B944C15216 |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Stockton | CA | 95210-1757 |  | 2012-07-31 | 2012-07-31 09:20 | 2012-07-31 09:37 | YORK - D1NA036N05606C | 67 | -3.9 | Yes | Yes | 22 | 18.8 | 3.2 | 2C91028E65754F60A14839C159422375 |  | R22 | Non-TXV |  | -5.821% | 1.0582 | 1.63% |  |  |  |  | Non-TXV |  |  | -5.821%
Valley Springs | CA | 95252-9388 |  | 2012-08-13 | 2012-08-13 13:57 | 2012-08-13 14:16 | RHEEM - UNK | 118 | 3.5 | Yes | Yes | 22.9 | 22.4 | 0.5 | 8023C177D70D4530B53FA92DC3D334C9 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Stockton | CA | 95209-4020 |  | 2012-05-22 | 2012-05-22 11:00 | 2012-05-22 11:17 | PAYNE - UNK | 87 | 10.4 | Yes | Yes | 26.1 | 20.1 | 6 | CD09D04C1EFE46B4B5C46D48470C7F38 |  | R22 | Non-TXV |  | 11.95% | 0.88046 | 22.97% | [5 empty] | Non-TXV | 11.95%
Valley Springs | CA | 95252-9174 |  | 2012-08-16 | 2012-08-16 10:19 | 2012-08-16 10:46 | YORK - H1CK036S06A | 132 | 3.9 | Yes | Yes | 20.1 | 21.5 | -1.4 | 450233D690CC481F82496C24015B05C7 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Rocklin | CA | 95677-1500 |  | 2012-08-03 | 2012-08-03 16:09 | 2012-08-03 16:09 | DAY & NIGHT - 591AN048-C | 122 | 0 | Yes | Yes | 24.7 | 20.4 | 4.3 | 7D5E918443DF4016A8FF3EDE56665638 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-1500 |  | 2012-08-03 | 2012-08-03 16:34 | 2012-08-03 16:34 | DAY & NIGHT - 591AN036-A | 82 | 0 | Yes | Yes | 21.9 | 20.3 | 1.7 | 9D42EA1329A340E1B62E5FDB3A7D238E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-9647 |  | 2012-08-02 | 2012-08-02 12:19 | 2012-08-02 12:41 | RUUD - UAHE-048JAS | 114 | 4.4 | Yes | Yes | 22.6 | 20.4 | 2.2 | C7704EAC090B48D2BD9CF242FE2464E0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.86% | 0.9614 | 7.417% | [5 empty] | Non-TXV | 3.86%
Rocklin | CA | 95677-3523 |  | 2012-05-16 | 2012-05-16 13:40 | 2012-05-16 14:05 | UNK - AC024M1021A | 52 | 1.9 | Yes | Yes | 18 | 19.9 | -1.9 | 523D26265ECC41348E7D1D7B94B9C986 |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Newman | CA | 95360-2734 |  | 2012-08-07 | 2012-08-07 13:06 | 2012-08-07 13:34 | GIBSON - JS3BC-036KA | 82 | 7 | Yes | Yes | 19.4 | 19.3 | 0.1 | 8F285AF59ABD4E0087B8E1EC78AADE42 |  | R22 | Non-TXV |  | 8.537% | 0.91463 | 16.41% | [5 empty] | Non-TXV | 8.537%
Paradise | CA | 95969-4054 |  | 2012-08-07 | 2012-08-07 08:55 | 2012-08-07 08:55 | AMERICAN STANDARD - 2YCX3036A1075AA | 81 | 0 | Yes | Yes | 22 | 20.7 | 1.3 | 1CB7266024C1433499009DCA884A7B8E |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-6332 |  | 2012-08-09 | 2012-08-09 11:13 | 2012-08-09 11:30 | PAYNE - PYG3NAA0360060NA-- | 98 | 3.6 | Yes | Yes | 28.3 | 22.8 | 5.5 | B36D5615C43F4844A9649E973BC62119 |  | R410A | TXV |  | 3.673% | 0.96327 | 7.06% | [5 empty] | TXV | 3.673%
Firebaugh | CA | 93622-2547 |  | 2012-05-31 | 2012-05-31 12:38 | 2012-05-31 13:23 | RUUD - URKA-A030JK6E | 54 | 1.6 | Yes | Yes | 23 | 20.2 | 2.8 | C123447D09D744B7872F5525E1B6C96E |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Planada | CA | 95365-0000 |  | 2012-08-14 | 2012-08-14 13:51 | 2012-08-14 14:09 | ARCOAIRE - HAC224AKC4 | 81 | 4.3 | Yes | Yes | 19 | 19.9 | -0.9 | 5279A411C7124FB8A1C93BAE4863ED91 |  | R22 | Non-TXV |  | 5.309% | 0.94691 | 10.2% | [5 empty] | Non-TXV | 5.309%
Chico | CA | 95928-9636 |  | 2012-06-08 | 2012-06-08 10:36 | 2012-06-08 11:38 | DAY & NIGHT - 542E036 | 130 | -7.6 | Yes | Yes | 22.5 | 20.1 | 2.5 | FDCEC25881544546BA7E95D02EE8837D |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Stockton | CA | 95206-5151 |  | 2012-08-14 | 2012-08-14 12:47 | 2012-08-14 13:05 | DAY & NIGHT - 561AJ042-A | 85 | 3.1 | Yes | Yes | 23 | 21.5 | 1.5 | 367DD8A45B164FD08954A18D4D5D67D9 |  | R22 | Non-TXV |  | 3.647% | 0.96353 | 7.009% | [5 empty] | Non-TXV | 3.647%
Los Banos | CA | 93635-6320 |  | 2012-05-17 | 2012-05-17 12:22 | 2012-05-17 12:44 | GOODMAN - CK301A | 76 | 8.9 | Yes | Yes | 29.9 | 24.2 | 5.7 | 6A4AE1542A3D430C9047AA51BB7909C0 |  | R22 | Non-TXV |  | 11.71% | 0.88289 | 22.51% | [5 empty] | Non-TXV | 11.71%
Tracy | CA | 95377-6634 |  | 2012-08-14 | 2012-08-14 12:42 | 2012-08-14 13:18 | UNITARY PRODUCTS GROUP - BRCSO421BD | 84 | 2.5 | Yes | Yes | 23 | 19 | 4 | 669E5F559C874CBC979E07BCC8BA958D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Paso Robles | CA | 93446-3008 |  | 2012-07-11 | 2012-07-11 14:48 | 2012-07-11 15:06 | AMANA - RCC36A2B | 114 | 5.6 | Yes | Yes | 14.7 | 15.5 | -0.8 | 9004B9929C02449E96E44EBF71E966E9 |  | R22 | Non-TXV |  | 4.912% | 0.95088 | 9.44% | [5 empty] | Non-TXV | 4.912%
Stockton | CA | 95215-0000 |  | 2012-05-31 | 2012-05-31 12:01 | 2012-05-31 12:21 | COLEMAN - BRCS0481BD | 116 | 4.8 | Yes | Yes | 18.4 | 20.3 | -1.9 | D36BF7429D5B4E3CBB0509979E420C03 |  | R22 | Non-TXV |  | 4.138% | 0.95862 | 7.952% | [5 empty] | Non-TXV | 4.138%
Marysville | CA | 95901-7129 |  | 2012-05-31 | 2012-05-31 13:52 | 2012-05-31 14:09 | PAYNE - PY1PN036060ABAA | 68 | 2.6 | Yes | Yes | 21 | 20.9 | 0.1 | 90FBFFD1B7A2412D8338E81C9D22A41E |  | R22 | Non-TXV |  | 3.824% | 0.96176 | 7.348% | [5 empty] | Non-TXV | 3.824%
Stockton | CA | 95210-4303 |  | 2012-05-31 | 2012-05-31 11:04 | 2012-05-31 11:21 | DAY & NIGHT - UNK | 50 | 2.1 | Yes | Yes | 22 | 21 | 1 | F0DC51C088724B7E8544459829F8F90E |  | R22 | Non-TXV |  | 4.2% | 0.958 | 8.071% | [5 empty] | Non-TXV | 4.2%
Manteca | CA | 95336-9134 |  | 2012-08-09 | 2012-08-09 10:02 | 2012-08-09 10:26 | BDP - 561CJ042-A | 80 | 21.6 | Yes | Yes | 15.5 | 17.7 | -2.2 | 1F760F4010E944D8BCEDAB601C0092ED | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 27% | 0.73 | 51.89% | [5 empty] | Non-TXV | 27%
Stockton | CA | 95204-2747 |  | 2012-05-07 | 2012-05-07 18:31 | 2012-05-07 19:01 | BRYANT - 561CJ024-D | 55 | 3.6 | Yes | Yes | 1.4 | 17.4 | -16 | 0F29EA6C91C242B6A32D58D3A0D5A56C | OK: Verified Refrigerant Charge | R22 | TXV |  | 6.545% | 0.93455 | 12.58% | [5 empty] | TXV | 6.545%
Winton | CA | 95388-9270 |  | 2012-08-06 | 2012-08-06 09:51 | 2012-08-06 09:51 | CARRIER - 48GS-030040301 | 55 | 0 | Yes | Yes | 23.1 | 21.4 | 1.7 | AC697459E435469C920D0977D7CF2289 |  | R22 | TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-7055 |  | 2012-08-15 | 2012-08-15 08:41 | 2012-08-15 08:58 | NORDYNE - JS3BA-048KA | 115 | 3.6 | Yes | Yes | 19.9 | 19.3 | 0.6 | D7D1B55075384762B736733A0BF92148 |  | R22 | Non-TXV |  | 3.13% | 0.9687 | 6.016% | [5 empty] | Non-TXV | 3.13%
Chowchilla | CA | 93610-2734 |  | 2012-05-14 | 2012-05-14 12:56 | 2012-05-14 12:56 | YPRK - D1NA036N05606C | 67 | 0 | Yes | Yes | 20.2 | 20.9 | -0.7 | 5F34D2BCA66042B695B8895E88B02048 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3245 |  | 2012-08-02 | 2012-08-02 08:49 | 2012-08-02 09:05 | GE - BTB942A100A0 | 101 | -5.9 | Yes | Yes | 24.1 | 20.4 | 3.7 | 24F0E8A0D62241A6839E644A074D1336 |  | R22 | Non-TXV |  | -5.842% | 1.0584 | 1.636% |  |  |  |  | Non-TXV |  |  | -5.842%
Los Banos | CA | 93635-9408 |  | 2012-08-16 | 2012-08-16 10:59 | 2012-08-16 11:28 | BRYANT - 561CJ060A | 152 | 8.2 | Yes | Yes | 26.6 | 22.3 | 4.3 | 26FCE0525ED9498EBED9F6A277AB8560 |  | R22 | TXV |  | 5.395% | 0.94605 | 10.37% | [5 empty] | TXV | 5.395%
Madera | CA | 93638-0476 |  | 2012-06-11 | 2012-06-11 15:27 | 2012-06-11 15:27 | OTHER - UNK | 59 | 0 | Yes | Yes | 19.4 | 20.4 | -1 | F941214BEFE94EA09790D8EA991A34F6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2072 |  | 2012-08-10 | 2012-08-10 14:57 | 2012-08-10 15:21 | NORDYNE - JS3BD048K | 143 | 11.1 | Yes | Yes | 25.6 | 24.8 | 0.8 | BD7C7EE6B81C4FC98CD65CFD27AFDF48 |  | R22 | Non-TXV |  | 7.762% | 0.92238 | 14.92% | [5 empty] | Non-TXV | 7.762%
Planada | CA | 95365-0000 |  | 2012-08-14 | 2012-08-14 13:15 | 2012-08-14 13:44 | GOODMAN - GPG13300701BB | 77 | 3.9 | Yes | Yes | 22.7 | 19.5 | 3.2 | BDB5B64197F546B99677CCFFE578CED3 |  | R22 | Non-TXV |  | 5.065% | 0.94935 | 9.734% | [5 empty] | Non-TXV | 5.065%
Los Banos | CA | 93635-4506 |  | 2012-05-24 | 2012-05-24 13:06 | 2012-05-24 13:28 | OTHER - MSC26-6A | 80 | 6.4 | Yes | Yes | 19.7 | 20.7 | -1 | F442D3662CF94B3C844DA8001F25A5DB |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Stockton | CA | 95210-5615 |  | 2012-08-09 | 2012-08-09 12:47 | 2012-08-09 14:00 | BRYANT - PA13NR048-H | 137 | 14.5 | Yes | Yes | 18.9 | 18.5 | 0.4 | 6701C7626F434B3D851E4D457993E155 |  | R22 | TXV |  | 10.58% | 0.89416 | 20.34% | [5 empty] | TXV | 10.58%
Chico | CA | 95926-3054 |  | 2012-05-14 | 2012-05-14 10:37 | 2012-05-14 11:06 | DAY N NIGHT - 591ANX030000AAAA | 76 | 3.9 | Yes | Yes | 22.5 | 21.5 | 1 | FCE4D39C0E194E9EB42F89D19FF32EF9 |  | R22 | Non-TXV |  | 5.132% | 0.94868 | 9.862% | [5 empty] | Non-TXV | 5.132%
Riverbank | CA | 95367-4217 |  | 2012-08-16 | 2012-08-16 16:53 | 2012-08-16 17:17 | RUUD - UAMB-48JBZ | 162 | 21.3 | Yes | Yes | 20 | 22.1 | -2.1 | 27D56AFFB5CD4EA1ADCD632065711B12 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.15% | 0.86852 | 25.27% | [5 empty] | Non-TXV | 13.15%
Chico | CA | 95926-3054 |  | 2012-05-16 | 2012-05-16 11:24 | 2012-05-16 11:52 | DAYNNIGHT - 591ANX030000AAAA | 77 | 4.7 | Yes | Yes | 19.1 | 20.1 | -1 | 6A301D92285F4CD290D8FFFE4D070C9A |  | R22 | Non-TXV |  | 6.104% | 0.93896 | 11.73% | [5 empty] | Non-TXV | 6.104%
Marysville | CA | 95901-4288 |  | 2012-07-13 | 2012-07-13 09:24 | 2012-07-13 09:49 | OTHER - 540JJ018 | 65 | -3.8 | Yes | Yes | 20.2 | 19.9 | 0.3 | C74842FDA38B42CD8F96A7BC368DCA95 |  | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Stockton | CA | 95205-2838 |  | 2012-05-15 | 2012-05-15 11:23 | 2012-05-15 11:41 | CARRIER - 48KL130311BE | 54 | 5.9 | Yes | Yes | 21.4 | 21.4 | 0 | 8DB7DF81709546E5AA3DF567C331BA2B |  | R22 | Non-TXV |  | 10.93% | 0.89074 | 21% | [5 empty] | Non-TXV | 10.93%
Stockton | CA | 95210-3621 |  | 2012-08-06 | 2012-08-06 11:55 | 2012-08-06 12:12 | CARRIER - 38EN030300 | 90 | 3.3 | Yes | Yes | 19.8 | 19.3 | 0.5 | 5B23220C77164EC6A1DF9219FE40F153 |  | R22 | Non-TXV |  | 3.667% | 0.96333 | 7.047% | [5 empty] | Non-TXV | 3.667%
Stockton | CA | 95210-1836 |  | 2012-08-07 | 2012-08-07 08:59 | 2012-08-07 09:19 | GE - BGTA742B1A01 | 100 | 3.1 | Yes | Yes | 18.1 | 18.5 | -0.4 | 406F37F9BE50494080529B0BA141731D |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Marysville | CA | 95901-4804 |  | 2012-05-17 | 2012-05-17 13:47 | 2012-05-17 14:07 | BRYANT - 561CJ030-D | 68 | 7.7 | Yes | Yes | 24.3 | 18.7 | 5.6 | 7448B4B604B54EF7A6862F30C772E2F4 |  | R22 | Non-TXV |  | 11.32% | 0.88676 | 21.76% | [5 empty] | Non-TXV | 11.32%
El Dorado | CA | 95623-4318 |  | 2012-07-26 | 2012-07-26 10:26 | 2012-07-26 10:46 | TRANE - TWD730B100A0 | 89 | -6.3 | Yes | Yes | 20.5 | 21 | -0.5 | 98161EA1A5554E7DA6B79456F4BA8DC7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.079% | 1.0708 | 1.982% |  |  |  |  | Non-TXV |  |  | -7.079%
Los Banos | CA | 93635-5308 |  | 2012-08-09 | 2012-08-09 12:35 | 2012-08-09 13:03 | RUUD - UNK | 77 | 13 | Yes | Yes | 23.9 | 25.1 | -1.2 | 18DAA68455E04FF09463921137B38467 |  | R22 | Non-TXV |  | 16.88% | 0.83117 | 32.45% | [5 empty] | Non-TXV | 16.88%
Los Banos | CA | 93635-5242 |  | 2012-05-22 | 2012-05-22 14:46 | 2012-05-22 15:11 | BRYANT - 561CJ042-B | 81 | -3 | Yes | Yes | 23.5 | 21.9 | 1.6 | B862AFB048F346E29DCE9D47EA70ACBE |  | R22 | TXV |  | -3.704% | 1.037 | 1.037% |  |  |  |  | TXV |  |  | -3.704%
Stockton | CA | 95210-1110 |  | 2012-05-07 | 2012-05-07 11:09 | 2012-05-07 11:09 | RHEEM - RRKA-A024JK06E | 50 | 0 | Yes | Yes | 23.2 | 20.3 | 2.9 | 81D2039B43824227815DC203F720E9FD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-5761 |  | 2012-05-30 | 2012-05-30 11:41 | 2012-05-30 12:04 | CARRIER - 38BRC024 | 82 | -7.7 | Yes | Yes | 18 | 20.8 | -2.8 | 3B5CB60F4A4641909BEED772559EBE53 |  | R22 | Non-TXV |  | -9.39% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.39%
Tracy | CA | 95377-7974 |  | 2012-08-15 | 2012-08-15 14:30 | 2012-08-15 14:49 | GOODMAN - CLT36-1A | 140 | 4.6 | Yes | Yes | 21 | 20.9 | 0.1 | 7F609E2807A54B3AA6E5950D5CA302B6 |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Stockton | CA | 95210-3606 |  | 2012-05-24 | 2012-05-24 14:56 | 2012-05-24 15:13 | GMC - VSC130361AA | 119 | 14.4 | Yes | Yes | 24.2 | 22.7 | 1.5 | E003729528C142AAADC8FB1154E8E006 |  | R22 | Non-TXV |  | 12.1% | 0.87899 | 23.26% | [5 empty] | Non-TXV | 12.1%
Corning | CA | 96021-3326 |  | 2012-08-02 | 2012-08-02 10:58 | 2012-08-02 11:17 | TEMPSTAR - PGAD30D1K3 | 78 | 6.1 | Yes | Yes | 21.8 | 21 | 0.8 | 247CB3E240084644B144891C974D5811 |  | R22 | Non-TXV |  | 7.821% | 0.92179 | 15.03% | [5 empty] | Non-TXV | 7.821%
Los Banos | CA | 93635-2600 |  | 2012-08-06 | 2012-08-06 13:40 | 2012-08-06 15:00 | DAY & NIGHT - 593CK042-A | 92 | 3 | Yes | Yes | 18.6 | 18.5 | 0.1 | 716A84FB865B43E98EEE4E2798A9E040 |  | R22 | Non-TXV |  | 3.261% | 0.96739 | 6.267% | [5 empty] | Non-TXV | 3.261%
Madera | CA | 93637-5662 |  | 2012-08-09 | 2012-08-09 11:21 | 2012-08-09 11:42 | DAY & NIGHT - 561AJ030-1 | 72 | 2.3 | Yes | Yes | 18.4 | 19.9 | -1.5 | 86B3D81D72F84121BDB737424A9E4FFE |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Shingle Springs | CA | 95682-9324 |  | 2013-11-20 | 2013-11-20 10:00 | 2013-11-20 10:00 | YORK - UNK | 81 | 0 | Yes | Yes | 35 | 20.7 | 14.3 | 08D5E8495A024E30A7A6477C1CC82018 | Actual Superheat must be between -2°F and 100°F. Check entries and calibration. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-7974 |  | 2012-08-14 | 2012-08-14 13:32 | 2012-08-14 13:49 | GOODMAN - CLT30-1A | 107 | 3.5 | Yes | Yes | 18.4 | 17.6 | 0.8 | 359C9BBF5FA14685AAD803AA7F306D9A |  | R22 | Non-TXV |  | 3.271% | 0.96729 | 6.286% | [5 empty] | Non-TXV | 3.271%
Fresno | CA | 93722-3317 |  | 2012-06-07 | 2012-06-07 17:01 | 2012-06-07 17:23 | CARRIER - UNK | 52 | 1.9 | Yes | Yes | 16.9 | 19.9 | -3 | 4950EC11AC664B6F962451AA4B7306C3 |  | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Stockton | CA | 95210-1624 |  | 2012-05-15 | 2012-05-15 14:25 | 2012-05-15 14:44 | RUUD - RRMA-A036JK08X | 99 | 3.2 | Yes | Yes | 22.1 | 19.8 | 2.3 | CE2537C2597040BDB63F556D5E84AAA0 |  | R22 | Non-TXV |  | 3.232% | 0.96768 | 6.212% | [5 empty] | Non-TXV | 3.232%
Firebaugh | CA | 93622-2422 |  | 2012-05-31 | 2012-05-31 13:07 | 2012-05-31 13:24 | PAYNE - N/A | 64 | 1.9 | Yes | Yes | 22.4 | 21.2 | 1.2 | B30F2EFC48E54792B3FD39DB0AC081F9 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Los Banos | CA | 93635-9230 |  | 2012-08-16 | 2012-08-16 15:08 | 2012-08-16 15:29 | OTHER - JS5BD036K | 138 | 10.2 | Yes | Yes | 18.6 | 16.9 | 1.7 | B992BF22D37E458FA3A0693160B3D6F7 |  | R22 | Non-TXV |  | 7.391% | 0.92609 | 14.2% | [5 empty] | Non-TXV | 7.391%
Chico | CA | 95926-4770 |  | 2012-05-16 | 2012-05-16 14:22 | 2012-05-16 14:43 | DAYNNIGHT - 58CJ024050 | 125 | 3.1 | Yes | Yes | 15.9 | 17.2 | -1.3 | 67910301484C4720AEE91CED5CEBA240 |  | R22 | Non-TXV |  | 2.48% | 0.9752 | 4.766% | [5 empty] | Non-TXV | 2.48%
Stockton | CA | 95210-1251 |  | 2012-05-07 | 2012-05-07 13:47 | 2012-05-07 14:05 | HEIL - PGAA36C1K3 | 81 | 2.9 | Yes | Yes | 21.5 | 23.1 | -1.6 | 12EE047BC0C2468DBF934A14FDB91DDD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.58% | 0.9642 | 6.88% | [5 empty] | Non-TXV | 3.58%
Stockton | CA | 95209-4025 |  | 2012-05-16 | 2012-05-16 11:11 | 2012-05-16 11:35 | RHEEM - RRNA-B024JK06X | 70 | 5.7 | Yes | Yes | 16.3 | 18.7 | -2.4 | 6AE3BF61B28A42C29A915070A1943A38 | OK: Verified Refrigerant Charge | R22 | TXV |  | 8.143% | 0.91857 | 15.65% | [5 empty] | TXV | 8.143%
Manteca | CA | 95337-8237 |  | 2012-08-10 | 2012-08-10 15:47 | 2012-08-10 16:18 | GOODMAN - CLJ48-1 | 111 | 14.8 | Yes | Yes | 21.7 | 18.6 | 3.1 | B1E0F4E0EBCB46FFB6E62C2760053BCE |  | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Merced | CA | 95348-1603 |  | 2012-05-11 | 2012-05-11 10:57 | 2012-05-11 11:16 | AMANA - PGB24C0702E | 64 | 1.9 | Yes | Yes | 24.5 | 22.5 | 2 | 9D7EED9DA7174C7BA4C0019A964A85D5 |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Tracy | CA | 95376-8148 |  | 2012-06-21 | 2012-06-21 15:50 | 2012-06-21 16:11 | RUUD - UAPL-036JAZ | 141 | 27.2 | Yes | Yes | 20.5 | 21.4 | -0.9 | 65694BC61AFF4F3BACB025F39F124542 |  | R410A | Non-TXV |  | 19.29% | 0.80709 | 37.07% | [5 empty] | Non-TXV | 19.29%
Chico | CA | 95926-3504 |  | 2012-08-02 | 2012-08-02 11:46 | 2012-08-02 19:03 | GOODMAN - GSC130481BA | 100 | 3.1 | Yes | Yes | 24.4 | 21.3 | 3.2 | 4B319B00F33947E8ADEBAD3462A28BF2 |  | R22 | Non-TXV |  | 3.1% | 0.969 | 5.958% | [5 empty] | Non-TXV | 3.1%
Los Banos | CA | 93635-2623 |  | 2012-05-08 | 2012-05-08 11:52 | 2012-05-08 12:18 | GOODMAN - CKJ-421B | 85 | 7.8 | Yes | Yes | 21.3 | 20.2 | 1.1 | 063193EDB8B547B193A67853C5213EAA | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.176% | 0.90824 | 17.64% | [5 empty] | Non-TXV | 9.176%
Fresno | CA | 93722-2748 |  | 2012-05-14 | 2012-05-14 11:41 | 2012-05-14 12:07 | YORK - H2DH036906A | 124 | 4 | Yes | Yes | 23 | 19.4 | 3.6 | 8F1D9CE8E49A4DB3A43016C419C16DB5 |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Shingle Springs | CA | 95682-9439 |  | 2012-08-02 | 2012-08-02 17:00 | 2012-08-02 17:38 | TRANE - BW00360100A0 | 139 | 30 | Yes | Yes | 21.7 | 21.5 | 0.2 | 8AB68998F1744E9E8E178E7A2495777E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 21.58% | 0.78417 | 41.48% | [5 empty] | Non-TXV | 21.58%
Shingle Springs | CA | 95682-9439 |  | 2012-08-02 | 2012-08-02 18:01 | 2012-08-02 18:18 | TRANE - BWC024C100A1 | 123 | 6.7 | Yes | Yes | 27.9 | 22 | 5.9 | 4D6B2310438844C497B6866B156B9AA6 |  | R22 | Non-TXV |  | 5.447% | 0.94553 | 10.47% | [5 empty] | Non-TXV | 5.447%
Stockton | CA | 95204-5830 |  | 2012-05-09 | 2012-05-09 13:00 | 2012-05-09 13:18 | RHEEM - UNK | 35 | 2.9 | Yes | Yes | 16 | 18.6 | -2.6 | FB6344EA42554ED4ACC4AA90E1323385 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.286% | 0.91714 | 15.92% | [5 empty] | Non-TXV | 8.286%
Chowchilla | CA | 93610-2828 |  | 2012-05-11 | 2012-05-11 09:51 | 2012-05-11 10:11 | YORK - N1DB030S06B | 70 | 3.8 | Yes | Yes | 22.7 | 21.4 | 1.3 | BA1AD5ED370D4279BDAFD012A0BA6010 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.429% | 0.94571 | 10.43% | [5 empty] | Non-TXV | 5.429%
Chico | CA | 95973-8318 |  | 2012-08-16 | 2012-08-16 18:33 | 2012-08-16 19:28 | YORK - H1CH030506A | 179 | 16.4 | Yes | Yes | 20.7 | 21.5 | -0.8 | 8473AB3AABDD48C0825827ADBB634D1D |  | R22 | Non-TXV |  | 9.162% | 0.90838 | 17.61% | [5 empty] | Non-TXV | 9.162%
Winton | CA | 95388-9777 |  | 2012-08-03 | 2012-08-03 12:15 | 2012-08-03 12:55 | YORK - H4DB036S06A | 73 | -4.3 | Yes | Yes | 28.1 | 22.4 | 5.7 | 6CB25230B897463A9E8BFEFA8E8F8BC2 |  | R22 | Non-TXV |  | -5.89% | 1.0589 | 1.65% |  |  |  |  | Non-TXV |  |  | -5.89%
Madera | CA | 93637-1411 |  | 2012-08-09 | 2012-08-09 10:56 | 2012-08-09 11:17 | YORK - H2RD036S06B | 96 | 3 | Yes | Yes | 17.4 | 18.8 | -1.4 | 4781C5FA0B494DE994BBFD4EC234A127 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Newman | CA | 95360-9509 |  | 2012-08-08 | 2012-08-08 12:43 | 2012-08-08 13:12 | GOODMAN - CKL-36-1L | 85 | 3.8 | Yes | Yes | 19.7 | 20.4 | -0.7 | AFE4F64577CC46CE93552C873B38B351 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Lathrop | CA | 95330-0000 |  | 2012-08-10 | 2012-08-10 13:39 | 2012-08-10 14:00 | BRYANT - 561CJ060-H | 133 | 3.9 | Yes | Yes | 19.4 | 21.5 | -2.1 | 8505243C3D4E4E5285B12F457882E80D |  | R22 | Non-TXV |  | 2.932% | 0.97068 | 5.635% | [5 empty] | Non-TXV | 2.932%
Magalia | CA | 95954-8803 |  | 2012-08-08 | 2012-08-08 09:51 | 2012-08-08 10:12 | COLEMAN - 3236-901 | 102 | 4.6 | Yes | Yes | 20.8 | 20.8 | 0 | 2A1B3F88BE05406994BF7A03F1F285E6 |  | R22 | Non-TXV |  | 4.51% | 0.9549 | 8.667% | [5 empty] | Non-TXV | 4.51%
Magalia | CA | 95954-9647 |  | 2012-06-14 | 2012-06-14 10:07 | 2012-06-14 10:39 | RHEEM - RAKA-036JAS | 75 | 10.8 | Yes | Yes | 23.7 | 21.2 | 2.5 | 6B015CCE699D46AEB32F2A6B6ADB7917 |  | R22 | Non-TXV |  | 14.4% | 0.856 | 27.67% | [5 empty] | Non-TXV | 14.4%
Magalia | CA | 95954-9572 |  | 2012-08-09 | 2012-08-09 10:12 | 2012-08-09 10:46 | BRYANT - 583BNW036090AB | 105 | 3.3 | Yes | Yes | 24.9 | 20.6 | 4.3 | 7CED0AEE33814815B87CDC926717051B |  | R410A | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Fresno | CA | 93711-2651 |  | 2012-05-16 | 2012-05-16 11:05 | 2012-05-16 11:22 | ICP - GPFM24K040E | 54 | 1.6 | Yes | Yes | 21.4 | 20.9 | 0.5 | 82315C08EAC040C4B60B2DEC674332AA |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95204-4156 |  | 2012-08-02 | 2012-08-02 14:55 | 2012-08-02 15:15 | HEIL - PGAA36C1K1 | 77 | 5.3 | Yes | Yes | 22 | 20.1 | 1.9 | BA65A8380ADF4A809084CEE7DA167F47 |  | R22 | Non-TXV |  | 6.883% | 0.93117 | 13.23% | [5 empty] | Non-TXV | 6.883%
Manteca | CA | 95336-2870 |  | 2012-08-15 | 2012-08-15 10:36 | 2012-08-15 11:05 | WHIRLPOOL - UNK | 85 | 25.7 | Yes | Yes | 16.9 | 19.9 | -3 | D749B2B6D3F140F29120A7BA6CCB6E4C |  | R22 | Non-TXV |  | 30.24% | 0.69765 | 58.11% | [5 empty] | Non-TXV | 30.24%
Winton | CA | 95388-9761 |  | 2012-05-09 | 2012-05-09 09:37 | 2012-05-09 10:01 | BRYANT - 582ANW042060NAAG | 100 | 2.9 | Yes | Yes | 23.3 | 18.8 | 4.5 | 2E8402CABCA541E6B83D004895B6B788 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Chico | CA | 95926-3065 |  | 2012-05-14 | 2012-05-14 17:28 | 2012-05-14 17:44 | GRAND TIRE - JS3B-030KA | 69 | 2.4 | Yes | Yes | 20.6 | 22.1 | -1.5 | DFFDD4F15B9B4015946680494BC72C5C |  | R22 | Non-TXV |  | 3.478% | 0.96522 | 6.684% | [5 empty] | Non-TXV | 3.478%
Stockton | CA | 95219-3605 |  | 2012-06-15 | 2012-06-15 09:38 | 2012-06-15 09:54 | DAY & NIGHT - 593ANX060000AAAA | 231 | 8.6 | Yes | Yes | 23.5 | 20.8 | 2.7 | 8A53D58E0E49483F8FCC2F2641CBC41E |  | R22 | Non-TXV |  | 3.723% | 0.96277 | 7.155% | [5 empty] | Non-TXV | 3.723%
Atwater | CA | 95301-9609 |  | 2012-08-10 | 2012-08-10 12:41 | 2012-08-10 12:59 | RUUD - URGG-07E48JKR | 136 | -8 | Yes | Yes | 24.1 | 19.5 | 4.6 | D6492A657FEF49C790ECD24BB241924E |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Manteca | CA | 95337-6100 |  | 2012-05-17 | 2012-05-17 14:26 | 2012-05-17 14:46 | TRANE - TTD730B100A0 | 69 | 6.3 | Yes | Yes | 19.4 | 20.7 | -1.3 | 4174BFE709F6472DB5EA5AF56C724F6B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.13% | 0.9087 | 17.55% | [5 empty] | Non-TXV | 9.13%
Gridley | CA | 95948-9300 |  | 2012-07-19 | 2012-07-19 09:43 | 2012-07-19 09:59 | RUUD - UNK | 95 | 5.1 | Yes | Yes | 15 | 17.7 | -2.7 | 3B63239243D64C86B08B799F007CEFC5 |  | R22 | Non-TXV |  | 5.368% | 0.94632 | 10.32% | [5 empty] | Non-TXV | 5.368%
Newman | CA | 95360-9505 |  | 2012-08-08 | 2012-08-08 13:42 | 2012-08-08 14:13 | GOODMAN - CKL-42-11 | 104 | 7.9 | Yes | Yes | 16.8 | 19.2 | -2.4 | D635E6C0FF4B4A0AB225F6486F1B28CC |  | R22 | Non-TXV |  | 7.596% | 0.92404 | 14.6% | [5 empty] | Non-TXV | 7.596%
Tracy | CA | 95377-8701 |  | 2012-08-14 | 2012-08-14 11:48 | 2012-08-14 12:06 | LENNOX - 13ACC-030-230-01 | 106 | 3.3 | Yes | Yes | 21.6 | 21 | 0.6 | 1A9CF50F6AFE4308A163999735954E78 |  | R22 | Non-TXV |  | 3.113% | 0.96887 | 5.983% | [5 empty] | Non-TXV | 3.113%
Madera | CA | 93637-8662 |  | 2012-05-07 | 2012-05-07 11:50 | 2012-05-07 12:19 | CARRIER - 38BRC060360 | 200 | 5.9 | Yes | Yes | 23.3 | 19.8 | 3.5 | DCE41A0E6C3C445AB3A3900EF215588E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.95% | 0.9705 | 5.669% | [5 empty] | Non-TXV | 2.95%
Stockton | CA | 95204-2655 |  | 2012-08-06 | 2012-08-06 15:06 | 2012-08-06 15:25 | HEIL - PGC036K080A | 71 | -6.7 | Yes | Yes | 20 | 21.3 | -1.3 | 1D37FD525B224A05969363103313AE85 |  | R22 | Non-TXV |  | -9.437% | 1.0944 | 2.643% |  |  |  |  | Non-TXV |  |  | -9.437%
Madera | CA | 93638-0102 |  | 2012-08-10 | 2012-08-10 08:58 | 2012-08-10 09:16 | LENNOX - 12GCS060X1005PB | 159 | 11.5 | Yes | Yes | 19.6 | 20.4 | -0.8 | 0D7140DE623B49BE9AF4CD3B0F90F155 |  | R22 | Non-TXV |  | 7.233% | 0.92767 | 13.9% | [5 empty] | Non-TXV | 7.233%
Los Banos | CA | 93635-3035 |  | 2012-08-07 | 2012-08-07 09:03 | 2012-08-07 09:26 | GOODMAN - CK301B | 76 | 8.9 | Yes | Yes | 23.3 | 21.8 | 1.5 | B53347A15BB542DD8D6D4300119020DF |  | R22 | Non-TXV |  | 11.71% | 0.88289 | 22.51% | [5 empty] | Non-TXV | 11.71%
Madera | CA | 93637-6506 |  | 2012-08-10 | 2012-08-10 10:01 | 2012-08-10 10:21 | LENNOX - 13ACD03623002 | 111 | 9.3 | Yes | Yes | 20.4 | 19.7 | 0.7 | 9210030E6BED45FDB7D2C060E5710616 |  | R22 | Non-TXV |  | 8.378% | 0.91622 | 16.1% | [5 empty] | Non-TXV | 8.378%
Madera | CA | 93638-7832 |  | 2012-08-10 | 2012-08-10 23:35 | 2012-08-10 23:55 | CARRIER - 48GX-0360301 | 82 | 3.1 | Yes | Yes | 16.9 | 15.9 | 1 | FD03BF97D2CD456B86A6A986348FF02D |  | R22 | Non-TXV |  | 3.78% | 0.9622 | 7.265% | [5 empty] | Non-TXV | 3.78%
Stockton | CA | 95204-3939 |  | 2012-05-11 | 2012-05-11 12:01 | 2012-05-11 12:18 | PAYNE - 588ANW024040AAAD | 40 | 3.4 | Yes | Yes | 18.3 | 20.9 | -2.6 | 5159401C84804352A4223B00B2B129F2 |  | R22 | Non-TXV |  | 8.5% | 0.915 | 16.34% | [5 empty] | Non-TXV | 8.5%
Madera | CA | 93638-9666 |  | 2012-08-03 | 2012-08-03 14:17 | 2012-08-03 14:41 | CARRIER - UNK | 70 | 3.2 | Yes | Yes | 16.3 | 18.2 | -1.9 | FAC2BD5B08284983811F2CE267A57DB5 |  | R22 | Non-TXV |  | 4.571% | 0.95429 | 8.785% | [5 empty] | Non-TXV | 4.571%
Manteca | CA | 95336-6318 |  | 2012-08-09 | 2012-08-09 11:46 | 2012-08-09 12:14 | DAY & NIGHT - 585GW024040ABAE | 54 | 6.1 | Yes | Yes | 24.8 | 19.9 | 4.9 | 59D869002B2949E5AF1D442FE92A1B74 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.3% | 0.88704 | 21.71% | [5 empty] | Non-TXV | 11.3%
Los Banos | CA | 93635-7427 |  | 2012-08-14 | 2012-08-14 10:33 | 2012-08-14 10:58 | AIRE-FLO - PA13NR030000AEAA | 86 | 8.4 | Yes | Yes | 18.6 | 20.1 | -1.5 | F1E1CF126C154B49AFCCAAAEB4F2C723 |  | R22 | Non-TXV |  | 9.767% | 0.90233 | 18.77% | [5 empty] | Non-TXV | 9.767%
Los Banos | CA | 93635-2643 |  | 2012-08-08 | 2012-08-08 11:25 | 2012-08-08 11:45 | BDP - 588ANW02404ACDC | 43 | 3.8 | Yes | Yes | 25.3 | 20.4 | 4.9 | E19BBAEDDE4A43A3ADAA7C169AEEF3B1 |  | R22 | Non-TXV |  | 8.837% | 0.91163 | 16.98% | [5 empty] | Non-TXV | 8.837%
Los Banos | CA | 93635-3006 |  | 2012-05-09 | 2012-05-09 14:08 | 2012-05-09 14:27 | BRYANT - 588ANW030060ADAD | 58 | 4.1 | Yes | Yes | 26.7 | 22.7 | 4 | FFC259E5BE914BFA9596AC870F0DA581 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Madera | CA | 93637-4119 |  | 2012-05-07 | 2012-05-07 16:23 | 2012-05-07 16:51 | YORK - D1NA042N05606C | 76 | 6.6 | Yes | Yes | 25.8 | 22 | 3.8 | EF2156E8D3464A2B93821E353E8FA2FD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.684% | 0.91316 | 16.69% | [5 empty] | Non-TXV | 8.684%
Los Banos | CA | 93635-6408 |  | 2012-08-13 | 2012-08-13 13:55 | 2012-08-13 14:14 | BRYANT - 561CJ060-A | 135 | 4.2 | Yes | Yes | 20.4 | 20.4 | 0 | 0EA36478E96D4CCDA82A6838C0E5ED30 |  | R22 | Non-TXV |  | 3.111% | 0.96889 | 5.979% | [5 empty] | Non-TXV | 3.111%
Chico | CA | 95973-9293 |  | 2012-08-09 | 2012-08-09 19:21 | 2012-08-09 19:40 | LENNOX - HS26-048-3P | 114 | 0 | Yes | Yes | 23 | 21.3 | 1.8 | 5E5131909FD8446EBC9BD50433FE8562 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-9293 |  | 2012-08-09 | 2012-08-09 19:44 | 2012-08-09 20:04 | LENNOX - HS26-030-3P | 68 | 7.5 | Yes | Yes | 25.4 | 22.2 | 3.2 | 577145FA48614534A3525F9BA3E83BAD |  | R22 | Non-TXV |  | 11.03% | 0.88971 | 21.2% | [5 empty] | Non-TXV | 11.03%
Fresno | CA | 93727-4439 |  | 2012-05-09 | 2012-05-09 17:46 | 2012-05-09 18:12 | EVCON - ACO18M1021CG | 49 | 8.6 | Yes | Yes | 24 | 20.4 | 3.6 | DD569C8AA48D46B0A1EE1692D8A43A23 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 17.55% | 0.82449 | 33.73% | [5 empty] | Non-TXV | 17.55%
Riverbank | CA | 95367-3089 |  | 2012-08-16 | 2012-08-16 13:48 | 2012-08-16 14:06 | DAY & NIGHT - 591ANX024000AAAA | 53 | 2 | Yes | Yes | 26.7 | 22.3 | 4.4 | 37E7672BA96E47F3A4CFF6CF17322180 |  | R22 | Non-TXV |  | 3.774% | 0.96226 | 7.252% | [5 empty] | Non-TXV | 3.774%
Stockton | CA | 95215-5851 |  | 2012-08-08 | 2012-08-08 12:09 | 2012-08-08 12:26 | GOODMAN - PGB036075-1A | 60 | 3.1 | Yes | Yes | 24.5 | 21 | 3.5 | 149B247ABB6E4E1A80A33F820DF41AC3 |  | R22 | Non-TXV |  | 5.167% | 0.94833 | 9.929% | [5 empty] | Non-TXV | 5.167%
Chowchilla | CA | 93610-9427 |  | 2012-08-10 | 2012-08-10 13:37 | 2012-08-10 14:03 | NORDYNE - FS5BD060K | 232 | 13.6 | Yes | Yes | 27.2 | 21.5 | 5.7 | 6C7722FCB6834580BE0323248549EAAD |  | R22 | Non-TXV |  | 5.862% | 0.94138 | 11.27% | [5 empty] | Non-TXV | 5.862%
Fresno | CA | 93727-9318 |  | 2012-05-07 | 2012-05-07 12:09 | 2012-05-07 12:09 | ICP - PGF036K060B | 71 | 0 | Yes | Yes | 20.2 | 20.4 | -0.2 | 1DD2BF1D4C624B4C8BE08447CBD931EF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-5608 |  | 2012-08-14 | 2012-08-14 08:46 | 2012-08-14 09:15 | GOODMAN - CKJ60-1C | 149 | 4.4 | Yes | Yes | 21.6 | 18.2 | 3.4 | C3F6F9F3EC5D4D06ADA0EBA6233118CE |  | R22 | Non-TXV |  | 2.953% | 0.97047 | 5.675% | [5 empty] | Non-TXV | 2.953%
Chico | CA | 95928-5777 |  | 2012-05-08 | 2012-05-08 12:27 | 2012-05-08 12:44 | OTHER - UNK | 85 | 8.8 | Yes | Yes | 21 | 22.4 | -1.4 | 0E7877A42CAE480AA484CA05B61E938C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10.35% | 0.89647 | 19.9% | [5 empty] | Non-TXV | 10.35%
Stockton | CA | 95205-2572 |  | 2012-05-14 | 2012-05-14 15:30 | 2012-05-14 15:30 | CARRIER - 38EZG036310 | 99 | 0 | Yes | Yes | 17.6 | 20.4 | -2.8 | 40F7293995B94226912448189CB4717A | OK: Verified Refrigerant Charge | R410A | TXV |  | 0% | 1 | 0%
Williams | CA | 95987-0000 |  | 2012-08-06 | 2012-08-06 14:03 | 2012-08-06 14:03 | GOODMAN - CJ24-1AB | 101 | 0 | Yes | Yes | 24.4 | 18.8 | 5.6 | 029C5EAB1A6E4110B39D2D4E9E0E5AC0 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3166 |  | 2012-08-07 | 2012-08-07 10:32 | 2012-08-07 10:52 | YORK - H1CF036S06A | 132 | 4.8 | Yes | Yes | 19.6 | 20.9 | -1.3 | ED81C9CA5FC348AE85EEC6E2140E7C20 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Stockton | CA | 95210-4265 |  | 2012-08-16 | 2012-08-16 11:33 | 2012-08-16 11:51 | DAY & NIGHT - 38TH030310 | 67 | 9.8 | Yes | Yes | 21.3 | 20.6 | 0.7 | D831EFD09FC0486AB2EE43D03487D101 |  | R22 | Non-TXV |  | 14.63% | 0.85373 | 28.11% | [5 empty] | Non-TXV | 14.63%
Grass Valley | CA | 95945-7855 |  | 2012-05-08 | 2012-05-08 17:31 | 2012-05-08 17:31 | PAYNE - PA10JA024-C | 85 | 0 | Yes | Yes | 25.4 | 20.1 | 5.3 | F011429917AF494E9A53664B3C2EE9C7 | OK: Verified Refrigerant Charge | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-5117 |  | 2012-08-02 | 2012-08-02 13:21 | 2012-08-02 13:39 | RHEEM - RAFD-030JAS | 69 | 2 | Yes | Yes | 26.5 | 21.4 | 5.2 | 8A878720D7E24C33999D1F29728FE4AB |  | R22 | Non-TXV |  | 2.899% | 0.97101 | 5.57% | [5 empty] | Non-TXV | 2.899%
Stockton | CA | 95206-2887 |  | 2012-05-10 | 2012-05-10 11:09 | 2012-05-10 11:28 | DAY NIGHT - 561CJ030-A | 77 | 12 | Yes | Yes | 19.1 | 22.1 | -3 | 4DE90FA198B04F36901A57E69EE79E7A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 15.58% | 0.84416 | 29.95% | [5 empty] | Non-TXV | 15.58%
Stockton | CA | 95212-3130 |  | 2012-08-08 | 2012-08-08 15:10 | 2012-08-08 15:28 | YORK - H2RA036S06E | 63 | 3.3 | Yes | Yes | 22.7 | 21.5 | 1.2 | 26024047E8A441BB8424727C1E42E43A |  | R22 | Non-TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | Non-TXV | 5.238%
Paradise | CA | 95969-4418 |  | 2012-05-09 | 2012-05-09 12:55 | 2012-05-09 12:55 | CARRIER - 48GS-024060301 | 59 | 0 | Yes | Yes | 22 | 22 | 0 | CDB817D5C62742A3852575374E8E110F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-3517 |  | 2012-05-18 | 2012-05-18 14:44 | 2012-05-18 15:01 | AMANA - PGB36C0902E | 64 | 1.9 | Yes | Yes | 27.1 | 21.3 | 5.9 | C6A18F20533142D68D9BAF3B516D39F7 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Stockton | CA | 95206-1876 |  | 2012-05-07 | 2012-05-07 17:54 | 2012-05-07 18:15 | RHEEM - UNK | 67 | 13.1 | Yes | Yes | 21.3 | 22.7 | -1.4 | 6A2286C352D04609BF10E7CDA0A61653 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 19.55% | 0.80448 | 37.58% | [5 empty] | Non-TXV | 19.55%
Gustine | CA | 95322-9603 |  | 2012-08-13 | 2012-08-13 13:41 | 2012-08-13 13:41 | CARRIER - 38BE036300 | 117 | 13.4 | Yes | Yes | 25.4 | 19.5 | 5.9 | F210CC84619D42FA91E1A23CC729DB44 | Add refrigerant: 13.4 oz Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 11.45% | 0.88547 | 22.01% | [5 empty] | Non-TXV | 11.45%
Tracy | CA | 95377-8543 |  | 2012-08-14 | 2012-08-14 09:56 | 2012-08-14 09:56 | BRYANT - 561CJ048-F | 98 | 0 | Yes | Yes | 21.1 | 19.9 | 1.2 | 832D923ABFA548198B593A51A4E414DC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95377-8543 |  | 2012-08-14 | 2012-08-14 10:07 | 2012-08-14 10:26 | BRYANT - 561CJ036-F | 74 | -4.4 | Yes | Yes | 24.7 | 20.1 | 4.6 | 86DF3C25E1F541509B825824147F3524 |  | R22 | Non-TXV |  | -5.946% | 1.0595 | 1.665% |  |  |  |  | Non-TXV |  |  | -5.946%
Chico | CA | 95926-2907 |  | 2012-05-07 | 2012-05-07 20:53 | 2012-05-07 21:19 | UTILITY APPLIANCE CORP - M-C-3000 | 45 | 1.3 | Yes | Yes | 19.5 | 22 | -2.5 | 851A67FC59CF4143B7E2C46A92BC024D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Fresno | CA | 93727-7848 |  | 2012-05-07 | 2012-05-07 14:48 | 2012-05-07 14:48 | COLEMAN - BRCQ0481BDG | 103 | 0 | Yes | Yes | 21.5 | 19 | 2.5 | 4B99D5DEA14D492ABA1E1079863A02A6 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-0851 |  | 2012-06-11 | 2012-06-11 14:22 | 2012-06-11 15:19 | CARRIER - UNK | 70 | 4.6 | Yes | Yes | 17.1 | 19.9 | -2.8 | 86A982CA39E14C2886B716D0FAB0687F |  | R22 | Non-TXV |  | 6.571% | 0.93429 | 12.63% | [5 empty] | Non-TXV | 6.571%
Manteca | CA | 95336-3040 |  | 2012-08-15 | 2012-08-15 15:53 | 2012-08-15 16:29 | PAYNE - 567C048RCU | 76 | 20.4 | Yes | Yes | 15.4 | 17.6 | -2.2 | 0C6D84F9B99C4FCE97FF1DD687FE5567 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 26.84% | 0.73158 | 51.58% | [5 empty] | Non-TXV | 26.84%
Los Banos | CA | 93635-6336 |  | 2012-08-09 | 2012-08-09 10:50 | 2012-08-09 11:18 | BRYANT - 561CJ048A | 102 | 12 | Yes | Yes | 24.6 | 20.4 | 4.2 | 14FB0AED248A49668BB7EA89578295ED |  | R22 | Non-TXV |  | 11.76% | 0.88235 | 22.61% | [5 empty] | Non-TXV | 11.76%
Tracy | CA | 95377-8417 |  | 2012-08-14 | 2012-08-14 12:23 | 2012-08-14 12:42 | CARRIER - 38CKC060370 | 133 | 3.9 | Yes | Yes | 24.8 | 21 | 3.8 | 78B71B4F5CC2406CA1BF853564FE7065 |  | R22 | Non-TXV |  | 2.932% | 0.97068 | 5.635% | [5 empty] | Non-TXV | 2.932%
Manteca | CA | 95336-2928 |  | 2012-08-06 | 2012-08-06 11:57 | 2012-08-06 12:18 | PAYNE - PA10JA036-C | 73 | 2.2 | Yes | Yes | 20.2 | 19.3 | 0.9 | 9737318F6D664710941D413A70E94B6E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.014% | 0.96986 | 5.792% | [5 empty] | Non-TXV | 3.014%
Manteca | CA | 95336-3547 |  | 2012-06-22 | 2012-06-22 13:20 | 2012-06-22 14:03 | GUARDIAN - GCGD30S41S3A | 62 | 1.9 | Yes | Yes | 20 | 21 | -1 | 29776F51B7DD4F6B95A45406FF2EF85B |  | R410A | Non-TXV |  | 3.065% | 0.96935 | 5.889% | [5 empty] | Non-TXV | 3.065%
Livingston | CA | 95334-1642 |  | 2012-05-08 | 2012-05-08 14:57 | 2012-05-08 15:14 | CARRIER - 38CK030-331 | 85 | 6.5 | Yes | Yes | 22.7 | 22.1 | 0.6 | B849B9ACECDC4E6E8141BE04A7274CEE | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Stockton | CA | 95212-3816 |  | 2012-08-07 | 2012-08-07 14:28 | 2012-08-07 14:45 | GOODMAN - CKL30-1L | 74 | 3.7 | Yes | Yes | 17.2 | 17.8 | -0.5 | 68B604AC080843399732F9C6754BDC1C |  | R22 | TXV |  | 5% | 0.95 | 9.609% | [5 empty] | TXV | 5%
Los Banos | CA | 93635-2643 |  | 2012-08-15 | 2012-08-15 10:14 | 2012-08-15 10:42 | GOODMAN - CK24-18 | 70 | 3.5 | Yes | Yes | 18.4 | 19.8 | -1.4 | CAE5759966BA478C98B5FCDA948E4153 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Yuba City | CA | 95991-1226 |  | 2012-06-11 | 2012-06-11 11:14 | 2012-06-11 11:14 | DAY & NIGHT - UNK DATA PLATE PAINTED | 68 | 0 | Yes | Yes | 20.7 | 19.9 | 0.8 | 5D32626ECC9A4A2CA81CCDB2564C4C2B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-4343 |  | 2012-06-11 | 2012-06-11 13:08 | 2012-06-11 13:34 | OTHER - 113ANA042-C | 85 | 0.6 | Yes | Yes | 18 | 20.4 | -2.4 | 7E125A1F9ACA4A78BD09A91DED0B9D15 |  | R410A | TXV |  | 0.7059% | 0.99294 | 1.357% | [5 empty] | TXV | 0.7059%
Yuba City | CA | 95993-5234 |  | 2012-05-17 | 2012-05-17 12:04 | 2012-05-17 12:04 | DAY NITE - UNK | 70 | 0 | Yes | Yes | 0 | 18.8 | -18.8 | DF58D61AB24A4D5D8AB260DB3362447A | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8249 |  | 2012-05-09 | 2012-05-09 12:43 | 2012-05-09 12:43 | GOODMAN - CJ30-1FB | 110 | 0 | Yes | Yes | 21.2 | 19.9 | 1.3 | 317994E93A7944698C7D96372B695E8F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3520 |  | 2012-08-13 | 2012-08-13 11:03 | 2012-08-13 11:19 | BRYANT - 38CKC048360 | 109 | -10.3 | Yes | Yes | 17.9 | 19.3 | -1.4 | 619800C939B94E80B85A8DD4E9F3E263 |  | R22 | Non-TXV |  | -9.45% | 1.0945 | 2.646% |  |  |  |  | Non-TXV |  |  | -9.45%
Atwater | CA | 95301-2256 |  | 2012-08-07 | 2012-08-07 10:30 | 2012-08-07 10:47 | DAY & NIGHT - 561CJ030-B | 69 | -2.5 | Yes | Yes | 20 | 20.4 | -0.4 | 9410D26E4D3D446E99AFA9BDAA094B4D |  | R22 | TXV |  | -3.623% | 1.0362 | 1.015% |  |  |  |  | TXV |  |  | -3.623%
Tracy | CA | 95377-8727 |  | 2012-08-14 | 2012-08-14 09:23 | 2012-08-14 09:40 | CARRIER - 38CKC048360 | 98 | 2.9 | Yes | Yes | 24.8 | 20.3 | 4.6 | AEFC9343956D40F6A87B3A4A3970AB2E |  | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.687% | [5 empty] | Non-TXV | 2.959%
Yuba City | CA | 95993-5108 |  | 2012-06-08 | 2012-06-08 14:34 | 2012-06-08 14:57 | DAY & NIGHT - 565AJ024 | 70 | 4 | Yes | Yes | 20 | 19.3 | 0.7 | 0DCD5647E8FE46FCBB6C93AFBDA8F3DF |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Yuba City | CA | 95993-1443 |  | 2012-06-15 | 2012-06-15 20:06 | 2012-06-15 20:24 | LENNOX - 13ACC-036-0230-01 | 114 | 6 | Yes | Yes | 21.3 | 20.9 | 0.4 | 58FC31CC95D84FDF9A626D18B3D69478 |  | R22 | Non-TXV |  | 5.263% | 0.94737 | 10.11% | [5 empty] | Non-TXV | 5.263%
Tracy | CA | 95376-4116 |  | 2012-08-08 | 2012-08-08 10:19 | 2012-08-08 10:43 | BRYANT - 561CJ036-E | 70 | 3 | Yes | Yes | 23.8 | 20.4 | 3.4 | 31BF4F3D513D4723A5C03956D3E4B13C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Stockton | CA | 95209-1764 |  | 2012-05-18 | 2012-05-18 12:38 | 2012-05-18 12:58 | DAYNIGHT - 569CJ036 | 102 | -7.2 | Yes | Yes | 19.6 | 22.4 | -2.8 | 8642D3D903D7470795E487E4AA5B02FB |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Yuba City | CA | 95993-8301 |  | 2012-08-16 | 2012-08-16 09:58 | 2012-08-16 10:33 | LENNOX - HS26-651-1P | 168 | -9.3 | Yes | Yes | 22 | 20.1 | 1.9 | 2D52E3089F74437AB2DC0FC40B5A7F0D |  | R22 | TXV |  | -5.536% | 1.0554 | 1.55% |  |  |  |  | TXV |  |  | -5.536%
Stockton | CA | 95207-2716 |  | 2012-08-03 | 2012-08-03 13:59 | 2012-08-03 14:16 | AMANA - ARCF24VOID | 64 | 5.3 | Yes | Yes | 17 | 19.2 | -2.2 | F055034FAB314D72BDFA94CD3AD43685 |  | R22 | Non-TXV |  | 8.281% | 0.91719 | 15.91% | [5 empty] | Non-TXV | 8.281%
Stockton | CA | 95206-6047 |  | 2012-07-18 | 2012-07-18 10:39 | 2012-07-18 11:02 | GOODMAN - GSC130301DB | 87 | 11.9 | Yes | Yes | 14.4 | 16.6 | -2.2 | 37C39C2204DB427F80371F4E8CCB5023 |  | R22 | Non-TXV |  | 13.68% | 0.86322 | 26.29% | [5 empty] | Non-TXV | 13.68%
Tracy | CA | 95304-7561 |  | 2012-08-15 | 2012-08-15 09:48 | 2012-08-15 10:06 | YORK - BRCQ0481BD | 103 | 3.1 | Yes | Yes | 24.9 | 19.3 | 5.6 | C1ACB54E2AEB4CD38EBDD7D89AC0D5BD |  | R22 | Non-TXV |  | 3.01% | 0.9699 | 5.784% | [5 empty] | Non-TXV | 3.01%
Paradise | CA | 95969-3279 |  | 2012-08-09 | 2012-08-09 14:40 | 2012-08-09 18:24 | TEMPSTAR - PGAA30C1K3 | 75 | 8.9 | Yes | Yes | 19.8 | 21.8 | -2 | 2F6C0D29F6CC49578344475DF2682ACA |  | R22 | Non-TXV |  | 11.87% | 0.88133 | 22.81% | [5 empty] | Non-TXV | 11.87%
Yuba City | CA | 95993-8983 |  | 2012-05-09 | 2012-05-09 11:41 | 2012-05-09 11:59 | NORDYNE - JS3BC-042KA | 102 | 10.7 | Yes | Yes | 16.6 | 18.9 | -2.3 | 114B9A29505C4CCF87DD7930BEF3B24E | OK: Verified Refrigerant Charge | R22 | TXV |  | 10.49% | 0.8951 | 20.16% | [5 empty] | TXV | 10.49%
Chico | CA | 95928-5942 |  | 2012-05-22 | 2012-05-22 10:30 | 2012-05-22 10:54 | TRAIN - YCC024F1LOBH | 65 | 3.8 | Yes | Yes | 21.1 | 19.8 | 1.3 | DFDD86783C174B7C9477D2DB790E3854 |  | R22 | Non-TXV |  | 5.846% | 0.94154 | 11.24% | [5 empty] | Non-TXV | 5.846%
Stockton | CA | 95212-3497 |  | 2012-05-29 | 2012-05-29 10:40 | 2012-05-29 11:01 | CARRIER - 38CKC048370 | 99 | -5.2 | Yes | Yes | 25.6 | 20.2 | 5.5 | 0AC7AFB80C2944C7B1C4663A44B5243B |  | R22 | TXV |  | -5.253% | 1.0525 | 1.471% |  |  |  |  | TXV |  |  | -5.253%
Stockton | CA | 95205-3113 |  | 2012-05-29 | 2012-05-29 15:14 | 2012-05-29 15:31 | RHEEM - UNK | 64 | 3.9 | Yes | Yes | 17.7 | 20.4 | -2.7 | 34F2DBC4236943F8B6D68B9449A39731 |  | R22 | Non-TXV |  | 6.094% | 0.93906 | 11.71% | [5 empty] | Non-TXV | 6.094%
Fresno | CA | 93722-5804 |  | 2012-06-06 | 2012-06-06 16:23 | 2012-06-06 17:06 | ICP - N2A324AKA200 | 70 | 10.5 | Yes | Yes | 24.4 | 18.7 | 5.8 | 8518E6404E254B779B5F446D3EB6EA0C |  | R22 | TXV |  | 15% | 0.85 | 28.83% | [5 empty] | TXV | 15%
Fresno | CA | 93726-2908 |  | 2012-05-09 | 2012-05-09 11:56 | 2012-05-09 12:17 | GEMERAL ELECTRIC - TA036H1D | 85 | 2.6 | Yes | Yes | 16.1 | 15.3 | 0.8 | 1774E41A82544483AC31D179E70F1980 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Paradise | CA | 95969-5646 |  | 2012-08-15 | 2012-08-15 15:06 | 2012-08-15 15:06 | OTHER - BRCO50421BD | 84 | 0 | Yes | Yes | 21.7 | 21.3 | 0.5 | 4F2DA90C23FA4B47B87A1F5BAFBC829A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-6819 |  | 2012-08-10 | 2012-08-10 11:43 | 2012-08-10 12:20 | LENNOX - GCS20R-411-100-2P | 70 | 9.8 | Yes | Yes | 21.5 | 18 | 3.5 | 4CB8A5031EAE43B7925184326D163549 |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Paradise | CA | 95969-2303 |  | 2012-08-09 | 2012-08-09 13:34 | 2012-08-09 13:52 | CARRIER - 48SS-03608031 | 67 | 5.3 | Yes | Yes | 19.5 | 21.1 | -1.6 | 5E8555F706FE4AD88A185D78BFF1E1BA |  | R22 | Non-TXV |  | 7.91% | 0.9209 | 15.2% | [5 empty] | Non-TXV | 7.91%
Stockton | CA | 95210-3478 |  | 2012-05-31 | 2012-05-31 14:06 | 2012-05-31 14:24 | BDP - 569BJ030 | 79 | 2.7 | Yes | Yes | 19.9 | 19.1 | 0.8 | F5AAA097DAD14CBA9B4707AB89E9B055 |  | R22 | Non-TXV |  | 3.418% | 0.96582 | 6.568% | [5 empty] | Non-TXV | 3.418%
Chico | CA | 95973-9734 |  | 2012-05-07 | 2012-05-07 19:45 | 2012-05-07 20:05 | AMANA - PHB36C02E1 | 83 | 4.2 | Yes | Yes | 17.5 | 19.3 | -1.8 | 3F147BBF75CF4FDFA9A78E759C0E1065 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.06% | 0.9494 | 9.725% | [5 empty] | Non-TXV | 5.06%
Atascadero | CA | 93422-5575 |  | 2012-07-10 | 2012-07-10 15:24 | 2012-07-10 15:42 | YORK - H1RA024S06A | 59 | 1.9 | Yes | Yes | 20.3 | 20.2 | 0.1 | DA574FB028CC4C49A34EAF53809EB3CE |  | R22 | Non-TXV |  | 3.22% | 0.9678 | 6.189% | [5 empty] | Non-TXV | 3.22%
Stockton | CA | 95210-1246 |  | 2012-05-07 | 2012-05-07 13:10 | 2012-05-07 13:28 | LENNOX - GCS29-024-50-2PA | 52 | 2 | Yes | Yes | 23.5 | 22 | 1.5 | 1B8E6511012C4879A131179BAFF7FC9F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Murphys | CA | 95247-9501 |  | 2012-07-17 | 2012-07-17 09:36 | 2012-07-17 09:52 | CARRIER - 48SS-042100331 | 83 | -5.9 | Yes | Yes | 20.5 | 18.7 | 1.8 | 65654D44DA6F4AE6B6409F5ACE074DC4 |  | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Stockton | CA | 95207-3920 |  | 2012-06-07 | 2012-06-07 14:50 | 2012-06-07 15:09 | OTHER - 35AW24106 | 69 | 5.2 | Yes | Yes | 21.6 | 20.8 | 0.8 | 664784DAD13141BAA776D51B3CFE8451 |  | R22 | Non-TXV |  | 7.536% | 0.92464 | 14.48% | [5 empty] | Non-TXV | 7.536%
Stockton | CA | 95210-3223 |  | 2012-08-13 | 2012-08-13 13:12 | 2012-08-13 13:12 | GE - BTB936A10002 | 83 | 0 | Yes | Yes | 18.3 | 20.2 | -1.9 | B74D96C05AC547B2903D5EABBDA4E212 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-3342 |  | 2012-08-03 | 2012-08-03 12:17 | 2012-08-03 12:34 | RUUD - 13AJN36A01 | 90 | 2.7 | Yes | Yes | 19 | 19.9 | -0.9 | 433CFC1096A94897B3E8EBECE4F694F7 |  | R410A | TXV |  | 3% | 0.97 | 5.765% | [5 empty] | TXV | 3%
Newman | CA | 95360-2711 |  | 2012-08-14 | 2012-08-14 08:17 | 2012-08-14 08:39 | GOODMAN - UNK | 100 | 15.9 | Yes | Yes | 17.1 | 19.1 | -2 | FF09338AD5E84454B5670848282FB11A |  | R22 | Non-TXV |  | 15.9% | 0.841 | 30.56% | [5 empty] | Non-TXV | 15.9%
Merced | CA | 95340-1529 |  | 2012-05-07 | 2012-05-07 19:07 | 2012-05-07 19:07 | FRASER JOHNSTONE - 100WB42D1NF | 90 | 0 | Yes | Yes | 15.7 | 24.7 | -9 | A3ACFA1E754C4FD38DBD8829C2C57EA7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-1335 |  | 2012-06-06 | 2012-06-06 10:55 | 2012-06-06 11:13 | AMANA - PGB36B07O2A | 118 | 6 | Yes | Yes | 26.4 | 20.4 | 6 | AACC1C930F3D4EEC9DF4C7F86FC1A8BA |  | R22 | Non-TXV |  | 5.085% | 0.94915 | 9.772% | [5 empty] | Non-TXV | 5.085%
Stockton | CA | 95210-3219 |  | 2012-08-06 | 2012-08-06 08:14 | 2012-08-06 08:35 | GE - BTB930A100A3 | 53 | -3.1 | Yes | Yes | 23.5 | 18.7 | 4.8 | A66D72CDB5FA48069D8ED27EE460B8F8 |  | R22 | Non-TXV |  | -5.849% | 1.0585 | 1.638% |  |  |  |  | Non-TXV |  |  | -5.849%
Yuba City | CA | 95993-5194 |  | 2012-08-16 | 2012-08-16 11:21 | 2012-08-16 11:42 | LENNOX - 13ACC-060-230-01 | 168 | 5.4 | Yes | Yes | 21.2 | 19.8 | 1.4 | B0DA9AC2598A4C6990D7933E38C111CF |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Lathrop | CA | 95330-9593 |  | 2012-05-31 | 2012-05-31 12:08 | 2012-05-31 12:41 | GOODMAN - GPG13300701AB | 77 | 2.7 | Yes | Yes | 19.4 | 19.7 | -0.3 | 09C66E4E18414F098C59A11EEE6DB142 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.506% | 0.96494 | 6.739% | [5 empty] | Non-TXV | 3.506%
Yuba City | CA | 95993-9710 |  | 2012-08-16 | 2012-08-16 13:31 | 2012-08-16 13:52 | YORK - H4DE048S06A | 111 | 9.8 | Yes | Yes | 18 | 20.2 | -2.2 | 78E10DB1BD964B6385957F49751B2D38 |  | R22 | Non-TXV |  | 8.829% | 0.91171 | 16.97% | [5 empty] | Non-TXV | 8.829%
Yuba City | CA | 95993-9710 |  | 2012-08-16 | 2012-08-16 13:57 | 2012-08-16 14:15 | TRANE - 2TTB2024A1000AA | 80 | 8 | Yes | Yes | 21 | 19.6 | 1.4 | 990E82B65AB04113B999D3E2F7007D33 |  | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Stockton | CA | 95206-1407 |  | 2012-08-16 | 2012-08-16 10:16 | 2012-08-16 10:55 | LENNOX - HS26-411 | 144 | 4.6 | Yes | Yes | 21.1 | 19.7 | 1.4 | 17F286C6A1B0489B93B68F117EF8A694 |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Magalia | CA | 95954-9560 |  | 2012-08-13 | 2012-08-13 11:23 | 2012-08-13 12:30 | COLEMAN - 3236-901 | 102 | 6.4 | Yes | Yes | 21.6 | 19.3 | 2.3 | DD8BAC01976B4409B55A123F92A8541F |  | R22 | Non-TXV |  | 6.275% | 0.93725 | 12.06% | [5 empty] | Non-TXV | 6.275%
Chico | CA | 95973-0370 |  | 2012-08-09 | 2012-08-09 11:03 | 2012-08-09 11:24 | COLEMAN - UNK | 54 | 8.3 | Yes | Yes | 22.7 | 21.2 | 1.5 | 9A419ED7E9E94C19BCDE9015D61B0EF9 |  | R22 | Non-TXV |  | 15.37% | 0.8463 | 29.54% | [5 empty] | Non-TXV | 15.37%
Live Oak | CA | 95953-2826 |  | 2012-08-13 | 2012-08-13 11:22 | 2012-08-13 11:22 | CARRIER - 24ABA348A300 | 127 | 0 | Yes | Yes | 23.4 | 19.4 | 4.1 | 620554F583614B03974871050D1C0590 |  | R410A | TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-8318 |  | 2012-07-26 | 2012-07-26 10:28 | 2012-07-26 10:48 | LENNOX - 10ACB42-12P | 87 | -4 | Yes | Yes | 17.5 | 19.6 | -2.1 | 0881BBBB14B04F43830EDCCBE992FB07 |  | R22 | TXV |  | -4.598% | 1.046 | 1.288% |  |  |  |  | TXV |  |  | -4.598%
Merced | CA | 95341-9045 |  | 2012-08-14 | 2012-08-14 10:02 | 2012-08-14 10:55 | PAYNE - PY1PNB042090AAAA | 100 | 5.8 | Yes | Yes | 25.4 | 21 | 4.4 | 23D4A65FC8FF435B89D77C5272A42DB6 |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Sanger | CA | 93657-8712 |  | 2012-05-22 | 2012-05-22 12:21 | 2012-05-22 12:40 | OTHER - 55AW24106 | 69 | 2.1 | Yes | Yes | 18.5 | 19.8 | -1.3 | 0A95BB9CCB854A87808F7111CFB0D1C2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Madera | CA | 93638-0101 |  | 2012-06-11 | 2012-06-11 10:23 | 2012-06-11 10:40 | RUUD - UNK | 85 | 3.7 | Yes | Yes | 15.5 | 18.2 | -2.7 | F2B52C47370D491B93CF1EA1D67D30C5 |  | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Oroville | CA | 95966-5217 |  | 2012-06-06 | 2012-06-06 09:09 | 2012-06-06 09:35 | BRYANT - 588ANW0300B0ACBD | 80 | 4.3 | Yes | Yes | 19.5 | 19.5 | 0.1 | FEB8710F6AFB4A8FBC9B57328D6EAF8F |  | R22 | Non-TXV |  | 5.375% | 0.94625 | 10.33% | [5 empty] | Non-TXV | 5.375%
Chico | CA | 95926-3194 |  | 2012-05-22 | 2012-05-22 10:11 | 2012-05-22 10:11 | TEMPSTAR - N4A348AKB200 | 113 | 0 | Yes | Yes | 21.5 | 19.8 | 1.7 | 0F9268D0D23A42F7A774E2D4334069D2 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Cameron Park | CA | 95682-8948 |  | 2012-05-31 | 2012-05-31 10:49 | 2012-05-31 10:49 | BDP - 541DJ018 | 83 | 0 | Yes | Yes | 17.1 | 18.5 | -1.4 | 9609B981F00E40E58319A6A5E97C2DEF |  | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-3525 |  | 2012-05-29 | 2012-05-29 13:20 | 2012-05-29 13:41 | CARRIER - 38EN018310 | 59 | 1.9 | Yes | Yes | 22.2 | 20.1 | 2.1 | 0E0C45654310411FB286C02076137035 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.22% | 0.9678 | 6.189% | [5 empty] | Non-TXV | 3.22%
Stockton | CA | 95203-1537 |  | 2012-08-13 | 2012-08-13 10:10 | 2012-08-13 10:36 | RHEEM - RAKA-042JAZ | 79 | 4.2 | Yes | Yes | 20.5 | 20.9 | -0.4 | B2862C8DF68549A0901C2D532C2351BE |  | R22 | Non-TXV |  | 5.316% | 0.94684 | 10.22% | [5 empty] | Non-TXV | 5.316%
Los Banos | CA | 93635-2995 |  | 2012-08-07 | 2012-08-07 09:34 | 2012-08-07 10:00 | GOODMAN - CK301T | 76 | 3.6 | Yes | Yes | 21.4 | 20.2 | 1.2 | A3F1C49647B143198D1E54E8CA76B8AD |  | R22 | Non-TXV |  | 4.737% | 0.95263 | 9.103% | [5 empty] | Non-TXV | 4.737%
Lincoln | CA | 95648-8226 |  | 2012-08-15 | 2012-08-15 10:24 | 2012-08-15 10:24 | YORK - H2RA030S06D | 62 | 0 | Yes | Yes | 20 | 21.5 | -1.5 | 102F31C366C5470FBF929BD2EEABCA74 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95219-7245 |  | 2012-06-19 | 2012-06-19 12:59 | 2012-06-19 13:19 | LENNOX - 13ACC-042-230-02 | 123 | 6.1 | Yes | Yes | 19.9 | 19.9 | 0 | 9919F9DC998348D1BB63D48A6CE9BC83 |  | R22 | Non-TXV |  | 4.959% | 0.95041 | 9.531% | [5 empty] | Non-TXV | 4.959%
Stockton | CA | 95210-5329 |  | 2012-05-29 | 2012-05-29 11:52 | 2012-05-29 12:11 | BDP - 561CJ030-C | 76 | -4.5 | Yes | Yes | 18.8 | 19.9 | -1.1 | 0409E49D20914417AACF751A067BC4C0 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Manteca | CA | 95337-6687 |  | 2012-08-10 | 2012-08-10 10:48 | 2012-08-10 11:13 | RHEEM - RAMC-036JBZ | 93 | 2.8 | Yes | Yes | 19.4 | 19.9 | -0.5 | 9EE9CCE3CB2E41E7A93F3413388EE9F2 |  | R22 | Non-TXV |  | 3.011% | 0.96989 | 5.786% | [5 empty] | Non-TXV | 3.011%
Paradise | CA | 95969-5313 |  | 2012-05-09 | 2012-05-09 11:43 | 2012-05-09 11:43 | CARRIER - 48KNA030--321BF | 70 | 0 | Yes | Yes | 18.3 | 20.4 | -2.1 | 851F68A03BD24B1484ABE3DB789F1CED | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2562 |  | 2012-08-02 | 2012-08-02 13:43 | 2012-08-02 14:02 | GOODMAN - GPG133600701AB | 112 | 10.3 | Yes | Yes | 16.1 | 17.9 | -1.8 | DBCF6D5EEBFB42A48815B28BD0930F9C |  | R22 | TXV |  | 9.196% | 0.90804 | 17.67% | [5 empty] | TXV | 9.196%
Fresno | CA | 93710-7128 |  | 2012-05-24 | 2012-05-24 12:46 | 2012-05-24 13:08 | NORDYNE - FS3BC-036KA | 82 | 2.5 | Yes | Yes | 24.3 | 21 | 3.3 | C37E404DAE8647558872520ED646F798 |  | R22 | Non-TXV |  | 3.049% | 0.96951 | 5.859% | [5 empty] | Non-TXV | 3.049%
Merced | CA | 95348-1331 |  | 2012-08-03 | 2012-08-03 12:28 | 2012-08-03 13:15 | CARRIER - BRCS0361BD | 62 | 3.3 | Yes | Yes | 20.4 | 18.8 | 1.6 | 4AC9CF99D13C44A58A7B82B4C5AF01D1 |  | R22 | Non-TXV |  | 5.323% | 0.94677 | 10.23% | [5 empty] | Non-TXV | 5.323%
Stockton | CA | 95210-5351 |  | 2012-05-29 | 2012-05-29 10:46 | 2012-05-29 11:03 | BDP - 561CJ030-C | 76 | -4.5 | Yes | Yes | 18.2 | 18.7 | -0.5 | AD1D9176BC48491AB06C7DD021C98927 |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Stockton | CA | 95212-1908 |  | 2012-08-08 | 2012-08-08 16:03 | 2012-08-08 16:39 | RUUD - UAHE-042JAS | 101 | 11.4 | Yes | Yes | 16.3 | 16.9 | -0.6 | ECD2085B230F4ECEA018DAD3FA6A8F02 |  | R22 | Non-TXV |  | 11.29% | 0.88713 | 21.69% | [5 empty] | Non-TXV | 11.29%
Valley Springs | CA | 95252-9365 |  | 2012-08-13 | 2012-08-13 11:43 | 2012-08-13 12:00 | CARRIER - 38EH036300 | 118 | 5 | Yes | Yes | 22.3 | 21.5 | 0.8 | CA136FDCC57F4C6380CDCEC79EDB30D3 |  | R22 | Non-TXV |  | 4.237% | 0.95763 | 8.143% | [5 empty] | Non-TXV | 4.237%
Stockton | CA | 95205-2593 |  | 2012-08-10 | 2012-08-10 16:19 | 2012-08-10 16:37 | CARRIER - UNK | 99 | 4.8 | Yes | Yes | 24.9 | 20.4 | 4.6 | 53BB38ACD9F0425AB9B0A6641B125B06 |  | R410A | TXV |  | 4.848% | 0.95152 | 9.318% | [5 empty] | TXV | 4.848%
Stockton | CA | 95207-3447 |  | 2012-08-07 | 2012-08-07 09:28 | 2012-08-07 09:45 | PAYNE - 591ANX036000AAAA | 85 | 12 | Yes | Yes | 20.3 | 19.7 | 0.6 | C8EAE1554DFC46A9851256C2C25C1909 |  | R22 | Non-TXV |  | 14.12% | 0.85882 | 27.13% | [5 empty] | Non-TXV | 14.12%
Los Banos | CA | 93635-3034 |  | 2012-08-15 | 2012-08-15 09:18 | 2012-08-15 09:18 | OTHER - UNK | 73 | 0 | Yes | Yes | 4 | 19.8 | -15.8 | 821100294F494EB9A5C7F20343D69333 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95337-6748 |  | 2012-08-15 | 2012-08-15 14:49 | 2012-08-15 15:18 | PHILCO - UNK | 104 | 8 | Yes | Yes | 21.2 | 21 | 0.2 | E850BFC1EFD34BBD8ED669FFC45C130E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.692% | 0.92308 | 14.78% | [5 empty] | Non-TXV | 7.692%
Mendota | CA | 93640-2614 |  | 2012-05-31 | 2012-05-31 11:29 | 2012-05-31 11:49 | GOODMAN - GSC130301CA | 106 | 3.1 | Yes | Yes | 23.2 | 21 | 2.2 | BDB771AB01A644E5AA0BB5C9763C8A4D |  | R22 | Non-TXV |  | 2.925% | 0.97075 | 5.62% | [5 empty] | Non-TXV | 2.925%
Stockton | CA | 95210-5361 |  | 2012-05-29 | 2012-05-29 10:08 | 2012-05-29 10:25 | BDP - 561CJ030-C | 76 | -5.4 | Yes | Yes | 22.6 | 18.7 | 3.9 | FCD693AD7E3E4537B86BDB67727E1111 | OK: Verified Refrigerant Charge. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Chowchilla | CA | 93610-9315 |  | 2012-05-08 | 2012-05-08 10:37 | 2012-05-08 10:56 | FRASER N JOHNSTON - 24E3DATA | 55 | -4.5 | Yes | Yes | 17.4 | 14.4 | 3 | BD77B79374194B249D9B37EA6DE9D3CA |  | R22 | Non-TXV |  | -8.182% | 1.0818 | 2.291% |  |  |  |  | Non-TXV |  |  | -8.182%
Chowchilla | CA | 93610-9315 |  | 2012-05-08 | 2012-05-08 11:09 | 2012-05-08 11:25 | FRASER N JOHNSTON - 24E3DATA | 55 | 1.7 | Yes | Yes | 20.2 | 20.4 | -0.2 | 6EE4CAD49B504FFD9E9FB8531BFFEAB8 |  | R22 | Non-TXV |  | 3.091% | 0.96909 | 5.94% | [5 empty] | Non-TXV | 3.091%
Los Banos | CA | 93635-5477 |  | 2012-05-17 | 2012-05-17 12:55 | 2012-05-17 13:25 | YORK - H2RA030S06D | 62 | 9.1 | Yes | Yes | 27 | 24.8 | 2.2 | 3BE88969AE3E490DABD6E836C689FDC2 |  | R22 | Non-TXV |  | 14.68% | 0.85323 | 28.21% | [5 empty] | Non-TXV | 14.68%
Loomis | CA | 95650-8848 |  | 2012-05-11 | 2012-05-11 11:54 | 2012-05-11 12:20 | TRANE - YCX060G1M0AB | 160 | 22.6 | Yes | Yes | 24.2 | 19.5 | 4.7 | 86E3F15C9F5E486E819669F342A21F9E | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.12% | 0.85875 | 27.15% | [5 empty] | Non-TXV | 14.12%
Auburn | CA | 95602-2053 |  | 2012-08-03 | 2012-08-03 10:48 | 2012-08-03 11:13 | BRYANT - 550AN036-E | 110 | 11.1 | Yes | Yes | 19.6 | 20.2 | -0.5 | 0F18E073BB3D4AE58D66FBF342CA9CA2 |  | R410A | TXV |  | 10.09% | 0.89909 | 19.39% | [5 empty] | TXV | 10.09%
Los Banos | CA | 93635-5238 |  | 2012-08-08 | 2012-08-08 17:02 | 2012-08-08 17:21 | BRYANT - 561CJ60-A | 152 | 4.7 | Yes | Yes | 23.3 | 19.7 | 3.6 | 38D1023991334B83AB3384A5F65DB9E5 |  | R22 | Non-TXV |  | 3.092% | 0.96908 | 5.942% | [5 empty] | Non-TXV | 3.092%
Magalia | CA | 95954-9541 |  | 2012-08-08 | 2012-08-08 12:35 | 2012-08-08 12:59 | PAYNE - 542D024HP | 101 | 3 | Yes | Yes | 19 | 20.8 | -1.8 | 234A2486757B455680A74EB36EBD9C21 |  | R22 | Non-TXV |  | 2.97% | 0.9703 | 5.708% | [5 empty] | Non-TXV | 2.97%
Los Banos | CA | 93635-5112 |  | 2012-08-09 | 2012-08-09 10:15 | 2012-08-09 10:38 | NORDYNE - JS3BA042KA | 87 | 10.2 | Yes | Yes | 19.3 | 19.3 | 0 | 257B53F5C6B14650B19F209B3C2C3C5B |  | R22 | Non-TXV |  | 11.72% | 0.88276 | 22.53% | [5 empty] | Non-TXV | 11.72%
Manteca | CA | 95337-4401 |  | 2012-08-09 | 2012-08-09 15:52 | 2012-08-09 16:17 | OTHER - UNK | 56 | 12 | Yes | Yes | 23.7 | 20.4 | 3.3 | 0965EFCE33904DDAA1A40AF2273CBD9F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.43% | 0.78571 | 41.18% | [5 empty] | Non-TXV | 21.43%
Chico | CA | 95973-7816 |  | 2012-08-13 | 2012-08-13 10:02 | 2012-08-13 10:40 | DAY & NIGHT - 541DJ034 | 118 | 11.2 | Yes | Yes | 23 | 21.5 | 1.5 | C2D87D1A23304632BC066F512F7FAA4D |  | R22 | Non-TXV |  | 9.492% | 0.90508 | 18.24% | [5 empty] | Non-TXV | 9.492%
Magalia | CA | 95954-9637 |  | 2012-08-15 | 2012-08-15 09:39 | 2012-08-15 10:02 | DAY & NIGHT - 597ANX042000AAAA | 164 | 9.9 | Yes | Yes | 23.8 | 20.9 | 2.9 | 9535048DE1DD45CA9872B05C68364CC8 |  | R22 | Non-TXV |  | 6.037% | 0.93963 | 11.6% | [5 empty] | Non-TXV | 6.037%
Atwater | CA | 95301-2625 |  | 2012-05-10 | 2012-05-10 12:55 | 2012-05-10 13:13 | RHEEM - HC-80-36-21C | 50 | -3.5 | Yes | Yes | 21.1 | 20.4 | 0.7 | 5366DC73A5BF4D50B442F46551749864 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Atwater | CA | 95301-3513 |  | 2012-08-08 | 2012-08-08 11:05 | 2012-08-08 11:05 | AMANA - APG1336070M41AB | 85 | 0 | Yes | Yes | 17.5 | 18.8 | -1.3 | 45A343F2EDF749629D1A44255D2AE3AA |  | R410A | TXV |  | 0% | 1 | 0%
Rocklin | CA | 95677-4767 |  | 2012-05-22 | 2012-05-22 15:29 | 2012-05-22 15:49 | GOODMAN - CJ30-1FB | 110 | 4.3 | Yes | Yes | 19.4 | 19.3 | 0.1 | 36F951CB529E4BC7BBE61824461704EE | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.909% | 0.96091 | 7.512% | [5 empty] | Non-TXV | 3.909%
Los Banos | CA | 93635-5101 |  | 2012-08-08 | 2012-08-08 12:31 | 2012-08-08 12:53 | DAY & NIGHT - 580AN03606A | 80 | 4 | Yes | Yes | 24.9 | 20.8 | 4.1 | 0728E3C6AC1F4086B7A3FB2AE6AD471E |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Loomis | CA | 95650-8748 |  | 2012-08-03 | 2012-08-03 12:05 | 2012-08-03 12:24 | BDP - 565BJ030 | 72 | 10.8 | Yes | Yes | 22.5 | 20.8 | 1.7 | F815731C8090423ABED8AD9067405A6F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15% | 0.85 | 28.83% | [5 empty] | Non-TXV | 15%
Madera | CA | 93638-0858 |  | 2012-06-12 | 2012-06-12 09:34 | 2012-06-12 09:58 | CARRIER - N/A | 80 | 2.4 | Yes | Yes | 22.7 | 20.4 | 2.3 | D64DA5965ED14AE08B9409DF0792F86B |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95212-3061 |  | 2012-08-03 | 2012-08-03 13:47 | 2012-08-03 14:03 | AMANA - RCE36C2C | 160 | 22.4 | Yes | Yes | 20.5 | 20.4 | 0.1 | 039FEDBE318B42BAA423C551BCF8F43C |  | R22 | Non-TXV |  | 14% | 0.86 | 26.9% | [5 empty] | Non-TXV | 14%
Clovis | CA | 93612-3323 |  | 2012-05-15 | 2012-05-15 14:29 | 2012-05-15 14:29 | ICP - N4A336AKB200 | 83 | 0 | Yes | Yes | 24.5 | 21 | 3.5 | 6F62E859CC2141C49AD713CA48A95C6F |  | R410A | Non-TXV |  | 0% | 1 | 0%
Newman | CA | 95360-9570 |  | 2012-08-14 | 2012-08-14 13:35 | 2012-08-14 13:51 | CARRIER - 38ETG030300 | 133 | 4.9 | Yes | Yes | 20.8 | 19.3 | 1.5 | 9936BCEC1CF64830A9B3D05AB3F41B28 |  | R410A | TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | TXV | 3.684%
Manteca | CA | 95336-4404 |  | 2012-05-18 | 2012-05-18 11:43 | 2012-05-18 12:02 | GOODMAN - CKL30-1D | 70 | 4 | Yes | Yes | 21.7 | 21.9 | -0.2 | 5190F1B3993F413186290C3AF916CBAB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Stockton | CA | 95210-4604 |  | 2012-05-29 | 2012-05-29 15:30 | 2012-05-29 15:53 | CARRIER - 38EB024300 | 53 | 14 | Yes | Yes | 18.2 | 21.2 | -3 | 9B94018432FC41EF8CFBA592AC1A849D |  | R22 | Non-TXV |  | 26.42% | 0.73585 | 50.76% | [5 empty] | Non-TXV | 26.42%
Newman | CA | 95360-1436 |  | 2012-05-17 | 2012-05-17 10:22 | 2012-05-17 10:57 | RUUD - UAFD-036JAS | 80 | 2.4 | Yes | Yes | 22.5 | 19.1 | 3.4 | 02B098C7C6294FCF96F961A77CF3DCC2 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Chico | CA | 95973-8209 |  | 2012-05-07 | 2012-05-07 14:36 | 2012-05-07 15:06 | LENNOX - 13ACC-030-230-01 | 106 | 6 | Yes | Yes | 21.2 | 19.3 | 1.9 | D69A1C09704F464B826A27E355B29460 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.66% | 0.9434 | 10.88% | [5 empty] | Non-TXV | 5.66%
Red Bluff | CA | 96080-4023 |  | 2012-05-29 | 2012-05-29 10:32 | 2012-05-29 10:48 | DAY & NIGHT - 584ANWO481 | 96 | 4.5 | Yes | Yes | 21.4 | 21 | 0.4 | D882362BB9714C0C85EAD96CB7A3BFCF |  | R22 | Non-TXV |  | 4.688% | 0.95312 | 9.008% | [5 empty] | Non-TXV | 4.688%
Orosi | CA | 93647-2101 |  | 2012-08-08 | 2012-08-08 16:21 | 2012-08-08 16:41 | GOODMAN - PGB024030-1 | 54 | 2 | Yes | Yes | 16.2 | 16 | 0.2 | EEB71292456E4AB9854DDD741638D8E8 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Merced | CA | 95340-1536 |  | 2012-05-31 | 2012-05-31 15:29 | 2012-05-31 15:54 | AIRE-FLO - 80WR30G1NA | 84 | 3.8 | Yes | Yes | 22.6 | 21.3 | 1.3 | DB16DF5A52F34E63824772E2105F6D5A |  | R22 | Non-TXV |  | 4.524% | 0.95476 | 8.694% | [5 empty] | Non-TXV | 4.524%
Paradise | CA | 95969-2511 |  | 2012-05-09 | 2012-05-09 10:26 | 2012-05-09 10:52 | BRYANT - 582ANW030060AAAD | 50 | 3.2 | Yes | Yes | 25.4 | 23.7 | 1.7 | EE4DC6F62286427382DA721413C70194 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.4% | 0.936 | 12.3% | [5 empty] | Non-TXV | 6.4%
Olivehurst | CA | 95961-0000 |  | 2012-07-11 | 2012-07-11 12:18 | 2012-07-11 12:40 | TRANE - 2TTR2042B1000AA | 86 | 9.5 | Yes | Yes | 16 | 18.2 | -2.2 | 955979C59BBD4BADB62EBFF76413AF37 |  | R22 | TXV |  | 11.05% | 0.88953 | 21.23% | [5 empty] | TXV | 11.05%
Paradise | CA | 95969-3363 |  | 2012-05-11 | 2012-05-11 11:10 | 2012-05-11 11:10 | COLEMAN - 95300901 | 80 | 0 | Yes | Yes | 20.9 | 22.1 | -1.2 | 883BD6547CFC4F51937E9D0836CAFCE7 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3813 |  | 2012-08-07 | 2012-08-07 12:54 | 2012-08-07 13:23 | DAY & NIGHT - 589ANW042060ADAF | 87 | 10 | Yes | Yes | 24.2 | 20.4 | 3.8 | 8A9C3FAA63644B628875D356159236F6 |  | R22 | Non-TXV |  | 11.49% | 0.88506 | 22.09% | [5 empty] | Non-TXV | 11.49%
Stockton | CA | 95212-2887 |  | 2012-08-03 | 2012-08-03 12:43 | 2012-08-03 13:01 | YORK - H2RC036S06G | 83 | 2.5 | Yes | Yes | 19.4 | 20.4 | -1 | 9E2E6368426146E4AFC5E1EDC97EEF00 |  | R22 | Non-TXV |  | 3.012% | 0.96988 | 5.788% | [5 empty] | Non-TXV | 3.012%
Marysville | CA | 95901-4209 |  | 2012-05-15 | 2012-05-15 13:27 | 2012-05-15 13:46 | CARRIER - 48GX-030040301AD | 85 | 9.6 | Yes | Yes | 27.7 | 22.1 | 5.6 | B93697DE4EE74A2A8B62042F47DD96C1 |  | R22 | Non-TXV |  | 11.29% | 0.88706 | 21.7% | [5 empty] | Non-TXV | 11.29%
Paradise | CA | 95969-3663 |  | 2012-08-07 | 2012-08-07 19:13 | 2012-08-07 19:13 | BRYANT - 561CJ030-E | 70 | 0 | Yes | Yes | 25 | 21.3 | 3.8 | 3D4AA252FEAC4DAB8FAD9BDC4B715D6D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Georgetown | CA | 95634-9644 |  | 2012-07-16 | 2012-07-16 10:32 | 2012-07-16 10:32 | OTHER - FADED | 64 | 0 | Yes | Yes | 21.3 | 19.9 | 1.4 | 8F30AA3E00F64C9381F529FD7FBCF9D0 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7005 |  | 2012-05-10 | 2012-05-10 11:03 | 2012-05-10 11:29 | GOODMAN - PGB042075-1B | 80 | -4.7 | Yes | Yes | 22.3 | 18.6 | 3.7 | CE99EB85851F47668089DBBB6216C729 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Stockton | CA | 95205-4111 |  | 2012-08-09 | 2012-08-09 14:19 | 2012-08-09 14:38 | CARRIER - 38TH042310 | 112 | 9.8 | Yes | Yes | 22.3 | 20.4 | 1.9 | 647777F1B3434789AAA32FF2F413D4B5 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Los Banos | CA | 93635-0000 |  | 2012-08-06 | 2012-08-06 12:23 | 2012-08-06 12:48 | OTHER - JS5BD-030K | 134 | 4.2 | Yes | Yes | 17.1 | 19 | -1.9 | 0C70EED4D5E8475AAC583094FC834CD0 |  | R22 | Non-TXV |  | 3.134% | 0.96866 | 6.023% | [5 empty] | Non-TXV | 3.134%
Fresno | CA | 93710-6435 |  | 2012-05-11 | 2012-05-11 15:20 | 2012-05-11 15:39 | PAYNE - 593BJ036-A | 85 | 2.8 | Yes | Yes | 17.5 | 19.9 | -2.4 | 1DAC6246005A4F6D9E9BFD9AA0D4EF98 |  | R22 | Non-TXV |  | 3.294% | 0.96706 | 6.331% | [5 empty] | Non-TXV | 3.294%
Stockton | CA | 95210-2272 |  | 2012-05-15 | 2012-05-15 11:51 | 2012-05-15 12:10 | CARRIER - 38EB030300 | 84 | 2.8 | Yes | Yes | 20.2 | 20.4 | -0.2 | 3F775AADB74D4CF2ADBC901500D20620 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Marysville | CA | 95901-6541 |  | 2012-08-13 | 2012-08-13 16:43 | 2012-08-13 17:05 | BRYANT - 561CJ036-E | 74 | 7 | Yes | Yes | 20.2 | 18.6 | 1.6 | 99E5B12EE8D442EEB6C2D514D3AB5E47 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.459% | 0.90541 | 18.18% | [5 empty] | Non-TXV | 9.459%
Merced | CA | 95348-1560 |  | 2012-08-09 | 2012-08-09 18:19 | 2012-08-09 18:37 | CARRIER - UNK | 71 | 3 | Yes | Yes | 17 | 17.2 | -0.2 | 74EFC854245A4AA8A21FD439E28950C6 |  | R22 | Non-TXV |  | 4.225% | 0.95775 | 8.12% | [5 empty] | Non-TXV | 4.225%
Stockton | CA | 95206-6116 |  | 2012-05-15 | 2012-05-15 14:20 | 2012-05-15 14:40 | RHEEM - JAMA-048JBZ | 172 | 10.3 | Yes | Yes | 17.8 | 20.6 | -2.8 | 4FFF82979AE24C31B43651C232D32EC7 | OK: Verified Refrigerant Charge | R22 | TXV |  | 5.988% | 0.94012 | 11.51% | [5 empty] | TXV | 5.988%
Wheatland | CA | 95692-9433 |  | 2012-08-15 | 2012-08-15 15:26 | 2012-08-15 15:26 | COLEMAN - UNK FADED | 79 | 0 | Yes | Yes | 21.9 | 20.3 | 1.7 | 652B4D72FE714672A8E61800FE806712 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-4136 |  | 2012-08-08 | 2012-08-08 12:58 | 2012-08-08 13:26 | DAY & NIGHT - 589ANW04808ABAG | 86 | 5 | Yes | Yes | 26.6 | 22.1 | 4.5 | 9FF0280302994935AAE5C472DF065CD1 |  | R22 | Non-TXV |  | 5.814% | 0.94186 | 11.17% | [5 empty] | Non-TXV | 5.814%
Merced | CA | 95340-1427 |  | 2012-08-08 | 2012-08-08 10:57 | 2012-08-08 11:41 | RHEEM - RAPB036JAZ | 160 | 13.2 | Yes | Yes | 20.7 | 22 | -1.3 | E75C1BC96D4C422F8088331AC7BC270D |  | R22 | Non-TXV |  | 8.25% | 0.9175 | 15.85% | [5 empty] | Non-TXV | 8.25%
Stockton | CA | 95210-4631 |  | 2012-05-31 | 2012-05-31 13:34 | 2012-05-31 13:51 | BRYANT - 563CN018-B | 80 | 2.8 | Yes | Yes | 18.1 | 19.8 | -1.7 | 7A54690073C34592AD0B623EB2A52CCA |  | R22 | Non-TXV |  | 3.5% | 0.965 | 6.726% | [5 empty] | Non-TXV | 3.5%
Stockton | CA | 95206-1949 |  | 2012-06-08 | 2012-06-08 13:39 | 2012-06-08 13:57 | RHEEM - RRKA-A030JK06X | 54 | 4.7 | Yes | Yes | 17.3 | 19.9 | -2.6 | 1DF371B850C8407FBCAD3BFEC8DB4961 |  | R22 | Non-TXV |  | 8.704% | 0.91296 | 16.73% | [5 empty] | Non-TXV | 8.704%
Paradise | CA | 95969-3166 |  | 2012-08-08 | 2012-08-08 13:35 | 2012-08-08 16:50 | LENNOX - 10GCS024X-50-3PA | 50 | 1.9 | Yes | Yes | 20.2 | 19.9 | 0.3 | 982570E3B2ED4D3A889901D4BF18BE6E |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Merced | CA | 95348-8712 |  | 2012-08-13 | 2012-08-13 10:35 | 2012-08-13 10:56 | GIBSON - JS3BA-042KA | 86 | 3.5 | Yes | Yes | 20.2 | 19.8 | 0.4 | 68F080B51CD14CD4819F680C623720A9 |  | R22 | Non-TXV |  | 4.07% | 0.9593 | 7.821% | [5 empty] | Non-TXV | 4.07%
Los Banos | CA | 93635-5302 |  | 2012-08-09 | 2012-08-09 09:15 | 2012-08-09 09:33 | PAYNE - PY3GNAA36060NA | 100 | 5.9 | Yes | Yes | 23.8 | 20.4 | 3.4 | 16D3583E2DB947A9B12745B71EF01D02 |  | R410A | Non-TXV |  | 5.9% | 0.941 | 11.34% | [5 empty] | Non-TXV | 5.9%
Wheatland | CA | 95692-9229 |  | 2012-07-24 | 2012-07-24 12:43 | 2012-07-24 12:43 | AMANA - RCB30C2A | 77 | 0 | Yes | Yes | 22.8 | 21 | 1.8 | 02CAF738638447BBBDF8830F7092C21F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Atwater | CA | 95301-4040 |  | 2012-08-15 | 2012-08-15 14:13 | 2012-08-15 14:38 | AMERICAN STANDARD - YCC036F1M0BE | 83 | 4.2 | Yes | Yes | 25.3 | 21.3 | 4 | 831A913415CB4C97BFF69562A219B098 |  | R22 | Non-TXV |  | 5.06% | 0.9494 | 9.725% | [5 empty] | Non-TXV | 5.06%
Dinuba | CA | 93618-9623 |  | 2012-05-08 | 2012-05-08 11:37 | 2012-05-08 12:02 | SNYDER GENERAL - AR 703036 | 70 | 22.4 | Yes | Yes | 14.6 | 18.8 | -4.2 | 7086F3FD98794C9D8A9991AF2216A433 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 32% | 0.68 | 61.5% | [5 empty] | Non-TXV | 32%
Stockton | CA | 95206-3852 |  | 2012-05-23 | 2012-05-23 15:13 | 2012-05-23 15:30 | PAYNE - 585B024050YACR | 51 | 6.2 | Yes | Yes | 20 | 22 | -2 | FEE62C2FAE8B4EFB9E2A96AA51816A12 |  | R22 | Non-TXV |  | 12.16% | 0.87843 | 23.36% | [5 empty] | Non-TXV | 12.16%
Kerman | CA | 93630-9366 |  | 2012-05-17 | 2012-05-17 13:49 | 2012-05-17 14:15 | LENNOX - 13ACC-036-230-01 | 115 | 3.4 | Yes | Yes | 23.8 | 20.4 | 3.4 | 8EE352DFE89B450D843D9659832C1600 |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Newman | CA | 95360-1230 |  | 2012-08-07 | 2012-08-07 10:31 | 2012-08-07 10:49 | YORK - D1NP048N06506A | 133 | 4.8 | Yes | Yes | 20.7 | 19.5 | 1.3 | A9AA30910F044065B220DCC8FBA1B5DB |  | R22 | Non-TXV |  | 3.609% | 0.96391 | 6.936% | [5 empty] | Non-TXV | 3.609%
Chowchilla | CA | 93610-1810 |  | 2012-08-03 | 2012-08-03 14:43 | 2012-08-03 14:43 | AMERICAN STANDARD - TTD748 B 100 A0 | 66 | 0 | Yes | Yes | 19 | 20.1 | -1.1 | 8FA672983FE54CC4BDD314779A05C949 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95209-2192 |  | 2012-06-15 | 2012-06-15 10:17 | 2012-06-15 10:34 | BDP - 585GJ018040 | 55 | -3.2 | Yes | Yes | 16 | 18.7 | -2.7 | DBE3C0A15A6646368EE36670858657AF |  | R22 | Non-TXV |  | -5.818% | 1.0582 | 1.629% |  |  |  |  | Non-TXV |  |  | -5.818%
Manteca | CA | 95337-6004 |  | 2012-06-01 | 2012-06-01 15:46 | 2012-06-01 16:07 | AMERICAN STANDARD - 2A7A2042B1000AA | 86 | 5.8 | Yes | Yes | 26.7 | 21 | 5.7 | E9C1E339D712473EA247A9B9F03FF2C4 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.744% | 0.93256 | 12.96% | [5 empty] | Non-TXV | 6.744%
Chowchilla | CA | 93610-9426 |  | 2012-08-10 | 2012-08-10 14:23 | 2012-08-10 14:46 | CARRIER - 38BR042300 | 131 | 17.6 | Yes | Yes | 25.3 | 20.4 | 4.9 | D1C66EBAA46349748C4CBF59AC1768B9 |  | R22 | Non-TXV |  | 13.44% | 0.86565 | 25.82% | [5 empty] | Non-TXV | 13.44%
Chowchilla | CA | 93610-2037 |  | 2012-08-03 | 2012-08-03 10:56 | 2012-08-03 11:17 | AMERICAN STANDARD - TTD48 B 100 AO | 65 | 2.2 | Yes | Yes | 19.2 | 20.4 | -1.2 | 9AD88C16BF4E469C94BC007BB99FFB73 |  | R22 | Non-TXV |  | 3.385% | 0.96615 | 6.504% | [5 empty] | Non-TXV | 3.385%
Paradise | CA | 95969-4808 |  | 2012-05-10 | 2012-05-10 13:34 | 2012-05-10 19:07 | DAY N NIGHT - PGD342090K001C1 | 99 | 3.5 | Yes | Yes | 30 | 24.5 | 5.6 | A54BCAA7397E4BA19A2FC128540656EA | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 3.535% | 0.96465 | 6.794% | [5 empty] | Non-TXV | 3.535%
Manteca | CA | 95337-6873 |  | 2012-08-10 | 2012-08-10 15:04 | 2012-08-10 15:21 | TRANE - TTN048C100A1 | 151 | 12.3 | Yes | Yes | 24.4 | 20.4 | 4 | 2EEDB451B6454375BF10150505EB5CB3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.146% | 0.91854 | 15.65% | [5 empty] | Non-TXV | 8.146%
Fresno | CA | 93722-7934 |  | 2012-05-16 | 2012-05-16 16:07 | 2012-05-16 16:31 | YORK - H2RC048S06HA | 120 | 3.6 | Yes | Yes | 24 | 19.8 | 4.2 | B34DA4773539482A83B86E2A7B0D7B06 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Newman | CA | 95360-9636 |  | 2012-08-14 | 2012-08-14 11:50 | 2012-08-14 12:14 | BRYANT - 563CN048-H | 136 | -7.4 | Yes | Yes | 18.4 | 18.3 | 0.1 | 267754E3DFE34B86AFD93AA57DBA4B3C |  | R22 | TXV |  | -5.441% | 1.0544 | 1.524% |  |  |  |  | TXV |  |  | -5.441%
Merced | CA | 95348-2709 |  | 2012-07-03 | 2012-07-03 13:55 | 2012-07-03 14:21 | AMANA - PGD48C0902G | 85 | 3.5 | Yes | Yes | 18.7 | 20.8 | -2.1 | CC63F7795E3343CBB2E6FEEE1E9ED962 |  | R22 | Non-TXV |  | 4.118% | 0.95882 | 7.913% | [5 empty] | Non-TXV | 4.118%
Merced | CA | 95348-2202 |  | 2012-08-03 | 2012-08-03 09:21 | 2012-08-03 09:57 | AMERICAN STANDARD - YCP036F1M0AA | 106 | 4.8 | Yes | Yes | 17.8 | 19.6 | -1.8 | E7A850F3B7F44F4B8F8663723660C8B5 |  | R22 | Non-TXV |  | 4.528% | 0.95472 | 8.702% | [5 empty] | Non-TXV | 4.528%
Chico | CA | 95928-6436 |  | 2012-05-30 | 2012-05-30 12:48 | 2012-05-30 13:35 | TRANE - YCC036F1MOBJ | 85 | 6.1 | Yes | Yes | 27 | 22.9 | 4.2 | 4A8F973F943048198B1E956F22B9803F |  | R22 | Non-TXV |  | 7.176% | 0.92824 | 13.79% | [5 empty] | Non-TXV | 7.176%
Stockton | CA | 95209-4017 |  | 2012-08-10 | 2012-08-10 12:51 | 2012-08-10 13:10 | DAY & NIGHT - 567C036RCU | 67 | -6.3 | Yes | Yes | 14.8 | 17.7 | -2.9 | 2770556A731243DD96CBA7C75504B708 |  | R22 | Non-TXV |  | -9.403% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.403%
Atwater | CA | 95301-4449 |  | 2012-05-15 | 2012-05-15 14:00 | 2012-05-15 14:17 | CARRIER - 48GS-036090311 | 68 | 2 | Yes | Yes | 26 | 21.5 | 4.5 | 550F84E18B2B4A62B65156C63D3B921C |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Los Banos | CA | 93635-7405 |  | 2012-08-14 | 2012-08-14 15:12 | 2012-08-14 15:36 | OTHER - JS3BC030KA | 68 | 7.2 | Yes | Yes | 17.5 | 17.5 | 0 | CE4D4CDAFDE94FDDA10AF2BE528F5C17 |  | R22 | Non-TXV |  | 10.59% | 0.89412 | 20.35% | [5 empty] | Non-TXV | 10.59%
Grass Valley | CA | 95949-6415 |  | 2012-05-08 | 2012-05-08 11:42 | 2012-05-08 15:03 | CARRIER - 48NMT042300 | 100 | 5 | Yes | Yes | 23.8 | 20.4 | 3.4 | 47663084EC504F4C813B7A4C299E0E6A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Los Banos | CA | 93635-4819 |  | 2012-08-08 | 2012-08-08 16:41 | 2012-08-08 16:59 | CARRIER - FS3BC-D42KA | 102 | 5.6 | Yes | Yes | 28 | 22 | 6 | 0D68524939FF43218CE1E0FA0E68E941 |  | R22 | Non-TXV |  | 5.49% | 0.9451 | 10.55% | [5 empty] | Non-TXV | 5.49%
Madera | CA | 93638-9330 |  | 2012-06-12 | 2012-06-12 10:30 | 2012-06-12 10:54 | CARRIER - 24ABA330A300 | 69 | 0.7 | Yes | Yes | 19.3 | 21.3 | -2 | 66237C9342A94D119A1097C406EDF443 |  | R410A | TXV |  | 1.014% | 0.98986 | 1.95% | [5 empty] | TXV | 1.014%
Winton | CA | 95388-9389 |  | 2012-05-14 | 2012-05-14 16:27 | 2012-05-14 16:46 | LENNOX - NA | 50 | 1.5 | Yes | Yes | 17 | 19.3 | -2.3 | 1F7E91C4046E49119AFA05AF14854AA9 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Los Banos | CA | 93635-2801 |  | 2012-05-09 | 2012-05-09 11:58 | 2012-05-09 12:19 | BRYANT - 561AJ024-B | 63 | -3.7 | Yes | Yes | 17.1 | 18.1 | -1 | B00F879CF294416A84DBB65DE551B574 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -5.873% | 1.0587 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.873%
Atwater | CA | 95301-2813 |  | 2012-08-15 | 2012-08-15 09:42 | 2012-08-15 10:00 | GOODMAN - PGB036075-1A | 83 | -5.9 | Yes | Yes | 26 | 20.6 | 5.4 | A6B8D2492ADF4CCEA5B668946C893B33 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -7.108% | 1.0711 | 1.991% |  |  |  |  | Non-TXV |  |  | -7.108%
Atwater | CA | 95301-3845 |  | 2012-05-11 | 2012-05-11 15:54 | 2012-05-11 16:15 | BRYANT - 588ANW030060ACAD | 85 | 7.2 | Yes | Yes | 23.9 | 22 | 1.9 | 97FDFC09A12F4CCFBC271DF3142BB69F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Stockton | CA | 95212-3476 |  | 2012-08-16 | 2012-08-16 09:45 | 2012-08-16 09:45 | CARRIER - 38CKC042340 | 80 | 0 | Yes | Yes | 17.2 | 18.5 | -1.3 | E85A9B6DBA27480C91479E71AA82F246 |  | R22 | TXV |  | 0% | 1 | 0%
Newman | CA | 95360-1445 |  | 2012-08-07 | 2012-08-07 14:37 | 2012-08-07 14:55 | YORK - H2RD036S06B | 99 | 3.2 | Yes | Yes | 19.2 | 19 | 0.2 | 083CAE805EE64772829B10621FA0BFFB |  | R22 | Non-TXV |  | 3.232% | 0.96768 | 6.212% | [5 empty] | Non-TXV | 3.232%
Selma | CA | 93662-2148 |  | 2012-05-18 | 2012-05-18 10:25 | 2012-05-18 10:56 | AMERICAN STANSARD - YCC048F1H0BF | 128 | 3.8 | Yes | Yes | 22.4 | 20.4 | 2 | 2A325D5E354A49B2B0CC1D333230D1FD |  | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Madera | CA | 93637-8656 |  | 2012-08-13 | 2012-08-13 11:10 | 2012-08-13 11:38 | AIRE-FLO - 38BRC042340 | 103 | 6.4 | Yes | Yes | 17.8 | 19.8 | -2 | 2901AC364C224058820BAD03B6BC6784 |  | R22 | Non-TXV |  | 6.214% | 0.93786 | 11.94% | [5 empty] | Non-TXV | 6.214%
Madera | CA | 93637-8656 |  | 2012-08-13 | 2012-08-13 11:24 | 2012-08-13 11:50 | AIRE-FLO - 38BRC042340 | 103 | 8.4 | Yes | Yes | 18.4 | 19.3 | -0.9 | F7E0341190C34D1BA1EDEA5AF7B61B5A |  | R22 | Non-TXV |  | 8.155% | 0.91845 | 15.67% | [5 empty] | Non-TXV | 8.155%
Chowchilla | CA | 93610-3407 |  | 2012-08-13 | 2012-08-13 15:41 | 2012-08-13 16:07 | OTHER - 80WE30G1 | 90 | 11.1 | Yes | Yes | 22.5 | 23.6 | -1.1 | C88B641F18D74696B72A2BA43D0E2EDE |  | R22 | Non-TXV |  | 12.33% | 0.87667 | 23.7% | [5 empty] | Non-TXV | 12.33%
Stockton | CA | 95212-3833 |  | 2012-08-07 | 2012-08-07 17:39 | 2012-08-07 19:01 | GOODMAN - VSC130481AA | 145 | 5.9 | Yes | Yes | 22.4 | 23.7 | -1.3 | D60694C20F87481B92623E951D747577 |  | R22 | Non-TXV |  | 4.069% | 0.95931 | 7.82% | [5 empty] | Non-TXV | 4.069%
Stockton | CA | 95206-1930 |  | 2012-05-07 | 2012-05-07 17:09 | 2012-05-07 17:31 | GOODMAN - GPG133000701BB | 77 | 4.4 | Yes | Yes | 30 | 24.2 | 5.8 | 5B566D91DB344950819758B5C1C33C08 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Merced | CA | 95341-5589 |  | 2012-08-07 | 2012-08-07 10:45 | 2012-08-07 11:04 | PAYNE - 591ANX03000ABAA | 70 | 2.9 | Yes | Yes | 23.2 | 21.4 | 1.8 | 24C8795E9370418BA66E2F4D51BF3A8E |  | R22 | Non-TXV |  | 4.143% | 0.95857 | 7.962% | [5 empty] | Non-TXV | 4.143%
Merced | CA | 95348-2202 |  | 2012-08-03 | 2012-08-03 08:58 | 2012-08-03 09:19 | GOODMAN - PCB048075-REVA | 82 | 3.3 | Yes | Yes | 19.1 | 21 | -1.9 | 288D1AEE00DB47D9A74A4A5BD19B0EAB |  | R22 | Non-TXV |  | 4.024% | 0.95976 | 7.734% | [5 empty] | Non-TXV | 4.024%
Los Banos | CA | 93635-3284 |  | 2012-05-16 | 2012-05-16 14:24 | 2012-05-16 14:44 | DAT AND NIGHT - UNK | 110 | 7.3 | Yes | Yes | 21.2 | 21.5 | -0.3 | 0A93911B0A284E65968877C5C4BCF0EE |  | R22 | Non-TXV |  | 6.636% | 0.93364 | 12.75% | [5 empty] | Non-TXV | 6.636%
Stockton | CA | 95212-3516 |  | 2012-08-07 | 2012-08-07 16:44 | 2012-08-07 16:44 | CARRIER - 38CKC048370 | 104 | 0 | Yes | Yes | 15.9 | 18.3 | -2.4 | B511ABC20518449A923E69D387ECAA11 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-1418 |  | 2012-08-03 | 2012-08-03 11:44 | 2012-08-03 12:09 | YORK - UNK | 104 | 3.2 | Yes | Yes | 25 | 19.5 | 5.5 | B66804AD22F944EDAF735237F374A104 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Los Banos | CA | 93635-5422 |  | 2012-05-22 | 2012-05-22 10:14 | 2012-05-22 10:36 | BDP - 561AJX036 | 69 | 0.7 | Yes | Yes | 27.3 | 21.5 | 5.8 | 9403499C36E148EAB5E3E043CDCDF72E |  | R22 | TXV |  | 1.014% | 0.98986 | 1.95% | [5 empty] | TXV | 1.014%
Merced | CA | 95348-8719 |  | 2012-08-06 | 2012-08-06 08:33 | 2012-08-06 09:08 | GOODMAN - CKL60-1L | 115 | 3.4 | Yes | Yes | 18 | 20.7 | -2.7 | 0AF37B6F54AB4BF39BC4DEE4CE9E3AFF |  | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Los Banos | CA | 93635-5452 |  | 2012-05-17 | 2012-05-17 11:42 | 2012-05-17 12:13 | RUUD - UAKA030JAZ | 66 | 10.8 | Yes | Yes | 23.7 | 24 | -0.3 | 3BBBEB178CFA4C05AF40BA7FB9D6D607 |  | R22 | Non-TXV |  | 16.36% | 0.83636 | 31.45% | [5 empty] | Non-TXV | 16.36%
Los Banos | CA | 93635-5422 |  | 2012-08-13 | 2012-08-13 15:39 | 2012-08-13 16:06 | BRYANT - 561AJ036-D | 74 | 3.1 | Yes | Yes | 19.3 | 19.6 | -0.3 | 22792A6F14B642DBACB2830DCAF116F7 |  | R22 | Non-TXV |  | 4.189% | 0.95811 | 8.051% | [5 empty] | Non-TXV | 4.189%
Stockton | CA | 95209-1759 |  | 2012-05-18 | 2012-05-18 14:09 | 2012-05-18 14:28 | PAYNE - 561CJ048-A | 105 | -7.7 | Yes | Yes | 21 | 21.9 | -0.9 | 4AF13B9F780F462DA44BD72017791944 |  | R22 | Non-TXV |  | -7.333% | 1.0733 | 2.054% |  |  |  |  | Non-TXV |  |  | -7.333%
Stockton | CA | 95209-4021 |  | 2012-08-02 | 2012-08-02 16:28 | 2012-08-02 18:02 | BRYANT - 574ANWO42090NA | 168 | 5 | Yes | Yes | 22.1 | 22.1 | 0 | 18A5CADDB5F94D598B740E0AFBF33FB9 |  | R22 | TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | TXV | 2.976%
Madera | CA | 93637-4301 |  | 2012-08-09 | 2012-08-09 12:48 | 2012-08-09 14:06 | TRANE - YCY036G1M0AD | 129 | 5.4 | Yes | Yes | 24.1 | 19.6 | 4.5 | F7641BD9AD8D4C0ABFD6BAC8D48977F4 |  | R22 | Non-TXV |  | 4.186% | 0.95814 | 8.045% | [5 empty] | Non-TXV | 4.186%
Madera | CA | 93637-4301 |  | 2012-08-09 | 2012-08-09 12:53 | 2012-08-09 14:05 | TRANE - YCY036G1M0AD | 129 | 4.4 | Yes | Yes | 21.3 | 20.9 | 0.4 | FF00D5B46D244D1C9E14AB5B5562C22C |  | R22 | Non-TXV |  | 3.411% | 0.96589 | 6.555% | [5 empty] | Non-TXV | 3.411%
Atwater | CA | 95301-0000 |  | 2012-08-15 | 2012-08-15 08:15 | 2012-08-15 08:44 | DAY & NIGHT - UNK | 75 | -4.4 | Yes | Yes | 21.5 | 20.1 | 1.4 | B6CB1BD56A7B4815A57A11A731C715D0 |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Stockton | CA | 95207-7843 |  | 2012-06-13 | 2012-06-13 10:28 | 2012-06-13 10:49 | TRANE - YCC024F1LOBF | 64 | 4.1 | Yes | Yes | 18.3 | 18.8 | -0.5 | AE9413895B2348C789AD9D12B30A553D |  | R22 | Non-TXV |  | 6.406% | 0.93594 | 12.31% | [5 empty] | Non-TXV | 6.406%
Stockton | CA | 95212-1812 |  | 2012-08-09 | 2012-08-09 14:24 | 2012-08-09 14:43 | GOODMAN - CE30-1GB | 75 | 14.7 | Yes | Yes | 16.7 | 18 | -1.3 | EFF3954DA75B45AFBC3F0C98EE9671ED |  | R22 | Non-TXV |  | 19.6% | 0.804 | 37.67% | [5 empty] | Non-TXV | 19.6%
Los Banos | CA | 93635-2954 |  | 2012-08-15 | 2012-08-15 09:51 | 2012-08-15 10:12 | OTHER - CA3042VAK1 | 97 | 4 | Yes | Yes | 17.4 | 19.2 | -1.8 | A5157EE5DED44C6988CD4AAA600D47C2 |  | R22 | Non-TXV |  | 4.124% | 0.95876 | 7.925% | [5 empty] | Non-TXV | 4.124%
Chico | CA | 95926-2920 |  | 2012-05-08 | 2012-05-08 16:05 | 2012-05-08 18:07 | BRYANT - 561CJ030-A | 73 | 7.3 | Yes | Yes | 20.2 | 21 | -0.8 | 223963486F82414FB696EAE29BD01A7A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 10% | 0.9 | 19.22% | [5 empty] | Non-TXV | 10%
Merced | CA | 95340-6981 |  | 2012-07-02 | 2012-07-02 09:06 | 2012-07-02 09:25 | PAYNE - PY1PNB042060AAAA | 100 | 8.3 | Yes | Yes | 23.7 | 18.2 | 5.5 | B7BF641F496C414383E64BCB2E450402 |  | R22 | Non-TXV |  | 8.3% | 0.917 | 15.95% | [5 empty] | Non-TXV | 8.3%
Madera | CA | 93638-1884 |  | 2012-06-12 | 2012-06-12 10:27 | 2012-06-12 10:45 | BRYANT - 582ANW042060NAAG | 100 | 2.9 | Yes | Yes | 21.2 | 20.1 | 1.1 | A31CFB575B7849DEA5B16E5309405703 |  | R22 | Non-TXV |  | 2.9% | 0.971 | 5.573% | [5 empty] | Non-TXV | 2.9%
Stockton | CA | 95209-5007 |  | 2012-05-16 | 2012-05-16 11:54 | 2012-05-16 12:17 | WESTINGHOUSE - IEO24PAAON | 57 | 2.9 | Yes | Yes | 19.1 | 18.6 | 0.5 | C00C1751150E45F29B1D0224F6ED38C0 |  | R22 | Non-TXV |  | 5.088% | 0.94912 | 9.777% | [5 empty] | Non-TXV | 5.088%
Tracy | CA | 95377-8652 |  | 2012-08-14 | 2012-08-14 10:54 | 2012-08-14 11:12 | BRYANT - 563CN042-C | 108 | 3.4 | Yes | Yes | 24.4 | 21 | 3.4 | FA965EDAEF404F7EABAFEDAEB4C786C1 |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Grass Valley | CA | 95945-0000 |  | 2012-05-08 | 2012-05-08 12:30 | 2012-05-08 12:30 | CARRIER - 38CKC024340 | 85 | 0 | Yes | Yes | 19 | 20.2 | -1.2 | C697C65B565E4762B44DE6D75AFBE186 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-5334 |  | 2012-05-29 | 2012-05-29 12:24 | 2012-05-29 12:42 | BDP - 561CJ024-C | 72 | -4.2 | Yes | Yes | 19.6 | 19.1 | 0.5 | 687791F624B346D0B4382C0811106DB2 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Grass Valley | CA | 95945-8636 |  | 2012-08-14 | 2012-08-14 12:20 | 2012-08-14 12:37 | UNITARY PRODUCTS GROUP - BRCQ0551BE | 86 | 13.4 | Yes | Yes | 23.8 | 20.4 | 3.4 | E9A151C01CAD45308E551E7741A72F76 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.58% | 0.84419 | 29.94% | [5 empty] | Non-TXV | 15.58%
Chowchilla | CA | 93610-3031 |  | 2012-05-08 | 2012-05-08 11:52 | 2012-05-08 12:09 | YORK - D1NA036N05606C | 67 | 2 | Yes | Yes | 18 | 20.7 | -2.7 | EF4A0A0E4F2344A08F66744F8E017541 |  | R22 | Non-TXV |  | 2.985% | 0.97015 | 5.737% | [5 empty] | Non-TXV | 2.985%
Magalia | CA | 95954-9506 |  | 2012-08-08 | 2012-08-08 12:05 | 2012-08-08 12:33 | CARRIER - 48SX0360B0321AA | 84 | 2.8 | Yes | Yes | 19.8 | 22.2 | -2.4 | 1657EF0E8B0645999AAD7B6E2073F00D |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Gridley | CA | 95948-9717 |  | 2012-07-19 | 2012-07-19 10:52 | 2012-07-19 11:11 | RUUD - 13AJA36A01 | 108 | 10.5 | Yes | Yes | 18 | 18.7 | -0.7 | 9C129C12F4A2415BAE613518D8F1F05F |  | R22 | Non-TXV |  | 9.722% | 0.90278 | 18.68% | [5 empty] | Non-TXV | 9.722%
Stockton | CA | 95203-1216 |  | 2012-08-08 | 2012-08-08 16:53 | 2012-08-08 17:10 | DAY & NIGHT - 588ANW036080ABAF | 67 | 2.8 | Yes | Yes | 17.6 | 20.4 | -2.8 | 9186660BA0974078898882671EEEF5CC |  | R22 | Non-TXV |  | 4.179% | 0.95821 | 8.031% | [5 empty] | Non-TXV | 4.179%
Stockton | CA | 95202-1206 |  | 2012-07-04 | 2012-07-04 10:10 | 2012-07-04 10:43 | WEATHER KING - 10AJB24A01 | 65 | 5.5 | Yes | Yes | 19.2 | 20.4 | -1.2 | 036F2E31F5D94D8EA5AC36953389324D |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Magalia | CA | 95954-9320 |  | 2012-08-09 | 2012-08-09 11:28 | 2012-08-09 11:59 | COLEMAN - 9541A801 | 50 | 5.4 | Yes | Yes | 19.9 | 20.3 | -0.4 | 152FC9EDB4CF4C10BCA956B50DCD1036 |  | R22 | Non-TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | Non-TXV | 10.8%
Lathrop | CA | 95330-8855 |  | 2012-05-15 | 2012-05-15 14:30 | 2012-05-15 14:52 | CARRIER - 38EZG042300 | 100 | 7 | Yes | Yes | 17.8 | 20.4 | -2.6 | 95B4AF048EF840FBAE585D061C562D48 |  | R410A | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Merced | CA | 95341-7027 |  | 2012-05-11 | 2012-05-11 10:03 | 2012-05-11 10:22 | BRYANT - 582ANW0360NBAF | 72 | 3.8 | Yes | Yes | 25.5 | 20.3 | 5.2 | B996DBD5660D45A499D53271541EC52A | OK: Verified Refrigerant Charge. |  |  |  | 5.278% | 0.94722 | 10.14% | [5 empty] | 0 | 5.278%
Stockton | CA | 95202-1206 |  | 2012-06-15 | 2012-06-15 17:09 | 2012-06-15 17:28 | WEATHER KING - 10AJB24A01 | 65 | 2.5 | Yes | Yes | 24.5 | 19.7 | 4.8 | E3FE952D3B074093863A5119A8082B6A |  | R22 | Non-TXV |  | 3.846% | 0.96154 | 7.391% | [5 empty] | Non-TXV | 3.846%
Madera | CA | 93637-5028 |  | 2012-08-13 | 2012-08-13 12:44 | 2012-08-13 13:01 | CARRIER - 48KLA142321BE | 80 | 9.3 | Yes | Yes | 24.6 | 18.6 | 6 | 2C23E22A37A24D72826EA84E25039E6C |  | R22 | Non-TXV |  | 11.62% | 0.88375 | 22.34% | [5 empty] | Non-TXV | 11.62%
Madera | CA | 93637-5028 |  | 2012-08-13 | 2012-08-13 12:46 | 2012-08-13 12:46 | CARRIER - 48KLA142321BE | 80 | 0 | Yes | Yes | 0 | 10.8 | -10.8 | C412306022B149F2A23BD8F90B96B8F5 | Liquid Temperature cannot be less than outdoor air temperature minus 2°F. Check entries and calibration. Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-4429 |  | 2012-08-02 | 2012-08-02 09:55 | 2012-08-02 10:13 | PAYNE - 591ANX060000AAAA | 170 | 5 | Yes | Yes | 18.7 | 20.4 | -1.7 | 394EF1DA0F3445DA938BAD85AFE71E9E |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Stockton | CA | 95206-4849 |  | 2012-06-12 | 2012-06-12 12:15 | 2012-06-12 12:32 | WEATHER KING - 10AJB30B01 | 68 | 6.5 | Yes | Yes | 19 | 20.4 | -1.4 | 338A3D7659A8442DB3182D057DC8EDAB |  | R22 | Non-TXV |  | 9.559% | 0.90441 | 18.37% | [5 empty] | Non-TXV | 9.559%
Stockton | CA | 95203-1027 |  | 2012-05-10 | 2012-05-10 10:59 | 2012-05-10 11:24 | UNK - JS5BD-018KA | 78 | 3.1 | Yes | Yes | 15.2 | 17.9 | -2.7 | 0C3C668DC89343F783DA7D2F9229DB6C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.974% | 0.96026 | 7.638% | [5 empty] | Non-TXV | 3.974%
Stockton | CA | 95209-1107 |  | 2012-05-22 | 2012-05-22 10:18 | 2012-05-22 10:35 | PAYNE - AC048X1021A | 117 | 6.1 | Yes | Yes | 22.7 | 19.4 | 3.3 | 7263F1C566E34D2CBA638D655FE1277D |  | R22 | TXV |  | 5.214% | 0.94786 | 10.02% | [5 empty] | TXV | 5.214%
Stockton | CA | 95209-4037 |  | 2012-08-07 | 2012-08-07 11:30 | 2012-08-07 11:50 | PAYNE - 5858024075YACR | 52 | 14.5 | Yes | Yes | 16.8 | 18.3 | -1.5 | AFFB0449FFBF49DEAB3B878252A288E8 |  | R22 | Non-TXV |  | 27.88% | 0.72115 | 53.59% | [5 empty] | Non-TXV | 27.88%
Stockton | CA | 95205-8403 |  | 2012-08-09 | 2012-08-09 16:33 | 2012-08-09 16:33 | OTHER - ACS030A2C1 | 71 | 0 | Yes | Yes | 25.8 | 20.2 | 5.6 | C20D5623EDC64E4BA03C01922C1D085F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Tracy | CA | 95376-5143 |  | 2012-08-08 | 2012-08-08 12:01 | 2012-08-08 12:33 | DAY & NIGHT - 565BJ030 | 72 | 2.2 | Yes | Yes | 22.7 | 20.4 | 2.3 | C1585427866149FEB96A9F6F18A22B7D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Manteca | CA | 95336-4053 |  | 2012-05-08 | 2012-05-08 11:35 | 2012-05-08 11:56 | GENERAL ELECTRIC - BGTA736B1B | 80 | 6.4 | Yes | Yes | 21.5 | 21.4 | 0.1 | A78D85C663674E97A7078BAF1DD1F5FB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Merced | CA | 95348-2251 |  | 2012-05-30 | 2012-05-30 13:19 | 2012-05-30 13:38 | BDP - 565BJ018 | 50 | 1.5 | Yes | Yes | 21.6 | 19.9 | 1.7 | 47F6CFA510A94681999D9590EA059357 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Fresno | CA | 93722-6728 |  | 2012-05-16 | 2012-05-16 14:20 | 2012-05-16 14:20 | DAY & NIGHT - 585J030040 | 68 | 0 | Yes | Yes | 24.9 | 19.7 | 5.2 | E7870D154CC249EB869B847522B25708 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95993-8991 |  | 2012-05-10 | 2012-05-10 12:13 | 2012-05-10 12:13 | ARMSTRONG - SCU12E48A | 130 | 0 | Yes | Yes | 26.7 | 21.3 | 5.5 | 925238AE8184406899879F33006AAF63 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-2807 |  | 2012-06-13 | 2012-06-13 09:48 | 2012-06-13 10:16 | RUUD - RRKA-A030JKO6E | 56 | 1.8 | Yes | Yes | 18 | 20.4 | -2.4 | D828BC82E60D418F80D0629EE4B0599B |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Durham | CA | 95938-9518 |  | 2012-08-14 | 2012-08-14 20:33 | 2012-08-14 20:56 | ALLEGIANCE - 7A2060A100A2 | 167 | 6.1 | Yes | Yes | 20 | 21.2 | -1.2 | E1B7D813DA0D46ACA459C2AB18DCA9A9 |  | R410A | Non-TXV |  | 3.653% | 0.96347 | 7.02% | [5 empty] | Non-TXV | 3.653%
Atwater | CA | 95301-4588 |  | 2012-08-10 | 2012-08-10 08:46 | 2012-08-10 09:04 | GOODMAN - CK30-1A | 76 | -5.4 | Yes | Yes | 21.8 | 20.4 | 1.4 | 051D1BC6DA324F57BB1C59E67FA00B76 |  | R22 | Non-TXV |  | -7.105% | 1.0711 | 1.99% |  |  |  |  | Non-TXV |  |  | -7.105%
Stockton | CA | 95215-7306 |  | 2012-07-03 | 2012-07-03 12:59 | 2012-07-03 13:17 | RUUD - URKA-A024JK06E | 50 | 4.5 | Yes | Yes | 17.9 | 19.9 | -2 | 5C774FAEB97140E1AE620232A37E9D43 |  | R22 | Non-TXV |  | 9% | 0.91 | 17.3% | [5 empty] | Non-TXV | 9%
Kerman | CA | 93630-9347 |  | 2012-06-14 | 2012-06-14 09:33 | 2012-06-14 09:50 | LENNOX - GCS29X-036-75-2PA | 85 | -5 | Yes | Yes | 17.5 | 20.2 | -2.7 | 002635734ADA49ACAE0CDB0699692FE5 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Kerman | CA | 93630-9347 |  | 2012-06-14 | 2012-06-14 09:51 | 2012-06-14 09:51 | LENNOX - GCS29X-036-75-2PA | 85 | 0 | Yes | Yes | 18.5 | 19.6 | -1.1 | 02FC243A671F4B4EA45BE0FE5430CB93 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3546 |  | 2012-05-07 | 2012-05-07 12:36 | 2012-05-07 13:01 | WESTING - 1E030BCAON | 105 | 3.5 | Yes | Yes | 28 | 22.4 | 5.6 | 2984CD868B3C48328953CE4C580BAABE |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Yuba City | CA | 95993-8929 |  | 2012-08-16 | 2012-08-16 10:45 | 2012-08-16 11:09 | GIBSON - JS3BC-060KA | 155 | -14.6 | Yes | Yes | 23 | 19.8 | 3.2 | 3D9999A2BB8B4F86A80D04F137434040 |  | R22 | Non-TXV |  | -9.419% | 1.0942 | 2.638% |  |  |  |  | Non-TXV |  |  | -9.419%
Yuba City | CA | 95991-8857 |  | 2012-08-10 | 2012-08-10 14:53 | 2012-08-10 14:53 | YORK - CMA03611A | 95 | 0 | Yes | Yes | 22.5 | 21.9 | 0.6 | C00A7E66FD82486BBF434764EAEC905A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-8823 |  | 2012-08-03 | 2012-08-03 12:48 | 2012-08-03 13:08 | OTHER - CHQ30-18 | 169 | -17.9 | Yes | Yes | 18 | 20.4 | -2.4 | 309CE3E9F0F743D5841B98935D7365B3 |  | R22 | Non-TXV |  | -10.59% | 1.1059 | 2.966% |  |  |  |  | Non-TXV |  |  | -10.59%
Stockton | CA | 95203-1419 |  | 2012-08-08 | 2012-08-08 17:13 | 2012-08-08 17:31 | CARRIER - 58GAN036060 | 78 | 4.8 | Yes | Yes | 21 | 20.2 | 0.8 | 22CF0FD20C594FE18C79CDAEA650C111 |  | R22 | Non-TXV |  | 6.154% | 0.93846 | 11.83% | [5 empty] | Non-TXV | 6.154%
Stockton | CA | 95203-2017 |  | 2012-08-14 | 2012-08-14 10:38 | 2012-08-14 11:01 | OTHER - 563CN036-B | 122 | 5.9 | Yes | Yes | 19.8 | 20.4 | -0.6 | 9596E2E33FEF4B5BB4047BDD23AE5A87 |  | R22 | TXV |  | 4.836% | 0.95164 | 9.294% | [5 empty] | TXV | 4.836%
Los Banos | CA | 93635-3034 |  | 2012-08-13 | 2012-08-13 11:22 | 2012-08-13 11:42 | YORK - D1NP036N05606A | 108 | 3.4 | Yes | Yes | 18.9 | 20.9 | -2 | F1E4D695E45D45DE959EFCC4F788A62C |  | R22 | Non-TXV |  | 3.148% | 0.96852 | 6.05% | [5 empty] | Non-TXV | 3.148%
Stockton | CA | 95212-3108 |  | 2012-08-06 | 2012-08-06 14:09 | 2012-08-06 14:27 | GOODMAN - CRT48-1 | 145 | -8.5 | Yes | Yes | 27.2 | 21.3 | 5.9 | D4090326319E4B9685E219EAF043BC6F |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Winton | CA | 95388-9767 |  | 2012-08-03 | 2012-08-03 10:00 | 2012-08-03 10:26 | GE - BTN936A100B2 | 144 | -8.5 | Yes | Yes | 23.6 | 19.9 | 3.7 | 35271C28985C439CB20906959397A4CD |  | R22 | Non-TXV |  | -5.903% | 1.059 | 1.653% |  |  |  |  | Non-TXV |  |  | -5.903%
Atwater | CA | 95301-2119 |  | 2012-08-06 | 2012-08-06 15:14 | 2012-08-06 15:14 | AMERICAN STANDARD - YCC036F1M0BC | 83 | 0 | Yes | Yes | 23.6 | 21.5 | 2.1 | 67A9F8B114C5497682FD9259AFA6BA2A | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3495 |  | 2012-08-16 | 2012-08-16 10:53 | 2012-08-16 11:11 | CARRIER - 38CKC948370 | 99 | -9.9 | Yes | Yes | 16 | 17.5 | -1.5 | BDB2AA49815C4F99ACF2EF03B14E0338 |  | R22 | TXV |  | -10% | 1.1 | 2.8% |  |  |  |  | TXV |  |  | -10%
Stockton | CA | 95203-3019 |  | 2012-08-13 | 2012-08-13 10:43 | 2012-08-13 11:02 | YORK - H2DH036S06B | 124 | 7.6 | Yes | Yes | 18.1 | 20.4 | -2.3 | 8AAAA79B120D425788FFD43933AB002C |  | R22 | Non-TXV |  | 6.129% | 0.93871 | 11.78% | [5 empty] | Non-TXV | 6.129%
Stockton | CA | 95203-3019 |  | 2012-08-13 | 2012-08-13 10:52 | 2012-08-13 11:18 | LENNOX - 13HPD-024-01 | 99 | 3 | Yes | Yes | 23 | 20.4 | 2.6 | 7C50C236D96B4746AA25AE100DE5A8E3 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Yuba City | CA | 95993-3550 |  | 2012-05-17 | 2012-05-17 11:09 | 2012-05-17 11:09 | DAY&NITE - 585B02450 YACR | 54 | 0 | Yes | Yes | 19 | 18.8 | 0.2 | CEF1ED092ED147F78692D970E3B9E719 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-8857 |  | 2012-08-10 | 2012-08-10 14:32 | 2012-08-10 14:49 | UNITARY PRODUCTS GROUP - TCGD30S21S1HA | 59 | 3.5 | Yes | Yes | 18.6 | 21.3 | -2.7 | B855FE0356F7456FA9E7EDCC9E3A5217 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.932% | 0.94068 | 11.4% | [5 empty] | Non-TXV | 5.932%
Stockton | CA | 95206-2494 |  | 2012-08-08 | 2012-08-08 12:38 | 2012-08-08 13:11 | GOODMAN - CK30-1A | 76 | 3.3 | Yes | Yes | 19 | 21.8 | -2.8 | A868799C0D864B938325954267672B04 |  | R22 | Non-TXV |  | 4.342% | 0.95658 | 8.345% | [5 empty] | Non-TXV | 4.342%
Stockton | CA | 95212-3201 |  | 2012-08-08 | 2012-08-08 14:27 | 2012-08-08 14:44 | OTHER - DAGA-060JA | 191 | -11.2 | Yes | Yes | 28.1 | 22.1 | 6 | 0631534811C249EA91D350D4C64926B4 |  | R22 | Non-TXV |  | -5.864% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.864%
Stockton | CA | 95210-5335 |  | 2012-05-29 | 2012-05-29 12:52 | 2012-05-29 13:11 | BDP - 561CJ030-C | 76 | 2.6 | Yes | Yes | 19.1 | 20.2 | -1.1 | 50F1E3B654804842AC83949E8E7C893D |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Kingsburg | CA | 93631-1602 |  | 2012-07-11 | 2012-07-11 08:47 | 2012-07-11 09:14 | RUUD - N/A | 60 | 6.2 | Yes | Yes | 20.4 | 19.7 | 0.8 | 7903DB873ED24ED1BB14D1DF5F26BF63 |  | R22 | Non-TXV |  | 10.33% | 0.89667 | 19.86% | [5 empty] | Non-TXV | 10.33%
Los Banos | CA | 93635-6415 |  | 2012-08-13 | 2012-08-13 11:47 | 2012-08-13 12:05 | BRYANT - 563CN060-E | 204 | 6.1 | Yes | Yes | 17.8 | 19.8 | -2 | 127005C9A3BC4DEE90B341BF8EA7415A |  | R22 | Non-TXV |  | 2.99% | 0.9701 | 5.746% | [5 empty] | Non-TXV | 2.99%
Stockton | CA | 95212-3221 |  | 2012-05-17 | 2012-05-17 11:29 | 2012-05-17 11:48 | CARRIER - 38CKC042350 | 82 | -4.8 | Yes | Yes | 25.6 | 21.2 | 4.4 | 9125AE10F1D54884823D6B23BC43203F |  | R22 | Non-TXV |  | -5.854% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.854%
Auburn | CA | 95602-2138 |  | 2012-08-08 | 2012-08-08 12:39 | 2012-08-08 12:39 | GE - BGTA718B1B | 36 | 0 | Yes | Yes | 17.2 | 19.5 | -2.3 | 0EDAA553D0174D70ACBF99347C5F2C45 | OK: Verified Refrigerant Charge Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-5132 |  | 2012-08-03 | 2012-08-03 19:19 | 2012-08-03 19:38 | - 550AN060-E | 185 | 5.7 | Yes | Yes | 23 | 21.3 | 1.8 | 291A238C2F724D63ADE4C2E06FE8F365 |  | R410A | Non-TXV |  | 3.081% | 0.96919 | 5.921% | [5 empty] | Non-TXV | 3.081%
Newman | CA | 95360-1225 |  | 2012-07-12 | 2012-07-12 09:22 | 2012-07-12 09:40 | OTHER - 36PAC-103C | 55 | 1.6 | Yes | Yes | 21.4 | 20.8 | 0.6 | FE635474B8104F3FB902928A5D10DD81 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.909% | 0.97091 | 5.591% | [5 empty] | Non-TXV | 2.909%
Merced | CA | 95348-1532 |  | 2012-05-14 | 2012-05-14 16:48 | 2012-05-14 17:15 | FRASER - 55AW24-106 | 72 | 2.8 | Yes | Yes | 27.3 | 22.1 | 5.2 | 3E3766C2EC284F2E9A6854D340D64A2B |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Stockton | CA | 95210-1829 |  | 2012-08-08 | 2012-08-08 10:42 | 2012-08-08 10:59 | RHEEM - UNK | 80 | -4.7 | Yes | Yes | 20 | 18.2 | 1.8 | 376054EF130C43A1A4648E940A86558B |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Los Banos | CA | 93635-8542 |  | 2012-08-16 | 2012-08-16 13:08 | 2012-08-16 13:31 | GOODMAN - CRT601 | 139 | 8.3 | Yes | Yes | 26.4 | 20.4 | 6 | DC81C02C5FDA4EA69E15FA73B27A7153 |  | R22 | Non-TXV |  | 5.971% | 0.94029 | 11.48% | [5 empty] | Non-TXV | 5.971%
Tracy | CA | 95377-9502 |  | 2012-06-26 | 2012-06-26 14:41 | 2012-06-26 15:06 | WEATHER KING - 10AJA6001 | 132 | 4 | Yes | Yes | 18.4 | 19.9 | -1.5 | E16CBBC6141B47AE83894222A1329127 |  | R22 | Non-TXV |  | 3.03% | 0.9697 | 5.824% | [5 empty] | Non-TXV | 3.03%
Chowchilla | CA | 93610-2238 |  | 2012-05-11 | 2012-05-11 12:04 | 2012-05-11 12:24 | FRASER-JOHNSTON - 80WE30G1NA | 86 | 2.6 | Yes | Yes | 19.4 | 19.4 | 0 | 733FF53C146749FD827E33E16CEE452D | OK: Verified Refrigerant Charge. |  |  |  | 3.023% | 0.96977 | 5.81% | [5 empty] | 0 | 3.023%
Stockton | CA | 95212-3500 |  | 2012-08-07 | 2012-08-07 13:41 | 2012-08-07 13:58 | YORK - AC042X1221A | 107 | 10.8 | Yes | Yes | 15.4 | 18.3 | -2.9 | 6A309EB677B3417EBFAAC92AD3355005 |  | R22 | Non-TXV |  | 10.09% | 0.89907 | 19.4% | [5 empty] | Non-TXV | 10.09%
Auburn | CA | 95602-2335 |  | 2012-07-25 | 2012-07-25 15:36 | 2012-07-25 15:36 | GE - BTB918A100AA | 36 | 0 | Yes | Yes | 17.2 | 19.5 | -2.3 | D2D69DAE35824616A03FE27933E073FF | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95926-1804 |  | 2012-08-02 | 2012-08-02 11:48 | 2012-08-02 18:11 | AMERICAN STANDARD - YCC030F1M0BJ | 72 | 3 | Yes | Yes | 23.7 | 21.5 | 2.2 | 546512CC51AA44DD879CD55C93270055 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Paradise | CA | 95969-4632 |  | 2012-05-11 | 2012-05-11 17:31 | 2012-05-11 17:31 | GOODMAN - CK30-1A | 83 | 0 | Yes | Yes | 23.5 | 24.2 | -0.7 | DC3E809D5A61459B86E444DB83C62FD5 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Winton | CA | 95388-9512 |  | 2012-05-07 | 2012-05-07 14:21 | 2012-05-07 14:21 | RHEEM - RRNA-B024JK06X | 70 | 0 | Yes | Yes | 18.2 | 19.7 | -1.5 | 4BF8A49DFF9046B9BEE0C6C5CC9300CC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-2445 |  | 2012-05-21 | 2012-05-21 12:06 | 2012-05-21 12:37 | DAY AND NIGHT - 588ANW04800AEGE | 104 | 3.2 | Yes | Yes | 26.1 | 20.8 | 5.3 | 026CF5B6FF8D463EB39367979D2336B0 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Madera | CA | 93637-3057 |  | 2012-05-14 | 2012-05-14 10:37 | 2012-05-14 10:57 | PAYNE - 585BJW024050AAAD | 115 | 2.5 | Yes | Yes | 17.9 | 19.9 | -2 | 9B1D9061D95F4D4A801359F14AEA7917 |  | R22 | Non-TXV |  | 2.174% | 0.97826 | 4.178% | [5 empty] | Non-TXV | 2.174%
Georgetown | CA | 95634-9300 |  | 2012-07-16 | 2012-07-16 09:30 | 2012-07-16 09:47 | GOODMAN - CK30-1T | 76 | 20.8 | Yes | Yes | 18.4 | 19.9 | -1.5 | 3744AC4709204D818917899EC02AF9A3 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 30°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 27.37% | 0.72632 | 52.6% | [5 empty] | Non-TXV | 27.37%
Valley Springs | CA | 95252-9259 |  | 2012-08-16 | 2012-08-16 09:20 | 2012-08-16 09:37 | YORK - ACP042G0701021C | 76 | -4.5 | Yes | Yes | 25.4 | 21 | 4.4 | E1EB5D16CCF342318AEEEFD95C0F0C1B |  | R22 | Non-TXV |  | -5.921% | 1.0592 | 1.658% |  |  |  |  | Non-TXV |  |  | -5.921%
Rocklin | CA | 95677-2317 |  | 2012-08-03 | 2012-08-03 13:50 | 2012-08-03 14:13 | BRYANT - 574BNW036060NB-- | 152 | -16.1 | Yes | Yes | 24.7 | 22.1 | 2.6 | EA0790CC6A494E24A2500599F93171FF |  | R410A | TXV |  | -10.59% | 1.1059 | 2.966% |  |  |  |  | TXV |  |  | -10.59%
Stockton | CA | 95205-7005 |  | 2012-05-17 | 2012-05-17 13:17 | 2012-05-17 13:39 | RHEEM - UNK | 63 | 2.7 | Yes | Yes | 18.5 | 19.3 | -0.8 | 550AB4B58F3D4B579E4DC5C19F0EA025 |  | R22 | Non-TXV |  | 4.286% | 0.95714 | 8.236% | [5 empty] | Non-TXV | 4.286%
Auburn | CA | 95602-2135 |  | 2012-05-16 | 2012-05-16 11:04 | 2012-05-16 11:31 | GOODAN - CKL30-1G | 74 | -7 | Yes | Yes | 19 | 18.8 | 0.2 | D838CFD067554740937DF48DE50897D4 |  | R22 | Non-TXV |  | -9.459% | 1.0946 | 2.649% |  |  |  |  | Non-TXV |  |  | -9.459%
Auburn | CA | 95602-2336 |  | 2012-07-09 | 2012-07-09 14:13 | 2012-07-09 14:13 | RHEEM - UNK FADED | 53 | 0 | Yes | Yes | 21.8 | 19.7 | 2.1 | 09CC25DF35AC43748E8E571073A0BE59 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93638-4834 |  | 2012-08-10 | 2012-08-10 11:52 | 2012-08-10 12:13 | AMERICAN STANDARD - 2YCC3030A1040AB | 88 | 12.8 | Yes | Yes | 27.3 | 27.2 | 0.1 | 70B586AF02154754B4A60C2AC1CFA3B5 |  | R22 | Non-TXV |  | 14.55% | 0.85455 | 27.95% | [5 empty] | Non-TXV | 14.55%
Madera | CA | 93638-1847 |  | 2012-06-11 | 2012-06-11 12:45 | 2012-06-11 13:06 | CARRIER - UNK | 80 | 2.9 | Yes | Yes | 23.4 | 23 | 0.4 | 67733869713146FBAA74AA7E0F49A2AA |  | R22 | Non-TXV |  | 3.625% | 0.96375 | 6.966% | [5 empty] | Non-TXV | 3.625%
Manteca | CA | 95336-4029 |  | 2012-05-07 | 2012-05-07 16:58 | 2012-05-07 20:26 | GARDIAN - GCGD36S21S1A | 65 | 2.3 | Yes | Yes | 27.1 | 23.9 | 3.2 | 236F137D336448D7944929697326EAF6 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.538% | 0.96462 | 6.8% | [5 empty] | Non-TXV | 3.538%
Stockton | CA | 95212-2740 |  | 2012-08-08 | 2012-08-08 15:02 | 2012-08-08 15:18 | CARRIER - 38CKC042---351 | 85 | 8.9 | Yes | Yes | 17.4 | 18.5 | -1.1 | 659DC41CA1154ADAA054E3E9F022470B |  | R22 | Non-TXV |  | 10.47% | 0.89529 | 20.12% | [5 empty] | Non-TXV | 10.47%
Valley Springs | CA | 95252-8524 |  | 2012-07-16 | 2012-07-16 11:15 | 2012-07-16 11:32 | BRYANT - 561CJ042-E | 80 | 3.6 | Yes | Yes | 21.8 | 19.3 | 2.5 | B9B98906E04747ADBE2A2314FF8C8AA9 |  | R22 | Non-TXV |  | 4.5% | 0.955 | 8.648% | [5 empty] | Non-TXV | 4.5%
Fresno | CA | 93725-1208 |  | 2012-05-24 | 2012-05-24 10:35 | 2012-05-24 10:35 | YORK - DAYQ-F036N070A | 58 | 0 | Yes | Yes | 20.2 | 20.1 | 0.2 | 86B1CD68C6424977B059F2358AC12758 |  | R410A | TXV |  | 0% | 1 | 0%
Merced | CA | 95341-5411 |  | 2012-05-21 | 2012-05-21 14:02 | 2012-05-21 14:29 | GOODMAN - CK301B | 76 | 12.6 | Yes | Yes | 19 | 20.4 | -1.4 | 2AAA274634814F5C8228B2E5F132E03D |  | R22 | Non-TXV |  | 16.58% | 0.83421 | 31.86% | [5 empty] | Non-TXV | 16.58%
Los Banos | CA | 93635-4520 |  | 2012-05-22 | 2012-05-22 17:35 | 2012-05-22 17:55 | RUUD - N/A | 75 | 3.7 | Yes | Yes | 23.1 | 22.1 | 1 | 5EA6209D852E4E1D8BE54FD22D85B127 |  | R22 | Non-TXV |  | 4.933% | 0.95067 | 9.481% | [5 empty] | Non-TXV | 4.933%
Auburn | CA | 95602-2137 |  | 2012-08-08 | 2012-08-08 12:01 | 2012-08-08 12:23 | GE - BGTA718B1B | 36 | 7.7 | Yes | Yes | 18.6 | 19.4 | -0.8 | D7726DEA24734D6FB4E3C2B70C9CF4B6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 21.39% | 0.78611 | 41.1% | [5 empty] | Non-TXV | 21.39%
Los Banos | CA | 93635-2614 |  | 2012-05-15 | 2012-05-15 09:36 | 2012-05-15 10:01 | PAYNE - UNK | 96 | 3 | Yes | Yes | 26.6 | 20.7 | 5.9 | 0A24BC50446740C3B7A1E1D4C7733200 |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Planada | CA | 95365-0000 |  | 2012-08-14 | 2012-08-14 14:52 | 2012-08-14 15:33 | TRANE - TTN024D100A0 | 81 | 2.4 | Yes | Yes | 16.6 | 18.1 | -1.5 | 5E3B3BE91DAA481E9EA7F8683D89CA81 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Stockton | CA | 95212-3519 |  | 2012-05-17 | 2012-05-17 10:12 | 2012-05-17 10:32 | CARRIER - 38CKC048360 | 98 | -5.8 | Yes | Yes | 24.1 | 21.3 | 2.9 | 4FCF8708F33641F3B6A79D522473B68B |  | R22 | Non-TXV |  | -5.918% | 1.0592 | 1.657% |  |  |  |  | Non-TXV |  |  | -5.918%
Lincoln | CA | 95648-3244 |  | 2012-07-11 | 2012-07-11 14:14 | 2012-07-11 14:14 | CARRIER - 38ETG04830 | 152 | 0 | Yes | Yes | 21.8 | 21 | 0.8 | 2707F4130C7E402F8F81A07527A765EF |  | R410A | Non-TXV |  | 0% | 1 | 0%
Dinuba | CA | 93618-3384 |  | 2012-05-08 | 2012-05-08 13:29 | 2012-05-08 14:01 | DAY AND NIGHT - N/A | 85 | 14.2 | Yes | Yes | 21 | 22.8 | -1.8 | 132C7FB2DF834C8C82348C058C2B5927 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 16.71% | 0.83294 | 32.11% | [5 empty] | Non-TXV | 16.71%
Merced | CA | 95341-5437 |  | 2012-08-06 | 2012-08-06 14:16 | 2012-08-06 14:42 | - H4DE030606A | 71 | 15 | Yes | Yes | 29.1 | 28.6 | 0.5 | 44FD8FA87B7A47558EAA91CA42633C53 |  | R22 | Non-TXV |  | 21.13% | 0.78873 | 40.6% | [5 empty] | Non-TXV | 21.13%
Kerman | CA | 93630-1908 |  | 2012-05-17 | 2012-05-17 11:39 | 2012-05-17 12:04 | CARRIER - N/A | 84 | 2.5 | Yes | Yes | 22.3 | 20.8 | 1.5 | F4F3413611934EFE8C9A3344E6B8379D |  | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Chico | CA | 95926-1328 |  | 2012-06-08 | 2012-06-08 19:05 | 2012-06-08 19:22 | TRANE - YCC036F1M0AA | 88 | 2.9 | Yes | Yes | 23.6 | 20.7 | 2.9 | C3688295208440A6AD570096B4867A71 |  | R22 | Non-TXV |  | 3.295% | 0.96705 | 6.333% | [5 empty] | Non-TXV | 3.295%
Stockton | CA | 95207-1132 |  | 2012-08-06 | 2012-08-06 13:51 | 2012-08-06 14:07 | PAYNE - AC048X1221A | 122 | 15.1 | Yes | Yes | 21.6 | 20.9 | 0.7 | 1CE6032EF7C443FFB84309DE8C690FB3 |  | R22 | Non-TXV |  | 12.38% | 0.87623 | 23.79% | [5 empty] | Non-TXV | 12.38%
Red Bluff | CA | 96080-4271 |  | 2012-07-02 | 2012-07-02 18:28 | 2012-07-02 18:52 | BRYANT - 582ANW02040AAAD | 54 | 2.5 | Yes | Yes | 23.5 | 21.1 | 2.5 | A509CFB3A65242FE8643205DB4A317F1 |  | R22 | Non-TXV |  | 4.63% | 0.9537 | 8.897% | [5 empty] | Non-TXV | 4.63%
Stockton | CA | 95215-4847 |  | 2012-07-19 | 2012-07-19 12:28 | 2012-07-19 12:46 | RHEEM - RRMA-A024JKO6E | 70 | 2.6 | Yes | Yes | 21.3 | 21.3 | 0 | 2D85A4C64430449C8A531D1616DB7C71 |  | R22 | TXV |  | 3.714% | 0.96286 | 7.138% | [5 empty] | TXV | 3.714%
Stockton | CA | 95212-3829 |  | 2012-08-16 | 2012-08-16 10:22 | 2012-08-16 10:22 | YORK - H1RA042S06G | 84 | 0 | Yes | Yes | 13.5 | 16.1 | -2.6 | 3BA2127DA51C43829B1AAE7E3709FD99 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-6085 |  | 2012-08-15 | 2012-08-15 13:15 | 2012-08-15 13:46 | CARRIER - 38BRC042340 | 105 | -9.9 | Yes | Yes | 18 | 20.1 | -2.1 | 1F81F4DDA6904F5D8B19DFFBCF420BDE |  | R22 | Non-TXV |  | -9.429% | 1.0943 | 2.64% |  |  |  |  | Non-TXV |  |  | -9.429%
Stockton | CA | 95202-1429 |  | 2012-07-06 | 2012-07-06 11:23 | 2012-07-06 11:40 | RHEEM - RRKA-A024JK06E | 50 | 2.9 | Yes | Yes | 19.7 | 19.3 | 0.4 | 061867E72E474EEEB17D2A44C1491153 |  | R22 | Non-TXV |  | 5.8% | 0.942 | 11.15% | [5 empty] | Non-TXV | 5.8%
Olivehurst | CA | 95961-0000 |  | 2012-05-17 | 2012-05-17 15:50 | 2012-05-17 16:05 | UNK - CCGD36S21Q1A | 46 | -4.3 | Yes | Yes | 21 | 19.8 | 1.2 | D6C68201B99942C1A0EDDF0CBF512471 |  | R22 | Non-TXV |  | -9.348% | 1.0935 | 2.618% |  |  |  |  | Non-TXV |  |  | -9.348%
Stockton | CA | 95203-1347 |  | 2012-07-02 | 2012-07-02 12:24 | 2012-07-02 12:42 | GOODMAN - PGB024075-1 | 54 | 2.9 | Yes | Yes | 20.1 | 20.4 | -0.3 | 10385E6E23E14CC1BDD20E7CB7CDF81D |  | R22 | Non-TXV |  | 5.37% | 0.9463 | 10.32% | [5 empty] | Non-TXV | 5.37%
Madera | CA | 93638-1893 |  | 2012-08-10 | 2012-08-10 12:30 | 2012-08-10 13:31 | CARRIER - 38CK034800 | 72 | 2.3 | Yes | Yes | 16.3 | 17.7 | -1.4 | 86C5FEC9E56542139BDC5073F7E2B79E |  | R22 | Non-TXV |  | 3.194% | 0.96806 | 6.139% | [5 empty] | Non-TXV | 3.194%
Manteca | CA | 95336-3456 |  | 2012-05-07 | 2012-05-07 21:04 | 2012-05-07 21:33 | GOODMAN - CK24-18 | 71 | 3.2 | Yes | Yes | 27 | 21.5 | 5.5 | 106875B2AEBC4625AF2F9DBC29C523A2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 34°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.507% | 0.95493 | 8.662% | [5 empty] | Non-TXV | 4.507%
Stockton | CA | 95210-5228 |  | 2012-06-01 | 2012-06-01 11:28 | 2012-06-01 11:50 | DAY & NIGHT - 541DJ018 | 83 | 2.9 | Yes | Yes | 20.9 | 19.2 | 1.7 | A446A4FDFA674A4BAA756A7D08E4BD88 |  | R22 | Non-TXV |  | 3.494% | 0.96506 | 6.715% | [5 empty] | Non-TXV | 3.494%
Marysville | CA | 95901-6713 |  | 2012-05-17 | 2012-05-17 15:45 | 2012-05-17 15:45 | COMFORT MAKER - NAC030AKA5 | 81 | 0 | Yes | Yes | 21.4 | 18.6 | 2.8 | F7DD4B4250C5447487501E2151320E84 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-0000 |  | 2012-08-07 | 2012-08-07 09:50 | 2012-08-07 10:12 | BRYANT - 563CN042-C | 105 | 15.4 | Yes | Yes | 19 | 20.1 | -1.1 | 60B1CDC4C23A4B508EC11CBA46893A42 |  | R22 | Non-TXV |  | 14.67% | 0.85333 | 28.19% | [5 empty] | Non-TXV | 14.67%
Marysville | CA | 95901-3566 |  | 2012-05-17 | 2012-05-17 12:48 | 2012-05-17 13:06 | YORK - D1NA024N05606C | 54 | 7.2 | Yes | Yes | 20.9 | 19.1 | 1.8 | 8053B49C86574944A343942C60B29818 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 13.33% | 0.86667 | 25.62% | [5 empty] | Non-TXV | 13.33%
Stockton | CA | 95212-0000 |  | 2012-08-07 | 2012-08-07 13:38 | 2012-08-07 13:56 | GOODMAN - CLJ48-1A | 130 | 4.1 | Yes | Yes | 21 | 20.2 | 0.8 | 1D92C09727CD4F6B9E7C7F3B5FF43876 |  | R22 | Non-TXV |  | 3.154% | 0.96846 | 6.061% | [5 empty] | Non-TXV | 3.154%
Hamilton City | CA | 95951-0000 |  | 2012-08-14 | 2012-08-14 17:34 | 2012-08-14 17:53 | AMANA - PGB36C0702D | 103 | 5.3 | Yes | Yes | 23.9 | 21.2 | 2.7 | BB01FF81D94D44F6BF2D815B2A436D18 |  | R22 | Non-TXV |  | 5.146% | 0.94854 | 9.889% | [5 empty] | Non-TXV | 5.146%
Madera | CA | 93638-0636 |  | 2012-06-11 | 2012-06-11 13:51 | 2012-06-11 14:08 | CARRIER - 48SS-030040321 | 54 | -3.8 | Yes | Yes | 18.7 | 19.6 | -0.8 | EAF5F4CF44A84012B9EAB529F3258DBB |  | R22 | Non-TXV |  | -7.037% | 1.0704 | 1.971% |  |  |  |  | Non-TXV |  |  | -7.037%
Valley Springs | CA | 95252-9029 |  | 2012-07-06 | 2012-07-06 11:18 | 2012-07-06 11:35 | CARRIER - 50YQ030300 | 92 | -5.4 | Yes | Yes | 23.2 | 20.4 | 2.8 | 7F9C5F8CA37948D3A084B69FF4C0389D |  | R22 | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Madera | CA | 93638-4408 |  | 2012-08-11 | 2012-08-11 00:12 | 2012-08-11 00:29 | RUUD - D1NA030N03606C | 76 | 2.8 | Yes | Yes | 22.5 | 24.5 | -2 | 540C62C1B06B46648620C824AF09A7BD |  | R22 | Non-TXV |  | 3.684% | 0.96316 | 7.08% | [5 empty] | Non-TXV | 3.684%
Stockton | CA | 95205-6400 |  | 2012-05-29 | 2012-05-29 18:11 | 2012-05-29 18:11 | GOODMAN - CKL36-1H | 71 | 0 | Yes | Yes | 17.8 | 20.2 | -2.4 | 9DA458EEB8CD42579A99C94D35576D45 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95202-1429 |  | 2012-07-10 | 2012-07-10 13:04 | 2012-07-10 13:22 | RHEEM - RRKA-A024JK06E | 51 | 2.4 | Yes | Yes | 19 | 20.4 | -1.4 | 803118727B1141208349D8C3A011B667 |  | R22 | Non-TXV |  | 4.706% | 0.95294 | 9.044% | [5 empty] | Non-TXV | 4.706%
Manteca | CA | 95337-6044 |  | 2012-05-11 | 2012-05-11 13:59 | 2012-05-11 14:17 | RHEEM - RRPL-B042JK08X | 112 | 4.3 | Yes | Yes | 22.5 | 20.1 | 2.4 | B02A0633CCB1404E9216DDC109AA2C1F | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 3.839% | 0.96161 | 7.378% | [5 empty] | Non-TXV | 3.839%
Chico | CA | 95973-9297 |  | 2012-08-07 | 2012-08-07 15:32 | 2012-08-07 18:31 | LENNOX - 13ACC-036-230-01 | 115 | 7.4 | Yes | Yes | 24.3 | 22.1 | 2.2 | 292784E5525143B898599F0A4F29942D |  | R22 | Non-TXV |  | 6.435% | 0.93565 | 12.37% | [5 empty] | Non-TXV | 6.435%
Fresno | CA | 93710-7017 |  | 2012-05-17 | 2012-05-17 11:07 | 2012-05-17 11:33 | YORK - D1NH046N05605C | 108 | 3.2 | Yes | Yes | 18.8 | 21 | -2.2 | 7DC65F1DD385445F8F66F819FF2EE7F8 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Fresno | CA | 93726-4520 |  | 2012-05-08 | 2012-05-08 15:49 | 2012-05-08 16:09 | BRYANT - 582ANW024060AAAD | 53 | 3.4 | Yes | Yes | 23 | 22.6 | 0.4 | C51C572F519146A4B7A1693FF3D63788 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6.415% | 0.93585 | 12.33% | [5 empty] | Non-TXV | 6.415%
Stockton | CA | 95205-7789 |  | 2012-08-14 | 2012-08-14 16:08 | 2012-08-14 16:28 | RUUD - UAMB-048JBZ | 162 | 6.6 | Yes | Yes | 21.6 | 19 | 2.6 | 7CAF55BD52E94B5E92CCD96373423B7A |  | R22 | Non-TXV |  | 4.074% | 0.95926 | 7.829% | [5 empty] | Non-TXV | 4.074%
Los Banos | CA | 93635-3155 |  | 2012-08-08 | 2012-08-08 10:48 | 2012-08-08 11:20 | AMERICAN STANDARD - 4YC40241064AA | 93 | 3.9 | Yes | Yes | 23.5 | 20.2 | 3.3 | 960EA296AB364F4D89D9020526DE65AB |  | R410A | Non-TXV |  | 4.194% | 0.95806 | 8.059% | [5 empty] | Non-TXV | 4.194%
Marysville | CA | 95901-3421 |  | 2012-08-13 | 2012-08-13 12:37 | 2012-08-13 13:32 | CARRIER - 38BRG042310 | 85 | 5.3 | Yes | Yes | 24.3 | 19.8 | 4.5 | 6542C31DA245448E990CF548393AF4ED |  | R22 | Non-TXV |  | 6.235% | 0.93765 | 11.98% | [5 empty] | Non-TXV | 6.235%
Los Banos | CA | 93635-2604 |  | 2012-08-06 | 2012-08-06 13:21 | 2012-08-06 13:38 | RHEEM - UNK | 110 | 3.6 | Yes | Yes | 25 | 19.9 | 5.1 | 4706A6AFED85482F91D2FFCDE31E921B |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%
Stockton | CA | 95212-3028 |  | 2012-08-03 | 2012-08-03 14:51 | 2012-08-03 15:11 | YORK - H1RD036S06G | 145 | 5.3 | Yes | Yes | 17.4 | 19.5 | -2.1 | D08C1CBB605A4FD5A8DFF63AC0969803 |  | R22 | Non-TXV |  | 3.655% | 0.96345 | 7.024% | [5 empty] | Non-TXV | 3.655%
Madera | CA | 93637-6162 |  | 2012-05-07 | 2012-05-07 13:00 | 2012-05-07 13:25 | RHEEM - RRNA-B048JK10X | 153 | 4.5 | Yes | Yes | 20.2 | 20.4 | -0.2 | A7931C254F03454085268ED69B855A5E | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Madera | CA | 93638-1876 |  | 2012-06-13 | 2012-06-13 11:54 | 2012-06-13 12:25 | PAYNE - PYPNB042060AAAA | 100 | -4.1 | Yes | Yes | 26.6 | 20.8 | 5.8 | D574267019CB491C967FA18410F6D420 |  | R22 | TXV |  | -4.1% | 1.041 | 1.148% |  |  |  |  | TXV |  |  | -4.1%
Lathrop | CA | 95330-8948 |  | 2012-08-09 | 2012-08-09 14:55 | 2012-08-09 15:11 | YORK - H1RA042S06D | 84 | 9 | Yes | Yes | 17.6 | 20.1 | -2.5 | 739F8E83272D457E8398A44EB469F244 |  | R22 | Non-TXV |  | 10.71% | 0.89286 | 20.59% | [5 empty] | Non-TXV | 10.71%
Stockton | CA | 95210-2227 |  | 2012-08-09 | 2012-08-09 10:50 | 2012-08-09 11:11 | COLEMAN - 9536-90 | 57 | 4.3 | Yes | Yes | 24.8 | 21.7 | 3.1 | 878A45593596415BB993659257F2EDEB |  | R22 | Non-TXV |  | 7.544% | 0.92456 | 14.5% | [5 empty] | Non-TXV | 7.544%
Madera | CA | 93638-1878 |  | 2012-06-11 | 2012-06-11 13:46 | 2012-06-11 14:13 | BRYANT - 582ANW030040NAAD | 55 | 3.5 | Yes | Yes | 25.3 | 22 | 3.3 | 10370CCA1D874A0EB34984E97C25FFFD |  | R22 | Non-TXV |  | 6.364% | 0.93636 | 12.23% | [5 empty] | Non-TXV | 6.364%
Los Banos | CA | 93635-3170 |  | 2012-05-10 | 2012-05-10 12:40 | 2012-05-10 12:57 | BRYANT - 561AJX0300000ABAA | 72 | 5.8 | Yes | Yes | 20.4 | 21.9 | -1.5 | 8BF4D614F9D74865BEA35EBF3D6D85CF | OK: Verified Refrigerant Charge. |  |  |  | 8.056% | 0.91944 | 15.48% | [5 empty] | 0 | 8.056%
Madera | CA | 93637-5507 |  | 2012-07-05 | 2012-07-05 10:29 | 2012-07-05 10:53 | GOODMAN - GS3130241AE | 93 | 3 | Yes | Yes | 16.7 | 18.8 | -2.1 | D29BABB074CB42889892170D54947BBA |  | R22 | Non-TXV |  | 3.226% | 0.96774 | 6.199% | [5 empty] | Non-TXV | 3.226%
Madera | CA | 93638-1735 |  | 2012-06-11 | 2012-06-11 14:17 | 2012-06-11 14:46 | RUUD - URKA-A030JK08E | 54 | 2 | Yes | Yes | 26.2 | 22.7 | 3.5 | 53242EB508304696A895E78442C5EF64 |  | R22 | Non-TXV |  | 3.704% | 0.96296 | 7.118% | [5 empty] | Non-TXV | 3.704%
Stockton | CA | 95210-1402 |  | 2012-06-06 | 2012-06-06 12:14 | 2012-06-06 12:31 | RHEEM - HC-80-24-21C | 49 | 3.6 | Yes | Yes | 25.1 | 22.1 | 3 | 7D5183BA485246AAA3F4E1001C92E89D |  | R22 | Non-TXV |  | 7.347% | 0.92653 | 14.12% | [5 empty] | Non-TXV | 7.347%
Madera | CA | 93638-1018 |  | 2012-08-10 | 2012-08-10 11:20 | 2012-08-10 12:28 | CARRIER - 48SS033040321 | 54 | 1.8 | Yes | Yes | 20.9 | 17.4 | 3.6 | 55022BCDEF5F426EA69703F65CE39892 |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Stockton | CA | 95206-5212 |  | 2012-08-14 | 2012-08-14 14:06 | 2012-08-14 14:26 | BRYANT - 563CN042-A | 135 | -12.7 | Yes | Yes | 20 | 15.4 | 4.6 | 687876A8038E43B0B6BB96659210C2BC |  | R22 | Non-TXV |  | -9.407% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.407%
Madera | CA | 93637-5518 |  | 2012-07-03 | 2012-07-03 13:00 | 2012-07-03 13:21 | RUUD - 13AJA24A01757 | 66 | 9.5 | Yes | Yes | 22.3 | 21.3 | 1 | 0F85EA5AE28C47D0AB93AAD6466823CF |  | R22 | Non-TXV |  | 14.39% | 0.85606 | 27.66% | [5 empty] | Non-TXV | 14.39%
Stockton | CA | 95209-1657 |  | 2012-05-31 | 2012-05-31 16:49 | 2012-05-31 17:11 | PAYNE - 561AJX036-A | 80 | 4.8 | Yes | Yes | 25.6 | 21 | 4.7 | AFA4331C460A4497BA238E7ED93BF902 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Madera | CA | 93637-5711 |  | 2012-08-09 | 2012-08-09 11:47 | 2012-08-09 12:09 | RUUD - RRGH-05N30JKR | 79 | 2.5 | Yes | Yes | 19.4 | 19.1 | 0.3 | A16032FA68E9481181BF1CB83E61EB82 |  | R22 | Non-TXV |  | 3.165% | 0.96835 | 6.082% | [5 empty] | Non-TXV | 3.165%
Los Banos | CA | 93635-3236 |  | 2012-08-07 | 2012-08-07 10:49 | 2012-08-07 11:14 | AMERICAN STANDARD - YCY036G1MOAB | 129 | 11.3 | Yes | Yes | 22.1 | 20.4 | 1.7 | 1D8D84B5AFDE4CE790A39D4B026FA6EF |  | R22 | Non-TXV |  | 8.76% | 0.9124 | 16.83% | [5 empty] | Non-TXV | 8.76%
Madera | CA | 93638-0741 |  | 2012-08-10 | 2012-08-10 12:54 | 2012-08-10 13:15 | CARRIER - 38CK048320 | 104 | 14.6 | Yes | Yes | 21.5 | 22.9 | -1.4 | C650BC5D49A341C58A6F3FBB969E824D |  | R22 | Non-TXV |  | 14.04% | 0.85962 | 26.98% | [5 empty] | Non-TXV | 14.04%
Stockton | CA | 95212-0000 |  | 2012-08-08 | 2012-08-08 13:24 | 2012-08-08 13:40 | YORK - H1RA042S06G | 84 | 2.7 | Yes | Yes | 26.7 | 21.9 | 4.8 | 65ACF176E3614A89892AD1798A0C5B52 |  | R22 | Non-TXV |  | 3.214% | 0.96786 | 6.177% | [5 empty] | Non-TXV | 3.214%
Madera | CA | 93637-5517 |  | 2012-07-03 | 2012-07-03 10:04 | 2012-07-03 10:04 | ARCOAIRE - NAC018AKA1 | 57 | 0 | Yes | Yes | 17 | 19.9 | -2.9 | 8FFF1D7C54394B47AAA40882B003439A |  | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5517 |  | 2012-07-05 | 2012-07-05 12:03 | 2012-07-05 13:21 | ARCOAIRE - AG018GB3 | 59 | 4.2 | Yes | Yes | 21 | 19.8 | 1.2 | C0B94E4DBA834DF1A8D5FFAE9701036B |  | R22 | Non-TXV |  | 7.119% | 0.92881 | 13.68% | [5 empty] | Non-TXV | 7.119%
Stockton | CA | 95206-0000 |  | 2012-08-07 | 2012-08-07 09:10 | 2012-08-07 09:30 | CARRIER - 38CKC048300 | 105 | 25.6 | Yes | Yes | 18.5 | 19.2 | -0.7 | 236AACE1F2C342CB8AEEF6070D513E55 |  | R22 | Non-TXV |  | 24.38% | 0.75619 | 46.85% | [5 empty] | Non-TXV | 24.38%
Stockton | CA | 95206-6249 |  | 2012-08-16 | 2012-08-16 14:01 | 2012-08-16 14:18 | GOODMAN - CKL60-1 | 115 | 8.4 | Yes | Yes | 23.3 | 20.1 | 3.2 | 10CF13A59F4747A9914E66367A781994 |  | R22 | Non-TXV |  | 7.304% | 0.92696 | 14.04% | [5 empty] | Non-TXV | 7.304%
Stockton | CA | 95206-3711 |  | 2012-05-23 | 2012-05-23 12:37 | 2012-05-23 12:57 | OTHER - NAC036AKA5 | 87 | -5.1 | Yes | Yes | 17.9 | 20.9 | -3 | 70C264398F2C40E8B2921329B62E40A0 |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Stockton | CA | 95205-6400 |  | 2012-07-24 | 2012-07-24 13:59 | 2012-07-24 14:21 | GOODMAN - GPG1324045M41AB | 80 | 10.1 | Yes | Yes | 18.5 | 17.8 | 0.8 | D20B455979D64D679E8B3591A0BCE6C7 |  | R410A | TXV |  | 12.62% | 0.87375 | 24.26% | [5 empty] | TXV | 12.62%
Stockton | CA | 95212-1019 |  | 2012-08-07 | 2012-08-07 15:18 | 2012-08-07 15:37 | ARMSTRONG - MR51-42P1 | 108 | 3.3 | Yes | Yes | 27.8 | 21.9 | 5.9 | 4C47EDC83BDC4925A2A883195E39C1B5 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Shingle Springs | CA | 95682-9570 |  | 2012-08-02 | 2012-08-02 13:36 | 2012-08-02 13:36 | JANITROL - UNK | 88 | 0 | Yes | Yes | 23.7 | 21.5 | 2.2 | E3CAFDF9DD63483F95861B71D30B8CF8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-6850 |  | 2012-08-09 | 2012-08-09 14:34 | 2012-08-09 15:02 | TRANE - 2YCC3036A1096AA | 82 | 5.3 | Yes | Yes | 25.4 | 21.2 | 4.2 | 25CBB0D58D064B0AA413FB8B5D38F559 |  | R22 | Non-TXV |  | 6.463% | 0.93537 | 12.42% | [5 empty] | Non-TXV | 6.463%
Shingle Springs | CA | 95682-7310 |  | 2012-08-07 | 2012-08-07 11:58 | 2012-08-07 12:23 | CARRIER - 38CKC042310 | 82 | 18.6 | Yes | Yes | 17.2 | 19.3 | -2.1 | F568C024B844464CBF3D0C3226700B2F |  | R22 | Non-TXV |  | 22.68% | 0.77317 | 43.59% | [5 empty] | Non-TXV | 22.68%
Stockton | CA | 95210-2301 |  | 2012-05-16 | 2012-05-16 11:46 | 2012-05-16 12:03 | RHEEM - RRNA-B024JK06X | 70 | 2.1 | Yes | Yes | 18.1 | 18.8 | -0.7 | 191F45E5D40A47298A35DFD867666554 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95209-5132 |  | 2012-08-02 | 2012-08-02 15:45 | 2012-08-02 16:11 | PAYNE - 565B036 | 84 | 4.3 | Yes | Yes | 24.6 | 22.3 | 2.3 | 042952DD38094CE195B9EA67FEFC5886 |  | R22 | Non-TXV |  | 5.119% | 0.94881 | 9.838% | [5 empty] | Non-TXV | 5.119%
Paradise | CA | 95969-2969 |  | 2012-08-03 | 2012-08-03 11:22 | 2012-08-03 11:43 | RUUD - UAMB-048JAZ | 169 | -15.9 | Yes | Yes | 22.9 | 19.2 | 3.7 | CED407123CE043B9AE3985C83D351AB3 |  | R22 | Non-TXV |  | -9.408% | 1.0941 | 2.635% |  |  |  |  | Non-TXV |  |  | -9.408%
Paradise | CA | 95969-4019 |  | 2012-05-11 | 2012-05-11 12:20 | 2012-05-11 12:58 | INTERTIHERM - 36 | 70 | 2.8 | Yes | Yes | 22.1 | 22 | 0.1 | A037ABA0136C4089882FB202472F4D4C | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Stockton | CA | 95210-1720 |  | 2012-05-09 | 2012-05-09 14:42 | 2012-05-09 14:42 | ICP - PGC030K060D | 52 | 0 | Yes | Yes | 24.9 | 22.5 | 2.5 | 87C5CB5228E6451598CEF7A448784EE1 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
French Camp | CA | 95231-9712 |  | 2012-07-09 | 2012-07-09 09:40 | 2012-07-09 10:05 | TRANE - 2YCX3042A1096AA | 88 | 3.7 | Yes | Yes | 23.7 | 20.2 | 3.5 | 44DBCEC2DF834AB49C85C2597662AE3E |  | R22 | Non-TXV |  | 4.205% | 0.95795 | 8.08% | [5 empty] | Non-TXV | 4.205%
Lathrop | CA | 95330-9050 |  | 2012-08-09 | 2012-08-09 13:18 | 2012-08-09 13:35 | RHEEM - RAJC-030JAS | 88 | 2.8 | Yes | Yes | 21.9 | 20.6 | 1.3 | 5E1F7D1AF2564478A73C4A7E0D15E2C1 |  | R22 | Non-TXV |  | 3.182% | 0.96818 | 6.115% | [5 empty] | Non-TXV | 3.182%
Atwater | CA | 95301-4429 |  | 2012-08-09 | 2012-08-09 10:25 | 2012-08-09 10:54 | RHEEM - RRNL-B36JK06X | 92 | -5.4 | Yes | Yes | 21.6 | 20.7 | 1 | 9295B0852A8341F39ADABD8AC8B1057D |  | R410A | Non-TXV |  | -5.87% | 1.0587 | 1.644% |  |  |  |  | Non-TXV |  |  | -5.87%
Atwater | CA | 95301-4531 |  | 2012-08-09 | 2012-08-09 14:02 | 2012-08-09 14:02 | COLEMAN - GCGD48S21S2A | 69 | 0 | Yes | Yes | 22.2 | 20.2 | 2 | 4B329D4E60234050BA7D05031706F5C7 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-1125 |  | 2012-08-16 | 2012-08-16 15:26 | 2012-08-16 18:31 | YORK - DAYP-F036N070A | 98 | 5.6 | Yes | Yes | 24.2 | 20.8 | 3.4 | 53BC9CDBD0384B9CB1D310A20B2EA025 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Pollock Pines | CA | 95726-9497 |  | 2012-08-16 | 2012-08-16 09:44 | 2012-08-16 09:44 | LENNOX - GCS16H-311-75-1P | 211 | 0 | Yes | Yes | 23.9 | 20.1 | 3.8 | A603A7FD00D7451FB0AECD9A1D196172 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Lathrop | CA | 95330-9058 |  | 2012-05-15 | 2012-05-15 13:04 | 2012-05-15 13:20 | RHEEM - RAMA-030JAS | 96 | 2.9 | Yes | Yes | 20.7 | 21 | -0.3 | 7BFB6CAE76E24C88BC62843D30A02E71 |  | R22 | Non-TXV |  | 3.021% | 0.96979 | 5.805% | [5 empty] | Non-TXV | 3.021%
Winton | CA | 95388-9501 |  | 2012-08-08 | 2012-08-08 09:35 | 2012-08-08 09:52 | GE - UNK | 65 | -3.8 | Yes | Yes | 21.1 | 21.2 | 0 | 9B09DC7CFBAC4F51A6F5529F55BF5DBE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | -5.846% | 1.0585 | 1.637% |  |  |  |  | Non-TXV |  |  | -5.846%
Tracy | CA | 95377-7930 |  | 2012-06-25 | 2012-06-25 14:12 | 2012-06-25 14:31 | GOODMAN - CKT42-1AB | 125 | 3.8 | Yes | Yes | 19.5 | 20.3 | -0.8 | F8342D0F12474A46934D6F0AFB37D029 |  | R22 | Non-TXV |  | 3.04% | 0.9696 | 5.842% | [5 empty] | Non-TXV | 3.04%
Grass Valley | CA | 95945-0000 |  | 2012-05-08 | 2012-05-08 11:42 | 2012-05-08 12:00 | AMERICAN STANDARD - YCPOO42F1MOAB | 128 | 3.8 | Yes | Yes | 26 | 20.4 | 5.6 | 385DC8EF83304D35AED9419A7891FD20 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.969% | 0.97031 | 5.705% | [5 empty] | Non-TXV | 2.969%
Merced | CA | 95348-2385 |  | 2012-05-17 | 2012-05-17 12:49 | 2012-05-17 13:13 | TRANE - 2TTB3024A1000AA | 82 | 5 | Yes | Yes | 23.9 | 20.4 | 3.5 | 56A2C3C7B36C48CDA9CE126540CB070F |  | R22 | Non-TXV |  | 6.098% | 0.93902 | 11.72% | [5 empty] | Non-TXV | 6.098%
Orosi | CA | 93647-2155 |  | 2012-08-08 | 2012-08-08 14:35 | 2012-08-08 15:15 | GOODMAN - GSC130361DE | 119 | 6.3 | Yes | Yes | 17.6 | 17.1 | 0.5 | A4699B0170FD459BA3D5E4DB9CD5B14B |  | R22 | Non-TXV |  | 5.294% | 0.94706 | 10.17% | [5 empty] | Non-TXV | 5.294%
Merced | CA | 95348-3760 |  | 2012-05-17 | 2012-05-17 14:35 | 2012-05-17 14:57 | TRANE - BTD724A100B0 | 68 | 4.6 | Yes | Yes | 28.5 | 22.5 | 6 | E91AEA04ED884FC4BC9533894CEE91CB |  | R22 | Non-TXV |  | 6.765% | 0.93235 | 13% | [5 empty] | Non-TXV | 6.765%
El Dorado Hills | CA | 95762-3516 |  | 2012-07-20 | 2012-07-20 15:37 | 2012-07-20 15:37 | RHEEM - RQNL-B042JK | 176 | 0 | Yes | Yes | 21.4 | 21.3 | 0.1 | 82FDD884BE99441EA5EFC1363E68AB1C |  | R410A | TXV |  | 0% | 1 | 0%
Atascadero | CA | 93422-5352 |  | 2012-07-11 | 2012-07-11 09:49 | 2012-07-11 10:07 | DAY & NIGHT - UNK | 80 | -4.7 | Yes | Yes | 25.7 | 20.2 | 5.5 | BA1F2F1FD49E4FA79FD5F218B4233910 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Stockton | CA | 95206-3857 |  | 2012-05-23 | 2012-05-23 15:53 | 2012-05-23 16:11 | GOODMAN - CKL49-1 | 90 | 3.5 | Yes | Yes | 22.9 | 21.5 | 1.4 | 15C3D79BCBD74430AF5AF355B3F57E83 |  | R22 | Non-TXV |  | 3.889% | 0.96111 | 7.474% | [5 empty] | Non-TXV | 3.889%
Stockton | CA | 95212-2875 |  | 2012-08-08 | 2012-08-08 16:32 | 2012-08-08 16:32 | YORK - H2RC036S06A | 83 | 0 | Yes | Yes | 22.6 | 22.1 | 0.5 | EB1521A2778D4F3FB77E227A7968933D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Orosi | CA | 93647-9705 |  | 2012-05-09 | 2012-05-09 20:21 | 2012-05-09 20:41 | WEATHERKING - N/A | 120 | 3.8 | Yes | Yes | 16.7 | 20.9 | -4.2 | 1A31DC6F2A1D49B2A1EB223829A8907A | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.167% | 0.96833 | 6.086% | [5 empty] | Non-TXV | 3.167%
Madera | CA | 93637-6122 |  | 2012-08-10 | 2012-08-10 09:34 | 2012-08-10 09:51 | PAYNE - UNK | 68 | 11.8 | Yes | Yes | 22.6 | 23.1 | -0.5 | 7AE008716DA24BDB8E832070F4128DD2 |  | R22 | Non-TXV |  | 17.35% | 0.82647 | 33.35% | [5 empty] | Non-TXV | 17.35%
Orosi | CA | 93647-2156 |  | 2012-08-08 | 2012-08-08 15:49 | 2012-08-08 16:05 | GOODMAN - GSC130361DF | 120 | 3.9 | Yes | Yes | 18.6 | 18.5 | 0.1 | F43E0A75BE784A8FB347C11F908DE8A9 |  | R22 | Non-TXV |  | 3.25% | 0.9675 | 6.246% | [5 empty] | Non-TXV | 3.25%
Stockton | CA | 95204-4139 |  | 2012-08-02 | 2012-08-02 16:03 | 2012-08-03 01:39 | HEIL - PGC030K060A | 52 | 4.3 | Yes | Yes | 21.7 | 20.4 | 1.3 | 855BD3771B124CBAB5437FE3421CD96B |  | R22 | Non-TXV |  | 8.269% | 0.91731 | 15.89% | [5 empty] | Non-TXV | 8.269%
Stockton | CA | 95212-2748 |  | 2012-08-08 | 2012-08-08 17:09 | 2012-08-08 17:26 | CARRIER - 24ABA348A300 | 122 | 9.4 | Yes | Yes | 20.3 | 21.2 | -0.9 | EE161DFCE6654CCBAD9D317B6D424E85 |  | R410A | Non-TXV |  | 7.705% | 0.92295 | 14.81% | [5 empty] | Non-TXV | 7.705%
Selma | CA | 93662-3117 |  | 2012-05-10 | 2012-05-10 15:40 | 2012-05-10 16:00 | RHEEM - 7294F450507A97 | 85 | 4.7 | Yes | Yes | 20.5 | 23.7 | -3.2 | BEDC61871FD94C80850A8B4EC529B271 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Stockton | CA | 95206-2225 |  | 2012-08-14 | 2012-08-14 10:13 | 2012-08-14 10:31 | AMANA - PGC48B0902A | 135 | 4.1 | Yes | Yes | 24 | 21.2 | 2.8 | 91A675B55AD74CFA8EFF94132E2A1CBA |  | R22 | Non-TXV |  | 3.037% | 0.96963 | 5.837% | [5 empty] | Non-TXV | 3.037%
Planada | CA | 95365-0000 |  | 2012-06-06 | 2012-06-06 11:39 | 2012-06-06 12:05 | TRANE - TTN024D100AO | 81 | 6.4 | Yes | Yes | 18.2 | 19.3 | -1.1 | 3A46C2E75A3F402D9DE89685CAD187D6 |  | R22 | Non-TXV |  | 7.901% | 0.92099 | 15.18% | [5 empty] | Non-TXV | 7.901%
Merced | CA | 95340-4948 |  | 2012-05-16 | 2012-05-16 09:47 | 2012-05-16 10:10 | ARI - TCGD24S21SA1 | 64 | 5.6 | Yes | Yes | 26.1 | 20.4 | 5.7 | 9C359512051A44D3B26224B239AA23ED |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Merced | CA | 95340-4902 |  | 2012-05-10 | 2012-05-10 09:56 | 2012-05-10 09:56 | TRANE - BTD72AA100C0 | 85 | 0 | Yes | Yes | 27 | 21.9 | 5.1 | 9ABD2CE2ED9B4C99AFF99C5BA9D43842 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3112 |  | 2012-08-06 | 2012-08-06 16:22 | 2012-08-06 16:49 | PAYNE - PY1PNB036090AAAA | 56 | 2.1 | Yes | Yes | 19.1 | 20.6 | -1.5 | 06307B77DADC43B2A040A8CFBEA2A356 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.75% | 0.9625 | 7.207% | [5 empty] | Non-TXV | 3.75%
Stockton | CA | 95206-3618 |  | 2012-08-14 | 2012-08-14 09:34 | 2012-08-14 09:55 | DAY & NIGHT - 585HJ024040 | 68 | -4.8 | Yes | Yes | 20 | 21 | -1 | C57E688EE14D4458A776E6E39842DEA0 |  | R22 | Non-TXV |  | -7.059% | 1.0706 | 1.977% |  |  |  |  | Non-TXV |  |  | -7.059%
Stockton | CA | 95212-1019 |  | 2012-08-07 | 2012-08-07 14:24 | 2012-08-07 14:43 | CARRIER - 38EA048300 | 90 | 2.6 | Yes | Yes | 26.7 | 21.5 | 5.3 | 1A528CC2DF634DBBBF4E0CC3E3A7D9F9 |  | R22 | Non-TXV |  | 2.889% | 0.97111 | 5.552% | [5 empty] | Non-TXV | 2.889%
Stockton | CA | 95206-3334 |  | 2012-08-14 | 2012-08-14 15:25 | 2012-08-14 15:54 | GOODMAN - GSC130301AE | 117 | 3.5 | Yes | Yes | 22 | 21.2 | 0.8 | E2BBC0C7C1DB4088B901BEB609418666 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.749% | [5 empty] | Non-TXV | 2.991%
Stockton | CA | 95206-2491 |  | 2012-08-08 | 2012-08-08 09:13 | 2012-08-08 09:13 | RHEEM - RRGG-05N25JKR | 39 | 0 | Yes | Yes | 24 | 21 | 3 | 262DAAF971C646B58C0F0E95050647DB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-9067 |  | 2012-08-08 | 2012-08-08 13:24 | 2012-08-08 13:45 | AIRE-FLO - PGAD47D1K8 | 212 | 12.8 | Yes | Yes | 28.4 | 22.5 | 5.9 | C61B91376A254D9DB2FFBFFB8A168C40 |  | R22 | Non-TXV |  | 6.038% | 0.93962 | 11.6% | [5 empty] | Non-TXV | 6.038%
Stockton | CA | 95210-4310 |  | 2012-08-08 | 2012-08-08 11:39 | 2012-08-08 11:57 | BDP - 585B030075YACR | 50 | 1.9 | Yes | Yes | 22.5 | 19.5 | 3 | 8192285467894AB1AAE9520D7CF75E13 |  | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Stockton | CA | 95209-1301 |  | 2012-08-06 | 2012-08-06 10:35 | 2012-08-06 10:52 | GOODMAN - CKL49-A | 112 | 15.7 | Yes | Yes | 15.5 | 17.9 | -2.4 | CE097B160FFE495EB76572A0B5EB4B86 |  | R22 | Non-TXV |  | 14.02% | 0.85982 | 26.94% | [5 empty] | Non-TXV | 14.02%
Stockton | CA | 95210-3335 |  | 2012-08-08 | 2012-08-08 09:47 | 2012-08-08 10:05 | RUUD - UAKA-042JAZ | 79 | -5.6 | Yes | Yes | 25.7 | 19.9 | 5.8 | BA82CEC74140496C9C2364F5EC38606C |  | R22 | Non-TXV |  | -7.089% | 1.0709 | 1.985% |  |  |  |  | Non-TXV |  |  | -7.089%
Madera | CA | 93637-6225 |  | 2012-08-11 | 2012-08-11 01:00 | 2012-08-11 01:18 | CARRIER - 38BRC030320 | 100 | 3 | Yes | Yes | 18 | 18.6 | -0.6 | 3B224D74C35C4467AAE91B34702D85BB |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95209-1905 |  | 2012-08-03 | 2012-08-03 11:48 | 2012-08-03 12:08 | YORK - H2RD036S06B | 96 | 12.2 | Yes | Yes | 22.6 | 18.8 | 3.9 | C9CD6375B6484842A8D72D489AEE5E3F |  | R22 | Non-TXV |  | 12.71% | 0.87292 | 24.42% | [5 empty] | Non-TXV | 12.71%
Stockton | CA | 95207-2018 |  | 2012-08-10 | 2012-08-10 11:58 | 2012-08-10 12:19 | RHEEM - RAFD-036JAS | 80 | 12.2 | Yes | Yes | 15.5 | 18.3 | -2.7 | 1EF2EA648186456E96E6EC248EB7A265 |  | R22 | Non-TXV |  | 15.25% | 0.8475 | 29.31% | [5 empty] | Non-TXV | 15.25%
Stockton | CA | 95205-2520 |  | 2012-08-07 | 2012-08-07 10:22 | 2012-08-07 10:38 | GOODMAN - KL60-1L | 115 | 4.2 | Yes | Yes | 19 | 19.9 | -0.9 | 71AB992343C2438FA294076689224C4A |  | R22 | Non-TXV |  | 3.652% | 0.96348 | 7.019% | [5 empty] | Non-TXV | 3.652%
Tracy | CA | 95376-5403 |  | 2012-08-08 | 2012-08-08 15:00 | 2012-08-08 15:48 | TRANE - TTR742A100A0 | 138 | 11.3 | Yes | Yes | 24.6 | 21 | 3.6 | BB451BA4FE16495394443FC3CB9C4764 |  | R22 | Non-TXV |  | 8.188% | 0.91812 | 15.74% | [5 empty] | Non-TXV | 8.188%
Stockton | CA | 95209-2253 |  | 2012-08-06 | 2012-08-06 16:53 | 2012-08-06 18:43 | GE - BGTA736B1B | 96 | 12 | Yes | Yes | 18.7 | 19.7 | -1 | 43E57DC9A8044175AABEE92A555AA75C |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Oroville | CA | 95965-4715 |  | 2012-07-18 | 2012-07-18 13:06 | 2012-07-18 16:43 | - NA | 82 | 4.5 | Yes | Yes | 18.9 | 21.5 | -2.6 | 664E513397BB4A36B2C36B534587BA8B |  | R22 | Non-TXV |  | 5.488% | 0.94512 | 10.55% | [5 empty] | Non-TXV | 5.488%
Atwater | CA | 95301-2738 |  | 2012-08-07 | 2012-08-07 09:17 | 2012-08-07 09:45 | PAYNE - 36/100YAC108C | 66 | 2.7 | Yes | Yes | 22 | 20.4 | 1.6 | EC0772BD29224546848693BE7947B126 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.091% | 0.95909 | 7.862% | [5 empty] | Non-TXV | 4.091%
Oroville | CA | 95966-6324 |  | 2012-08-10 | 2012-08-10 17:00 | 2012-08-10 17:18 | GOODMAN - GS4160813C140361AE | 149 | 4.5 | Yes | Yes | 25.1 | 21.1 | 4 | ED12B20BBE4C431287006B75016F65C7 |  | R22 | Non-TXV |  | 3.02% | 0.9698 | 5.804% | [5 empty] | Non-TXV | 3.02%
Gustine | CA | 95322-1752 |  | 2012-08-14 | 2012-08-14 11:36 | 2012-08-14 12:00 | RHEEM - UNK | 74 | 5.6 | Yes | Yes | 20.8 | 19.8 | 1 | F0C040BA09FC458CB191BD33B9A2ED89 |  | R22 | Non-TXV |  | 7.568% | 0.92432 | 14.54% | [5 empty] | Non-TXV | 7.568%
Merced | CA | 95348-3519 |  | 2012-08-03 | 2012-08-03 09:59 | 2012-08-03 10:23 | GE - BTR948A100A0 | 144 | 7.1 | Yes | Yes | 18.2 | 19.7 | -1.5 | DE294518B66B432E8B04E318E30F4539 |  | R22 | Non-TXV |  | 4.931% | 0.95069 | 9.475% | [5 empty] | Non-TXV | 4.931%
Merced | CA | 95348-1409 |  | 2012-08-13 | 2012-08-13 10:06 | 2012-08-13 10:33 | CARRIER - 48GSN03006030 | 59 | 2.4 | Yes | Yes | 18.9 | 19.8 | -0.9 | 840EC91DB18544B5A4889B23CAC6D27C |  | R22 | Non-TXV |  | 4.068% | 0.95932 | 7.817% | [5 empty] | Non-TXV | 4.068%
Newman | CA | 95360-1417 |  | 2012-08-14 | 2012-08-14 10:06 | 2012-08-14 10:24 | YORK - 024S06A | 81 | -4.8 | Yes | Yes | 20.8 | 18.2 | 2.6 | A6B2EA4F1E4A4E4E946951A6F2FEAD0E |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Livingston | CA | 95334-1615 |  | 2012-05-16 | 2012-05-16 12:00 | 2012-05-16 12:18 | CARRIER - 38BRC030310 | 116 | 3.4 | Yes | Yes | 21.7 | 19 | 2.7 | 3F72A395AD5A46E29E1E2D20138D7441 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.931% | 0.97069 | 5.633% | [5 empty] | Non-TXV | 2.931%
Atwater | CA | 95301-3822 |  | 2012-07-02 | 2012-07-02 11:25 | 2012-07-02 11:49 | AMERICAN STANDARD - 2YCX3030A1064AA | 88 | 2.6 | Yes | Yes | 19.5 | 18.1 | 1.4 | 90EEBDB5A8FD4066A7BEF0AA00EA3568 |  | R22 | Non-TXV |  | 2.955% | 0.97045 | 5.678% | [5 empty] | Non-TXV | 2.955%
Stockton | CA | 95209-4249 |  | 2012-05-16 | 2012-05-16 10:37 | 2012-05-16 10:37 | CARRIER - 38CKC042---351-- | 93 | 0 | Yes | Yes | 18 | 20.4 | -2.4 | A655A4C38B5C4133B572DA6C082A03CC | OK: Verified Refrigerant Charge | R22 | TXV |  | 0% | 1 | 0%
Merced | CA | 95341-5500 |  | 2012-08-07 | 2012-08-07 11:07 | 2012-08-07 11:27 | OTHER - GS3BA-0368A | 69 | 3.7 | Yes | Yes | 24.4 | 19.8 | 4.6 | C68CBE821101418FBCA4DB7277A5D136 |  | R22 | Non-TXV |  | 5.362% | 0.94638 | 10.31% | [5 empty] | Non-TXV | 5.362%
Gustine | CA | 95322-1511 |  | 2012-08-13 | 2012-08-13 09:44 | 2012-08-13 10:06 | RHEEM - RRMA-A030JK06X | 80 | -5.6 | Yes | Yes | 25 | 21.5 | 3.5 | 4441C7BBAB8D4861A146425613C84C48 |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Fresno | CA | 93726-3639 |  | 2012-05-10 | 2012-05-10 10:53 | 2012-05-10 11:13 | BRYANT - 589ANW036080ACBF | 84 | 2.5 | Yes | Yes | 22.8 | 20.8 | 2 | 3D6037D7F18349F585A83AA6C7A1BDE3 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Stockton | CA | 95206-5838 |  | 2012-08-15 | 2012-08-15 09:28 | 2012-08-15 09:49 | OTHER - 561CJ030-B | 75 | 6.2 | Yes | Yes | 18 | 20.4 | -2.4 | C2393568EADB4CEC8E137748A1799A54 |  | R22 | Non-TXV |  | 8.267% | 0.91733 | 15.89% | [5 empty] | Non-TXV | 8.267%
Atwater | CA | 95301-4022 |  | 2012-08-16 | 2012-08-16 10:30 | 2012-08-16 10:58 | ARCOAIRE - PGC036K060E | 68 | 2 | Yes | Yes | 19.7 | 21.2 | -1.5 | 8EA3678D9F9849E5B0420F9E8323F563 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Atwater | CA | 95301-3621 |  | 2012-08-15 | 2012-08-15 08:55 | 2012-08-15 09:10 | LENNOX - PGE10A36D075-1PA | 75 | -2.8 | Yes | Yes | 22 | 18.2 | 3.8 | 831BC0DF94AD4C3B986071255D9239E3 |  | R22 | TXV |  | -3.733% | 1.0373 | 1.046% |  |  |  |  | TXV |  |  | -3.733%
Newman | CA | 95360-2422 |  | 2012-08-08 | 2012-08-08 15:30 | 2012-08-08 15:46 | TRANE - H2RD036S06B | 99 | 8.6 | Yes | Yes | 19.4 | 20.8 | -1.4 | A2912ABF94284A19AEAE9E0041A1D519 |  | R22 | Non-TXV |  | 8.687% | 0.91313 | 16.69% | [5 empty] | Non-TXV | 8.687%
Gustine | CA | 95322-1320 |  | 2012-08-13 | 2012-08-13 08:55 | 2012-08-13 09:23 | OTHER - TZAA-336-2A | 108 | -6.4 | Yes | Yes | 24.4 | 20.4 | 4 | 6F6018107EFA4810A8373B375D2D2D3C |  | R22 | Non-TXV |  | -5.926% | 1.0593 | 1.66% |  |  |  |  | Non-TXV |  |  | -5.926%
Newman | CA | 95360-1811 |  | 2012-08-08 | 2012-08-08 13:13 | 2012-08-08 13:13 | PAYNE - UNK | 77 | 0 | Yes | Yes | 18.7 | 21 | -2.3 | 0E13A7D5D28E4B97BA6E8AD383E6929B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93711-2904 |  | 2012-06-15 | 2012-06-15 14:14 | 2012-06-15 14:32 | DAY & NIGHT - 24/60YAC-108T | 54 | 1.6 | Yes | Yes | 22.4 | 19.6 | 2.8 | 2618F31D70FD4837B2E20431A04E6BE7 |  | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Madera | CA | 93637-8840 |  | 2012-08-13 | 2012-08-13 09:39 | 2012-08-13 10:30 | CARRIER - 48SDN036060301 | 167 | 11.6 | Yes | Yes | 22.1 | 23.4 | -1.3 | 74FB9DE6B4CD45B88769FD85C88FE0F5 |  | R22 | Non-TXV |  | 6.946% | 0.93054 | 13.35% | [5 empty] | Non-TXV | 6.946%
Los Banos | CA | 93635-3604 |  | 2012-08-07 | 2012-08-07 13:34 | 2012-08-07 13:50 | RUUD - UAJC042JAS | 99 | 12.8 | Yes | Yes | 22 | 20.6 | 1.4 | F9226AEB09DF46359C898AF7F5E2A794 |  | R22 | Non-TXV |  | 12.93% | 0.87071 | 24.85% | [5 empty] | Non-TXV | 12.93%
Stockton | CA | 95207-1119 |  | 2012-05-31 | 2012-05-31 10:32 | 2012-05-31 10:52 | FRESCHI - 60WR24E1NA | 56 | 7.4 | Yes | Yes | 18.4 | 20.1 | -1.7 | 8739F004A54A4A8E82D6B059C1BF893D |  | R22 | Non-TXV |  | 13.21% | 0.86786 | 25.39% | [5 empty] | Non-TXV | 13.21%
Fresno | CA | 93722-4012 |  | 2012-05-18 | 2012-05-18 11:05 | 2012-05-18 11:23 | CARRIER - UNK | 70 | -4.1 | Yes | Yes | 17.7 | 20.6 | -2.9 | 0DD5704C41A44730AE494AF152820298 |  | R22 | Non-TXV |  | -5.857% | 1.0586 | 1.64% |  |  |  |  | Non-TXV |  |  | -5.857%
Stockton | CA | 95210-1320 |  | 2012-08-03 | 2012-08-03 10:39 | 2012-08-03 10:59 | GE - BGTA836R1C | 94 | -5.5 | Yes | Yes | 21.3 | 18.5 | 2.8 | C7709888AFB94024820AD4B590F81435 |  | R22 | Non-TXV |  | -5.851% | 1.0585 | 1.639% |  |  |  |  | Non-TXV |  |  | -5.851%
Merced | CA | 95340-2736 |  | 2012-05-07 | 2012-05-07 15:39 | 2012-05-07 16:07 | AMANA - RCB362B | 85 | 3 | Yes | Yes | 25.5 | 22.4 | 3.1 | 208FEC76ADDA4485927290D6929982B9 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Stockton | CA | 95210-1246 |  | 2012-05-11 | 2012-05-11 09:16 | 2012-05-11 09:32 | RHEEM - RRMA-A030JK06X | 80 | -4.7 | Yes | Yes | 20.5 | 19.4 | 1.1 | 87D76784F63F4063888CA34437845BE8 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Atwater | CA | 95301-4120 |  | 2012-08-15 | 2012-08-15 15:32 | 2012-08-15 15:49 | GOODMAN - GPG13360701AC | 112 | 3.4 | Yes | Yes | 20.8 | 18.5 | 2.3 | 24E39CCB0AF34498BD72BB5E4FE20889 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Dos Palos | CA | 93620-2211 |  | 2012-05-31 | 2012-05-31 11:25 | 2012-05-31 11:43 | GOODMAN - UNK | 79 | 8.6 | Yes | Yes | 22.6 | 22.1 | 0.5 | 349583E9663444DF96CD671401153601 |  | R22 | Non-TXV |  | 10.89% | 0.89114 | 20.92% | [5 empty] | Non-TXV | 10.89%
Merced | CA | 95341-7705 |  | 2012-05-29 | 2012-05-29 12:32 | 2012-05-29 12:52 | AIRE-FLO - UNK | 85 | 12.7 | Yes | Yes | 18.2 | 19.8 | -1.6 | CA4EF5E59BC141DE881215E98DEE013A |  | R22 | Non-TXV |  | 14.94% | 0.85059 | 28.71% | [5 empty] | Non-TXV | 14.94%
Madera | CA | 93638-3420 |  | 2012-06-12 | 2012-06-12 13:29 | 2012-06-12 13:46 | RHEEM - UNK | 69 | 3 | Yes | Yes | 19.1 | 20.4 | -1.3 | D6BE68A4DB0C4A469E46AC541D5CE634 |  | R22 | Non-TXV |  | 4.348% | 0.95652 | 8.356% | [5 empty] | Non-TXV | 4.348%
Lodi | CA | 95240-6830 |  | 2012-08-16 | 2012-08-16 15:48 | 2012-08-16 16:05 | YORK - TCGD36S41S3HA | 73 | 2.3 | Yes | Yes | 21.1 | 19.8 | 1.3 | 6C929BE663584BBBB7521EB9C1F9058D |  | R410A | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Manteca | CA | 95336-3461 |  | 2012-05-07 | 2012-05-07 14:08 | 2012-05-07 20:54 | AMANA - ZRCF30U01D | 118 | 12.3 | Yes | Yes | 26.9 | 22.4 | 4.5 | A69AF00F833F48759D36B3043A05AE38 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 10.42% | 0.89576 | 20.03% | [5 empty] | Non-TXV | 10.42%
Merced | CA | 95340-3246 |  | 2012-05-07 | 2012-05-07 13:08 | 2012-05-07 13:08 | YORK - D1NP042N06506A | 150 | 0 | Yes | Yes | 24.5 | 19 | 5.5 | 357F02619B474995AAA50BBDBF7644C8 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-6011 |  | 2012-08-07 | 2012-08-07 08:46 | 2012-08-07 09:04 | PAYNE - 30RCUH108C | 117 | 13.5 | Yes | Yes | 15.7 | 18.6 | -2.9 | 45C6A73AB2CA492F95BA508AFFB0F21D |  | R22 | Non-TXV |  | 11.54% | 0.88462 | 22.17% | [5 empty] | Non-TXV | 11.54%
Stockton | CA | 95206-1243 |  | 2012-05-07 | 2012-05-07 15:19 | 2012-05-07 15:39 | PAYNE - PA13NR030-H | 75 | 5.8 | Yes | Yes | 19.5 | 21.9 | -2.4 | 258D0CB1C85243DCB57629E889FB41E9 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.733% | 0.92267 | 14.86% | [5 empty] | Non-TXV | 7.733%
Atwater | CA | 95301-4879 |  | 2012-06-14 | 2012-06-14 09:49 | 2012-06-14 10:10 | RHEEM - RAFA-030JA | 59 | 3.5 | Yes | Yes | 21 | 20 | 1.1 | C5F43DE82BA44E84B3216856F4CE6630 |  | R22 | Non-TXV |  | 5.932% | 0.94068 | 11.4% | [5 empty] | Non-TXV | 5.932%
Merced | CA | 95340-1557 |  | 2012-08-08 | 2012-08-08 16:28 | 2012-08-08 16:48 | AIRE-FLO - RRKAA42JK08X | 69 | 8.5 | Yes | Yes | 23.5 | 24.2 | -0.7 | 784EB7D3C2364C3BBE7B2C1AA30B155B |  | R22 | Non-TXV |  | 12.32% | 0.87681 | 23.67% | [5 empty] | Non-TXV | 12.32%
Stockton | CA | 95210-1157 |  | 2012-05-21 | 2012-05-21 15:33 | 2012-05-21 15:51 | HIUGH EFFICIENCY - CA553OVKD2 | 74 | 8.9 | Yes | Yes | 22.5 | 21.3 | 1.2 | 3F45FFE7B79044C9A451774E35D4BAC1 |  | R22 | Non-TXV |  | 12.03% | 0.87973 | 23.11% | [5 empty] | Non-TXV | 12.03%
Stockton | CA | 95212-1123 |  | 2012-08-09 | 2012-08-09 15:24 | 2012-08-09 15:41 | GE - BGTA742B1B | 101 | 30.5 | Yes | Yes | 15.9 | 18.1 | -2.2 | 7B318C1F118D46B88E4E056C21AB88CD |  | R22 | Non-TXV |  | 30.2% | 0.69802 | 58.03% | [5 empty] | Non-TXV | 30.2%
Fresno | CA | 93722-4552 |  | 2012-05-31 | 2012-05-31 13:04 | 2012-05-31 13:22 | GOODMAN - GPG1324045M41AD | 84 | 2.5 | Yes | Yes | 17.9 | 18.5 | -0.6 | 1B2476037E7047D2A0C4FA3F118F795B |  | R410A | Non-TXV |  | 2.976% | 0.97024 | 5.72% | [5 empty] | Non-TXV | 2.976%
Merced | CA | 95340-2354 |  | 2012-05-07 | 2012-05-07 16:25 | 2012-05-07 16:47 | TRANE - BRD724A100CO | 85 | 3.8 | Yes | Yes | 21.4 | 23.3 | -1.9 | 1B12909217E243A9ACCC435AEF2E0212 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Stockton | CA | 95207-2107 |  | 2012-08-07 | 2012-08-07 10:51 | 2012-08-07 11:08 | HEIL - CA5536VKD2 | 82 | -7.7 | Yes | Yes | 16 | 17.5 | -1.5 | ECBB0758D58542F8B152D86548182126 |  | R22 | Non-TXV |  | -9.39% | 1.0939 | 2.63% |  |  |  |  | Non-TXV |  |  | -9.39%
Atwater | CA | 95301-4829 |  | 2012-08-10 | 2012-08-10 13:33 | 2012-08-10 13:54 | GUARDIAN - GCGD36S21S2B | 75 | 6.6 | Yes | Yes | 14 | 16.6 | -2.6 | 219072667679440D9E061AF488D10B4C |  | R22 | Non-TXV |  | 8.8% | 0.912 | 16.91% | [5 empty] | Non-TXV | 8.8%
Stockton | CA | 95205-2471 |  | 2012-08-07 | 2012-08-07 10:39 | 2012-08-07 10:57 | GOODMAN - CKL36-1K | 84 | 5.3 | Yes | Yes | 20.3 | 20.4 | -0.1 | 72DE8C7C762C4760B119A4C9ED84E84F |  | R22 | Non-TXV |  | 6.31% | 0.9369 | 12.13% | [5 empty] | Non-TXV | 6.31%
Fresno | CA | 93726-0715 |  | 2012-05-09 | 2012-05-09 14:39 | 2012-05-09 14:39 | HEIL - NRGF42DDB04 | 90 | 0 | Yes | Yes | 27.9 | 22.4 | 5.5 | 2BB06F8DA21349FBA0FF382E75802955 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95215-7352 |  | 2012-08-08 | 2012-08-08 12:32 | 2012-08-08 12:55 | DAY & NIGHT - 10AN030040 | 72 | 9 | Yes | Yes | 20.6 | 22 | -1.4 | 9A3463BD6E694BB2AE97DEAC01780ACD |  | R22 | Non-TXV |  | 12.5% | 0.875 | 24.02% | [5 empty] | Non-TXV | 12.5%
Stockton | CA | 95215-7555 |  | 2012-08-08 | 2012-08-08 14:17 | 2012-08-08 14:34 | PAYNE - PY1PNB030060AAAA | 55 | 2.3 | Yes | Yes | 17.9 | 20.3 | -2.3 | 4339B4992FA44600AA9CB29E83C7F895 |  | R22 | Non-TXV |  | 4.182% | 0.95818 | 8.037% | [5 empty] | Non-TXV | 4.182%
Atwater | CA | 95301-3808 |  | 2012-05-10 | 2012-05-10 10:50 | 2012-05-10 11:08 | RHEEM - RRNA-B036JK06X | 83 | 2.4 | Yes | Yes | 24 | 20.9 | 3.1 | A75DBF496F5043D28D95B941452A3667 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.892% | 0.97108 | 5.557% | [5 empty] | Non-TXV | 2.892%
Fresno | CA | 93727-1957 |  | 2012-05-07 | 2012-05-07 15:53 | 2012-05-07 22:20 | BRYANT - 582ANW042090NAAG | 100 | 0 | Yes | Yes | 13.6 | 25.3 | -11.7 | 5CF95F0FA85C4A35A51D4B7BA519F30F |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93726-2225 |  | 2012-05-11 | 2012-05-11 12:42 | 2012-05-11 13:02 | AMERICA STANDARD - UNK | 65 | 2 | Yes | Yes | 17.1 | 19.9 | -2.8 | 81AE440588DD49E0AD94CE107D09FA91 |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Stockton | CA | 95206-1837 |  | 2012-08-07 | 2012-08-07 12:06 | 2012-08-07 12:29 | DAY & NIGHT - 588ANW030060ABAD | 55 | 4.4 | Yes | Yes | 17 | 19.2 | -2.2 | 2D40F5F264934ABBA25B41C1328214E1 |  | R22 | Non-TXV |  | 8% | 0.92 | 15.37% | [5 empty] | Non-TXV | 8%
Madera | CA | 93638-2699 |  | 2012-06-12 | 2012-06-12 14:30 | 2012-06-12 14:48 | GOODMAN - PGB030075-1 | 56 | 1.7 | Yes | Yes | 19.4 | 20.4 | -1 | 0E5534A4E8794CF4AD7FD07C6495DAA2 |  | R22 | Non-TXV |  | 3.036% | 0.96964 | 5.834% | [5 empty] | Non-TXV | 3.036%
Madera | CA | 93638-9303 |  | 2012-08-10 | 2012-08-10 14:55 | 2012-08-10 17:08 | CARRIER - 38ETG030300 | 136 | 4.4 | Yes | Yes | 18.4 | 19.3 | -0.9 | 0F6B7835FD73418084A32B286D9C14DE |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Sanger | CA | 93657-2760 |  | 2012-06-11 | 2012-06-11 10:28 | 2012-06-11 10:45 | RHEEM - RRKA-A024JK06X | 50 | 1.8 | Yes | Yes | 20.9 | 21 | -0.1 | 128C7AAC626E4FF59097FF3404D90313 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.6% | 0.964 | 6.918% | [5 empty] | Non-TXV | 3.6%
Sanger | CA | 93657-3574 |  | 2012-05-22 | 2012-05-22 10:32 | 2012-05-22 18:34 | UNITARY PRODUCTS GROUP - H2RCO36S06G | 83 | 3.4 | Yes | Yes | 23.2 | 19.4 | 3.8 | E077CCF1F4F74DCAA5EA179B99D25DC1 |  | R22 | Non-TXV |  | 4.096% | 0.95904 | 7.872% | [5 empty] | Non-TXV | 4.096%
Fresno | CA | 93727-3251 |  | 2012-05-16 | 2012-05-16 13:18 | 2012-05-16 13:35 | YORK - D3Y5036N04506B | 78 | 2.3 | Yes | Yes | 26.5 | 20.6 | 5.9 | 58776B514A8C4FDDBF89EC1411BA37AC | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Los Banos | CA | 93635-3241 |  | 2012-05-11 | 2012-05-11 11:34 | 2012-05-11 12:00 | BRYANT - UNK | 85 | 4.7 | Yes | Yes | 22.7 | 20.7 | 2 | C26B128B29074BC48061ABC34D5997F5 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.529% | 0.94471 | 10.63% | [5 empty] | Non-TXV | 5.529%
Madera | CA | 93637-8824 |  | 2012-08-10 | 2012-08-10 10:36 | 2012-08-10 10:52 | CARRIER - 48GX042060311 | 118 | 11.5 | Yes | Yes | 21.8 | 21.2 | 0.6 | E110767743084C72BAD79765DADFA713 |  | R22 | Non-TXV |  | 9.746% | 0.90254 | 18.73% | [5 empty] | Non-TXV | 9.746%
Stockton | CA | 95207-2427 |  | 2012-08-06 | 2012-08-06 09:37 | 2012-08-06 09:55 | CARRIER - 38TDB036300 | 137 | 5.2 | Yes | Yes | 23.5 | 18.6 | 5 | E61066DEB9BF4D7FAFB67C6B4BE0C344 |  | R410A | TXV |  | 3.796% | 0.96204 | 7.294% | [5 empty] | TXV | 3.796%
Stockton | CA | 95206-6125 |  | 2012-05-11 | 2012-05-11 12:54 | 2012-05-11 12:54 | GOODMAN - CKJ30-1A | 93 | 0 | Yes | Yes | 20.3 | 22.1 | -1.8 | 05040F96400548DC9046038AAB06657F | OK: Verified Refrigerant Charge | R22 | TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3609 |  | 2012-05-07 | 2012-05-07 14:47 | 2012-05-07 14:47 | GOODMAN - PGB0240751 | 54 | 0 | Yes | Yes | 19 | 21.5 | -2.5 | 753E37A81FAA4F9094419531505C14D6 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-3805 |  | 2012-05-23 | 2012-05-23 13:12 | 2012-05-23 13:33 | DAY & NIGHT - 588ANW036060ADAF | 67 | 4.9 | Yes | Yes | 21.6 | 22 | -0.4 | 344C71441360425E9DD667C080990DA1 |  | R22 | Non-TXV |  | 7.313% | 0.92687 | 14.05% | [5 empty] | Non-TXV | 7.313%
Williams | CA | 95987-0000 |  | 2012-08-06 | 2012-08-06 14:39 | 2012-08-06 14:58 | - YCC024F1L0BA | 64 | 14.5 | Yes | Yes | 17.6 | 19.7 | -2.1 | 767F2944D6C746409C7C09F05A9440CB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 22.66% | 0.77344 | 43.54% | [5 empty] | Non-TXV | 22.66%
Stockton | CA | 95207-4432 |  | 2012-06-22 | 2012-06-22 08:10 | 2012-06-22 08:27 | OTHER - PGE10B36D075LA-3A | 58 | -5.5 | Yes | Yes | 22.9 | 19.8 | 3.1 | 3A0BEEB00F194B65BC173425DDE43A25 |  | R22 | Non-TXV |  | -9.483% | 1.0948 | 2.656% |  |  |  |  | Non-TXV |  |  | -9.483%
Madera | CA | 93637-4817 |  | 2012-08-09 | 2012-08-09 12:13 | 2012-08-09 16:38 | CARRIER - UNK | 80 | 0 | Yes | Yes | 16.4 | 18.6 | -2.2 | CD7A530B6EC44F869FB30FD76C78ECF1 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Livingston | CA | 95334-9465 |  | 2012-05-29 | 2012-05-29 10:37 | 2012-05-29 10:54 | CARRIER - 591ANX024000AAAA | 51 | 3.5 | Yes | Yes | 18.5 | 20.3 | -1.8 | CABD8D7C035D4EED958A0F8927B05372 |  | R22 | Non-TXV |  | 6.863% | 0.93137 | 13.19% | [5 empty] | Non-TXV | 6.863%
Madera | CA | 93637-8826 |  | 2012-05-17 | 2012-05-17 15:57 | 2012-05-17 16:41 | CARRIER - 48GX-042060311 | 85 | 2.6 | Yes | Yes | 26 | 23.3 | 2.7 | 15B1EDFDCB534626ACFBDE75F9843AED |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Merced | CA | 95348-2024 |  | 2012-05-11 | 2012-05-11 13:25 | 2012-05-11 13:52 | CARRIER - 48GS-042060301 | 100 | -5.9 | Yes | Yes | 22.2 | 20.4 | 1.8 | 002CE388AE6B495DBA16C9A784771725 |  | R22 | Non-TXV |  | -5.9% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.9%
Livingston | CA | 95334-9580 |  | 2012-08-10 | 2012-08-10 09:34 | 2012-08-10 09:59 | RUUD - UNK | 67 | 3.2 | Yes | Yes | 18.7 | 17.7 | 1 | 4E9C246B62E349F18302E23E2FDDA194 |  | R22 | Non-TXV |  | 4.776% | 0.95224 | 9.179% | [5 empty] | Non-TXV | 4.776%
Atwater | CA | 95301-4891 |  | 2012-05-08 | 2012-05-08 13:39 | 2012-05-08 14:00 | LENNEX - HS9-311-3F | 77 | 8.5 | Yes | Yes | 21.6 | 21.4 | 0.2 | E9DCD589B17F4041B89371B784A930A7 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 11.04% | 0.88961 | 21.21% | [5 empty] | Non-TXV | 11.04%
Merced | CA | 95348-1627 |  | 2012-07-06 | 2012-07-06 11:28 | 2012-07-06 12:03 | TRANE - 4YCC3024AA1064AAAA | 85 | 4.1 | Yes | Yes | 20.1 | 19.7 | 0.4 | 6682EB2B980F4BF680CB196251040B0B |  | R410A | Non-TXV |  | 4.824% | 0.95176 | 9.27% | [5 empty] | Non-TXV | 4.824%
Manteca | CA | 95337-6501 |  | 2012-08-15 | 2012-08-15 12:04 | 2012-08-15 12:32 | HEIL - CA5542VKD2 | 98 | 2.9 | Yes | Yes | 25.9 | 20.6 | 5.3 | D46F5412D10D4DC5BCCBAC62E4D81813 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.959% | 0.97041 | 5.687% | [5 empty] | Non-TXV | 2.959%
Orland | CA | 95963-1517 |  | 2012-05-17 | 2012-05-17 11:29 | 2012-05-17 11:57 | PAYNE - PA11JA036-C | 73 | 10.8 | Yes | Yes | 22.8 | 22 | 0.8 | 6A376BE486EF4F81A28CC56E84EA28AF |  | R22 | Non-TXV |  | 14.79% | 0.85205 | 28.43% | [5 empty] | Non-TXV | 14.79%
Stockton | CA | 95206-6110 |  | 2012-08-15 | 2012-08-15 14:12 | 2012-08-15 14:45 | RUUD - UAMA-030JBZ | 96 | 5.8 | Yes | Yes | 18.9 | 19.7 | -0.8 | A4E785A316D749F3AD7192D355769ECA |  | R22 | Non-TXV |  | 6.042% | 0.93958 | 11.61% | [5 empty] | Non-TXV | 6.042%
Merced | CA | 95340-3069 |  | 2012-05-07 | 2012-05-07 11:56 | 2012-05-07 11:56 | RHEEM - RAND-060JAZ | 176 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | 7FD37317911E41EA9D33E7A4DA2730AC | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-3420 |  | 2012-05-30 | 2012-05-30 16:08 | 2012-05-30 16:27 | YORK - H2RA030S06A | 62 | 2.2 | Yes | Yes | 18.1 | 19.3 | -1.2 | 9B4A96CDDB714F41B4417D8100C44BD2 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.548% | 0.96452 | 6.819% | [5 empty] | Non-TXV | 3.548%
Stockton | CA | 95209-2123 |  | 2012-05-17 | 2012-05-17 13:02 | 2012-05-17 13:22 | RHEEM - RRKA-A030JK08E | 54 | 7.8 | Yes | Yes | 20.4 | 20.2 | 0.2 | 2709D143178F4CEFBABD64014B083B8B |  | R22 | Non-TXV |  | 14.44% | 0.85556 | 27.76% | [5 empty] | Non-TXV | 14.44%
Merced | CA | 95348-1550 |  | 2012-07-03 | 2012-07-03 11:00 | 2012-07-03 11:30 | AMERICAN STANDARD - YCC024F1LOBH | 66 | 2.8 | Yes | Yes | 19.7 | 21.4 | -1.7 | 89E656AB88B7481784D392455C72BC33 |  | R22 | Non-TXV |  | 4.242% | 0.95758 | 8.153% | [5 empty] | Non-TXV | 4.242%
Merced | CA | 95340-2409 |  | 2012-08-03 | 2012-08-03 12:40 | 2012-08-03 13:00 | RHEEM - UNK | 74 | 3.8 | Yes | Yes | 22.5 | 20.2 | 2.3 | 81951DFD0E734CACBCD957122B2D821A |  | R22 | Non-TXV |  | 5.135% | 0.94865 | 9.869% | [5 empty] | Non-TXV | 5.135%
Stockton | CA | 95206-4677 |  | 2012-08-13 | 2012-08-13 13:58 | 2012-08-13 14:19 | OTHER - 563CN036-B | 85 | 2.6 | Yes | Yes | 20 | 21 | -1 | C20CA7DC4CD740C78DFE3B524060AF11 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Livingston | CA | 95334-9452 |  | 2012-06-07 | 2012-06-07 10:02 | 2012-06-07 10:23 | AMERICAN STANDARD - 2TTX4036A1000AA | 118 | 3.5 | Yes | Yes | 23.9 | 19.3 | 4.6 | FC0407F07CC8428FA0EB74C6EB41E2A4 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Manteca | CA | 95337-5172 |  | 2012-08-10 | 2012-08-10 09:49 | 2012-08-10 10:19 | PAYNE - 565EJ024-A | 70 | 13.9 | Yes | Yes | 16.8 | 19.8 | -3 | AF7336ABD0894E09B520DCA6F3FB176E | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 19.86% | 0.80143 | 38.16% | [5 empty] | Non-TXV | 19.86%
Livingston | CA | 95334-9458 |  | 2012-08-09 | 2012-08-09 09:32 | 2012-08-09 10:02 | CARRIER - 591ANX036000AAAA | 84 | 3 | Yes | Yes | 20.3 | 19.8 | 0.5 | 53418D7EF36E4570B36B56ACB113A5E9 |  | R22 | Non-TXV |  | 3.571% | 0.96429 | 6.864% | [5 empty] | Non-TXV | 3.571%
Stockton | CA | 95209-1323 |  | 2012-08-02 | 2012-08-02 13:07 | 2012-08-02 13:27 | PAYNE - 5670042RCL | 58 | 10.4 | Yes | Yes | 25.9 | 20.3 | 5.6 | D54FA31DBC7F439F8672170699EA463B |  | R22 | Non-TXV |  | 17.93% | 0.82069 | 34.46% | [5 empty] | Non-TXV | 17.93%
Manteca | CA | 95336-6230 |  | 2012-08-10 | 2012-08-10 11:31 | 2012-08-10 11:58 | PAYNE - 585EJW030075-H | 58 | 4.1 | Yes | Yes | 19 | 19.9 | -0.9 | DC6F31D5B9914D378295C7FF78C9C41B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 7.069% | 0.92931 | 13.58% | [5 empty] | Non-TXV | 7.069%
Stockton | CA | 95206-3612 |  | 2012-08-09 | 2012-08-09 12:37 | 2012-08-09 12:55 | OTHER - NAC036AKC | 94 | -9.5 | Yes | Yes | 19 | 19.9 | -0.9 | 94681FF00CBF4A009C48C5C07517E7FE |  | R22 | Non-TXV |  | -10.11% | 1.1011 | 2.83% |  |  |  |  | Non-TXV |  |  | -10.11%
Stockton | CA | 95209-2554 |  | 2012-08-03 | 2012-08-03 11:12 | 2012-08-03 11:31 | RUUD - UNK | 96 | 6.1 | Yes | Yes | 16.2 | 18.6 | -2.4 | 16B8B4A87C114681B654429F60685FCF |  | R22 | Non-TXV |  | 6.354% | 0.93646 | 12.21% | [5 empty] | Non-TXV | 6.354%
Manteca | CA | 95336-2957 |  | 2012-08-06 | 2012-08-06 14:47 | 2012-08-06 15:18 | AMERICAN STANDARD - YCC030F1MOBJ | 70 | 6 | Yes | Yes | 19.3 | 19.3 | 0 | DEA8F628701E4584B3928A57268951BB | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Riverbank | CA | 95367-3832 |  | 2012-08-16 | 2012-08-16 15:30 | 2012-08-16 15:54 | RUUD - RAFD-042JBS | 79 | 15.9 | Yes | Yes | 19.7 | 21.2 | -1.5 | 5B011597EA354E24820E5AD8107CC69F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.13% | 0.79873 | 38.68% | [5 empty] | Non-TXV | 20.13%
Manteca | CA | 95337-6644 |  | 2012-08-09 | 2012-08-09 15:16 | 2012-08-09 15:40 | TRANE - TTB042C131UJUBF00A1 | 96 | 14.5 | Yes | Yes | 17.7 | 19.2 | -1.5 | 59D13E82F6764EDCB022A597ABEBDB34 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.1% | 0.84896 | 29.03% | [5 empty] | Non-TXV | 15.1%
Stockton | CA | 95212-3065 |  | 2012-08-06 | 2012-08-06 13:33 | 2012-08-06 13:50 | CARRIER - 38CKC036350 | 74 | 3.7 | Yes | Yes | 17.2 | 19.7 | -2.5 | 318D2DB3C7C9412381F64BFB4A5BD750 |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Stockton | CA | 95206-4501 |  | 2012-08-13 | 2012-08-13 10:14 | 2012-08-13 10:37 | GOODMAN - CLJ48-1 | 117 | -11 | Yes | Yes | 19 | 21.5 | -2.5 | 889EEFB061CD4E22A9DC8B9C277A32ED |  | R22 | Non-TXV |  | -9.402% | 1.094 | 2.633% |  |  |  |  | Non-TXV |  |  | -9.402%
Manteca | CA | 95336-6917 |  | 2012-08-07 | 2012-08-07 15:01 | 2012-08-07 15:28 | DAY & NIGHT - 585GJW030040ABAF | 58 | 1.8 | Yes | Yes | 18.8 | 19.5 | -0.7 | 0B352D0CCE7B4AF88084023E9C5E80F8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.103% | 0.96897 | 5.964% | [5 empty] | Non-TXV | 3.103%
Manteca | CA | 95336-2547 |  | 2012-08-06 | 2012-08-06 10:30 | 2012-08-06 10:46 | GE - BTN736A100A1 | 144 | 5 | Yes | Yes | 18.1 | 19.7 | -1.6 | 1779385B5B434AD9BEB6259098C524A1 |  | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Fresno | CA | 93727-8115 |  | 2012-05-31 | 2012-05-31 10:30 | 2012-05-31 10:48 | CARRIER - N/A | 90 | 2.9 | Yes | Yes | 21.7 | 18.8 | 2.9 | 7AB31C199DEE4540897921D67E921CFF |  | R22 | Non-TXV |  | 3.222% | 0.96778 | 6.192% | [5 empty] | Non-TXV | 3.222%
Manteca | CA | 95336-2703 |  | 2012-08-06 | 2012-08-06 11:13 | 2012-08-06 11:47 | OTHER - DRCS0481BC | 90 | 17.9 | Yes | Yes | 17.3 | 19.3 | -2 | 55C50C40004F43A38F7A225AF8285AB2 |  | R22 | Non-TXV |  | 19.89% | 0.80111 | 38.22% | [5 empty] | Non-TXV | 19.89%
Manteca | CA | 95336-4103 |  | 2012-08-07 | 2012-08-07 11:05 | 2012-08-07 11:34 | AMANA - RCA42A2A | 120 | 6.8 | Yes | Yes | 18.6 | 19.7 | -1.1 | E72BC82EA6BA40588231DA5C004D3FF8 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.667% | 0.94333 | 10.89% | [5 empty] | Non-TXV | 5.667%
Stockton | CA | 95209-2063 |  | 2012-05-17 | 2012-05-17 11:10 | 2012-05-17 11:32 | PAYNE - 24-60YAC108TC | 51 | 4.5 | Yes | Yes | 16.2 | 18.3 | -2.1 | 0FF741BCC8BD4C03B103C4A87A2AD0D2 |  | R22 | Non-TXV |  | 8.824% | 0.91176 | 16.96% | [5 empty] | Non-TXV | 8.824%
Manteca | CA | 95336-2627 |  | 2012-08-06 | 2012-08-06 10:25 | 2012-08-06 10:43 | LENNOX - 13GEP36075ALP-2A | 117 | 3.4 | Yes | Yes | 20.2 | 20.4 | -0.2 | E86B6F32C57241E2B4EC5C82D9249E16 |  | R410A | Non-TXV |  | 2.906% | 0.97094 | 5.585% | [5 empty] | Non-TXV | 2.906%
Atwater | CA | 95301-4717 |  | 2012-08-10 | 2012-08-10 10:36 | 2012-08-10 10:52 | TRANE - TTD748B100A0 | 116 | -6.8 | Yes | Yes | 22.1 | 19.7 | 2.4 | 5FA7C37370CE40D59A9B32D9B9AAA26B |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Stockton | CA | 95210-3445 |  | 2012-08-02 | 2012-08-02 11:05 | 2012-08-02 11:25 | PAYNE - PA13NR036-E | 100 | 3 | Yes | Yes | 19.2 | 19.9 | -0.7 | FC3AEAD86D3843A6989FE5E8C1F095DA |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95207-2525 |  | 2012-06-19 | 2012-06-19 12:56 | 2012-06-19 13:14 | GIBSON - JS3BC-042KA | 102 | 5.9 | Yes | Yes | 18.1 | 19.8 | -1.7 | BF8B946DCC6040BA9CBDAA10D9AEE7ED |  | R22 | Non-TXV |  | 5.784% | 0.94216 | 11.12% | [5 empty] | Non-TXV | 5.784%
Fresno | CA | 93726-3613 |  | 2012-05-09 | 2012-05-09 16:13 | 2012-05-09 16:30 | - | 115 | 2.6 | Yes | Yes | 16.3 | 19.3 | -3 | B8CBD98CF06C4DD998AB6CC99FAB019D |  | R22 | Non-TXV |  | 2.261% | 0.97739 | 4.345% | [5 empty] | Non-TXV | 2.261%
Merced | CA | 95341-7721 |  | 2012-08-10 | 2012-08-10 09:54 | 2012-08-10 10:13 | GIBSON - JS3BA-036KA | 69 | 3.8 | Yes | Yes | 26.4 | 21.5 | 4.9 | 59ACA16BD83541C590E216089DAB5038 |  | R22 | Non-TXV |  | 5.507% | 0.94493 | 10.58% | [5 empty] | Non-TXV | 5.507%
Fresno | CA | 93720-0517 |  | 2012-07-09 | 2012-07-09 10:30 | 2012-07-09 10:46 | LENNOX - GCS29X-042-75-2PA | 73 | -2.7 | Yes | Yes | 23.7 | 22.4 | 1.3 | 4C67874AC22C449C83BF27855EAC5EFD |  | R22 | TXV |  | -3.699% | 1.037 | 1.036% |  |  |  |  | TXV |  |  | -3.699%
Sanger | CA | 93657-0000 |  | 2012-05-22 | 2012-05-22 14:43 | 2012-05-22 15:01 | GOODMAN - D1361C | 109 | 14.2 | Yes | Yes | 17 | 19.9 | -2.9 | 5E60375D4B6A469CA952B42658E790A2 |  | R22 | Non-TXV |  | 13.03% | 0.86972 | 25.04% | [5 empty] | Non-TXV | 13.03%
Merced | CA | 95348-2129 |  | 2012-05-17 | 2012-05-17 13:19 | 2012-05-17 13:49 | TRANE - YCC024F1L0BE | 64 | 7.1 | Yes | Yes | 22.4 | 21 | 1.4 | 3D69588DF20144EBA3AD3DE2C32A4998 |  | R22 | Non-TXV |  | 11.09% | 0.88906 | 21.32% | [5 empty] | Non-TXV | 11.09%
Manteca | CA | 95336-3102 |  | 2012-08-06 | 2012-08-06 15:33 | 2012-08-06 15:53 | BRYANT - 561CJ030-A | 66 | 2.3 | Yes | Yes | 18.8 | 19.7 | -0.9 | 4DDAEBBB3BB342E2B7798407916FB5E8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.485% | 0.96515 | 6.697% | [5 empty] | Non-TXV | 3.485%
Red Bluff | CA | 96080-2151 |  | 2012-05-16 | 2012-05-16 10:02 | 2012-05-16 10:40 | DAY N NIGHT - 585CJ042100 | 104 | 3.1 | Yes | Yes | 22.3 | 21.4 | 0.9 | 8A308CBAE5DB4AAC8D33B4F81B979AFF |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Merced | CA | 95341-6534 |  | 2012-06-12 | 2012-06-12 13:53 | 2012-06-12 14:21 | AMANA - 2YCX3030A1064AA | 88 | 3.2 | Yes | Yes | 20 | 20.2 | -0.1 | 4B9F6E3EC1424945963CAE560ED66D42 |  | R22 | Non-TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | Non-TXV | 3.636%
Merced | CA | 95348-2353 |  | 2012-05-31 | 2012-05-31 10:45 | 2012-05-31 11:02 | RHEEM - NA | 70 | 2.1 | Yes | Yes | 18.4 | 19.3 | -0.9 | 2C55F25BC78E4DDCBB7300A24536DCCE | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Manteca | CA | 95337-6768 |  | 2012-05-11 | 2012-05-11 15:19 | 2012-05-11 15:42 | - 591ANX036000AAA | 84 | 12.4 | Yes | Yes | 20 | 22.8 | -2.8 | EA5B0DD552F143138A9F6BF16CC4DE17 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 14.76% | 0.85238 | 28.37% | [5 empty] | Non-TXV | 14.76%
Stockton | CA | 95205-2540 |  | 2012-08-14 | 2012-08-14 11:21 | 2012-08-14 11:39 | GOODMAN - CKL60-1 | 115 | 4.9 | Yes | Yes | 22.7 | 19.3 | 3.4 | 99D3F32E18954A3AABC8C160CAF4FA9D |  | R22 | Non-TXV |  | 4.261% | 0.95739 | 8.188% | [5 empty] | Non-TXV | 4.261%
Fresno | CA | 93727-3761 |  | 2012-05-24 | 2012-05-24 14:01 | 2012-05-24 15:38 | YORK - D1NA030N05606C | 76 | 2.3 | Yes | Yes | 27.6 | 22.3 | 5.3 | 760580099EA54AC59FD59A28BA7B9318 |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95219-7133 |  | 2012-08-15 | 2012-08-15 13:20 | 2012-08-15 13:44 | CARRIER - 38CKC036350 | 77 | -9.5 | Yes | Yes | 17.5 | 19.1 | -1.6 | EB14AA13B3814505824BD45EABC0EC83 |  | R22 | TXV |  | -12.34% | 1.1234 | 3.455% |  |  |  |  | TXV |  |  | -12.34%
Stockton | CA | 95219-7133 |  | 2012-08-15 | 2012-08-15 13:43 | 2012-08-15 13:48 | CARRIER - 38CKC036350 | 77 | 14.4 | Yes | Yes | 16.4 | 17.6 | -1.2 | DB4C6896749A4EDABEB80B2E091A477E |  | R22 | TXV |  | 18.7% | 0.81299 | 35.94% | [5 empty] | TXV | 18.7%
Manteca | CA | 95337-5161 |  | 2012-08-09 | 2012-08-09 13:11 | 2012-08-09 13:33 | DAY & NIGHT - 565BJ030 | 72 | 2.5 | Yes | Yes | 20.9 | 21.7 | -0.8 | 219FDA11F8624C59A9E134AB52717EC7 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Atwater | CA | 95301-4582 |  | 2012-08-09 | 2012-08-09 13:17 | 2012-08-09 13:34 | RUUD - UAKA-048JAZ | 103 | 4.1 | Yes | Yes | 21 | 19.5 | 1.5 | 7BA2C9AFD98F4725923A0FBF96DACF7D |  | R22 | Non-TXV |  | 3.981% | 0.96019 | 7.65% | [5 empty] | Non-TXV | 3.981%
Atwater | CA | 95301-4724 |  | 2012-08-09 | 2012-08-09 15:02 | 2012-08-09 15:23 | DAY & NIGHT - 591ANX036000AAAA | 90 | 3.2 | Yes | Yes | 23.5 | 18.5 | 5 | FCD80E26A0CF4ACF87EFDB45C4A1DBEE |  | R22 | Non-TXV |  | 3.556% | 0.96444 | 6.833% | [5 empty] | Non-TXV | 3.556%
Manteca | CA | 95336-5049 |  | 2012-08-15 | 2012-08-15 09:36 | 2012-08-15 10:01 | DAY & NIGHT - 587ANZ042080 | 72 | 3.8 | Yes | Yes | 16.9 | 19.9 | -3 | B56FD91FF6EB47269F18CF31E8D6855B |  | R22 | Non-TXV |  | 5.278% | 0.94722 | 10.14% | [5 empty] | Non-TXV | 5.278%
Fresno | CA | 93725-1527 |  | 2012-05-10 | 2012-05-10 12:56 | 2012-05-10 13:26 | GOODMAN - GPG13480701AC | 143 | 5.6 | Yes | Yes | 24.1 | 20.4 | 3.7 | E1E328C343F3456FB0216D9502D78BD0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.916% | 0.96084 | 7.526% | [5 empty] | Non-TXV | 3.916%
Stockton | CA | 95207-7424 |  | 2012-08-10 | 2012-08-10 08:54 | 2012-08-10 09:17 | RHEEM - UNK | 128 | 20 | Yes | Yes | 17.4 | 19.1 | -1.7 | 81283428FC8F4247844CEBBBDB73BF57 |  | R22 | Non-TXV |  | 15.62% | 0.84375 | 30.03% | [5 empty] | Non-TXV | 15.62%
Gustine | CA | 95322-9647 |  | 2012-08-14 | 2012-08-14 12:44 | 2012-08-14 13:21 | BRYANT - 561CJ048-A | 84 | 2.6 | Yes | Yes | 20.1 | 16.9 | 3.2 | 670EF66FF6AD4A9A8D58C90EA572A304 |  | R22 | Non-TXV |  | 3.095% | 0.96905 | 5.948% | [5 empty] | Non-TXV | 3.095%
Gustine | CA | 95322-1310 |  | 2012-08-13 | 2012-08-13 11:11 | 2012-08-13 11:30 | OTHER - UNK | 75 | 2.4 | Yes | Yes | 22.3 | 18 | 4.3 | 00E1CA5710D44C80917DAD0E182AB030 |  | R22 | Non-TXV |  | 3.2% | 0.968 | 6.15% | [5 empty] | Non-TXV | 3.2%
Fresno | CA | 93727-2321 |  | 2012-06-25 | 2012-06-25 08:59 | 2012-06-25 09:29 | CARRIER - 48KLA124-300BE | 68 | 2.4 | Yes | Yes | 23.7 | 19.5 | 4.2 | F556937A79FF47E69D76F4F10F5CFF66 |  | R22 | Non-TXV |  | 3.529% | 0.96471 | 6.783% | [5 empty] | Non-TXV | 3.529%
Merced | CA | 95340-0657 |  | 2012-08-03 | 2012-08-03 13:08 | 2012-08-03 14:32 | OTHER - UNK | 76 | 2.7 | Yes | Yes | 18.2 | 19.9 | -1.7 | 559FACA683AF461186D5CA85CDD02A92 |  | R22 | Non-TXV |  | 3.553% | 0.96447 | 6.827% | [5 empty] | Non-TXV | 3.553%
Manteca | CA | 95337-6656 |  | 2012-08-10 | 2012-08-10 12:31 | 2012-08-10 13:21 | BRYANT - 563CN042-C | 104 | 3.7 | Yes | Yes | 18.7 | 20.2 | -1.5 | 3C2166ADC559431A8A4443AEFD16438F |  | R22 | Non-TXV |  | 3.558% | 0.96442 | 6.837% | [5 empty] | Non-TXV | 3.558%
Stockton | CA | 95210-4442 |  | 2012-08-02 | 2012-08-02 14:25 | 2012-08-02 14:45 | CARRIER - 591ANX042000ABAA | 112 | 3.5 | Yes | Yes | 24.5 | 19.9 | 4.6 | EC4B6D2D5DD74916AACBA7754789063F |  | R22 | Non-TXV |  | 3.125% | 0.96875 | 6.006% | [5 empty] | Non-TXV | 3.125%
Chico | CA | 95928-5100 |  | 2012-05-08 | 2012-05-08 11:21 | 2012-05-08 11:40 | AMERICAN STANDARD - 4A7B4030E1000AA | 112 | 4.6 | Yes | Yes | 19.9 | 22 | -2.1 | 1AED2A6558DC4F698E8FE53F8B813FEC | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R410A | Non-TXV |  | 4.107% | 0.95893 | 7.893% | [5 empty] | Non-TXV | 4.107%
Manteca | CA | 95337-5404 |  | 2012-05-10 | 2012-05-10 15:00 | 2012-05-10 15:18 | BRYANT - 112RNA036-C | 88 | -6.3 | Yes | Yes | 19.5 | 20.6 | -1.1 | 66F7F92C83B840489D15E35529E843FB | OK: Verified Refrigerant Charge | R22 | TXV |  | -7.159% | 1.0716 | 2.005% |  |  |  |  | TXV |  |  | -7.159%
Stockton | CA | 95209-4180 |  | 2012-08-06 | 2012-08-06 12:06 | 2012-08-06 12:28 | YORK - H1DE036S06C | 84 | 9.4 | Yes | Yes | 17.1 | 19.9 | -2.8 | 2169F0B9FBDE4452A713558E058D1DE3 |  | R22 | Non-TXV |  | 11.19% | 0.8881 | 21.51% | [5 empty] | Non-TXV | 11.19%
Stockton | CA | 95207-5202 |  | 2012-08-03 | 2012-08-03 15:11 | 2012-08-03 15:37 | PAYNE - 561AJ036-B | 73 | 2.8 | Yes | Yes | 22.2 | 22.8 | -0.6 | 6F15F209E6E74A1A8BAA453B501CA344 |  | R22 | Non-TXV |  | 3.836% | 0.96164 | 7.371% | [5 empty] | Non-TXV | 3.836%
Stockton | CA | 95204-1423 |  | 2012-08-03 | 2012-08-03 15:21 | 2012-08-03 15:41 | RHEEM - RAFD-036JAS | 80 | 7 | Yes | Yes | 23.6 | 21 | 2.6 | C2F653091B284BF38562C528D46851B7 |  | R22 | Non-TXV |  | 8.75% | 0.9125 | 16.82% | [5 empty] | Non-TXV | 8.75%
Merced | CA | 95348-8703 |  | 2012-08-03 | 2012-08-03 13:51 | 2012-08-03 14:23 | GIBSON - 3SBA-042KA | 85 | 4.3 | Yes | Yes | 17.5 | 20.4 | -2.9 | CFEB44F0AFE74B4695418345F30A2D5E |  | R22 | Non-TXV |  | 5.059% | 0.94941 | 9.722% | [5 empty] | Non-TXV | 5.059%
Stockton | CA | 95210-3660 |  | 2012-08-02 | 2012-08-02 10:30 | 2012-08-02 10:47 | CARRIER - 567GJ036 | 93 | -5.5 | Yes | Yes | 27.7 | 21.8 | 6 | B3821850E71A49BDB01C764E4E55F795 |  | R22 | Non-TXV |  | -5.914% | 1.0591 | 1.656% |  |  |  |  | Non-TXV |  |  | -5.914%
Clovis | CA | 93612-0403 |  | 2012-05-10 | 2012-05-10 14:01 | 2012-05-10 14:21 | UNK - UMK | 75 | 2.3 | Yes | Yes | 18.5 | 20.7 | -2.2 | 355A35C7C5E449E0B81F5C7626442207 |  | R22 | Non-TXV |  | 3.067% | 0.96933 | 5.893% | [5 empty] | Non-TXV | 3.067%
Stockton | CA | 95206-6070 |  | 2012-05-11 | 2012-05-11 13:40 | 2012-05-11 14:00 | GOODMAN - CLJ36-1A | 109 | 12.4 | Yes | Yes | 20.4 | 23.2 | -2.8 | 66B4833C0A554D90A518C710EC8BCD65 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 11.38% | 0.88624 | 21.86% | [5 empty] | Non-TXV | 11.38%
Paradise | CA | 95969-2922 |  | 2012-08-03 | 2012-08-03 10:54 | 2012-08-03 11:09 | ARCOAIRE - YCC030F1MOBG | 69 | 6.3 | Yes | Yes | 22.6 | 20.8 | 1.8 | 66FB80F9077744188D3D872A154CC340 |  | R22 | Non-TXV |  | 9.13% | 0.9087 | 17.55% | [5 empty] | Non-TXV | 9.13%
Livingston | CA | 95334-9410 |  | 2012-08-09 | 2012-08-09 11:04 | 2012-08-09 11:09 | RHEEM - RRGP-05E36JKR | 80 | 7.4 | Yes | Yes | 17.4 | 19.8 | -2.4 | 64913498296A4A37A32380880E6046F0 |  | R22 | Non-TXV |  | 9.25% | 0.9075 | 17.78% | [5 empty] | Non-TXV | 9.25%
Manteca | CA | 95337-5314 |  | 2012-05-09 | 2012-05-09 12:28 | 2012-05-09 12:55 | BDP - 561CJ036-D | 83 | 21.8 | Yes | Yes | 25.8 | 20.4 | 5.4 | 2673780429B941128661B5BAE0F395D6 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 26.27% | 0.73735 | 50.48% | [5 empty] | Non-TXV | 26.27%
Stockton | CA | 95205-2582 |  | 2012-06-07 | 2012-06-07 12:02 | 2012-06-07 12:20 | CARRIER - 38EZG036310 | 99 | 5 | Yes | Yes | 18.6 | 19.9 | -1.3 | 542E0C4A157F4471B63924391C293BC9 |  | R410A | TXV |  | 5.051% | 0.94949 | 9.706% | [5 empty] | TXV | 5.051%
Stockton | CA | 95204-2634 |  | 2012-08-02 | 2012-08-02 14:04 | 2012-08-02 14:04 | GE - BTN936B100A0 | 59 | 0 | Yes | Yes | 21.6 | 19.9 | 1.7 | EBACA84CC99A4F24B205C8A97DAF05FB |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95204-3314 |  | 2012-08-13 | 2012-08-13 13:49 | 2012-08-13 14:08 | BDP - 585HJ030040 | 68 | 3.7 | Yes | Yes | 16.7 | 18.5 | -1.8 | 64F88F2C9AC64AB480142FFACCC64E4D |  | R22 | Non-TXV |  | 5.441% | 0.94559 | 10.46% | [5 empty] | Non-TXV | 5.441%
Atwater | CA | 95301-2826 |  | 2012-08-07 | 2012-08-07 12:08 | 2012-08-07 12:39 | GOODMAN - UNK | 75 | -4.4 | Yes | Yes | 24.4 | 20.9 | 3.5 | C724A68B50014480BBC038CD0CDCA67C |  | R22 | Non-TXV |  | -5.867% | 1.0587 | 1.643% |  |  |  |  | Non-TXV |  |  | -5.867%
Livingston | CA | 95334-1820 |  | 2012-08-10 | 2012-08-10 10:00 | 2012-08-10 10:33 | CARRIER - DRCS0361BD | 95 | 4.6 | Yes | Yes | 18.5 | 20.4 | -1.9 | 658B7664C76E4931B43882C213F77405 |  | R22 | Non-TXV |  | 4.842% | 0.95158 | 9.305% | [5 empty] | Non-TXV | 4.842%
Stockton | CA | 95206-1253 |  | 2012-08-14 | 2012-08-14 11:18 | 2012-08-14 11:34 | GIBSON - JS5BD-036K | 138 | 14 | Yes | Yes | 25 | 22.3 | 2.7 | 8407A2F76DFD4417AD5E8CC3146C40FF |  | R22 | Non-TXV |  | 10.14% | 0.89855 | 19.5% | [5 empty] | Non-TXV | 10.14%
Livingston | CA | 95334-1862 |  | 2012-08-09 | 2012-08-09 10:04 | 2012-08-09 10:28 | RHEEM - UNK | 89 | 6.1 | Yes | Yes | 17.3 | 19.3 | -2 | A712FCD145114741B079F5706F3F4D6E |  | R22 | Non-TXV |  | 6.854% | 0.93146 | 13.17% | [5 empty] | Non-TXV | 6.854%
Madera | CA | 93638-3464 |  | 2012-06-12 | 2012-06-12 09:28 | 2012-06-12 09:46 | YORK - D2NP024N05606A | 100 | 16.6 | Yes | Yes | 24.2 | 25.9 | -1.7 | E08AC6FC2AD845D197F9CA092383AD57 |  | R22 | Non-TXV |  | 16.6% | 0.834 | 31.9% | [5 empty] | Non-TXV | 16.6%
Magalia | CA | 95954-9675 |  | 2012-08-15 | 2012-08-15 10:10 | 2012-08-15 10:31 | DAY & NIGHT - 54E030HP | 97 | 3 | Yes | Yes | 25.5 | 21.2 | 4.3 | 420F3DC543C74217982CF38662E4477C |  | R22 | Non-TXV |  | 3.093% | 0.96907 | 5.944% | [5 empty] | Non-TXV | 3.093%
Fresno | CA | 93720-2418 |  | 2012-06-13 | 2012-06-13 12:00 | 2012-06-13 12:17 | DAY & NIGHT - 569CJ036 | 102 | 3 | Yes | Yes | 22.7 | 21 | 1.7 | 0AC75016D0EB4FCFBC99798534D68C2F |  | R22 | Non-TXV |  | 2.941% | 0.97059 | 5.652% | [5 empty] | Non-TXV | 2.941%
Planada | CA | 95365-8033 |  | 2012-06-06 | 2012-06-06 12:09 | 2012-06-06 12:37 | RHEEM - RRNL-B030JK06X | 76 | 5.1 | Yes | Yes | 26 | 20.1 | 5.9 | D2C7E7D12D69458CB9E402CBFC341574 |  | R410A | Non-TXV |  | 6.711% | 0.93289 | 12.9% | [5 empty] | Non-TXV | 6.711%
Fresno | CA | 93726-4211 |  | 2012-05-22 | 2012-05-22 11:56 | 2012-05-22 12:22 | CARRIER - 48KLA148--300BE | 118 | 3.5 | Yes | Yes | 22.5 | 19.3 | 3.2 | 84FAA8C86C2D4D2A9641A8E667F859A2 |  | R22 | Non-TXV |  | 2.966% | 0.97034 | 5.7% | [5 empty] | Non-TXV | 2.966%
Manteca | CA | 95337-8703 |  | 2012-05-14 | 2012-05-14 14:27 | 2012-05-14 15:19 | YORK - H1RA048S06D | 117 | 15.8 | Yes | Yes | 17.5 | 20.3 | -2.8 | 54B3BF85ACC54D88B654F81ADB466B17 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 13.5% | 0.86496 | 25.95% | [5 empty] | Non-TXV | 13.5%
Red Bluff | CA | 96080-4131 |  | 2012-05-16 | 2012-05-16 10:51 | 2012-05-16 10:51 | AMERICAN STANDARD - YCY042G1MOAD | 105 | 0 | Yes | Yes | 18.9 | 21.5 | -2.6 | B9BDC37F2BE04C6EB063CFFFC44107AE |  | R22 | Non-TXV |  | 0% | 1 | 0%
Manteca | CA | 95336-6420 |  | 2012-08-07 | 2012-08-07 14:47 | 2012-08-07 15:28 | DAY & NIGHT - 585EJW0300AAAE | 58 | 9 | Yes | Yes | 19 | 20.9 | -1.9 | 358DAD377CA94EB7AA779E2FA63244A8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 15.52% | 0.84483 | 29.82% | [5 empty] | Non-TXV | 15.52%
Tracy | CA | 95377-8405 |  | 2012-08-14 | 2012-08-14 15:01 | 2012-08-14 15:17 | CARRIER - 38CKC036350 | 74 | 2.3 | Yes | Yes | 25.5 | 21.5 | 4.1 | BA2C9A4AAE2948EA8C40BE8035DD7871 |  | R22 | Non-TXV |  | 3.108% | 0.96892 | 5.973% | [5 empty] | Non-TXV | 3.108%
Fresno | CA | 93727-7248 |  | 2012-05-09 | 2012-05-09 10:20 | 2012-05-09 10:39 | GOODMAN - PGB042075-1A | 68 | 2.2 | Yes | Yes | 19.8 | 19.9 | -0.1 | FCAABB8B6559482B85F3FD5AE1023311 |  |  |  |  | 3.235% | 0.96765 | 6.218% | [5 empty] | 0 | 3.235%
Paradise | CA | 95969-3014 |  | 2012-08-03 | 2012-08-03 12:57 | 2012-08-03 13:24 | TEMPSTAR - CA9042VKD2 | 128 | 11.8 | Yes | Yes | 18.8 | 21.3 | -2.5 | 9ED8A639340F4E36AC0088E10539C310 |  | R22 | Non-TXV |  | 9.219% | 0.90781 | 17.72% | [5 empty] | Non-TXV | 9.219%
Stockton | CA | 95215-7413 |  | 2012-05-31 | 2012-05-31 13:05 | 2012-05-31 13:05 | OTHER - R2A342GKR100 | 113 | 0 | Yes | Yes | 19.6 | 20.1 | -0.4 | 0B0AA6EA5ADB43CB9DC7359ADA4565E2 |  | R22 | TXV |  | 0% | 1 | 0%
Hamilton City | CA | 95951-0000 |  | 2012-08-14 | 2012-08-14 15:34 | 2012-08-14 16:18 | BRYANT - 561CJX036000AEAA | 70 | 2.8 | Yes | Yes | 23.5 | 21.3 | 2.3 | 4E00004E01534415A85093FC9DC09F54 |  | R22 | Non-TXV |  | 4% | 0.96 | 7.687% | [5 empty] | Non-TXV | 4%
Merced | CA | 95340-0952 |  | 2012-08-03 | 2012-08-03 10:22 | 2012-08-03 10:56 | RUUD - RRGG-07N43JKR | 109 | 4.8 | Yes | Yes | 25.4 | 20.2 | 5.2 | AE6823EA98E647CCA481C99D73764AEB |  | R22 | Non-TXV |  | 4.404% | 0.95596 | 8.463% | [5 empty] | Non-TXV | 4.404%
Merced | CA | 95340-0948 |  | 2012-08-03 | 2012-08-03 10:01 | 2012-08-03 10:19 | RHEEM - RRPLB036JK06X | 92 | 4.8 | Yes | Yes | 20.7 | 19.7 | 1.1 | 660B90CA2C644C97B1228FB789AFB00B |  | R410A | Non-TXV |  | 5.217% | 0.94783 | 10.03% | [5 empty] | Non-TXV | 5.217%
Magalia | CA | 95954-9517 |  | 2012-08-09 | 2012-08-09 09:32 | 2012-08-09 10:10 | CARRIER - 38EE045300 | 85 | 3.8 | Yes | Yes | 24.7 | 20.8 | 3.9 | 06F439784B224FE793640CB1FB9CD9E3 |  | R22 | Non-TXV |  | 4.471% | 0.95529 | 8.591% | [5 empty] | Non-TXV | 4.471%
Atwater | CA | 95301-4879 |  | 2012-05-16 | 2012-05-16 12:56 | 2012-05-16 13:16 | LENNOX - HCS311-3H | 78 | 2.3 | Yes | Yes | 16.2 | 18.1 | -1.9 | 48C4DB739F1142D89C36193F57DCE820 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Oroville | CA | 95966-3838 |  | 2012-08-07 | 2012-08-07 12:08 | 2012-08-07 12:57 | CARRIER - 38YR042310 | 152 | 6.5 | Yes | Yes | 18.4 | 20.2 | -1.8 | 9581B389F33C4CFA9FA2002689743A91 |  | R22 | Non-TXV |  | 4.276% | 0.95724 | 8.218% | [5 empty] | Non-TXV | 4.276%
Stockton | CA | 95210-3136 |  | 2012-06-11 | 2012-06-11 14:58 | 2012-06-11 15:16 | HEIL - PGAA24C1K3 | 64 | 2.2 | Yes | Yes | 22.1 | 23.5 | -1.4 | 1CD4D65B14554ED78319436BF02859C9 |  | R22 | Non-TXV |  | 3.438% | 0.96562 | 6.606% | [5 empty] | Non-TXV | 3.438%
Manteca | CA | 95336-4123 |  | 2012-08-15 | 2012-08-15 12:50 | 2012-08-15 13:11 | PAYNE - PA10JA036-C | 73 | 2.3 | Yes | Yes | 26 | 20.7 | 5.3 | C5BD31F095384A3B8CA18CE60D4138A3 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.151% | 0.96849 | 6.055% | [5 empty] | Non-TXV | 3.151%
Paradise | CA | 95969-5451 |  | 2012-05-11 | 2012-05-11 14:15 | 2012-05-11 17:23 | PAYNE - PA10JA048000AAAA | 99 | 3.1 | Yes | Yes | 24.4 | 23.5 | 1 | 1642EA1B3D52481A9CDB5973168B1D4B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.131% | 0.96869 | 6.018% | [5 empty] | Non-TXV | 3.131%
Manteca | CA | 95337-5412 |  | 2012-05-10 | 2012-05-10 12:48 | 2012-05-10 13:14 | DAY & NITE - 585GJW024040 | 54 | 2.7 | Yes | Yes | 17 | 19.5 | -2.5 | 351B7BB1577E4BCCABAC096244BEAC79 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Paradise | CA | 95969-5219 |  | 2012-08-03 | 2012-08-03 13:48 | 2012-08-03 14:18 | CARRIER - NA | 78 | 4.1 | Yes | Yes | 25.2 | 22.9 | 2.4 | 7FB1D24CE30E46BBBDEE5C0C1C3434A9 |  | R22 | Non-TXV |  | 5.256% | 0.94744 | 10.1% | [5 empty] | Non-TXV | 5.256%
Merced | CA | 95341-5542 |  | 2012-08-07 | 2012-08-07 11:30 | 2012-08-07 11:53 | YORK - D1NA042N04606C | 76 | 3.5 | Yes | Yes | 22.6 | 20.1 | 2.5 | AA374593D24746E8A9DF1B6A73B4166D |  | R22 | Non-TXV |  | 4.605% | 0.95395 | 8.85% | [5 empty] | Non-TXV | 4.605%
Oroville | CA | 95965-4141 |  | 2012-08-07 | 2012-08-07 10:41 | 2012-08-07 10:57 | CARRIER - 38EH036300 | 116 | 6.1 | Yes | Yes | 20 | 22.4 | -2.4 | FA0B86AB686140BB84C461349D69A22B |  | R22 | Non-TXV |  | 5.259% | 0.94741 | 10.11% | [5 empty] | Non-TXV | 5.259%
Stockton | CA | 95205-7009 |  | 2012-08-06 | 2012-08-06 09:17 | 2012-08-06 09:44 | HEIL - PGAA30C1K4 | 79 | 2.4 | Yes | Yes | 17 | 17.6 | -0.6 | 19088693697C469CA8BB5EEF5123D24B |  | R22 | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Stockton | CA | 95205-7881 |  | 2012-08-07 | 2012-08-07 12:55 | 2012-08-07 13:11 | PAYNE - PY3GNAA36060NA | 100 | 3 | Yes | Yes | 21 | 19.7 | 1.3 | BC095AE5AE60476DAED8BB611BEFA9C9 |  | R410A | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Durham | CA | 95938-9622 |  | 2012-07-24 | 2012-07-24 11:14 | 2012-07-24 11:36 | RUUD - URGF-05E30JKR | 70 | 4.9 | Yes | Yes | 19.9 | 21.7 | -1.8 | 03C310875B5F4E5EA3276191E22297A4 |  | R22 | Non-TXV |  | 7% | 0.93 | 13.45% | [5 empty] | Non-TXV | 7%
Fresno | CA | 93711-6545 |  | 2012-07-05 | 2012-07-05 13:16 | 2012-07-05 13:39 | AMERICAN STANDARD - YCC024F1L0BJ | 65 | 1.9 | Yes | Yes | 22.9 | 20.2 | 2.8 | 6648142C423E414796A47D13D136FA86 |  | R22 | Non-TXV |  | 2.923% | 0.97077 | 5.618% | [5 empty] | Non-TXV | 2.923%
Stockton | CA | 95209-2745 |  | 2012-08-02 | 2012-08-02 14:40 | 2012-08-02 14:57 | PAYNE - 585A024055YACR | 51 | 3.6 | Yes | Yes | 24.2 | 22.8 | 1.4 | 8060989F43334DD0B00CC1DC2EDDC0E1 |  | R22 | Non-TXV |  | 7.059% | 0.92941 | 13.57% | [5 empty] | Non-TXV | 7.059%
Manteca | CA | 95336-2879 |  | 2012-08-06 | 2012-08-06 12:47 | 2012-08-06 13:11 | RUUD - UAKA-042JAZ | 79 | 2.9 | Yes | Yes | 18.1 | 18.7 | -0.6 | 6738B8A8782E4136AEC6109166DFF690 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.671% | 0.96329 | 7.055% | [5 empty] | Non-TXV | 3.671%
Red Bluff | CA | 96080-7916 |  | 2012-08-06 | 2012-08-06 14:49 | 2012-08-06 17:58 | RHEEM - RPFB-060JAS | 208 | 6.2 | Yes | Yes | 19.9 | 20.4 | -0.5 | 2361752A52BC4D448688005E777FEF5C |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Atwater | CA | 95301-4847 |  | 2012-05-11 | 2012-05-11 12:37 | 2012-05-11 12:57 | GOODMAN - CK30-10 | 80 | 7.7 | Yes | Yes | 19.4 | 20.4 | -1 | F970F84259124CD494FD69669F5DCC5D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.625% | 0.90375 | 18.5% | [5 empty] | Non-TXV | 9.625%
Live Oak | CA | 95953-2241 |  | 2012-08-13 | 2012-08-13 10:56 | 2012-08-13 21:04 | BRYANT - 583BNW036060NC-- | 110 | -10.4 | Yes | Yes | 18.4 | 19.2 | -0.7 | 8388569076F04C50BAE7DB3560537336 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R410A | Non-TXV |  | -9.455% | 1.0945 | 2.648% |  |  |  |  | Non-TXV |  |  | -9.455%
Los Banos | CA | 93635-3028 |  | 2012-05-15 | 2012-05-15 11:37 | 2012-05-15 11:55 | NORDEN - R4GD036K072X | 100 | 8.3 | Yes | Yes | 21.2 | 18.8 | 2.4 | 823C8F4FC07F49BABC740EBAC08DBBFF |  | R22 | Non-TXV |  | 8.3% | 0.917 | 15.95% | [5 empty] | Non-TXV | 8.3%
Yuba City | CA | 95991-2440 |  | 2012-08-03 | 2012-08-03 09:16 | 2012-08-03 09:39 | AIRE-FLO - 13ACD-036-230-12 | 92 | 2.8 | Yes | Yes | 19 | 19.5 | -0.5 | A1E3B989413B4A8592FC1F4E2EA1D9DE |  | R22 | Non-TXV |  | 3.043% | 0.96957 | 5.849% | [5 empty] | Non-TXV | 3.043%
Yuba City | CA | 95993-3550 |  | 2012-05-17 | 2012-05-17 13:21 | 2012-05-17 13:21 | DAY NITE - 585024050 YACR | 54 | 0 | Yes | Yes | 17 | 19.3 | -2.3 | E20A950544414D76909D27094BC68F3C |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chico | CA | 95973-0404 |  | 2012-05-09 | 2012-05-09 11:07 | 2012-05-09 11:25 | DAY & NIGHT - 588ANW036080ABBF | 67 | 4.8 | Yes | Yes | 22.1 | 21 | 1.1 | 48E825AD1F1E4C3C8A11DB577643FCCE | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 7.164% | 0.92836 | 13.77% | [5 empty] | Non-TXV | 7.164%
Stockton | CA | 95210-1710 |  | 2012-05-09 | 2012-05-09 12:30 | 2012-05-09 12:48 | WESTINGHOUSE - ID030BEAON | 88 | 2.7 | Yes | Yes | 21.1 | 20.9 | 0.2 | 2D38F23174C846DA90F209400E85E020 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.068% | 0.96932 | 5.896% | [5 empty] | Non-TXV | 3.068%
Chowchilla | CA | 93610-2220 |  | 2012-05-08 | 2012-05-08 12:40 | 2012-05-08 12:58 | ARCOAIRE - PGF036K080E | 70 | 2.4 | Yes | Yes | 16.6 | 19.5 | -2.9 | 4E8A236F853C47BCB962F5B7DD8566D5 |  | R22 | Non-TXV |  | 3.429% | 0.96571 | 6.589% | [5 empty] | Non-TXV | 3.429%
Le Grand | CA | 95333-9644 |  | 2012-08-14 | 2012-08-14 11:41 | 2012-08-14 12:11 | RUUD - UNK | 80 | 2.4 | Yes | Yes | 18.3 | 18.8 | -0.5 | B1156F4CF9DC401D9201DABE6E84D39E |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Stockton | CA | 95209-1504 |  | 2012-05-18 | 2012-05-18 13:24 | 2012-05-18 13:45 | PAYNE - 567C042RCU | 75 | 17.7 | Yes | Yes | 19.4 | 21.4 | -2 | 07F3D4A377DA465CADD48CAB2B2C153D |  | R22 | Non-TXV |  | 23.6% | 0.764 | 45.35% | [5 empty] | Non-TXV | 23.6%
Los Banos | CA | 93635-4528 |  | 2012-08-09 | 2012-08-09 09:50 | 2012-08-09 10:07 | OTHER - R4GDX36K100X | 115 | 10.6 | Yes | Yes | 24.1 | 21.9 | 2.2 | A4ED90062007449ABBB774D5C93160DD |  | R22 | Non-TXV |  | 9.217% | 0.90783 | 17.71% | [5 empty] | Non-TXV | 9.217%
Oroville | CA | 95966-9205 |  | 2012-08-16 | 2012-08-16 11:28 | 2012-08-16 13:38 | CARRIER - 38CKB048300 | 99 | 2.9 | Yes | Yes | 24.1 | 21.2 | 2.9 | 4501D00E6AA84CB79C5C687E46153ACC |  | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Yuba City | CA | 95991-1514 |  | 2012-07-24 | 2012-07-24 14:50 | 2012-07-24 15:08 | BDP - 585B025050YACR | 51 | 1.6 | Yes | Yes | 18.2 | 17.2 | 1 | CC5AD3DD598B4CCEA25E97BFA128878A |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Chico | CA | 95928-5444 |  | 2012-05-15 | 2012-05-15 10:52 | 2012-05-15 11:13 | DAYNNIGHT - 58HJW024040 | 67 | 2.8 | Yes | Yes | 23.9 | 22.2 | 1.7 | 1DB3A9055D9446A6B4646BEFCE5B3362 |  | R22 | Non-TXV |  | 4.179% | 0.95821 | 8.031% | [5 empty] | Non-TXV | 4.179%
Atwater | CA | 95301-2281 |  | 2012-08-09 | 2012-08-09 11:19 | 2012-08-09 11:35 | DAY & NIGHT - UNK | 75 | 7.2 | Yes | Yes | 21.4 | 20.4 | 1 | C362D04D4911455ABF3D9B31BE3F2547 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.6% | 0.904 | 18.45% | [5 empty] | Non-TXV | 9.6%
Madera | CA | 93637-6262 |  | 2012-05-08 | 2012-05-08 12:19 | 2012-05-08 12:19 | RHEEM - RRNA-B024JK06X | 70 | 0 | Yes | Yes | 19 | 20.4 | -1.4 | 362B9BCE065B4E448F39EC039A6CEE1D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Jackson | CA | 95642-9641 |  | 2012-07-17 | 2012-07-17 09:30 | 2012-07-17 10:03 | AIRE-FLO - AFAIR12B36PA | 107 | 3.2 | Yes | Yes | 26 | 20.4 | 5.6 | A69958D45A5242BAA15237BA1EB910B4 |  | R22 | Non-TXV |  | 2.991% | 0.97009 | 5.747% | [5 empty] | Non-TXV | 2.991%
Atwater | CA | 95301-2281 |  | 2012-08-06 | 2012-08-06 12:51 | 2012-08-06 13:21 | DAY & NIGHT - UNK | 65 | 3 | Yes | Yes | 21.5 | 19.5 | 2 | E7E8E853BC6A4CF9963A09F681C35729 |  | R22 | Non-TXV |  | 4.615% | 0.95385 | 8.87% | [5 empty] | Non-TXV | 4.615%
Merced | CA | 95348-4328 |  | 2012-08-06 | 2012-08-06 09:35 | 2012-08-06 10:13 | TEMPSTAR - NCAA4548UP | 137 | 5.2 | Yes | Yes | 18 | 20.4 | -2.4 | 921D099346784B179CB490DCE55BE475 |  | R22 | Non-TXV |  | 3.796% | 0.96204 | 7.294% | [5 empty] | Non-TXV | 3.796%
Willows | CA | 95988-3129 |  | 2012-05-29 | 2012-05-29 14:34 | 2012-05-29 15:23 | GOODMAN - GSC130241AE | 91 | 6.7 | Yes | Yes | 24.4 | 22.6 | 1.8 | 2CFAC9B1EE5A48A3B74F2CD281838170 |  | R22 | Non-TXV |  | 7.363% | 0.92637 | 14.15% | [5 empty] | Non-TXV | 7.363%
Stockton | CA | 95210-2744 |  | 2012-06-11 | 2012-06-11 08:55 | 2012-06-11 09:13 | BDP - 561CJ024-C | 72 | -4.2 | Yes | Yes | 19 | 20.6 | -1.6 | 94C5A4BE1DE94DFAA19505A71DCBA8E6 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Merced | CA | 95340-3831 |  | 2012-05-18 | 2012-05-18 10:13 | 2012-05-18 10:41 | UNK - BRCS0181BD | 54 | 8.4 | Yes | Yes | 20.4 | 20.4 | 0 | 6DEC53F4B96B4B76B8043C92B58814B3 |  | R22 | Non-TXV |  | 15.56% | 0.84444 | 29.89% | [5 empty] | Non-TXV | 15.56%
Yuba City | CA | 95993-7116 |  | 2012-05-10 | 2012-05-10 13:09 | 2012-05-10 13:09 | BRYANT - 582ANW030060AAAD | 59 | 0 | Yes | Yes | 24.2 | 20.9 | 3.3 | A5F469424501466D82D2D3B3775226C7 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Dos Palos | CA | 93620-9706 |  | 2012-08-03 | 2012-08-03 10:12 | 2012-08-03 10:30 | AMERICAN STANDARD - WCY042F100AB | 136 | 10.4 | Yes | Yes | 22.6 | 16.6 | 6 | 2E87E67A2E34407BA54B1CAA92BAE5B2 |  | R22 | Non-TXV |  | 7.647% | 0.92353 | 14.7% | [5 empty] | Non-TXV | 7.647%
Magalia | CA | 95954-9657 |  | 2012-06-14 | 2012-06-14 09:38 | 2012-06-14 09:54 | BARD - PH30 | 85 | 5.1 | Yes | Yes | 25.2 | 22.6 | 2.6 | 2C37DB7E902142D4A84563CEA505A824 |  | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Yuba City | CA | 95991-8834 |  | 2012-08-03 | 2012-08-03 09:53 | 2012-08-03 10:21 | COLEMAN - UNK | 70 | 13 | Yes | Yes | 21 | 21 | 0 | 586859734A1B419585615CD3C72C73DB |  | R22 | Non-TXV |  | 18.57% | 0.81429 | 35.69% | [5 empty] | Non-TXV | 18.57%
Stockton | CA | 95210-2227 |  | 2012-08-07 | 2012-08-07 10:19 | 2012-08-07 10:35 | ICP - N2A348AKA200 | 124 | -7.3 | Yes | Yes | 24.1 | 18.2 | 5.9 | 6FBD349CD6B745FDBF4B9335E4E44E3C |  | R22 | Non-TXV |  | -5.887% | 1.0589 | 1.649% |  |  |  |  | Non-TXV |  |  | -5.887%
Merced | CA | 95348-1655 |  | 2012-06-08 | 2012-06-08 13:04 | 2012-06-08 13:22 | ARCOAIRE - PGF024K040E | 54 | 5.3 | Yes | Yes | 22.1 | 21.5 | 0.6 | 9C0CF5B58C734BCD88A99A3DF40093DF |  | R22 | Non-TXV |  | 9.815% | 0.90185 | 18.86% | [5 empty] | Non-TXV | 9.815%
Yuba City | CA | 95991-7550 |  | 2012-07-10 | 2012-07-10 12:52 | 2012-07-10 12:52 | DAY & NIGHT - 591ANX024000AAAA | 56 | 0 | Yes | Yes | 24.1 | 19.5 | 4.6 | 7BEB61EF21F448BD91F9C36FA77096B0 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Oroville | CA | 95966-7725 |  | 2012-08-16 | 2012-08-16 13:42 | 2012-08-16 14:16 | TRANE - 2TT122042A100AA | 86 | 8.1 | Yes | Yes | 22.5 | 21.5 | 1 | 5C9B4C75F65C4EEAA48C7153F2C6BF8E |  | R22 | Non-TXV |  | 9.419% | 0.90581 | 18.1% | [5 empty] | Non-TXV | 9.419%
Merced | CA | 95341-6037 |  | 2012-05-09 | 2012-05-09 16:46 | 2012-05-09 17:06 | FRASER & JOHNSTONE - 60WE30G1NA | 87 | -5.1 | Yes | Yes | 21.4 | 20.7 | 0.7 | A80FEE06A9B14D69AB59B4FC8419B02C |  | R22 | Non-TXV |  | -5.862% | 1.0586 | 1.642% |  |  |  |  | Non-TXV |  |  | -5.862%
Orland | CA | 95963-9284 |  | 2012-08-14 | 2012-08-14 17:57 | 2012-08-14 18:35 | TRANE - TWB3048A1000AA | 153 | 4.6 | Yes | Yes | 23.7 | 22.9 | 0.8 | 21B08610932B4EDD85F5A738E5119942 |  | R22 | Non-TXV |  | 3.007% | 0.96993 | 5.778% | [5 empty] | Non-TXV | 3.007%
Stockton | CA | 95206-2802 |  | 2012-05-18 | 2012-05-18 14:38 | 2012-05-18 14:56 | CARRIER - 38CKC030340 | 67 | 5.3 | Yes | Yes | 17.2 | 19.8 | -2.6 | 33EBFDE6D7C2447B9468CF9FB9860C7A | OK: Verified Refrigerant Charge | R22 | TXV |  | 7.91% | 0.9209 | 15.2% | [5 empty] | TXV | 7.91%
Merced | CA | 95340-3349 |  | 2012-05-08 | 2012-05-08 11:54 | 2012-05-08 11:54 | GOODMAN - CKL60-1L | 115 | 0 | Yes | Yes | 24 | 18.5 | 5.6 | E71DE420A28E4BA88E3F82D6314525AF | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Red Bluff | CA | 96080-4404 |  | 2012-05-29 | 2012-05-29 09:58 | 2012-05-29 10:18 | BRYANT - 582ANW036090NBAF | 70 | 4 | Yes | Yes | 19.8 | 19.6 | 0.2 | 3A90B82FD58E460797044AA4E9A16155 |  | R22 | Non-TXV |  | 5.714% | 0.94286 | 10.98% | [5 empty] | Non-TXV | 5.714%
Stockton | CA | 95203-3213 |  | 2012-08-13 | 2012-08-13 11:20 | 2012-08-13 11:20 | GOODMAN - CKL30-1D | 70 | 0 | Yes | Yes | 24.1 | 21 | 3.1 | 1E592E6FF7874540AD6379056E04C6CC |  | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93727-7005 |  | 2012-05-11 | 2012-05-11 12:57 | 2012-05-11 13:15 | RHEEM - N/A | 60 | 2.8 | Yes | Yes | 20.3 | 21.5 | -1.2 | 7BAB7BFB1E194BE894EFF8248C9FE4F8 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.667% | 0.95333 | 8.968% | [5 empty] | Non-TXV | 4.667%
Grass Valley | CA | 95945-4124 |  | 2012-05-16 | 2012-05-16 12:13 | 2012-05-16 12:30 | FRASER-JOHNSTON - HDEC-018SB | 56 | 7.9 | Yes | Yes | 15.9 | 18.7 | -2.8 | 07EE3F4432F547E9A5B878D21051B7E1 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 14.11% | 0.85893 | 27.11% | [5 empty] | Non-TXV | 14.11%
Fresno | CA | 93706-9149 |  | 2012-06-14 | 2012-06-14 12:17 | 2012-06-14 12:37 | NORDYNE - N/A | 105 | 3.3 | Yes | Yes | 23.5 | 20.7 | 2.8 | 5E87F383CA8D4D558CBE9D7A5DFA7EBF |  | R22 | Non-TXV |  | 3.143% | 0.96857 | 6.04% | [5 empty] | Non-TXV | 3.143%
Oroville | CA | 95965-5818 |  | 2012-08-07 | 2012-08-07 11:26 | 2012-08-07 11:43 | CARRIER - 38TH030310 | 68 | 7.8 | Yes | Yes | 19.8 | 21.4 | -1.6 | ACFE974064BE4BDBA71CCA875CE62BF3 |  | R22 | Non-TXV |  | 11.47% | 0.88529 | 22.04% | [5 empty] | Non-TXV | 11.47%
Shingle Springs | CA | 95682-9539 |  | 2012-08-02 | 2012-08-02 12:51 | 2012-08-02 13:19 | YORK - CP042 | 118 | 7.8 | Yes | Yes | 21.5 | 20.3 | 1.2 | 3A822A909F5F4E1D9FB7E13F5CD77365 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 6.61% | 0.9339 | 12.7% | [5 empty] | Non-TXV | 6.61%
Madera | CA | 93637-4917 |  | 2012-08-13 | 2012-08-13 09:06 | 2012-08-13 09:23 | CARRIER - UNK | 88 | 11.5 | Yes | Yes | 17.9 | 17.7 | 0.2 | 7CB4022B36304177A5501823310955A3 |  | R22 | Non-TXV |  | 13.07% | 0.86932 | 25.11% | [5 empty] | Non-TXV | 13.07%
Rocklin | CA | 95765-5422 |  | 2012-08-03 | 2012-08-03 14:57 | 2012-08-03 15:16 | YORK - H1RA042S06A | 84 | 28 | Yes | Yes | 19.4 | 21.5 | -2.1 | AA246B79FC4A4FB182074078A881B4D6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 33.33% | 0.66667 | 64.06% | [5 empty] | Non-TXV | 33.33%
Oroville | CA | 95965-4359 |  | 2012-08-07 | 2012-08-07 10:36 | 2012-08-07 10:57 | COLEMAN - 9536A901 | 88 | 6.6 | Yes | Yes | 21.3 | 20.4 | 0.9 | 18C963DBED974C8D9E7360946D3807E7 |  | R22 | Non-TXV |  | 7.5% | 0.925 | 14.41% | [5 empty] | Non-TXV | 7.5%
Chico | CA | 95926-3054 |  | 2012-05-16 | 2012-05-16 12:18 | 2012-05-16 12:39 | TEMPSTAR - TCA030AKA1 | 75 | 9 | Yes | Yes | 21.5 | 20.7 | 0.8 | 58C0798E17CD4BF1A2FFFDB0444AD744 |  | R22 | Non-TXV |  | 12% | 0.88 | 23.06% | [5 empty] | Non-TXV | 12%
Oroville | CA | 95965-4127 |  | 2012-08-07 | 2012-08-07 09:43 | 2012-08-07 09:59 | BRYANT - 36-579F | 72 | 4.7 | Yes | Yes | 23.1 | 21.7 | 1.4 | F1FB2BD8CB8C40DF9E7945C4EA5900E5 |  | R22 | Non-TXV |  | 6.528% | 0.93472 | 12.54% | [5 empty] | Non-TXV | 6.528%
Loomis | CA | 95650-9073 |  | 2012-08-03 | 2012-08-03 13:06 | 2012-08-03 13:06 | GE - BGTA724B1B | 46 | 0 | Yes | Yes | 22 | 20.7 | 1.3 | 2F0E150F72604EF0A32F9490B8EBAB3C | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Rocklin | CA | 95765-4834 |  | 2012-08-08 | 2012-08-08 14:57 | 2012-08-08 15:16 | YORK - H1CF030S06A | 112 | 10.2 | Yes | Yes | 17.4 | 19.9 | -2.5 | D3768BD2F4D84A1EA37C7CB1FA377E6D | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 9.107% | 0.90893 | 17.5% | [5 empty] | Non-TXV | 9.107%
Rocklin | CA | 95765-4834 |  | 2012-08-08 | 2012-08-08 15:30 | 2012-08-08 15:49 | YORK - H1CF030S06A | 112 | 17.3 | Yes | Yes | 17.2 | 20.2 | -3 | CF510FDF8D34487583DF53314DB8BD46 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.45% | 0.84554 | 29.68% | [5 empty] | Non-TXV | 15.45%
Chico | CA | 95926-4222 |  | 2012-05-07 | 2012-05-07 21:31 | 2012-05-07 21:50 | DAY N NIGHT - 24/60 YAC-60442 | 54 | 2.7 | Yes | Yes | 19.6 | 22.5 | -2.9 | 8BBA5A33F05C4A178D5CCD0BE94F290D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Auburn | CA | 95602-2143 |  | 2012-07-25 | 2012-07-25 14:54 | 2012-07-25 15:18 | UNITARY PRODUCTS GROUP - TCGD18S21S1HA | 50 | 5.4 | Yes | Yes | 23.9 | 19.9 | 4 | D2FF5A457610430FA33A3096A2C9880F |  | R22 | Non-TXV |  | 10.8% | 0.892 | 20.76% | [5 empty] | Non-TXV | 10.8%
Manteca | CA | 95336-6313 |  | 2012-08-07 | 2012-08-07 11:58 | 2012-08-07 12:24 | DAY & NIGHT - 585EJW023050AAE | 54 | 6.5 | Yes | Yes | 18.9 | 19.7 | -0.8 | CBEBE5E7450E49E9B3DA5FE73D677E1B | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 12.04% | 0.87963 | 23.13% | [5 empty] | Non-TXV | 12.04%
Lathrop | CA | 95330-9017 |  | 2012-05-31 | 2012-05-31 09:42 | 2012-05-31 10:00 | RUUD - UAJC-042JAS | 99 | 2.9 | Yes | Yes | 18.5 | 19.6 | -1.1 | 7C7A2B18DA0441FB8CFEAFE82ABE017E | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 2.929% | 0.97071 | 5.629% | [5 empty] | Non-TXV | 2.929%
Atwater | CA | 95301-2820 |  | 2012-08-07 | 2012-08-07 08:27 | 2012-08-07 08:27 | ARCOAIRE - HAC060AKC4 | 126 | 0 | Yes | Yes | 18.4 | 18.2 | 0.2 | EFDE8A8E68744B9AA62F895DDF796471 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Valley Springs | CA | 95252-9682 |  | 2012-07-05 | 2012-07-05 13:47 | 2012-07-05 14:07 | BDP - 542E3060 | 208 | 6.2 | Yes | Yes | 25.9 | 22 | 3.9 | 78F51A45C8DA49499D713EEC96F669BB |  | R22 | Non-TXV |  | 2.981% | 0.97019 | 5.728% | [5 empty] | Non-TXV | 2.981%
Stockton | CA | 95215-7340 |  | 2012-08-08 | 2012-08-08 13:36 | 2012-08-08 13:36 | YORK - D1NP048N09006A | 132 | 0 | Yes | Yes | 20 | 19.9 | 0.1 | 3ECAFC08B0A343649D77B3C415396D88 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Corning | CA | 96021-2514 |  | 2012-08-08 | 2012-08-08 10:03 | 2012-08-08 11:12 | YORK - CMA06011A | 195 | 15.8 | Yes | Yes | 23.7 | 20.6 | 3.2 | DAE510B22B45409FA9E39F6F46BA4817 |  | R22 | Non-TXV |  | 8.103% | 0.91897 | 15.57% | [5 empty] | Non-TXV | 8.103%
Auburn | CA | 95602-9139 |  | 2012-08-08 | 2012-08-08 09:16 | 2012-08-08 09:16 | COLEMAN - UNK FADED | 58 | 0 | Yes | Yes | 20.6 | 20.1 | 0.6 | 9D69344C64A7418B8249047369C1F85B |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-7521 |  | 2012-06-14 | 2012-06-14 16:00 | 2012-06-14 16:16 | RHEEM - UNK | 85 | 7.2 | Yes | Yes | 20.6 | 19 | 1.6 | B4F9CC3ADB9A487F9DAA31E6DC513A93 |  | R22 | Non-TXV |  | 8.471% | 0.91529 | 16.28% | [5 empty] | Non-TXV | 8.471%
Fresno | CA | 93727-7006 |  | 2012-05-21 | 2012-05-21 10:42 | 2012-05-21 11:02 | RHEM - N/A | 70 | 2.1 | Yes | Yes | 24.6 | 19.8 | 4.8 | 7484A329ACF44777858409FDE0E6E9D3 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Auburn | CA | 95602-2151 |  | 2012-07-09 | 2012-07-09 14:42 | 2012-07-09 15:05 | CARRIER - 38GS024330 | 48 | 8.2 | Yes | Yes | 17.4 | 20.4 | -3 | 38AA4F40E1B344A3B9162851506DEA9F | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 17.08% | 0.82917 | 32.83% | [5 empty] | Non-TXV | 17.08%
Manteca | CA | 95336-2933 |  | 2012-08-06 | 2012-08-06 14:04 | 2012-08-06 14:32 | GOODMAN - GSC130481AA | 158 | 66 | Yes | Yes | 18.4 | 19.8 | -1.4 | 6AE65DB2C239419AB51670C10EFB840D |  | R22 | Non-TXV |  | 41.77% | 0.58228 | 80.28% | [5 empty] | Non-TXV | 41.77%
Manteca | CA | 95336-3237 |  | 2012-08-07 | 2012-08-07 09:37 | 2012-08-07 10:09 | TRANE - BTD736A100A0 | 88 | 3.7 | Yes | Yes | 18.3 | 19.3 | -1 | 6C6F663EBC52452CAE1C80178E547171 |  | R22 | Non-TXV |  | 4.205% | 0.95795 | 8.08% | [5 empty] | Non-TXV | 4.205%
Atwater | CA | 95301-8546 |  | 2012-05-08 | 2012-05-08 12:59 | 2012-05-08 13:20 | RHEEM - RRNA-B030JK06X | 72 | 4.2 | Yes | Yes | 25.1 | 22.3 | 2.8 | BE6690F20D2E41FBB7E34A10168DFEC4 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Stockton | CA | 95210-2277 |  | 2012-08-02 | 2012-08-02 13:51 | 2012-08-02 14:08 | BDP - 585HJ030040 | 68 | 2.2 | Yes | Yes | 24.5 | 20.4 | 4.1 | CC6D62487CBB4FCB808A64B3F49A4183 |  | R22 | Non-TXV |  | 3.235% | 0.96765 | 6.218% | [5 empty] | Non-TXV | 3.235%
Livingston | CA | 95334-1222 |  | 2012-05-16 | 2012-05-16 11:05 | 2012-05-16 11:31 | RHEEM - RRNL-B024JK06X | 79 | 2.4 | Yes | Yes | 18.5 | 18.7 | -0.2 | D8C2E526985A48B284DF97F244CDEF33 |  | R410A | Non-TXV |  | 3.038% | 0.96962 | 5.838% | [5 empty] | Non-TXV | 3.038%
Stockton | CA | 95207-1642 |  | 2012-08-06 | 2012-08-06 12:58 | 2012-08-06 13:17 | NORDYNE - GR4GA-060K096X | 87 | 15.9 | Yes | Yes | 24.9 | 20.4 | 4.5 | E05887BC7FD547149289F6D289131CDE |  | R22 | Non-TXV |  | 18.28% | 0.81724 | 35.12% | [5 empty] | Non-TXV | 18.28%
Merced | CA | 95348-2351 |  | 2012-05-14 | 2012-05-14 10:47 | 2012-05-14 11:19 | FRASER - UNK | 72 | 2.5 | Yes | Yes | 21.9 | 19.3 | 2.6 | 5BDC3B01378040BCB8EF0B6A5382BA3D |  | R22 | Non-TXV |  | 3.472% | 0.96528 | 6.673% | [5 empty] | Non-TXV | 3.472%
Chico | CA | 95928-4163 |  | 2012-05-08 | 2012-05-08 12:39 | 2012-05-08 12:39 | PAIN - PY3GNAA36090NA | 100 | 0 | Yes | Yes | 18.1 | 21 | -2.9 | 26B6E2A2E4594AC4BDC3A6E0191A77A4 | OK: Verified Refrigerant Charge | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95212-3489 |  | 2012-08-10 | 2012-08-10 15:45 | 2012-08-10 16:01 | CARRIER - AC036X1222A | 83 | 15.1 | Yes | Yes | 15.8 | 18 | -2.2 | E84E4AB4DD5A4A5CB3BA4F3B9CC5156A |  | R22 | Non-TXV |  | 18.19% | 0.81807 | 34.96% | [5 empty] | Non-TXV | 18.19%
Marysville | CA | 95901-9778 |  | 2012-08-03 | 2012-08-03 14:53 | 2012-08-03 14:53 | HEIL - A4S53683V1 | 93 | 0 | Yes | Yes | 22.5 | 19.3 | 3.2 | D887389A76DF4A588BFDA9A0AF485348 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-5942 |  | 2012-05-09 | 2012-05-09 11:02 | 2012-05-09 11:02 | CARRIER - N/A | 75 | 0 | Yes | Yes | 25.2 | 21.1 | 4.2 | 7DA902E0D61F415ABD4919941E4864AC | Liquid Temperature cannot be greater than condenser saturation temperature. Check entries and calibration. Actual Subcooling must be between -1°F and 50°F. Check liquid pressure and temperature entries. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Los Banos | CA | 93635-3251 |  | 2012-08-07 | 2012-08-07 12:11 | 2012-08-07 12:32 | RHEEM - RAPC048JAZ | 85 | 7.8 | Yes | Yes | 12.5 | 13.9 | -1.4 | 7F567DCEFFD04CDA96248AC66F432EF1 |  | R22 | Non-TXV |  | 9.176% | 0.90824 | 17.64% | [5 empty] | Non-TXV | 9.176%
Lathrop | CA | 95330-8834 |  | 2012-08-09 | 2012-08-09 13:49 | 2012-08-09 14:07 | GOODMAN - CKL36-1L | 84 | 3.1 | Yes | Yes | 23.6 | 21.5 | 2.2 | F8CBD6047F7142A2B9815DBFC3F33E64 |  | R22 | Non-TXV |  | 3.69% | 0.9631 | 7.092% | [5 empty] | Non-TXV | 3.69%
Marysville | CA | 95901-4419 |  | 2012-08-13 | 2012-08-13 15:43 | 2012-08-13 16:00 | LENNOX - 12GCS030X-75-3PB | 85 | 11.1 | Yes | Yes | 23.9 | 18.6 | 5.3 | 655CC4702D09431893FA2C18960F1DD3 |  | R22 | Non-TXV |  | 13.06% | 0.86941 | 25.1% | [5 empty] | Non-TXV | 13.06%
Marysville | CA | 95901-9759 |  | 2012-08-13 | 2012-08-13 14:07 | 2012-08-13 14:31 | BRYANT - BRCQ0361BD | 85 | 17.4 | Yes | Yes | 19.2 | 20.5 | -1.3 | 9247E7C5DEA84C0B9506AEC8D78C76CC | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 20.47% | 0.79529 | 39.34% | [5 empty] | Non-TXV | 20.47%
Stockton | CA | 95210-2744 |  | 2012-06-11 | 2012-06-11 09:32 | 2012-06-11 09:50 | BDP - 561CJ024-C | 72 | -5.1 | Yes | Yes | 20.8 | 19.8 | 1 | FDC9A1BECA98485A8F55398377736A7D |  | R22 | Non-TXV |  | -7.083% | 1.0708 | 1.984% |  |  |  |  | Non-TXV |  |  | -7.083%
Stockton | CA | 95205-4614 |  | 2012-08-16 | 2012-08-16 11:46 | 2012-08-16 12:06 | CARRIER - 48NMX036 | 84 | 4.4 | Yes | Yes | 18.6 | 19.3 | -0.7 | 11E44D8018734D9BB4A554C73C16B786 |  | R22 | Non-TXV |  | 5.238% | 0.94762 | 10.07% | [5 empty] | Non-TXV | 5.238%
Firebaugh | CA | 93622-2833 |  | 2012-07-09 | 2012-07-09 08:32 | 2012-07-09 08:52 | BDP - 588ANW030040ABAD | 53 | 1.6 | Yes | Yes | 24.9 | 19.9 | 5 | C4D923B6B6A54E8191D6DB88CCC9D44A |  | R22 | Non-TXV |  | 3.019% | 0.96981 | 5.802% | [5 empty] | Non-TXV | 3.019%
Marysville | CA | 95901-4287 |  | 2012-07-13 | 2012-07-13 08:53 | 2012-07-13 09:12 | BRYANT - 661CJO18-A09869 | 75 | 14.1 | Yes | Yes | 19 | 19.3 | -0.3 | 597DBE1B5ED34D2885EBA3A7B34B773B |  | R22 | Non-TXV |  | 18.8% | 0.812 | 36.13% | [5 empty] | Non-TXV | 18.8%
Clovis | CA | 93612-3665 |  | 2012-05-15 | 2012-05-15 11:56 | 2012-05-15 12:15 | CARIER - 38GS018310 | 48 | -2.8 | Yes | Yes | 19.2 | 20.4 | -1.2 | 228521160A23456DB62DA45C4F8465AB |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Stockton | CA | 95215-4847 |  | 2012-05-31 | 2012-05-31 11:04 | 2012-05-31 11:22 | TRANE - TTP036C100A3 | 132 | 6.8 | Yes | Yes | 20.5 | 21 | -0.5 | 4849F2F66430471C8B1C2C227F4ED609 |  | R22 | Non-TXV |  | 5.152% | 0.94848 | 9.9% | [5 empty] | Non-TXV | 5.152%
Marysville | CA | 95901-4286 |  | 2012-05-21 | 2012-05-21 10:39 | 2012-05-21 10:55 | GOODMAN - GSH13018 | 126 | -11.9 | Yes | Yes | 19 | 19.7 | -0.7 | 40DD446C76284D279FF6E93D82F7AA88 |  | R22 | Non-TXV |  | -9.444% | 1.0944 | 2.645% |  |  |  |  | Non-TXV |  |  | -9.444%
Stockton | CA | 95207-6053 |  | 2012-06-15 | 2012-06-15 11:26 | 2012-06-15 11:49 | GOODMAN - PGB024050-REVA | 54 | 10.8 | Yes | Yes | 16.4 | 19.1 | -2.7 | 3B704CA0D7534CB8BD0969A518AE4B9A |  | R22 | Non-TXV |  | 20% | 0.8 | 38.44% | [5 empty] | Non-TXV | 20%
Merced | CA | 95341-6940 |  | 2012-08-07 | 2012-08-07 12:48 | 2012-08-07 13:27 | YORK - D2NP036N05606A | 108 | 3.3 | Yes | Yes | 21.2 | 21.7 | -0.5 | 47C9A42A911D4BCCA60351B4AFE00B38 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Merced | CA | 95341-5784 |  | 2012-05-10 | 2012-05-10 10:18 | 2012-05-10 10:47 | PAYNE - 585HJ01840 | 61 | 2 | Yes | Yes | 22.4 | 21 | 1.4 | AF8CD9C50A914A24A8912DF3E7EC4CF3 |  | R22 | Non-TXV |  | 3.279% | 0.96721 | 6.301% | [5 empty] | Non-TXV | 3.279%
Dinuba | CA | 93618-2456 |  | 2012-05-09 | 2012-05-09 19:16 | 2012-05-09 19:49 | GOODMAN - GPG10240451A | 50 | 4.9 | Yes | Yes | 27.3 | 22 | 5.3 | 68833BD2BFA54DA3899DFA778290455D | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 9.8% | 0.902 | 18.83% | [5 empty] | Non-TXV | 9.8%
Plumas Lake | CA | 95961-9103 |  | 2012-07-18 | 2012-07-18 13:55 | 2012-07-18 14:14 | CARRIER - 38CKC0300340 | 70 | -4.9 | Yes | Yes | 17 | 19.2 | -2.2 | 6350963A56E540A3A48605C8CD4DAC2E |  | R22 | Non-TXV |  | -7% | 1.07 | 1.96% |  |  |  |  | Non-TXV |  |  | -7%
Los Banos | CA | 93635-3169 |  | 2012-08-07 | 2012-08-07 10:13 | 2012-08-07 10:38 | RHEEM - RAKA030JAS | 68 | 9.9 | Yes | Yes | 20.5 | 21.4 | -0.9 | 0D9D1A4B27D843E49D203580AA1F8D11 |  | R22 | Non-TXV |  | 14.56% | 0.85441 | 27.98% | [5 empty] | Non-TXV | 14.56%
San Andreas | CA | 95249-9722 |  | 2012-07-19 | 2012-07-19 10:24 | 2012-07-19 10:40 | BRYANT - 561CJ036-E | 74 | 2.2 | Yes | Yes | 18.9 | 19.4 | -0.5 | 98E63F210A4B46F2A08E9A0F3620DDAB |  | R22 | Non-TXV |  | 2.973% | 0.97027 | 5.713% | [5 empty] | Non-TXV | 2.973%
Planada | CA | 95365-8013 |  | 2012-08-14 | 2012-08-14 12:14 | 2012-08-14 12:38 | BRYANT - 582ANW036060NBAF | 68 | 2.3 | Yes | Yes | 24.6 | 20.4 | 4.3 | 091FC5034F5E4920A563CE6455FCA997 |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Stockton | CA | 95207-2357 |  | 2012-08-07 | 2012-08-07 10:20 | 2012-08-07 10:20 | PAYNE - RCB36C2A | 85 | 0 | Yes | Yes | 17.1 | 17.9 | -0.8 | D352716F91FE4AC6B048AD19C65ECFF5 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Chowchilla | CA | 93610-3404 |  | 2012-05-24 | 2012-05-24 12:47 | 2012-05-24 12:47 | AERICAN STANDARD - 4YCY4024A164AA | 93 | 0 | Yes | Yes | 23 | 21.1 | 2 | 255F885E7627497183F28DBC0424CFD9 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-3542 |  | 2012-08-06 | 2012-08-06 13:29 | 2012-08-06 13:49 | RHEEM - RRMAA042JK08X | 114 | 13.1 | Yes | Yes | 22.6 | 21 | 1.6 | FBAC5D2E50D34A32AF8C837E21B58698 |  | R22 | Non-TXV |  | 11.49% | 0.88509 | 22.08% | [5 empty] | Non-TXV | 11.49%
Chico | CA | 95926-7742 |  | 2012-05-08 | 2012-05-08 13:40 | 2012-05-08 14:04 | LENNOX - HS14-651V-3P | 195 | 9.9 | Yes | Yes | 20.7 | 23.3 | -2.6 | 6F6F5B7E25DB4713BB59E3BE38DB2FFD | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 5.077% | 0.94923 | 9.757% | [5 empty] | Non-TXV | 5.077%
Chico | CA | 95926-7742 |  | 2012-05-08 | 2012-05-08 14:06 | 2012-05-08 15:05 | LENNOX - HS14-511U-3P | 195 | 8.5 | Yes | Yes | 23 | 22.2 | 0.8 | 6518807D872B43BC9C47D958FE5B86B3 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.359% | 0.95641 | 8.377% | [5 empty] | Non-TXV | 4.359%
Stockton | CA | 95205-2484 |  | 2012-08-09 | 2012-08-09 10:24 | 2012-08-09 10:40 | OTHER - B33JK | 54 | 4.2 | Yes | Yes | 17.8 | 20.4 | -2.6 | BAA8664E825347128736F361985F17E3 |  | R22 | Non-TXV |  | 7.778% | 0.92222 | 14.95% | [5 empty] | Non-TXV | 7.778%
Clovis | CA | 93611-0609 |  | 2012-08-16 | 2012-08-16 19:17 | 2012-08-16 19:36 | OTHER - 100WR42G1NA | 85 | 2.6 | Yes | Yes | 16.5 | 19.3 | -2.8 | E8E77BCD5BCA42C6A4D15272D4DA23E9 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Manteca | CA | 95336-3614 |  | 2012-05-30 | 2012-05-30 15:49 | 2012-05-30 16:06 | RHEEM - UNK | 54 | 3 | Yes | Yes | 16.4 | 16.4 | 0 | 9F485ECDB7AD4882B5D8F782F66D0DE8 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.556% | 0.94444 | 10.68% | [5 empty] | Non-TXV | 5.556%
Stockton | CA | 95210-2744 |  | 2012-06-11 | 2012-06-11 08:17 | 2012-06-11 08:36 | BRYANT - 113RNA030-B | 84 | -4.9 | Yes | Yes | 22 | 19.1 | 2.9 | 6F7B9897989F4ECAB816E6165C5B7746 |  | R22 | Non-TXV |  | -5.833% | 1.0583 | 1.634% |  |  |  |  | Non-TXV |  |  | -5.833%
Manteca | CA | 95337-5421 |  | 2012-05-10 | 2012-05-10 13:34 | 2012-05-10 14:01 | BRYANT - 583BNW042090AAF | 144 | 6.1 | Yes | Yes | 28.4 | 22.5 | 5.9 | 3B1632170DB04957AA408DD678016F9D | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 4.236% | 0.95764 | 8.141% | [5 empty] | Non-TXV | 4.236%
Merced | CA | 95340-3450 |  | 2012-05-07 | 2012-05-07 17:12 | 2012-05-07 17:12 | AMERICAN STANDER - 2YCX3048A1096AA | 144 | 0 | Yes | Yes | 26.8 | 24.5 | 2.4 | 559ECA293B2D4FE8BD88154A379290F0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 0% | 1 | 0%
Fresno | CA | 93725-1523 |  | 2012-08-10 | 2012-08-10 12:20 | 2012-08-10 12:38 | BDP - 585B030075 | 90 | 3.7 | Yes | Yes | 17.8 | 19.5 | -1.7 | 706B4B2BB4774641ADBC4E26A14E21C6 | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.111% | 0.95889 | 7.901% | [5 empty] | Non-TXV | 4.111%
Stockton | CA | 95210-4498 |  | 2012-05-24 | 2012-05-24 14:00 | 2012-05-24 14:17 | BDP - 561AJ030-A | 67 | 12.6 | Yes | Yes | 24.1 | 22.9 | 1.3 | DC875F9DF1EC4D4FB616D7C0B7226E0E |  | R22 | Non-TXV |  | 18.81% | 0.81194 | 36.14% | [5 empty] | Non-TXV | 18.81%
Stockton | CA | 95210-2717 |  | 2012-06-13 | 2012-06-13 13:08 | 2012-06-13 13:24 | PAYNE - PY3PNA030060NB | 96 | 4 | Yes | Yes | 25.3 | 19.3 | 6 | 262ED73E0E124C0CAE705809CAFA21B5 |  | R22 | Non-TXV |  | 4.167% | 0.95833 | 8.007% | [5 empty] | Non-TXV | 4.167%
Merced | CA | 95340-0914 |  | 2012-05-07 | 2012-05-07 14:22 | 2012-05-07 14:44 | GOODMAN - GPG13300701BB | 85 | 5.1 | Yes | Yes | 24.9 | 20.7 | 4.2 | 7F78672EDD9346A492715EFE8402C82F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 6% | 0.94 | 11.53% | [5 empty] | Non-TXV | 6%
Stockton | CA | 95207-2735 |  | 2012-06-19 | 2012-06-19 09:56 | 2012-06-19 09:56 | RHEEM - RRNL-BO24JK06X | 78 | 0 | Yes | Yes | 19.7 | 18 | 1.7 | 620F48F634E74998AF5895EF1C0D9114 |  | R22 | TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-5734 |  | 2012-05-14 | 2012-05-14 13:57 | 2012-05-14 14:17 | BRYANT - 561CJ048-A | 110 | -5.7 | Yes | Yes | 23.5 | 20.4 | 3.1 | 228CDBFAB54042B7B5BD3F26B9E125EF | OK: Verified Refrigerant Charge | R22 | TXV |  | -5.182% | 1.0518 | 1.451% |  |  |  |  | TXV |  |  | -5.182%
Lathrop | CA | 95330-9432 |  | 2012-05-31 | 2012-05-31 10:17 | 2012-05-31 10:38 | OTHER - AC036GA | 76 | 2.4 | Yes | Yes | 23.2 | 19.4 | 3.8 | 4A2E0FC510AA4105B78BED80D09DF690 |  | R22 | Non-TXV |  | 3.158% | 0.96842 | 6.069% | [5 empty] | Non-TXV | 3.158%
El Dorado | CA | 95623-4256 |  | 2012-07-26 | 2012-07-26 11:14 | 2012-07-26 11:14 | - DCYP-F024N045XB | 100 | 0 | Yes | Yes | 17.8 | 19.7 | -1.9 | 10E3640039DA4C07803D88ED01CA8732 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2507 |  | 2012-08-08 | 2012-08-08 11:41 | 2012-08-08 12:15 | OTHER - H1RA024S06D | 59 | 9.3 | Yes | Yes | 17 | 19.9 | -2.9 | 3F8208D14EF84430BCDE40630473F072 |  | R22 | Non-TXV |  | 15.76% | 0.84237 | 30.29% | [5 empty] | Non-TXV | 15.76%
Newman | CA | 95360-1521 |  | 2012-05-17 | 2012-05-17 09:33 | 2012-05-17 09:51 | RHEEM - RRNA-A042JK08X | 114 | 3.4 | Yes | Yes | 22.8 | 19.1 | 3.7 | F3148128C7124A7693D44DFD8F2C282E |  | R22 | Non-TXV |  | 2.982% | 0.97018 | 5.732% | [5 empty] | Non-TXV | 2.982%
Madera | CA | 93638-4844 |  | 2012-08-10 | 2012-08-10 13:32 | 2012-08-10 14:19 | YORK - D1NQ042N06506NXA | 72 | 2.6 | Yes | Yes | 21.1 | 20.2 | 0.9 | A3F64F3F142D4C21A5A0EE43C067FDA7 |  | R410A | Non-TXV |  | 3.611% | 0.96389 | 6.94% | [5 empty] | Non-TXV | 3.611%
Fresno | CA | 93725-1740 |  | 2012-05-11 | 2012-05-11 15:52 | 2012-05-11 16:12 | CARRIER - 48SS-36080321 | 67 | 2.3 | Yes | Yes | 22.7 | 23.2 | -0.5 | F16137190E8349C0BBA13EC4A6D9A848 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 3.433% | 0.96567 | 6.597% | [5 empty] | Non-TXV | 3.433%
Penn Valley | CA | 95946-9105 |  | 2012-08-14 | 2012-08-14 16:26 | 2012-08-14 16:48 | RHEEM - 13PJA42A01 | 150 | -37.8 | Yes | Yes | 20.5 | 19.9 | 0.6 | EA6CACF839ED4775B95AA771FE0BF422 |  | R22 | TXV |  | -25.2% | 1.252 | 7.057% |  |  |  |  | TXV |  |  | -25.2%
Cameron Park | CA | 95682-7629 |  | 2012-08-07 | 2012-08-07 16:07 | 2012-08-07 16:24 | RUUD - 13AJN42A01 | 106 | -7.2 | Yes | Yes | 22.1 | 19.7 | 2.4 | 8A8736894CAD4DC3A1FDC4DB9D1E7C5C |  | R410A | TXV |  | -6.792% | 1.0679 | 1.902% |  |  |  |  | TXV |  |  | -6.792%
Chico | CA | 95973-0547 |  | 2012-08-09 | 2012-08-09 12:52 | 2012-08-09 18:25 | COLEMAN - PRCS0361BD | 98 | 7.8 | Yes | Yes | 23.5 | 20.2 | 3.3 | C3C666C00046478B864F7C256C533764 |  | R22 | Non-TXV |  | 7.959% | 0.92041 | 15.3% | [5 empty] | Non-TXV | 7.959%
Chowchilla | CA | 93610-2760 |  | 2012-05-21 | 2012-05-21 13:06 | 2012-05-21 13:39 | CARRIER - UNK | 88 | 4.4 | Yes | Yes | 25.8 | 22.1 | 3.7 | FC7FDD80DE034F2980D696367E3618AE |  | R22 | Non-TXV |  | 5% | 0.95 | 9.609% | [5 empty] | Non-TXV | 5%
Atascadero | CA | 93422-5575 |  | 2012-07-10 | 2012-07-10 14:19 | 2012-07-10 14:37 | RHEEM - RACA-018AAQ | 30 | 3.3 | Yes | Yes | 19.6 | 19.4 | 0.2 | 3A6194B250204B53BB83BF70F19F12DA |  | R22 | Non-TXV |  | 11% | 0.80588 | 37.31% | [5 empty] | Non-TXV | 11%
Stockton | CA | 95210-3330 |  | 2012-08-03 | 2012-08-03 10:06 | 2012-08-03 10:24 | INTERTHERM - ACC-042BCRAA | 80 | -4.7 | Yes | Yes | 21.8 | 19.7 | 2.1 | 8D4F1BBC18BB44908B035E2F027F6019 |  | R22 | Non-TXV |  | -5.875% | 1.0588 | 1.645% |  |  |  |  | Non-TXV |  |  | -5.875%
Grass Valley | CA | 95945-8682 |  | 2012-08-14 | 2012-08-14 13:12 | 2012-08-14 13:12 | GOODMAN - PGB042100-1 | 68 | 0 | Yes | Yes | 22.5 | 19.3 | 3.2 | BF3CA5C291504F268D5FB211764A2ECE | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3738 |  | 2012-05-11 | 2012-05-11 11:39 | 2012-05-11 12:00 | STANDARD - 7B0023B100A1 | 54 | 1.6 | Yes | Yes | 18.5 | 20.3 | -1.8 | 795CA8DC76A84E678EC3D1DF5C11FF77 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 2.963% | 0.97037 | 5.694% | [5 empty] | Non-TXV | 2.963%
Merced | CA | 95341-5837 |  | 2012-08-07 | 2012-08-07 12:21 | 2012-08-07 12:46 | COMFORT AIRE - GPCM030K060D | 51 | 3.7 | Yes | Yes | 20.2 | 20.7 | -0.4 | 7F65D77EA5EE4267BC26648DE98EF523 |  | R22 | Non-TXV |  | 7.255% | 0.92745 | 13.94% | [5 empty] | Non-TXV | 7.255%
Magalia | CA | 95954-9550 |  | 2012-05-30 | 2012-05-30 11:32 | 2012-05-30 11:49 | COLMAN - 9548A901 | 80 | 10.7 | Yes | Yes | 20.5 | 20.8 | -0.3 | 7078732C3FE04EB6815831B30E990CEE |  | R22 | Non-TXV |  | 13.38% | 0.86625 | 25.7% | [5 empty] | Non-TXV | 13.38%
Los Banos | CA | 93635-4543 |  | 2012-05-22 | 2012-05-22 15:52 | 2012-05-22 16:14 | BRYANT - 563CN036-A | 122 | -4.6 | Yes | Yes | 21.5 | 22 | -0.5 | E477A5E164684827A0521BC6819858AF |  | R22 | TXV |  | -3.77% | 1.0377 | 1.056% |  |  |  |  | TXV |  |  | -3.77%
Madera | CA | 93638-3498 |  | 2012-06-12 | 2012-06-12 13:28 | 2012-06-12 13:28 | AIRE-FLO - 48SS024040321 | 38 | 0 | Yes | Yes | 26 | 28.6 | -2.6 | 6C63AFFD16AA4BD68B74C918BC15ED26 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95210-3599 |  | 2012-05-31 | 2012-05-31 15:09 | 2012-05-31 15:25 | AMERICAN STANDARD - ID718B100A0 | 50 | 1.7 | Yes | Yes | 19.5 | 19.9 | -0.4 | FE9E2A78318245CA9F70999316815F48 |  | R22 | Non-TXV |  | 3.4% | 0.966 | 6.534% | [5 empty] | Non-TXV | 3.4%
Clovis | CA | 93612-3454 |  | 2012-08-13 | 2012-08-13 17:06 | 2012-08-13 17:22 | ARCOAIRE - RD030CA | 60 | 1.8 | Yes | Yes | 18 | 20.1 | -2.1 | 1A8104EF5750415792CACEC0EE70D8B1 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Gustine | CA | 95322-1612 |  | 2012-08-13 | 2012-08-13 10:27 | 2012-08-13 10:27 | RHEEM - RRNL-B030JK06X | 76 | 0 | Yes | Yes | 21 | 20.1 | 0.9 | EBFD4248D6F74B2EA4479AA6134BCB54 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Clovis | CA | 93611-4578 |  | 2012-08-13 | 2012-08-13 19:04 | 2012-08-13 19:35 | DAY & NIGHT - 5850367YACR | 76 | 2.6 | Yes | Yes | 18.2 | 19.8 | -1.6 | A0C2686CF3A3412E8F23C8009AC9CA56 |  | R22 | Non-TXV |  | 3.421% | 0.96579 | 6.575% | [5 empty] | Non-TXV | 3.421%
Stockton | CA | 95205-4104 |  | 2012-05-15 | 2012-05-15 12:15 | 2012-05-15 12:32 | HEIL - PGAA30C1K3 | 75 | 4.1 | Yes | Yes | 18.4 | 21 | -2.6 | 03F1F936B37D4F71B3F577798AD638D5 |  | R22 | Non-TXV |  | 5.467% | 0.94533 | 10.51% | [5 empty] | Non-TXV | 5.467%
Grass Valley | CA | 95945-6639 |  | 2012-05-30 | 2012-05-30 14:39 | 2012-05-30 14:39 | RHEEM - UNK | 58 | 0 | Yes | Yes | 22.7 | 19.1 | 3.6 | A460C9C62CDE4A10A814A00033DF8C2B | OK: Verified Refrigerant Charge. Superheat recommendation is opposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Stockton | CA | 95206-2109 |  | 2012-05-07 | 2012-05-07 18:54 | 2012-05-07 19:14 | GOODMAN - CLJ36-1A | 90 | -10.3 | Yes | Yes | 17.5 | 20.2 | -2.7 | 79B9D2A5506D42B99AE0056EDF31D2B0 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | -11.44% | 1.1144 | 3.205% |  |  |  |  | Non-TXV |  |  | -11.44%
Fresno | CA | 93727-7005 |  | 2012-05-30 | 2012-05-30 15:33 | 2012-05-30 15:59 | RHEEM - N/A | 60 | 3.5 | Yes | Yes | 21.2 | 21 | 0.2 | 3107B206423E4E4698714B974004141D | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 5.833% | 0.94167 | 11.21% | [5 empty] | Non-TXV | 5.833%
Yuba City | CA | 95993-7140 |  | 2012-05-10 | 2012-05-10 10:30 | 2012-05-10 10:54 | BDP COMPANY - 565BJ024 | 70 | 6 | Yes | Yes | 23.6 | 20.1 | 3.5 | 36D463DD906A4447B8943D80CB492DE1 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 8.571% | 0.91429 | 16.47% | [5 empty] | Non-TXV | 8.571%
Stockton | CA | 95207-1150 |  | 2012-06-22 | 2012-06-22 12:39 | 2012-06-22 12:58 | RHEEM - RRNA-B024JK06X | 77 | 9.7 | Yes | Yes | 18.3 | 19.2 | -0.9 | 83BB72F6EB9A4E5BBA6B87725564A750 |  | R22 | TXV |  | 12.6% | 0.87403 | 24.21% | [5 empty] | TXV | 12.6%
Merced | CA | 95348-1547 |  | 2012-05-08 | 2012-05-08 17:46 | 2012-05-08 18:03 | RHEEM - N/A | 50 | 1.9 | Yes | Yes | 23.7 | 23.7 | 0 | 40BF91DFAEF34ED49165B4445D1AF18B | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.8% | 0.962 | 7.303% | [5 empty] | Non-TXV | 3.8%
Yuba City | CA | 95991-1511 |  | 2012-07-24 | 2012-07-24 13:48 | 2012-07-24 14:04 | NORDYNE - GR4GA-024K045X | 70 | 2.1 | Yes | Yes | 27 | 21.1 | 5.9 | 6832AC527A124AC5960C2C0CE5F07BB4 |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Yuba City | CA | 95993-2737 |  | 2012-05-10 | 2012-05-10 14:34 | 2012-05-10 14:34 | CARRIER - 48GX-024040301AD | 55 | 0 | Yes | Yes | 21.3 | 20.9 | 0.4 | 34DB4DEC92184E9E9323A4A3FB2D8F74 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Yuba City | CA | 95991-1568 |  | 2012-07-26 | 2012-07-26 11:13 | 2012-07-26 11:37 | DAY & NIGHT - 540AJ018 | 83 | -7.8 | Yes | Yes | 17 | 19.9 | -2.9 | 32D69A8048CF45A3AE7EF303F5199C42 |  | R22 | Non-TXV |  | -9.398% | 1.094 | 2.632% |  |  |  |  | Non-TXV |  |  | -9.398%
Madera | CA | 93638-3712 |  | 2012-06-12 | 2012-06-12 09:56 | 2012-06-12 10:15 | NORDYNE - GR6GDX30K045X | 96 | 6.7 | Yes | Yes | 27.6 | 21.7 | 5.9 | E19042BF40CD42CA928BB9034DF00E85 |  | R410A | Non-TXV |  | 6.979% | 0.93021 | 13.41% | [5 empty] | Non-TXV | 6.979%
Fresno | CA | 93710-6519 |  | 2012-05-11 | 2012-05-11 13:44 | 2012-05-11 14:01 | - | 85 | 2.6 | Yes | Yes | 18.1 | 21 | -2.9 | C6B5259AD07C4CDE8995DCF8014D73E4 |  | R22 | Non-TXV |  | 3.059% | 0.96941 | 5.878% | [5 empty] | Non-TXV | 3.059%
Lodi | CA | 95240-9714 |  | 2012-06-25 | 2012-06-25 09:58 | 2012-06-25 10:16 | ICP - PGAD30D1K5 | 78 | -4.6 | Yes | Yes | 20.4 | 19.1 | 1.3 | 26382BFA7A31489095EEA1240F968D97 |  | R22 | Non-TXV |  | -5.897% | 1.059 | 1.652% |  |  |  |  | Non-TXV |  |  | -5.897%
Caruthers | CA | 93609-9713 |  | 2012-06-15 | 2012-06-15 12:06 | 2012-06-15 12:43 | LENNOX - GCS29X-042-75-1PA | 73 | 8.8 | Yes | Yes | 19.2 | 20.7 | -1.5 | 12EC2AE277BC41D9AE856508EC4CEB70 |  | R22 | Non-TXV |  | 12.05% | 0.87945 | 23.17% | [5 empty] | Non-TXV | 12.05%
Live Oak | CA | 95953-2072 |  | 2012-05-24 | 2012-05-24 13:21 | 2012-05-24 13:21 | TRANE - TTR030C100A2 | 74 | 0 | Yes | Yes | 20.4 | 19.7 | 0.7 | 179E6BD4457C424E9017DA924C408572 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 0% | 1 | 0%
Madera | CA | 93637-5411 |  | 2012-05-16 | 2012-05-16 15:05 | 2012-05-16 15:26 | YORK - DCYZ-F036N070 | 65 | 2 | Yes | Yes | 18.4 | 20.4 | -2 | B98C3E0664FA412C95706670745B9AFB |  | R22 | Non-TXV |  | 3.077% | 0.96923 | 5.913% | [5 empty] | Non-TXV | 3.077%
Los Banos | CA | 93635-3140 |  | 2012-05-10 | 2012-05-10 11:29 | 2012-05-10 11:29 | DAY AND NIGHT - 588ANW024040ACAD | 48 | 0 | Yes | Yes | 19.4 | 20.2 | -0.8 | 9A418BA6DF3D4C23A74EAFB1A54D15DE | OK: Verified Refrigerant Charge. |  |  |  | 0% | 1 | 0%
Yuba City | CA | 95993-5219 |  | 2012-05-09 | 2012-05-09 13:26 | 2012-05-09 13:26 | CARRIER - 48GS-030060301-- | 59 | 0 | Yes | Yes | 25.8 | 22.1 | 3.7 | 51DB9171C6F64F56A6D3D4AAF552AC8F | OK: Verified Refrigerant Charge. Condenser saturation temperature > 27°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 0% | 1 | 0%
Grass Valley | CA | 95945-4123 |  | 2012-05-16 | 2012-05-16 11:18 | 2012-05-16 11:40 | FRASER-JOHNSTON - HDEC-F018SC | 56 | 8.5 | Yes | Yes | 17 | 19.8 | -2.8 | 25817844138D4A8ABBC18751C188F279 | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 15.18% | 0.84821 | 29.17% | [5 empty] | Non-TXV | 15.18%
Oakdale | CA | 95361-3394 |  | 2012-05-24 | 2012-05-24 12:23 | 2012-05-24 12:52 | DAY & NIGHT - 591ANX048000ABAA | 115 | 3.4 | Yes | Yes | 17.7 | 19.3 | -1.6 | F86711F443FD4979B482BEC428D6A6E1 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 29°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 2.957% | 0.97043 | 5.682% | [5 empty] | Non-TXV | 2.957%
Caruthers | CA | 93609-9440 |  | 2012-06-14 | 2012-06-14 13:00 | 2012-06-14 13:25 | ECONAIR - BRCS048B | 111 | 9.7 | Yes | Yes | 23.5 | 20.4 | 3.1 | F4236A9063BD4DE78A78FD5AD496BE9C | OK: Verified Refrigerant Charge. Condenser saturation temperature > 26°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 8.739% | 0.91261 | 16.79% | [5 empty] | Non-TXV | 8.739%
Stockton | CA | 95206-1650 |  | 2012-05-07 | 2012-05-07 19:45 | 2012-05-07 19:45 | CARRIER - 38CKCO30340 | 85 | 0 | Yes | Yes | 24.5 | 22.2 | 2.3 | A716E35F4DC14B7285669D8697168D67 | OK: Verified Refrigerant Charge | R22 | Non-TXV |  | 0% | 1 | 0%
Gustine | CA | 95322-1620 |  | 2012-05-15 | 2012-05-15 14:04 | 2012-05-15 14:23 | RHEEM - RRNA-B030JK06X | 72 | 6.5 | Yes | Yes | 19.7 | 19.3 | 0.4 | 6DF76EABA7CA41A8B887D2FCA7DF84CB |  | R22 | Non-TXV |  | 9.028% | 0.90972 | 17.35% | [5 empty] | Non-TXV | 9.028%
Stockton | CA | 95209-1234 |  | 2012-05-22 | 2012-05-22 11:57 | 2012-05-22 12:14 | DAYNIGHT - 585A024055YACR | 51 | 7.5 | Yes | Yes | 20.1 | 19 | 1.1 | A38CF588239F4DF28E2CAD6734B86B10 |  | R22 | Non-TXV |  | 14.71% | 0.85294 | 28.26% | [5 empty] | Non-TXV | 14.71%
Auburn | CA | 95603-3737 |  | 2012-05-15 | 2012-05-15 11:16 | 2012-05-15 11:16 | STANDARD - 7B0023B100A1 | 54 | 0 | Yes | Yes | 18 | 20.2 | -2.2 | AB6D84B9F5E545149A12D14EAA308F8D |  | R22 | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95341-7722 |  | 2012-05-10 | 2012-05-10 12:59 | 2012-05-10 13:18 | RHEEM - RAKA030AZ | 85 | 3.7 | Yes | Yes | 27 | 21 | 6 | CD3562ACBEA248459219F90A1F03C80F | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Auburn | CA | 95603-3738 |  | 2012-05-10 | 2012-05-10 11:12 | 2012-05-10 11:33 | STANDARD - 7B0023B100A1 | 54 | 2.8 | Yes | Yes | 16.5 | 18.5 | -2 | 8311D59B9B3C4041AC9CD454343933CD | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 5.185% | 0.94815 | 9.965% | [5 empty] | Non-TXV | 5.185%
Stockton | CA | 95206-4845 |  | 2012-05-30 | 2012-05-30 11:31 | 2012-05-30 11:49 | GOODMAN - CKL36-1H | 71 | 6.3 | Yes | Yes | 19.4 | 19.9 | -0.5 | B95E46B74523409F8C4BF044E639E899 |  | R22 | Non-TXV |  | 8.873% | 0.91127 | 17.05% | [5 empty] | Non-TXV | 8.873%
Auburn | CA | 95603-3742 |  | 2012-05-10 | 2012-05-10 13:25 | 2012-05-10 13:44 | STANDARD - 7B0023B100A1 | 54 | 11 | Yes | Yes | 22 | 19.9 | 2.1 | 80855427D7924BEBA75DA0D2B9B80A91 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 20.37% | 0.7963 | 39.15% | [5 empty] | Non-TXV | 20.37%
Stockton | CA | 95210-2319 |  | 2012-05-16 | 2012-05-16 14:04 | 2012-05-16 14:21 | PAYNE - 24/60YAC-108C | 51 | 1.6 | Yes | Yes | 22.1 | 19.2 | 2.9 | 1E3CC6BA74FE4F04A98D93D405F9CC4A |  | R22 | Non-TXV |  | 3.137% | 0.96863 | 6.029% | [5 empty] | Non-TXV | 3.137%
Rocklin | CA | 95677-3179 |  | 2012-05-11 | 2012-05-11 15:24 | 2012-05-11 15:24 | CARRIER - 38EN018310SM | 59 | 0 | Yes | Yes | -0.2 | 22.5 | -22.7 | F7E95C4BD74F4CC3B38D12B9E3109C4D | Actual Subcooling must be between -1°F and 45°F. Check liquid pressure and temperature entries. Actual Superheat must be between -2°F and 100°F. Check entries and calibration. Evaporator saturation temperature is <25°F. Please check entries. | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3744 |  | 2012-05-15 | 2012-05-15 13:23 | 2012-05-15 13:47 | STANDARD - 7B0023B100A1 | 54 | 10.9 | Yes | Yes | 18 | 18.8 | -0.8 | 23419A214189479CBB42F5443D07B536 |  | R22 | Non-TXV |  | 20.19% | 0.79815 | 38.79% | [5 empty] | Non-TXV | 20.19%
Manteca | CA | 95336-3045 |  | 2012-05-18 | 2012-05-18 13:32 | 2012-05-18 13:50 | BRYANT - 598BN060-A | 200 | 7.3 | Yes | Yes | 19.4 | 20.4 | -1 | 9D88F97B11B248CEB7CF4C3FB61B820B | OK: Verified Refrigerant Charge | R410A | TXV |  | 3.65% | 0.9635 | 7.014% | [5 empty] | TXV | 3.65%
Auburn | CA | 95603-3742 |  | 2012-05-15 | 2012-05-15 11:59 | 2012-05-15 12:19 | STANDARD - 7B0023B100A1 | 54 | 9.5 | Yes | Yes | 20 | 19.3 | 0.7 | CC62D1843BD04B18BA9F210561424B6A |  | R22 | Non-TXV |  | 17.59% | 0.82407 | 33.81% | [5 empty] | Non-TXV | 17.59%
Stockton | CA | 95210-6630 |  | 2012-06-20 | 2012-06-20 09:28 | 2012-06-20 09:45 | CARRIER - 38TD036300 | 187 | 6.8 | Yes | Yes | 20.9 | 19.3 | 1.6 | C194372252D549FEBD4B0B6B84B5008F |  | R22 | TXV |  | 3.636% | 0.96364 | 6.988% | [5 empty] | TXV | 3.636%
Auburn | CA | 95602-2181 |  | 2012-07-12 | 2012-07-12 08:24 | 2012-07-12 08:51 | OTHER - UNK | 65 | 5.5 | Yes | Yes | 19 | 20.9 | -1.9 | 662D578567D24F459549495EC5E44B83 |  | R22 | Non-TXV |  | 8.462% | 0.91538 | 16.26% | [5 empty] | Non-TXV | 8.462%
Stockton | CA | 95210-6626 |  | 2012-05-21 | 2012-05-21 12:38 | 2012-05-21 12:55 | GOODMAN - CM18-1EB | 49 | 1.8 | Yes | Yes | 18.2 | 19.9 | -1.7 | 7B1BB6F0B700412685B6A8845177E663 |  | R22 | Non-TXV |  | 3.673% | 0.96327 | 7.06% | [5 empty] | Non-TXV | 3.673%
Auburn | CA | 95603-3738 |  | 2012-05-14 | 2012-05-14 12:12 | 2012-05-14 12:12 | STANDARD - 7B0023B100A1 | 54 | 0 | Yes | Yes | 19 | 19.5 | -0.5 | A678F7C3ADAB4C648714CC893CB406D6 |  | R22 | Non-TXV |  | 0% | 1 | 0%
Auburn | CA | 95603-3737 |  | 2012-05-14 | 2012-05-14 10:16 | 2012-05-14 10:36 | STANDARD - 7B0023B100A1 | 54 | 9.1 | Yes | Yes | 16 | 18.8 | -2.8 | 422F5CFE7F514B478AB5534CBB3D0202 |  | R22 | Non-TXV |  | 16.85% | 0.83148 | 32.39% | [5 empty] | Non-TXV | 16.85%
Rocklin | CA | 95765-5165 |  | 2012-05-23 | 2012-05-23 15:21 | 2012-05-23 15:42 | GOODMAN - CKT42-1AB | 132 | -10.4 | Yes | Yes | 20 | 20.3 | -0.3 | 08FF74C5DD7C4D1EAB83586E7F8119F0 |  | R22 | TXV |  | -7.879% | 1.0788 | 2.206% |  |  |  |  | TXV |  |  | -7.879%
Stockton | CA | 95209-2345 |  | 2012-06-21 | 2012-06-21 11:40 | 2012-06-21 11:40 | RHEEM - RRNL-B024JK06X | 78 | 0 | Yes | Yes | 18.5 | 21 | -2.5 | B2D11EE677944636BB4D8E7465FBF365 |  |  |  |  | 0% | 1 | 0%
Livingston | CA | 95334-1222 |  | 2012-05-08 | 2012-05-08 10:06 | 2012-05-08 10:31 | RHEEM - RRNL-BO24JK06X | 78 | 2.3 | Yes | Yes | 19 | 19 | 0 | CB0D6A9BA20D45CA9C366002A6349C4B | OK: Verified Refrigerant Charge. | R410A | Non-TXV |  | 2.949% | 0.97051 | 5.667% | [5 empty] | Non-TXV | 2.949%
Tracy | CA | 95377-7963 |  | 2012-06-25 | 2012-06-25 10:35 | 2012-06-25 10:54 | CARRIER - 38CMC060300 | 160 | 4.8 | Yes | Yes | 17.5 | 18.7 | -1.2 | 308D4DB6381E42DB92DC9D849DAFBF7F |  | R22 | Non-TXV |  | 3% | 0.97 | 5.765% | [5 empty] | Non-TXV | 3%
Marysville | CA | 95901-3564 |  | 2012-05-15 | 2012-05-15 12:44 | 2012-05-15 12:44 | BRYANT - 574DNWA24040NA | 77 | 0 | Yes | Yes | 24 | 19.9 | 4.1 | 8F23626B71204E74A6F11398A881FF6A | OK: Verified Refrigerant Charge | R410A | TXV |  | 0% | 1 | 0%
Stockton | CA | 95207-2355 |  | 2012-06-06 | 2012-06-06 15:48 | 2012-06-06 16:10 | RHEEM - RRNL-B024JKO6X | 78 | 8.6 | Yes | Yes | 19.2 | 21.3 | -2.1 | 6CFF7C45233B44888B619F31A04FAD2A |  | R410A | TXV |  | 11.03% | 0.88974 | 21.19% | [5 empty] | TXV | 11.03%
Stockton | CA | 95209-2750 |  | 2012-05-21 | 2012-05-21 09:20 | 2012-05-21 09:36 | DAYNIGHT - 585A024055YACR | 52 | 3.8 | Yes | Yes | 23.5 | 19.9 | 3.6 | E6566D40A7B1439790AB5262666EA858 |  | R22 | Non-TXV |  | 7.308% | 0.92692 | 14.04% | [5 empty] | Non-TXV | 7.308%
Atascadero | CA | 93422-3383 |  | 2012-07-10 | 2012-07-10 15:57 | 2012-07-10 16:22 | BDP - 565BJ024 | 70 | 2.3 | Yes | Yes | 20.9 | 21.1 | -0.2 | 35465EB8756B49E5BD95EDB456620242 |  | R22 | Non-TXV |  | 3.286% | 0.96714 | 6.314% | [5 empty] | Non-TXV | 3.286%
Stockton | CA | 95210-5666 |  | 2012-06-01 | 2012-06-01 15:03 | 2012-06-01 15:19 | CARRIER - 38CKC030340 | 68 | 2.3 | Yes | Yes | 22.7 | 19.1 | 3.7 | 2B5C75853A5D4E639D1EB2CC876C54CB |  | R22 | Non-TXV |  | 3.382% | 0.96618 | 6.5% | [5 empty] | Non-TXV | 3.382%
Atascadero | CA | 93422-5575 |  | 2012-07-10 | 2012-07-10 13:47 | 2012-07-10 14:05 | RHEEM - RACA-018AAQ | 30 | 2.5 | Yes | Yes | 18.1 | 19.3 | -1.2 | 35051B9E7EF742AD84E1F2083F21B763 |  | R22 | Non-TXV |  | 8.333% | 0.85294 | 28.26% | [5 empty] | Non-TXV | 8.333%
Los Banos | CA | 93635-6396 |  | 2012-05-18 | 2012-05-18 11:51 | 2012-05-18 12:23 | GIBSON - JS3BC-036KA | 82 | 3.2 | Yes | Yes | 23.8 | 21.9 | 1.9 | 4180D7BB8B144B1D8652E7D22EEF9F1E | OK: Verified Refrigerant Charge. Superheat recommendation is oposite of indication from delta subcooling. Please check entries for pressure and temperature. If okay, then check refrigerant line restriction. | R22 | Non-TXV |  | 3.902% | 0.96098 | 7.5% | [5 empty] | Non-TXV | 3.902%
Stockton | CA | 95219-3922 |  | 2012-07-24 | 2012-07-24 14:33 | 2012-07-24 14:50 | GOODMAN - PGB024050-1REV | 54 | 4.4 | Yes | Yes | 22.1 | 20.2 | 2 | 68C9E73BBD174DF582CD23FAB9BF1B1D |  | R22 | Non-TXV |  | 8.148% | 0.91852 | 15.66% | [5 empty] | Non-TXV | 8.148%
Clovis | CA | 93611-0610 |  | 2012-05-15 | 2012-05-15 13:41 | 2012-05-15 13:59 | YORK - DAYA-F042N090C | 76 | 2.3 | Yes | Yes | 24.2 | 21 | 3.2 | CC502EB8782C430B8EA8EE9B18AB271C |  | R22 | Non-TXV |  | 3.026% | 0.96974 | 5.816% | [5 empty] | Non-TXV | 3.026%
Stockton | CA | 95210-6662 |  | 2012-06-25 | 2012-06-25 14:07 | 2012-06-25 14:24 | GOODMAN - CKL18-1C | 72 | 2.2 | Yes | Yes | 19.9 | 21 | -1.1 | 5AD497B1FB584DC1A95DF65FE37837C9 |  | R22 | Non-TXV |  | 3.056% | 0.96944 | 5.872% | [5 empty] | Non-TXV | 3.056%
Los Banos | CA | 93635-3288 |  | 2012-05-11 | 2012-05-11 14:38 | 2012-05-11 14:54 | BRYANT - 563CN048 | 136 | -5.3 | Yes | Yes | 15.4 | 16.5 | -1.1 | B81672D7D16B4C328A4D8729C3813E9F | OK: Verified Refrigerant Charge | R22 | TXV |  | -3.897% | 1.039 | 1.091% |  |  |  |  | TXV |  |  | -3.897%
Fresno | CA | 93706-9203 |  | 2012-06-13 | 2012-06-13 11:10 | 2012-06-13 11:30 | AMERICAN STANDARD - YCC030F1MOBF | 83 | 4 | Yes | Yes | 20.6 | 19.3 | 1.3 | E234DC1749A0458C99F7BCFF07676DB8 |  | R22 | Non-TXV |  | 4.819% | 0.95181 | 9.262% | [5 empty] | Non-TXV | 4.819%
Marysville | CA | 95901-3618 |  | 2012-05-22 | 2012-05-22 12:42 | 2012-05-22 12:42 | DAY & NIGHT - PGD324060K001C1 | 72 | 0 | Yes | Yes | 23 | 18.8 | 4.2 | 02F9EFCD660C47408064FB1DA6EDADD0 |  | R410A | Non-TXV |  | 0% | 1 | 0%
Merced | CA | 95340-9284 |  | 2012-05-08 | 2012-05-08 11:30 | 2012-05-08 11:49 | RHEEM - RRNAB042JK08X | 104 | 3.8 | Yes | Yes | 25.9 | 20.7 | 5.3 | 2DDB148890D848BD929A6C0EA8E944B2 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 3.654% | 0.96346 | 7.022% | [5 empty] | Non-TXV | 3.654%
Fresno | CA | 93726-2801 |  | 2012-05-09 | 2012-05-09 12:44 | 2012-05-09 13:02 | GOODMAN - GSC130036DE | 75 | 2.5 | Yes | Yes | 19.1 | 19.8 | -0.7 | 23F26DB615E9453FB8C771976A7ED14C |  | R22 | Non-TXV |  | 3.333% | 0.96667 | 6.406% | [5 empty] | Non-TXV | 3.333%
Fresno | CA | 93726-5009 |  | 2012-05-30 | 2012-05-30 11:52 | 2012-05-30 12:16 | WESTINGHOUSE - 1D02401A | 85 | 3.7 | Yes | Yes | 21 | 21.2 | -0.2 | BCD4DC7C15F048CF95D4F105ABB3BBA5 | OK: Verified Refrigerant Charge. Condenser saturation temperature > 28°F above outdoor air temperature. Clean condenser or check and remove non-condensibles. Purge hoses of non condensibles. | R22 | Non-TXV |  | 4.353% | 0.95647 | 8.365% | [5 empty] | Non-TXV | 4.353%
Paso Robles | CA | 93446-3604 |  | 2012-07-11 | 2012-07-11 11:44 | 2012-07-11 12:03 | OTHER - 24KLB1L | 41 | 1.5 | Yes | Yes | 25.5 | 22 | 3.5 | CF491029430B4248B59EF9B342DCE247 |  | R22 | Non-TXV |  | 3.659% | 0.96341 | 7.031% | [5 empty] | Non-TXV | 3.659%
Stockton | CA | 95206-2250 |  | 2012-05-09 | 2012-05-09 10:11 | 2012-05-09 10:33 | RHEEM - UNK | 55 | 6.4 | Yes | Yes | 22.2 | 20.4 | 1.8 | 4D0F0E9C12F8466FB13BC23F1DED6160 | OK: Verified Refrigerant Charge. | R22 | Non-TXV |  | 11.64% | 0.88364 | 22.36% | [5 empty] | Non-TXV | 11.64%
Marysville | CA | 95901-4276 |  | 2012-05-21 | 2012-05-21 11:54 | 2012-05-21 12:20 | GOODMAN - CPKE18-1A | 75 | -7.1 | Yes | Yes | 19 | 19.9 | -0.9 | 379254D4E38D44EF8755DB5B22E00838 |  | R22 | Non-TXV |  | -9.467% | 1.0947 | 2.651% |  |  |  |  | Non-TXV |  |  | -9.467%
Lodi | CA | 95242-9222 |  | 2012-07-16 | 2012-07-16 14:41 | 2012-07-16 15:00 | BRYANT - 563CN042-D | 108 | 9.3 | Yes | Yes | 19.8 | 20.1 | -0.3 | 58EDC38862954844A1D41D353110CF17 |  | R22 | Non-TXV |  | 8.611% | 0.91389 | 16.55% | [5 empty] | Non-TXV | 8.611%
Oroville | CA | 95966-5323 |  | 2012-05-31 | 2012-05-31 19:08 | 2012-05-31 19:25 | RUUD - URGG-05N25JKR | 49 | 4.1 | Yes | Yes | 22.7 | 21.8 | 1 | B48ECE4BB6154E429929541490F9689D |  | R22 | Non-TXV |  | 8.367% | 0.91633 | 16.08% | [5 empty] | Non-TXV | 8.367%
Stockton | CA | 95210-4458 |  | 2012-05-31 | 2012-05-31 09:54 | 2012-05-31 10:11 | PAYNE - 591AN060-A | 170 | -10 | Yes | Yes | 26.6 | 20.6 | 6 | 87800F9FB19C4E9D870F2D4685892400 |  | R22 | Non-TXV |  | -5.882% | 1.0588 | 1.647% |  |  |  |  | Non-TXV |  |  | -5.882%
Fresno | CA | 93722-5504 |  | 2012-07-10 | 2012-07-10 09:20 | 2012-07-10 09:40 | OTHER - CA7036KA1 | 110 | 3.6 | Yes | Yes | 18.1 | 19.9 | -1.8 | 68B181C5606046348EA3075161540622 |  | R22 | Non-TXV |  | 3.273% | 0.96727 | 6.289% | [5 empty] | Non-TXV | 3.273%