## DEER2016
EER and IEER Market Data Published with DEER 2016
AC Units, 65 to 134 kBtuh
Mfgr | Model # | Nom Cap Tons | Heat Source | Rated EER | 2 Spd IEER | Code EER | Code IEER | Pass Code?
Lennox | KGA092S4M | 7.5 | Gas | 11 | 13 | 11 | 12.7 | OK
Lennox | KGA092H4M | 7.5 | Gas | 12.5 | 14 | 11 | 12.7 | OK
Lennox | KGA102H4M | 8.5 | Gas | 12.2 | 14 | 11 | 12.7 | OK
Lennox | KGA120H4M | 10 | Gas | 12 | 13.8 | 11 | 12.7 | OK
McQuay | MPS 007B (R410A) | 7 | Gas/Elec | 11.2 | 14.5 | 11 | 12.7 | OK
McQuay | MPS 008B (R410A) | 8 | Gas/Elec | 11.2 | 14.4 | 11 | 12.7 | OK
McQuay | MPS 010B (R410A) | 10 | Gas/Elec | 11.2 | 14.6 | 11 | 12.7 | OK
McQuay | MPS 012B (R410A) | 12 | Gas/Elec | 11 | 13.5 | 11 | 12.7 | OK
Ruud | RKNL-C102 (R410A) | 8.5 | Gas | 11.2 | 14.4 | 11 | 12.7 | OK
Ruud | RKNL-C120 (R410A) | 10 | Gas | 11.2 | 14.4 | 11 | 12.7 | OK
Ruud | RLRL-C120 (R410A) | 10 | Gas | 12.5 | 15.6 | 11 | 12.7 | OK
York | ZXG12 (R410A) | 10 | Gas | 11 | 14.4 | 11 | 12.7 | OK
York | ZYG12 (R410A) | 10 | Gas | 11.5 | 14.4 | 11 | 12.7 | OK
Ruud | RKNL-C090 (R410A) | 7.5 | Elec | 11.2 | 14.5 | 11.2 | 12.9 | OK
Ruud | RLRL-C090 (R410A) | 7.5 | Elec | 13 | 15.8 | 11.2 | 12.9 | OK
York | ZXE12 (R410A) | 10 | Elec | 11.2 | 14.8 | 11.2 | 12.9 | OK
York | ZYE12 (R410A) | 10 | Elec | 11.7 | 14.4 | 11.2 | 12.9 | OK
AC Units, 135 to 239 kBtuh
Mfgr | Model # | Nom Cap Tons | Heat Source | EER | 2 Spd IEER | Code EER | Code IEER | Pass Code?
Lennox | KGA180S4M | 15 | Gas | 10.8 | 12.8 | 10.8 | 12.2 | OK
Lennox | KGA240S4M | 20 | Gas | 10.8 | 13 | 10.8 | 12.2 | OK
Lennox | KGA210S4M | 17.5 | Gas | 10.8 | 13.1 | 10.8 | 12.2 | OK
Lennox | KGA180H4M | 15 | Gas | 12 | 13.7 | 10.8 | 12.2 | OK
Lennox | KGA210H4M | 17.5 | Gas | 12 | 14 | 10.8 | 12.2 | OK
Lennox | KGA156H4M | 13 | Gas | 12 | 14.1 | 10.8 | 12.2 | OK
Lennox | KGA240H4M | 20 | Gas | 12 | 14.5 | 10.8 | 12.2 | OK
Lennox | SGC240H4M | 20 | Gas | 12.6 | 16.6 | 10.8 | 12.2 | OK
McQuay | MPS 012B (R410A) | 12 | Gas/Elec | 11 | 13.5 | 10.8 | 12.2 | OK
McQuay | MPS 015B (R410A) | 15 | Gas/Elec | 11.1 | 14.6 | 10.8 | 12.2 | OK
McQuay | MPS 020B (R410A) | 20 | Gas/Elec | 11.1 | 14.8 | 10.8 | 12.2 | OK
Ruud | RKNL-C180 (R410A) | 15 | Gas | 11.1 | 14.4 | 10.8 | 12.2 | OK
Ruud | RKNL-C240 (R410A) | 20 | Gas | 11.1 | 14.8 | 10.8 | 12.2 | OK
Ruud | RKNL-C210 (R410A) | 17.5 | Gas | 11.6 | 14.5 | 10.8 | 12.2 | OK
Ruud | RLNL-C180 (R410A) | 15 | Elec | 11.1 | 14.6 | 11 | 12.4 | OK
Carrier | 50A2-020 | 20 | Elec | 10.3 | 11.8 | 11 | 12.4 | FAIL
AC Units, 240 to 759 kBtuh
Mfgr | Model # | Nom Cap Tons | Heat Source | EER | 2 Spd IEER | Code EER | Code IEER | Pass Code?
York | YPAL060N | 60 | Gas | 9.8 | 11.83 | 9.8 | 11.4 | OK
York | YPAL051N | 55 | Gas | 9.9 | 11.56 | 9.8 | 11.4 | OK
Lennox | LGH540S4 | 45 | Gas | 10 | 11.7 | 9.8 | 11.4 | OK
Carrier | 48A2-030 | 30 | Gas | 10 | 11.7 | 9.8 | 11.4 | OK
Carrier | 48A2-035 | 35 | Gas | 10 | 11.8 | 9.8 | 11.4 | OK
Carrier | 48A2-025 | 25 | Gas | 10 | 12 | 9.8 | 11.4 | OK
York | YPAL050N | 50 | Gas | 10 | 12.17 | 9.8 | 11.4 | OK
Carrier | 48A2-027 | 27 | Gas | 10.1 | 12 | 9.8 | 11.4 | OK
Lennox | LGH360H4V | 30 | Gas | 10.6 | 13.5 | 9.8 | 11.4 | OK
Lennox | LGH420H4V | 35 | Gas | 10.8 | 12.5 | 9.8 | 11.4 | OK
Lennox | LGH480H4V | 40 | Gas | 10.8 | 13 | 9.8 | 11.4 | OK
Lennox | LGH300H4V | 25 | Gas | 11.6 | 14.3 | 9.8 | 11.4 | OK
York | YPAL060E | 60 | Elec | 10.1 | 11.83 | 10 | 11.6 | OK
Carrier | 50A2-030 | 30 | Elec | 10.1 | 11.9 | 10 | 11.6 | OK
Carrier | 50A2-025 | 25 | Elec | 10.1 | 12.3 | 10 | 11.6 | OK
Carrier | 50A2-030 | 30 | Elec | 10.1 | 12.4 | 10 | 11.6 | OK
Carrier | 50A2-035 | 35 | Elec | 10.1 | 12.4 | 10 | 11.6 | OK
Carrier | 50A2-025 | 25 | Elec | 10.1 | 12.5 | 10 | 11.6 | OK
Carrier | 50A2-035 | 35 | Elec | 10.1 | 13.2 | 10 | 11.6 | OK
Carrier | 50A2-027 | 27 | Elec | 10.2 | 12.3 | 10 | 11.6 | OK
Carrier | 50A2-027 | 27 | Elec | 10.2 | 12.5 | 10 | 11.6 | OK
Carrier | 50A2-060 | 60 | Elec | 10.2 | 13.1 | 10 | 11.6 | OK
York | YPAL050E | 50 | Elec | 10.3 | 12.17 | 10 | 11.6 | OK
Carrier | 50A2-040 | 40 | Elec | 10.5 | 13.1 | 10 | 11.6 | OK
Lennox | LCH420H4V | 35 | Elec | 10.8 | 12.5 | 10 | 11.6 | OK
Lennox | LCH480H4V | 40 | Elec | 10.8 | 13 | 10 | 11.6 | OK
Lennox | LCH360H4V | 30 | Elec | 10.8 | 13.5 | 10 | 11.6 | OK
Lennox | LGH480S4V | 40 | Gas | 9.8 | 11 | 9.8 | 11.4 | FAIL
Lennox | LGH600S4V | 50 | Gas | 9.8 | 11 | 9.8 | 11.4 | FAIL
Lennox | LGH420S4V | 35 | Gas | 10 | 11 | 9.8 | 11.4 | FAIL
York | YPAL051E | 55 | Elec | 10.2 | 11.56 | 10 | 11.6 | FAIL
Lennox | LCH300H4V | 25 | Elec | 11.8 | 12.5 | 10 | 11.6 | OK | Specified in mfg literature as 1 speed unit

## PGE_65to135
New market data provided by PG&E for 65 to 134 kBtuh systems
Mfr | Model | Model Family | AC or HP | Split or Pkgd | Heating Type (Gas/None, Electric) | Source | Currently for Sale | EE Participation | Capacity (Btuh) | EER | IEER | Fan Control (2,M,V) | Heat Type for Chart | Code EER | Code IEER | Pass Code?
Lennox | SCC120H4M | Strategos | AC | P | Electric | Catalogue | Yes |  | 123000 | 12.1 | 15.2 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Lennox | LCH120H*M | Emergence | AC | P | Electric | Catalogue | Yes |  | 119000 | 12.2 | 14 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Lennox | LCH092H*M | Emergence | AC | P | Electric | Catalogue | Yes |  | 90000 | 12.7 | 14 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Rheem | RLNL-H102*R******* | Classic | AC | P | None | Catalogue | Yes |  | 101000 | 11.2 | 14.4 | M | Elec/None | 11.2 | 12.9 | OK | 2
Rheem | RLNL-H090*R******* | Classic | AC | P | None | Catalogue | Yes |  | 93000 | 11.2 | 14.5 | M | Elec/None | 11.2 | 12.9 | OK | 2
Rheem | RLNL-H120*R******* | Classic | AC | P | None | Catalogue | Yes |  | 123000 | 11.2 | 14.6 | M | Elec/None | 11.2 | 12.9 | OK | 2
York | ZXE12***3 | Prestige | AC | P | None | Catalogue | Yes |  | 116000 | 11.2 | 14.8 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Daikin | DCC090****V***A |  | AC | P | None | Catalogue | Yes |  | 88000 | 11.3 | 13 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Daikin | DCC120****V***A |  | AC | P | None | Catalogue | Yes |  | 116000 | 11.3 | 13 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Daikin | DCC102****V***A |  | AC | P | None | Catalogue | Yes |  | 102000 | 11.3 | 13.4 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
York | ZYE12***3 | Prestige | AC | P | None | Catalogue | Yes |  | 116000 | 11.7 | 14.4 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Aaon | RN-008-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 96000 | 12 | 13.9 | V | Elec/None | 11.2 | 12.9 | OK | 2
ICP | RAH110*0*****T |  | AC | P | None | Catalogue | Yes |  | 111000 | 12 | 14.5 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
ICP | RAH090*0*****T |  | AC | P | None | Catalogue | Yes |  | 89000 | 12.2 | 14 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
ICP | RAH102*0*****T |  | AC | P | None | Catalogue | Yes |  | 97000 | 12.2 | 14 | 2 | Elec/None | 11.2 | 12.9 | OK | 2
Aaon | RN-010-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 117000 | 12.2 | 14 | V | Elec/None | 11.2 | 12.9 | OK | 2
Aaon | RN-007-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 74000 | 12.5 | 14.8 | V | Elec/None | 11.2 | 12.9 | OK | 2
Rheem | RLRL-H120*R | Prestige | AC | P | None | Catalogue | Yes |  | 124000 | 12.5 | 15.6 | M | Elec/None | 11.2 | 12.9 | OK | 2
Aaon | RN-011-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 128000 | 12.8 | 15.4 | V | Elec/None | 11.2 | 12.9 | OK | 2
Rheem | RLRL-H090*R | Prestige | AC | P | None | Catalogue | Yes |  | 95000 | 13 | 15.8 | M | Elec/None | 11.2 | 12.9 | OK | 2
Aaon | RN-009-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 106000 | 13.9 | 16.8 | V | Elec/None | 11.2 | 12.9 | OK | 2
Trane | (T/Y)SC120F | Precedent | AC | P | None/Gas | Catalogue | Yes |  | 119000 | 11.3 | 13 | M | Gas | 11 | 12.7 | OK | 2
Trane | (T/Y)HC120 | Precedent | AC | P | None/Gas | Catalogue | Yes |  | 116000 | 12.4 | 14.7 | M | Gas | 11 | 12.7 | OK | 2
Trane | (T/Y)HC102 | Precedent | AC | P | None/Gas | Catalogue | Yes |  | 104000 | 12.5 | 14.7 | M | Gas | 11 | 12.7 | OK | 2
Trane | (T/Y)HC092 | Precedent | AC | P | None/Gas | Catalogue | Yes |  | 92000 | 12.6 | 14.5 | M | Gas | 11 | 12.7 | OK | 2
Trane | (T/Y)HC074 | Precedent | AC | P | None/Gas | Catalogue | Yes |  | 73000 | 13.1 | 15.5 | M | Gas | 11 | 12.7 | OK | 2
Bryant | 580J*08*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 90000 | 11 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2 | Heat | EER | Min IEER
Bryant | 580J*09*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 102000 | 11 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2 | Gas | 11 | 12.7 | Code
Carrier | 48TC*D08****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 90000 | 11 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2 | Gas | 11.5 | 13
Carrier | 48TC*D09****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 102000 | 11 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2 | Gas | 12 | 13.5
ICP | RGS090*******T |  | AC | P | Gas | Catalogue | Yes |  | 83000 | 11 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2 | Gas | 12.5 | 14
ICP | RGS102*******T |  | AC | P | Gas | Catalogue | Yes |  | 99000 | 11 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2 | Gas | 13 | 15.5
Lennox | KGA092S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 88200 | 11 | 13 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | ZGA092S4M | Raider | AC | P | Gas | Catalogue | Yes |  | 88200 | 11 | 13 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | KGA102S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 99600 | 11 | 13 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | ZGA102S4M | Raider | AC | P | Gas | Catalogue | Yes |  | 99900 | 11 | 13 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | KGA120S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 118400 | 11 | 13 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | ZGA120S4M | Raider | AC | P | Gas | Catalogue | Yes |  | 118400 | 11 | 13 | 2 | Gas | 11 | 12.7 | OK | 2
York | ZXG12***3 | Prestige | AC | P | Gas | Catalogue | Yes |  | 116000 | 11 | 14.4 | 2 | Gas | 11 | 12.7 | OK | 2
York | ZYG12***3 | Prestige | AC | P | Gas | Catalogue | Yes |  | 116000 | 11 | 14.4 | 2 | Gas | 11 | 12.7 | OK | 2
Bryant | 580J*12*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 120000 | 11.1 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2
Carrier | 48TC*D12****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 120000 | 11.1 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2
ICP | RGS120*******T |  | AC | P | Gas | Catalogue | Yes |  | 114000 | 11.1 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2
Daikin | DCG120210*V***A |  | AC | P | Gas | Catalogue | Yes |  | 116000 | 11.3 | 12.8 | 2 | Gas | 11 | 12.7 | OK | 2
Daikin | DCG090210*V***A |  | AC | P | Gas | Catalogue | Yes |  | 88000 | 11.3 | 13 | 2 | Gas | 11 | 12.7 | OK | 2
Daikin | DCG102210*V***A |  | AC | P | Gas | Catalogue | Yes |  | 102000 | 11.3 | 13.4 | 2 | Gas | 11 | 12.7 | OK | 2
Bryant | 581J*08*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 90000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
Bryant | 581J*09*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 102000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
Carrier | 48HC-*08****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 90000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
Carrier | 48HC-*09****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 102000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
ICP | RGH090*******T |  | AC | P | Gas | Catalogue | Yes |  | 89000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
ICP | RGH102*******T |  | AC | P | Gas | Catalogue | Yes |  | 97000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | LGH120**M | Emergence | AC | P | Gas | Catalogue | Yes |  | 120000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | KGA120H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 122000 | 12 | 13.8 | 2 | Gas | 11 | 12.7 | OK | 2
Bryant | 581J*11*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 120000 | 12 | 14.3 | 2 | Gas | 11 | 12.7 | OK | 2
Carrier | 48HC-*11****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 120000 | 12 | 14.3 | 2 | Gas | 11 | 12.7 | OK | 2
ICP | RGH110*******T |  | AC | P | Gas | Catalogue | Yes |  | 111000 | 12 | 14.3 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | SGC120H4M | Strategos | AC | P | Gas | Catalogue | Yes |  | 123000 | 12.1 | 14.7 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | KGA102H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 103800 | 12.2 | 14 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | LGH092**M | Emergence | AC | P | Gas | Catalogue | Yes |  | 90000 | 12.5 | 14 | 2 | Gas | 11 | 12.7 | OK | 2
Lennox | KGA092H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 93000 | 12.5 | 14 | 2 | Gas | 11 | 12.7 | OK | 2
Aaon | RN-008-3-*-EB**-***:*******D |  | AC | P | Gas/Electric | Catalogue | Yes |  | 96000 | 11.9 | 13.9 | V | Gas | 11 | 12.7 | OK | 2
Aaon | RN-010-3-*-EB**-***:*******D |  | AC | P | Gas/Electric | Catalogue | Yes |  | 117000 | 12.1 | 14 | V | Gas | 11 | 12.7 | OK | 2
Lennox | L(G,C)H102H*M | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 103800 | 12.4 | 14 | 2 | Gas | 11 | 12.7 | OK | 2
Aaon | RN-007-3-*-EB**-***:*******D |  | AC | P | Gas/Electric | Catalogue | Yes |  | 74000 | 12.4 | 14.8 | V | Gas | 11 | 12.7 | OK | 2
Aaon | RN-011-3-*-EB**-***:*******D |  | AC | P | Gas/Electric | Catalogue | Yes |  | 128000 | 12.7 | 15.4 | V | Gas | 11 | 12.7 | OK | 2
Aaon | RN-009-3-*-EB**-***:*******D |  | AC | P | Gas/Electric | Catalogue | Yes |  | 106000 | 13.8 | 16.8 | V | Gas | 11 | 12.7 | OK | 2
ICP | RHS120*0*****T |  | HP | P | Electric | Catalogue | Yes |  | 117000 | 11 | 12.5 | 2 | HP | 10.8 | 12 | OK | 2
Daikin | DCH120****V***A |  | HP | P | Electric | Catalogue | Yes |  | 113000 | 11.1 | 12.6 | 2 | HP | 10.8 | 12 | OK | 2
Daikin | DCH102****V***A |  | HP | P | Electric | Catalogue | Yes |  | 102000 | 11.1 | 13 | 2 | HP | 10.8 | 12 | OK | 2
Aaon | RN-008-3-*-E6**-***:*******D |  | HP | P | Electric | Catalogue | Yes |  | 87000 | 11.1 | 13 | V | HP | 10.8 | 12 | OK | 2
ICP | RHS090*0*****T |  | HP | P | Electric | Catalogue | Yes |  | 88000 | 11.2 | 12.5 | 2 | HP | 10.8 | 12 | OK | 2
ICP | RHS102*0*****T |  | HP | P | Electric | Catalogue | Yes |  | 99000 | 11.2 | 12.5 | 2 | HP | 10.8 | 12 | OK | 2
Daikin | DCH090****V***A |  | HP | P | Electric | Catalogue | Yes |  | 90000 | 11.5 | 12.8 | 2 | HP | 10.8 | 12 | OK | 2
Aaon | RN-009-3-*-E6**-***:*******D |  | HP | P | Electric | Catalogue | Yes |  | 95000 | 11.8 | 14.8 | V | HP | 10.8 | 12 | OK | 2
ICP | RHH102*0*****T |  | HP | P | Electric | Catalogue | Yes |  | 100000 | 12 | 12.9 | 2 | HP | 10.8 | 12 | OK | 2
ICP | RHH090*0*****T |  | HP | P | Electric | Catalogue | Yes |  | 90000 | 12.1 | 13.7 | 2 | HP | 10.8 | 12 | OK | 2
ICP | RHH120*0*****T |  | HP | P | Electric | Catalogue | Yes |  | 119000 | 12.3 | 13.6 | 2 | HP | 10.8 | 12 | OK | 2
These are systems that do not meet code requirements
ICP | RAS090*0*****T |  | AC | P | None | Catalogue | Yes |  | 83000 | 11 | 12.8 | 2 |  | 11.2 | 12.9 | FAIL
ICP | RAS102*0*****T |  | AC | P | None | Catalogue | Yes |  | 99000 | 11 | 12.8 | 2 |  | 11.2 | 12.9 | FAIL
York | ZXE14***3 | Prestige | AC | P | None | Catalogue | Yes |  | 135000 | 11 | 13 | 2 |  | 11.2 | 12.9 | FAIL
ICP | RAS120*0*****T |  | AC | P | None | Catalogue | Yes |  | 114000 | 11.1 | 12.8 | 2 |  | 11.2 | 12.9 | FAIL
Bryant | 581J*12*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 120000 | 11.5 | 12.4 | 2 |  | 11 | 12.7 | FAIL
Carrier | 48HC-*12****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 120000 | 11.5 | 12.4 | 2 |  | 11 | 12.7 | FAIL
ICP | RGH120*******T |  | AC | P | Gas | Catalogue | Yes |  | 115000 | 11.5 | 12.4 | 2 |  | 11 | 12.7 | FAIL
ICP | RAH120*0*****T |  | AC | P | None | Catalogue | Yes |  | 115000 | 11.7 | 12.6 | 2 | Elec/None | 11.2 | 12.9 | FAIL | 2
These systems appear to be multispeed or variable speed
Lennox | LCH094U*E | Emergence Ultra | AC | P | Electric | Catalogue | Yes |  | 90000 | 13.9 | 21.5 | 2 |  | 11.2 | 12.9 | OK
Carrier | 48LC-**08****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 90000 | 13 | 19.8 | V |  | 11 | 12.7 | OK
Carrier | 48LC-**07****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 72000 | 13 | 20.5 | V |  | 11 | 12.7 | OK
Carrier | 48LC-**12****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 120000 | 13 | 20.6 | V |  | 11 | 12.7 | OK
Lennox | LGH094**M | Emergence Ultra | AC | P | Gas | Catalogue | Yes |  | 90000 | 13.4 | 20.7 | 2 |  | 11 | 12.7 | OK
Carrier | 48LC-**09****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 102000 | 13.5 | 20.8 | V |  | 11 | 12.7 | OK
Lennox | LCH122U*M | Emergence Ultra | AC | P | Electric | Catalogue | Yes |  | 119000 | 12.6 | 19.2 | 2 |  | 11.2 | 12.9 | OK
Lennox | L(G,C)H122U*M | Emergence Ultra | AC | P | Gas/Electric | Catalogue | Yes |  | 119000 | 12.6 | 19.2 | 2 |  | 11 | 12.7 | OK
Lennox | L(G,C)H122U*E | Emergence Ultra | AC | P | Gas/Electric | Catalogue | Yes |  | 119000 | 13.1 | 20 | 2 |  | 11 | 12.7 | OK
Lennox | L(G,C)H094U*M | Emergence Ultra | AC | P | Gas/Electric | Catalogue | Yes |  | 93700 | 13.4 | 20.7 | 2 |  | 11 | 12.7 | OK
Lennox | L(G,C)H094U*E | Emergence Ultra | AC | P | Gas/Electric | Catalogue | Yes |  | 93700 | 13.9 | 21.5 | 2 |  | 11 | 12.7 | OK
Daikin | DPS010AHCY4 | Rebel | AC | P | None | Catalogue | Yes |  | 120000 | 12.5 | 19.4 | V |  | 11.2 | 12.9 | OK
Daikin | DPS007AHCY4 | Rebel | AC | P | None | Catalogue | Yes |  | 90000 | 12.6 | 20.6 | V |  | 11.2 | 12.9 | OK

## PGE_135to240
New market data provided by PG&E for 135to 239 kBtuh systems
Mfr | Model | Model Family | AC or HP | Split or Pkgd | Heating Type (Gas/None, Electric) | Source | Currently for Sale | EE Participation | Capacity (Btuh) | EER | IEER | Fan Control (2,M,V) | Heat Type for Chart | Code EER | Code IEER | Pass Code?
Daikin | DCC180****V***A |  | AC | P | None | Catalogue | Yes |  | 180000 | 11 | 12.8 | 2 | Elec/None | 11 | 12.4 | OK | 2
ICP | RAS210*0*****T |  | AC | P | None | Catalogue | Yes |  | 208000 | 11 | 12.9 | 2 | Elec/None | 11 | 12.4 | OK | 2
Rheem | RLNL-H151*R******* | Classic | AC | P | None | Catalogue | Yes |  | 146000 | 11 | 13.5 | M | Elec/None | 11 | 12.4 | OK | 2
Rheem | RLNL-H180*R****** | Classic | AC | P | None | Catalogue | Yes |  | 188000 | 11.1 | 14.6 | M | Elec/None | 11 | 12.4 | OK | 2
Lennox | LCH150S*M | Emergence | AC | P | Electric | Catalogue | Yes |  | 142600 | 11.2 | 13.1 | 2 | Elec/None | 11 | 12.4 | OK | 2
AAON | RN-015-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 182000 | 11.4 | 13.2 | V | Elec/None | 11 | 12.4 | OK | 2
Rheem | RLNL-H210*R****** | Classic | AC | P | None | Catalogue | Yes |  | 212000 | 11.6 | 14.5 | M | Elec/None | 11 | 12.4 | OK | 2
Lennox | LCH240H*M | Emergence | AC | P | Electric | Catalogue | Yes |  | 238000 | 12 | 14.5 | M | Elec/None | 11 | 12.4 | OK | 2
ICP | RAH181*0*****T |  | AC | P | None | Catalogue | Yes |  | 174000 | 12.2 | 13.7 | 2 | Elec/None | 11 | 12.4 | OK | 2
ICP | RAH210*0*****T |  | AC | P | None | Catalogue | Yes |  | 202000 | 12.2 | 13.8 | 2 | Elec/None | 11 | 12.4 | OK | 2
ICP | RAH240*0*****T |  | AC | P | None | Catalogue | Yes |  | 236000 | 12.2 | 14 | 2 | Elec/None | 11 | 12.4 | OK | 2
AAON | RN-013-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 146000 | 12.2 | 14.4 | V | Elec/None | 11 | 12.4 | OK | 2
Rheem | RLRL-H180*R | Prestige | AC | P | None | Catalogue | Yes |  | 178000 | 12.2 | 15 | M | Elec/None | 11 | 12.4 | OK | 2
ICP | RAH150*0*****T |  | AC | P | None | Catalogue | Yes |  | 146000 | 12.4 | 14.1 | 2 | Elec/None | 11 | 12.4 | OK | 2
AAON | RN-016-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 194000 | 12.4 | 14.2 | V | Elec/None | 11 | 12.4 | OK | 2
AAON | RN-020-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 238000 | 12.4 | 14.8 | V | Elec/None | 11 | 12.4 | OK | 2
AAON | RN-018-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 212000 | 12.5 | 14.3 | V | Elec/None | 11 | 12.4 | OK | 2
Bryant | 580J*16*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 180000 | 10.8 | 12.4 | 2 | Gas | 10.8 | 12.2 | OK | 2
Carrier | 48TC*D16****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 180000 | 10.8 | 12.4 | 2 | Gas | 10.8 | 12.2 | OK | 2
ICP | RGS180*******T |  | AC | P | Gas | Catalogue | Yes |  | 174000 | 10.8 | 12.4 | 2 | Gas | 10.8 | 12.2 | OK | 2
Daikin | DCG180350*V***A |  | AC | P | Gas | Catalogue | Yes |  | 180000 | 10.8 | 12.6 | 2 | Gas | 10.8 | 12.2 | OK | 2
Lennox | KGA180S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 182000 | 10.8 | 12.6 | M | Gas | 10.8 | 12.2 | OK | 2
Bryant | 580J*17*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 180000 | 10.8 | 12.7 | 2 | Gas | 10.8 | 12.2 | OK | 2
Bryant | 580J*20*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 210000 | 10.8 | 12.7 | 2 | Gas | 10.8 | 12.2 | OK | 2 | Heat | EER | Min IEER
Carrier | 48TC**18****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 180000 | 10.8 | 12.7 | 2 | Gas | 10.8 | 12.2 | OK | 2 | Gas | 10.8 | 12.2 | Code
Carrier | 48TC**21****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 210000 | 10.8 | 12.7 | 2 | Gas | 10.8 | 12.2 | OK | 2 | Gas | 11.5 | 13
ICP | RGS210*******T |  | AC | P | Gas | Catalogue | Yes |  | 208000 | 10.8 | 12.7 | 2 | Gas | 10.8 | 12.2 | OK | 2 | Gas | 12 | 13.5
Lennox | KGA240S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 238000 | 10.8 | 13 | M | Gas | 10.8 | 12.2 | OK | 2 | Gas | 12.5 | 14
Lennox | KGA210S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 204000 | 10.8 | 13.1 | M | Gas | 10.8 | 12.2 | OK | 2
Trane | (E/G)AC180 | Foundation | AC | P | Gas/Electric | Catalogue | Yes |  | 183000 | 11 | 12.8 | M | Gas | 10.8 | 12.2 | OK | 2
Trane | (E/G)AC210 | Foundation | AC | P | Gas/Electric | Catalogue | Yes |  | 212000 | 11 | 12.8 | M | Gas | 10.8 | 12.2 | OK | 2
Trane | (T/Y)S*210F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 210000 | 11 | 12.9 | 2 | Gas | 10.8 | 12.2 | OK | 2
Lennox | LGH150S*M | Emergence | AC | P | Gas | Catalogue | Yes |  | 142600 | 11 | 13.1 | 2 | Gas | 10.8 | 12.2 | OK | 2
Trane | (T/Y)S*180F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 186000 | 11 | 13.2 | 2 | Gas | 10.8 | 12.2 | OK | 2
Trane | (T/Y)S*150F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 150000 | 11 | 13.5 | 2 | Gas | 10.8 | 12.2 | OK | 2
AAON | RN-015-3-*-EB**-***:*******D |  | AC | P | Electric/Gas | Catalogue | Yes |  | 182000 | 11.3 | 13.2 | V | Gas | 10.8 | 12.2 | OK | 2
Trane | (T/Y)H*210F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 214800 | 11.8 | 14 | 2 | Gas | 10.8 | 12.2 | OK | 2
Bryant | 581J*17*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 180000 | 12 | 13.5 | 2 | Gas | 10.8 | 12.2 | OK | 2
Carrier | 48HC-*17****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 180000 | 12 | 13.5 | 2 | Gas | 10.8 | 12.2 | OK | 2 | Verified in Carrier literature: 48HC-17-28-01PD.pdf
ICP | RGH181*******T |  | AC | P | Gas | Catalogue | Yes |  | 174000 | 12 | 13.5 | 2 | Gas | 10.8 | 12.2 | OK | 2
Bryant | 581J*20*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 216000 | 12 | 13.6 | 2 | Gas | 10.8 | 12.2 | OK | 2
Carrier | 48HC-*20****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 216000 | 12 | 13.6 | 2 | Gas | 10.8 | 12.2 | OK | 2
ICP | RGH210*******T |  | AC | P | Gas | Catalogue | Yes |  | 202000 | 12 | 13.6 | 2 | Gas | 10.8 | 12.2 | OK | 2
Lennox | KGA180H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 176000 | 12 | 13.7 | M | Gas | 10.8 | 12.2 | OK | 2
Lennox | L(G,C)H180H*M | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 176000 | 12 | 13.7 | M | Gas | 10.8 | 12.2 | OK | 2
ICP | RGH240*******T |  | AC | P | Gas | Catalogue | Yes |  | 236000 | 12 | 13.8 | 2 | Gas | 10.8 | 12.2 | OK | 2
Lennox | KGA210H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 204000 | 12 | 14 | M | Gas | 10.8 | 12.2 | OK | 2
Lennox | L(G,C)H210H*M | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 204000 | 12 | 14 | M | Gas | 10.8 | 12.2 | OK | 2
Lennox | KGA156H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 156000 | 12 | 14.1 | M | Gas | 10.8 | 12.2 | OK | 2
Lennox | L(G,C)H156H*M | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 156000 | 12 | 14.1 | M | Gas | 10.8 | 12.2 | OK | 2
Lennox | KGA240H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 238000 | 12 | 14.5 | M | Gas | 10.8 | 12.2 | OK | 2
AAON | RN-013-3-*-EB**-***:*******D |  | AC | P | Electric/Gas | Catalogue | Yes |  | 146000 | 12.1 | 14.4 | V | Gas | 10.8 | 12.2 | OK | 2
Trane | (T/Y)H*150F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 152400 | 12.1 | 15 | 2 | Gas | 10.8 | 12.2 | OK | 2
Trane | (T/Y)H*180F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 180500 | 12.1 | 15 | 2 | Gas | 10.8 | 12.2 | OK | 2
Bryant | 581J*14*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 150000 | 12.2 | 13.9 | 2 | Gas | 10.8 | 12.2 | OK | 2
Carrier | 48HC-*14****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 150000 | 12.2 | 13.9 | 2 | Gas | 10.8 | 12.2 | OK | 2
ICP | RGH150*******T |  | AC | P | Gas | Catalogue | Yes |  | 146000 | 12.2 | 13.9 | 2 | Gas | 10.8 | 12.2 | OK | 2
AAON | RN-016-3-*-EB**-***:*******D |  | AC | P | Electric/Gas | Catalogue | Yes |  | 194000 | 12.3 | 14.2 | V | Gas | 10.8 | 12.2 | OK | 2
AAON | RN-020-3-*-EB**-***:*******D |  | AC | P | Electric/Gas | Catalogue | Yes |  | 238000 | 12.3 | 14.8 | V | Gas | 10.8 | 12.2 | OK | 2
AAON | RN-018-3-*-EB**-***:*******D |  | AC | P | Electric/Gas | Catalogue | Yes |  | 212000 | 12.4 | 14.3 | V | Gas | 10.8 | 12.2 | OK | 2
Systems that fail to meed T24-2016 code
ICP | RAS150*0*****T |  | AC | P | None | Catalogue | Yes |  | 140000 | 10.8 | 11.8 | 2 | Elec/None | 11 | 12.4 | FAIL | 2
ICP | RAS180*0*****T |  | AC | P | None | Catalogue | Yes |  | 174000 | 10.8 | 12.4 | 2 | Elec/None | 11 | 12.4 | FAIL | 2
Daikin | DCC150****V***A |  | AC | P | None | Catalogue | Yes |  | 144000 | 11 | 12.2 | 2 | Elec/None | 11 | 12.4 | FAIL | 2
Bryant | 580J*14*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 150000 | 10.8 | 11.8 | 2 | Gas | 10.8 | 12.2 | FAIL | 2
Carrier | 48TC*D14****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 150000 | 10.8 | 11.8 | 2 | Gas | 10.8 | 12.2 | FAIL | 2
ICP | RGS150*******T |  | AC | P | Gas | Catalogue | Yes |  | 140000 | 10.8 | 11.8 | 2 | Gas | 10.8 | 12.2 | FAIL | 2
Daikin | DCG150210*V***A |  | AC | P | Gas | Catalogue | Yes |  | 144000 | 10.8 | 12 | 2 | Gas | 10.8 | 12.2 | FAIL | 2
Lennox | ZGA150S4M | Raider | AC | P | Gas | Catalogue | Yes |  | 142000 | 10.8 | 12 | M | Gas | 10.8 | 12.2 | FAIL | 2
Lennox | KGA150S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 142600 | 11 | 12 | M | Gas | 10.8 | 12.2 | FAIL | 2
These systems appear to be multispeed or variable speed
Lennox | LCH152U*M | Emergence Ultra | AC | P | Electric | Catalogue | Yes |  | 141900 | 12 | 18.1 | 2 | Elec/None | 11 | 12.4 | OK | V?
Daikin | DPS012AHCY4 | Rebel | AC | P | None | Catalogue | Yes |  | 144000 | 12.1 | 18.5 | V | Elec/None | 11 | 12.4 | OK | V?
Lennox | LCH152U*E | Emergence Ultra | AC | P | Electric | Catalogue | Yes |  | 141900 | 12.3 | 18.9 | 2 | Elec/None | 11 | 12.4 | OK | V?
Carrier | 48LC-**20****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 210000 | 12 | 17.7 | V | Gas | 10.8 | 12.2 | OK | V?
Lennox | LGH152U4M | Emergence Ultra | AC | P | Gas | Catalogue | Yes |  | 141900 | 12 | 18.1 | 2 | Gas | 10.8 | 12.2 | OK | V?
Lennox | LGH152U*E | Emergence Ultra | AC | P | Gas | Catalogue | Yes |  | 141900 | 12.3 | 18.9 | 2 | Gas | 10.8 | 12.2 | OK | V?
Trane | (T/Y)Z*210F | Voyager e-Flex | AC | P | Gas/Electric | Catalogue | Yes |  | 205000 | 12.3 | 19.3 | V | Gas | 10.8 | 12.2 | OK | V?
Carrier | 48LC-**14****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 150000 | 12.4 | 19.1 | V | Gas | 10.8 | 12.2 | OK | V?
Carrier | 48LC-**17****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 180000 | 12.5 | 18.4 | V | Gas | 10.8 | 12.2 | OK | V?
Trane | (T/Y)Z*150F | Voyager e-Flex | AC | P | Gas/Electric | Catalogue | Yes |  | 154000 | 12.5 | 20 | V | Gas | 10.8 | 12.2 | OK | V?
Trane | (T/Y)Z*180F | Voyager e-Flex | AC | P | Gas/Electric | Catalogue | Yes |  | 180000 | 12.7 | 20.1 | V | Gas | 10.8 | 12.2 | OK | V?
Lennox | LGH180U4M | Emergence Ultra | AC | P | Gas | Catalogue | Yes |  | 185300 | 12.7 | 20.2 | M | Gas | 10.8 | 12.2 | OK | V?
ICP | RHS181*0*****T |  | HP | P | Electric | Catalogue | Yes |  | 172000 | 10.8 | 12 | 2 | HP | 10.8 | 12.2 | FAIL | 2

## PGE_240+
New market data provided by PG&E for 240 to 760 kBtuh systems
Mfr | Model | Model Family | AC or HP | Split or Pkgd | Heating Type (Gas/None, Electric) | Source | Currently for Sale | EE Participation | Capacity (Btuh) | EER | IEER | Fan Control (2,M,V) | Heat Type for Chart | Code EER | Code IEER | Pass Code?
ICP | RAS300*0*****T |  | AC | P | None | Catalogue | Yes |  | 282000 | 10 | 11.7 | 2 | Elec/None | 10 | 11.6 | OK | 2
ICP | RAS240*0*****T |  | AC | P | None | Catalogue | Yes |  | 242000 | 10 | 11.9 | 2 | Elec/None | 10 | 11.6 | OK | 2
Daikin | DCC300****V***A |  | AC | P | None | Catalogue | Yes |  | 290000 | 10.2 | 11.8 | 2 | Elec/None | 10 | 11.6 | OK | 2
ICP | RAS336*0*****T |  | AC | P | None | Catalogue | Yes |  | 330000 | 10.4 | 11.7 | 2 | Elec/None | 10 | 11.6 | OK | 2
Lennox | LCH360H*V | Emergence | AC | P | Electric | Catalogue | Yes |  | 370000 | 10.8 | 13.5 | V | Elec/None | 10 | 11.6 | OK | 2
Rheem | RLNL-H240*R****** | Classic | AC | P | None | Catalogue | Yes |  | 244000 | 11.1 | 14.8 | M | Elec/None | 10 | 11.6 | OK | 2
ICP | RAH300*0*****T |  | AC | P | None | Catalogue | Yes |  | 282000 | 11.4 | 12.7 | 2 | Elec/None | 10 | 11.6 | OK | 2
Lennox | SCC288**M | Strategos | AC | P | Electric | Catalogue | Yes |  | 288000 | 11.6 | 14.2 | M | Elec/None | 10 | 11.6 | OK | 2
Lennox | LCH300H*V | Emergence | AC | P | Electric | Catalogue | Yes |  | 310000 | 11.8 | 14.3 | V | Elec/None | 10 | 11.6 | OK | 2
Lennox | LCH180H*M | Emergence | AC | P | Electric | Catalogue | Yes |  | 176000 | 12 | 13.7 | M | Elec/None | 10 | 11.6 | OK | 2
Lennox | LCH210H*M | Emergence | AC | P | Electric | Catalogue | Yes |  | 204000 | 12 | 14 | M | Elec/None | 10 | 11.6 | OK | 2
Rheem | RLRL-H240*R | Prestige | AC | P | None | Catalogue | Yes |  | 240000 | 12.2 | 15 | M | Elec/None | 10 | 11.6 | OK | 2
Lennox | LCH242H*V | Emergence | AC | P | Electric | Catalogue | Yes |  | 244000 | 12.5 | 15.5 | V | Elec/None | 10 | 11.6 | OK | 2
Lennox | SCC240**M | Strategos | AC | P | Electric | Catalogue | Yes |  | 240000 | 12.8 | 16.8 | M | Elec/None | 10 | 11.6 | OK | 2
Daikin | DCG300400*V***A |  | AC | P | Gas | Catalogue | Yes |  | 290000 | 9.8 | 11.4 | 2 | Gas | 9.8 | 11.4 | OK | 2
Bryant | 580J*28*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 300000 | 9.8 | 11.5 | 2 | Gas | 9.8 | 11.4 | OK | 2
ICP | RGS300*******T |  | AC | P | Gas | Catalogue | Yes |  | 282000 | 9.8 | 11.5 | 2 | Gas | 9.8 | 11.4 | OK | 2
Bryant | 580J*24*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 240000 | 9.8 | 11.7 | 2 | Gas | 9.8 | 11.4 | OK | 2
ICP | RGS240*******T |  | AC | P | Gas | Catalogue | Yes |  | 242000 | 9.8 | 11.7 | 2 | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A2*030*(N,P,Q,1,2,3)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 308000 | 10 | 11.7 | 2 | Gas | 9.8 | 11.4 | OK | 2
Lennox | L(G,C)H540S*V | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 549000 | 10 | 11.7 | V | Gas | 9.8 | 11.4 | OK | 2 |  | Heat | EER | Min IEER
Trane | (E/G)AC300 | Foundation | AC | P | Gas/Electric | Catalogue | Yes |  | 290000 | 10 | 11.7 | M | Gas | 9.8 | 11.4 | OK | 2 |  | Gas | 9.8 | 11.4 | Code
Carrier | 48A2*035*(P,Q,R,2,3,4)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 366000 | 10 | 11.8 | 2 | Gas | 9.8 | 11.4 | OK | 2 |  | Gas | 10.8 | 12.3
Trane | (E/G)AC240 | Foundation | AC | P | Gas/Electric | Catalogue | Yes |  | 252000 | 10 | 11.9 | M | Gas | 9.8 | 11.4 | OK | 2 |  | Gas | 11.5 | 12.7
Carrier | 48A2*025*(L,N,P,J,1,2)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 272000 | 10 | 12 | 2 | Gas | 9.8 | 11.4 | OK | 2 |  | Gas | 12.5 | 15
Carrier | 48A3*050******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 520000 | 10 | 12 | V | Gas | 9.8 | 11.4 | OK | 2
Lennox | KGA300S4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 282000 | 10 | 12 | M | Gas | 9.8 | 11.4 | OK | 2
Trane | (T/Y)S*300F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 296400 | 10 | 12 | 2 | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A3*030******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 308000 | 10 | 12.3 | V | Gas | 9.8 | 11.4 | OK | 2
Trane | (T/Y)S*240F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 259000 | 10 | 12.3 | 2 | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A3*025******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 272000 | 10 | 12.4 | V | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A3*035******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 366000 | 10 | 12.8 | V | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A2*020*(L,N,P,J,1,2)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 240000 | 10.1 | 11.4 | 2 | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A3*020******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 240000 | 10.1 | 11.7 | V | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A2*027*(N,P,Q,J,1,2)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 282000 | 10.1 | 12 | 2 | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A3*027******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 282000 | 10.1 | 12.4 | V | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A3*060******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 615000 | 10.1 | 12.9 | V | Gas | 9.8 | 11.4 | OK | 2
Bryant | 580J*30*********D | Legacy | AC | P | Gas | Catalogue | Yes |  | 330000 | 10.2 | 11.5 | 2 | Gas | 9.8 | 11.4 | OK | 2
ICP | RGS336*******T |  | AC | P | Gas | Catalogue | Yes |  | 330000 | 10.2 | 11.5 | 2 | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48A3*040******** | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 425000 | 10.3 | 12.9 | V | Gas | 9.8 | 11.4 | OK | 2
Lennox | KGA300H4M | Landmark | AC | P | Gas | Catalogue | Yes |  | 282000 | 10.5 | 13.8 | M | Gas | 9.8 | 11.4 | OK | 2
Lennox | L(G,C)H300S*M | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 282000 | 10.5 | 13.8 | M | Gas | 9.8 | 11.4 | OK | 2
Trane | S*HL*205*****************D | IntelliPak I | AC | P | None/Gas | Catalogue | Yes |  | 240000 | 10.6 | 13.2 | V | Gas | 9.8 | 11.4 | OK | 2
Lennox | LGH360H*V | Emergence | AC | P | Gas | Catalogue | Yes |  | 370000 | 10.6 | 13.5 | V | Gas | 9.8 | 11.4 | OK | 2
Trane | S*HL*255*****************D | IntelliPak I | AC | P | None/Gas | Catalogue | Yes |  | 258000 | 10.7 | 13.6 | V | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48TC**25****-***G* | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 240000 | 10.8 | 12.4 | 2 | Gas | 9.8 | 11.4 | OK | 2
Lennox | L(G,C)H420H*V | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 443000 | 10.8 | 12.5 | V | Gas | 9.8 | 11.4 | OK | 2
Lennox | L(G,C)H480H*V | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 494000 | 10.8 | 13 | V | Gas | 9.8 | 11.4 | OK | 2
Trane | S*HL*20(4/E/F)*****************D | IntelliPak I | AC | P | None/Gas | Catalogue | Yes |  | 240000 | 10.8 | 13.5 | V | Gas | 9.8 | 11.4 | OK | 2
Trane | S*HL*25(4/E/F)*****************D | IntelliPak I | AC | P | None/Gas | Catalogue | Yes |  | 258000 | 10.8 | 13.7 | V | Gas | 9.8 | 11.4 | OK | 2
Trane | S*HL*305*****************D | IntelliPak I | AC | P | None/Gas | Catalogue | Yes |  | 324000 | 11 | 13.6 | V | Gas | 9.8 | 11.4 | OK | 2
Trane | (T/Y)H*240F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 248500 | 11 | 14 | 2 | Gas | 9.8 | 11.4 | OK | 2
Trane | S*HL*30(4/E/F)*****************D | IntelliPak I | AC | P | None/Gas | Catalogue | Yes |  | 324000 | 11.1 | 13.7 | V | Gas | 9.8 | 11.4 | OK | 2
Bryant | 581J*28*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 300000 | 11.2 | 12.5 | 2 | Gas | 9.8 | 11.4 | OK | 2 | 25
Carrier | 48HC-*28****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 300000 | 11.2 | 12.5 | 2 | Gas | 9.8 | 11.4 | OK | 2 | Verified in Carrier catalog 48HC-17-28-01PD, 6/2014
Lennox | SGC288**M | Strategos | AC | P | Gas | Catalogue | Yes |  | 288000 | 11.6 | 14.1 | M | Gas | 9.8 | 11.4 | OK | 2
Lennox | LGH300H*V | Emergence | AC | P | Gas | Catalogue | Yes |  | 310000 | 11.6 | 14.3 | V | Gas | 9.8 | 11.4 | OK | 2
Bryant | 581J*24*********D | Prefered | AC | P | Gas | Catalogue | Yes |  | 240000 | 12 | 13.8 | 2 | Gas | 9.8 | 11.4 | OK | 2
Carrier | 48HC-*24****-***G* | WeatherMaster | AC | P | Gas | Catalogue | Yes |  | 240000 | 12 | 13.8 | 2 | Gas | 9.8 | 11.4 | OK | 2
Lennox | L(G,C)H240H*M | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 238000 | 12 | 14.5 | M | Gas | 9.8 | 11.4 | OK | 2
Lennox | LGH242H*V | Emergence | AC | P | Gas | Catalogue | Yes |  | 244000 | 12.3 | 15.5 | V | Gas | 9.8 | 11.4 | OK | 2
Lennox | SGC240**M | Strategos | AC | P | Gas | Catalogue | Yes |  | 240000 | 12.6 | 16.6 | M | Gas | 9.8 | 11.4 | OK | 2
Systems that fail to meed T24-2016 code
Lennox | LCH600S*V | Emergence | AC | P | Electric | Catalogue | Yes |  | 598000 | 10 | 11 | V | Elec/None | 10 | 11.6 | FAIL | 2
Daikin | DCC240****V***A |  | AC | P | None | Catalogue | Yes |  | 240000 | 10 | 11.5 | 2 | Elec/None | 10 | 11.6 | FAIL | 2
Carrier | 48TC**29****-***** | WeatherMaker | AC | P | Gas | Catalogue | Yes |  | 300000 | 9.8 | 11 | 2 | Gas | 9.8 | 11.4 | FAIL | 2
Lennox | LGH600S*V | Emergence | AC | P | Gas | Catalogue | Yes |  | 598000 | 9.8 | 11 | V | Gas | 9.8 | 11.4 | FAIL | 2
Daikin | DCG240400*V***A |  | AC | P | Gas | Catalogue | Yes |  | 240000 | 9.8 | 11.3 | 2 | Gas | 9.8 | 11.4 | FAIL | 2
Carrier | 48A2*050*(Q,R,S,3,4,5)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 520000 | 10 | 10.5 | 2 | Gas | 9.8 | 11.4 | FAIL | 2
Lennox | L(G,C)H420S*V | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 433000 | 10 | 11 | V | Gas | 9.8 | 11.4 | FAIL | 2
Lennox | L(G,C)H480S*V | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 476000 | 10 | 11 | V | Gas | 9.8 | 11.4 | FAIL | 2
Carrier | 48A2*060*(R,S,T,4,5,6)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 615000 | 10.1 | 11.1 | 2 | Gas | 9.8 | 11.4 | FAIL | 2
Carrier | 48A2*040*(P,Q,R,2,3,4)* | Weathermaker | AC | P | Gas | Catalogue | Yes |  | 425000 | 10.3 | 11 | 2 | Gas | 9.8 | 11.4 | FAIL | 2
Systems that appear to be multi-speed or variable speed
Rheem | RLNL-H300*R****** | Classic | AC | P | None | Catalogue | Yes |  | 312000 | 10 | 14.1 | M | Elec/None | 10 | 11.6 | OK | 2
Trane | (T/Y)H*300F | Voyager | AC | P | Gas/Electric | Catalogue | Yes |  | 292300 | 10.6 | 15 | 2 | Gas | 9.8 | 11.4 | OK | 2
Daikin | DPS025AHCY4 | Rebel | AC | P | None | Catalogue | Yes |  | 300000 | 11.3 | 18.3 | V | Elec/None | 10 | 11.6 | OK | V?
Lennox | LCH180U*M | Emergence | AC | P | Electric | Catalogue | Yes |  | 185300 | 12.7 | 20.2 | M | Elec/None | 10 | 11.6 | OK | V?
Carrier | 48LC-**26****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 276000 | 11.1 | 17.8 | V | Gas | 9.8 | 11.4 | OK | V?
Carrier | 48LC-**24****-***** | WeatherExpert | AC | P | Gas | Catalogue | Yes |  | 240000 | 12 | 18 | V | Gas | 9.8 | 11.4 | OK | V?
Lennox | L(G,C)H240U*M | Emergence | AC | P | Gas/Electric | Catalogue | Yes |  | 241000 | 12 | 20 | M | Gas | 9.8 | 11.4 | OK | V?
Systems that appear to be single speed
AAON | RN-030-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 322000 | 11.1 | 12 | V | Elec/None | 10 | 11.6 | OK | 2 | 1 speed
AAON | RN-025-3-*-EB**-000:*******D |  | AC | P | None | Catalogue | Yes |  | 290000 | 11.8 | 12.7 | V | Elec/None | 10 | 11.6 | OK | 2 | 1 speed
AAON | RN-030-3-*-EB**-***:*******D |  | AC | P | Electric/Gas | Catalogue | Yes |  | 322000 | 11 | 12 | V | Gas | 9.8 | 11.4 | OK | 2 | 1 speed
AAON | RN-025-3-*-EB**-***:*******D |  | AC | P | Electric/Gas | Catalogue | Yes |  | 290000 | 11.7 | 12.7 | V | Gas | 9.8 | 11.4 | OK | 2 | 1 speed
ICP | RGH300*******T |  | AC | P | Gas | Catalogue | Yes |  | 282000 | 11.2 | 12 | 2 | Gas | 9.8 | 11.4 | OK | 2 | 1 speed

## Charts
Market Data for Rated IEER vs EER Taken from DEER2016 Survey and PG&E Survey
65 to 134 kBtuh | Minimum IEER for Gas AC units, 65 to 134 kBtuh
| Tier | EER | Min IEER
| Code | 11 | 12.7
| 1 | 11.5 | 13
| 2 | 12 | 13.5
| 3 | 12.5 | 14
| 4 | 13 | 15
135 to 239 kBtuh | Minimum IEER for Gas AC units, 135 to 239 kBtuh
| Tier | EER | Min IEER
| Code | 10.8 | 12.2
| 1 | 11.5 | 13
| 2 | 12 | 13.5
| 3 | 12.5 | 14
240 to 759 kBtuh | Minimum IEER for Gas AC units, 240 to 749 kBtuh
| Tier | EER | Min IEER
| Code | 9.8 | 11.4
| 1 | 10.8 | 12.2
| 2 | 11.5 | 12.7
| 3 | 12.5 | 15.5
Minimum IEER for Gas AC units, >= 760 kBtuh
(based on market data for 240 to 759 kBtuh systems)
| Tier | EER | Min IEER
| Code | 9.5 | 11
| 1 | 10.2 | 11.6
| 2 | 11 | 12.3
| 3 | 12 | 13.8
240 to 759 kBtuh | Minimum IEER for AC units w/o heat, 240 to 749 kBtuh
| Tier | EER | Min IEER
| Code | 10 | 11.6
| 1 | 10.8 | 12.3
| 2 | 11.5 | 12.8
| 3 | 12.5 | 15.3
Minimum IEER for AC units w/o heat, >= 760 kBtuh
(based on market data for 240 to 759 kBtuh systems)
| Tier | EER | Min IEER
| Code | 9.7 | 11.2
| 1 | 10.2 | 11.7
| 2 | 11 | 12.4
| 3 | 12 | 13.8