## Measure Definitions
Current DEER Package HVAC Measures to Expire 12/31/2016
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | ReviewComment
807 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
808 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
809 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
810 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
811 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
812 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
813 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | Available | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
814 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | Available | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
815 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | Available | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
801 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
804 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
802 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
805 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
803 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
806 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | Available |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
816 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | Available | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
817 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | Available | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
818 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 7/13/2015 00:00:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | Available | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 1/1/2015 | 2016-12-31 | InEA_same |  |  |  |  | Standard | Measure expired for DEER2017 based on requirements for minimum IEER
New DEER Package HVAC Measures to Start 1/1/2017
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | ReviewComment
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer | DEER | CrossMeasWtd | None |  |  | None | airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-woutPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER13.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, no Econo; 2006 - 2009: EER = 10.1, one-speed fan, no Econo; 2010 - 2013: EER = 11, one-speed fan, no Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-11p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12, min IEER = 13.5 EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to135kBtuh-12p5eer-wPreEcono | DEER | CrossMeasWtd | None |  |  | None | airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to134kBtuh-EER13.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-134 kBTU/h; Pre-2005: EER = 10.1, one-speed fan, w/Econo; 2006 - 2009: EER = 10.1, one-speed fan, w/Econo; 2010 - 2013: EER = 11, one-speed fan, w/Econo; 2014 - 2015: EER = 11, IEER 12.7, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 11, IEER = 12.7, EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 134 kBTU/h, EER = 13, min IEER = 15, EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-65to134kBtuh-EER11.0-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5, one-speed fan, w/Econo; 2006 - 2009: EER = 9.5, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8, IEER = 12.2, EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5, min IEER = 13, EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12, min IEER = 13.5, EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5, one-speed fan, w/Econo; 2006 - 2009: EER = 9.5, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8, IEER = 12.2, EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12, min IEER = 13.5, EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5, one-speed fan, w/Econo; 2006 - 2009: EER = 9.5, one-speed fan, w/Econo; 2010 - 2013: EER = 10.8, one-speed fan, w/Econo; 2014 - 2015: EER = 10.8, IEER = 12.2, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8, IEER = 12.2, EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5, min IEER = 14, EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  |  | Proposed |  | f | f |  | ErRobNc | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, min IEER = 12.2, EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8, IEER = 11.4, EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8, min IEER 12.2, EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8, IEER = 11.4, EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5, min IEER = 12.7, EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3, one-speed fan, w/Econo; 2010 - 2013: EER = 9.8, one-speed fan, w/Econo; 2014 - 2015: EER = 9.8, IEER 11.4, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8, IEER = 11.4, EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5, min IEER = 15.5, EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2, min IEER = 11.6, EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9, one-speed fan, w/Econo; 2006 - 2009: EER = 9, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5, IEER = 11, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5, IEEER = 11, EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2, min IEER = 11.6, EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11, min IEER = 12.3, EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9, one-speed fan, w/Econo; 2006 - 2009: EER = 9, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5, IEER = 11, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5, IEEER = 11, EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11, min IEER = 12.3, EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER
1 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12, min IEER = 13.8, EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2017 | D17 v1.0 |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | f |  | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9, one-speed fan, w/Econo; 2006 - 2009: EER = 9, one-speed fan, w/Econo; 2010 - 2013: EER = 9.5, one-speed fan, w/Econo; 2014 - 2015: EER = 9.5, IEER = 11, two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5, IEEER = 11, EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12, min IEER = 13.8, EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  |  | Proposed | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC |  | None | 2017-01-01 |  | NoInEA |  |  |  |  | Standard | Measure updated for DEER2017 based on requirements for minimum IEER

## Cross Measure Weights
Cross Measure Weights Group definitions
Index | Cross-Measure Weight Group | Measure ID | Weight Set
| airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-woutPreEcono | Equal-Weights
| airAC-SpltPkg-65to134kBtuh-12p5eer-woutPreEcono | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-woutPreEcono | Equal-Weights
| airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | NE-HVAC-airAC-SpltPkg-65to134kBtuh-12p0eer-wPreEcono | Equal-Weights
| airAC-SpltPkg-65to134kBtuh-12p5eer-wPreEcono | NE-HVAC-airAC-SpltPkg-65to134kBtuh-13p0eer-wPreEcono | Equal-Weights