## GeneralLitReview
Whole House Fan Literature Survey for DEER 2017 Release
This worksheet contains notes from a literature survey conducted to support the Whole House Fan measure development.
NREL/ DOE Technology Fact Sheet: Whole House Fan
DOE/GO-10099-745; March 1999
Air flow:
CFM = 0.5 to 1.0 x FlrArea x ClgHt
|  | 4 | to | 8 | Range of cfm/sf
|  | 30 | to | 60 | ACH
Fan Power:
120 to 600 Watts
Green Building Adviser
Oct 26 2012
15 to 20 ACH
200 to 700 Watts
2000 to 6000 cfm
if area is 1000 to 3000, this is 2 cfm/sf
|  | ---> | 15 | ACH
Measured Natural Cooling Enhancement of a Whole House Fan
FSEC-PF-273-92
1991 Field test changing from natural ventilation-only to whole house fan
House did not have AC
24 inch model with 1/3rd hp motor
Design airflow 3100 cfm/ 1 inch static
Measured air flow and power
1150 cfm at low speed
2060 cfm at high speed
|  |  | 265 W low/ 350 Watts high |  |  |  | W | CFM
|  |  | 0.1699 | Actual W/cfm at high speed |  |  | 350 | 2060
House: cond floor area = 1300 sf
|  | 2.3846 | rated cfm/sf |  | 1.5846 | actual cfm/sf
|  | 17.8846 | ACH |  | 11.8846 | ACH
Ventilating Residences and Their Attics for Energy Conservation
Center for Building Technology, National Bureau of Standards
D. M. Burch and S. J. Treado, 1978
Physical tests in Houston
Use whole-house fan whenever:
TOA <= 82 F
RHoa <= 75%
|  | 1020 | sq ft conditioned area
|  | 439 | sq ft garage
|  | 2.5 | ton AC unit
|  | 13200 | cfm WWF at high speed
|  | 8840 | cfm of WWF at low spd
|  | 8 | clg ht (not provided in article)
|  | 8160 | volume
|  | 1.6176 | rated air changes / min
|  | 0.8 | reported air changes/min
|  | 48 | ACH | High ACH allows comfort at high indoor temperature
|  | 8 | velocity w/ AC, ft/min
|  | 40 | velocity at 48 ACH, ft/min
|  | 400 | AC cfm/ton
|  | 7.3529 | ACH for Air Conditioner fan
Building America Measure Guideline: Ventilation Cooling
D. Springer, et al, USDOE, April 2012
Whole House Fan simulation study
|  | 1527 | cfm
|  | 228 | W
|  | 0.14931 | W/cfm
Fan operates between 8 pm and 8 am if Tzone - Toa > 5 F
and Tzone > 65 F
|  | 2400 | sq ft house
|  | 0.63625 | cfm/sf
|  | 4.7719 | ACH
Indicates typical WHFan ACH can vary from 5 to 30 ACH

## Product Data
Whole House Fan Product Data from Manufacturer Literature for DEER 2017 Release
MFG | Model | CFM hi | CFM lo | Watt, hi | Watt, lo | R value | Motor | W/cfm hi | W/cfm lo | Min spd ratio
Tamarack | HV1000 | 1000 |  | 70 |  | 38 |  | 0.07
Tamarack | HV1600 | 1600 | 1150 | 230 | 207 | 38 |  | 0.14375 | 0.18 | 71.88%
Tamarack | HV3400 | 3400 | 1900 | 450 | 340 | 38 |  | 0.13235 | 0.17895 | 55.88%
AirScape | 1.0 WHF | 1047 | 600 | 85 | 55 | 14 |  | 0.081184 | 0.091667 | 57.31%
AirScape | 3.5e WHF | 3500 | 800 | 385 | 20 | 10 |  | 0.11 | 0.025 | 22.86%
AirScape | 5.0e WHF | 5064 | 1316 | 810 | 28 | 10 |  | 0.15995 | 0.021277 | 25.99%
Kohilo | 1.5 | 1532 | NA | 168 | NA | backdraft damper |  | 0.10966
Kohilo | 2.8 | 2850 | NA | 297 | NA | backdraft damper |  | 0.10421
QuietCool | HV1000 | 1104 | 552 | 78 | 39 | 6.8 |  | 0.070652 | 0.070652 | 50%
QuietCool | CL-4700 | 4672 | 3586 | 591 | 491 | 5 | PSC | 0.1265 | 0.13692 | 76.76%
QuietCool | ES-4700 | 4427 | 2050 | 494 | 64 | 5 | ECM | 0.11159 | 0.03122 | 46.31%
QuietCool | CL-3100 | 3190 | 1906 | 320 | 231 | 5 | PSC | 0.10031 | 0.1212 | 59.75%
QuietCool | ES-3100 | 3103 | NA | 264 | NA | 5 | ECM | 0.085079
QuietCool | CL-6400 | 6306 | 3226 | 703 | 329 | 5 | PSC | 0.11148 | 0.10198 | 51.16%
QuietCool | ES-6400 | 6328 | 2860 | 527 | 179 | 5 | ECM | 0.083281 | 0.062587 | 45.2%
[7 empty] | Average | 0.10667 | 0.092859
The following values are used for the DEER 2017 modeling:
[8 empty] | 0.15 | PSC | from Building America Report
[8 empty] | 0.12386 | ECM | scaled based on QuiedCool ECM vs PSC
ECM/PSC
[7 empty] | QuietCool 6400 | 74.7%
[7 empty] | QuietCool 4700 | 88.21%
[7 empty] | QuietCool 3100 | 84.81%
[7 empty] | Average: | 82.58%
[7 empty] | Alternate source: | 83.5% | avg of 1/3 and 1/2 hp motors
Note on J33: Doug Maddox: Energy Savings Potential and R&D Opportunities for Commercial Refrigeration Final Report Submitted to: U.S. Department of Energy Energy Efficiency and Renewable Energy Building Technologies Program Navigant Consulting, Inc. September 23, 2009