## Intro
DEER Packaged and Split HVAC Technology Cost Development
8/31/2015
This workbook documents the development of Residential and Commercial Split and Packaged HVAC technology costs and Commercial Boiler technology costs based on the Itron
"Ex Ante Cost Study" (2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report.pdf).
Tab | Description
CostModel Coef | The two tables on this worksheet compile the cost model data from table 3-11 and 3-17 from the Itron report for residential and commercial HVAC technologies,
including the following cost categories:
| ● | spltDXHP | commercial and residential SEER-rated, split system HP
| ● | spltDXAC | commercial and residential SEER-rated, split system AC
| ● | pkgDX<5tons | commercial SEER rated packaged AC, 60,000 kBTU/hr rated capacity or less
| ● | pkgDX>5tons | commercial EER-rated, packaged AC, 65,000 - 240,000 BTU/hr rated capacity
| ● | pkgHP<65k | commercial SEER-rated, packaged HP less than 65,000 BTU/hr rated capacity
| ● | Boiler<300k | commercial hot water boiler less than 300 kBTU/hr rated capacity
| ● | Boiler>300k | commercial hot water boiler greater than 300 kBTU/hr rated capacity
| ● | Boiler-Cond | commercial hot water boiler - condensing
| ● | StmBlr | commercial steam boiler
This table is used to apply the cost model to the applicable HVAC technologies utilized in DEER measures.
pkg Technology | These worksheets take the standard technology export from READI (exante1314 database) and apply the cost model to all applicable technologies.
& | The following steps are taken to determine the technology cost values:
boiler Technology | ● | the cost category (as listed above for various technology types) for each technology is determined.
| ● | out-of-scope technologies are identified; technologies are out of scope based on specific parameter values (efficiency range and capacity range)
as well as overall technology type
| ● | for the boiler technologies, new cost IDs are assigned based on unique costs (reset control scenario not part of boiler costs)
| ● | A constant material cost (i.e. the cost does not vary by number of units) and a per-unit material cost is calculated according to the cost model
MeasureCost | This worksheet formats the cost data into the standard ex ante MeasureCost table format for import into the ex ante database.
Measure | This worksheet takes the standard Measure table export from READI for the relevant DEER measures and assigns the MeasCostID and StdCostID where applicable.
Proposed addition to the ex ante "MeasureCost" table
Many HVAC technologies are defined for a range of capacities; for example, the technology: dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd, which has the description:
EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo
This technology has a normalizing unit of "Cap-Tons", or rated tons of cooling capacity, and has a capacity range of 11.5 - 20 tons. Energy savings and costs are defined "per ton" of
installed capacity. Claims that reference this technology specify the total number of tons being claimed; the total energy impacts and measures costs are calculated accordingly.
From the Cost Report, the material cost for the technology is determined using: Total Material cost = $4439.26 + $1150.27 * Cap-Ton (see [pkg Technology] tab for details).
A single material cost cannot be determined for the technology as it is defined. However, multiple cost records can be defined for specific capacity values for this technology.
for example: | 12 ton: | CostID = dxAC-Com-EER12.5-2Spd-12ton |  | material cost / ton = ( $4439.26 + $1150.27 * 12)/12 | 1520.2083 | per ton
| 14 ton: | CostID = dxAC-Com-EER12.5-2Spd-14ton |  | material cost / ton = ( $4439.26 + $1150.27 * 14)/14 | 1467.36 | per ton
| 20 ton: | CostID = dxAC-Com-EER12.5-2Spd-20ton |  | material cost / ton = ( $4439.26 + $1150.27 * 20)/20 | 1372.233 | per ton
Program administrator (PA) implementations for this technology type would likewise need to be defined for each individual capacity rating offered by the program.
In some circumstances, such as if the PA incents only a specific piece of equipment or specific capacity, this may be a reasonable and efficient approach to defining
Implementations and Measure Costs. In other circumstances, however, this requirement may lead to having to define dozens of Implementations for a single technology type,
all of which are derived from the same data.
A relatively simple addition to the cost table, however, allows the cost model data to be utilized across the full range of the technology definition, without the need
to define cost records or Implementation records for individual technology capacities.
The new cost record fields are:
MatlCostConst | a material cost "constant" value; the units are $ per installation, in comparison to the existing MatlCost field, which has units of $/Unit
LaborCostConst | a labor cost "constant" value; the units are $ per installation, in comparison to the existing LaborCost field, which has units of $/Unit
MinUnit | this field defines the minimum number of units that can be claimed for a single installation utilizing this cost record
MaxUnit | this field defines the maximum number of units that can be claimed for a single installation utilizing this cost record
All new fields are optional and default to not being used, but If either the MatlCostConst or LaborCostConst fields are specified, the MinUnit and MaxUnit fields must also be specified.
The basic material cost associated with a claim (i.e. not including locations cost adjustment) is determined as (Number of Installations) * MatlCostConst + (Total Number of Units) * MatlCost,
as opposed to just the (Total Number of Units) * MatlCost.
Claims that reference cost records that use these constant cost values need to claim individual installations of the technology or would need to specify the number
of installations being claimed.
All existing ex ante cost records submitted by PAs are compatible with the proposed augmented cost record format, since all of the previously existing fields retain their definitions
and the new fields default to not being used.
Issues:
2015-08-13 | ● | While the code requirement for the thermal efficiency of boilers over 300 kBTU/hr is 0.80, the data collection for the cost report did not
find any units with ratings less than 0.82. As such, costs are not available for the standard replacement boilers over 300 kBTU/hr.
| ● | The cost model leads to a lower cost for condensing boilers than for lower-efficiency non-condensing boilers.

## CostModel Coef
Cost Model Coefficients
from 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report.pdf
HVAC (packaged and split) |  |  | parameter type => |  | cont |  |  | cont |  |  | cont |  |  |  | material costs at min/max range:
|  | Constants |  | Eff |  | SEER/EER Range |  | Capacity | Capacity Range |  | Contractor | Capacity | Capacity Range |  | Minimum Capacity |  | Maximum Capacity
Sector | Category | Intercept | Manuf. | Type | SEER/EER | Min | Max | tons | Min | Max | MarkUp | BTU/hr | Min | Max | Min Eff. | Max Eff. | Min Eff. | Max Eff.
All | spltDXHP | -6472.086 | 533.053 | SEER | 456.91 | 13 | 16 | 495.468 | 1.45 | 4.9167 | 20% | 0.041289 | 17400 | 59000 | 496.0177 | 1441.3487 | 495.6301 | 774.4226
All | spltDXAC | -2762.95 | -2.081 | SEER | 230.32 | 13 | 21 | 276.012 | 1.4167 | 4.8333 | 20% | 0.023001 | 17000 | 58000 | 437.7501 | 1738.3807 | 323.418 | 704.6373
Com | pkgDX<5tons | -2295.3947 | -12.128 | SEER | 289.41 | 12 | 14 | 310.44 | 2 | 5 | 25% | 0.02587 | 24000 | 60000 | 893.1386 | 1182.5486 | 543.5195 | 659.2835
Com | pkgDX>5tons | -26554.8064 | 1351.361 | EER | 2312.226 | 9.5 | 13 | 958.56 | 6.9167 | 105.8683 | 20% | 0.07988 | 83000 | 1270420 | 490.5169 | 1660.5589 | 927.9815 | 1004.4235
COm | pkgHP<65k | -2912.992 | 175.611 | SEER | 354.91 | 13 | 15 | 298.716 | 2 | 5 | 20% | 0.024893 | 24000 | 60000 | 1236.9405 | 1591.8505 | 674.0058 | 815.9698
Commercial Space Heating Boilers | [14 empty] | material costs at min/max range:
|  | Constants |  | Eff |  | Efficiency Range |  | Capacity | Capacity Range |  | Contractor |  |  |  | Minimum Capacity |  | Maximum Capacity
Sector | Category | Intercept | Manuf. | Type | Eff | Min | Max | kBTU/hr | Min | Max | MarkUp |  |  |  | Min Eff. | Max Eff. | Min Eff. | Max Eff.
Com | Boiler<300k | -92569.8143 | 0 | AFUE | 111173.9551 | 0.83 | 0.85 | 13.5499 | 90 | 238 | 30% |  |  |  | 10.2673 | 34.9727 | 12.3086 | 21.6509
Com | Boiler>300k | -419977.5485 | 93.5035 | Et | 505493.1666 | 0.83 | 0.88 | 13.5353 | 300 | 4000 | 30% |  |  |  | 12.4529 | 96.7018 | 13.4541 | 19.7728
Com | Boiler-Cond | -129921.14 | 230.8112 | Et | 143589.4523 | 0.9 | 0.96 | 9.8654 | 300 | 4000 | 30% |  |  |  | 8.3327 | 37.0506 | 9.7504 | 11.9043
Com | StmBlr | -341927.8006 | 6196.0766 | Et | 417095.9886 | 0.8 | 0.85 | 13.3049 | 250 | 3188 | 20% |  |  |  | 5.0852 | 88.5044 | 12.6603 | 19.202
Note on H19: Paul Reeves: minimum Et of 0.82 increased to 0.83 to staballize costs at minimum size and eff. range
Note on K20: Paul Reeves: mininum cost coef. range of 67 kBTUh increased to 300 to stabalize costs at the minimum effic. and capacity range.

## pkg Technology
Ex Ante database Technology Export
Technology Group: dX AC Equipment (dxAC_equip)
Technology Type: EER Rated Package Rooftop AC (pkgEER)
This file created on 8/7/2015 10:35:27 AM while connected to localhost as sptviewer.
Program/Database Description: READI v.2.2.1 (Current DEER and Non-DEER Ex Ante data. Includes data for review)
[18 empty] | Cost Model | Category | Cost Coefficients |  |  | MatlCost | MatlCost | Minimum | Maximum
TechID | TechSource | 1spd-IEER | 2spd-IEER | EER | Cap_Min_kBTUh | Cap_Max_kBTUh | Condenser_Type | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Fan_spd | Tech Desc |  |  | Category | Index | $ | $/ton | Markup | $ | $/unit | Units | Units
dxAC-Com-Pkg-110to135kBTUh-EER10.1-1Spd | DEER2015 | 10.6 | 13.6 | 10.1 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), EIR = 0, Fan W/CFM = 0.4, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-110to135kBTUh-EER11.0-1Spd | DEER2015 | 11.6 | 14.1 | 11 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0, Fan W/CFM = 0.4, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | DEER2015 | 11.6 | 14.1 | 11 | 110 | 135 | Air | 0.663 | 0.27299 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 231.0406 | 958.56 | 0.2 | 277.25 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | DEER2015 | 12.2 | 14.3 | 11.5 | 110 | 135 | Air | 0.663 | 0.25964 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 1387.1536 | 958.56 | 0.2 | 1664.58 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | DEER2015 | 12.8 | 14.6 | 12 | 110 | 135 | Air | 0.663 | 0.24716 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 2543.2666 | 958.56 | 0.2 | 3051.92 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | DEER2015 | 13.3 | 14.9 | 12.5 | 110 | 135 | Air | 0.663 | 0.23591 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 3699.3796 | 958.56 | 0.2 | 4439.26 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-135to240kBTUh-EER10.8-1Spd | DEER2015 | 11.4 | 13.3 | 10.8 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0, Fan W/CFM = 0.41, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | DEER2015 | 11.4 | 13.3 | 10.8 | 135 | 240 | Air | 0.696 | 0.27372 | 326.4 | 0.41 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | -231.4046 | 958.56 | 0.2 | -277.69 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | DEER2015 | 12.4 | 14.2 | 11.5 | 135 | 240 | Air | 0.696 | 0.25481 | 326.4 | 0.41 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 1387.1536 | 958.56 | 0.2 | 1664.58 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | DEER2015 | 13.1 | 14.8 | 12 | 135 | 240 | Air | 0.696 | 0.24278 | 326.4 | 0.41 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 2543.2666 | 958.56 | 0.2 | 3051.92 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | DEER2015 | 13.8 | 15.5 | 12.5 | 135 | 240 | Air | 0.696 | 0.23149 | 326.4 | 0.41 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 3699.3796 | 958.56 | 0.2 | 4439.26 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-135to240kBTUh-EER9.5-1Spd | DEER2015 | 11.4 | 11.6 | 9.5 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), EIR = 0, Fan W/CFM = 0.41, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-240to760kBTUh-EER10.0-VarSpd | DEER2015 | 10.6 | 11.9 | 10 | 240 | 760 | Air | 0.708 | 0.28182 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10 (1 spd IEER = 10.6, 2 spd IEER = 11.9), EIR = 0.282, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | pkgDX>5tons | 4 | -2081.1854 | 958.56 | 0.2 | -2497.42 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | DEER2015 | 11.6 | 12.8 | 10.8 | 240 | 760 | Air | 0.705 | 0.25464 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | -231.4046 | 958.56 | 0.2 | -277.69 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-240to760kBTUh-EER10.8-VarSpd | DEER2015 | 11.6 | 12.8 | 10.8 | 240 | 760 | Air | 0.708 | 0.25619 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.256, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | pkgDX>5tons | 4 | -231.4046 | 958.56 | 0.2 | -277.69 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | DEER2015 | 12.4 | 13.6 | 11.5 | 240 | 760 | Air | 0.705 | 0.23585 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 1387.1536 | 958.56 | 0.2 | 1664.58 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-240to760kBTUh-EER11.5-VarSpd | DEER2015 | 12.4 | 13.6 | 11.5 | 240 | 760 | Air | 0.708 | 0.23663 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.237, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | DEER2015 | 13.6 | 14.8 | 12.5 | 240 | 760 | Air | 0.705 | 0.21257 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 3699.3796 | 958.56 | 0.2 | 4439.26 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-240to760kBTUh-EER12.5-VarSpd | DEER2015 | 13.6 | 14.8 | 12.5 | 240 | 760 | Air | 0.708 | 0.21235 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.212, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-240to760kBTUh-EER9.3-1Spd | DEER2015 | 11.1 | 11.1 | 9.3 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-240to760kBTUh-EER9.5-VarSpd | DEER2015 | 11.3 | 11.3 | 9.5 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-240to760kBTUh-EER9.8-1Spd | DEER2015 | 11.7 | 11.7 | 9.8 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | DEER2015 | 10.4 | 11.7 | 9.8 | 240 | 760 | Air | 0.705 | 0.28622 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | -2543.6306 | 958.56 | 0.2 | -3052.36 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-65to110kBTUh-EER10.1-1Spd-NoEcon | DEER2015 | 10.6 | 13.6 | 10.1 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), EIR = 0, Fan W/CFM = 0.4, one-speed fan, without Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-65to110kBTUh-EER11.0-1Spd-NoEcon | DEER2015 | 11.6 | 14.1 | 11 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0, Fan W/CFM = 0.4, one-speed fan, without Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | DEER2015 | 11.6 | 14.1 | 11 | 65 | 110 | Air | 0.663 | 0.27299 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 231.0406 | 958.56 | 0.2 | 277.25 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | DEER2015 | 12.2 | 14.3 | 11.5 | 65 | 110 | Air | 0.663 | 0.25964 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 1387.1536 | 958.56 | 0.2 | 1664.58 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | DEER2015 | 12.8 | 14.6 | 12 | 65 | 110 | Air | 0.663 | 0.24716 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 2543.2666 | 958.56 | 0.2 | 3051.92 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | DEER2015 | 13.9 | 15.1 | 13 | 65 | 110 | Air | 0.663 | 0.22552 | 318 | 0.4 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 4855.4926 | 958.56 | 0.2 | 5826.59 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | DEER2015 | 10.9 | 12.1 | 10.2 | 760 |  | Air | 0.705 | 0.27298 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | -1618.7402 | 958.56 | 0.2 | -1942.49 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-gte760kBTUh-EER10.2-VarSpd | DEER2015 | 10.9 | 12.1 | 10.2 | 760 |  | Air | 0.708 | 0.27513 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.275, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | DEER2015 | 11.8 | 13.1 | 11 | 760 |  | Air | 0.705 | 0.24907 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 231.0406 | 958.56 | 0.2 | 277.25 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-gte760kBTUh-EER11.0-VarSpd | DEER2015 | 11.8 | 13.1 | 11 | 760 |  | Air | 0.708 | 0.25044 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.25, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | DEER2015 | 13 | 14.2 | 12 | 760 |  | Air | 0.705 | 0.22373 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | 2543.2666 | 958.56 | 0.2 | 3051.92 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-gte760kBTUh-EER12.0-VarSpd | DEER2015 | 13 | 14.2 | 12 | 760 |  | Air | 0.708 | 0.22398 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-gte760kBTUh-EER9.0-1Spd | DEER2015 | 10.7 | 10.7 | 9 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-gte760kBTUh-EER9.2-VarSpd | DEER2015 | 11 | 11 | 9.2 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.2 (1 spd IEER = 11, 2 spd IEER = 11), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-gte760kBTUh-EER9.5-1Spd | DEER2015 | 11.3 | 11.3 | 9.5 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | one-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | DEER2015 | 10 | 11.3 | 9.5 | 760 |  | Air | 0.705 | 0.29707 | 320.4 | 0.61 | 0 | 100 | two-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo |  |  | pkgDX>5tons | 4 | -3237.2984 | 958.56 | 0.2 | -3884.76 | 1150.27 | 6.9167 | 105.8683
dxAC-Com-Pkg-gte760kBTUh-EER9.7-VarSpd | DEER2015 | 10.3 | 11.6 | 9.7 | 760 |  | Air | 0.708 | 0.29277 | 321.6 | 0.72 | 0 | 100 | var-speed | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.7 (1 spd IEER = 10.3, 2 spd IEER = 11.6), EIR = 0.293, Fan W/CFM = 0.72, var-speed fan, with Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ex Ante database Technology Export
Technology Group: dX AC Equipment (dxAC_equip)
Technology Type: SEER Rated Package Rooftop AC (pkgSEER)
This file created on 8/7/2015 10:35:48 AM while connected to localhost as sptviewer.
Program/Database Description: READI v.2.2.1 (Current DEER and Non-DEER Ex Ante data. Includes data for review)
TechID | TechSource | Sector | SEER | EER | Cap_Min_kBTUh | Cap_Max_kBTUh | Condenser_Type | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Fan_spd | Tech Desc
dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 11.75 | 55 | 65 | Air | 0.732 | 0.249 | 385.2 | 0.294 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo |  |  | pkgDX<5tons | 3 | 1744.2173 | 310.44 | 0.25 | 2180.2716 | 388.05 | 2 | 5
dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 12.58 | 55 | 65 | Air | 0.732 | 0.2362 | 385.2 | 0.251 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  |  | pkgDX<5tons | 3 | 2033.6273 | 310.44 | 0.25 | 2542.0341 | 388.05 | 2 | 5
dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 55 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  |  | pkgDX<5tons | 3 | 2323.0373 | 310.44 | 0.25 | 2903.7966 | 388.05 | 2 | 5
dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  |  | pkgDX<5tons | 3 | 2612.4473 | 310.44 | 0.25 | 3265.5591 | 388.05 | 2 | 5
dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | DEER2015 | Com | 18 | 14.04 | 55 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  |  | pkgDX<5tons | 3 | 2901.8573 | 310.44 | 0.25 | 3627.3216 | 388.05 | 2 | 5
dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 12.04 | 18 | 55 | Air | 0.6932 | 0.2456 | 338.3 | 0.294 | 0 | 100 | one-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo |  |  | pkgDX<5tons | 3 | 1744.2173 | 310.44 | 0.25 | 2180.2716 | 388.05 | 2 | 5
dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 12.9 | 18 | 55 | Air | 0.6932 | 0.234 | 338.3 | 0.251 | 0 | 100 | one-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo |  |  | pkgDX<5tons | 3 | 2033.6273 | 310.44 | 0.25 | 2542.0341 | 388.05 | 2 | 5
dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 18 | 55 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | pkgDX<5tons | 3 | 2323.0373 | 310.44 | 0.25 | 2903.7966 | 388.05 | 2 | 5
dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 18 | 55 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | pkgDX<5tons | 3 | 2612.4473 | 310.44 | 0.25 | 3265.5591 | 388.05 | 2 | 5
dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | DEER2015 | Com | 18 | 14.04 | 18 | 55 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | pkgDX<5tons | 3 | 2901.8573 | 310.44 | 0.25 | 3627.3216 | 388.05 | 2 | 5
dxAC-Com-Pkg-SEER-10.0 | DEER2015 | Com | 9.7 | 9.213 | 18 | 65 | Air | 0.6975 | 0.2971 | 372.4 | 0.4325 | 0 | 100 | one-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 9.7 (EER = 9.2), EIR = 0.297, Fan W/CFM = 0.43, one-speed fan, without Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Pkg-SEER-13.0 | DEER2015 | Com | 13 | 11.06 | 18 | 65 | Air | 0.732 | 0.2557 | 376.2 | 0.3785 | 0 | 100 | one-speed | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 13 (EER = 11.1), EIR = 0.256, Fan W/CFM = 0.38, one-speed fan, withpit Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Split-45to55kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 11.82 | 45 | 55 | Air | 0.7592 | 0.2466 | 391.6 | 0.294 | 0 | 100 | one-speed | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo |  |  | spltDXAC | 2 | 459.449 | 276.012 | 0.2 | 551.3388 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-45to55kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 12.78 | 45 | 55 | Air | 0.744 | 0.2322 | 385.2 | 0.251 | 0 | 100 | one-speed | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  |  | spltDXAC | 2 | 689.769 | 276.012 | 0.2 | 827.7228 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-45to55kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 45 | 55 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | spltDXAC | 2 | 920.089 | 276.012 | 0.2 | 1104.1068 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-45to55kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 45 | 55 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | spltDXAC | 2 | 1150.409 | 276.012 | 0.2 | 1380.4908 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-45to55kBTUh-SEER-18.0 | DEER2015 | Com | 18 | 14.04 | 45 | 55 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | spltDXAC | 2 | 1380.729 | 276.012 | 0.2 | 1656.8748 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-55to65kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 11.75 | 55 | 65 | Air | 0.732 | 0.249 | 385.2 | 0.294 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo |  |  | spltDXAC | 2 | 459.449 | 276.012 | 0.2 | 551.3388 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-55to65kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 12.58 | 55 | 65 | Air | 0.732 | 0.2362 | 385.2 | 0.251 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  |  | spltDXAC | 2 | 689.769 | 276.012 | 0.2 | 827.7228 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-55to65kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 55 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  |  | spltDXAC | 2 | 920.089 | 276.012 | 0.2 | 1104.1068 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-55to65kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  |  | spltDXAC | 2 | 1150.409 | 276.012 | 0.2 | 1380.4908 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-55to65kBTUh-SEER-18.0 | DEER2015 | Com | 18 | 14.04 | 55 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  |  | spltDXAC | 2 | 1380.729 | 276.012 | 0.2 | 1656.8748 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-lt45kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 12.17 | 18 | 45 | Air | 0.7541 | 0.2393 | 385.2 | 0.294 | 0 | 100 | one-speed | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo |  |  | spltDXAC | 2 | 459.449 | 276.012 | 0.2 | 551.3388 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-lt45kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 12.78 | 18 | 45 | Air | 0.744 | 0.2322 | 385.2 | 0.251 | 0 | 100 | one-speed | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  |  | spltDXAC | 2 | 689.769 | 276.012 | 0.2 | 827.7228 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-lt45kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 18 | 45 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | spltDXAC | 2 | 920.089 | 276.012 | 0.2 | 1104.1068 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-lt45kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 18 | 45 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | spltDXAC | 2 | 1150.409 | 276.012 | 0.2 | 1380.4908 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-lt45kBTUh-SEER-18.0 | DEER2015 | Com | 18 | 14.04 | 18 | 45 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  |  | spltDXAC | 2 | 1380.729 | 276.012 | 0.2 | 1656.8748 | 331.2144 | 1.4167 | 4.8333
dxAC-Com-Split-SEER-10.0 | DEER2015 | Com | 10 | 8.521 | 18 | 65 | Air | 0.744 | 0.3445 | 385.2 | 0.365 | 0 | 100 | one-speed | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 10 (EER = 8.5), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan, without Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Com-Split-SEER-13.0 | DEER2015 | Com | 13 | 11.08 | 18 | 65 | Air | 0.744 | 0.2582 | 385.2 | 0.348 | 0 | 100 | one-speed | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 13 (EER = 11.1), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan, without Econo |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Res-EvapAC-SEER-17.4 | DEER2015 | Res | 17.4 |  | 18 | 45 | Evap |  |  |  | 0 | 0 | 100 | one-speed | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17.4, one-speed fan, evaporative cooled condenser |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Res-Split-45to65kBTUh-SEER-14.0 | DEER2015 | Res | 14 | 11.82 | 45 | 65 | Air | 0.7592 | 0.2466 | 391.6 | 0.294 | 0 | 100 | one-speed | Residencial SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan |  |  | spltDXAC | 2 | 459.449 | 276.012 | 0.2 | 551.3388 | 331.2144 | 1.4167 | 4.8333
dxAC-Res-Split-lt45kBTUh-SEER-14.0 | DEER2015 | Res | 14 | 12.17 | 18 | 45 | Air | 0.7541 | 0.2393 | 385.2 | 0.294 | 0 | 100 | one-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan |  |  | spltDXAC | 2 | 459.449 | 276.012 | 0.2 | 551.3388 | 331.2144 | 1.4167 | 4.8333
dxAC-Res-Split-SEER-10.0 | DEER2015 | Res | 10 | 8.521 | 18 | 65 | Air | 0.744 | 0.3445 | 385.2 | 0.365 | 0 | 100 | one-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 10 (EER = 8.5), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Res-Split-SEER-13.0 | DEER2015 | Res | 13 | 11.08 | 18 | 65 | Air | 0.744 | 0.2582 | 385.2 | 0.348 | 0 | 100 | one-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 13 (EER = 11.1), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Res-Split-SEER-15.0 | DEER2015 | Res | 15 | 12.78 | 18 | 65 | Air | 0.744 | 0.2322 | 385.2 | 0.251 | 0 | 100 | one-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  |  | spltDXAC | 2 | 689.769 | 276.012 | 0.2 | 827.7228 | 331.2144 | 1.4167 | 4.8333
dxAC-Res-Split-SEER-16.0 | DEER2015 | Res | 16 | 12.48 | 18 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  |  | spltDXAC | 2 | 920.089 | 276.012 | 0.2 | 1104.1068 | 331.2144 | 1.4167 | 4.8333
dxAC-Res-Split-SEER-17.0 | DEER2015 | Res | 17 | 13.26 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  |  | spltDXAC | 2 | 1150.409 | 276.012 | 0.2 | 1380.4908 | 331.2144 | 1.4167 | 4.8333
dxAC-Res-Split-SEER-18.0 | DEER2015 | Res | 18 | 14.04 | 18 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  |  | spltDXAC | 2 | 1380.729 | 276.012 | 0.2 | 1656.8748 | 331.2144 | 1.4167 | 4.8333
dxAC-Res-Split-SEER-19.0 | DEER2015 | Res | 19 | 14.82 | 18 | 65 | Air | 0.724 | 0.201 | 360 | 0.233 | 0 | 100 | two-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Res-Split-SEER-20.0 | DEER2015 | Res | 20 | 15.6 | 18 | 65 | Air | 0.724 | 0.1897 | 360 | 0.233 | 0 | 100 | two-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxAC-Res-Split-SEER-21.0 | DEER2015 | Res | 21 | 16.38 | 18 | 65 | Air | 0.724 | 0.1795 | 360 | 0.233 | 0 | 100 | two-speed | Residencial SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan |  |  | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TechID | TechSource | Sector | SEER | EER | HSPF | COP | Cap_Min_kBTUh | Cap_Max_kBTUh | Condenser_Type | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | Fan_spd | CrankRatio | CRANKCASE-MAX-T | Tech Desc
dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 11.11 | 8 | 3.17 | 55 | 65 | Air | 0.717 | 0.2705 | 335.4 | 0.294 | two-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | pkgHP<65k | 5 | 2231.359 | 298.716 | 0.2 | 2677.6308 | 358.4592 | 2 | 5
dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 11.91 | 8.2 | 3.24 | 55 | 65 | Air | 0.717 | 0.2559 | 335.4 | 0.251 | two-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | pkgHP<65k | 5 | 2586.269 | 298.716 | 0.2 | 3103.5228 | 358.4592 | 2 | 5
dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 8.5 | 3.37 | 55 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | two-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | pkgHP<65k | 5 | 2941.179 | 298.716 | 0.2 | 3529.4148 | 358.4592 | 2 | 5
dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 9 | 3.57 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | two-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | pkgHP<65k | 5 | 3296.089 | 298.716 | 0.2 | 3955.3068 | 358.4592 | 2 | 5
dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 11.93 | 8 | 3.39 | 18 | 55 | Air | 0.744 | 0.2447 | 385.2 | 0.294 | one-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | pkgHP<65k | 5 | 2231.359 | 298.716 | 0.2 | 2677.6308 | 358.4592 | 2 | 5
dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 12.78 | 8.2 | 3.48 | 18 | 65 | Air | 0.744 | 0.2262 | 385.2 | 0.294 | one-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo | pkgHP<65k | 5 | 2586.269 | 298.716 | 0.2 | 3103.5228 | 358.4592 | 2 | 5
dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 8.5 | 3.37 | 18 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | two-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | pkgHP<65k | 5 | 2941.179 | 298.716 | 0.2 | 3529.4148 | 358.4592 | 2 | 5
dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 9 | 3.57 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | two-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | pkgHP<65k | 5 | 3296.089 | 298.716 | 0.2 | 3955.3068 | 358.4592 | 2 | 5
dxHP-Com-Pkg-lt65kBTUh-SEER-10.0 | DEER2015 | Com | 10 | 8.521 | 7.1 | 3.01 | 18 | 65 | Air | 0.744 | 0.3445 | 385.2 | 0.365 | one-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 10 (HSPF = 7.1), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan, without Econo | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxHP-Com-Pkg-lt65kBTUh-SEER-13.0 | DEER2015 | Com | 13 | 11.08 | 8.2 | 3.49 | 18 | 65 | Air | 0.744 | 0.2582 | 385.2 | 0.348 | one-speed | 0 | 100 | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 13 (HSPF = 8.2), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan, without Econo | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TechID | TechSource | Sector | SEER | EER | HSPF | COP | Cap_Min_kBTUh | Cap_Max_kBTUh | Condenser_Type | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Fan_spd | Tech Desc
dxHP-Com-Split-55to65kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 11.11 | 8.2 | 3.25 | 55 | 65 | Air | 0.717 | 0.2705 | 335.4 | 0.294 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | spltDXHP | 1 | 457.707 | 495.468 | 0.2 | 549.2484 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-55to65kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 11.91 | 8.7 | 3.44 | 55 | 65 | Air | 0.717 | 0.2559 | 335.4 | 0.251 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | spltDXHP | 1 | 914.617 | 495.468 | 0.2 | 1097.5404 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-55to65kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 9 | 3.57 | 55 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | spltDXHP | 1 | 1371.527 | 495.468 | 0.2 | 1645.8324 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-55to65kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 9.4 | 3.74 | 55 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | spltDXHP | 1 | 1828.437 | 495.468 | 0.2 | 2194.1244 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-55to65kBTUh-SEER-18.0 | DEER2015 | Com | 18 | 14.04 | 9.7 | 3.86 | 55 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | spltDXHP | 1 | 2285.347 | 495.468 | 0.2 | 2742.4164 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-lt55kBTUh-SEER-14.0 | DEER2015 | Com | 14 | 11.93 | 8.2 | 3.48 | 18 | 55 | Air | 0.744 | 0.2447 | 385.2 | 0.294 | 0 | 100 | one-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | spltDXHP | 1 | 457.707 | 495.468 | 0.2 | 549.2484 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-lt55kBTUh-SEER-15.0 | DEER2015 | Com | 15 | 12.78 | 8.7 | 3.68 | 18 | 65 | Air | 0.744 | 0.2322 | 385.2 | 0.251 | 0 | 100 | one-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | spltDXHP | 1 | 914.617 | 495.468 | 0.2 | 1097.5404 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-lt55kBTUh-SEER-16.0 | DEER2015 | Com | 16 | 12.48 | 9 | 3.57 | 18 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | spltDXHP | 1 | 1371.527 | 495.468 | 0.2 | 1645.8324 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-lt55kBTUh-SEER-17.0 | DEER2015 | Com | 17 | 13.26 | 9.4 | 3.74 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | spltDXHP | 1 | 1828.437 | 495.468 | 0.2 | 2194.1244 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-lt55kBTUh-SEER-18.0 | DEER2015 | Com | 18 | 14.04 | 9.7 | 3.86 | 18 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | spltDXHP | 1 | 2285.347 | 495.468 | 0.2 | 2742.4164 | 594.5616 | 1.45 | 4.9167
dxHP-Com-Split-SEER-10.0 | DEER2015 | Com | 10 | 8.521 | 7.1 | 3.01 | 18 | 65 | Air | 0.744 | 0.3445 | 385.2 | 0.365 | 0 | 100 | one-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 10 (HSPF = 7.1), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan, without Econo | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxHP-Com-Split-SEER-13.0 | DEER2015 | Com | 13 | 11.08 | 8.2 | 3.49 | 18 | 65 | Air | 0.744 | 0.2582 | 385.2 | 0.348 | 0 | 100 | one-speed | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 13 (HSPF = 8.2), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan, without Econo | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxHP-Res-Split-SEER-10.0 | DEER2015 | Res | 10 | 8.521 | 7.1 | 3.01 | 18 | 65 | Air | 0.744 | 0.3445 | 385.2 | 0.365 | 0 | 100 | one-speed | Residential SEER-rated split Heat Pumps, SEER = 10 (EER = 8.5), HSPF = 7.1 (COP = 3.01), EIR = 0.345, Fan W/CFM = 0.37, one-speed fan | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxHP-Res-Split-SEER-13.0 | DEER2015 | Res | 13 | 11.08 | 8.2 | 3.49 | 18 | 65 | Air | 0.744 | 0.2582 | 385.2 | 0.348 | 0 | 100 | one-speed | Residential SEER-rated split Heat Pumps, SEER = 13 (EER = 11.1), HSPF = 8.2 (COP = 3.49), EIR = 0.258, Fan W/CFM = 0.35, one-speed fan | out of scope | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dxHP-Res-Split-SEER-14.0 | DEER2015 | Res | 14 | 11.93 | 8.2 | 3.48 | 18 | 65 | Air | 0.744 | 0.2447 | 385.2 | 0.294 | 0 | 100 | one-speed | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | spltDXHP | 1 | 457.707 | 495.468 | 0.2 | 549.2484 | 594.5616 | 1.45 | 4.9167
dxHP-Res-Split-SEER-15.0 | DEER2015 | Res | 15 | 12.78 | 8.7 | 3.68 | 18 | 65 | Air | 0.744 | 0.2322 | 385.2 | 0.251 | 0 | 100 | one-speed | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | spltDXHP | 1 | 914.617 | 495.468 | 0.2 | 1097.5404 | 594.5616 | 1.45 | 4.9167
dxHP-Res-Split-SEER-16.0 | DEER2015 | Res | 16 | 12.48 | 9 | 3.57 | 18 | 65 | Air | 0.724 | 0.2381 | 360 | 0.271 | 0 | 100 | two-speed | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | spltDXHP | 1 | 1371.527 | 495.468 | 0.2 | 1645.8324 | 594.5616 | 1.45 | 4.9167
dxHP-Res-Split-SEER-17.0 | DEER2015 | Res | 17 | 13.26 | 9.4 | 3.74 | 18 | 65 | Air | 0.724 | 0.2225 | 360 | 0.271 | 0 | 100 | two-speed | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | spltDXHP | 1 | 1828.437 | 495.468 | 0.2 | 2194.1244 | 594.5616 | 1.45 | 4.9167
dxHP-Res-Split-SEER-18.0 | DEER2015 | Res | 18 | 14.04 | 9.7 | 3.86 | 18 | 65 | Air | 0.724 | 0.2086 | 360 | 0.271 | 0 | 100 | two-speed | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | spltDXHP | 1 | 2285.347 | 495.468 | 0.2 | 2742.4164 | 594.5616 | 1.45 | 4.9167

## boiler Technology
DEER Boiler Technologies
[15 empty] | Cost Model | Eff within | Category |  | Cost Coefficients |  |  | MatlCost | MatlCost | Minimum | Maximum
TechID | MeasCostID | Version | Case | Type | CapRange | Min_HeatCap | Max_HeatCap | Effic | Units | AltEffic | AltUnits | Draft | Condensing | Description | Category | range | Index | In-Scope | $ | $/kBTU/hr | Markup | $ | $/unit | Units | Units
W-Boiler_AF-lt300k-0.82-fDraft | W-Boiler_AF-lt300k-0.82-fDraft |  | Standard | HW | < 300 |  | 300 | 82 | AFUE |  |  | fDraft | no | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Boiler<300k | FALSE | 1 | FALSE
W-Boiler_Et-300to2500k-0.8-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft |  | Standard | HW | 300 - 2500 | 300 | 2500 | 80 | Et |  |  | fDraft | no | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Boiler>300k | FALSE | 2 | FALSE
W-Boiler_Et-gt2500k-0.8-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft |  | Standard | HW | > 2500 | 2500 |  | 80 | Et | 82 | Ec | fDraft | no | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Boiler>300k | FALSE | 2 | FALSE
S-Boiler_AF-lt300k-0.8-fDraft | S-Boiler_AF-lt300k-0.8-fDraft |  | Standard | Stm | < 300 |  | 300 | 80 | AFUE |  |  | fDraft | no | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | out of scope | FALSE | 0 | FALSE
S-Boiler_Et-300to2500k-0.79-fDraft | S-Boiler_Et-300to2500k-0.79-fDraft |  | Standard | Stm | 300 - 2500 | 300 | 2500 | 79 | Et |  |  | fDraft | no | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | StmBlr | FALSE | 4 | FALSE
S-Boiler_Et-gt2500k-0.79-fDraft | S-Boiler_Et-gt2500k-0.79-fDraft |  | Standard | Stm | > 2500 | 2500 |  | 79 | Et | 82 | Ec | fDraft | no | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | StmBlr | FALSE | 4 | FALSE
W-Boiler_AF-lt300k-0.84-fDraft | W-Boiler_AF-lt300k-0.84-fDraft |  | Measure | HW | < 300 |  | 300 | 84 | AFUE |  |  | fDraft | no | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F) | Boiler<300k | TRUE | 1 | TRUE | 816.308 | 13.5499 | 30% | 1061 | 17.61 | 90 | 238
W-Boiler_AF-lt300k-0.845-fDraft | W-Boiler_AF-lt300k-0.845-fDraft |  | Measure | HW | < 300 |  | 300 | 84.5 | AFUE |  |  | fDraft | no | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F) | Boiler<300k | TRUE | 1 | TRUE | 1372.1778 | 13.5499 | 30% | 1784 | 17.61 | 90 | 238
W-Boiler_AF-lt300k-0.85-fDraft | W-Boiler_AF-lt300k-0.85-fDraft |  | Measure | HW | < 300 |  | 300 | 85 | AFUE |  |  | fDraft | no | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F) | Boiler<300k | TRUE | 1 | TRUE | 1928.0475 | 13.5499 | 30% | 2506 | 17.61 | 90 | 238
W-Boiler_AF-lt300k-0.87-fDraft | W-Boiler_AF-lt300k-0.87-fDraft |  | Measure | HW | < 300 |  | 300 | 87 | AFUE |  |  | fDraft | no | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F) | Boiler<300k | FALSE | 1 | FALSE
W-Boiler_AF-lt300k-0.9-fDraft-CndStd | W-Boiler_AF-lt300k-0.9-fDraft |  | Measure | HW | < 300 |  | 300 | 90 | AFUE |  |  | fDraft | yes | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F) | Boiler-Cond | FALSE | 3 | FALSE
W-Boiler_AF-lt300k-0.9-fDraft-CndLow | W-Boiler_AF-lt300k-0.9-fDraft |  | Measure | HW | < 300 |  | 300 | 90 | AFUE |  |  | fDraft | yes | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F) | Boiler-Cond | FALSE | 3 | FALSE
W-Boiler_AF-lt300k-0.9-fDraft-CndReset | W-Boiler_AF-lt300k-0.9-fDraft |  | Measure | HW | < 300 |  | 300 | 90 | AFUE |  |  | fDraft | yes | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F) | Boiler-Cond | FALSE | 3 | FALSE
W-Boiler_AF-lt300k-0.94-fDraft-CndStd | W-Boiler_AF-lt300k-0.94-fDraft |  | Measure | HW | < 300 |  | 300 | 94 | AFUE |  |  | fDraft | yes | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F) | Boiler-Cond | FALSE | 3 | FALSE
W-Boiler_AF-lt300k-0.94-fDraft-CndLow | W-Boiler_AF-lt300k-0.94-fDraft |  | Measure | HW | < 300 |  | 300 | 94 | AFUE |  |  | fDraft | yes | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F) | Boiler-Cond | FALSE | 3 | FALSE
W-Boiler_AF-lt300k-0.94-fDraft-CndReset | W-Boiler_AF-lt300k-0.94-fDraft |  | Measure | HW | < 300 |  | 300 | 94 | AFUE |  |  | fDraft | yes | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F) | Boiler-Cond | FALSE | 3 | FALSE
W-Boiler_Et-300to2500k-0.83-fDraft | W-Boiler_Et-300to2500k-0.83-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 83 | Et |  |  | fDraft | no | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F) | Boiler>300k | TRUE | 2 | TRUE | -324.7167 | 13.5353 | 30% | -422 | 17.6 | 300 | 4000
W-Boiler_Et-300to2500k-0.85-fDraft | W-Boiler_Et-300to2500k-0.85-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 85 | Et |  |  | fDraft | no | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F) | Boiler>300k | TRUE | 2 | TRUE | 9785.1466 | 13.5353 | 30% | 12721 | 17.6 | 300 | 4000
W-Boiler_Et-300to2500k-0.9-fDraft-CndStd | W-Boiler_Et-300to2500k-0.9-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 90 | Et |  |  | fDraft | yes | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | Boiler-Cond | TRUE | 3 | TRUE | -459.8218 | 9.8654 | 30% | -598 | 12.83 | 300 | 4000
W-Boiler_Et-300to2500k-0.9-fDraft-CndLow | W-Boiler_Et-300to2500k-0.9-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 90 | Et |  |  | fDraft | yes | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
W-Boiler_Et-300to2500k-0.9-fDraft-CndReset | W-Boiler_Et-300to2500k-0.9-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 90 | Et |  |  | fDraft | yes | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
W-Boiler_Et-300to2500k-0.94-fDraft-CndStd | W-Boiler_Et-300to2500k-0.94-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 94 | Et |  |  | fDraft | yes | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | Boiler-Cond | TRUE | 3 | TRUE | 5283.7563 | 9.8654 | 30% | 6869 | 12.83 | 300 | 4000
W-Boiler_Et-300to2500k-0.94-fDraft-CndLow | W-Boiler_Et-300to2500k-0.94-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 94 | Et |  |  | fDraft | yes | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
W-Boiler_Et-300to2500k-0.94-fDraft-CndReset | W-Boiler_Et-300to2500k-0.94-fDraft |  | Measure | HW | 300 - 2500 | 300 | 2500 | 94 | Et |  |  | fDraft | yes | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
W-Boiler_Et-gt2500k-0.83-fDraft | W-Boiler_Et-gt2500k-0.83-fDraft |  | Measure | HW | > 2500 | 2500 |  | 83 | Et | 85 | Ec | fDraft | no | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F) | Boiler>300k | TRUE | 2 | TRUE | -324.7167 | 13.5353 | 30% | -422 | 17.6 | 300 | 4000
W-Boiler_Et-gt2500k-0.85-fDraft | W-Boiler_Et-gt2500k-0.85-fDraft |  | Measure | HW | > 2500 | 2500 |  | 85 | Et | 87 | Ec | fDraft | no | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F) | Boiler>300k | TRUE | 2 | TRUE | 9785.1466 | 13.5353 | 30% | 12721 | 17.6 | 300 | 4000
W-Boiler_Et-gt2500k-0.9-fDraft-CndStd | W-Boiler_Et-gt2500k-0.9-fDraft |  | Measure | HW | > 2500 | 2500 |  | 90 | Et |  | Ec | fDraft | yes | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | Boiler-Cond | TRUE | 3 | TRUE | -459.8218 | 9.8654 | 30% | -598 | 12.83 | 300 | 4000
W-Boiler_Et-gt2500k-0.9-fDraft-CndLow | W-Boiler_Et-gt2500k-0.9-fDraft |  | Measure | HW | > 2500 | 2500 |  | 90 | Et |  | Ec | fDraft | yes | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
W-Boiler_Et-gt2500k-0.9-fDraft-CndReset | W-Boiler_Et-gt2500k-0.9-fDraft |  | Measure | HW | > 2500 | 2500 |  | 90 | Et |  | Ec | fDraft | yes | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
W-Boiler_Et-gt2500k-0.94-fDraft-CndStd | W-Boiler_Et-gt2500k-0.94-fDraft |  | Measure | HW | > 2500 | 2500 |  | 94 | Et |  | Ec | fDraft | yes | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | Boiler-Cond | TRUE | 3 | TRUE | 5283.7563 | 9.8654 | 30% | 6869 | 12.83 | 300 | 4000
W-Boiler_Et-gt2500k-0.94-fDraft-CndLow | W-Boiler_Et-gt2500k-0.94-fDraft |  | Measure | HW | > 2500 | 2500 |  | 94 | Et |  | Ec | fDraft | yes | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
W-Boiler_Et-gt2500k-0.94-fDraft-CndReset | W-Boiler_Et-gt2500k-0.94-fDraft |  | Measure | HW | > 2500 | 2500 |  | 94 | Et |  | Ec | fDraft | yes | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | Boiler-Cond | TRUE | 3 | FALSE
S-Boiler_AF-lt300k-0.82-fDraft | S-Boiler_AF-lt300k-0.82-fDraft |  | Measure | Stm | < 300 |  | 300 | 82 | AFUE |  |  | fDraft | no | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | out of scope | FALSE | 0 | FALSE
S-Boiler_AF-lt300k-0.83-fDraft | S-Boiler_AF-lt300k-0.83-fDraft |  | Measure | Stm | < 300 |  | 300 | 83 | AFUE |  |  | fDraft | no | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F) | out of scope | FALSE | 0 | FALSE
S-Boiler_Et-300to2500k-0.81-fDraft | S-Boiler_Et-300to2500k-0.81-fDraft |  | Measure | Stm | 300 - 2500 | 300 | 2500 | 81 | Et |  |  | fDraft | no | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | StmBlr | TRUE | 4 | TRUE | 2116.0268 | 13.3049 | 20% | 2539 | 15.97 | 250 | 3188
S-Boiler_Et-300to2500k-0.82-fDraft | S-Boiler_Et-300to2500k-0.82-fDraft |  | Measure | Stm | 300 - 2500 | 300 | 2500 | 82 | Et |  |  | fDraft | no | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | StmBlr | TRUE | 4 | TRUE | 6286.9867 | 13.3049 | 20% | 7544 | 15.97 | 250 | 3188
S-Boiler_Et-gt2500k-0.8-fDraft | S-Boiler_Et-gt2500k-0.8-fDraft |  | Measure | Stm | > 2500 | 2500 |  | 80 | Et |  |  | fDraft | no | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | StmBlr | TRUE | 4 | TRUE | -2054.9331 | 13.3049 | 20% | -2466 | 15.97 | 250 | 3188
S-Boiler_Et-gt2500k-0.81-fDraft | S-Boiler_Et-gt2500k-0.81-fDraft |  | Measure | Stm | > 2500 | 2500 |  | 81 | Et |  |  | fDraft | no | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | StmBlr | TRUE | 4 | TRUE | 2116.0268 | 13.3049 | 20% | 2539 | 15.97 | 250 | 3188
S-Boiler_Et-gt2500k-0.82-fDraft | S-Boiler_Et-gt2500k-0.82-fDraft |  | Measure | Stm | > 2500 | 2500 |  | 82 | Et |  |  | fDraft | no | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | StmBlr | TRUE | 4 | TRUE | 6286.9867 | 13.3049 | 20% | 7544 | 15.97 | 250 | 3188
Note on B7: Paul Reeves: TechID not used for CostID when the control scenario is included in the TechID, since the control scenario is not a parameter in the cost model
Note on R18: Paul Reeves: AFUE rated condensing furnaces not included
Note on T19: Paul Reeves: repeated technology cost since cost is not dependent on the type of reset control

## MeasureCost
exante1314 database tables: MeasureCost
This file created on 8/8/2015 2:36:12 PM while connected to localhost as sptviewer.
Program/Database Description: READI v.2.2.1 (Current DEER and Non-DEER Ex Ante data. Includes data for review)
[18 empty] | Costs values per Unit |  |  |  | New Field | New Field | New Field | New Field
PA | MeasCostID | Description | NormUnit | Version | VersionSource | SourceDesc | Sector | UseCategory | UseSubCategory | TechGroup | TechType | TechID | BldgType | BldgVint | BldgLoc | CostQualifier | CostType | GenCost | LaborCost | MatlCost | InstallHrs | MatlConst | LaborConst | MinUnit | MaxUnit | LaborRate | LocCostAdj | MeasAppType | DelivType | NumUses | StartDate | ExpiryDate | Status | ReviewStatus | Comment | NomCostValue
Any | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 277.25 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 277.25 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 1664.58 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1664.58 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 3051.92 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3051.92 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 4439.26 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 4439.26 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | -277.69 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -277.69 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 1664.58 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1664.58 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 3051.92 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3051.92 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 4439.26 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 4439.26 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-240to760kBTUh-EER10.0-VarSpd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER10.0-VarSpd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | -2497.42 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -2497.42 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | -277.69 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -277.69 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 1664.58 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1664.58 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 4439.26 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 4439.26 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | -3052.36 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -3052.36 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 2180.2716 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2180.27157125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 2542.0341 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2542.03407125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 2903.7966 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2903.79657125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 3265.5591 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3265.55907125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 3627.3216 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3627.32157125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 277.25 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 277.25 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 1664.58 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1664.58 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 3051.92 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3051.92 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 5826.59 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 5826.59 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | -1942.49 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -1942.49 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 277.25 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 277.25 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | 3051.92 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3051.92 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | Any | Any | Any | Any | Full |  |  | 1150.27 |  | -3884.76 |  | 6.9 | 106 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -3884.76 + 1150.27 * Number of Units (Cap-Ton); Only units between 6.9 and 106 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 2180.2716 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2180.27157125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 2542.0341 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2542.03407125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 2903.7966 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2903.79657125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 3265.5591 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3265.55907125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 388.05 |  | 3627.3216 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3627.32157125 + 388.05 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 25%
Any | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 551.3388 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 551.3388 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 827.7228 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 827.7228 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1104.1068 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1104.1068 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1380.4908 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1380.4908 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1656.8748 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1656.8748 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 551.3388 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 551.3388 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 827.7228 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 827.7228 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1104.1068 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1104.1068 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1380.4908 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1380.4908 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1656.8748 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1656.8748 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 551.3388 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 551.3388 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 827.7228 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 827.7228 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1104.1068 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1104.1068 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1380.4908 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1380.4908 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1656.8748 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1656.8748 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 551.3388 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 551.3388 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 551.3388 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 551.3388 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Res-Split-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 827.7228 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 827.7228 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Res-Split-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1104.1068 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1104.1068 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Res-Split-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1380.4908 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1380.4908 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxAC-Res-Split-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 331.2144 |  | 1656.8748 |  | 1.4 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1656.8748 + 331.2144 * Number of Units (Cap-Ton); Only units between 1.4 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 2677.6308 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2677.6308 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 3103.5228 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3103.5228 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 3529.4148 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3529.4148 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 3955.3068 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3955.3068 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 2677.6308 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2677.6308 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 3103.5228 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3103.5228 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 3529.4148 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3529.4148 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 358.4592 |  | 3955.3068 |  | 2 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 3955.3068 + 358.4592 * Number of Units (Cap-Ton); Only units between 2 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 549.2484 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 549.2484 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 1097.5404 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1097.5404 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 1645.8324 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1645.8324 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 2194.1244 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2194.1244 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 2742.4164 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2742.4164 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 549.2484 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 549.2484 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 1097.5404 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1097.5404 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 1645.8324 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1645.8324 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 2194.1244 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2194.1244 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 2742.4164 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2742.4164 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Res-Split-SEER-14.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Res-Split-SEER-14.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 549.2484 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 549.2484 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Res-Split-SEER-15.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Res-Split-SEER-15.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 1097.5404 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1097.5404 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Res-Split-SEER-16.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Res-Split-SEER-16.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 1645.8324 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1645.8324 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Res-Split-SEER-17.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Res-Split-SEER-17.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 2194.1244 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2194.1244 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | dxHP-Res-Split-SEER-18.0 | <from TechID> | Cap-Ton | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Res | HVAC | SpaceCool | dxAC_equip | spltSEER | dxHP-Res-Split-SEER-18.0 | Any | Any | Any | Any | Full |  |  | 594.5616 |  | 2742.4164 |  | 1.5 | 5 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2742.4164 + 594.5616 * Number of Units (Cap-Ton); Only units between 1.5 and 5 tons can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | S-Boiler_Et-300to2500k-0.81-fDraft | Steam boiler (300 - 2500 kBtuh, 81.0 Et, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 15.97 |  | 2539 |  | 250 | 3190 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2539 + 15.97 * Number of Units (Cap-kBTUh); Only unts between 250 and 3190 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | S-Boiler_Et-300to2500k-0.82-fDraft | Steam boiler (300 - 2500 kBtuh, 82.0 Et, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 15.97 |  | 7544 |  | 250 | 3190 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 7544 + 15.97 * Number of Units (Cap-kBTUh); Only unts between 250 and 3190 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | S-Boiler_Et-gt2500k-0.81-fDraft | Steam boiler (> 2500 kBtuh, 81.0 Et, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 15.97 |  | 2539 |  | 250 | 3190 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2539 + 15.97 * Number of Units (Cap-kBTUh); Only unts between 250 and 3190 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | S-Boiler_Et-gt2500k-0.82-fDraft | Steam boiler (> 2500 kBtuh, 82.0 Et, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 15.97 |  | 7544 |  | 250 | 3190 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 7544 + 15.97 * Number of Units (Cap-kBTUh); Only unts between 250 and 3190 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | S-Boiler_Et-gt2500k-0.8-fDraft | Steam boiler (> 2500 kBtuh, 80.0 Et, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 15.97 |  | -2466 |  | 250 | 3190 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -2466 + 15.97 * Number of Units (Cap-kBTUh); Only unts between 250 and 3190 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 20%
Any | W-Boiler_AF-lt300k-0.845-fDraft | Hot water boiler (< 300 kBtuh, 84.5 AFUE, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | Any | Any | Any | Any | Full |  |  | 17.61 |  | 1784 |  | 90 | 240 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1784 + 17.61 * Number of Units (Cap-kBTUh); Only unts between 90 and 240 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_AF-lt300k-0.84-fDraft | Hot water boiler (< 300 kBtuh, 84.0 AFUE, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | Any | Any | Any | Any | Full |  |  | 17.61 |  | 1061 |  | 90 | 240 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 1061 + 17.61 * Number of Units (Cap-kBTUh); Only unts between 90 and 240 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_AF-lt300k-0.85-fDraft | Hot water boiler (< 300 kBtuh, 85.0 AFUE, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  | Any | Any | Any | Any | Full |  |  | 17.61 |  | 2506 |  | 90 | 240 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 2506 + 17.61 * Number of Units (Cap-kBTUh); Only unts between 90 and 240 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-300to2500k-0.83-fDraft | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 17.6 |  | -422 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -422 + 17.6 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-300to2500k-0.85-fDraft | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 17.6 |  | 12721 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 12721 + 17.6 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-300to2500k-0.94-fDraft | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 12.83 |  | 6869 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 6869 + 12.83 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-300to2500k-0.9-fDraft | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 12.83 |  | -598 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -598 + 12.83 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-gt2500k-0.83-fDraft | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 17.6 |  | -422 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -422 + 17.6 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-gt2500k-0.85-fDraft | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 17.6 |  | 12721 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 12721 + 17.6 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-gt2500k-0.94-fDraft | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 12.83 |  | 6869 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = 6869 + 12.83 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Any | W-Boiler_Et-gt2500k-0.9-fDraft | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, forced draft) | Cap-kBTUh | DEER2016 | D16v3 | 2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report | Com | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et |  | Any | Any | Any | Any | Full |  |  | 12.83 |  | -598 |  | 300 | 4000 |  | HVAC50 | RobNc | Any | 0 | 2015-01-01 |  | Proposed | DEER | Total Material cost = -598 + 12.83 * Number of Units (Cap-kBTUh); Only unts between 300 and 4000 kBTUh/hr can be claimed with this cost reference; Constant and perUnit costs include contractor markup of 30%
Note on C5: Paul Reeves: for records that specify a TechID, the cost Description is taken from the technology definition

## Measure
Ex Ante Source Tables Export
Measure Table (exante.Measure)
This file created on 8/11/2015 11:50:01 AM while connected to localhost as sptviewer.
Program/Database Description: READI v.2.2.1 (Current DEER and Non-DEER Ex Ante data. Includes data for review) | [51 empty] | Determination of Incremental Measure Cost
[49 empty] | size |  |  | Meas Tech |  |  | Std Tech
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | StdCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | min | max | use | const | per unit | $ | const | per unit | $ | Incremental $/unit | MeasureID
801 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | 277.25 | 1150.27 | 11779.95 | 138.733 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer
802 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | 277.25 | 1150.27 | 11779.95 | 277.467 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer
803 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 5826.59 | 1150.27 | 17329.29 | 277.25 | 1150.27 | 11779.95 | 554.934 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer
804 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | 277.25 | 1150.27 | 11779.95 | 138.733 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono
805 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | 277.25 | 1150.27 | 11779.95 | 277.467 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono
806 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 5826.59 | 1150.27 | 17329.29 | 277.25 | 1150.27 | 11779.95 | 554.934 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono
807 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | 277.25 | 1150.27 | 11779.95 | 138.733 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer
808 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | 277.25 | 1150.27 | 11779.95 | 277.467 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer
809 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 4439.26 | 1150.27 | 15941.96 | 277.25 | 1150.27 | 11779.95 | 416.201 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer
810 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | -277.69 | 1150.27 | 11225.01 | 194.227 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer
811 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | -277.69 | 1150.27 | 11225.01 | 332.961 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer
812 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 4439.26 | 1150.27 | 15941.96 | -277.69 | 1150.27 | 11225.01 | 471.695 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer
813 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | -277.69 | 1150.27 | 11225.01 | -3052.36 | 1150.27 | 8450.34 | 277.467 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer
814 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | -3052.36 | 1150.27 | 8450.34 | 471.694 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer
815 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 4439.26 | 1150.27 | 15941.96 | -3052.36 | 1150.27 | 8450.34 | 749.162 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer
816 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | -1942.49 | 1150.27 | 9560.21 | -3884.76 | 1150.27 | 7617.94 | 194.227 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer
817 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 277.25 | 1150.27 | 11779.95 | -3884.76 | 1150.27 | 7617.94 | 416.201 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer
818 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | -3884.76 | 1150.27 | 7617.94 | 693.668 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer
819 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2542.0341 | 388.05 | 4094.2341 | 2180.2716 | 388.05 | 3732.4716 | 90.4406 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer
820 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2903.7966 | 388.05 | 4455.9966 | 2180.2716 | 388.05 | 3732.4716 | 180.8813 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer
821 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3265.5591 | 388.05 | 4817.7591 | 2180.2716 | 388.05 | 3732.4716 | 271.3219 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer
822 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3627.3216 | 388.05 | 5179.5216 | 2180.2716 | 388.05 | 3732.4716 | 361.7625 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer
823 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2542.0341 | 388.05 | 4094.2341 | 2180.2716 | 388.05 | 3732.4716 | 90.4406 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer
824 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2903.7966 | 388.05 | 4455.9966 | 2180.2716 | 388.05 | 3732.4716 | 180.8813 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer
825 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3265.5591 | 388.05 | 4817.7591 | 2180.2716 | 388.05 | 3732.4716 | 271.3219 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer
826 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3627.3216 | 388.05 | 5179.5216 | 2180.2716 | 388.05 | 3732.4716 | 361.7625 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer
827 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2542.0341 | 388.05 | 4094.2341 | 2180.2716 | 388.05 | 3732.4716 | 90.4406 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono
828 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2903.7966 | 388.05 | 4455.9966 | 2180.2716 | 388.05 | 3732.4716 | 180.8813 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono
829 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3265.5591 | 388.05 | 4817.7591 | 2180.2716 | 388.05 | 3732.4716 | 271.3219 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono
830 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3627.3216 | 388.05 | 5179.5216 | 2180.2716 | 388.05 | 3732.4716 | 361.7625 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono
831 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer
832 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer
833 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer
834 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer
835 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer
836 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer
837 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer
838 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer
839 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer
840 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer
841 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer
842 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer
843 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono
844 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono
845 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono
846 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono
847 | RE-HV-ResAC-lt45kBtuh-15S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-15S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-15.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | RE-HV-ResAC-lt45kBtuh-15S
848 | RE-HV-ResAC-lt45kBtuh-16S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-16S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-16.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | RE-HV-ResAC-lt45kBtuh-16S
849 | RE-HV-ResAC-lt45kBtuh-17S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-17S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-17.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | RE-HV-ResAC-lt45kBtuh-17S
850 | RE-HV-ResAC-lt45kBtuh-18S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-18S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-18.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | RE-HV-ResAC-lt45kBtuh-18S
851 | RE-HV-ResAC-lt45kBtuh-19S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-19S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-19.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
852 | RE-HV-ResAC-lt45kBtuh-20S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-20S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-20.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
853 | RE-HV-ResAC-lt45kBtuh-21S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-21S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-21.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
855 | RE-HV-ResAC-45to65kBtuh-15S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-15S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-15.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | RE-HV-ResAC-45to65kBtuh-15S
856 | RE-HV-ResAC-45to65kBtuh-16S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-16S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-16.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | RE-HV-ResAC-45to65kBtuh-16S
857 | RE-HV-ResAC-45to65kBtuh-17S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-17S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-17.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | RE-HV-ResAC-45to65kBtuh-17S
858 | RE-HV-ResAC-45to65kBtuh-18S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-18S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-18.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | RE-HV-ResAC-45to65kBtuh-18S
859 | RE-HV-ResAC-45to65kBtuh-19S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-19S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-19.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
860 | RE-HV-ResAC-45to65kBtuh-20S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-20S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-20.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
861 | RE-HV-ResAC-45to65kBtuh-21S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-21S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-21.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
863 | RE-HV-ResHP-15p0S-8p7H | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-15p0S-8p7H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-15.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | RE-HV-ResHP-15p0S-8p7H
864 | RE-HV-ResHP-16p0S-9p0H | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-16p0S-9p0H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-16.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | RE-HV-ResHP-16p0S-9p0H
865 | RE-HV-ResHP-17p0S-9p4H | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-17p0S-9p4H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-17.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | RE-HV-ResHP-17p0S-9p4H
866 | RE-HV-ResHP-18p0S-9p7H | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-18p0S-9p7H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-18.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | RE-HV-ResHP-18p0S-9p7H
867 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3103.5228 | 358.4592 | 4178.9004 | 2677.6308 | 358.4592 | 3753.0084 | 141.964 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf
868 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3529.4148 | 358.4592 | 4604.7924 | 2677.6308 | 358.4592 | 3753.0084 | 283.928 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf
869 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3955.3068 | 358.4592 | 5030.6844 | 2677.6308 | 358.4592 | 3753.0084 | 425.892 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf
870 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3103.5228 | 358.4592 | 4178.9004 | 2677.6308 | 358.4592 | 3753.0084 | 141.964 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf
871 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3529.4148 | 358.4592 | 4604.7924 | 2677.6308 | 358.4592 | 3753.0084 | 283.928 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf
872 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3955.3068 | 358.4592 | 5030.6844 | 2677.6308 | 358.4592 | 3753.0084 | 425.892 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf
873 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3103.5228 | 358.4592 | 4178.9004 | 2677.6308 | 358.4592 | 3753.0084 | 141.964 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono
874 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3529.4148 | 358.4592 | 4604.7924 | 2677.6308 | 358.4592 | 3753.0084 | 283.928 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono
875 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3955.3068 | 358.4592 | 5030.6844 | 2677.6308 | 358.4592 | 3753.0084 | 425.892 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono
876 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf
877 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf
878 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf
879 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf
880 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf
881 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf
882 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf
883 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf
884 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono
885 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono
886 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono
887 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono
901 | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF | W-Boiler_AF-lt300k-0.84-fDraft |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 90 | 240 | 200 | 1061 | 17.61 | 4583 |  |  |  |  | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | 7 | #N/A | W-Boiler_AF-lt300k-0.84-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
902 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF | W-Boiler_AF-lt300k-0.845-fDraft |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 90 | 240 | 200 | 1784 | 17.61 | 5306 |  |  |  |  | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | 6 | #N/A | W-Boiler_AF-lt300k-0.845-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
903 | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF | W-Boiler_AF-lt300k-0.85-fDraft |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 90 | 240 | 200 | 2506 | 17.61 | 6028 |  |  |  |  | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | 8 | #N/A | W-Boiler_AF-lt300k-0.85-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
904 | NG-HVAC-Blr-HW-lt300kBtuh-87p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-87p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.87-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
905 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndStd | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.9-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
906 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndLow | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.9-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
907 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndReset | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.9-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
908 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndStd | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.94-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
909 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndLow | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.94-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
910 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndReset | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.94-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
911 | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.83-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -422 | 17.6 | 34778 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | 9 | #N/A | W-Boiler_Et-300to2500k-0.83-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
912 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.85-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 12721 | 17.6 | 47921 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | 10 | #N/A | W-Boiler_Et-300to2500k-0.85-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
913 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | 12 | #N/A | W-Boiler_Et-300to2500k-0.9-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
914 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | 12 | #N/A | W-Boiler_Et-300to2500k-0.9-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
915 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | 12 | #N/A | W-Boiler_Et-300to2500k-0.9-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
916 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | 11 | #N/A | W-Boiler_Et-300to2500k-0.94-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
917 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | 11 | #N/A | W-Boiler_Et-300to2500k-0.94-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
918 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | 11 | #N/A | W-Boiler_Et-300to2500k-0.94-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
919 | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.83-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -422 | 17.6 | 34778 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | 13 | #N/A | W-Boiler_Et-gt2500k-0.83-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
920 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.85-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 12721 | 17.6 | 47921 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | 14 | #N/A | W-Boiler_Et-gt2500k-0.85-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
921 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | #N/A | #N/A | W-Boiler_Et-gt2500k-0.9-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
922 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | #N/A | #N/A | W-Boiler_Et-gt2500k-0.9-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
923 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | #N/A | #N/A | W-Boiler_Et-gt2500k-0.9-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
924 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | 15 | #N/A | W-Boiler_Et-gt2500k-0.94-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
925 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | 15 | #N/A | W-Boiler_Et-gt2500k-0.94-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
926 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | 15 | #N/A | W-Boiler_Et-gt2500k-0.94-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
927 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_AF |  |  | HVAC-Blr | Steam boiler,< 300 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | S-Boiler_AF-lt300k-0.82-fDraft | S-Boiler_AF-lt300k-0.8-fDraft
928 | NG-HVAC-Blr-Stm-lt300kBtuh-83p0AFUE-Drft | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-lt300kBtuh-83p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_AF |  |  | HVAC-Blr | Steam boiler,< 300 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | S-Boiler_AF-lt300k-0.83-fDraft | S-Boiler_AF-lt300k-0.8-fDraft
929 | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-300to2500k-0.81-fDraft |  | HVAC-Blr | Steam boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 2539 | 15.97 | 26494 |  |  |  |  | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | 1 | #N/A | S-Boiler_Et-300to2500k-0.81-fDraft | S-Boiler_Et-300to2500k-0.79-fDraft
930 | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-300to2500k-0.82-fDraft |  | HVAC-Blr | Steam boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 7544 | 15.97 | 31499 |  |  |  |  | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | 2 | #N/A | S-Boiler_Et-300to2500k-0.82-fDraft | S-Boiler_Et-300to2500k-0.79-fDraft
931 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-gt2500k-0.8-fDraft |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | -2466 | 15.97 | 21489 |  |  |  |  | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | 5 | #N/A | S-Boiler_Et-gt2500k-0.8-fDraft | S-Boiler_Et-gt2500k-0.79-fDraft
932 | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-gt2500k-0.81-fDraft |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 2539 | 15.97 | 26494 |  |  |  |  | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | 3 | #N/A | S-Boiler_Et-gt2500k-0.81-fDraft | S-Boiler_Et-gt2500k-0.79-fDraft
933 | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-gt2500k-0.82-fDraft |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 7544 | 15.97 | 31499 |  |  |  |  | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | 4 | #N/A | S-Boiler_Et-gt2500k-0.82-fDraft | S-Boiler_Et-gt2500k-0.79-fDraft

## techParams (hidden)
Technology Parameters for dxAC_equip:pkgEER
TechTypeID | ParamID | ParamOrd | Code | Display | Units | ValueType | ValMin | ValMax | List | Required
2 | 210 | 1 | 1spd-IEER | One-Speed IEER | BTU/Watt | Float | 7 | 30 |  | TRUE
2 | 211 | 2 | 2spd-IEER | Two-Speed IEER | BTU/Watt | Float | 7 | 30 |  | TRUE
2 | 51 | 3 | EER | EER | BTU/Whr | Float | 7 | 30 |  | TRUE
2 | 212 | 4 | Cap_Min_kBTUh | Min Capacity (kBTUh) | kBTUh | Float | 7 | 760 |  | TRUE
2 | 213 | 5 | Cap_Max_kBTUh | Max Capacity (kBTUh) | kBTUh | Float | 7 | 760 |  | FALSE
2 | 26 | 6 | Condenser_Type | Condenser Type |  | List |  |  | Condenser Type | TRUE
2 | 214 | 7 | SensCapRatio | SHR | ratio | Text |  |  |  | FALSE
2 | 215 | 8 | COOLING-EIR | COOLING-IER (DOE2) | ratio | Float | 0 | 1 |  | FALSE
2 | 216 | 9 | CFMperTon | Supply Fan CFM/Ton | CFM/Ton | Float | 100 | 500 |  | FALSE
2 | 217 | 10 | WperCFM | Supply Fan W/CFM | W/CFM | Float | 0 | 1 |  | TRUE
2 | 218 | 11 | CrankRatio | CrankRatio (DOE2) | ratio | Float | 0 | 100000 |  | FALSE
2 | 219 | 12 | CRANKCASE-MAX-T | CRANKCASE-MAX-T (DOE2) | F | Float | 0 | 120 |  | FALSE
2 | 221 | 14 | Fan_spd | Fan Speed |  | List |  |  | Fan Speed | TRUE
Technology Parameters for dxAC_equip:pkgSEER and dxAC_equip:spltSEER
TechTypeID | ParamID | ParamOrd | Code | Display | Units | ValueType | ValMin | ValMax | List | Required
1 | 1087 | 1 | Sector | Sector |  | List |  |  | Sector | TRUE
1 | 188 | 2 | SEER | SEER | BTU/Whr | Float | 7 | 30 |  | TRUE
1 | 51 | 3 | EER | EER | BTU/Whr | Float | 7 | 30 |  | TRUE
1 | 212 | 4 | Cap_Min_kBTUh | Min Capacity (kBTUh) | kBTUh | Float | 7 | 760 |  | TRUE
1 | 213 | 5 | Cap_Max_kBTUh | Max Capacity (kBTUh) | kBTUh | Float | 7 | 760 |  | FALSE
1 | 26 | 6 | Condenser_Type | Condenser Type |  | List |  |  | Condenser Type | TRUE
1 | 214 | 7 | SensCapRatio | SHR | ratio | Text |  |  |  | FALSE
1 | 215 | 8 | COOLING-EIR | COOLING-IER (DOE2) | ratio | Float | 0 | 1 |  | FALSE
1 | 216 | 9 | CFMperTon | Supply Fan CFM/Ton | CFM/Ton | Float | 100 | 500 |  | FALSE
1 | 217 | 10 | WperCFM | Supply Fan W/CFM | W/CFM | Float | 0 | 1 |  | TRUE
1 | 218 | 11 | CrankRatio | CrankRatio (DOE2) | ratio | Float | 0 | 100000 |  | FALSE
1 | 219 | 12 | CRANKCASE-MAX-T | CRANKCASE-MAX-T (DOE2) | F | Float | 0 | 120 |  | FALSE
1 | 221 | 14 | Fan_spd | Fan Speed |  | List |  |  | Fan Speed | TRUE

## ParamLists (hidden)
Technology Parameter Lists utilized by TechType: pkgEER, pkgSEER and spltSEER
List | Code | Description
Condenser Type | Air | Air-cooled Condenser
Condenser Type | Evap | Evaporatively-cooled Condenser
Condenser Type | Water | Water-cooled Condenser
Fan Speed | one-speed | constant volume fan
Fan Speed | two-speed | two speed fan
Fan Speed | var-speed | variable speed fan
Sector | Com | commercial sector
Sector | Res | residential sector
Sector | Ind | industrial sector
Sector | Ag | agricultural sector